## README
Mapping criteria for selecting natural gas generators to model as not retained in the 2024-2025 TPP |  |  | Date: 01-11-24
Summary | This workbook contains the information being utilized in the 2024-2025 TPP busbar mapping process to identify which gas resources to model as not retained in the base case and high gas retirement scenario sensitivity portfolio. As noted in the Proposed Decision, IRP staff are still working to identify which resources should be modeled as not retained, so this workbook only depicts the data for the criteria and how the criteria will be applied to the identified specific thermal resources.
Purpose | The IRP portfolios only contain system level MW amount information on how much gas is not retained; unit specific information is not modeled. Because the TPP studies require modeling of specific units and locations, CPUC staff will share the specific list of units to model as offline with CAISO. In order to specify in the transmitted portfolios which units should be assumed to not be retained for transmission planning purposes, CPUC staff will consider the following metrics and criteria:
Selection Criteria | Capacity Factor | Criteria will prioritize not retaining resources with higher capacity factors (CFs). Resources will be sorted into quartiles based on their CFs by plant type (i.e. CCGTs will be binned only amongst other CCGTs and likewise for Peakers) and will be given a score between 1 and 4 with 4 being the highest quartile and thus highest capacity factors. CFs calculated with publicly available date from the CAISO's master generating list (1) and EIA data (2).
| Heat Rate | Criteria will prioritize not retaining resources with higher heat rates. Resources will be sorted into quartiles based on their heat rates by plant type (i.e. CCGTs will be binned only amongst other CCGTs and likewise for Peakers) and will be given a score between 1 and 4 with 4 being the highest quartile. Heat rates are derived from confidential internal CPUC IRP data (3) not included in this workbook.
| Age | Criteria will prioritize not retaining older resources. Resources will be sorted into quartiles based on their age by plant type and will be given a score between 1 and 4 with 4 being the highest quartile. Age is based on CAISO's master generating list (1) info on online dates.
| 2028 LCR Studies Local Effectiveness Factor (LEF) | Criteria will prioritize not retaining resources with low or now LEF percentages. Resources will be sorted into quartiles based on LEF percentages and given a score between 1 and 4. Resources with the lowest or no LEF percentage will be given the highest score of 4. Unlike the criteria above this will be done across both CCGTs and Peakers; all resources will be compared together.
| Proximity to Disadvantaged Communities | Criteria will prioritize not retaining resources located within a disadvantaged community (DAC). Resources within DACs receive the highest score of 4, those within 5 miles receive a score of 3, those between 5 and 10 miles away receive a score of 2, and those beyond 10 miles from a DAC receive a score of 1.
| CF weighted NOx Emission Rate | Criteria will prioritize not retaining resources with higher NOx emission rates weighted by their capacity factors. Resources will be sorted into quartiles based on weighted NOx emission rates and given a score between 1 and 4. Resources with the highest emission rates will be given the highest score of 4. These quartile calculations will be done across both CCGTs and Peakers. Emission rates calculated based on publicly available EIA emissions data (2).
| Air Quality Non-attainment Zone location | Criteria will prioritize not retaining resources located within Ozone and PM2.5 EPA Non-Attainment Areas (NAAs). A table in the tab “LCR_Battery_Info” shows the scoring breakdown between 1 and 4 based on the NAA status (5) with a score of 4 going to resources located within the highest non-attainment zones for both Ozone and PM2.5. |  | `
Additionally, existing contracts with resources will be a factor considered by staff, but that info is not included in this workbook for confidentiality reasons. Likewise, some data such has heat rates have also been omitted with only the score from 1 to 4 being included.
Criteria Scoring | As noted above, all criteria are scaled on a score between 1 and 4 with higher scores being more likely selected to be modeled as not retained.
Some data are not available for all identified resources. In these cases, the resource is given a default score in the middle of distribution, offset to make it easily noted that data is missing (e.g. resources with missing heat rates are given a score of 2.5).
Several ways to combine the scores are shown in the tabs as examples of potential methods for CPUC staff to rank the resources for selection.
Resources Included | CPUC IRP staff have identified 136 CCGT, Peakers, and Reciprocating Engine resources totaling ~25 GW NDC in the CAISO master generating list and 37 CHPs totaling ~1.96 GW.
The OTC resources have been excluded since those are already modeled for retirement. Additionally, several smaller resources in the CAISO master generating list, totaling less than 240 MW, are excluded because CPUC staff do not have data on the resources.
Separation of CHPs from Gas Resources | The IRP portfolios have separate retirement assumptions for CHPs, which are phased out between 2030 and 2040 as a default input assumption to the RESOLVE model. Because of that this workbook has a separate tab for the identified CHP resources.
Data Sources | (1) CAISO's master generating capability list for information including plant names, online dates, and net dependable capacity MWs.
(2) US Energy Information Administration (EIA) data on 2018 emissions and EPA's information on air quality non-attainment zones.
(3) Internal CPUC IRP data on existing generators for information including capacity factors, plant type, nearest busbar mapping substation, and proximity to DACs.
(4) CAISO's 2028 LCR Studies and 2022-2023 TPP for LEF percentages and LCR information.
(5) Environmental Protection Agency Green Book of Nonattainment Areas for Criteria Pollutants.

## CCGT_and_Peakers
Note: | Columns highlighted in blue are the score values for the criteria for each resource.
[35 empty] | *Resources with Not Available CF receive a 2.5 |  | *Resources with Not Available data receive a 2.5 | [9 empty] | *Resources with No published LEF receive a 4 | [7 empty] | *Resources with Not Available data receive a 2.5 |  |  | *Resources with Not Available data receive a 1.75
CAISO Master Generator List Information | [9 empty] | IRP Modeled Interconnection Point |  | EIA 2018 Emissions Data | [15 empty] | IRP Info | [10 empty] | Age |  |  | Local Need | [7 empty] | DACs and Air Pollution | [8 empty] | Sample Scoring Combinations (Scaled so Max Score=100)
RESOURCE_ID | GEN_UNIT_NAME | NET_DEPENDABLE_CAPACITY (MW) | NAMEPLATE_CAPACITY (MW) | PTO_AREA | OWNER_OR_QF | UNIT_TYPE | ENERGY_SOURCE | ZONE | COD | Substation | Voltage | EIA Code | 2018 Generation (MWh) | 2018 Useful Thermal Output (MMBtu) | 2018 Total Fuel Consumption (MMBtu) | 2018 Fuel Consumption for Electric Generation (MMBtu) | 2018 Fuel Consumption for Useful Thermal Output (MMBtu) | 2018 SO2 Emission (Tons) | 2018 NOx Emission (Tons) | 2018 CO2 Emission (Tons) | SO2 Emission Rate (Tons/total MMBtu) | NOx Emission Rate (Tons/total MMBtu) | CO2 Emission Rate (Tons/total MMBtu) | Heat Rate (MMBtu/MWh) | SO2 Emission Rate (Tons/MWh) | NOx Emission Rate (Tons/MWh) | CO2 Emission Rate (Tons/total MWh) | RESOLVE Type | Technology | Plant Name | Nameplate Capacity (MW) | AUG NQC (online 2020) | SEP NQC (online 2020) | Capacity Factor (2018) | Capcity Factor (2018) Quartile* – by Type | CONFIDENTIAL: Heat Rate (2018) (MMBtu/MWh) | Heat Rate (2018) Quartile* – by Type | CONFIDENTIAL: Has Contract past model year | Age in 2035 | Age in 2039 | Age Quartile – by Type | In Local Area | Local Area | Sub Area | Has 2028 LCR Study LEF | 2028 LCR Study Highest Local Effectiveness Factor (%) | LEF Quartile* – All Plants(Highest %=1) | 4-hr Storage able to charge in LCR (MW) | Storage Displacement Potential (High = 4-hr str > plant MW) | DAC Status | If out of DAC, distance to DAC | DAC Rank (4=inDAC to 1=outsideDAC) | NOx Emissions Rate (2018) (lbs/MWh) | CF weighted NOx Rate (CF * NOx Rate) | Nox Emissions Rate Quartile* – All Plants | Ozone Attainment Status (8hr-O3 2015) | PM2.5 Attainment Status (2012 Standard) | Ozone+PM2.5 Rank* | Simple Sum Score of all Criteria | Weighting Equally CF & Heat Rate Criteria Combined, DAC, Nox, NAZ Criteria Combined, and the LEF Criteria | Weighting Equally CF & Heat Rate Criteria Combined and DAC, Nox, NAZ Criteria Combined; Excluding Age and LEF Criteria
BDGRCK_1_UNITS | BADGER CREEK LIMITED | 48.08 | 55.3 | PGAE | Badger Creek Limited | COMBUSTION TURBINE | NATURAL GAS | ZP26 | 1991-04-01 | Badger Creek Co-Gen | 115 | 10650 | 7556 | 7823 | 74479 | 57470 | 17009 | 0.022 | 61.559 | 4356.9911 | 2.9539e-07 | 0.00082653 | 0.0585 | 7.6059 | 2.2467e-06 | 0.0062865 | 0.44494 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Badger Creek Limited | 46 | 40.2 | 38.6 | 1.875% | 1 |  | 1 |  | 44.7808 | 48.7836 | 4 | Yes | Kern | South Kern PP | No | No Published Factor | 4 | 270 | High | In_DAC |  | 4 | 12.5729 | 0.23576 | 4 | NA_Extreme | NA_Moderate | 4 | 78.5714 | 75 | 62.5
BEARMT_1_UNIT | Bear Mountain Limited | 49.21 | 48.1 | PGAE | Bear Mountain Limited | COMBUSTION TURBINE | NATURAL GAS | ZP26 | 1995-04-03 | Columbus | 115 | 10649 | 35766 | 24605 | 335893 | 279971 | 55922 | 0.092 | 264.37 | 19649.6034 | 2.739e-07 | 0.00078707 | 0.0585 | 7.8279 | 2.144e-06 | 0.006161 | 0.45793 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Bear Mountain Limited | 46 | 44 | 44 | 8.876% | 4 |  | 1 |  | 40.7726 | 44.7753 | 4 | Yes | Kern | South Kern PP, Westpark | No | No Published Factor | 4 | 270 | High | DAC_Adjacent | 0.80638 | 3 | 12.3221 | 1.0937 | 4 | NA_Extreme | NA_Moderate | 4 | 85.7143 | 84.7222 | 77.0833
CENTRY_6_PL1X4 | CENTURY GENERATING PLANT (AGGREGATE) | 41.4 |  | SCE | Colton Power, LP | FTUR | NATURAL GAS | SP15 | 2001-09-17 | Vista (SCE) | 230 | 55934 | 1266 | 0 | 20013 | 20013 | 0 | 0.0058401 | 3.1926 | 1170.7523 | 2.9182e-07 | 0.00015953 | 0.0585 | 15.8081 | 4.613e-06 | 0.0025218 | 0.92476 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Century Generating Facility | 44.8 | 36 | 36 | 0.3226% | 1 |  | 4 |  | 34.3096 | 38.3123 | 3 | Yes | LA Basin | Eastern | No | No Published Factor | 4 | 1141 | High | In_DAC |  | 4 | 5.0436 | 0.01627 | 3 | NA_Extreme | NA_Moderate | 4 | 82.1429 | 84.7222 | 77.0833
CHALK_1_UNIT | CHALK CLIFF LIMITED | 48.67 | 55.1 | PGAE | Chalk Cliff Limited | COMBUSTION TURBINE | NATURAL GAS | ZP26 | 1990-03-20 | Taft | 115 | 50003 | 15300 | 12807 | 146125 | 117668 | 28457 | 0.042151 | 23.0425 | 8548.2528 | 2.8846e-07 | 0.00015769 | 0.0585 | 7.6907 | 2.2184e-06 | 0.0012128 | 0.4499 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Chalk Cliff Limited | 46 | 43.06 | 43.72 | 3.797% | 2 |  | 1 |  | 45.8137 | 49.8164 | 4 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | DAC_Adjacent | 2.0359 | 3 | 2.4255 | 0.092094 | 4 | NA_Extreme | NA_Moderate | 4 | 78.5714 | 76.3889 | 64.5833
CHWCHL_1_UNIT | CHOW 2 PEAKER PLANT | 48.6 | 48.6 | PGAE | California Power Holdings, LLC | RECIPROCATING ENGINE | NATURAL GAS | NP15 | 2001-06-13 | Chowchilla | 115 | 56185 | 18429 | 0 | 191132 | 191132 | 0 | 0.056216 | 259.3408 | 11181.144 | 2.9412e-07 | 0.0013569 | 0.0585 | 10.3713 | 3.0504e-06 | 0.014072 | 0.60671 | CAISO_Reciprocating_Engine | Natural Gas Internal Combustion Engine | Chowchilla II | 49.6 | 48 | 48 | 4.241% | 3 |  | 2 |  | 34.5726 | 38.5753 | 3 | Yes | Fresno | Herndon, Panoche 115 kV, Wilson 115 kV | No | No Published Factor | 4 | 793 | High | DAC_Adjacent | 0.29385 | 3 | 28.1449 | 1.1938 | 4 | NA_Extreme | NA_Moderate | 4 | 82.1429 | 84.7222 | 77.0833
CORONS_6_CLRWTR | Clearwater Power Plant | 28 |  | SCE | City of Riverside (MSSA) | COMBINED CYCLE | NATURAL GAS | SP15 | 2005-02-28 | Mira Loma | 500 | 56356 | 14932 | 10116 | 132745 | 110753 | 21992 | 0.038476 | 17.9557 | 7765.5283 | 2.8985e-07 | 0.00013526 | 0.0585 | 7.4172 | 2.1499e-06 | 0.0010033 | 0.4339 | CAISO_CCGT2 | Natural Gas Fired Combined Cycle | Clearwater Power Plant | 49 | 28 | 28 | 3.479% | 1 |  | 2 |  | 30.8575 | 34.8603 | 3 | Yes | LA Basin | Eastern | No | No Published Factor | 4 | 1141 | High | In_DAC |  | 4 | 2.0066 | 0.069802 | 4 | NA_Extreme | NA_Moderate | 4 | 78.5714 | 79.1667 | 68.75
DOUBLC_1_UNITS | DOUBLE "C" LIMITED | 52.23 | 55.3 | PGAE | DOUBLE "C" LIMITED | COMBUSTION TURBINE | NATURAL GAS | ZP26 | 1989-03-14 | Double "C" Co-Gen | 115 | 50493 | 26465 | 0 | 273942 | 273942 | 0 | 0.079022 | 43.1986 | 16025.4951 | 2.8846e-07 | 0.00015769 | 0.0585 | 10.3511 | 2.9859e-06 | 0.0016323 | 0.60554 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Double C Generation Limited Partnership | 49.8 | 49.5 | 50.03 | 6.067% | 3 |  | 2 |  | 46.8301 | 50.8329 | 4 | Yes | Kern | South Kern PP | No | No Published Factor | 4 | 270 | High | In_DAC |  | 4 | 3.2646 | 0.19805 | 4 | NA_Extreme | NA_Moderate | 4 | 89.2857 | 87.5 | 81.25
DREWS_6_PL1X4 | Drews Generating Plant | 41.4 |  | SCE | Colton Power, LP | FTUR | NATURAL GAS | SP15 | 2001-08-14 | Vista (SCE) | 230 | 55935 | 777 | 0 | 16686 | 16686 | 0 | 0.0049029 | 2.6803 | 976.1242 | 2.9383e-07 | 0.00016063 | 0.0585 | 21.4749 | 6.31e-06 | 0.0034495 | 1.2563 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Drews Generating Facility | 44.8 | 36 | 36 | 0.198% | 1 |  | 4 |  | 34.4027 | 38.4055 | 3 | Yes | LA Basin | Eastern | No | No Published Factor | 4 | 1141 | High | In_DAC |  | 4 | 6.899 | 0.013659 | 3 | NA_Extreme | NA_Moderate | 4 | 82.1429 | 84.7222 | 77.0833
ELKHIL_2_PL1X3 | ELK HILLS COMBINED CYCLE (AGGREGATE) | 551.7 |  | PGAE | Elk Hills Power, LLC | COMBINED CYCLE | NATURAL GAS | NP15 | 2003-07-24 | Elk Hills | 230 | 55400 | 3797551 | 1351841 | 27124965 | 24621555 | 2503410 | 7.134 | 63.223 | 1586799.3774 | 2.63e-07 | 2.3308e-06 | 0.0585 | 6.4835 | 1.7052e-06 | 1.5112e-05 | 0.37928 | CAISO_CCGT1 | Natural Gas Fired Combined Cycle | Elk Hills Power LLC | 623 | 380 | 380 | 69.58% | 4 |  | 1 |  | 32.4603 | 36.463 | 3 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | In_DAC |  | 4 | 0.030224 | 0.021031 | 3 | NA_Extreme | NA_Moderate | 4 | 82.1429 | 84.7222 | 77.0833
ETIWND_6_GRPLND | Grapeland Peaker | 45.64 | 59 | SCE | Southern California Edison Company | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2007-09-20 | Rancho Vista | 500 | 56472 | 9892 | 0 | 129335 | 129335 | 0 | 0.036 | 0.88 | 7566.0447 | 2.7835e-07 | 6.804e-06 | 0.0585 | 13.0747 | 3.6393e-06 | 8.8961e-05 | 0.76487 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Grapeland Peaker | 59.8 | 47.39 | 47.39 | 1.888% | 1 |  | 4 |  | 28.2986 | 32.3014 | 2 | Yes | LA Basin | Eastern | No | No Published Factor | 4 | 1141 | High | In_DAC |  | 4 | 0.17792 | 0.0033598 | 1 | NA_Extreme | NA_Moderate | 4 | 71.4286 | 79.1667 | 68.75
BASICE_2_UNITS | King City Cogen | 120 | 120 | PGAE | Calpine King City Cogen | COMBINED CYCLE | NATURAL GAS | NP15 | 1989-03-14 | Coburn | 230 | 10294 | 374693 | 121100 | 3208606 | 2939494 | 269112 | 0.029 | 0.656 | 187702.1409 | 9.0382e-09 | 2.0445e-07 | 0.0585 | 7.8451 | 7.0905e-08 | 1.6039e-06 | 0.45893 | CAISO_Peaker1 | Natural Gas Fired Combined Cycle | King City Power Plant | 133.2 | 0 | 0 | 32.11% | 4 |  | 1 |  | 46.8301 | 50.8329 | 4 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | Outside_DAC | 36.7292 | 1 | 0.0032079 | 0.0010301 | 1 | A | A | 1 | 57.1429 | 62.5 | 43.75
GLNARM_7_UNIT 1 | GLEN ARM UNIT 1 | 22.13 | 30.6 | SCE | City of Pasadena | COMBUSTION TURBINE | NATURAL GAS | SP15 | 1976-01-01 | Eagle Rock (SCE) | 230 | 422 | 107233.32 | 0 | 1166292 | 1166292 | 0 | 0.235 | 7.321 | 68227.6058 | 2.0149e-07 | 6.2772e-06 | 0.0585 | 10.8762 | 2.1915e-06 | 6.8272e-05 | 0.63625 | CAISO_CCGT2 | Natural Gas Fired Combustion Turbine | Glenarm | 265.6 | 196.62 | 196.62 | 4.609% | 1 |  | 4 |  | 60.0384 | 64.0411 | 4 | Yes | LA Basin | Western | No | No Published Factor | 4 | 1141 | High | DAC_Adjacent | 1.863 | 3 | 0.13654 | 0.0062932 | 2 | NA_Extreme | NA_Moderate | 4 | 78.5714 | 79.1667 | 68.75
GLNARM_7_UNIT 2 | GLEN ARM UNIT 2 | 22.38 | 30.6 | SCE | City of Pasadena | COMBUSTION TURBINE | NATURAL GAS | SP15 | 1976-01-01 | Eagle Rock (SCE) | 230 | 422 | 107233.32 | 0 | 1166292 | 1166292 | 0 | 0.235 | 7.321 | 68227.6058 | 2.0149e-07 | 6.2772e-06 | 0.0585 | 10.8762 | 2.1915e-06 | 6.8272e-05 | 0.63625 | CAISO_CCGT2 | Natural Gas Fired Combustion Turbine | Glenarm | 265.6 | 196.62 | 196.62 | 4.609% | 1 |  | 4 |  | 60.0384 | 64.0411 | 4 | Yes | LA Basin | Western | No | No Published Factor | 4 | 1141 | High | DAC_Adjacent | 1.863 | 3 | 0.13654 | 0.0062932 | 2 | NA_Extreme | NA_Moderate | 4 | 78.5714 | 79.1667 | 68.75
GRZZLY_1_BERKLY | Berkeley Cogeneration | 26.35 | 32.5 | PGAE | The Regents of the University of California | COMBINED CYCLE | NATURAL GAS | NP15 | 2018-02-20 | Oakland J 1 | 115 | 50849 | 167747.305 | 669496 | 2008797 | 946108 | 1062689 | 0.58088 | 274.1654 | 117513.8043 | 2.8917e-07 | 0.00013648 | 0.0585 | 5.6401 | 1.6309e-06 | 0.00076977 | 0.32994 | CAISO_Peaker2 | Natural Gas Fired Combined Cycle | PE Berkeley | 28.5 | 14.67 | 14.17 | 67.19% | 4 |  | 3 |  | 17.8712 | 21.874 | 1 | Yes | Bay Area | 0 | No | No Published Factor | 4 | 2220 | High | DAC_Adjacent | 1.918 | 3 | 1.5395 | 1.0344 | 4 | NA_Marginal | A | 1.25 | 72.3214 | 85.4167 | 78.125
BORDER_6_UNITA1 | CalPeak Power Border Unit 1 | 51.25 | 52 | SDGE | CalPeak Power - Border LLC | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2001-10-26 | Otay Mesa | 230 | 55510 | 11381 | 0 | 126107 | 126107 | 0 | 0.036 | 0.701 | 7377.208 | 2.8547e-07 | 5.5588e-06 | 0.0585 | 11.0805 | 3.1632e-06 | 6.1594e-05 | 0.6482 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | CalPeak Power Border Peaker Plant | 60.5 | 51.25 | 51.25 | 2.147% | 2 |  | 3 |  | 34.2027 | 38.2055 | 3 | Yes | SD-IV | San Diego, Border | Yes | 21 | 2 | 920 | High | DAC_Adjacent | 6.0665 | 2 | 0.12319 | 0.0026454 | 1 | NA_Moderate | A | 1.5 | 51.7857 | 50 | 50
BUCKBL_2_PL1X3 | Blythe Energy Center | 493.63 |  | SCE | Blythe Energy Inc | COMBINED CYCLE | NATURAL GAS | SP15 | 2010-07-31 | BlytheSC 161 kV | 161 | 55295 | 2695876 | 0 | 19860251 | 19860251 | 0 | 6.058 | 72.27 | 1161816.5746 | 3.0503e-07 | 3.6389e-06 | 0.0585 | 7.3669 | 2.2471e-06 | 2.6808e-05 | 0.43096 | CAISO_CCGT1 | Natural Gas Fired Combined Cycle | Blythe Energy Inc | 591 | 490 | 490 | 52.07% | 4 |  | 2 |  | 25.4356 | 29.4384 | 2 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | DAC_Adjacent | 4.3913 | 3 | 0.053615 | 0.027919 | 3 | A | A | 1 | 67.8571 | 77.7778 | 66.6667
HENRTA_6_UNITA1 | GWF HENRIETTA PEAKER PLANT UNIT 1 | 49.98 | 50 | PGAE | MRP San Joaquin Energy, LLC | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2002-07-01 | Henrietta | 230 | 55807 | 32903 | 0 | 370609 | 370609 | 0 | 0.103 | 2.293 | 21680.4752 | 2.7792e-07 | 6.1871e-06 | 0.0585 | 11.2637 | 3.1304e-06 | 6.969e-05 | 0.65892 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Henrietta Peaker | 98 | 89.88 | 91.87 | 3.833% | 2 |  | 3 |  | 33.5233 | 37.526 | 3 | Yes | Fresno | 0 | No | No Published Factor | 4 | 793 | High | In_DAC |  | 4 | 0.13938 | 0.005342 | 1 | NA_Extreme | NA_Moderate | 4 | 75 | 79.1667 | 68.75
CARLS1_2_CARCT1 | Carlsbad 1 | 422 |  | SDGE | Carlsbad Energy Center LLC | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2018-11-19 | Encina | 230 | 59002 | 132599 | 0 | 1287534 | 1287534 | 0 | 0.37216 | 203.4497 | 75320.2133 | 2.8905e-07 | 0.00015802 | 0.0585 | 9.71 | 2.8067e-06 | 0.0015343 | 0.56803 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Carlsbad Energy Center | 659 | 527.5 | 527.5 | 2.297% | 2 |  | 3 |  | 17.126 | 21.1288 | 1 | Yes | SD-IV | San Diego | Yes | 20 | 2 | 920 | High | Outside_DAC | 31.4204 | 1 | 3.0686 | 0.070485 | 4 | NA_Moderate | A | 1.5 | 51.7857 | 55.5556 | 58.3333
CARLS2_1_CARCT1 | Carlsbad 2 | 105.5 | 105.5 | SDGE | Carlsbad Energy Center LLC | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2018-11-20 | Encina | 230 | 59002 | 132599 | 0 | 1287534 | 1287534 | 0 | 0.37216 | 203.4497 | 75320.2133 | 2.8905e-07 | 0.00015802 | 0.0585 | 9.71 | 2.8067e-06 | 0.0015343 | 0.56803 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Carlsbad Energy Center | 659 | 527.5 | 527.5 | 2.297% | 2 |  | 3 |  | 17.1233 | 21.126 | 1 | Yes | SD-IV | San Diego | Yes | 21 | 2 | 920 | High | Outside_DAC | 31.4204 | 1 | 3.0686 | 0.070485 | 4 | NA_Moderate | A | 1.5 | 51.7857 | 55.5556 | 58.3333
CENTER_6_PEAKER | Center Peaker | 47.3 | 59 | SCE | Southern California Edison Company | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2007-09-20 | Center | 230 | 56475 | 14862 | 0 | 180806 | 180806 | 0 | 0.053 | 0.808 | 10577.0772 | 2.9313e-07 | 4.4689e-06 | 0.0585 | 12.1657 | 3.5661e-06 | 5.4367e-05 | 0.71169 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Center Peaker | 59.8 | 47.11 | 47.11 | 2.837% | 2 |  | 3 |  | 28.2986 | 32.3014 | 2 | Yes | LA Basin | Western | Yes | 18 | 2 | 1141 | High | In_DAC |  | 4 | 0.10873 | 0.0030849 | 1 | NA_Extreme | NA_Moderate | 4 | 64.2857 | 62.5 | 68.75
HENRTA_6_UNITA2 | GWF HENRIETTA PEAKER PLANT UNIT 2 | 49.42 | 50 | PGAE | MRP San Joaquin Energy, LLC | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2002-07-01 | Henrietta | 230 | 55807 | 32903 | 0 | 370609 | 370609 | 0 | 0.103 | 2.293 | 21680.4752 | 2.7792e-07 | 6.1871e-06 | 0.0585 | 11.2637 | 3.1304e-06 | 6.969e-05 | 0.65892 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Henrietta Peaker | 98 | 89.88 | 91.87 | 3.833% | 2 |  | 3 |  | 33.5233 | 37.526 | 3 | Yes | Fresno | 0 | No | No Published Factor | 4 | 793 | High | In_DAC |  | 4 | 0.13938 | 0.005342 | 1 | NA_Extreme | NA_Moderate | 4 | 75 | 79.1667 | 68.75
HIDSRT_2_UNITS | HIGH DESERT POWER PROJECT AGGREGATE | 850 |  | SCE | High Desert Power Project, LLC | COMBINED CYCLE | NATURAL GAS | SP15 | 2003-04-21 | Roadway | 115 | 55518 | 3019302 | 0 | 22459294 | 22459294 | 0 | 6.781 | 95.897 | 1313859.5289 | 3.0192e-07 | 4.2698e-06 | 0.0585 | 7.4386 | 2.2459e-06 | 3.1761e-05 | 0.43515 | CAISO_CCGT1 | Natural Gas Fired Combined Cycle | High Desert Power Plant | 852 | 830 | 830 | 40.45% | 3 |  | 2 |  | 32.7178 | 36.7205 | 3 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | DAC_Adjacent | 0.59977 | 3 | 0.063523 | 0.025698 | 3 | NA_Severe 15 | A | 2.25 | 72.3214 | 77.0833 | 65.625
KERNFT_1_UNITS | KERN FRONT LIMITED | 52.4 | 60 | PGAE | KERN FRONT LIMITED | COMBUSTION TURBINE | NATURAL GAS | ZP26 | 1989-01-07 | Hi-Sierra Co-Gen | 115 | 50494 | 18945 | 0 | 197327 | 197327 | 0 | 0.056921 | 31.117 | 11543.5489 | 2.8846e-07 | 0.00015769 | 0.0585 | 10.4158 | 3.0046e-06 | 0.0016425 | 0.60932 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Kern Front Limited | 49.8 | 48.6 | 49.11 | 4.343% | 3 |  | 2 |  | 47.011 | 51.0137 | 4 | Yes | Kern | South Kern PP | No | No Published Factor | 4 | 270 | High | In_DAC |  | 4 | 3.285 | 0.14266 | 4 | NA_Extreme | NA_Moderate | 4 | 89.2857 | 87.5 | 81.25
COCOPP_2_CTG1 | Marsh Landing 1 | 204.2 | 222 | PGAE | Marsh Landing LLC | FTUR | NATURAL GAS | NP15 | 2013-05-01 | Contra Costa PP | 230 | 57267 | 219407 | 0 | 2538590 | 2538590 | 0 | 0.776 | 9.163 | 148506.4785 | 3.0568e-07 | 3.6095e-06 | 0.0585 | 11.5702 | 3.5368e-06 | 4.1763e-05 | 0.67685 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Marsh Landing Generating Station | 828 | 757.6 | 764.2 | 3.025% | 2 |  | 4 |  | 22.6822 | 26.6849 | 1 | Yes | Bay Area | Contra Costa | No | No Published Factor | 4 | 2220 | High | DAC_Adjacent | 1.123 | 3 | 0.083525 | 0.0025266 | 1 | NA_Marginal | A | 1.25 | 58.0357 | 72.9167 | 59.375
COCOPP_2_CTG2 | Marsh Landing 2 | 202.7 | 222 | PGAE | Marsh Landing LLC | FTUR | NATURAL GAS | NP15 | 2013-05-01 | Contra Costa PP | 230 | 57267 | 219407 | 0 | 2538590 | 2538590 | 0 | 0.776 | 9.163 | 148506.4785 | 3.0568e-07 | 3.6095e-06 | 0.0585 | 11.5702 | 3.5368e-06 | 4.1763e-05 | 0.67685 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Marsh Landing Generating Station | 828 | 757.6 | 764.2 | 3.025% | 2 |  | 4 |  | 22.6822 | 26.6849 | 1 | Yes | Bay Area | Contra Costa | No | No Published Factor | 4 | 2220 | High | DAC_Adjacent | 1.123 | 3 | 0.083525 | 0.0025266 | 1 | NA_Marginal | A | 1.25 | 58.0357 | 72.9167 | 59.375
COCOPP_2_CTG3 | Marsh Landing 3 | 208.96 | 222 | PGAE | Marsh Landing LLC | FTUR | NATURAL GAS | NP15 | 2013-05-01 | Contra Costa PP | 230 | 57267 | 219407 | 0 | 2538590 | 2538590 | 0 | 0.776 | 9.163 | 148506.4785 | 3.0568e-07 | 3.6095e-06 | 0.0585 | 11.5702 | 3.5368e-06 | 4.1763e-05 | 0.67685 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Marsh Landing Generating Station | 828 | 757.6 | 764.2 | 3.025% | 2 |  | 4 |  | 22.6822 | 26.6849 | 1 | Yes | Bay Area | Contra Costa | No | No Published Factor | 4 | 2220 | High | DAC_Adjacent | 1.123 | 3 | 0.083525 | 0.0025266 | 1 | NA_Marginal | A | 1.25 | 58.0357 | 72.9167 | 59.375
COCOPP_2_CTG4 | Marsh Landing 4 | 204.29 | 222 | PGAE | Marsh Landing LLC | FTUR | NATURAL GAS | NP15 | 2013-05-01 | Contra Costa PP | 230 | 57267 | 219407 | 0 | 2538590 | 2538590 | 0 | 0.776 | 9.163 | 148506.4785 | 3.0568e-07 | 3.6095e-06 | 0.0585 | 11.5702 | 3.5368e-06 | 4.1763e-05 | 0.67685 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Marsh Landing Generating Station | 828 | 757.6 | 764.2 | 3.025% | 2 |  | 4 |  | 22.6822 | 26.6849 | 1 | Yes | Bay Area | Contra Costa | No | No Published Factor | 4 | 2220 | High | DAC_Adjacent | 1.123 | 3 | 0.083525 | 0.0025266 | 1 | NA_Marginal | A | 1.25 | 58.0357 | 72.9167 | 59.375
COLTON_6_AGUAM1 | AGUA MANSA UNIT 1 (CITY OF COLTON) | 43 | 45.5 | SCE | City of Colton | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2003-06-27 | Vista (SCE) | 230 | 55951 | 7862 | 0 | 90083 | 90083 | 0 | 0.026 | 0.814 | 5269.8187 | 2.8862e-07 | 9.0361e-06 | 0.0585 | 11.458 | 3.307e-06 | 0.00010354 | 0.67029 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Agua Mansa Power Plant | 60.5 | 43 | 43 | 1.483% | 1 |  | 3 |  | 32.5342 | 36.537 | 2 | Yes | LA Basin | Eastern | No | No Published Factor | 4 | 1141 | High | In_DAC |  | 4 | 0.20707 | 0.0030718 | 1 | NA_Extreme | NA_Moderate | 4 | 67.8571 | 75 | 62.5
COLUSA_2_PL1X3 | Colusa Generating Station | 641 |  | PGAE | Pacific Gas & Electric Company | COMBINED CYCLE | NATURAL GAS | NP15 | 2010-12-22 | Delevan | 230 | 56532 | 2986301 | 0 | 21621556 | 21621556 | 0 | 6.468 | 42.666 | 1264852.1979 | 2.9915e-07 | 1.9733e-06 | 0.0585 | 7.2402 | 2.1659e-06 | 1.4287e-05 | 0.42355 | CAISO_CCGT1 | Natural Gas Fired Combined Cycle | Colusa Generating Station | 712.4 | 594.94 | 607.51 | 47.85% | 4 |  | 1 |  | 25.0411 | 29.0438 | 2 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | Outside_DAC | 38.9593 | 1 | 0.028574 | 0.013674 | 3 | A | A | 1 | 57.1429 | 68.0556 | 52.0833
KERNRG_1_UNITS | South Belridge Cogen Facility | 55.2 | 69.6 | PGAE | Aera Energy LLC | COMBUSTION TURBINE | NATURAL GAS | ZP26 | 1985-01-01 | Kernridge | 115 | 50752 | 439356 | 1592489 | 5305134 | 2605999 | 2699135 | 1.5452 | 844.7009 | 310348.1729 | 2.9126e-07 | 0.00015922 | 0.0585 | 5.9314 | 1.7276e-06 | 0.00094442 | 0.34698 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | South Belridge Cogeneration Facility | 94.2 | 0.2 | 0.42 | 53.24% | 4 |  | 3 |  | 51.0301 | 55.0329 | 4 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | In_DAC |  | 4 | 1.8888 | 1.0057 | 4 | NA_Extreme | NA_Moderate | 4 | 96.4286 | 95.8333 | 93.75
KINGCO_1_KINGBR | Kingsburg Cogen | 34.5 | 34.5 | PGAE | KES Kingsburg, L.P. | COMBUSTION TURBINE | NATURAL GAS | NP15 | 1990-12-05 | McCall | 230 | 10405 | 4964 | 1716 | 55903 | 50860 | 5043 | 0.017 | 0.55 | 3270.3027 | 3.041e-07 | 9.8385e-06 | 0.0585 | 10.2458 | 3.1157e-06 | 0.0001008 | 0.59937 | CAISO_Peaker2 | Natural Gas Fired Combined Cycle | Kingsburg Cogen | 36.2 | 34.5 | 34.5 | 1.565% | 1 |  | 2 |  | 45.1014 | 49.1041 | 4 | Yes | Fresno | Herndon, Hanford | No | No Published Factor | 4 | 793 | High | In_DAC |  | 4 | 0.20161 | 0.0031559 | 1 | NA_Extreme | NA_Moderate | 4 | 71.4286 | 70.8333 | 56.25
LAPLMA_2_UNIT 1 | La Paloma Generating Plant Unit #1 | 267 | 295 | PGAE | CXA La Paloma LLC | COMBINED CYCLE | NATURAL GAS | ZP26 | 2003-01-10 | Sunset | 230 | 55151 | 1059098 | 0 | 7955982 | 7955982 | 0 | 2.393 | 31.012 | 465421.6986 | 3.0078e-07 | 3.8979e-06 | 0.0585 | 7.512 | 2.2595e-06 | 2.9282e-05 | 0.43945 | CAISO_CCGT1 | Natural Gas Fired Combined Cycle | La Paloma Generating Plant | 1200 | 1029.44 | 1029.44 | 10.08% | 2 |  | 2 |  | 32.9945 | 36.9973 | 4 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | In_DAC |  | 4 | 0.058563 | 0.0059003 | 2 | NA_Extreme | NA_Moderate | 4 | 78.5714 | 77.7778 | 66.6667
LAPLMA_2_UNIT 2 | La Paloma Generating Plant Unit #2 | 266 | 295 | PGAE | CXA La Paloma LLC | COMBINED CYCLE | NATURAL GAS | ZP26 | 2003-03-05 | Sunset | 230 | 55151 | 1059098 | 0 | 7955982 | 7955982 | 0 | 2.393 | 31.012 | 465421.6986 | 3.0078e-07 | 3.8979e-06 | 0.0585 | 7.512 | 2.2595e-06 | 2.9282e-05 | 0.43945 | CAISO_CCGT1 | Natural Gas Fired Combined Cycle | La Paloma Generating Plant | 1200 | 1029.44 | 1029.44 | 10.08% | 2 |  | 2 |  | 32.8466 | 36.8493 | 3 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | In_DAC |  | 4 | 0.058563 | 0.0059003 | 2 | NA_Extreme | NA_Moderate | 4 | 75 | 77.7778 | 66.6667
LAPLMA_2_UNIT 3 | La Paloma Generating Plant Unit #3 | 266 | 295 | PGAE | CXA La Paloma LLC | COMBINED CYCLE | NATURAL GAS | ZP26 | 2003-01-13 | Sunset | 230 | 55151 | 1059098 | 0 | 7955982 | 7955982 | 0 | 2.393 | 31.012 | 465421.6986 | 3.0078e-07 | 3.8979e-06 | 0.0585 | 7.512 | 2.2595e-06 | 2.9282e-05 | 0.43945 | CAISO_CCGT1 | Natural Gas Fired Combined Cycle | La Paloma Generating Plant | 1200 | 1029.44 | 1029.44 | 10.08% | 2 |  | 2 |  | 32.9863 | 36.989 | 3 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | In_DAC |  | 4 | 0.058563 | 0.0059003 | 2 | NA_Extreme | NA_Moderate | 4 | 75 | 77.7778 | 66.6667
LAPLMA_2_UNIT 4 | LA PALOMA GENERATING PLANT, UNIT #4 | 267 | 295 | PGAE | CXA La Paloma LLC | COMBINED CYCLE | NATURAL GAS | ZP26 | 2003-03-05 | Sunset | 230 | 55151 | 1059098 | 0 | 7955982 | 7955982 | 0 | 2.393 | 31.012 | 465421.6986 | 3.0078e-07 | 3.8979e-06 | 0.0585 | 7.512 | 2.2595e-06 | 2.9282e-05 | 0.43945 | CAISO_CCGT1 | Natural Gas Fired Combined Cycle | La Paloma Generating Plant | 1200 | 1029.44 | 1029.44 | 10.08% | 2 |  | 2 |  | 32.8466 | 36.8493 | 3 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | In_DAC |  | 4 | 0.058563 | 0.0059003 | 2 | NA_Extreme | NA_Moderate | 4 | 75 | 77.7778 | 66.6667
LEBECS_2_UNITS | Pastoria Energy Facility | 799.47 |  | SCE | Pastoria Energy Facility, LLC | COMBINED CYCLE | NATURAL GAS | SP15 | 2005-05-04 | Pastoria | 230 | 55656 | 4325910 | 0 | 30793325 | 30793325 | 0 | 9.297 | 96.644 | 1801396.9396 | 3.0192e-07 | 3.1385e-06 | 0.0585 | 7.1183 | 2.1491e-06 | 2.2341e-05 | 0.41642 | CAISO_CCGT1 | Natural Gas Fired Combined Cycle | Pastoria Energy Facility, LLC | 779 | 765 | 765 | 63.39% | 4 |  | 1 |  | 30.6795 | 34.6822 | 2 | Yes | BC/Ventura | 0 | No | No Published Factor | 4 | 657 | Low | DAC_Adjacent | 6.1934 | 2 | 0.044681 | 0.028325 | 3 | NA_Extreme | NA_Moderate | 4 | 71.4286 | 79.1667 | 68.75
ELCAJN_6_LM6K | El Cajon Energy Center | 48.1 | 49.7 | SDGE | El Cajon Energy, LLC | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2010-06-16 | El Cajon | 69 | 57001 | 16736 | 0 | 187781 | 187781 | 0 | 0.058 | 1.107 | 10985.1118 | 3.0887e-07 | 5.8952e-06 | 0.0585 | 11.2202 | 3.4656e-06 | 6.6145e-05 | 0.65638 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | El Cajon Energy Center | 49.9 | 48.1 | 48.1 | 3.829% | 2 |  | 3 |  | 25.5589 | 29.5616 | 2 | Yes | SD-IV | San Diego, El Cajon | Yes | 22 | 1 | 920 | High | In_DAC |  | 4 | 0.13229 | 0.0050649 | 1 | NA_Moderate | A | 1.5 | 51.7857 | 47.2222 | 58.3333
ELCAJN_6_UNITA1 | Cuyamaca Peak Energy Plant | 45.42 | 48 | SDGE | San Diego Gas & Electric | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2002-05-29 | Santee | 115 | 55512 | 14888 | 0 | 170558 | 170558 | 0 | 0.051 | 0.945 | 9977.5734 | 2.9902e-07 | 5.5406e-06 | 0.0585 | 11.4561 | 3.4256e-06 | 6.3474e-05 | 0.67018 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Cuyamaca Peak Energy Plant | 48.7 | 45.42 | 45.42 | 3.49% | 2 |  | 3 |  | 33.6137 | 37.6164 | 3 | Yes | SD-IV | San Diego, El Cajon | Yes | 22 | 1 | 920 | High | In_DAC |  | 4 | 0.12695 | 0.0044303 | 1 | NA_Moderate | A | 1.5 | 55.3571 | 47.2222 | 58.3333
LIVOAK_1_UNIT 1 | LIVE OAK LIMITED | 49.7 | 55.3 | PGAE | Live Oak Limited | COMBUSTION TURBINE | NATURAL GAS | ZP26 | 1991-03-16 | Badger Creek Co-Gen | 115 | 54768 | 22188 | 17000 | 208677 | 170903 | 37774 | 0.062 | 175.099 | 12207.5193 | 2.9711e-07 | 0.00083909 | 0.0585 | 7.7025 | 2.2885e-06 | 0.0064631 | 0.45059 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Live Oak Limited | 46 | 42.5 | 43 | 5.506% | 3 |  | 1 |  | 44.8247 | 48.8274 | 4 | Yes | Kern | South Kern PP, Kern Oil | No | No Published Factor | 4 | 270 | High | In_DAC |  | 4 | 12.9262 | 0.71175 | 4 | NA_Extreme | NA_Moderate | 4 | 85.7143 | 83.3333 | 75
ELSEGN_2_UN1011 | El Segundo Energy Center 5/6 | 274.31 |  | SCE | El Segundo Energy Center LLC | COMBINED CYCLE | NATURAL GAS | SP15 | 2013-06-29 | El Segundo | 230 | 57901 | 1054778 | 0 | 8976146 | 8976146 | 0 | 2.6777 | 1249.6014 | 525100.876 | 2.9831e-07 | 0.00013921 | 0.0585 | 8.51 | 2.5387e-06 | 0.0011847 | 0.49783 | CAISO_CCGT2 | Natural Gas Fired Combined Cycle | El Segundo Energy Center LLC | 537.4 | 526.68 | 526.68 | 22.41% | 2 |  | 3 |  | 22.5205 | 26.5233 | 1 | Yes | LA Basin | Western, El Nido | Yes | 27 | 1 | 1141 | High | In_DAC |  | 4 | 2.3694 | 0.53088 | 4 | NA_Extreme | NA_Moderate | 4 | 67.8571 | 62.5 | 81.25
ELSEGN_2_UN2021 | El Segundo Energy Center 7/8 | 271.74 |  | SCE | El Segundo Energy Center LLC | COMBINED CYCLE | NATURAL GAS | SP15 | 2013-06-29 | El Segundo | 230 | 57901 | 1054778 | 0 | 8976146 | 8976146 | 0 | 2.6777 | 1249.6014 | 525100.876 | 2.9831e-07 | 0.00013921 | 0.0585 | 8.51 | 2.5387e-06 | 0.0011847 | 0.49783 | CAISO_CCGT2 | Natural Gas Fired Combined Cycle | El Segundo Energy Center LLC | 537.4 | 526.68 | 526.68 | 22.41% | 2 |  | 3 |  | 22.5205 | 26.5233 | 1 | Yes | LA Basin | Western, El Nido | Yes | 27 | 1 | 1141 | High | In_DAC |  | 4 | 2.3694 | 0.53088 | 4 | NA_Extreme | NA_Moderate | 4 | 67.8571 | 62.5 | 81.25
ESCNDO_6_PL1X2 | MMC Escondido Aggregate | 48.71 | 49.5 | SDGE | Escondido Energy Center | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2014-01-25 | Escondido | 230 | 55538 | 25261 | 0 | 264756 | 264756 | 0 | 0.08 | 1.17 | 15488.1179 | 3.0217e-07 | 4.4192e-06 | 0.0585 | 10.4808 | 3.1669e-06 | 4.6316e-05 | 0.61312 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Escondido Energy Center | 49.9 | 48.71 | 48.71 | 5.779% | 3 |  | 2 |  | 21.9452 | 25.9479 | 1 | Yes | SD-IV | San Diego | Yes | 21 | 2 | 920 | High | Outside_DAC | 22.2991 | 1 | 0.092633 | 0.0053532 | 1 | NA_Moderate | A | 1.5 | 41.0714 | 47.2222 | 45.8333
ESCNDO_6_UNITB1 | CalPeak Power Enterprise Unit 1 | 48.04 | 52 | SDGE | CalPeak Power - Enterprise LLC | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2001-10-23 | Escondido | 230 | 55513 | 12241 | 0 | 135153 | 135153 | 0 | 0.04 | 0.902 | 7906.3953 | 2.9596e-07 | 6.6739e-06 | 0.0585 | 11.041 | 3.2677e-06 | 7.3687e-05 | 0.64589 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | CalPeak Power Enterprise Peaker Plant | 58.9 | 48.04 | 48.04 | 2.372% | 2 |  | 3 |  | 34.211 | 38.2137 | 3 | Yes | SD-IV | San Diego | Yes | 21 | 2 | 920 | High | Outside_DAC | 22.0442 | 1 | 0.14737 | 0.0034964 | 1 | NA_Moderate | A | 1.5 | 48.2143 | 47.2222 | 45.8333
ESCO_6_GLMQF | Goal Line Cogen | 49.9 | 49.9 | SDGE | Goal Line, L.P. | COMBUSTION TURBINE | NATURAL GAS | SP15 | 1994-01-01 | Escondido | 230 | 54749 | 18142 | 13581 | 176484 | 146962 | 29522 | 0.051 | 1.254 | 10324.2419 | 2.8898e-07 | 7.1055e-06 | 0.0585 | 8.1007 | 2.3409e-06 | 5.7559e-05 | 0.47388 | CAISO_Peaker1 | Natural Gas Fired Combined Cycle | Goal Line LP | 51.4 | 36.41 | 34.79 | 4.029% | 3 |  | 1 |  | 42.0247 | 46.0274 | 4 | Yes | SD-IV | San Diego | Yes | 22 | 1 | 920 | High | Outside_DAC | 21.3375 | 1 | 0.11512 | 0.0046383 | 1 | NA_Moderate | A | 1.5 | 44.6429 | 34.7222 | 39.5833
LODI25_2_UNIT 1 | LODI GAS TURBINE | 25 | 25.4 | PGAE | NCPA (MSS Agreement - S14) | FTUR | NATURAL GAS | NP15 | 1986-01-01 | Lodi | 230 | 7451 | 3492 | 0 | 56217 | 56217 | 0 | 0.016232 | 8.8734 | 3288.6715 | 2.8873e-07 | 0.00015784 | 0.0585 | 16.0988 | 4.6483e-06 | 0.0025411 | 0.94177 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Lodi | 27.4 | 23.8 | 23.8 | 1.455% | 1 |  | 4 |  | 50.0301 | 54.0329 | 4 | Yes | Stockton | Lockeford | No | No Published Factor | 4 | 545 | High | DAC_Adjacent | 2.1101 | 3 | 5.0821 | 0.073937 | 4 | NA_Extreme | NA_Moderate | 4 | 85.7143 | 84.7222 | 77.0833
GATWAY_2_PL1X3 | GATEWAY GENERATING STATION | 585 |  | PGAE | Pacific Gas & Electric Company | COMBINED CYCLE | NATURAL GAS | NP15 | 2009-01-06 | Contra Costa PP | 230 | 56476 | 2929751 | 0 | 21178639 | 21178639 | 0 | 6.469 | 68.529 | 1238941.7343 | 3.0545e-07 | 3.2358e-06 | 0.0585 | 7.2288 | 2.208e-06 | 2.3391e-05 | 0.42288 | CAISO_CCGT1 | Natural Gas Fired Combined Cycle | Gateway Generating Station | 619.7 | 523.12 | 533.12 | 53.97% | 4 |  | 1 |  | 27 | 31.0027 | 2 | Yes | Bay Area | Contra Costa | No | No Published Factor | 4 | 2220 | High | DAC_Adjacent | 0.80048 | 3 | 0.046781 | 0.025248 | 3 | NA_Marginal | A | 1.25 | 65.1786 | 74.3056 | 61.4583
GILROY_1_UNIT | GILROY COGEN AGGREGATE | 120 |  | PGAE | Calpine Gilroy Cogen, L.P. | COMBINED CYCLE | NATURAL GAS | NP15 | 1987-01-01 | Llagas | 115 | 10034 | 102682 | 57166 | 915492 | 791214 | 124278 | 0.266 | 10.354 | 53555.9082 | 2.9055e-07 | 1.131e-05 | 0.0585 | 7.7055 | 2.2389e-06 | 8.7147e-05 | 0.45077 | CAISO_Peaker1 | Natural Gas Fired Combined Cycle | Gilroy Power Plant | 130 | 105 | 110 | 9.017% | 4 |  | 1 |  | 49.0301 | 53.0329 | 4 | Yes | Bay Area | Llagas, San Jose, South Bay-Moss Landing | Yes | 56 | 1 | 2220 | High | In_DAC |  | 4 | 0.17429 | 0.015716 | 3 | NA_Marginal | A | 1.25 | 65.1786 | 52.0833 | 65.625
GILRPP_1_PL1X2 | GILROY ENERGY CENTER UNITS 1&2 AGGREGATE | 95.2 |  | PGAE | Gilroy Energy Center, LLC | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2002-01-29 | Llagas | 115 | 55810 | 25659 | 0 | 304435 | 304435 | 0 | 0.093 | 4.683 | 17809.3232 | 3.0548e-07 | 1.5383e-05 | 0.0585 | 11.8646 | 3.6245e-06 | 0.00018251 | 0.69408 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Gilroy Peaking Energy Center | 135 | 141.4 | 141.4 | 2.17% | 2 |  | 3 |  | 33.9425 | 37.9452 | 3 | Yes | Bay Area | Llagas, San Jose, South Bay-Moss Landing | Yes | 56 | 1 | 2220 | High | In_DAC |  | 4 | 0.36502 | 0.0079198 | 2 | NA_Marginal | A | 1.25 | 58.0357 | 49.3056 | 61.4583
GILRPP_1_PL3X4 | GILROY ENERGY CENTER, UNIT #3 | 46.2 | 49.9 | PGAE | Gilroy Energy Center, LLC | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2002-02-28 | Llagas | 115 | 55810 | 25659 | 0 | 304435 | 304435 | 0 | 0.093 | 4.683 | 17809.3232 | 3.0548e-07 | 1.5383e-05 | 0.0585 | 11.8646 | 3.6245e-06 | 0.00018251 | 0.69408 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Gilroy Peaking Energy Center | 135 | 141.4 | 141.4 | 2.17% | 2 |  | 3 |  | 33.8603 | 37.863 | 3 | Yes | Bay Area | Llagas, San Jose, South Bay-Moss Landing | Yes | 56 | 1 | 2220 | High | In_DAC |  | 4 | 0.36502 | 0.0079198 | 2 | NA_Marginal | A | 1.25 | 58.0357 | 49.3056 | 61.4583
GLNARM_2_UNIT 5 | Glenarm Turbine 5 | 65.81 | 71 | SCE | City of Pasadena | COMBINED CYCLE | NATURAL GAS | SP15 | 2016-12-20 | Gould | 230 | 422 | 107233.32 | 0 | 1166292 | 1166292 | 0 | 0.235 | 7.321 | 68227.6058 | 2.0149e-07 | 6.2772e-06 | 0.0585 | 10.8762 | 2.1915e-06 | 6.8272e-05 | 0.63625 | CAISO_CCGT2 | Natural Gas Fired Combustion Turbine | Glenarm | 265.6 | 196.62 | 196.62 | 4.609% | 1 |  | 4 |  | 19.0411 | 23.0438 | 1 | Yes | LA Basin | Western | Yes | 10 | 3 | 1141 | High | DAC_Adjacent | 1.863 | 3 | 0.13654 | 0.0062932 | 2 | NA_Extreme | NA_Moderate | 4 | 64.2857 | 70.8333 | 68.75
MIRLOM_6_PEAKER | Mira Loma Peaker | 47.18 | 59 | SCE | Southern California Edison Company | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2007-09-20 | Mira Loma | 500 | 56473 | 24008 | 0 | 243113 | 243113 | 0 | 0.074 | 1.774 | 14222.0112 | 3.0439e-07 | 7.297e-06 | 0.0585 | 10.1263 | 3.0823e-06 | 7.3892e-05 | 0.59239 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Mira Loma Peaker | 49.8 | 46 | 46 | 5.503% | 3 |  | 2 |  | 28.2986 | 32.3014 | 2 | Yes | LA Basin | Eastern | No | No Published Factor | 4 | 1141 | High | In_DAC |  | 4 | 0.14778 | 0.008133 | 2 | NA_Extreme | NA_Moderate | 4 | 75 | 81.9444 | 72.9167
MKTRCK_1_UNIT 1 | MCKITTRICK LIMITED | 47.72 | 57.9 | PGAE | McKittrick Limited | COMBUSTION TURBINE | NATURAL GAS | ZP26 | 1991-10-16 | Temblor | 115 | 50612 | 21742 | 19119 | 210698 | 168212 | 42486 | 0.054 | 154.424 | 12325.747 | 2.5629e-07 | 0.00073292 | 0.0585 | 7.7367 | 1.9829e-06 | 0.0056704 | 0.4526 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | McKittrick Limited | 46 | 42 | 42.12 | 5.396% | 3 |  | 1 |  | 44.2384 | 48.2411 | 4 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | In_DAC |  | 4 | 11.3408 | 0.6119 | 4 | NA_Extreme | NA_Moderate | 4 | 85.7143 | 83.3333 | 75
OAK C_7_UNIT 3 | OAKLAND STATION C GT UNIT 3 | 55 | 55 | PGAE | Oakland Power Company LLC | COMBUSTION TURBINE | DISTILLATE | NP15 | 1978-01-01 | Oakland C | 115 | 6211 | 3852 | 0 | 65556 | 65556 | 0 | 10.3723 | 29.3388 | 5123.4491 | 0.00015822 | 0.00044754 | 0.078154 | 17.0187 | 0.0026927 | 0.0076165 | 1.3301 | CAISO_Peaker2 | Petroleum Liquids | Dynegy Oakland Power Plant | 223.5 | 165 | 165 | 0.1967% | 1 |  | 4 |  | 58.0356 | 62.0384 | 4 | Yes | Bay Area | Oakland | No | No Published Factor | 4 | 2220 | High | DAC_Adjacent | 0.35501 | 3 | 15.233 | 0.02997 | 3 | NA_Marginal | A | 1.25 | 72.3214 | 74.3056 | 61.4583
OMAR_2_UNIT 1 | KERN RIVER COGENERATION CO. UNIT 1 | 75 | 85 | SCE | Chevron Power Holdings, INC | FTUR | NATURAL GAS | SP15 | 1985-05-01 | Dexzel | 115 | 10496 | 729451 | 2695012 | 8990991 | 4344417 | 4646574 | 2.6187 | 1431.5752 | 525969.3025 | 2.9126e-07 | 0.00015922 | 0.0585 | 5.9557 | 1.7347e-06 | 0.00094829 | 0.34841 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Kern River Cogeneration | 300 | 297.01 | 302.36 | 27.76% | 4 |  | 4 |  | 50.7014 | 54.7041 | 4 | Yes | BC/Ventura | 0 | No | No Published Factor | 4 | 657 | High | In_DAC |  | 4 | 1.8966 | 0.52643 | 4 | NA_Extreme | NA_Moderate | 4 | 100 | 100 | 100
GOLETA_6_ELLWOD | ELLWOOD ENERGY SUPPORT FACILITY | 54 | 56 | SCE | GenOn California South, LP | COMBUSTION TURBINE | NATURAL GAS | SP15 | 1998-04-29 | Goleta | 230 | 8076 | 6212 | 0 | 89752 | 89752 | 0 | 0.02589 | 14.1534 | 5250.4554 | 2.8846e-07 | 0.00015769 | 0.0585 | 14.4482 | 4.1678e-06 | 0.0022784 | 0.84521 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Ellwood | 58 | 0 | 0 | 1.223% | 1 |  | 4 |  | 37.6986 | 41.7014 | 3 | Yes | BC/Ventura | S.Clara, Moorpark, Goleta | No | No Published Factor | 4 | 657 | High | Outside_DAC | 41.9625 | 1 | 4.5568 | 0.055713 | 4 | A | A | 1 | 64.2857 | 70.8333 | 56.25
GOLETA_6_EXGEN | EXXON COMPANY USA | 48.2 | 48.2 | SCE | SOUTHERN CALIFORNIA EDISON COMPANY |  | OTHER | SP15 | 1993-08-19 | Goleta | 230 | 50270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | CAISO_Peaker1 | Natural Gas Fired Combined Cycle | EXXON COMPANY USA | 49.3 | 0 | 0 | 0% | 1 |  | 1 |  | 42.3945 | 46.3973 | 4 | Yes | BC/Ventura | S.Clara, Moorpark, Goleta | No | No Published Factor | 4 | 657 | High | Outside_DAC | 52.172 | 1 | Not Available | Not Available | 2.5 | A | A | 1 | 51.7857 | 54.1667 | 31.25
GRNLF1_1_PL1X2 | Greenleaf 1 | 60 |  | PGAE | Calpine Greenleaf Holdings, Inc. | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2022-06-24 | Pease | 115 | 10350 | 67014 | 28766 | 596062 | 530684 | 65378 | 0.161 | 29.759 | 34869.3836 | 2.7011e-07 | 4.9926e-05 | 0.0585 | 7.919 | 2.139e-06 | 0.00039536 | 0.46326 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Greenleaf 1 Power Plant | 0 | 0 | 0 | Not Available | 2.5 |  | 1 |  | 13.5288 | 17.5315 | 1 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | DAC_Adjacent | 6.5243 | 2 | 0.79073 | Not Available | 2.5 | A | A | 1 | 50 | 63.1944 | 44.7917
OMAR_2_UNIT 2 | KERN RIVER COGENERATION CO. UNIT 2 | 75 | 85 | SCE | Chevron Power Holdings, INC | FTUR | NATURAL GAS | SP15 | 1985-05-01 | Dexzel | 115 | 10496 | 729451 | 2695012 | 8990991 | 4344417 | 4646574 | 2.6187 | 1431.5752 | 525969.3025 | 2.9126e-07 | 0.00015922 | 0.0585 | 5.9557 | 1.7347e-06 | 0.00094829 | 0.34841 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Kern River Cogeneration | 300 | 297.01 | 302.36 | 27.76% | 4 |  | 4 |  | 50.7014 | 54.7041 | 4 | Yes | BC/Ventura | 0 | No | No Published Factor | 4 | 657 | High | In_DAC |  | 4 | 1.8966 | 0.52643 | 4 | NA_Extreme | NA_Moderate | 4 | 100 | 100 | 100
OMAR_2_UNIT 3 | KERN RIVER COGENERATION CO. UNIT 3 | 75 | 85 | SCE | Chevron Power Holdings, INC | FTUR | NATURAL GAS | SP15 | 1985-05-01 | Dexzel | 115 | 10496 | 729451 | 2695012 | 8990991 | 4344417 | 4646574 | 2.6187 | 1431.5752 | 525969.3025 | 2.9126e-07 | 0.00015922 | 0.0585 | 5.9557 | 1.7347e-06 | 0.00094829 | 0.34841 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Kern River Cogeneration | 300 | 297.01 | 302.36 | 27.76% | 4 |  | 4 |  | 50.7014 | 54.7041 | 4 | Yes | BC/Ventura | 0 | No | No Published Factor | 4 | 657 | High | In_DAC |  | 4 | 1.8966 | 0.52643 | 4 | NA_Extreme | NA_Moderate | 4 | 100 | 100 | 100
OMAR_2_UNIT 4 | KERN RIVER COGENERATION CO. UNIT 4 | 75 | 85 | SCE | Chevron Power Holdings, INC | FTUR | NATURAL GAS | SP15 | 1985-05-01 | Dexzel | 115 | 10496 | 729451 | 2695012 | 8990991 | 4344417 | 4646574 | 2.6187 | 1431.5752 | 525969.3025 | 2.9126e-07 | 0.00015922 | 0.0585 | 5.9557 | 1.7347e-06 | 0.00094829 | 0.34841 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Kern River Cogeneration | 300 | 297.01 | 302.36 | 27.76% | 4 |  | 4 |  | 50.7014 | 54.7041 | 4 | Yes | BC/Ventura | 0 | No | No Published Factor | 4 | 657 | High | In_DAC |  | 4 | 1.8966 | 0.52643 | 4 | NA_Extreme | NA_Moderate | 4 | 100 | 100 | 100
PNCHEG_2_PL1X4 | PANOCHE ENERGY CENTER (Aggregated) | 417 |  | PGAE | PANOCHE ENERGY CENTER | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2009-05-27 | Panoche | 230 | 56803 | 615796 | 0 | 5741979 | 5741979 | 0 | 1.729 | 31.658 | 335903.427 | 3.0112e-07 | 5.5134e-06 | 0.0585 | 9.3245 | 2.8077e-06 | 5.141e-05 | 0.54548 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Panoche Energy Center | 432 | 395.6 | 400.1 | 16.27% | 4 |  | 1 |  | 26.6137 | 30.6164 | 2 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | In_DAC |  | 4 | 0.10282 | 0.016731 | 3 | NA_Extreme | NA_Moderate | 4 | 78.5714 | 84.7222 | 77.0833
PNCHPP_1_PL1X2 | Midway Peaking Aggregate | 119.91 |  | PGAE | Midway Peaking, LLC | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2009-05-03 | Panoche | 230 | 56639 | 49354 | 0 | 543937 | 543937 | 0 | 0.169 | 5.238 | 31820.0924 | 3.107e-07 | 9.6298e-06 | 0.0585 | 11.0211 | 3.4242e-06 | 0.00010613 | 0.64473 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Midway Peaking LLC | 139.8 | 108.35 | 110.52 | 4.03% | 3 |  | 3 |  | 26.6795 | 30.6822 | 2 | Yes | Fresno | Panoche 115 kV | No | No Published Factor | 4 | 793 | High | In_DAC |  | 4 | 0.21226 | 0.0085543 | 2 | NA_Extreme | NA_Moderate | 4 | 78.5714 | 86.1111 | 79.1667
PNOCHE_1_PL1X2 | Panoche Peaker | 49.97 |  | PGAE | Wellhead Power Panoche, LLC | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2005-06-14 | Panoche | 230 | 55874 | 11298 | 0 | 183238 | 183238 | 0 | 0.052806 | 28.8673 | 10719.3482 | 2.8818e-07 | 0.00015754 | 0.0585 | 16.2186 | 4.6739e-06 | 0.0025551 | 0.94878 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Panoche Peaker | 49.9 | 49.97 | 49.97 | 2.585% | 2 |  | 4 |  | 30.5671 | 34.5699 | 2 | Yes | Fresno | Herndon, Panoche 115 kV | No | No Published Factor | 4 | 793 | High | In_DAC |  | 4 | 5.1102 | 0.13208 | 4 | NA_Extreme | NA_Moderate | 4 | 85.7143 | 91.6667 | 87.5
HINSON_6_LBECH1 | Long Beach Unit 1 | 63 | 70 | SCE | Long Beach Generation LLC | FTUR | NATURAL GAS | SP15 | 2007-08-01 | HarborGen | 230 | 341 | 22511 | 0 | 385250 | 385250 | 0 | 0.122 | 6.411 | 22536.9677 | 3.1668e-07 | 1.6641e-05 | 0.0585 | 17.1139 | 5.4196e-06 | 0.00028479 | 1.0012 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Long Beach Generation LLC | 252 | 260 | 260 | 1.02% | 1 |  | 4 |  | 28.4356 | 32.4384 | 2 | Yes | LA Basin | Western | Yes | 12 | 3 | 1141 | High | In_DAC |  | 4 | 0.56959 | 0.0058083 | 1 | NA_Extreme | A | 2.5 | 62.5 | 66.6667 | 62.5
HINSON_6_LBECH2 | Long Beach Unit 2 | 63 | 70 | SCE | Long Beach Generation LLC | FTUR | NATURAL GAS | SP15 | 2007-08-01 | HarborGen | 230 | 341 | 22511 | 0 | 385250 | 385250 | 0 | 0.122 | 6.411 | 22536.9677 | 3.1668e-07 | 1.6641e-05 | 0.0585 | 17.1139 | 5.4196e-06 | 0.00028479 | 1.0012 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Long Beach Generation LLC | 252 | 260 | 260 | 1.02% | 1 |  | 4 |  | 28.4356 | 32.4384 | 2 | Yes | LA Basin | Western | Yes | 12 | 3 | 1141 | High | In_DAC |  | 4 | 0.56959 | 0.0058083 | 1 | NA_Extreme | A | 2.5 | 62.5 | 66.6667 | 62.5
HINSON_6_LBECH3 | Long Beach Unit 3 | 63 | 70 | SCE | Long Beach Generation LLC | FTUR | NATURAL GAS | SP15 | 2007-08-01 | HarborGen | 230 | 341 | 22511 | 0 | 385250 | 385250 | 0 | 0.122 | 6.411 | 22536.9677 | 3.1668e-07 | 1.6641e-05 | 0.0585 | 17.1139 | 5.4196e-06 | 0.00028479 | 1.0012 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Long Beach Generation LLC | 252 | 260 | 260 | 1.02% | 1 |  | 4 |  | 28.4356 | 32.4384 | 2 | Yes | LA Basin | Western | Yes | 12 | 3 | 1141 | High | In_DAC |  | 4 | 0.56959 | 0.0058083 | 1 | NA_Extreme | A | 2.5 | 62.5 | 66.6667 | 62.5
HINSON_6_LBECH4 | Long Beach Unit 4 | 63 | 70 | SCE | Long Beach Generation LLC | FTUR | NATURAL GAS | SP15 | 2007-08-01 | HarborGen | 230 | 341 | 22511 | 0 | 385250 | 385250 | 0 | 0.122 | 6.411 | 22536.9677 | 3.1668e-07 | 1.6641e-05 | 0.0585 | 17.1139 | 5.4196e-06 | 0.00028479 | 1.0012 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Long Beach Generation LLC | 252 | 260 | 260 | 1.02% | 1 |  | 4 |  | 28.4356 | 32.4384 | 2 | Yes | LA Basin | Western | Yes | 12 | 3 | 1141 | High | In_DAC |  | 4 | 0.56959 | 0.0058083 | 1 | NA_Extreme | A | 2.5 | 62.5 | 66.6667 | 62.5
HNTGBH_2_PL1X3 | Huntington Beach Energy | 673.8 |  | SCE | AES Huntington Beach Energy LLC | COMBINED CYCLE | NATURAL GAS | SP15 | 2020-02-04 | Huntington Beach | 230 | 335 | 319522 | 0 | 3685102 | 3685102 | 0 | 1.122 | 25.272 | 215576.9624 | 3.0447e-07 | 6.8579e-06 | 0.0585 | 11.5332 | 3.5115e-06 | 7.9093e-05 | 0.67469 | CAISO_CCGT2 | Natural Gas Steam Turbine | AES Huntington Beach LLC | 218 | 899.6 | 899.6 | 16.73% | 2 |  | 4 |  | 15.9151 | 19.9178 | 1 | Yes | LA Basin | Western | Yes | 16 | 2 | 1141 | High | DAC_Adjacent | 2.3814 | 3 | 0.15819 | 0.026467 | 3 | NA_Extreme | NA_Moderate | 4 | 67.8571 | 69.4444 | 79.1667
HUMBPP_1_UNITS3 | Humboldt Bay Generating Station 3 | 65.08 | 83.2 | PGAE | Pacific Gas & Electric Company | RECIPROCATING ENGINE | NATURAL GAS | NP15 | 2010-09-29 | Wildwood Solar | 115 | 246 | 383862 | 0 | 3372675 | 3372675 | 0 | 3.1393 | 4488.9529 | 197650.2736 | 9.3082e-07 | 0.001331 | 0.058603 | 8.7862 | 8.1783e-06 | 0.011694 | 0.5149 | CAISO_Reciprocating_Engine | Natural Gas Internal Combustion Engine | Humboldt Bay | 167 | 162.7 | 162.7 | 26.24% | 4 |  | 1 |  | 25.2712 | 29.274 | 2 | Yes | Humboldt | 0 | No | No Published Factor | 4 | 19 | Low | Outside_DAC | 178.208 | 1 | 23.3884 | 6.137 | 4 | A | A | 1 | 60.7143 | 70.8333 | 56.25
HUMBPP_6_UNITS | Humboldt Bay Generating Station 1 | 97.62 |  | PGAE | Pacific Gas & Electric Company | RECIPROCATING ENGINE | NATURAL GAS | NP15 | 2010-09-29 | Wildwood Solar | 115 | 246 | 383862 | 0 | 3372675 | 3372675 | 0 | 3.1393 | 4488.9529 | 197650.2736 | 9.3082e-07 | 0.001331 | 0.058603 | 8.7862 | 8.1783e-06 | 0.011694 | 0.5149 | CAISO_Reciprocating_Engine | Natural Gas Internal Combustion Engine | Humboldt Bay | 167 | 162.7 | 162.7 | 26.24% | 4 |  | 1 |  | 25.2712 | 29.274 | 2 | Yes | Humboldt | 0 | No | No Published Factor | 4 | 19 | Low | Outside_DAC | 178.208 | 1 | 23.3884 | 6.137 | 4 | A | A | 1 | 60.7143 | 70.8333 | 56.25
INDIGO_1_UNIT 1 | INDIGO PEAKER UNIT 1 | 45.3 | 45.3 | SCE | Wildflower Energy LP | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2001-09-19 | Devers | 500 | 55541 | 33376 | 0 | 358256 | 358256 | 0 | 0.107 | 3.955 | 20957.8297 | 2.9867e-07 | 1.104e-05 | 0.0585 | 10.7339 | 3.2059e-06 | 0.0001185 | 0.62793 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Indigo Energy Facility | 149.7 | 126 | 126 | 2.545% | 2 |  | 2 |  | 34.3041 | 38.3068 | 3 | Yes | LA Basin | Eastern, Valley-Devers | No | No Published Factor | 4 | 1141 | High | Outside_DAC | 25.2861 | 1 | 0.237 | 0.0060319 | 2 | NA_Severe 15 | A | 2.25 | 58.0357 | 64.5833 | 46.875
INDIGO_1_UNIT 2 | INDIGO PEAKER UNIT 2 | 45.3 | 45.3 | SCE | Wildflower Energy LP | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2001-09-19 | Devers | 500 | 55541 | 33376 | 0 | 358256 | 358256 | 0 | 0.107 | 3.955 | 20957.8297 | 2.9867e-07 | 1.104e-05 | 0.0585 | 10.7339 | 3.2059e-06 | 0.0001185 | 0.62793 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Indigo Energy Facility | 149.7 | 126 | 126 | 2.545% | 2 |  | 2 |  | 34.3041 | 38.3068 | 3 | Yes | LA Basin | Eastern, Valley-Devers | No | No Published Factor | 4 | 1141 | High | Outside_DAC | 25.2861 | 1 | 0.237 | 0.0060319 | 2 | NA_Severe 15 | A | 2.25 | 58.0357 | 64.5833 | 46.875
INDIGO_1_UNIT 3 | INDIGO PEAKER UNIT 3 | 45.3 | 45.3 | SCE | Wildflower Energy LP | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2001-09-19 | Devers | 500 | 55541 | 33376 | 0 | 358256 | 358256 | 0 | 0.107 | 3.955 | 20957.8297 | 2.9867e-07 | 1.104e-05 | 0.0585 | 10.7339 | 3.2059e-06 | 0.0001185 | 0.62793 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Indigo Energy Facility | 149.7 | 126 | 126 | 2.545% | 2 |  | 2 |  | 34.3041 | 38.3068 | 3 | Yes | LA Basin | Eastern, Valley-Devers | No | No Published Factor | 4 | 1141 | High | Outside_DAC | 25.2861 | 1 | 0.237 | 0.0060319 | 2 | NA_Severe 15 | A | 2.25 | 58.0357 | 64.5833 | 46.875
KELSO_2_UNITS | Mariposa Energy | 198.03 |  | PGAE | Mariposa Energy, LLC | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2012-10-01 | Kelso | 230 | 57483 | 112210 | 0 | 1228889 | 1228889 | 0 | 0.408 | 7.52 | 71889.5047 | 3.3201e-07 | 6.1193e-06 | 0.0585 | 10.9517 | 3.636e-06 | 6.7017e-05 | 0.64067 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Mariposa Energy Project | 199.6 | 192.36 | 194.59 | 6.418% | 3 |  | 3 |  | 23.263 | 27.2658 | 1 | Yes | Bay Area | Contra Costa | No | No Published Factor | 4 | 2220 | High | DAC_Adjacent | 3.0934 | 3 | 0.13403 | 0.0086017 | 2 | NA_Marginal | A | 1.25 | 61.6071 | 75.6944 | 63.5417
PNOCHE_1_UNITA1 | CalPeak Power Panoche Unit 1 | 52.3 | 57 | PGAE | CalPeak Power - Panoche LLC | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2001-12-27 | Panoche | 230 | 55508 | 14215 | 0 | 156850 | 156850 | 0 | 0.046 | 0.816 | 9175.661 | 2.9327e-07 | 5.2024e-06 | 0.0585 | 11.0341 | 3.236e-06 | 5.7404e-05 | 0.64549 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | CalPeak Power Panoche Peaker Plant | 60.5 | 52.01 | 52.01 | 2.682% | 2 |  | 3 |  | 34.0329 | 38.0356 | 3 | Yes | Fresno | Panoche 115 kV | No | No Published Factor | 4 | 793 | High | In_DAC |  | 4 | 0.11481 | 0.0030794 | 1 | NA_Extreme | NA_Moderate | 4 | 75 | 79.1667 | 68.75
RVRVEW_1_UNITA1 | Riverview Energy Center (GP Antioch) | 48.7 | 50 | PGAE | Gilroy Energy Center, LLC | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2003-05-02 | Fibreboard (SPI Sonora) | 115 | 55963 | 18001 | 0 | 205484 | 205484 | 0 | 0.064 | 1.998 | 12020.7301 | 3.1146e-07 | 9.7234e-06 | 0.0585 | 11.4151 | 3.5554e-06 | 0.00011099 | 0.66778 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Riverview Energy Center | 47 | 47.6 | 47.6 | 4.372% | 3 |  | 3 |  | 32.6877 | 36.6904 | 3 | Yes | Bay Area | Contra Costa | No | No Published Factor | 4 | 2220 | High | DAC_Adjacent | 0.45355 | 3 | 0.22199 | 0.0097056 | 3 | NA_Marginal | A | 1.25 | 72.3214 | 78.4722 | 67.7083
SBERDO_2_PSP4 | Mountainview Gen Sta. Unit 4 | 555 |  | SCE | Southern California Edison Company | COMBINED CYCLE | NATURAL GAS | SP15 | 2006-01-19 | San Bernarino | 230 | 358 | 2091874.84 | 0 | 16733883 | 16733883 | 0 | 4.564 | 96.327 | 978925.3231 | 2.7274e-07 | 5.7564e-06 | 0.0585 | 7.9995 | 2.1818e-06 | 4.6048e-05 | 0.46797 | CAISO_CCGT1 | Natural Gas Fired Combined Cycle | Mountainview Generating Station | 1036.8 | 1110 | 1110 | 23.03% | 2 |  | 3 |  | 29.9671 | 33.9699 | 2 | Yes | LA Basin | Eastern, West of Devers | No | No Published Factor | 4 | 1141 | High | DAC_Adjacent | 0.13304 | 3 | 0.092096 | 0.021212 | 3 | NA_Extreme | NA_Moderate | 4 | 75 | 81.9444 | 72.9167
KNGCTY_6_UNITA1 | King City Energy Center, Unit 1 | 44.6 | 49.9 | PGAE | Gilroy Energy Center, LLC | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2002-01-14 | Coburn | 230 | 55811 | 8584 | 0 | 96422 | 96422 | 0 | 0.027922 | 15.2638 | 5640.6476 | 2.8958e-07 | 0.0001583 | 0.0585 | 11.2328 | 3.2527e-06 | 0.0017782 | 0.65711 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | King City Peaking | 47.3 | 44.6 | 44.6 | 2.072% | 1 |  | 3 |  | 33.9836 | 37.9863 | 3 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | Outside_DAC | 36.6048 | 1 | 3.5563 | 0.073676 | 4 | A | A | 1 | 60.7143 | 66.6667 | 50
SCHLTE_1_PL1X3 | Tracy Combined Cycle Power Plant | 336.04 |  | PGAE | MRP San Joaquin Energy, LLC | COMBINED CYCLE | NATURAL GAS | NP15 | 2012-10-31 | GWF Tracy | 115 | 55933 | 868383 | 0 | 7084590 | 7084590 | 0 | 2.16 | 32.802 | 414445.6224 | 3.0489e-07 | 4.63e-06 | 0.0585 | 8.1584 | 2.4874e-06 | 3.7774e-05 | 0.47726 | CAISO_CCGT2 | Natural Gas Fired Combined Cycle | Tracy Combined Cycle Power Plant | 336.1 | 309.51 | 314.34 | 29.49% | 3 |  | 3 |  | 23.1808 | 27.1836 | 1 | Yes | Stockton | Tesla-Bellota | No | No Published Factor | 4 | 545 | High | DAC_Adjacent | 2.1325 | 3 | 0.075547 | 0.022282 | 3 | NA_Extreme | NA_Moderate | 4 | 75 | 86.1111 | 79.1667
SGREGY_6_SANGER | Algonquin Power Sanger 2 | 48.3 | 48.3 | PGAE | Algonquin Power Sanger LLC | COMBINED CYCLE | NATURAL GAS | NP15 | 2017-06-01 | Sanger | 115 | 57564 | 176139 | 0 | 1232505 | 1232505 | 0 | 0.379 | 9.705 | 72101.0393 | 3.075e-07 | 7.8742e-06 | 0.0585 | 6.9973 | 2.1517e-06 | 5.5099e-05 | 0.40934 | CAISO_CCGT2 | Natural Gas Fired Combined Cycle | Algonquin Power Sanger LLC | 61.5 | 48.08 | 48.08 | 32.69% | 3 |  | 2 |  | 18.5945 | 22.5973 | 1 | Yes | Fresno | Herndon | No | No Published Factor | 4 | 793 | High | In_DAC |  | 4 | 0.1102 | 0.036029 | 3 | NA_Extreme | NA_Moderate | 4 | 75 | 84.7222 | 77.0833
SIERRA_1_UNITS | HIGH SIERRA LIMITED | 52.43 | 60.3 | PGAE | HIGH SIERRA LIMITED | COMBUSTION TURBINE | NATURAL GAS | ZP26 | 1989-02-24 | Kern Front Co-Gen | 115 | 50495 | 28059 | 7638 | 291746 | 270532 | 21214 | 0.084157 | 46.0059 | 17067.0219 | 2.8846e-07 | 0.00015769 | 0.0585 | 9.6415 | 2.7812e-06 | 0.0015204 | 0.56403 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | High Sierra Limited | 49.8 | 49.57 | 50.13 | 6.432% | 3 |  | 1 |  | 46.8795 | 50.8822 | 4 | Yes | Kern | South Kern PP | No | No Published Factor | 4 | 270 | High | In_DAC |  | 4 | 3.0408 | 0.19558 | 4 | NA_Extreme | NA_Moderate | 4 | 85.7143 | 83.3333 | 75
SUNRIS_2_PL1X3 | Sunrise Power Project AGGREGATE II | 586.02 |  | PGAE | Sunrise Power Company | COMBINED CYCLE | NATURAL GAS | NP15 | 2001-06-07 | Sunrise | 230 | 55182 | 2671368 | 0 | 19102277 | 19102277 | 0 | 5.61 | 50.19 | 1117475.405 | 2.9368e-07 | 2.6274e-06 | 0.0585 | 7.1507 | 2.1e-06 | 1.8788e-05 | 0.41832 | CAISO_CCGT1 | Natural Gas Fired Combined Cycle | Sunrise Power LLC | 605.4 | 586.02 | 586.02 | 50.37% | 4 |  | 1 |  | 34.589 | 38.5918 | 4 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | In_DAC |  | 4 | 0.037576 | 0.018928 | 3 | NA_Extreme | NA_Moderate | 4 | 85.7143 | 84.7222 | 77.0833
LARKSP_6_UNIT 1 | LARKSPUR PEAKER UNIT 1 | 49 | 49 | SDGE | Wildflower Energy LP | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2001-09-13 | Otay Mesa | 230 | 55542 | 44783 | 0 | 433756 | 433756 | 0 | 0.138 | 4.272 | 25374.5489 | 3.1815e-07 | 9.8489e-06 | 0.0585 | 9.6857 | 3.0815e-06 | 9.5393e-05 | 0.56661 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Larkspur Energy Facility | 99.8 | 92 | 92 | 5.122% | 3 |  | 1 |  | 34.3205 | 38.3233 | 3 | Yes | SD-IV | San Diego, Border | Yes | 22 | 1 | 920 | High | DAC_Adjacent | 6.1273 | 2 | 0.19079 | 0.009773 | 3 | NA_Moderate | A | 1.5 | 51.7857 | 43.0556 | 52.0833
LARKSP_6_UNIT 2 | LARKSPUR PEAKER UNIT 2 | 49 | 49 | SDGE | Wildflower Energy LP | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2001-09-13 | Otay Mesa | 230 | 55542 | 44783 | 0 | 433756 | 433756 | 0 | 0.138 | 4.272 | 25374.5489 | 3.1815e-07 | 9.8489e-06 | 0.0585 | 9.6857 | 3.0815e-06 | 9.5393e-05 | 0.56661 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Larkspur Energy Facility | 99.8 | 92 | 92 | 5.122% | 3 |  | 1 |  | 34.3205 | 38.3233 | 3 | Yes | SD-IV | San Diego, Border | Yes | 22 | 1 | 920 | High | DAC_Adjacent | 6.1273 | 2 | 0.19079 | 0.009773 | 3 | NA_Moderate | A | 1.5 | 51.7857 | 43.0556 | 52.0833
VERNON_6_GONZL1 | H. Gonzales Unit #1 | 5.75 | 5.5 | SCE | City of Vernon | FTUR | NATURAL GAS | SP15 | 2013-06-13 | Laguna Bell | 230 | 7436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | CAISO_Peaker2 | Petroleum Liquids | H. Gonzales Unit #1 | 30 | 11.5 | 11.5 | 0% | 1 |  | 4 |  | 22.5644 | 26.5671 | 1 | Yes | LA Basin | Western | No | No Published Factor | 4 | 1141 | High | In_DAC |  | 4 | Not Available | Not Available | 2.5 | NA_Extreme | NA_Moderate | 4 | 73.2143 | 83.3333 | 75
LECEF_1_UNITS | LOS ESTEROS ENERGY FACILITY AGGREGATE | 309.84 |  | PGAE | Los Esteros Critical Energy Facility, LLC | COMBINED CYCLE | NATURAL GAS | NP15 | 2013-07-31 | Los Esteros | 115 | 55748 | 356431 | 0 | 3006451 | 3006451 | 0 | 0.899 | 8.822 | 175876.156 | 2.9902e-07 | 2.9344e-06 | 0.0585 | 8.4349 | 2.5222e-06 | 2.4751e-05 | 0.49344 | CAISO_CCGT2 | Natural Gas Fired Combined Cycle | Los Esteros Critical Energy Center | 306.1 | 297.54 | 304 | 13.29% | 2 |  | 3 |  | 22.4329 | 26.4356 | 1 | Yes | Bay Area | San Jose, South Bay-Moss Landing | Yes | 7 | 4 | 2220 | High | In_DAC |  | 4 | 0.049502 | 0.0065801 | 2 | NA_Marginal | A | 1.25 | 61.6071 | 74.3056 | 61.4583
VERNON_6_MALBRG | Malburg Generating Station | 139 |  | SCE | City of Vernon | COMBINED CYCLE | NATURAL GAS | SP15 | 2005-10-17 | Laguna Bell | 230 | 56041 | 479363 | 0 | 3974419 | 3974419 | 0 | 1.191 | 15.914 | 232501.8887 | 2.9967e-07 | 4.0041e-06 | 0.0585 | 8.291 | 2.4845e-06 | 3.3198e-05 | 0.48502 | CAISO_CCGT2 | Natural Gas Fired Combined Cycle | Malburg | 130 | 134 | 134 | 42.09% | 4 |  | 3 |  | 30.2247 | 34.2274 | 2 | Yes | LA Basin | Western | Yes | 34 | 1 | 1141 | High | In_DAC |  | 4 | 0.066396 | 0.027949 | 3 | NA_Extreme | NA_Moderate | 4 | 75 | 68.0556 | 89.5833
HARBGN_7_UNITS | HARBOR COGEN COMBINED CYCLE | 109.01 |  | SCE | Harbor Cogeneration Company | COMBINED CYCLE | NATURAL GAS | SP15 | 2001-06-14 | HarborGen | 230 | 50541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | CAISO_CCGT2 | Natural Gas Fired Combined Cycle | HARBOR COGEN COMBINED CYCLE | 107.4 | 100 | 100 | 0% | 1 |  | 4 |  | 34.5699 | 38.5726 | 4 | Yes | LA Basin | Western | Yes | 23 | 1 | 1141 | High | In_DAC |  | 4 | Not Available | Not Available | 2.5 | NA_Extreme | NA_Moderate | 4 | 73.2143 | 58.3333 | 75
LMBEPK_2_UNITA1 | Lambie Energy Center, Unit #1 | 47.5 | 49.9 | PGAE | Gilroy Energy Center, LLC | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2003-01-06 | Lambie | 230 | 55626 | 13299 | 0 | 157496 | 157496 | 0 | 0.049 | 1.595 | 9213.4517 | 3.1112e-07 | 1.0127e-05 | 0.0585 | 11.8427 | 3.6845e-06 | 0.00011993 | 0.69279 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Lambie Energy Center | 47 | 47.5 | 47.5 | 3.23% | 2 |  | 3 |  | 33.0055 | 37.0082 | 3 | Yes | Bay Area | Contra Costa | No | No Published Factor | 4 | 2220 | High | Outside_DAC | 10.7271 | 1 | 0.23987 | 0.007748 | 2 | NA_Marginal | A | 1.25 | 58.0357 | 65.9722 | 48.9583
LMBEPK_2_UNITA2 | Creed Energy Center, Unit #1 | 47.6 | 49.9 | PGAE | Creed Energy Facility, LLC | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2003-01-06 | Lambie | 230 | 55625 | 12968 | 0 | 152402 | 152402 | 0 | 0.051 | 1.612 | 8915.4548 | 3.3464e-07 | 1.0577e-05 | 0.0585 | 11.7522 | 3.9328e-06 | 0.00012431 | 0.6875 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Creed Energy Center | 47 | 47.6 | 47.6 | 3.15% | 2 |  | 3 |  | 33.0055 | 37.0082 | 3 | Yes | Bay Area | Contra Costa | No | No Published Factor | 4 | 2220 | High | Outside_DAC | 12.149 | 1 | 0.24861 | 0.0078306 | 2 | NA_Marginal | A | 1.25 | 58.0357 | 65.9722 | 48.9583
LMBEPK_2_UNITA3 | Goose Haven Energy Center, Unit #1 | 47.75 | 49.9 | PGAE | Goose Haven Energy Center, LLC | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2003-01-06 | Lambie | 230 | 55627 | 12447 | 0 | 147470 | 147470 | 0 | 0.045 | 1.528 | 8626.9348 | 3.0515e-07 | 1.0361e-05 | 0.0585 | 11.8478 | 3.6153e-06 | 0.00012276 | 0.69309 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Goose Haven Energy Center | 47 | 47.4 | 47.4 | 3.023% | 2 |  | 3 |  | 33.0055 | 37.0082 | 3 | Yes | Bay Area | Contra Costa | No | No Published Factor | 4 | 2220 | High | Outside_DAC | 11.1521 | 1 | 0.24552 | 0.0074225 | 2 | NA_Marginal | A | 1.25 | 58.0357 | 65.9722 | 48.9583
UNOCAL_1_UNITS | TOSCO (RODEO PLANT) | 49.85 | 57.3 | PGAE | Pacific Gas & Electric Company | FTUR | NATURAL GAS | NP15 | 1987-05-21 | Christie | 115 | 50119 | 390019 | 4046579 | 6966279 | 1778356 | 5187923 | 1.7979 | 855.2419 | 122675.5158 | 2.5809e-07 | 0.00012277 | 0.01761 | 4.5597 | 1.1768e-06 | 0.00055978 | 0.080295 | CAISO_Peaker1 | Other Gases | Phillips 66 Rodeo Refinery | 54.9 | 0.07 | 0.31 | 81.1% | 4 |  | 1 |  | 48.6466 | 52.6493 | 4 | Yes | Bay Area | Pittsburg | Yes | 23 | 1 | 2220 | High | In_DAC |  | 4 | 1.1196 | 0.90795 | 4 | NA_Marginal | A | 1.25 | 68.75 | 54.8611 | 69.7917
LGHTHP_6_ICEGEN | CARSON COGENERATION | 48 | 54.7 | SCE | Carson Hybrid Energy Storage LLC | COMBINED CYCLE | NATURAL GAS | SP15 | 1989-12-22 | Lightpipe | 230 | 10169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | CAISO_Peaker1 | Natural Gas Fired Combined Cycle | CARSON COGENERATION | 55.8 | 48 | 48 | 0% | 1 |  | 3 |  | 46.0548 | 50.0575 | 4 | Yes | LA Basin | Western | Yes | 22 | 1 | 1141 | High | In_DAC |  | 4 | Not Available | Not Available | 2.5 | NA_Extreme | NA_Moderate | 4 | 69.6429 | 54.1667 | 68.75
LODIEC_2_PL1X2 | Lodi Energy Center | 302.58 |  | PGAE | Northern California Power Agency - Lodi Energy Center | COMBINED CYCLE | NATURAL GAS | NP15 | 2012-11-27 | Eight Mile | 230 | 57978 | 1406540 | 0 | 9981568 | 9981568 | 0 | 2.994 | 29.301 | 583917.6525 | 2.9995e-07 | 2.9355e-06 | 0.0585 | 7.0965 | 2.1286e-06 | 2.0832e-05 | 0.41514 | CAISO_CCGT1 | Natural Gas Fired Combined Cycle | Lodi Energy Center | 288.9 | 302.58 | 302.58 | 55.58% | 4 |  | 1 |  | 23.1068 | 27.1096 | 1 | Yes | Sierra | South of Rio Oso, South of Palermo | Yes | 14 | 3 | 75 | Low | DAC_Adjacent | 3.0715 | 3 | 0.041664 | 0.023156 | 3 | NA_Extreme | NA_Moderate | 4 | 67.8571 | 73.6111 | 72.9167
MALAGA_1_PL1X2 | Malaga Power Aggregate | 96.61 |  | PGAE | Malaga Power, LLC | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2005-09-19 | West Fresno | 115 | 56239 | 27660 | 0 | 287868 | 287868 | 0 | 0.088 | 2.32 | 16840.1605 | 3.057e-07 | 8.0592e-06 | 0.0585 | 10.4074 | 3.1815e-06 | 8.3876e-05 | 0.60883 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Malaga Power LLC | 121 | 96 | 96 | 2.61% | 2 |  | 2 |  | 30.3014 | 34.3041 | 2 | Yes | Fresno | Herndon | Yes | 19 | 2 | 793 | High | In_DAC |  | 4 | 0.16775 | 0.0043775 | 1 | NA_Extreme | NA_Moderate | 4 | 60.7143 | 58.3333 | 62.5
METEC_2_PL1X3 | Metcalf Energy Center | 597.05 |  | PGAE | Metcalf Energy Center, LLC | COMBINED CYCLE | NATURAL GAS | NP15 | 2005-05-27 | Metcalf | 115 | 55393 | 2079832 | 0 | 15832385 | 15832385 | 0 | 4.581 | 56.936 | 926188.0581 | 2.8934e-07 | 3.5962e-06 | 0.0585 | 7.6123 | 2.2026e-06 | 2.7375e-05 | 0.44532 | CAISO_CCGT1 | Natural Gas Fired Combined Cycle | Metcalf Energy Center | 635 | 570 | 580 | 37.39% | 3 |  | 2 |  | 30.6164 | 34.6192 | 2 | Yes | Bay Area | South Bay-Moss Landing | Yes | 13 | 3 | 2220 | High | DAC_Adjacent | 8.2664 | 2 | 0.054751 | 0.020471 | 3 | NA_Marginal | A | 1.25 | 58.0357 | 63.1944 | 57.2917
SHELRF_1_UNITS | SHELL OIL REFINERY AGGREGATE | 100 |  | PGAE | Martinez Refining Company-Division of Equilon Enterprises, LLC | COMBINED CYCLE | NATURAL GAS | NP15 | 1995-01-01 | Martinez | 115 | 54912 | 810838 | 2889693 | 10964752 | 5407653 | 5557099 | 3.5673 | 1157.2265 | 479186.36 | 3.2534e-07 | 0.00010554 | 0.043702 | 6.6692 | 2.1698e-06 | 0.00070387 | 0.29146 | CAISO_Peaker2 | Natural Gas Fired Combined Cycle | Martinez Refining | 100 | 27.71 | 26.98 | 92.56% | 4 |  | 4 |  | 41.0247 | 45.0274 | 4 | Yes | Bay Area | Pittsburg | Yes | 20 | 2 | 2220 | High | In_DAC |  | 4 | 1.4077 | 1.303 | 4 | NA_Marginal | A | 1.25 | 83.0357 | 75.6944 | 88.5417
ALMEGT_1_UNIT 1 | ALAMEDA GT UNIT 1 | 25 | 25.4 | PGAE | NCPA (MSS Agreement - S14) | FTUR | NATURAL GAS | NP15 | 1986-01-01 | Cartwright Jenny | 115 | 7450 | 9563 | 0 | 143953 | 143953 | 0 | 0.041485 | 22.6784 | 8421.1917 | 2.8818e-07 | 0.00015754 | 0.0585 | 15.0531 | 4.3381e-06 | 0.0023715 | 0.8806 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Alameda | 54.8 | 46.9 | 46.9 | 1.992% | 1 |  | 4 |  | 50.0301 | 54.0329 | 4 | Yes | Bay Area | Oakland | Yes | 17 | 2 | 2220 | High | DAC_Adjacent | 0.97185 | 3 | 4.7429 | 0.094484 | 4 | NA_Marginal | A | 1.25 | 68.75 | 60.4167 | 65.625
MNDALY_6_MCGRTH | McGrath Beach Peaker | 48.56 | 59 | SCE | Southern California edison | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2012-11-01 | Mandalay | 230 | 56471 | 23962 | 0 | 242811 | 242811 | 0 | 0.072 | 1.384 | 14204.3444 | 2.9653e-07 | 5.6999e-06 | 0.0585 | 10.1332 | 3.0048e-06 | 5.7758e-05 | 0.59279 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | McGrath Peaker | 49.8 | 47.2 | 47.2 | 5.493% | 3 |  | 2 |  | 23.1781 | 27.1808 | 1 | Yes | BC/Ventura | S.Clara, Moorpark | No | No Published Factor | 4 | 657 | High | In_DAC |  | 4 | 0.11552 | 0.006345 | 2 | NA_Serious | A | 2 | 64.2857 | 76.3889 | 64.5833
MOSSLD_2_PSP1 | MOSS LANDING POWER BLOCK 1 | 510 |  | PGAE | Moss Landing Power Company LLC | COMBINED CYCLE | NATURAL GAS | NP15 | 2002-07-01 | Moss Landing | 115 | 260 | 4178781.84 | 0 | 29433380 | 29433380 | 0 | 9.117 | 126.327 | 1721840.7124 | 3.0975e-07 | 4.292e-06 | 0.0585 | 7.0435 | 2.1817e-06 | 3.0231e-05 | 0.41204 | CAISO_CCGT1 | Natural Gas Fired Combined Cycle | Dynegy Moss Landing Power Plant | 1398 | 1020 | 1020 | 34.12% | 3 |  | 1 |  | 33.5233 | 37.526 | 4 | Yes | Bay Area | South Bay-Moss Landing | Yes | 20 | 2 | 2220 | High | DAC_Adjacent | 1.5306 | 3 | 0.060461 | 0.020631 | 3 | A | A | 1 | 60.7143 | 52.7778 | 54.1667
MOSSLD_2_PSP2 | MOSS LANDING POWER BLOCK 2 | 510 |  | PGAE | Moss Landing Power Company LLC | COMBINED CYCLE | NATURAL GAS | NP15 | 2002-07-11 | Moss Landing | 115 | 260 | 4178781.84 | 0 | 29433380 | 29433380 | 0 | 9.117 | 126.327 | 1721840.7124 | 3.0975e-07 | 4.292e-06 | 0.0585 | 7.0435 | 2.1817e-06 | 3.0231e-05 | 0.41204 | CAISO_CCGT1 | Natural Gas Fired Combined Cycle | Dynegy Moss Landing Power Plant | 1398 | 1020 | 1020 | 34.12% | 3 |  | 1 |  | 33.4959 | 37.4986 | 4 | Yes | Bay Area | South Bay-Moss Landing | Yes | 20 | 2 | 2220 | High | DAC_Adjacent | 1.5306 | 3 | 0.060461 | 0.020631 | 3 | A | A | 1 | 60.7143 | 52.7778 | 54.1667
MRCHNT_2_PL1X3 | Desert Star Energy Center | 494.58 |  | SCE | San Diego Gas & Electric Company | COMBINED CYCLE | NATURAL GAS | SP15 | 2012-06-18 | Eldorado | 230 | 55077 | 1659922 | 0 | 12788899 | 12788899 | 0 | 3.791 | 82.529 | 748145.3698 | 2.9643e-07 | 6.4532e-06 | 0.0585 | 7.7045 | 2.2838e-06 | 4.9719e-05 | 0.45071 | CAISO_CCGT1 | Natural Gas Fired Combined Cycle | Desert Star Energy Center | 536 | 419.25 | 419.25 | 35.35% | 3 |  | 3 |  | 23.5507 | 27.5534 | 1 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | Outside_DAC | 8229.8474 | 1 | 0.099437 | 0.035153 | 3 | A | A | 1 | 57.1429 | 72.2222 | 58.3333
MRGT_6_MEF2 | Miramar Energy Facility II | 44 | 67.5 | SDGE | San Diego Gas & Electric | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2009-08-07 | Penasquitos | 230 | 56232 | 92448 | 0 | 929471 | 929471 | 0 | 0.28 | 8.849 | 54373.674 | 3.0125e-07 | 9.5205e-06 | 0.0585 | 10.054 | 3.0287e-06 | 9.5719e-05 | 0.58815 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Miramar Energy Facility | 106 | 89 | 89 | 9.956% | 4 |  | 2 |  | 26.4164 | 30.4192 | 2 | Yes | SD-IV | San Diego | Yes | 23 | 1 | 920 | High | DAC_Adjacent | 9.6766 | 2 | 0.19144 | 0.01906 | 3 | NA_Moderate | A | 1.5 | 55.3571 | 51.3889 | 64.5833
MRGT_6_MMAREF | Miramar Energy Facility | 45 | 68 | SDGE | San Diego Gas & Electric | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2005-07-27 | Penasquitos | 230 | 56232 | 92448 | 0 | 929471 | 929471 | 0 | 0.28 | 8.849 | 54373.674 | 3.0125e-07 | 9.5205e-06 | 0.0585 | 10.054 | 3.0287e-06 | 9.5719e-05 | 0.58815 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Miramar Energy Facility | 106 | 89 | 89 | 9.956% | 4 |  | 2 |  | 30.4493 | 34.4521 | 2 | Yes | SD-IV | San Diego | Yes | 23 | 1 | 920 | High | DAC_Adjacent | 9.6766 | 2 | 0.19144 | 0.01906 | 3 | NA_Moderate | A | 1.5 | 55.3571 | 51.3889 | 64.5833
OAK C_7_UNIT 1 | OAKLAND STATION C GT UNIT 1 | 55 | 55 | PGAE | Oakland Power Company LLC | COMBUSTION TURBINE | DISTILLATE | NP15 | 1978-01-01 | Oakland C | 115 | 6211 | 3852 | 0 | 65556 | 65556 | 0 | 10.3723 | 29.3388 | 5123.4491 | 0.00015822 | 0.00044754 | 0.078154 | 17.0187 | 0.0026927 | 0.0076165 | 1.3301 | CAISO_Peaker2 | Petroleum Liquids | Dynegy Oakland Power Plant | 223.5 | 165 | 165 | 0.1967% | 1 |  | 4 |  | 58.0356 | 62.0384 | 4 | Yes | Bay Area | Oakland | Yes | 17 | 2 | 2220 | High | DAC_Adjacent | 0.35501 | 3 | 15.233 | 0.02997 | 3 | NA_Marginal | A | 1.25 | 65.1786 | 57.6389 | 61.4583
ALMEGT_1_UNIT 2 | ALAMEDA GT UNIT 2 | 25 | 25.4 | PGAE | NCPA (MSS Agreement - S14) | FTUR | NATURAL GAS | NP15 | 1986-01-01 | Cartwright Jenny | 115 | 7450 | 9563 | 0 | 143953 | 143953 | 0 | 0.041485 | 22.6784 | 8421.1917 | 2.8818e-07 | 0.00015754 | 0.0585 | 15.0531 | 4.3381e-06 | 0.0023715 | 0.8806 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Alameda | 54.8 | 46.9 | 46.9 | 1.992% | 1 |  | 4 |  | 50.0301 | 54.0329 | 4 | Yes | Bay Area | Oakland | Yes | 17 | 2 | 2220 | High | DAC_Adjacent | 0.97185 | 3 | 4.7429 | 0.094484 | 4 | NA_Marginal | A | 1.25 | 68.75 | 60.4167 | 65.625
OGROVE_6_PL1X2 | Orange Grove Energy Center | 96 |  | SDGE | Orange Grove Energy, L.P. | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2010-06-16 | Escondido | 230 | 56914 | 33879 | 0 | 377648 | 377648 | 0 | 0.112 | 2.134 | 22092.2538 | 2.9657e-07 | 5.6508e-06 | 0.0585 | 11.147 | 3.3059e-06 | 6.2989e-05 | 0.65209 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Orange Grove Peaking Facility | 118 | 96 | 96 | 3.278% | 2 |  | 3 |  | 25.5589 | 29.5616 | 2 | Yes | SD-IV | San Diego | Yes | 20 | 2 | 920 | High | Outside_DAC | 25.725 | 1 | 0.12598 | 0.0041289 | 1 | NA_Moderate | A | 1.5 | 44.6429 | 47.2222 | 45.8333
YUBACT_1_SUNSWT | YUBA CITY COGEN | 49.97 | 49 | PGAE | Yuba City Cogeneration Partners, L.P. | COMBUSTION TURBINE | NATURAL GAS | NP15 | 1990-12-27 | Pease | 115 | 52186 | 10599 | 7928 | 104566 | 86134 | 18432 | 0.031496 | 17.218 | 6117.0683 | 3.0121e-07 | 0.00016466 | 0.0585 | 8.1266 | 2.4478e-06 | 0.0013381 | 0.4754 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Yuba City Cogen Partners | 49 | 49.97 | 49.97 | 2.469% | 2 |  | 4 |  | 45.0411 | 49.0438 | 4 | Yes | Sierra | Pease, Drum-Rio Oso | Yes | 17 | 2 | 75 | High | DAC_Adjacent | 1.2255 | 3 | 2.6763 | 0.066084 | 4 | A | A | 1 | 71.4286 | 63.8889 | 70.8333
YUBACT_6_UNITA1 | Yuba City Energy Center (Calpine) | 47.16 | 49.9 | PGAE | Gilroy Energy Center, LLC | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2002-07-26 | Pease | 115 | 55813 | 32148 | 0 | 374248 | 374248 | 0 | 0.11375 | 62.1852 | 21893.3552 | 3.0395e-07 | 0.00016616 | 0.0585 | 11.6414 | 3.5384e-06 | 0.0019343 | 0.68102 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Yuba City Energy Center | 47.3 | 47.6 | 47.6 | 7.759% | 4 |  | 3 |  | 33.4548 | 37.4575 | 3 | Yes | Sierra | Pease, Drum-Rio Oso | Yes | 17 | 2 | 75 | High | DAC_Adjacent | 1.2684 | 3 | 3.8687 | 0.30016 | 4 | A | A | 1 | 71.4286 | 68.0556 | 77.0833
LMEC_1_PL1X3 | Los Medanos Energy Center AGGREGATE | 580 |  | PGAE | Los Medanos Energy Center, LLC | COMBINED CYCLE | NATURAL GAS | NP15 | 2001-06-09 | Pittsburg | 115 | 55217 | 3274740 | 1452902 | 24632826 | 21838781 | 2794045 | 7.478 | 89.347 | 1441010.2634 | 3.0358e-07 | 3.6272e-06 | 0.0585 | 6.6689 | 2.0245e-06 | 2.4189e-05 | 0.39013 | CAISO_CCGT2 | Natural Gas Fired Combined Cycle | Los Medanos Energy Center | 678.3 | 574.53 | 574.53 | 55.11% | 4 |  | 3 |  | 34.5836 | 38.5863 | 4 | Yes | Bay Area | Pittsburg | Yes | 16 | 2 | 2220 | High | In_DAC |  | 4 | 0.048378 | 0.026662 | 3 | NA_Marginal | A | 1.25 | 75.8929 | 68.75 | 78.125
DELTA_2_PL1X4 | DELTA ENERGY CENTER AGGREGATE | 880 |  | PGAE | Delta Energy Center, LLC | COMBINED CYCLE | NATURAL GAS | NP15 | 2002-06-17 | Delta EC | 230 | 55333 | 3081664 | 0 | 22825752 | 22825752 | 0 | 6.622 | 83.957 | 1335297.1722 | 2.9011e-07 | 3.6782e-06 | 0.0585 | 7.407 | 2.1488e-06 | 2.7244e-05 | 0.4333 | CAISO_CCGT1 | Natural Gas Fired Combined Cycle | Delta Energy Center | 943.5 | 813 | 813 | 37.29% | 3 |  | 2 |  | 33.5616 | 37.5644 | 4 | Yes | Bay Area | Pittsburg | Yes | 15 | 2 | 2220 | High | In_DAC |  | 4 | 0.054488 | 0.020316 | 3 | NA_Marginal | A | 1.25 | 68.75 | 60.4167 | 65.625
OTAY_6_PL1X2 | Chula Vista Energy Center, LLC | 39.57 | 40 | SDGE | Chula Vista Energy Center, LLC | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2006-06-08 | Miguel | 230 | 55540 | 3070 | 0 | 51755 | 51755 | 0 | 0.02 | 0.418 | 3027.6464 | 3.8644e-07 | 8.0765e-06 | 0.0585 | 16.8583 | 6.5147e-06 | 0.00013616 | 0.9862 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Chula Vista Energy Center | 44 | 35.5 | 35.5 | 0.7965% | 1 |  | 4 |  | 29.5836 | 33.5863 | 2 | Yes | SD-IV | San Diego | Yes | 22 | 1 | 920 | High | DAC_Adjacent | 1.0079 | 3 | 0.27231 | 0.0021689 | 1 | NA_Moderate | A | 1.5 | 48.2143 | 44.4444 | 54.1667
OTMESA_2_PL1X3 | OTAY MESA ENERGY CENTER | 603.68 | 689 | SDGE | Otay Mesa Energy Center, LLC | COMBINED CYCLE | NATURAL GAS | SP15 | 2009-10-02 | Otay Mesa | 230 | 55345 | 493151 | 0 | 3707001 | 3707001 | 0 | 1.119 | 18.132 | 216858.0449 | 3.0186e-07 | 4.8913e-06 | 0.0585 | 7.517 | 2.2691e-06 | 3.6768e-05 | 0.43974 | CAISO_CCGT1 | Natural Gas Fired Combined Cycle | Otay Mesa Generating Project | 688.5 | 603.6 | 603.6 | 8.177% | 1 |  | 1 |  | 26.263 | 30.2658 | 2 | Yes | SD-IV | San Diego | Yes | 20 | 2 | 920 | High | DAC_Adjacent | 8.3474 | 2 | 0.073535 | 0.0060127 | 2 | NA_Moderate | A | 1.5 | 41.0714 | 40.2778 | 35.4167
PALALT_7_COBUG | Cooperatively Owned Back Up Generator | 4.5 | 5.2 | PGAE | NCPA (MSS Agreement - S14) | FTUR | NATURAL GAS | NP15 | 2007-10-15 | Monte Vista | 230 | 57714 | 31 | 0 | 398 | 398 | 0 | 0.0001158 | 0.53422 | 23.2828 | 2.9095e-07 | 0.0013423 | 0.0585 | 12.8387 | 3.7355e-06 | 0.017233 | 0.75106 | CAISO_Peaker2 | Natural Gas Internal Combustion Engine | City of Palo Alto | 4.4 | 4.5 | 4.5 | 0.08043% | 1 |  | 4 |  | 28.2301 | 32.2329 | 2 | Yes | Bay Area | 0 | No | No Published Factor | 4 | 2220 | High | DAC_Adjacent | 1.3547 | 3 | 34.4661 | 0.02772 | 3 | NA_Marginal | A | 1.25 | 65.1786 | 74.3056 | 61.4583
PALOMR_2_PL1X3 | Palomar Energy Center | 588.21 |  | SDGE | San Diego Gas & Electric | COMBINED CYCLE | NATURAL GAS | SP15 | 2005-10-14 | Palomar Energy | 230 | 55985 | 1925066 | 0 | 13759446 | 13759446 | 0 | 4.175 | 45.365 | 804921.973 | 3.0343e-07 | 3.297e-06 | 0.0585 | 7.1475 | 2.1688e-06 | 2.3565e-05 | 0.41813 | CAISO_CCGT1 | Natural Gas Fired Combined Cycle | Palomar Energy | 559 | 565.61 | 565.61 | 39.31% | 3 |  | 1 |  | 30.2329 | 34.2356 | 2 | Yes | SD-IV | San Diego | Yes | 21 | 2 | 920 | High | Outside_DAC | 21.9154 | 1 | 0.047131 | 0.018528 | 3 | NA_Moderate | A | 1.5 | 48.2143 | 48.6111 | 47.9167
PIOPIC_2_CTG1 | Pio Pico Unit 1 | 111.3 | 111.3 | SDGE | Pio Pico Energy Center | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2016-11-03 | Otay Mesa | 230 | 57555 | 150057 | 0 | 1505278 | 1505278 | 0 | 0.447 | 9.355 | 88058.1484 | 2.9696e-07 | 6.2148e-06 | 0.0585 | 10.0314 | 2.9789e-06 | 6.2343e-05 | 0.58683 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Pio Pico Energy Center | 395.4 | 336 | 336 | 4.332% | 3 |  | 2 |  | 19.1699 | 23.1726 | 1 | Yes | SD-IV | San Diego | Yes | 19 | 2 | 920 | High | DAC_Adjacent | 8.0067 | 2 | 0.12469 | 0.0054017 | 1 | NA_Moderate | A | 1.5 | 44.6429 | 50 | 50
PIOPIC_2_CTG2 | Pio Pico Unit 2 | 112.7 | 112.7 | SDGE | Pio Pico Energy Center | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2016-11-03 | Otay Mesa | 230 | 57555 | 150057 | 0 | 1505278 | 1505278 | 0 | 0.447 | 9.355 | 88058.1484 | 2.9696e-07 | 6.2148e-06 | 0.0585 | 10.0314 | 2.9789e-06 | 6.2343e-05 | 0.58683 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Pio Pico Energy Center | 395.4 | 336 | 336 | 4.332% | 3 |  | 2 |  | 19.1699 | 23.1726 | 1 | Yes | SD-IV | San Diego | Yes | 19 | 2 | 920 | High | DAC_Adjacent | 8.0067 | 2 | 0.12469 | 0.0054017 | 1 | NA_Moderate | A | 1.5 | 44.6429 | 50 | 50
PIOPIC_2_CTG3 | Pio Pico Unit 3 | 112 | 112 | SDGE | Pio Pico Energy Center | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2016-11-03 | Otay Mesa | 230 | 57555 | 150057 | 0 | 1505278 | 1505278 | 0 | 0.447 | 9.355 | 88058.1484 | 2.9696e-07 | 6.2148e-06 | 0.0585 | 10.0314 | 2.9789e-06 | 6.2343e-05 | 0.58683 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Pio Pico Energy Center | 395.4 | 336 | 336 | 4.332% | 3 |  | 2 |  | 19.1699 | 23.1726 | 1 | Yes | SD-IV | San Diego | Yes | 19 | 2 | 920 | High | DAC_Adjacent | 8.0067 | 2 | 0.12469 | 0.0054017 | 1 | NA_Moderate | A | 1.5 | 44.6429 | 50 | 50
BARRE_6_PEAKER | Barre Peaker | 49 | 59 | SCE | Southern California Edison Company | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2007-09-20 | Barre | 230 | 56474 | 33130 | 0 | 338877 | 338877 | 0 | 0.1 | 2.052 | 19824.1661 | 2.9509e-07 | 6.0553e-06 | 0.0585 | 10.2287 | 3.0184e-06 | 6.1938e-05 | 0.59838 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Barre Peaker | 49.8 | 47 | 47 | 7.594% | 4 |  | 2 |  | 28.2986 | 32.3014 | 2 | Yes | LA Basin | Western | Yes | 13 | 3 | 1141 | High | In_DAC |  | 4 | 0.12388 | 0.0094075 | 2 | NA_Extreme | NA_Moderate | 4 | 75 | 77.7778 | 79.1667
ALAMIT_2_PL1X3 | Alamitos Energy Center Unit 7 | 674.7 |  | SCE | AES Alamitos Energy LLC | COMBINED CYCLE | NATURAL GAS | SP15 | 2020-02-06 | Alamitos | 230 | 315 | 958300 | 0 | 12353001 | 12353001 | 0 | 3.817 | 49.845 | 722645.5148 | 3.0899e-07 | 4.0351e-06 | 0.0585 | 12.8905 | 3.9831e-06 | 5.2014e-05 | 0.75409 | CAISO_CCGT2 | Natural Gas Steam Turbine | AES Alamitos LLC | 1115 | 1840.52 | 1840.52 | 9.811% | 1 |  | 4 |  | 15.9096 | 19.9123 | 1 | Yes | LA Basin | Western | Yes | 12 | 3 | 1141 | High | DAC_Adjacent | 3.5308 | 3 | 0.10403 | 0.010206 | 3 | NA_Extreme | NA_Moderate | 4 | 67.8571 | 73.6111 | 72.9167
ANAHM_2_CANYN1 | CANYON POWER PLANT UNIT 1 | 49.21 | 71.2 | SCE | City of Anaheim (MSS Agreement - S14) | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2011-09-16 | Villa Park | 230 | 57027 | 181871 | 0 | 1939008 | 1939008 | 0 | 0.584 | 8.334 | 113431.1763 | 3.0118e-07 | 4.2981e-06 | 0.0585 | 10.6614 | 3.2111e-06 | 4.5824e-05 | 0.62369 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Canyon Power Plant | 200 | 194.8 | 194.8 | 10.38% | 4 |  | 2 |  | 24.3068 | 28.3096 | 2 | Yes | LA Basin | Western | Yes | 10 | 3 | 1141 | High | In_DAC |  | 4 | 0.091647 | 0.0095137 | 2 | NA_Extreme | NA_Moderate | 4 | 75 | 77.7778 | 79.1667
ANAHM_2_CANYN2 | CANYON POWER PLANT UNIT 2 | 48.04 | 71.2 | SCE | City of Anaheim (MSS Agreement - S14) | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2011-09-16 | Villa Park | 230 | 57027 | 181871 | 0 | 1939008 | 1939008 | 0 | 0.584 | 8.334 | 113431.1763 | 3.0118e-07 | 4.2981e-06 | 0.0585 | 10.6614 | 3.2111e-06 | 4.5824e-05 | 0.62369 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Canyon Power Plant | 200 | 194.8 | 194.8 | 10.38% | 4 |  | 2 |  | 24.3068 | 28.3096 | 2 | Yes | LA Basin | Western | Yes | 10 | 3 | 1141 | High | In_DAC |  | 4 | 0.091647 | 0.0095137 | 2 | NA_Extreme | NA_Moderate | 4 | 75 | 77.7778 | 79.1667
REDBLF_6_UNIT | RED BLUFF PEAKER PLANT | 44 | 44 | PGAE | California Power Holdings, LLC | RECIPROCATING ENGINE | NATURAL GAS | NP15 | 2001-08-11 | Cottonwood | 230 | 56184 | 13845 | 0 | 142989 | 142989 | 0 | 0.042056 | 194.0174 | 8364.7981 | 2.9412e-07 | 0.0013569 | 0.0585 | 10.3278 | 3.0376e-06 | 0.014014 | 0.60417 | CAISO_Reciprocating_Engine | Natural Gas Internal Combustion Engine | Red Bluff | 46.4 | 44 | 44 | 3.406% | 2 |  | 2 |  | 34.411 | 38.4137 | 3 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | Outside_DAC | 39.2705 | 1 | 28.0271 | 0.95466 | 4 | A | A | 1 | 60.7143 | 66.6667 | 50
RUSCTY_2_UNITS | Russell City Energy Center | 615.18 |  | PGAE | Russell City Energy Company, LLC | COMBINED CYCLE | NATURAL GAS | NP15 | 2013-08-08 | East Shore | 230 | 56467 | 1010425 | 0 | 7578352 | 7578352 | 0 | 2.221 | 27.581 | 443330.4978 | 2.9307e-07 | 3.6394e-06 | 0.0585 | 7.5002 | 2.1981e-06 | 2.7296e-05 | 0.43876 | CAISO_CCGT1 | Natural Gas Fired Combined Cycle | Russell City Energy Center | 655 | 597.4 | 613.22 | 17.61% | 2 |  | 3 |  | 22.411 | 26.4137 | 1 | Yes | Bay Area | Ames | Yes | 4 | 4 | 2220 | High | In_DAC |  | 4 | 0.054593 | 0.0096138 | 3 | NA_Marginal | A | 1.25 | 65.1786 | 77.0833 | 65.625
ANAHM_2_CANYN3 | CANYON POWER PLANT UNIT 3 | 46.49 | 71.2 | SCE | City of Anaheim (MSS Agreement - S14) | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2011-07-30 | Villa Park | 230 | 57027 | 181871 | 0 | 1939008 | 1939008 | 0 | 0.584 | 8.334 | 113431.1763 | 3.0118e-07 | 4.2981e-06 | 0.0585 | 10.6614 | 3.2111e-06 | 4.5824e-05 | 0.62369 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Canyon Power Plant | 200 | 194.8 | 194.8 | 10.38% | 4 |  | 2 |  | 24.4384 | 28.4411 | 2 | Yes | LA Basin | Western | Yes | 10 | 3 | 1141 | High | In_DAC |  | 4 | 0.091647 | 0.0095137 | 2 | NA_Extreme | NA_Moderate | 4 | 75 | 77.7778 | 79.1667
ANAHM_2_CANYN4 | CANYON POWER PLANT UNIT 4 | 49.8 | 71.2 | SCE | City of Anaheim (MSS Agreement - S14) | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2011-07-30 | Villa Park | 230 | 57027 | 181871 | 0 | 1939008 | 1939008 | 0 | 0.584 | 8.334 | 113431.1763 | 3.0118e-07 | 4.2981e-06 | 0.0585 | 10.6614 | 3.2111e-06 | 4.5824e-05 | 0.62369 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Canyon Power Plant | 200 | 194.8 | 194.8 | 10.38% | 4 |  | 2 |  | 24.4384 | 28.4411 | 2 | Yes | LA Basin | Western | Yes | 10 | 3 | 1141 | High | In_DAC |  | 4 | 0.091647 | 0.0095137 | 2 | NA_Extreme | NA_Moderate | 4 | 75 | 77.7778 | 79.1667
GLNARM_7_UNIT 3 | GLEN ARM UNIT 3 | 44.83 | 47.3 | SCE | City of Pasadena | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2004-01-08 | Eagle Rock (SCE) | 230 | 422 | 107233.32 | 0 | 1166292 | 1166292 | 0 | 0.235 | 7.321 | 68227.6058 | 2.0149e-07 | 6.2772e-06 | 0.0585 | 10.8762 | 2.1915e-06 | 6.8272e-05 | 0.63625 | CAISO_CCGT2 | Natural Gas Fired Combustion Turbine | Glenarm | 265.6 | 196.62 | 196.62 | 4.609% | 1 |  | 4 |  | 32 | 36.0027 | 3 | Yes | LA Basin | Western | Yes | 10 | 3 | 1141 | High | DAC_Adjacent | 1.863 | 3 | 0.13654 | 0.0062932 | 2 | NA_Extreme | NA_Moderate | 4 | 71.4286 | 70.8333 | 68.75
GLNARM_7_UNIT 4 | GLEN ARM UNIT 4 | 42.42 | 47.3 | SCE | City of Pasadena | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2004-01-08 | Eagle Rock (SCE) | 230 | 422 | 107233.32 | 0 | 1166292 | 1166292 | 0 | 0.235 | 7.321 | 68227.6058 | 2.0149e-07 | 6.2772e-06 | 0.0585 | 10.8762 | 2.1915e-06 | 6.8272e-05 | 0.63625 | CAISO_CCGT2 | Natural Gas Fired Combustion Turbine | Glenarm | 265.6 | 196.62 | 196.62 | 4.609% | 1 |  | 4 |  | 32 | 36.0027 | 3 | Yes | LA Basin | Western | Yes | 10 | 3 | 1141 | High | DAC_Adjacent | 1.863 | 3 | 0.13654 | 0.0062932 | 2 | NA_Extreme | NA_Moderate | 4 | 71.4286 | 70.8333 | 68.75
TIDWTR_2_UNITS | MARTINEZ COGEN LIMITED PARTNERSHIP | 114.8 | 114.8 | PGAE | Martinez Cogen Limited Partnership | FTUR | NATURAL GAS | NP15 | 1987-02-23 | Gill Ranch | 115 | 10342 | 673306 | 1686404 | 7074502 | 4115901 | 2958601 | 2.0423 | 953.0625 | 413855.4785 | 2.8868e-07 | 0.00013472 | 0.0585 | 6.113 | 1.7647e-06 | 0.00082353 | 0.35761 | CAISO_Peaker1 | Natural Gas Fired Combined Cycle | Foster Wheeler Martinez | 113.5 | 11.19 | 8.61 | 67.72% | 4 |  | 2 |  | 48.8849 | 52.8877 | 4 | Yes | Bay Area | Pittsburg | Yes | 10 | 3 | 2220 | High | DAC_Adjacent | 0.48269 | 3 | 1.6471 | 1.1154 | 4 | NA_Marginal | A | 1.25 | 75.8929 | 72.9167 | 71.875
RVSIDE_6_SPRING | SPRINGS GENERATION PROJECT AGGREGATE | 36 |  | SCE | City of Riverside (MSSA) | FTUR | NATURAL GAS | SP15 | 2002-06-13 | Vista (SCE) | 230 | 56144 | 465 | 0 | 6529 | 6529 | 0 | 0.0018813 | 1.0284 | 381.9438 | 2.8815e-07 | 0.00015752 | 0.0585 | 14.0409 | 4.0458e-06 | 0.0022117 | 0.82138 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Springs Generating Station | 40 | 36 | 36 | 0.1327% | 1 |  | 4 |  | 33.5726 | 37.5753 | 3 | Yes | LA Basin | Eastern | Yes | 34 | 1 | 1141 | High | DAC_Adjacent | 0.31088 | 3 | 4.4234 | 0.0058701 | 1 | NA_Extreme | NA_Moderate | 4 | 60.7143 | 51.3889 | 64.5833
RVSIDE_2_RERCU3 | Riverside Energy Res. Ctr Unit 3 | 49 | 71 | SCE | City of Riverside (MSSA) | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2011-04-01 | Mira Loma | 500 | 56143 | 86351 | 0 | 934103 | 934103 | 0 | 0.283 | 4.823 | 54644.6441 | 3.0296e-07 | 5.1632e-06 | 0.0585 | 10.8175 | 3.2773e-06 | 5.5853e-05 | 0.63282 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Riverside Energy Resource Center | 196 | 194.85 | 194.85 | 5.029% | 3 |  | 2 |  | 24.7671 | 28.7699 | 2 | Yes | LA Basin | Eastern | Yes | 9 | 4 | 1141 | High | In_DAC |  | 4 | 0.11171 | 0.0056181 | 1 | NA_Extreme | NA_Moderate | 4 | 71.4286 | 79.1667 | 68.75
RVSIDE_2_RERCU4 | Riverside Energy Res. Ctr Unit 4 | 49 | 71.2 | SCE | City of Riverside (MSSA) | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2011-04-01 | Mira Loma | 500 | 56143 | 86351 | 0 | 934103 | 934103 | 0 | 0.283 | 4.823 | 54644.6441 | 3.0296e-07 | 5.1632e-06 | 0.0585 | 10.8175 | 3.2773e-06 | 5.5853e-05 | 0.63282 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Riverside Energy Resource Center | 196 | 194.85 | 194.85 | 5.029% | 3 |  | 2 |  | 24.7671 | 28.7699 | 2 | Yes | LA Basin | Eastern | Yes | 9 | 4 | 1141 | High | In_DAC |  | 4 | 0.11171 | 0.0056181 | 1 | NA_Extreme | NA_Moderate | 4 | 71.4286 | 79.1667 | 68.75
RVSIDE_6_RERCU1 | Riverside Energy Res. Ctr Unit 1 | 48.35 | 48.5 | SCE | City of Riverside (MSSA) | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2006-06-01 | Mira Loma | 500 | 56143 | 86351 | 0 | 934103 | 934103 | 0 | 0.283 | 4.823 | 54644.6441 | 3.0296e-07 | 5.1632e-06 | 0.0585 | 10.8175 | 3.2773e-06 | 5.5853e-05 | 0.63282 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Riverside Energy Resource Center | 196 | 194.85 | 194.85 | 5.029% | 3 |  | 2 |  | 29.6027 | 33.6055 | 2 | Yes | LA Basin | Eastern | Yes | 9 | 4 | 1141 | High | In_DAC |  | 4 | 0.11171 | 0.0056181 | 1 | NA_Extreme | NA_Moderate | 4 | 71.4286 | 79.1667 | 68.75
SENTNL_2_CTG1 | Sentinel Unit 1 | 107.68 | 131.8 | SCE | Sentinel Energy Center, LLC | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2013-05-06 | Devers | 500 | 57482 | 485658 | 0 | 4981514 | 4981514 | 0 | 1.498 | 25.839 | 291416.535 | 3.0071e-07 | 5.187e-06 | 0.0585 | 10.2572 | 3.0845e-06 | 5.3204e-05 | 0.60004 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Sentinel Energy Center, LLC | 800 | 802.08 | 802.08 | 6.93% | 3 |  | 1 |  | 22.6685 | 26.6712 | 1 | Yes | LA Basin | Eastern, Valley-Devers | Yes | 7 | 4 | 1141 | High | Outside_DAC | 27.1901 | 1 | 0.10641 | 0.0073741 | 2 | NA_Severe 15 | A | 2.25 | 50.8929 | 64.5833 | 46.875
SENTNL_2_CTG2 | Sentinel Unit 2 | 104.19 | 131.8 | SCE | Sentinel Energy Center, LLC | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2013-05-06 | Devers | 500 | 57482 | 485658 | 0 | 4981514 | 4981514 | 0 | 1.498 | 25.839 | 291416.535 | 3.0071e-07 | 5.187e-06 | 0.0585 | 10.2572 | 3.0845e-06 | 5.3204e-05 | 0.60004 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Sentinel Energy Center, LLC | 800 | 802.08 | 802.08 | 6.93% | 3 |  | 1 |  | 22.6685 | 26.6712 | 1 | Yes | LA Basin | Eastern, Valley-Devers | Yes | 7 | 4 | 1141 | High | Outside_DAC | 27.1901 | 1 | 0.10641 | 0.0073741 | 2 | NA_Severe 15 | A | 2.25 | 50.8929 | 64.5833 | 46.875
SENTNL_2_CTG3 | Sentinel Unit 3 | 105.69 | 131.8 | SCE | Sentinel Energy Center, LLC | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2013-05-06 | Devers | 500 | 57482 | 485658 | 0 | 4981514 | 4981514 | 0 | 1.498 | 25.839 | 291416.535 | 3.0071e-07 | 5.187e-06 | 0.0585 | 10.2572 | 3.0845e-06 | 5.3204e-05 | 0.60004 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Sentinel Energy Center, LLC | 800 | 802.08 | 802.08 | 6.93% | 3 |  | 1 |  | 22.6685 | 26.6712 | 1 | Yes | LA Basin | Eastern, Valley-Devers | Yes | 7 | 4 | 1141 | High | Outside_DAC | 27.1901 | 1 | 0.10641 | 0.0073741 | 2 | NA_Severe 15 | A | 2.25 | 50.8929 | 64.5833 | 46.875
SENTNL_2_CTG4 | Sentinel Unit 4 | 106.55 | 131.8 | SCE | Sentinel Energy Center, LLC | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2013-05-06 | Devers | 500 | 57482 | 485658 | 0 | 4981514 | 4981514 | 0 | 1.498 | 25.839 | 291416.535 | 3.0071e-07 | 5.187e-06 | 0.0585 | 10.2572 | 3.0845e-06 | 5.3204e-05 | 0.60004 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Sentinel Energy Center, LLC | 800 | 802.08 | 802.08 | 6.93% | 3 |  | 1 |  | 22.6685 | 26.6712 | 1 | Yes | LA Basin | Eastern, Valley-Devers | Yes | 7 | 4 | 1141 | High | Outside_DAC | 27.1901 | 1 | 0.10641 | 0.0073741 | 2 | NA_Severe 15 | A | 2.25 | 50.8929 | 64.5833 | 46.875
SENTNL_2_CTG5 | Sentinel Unit 5 | 107.52 | 131.8 | SCE | Sentinel Energy Center, LLC | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2013-05-06 | Devers | 500 | 57482 | 485658 | 0 | 4981514 | 4981514 | 0 | 1.498 | 25.839 | 291416.535 | 3.0071e-07 | 5.187e-06 | 0.0585 | 10.2572 | 3.0845e-06 | 5.3204e-05 | 0.60004 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Sentinel Energy Center, LLC | 800 | 802.08 | 802.08 | 6.93% | 3 |  | 1 |  | 22.6685 | 26.6712 | 1 | Yes | LA Basin | Eastern, Valley-Devers | Yes | 7 | 4 | 1141 | High | Outside_DAC | 27.1901 | 1 | 0.10641 | 0.0073741 | 2 | NA_Severe 15 | A | 2.25 | 50.8929 | 64.5833 | 46.875
SENTNL_2_CTG6 | Sentinel Unit 6 | 105 | 131.8 | SCE | Sentinel Energy Center, LLC | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2013-05-06 | Devers | 500 | 57482 | 485658 | 0 | 4981514 | 4981514 | 0 | 1.498 | 25.839 | 291416.535 | 3.0071e-07 | 5.187e-06 | 0.0585 | 10.2572 | 3.0845e-06 | 5.3204e-05 | 0.60004 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Sentinel Energy Center, LLC | 800 | 802.08 | 802.08 | 6.93% | 3 |  | 1 |  | 22.6685 | 26.6712 | 1 | Yes | LA Basin | Eastern, Valley-Devers | Yes | 7 | 4 | 1141 | High | Outside_DAC | 27.1901 | 1 | 0.10641 | 0.0073741 | 2 | NA_Severe 15 | A | 2.25 | 50.8929 | 64.5833 | 46.875
SENTNL_2_CTG7 | Sentinel Unit 7 | 106.73 | 131.8 | SCE | Sentinel Energy Center, LLC | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2013-05-06 | Devers | 500 | 57482 | 485658 | 0 | 4981514 | 4981514 | 0 | 1.498 | 25.839 | 291416.535 | 3.0071e-07 | 5.187e-06 | 0.0585 | 10.2572 | 3.0845e-06 | 5.3204e-05 | 0.60004 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Sentinel Energy Center, LLC | 800 | 802.08 | 802.08 | 6.93% | 3 |  | 1 |  | 22.6685 | 26.6712 | 1 | Yes | LA Basin | Eastern, Valley-Devers | Yes | 7 | 4 | 1141 | High | Outside_DAC | 27.1901 | 1 | 0.10641 | 0.0073741 | 2 | NA_Severe 15 | A | 2.25 | 50.8929 | 64.5833 | 46.875
SENTNL_2_CTG8 | Sentinel Unit 8 | 106.85 | 131.8 | SCE | Sentinel Energy Center, LLC | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2013-05-06 | Devers | 500 | 57482 | 485658 | 0 | 4981514 | 4981514 | 0 | 1.498 | 25.839 | 291416.535 | 3.0071e-07 | 5.187e-06 | 0.0585 | 10.2572 | 3.0845e-06 | 5.3204e-05 | 0.60004 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Sentinel Energy Center, LLC | 800 | 802.08 | 802.08 | 6.93% | 3 |  | 1 |  | 22.6685 | 26.6712 | 1 | Yes | LA Basin | Eastern, Valley-Devers | Yes | 7 | 4 | 1141 | High | Outside_DAC | 27.1901 | 1 | 0.10641 | 0.0073741 | 2 | NA_Severe 15 | A | 2.25 | 50.8929 | 64.5833 | 46.875
RVSIDE_6_RERCU2 | Riverside Energy Res. Ctr Unit 2 | 48.5 | 48.5 | SCE | City of Riverside (MSSA) | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2006-06-01 | Mira Loma | 500 | 56143 | 86351 | 0 | 934103 | 934103 | 0 | 0.283 | 4.823 | 54644.6441 | 3.0296e-07 | 5.1632e-06 | 0.0585 | 10.8175 | 3.2773e-06 | 5.5853e-05 | 0.63282 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Riverside Energy Resource Center | 196 | 194.85 | 194.85 | 5.029% | 3 |  | 2 |  | 29.6027 | 33.6055 | 2 | Yes | LA Basin | Eastern | Yes | 9 | 4 | 1141 | High | In_DAC |  | 4 | 0.11171 | 0.0056181 | 1 | NA_Extreme | NA_Moderate | 4 | 71.4286 | 79.1667 | 68.75
SBERDO_2_PSP3 | Mountainview Gen Sta. Unit 3 | 555 |  | SCE | Southern California Edison Company | COMBINED CYCLE | NATURAL GAS | SP15 | 2005-12-10 | San Bernarino | 230 | 358 | 2091874.84 | 0 | 16733883 | 16733883 | 0 | 4.564 | 96.327 | 978925.3231 | 2.7274e-07 | 5.7564e-06 | 0.0585 | 7.9995 | 2.1818e-06 | 4.6048e-05 | 0.46797 | CAISO_CCGT1 | Natural Gas Fired Combined Cycle | Mountainview Generating Station | 1036.8 | 1110 | 1110 | 23.03% | 2 |  | 3 |  | 30.0767 | 34.0795 | 2 | Yes | LA Basin | Eastern, West of Devers | Yes | 9 | 4 | 1141 | High | DAC_Adjacent | 0.13304 | 3 | 0.092096 | 0.021212 | 3 | NA_Extreme | NA_Moderate | 4 | 75 | 81.9444 | 72.9167
DUANE_1_PL1X3 | DONALD VON RAESFELD POWER PROJECT | 147.8 |  | PGAE | City of Santa Clara DBA Silicon Valley Power (MSS Agreement - S14) | COMBINED CYCLE | NATURAL GAS | NP15 | 2005-03-24 | FMC | 115 | 56026 | 861341 | 0 | 7378537 | 7378537 | 0 | 2.053 | 21.104 | 431641.4018 | 2.7824e-07 | 2.8602e-06 | 0.0585 | 8.5663 | 2.3835e-06 | 2.4501e-05 | 0.50113 | CAISO_CCGT2 | Natural Gas Fired Combined Cycle | Donald Von Raesfeld Power Plant | 154 | 143.5 | 143.5 | 63.85% | 4 |  | 3 |  | 30.7918 | 34.7945 | 3 | Yes | Bay Area | San Jose, South Bay-Moss Landing | Yes | 8 | 4 | 2220 | High | In_DAC |  | 4 | 0.049003 | 0.031287 | 3 | NA_Marginal | A | 1.25 | 79.4643 | 85.4167 | 78.125
STIGCT_2_LODI | LODI STIG UNIT | 49.9 | 51.2 | PGAE | NCPA (MSS Agreement - S14) | COMBUSTION TURBINE | NATURAL GAS | NP15 | 1996-01-01 | Eight Mile | 230 | 7449 | 11838 | 0 | 111717 | 111717 | 0 | 0.033 | 0.913 | 6535.3989 | 2.9539e-07 | 8.1724e-06 | 0.0585 | 9.4372 | 2.7876e-06 | 7.7125e-05 | 0.55207 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Combustion Turbine Project No 2 | 50 | 49.5 | 49.5 | 2.703% | 2 |  | 1 |  | 40.0247 | 44.0274 | 3 | Yes | Sierra | South of Rio Oso, South of Palermo | Yes | 14 | 3 | 75 | High | DAC_Adjacent | 3.0931 | 3 | 0.15425 | 0.0041689 | 1 | NA_Extreme | NA_Moderate | 4 | 60.7143 | 59.7222 | 52.0833
GWFPWR_1_UNITS | Hanford Peaker Plant | 98.46 |  | PGAE | MRP San Joaquin Energy, LLC | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2001-08-27 | Waukena | 115 | 55698 | 15605 | 0 | 183100 | 183100 | 0 | 0.054 | 24.363 | 10711.2752 | 2.9492e-07 | 0.00013306 | 0.0585 | 11.7334 | 3.4604e-06 | 0.0015612 | 0.6864 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Hanford Energy Park Peaker | 92.2 | 90.59 | 92.58 | 1.932% | 1 |  | 3 |  | 34.3671 | 38.3699 | 3 | Yes | Fresno | Herndon, Hanford | Yes | 8 | 4 | 793 | High | DAC_Adjacent | 1.955 | 3 | 3.1225 | 0.060329 | 4 | NA_Extreme | NA_Moderate | 4 | 78.5714 | 80.5556 | 70.8333
TERMEX_2_PL1X3 | TDM | 625 |  | SDGE | Termoelectrica De Mexicali S. de R.L. de C.V. (non-pro forma agreement) | COMBINED CYCLE | NATURAL GAS | SP15 | 2003-07-30 | Imperial Valley | 230 | 55719 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | CAISO_CCGT1 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 2.5 |  | 2.5 |  | 32.4438 | 36.4466 | 3 | Yes | SD-IV | 0 | Yes | 25 | 1 | 920 | High | Not Available | Not Available | 1 | Not Available | Not Available | 2.5 | Not Available | Not Available | 1.75 | 50.8929 | 43.75 | 53.125
CALPIN_1_AGNEW | Agnews Power Plant | 28.56 | 41.5 | PGAE | O.L.S. Energy-Agnews, Inc. | COMBUSTION TURBINE | NATURAL GAS | NP15 | 1990-10-19 | Los Esteros | 115 | 50748 | 15801 | 0 | 151465 | 151465 | 0 | 0.044159 | 20.6077 | 8860.6407 | 2.9155e-07 | 0.00013606 | 0.0585 | 9.5858 | 2.7947e-06 | 0.0013042 | 0.56076 | CAISO_CCGT2 | Natural Gas Fired Combined Cycle | Agnews Power Plant | 32 | 28.56 | 28.56 | 5.637% | 1 |  | 4 |  | 45.2301 | 49.2329 | 4 | Yes | Bay Area | San Jose, South Bay-Moss Landing | Yes | 7 | 4 | 2220 | High | DAC_Adjacent | 1.1494 | 3 | 2.6084 | 0.14703 | 4 | NA_Marginal | A | 1.25 | 75.8929 | 77.0833 | 65.625
CSCGNR_1_UNIT 1 | GIANERA PEAKER UNIT 1 | 24.75 | 24.8 | PGAE | City of Santa Clara DBA Silicon Valley Power (MSS Agreement - S14) | FTUR | NATURAL GAS | NP15 | 1987-01-01 | Los Esteros | 115 | 7231 | 8019 | 0 | 117278 | 117278 | 0 | 0.03406 | 18.6192 | 6860.7151 | 2.9042e-07 | 0.00015876 | 0.0585 | 14.625 | 4.2474e-06 | 0.0023219 | 0.85556 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Gianera | 64.6 | 48 | 48 | 1.417% | 1 |  | 4 |  | 49.0301 | 53.0329 | 4 | Yes | Bay Area | San Jose, South Bay-Moss Landing | Yes | 7 | 4 | 2220 | High | DAC_Adjacent | 1.1779 | 3 | 4.6438 | 0.065804 | 4 | NA_Marginal | A | 1.25 | 75.8929 | 77.0833 | 65.625
VACADX_1_UNITA1 | CalPeak Power Vaca Dixon Unit 1 | 51.91 | 57 | PGAE | CalPeak Power - Vaca-Dixon LLC | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2002-06-21 | Vaca Dixon | 500 | 55499 | 11340 | 0 | 124887 | 124887 | 0 | 0.035 | 0.628 | 7305.8385 | 2.8025e-07 | 5.0285e-06 | 0.0585 | 11.013 | 3.0864e-06 | 5.5379e-05 | 0.64425 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | CalPeak Power Vaca Dixon Peaker Plant | 60.5 | 50.61 | 50.61 | 2.14% | 1 |  | 3 |  | 33.5507 | 37.5534 | 3 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | Outside_DAC | 23.3294 | 1 | 0.11076 | 0.0023699 | 1 | NA_Moderate | A | 1.5 | 51.7857 | 59.7222 | 39.5833
CSCGNR_1_UNIT 2 | GIANERA PEAKER UNIT 2 | 24.75 | 24.8 | PGAE | City of Santa Clara DBA Silicon Valley Power (MSS Agreement - S14) | FTUR | NATURAL GAS | NP15 | 1986-01-01 | Los Esteros | 115 | 7231 | 8019 | 0 | 117278 | 117278 | 0 | 0.03406 | 18.6192 | 6860.7151 | 2.9042e-07 | 0.00015876 | 0.0585 | 14.625 | 4.2474e-06 | 0.0023219 | 0.85556 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Gianera | 64.6 | 48 | 48 | 1.417% | 1 |  | 4 |  | 50.0301 | 54.0329 | 4 | Yes | Bay Area | San Jose, South Bay-Moss Landing | Yes | 7 | 4 | 2220 | High | DAC_Adjacent | 1.1779 | 3 | 4.6438 | 0.065804 | 4 | NA_Marginal | A | 1.25 | 75.8929 | 77.0833 | 65.625
BOGUE_1_UNITA1 | Feather River Energy Center, Unit #1 | 48.69 | 49.9 | PGAE | Gilroy Energy Center, LLC | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2002-12-23 | Bogue | 115 | 55847 | 33113 | 0 | 388898 | 388898 | 0 | 0.122 | 15.105 | 22750.3742 | 3.1371e-07 | 3.8841e-05 | 0.0585 | 11.7446 | 3.6844e-06 | 0.00045617 | 0.68705 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Feather River Energy Center | 47 | 47.6 | 47.6 | 8.043% | 4 |  | 3 |  | 33.0438 | 37.0466 | 3 | Yes | Sierra | Bogue, Drum-Rio Oso | Yes | 5 | 4 | 75 | High | DAC_Adjacent | 0.3758 | 3 | 0.91233 | 0.073375 | 4 | A | A | 1 | 78.5714 | 84.7222 | 77.0833
VESTAL_2_WELLHD | Wellhead Power Delano | 49 | 49.5 | SCE | Delano Energy Center, LLC | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2013-01-16 | Smyrna | 115 | 58122 | 5455 | 0 | 67225 | 67225 | 0 | 0.019 | 0.308 | 3932.6351 | 2.8263e-07 | 4.5816e-06 | 0.0585 | 12.3236 | 3.483e-06 | 5.6462e-05 | 0.72092 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Delano Energy Center | 48.5 | 49 | 49 | 1.284% | 1 |  | 3 |  | 22.9699 | 26.9726 | 1 | Yes | BC/Ventura | Vestal | No | No Published Factor | 4 | 657 | High | In_DAC |  | 4 | 0.11292 | 0.0014499 | 1 | NA_Extreme | NA_Moderate | 4 | 64.2857 | 75 | 62.5
WALCRK_2_CTG1 | Walnut Creek Energy Park Unit 1 | 97.32 | 102.5 | SCE | Walnut Creek Energy, LLC | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2013-03-21 | Walnut | 230 | 57515 | 382025 | 0 | 3901517 | 3901517 | 0 | 1.132 | 20.98 | 228237.1515 | 2.9014e-07 | 5.3774e-06 | 0.0585 | 10.2127 | 2.9632e-06 | 5.4918e-05 | 0.59744 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Walnut Creek Energy Park | 500 | 483.13 | 483.13 | 8.722% | 4 |  | 1 |  | 22.7945 | 26.7973 | 1 | Yes | LA Basin | Western | Yes | 12 | 3 | 1141 | High | In_DAC |  | 4 | 0.10984 | 0.0095799 | 2 | NA_Extreme | NA_Moderate | 4 | 67.8571 | 73.6111 | 72.9167
WALCRK_2_CTG2 | Walnut Creek Energy Park Unit 2 | 96.91 | 102.5 | SCE | Walnut Creek Energy, LLC | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2013-03-21 | Walnut | 230 | 57515 | 382025 | 0 | 3901517 | 3901517 | 0 | 1.132 | 20.98 | 228237.1515 | 2.9014e-07 | 5.3774e-06 | 0.0585 | 10.2127 | 2.9632e-06 | 5.4918e-05 | 0.59744 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Walnut Creek Energy Park | 500 | 483.13 | 483.13 | 8.722% | 4 |  | 1 |  | 22.7945 | 26.7973 | 1 | Yes | LA Basin | Western | Yes | 12 | 3 | 1141 | High | In_DAC |  | 4 | 0.10984 | 0.0095799 | 2 | NA_Extreme | NA_Moderate | 4 | 67.8571 | 73.6111 | 72.9167
WALCRK_2_CTG3 | Walnut Creek Energy Park Unit 3 | 96.65 | 102.5 | SCE | Walnut Creek Energy, LLC | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2013-03-21 | Walnut | 230 | 57515 | 382025 | 0 | 3901517 | 3901517 | 0 | 1.132 | 20.98 | 228237.1515 | 2.9014e-07 | 5.3774e-06 | 0.0585 | 10.2127 | 2.9632e-06 | 5.4918e-05 | 0.59744 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Walnut Creek Energy Park | 500 | 483.13 | 483.13 | 8.722% | 4 |  | 1 |  | 22.7945 | 26.7973 | 1 | Yes | LA Basin | Western | Yes | 12 | 3 | 1141 | High | In_DAC |  | 4 | 0.10984 | 0.0095799 | 2 | NA_Extreme | NA_Moderate | 4 | 67.8571 | 73.6111 | 72.9167
WALCRK_2_CTG4 | Walnut Creek Energy Park Unit 4 | 96.6 | 102.5 | SCE | Walnut Creek Energy, LLC | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2013-03-29 | Walnut | 230 | 57515 | 382025 | 0 | 3901517 | 3901517 | 0 | 1.132 | 20.98 | 228237.1515 | 2.9014e-07 | 5.3774e-06 | 0.0585 | 10.2127 | 2.9632e-06 | 5.4918e-05 | 0.59744 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Walnut Creek Energy Park | 500 | 483.13 | 483.13 | 8.722% | 4 |  | 1 |  | 22.7726 | 26.7753 | 1 | Yes | LA Basin | Western | Yes | 12 | 3 | 1141 | High | In_DAC |  | 4 | 0.10984 | 0.0095799 | 2 | NA_Extreme | NA_Moderate | 4 | 67.8571 | 73.6111 | 72.9167
WALCRK_2_CTG5 | Walnut Creek Energy Park Unit 5 | 96.65 | 102.5 | SCE | Walnut Creek Energy, LLC | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2013-04-30 | Walnut | 230 | 57515 | 382025 | 0 | 3901517 | 3901517 | 0 | 1.132 | 20.98 | 228237.1515 | 2.9014e-07 | 5.3774e-06 | 0.0585 | 10.2127 | 2.9632e-06 | 5.4918e-05 | 0.59744 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Walnut Creek Energy Park | 500 | 483.13 | 483.13 | 8.722% | 4 |  | 1 |  | 22.6849 | 26.6877 | 1 | Yes | LA Basin | Western | Yes | 12 | 3 | 1141 | High | In_DAC |  | 4 | 0.10984 | 0.0095799 | 2 | NA_Extreme | NA_Moderate | 4 | 67.8571 | 73.6111 | 72.9167
WOLFSK_1_UNITA1 | Wolfskill Energy Center | 48.68 | 49.9 | PGAE | Gilroy Energy Center, LLC | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2003-03-22 | Peabody | 230 | 55855 | 9388 | 0 | 111140 | 111140 | 0 | 0.035 | 0.919 | 6501.6446 | 3.1492e-07 | 8.2689e-06 | 0.0585 | 11.8385 | 3.7282e-06 | 9.7891e-05 | 0.69255 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Wolfskill Energy Center | 47 | 46.9 | 46.9 | 2.28% | 2 |  | 3 |  | 32.8 | 36.8027 | 3 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | Outside_DAC | 11.2239 | 1 | 0.19578 | 0.0044642 | 1 | NA_Marginal | A | 1.25 | 54.4643 | 63.1944 | 44.7917
AGRICO_6_PL3N5 | Fresno Peaker | 22.69 |  | PGAE | Fresno Cogeneration Partners, LP | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2006-08-30 | Helm | 230 | 10156 | 5887 | 21636 | 117540 | 57438 | 60102 | 0.011 | 0.178 | 6876.042 | 9.3585e-08 | 1.5144e-06 | 0.0585 | 9.7568 | 9.1309e-07 | 1.4775e-05 | 0.57077 | CAISO_Peaker2 | Natural Gas Fired Combined Cycle | Fresno Cogen Partners | 82.6 | 73.29 | 73.29 | 0.8136% | 1 |  | 1 |  | 29.3562 | 33.3589 | 2 | Yes | Fresno | Herndon | Yes | 4 | 4 | 793 | High | In_DAC |  | 4 | 0.029551 | 0.00024042 | 1 | NA_Extreme | NA_Moderate | 4 | 60.7143 | 66.6667 | 50
AGRICO_7_UNIT | Fresno Cogen | 50.6 |  | PGAE | Fresno Cogeneration Partners, LP | OTHER | NATURAL GAS | NP15 | 2023-03-14 | Helm | 230 | 10156 | 5887 | 21636 | 117540 | 57438 | 60102 | 0.011 | 0.178 | 6876.042 | 9.3585e-08 | 1.5144e-06 | 0.0585 | 9.7568 | 9.1309e-07 | 1.4775e-05 | 0.57077 | CAISO_Peaker2 | Natural Gas Fired Combined Cycle | Fresno Cogen Partners | 82.6 | 73.29 | 73.29 | 0.8136% | 1 |  | 1 |  | 12.8082 | 16.811 | 1 | Yes | Fresno | Herndon | Yes | 4 | 4 | 793 | High | In_DAC |  | 4 | 0.029551 | 0.00024042 | 1 | NA_Extreme | NA_Moderate | 4 | 57.1429 | 66.6667 | 50

## CHPs
[35 empty] | *Resources with Not Available CF receive a 2.5 |  | *Resources with Not Available data receive a 2.5 | [9 empty] | *Resources with No published LEF receive a 4 | [7 empty] | *Resources with Not Available data receive a 2.4 |  |  | *Resources with Not Available data receive a 1.75
CAISO Master Generator List Information | [9 empty] | IRP Modeled Interconnection Point |  | EIA 2018 Emissions Data | [15 empty] | IRP Info | [10 empty] | Age |  |  | Local Need | [7 empty] | DACs and Air Pollution | [8 empty] | Sample Scoring Combinations (Scaled so Max Highest Score=100)
RESOURCE_ID | GEN_UNIT_NAME | NET_DEPENDABLE_CAPACITY (MW) | NAMEPLATE_CAPACITY (MW) | PTO_AREA | OWNER_OR_QF | UNIT_TYPE | ENERGY_SOURCE | ZONE | COD | Substation | Voltage | EIA Code | 2018 Generation (MWh) | 2018 Useful Thermal Output (MMBtu) | 2018 Total Fuel Consumption (MMBtu) | 2018 Fuel Consumption for Electric Generation (MMBtu) | 2018 Fuel Consumption for Useful Thermal Output (MMBtu) | 2018 SO2 Emission (Tons) | 2018 NOx Emission (Tons) | 2018 CO2 Emission (Tons) | SO2 Emission Rate (Tons/total MMBtu) | NOx Emission Rate (Tons/total MMBtu) | CO2 Emission Rate (Tons/total MMBtu) | Heat Rate (MMBtu/MWh) | SO2 Emission Rate (Tons/MWh) | NOx Emission Rate (Tons/MWh) | CO2 Emission Rate (Tons/total MWh) | RESOLVE Type | Technology | Plant Name | Nameplate Capacity (MW) | AUG NQC (online 2020) | SEP NQC (online 2020) | Capacity Factor (2018) | Capcity Factor (2018) Quartile* – by Type | CONFIDENTIAL: Heat Rate (2018) (MMBtu/MWh) | Heat Rate (2018) Quartile* – by Type | CONFIDENTIAL: Has Contract past model year | Age in 2035 | Age in 2039 | Age Quartile – by Type | In Local Area | Local Area | Sub Area | Has 2028 LCR Study LEF | 2028 LCR Study Highest Local Effectiveness Factor (%) | LEF Quartile* – All Plants(Highest %=1) | 4-hr Storage able to charge in LCR (MW) | Storage Displacement Potential (High = 4-hr str > plant MW) | DAC Status | If out of DAC, distance to DAC | DAC Rank (4=inDAC to 1=outsideDAC) | NOx Emissions Rate (2018) (lbs/MWh) | CF weighted NOx Rate (CF * NOx Rate) | Nox Emissions Rate Quartile* – All Plants | Ozone Attainment Status (8hr-O3 2015) | PM2.5 Attainment Status (2012 Standard) | Ozone+PM2.5 Rank* | Simple Sum Score of all Criteria | Simple Sum Excluding Age and LEF criteria | Weighting CF & Heat Rate Criteria Combined Equally with DAC, Nox, NAZ Criteria Combined
CHEVCO_6_UNIT 2 | AERA ENERGY LLC. (COALINGA) | 8.5 | 12.5 | PGAE | Pacific Gas & Electric Company | FTUR | NATURAL GAS | ZP26 | 1988-06-03 | Gates | 115 | 50750 | 48672 | 374654 | 747415 | 241128 | 506287 | 0.21961 | 120.0551 | 43723.4723 | 2.9383e-07 | 0.00016063 | 0.0585 | 4.9541 | 1.4557e-06 | 0.00079577 | 0.28982 | CAISO_CHP | Natural Gas Fired Combustion Turbine | Coalinga Cogeneration Facility | 6.8 | 0.85 | 0.86 | 81.71% | 4 |  | 1 |  | 47.6082 | 51.611 | 3 | Yes | Fresno | Coalinga, Panoche 115 kV | No | No Published Factor | 4 | 793 | High | Outside_DAC | 10.6038 | 1 | 1.5915 | 1.3004 | 3 | NA_Extreme | NA_Moderate | 4 | 71.4286 | 65 | 64.5833
TENGEN_2_PL1X2 | Placerita Canyon Cogen | 37.7 |  | SCE | Shadow Wolf Energy, LLC | COMBUSTION TURBINE | NATURAL GAS | SP15 | 1990-03-06 | Sylmar | 230 | 52096 | 295809 | 1322830 | 3632354 | 1628063 | 2004291 | 1.0531 | 575.6884 | 212491.2259 | 2.8992e-07 | 0.00015849 | 0.0585 | 5.5038 | 1.5956e-06 | 0.00087229 | 0.32197 | CAISO_CHP | Natural Gas Fired Combustion Turbine | Berry Placerita Cogen | 42.8 | 37.6 | 37.59 | 78.9% | 4 |  | 2 |  | 45.8521 | 49.8548 | 2 | Yes | BC/Ventura | 0 | No | No Published Factor | 4 | 657 | High | DAC_Adjacent | 3.2817 | 3 | 1.7446 | 1.3764 | 3 | NA_Extreme | NA_Moderate | 4 | 78.5714 | 80 | 79.1667
SYCAMR_2_UNIT 2 | Sycamore Cogeneration Unit 2 | 76 | 90 | SCE | Chevron Power Holdings | FTUR | NATURAL GAS | SP15 | 1987-01-01 | Dexzel | 115 | 50134 | 1368124 | 4611532 | 17059703 | 8675096 | 8384607 | 4.9688 | 2716.3022 | 997985.66 | 2.9126e-07 | 0.00015922 | 0.0585 | 6.3409 | 1.8469e-06 | 0.0010096 | 0.37094 | CAISO_CHP | Natural Gas Fired Combustion Turbine | Sycamore Cogeneration | 300 | 317.41 | 317.99 | 52.06% | 2 |  | 1 |  | 49.0301 | 53.0329 | 3 | Yes | BC/Ventura | 0 | No | No Published Factor | 4 | 657 | High | In_DAC |  | 4 | 2.0192 | 1.0512 | 2 | NA_Extreme | NA_Moderate | 4 | 71.4286 | 65 | 60.4167
UNCHEM_1_UNIT | CONTRA COSTA CARBON PLANT | 19 | 20 | PGAE | Phillips 66 Company | STEAM | COAL | NP15 | 1983-01-01 | Christie | 115 | 50388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | CAISO_CHP | Petroleum Coke | CONTRA COSTA CARBON PLANT | 27.3 | 13.1 | 10.21 | 0% | 1 |  | 3 |  | 53.0329 | 57.0356 | 4 | Yes | Bay Area | Pittsburg | Yes | 24 | 1 | 2220 | High | DAC_Adjacent | 1.63 | 3 | Not Available | Not Available | 2.5 | NA_Marginal | A | 1.25 | 56.25 | 53.75 | 53.125
SMPRIP_1_SMPSON | Ripon Cogeneration Unit 1 | 46.05 | 56.9 | PGAE | AltaGas Ripon Energy Inc. | COMBUSTION TURBINE | NATURAL GAS | NP15 | 1988-04-19 | Ripon | 115 | 50299 | 9868 | 0 | 99585 | 99585 | 0 | 0.02869 | 15.6838 | 5825.6818 | 2.8809e-07 | 0.00015749 | 0.0585 | 10.0917 | 2.9074e-06 | 0.0015894 | 0.59036 | CAISO_CHP | Natural Gas Fired Combustion Turbine | AltaGas Ripon Energy Inc. | 49.5 | 46.05 | 46.05 | 2.276% | 1 |  | 4 |  | 47.7315 | 51.7342 | 3 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | DAC_Adjacent | 0.38097 | 3 | 3.1787 | 0.072339 | 1 | NA_Extreme | NA_Moderate | 4 | 71.4286 | 65 | 64.5833
PLMSSR_6_HISIER | High Sierra Cogeneration Aggregate | 6 | 6 | PGAE | Plumas Sierra REC | RECIPROCATING ENGINE | NATURAL GAS | NP15 | 2010-04-22 | Caribou | 115 | 57977 | 34849 | 70879 | 366892 | 233162 | 133730 | 0.10533 | 485.9127 | 21463.0322 | 2.8708e-07 | 0.0013244 | 0.0585 | 6.6906 | 1.9208e-06 | 0.0088611 | 0.3914 | CAISO_CHP | Natural Gas Internal Combustion Engine | High Sierra Cogeneration Plant | 6 | 0 | 0 | 66.3% | 3 |  | 4 |  | 25.7096 | 29.7123 | 1 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | Outside_DAC | 8229.8474 | 1 | 17.7222 | 11.7504 | 4 | A | A | 1 | 64.2857 | 65 | 68.75
DISCOV_1_CHEVRN | CHEVRON USA (EASTRIDGE) | 48.8 | 56.2 | PGAE | Pacific Gas & Electric Company | FTUR | NATURAL GAS | ZP26 | 1988-06-13 | Columbus | 115 | 52107 | 212906 | 1438083 | 2513076 | 860107 | 1652969 | 0.72872 | 398.366 | 147013.9199 | 2.8997e-07 | 0.00015852 | 0.0585 | 4.0398 | 1.1714e-06 | 0.00064039 | 0.23633 | CAISO_CHP | Natural Gas Fired Combustion Turbine | Kern River Eastridge Cogen | 48.8 | 2.58 | 2.34 | 49.8% | 2 |  | 3 |  | 47.5808 | 51.5836 | 2 | Yes | Kern | South Kern PP, Kern Oil | No | No Published Factor | 4 | 270 | High | In_DAC |  | 4 | 1.2808 | 0.63787 | 2 | NA_Extreme | NA_Moderate | 4 | 75 | 75 | 72.9167
SYCAMR_2_UNIT 1 | Sycamore Cogeneration Unit 1 | 74 | 90 | SCE | Chevron Power Holdings | FTUR | NATURAL GAS | SP15 | 1987-01-01 | Dexzel | 115 | 50134 | 1368124 | 4611532 | 17059703 | 8675096 | 8384607 | 4.9688 | 2716.3022 | 997985.66 | 2.9126e-07 | 0.00015922 | 0.0585 | 6.3409 | 1.8469e-06 | 0.0010096 | 0.37094 | CAISO_CHP | Natural Gas Fired Combustion Turbine | Sycamore Cogeneration | 300 | 317.41 | 317.99 | 52.06% | 2 |  | 1 |  | 49.0301 | 53.0329 | 3 | Yes | BC/Ventura | 0 | No | No Published Factor | 4 | 657 | High | In_DAC |  | 4 | 2.0192 | 1.0512 | 2 | NA_Extreme | NA_Moderate | 4 | 71.4286 | 65 | 60.4167
SUNSET_2_UNITS | MIDWAY SUNSET COGENERATION PLANT | 248 | 291 | PGAE | Midway Sunset Cogeneration Company | FTUR | NATURAL GAS | ZP26 | 1989-12-18 | Midway | 230 | 52169 | 850069 | 5237207 | 10249621 | 3703111 | 6546510 | 2.9718 | 1624.6107 | 599598.6436 | 2.8995e-07 | 0.0001585 | 0.0585 | 4.3562 | 1.2631e-06 | 0.00069048 | 0.25484 | CAISO_CHP | Natural Gas Fired Combustion Turbine | Midway Sunset Cogen | 234 | 229.5 | 232.23 | 41.47% | 1 |  | 1 |  | 46.0658 | 50.0685 | 2 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | DAC_Adjacent | 0.0043398 | 3 | 1.381 | 0.57269 | 1 | NA_Extreme | NA_Moderate | 4 | 57.1429 | 50 | 45.8333
CHEVCD_6_UNIT | CHEVRON USA (TAFT/CADET) | 11.5 | 11.5 | PGAE | Pacific Gas & Electric Company | COMBUSTION TURBINE | NATURAL GAS | ZP26 | 1982-07-26 | Taft | 115 | 52085 | 77245 | 748640 | 1197853 | 327341 | 870512 | 0.34957 | 191.0972 | 70073.9114 | 2.9183e-07 | 0.00015953 | 0.0585 | 4.2377 | 1.2367e-06 | 0.00067605 | 0.2479 | CAISO_CHP | Natural Gas Fired Combustion Turbine | Taft 26C Cogen | 12.4 | 1.02 | 1.09 | 71.11% | 3 |  | 3 |  | 53.4685 | 57.4712 | 4 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | DAC_Adjacent | 1.6151 | 3 | 1.3521 | 0.96151 | 2 | NA_Extreme | NA_Moderate | 4 | 82.1429 | 75 | 75
CHEVCO_6_UNIT 1 | CHEVRON USA (COALINGA) | 16.5 | 19 | PGAE | Pacific Gas & Electric Company | COMBUSTION TURBINE | NATURAL GAS | ZP26 | 1986-01-17 | Cantua | 115 | 52083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | CAISO_CHP | Natural Gas Fired Combustion Turbine | CHEVRON USA (COALINGA) | 6.8 | 2.09 | 1.94 | 0% | 1 |  | 4 |  | 49.9863 | 53.989 | 4 | Yes | Fresno | Coalinga, Panoche 115 kV | No | No Published Factor | 4 | 793 | High | Outside_DAC | 11.8172 | 1 | Not Available | Not Available | 2.5 | NA_Extreme | NA_Moderate | 4 | 73.2143 | 62.5 | 62.5
ARCOGN_2_UNITS | WATSON COGENERATION | 305 | 416.6 | SCE | Watson Cogeneration Company | COMBINED CYCLE | NATURAL GAS | SP15 | 1987-12-04 | Hinson | 230 | 50216 | 2988696 | 11797592 | 35475840 | 16447471 | 19028369 | 64.1622 | 4176.9838 | 1736126.8332 | 1.8086e-06 | 0.00011774 | 0.048938 | 5.5032 | 9.9532e-06 | 0.00064796 | 0.26932 | CAISO_CHP | Natural Gas Fired Combined Cycle | Watson Cogeneration | 405 | 259.89 | 256.73 | 84.24% | 4 |  | 2 |  | 48.1068 | 52.1096 | 3 | Yes | LA Basin | Western | Yes | 23 | 2 | 1141 | High | In_DAC |  | 4 | 1.2959 | 1.0917 | 3 | NA_Extreme | NA_Moderate | 4 | 78.5714 | 85 | 83.3333
OROVIL_6_UNIT | Oroville Cogeneration, LP | 7.5 | 9.8 | PGAE | Oroville Cogeneration, L.P. | RECIPROCATING ENGINE | NATURAL GAS | NP15 | 1989-12-18 | Wyandotte | 115 | 54477 | 156 | 1219 | 2614 | 795 | 1819 | 0.0007614 | 3.5126 | 152.9179 | 2.9128e-07 | 0.0013438 | 0.0585 | 5.0962 | 1.4844e-06 | 0.006848 | 0.29812 | CAISO_CHP | Natural Gas Internal Combustion Engine | Oroville Cogeneration LP | 7.7 | 7.5 | 7.5 | 0.2313% | 1 |  | 4 |  | 46.0658 | 50.0685 | 2 | Yes | Sierra | Drum-Rio Oso | Yes | 6 | 4 | 75 | High | DAC_Adjacent | 1.0652 | 3 | 13.696 | 0.031676 | 1 | NA_Marginal | A | 1.25 | 58.0357 | 51.25 | 53.125
GRNLF2_1_UNIT | GREENLEAF II COGEN | 49.2 | 63.8 | PGAE | Greenleaf Energy Unit 2 LLC | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2020-06-01 | Pease | 115 | 10349 | 226368 | 202800 | 2198215 | 1747551 | 450664 | 0.111 | 15.553 | 128594.68 | 5.0496e-08 | 7.0753e-06 | 0.0585 | 7.72 | 3.8982e-07 | 5.4621e-05 | 0.45161 | CAISO_CHP | Natural Gas Fired Combustion Turbine | Greenleaf 2 Power Plant | 49.5 | 49.2 | 49.2 | 52.2% | 2 |  | 3 |  | 15.5918 | 19.5945 | 1 | Yes | Sierra | Pease, Drum-Rio Oso | Yes | 17 | 4 | 75 | High | DAC_Adjacent | 1.2135 | 3 | 0.10924 | 0.057029 | 1 | A | A | 1 | 53.5714 | 50 | 52.0833
SALIRV_2_UNIT | Salinas River Cogeneration | 39 | 57 | PGAE | Chevron Power Holdings, Inc | FTUR | NATURAL GAS | NP15 | 1991-10-11 | Coburn | 230 | 50865 | 301448 | 913626 | 3998386 | 2133843 | 1864543 | 1.234 | 20.526 | 233903.9485 | 3.0862e-07 | 5.1336e-06 | 0.0585 | 7.0786 | 2.1846e-06 | 3.6339e-05 | 0.4141 | CAISO_CHP | Natural Gas Fired Combustion Turbine | Salinas River Cogeneration | 38.9 | 29.35 | 22.68 | 88.46% | 4 |  | 2 |  | 44.2521 | 48.2548 | 2 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | Outside_DAC | 35.6025 | 1 | 0.072677 | 0.064292 | 1 | A | A | 1 | 53.5714 | 45 | 50
VEDDER_1_SEKERN | TEXACO EXPLORATION & PROD (SE KERN RIVER | 34.47 | 39.7 | PGAE | Pacific Gas & Electric Company | FTUR | NATURAL GAS | ZP26 | 1989-01-31 | Columbus | 115 | 50751 | 121221 | 558058 | 1451453 | 630778 | 820675 | 0.42072 | 229.9938 | 84909.4079 | 2.8986e-07 | 0.00015846 | 0.0585 | 5.2035 | 1.5083e-06 | 0.00082454 | 0.3044 | CAISO_CHP | Natural Gas Fired Combustion Turbine | Southeast Kern River Cogen | 30.8 | 2.19 | 0.73 | 44.93% | 1 |  | 2 |  | 46.9452 | 50.9479 | 2 | Yes | Kern | South Kern PP, Kern Oil | No | No Published Factor | 4 | 270 | High | In_DAC |  | 4 | 1.6491 | 0.74091 | 2 | NA_Extreme | NA_Moderate | 4 | 67.8571 | 65 | 60.4167
SRINTL_6_UNIT | SRI INTERNATIONAL | 6.9 | 6.9 | PGAE | Pacific Gas & Electric Company | COMBUSTION TURBINE | NATURAL GAS | NP15 | 1987-03-10 | Monte Vista | 230 | 50537 | 28860 | 153875 | 459974 | 185197 | 274777 | 0.13339 | 72.9183 | 26908.2912 | 2.8999e-07 | 0.00015853 | 0.0585 | 6.4171 | 1.8609e-06 | 0.0010173 | 0.3754 | CAISO_CHP | Natural Gas Fired Combustion Turbine | SRI International Cogen Project | 6 | 0.78 | 0.75 | 54.91% | 2 |  | 1 |  | 48.8438 | 52.8466 | 3 | Yes | Bay Area | 0 | No | No Published Factor | 4 | 2220 | High | DAC_Adjacent | 1.49 | 3 | 2.0346 | 1.1172 | 3 | NA_Marginal | A | 1.25 | 61.6071 | 51.25 | 48.9583
UNVRSY_1_UNIT 1 | Berry Cogen 38 - Unit 1 | 38 | 38 | PGAE | Berry Petroleum Company | FTUR | NATURAL GAS | ZP26 | 1986-01-01 | Taft | 115 | 50170 | 293027 | 1660686 | 3889501 | 1482708 | 2406793 | 1.1278 | 616.5114 | 227534.2204 | 2.8995e-07 | 0.00015851 | 0.0585 | 5.06 | 1.4671e-06 | 0.00080204 | 0.29601 | CAISO_CHP | Natural Gas Fired Combustion Turbine | Berry Cogen | 38.7 | 34.03 | 34.36 | 86.44% | 4 |  | 2 |  | 50.0301 | 54.0329 | 4 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | DAC_Adjacent | 2.5234 | 3 | 1.6041 | 1.3865 | 4 | NA_Extreme | NA_Moderate | 4 | 89.2857 | 85 | 83.3333
CHEVCY_1_UNIT | CHEVRON USA (CYMRIC) | 24.3 | 24.3 | PGAE | Pacific Gas & Electric Company | COMBUSTION TURBINE | NATURAL GAS | ZP26 | 1982-10-15 | Temblor | 115 | 52081 | 44634 | 382541 | 654763 | 188250 | 466513 | 0.19071 | 104.2537 | 38303.3682 | 2.9126e-07 | 0.00015922 | 0.0585 | 4.2176 | 1.2284e-06 | 0.00067155 | 0.24673 | CAISO_CHP | Natural Gas Fired Combustion Turbine | Cymric 31X Cogen | 6.8 | 2.91 | 2.85 | 74.93% | 3 |  | 4 |  | 53.2466 | 57.2493 | 4 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | In_DAC |  | 4 | 1.3431 | 1.0064 | 2 | NA_Extreme | NA_Moderate | 4 | 89.2857 | 85 | 85.4167
CROKET_7_UNIT | CROCKETT COGEN | 240 | 240 | PGAE | Pacific Gas & Electric Company | COMBINED CYCLE | NATURAL GAS | NP15 | 1995-12-20 | Christie | 115 | 55084 | 1372884 | 2369377 | 12598202 | 8441402 | 4156800 | 3.6273 | 1692.7242 | 736989.6732 | 2.8792e-07 | 0.00013436 | 0.0585 | 6.1487 | 1.7703e-06 | 0.00082615 | 0.35969 | CAISO_CHP | Natural Gas Fired Combined Cycle | Crockett Cogen Project | 247.4 | 211.49 | 165.57 | 63.35% | 3 |  | 3 |  | 40.0575 | 44.0603 | 1 | Yes | Bay Area | Pittsburg | No | No Published Factor | 4 | 2220 | High | DAC_Adjacent | 0.6894 | 3 | 1.6523 | 1.0467 | 2 | NA_Marginal | A | 1.25 | 61.6071 | 61.25 | 63.5417
CHINO_6_CIMGEN | Chino Co-Generation | 26 | 31.6 | SCE | O.L.S. Energy - Chino | COMBINED CYCLE | NATURAL GAS | SP15 | 2018-06-27 | Chino | 230 | 50850 | 24709 | 34075 | 247531 | 180717 | 66814 | 0.071818 | 33.5152 | 14480.4624 | 2.9014e-07 | 0.0001354 | 0.0585 | 7.3138 | 2.122e-06 | 0.00099027 | 0.42786 | CAISO_CHP | Natural Gas Fired Combined Cycle | OLS Energy Chino | 30.8 | 26 | 26 | 9.158% | 1 |  | 3 |  | 17.5233 | 21.526 | 1 | Yes | LA Basin | Eastern | No | No Published Factor | 4 | 1141 | High | DAC_Adjacent | 1.5321 | 3 | 1.9805 | 0.18138 | 1 | NA_Extreme | NA_Moderate | 4 | 60.7143 | 60 | 58.3333
TANHIL_6_SOLART | Berry Cogen 18 | 17 | 17 | PGAE | Berry Petroleum Company | FTUR | NATURAL GAS | ZP26 | 1986-01-01 | Taft | 115 | 50170 | 293027 | 1660686 | 3889501 | 1482708 | 2406793 | 1.1278 | 616.5114 | 227534.2204 | 2.8995e-07 | 0.00015851 | 0.0585 | 5.06 | 1.4671e-06 | 0.00080204 | 0.29601 | CAISO_CHP | Natural Gas Fired Combustion Turbine | Berry Cogen | 38.7 | 34.03 | 34.36 | 86.44% | 4 |  | 2 |  | 50.0301 | 54.0329 | 4 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | DAC_Adjacent | 2.5234 | 3 | 1.6041 | 1.3865 | 4 | NA_Extreme | NA_Moderate | 4 | 89.2857 | 85 | 83.3333
STOILS_1_UNITS | Chevron Richmond Refinery | 56.2 |  | PGAE | Chevron Products Company | COMBINED CYCLE | NATURAL GAS | NP15 | 1992-08-31 | Richmond R | 115 | 52109 | 868496 | 6216691 | 11533622 | 3762757 | 7770865 | 3.3675 | 1237.2318 | 525119.3034 | 2.9197e-07 | 0.00010727 | 0.045529 | 4.3325 | 1.265e-06 | 0.00046475 | 0.19726 | CAISO_CHP | Natural Gas Fired Combined Cycle | Richmond Cogen | 155.6 | 5.14 | 0.07 | 63.72% | 3 |  | 1 |  | 43.3616 | 47.3644 | 2 | Yes | Bay Area | Pittsburg | Yes | 25 | 1 | 2220 | High | DAC_Adjacent | 0.78227 | 3 | 0.92951 | 0.59225 | 1 | NA_Marginal | A | 1.25 | 43.75 | 46.25 | 46.875
SNCLRA_2_UNIT1 | New Indy Oxnard | 27.8 | 29 | SCE | New-Indy Oxnard LLC | FTUR | NATURAL GAS | SP15 | 2016-04-15 | Santa Clara | 230 | 57585 | 189038 | 696758 | 2129815 | 1041131 | 1088684 | 0.62811 | 343.3676 | 124593.3079 | 2.9491e-07 | 0.00016122 | 0.0585 | 5.5075 | 1.6242e-06 | 0.00088792 | 0.32219 | CAISO_CHP | Natural Gas Fired Combustion Turbine | Oxnard Paper Mill | 29 | 15.63 | 15.94 | 74.41% | 3 |  | 4 |  | 19.7233 | 23.726 | 1 | Yes | BC/Ventura | S.Clara, Moorpark | No | No Published Factor | 4 | 657 | High | In_DAC |  | 4 | 1.7758 | 1.3214 | 3 | NA_Serious | A | 2 | 75 | 80 | 81.25
DEXZEL_1_UNIT | Western Power and Steam Cogeneration | 20 | 36.8 | PGAE | Western Power and Steam II LLC | COMBUSTION TURBINE | NATURAL GAS | ZP26 | 1989-11-30 | Kern Oil | 115 | 54410 | 148922 | 227303 | 1750887 | 1222274 | 528613 | 0.5076 | 277.4903 | 102426.1746 | 2.8991e-07 | 0.00015849 | 0.0585 | 8.2075 | 2.3795e-06 | 0.0013008 | 0.48013 | CAISO_CHP | Natural Gas Fired Combustion Turbine | Western Power & Steam Inc | 27.7 | 17.78 | 17.43 | 61.37% | 2 |  | 4 |  | 46.1151 | 50.1178 | 2 | Yes | Kern | South Kern PP, Kern Oil | No | No Published Factor | 4 | 270 | High | In_DAC |  | 4 | 2.6015 | 1.5966 | 4 | NA_Extreme | NA_Moderate | 4 | 85.7143 | 90 | 87.5
SYCAMR_2_UNIT 3 | Sycamore Cogeneration Unit 3 | 74 | 90 | SCE | Chevron Power Holdings | FTUR | NATURAL GAS | SP15 | 1987-01-01 | Dexzel | 115 | 50134 | 1368124 | 4611532 | 17059703 | 8675096 | 8384607 | 4.9688 | 2716.3022 | 997985.66 | 2.9126e-07 | 0.00015922 | 0.0585 | 6.3409 | 1.8469e-06 | 0.0010096 | 0.37094 | CAISO_CHP | Natural Gas Fired Combustion Turbine | Sycamore Cogeneration | 300 | 317.41 | 317.99 | 52.06% | 2 |  | 1 |  | 49.0301 | 53.0329 | 3 | Yes | BC/Ventura | 0 | No | No Published Factor | 4 | 657 | High | In_DAC |  | 4 | 2.0192 | 1.0512 | 2 | NA_Extreme | NA_Moderate | 4 | 71.4286 | 65 | 60.4167
CSCCOG_1_UNIT 1 | SANTA CLARA CO-GEN | 7 | 7 | PGAE | City of Santa Clara DBA Silicon Valley Power (MSS Agreement - S14) | FTUR | NATURAL GAS | NP15 | 1981-01-01 | FMC | 115 | 7232 | 45419 | 61225 | 737492 | 533409 | 204083 | 0.21418 | 117.0848 | 43142.9809 | 2.9042e-07 | 0.00015876 | 0.0585 | 11.7442 | 3.4107e-06 | 0.0018645 | 0.68703 | CAISO_CHP | Natural Gas Fired Combustion Turbine | Santa Clara Cogen | 7.8 | 6 | 6 | 66.47% | 3 |  | 4 |  | 55.0329 | 59.0356 | 4 | Yes | Bay Area | San Jose, South Bay-Moss Landing | No | No Published Factor | 4 | 2220 | High | In_DAC |  | 4 | 3.729 | 2.4788 | 4 | NA_Marginal | A | 1.25 | 86.6071 | 81.25 | 82.2917
TXMCKT_6_UNIT | McKittrick Cogen | 11.2 | 11.2 | PGAE | Chevron USA Inc | FTUR | NATURAL GAS | ZP26 | 1994-10-01 | Temblor | 115 | 52076 | 79176 | 10535 | 982409 | 947296 | 35113 | 0.28476 | 155.6667 | 57470.5254 | 2.8985e-07 | 0.00015845 | 0.0585 | 11.9644 | 3.468e-06 | 0.0018958 | 0.69991 | CAISO_CHP | Natural Gas Fired Combustion Turbine | McKittrick Cogen | 12 | 2.08 | 2.13 | 75.32% | 4 |  | 4 |  | 41.2767 | 45.2795 | 2 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | In_DAC |  | 4 | 3.7916 | 2.8558 | 4 | NA_Extreme | NA_Moderate | 4 | 92.8571 | 100 | 100
SNCLRA_6_PROCGN | Procter and Gamble Oxnard 2 | 47.9 | 49.5 | SCE | The Procter & Gamble Paper Products Company | FTUR | NATURAL GAS | SP15 | 1998-11-17 | Santa Clara | 230 | 50464 | 557802 | 807253 | 5547498 | 3932998 | 1614500 | 1.6205 | 885.8709 | 324526.368 | 2.9211e-07 | 0.00015969 | 0.0585 | 7.0509 | 2.0597e-06 | 0.0011259 | 0.41247 | CAISO_CHP | Natural Gas Fired Combustion Turbine | Oxnard | 68.7 | 45.47 | 45.25 | 92.69% | 4 |  | 1 |  | 37.1452 | 41.1479 | 1 | Yes | BC/Ventura | S.Clara, Moorpark | No | No Published Factor | 4 | 657 | High | In_DAC |  | 4 | 2.2519 | 2.0872 | 4 | NA_Serious | A | 2 | 71.4286 | 75 | 72.9167
SNCLRA_6_OXGEN | OXGEN | 47.7 | 47.7 | SCE | EF Oxnard LLC | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2020-06-01 | Santa Clara | 230 | 10776 | 157062 | 86544 | 1449560 | 1252870 | 196690 | 0.42184 | 230.6055 | 84798.6681 | 2.9101e-07 | 0.00015909 | 0.0585 | 7.9769 | 2.3214e-06 | 0.001269 | 0.46665 | CAISO_CHP | Natural Gas Fired Combustion Turbine | E F Oxnard Energy Facility | 48.5 | 48.13 | 48.13 | 36.97% | 1 |  | 3 |  | 15.5918 | 19.5945 | 1 | Yes | BC/Ventura | S.Clara, Moorpark | No | No Published Factor | 4 | 657 | High | In_DAC |  | 4 | 2.538 | 0.93826 | 2 | NA_Serious | A | 2 | 60.7143 | 60 | 58.3333
SYCAMR_2_UNIT 4 | Sycamore Cogeneration Unit 4 | 76 | 90 | SCE | Chevron Power Holdings | FTUR | NATURAL GAS | SP15 | 1987-01-01 | Dexzel | 115 | 50134 | 1368124 | 4611532 | 17059703 | 8675096 | 8384607 | 4.9688 | 2716.3022 | 997985.66 | 2.9126e-07 | 0.00015922 | 0.0585 | 6.3409 | 1.8469e-06 | 0.0010096 | 0.37094 | CAISO_CHP | Natural Gas Fired Combustion Turbine | Sycamore Cogeneration | 300 | 317.41 | 317.99 | 52.06% | 2 |  | 1 |  | 49.0301 | 53.0329 | 3 | Yes | BC/Ventura | 0 | No | No Published Factor | 4 | 657 | High | In_DAC |  | 4 | 2.0192 | 1.0512 | 2 | NA_Extreme | NA_Moderate | 4 | 71.4286 | 65 | 60.4167
SAMPSN_6_KELCO1 | KELCO QUALIFYING FACILITY | 25 | 28 | SCE | CP Kelco U.S., Inc. | COMBUSTION TURBINE | OTHER | SP15 | 2014-03-05 | Silvergate | 230 | 52147 | 81590 | 346189 | 1012885 | 454517 | 558368 | 0.29801 | 162.9099 | 59253.3589 | 2.9421e-07 | 0.00016084 | 0.0585 | 5.5707 | 1.639e-06 | 0.00089598 | 0.32589 | CAISO_CHP | Natural Gas Fired Combustion Turbine | C P Kelco San Diego Plant | 29.2 | 0.85 | 1.74 | 31.9% | 1 |  | 2 |  | 21.8384 | 25.8411 | 1 | Yes | SD-IV | San Diego | Yes | 22 | 3 | 920 | High | In_DAC |  | 4 | 1.792 | 0.57158 | 1 | NA_Moderate | A | 1.5 | 48.2143 | 47.5 | 45.8333
SEARLS_7_ARGUS | Argus Cogeneration | 19 | 62.5 | SCE | Searles Valley Minerals Inc. |  | OTHER | SP15 | 2013-11-15 | Inyokern | 115 | 10684 | 295787 | 12407613 | 15313999 | 1372865 | 13941134 | 360.1926 | 914.2492 | 1542119.9368 | 2.352e-05 | 5.97e-05 | 0.1007 | 4.6414 | 0.00010917 | 0.00027709 | 0.46739 | CAISO_CHP | Conventional Steam Coal | Argus Cogen Plant | 62.5 | 4.01 | 3.96 | 54.03% | 2 |  | 3 |  | 22.1397 | 26.1425 | 1 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | Outside_DAC | 27.1787 | 1 | 0.55418 | 0.2994 | 1 | A | A | 1 | 46.4286 | 40 | 43.75
CHEVMN_2_UNITS | CHEVRON U.S.A. UNITS 1 & 2 AGGREGATE | 124.87 | 170.7 | SCE | Chevron U.S.A. Inc. (Chevron CIC) |  | OTHER | SP15 | 1987-12-29 | Chevmain | 230 | 10213 | 1265325 | 344636 | 15508088 | 14359306 | 1148782 | 4.5612 | 1984.9378 | 852984.1261 | 2.9411e-07 | 0.00012799 | 0.055003 | 11.3483 | 3.3377e-06 | 0.0014525 | 0.62419 | CAISO_CHP | Natural Gas Fired Combined Cycle | El Segundo Cogen | 180.1 | 7.54 | 9.78 | 80.2% | 4 |  | 2 |  | 48.0384 | 52.0411 | 3 | Yes | LA Basin | Western, El Nido | No | No Published Factor | 4 | 1141 | High | In_DAC |  | 4 | 2.905 | 2.3299 | 4 | NA_Extreme | NA_Moderate | 4 | 89.2857 | 90 | 87.5
HOLGAT_1_BORAX | U.S. Borax, Unit 1 | 48.2 | 48.2 | SCE | U.S. Borax Inc. |  | OTHER | SP15 | 1984-06-01 | Kramer | 230 | 50115 | 282302 | 1732330 | 3742979 | 1401992 | 2340987 | 1.0827 | 591.8499 | 218962.7432 | 2.8925e-07 | 0.00015812 | 0.0585 | 4.9663 | 1.4365e-06 | 0.00078528 | 0.29053 | CAISO_CHP | Natural Gas Fired Combustion Turbine | US Borax | 48.2 | 12.56 | 11.63 | 66.86% | 3 |  | 2 |  | 51.6164 | 55.6192 | 4 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | DAC_Adjacent | 0.35003 | 3 | 1.5706 | 1.0501 | 2 | NA_Moderate | A | 1.5 | 69.6429 | 57.5 | 58.3333

## LCR_Battery_Info
2022-23 TPP Appendix J
| Area/Sub-area | Pmax MW | Energy MWh | Max. # of discharge hours | Max. MW of 4 hour battery (1 for 1 MW replacement) | Replacing mostly |  |  |  | Max. 4-hr storage | Replacing Gas? (per 2032 study) | Ozone Attainment Status | Ozone Score | PM2.5 Attainment Status | PM2.5 Score
| Humboldt | 19 | 76 | 11 | 19 | gas |  | Humboldt | Humboldt | 19 | Yes
North Coast/North Bay Overall |  | 410 | 3101 | 12 | 300 | geothermal |  | North Coast/North Bay Overall | North Coast/North Bay Overall | 300 | No | NA_Extreme | 2 | NA_Moderate | 2
| Eagle Rock (Sub) | 75 | 485 | 10 | 25 | geothermal |  | Sierra | Sierra | 75 | No | NA_Severe 15 | 1.75 | A | 0.5
| Fulton (Sub) | 265 | 1550 | 9 | 175 | geothermal |  | Stockton | Stockton | 545 | Yes | NA_Serious | 1.5
Sierra | [7 empty] | Bay Area | Bay Area | 2220 | Yes | NA_Moderate | 1
| Placer | 96 | 477 | 10 | 75 | hydro |  | Fresno | Fresno | 793 | No | NA_Marginal | 0.75
Stockton | [7 empty] | Kern | Kern | 270 | Yes | A | 0.5
| Telsa-Belloa | 546 | 4111 | 16 | 545 | gas |  | Big Creek-Ventura | BC/Ventura | 657 | Yes
Greater Bay Overall |  | 2970 | 15039 | 9 | 2220 | gas |  | LA Basin | LA Basin | 1141 | Yes
| Llagas | 80 | 556 | 10 | 18 | gas |  | San Diego-IV | SD-IV | 920 | Yes
| San Jose | 850 | 2143 | 15 | 536 | gas
| South Bay-Moss Landing | 1010 | 5641 | 19 | 965 | gas
| Oakland |  |  |  |  | distillate | limit reached
Greater Fresno Overall |  | 1223 | 5965 | 10 | 793 | hydro
| Panoche | 120 | 971 | 12 | 53 | gas
| Herndon | 450 | 2531 | 9 | 260 | hydro
| Borden | [5 empty] | Need eliminated
| Hanford | 62 | 433 | 10 | 38 | gas
Coalinga
| Reedley | 85 | 136 | 18 | 34 | none
Kern Overall
| Westpark | 45 | 223 | 8 | 20 | gas
Kern 70 kV
Kern Tevis
| Kern Oil | 130 | 632 | 9 | 100 | gas
| South Kern PP | 323 | 2017 | 10 | 150 | gas
Big Creek/Ventura |  | 743 | 3445 | 19 | 657 | gas
| Vestal | 181 | 851 | 18 | 152 | hydro
LA Basin Overall |  | 2881 | 21215 | 13 | 1141 | gas
| Eastern | 838 | 68232 | 12 | 240 | gas
| Western | 2067 | 13784 | 12 | 1141 | gas
| El Nido | 269 | 2001 | 11 | 68 | gas
San Diego/Imperial Valley Overall |  | 1585 | 8564 | 9 | 920 | gas
| San Diego | 1585 | 8564 | 9 | 920 | gas
| Border | 37 | 200 | 8 | 19 | gas