## README
Mapping criteria for selecting natural gas generators to model as not retained in the 2024-2025 TPP |  |  | Date: 02-15-24
Summary | This workbook contains the list of gas units the CAISO should model as not retained in the 2024-2025 TPP base case and high gas retirement sensitivity portfolios. This work also includes information utilized in the 2024-2025 TPP busbar mapping process to identify which gas resources to model as not retained.
Purpose | The IRP portfolios only contain system level MW amount information on how much gas is not retained; unit specific information is not modeled. Because the TPP studies require modeling of specific units and locations, CPUC staff will share the specific list of units to model as offline with CAISO. In order to specify in the transmitted portfolios which units should be assumed to not be retained for transmission planning purposes, CPUC staff will consider the following metrics and criteria factors discussed below. These factors will be used to create a scoring system to rank which units should be selected to be modeled as not retained.
Retirement of Once Through Cooling Plants | The planned retirement of the Once Through Cooling (OTC) plants are assumed in both the 24-25 TPP base case and High Gas Retirement Sensitivity. Those plants (~3.7 GW of capacity) are omitted from this analysis and these list of unit selection, but their retirements are still included in the portfolio.
Selection Results | The two tabs "CCGT_and_Peakers” and “CHPs” contain lists of CAISO identified plants by category and all the data/analysis that went into the scoring criteria and selection. The first columns in each tab identify if the generator is to be model as offline in the 2034 or 2039 model years for both the base case and high gas retirement sensitivity.
Selection Criteria Factors | IRP staff utilized the six factors below in the selection criteria to identify which gas units to model as not retained. Initially, staff also included Capacity Factor as a stand alone criteria factor, but following stakeholder feedback have excluded it as a direct factor. The factors are divided into three categories: 1) Environmental and Community Impact Factors, 2) Performance Related Factors, and 3) Local Reliability Factors.
Environmental and Community Impact Factors | Proximity to Disadvantaged Communities | Criteria will prioritize not retaining resources located within a disadvantaged community (DAC). Resources within DACs receive the highest score of 4, those within 5 miles receive a score of 3, those between 5 and 10 miles away receive a score of 2, and those beyond 10 miles from a DAC receive a score of 1.
| CF weighted NOx Emission Rate | Criteria will prioritize not retaining resources with higher NOx emission rates weighted by their capacity factors. Resources will be sorted into quartiles by plant type (i.e. CCGTs will be binned only amongst other CCGTs and likewise for Peakers) based on weighted NOx emission rates and given a score between 1 and 4. Resources with the highest emission rates will be given the highest score of 4. These quartile calculations will be done across both CCGTs and Peakers. Emission rates calculated based on publicly available EIA emissions data (2).
| Air Quality Non-attainment Zone location | Criteria will prioritize not retaining resources located within Ozone and PM2.5 EPA Non-Attainment Areas (NAAs). A table in the tab “LCR_Battery_Info” shows the scoring breakdown between 1 and 4 based on the NAA status (5) with a score of 4 going to resources located within the highest non-attainment zones for both Ozone and PM2.5.
Performance Related Factors | Heat Rate | Criteria will prioritize not retaining resources with higher heat rates. Resources will be sorted into quartiles based on their heat rates by plant type (i.e. CCGTs will be binned only amongst other CCGTs and likewise for Peakers) and will be given a score between 1 and 4 with 4 being the highest quartile. Heat rates are derived from confidential internal CPUC IRP data (3) not included in this workbook.
| Age | Criteria will prioritize not retaining older resources. Resources will be sorted into quartiles based on their age by plant type and will be given a score between 1 and 4 with 4 being the highest quartile. Age is based on CAISO's master generating list (1) info on commercial online dates.
Local Reliability Factors | 2028 LCR Studies Local Effectiveness Factor (LEF) | Criteria will prioritize not retaining resources with low or no CAISO local area Effectiveness Factor percentages. Resources will be sorted into quartiles based on LEF percentages and given a score between 1 and 3, with highest quartile receiving a 1, the middle two quartile receiving a 2, and the lowest quartile receiving a 3. Resources with no LEF percentage will be given the highest score of 4. This ranking will be done across both CCGTs and Peakers; all resources will be compared together.
Criteria Scoring | As noted above, all criteria are scaled on a score between 1 and 4 with higher scores being more likely selected to be modeled as not retained. |  |  | `
Some data are not available for all identified resources. In these cases, the resource is given a default score in the middle of distribution, offset to make it easily noted that data is missing (e.g. resources with missing heat rates are given a score of 2.5).
Resources Included | CPUC IRP staff have identified 136 CCGT, Peakers, and Reciprocating Engine resources totaling ~25 GW NDC in the CAISO master generating list and 37 CHPs totaling ~1.96 GW.
The OTC resources have been excluded since those are already modeled for retirement. Additionally, several smaller resources in the CAISO master generating list, totaling less than 240 MW, are excluded because CPUC staff do not have data on the resources.
Separation of CHPs from Gas Resources | The IRP portfolios have separate retirement assumptions for CHPs, which are phased out between 2030 and 2040 as a default input assumption to the RESOLVE model. Because of that this workbook has a separate tab for the identified CHP resources.
Selection Criteria Scoring | The scoring system implemented weighs the six factors by their categories as follows: 1) The three Environmental and Community Impact Factors combined contribute 50% of the score. 2) The two Performance Related Factors combined contribute 25% of the total score. 3) The single Local Reliability Factor contibutes 25% of the total score.
Staff implement two additional screens to initially exclude certain plants from being selected. The two screens are: 1) Exclude the plants in the youngest quartile from being selected. 2) Exclude plants in the highest Effectiveness Factor quartile from being selected.
The plants not excldued by the two screens were given scores. Plants were then selected to be modeled as not retained by their score, with higher scoring plants being selected until the MW amount needed to be modeled was reached. When selecting between plants with the same score, staff generally compared Age, LEF, and DAC scores to select. Additionally, to avoid partially retiring a unit to reach the MW amount required, staff compared generators with scores close to the cutoff score for potential inclusion.
| Application to CHPs | Staff used generally the same selection criteria scoring for identifying which CHP units should be modeled as not retained in both the base case and sensitivity portfolio. Since CHP capacity not retained was an input assumption the same amount is retired in both the base case and high gas retirement sensitivity.
The only difference in application of the selectioncriteria arises in the 2039 model year as 1.73 out of the total CHP capacity of 1.96 GW is required to be selected. Thus staff had to select some plants in the youngest and highest LEF quartiles. Staff still prioritize selecting the older and lower effectiveness factor plants of that group.
Data Sources | (1) CAISO's master generating capability list for information including plant names, online dates, and net dependable capacity MWs.
(2) US Energy Information Administration (EIA) data on 2018 emissions and EPA's information on air quality non-attainment zones.
(3) Internal CPUC IRP data on existing generators for information including capacity factors, plant type, nearest busbar mapping substation, and proximity to DACs.
(4) CAISO's 2028 LCR Studies and 2022-2023 TPP for LEF percentages and LCR information.
(5) Environmental Protection Agency Green Book of Nonattainment Areas for Criteria Pollutants.

## CCGT_and_Peakers
|  |  | Note: | Columns highlighted in blue are the score values for the criteria for each resource.
[38 empty] | *Resources with Not Available CF receive a 2.5 |  | *Resources with Not Available data receive a 2.5 | [9 empty] | *Resources with No published LEF receive a 4 | [8 empty] | *Resources with Not Available data receive a 2.5 |  |  |  |  | *Resources with Not Available data receive a 1.75
Selected to be modeled as not retained by portfolio and model year |  |  | CAISO Master Generator List Information | [9 empty] | IRP Modeled Interconnection Point |  | EIA 2018 Emissions Data | [15 empty] | IRP Info | [10 empty] | Age |  |  | Local Need | [7 empty] | DACs and Air Pollution | [11 empty] | Ranking Score (Highest=100)
2034 & 2039 Base Case | 2034 High Gas Ret. Sens. | 2039 High Gas Ret. Sens. | RESOURCE_ID | GEN_UNIT_NAME | NET_DEPENDABLE_CAPACITY (MW) | NAMEPLATE_CAPACITY (MW) | PTO_AREA | OWNER_OR_QF | UNIT_TYPE | ENERGY_SOURCE | ZONE | COD | Substation | Voltage | EIA Code | 2018 Generation (MWh) | 2018 Useful Thermal Output (MMBtu) | 2018 Total Fuel Consumption (MMBtu) | 2018 Fuel Consumption for Electric Generation (MMBtu) | 2018 Fuel Consumption for Useful Thermal Output (MMBtu) | 2018 SO2 Emission (Tons) | 2018 NOx Emission (Tons) | 2018 CO2 Emission (Tons) | SO2 Emission Rate (Tons/total MMBtu) | NOx Emission Rate (Tons/total MMBtu) | CO2 Emission Rate (Tons/total MMBtu) | Heat Rate (MMBtu/MWh) | SO2 Emission Rate (Tons/MWh) | NOx Emission Rate (Tons/MWh) | CO2 Emission Rate (Tons/total MWh) | RESOLVE Type | Technology | Plant Name | Nameplate Capacity (MW) | AUG NQC (online 2020) | SEP NQC (online 2020) | Capacity Factor (2018) | Capcity Factor (2018) Quartile* – by Type | CONFIDENTIAL: Heat Rate (2018) (MMBtu/MWh) | Heat Rate (2018) Quartile* – by Type | CONFIDENTIAL: Has Contract past model year | Age in 2035 | Age in 2039 | Age Quartile – by Type | In Local Area | Local Area | Sub Area | Has 2028 LCR Study LEF | 2028 LCR Study Highest Local Effectiveness Factor (%) | LEF Quartile* – All Plants(Highest %=1) | 4-hr Storage able to charge in LCR (MW) | Storage Displacement Potential (High = 4-hr str > plant MW) | DAC Status | If out of DAC, distance to DAC | DAC Rank (4=inDAC to 1=outsideDAC) | NOx Emissions Rate (2018) (lbs/MWh) | Nox Emissions Rate Quartile* – All Plants | CF weighted NOx Rate (CF * NOx Rate) | Nox Emissions Rate CF weighted Quartile* – All Plants | Nox Emissions Rate CF weighted Quartile* – By Plant Type | Ozone Attainment Status (8hr-O3 2015) | PM2.5 Attainment Status (2012 Standard) | Ozone+PM2.5 Rank (1-4 intergers) | Ozone+PM2.5 Rank* | Heat Rate & Age (.25), LEF (.25), DAC, NOx Emissions weighted by CF,and NAZ Combined (.5) | Exclude (1st Quartile Age, 1st Quartile LEF)
YES | YES | YES | OMAR_2_UNIT 1 | KERN RIVER COGENERATION CO. UNIT 1 | 75 | 85 | SCE | Chevron Power Holdings, INC | FTUR | NATURAL GAS | SP15 | 1985-05-01 | Dexzel | 115 | 10496 | 729451 | 2695012 | 8990991 | 4344417 | 4646574 | 2.6187 | 1431.5752 | 525969.3025 | 2.9126e-07 | 0.00015922 | 0.0585 | 5.9557 | 1.7347e-06 | 0.00094829 | 0.34841 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Kern River Cogeneration | 300 | 297.01 | 302.36 | 27.76% | 4 |  | 4 |  | 50.7014 | 54.7041 | 4 | Yes | BC/Ventura | 0 | No | No Published Factor | 4 | 657 | High | In_DAC |  | 4 | 1.8966 | 4 | 0.52643 | 4 | 4 | NA_Extreme | NA_Moderate | 4 | 4 | 100 | 0
YES | YES | YES | OMAR_2_UNIT 2 | KERN RIVER COGENERATION CO. UNIT 2 | 75 | 85 | SCE | Chevron Power Holdings, INC | FTUR | NATURAL GAS | SP15 | 1985-05-01 | Dexzel | 115 | 10496 | 729451 | 2695012 | 8990991 | 4344417 | 4646574 | 2.6187 | 1431.5752 | 525969.3025 | 2.9126e-07 | 0.00015922 | 0.0585 | 5.9557 | 1.7347e-06 | 0.00094829 | 0.34841 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Kern River Cogeneration | 300 | 297.01 | 302.36 | 27.76% | 4 |  | 4 |  | 50.7014 | 54.7041 | 4 | Yes | BC/Ventura | 0 | No | No Published Factor | 4 | 657 | High | In_DAC |  | 4 | 1.8966 | 4 | 0.52643 | 4 | 4 | NA_Extreme | NA_Moderate | 4 | 4 | 100 | 0
YES | YES | YES | OMAR_2_UNIT 3 | KERN RIVER COGENERATION CO. UNIT 3 | 75 | 85 | SCE | Chevron Power Holdings, INC | FTUR | NATURAL GAS | SP15 | 1985-05-01 | Dexzel | 115 | 10496 | 729451 | 2695012 | 8990991 | 4344417 | 4646574 | 2.6187 | 1431.5752 | 525969.3025 | 2.9126e-07 | 0.00015922 | 0.0585 | 5.9557 | 1.7347e-06 | 0.00094829 | 0.34841 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Kern River Cogeneration | 300 | 297.01 | 302.36 | 27.76% | 4 |  | 4 |  | 50.7014 | 54.7041 | 4 | Yes | BC/Ventura | 0 | No | No Published Factor | 4 | 657 | High | In_DAC |  | 4 | 1.8966 | 4 | 0.52643 | 4 | 4 | NA_Extreme | NA_Moderate | 4 | 4 | 100 | 0
YES | YES | YES | OMAR_2_UNIT 4 | KERN RIVER COGENERATION CO. UNIT 4 | 75 | 85 | SCE | Chevron Power Holdings, INC | FTUR | NATURAL GAS | SP15 | 1985-05-01 | Dexzel | 115 | 10496 | 729451 | 2695012 | 8990991 | 4344417 | 4646574 | 2.6187 | 1431.5752 | 525969.3025 | 2.9126e-07 | 0.00015922 | 0.0585 | 5.9557 | 1.7347e-06 | 0.00094829 | 0.34841 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Kern River Cogeneration | 300 | 297.01 | 302.36 | 27.76% | 4 |  | 4 |  | 50.7014 | 54.7041 | 4 | Yes | BC/Ventura | 0 | No | No Published Factor | 4 | 657 | High | In_DAC |  | 4 | 1.8966 | 4 | 0.52643 | 4 | 4 | NA_Extreme | NA_Moderate | 4 | 4 | 100 | 0
YES | YES | YES | KERNRG_1_UNITS | South Belridge Cogen Facility | 55.2 | 69.6 | PGAE | Aera Energy LLC | COMBUSTION TURBINE | NATURAL GAS | ZP26 | 1985-01-01 | Kernridge | 115 | 50752 | 439356 | 1592489 | 5305134 | 2605999 | 2699135 | 1.5452 | 844.7009 | 310348.1729 | 2.9126e-07 | 0.00015922 | 0.0585 | 5.9314 | 1.7276e-06 | 0.00094442 | 0.34698 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | South Belridge Cogeneration Facility | 94.2 | 0.2 | 0.42 | 53.24% | 4 |  | 3 |  | 51.0301 | 55.0329 | 4 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | In_DAC |  | 4 | 1.8888 | 3 | 1.0057 | 4 | 4 | NA_Extreme | NA_Moderate | 4 | 4 | 96.875 | 0
YES | YES | YES | LODI25_2_UNIT 1 | LODI GAS TURBINE | 25 | 25.4 | PGAE | NCPA (MSS Agreement - S14) | FTUR | NATURAL GAS | NP15 | 1986-01-01 | Lodi | 230 | 7451 | 3492 | 0 | 56217 | 56217 | 0 | 0.016232 | 8.8734 | 3288.6715 | 2.8873e-07 | 0.00015784 | 0.0585 | 16.0988 | 4.6483e-06 | 0.0025411 | 0.94177 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Lodi | 27.4 | 23.8 | 23.8 | 1.455% | 1 |  | 4 |  | 50.0301 | 54.0329 | 4 | Yes | Stockton | Lockeford | No | No Published Factor | 4 | 545 | High | DAC_Adjacent | 2.1101 | 3 | 5.0821 | 4 | 0.073937 | 4 | 4 | NA_Extreme | NA_Moderate | 4 | 4 | 95.8333 | 0
YES | YES | YES | DOUBLC_1_UNITS | DOUBLE "C" LIMITED | 52.23 | 55.3 | PGAE | DOUBLE "C" LIMITED | COMBUSTION TURBINE | NATURAL GAS | ZP26 | 1989-03-14 | Double "C" Co-Gen | 115 | 50493 | 26465 | 0 | 273942 | 273942 | 0 | 0.079022 | 43.1986 | 16025.4951 | 2.8846e-07 | 0.00015769 | 0.0585 | 10.3511 | 2.9859e-06 | 0.0016323 | 0.60554 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Double C Generation Limited Partnership | 49.8 | 49.5 | 50.03 | 6.067% | 3 |  | 2 |  | 46.8301 | 50.8329 | 4 | Yes | Kern | South Kern PP | No | No Published Factor | 4 | 270 | High | In_DAC |  | 4 | 3.2646 | 4 | 0.19805 | 4 | 4 | NA_Extreme | NA_Moderate | 4 | 4 | 93.75 | 0
YES | YES | YES | KERNFT_1_UNITS | KERN FRONT LIMITED | 52.4 | 60 | PGAE | KERN FRONT LIMITED | COMBUSTION TURBINE | NATURAL GAS | ZP26 | 1989-01-07 | Hi-Sierra Co-Gen | 115 | 50494 | 18945 | 0 | 197327 | 197327 | 0 | 0.056921 | 31.117 | 11543.5489 | 2.8846e-07 | 0.00015769 | 0.0585 | 10.4158 | 3.0046e-06 | 0.0016425 | 0.60932 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Kern Front Limited | 49.8 | 48.6 | 49.11 | 4.343% | 3 |  | 2 |  | 47.011 | 51.0137 | 4 | Yes | Kern | South Kern PP | No | No Published Factor | 4 | 270 | High | In_DAC |  | 4 | 3.285 | 4 | 0.14266 | 4 | 4 | NA_Extreme | NA_Moderate | 4 | 4 | 93.75 | 0
YES | YES | YES | PNOCHE_1_PL1X2 | Panoche Peaker | 49.97 |  | PGAE | Wellhead Power Panoche, LLC | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2005-06-14 | Panoche | 230 | 55874 | 11298 | 0 | 183238 | 183238 | 0 | 0.052806 | 28.8673 | 10719.3482 | 2.8818e-07 | 0.00015754 | 0.0585 | 16.2186 | 4.6739e-06 | 0.0025551 | 0.94878 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Panoche Peaker | 49.9 | 49.97 | 49.97 | 2.585% | 2 |  | 4 |  | 30.5671 | 34.5699 | 2 | Yes | Fresno | Herndon, Panoche 115 kV | No | No Published Factor | 4 | 793 | High | In_DAC |  | 4 | 5.1102 | 4 | 0.13208 | 4 | 4 | NA_Extreme | NA_Moderate | 4 | 4 | 93.75 | 0
YES | YES | YES | CENTRY_6_PL1X4 | CENTURY GENERATING PLANT (AGGREGATE) | 41.4 |  | SCE | Colton Power, LP | FTUR | NATURAL GAS | SP15 | 2001-09-17 | Vista (SCE) | 230 | 55934 | 1266 | 0 | 20013 | 20013 | 0 | 0.0058401 | 3.1926 | 1170.7523 | 2.9182e-07 | 0.00015953 | 0.0585 | 15.8081 | 4.613e-06 | 0.0025218 | 0.92476 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Century Generating Facility | 44.8 | 36 | 36 | 0.3226% | 1 |  | 4 |  | 34.3096 | 38.3123 | 3 | Yes | LA Basin | Eastern | No | No Published Factor | 4 | 1141 | High | In_DAC |  | 4 | 5.0436 | 4 | 0.01627 | 3 | 3 | NA_Extreme | NA_Moderate | 4 | 4 | 92.7083 | 0
YES | YES | YES | DREWS_6_PL1X4 | Drews Generating Plant | 41.4 |  | SCE | Colton Power, LP | FTUR | NATURAL GAS | SP15 | 2001-08-14 | Vista (SCE) | 230 | 55935 | 777 | 0 | 16686 | 16686 | 0 | 0.0049029 | 2.6803 | 976.1242 | 2.9383e-07 | 0.00016063 | 0.0585 | 21.4749 | 6.31e-06 | 0.0034495 | 1.2563 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Drews Generating Facility | 44.8 | 36 | 36 | 0.198% | 1 |  | 4 |  | 34.4027 | 38.4055 | 3 | Yes | LA Basin | Eastern | No | No Published Factor | 4 | 1141 | High | In_DAC |  | 4 | 6.899 | 4 | 0.013659 | 3 | 3 | NA_Extreme | NA_Moderate | 4 | 4 | 92.7083 | 0
YES | YES | YES | BDGRCK_1_UNITS | BADGER CREEK LIMITED | 48.08 | 55.3 | PGAE | Badger Creek Limited | COMBUSTION TURBINE | NATURAL GAS | ZP26 | 1991-04-01 | Badger Creek Co-Gen | 115 | 10650 | 7556 | 7823 | 74479 | 57470 | 17009 | 0.022 | 61.559 | 4356.9911 | 2.9539e-07 | 0.00082653 | 0.0585 | 7.6059 | 2.2467e-06 | 0.0062865 | 0.44494 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Badger Creek Limited | 46 | 40.2 | 38.6 | 1.875% | 1 |  | 1 |  | 44.7808 | 48.7836 | 4 | Yes | Kern | South Kern PP | No | No Published Factor | 4 | 270 | High | In_DAC |  | 4 | 12.5729 | 4 | 0.23576 | 4 | 4 | NA_Extreme | NA_Moderate | 4 | 4 | 90.625 | 0
YES | YES | YES | CORONS_6_CLRWTR | Clearwater Power Plant | 28 |  | SCE | City of Riverside (MSSA) | COMBINED CYCLE | NATURAL GAS | SP15 | 2005-02-28 | Mira Loma | 500 | 56356 | 14932 | 10116 | 132745 | 110753 | 21992 | 0.038476 | 17.9557 | 7765.5283 | 2.8985e-07 | 0.00013526 | 0.0585 | 7.4172 | 2.1499e-06 | 0.0010033 | 0.4339 | CAISO_CCGT2 | Natural Gas Fired Combined Cycle | Clearwater Power Plant | 49 | 28 | 28 | 3.479% | 1 |  | 2 |  | 30.8575 | 34.8603 | 3 | Yes | LA Basin | Eastern | No | No Published Factor | 4 | 1141 | High | In_DAC |  | 4 | 2.0066 | 4 | 0.069802 | 4 | 4 | NA_Extreme | NA_Moderate | 4 | 4 | 90.625 | 0
YES | YES | YES | LIVOAK_1_UNIT 1 | LIVE OAK LIMITED | 49.7 | 55.3 | PGAE | Live Oak Limited | COMBUSTION TURBINE | NATURAL GAS | ZP26 | 1991-03-16 | Badger Creek Co-Gen | 115 | 54768 | 22188 | 17000 | 208677 | 170903 | 37774 | 0.062 | 175.099 | 12207.5193 | 2.9711e-07 | 0.00083909 | 0.0585 | 7.7025 | 2.2885e-06 | 0.0064631 | 0.45059 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Live Oak Limited | 46 | 42.5 | 43 | 5.506% | 3 |  | 1 |  | 44.8247 | 48.8274 | 4 | Yes | Kern | South Kern PP, Kern Oil | No | No Published Factor | 4 | 270 | High | In_DAC |  | 4 | 12.9262 | 4 | 0.71175 | 4 | 4 | NA_Extreme | NA_Moderate | 4 | 4 | 90.625 | 0
YES | YES | YES | MKTRCK_1_UNIT 1 | MCKITTRICK LIMITED | 47.72 | 57.9 | PGAE | McKittrick Limited | COMBUSTION TURBINE | NATURAL GAS | ZP26 | 1991-10-16 | Temblor | 115 | 50612 | 21742 | 19119 | 210698 | 168212 | 42486 | 0.054 | 154.424 | 12325.747 | 2.5629e-07 | 0.00073292 | 0.0585 | 7.7367 | 1.9829e-06 | 0.0056704 | 0.4526 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | McKittrick Limited | 46 | 42 | 42.12 | 5.396% | 3 |  | 1 |  | 44.2384 | 48.2411 | 4 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | In_DAC |  | 4 | 11.3408 | 4 | 0.6119 | 4 | 4 | NA_Extreme | NA_Moderate | 4 | 4 | 90.625 | 0
YES | YES | YES | SIERRA_1_UNITS | HIGH SIERRA LIMITED | 52.43 | 60.3 | PGAE | HIGH SIERRA LIMITED | COMBUSTION TURBINE | NATURAL GAS | ZP26 | 1989-02-24 | Kern Front Co-Gen | 115 | 50495 | 28059 | 7638 | 291746 | 270532 | 21214 | 0.084157 | 46.0059 | 17067.0219 | 2.8846e-07 | 0.00015769 | 0.0585 | 9.6415 | 2.7812e-06 | 0.0015204 | 0.56403 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | High Sierra Limited | 49.8 | 49.57 | 50.13 | 6.432% | 3 |  | 1 |  | 46.8795 | 50.8822 | 4 | Yes | Kern | South Kern PP | No | No Published Factor | 4 | 270 | High | In_DAC |  | 4 | 3.0408 | 4 | 0.19558 | 4 | 4 | NA_Extreme | NA_Moderate | 4 | 4 | 90.625 | 0
YES | YES | YES | BEARMT_1_UNIT | Bear Mountain Limited | 49.21 | 48.1 | PGAE | Bear Mountain Limited | COMBUSTION TURBINE | NATURAL GAS | ZP26 | 1995-04-03 | Columbus | 115 | 10649 | 35766 | 24605 | 335893 | 279971 | 55922 | 0.092 | 264.37 | 19649.6034 | 2.739e-07 | 0.00078707 | 0.0585 | 7.8279 | 2.144e-06 | 0.006161 | 0.45793 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Bear Mountain Limited | 46 | 44 | 44 | 8.876% | 4 |  | 1 |  | 40.7726 | 44.7753 | 4 | Yes | Kern | South Kern PP, Westpark | No | No Published Factor | 4 | 270 | High | DAC_Adjacent | 0.80638 | 3 | 12.3221 | 4 | 1.0937 | 4 | 4 | NA_Extreme | NA_Moderate | 4 | 4 | 86.4583 | 0
YES | YES | YES | CHALK_1_UNIT | CHALK CLIFF LIMITED | 48.67 | 55.1 | PGAE | Chalk Cliff Limited | COMBUSTION TURBINE | NATURAL GAS | ZP26 | 1990-03-20 | Taft | 115 | 50003 | 15300 | 12807 | 146125 | 117668 | 28457 | 0.042151 | 23.0425 | 8548.2528 | 2.8846e-07 | 0.00015769 | 0.0585 | 7.6907 | 2.2184e-06 | 0.0012128 | 0.4499 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Chalk Cliff Limited | 46 | 43.06 | 43.72 | 3.797% | 2 |  | 1 |  | 45.8137 | 49.8164 | 4 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | DAC_Adjacent | 2.0359 | 3 | 2.4255 | 4 | 0.092094 | 4 | 4 | NA_Extreme | NA_Moderate | 4 | 4 | 86.4583 | 0
YES | YES | YES | CHWCHL_1_UNIT | CHOW 2 PEAKER PLANT | 48.6 | 48.6 | PGAE | California Power Holdings, LLC | RECIPROCATING ENGINE | NATURAL GAS | NP15 | 2001-06-13 | Chowchilla | 115 | 56185 | 18429 | 0 | 191132 | 191132 | 0 | 0.056216 | 259.3408 | 11181.144 | 2.9412e-07 | 0.0013569 | 0.0585 | 10.3713 | 3.0504e-06 | 0.014072 | 0.60671 | CAISO_Reciprocating_Engine | Natural Gas Internal Combustion Engine | Chowchilla II | 49.6 | 48 | 48 | 4.241% | 3 |  | 2 |  | 34.5726 | 38.5753 | 3 | Yes | Fresno | Herndon, Panoche 115 kV, Wilson 115 kV | No | No Published Factor | 4 | 793 | High | DAC_Adjacent | 0.29385 | 3 | 28.1449 | 4 | 1.1938 | 4 | 4 | NA_Extreme | NA_Moderate | 4 | 4 | 86.4583 | 0
|  |  | VERNON_6_GONZL1 | H. Gonzales Unit #1 | 5.75 | 5.5 | SCE | City of Vernon | FTUR | NATURAL GAS | SP15 | 2013-06-13 | Laguna Bell | 230 | 7436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | CAISO_Peaker2 | Petroleum Liquids | H. Gonzales Unit #1 | 30 | 11.5 | 11.5 | 0% | 1 |  | 4 |  | 22.5644 | 26.5671 | 1 | Yes | LA Basin | Western | No | No Published Factor | 4 | 1141 | High | In_DAC |  | 4 | Not Available | 2.4 | Not Available | 2.5 | 2.5 | NA_Extreme | NA_Moderate | 4 | 4 | 84.375 | 1
|  |  | SGREGY_6_SANGER | Algonquin Power Sanger 2 | 48.3 | 48.3 | PGAE | Algonquin Power Sanger LLC | COMBINED CYCLE | NATURAL GAS | NP15 | 2017-06-01 | Sanger | 115 | 57564 | 176139 | 0 | 1232505 | 1232505 | 0 | 0.379 | 9.705 | 72101.0393 | 3.075e-07 | 7.8742e-06 | 0.0585 | 6.9973 | 2.1517e-06 | 5.5099e-05 | 0.40934 | CAISO_CCGT2 | Natural Gas Fired Combined Cycle | Algonquin Power Sanger LLC | 61.5 | 48.08 | 48.08 | 32.69% | 3 |  | 2 |  | 18.5945 | 22.5973 | 1 | Yes | Fresno | Herndon | No | No Published Factor | 4 | 793 | High | In_DAC |  | 4 | 0.1102 | 2 | 0.036029 | 3 | 4 | NA_Extreme | NA_Moderate | 4 | 4 | 84.375 | 1
YES | YES | YES | ELKHIL_2_PL1X3 | ELK HILLS COMBINED CYCLE (AGGREGATE) | 551.7 |  | PGAE | Elk Hills Power, LLC | COMBINED CYCLE | NATURAL GAS | NP15 | 2003-07-24 | Elk Hills | 230 | 55400 | 3797551 | 1351841 | 27124965 | 24621555 | 2503410 | 7.134 | 63.223 | 1586799.3774 | 2.63e-07 | 2.3308e-06 | 0.0585 | 6.4835 | 1.7052e-06 | 1.5112e-05 | 0.37928 | CAISO_CCGT1 | Natural Gas Fired Combined Cycle | Elk Hills Power LLC | 623 | 380 | 380 | 69.58% | 4 |  | 1 |  | 32.4603 | 36.463 | 3 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | In_DAC |  | 4 | 0.030224 | 1 | 0.021031 | 3 | 3 | NA_Extreme | NA_Moderate | 4 | 4 | 83.3333 | 0
| YES | YES | GLNARM_7_UNIT 1 | GLEN ARM UNIT 1 | 22.13 | 30.6 | SCE | City of Pasadena | COMBUSTION TURBINE | NATURAL GAS | SP15 | 1976-01-01 | Eagle Rock (SCE) | 230 | 422 | 107233.32 | 0 | 1166292 | 1166292 | 0 | 0.235 | 7.321 | 68227.6058 | 2.0149e-07 | 6.2772e-06 | 0.0585 | 10.8762 | 2.1915e-06 | 6.8272e-05 | 0.63625 | CAISO_CCGT2 | Natural Gas Fired Combustion Turbine | Glenarm | 265.6 | 196.62 | 196.62 | 4.609% | 1 |  | 4 |  | 60.0384 | 64.0411 | 4 | Yes | LA Basin | Western | No | No Published Factor | 4 | 1141 | High | DAC_Adjacent | 1.863 | 3 | 0.13654 | 2 | 0.0062932 | 2 | 1 | NA_Extreme | NA_Moderate | 4 | 4 | 83.3333 | 0
| YES | YES | GLNARM_7_UNIT 2 | GLEN ARM UNIT 2 | 22.38 | 30.6 | SCE | City of Pasadena | COMBUSTION TURBINE | NATURAL GAS | SP15 | 1976-01-01 | Eagle Rock (SCE) | 230 | 422 | 107233.32 | 0 | 1166292 | 1166292 | 0 | 0.235 | 7.321 | 68227.6058 | 2.0149e-07 | 6.2772e-06 | 0.0585 | 10.8762 | 2.1915e-06 | 6.8272e-05 | 0.63625 | CAISO_CCGT2 | Natural Gas Fired Combustion Turbine | Glenarm | 265.6 | 196.62 | 196.62 | 4.609% | 1 |  | 4 |  | 60.0384 | 64.0411 | 4 | Yes | LA Basin | Western | No | No Published Factor | 4 | 1141 | High | DAC_Adjacent | 1.863 | 3 | 0.13654 | 2 | 0.0062932 | 2 | 1 | NA_Extreme | NA_Moderate | 4 | 4 | 83.3333 | 0
| YES | YES | PNCHPP_1_PL1X2 | Midway Peaking Aggregate | 119.91 |  | PGAE | Midway Peaking, LLC | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2009-05-03 | Panoche | 230 | 56639 | 49354 | 0 | 543937 | 543937 | 0 | 0.169 | 5.238 | 31820.0924 | 3.107e-07 | 9.6298e-06 | 0.0585 | 11.0211 | 3.4242e-06 | 0.00010613 | 0.64473 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Midway Peaking LLC | 139.8 | 108.35 | 110.52 | 4.03% | 3 |  | 3 |  | 26.6795 | 30.6822 | 2 | Yes | Fresno | Panoche 115 kV | No | No Published Factor | 4 | 793 | High | In_DAC |  | 4 | 0.21226 | 3 | 0.0085543 | 2 | 2 | NA_Extreme | NA_Moderate | 4 | 4 | 82.2917 | 0
YES | YES | YES | SBERDO_2_PSP4 | Mountainview Gen Sta. Unit 4 | 555 |  | SCE | Southern California Edison Company | COMBINED CYCLE | NATURAL GAS | SP15 | 2006-01-19 | San Bernarino | 230 | 358 | 2091874.84 | 0 | 16733883 | 16733883 | 0 | 4.564 | 96.327 | 978925.3231 | 2.7274e-07 | 5.7564e-06 | 0.0585 | 7.9995 | 2.1818e-06 | 4.6048e-05 | 0.46797 | CAISO_CCGT1 | Natural Gas Fired Combined Cycle | Mountainview Generating Station | 1036.8 | 1110 | 1110 | 23.03% | 2 |  | 3 |  | 29.9671 | 33.9699 | 2 | Yes | LA Basin | Eastern, West of Devers | No | No Published Factor | 4 | 1141 | High | DAC_Adjacent | 0.13304 | 3 | 0.092096 | 1 | 0.021212 | 3 | 3 | NA_Extreme | NA_Moderate | 4 | 4 | 82.2917 | 0
YES | YES | YES | SUNRIS_2_PL1X3 | Sunrise Power Project AGGREGATE II | 586.02 |  | PGAE | Sunrise Power Company | COMBINED CYCLE | NATURAL GAS | NP15 | 2001-06-07 | Sunrise | 230 | 55182 | 2671368 | 0 | 19102277 | 19102277 | 0 | 5.61 | 50.19 | 1117475.405 | 2.9368e-07 | 2.6274e-06 | 0.0585 | 7.1507 | 2.1e-06 | 1.8788e-05 | 0.41832 | CAISO_CCGT1 | Natural Gas Fired Combined Cycle | Sunrise Power LLC | 605.4 | 586.02 | 586.02 | 50.37% | 4 |  | 1 |  | 34.589 | 38.5918 | 4 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | In_DAC |  | 4 | 0.037576 | 1 | 0.018928 | 3 | 2 | NA_Extreme | NA_Moderate | 4 | 4 | 82.2917 | 0
| YES | YES | ETIWND_6_GRPLND | Grapeland Peaker | 45.64 | 59 | SCE | Southern California Edison Company | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2007-09-20 | Rancho Vista | 500 | 56472 | 9892 | 0 | 129335 | 129335 | 0 | 0.036 | 0.88 | 7566.0447 | 2.7835e-07 | 6.804e-06 | 0.0585 | 13.0747 | 3.6393e-06 | 8.8961e-05 | 0.76487 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Grapeland Peaker | 59.8 | 47.39 | 47.39 | 1.888% | 1 |  | 4 |  | 28.2986 | 32.3014 | 2 | Yes | LA Basin | Eastern | No | No Published Factor | 4 | 1141 | High | In_DAC |  | 4 | 0.17792 | 3 | 0.0033598 | 1 | 1 | NA_Extreme | NA_Moderate | 4 | 4 | 81.25 | 0
| YES | YES | HENRTA_6_UNITA1 | GWF HENRIETTA PEAKER PLANT UNIT 1 | 49.98 | 50 | PGAE | MRP San Joaquin Energy, LLC | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2002-07-01 | Henrietta | 230 | 55807 | 32903 | 0 | 370609 | 370609 | 0 | 0.103 | 2.293 | 21680.4752 | 2.7792e-07 | 6.1871e-06 | 0.0585 | 11.2637 | 3.1304e-06 | 6.969e-05 | 0.65892 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Henrietta Peaker | 98 | 89.88 | 91.87 | 3.833% | 2 |  | 3 |  | 33.5233 | 37.526 | 3 | Yes | Fresno | 0 | No | No Published Factor | 4 | 793 | High | In_DAC |  | 4 | 0.13938 | 3 | 0.005342 | 1 | 1 | NA_Extreme | NA_Moderate | 4 | 4 | 81.25 | 0
| YES | YES | HENRTA_6_UNITA2 | GWF HENRIETTA PEAKER PLANT UNIT 2 | 49.42 | 50 | PGAE | MRP San Joaquin Energy, LLC | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2002-07-01 | Henrietta | 230 | 55807 | 32903 | 0 | 370609 | 370609 | 0 | 0.103 | 2.293 | 21680.4752 | 2.7792e-07 | 6.1871e-06 | 0.0585 | 11.2637 | 3.1304e-06 | 6.969e-05 | 0.65892 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Henrietta Peaker | 98 | 89.88 | 91.87 | 3.833% | 2 |  | 3 |  | 33.5233 | 37.526 | 3 | Yes | Fresno | 0 | No | No Published Factor | 4 | 793 | High | In_DAC |  | 4 | 0.13938 | 3 | 0.005342 | 1 | 1 | NA_Extreme | NA_Moderate | 4 | 4 | 81.25 | 0
| YES | YES | KINGCO_1_KINGBR | Kingsburg Cogen | 34.5 | 34.5 | PGAE | KES Kingsburg, L.P. | COMBUSTION TURBINE | NATURAL GAS | NP15 | 1990-12-05 | McCall | 230 | 10405 | 4964 | 1716 | 55903 | 50860 | 5043 | 0.017 | 0.55 | 3270.3027 | 3.041e-07 | 9.8385e-06 | 0.0585 | 10.2458 | 3.1157e-06 | 0.0001008 | 0.59937 | CAISO_Peaker2 | Natural Gas Fired Combined Cycle | Kingsburg Cogen | 36.2 | 34.5 | 34.5 | 1.565% | 1 |  | 2 |  | 45.1014 | 49.1041 | 4 | Yes | Fresno | Herndon, Hanford | No | No Published Factor | 4 | 793 | High | In_DAC |  | 4 | 0.20161 | 3 | 0.0031559 | 1 | 1 | NA_Extreme | NA_Moderate | 4 | 4 | 81.25 | 0
| YES | YES | LAPLMA_2_UNIT 1 | La Paloma Generating Plant Unit #1 | 267 | 295 | PGAE | CXA La Paloma LLC | COMBINED CYCLE | NATURAL GAS | ZP26 | 2003-01-10 | Sunset | 230 | 55151 | 1059098 | 0 | 7955982 | 7955982 | 0 | 2.393 | 31.012 | 465421.6986 | 3.0078e-07 | 3.8979e-06 | 0.0585 | 7.512 | 2.2595e-06 | 2.9282e-05 | 0.43945 | CAISO_CCGT1 | Natural Gas Fired Combined Cycle | La Paloma Generating Plant | 1200 | 1029.44 | 1029.44 | 10.08% | 2 |  | 2 |  | 32.9945 | 36.9973 | 4 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | In_DAC |  | 4 | 0.058563 | 1 | 0.0059003 | 2 | 1 | NA_Extreme | NA_Moderate | 4 | 4 | 81.25 | 0
| YES | YES | PNOCHE_1_UNITA1 | CalPeak Power Panoche Unit 1 | 52.3 | 57 | PGAE | CalPeak Power - Panoche LLC | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2001-12-27 | Panoche | 230 | 55508 | 14215 | 0 | 156850 | 156850 | 0 | 0.046 | 0.816 | 9175.661 | 2.9327e-07 | 5.2024e-06 | 0.0585 | 11.0341 | 3.236e-06 | 5.7404e-05 | 0.64549 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | CalPeak Power Panoche Peaker Plant | 60.5 | 52.01 | 52.01 | 2.682% | 2 |  | 3 |  | 34.0329 | 38.0356 | 3 | Yes | Fresno | Panoche 115 kV | No | No Published Factor | 4 | 793 | High | In_DAC |  | 4 | 0.11481 | 2 | 0.0030794 | 1 | 1 | NA_Extreme | NA_Moderate | 4 | 4 | 81.25 | 0
| YES | YES | OAK C_7_UNIT 3 | OAKLAND STATION C GT UNIT 3 | 55 | 55 | PGAE | Oakland Power Company LLC | COMBUSTION TURBINE | DISTILLATE | NP15 | 1978-01-01 | Oakland C | 115 | 6211 | 3852 | 0 | 65556 | 65556 | 0 | 10.3723 | 29.3388 | 5123.4491 | 0.00015822 | 0.00044754 | 0.078154 | 17.0187 | 0.0026927 | 0.0076165 | 1.3301 | CAISO_Peaker2 | Petroleum Liquids | Dynegy Oakland Power Plant | 223.5 | 165 | 165 | 0.1967% | 1 |  | 4 |  | 58.0356 | 62.0384 | 4 | Yes | Bay Area | Oakland | No | No Published Factor | 4 | 2220 | High | DAC_Adjacent | 0.35501 | 3 | 15.233 | 4 | 0.02997 | 3 | 3 | NA_Marginal | A | 1 | 1.25 | 80.2083 | 0
| YES | YES | PNCHEG_2_PL1X4 | PANOCHE ENERGY CENTER (Aggregated) | 417 |  | PGAE | PANOCHE ENERGY CENTER | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2009-05-27 | Panoche | 230 | 56803 | 615796 | 0 | 5741979 | 5741979 | 0 | 1.729 | 31.658 | 335903.427 | 3.0112e-07 | 5.5134e-06 | 0.0585 | 9.3245 | 2.8077e-06 | 5.141e-05 | 0.54548 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Panoche Energy Center | 432 | 395.6 | 400.1 | 16.27% | 4 |  | 1 |  | 26.6137 | 30.6164 | 2 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | In_DAC |  | 4 | 0.10282 | 2 | 0.016731 | 3 | 3 | NA_Extreme | NA_Moderate | 4 | 4 | 80.2083 | 0
| YES | YES | GWFPWR_1_UNITS | Hanford Peaker Plant | 98.46 |  | PGAE | MRP San Joaquin Energy, LLC | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2001-08-27 | Waukena | 115 | 55698 | 15605 | 0 | 183100 | 183100 | 0 | 0.054 | 24.363 | 10711.2752 | 2.9492e-07 | 0.00013306 | 0.0585 | 11.7334 | 3.4604e-06 | 0.0015612 | 0.6864 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Hanford Energy Park Peaker | 92.2 | 90.59 | 92.58 | 1.932% | 1 |  | 3 |  | 34.3671 | 38.3699 | 3 | Yes | Fresno | Herndon, Hanford | Yes | 8 | 3 | 793 | High | DAC_Adjacent | 1.955 | 3 | 3.1225 | 4 | 0.060329 | 4 | 3 | NA_Extreme | NA_Moderate | 4 | 4 | 79.1667 | 0
|  |  | SCHLTE_1_PL1X3 | Tracy Combined Cycle Power Plant | 336.04 |  | PGAE | MRP San Joaquin Energy, LLC | COMBINED CYCLE | NATURAL GAS | NP15 | 2012-10-31 | GWF Tracy | 115 | 55933 | 868383 | 0 | 7084590 | 7084590 | 0 | 2.16 | 32.802 | 414445.6224 | 3.0489e-07 | 4.63e-06 | 0.0585 | 8.1584 | 2.4874e-06 | 3.7774e-05 | 0.47726 | CAISO_CCGT2 | Natural Gas Fired Combined Cycle | Tracy Combined Cycle Power Plant | 336.1 | 309.51 | 314.34 | 29.49% | 3 |  | 3 |  | 23.1808 | 27.1836 | 1 | Yes | Stockton | Tesla-Bellota | No | No Published Factor | 4 | 545 | High | DAC_Adjacent | 2.1325 | 3 | 0.075547 | 1 | 0.022282 | 3 | 3 | NA_Extreme | NA_Moderate | 4 | 4 | 79.1667 | 1
| YES | YES | MIRLOM_6_PEAKER | Mira Loma Peaker | 47.18 | 59 | SCE | Southern California Edison Company | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2007-09-20 | Mira Loma | 500 | 56473 | 24008 | 0 | 243113 | 243113 | 0 | 0.074 | 1.774 | 14222.0112 | 3.0439e-07 | 7.297e-06 | 0.0585 | 10.1263 | 3.0823e-06 | 7.3892e-05 | 0.59239 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Mira Loma Peaker | 49.8 | 46 | 46 | 5.503% | 3 |  | 2 |  | 28.2986 | 32.3014 | 2 | Yes | LA Basin | Eastern | No | No Published Factor | 4 | 1141 | High | In_DAC |  | 4 | 0.14778 | 3 | 0.008133 | 2 | 2 | NA_Extreme | NA_Moderate | 4 | 4 | 79.1667 | 0
| YES | YES | CALPIN_1_AGNEW | Agnews Power Plant | 28.56 | 41.5 | PGAE | O.L.S. Energy-Agnews, Inc. | COMBUSTION TURBINE | NATURAL GAS | NP15 | 1990-10-19 | Los Esteros | 115 | 50748 | 15801 | 0 | 151465 | 151465 | 0 | 0.044159 | 20.6077 | 8860.6407 | 2.9155e-07 | 0.00013606 | 0.0585 | 9.5858 | 2.7947e-06 | 0.0013042 | 0.56076 | CAISO_CCGT2 | Natural Gas Fired Combined Cycle | Agnews Power Plant | 32 | 28.56 | 28.56 | 5.637% | 1 |  | 4 |  | 45.2301 | 49.2329 | 4 | Yes | Bay Area | San Jose, South Bay-Moss Landing | Yes | 7 | 3 | 2220 | High | DAC_Adjacent | 1.1494 | 3 | 2.6084 | 4 | 0.14703 | 4 | 4 | NA_Marginal | A | 1 | 1.25 | 78.125 | 0
|  | YES | COLTON_6_AGUAM1 | AGUA MANSA UNIT 1 (CITY OF COLTON) | 43 | 45.5 | SCE | City of Colton | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2003-06-27 | Vista (SCE) | 230 | 55951 | 7862 | 0 | 90083 | 90083 | 0 | 0.026 | 0.814 | 5269.8187 | 2.8862e-07 | 9.0361e-06 | 0.0585 | 11.458 | 3.307e-06 | 0.00010354 | 0.67029 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Agua Mansa Power Plant | 60.5 | 43 | 43 | 1.483% | 1 |  | 3 |  | 32.5342 | 36.537 | 2 | Yes | LA Basin | Eastern | No | No Published Factor | 4 | 1141 | High | In_DAC |  | 4 | 0.20707 | 3 | 0.0030718 | 1 | 1 | NA_Extreme | NA_Moderate | 4 | 4 | 78.125 | 0
| YES | YES | LAPLMA_2_UNIT 2 | La Paloma Generating Plant Unit #2 | 266 | 295 | PGAE | CXA La Paloma LLC | COMBINED CYCLE | NATURAL GAS | ZP26 | 2003-03-05 | Sunset | 230 | 55151 | 1059098 | 0 | 7955982 | 7955982 | 0 | 2.393 | 31.012 | 465421.6986 | 3.0078e-07 | 3.8979e-06 | 0.0585 | 7.512 | 2.2595e-06 | 2.9282e-05 | 0.43945 | CAISO_CCGT1 | Natural Gas Fired Combined Cycle | La Paloma Generating Plant | 1200 | 1029.44 | 1029.44 | 10.08% | 2 |  | 2 |  | 32.8466 | 36.8493 | 3 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | In_DAC |  | 4 | 0.058563 | 1 | 0.0059003 | 2 | 1 | NA_Extreme | NA_Moderate | 4 | 4 | 78.125 | 0
|  | YES | LAPLMA_2_UNIT 3 | La Paloma Generating Plant Unit #3 | 266 | 295 | PGAE | CXA La Paloma LLC | COMBINED CYCLE | NATURAL GAS | ZP26 | 2003-01-13 | Sunset | 230 | 55151 | 1059098 | 0 | 7955982 | 7955982 | 0 | 2.393 | 31.012 | 465421.6986 | 3.0078e-07 | 3.8979e-06 | 0.0585 | 7.512 | 2.2595e-06 | 2.9282e-05 | 0.43945 | CAISO_CCGT1 | Natural Gas Fired Combined Cycle | La Paloma Generating Plant | 1200 | 1029.44 | 1029.44 | 10.08% | 2 |  | 2 |  | 32.9863 | 36.989 | 3 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | In_DAC |  | 4 | 0.058563 | 1 | 0.0059003 | 2 | 1 | NA_Extreme | NA_Moderate | 4 | 4 | 78.125 | 0
| YES | YES | LAPLMA_2_UNIT 4 | LA PALOMA GENERATING PLANT, UNIT #4 | 267 | 295 | PGAE | CXA La Paloma LLC | COMBINED CYCLE | NATURAL GAS | ZP26 | 2003-03-05 | Sunset | 230 | 55151 | 1059098 | 0 | 7955982 | 7955982 | 0 | 2.393 | 31.012 | 465421.6986 | 3.0078e-07 | 3.8979e-06 | 0.0585 | 7.512 | 2.2595e-06 | 2.9282e-05 | 0.43945 | CAISO_CCGT1 | Natural Gas Fired Combined Cycle | La Paloma Generating Plant | 1200 | 1029.44 | 1029.44 | 10.08% | 2 |  | 2 |  | 32.8466 | 36.8493 | 3 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | In_DAC |  | 4 | 0.058563 | 1 | 0.0059003 | 2 | 1 | NA_Extreme | NA_Moderate | 4 | 4 | 78.125 | 0
| YES | YES | DUANE_1_PL1X3 | DONALD VON RAESFELD POWER PROJECT | 147.8 |  | PGAE | City of Santa Clara DBA Silicon Valley Power (MSS Agreement - S14) | COMBINED CYCLE | NATURAL GAS | NP15 | 2005-03-24 | FMC | 115 | 56026 | 861341 | 0 | 7378537 | 7378537 | 0 | 2.053 | 21.104 | 431641.4018 | 2.7824e-07 | 2.8602e-06 | 0.0585 | 8.5663 | 2.3835e-06 | 2.4501e-05 | 0.50113 | CAISO_CCGT2 | Natural Gas Fired Combined Cycle | Donald Von Raesfeld Power Plant | 154 | 143.5 | 143.5 | 63.85% | 4 |  | 3 |  | 30.7918 | 34.7945 | 3 | Yes | Bay Area | San Jose, South Bay-Moss Landing | Yes | 8 | 3 | 2220 | High | In_DAC |  | 4 | 0.049003 | 1 | 0.031287 | 3 | 4 | NA_Marginal | A | 1 | 1.25 | 76.0417 | 0
|  | YES | LEBECS_2_UNITS | Pastoria Energy Facility | 799.47 |  | SCE | Pastoria Energy Facility, LLC | COMBINED CYCLE | NATURAL GAS | SP15 | 2005-05-04 | Pastoria | 230 | 55656 | 4325910 | 0 | 30793325 | 30793325 | 0 | 9.297 | 96.644 | 1801396.9396 | 3.0192e-07 | 3.1385e-06 | 0.0585 | 7.1183 | 2.1491e-06 | 2.2341e-05 | 0.41642 | CAISO_CCGT1 | Natural Gas Fired Combined Cycle | Pastoria Energy Facility, LLC | 779 | 765 | 765 | 63.39% | 4 |  | 1 |  | 30.6795 | 34.6822 | 2 | Yes | BC/Ventura | 0 | No | No Published Factor | 4 | 657 | Low | DAC_Adjacent | 6.1934 | 2 | 0.044681 | 1 | 0.028325 | 3 | 4 | NA_Extreme | NA_Moderate | 4 | 4 | 76.0417 | 0
|  | YES | SBERDO_2_PSP3 | Mountainview Gen Sta. Unit 3 | 555 |  | SCE | Southern California Edison Company | COMBINED CYCLE | NATURAL GAS | SP15 | 2005-12-10 | San Bernarino | 230 | 358 | 2091874.84 | 0 | 16733883 | 16733883 | 0 | 4.564 | 96.327 | 978925.3231 | 2.7274e-07 | 5.7564e-06 | 0.0585 | 7.9995 | 2.1818e-06 | 4.6048e-05 | 0.46797 | CAISO_CCGT1 | Natural Gas Fired Combined Cycle | Mountainview Generating Station | 1036.8 | 1110 | 1110 | 23.03% | 2 |  | 3 |  | 30.0767 | 34.0795 | 2 | Yes | LA Basin | Eastern, West of Devers | Yes | 9 | 3 | 1141 | High | DAC_Adjacent | 0.13304 | 3 | 0.092096 | 1 | 0.021212 | 3 | 3 | NA_Extreme | NA_Moderate | 4 | 4 | 76.0417 | 0
|  | YES | SHELRF_1_UNITS | SHELL OIL REFINERY AGGREGATE | 100 |  | PGAE | Martinez Refining Company-Division of Equilon Enterprises, LLC | COMBINED CYCLE | NATURAL GAS | NP15 | 1995-01-01 | Martinez | 115 | 54912 | 810838 | 2889693 | 10964752 | 5407653 | 5557099 | 3.5673 | 1157.2265 | 479186.36 | 3.2534e-07 | 0.00010554 | 0.043702 | 6.6692 | 2.1698e-06 | 0.00070387 | 0.29146 | CAISO_Peaker2 | Natural Gas Fired Combined Cycle | Martinez Refining | 100 | 27.71 | 26.98 | 92.56% | 4 |  | 4 |  | 41.0247 | 45.0274 | 4 | Yes | Bay Area | Pittsburg | Yes | 20 | 2 | 2220 | High | In_DAC |  | 4 | 1.4077 | 3 | 1.303 | 4 | 4 | NA_Marginal | A | 1 | 1.25 | 76.0417 | 0
|  | YES | HIDSRT_2_UNITS | HIGH DESERT POWER PROJECT AGGREGATE | 850 |  | SCE | High Desert Power Project, LLC | COMBINED CYCLE | NATURAL GAS | SP15 | 2003-04-21 | Roadway | 115 | 55518 | 3019302 | 0 | 22459294 | 22459294 | 0 | 6.781 | 95.897 | 1313859.5289 | 3.0192e-07 | 4.2698e-06 | 0.0585 | 7.4386 | 2.2459e-06 | 3.1761e-05 | 0.43515 | CAISO_CCGT1 | Natural Gas Fired Combined Cycle | High Desert Power Plant | 852 | 830 | 830 | 40.45% | 3 |  | 2 |  | 32.7178 | 36.7205 | 3 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | DAC_Adjacent | 0.59977 | 3 | 0.063523 | 1 | 0.025698 | 3 | 3 | NA_Severe 15 | A | 3 | 2.25 | 75 | 0
|  |  | VESTAL_2_WELLHD | Wellhead Power Delano | 49 | 49.5 | SCE | Delano Energy Center, LLC | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2013-01-16 | Smyrna | 115 | 58122 | 5455 | 0 | 67225 | 67225 | 0 | 0.019 | 0.308 | 3932.6351 | 2.8263e-07 | 4.5816e-06 | 0.0585 | 12.3236 | 3.483e-06 | 5.6462e-05 | 0.72092 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Delano Energy Center | 48.5 | 49 | 49 | 1.284% | 1 |  | 3 |  | 22.9699 | 26.9726 | 1 | Yes | BC/Ventura | Vestal | No | No Published Factor | 4 | 657 | High | In_DAC |  | 4 | 0.11292 | 2 | 0.0014499 | 1 | 1 | NA_Extreme | NA_Moderate | 4 | 4 | 75 | 1
|  |  | HARBGN_7_UNITS | HARBOR COGEN COMBINED CYCLE | 109.01 |  | SCE | Harbor Cogeneration Company | COMBINED CYCLE | NATURAL GAS | SP15 | 2001-06-14 | HarborGen | 230 | 50541 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | CAISO_CCGT2 | Natural Gas Fired Combined Cycle | HARBOR COGEN COMBINED CYCLE | 107.4 | 100 | 100 | 0% | 1 |  | 4 |  | 34.5699 | 38.5726 | 4 | Yes | LA Basin | Western | Yes | 23 | 1 | 1141 | High | In_DAC |  | 4 | Not Available | 2.4 | Not Available | 2.5 | 2.5 | NA_Extreme | NA_Moderate | 4 | 4 | 75 | 1
|  | YES | CSCGNR_1_UNIT 1 | GIANERA PEAKER UNIT 1 | 24.75 | 24.8 | PGAE | City of Santa Clara DBA Silicon Valley Power (MSS Agreement - S14) | FTUR | NATURAL GAS | NP15 | 1987-01-01 | Los Esteros | 115 | 7231 | 8019 | 0 | 117278 | 117278 | 0 | 0.03406 | 18.6192 | 6860.7151 | 2.9042e-07 | 0.00015876 | 0.0585 | 14.625 | 4.2474e-06 | 0.0023219 | 0.85556 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Gianera | 64.6 | 48 | 48 | 1.417% | 1 |  | 4 |  | 49.0301 | 53.0329 | 4 | Yes | Bay Area | San Jose, South Bay-Moss Landing | Yes | 7 | 3 | 2220 | High | DAC_Adjacent | 1.1779 | 3 | 4.6438 | 4 | 0.065804 | 4 | 3 | NA_Marginal | A | 1 | 1.25 | 73.9583 | 0
|  | YES | CSCGNR_1_UNIT 2 | GIANERA PEAKER UNIT 2 | 24.75 | 24.8 | PGAE | City of Santa Clara DBA Silicon Valley Power (MSS Agreement - S14) | FTUR | NATURAL GAS | NP15 | 1986-01-01 | Los Esteros | 115 | 7231 | 8019 | 0 | 117278 | 117278 | 0 | 0.03406 | 18.6192 | 6860.7151 | 2.9042e-07 | 0.00015876 | 0.0585 | 14.625 | 4.2474e-06 | 0.0023219 | 0.85556 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Gianera | 64.6 | 48 | 48 | 1.417% | 1 |  | 4 |  | 50.0301 | 54.0329 | 4 | Yes | Bay Area | San Jose, South Bay-Moss Landing | Yes | 7 | 3 | 2220 | High | DAC_Adjacent | 1.1779 | 3 | 4.6438 | 4 | 0.065804 | 4 | 3 | NA_Marginal | A | 1 | 1.25 | 73.9583 | 0
|  | YES | PALALT_7_COBUG | Cooperatively Owned Back Up Generator | 4.5 | 5.2 | PGAE | NCPA (MSS Agreement - S14) | FTUR | NATURAL GAS | NP15 | 2007-10-15 | Monte Vista | 230 | 57714 | 31 | 0 | 398 | 398 | 0 | 0.0001158 | 0.53422 | 23.2828 | 2.9095e-07 | 0.0013423 | 0.0585 | 12.8387 | 3.7355e-06 | 0.017233 | 0.75106 | CAISO_Peaker2 | Natural Gas Internal Combustion Engine | City of Palo Alto | 4.4 | 4.5 | 4.5 | 0.08043% | 1 |  | 4 |  | 28.2301 | 32.2329 | 2 | Yes | Bay Area | 0 | No | No Published Factor | 4 | 2220 | High | DAC_Adjacent | 1.3547 | 3 | 34.4661 | 4 | 0.02772 | 3 | 3 | NA_Marginal | A | 1 | 1.25 | 73.9583 | 0
|  | YES | RVRVEW_1_UNITA1 | Riverview Energy Center (GP Antioch) | 48.7 | 50 | PGAE | Gilroy Energy Center, LLC | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2003-05-02 | Fibreboard (SPI Sonora) | 115 | 55963 | 18001 | 0 | 205484 | 205484 | 0 | 0.064 | 1.998 | 12020.7301 | 3.1146e-07 | 9.7234e-06 | 0.0585 | 11.4151 | 3.5554e-06 | 0.00011099 | 0.66778 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Riverview Energy Center | 47 | 47.6 | 47.6 | 4.372% | 3 |  | 3 |  | 32.6877 | 36.6904 | 3 | Yes | Bay Area | Contra Costa | No | No Published Factor | 4 | 2220 | High | DAC_Adjacent | 0.45355 | 3 | 0.22199 | 3 | 0.0097056 | 3 | 3 | NA_Marginal | A | 1 | 1.25 | 73.9583 | 0
|  | YES | RVSIDE_2_RERCU3 | Riverside Energy Res. Ctr Unit 3 | 49 | 71 | SCE | City of Riverside (MSSA) | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2011-04-01 | Mira Loma | 500 | 56143 | 86351 | 0 | 934103 | 934103 | 0 | 0.283 | 4.823 | 54644.6441 | 3.0296e-07 | 5.1632e-06 | 0.0585 | 10.8175 | 3.2773e-06 | 5.5853e-05 | 0.63282 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Riverside Energy Resource Center | 196 | 194.85 | 194.85 | 5.029% | 3 |  | 2 |  | 24.7671 | 28.7699 | 2 | Yes | LA Basin | Eastern | Yes | 9 | 3 | 1141 | High | In_DAC |  | 4 | 0.11171 | 2 | 0.0056181 | 1 | 2 | NA_Extreme | NA_Moderate | 4 | 4 | 72.9167 | 0
|  | YES | RVSIDE_2_RERCU4 | Riverside Energy Res. Ctr Unit 4 | 49 | 71.2 | SCE | City of Riverside (MSSA) | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2011-04-01 | Mira Loma | 500 | 56143 | 86351 | 0 | 934103 | 934103 | 0 | 0.283 | 4.823 | 54644.6441 | 3.0296e-07 | 5.1632e-06 | 0.0585 | 10.8175 | 3.2773e-06 | 5.5853e-05 | 0.63282 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Riverside Energy Resource Center | 196 | 194.85 | 194.85 | 5.029% | 3 |  | 2 |  | 24.7671 | 28.7699 | 2 | Yes | LA Basin | Eastern | Yes | 9 | 3 | 1141 | High | In_DAC |  | 4 | 0.11171 | 2 | 0.0056181 | 1 | 2 | NA_Extreme | NA_Moderate | 4 | 4 | 72.9167 | 0
|  | YES | RVSIDE_6_RERCU1 | Riverside Energy Res. Ctr Unit 1 | 48.35 | 48.5 | SCE | City of Riverside (MSSA) | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2006-06-01 | Mira Loma | 500 | 56143 | 86351 | 0 | 934103 | 934103 | 0 | 0.283 | 4.823 | 54644.6441 | 3.0296e-07 | 5.1632e-06 | 0.0585 | 10.8175 | 3.2773e-06 | 5.5853e-05 | 0.63282 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Riverside Energy Resource Center | 196 | 194.85 | 194.85 | 5.029% | 3 |  | 2 |  | 29.6027 | 33.6055 | 2 | Yes | LA Basin | Eastern | Yes | 9 | 3 | 1141 | High | In_DAC |  | 4 | 0.11171 | 2 | 0.0056181 | 1 | 2 | NA_Extreme | NA_Moderate | 4 | 4 | 72.9167 | 0
|  | YES | RVSIDE_6_RERCU2 | Riverside Energy Res. Ctr Unit 2 | 48.5 | 48.5 | SCE | City of Riverside (MSSA) | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2006-06-01 | Mira Loma | 500 | 56143 | 86351 | 0 | 934103 | 934103 | 0 | 0.283 | 4.823 | 54644.6441 | 3.0296e-07 | 5.1632e-06 | 0.0585 | 10.8175 | 3.2773e-06 | 5.5853e-05 | 0.63282 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Riverside Energy Resource Center | 196 | 194.85 | 194.85 | 5.029% | 3 |  | 2 |  | 29.6027 | 33.6055 | 2 | Yes | LA Basin | Eastern | Yes | 9 | 3 | 1141 | High | In_DAC |  | 4 | 0.11171 | 2 | 0.0056181 | 1 | 2 | NA_Extreme | NA_Moderate | 4 | 4 | 72.9167 | 0
|  | YES | ALMEGT_1_UNIT 1 | ALAMEDA GT UNIT 1 | 25 | 25.4 | PGAE | NCPA (MSS Agreement - S14) | FTUR | NATURAL GAS | NP15 | 1986-01-01 | Cartwright Jenny | 115 | 7450 | 9563 | 0 | 143953 | 143953 | 0 | 0.041485 | 22.6784 | 8421.1917 | 2.8818e-07 | 0.00015754 | 0.0585 | 15.0531 | 4.3381e-06 | 0.0023715 | 0.8806 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Alameda | 54.8 | 46.9 | 46.9 | 1.992% | 1 |  | 4 |  | 50.0301 | 54.0329 | 4 | Yes | Bay Area | Oakland | Yes | 17 | 2 | 2220 | High | DAC_Adjacent | 0.97185 | 3 | 4.7429 | 4 | 0.094484 | 4 | 4 | NA_Marginal | A | 1 | 1.25 | 71.875 | 0
|  | YES | ALMEGT_1_UNIT 2 | ALAMEDA GT UNIT 2 | 25 | 25.4 | PGAE | NCPA (MSS Agreement - S14) | FTUR | NATURAL GAS | NP15 | 1986-01-01 | Cartwright Jenny | 115 | 7450 | 9563 | 0 | 143953 | 143953 | 0 | 0.041485 | 22.6784 | 8421.1917 | 2.8818e-07 | 0.00015754 | 0.0585 | 15.0531 | 4.3381e-06 | 0.0023715 | 0.8806 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Alameda | 54.8 | 46.9 | 46.9 | 1.992% | 1 |  | 4 |  | 50.0301 | 54.0329 | 4 | Yes | Bay Area | Oakland | Yes | 17 | 2 | 2220 | High | DAC_Adjacent | 0.97185 | 3 | 4.7429 | 4 | 0.094484 | 4 | 4 | NA_Marginal | A | 1 | 1.25 | 71.875 | 0
|  |  | GRZZLY_1_BERKLY | Berkeley Cogeneration | 26.35 | 32.5 | PGAE | The Regents of the University of California | COMBINED CYCLE | NATURAL GAS | NP15 | 2018-02-20 | Oakland J 1 | 115 | 50849 | 167747.305 | 669496 | 2008797 | 946108 | 1062689 | 0.58088 | 274.1654 | 117513.8043 | 2.8917e-07 | 0.00013648 | 0.0585 | 5.6401 | 1.6309e-06 | 0.00076977 | 0.32994 | CAISO_Peaker2 | Natural Gas Fired Combined Cycle | PE Berkeley | 28.5 | 14.67 | 14.17 | 67.19% | 4 |  | 3 |  | 17.8712 | 21.874 | 1 | Yes | Bay Area | 0 | No | No Published Factor | 4 | 2220 | High | DAC_Adjacent | 1.918 | 3 | 1.5395 | 3 | 1.0344 | 4 | 4 | NA_Marginal | A | 1 | 1.25 | 71.875 | 1
|  |  | LGHTHP_6_ICEGEN | CARSON COGENERATION | 48 | 54.7 | SCE | Carson Hybrid Energy Storage LLC | COMBINED CYCLE | NATURAL GAS | SP15 | 1989-12-22 | Lightpipe | 230 | 10169 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | CAISO_Peaker1 | Natural Gas Fired Combined Cycle | CARSON COGENERATION | 55.8 | 48 | 48 | 0% | 1 |  | 3 |  | 46.0548 | 50.0575 | 4 | Yes | LA Basin | Western | Yes | 22 | 1 | 1141 | High | In_DAC |  | 4 | Not Available | 2.4 | Not Available | 2.5 | 2.5 | NA_Extreme | NA_Moderate | 4 | 4 | 71.875 | 1
|  |  | VERNON_6_MALBRG | Malburg Generating Station | 139 |  | SCE | City of Vernon | COMBINED CYCLE | NATURAL GAS | SP15 | 2005-10-17 | Laguna Bell | 230 | 56041 | 479363 | 0 | 3974419 | 3974419 | 0 | 1.191 | 15.914 | 232501.8887 | 2.9967e-07 | 4.0041e-06 | 0.0585 | 8.291 | 2.4845e-06 | 3.3198e-05 | 0.48502 | CAISO_CCGT2 | Natural Gas Fired Combined Cycle | Malburg | 130 | 134 | 134 | 42.09% | 4 |  | 3 |  | 30.2247 | 34.2274 | 2 | Yes | LA Basin | Western | Yes | 34 | 1 | 1141 | High | In_DAC |  | 4 | 0.066396 | 1 | 0.027949 | 3 | 4 | NA_Extreme | NA_Moderate | 4 | 4 | 71.875 | 1
|  | YES | ANAHM_2_CANYN1 | CANYON POWER PLANT UNIT 1 | 49.21 | 71.2 | SCE | City of Anaheim (MSS Agreement - S14) | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2011-09-16 | Villa Park | 230 | 57027 | 181871 | 0 | 1939008 | 1939008 | 0 | 0.584 | 8.334 | 113431.1763 | 3.0118e-07 | 4.2981e-06 | 0.0585 | 10.6614 | 3.2111e-06 | 4.5824e-05 | 0.62369 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Canyon Power Plant | 200 | 194.8 | 194.8 | 10.38% | 4 |  | 2 |  | 24.3068 | 28.3096 | 2 | Yes | LA Basin | Western | Yes | 10 | 2 | 1141 | High | In_DAC |  | 4 | 0.091647 | 1 | 0.0095137 | 2 | 3 | NA_Extreme | NA_Moderate | 4 | 4 | 70.8333 | 0
|  | YES | ANAHM_2_CANYN2 | CANYON POWER PLANT UNIT 2 | 48.04 | 71.2 | SCE | City of Anaheim (MSS Agreement - S14) | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2011-09-16 | Villa Park | 230 | 57027 | 181871 | 0 | 1939008 | 1939008 | 0 | 0.584 | 8.334 | 113431.1763 | 3.0118e-07 | 4.2981e-06 | 0.0585 | 10.6614 | 3.2111e-06 | 4.5824e-05 | 0.62369 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Canyon Power Plant | 200 | 194.8 | 194.8 | 10.38% | 4 |  | 2 |  | 24.3068 | 28.3096 | 2 | Yes | LA Basin | Western | Yes | 10 | 2 | 1141 | High | In_DAC |  | 4 | 0.091647 | 1 | 0.0095137 | 2 | 3 | NA_Extreme | NA_Moderate | 4 | 4 | 70.8333 | 0
|  | YES | ANAHM_2_CANYN3 | CANYON POWER PLANT UNIT 3 | 46.49 | 71.2 | SCE | City of Anaheim (MSS Agreement - S14) | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2011-07-30 | Villa Park | 230 | 57027 | 181871 | 0 | 1939008 | 1939008 | 0 | 0.584 | 8.334 | 113431.1763 | 3.0118e-07 | 4.2981e-06 | 0.0585 | 10.6614 | 3.2111e-06 | 4.5824e-05 | 0.62369 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Canyon Power Plant | 200 | 194.8 | 194.8 | 10.38% | 4 |  | 2 |  | 24.4384 | 28.4411 | 2 | Yes | LA Basin | Western | Yes | 10 | 2 | 1141 | High | In_DAC |  | 4 | 0.091647 | 1 | 0.0095137 | 2 | 3 | NA_Extreme | NA_Moderate | 4 | 4 | 70.8333 | 0
|  | YES | ANAHM_2_CANYN4 | CANYON POWER PLANT UNIT 4 | 49.8 | 71.2 | SCE | City of Anaheim (MSS Agreement - S14) | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2011-07-30 | Villa Park | 230 | 57027 | 181871 | 0 | 1939008 | 1939008 | 0 | 0.584 | 8.334 | 113431.1763 | 3.0118e-07 | 4.2981e-06 | 0.0585 | 10.6614 | 3.2111e-06 | 4.5824e-05 | 0.62369 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Canyon Power Plant | 200 | 194.8 | 194.8 | 10.38% | 4 |  | 2 |  | 24.4384 | 28.4411 | 2 | Yes | LA Basin | Western | Yes | 10 | 2 | 1141 | High | In_DAC |  | 4 | 0.091647 | 1 | 0.0095137 | 2 | 3 | NA_Extreme | NA_Moderate | 4 | 4 | 70.8333 | 0
|  | YES | BARRE_6_PEAKER | Barre Peaker | 49 | 59 | SCE | Southern California Edison Company | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2007-09-20 | Barre | 230 | 56474 | 33130 | 0 | 338877 | 338877 | 0 | 0.1 | 2.052 | 19824.1661 | 2.9509e-07 | 6.0553e-06 | 0.0585 | 10.2287 | 3.0184e-06 | 6.1938e-05 | 0.59838 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Barre Peaker | 49.8 | 47 | 47 | 7.594% | 4 |  | 2 |  | 28.2986 | 32.3014 | 2 | Yes | LA Basin | Western | Yes | 13 | 2 | 1141 | High | In_DAC |  | 4 | 0.12388 | 2 | 0.0094075 | 2 | 3 | NA_Extreme | NA_Moderate | 4 | 4 | 70.8333 | 0
|  | YES | BOGUE_1_UNITA1 | Feather River Energy Center, Unit #1 | 48.69 | 49.9 | PGAE | Gilroy Energy Center, LLC | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2002-12-23 | Bogue | 115 | 55847 | 33113 | 0 | 388898 | 388898 | 0 | 0.122 | 15.105 | 22750.3742 | 3.1371e-07 | 3.8841e-05 | 0.0585 | 11.7446 | 3.6844e-06 | 0.00045617 | 0.68705 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Feather River Energy Center | 47 | 47.6 | 47.6 | 8.043% | 4 |  | 3 |  | 33.0438 | 37.0466 | 3 | Yes | Sierra | Bogue, Drum-Rio Oso | Yes | 5 | 3 | 75 | High | DAC_Adjacent | 0.3758 | 3 | 0.91233 | 3 | 0.073375 | 4 | 4 | A | A | 1 | 1 | 70.8333 | 0
|  | YES | KNGCTY_6_UNITA1 | King City Energy Center, Unit 1 | 44.6 | 49.9 | PGAE | Gilroy Energy Center, LLC | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2002-01-14 | Coburn | 230 | 55811 | 8584 | 0 | 96422 | 96422 | 0 | 0.027922 | 15.2638 | 5640.6476 | 2.8958e-07 | 0.0001583 | 0.0585 | 11.2328 | 3.2527e-06 | 0.0017782 | 0.65711 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | King City Peaking | 47.3 | 44.6 | 44.6 | 2.072% | 1 |  | 3 |  | 33.9836 | 37.9863 | 3 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | Outside_DAC | 36.6048 | 1 | 3.5563 | 4 | 0.073676 | 4 | 4 | A | A | 1 | 1 | 68.75 | 0
|  | YES | LMEC_1_PL1X3 | Los Medanos Energy Center AGGREGATE | 580 |  | PGAE | Los Medanos Energy Center, LLC | COMBINED CYCLE | NATURAL GAS | NP15 | 2001-06-09 | Pittsburg | 115 | 55217 | 3274740 | 1452902 | 24632826 | 21838781 | 2794045 | 7.478 | 89.347 | 1441010.2634 | 3.0358e-07 | 3.6272e-06 | 0.0585 | 6.6689 | 2.0245e-06 | 2.4189e-05 | 0.39013 | CAISO_CCGT2 | Natural Gas Fired Combined Cycle | Los Medanos Energy Center | 678.3 | 574.53 | 574.53 | 55.11% | 4 |  | 3 |  | 34.5836 | 38.5863 | 4 | Yes | Bay Area | Pittsburg | Yes | 16 | 2 | 2220 | High | In_DAC |  | 4 | 0.048378 | 1 | 0.026662 | 3 | 3 | NA_Marginal | A | 1 | 1.25 | 68.75 | 0
|  |  | ELSEGN_2_UN1011 | El Segundo Energy Center 5/6 | 274.31 |  | SCE | El Segundo Energy Center LLC | COMBINED CYCLE | NATURAL GAS | SP15 | 2013-06-29 | El Segundo | 230 | 57901 | 1054778 | 0 | 8976146 | 8976146 | 0 | 2.6777 | 1249.6014 | 525100.876 | 2.9831e-07 | 0.00013921 | 0.0585 | 8.51 | 2.5387e-06 | 0.0011847 | 0.49783 | CAISO_CCGT2 | Natural Gas Fired Combined Cycle | El Segundo Energy Center LLC | 537.4 | 526.68 | 526.68 | 22.41% | 2 |  | 3 |  | 22.5205 | 26.5233 | 1 | Yes | LA Basin | Western, El Nido | Yes | 27 | 1 | 1141 | High | In_DAC |  | 4 | 2.3694 | 4 | 0.53088 | 4 | 4 | NA_Extreme | NA_Moderate | 4 | 4 | 68.75 | 1
|  |  | ELSEGN_2_UN2021 | El Segundo Energy Center 7/8 | 271.74 |  | SCE | El Segundo Energy Center LLC | COMBINED CYCLE | NATURAL GAS | SP15 | 2013-06-29 | El Segundo | 230 | 57901 | 1054778 | 0 | 8976146 | 8976146 | 0 | 2.6777 | 1249.6014 | 525100.876 | 2.9831e-07 | 0.00013921 | 0.0585 | 8.51 | 2.5387e-06 | 0.0011847 | 0.49783 | CAISO_CCGT2 | Natural Gas Fired Combined Cycle | El Segundo Energy Center LLC | 537.4 | 526.68 | 526.68 | 22.41% | 2 |  | 3 |  | 22.5205 | 26.5233 | 1 | Yes | LA Basin | Western, El Nido | Yes | 27 | 1 | 1141 | High | In_DAC |  | 4 | 2.3694 | 4 | 0.53088 | 4 | 4 | NA_Extreme | NA_Moderate | 4 | 4 | 68.75 | 1
|  | YES | GOLETA_6_ELLWOD | ELLWOOD ENERGY SUPPORT FACILITY | 54 | 56 | SCE | GenOn California South, LP | COMBUSTION TURBINE | NATURAL GAS | SP15 | 1998-04-29 | Goleta | 230 | 8076 | 6212 | 0 | 89752 | 89752 | 0 | 0.02589 | 14.1534 | 5250.4554 | 2.8846e-07 | 0.00015769 | 0.0585 | 14.4482 | 4.1678e-06 | 0.0022784 | 0.84521 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Ellwood | 58 | 0 | 0 | 1.223% | 1 |  | 4 |  | 37.6986 | 41.7014 | 3 | Yes | BC/Ventura | S.Clara, Moorpark, Goleta | No | No Published Factor | 4 | 657 | High | Outside_DAC | 41.9625 | 1 | 4.5568 | 4 | 0.055713 | 3 | 3 | A | A | 1 | 1 | 67.7083 | 0
|  | YES | GLNARM_7_UNIT 3 | GLEN ARM UNIT 3 | 44.83 | 47.3 | SCE | City of Pasadena | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2004-01-08 | Eagle Rock (SCE) | 230 | 422 | 107233.32 | 0 | 1166292 | 1166292 | 0 | 0.235 | 7.321 | 68227.6058 | 2.0149e-07 | 6.2772e-06 | 0.0585 | 10.8762 | 2.1915e-06 | 6.8272e-05 | 0.63625 | CAISO_CCGT2 | Natural Gas Fired Combustion Turbine | Glenarm | 265.6 | 196.62 | 196.62 | 4.609% | 1 |  | 4 |  | 32 | 36.0027 | 3 | Yes | LA Basin | Western | Yes | 10 | 2 | 1141 | High | DAC_Adjacent | 1.863 | 3 | 0.13654 | 2 | 0.0062932 | 2 | 1 | NA_Extreme | NA_Moderate | 4 | 4 | 67.7083 | 0
|  | YES | GLNARM_7_UNIT 4 | GLEN ARM UNIT 4 | 42.42 | 47.3 | SCE | City of Pasadena | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2004-01-08 | Eagle Rock (SCE) | 230 | 422 | 107233.32 | 0 | 1166292 | 1166292 | 0 | 0.235 | 7.321 | 68227.6058 | 2.0149e-07 | 6.2772e-06 | 0.0585 | 10.8762 | 2.1915e-06 | 6.8272e-05 | 0.63625 | CAISO_CCGT2 | Natural Gas Fired Combustion Turbine | Glenarm | 265.6 | 196.62 | 196.62 | 4.609% | 1 |  | 4 |  | 32 | 36.0027 | 3 | Yes | LA Basin | Western | Yes | 10 | 2 | 1141 | High | DAC_Adjacent | 1.863 | 3 | 0.13654 | 2 | 0.0062932 | 2 | 1 | NA_Extreme | NA_Moderate | 4 | 4 | 67.7083 | 0
|  | YES | OAK C_7_UNIT 1 | OAKLAND STATION C GT UNIT 1 | 55 | 55 | PGAE | Oakland Power Company LLC | COMBUSTION TURBINE | DISTILLATE | NP15 | 1978-01-01 | Oakland C | 115 | 6211 | 3852 | 0 | 65556 | 65556 | 0 | 10.3723 | 29.3388 | 5123.4491 | 0.00015822 | 0.00044754 | 0.078154 | 17.0187 | 0.0026927 | 0.0076165 | 1.3301 | CAISO_Peaker2 | Petroleum Liquids | Dynegy Oakland Power Plant | 223.5 | 165 | 165 | 0.1967% | 1 |  | 4 |  | 58.0356 | 62.0384 | 4 | Yes | Bay Area | Oakland | Yes | 17 | 2 | 2220 | High | DAC_Adjacent | 0.35501 | 3 | 15.233 | 4 | 0.02997 | 3 | 3 | NA_Marginal | A | 1 | 1.25 | 67.7083 | 0
|  |  | KELSO_2_UNITS | Mariposa Energy | 198.03 |  | PGAE | Mariposa Energy, LLC | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2012-10-01 | Kelso | 230 | 57483 | 112210 | 0 | 1228889 | 1228889 | 0 | 0.408 | 7.52 | 71889.5047 | 3.3201e-07 | 6.1193e-06 | 0.0585 | 10.9517 | 3.636e-06 | 6.7017e-05 | 0.64067 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Mariposa Energy Project | 199.6 | 192.36 | 194.59 | 6.418% | 3 |  | 3 |  | 23.263 | 27.2658 | 1 | Yes | Bay Area | Contra Costa | No | No Published Factor | 4 | 2220 | High | DAC_Adjacent | 3.0934 | 3 | 0.13403 | 2 | 0.0086017 | 2 | 3 | NA_Marginal | A | 1 | 1.25 | 67.7083 | 1
|  |  | MNDALY_6_MCGRTH | McGrath Beach Peaker | 48.56 | 59 | SCE | Southern California edison | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2012-11-01 | Mandalay | 230 | 56471 | 23962 | 0 | 242811 | 242811 | 0 | 0.072 | 1.384 | 14204.3444 | 2.9653e-07 | 5.6999e-06 | 0.0585 | 10.1332 | 3.0048e-06 | 5.7758e-05 | 0.59279 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | McGrath Peaker | 49.8 | 47.2 | 47.2 | 5.493% | 3 |  | 2 |  | 23.1781 | 27.1808 | 1 | Yes | BC/Ventura | S.Clara, Moorpark | No | No Published Factor | 4 | 657 | High | In_DAC |  | 4 | 0.11552 | 2 | 0.006345 | 2 | 2 | NA_Serious | A | 2 | 2 | 67.7083 | 1
|  | YES | BUCKBL_2_PL1X3 | Blythe Energy Center | 493.63 |  | SCE | Blythe Energy Inc | COMBINED CYCLE | NATURAL GAS | SP15 | 2010-07-31 | BlytheSC 161 kV | 161 | 55295 | 2695876 | 0 | 19860251 | 19860251 | 0 | 6.058 | 72.27 | 1161816.5746 | 3.0503e-07 | 3.6389e-06 | 0.0585 | 7.3669 | 2.2471e-06 | 2.6808e-05 | 0.43096 | CAISO_CCGT1 | Natural Gas Fired Combined Cycle | Blythe Energy Inc | 591 | 490 | 490 | 52.07% | 4 |  | 2 |  | 25.4356 | 29.4384 | 2 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | DAC_Adjacent | 4.3913 | 3 | 0.053615 | 1 | 0.027919 | 3 | 3 | A | A | 1 | 1 | 66.6667 | 0
|  | YES | HINSON_6_LBECH1 | Long Beach Unit 1 | 63 | 70 | SCE | Long Beach Generation LLC | FTUR | NATURAL GAS | SP15 | 2007-08-01 | HarborGen | 230 | 341 | 22511 | 0 | 385250 | 385250 | 0 | 0.122 | 6.411 | 22536.9677 | 3.1668e-07 | 1.6641e-05 | 0.0585 | 17.1139 | 5.4196e-06 | 0.00028479 | 1.0012 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Long Beach Generation LLC | 252 | 260 | 260 | 1.02% | 1 |  | 4 |  | 28.4356 | 32.4384 | 2 | Yes | LA Basin | Western | Yes | 12 | 2 | 1141 | High | In_DAC |  | 4 | 0.56959 | 3 | 0.0058083 | 1 | 2 | NA_Extreme | A | 3 | 2.5 | 66.6667 | 0
|  | YES | HINSON_6_LBECH2 | Long Beach Unit 2 | 63 | 70 | SCE | Long Beach Generation LLC | FTUR | NATURAL GAS | SP15 | 2007-08-01 | HarborGen | 230 | 341 | 22511 | 0 | 385250 | 385250 | 0 | 0.122 | 6.411 | 22536.9677 | 3.1668e-07 | 1.6641e-05 | 0.0585 | 17.1139 | 5.4196e-06 | 0.00028479 | 1.0012 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Long Beach Generation LLC | 252 | 260 | 260 | 1.02% | 1 |  | 4 |  | 28.4356 | 32.4384 | 2 | Yes | LA Basin | Western | Yes | 12 | 2 | 1141 | High | In_DAC |  | 4 | 0.56959 | 3 | 0.0058083 | 1 | 2 | NA_Extreme | A | 3 | 2.5 | 66.6667 | 0
|  | YES | HINSON_6_LBECH3 | Long Beach Unit 3 | 63 | 70 | SCE | Long Beach Generation LLC | FTUR | NATURAL GAS | SP15 | 2007-08-01 | HarborGen | 230 | 341 | 22511 | 0 | 385250 | 385250 | 0 | 0.122 | 6.411 | 22536.9677 | 3.1668e-07 | 1.6641e-05 | 0.0585 | 17.1139 | 5.4196e-06 | 0.00028479 | 1.0012 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Long Beach Generation LLC | 252 | 260 | 260 | 1.02% | 1 |  | 4 |  | 28.4356 | 32.4384 | 2 | Yes | LA Basin | Western | Yes | 12 | 2 | 1141 | High | In_DAC |  | 4 | 0.56959 | 3 | 0.0058083 | 1 | 2 | NA_Extreme | A | 3 | 2.5 | 66.6667 | 0
|  | YES | HINSON_6_LBECH4 | Long Beach Unit 4 | 63 | 70 | SCE | Long Beach Generation LLC | FTUR | NATURAL GAS | SP15 | 2007-08-01 | HarborGen | 230 | 341 | 22511 | 0 | 385250 | 385250 | 0 | 0.122 | 6.411 | 22536.9677 | 3.1668e-07 | 1.6641e-05 | 0.0585 | 17.1139 | 5.4196e-06 | 0.00028479 | 1.0012 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Long Beach Generation LLC | 252 | 260 | 260 | 1.02% | 1 |  | 4 |  | 28.4356 | 32.4384 | 2 | Yes | LA Basin | Western | Yes | 12 | 2 | 1141 | High | In_DAC |  | 4 | 0.56959 | 3 | 0.0058083 | 1 | 2 | NA_Extreme | A | 3 | 2.5 | 66.6667 | 0
|  | YES | YUBACT_1_SUNSWT | YUBA CITY COGEN | 49.97 | 49 | PGAE | Yuba City Cogeneration Partners, L.P. | COMBUSTION TURBINE | NATURAL GAS | NP15 | 1990-12-27 | Pease | 115 | 52186 | 10599 | 7928 | 104566 | 86134 | 18432 | 0.031496 | 17.218 | 6117.0683 | 3.0121e-07 | 0.00016466 | 0.0585 | 8.1266 | 2.4478e-06 | 0.0013381 | 0.4754 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Yuba City Cogen Partners | 49 | 49.97 | 49.97 | 2.469% | 2 |  | 4 |  | 45.0411 | 49.0438 | 4 | Yes | Sierra | Pease, Drum-Rio Oso | Yes | 17 | 2 | 75 | High | DAC_Adjacent | 1.2255 | 3 | 2.6763 | 4 | 0.066084 | 4 | 3 | A | A | 1 | 1 | 66.6667 | 0
|  | YES | AGRICO_6_PL3N5 | Fresno Peaker | 22.69 |  | PGAE | Fresno Cogeneration Partners, LP | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2006-08-30 | Helm | 230 | 10156 | 5887 | 21636 | 117540 | 57438 | 60102 | 0.011 | 0.178 | 6876.042 | 9.3585e-08 | 1.5144e-06 | 0.0585 | 9.7568 | 9.1309e-07 | 1.4775e-05 | 0.57077 | CAISO_Peaker2 | Natural Gas Fired Combined Cycle | Fresno Cogen Partners | 82.6 | 73.29 | 73.29 | 0.8136% | 1 |  | 1 |  | 29.3562 | 33.3589 | 2 | Yes | Fresno | Herndon | Yes | 4 | 3 | 793 | High | In_DAC |  | 4 | 0.029551 | 1 | 0.00024042 | 1 | 1 | NA_Extreme | NA_Moderate | 4 | 4 | 65.625 | 0
|  | YES | CENTER_6_PEAKER | Center Peaker | 47.3 | 59 | SCE | Southern California Edison Company | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2007-09-20 | Center | 230 | 56475 | 14862 | 0 | 180806 | 180806 | 0 | 0.053 | 0.808 | 10577.0772 | 2.9313e-07 | 4.4689e-06 | 0.0585 | 12.1657 | 3.5661e-06 | 5.4367e-05 | 0.71169 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Center Peaker | 59.8 | 47.11 | 47.11 | 2.837% | 2 |  | 3 |  | 28.2986 | 32.3014 | 2 | Yes | LA Basin | Western | Yes | 18 | 2 | 1141 | High | In_DAC |  | 4 | 0.10873 | 2 | 0.0030849 | 1 | 1 | NA_Extreme | NA_Moderate | 4 | 4 | 65.625 | 0
|  | YES | REDBLF_6_UNIT | RED BLUFF PEAKER PLANT | 44 | 44 | PGAE | California Power Holdings, LLC | RECIPROCATING ENGINE | NATURAL GAS | NP15 | 2001-08-11 | Cottonwood | 230 | 56184 | 13845 | 0 | 142989 | 142989 | 0 | 0.042056 | 194.0174 | 8364.7981 | 2.9412e-07 | 0.0013569 | 0.0585 | 10.3278 | 3.0376e-06 | 0.014014 | 0.60417 | CAISO_Reciprocating_Engine | Natural Gas Internal Combustion Engine | Red Bluff | 46.4 | 44 | 44 | 3.406% | 2 |  | 2 |  | 34.411 | 38.4137 | 3 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | Outside_DAC | 39.2705 | 1 | 28.0271 | 4 | 0.95466 | 4 | 4 | A | A | 1 | 1 | 65.625 | 0
|  |  | RVSIDE_6_SPRING | SPRINGS GENERATION PROJECT AGGREGATE | 36 |  | SCE | City of Riverside (MSSA) | FTUR | NATURAL GAS | SP15 | 2002-06-13 | Vista (SCE) | 230 | 56144 | 465 | 0 | 6529 | 6529 | 0 | 0.0018813 | 1.0284 | 381.9438 | 2.8815e-07 | 0.00015752 | 0.0585 | 14.0409 | 4.0458e-06 | 0.0022117 | 0.82138 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Springs Generating Station | 40 | 36 | 36 | 0.1327% | 1 |  | 4 |  | 33.5726 | 37.5753 | 3 | Yes | LA Basin | Eastern | Yes | 34 | 1 | 1141 | High | DAC_Adjacent | 0.31088 | 3 | 4.4234 | 4 | 0.0058701 | 1 | 2 | NA_Extreme | NA_Moderate | 4 | 4 | 65.625 | 1
|  | YES | TIDWTR_2_UNITS | MARTINEZ COGEN LIMITED PARTNERSHIP | 114.8 | 114.8 | PGAE | Martinez Cogen Limited Partnership | FTUR | NATURAL GAS | NP15 | 1987-02-23 | Gill Ranch | 115 | 10342 | 673306 | 1686404 | 7074502 | 4115901 | 2958601 | 2.0423 | 953.0625 | 413855.4785 | 2.8868e-07 | 0.00013472 | 0.0585 | 6.113 | 1.7647e-06 | 0.00082353 | 0.35761 | CAISO_Peaker1 | Natural Gas Fired Combined Cycle | Foster Wheeler Martinez | 113.5 | 11.19 | 8.61 | 67.72% | 4 |  | 2 |  | 48.8849 | 52.8877 | 4 | Yes | Bay Area | Pittsburg | Yes | 10 | 2 | 2220 | High | DAC_Adjacent | 0.48269 | 3 | 1.6471 | 3 | 1.1154 | 4 | 4 | NA_Marginal | A | 1 | 1.25 | 65.625 | 0
|  | YES | GATWAY_2_PL1X3 | GATEWAY GENERATING STATION | 585 |  | PGAE | Pacific Gas & Electric Company | COMBINED CYCLE | NATURAL GAS | NP15 | 2009-01-06 | Contra Costa PP | 230 | 56476 | 2929751 | 0 | 21178639 | 21178639 | 0 | 6.469 | 68.529 | 1238941.7343 | 3.0545e-07 | 3.2358e-06 | 0.0585 | 7.2288 | 2.208e-06 | 2.3391e-05 | 0.42288 | CAISO_CCGT1 | Natural Gas Fired Combined Cycle | Gateway Generating Station | 619.7 | 523.12 | 533.12 | 53.97% | 4 |  | 1 |  | 27 | 31.0027 | 2 | Yes | Bay Area | Contra Costa | No | No Published Factor | 4 | 2220 | High | DAC_Adjacent | 0.80048 | 3 | 0.046781 | 1 | 0.025248 | 3 | 3 | NA_Marginal | A | 1 | 1.25 | 64.5833 | 0
|  |  | WALCRK_2_CTG1 | Walnut Creek Energy Park Unit 1 | 97.32 | 102.5 | SCE | Walnut Creek Energy, LLC | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2013-03-21 | Walnut | 230 | 57515 | 382025 | 0 | 3901517 | 3901517 | 0 | 1.132 | 20.98 | 228237.1515 | 2.9014e-07 | 5.3774e-06 | 0.0585 | 10.2127 | 2.9632e-06 | 5.4918e-05 | 0.59744 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Walnut Creek Energy Park | 500 | 483.13 | 483.13 | 8.722% | 4 |  | 1 |  | 22.7945 | 26.7973 | 1 | Yes | LA Basin | Western | Yes | 12 | 2 | 1141 | High | In_DAC |  | 4 | 0.10984 | 2 | 0.0095799 | 2 | 3 | NA_Extreme | NA_Moderate | 4 | 4 | 64.5833 | 1
|  |  | WALCRK_2_CTG2 | Walnut Creek Energy Park Unit 2 | 96.91 | 102.5 | SCE | Walnut Creek Energy, LLC | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2013-03-21 | Walnut | 230 | 57515 | 382025 | 0 | 3901517 | 3901517 | 0 | 1.132 | 20.98 | 228237.1515 | 2.9014e-07 | 5.3774e-06 | 0.0585 | 10.2127 | 2.9632e-06 | 5.4918e-05 | 0.59744 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Walnut Creek Energy Park | 500 | 483.13 | 483.13 | 8.722% | 4 |  | 1 |  | 22.7945 | 26.7973 | 1 | Yes | LA Basin | Western | Yes | 12 | 2 | 1141 | High | In_DAC |  | 4 | 0.10984 | 2 | 0.0095799 | 2 | 3 | NA_Extreme | NA_Moderate | 4 | 4 | 64.5833 | 1
|  |  | WALCRK_2_CTG3 | Walnut Creek Energy Park Unit 3 | 96.65 | 102.5 | SCE | Walnut Creek Energy, LLC | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2013-03-21 | Walnut | 230 | 57515 | 382025 | 0 | 3901517 | 3901517 | 0 | 1.132 | 20.98 | 228237.1515 | 2.9014e-07 | 5.3774e-06 | 0.0585 | 10.2127 | 2.9632e-06 | 5.4918e-05 | 0.59744 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Walnut Creek Energy Park | 500 | 483.13 | 483.13 | 8.722% | 4 |  | 1 |  | 22.7945 | 26.7973 | 1 | Yes | LA Basin | Western | Yes | 12 | 2 | 1141 | High | In_DAC |  | 4 | 0.10984 | 2 | 0.0095799 | 2 | 3 | NA_Extreme | NA_Moderate | 4 | 4 | 64.5833 | 1
|  |  | WALCRK_2_CTG4 | Walnut Creek Energy Park Unit 4 | 96.6 | 102.5 | SCE | Walnut Creek Energy, LLC | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2013-03-29 | Walnut | 230 | 57515 | 382025 | 0 | 3901517 | 3901517 | 0 | 1.132 | 20.98 | 228237.1515 | 2.9014e-07 | 5.3774e-06 | 0.0585 | 10.2127 | 2.9632e-06 | 5.4918e-05 | 0.59744 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Walnut Creek Energy Park | 500 | 483.13 | 483.13 | 8.722% | 4 |  | 1 |  | 22.7726 | 26.7753 | 1 | Yes | LA Basin | Western | Yes | 12 | 2 | 1141 | High | In_DAC |  | 4 | 0.10984 | 2 | 0.0095799 | 2 | 3 | NA_Extreme | NA_Moderate | 4 | 4 | 64.5833 | 1
|  |  | WALCRK_2_CTG5 | Walnut Creek Energy Park Unit 5 | 96.65 | 102.5 | SCE | Walnut Creek Energy, LLC | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2013-04-30 | Walnut | 230 | 57515 | 382025 | 0 | 3901517 | 3901517 | 0 | 1.132 | 20.98 | 228237.1515 | 2.9014e-07 | 5.3774e-06 | 0.0585 | 10.2127 | 2.9632e-06 | 5.4918e-05 | 0.59744 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Walnut Creek Energy Park | 500 | 483.13 | 483.13 | 8.722% | 4 |  | 1 |  | 22.6849 | 26.6877 | 1 | Yes | LA Basin | Western | Yes | 12 | 2 | 1141 | High | In_DAC |  | 4 | 0.10984 | 2 | 0.0095799 | 2 | 3 | NA_Extreme | NA_Moderate | 4 | 4 | 64.5833 | 1
|  | YES | YUBACT_6_UNITA1 | Yuba City Energy Center (Calpine) | 47.16 | 49.9 | PGAE | Gilroy Energy Center, LLC | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2002-07-26 | Pease | 115 | 55813 | 32148 | 0 | 374248 | 374248 | 0 | 0.11375 | 62.1852 | 21893.3552 | 3.0395e-07 | 0.00016616 | 0.0585 | 11.6414 | 3.5384e-06 | 0.0019343 | 0.68102 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Yuba City Energy Center | 47.3 | 47.6 | 47.6 | 7.759% | 4 |  | 3 |  | 33.4548 | 37.4575 | 3 | Yes | Sierra | Pease, Drum-Rio Oso | Yes | 17 | 2 | 75 | High | DAC_Adjacent | 1.2684 | 3 | 3.8687 | 4 | 0.30016 | 4 | 4 | A | A | 1 | 1 | 64.5833 | 0
|  |  | HNTGBH_2_PL1X3 | Huntington Beach Energy | 673.8 |  | SCE | AES Huntington Beach Energy LLC | COMBINED CYCLE | NATURAL GAS | SP15 | 2020-02-04 | Huntington Beach | 230 | 335 | 319522 | 0 | 3685102 | 3685102 | 0 | 1.122 | 25.272 | 215576.9624 | 3.0447e-07 | 6.8579e-06 | 0.0585 | 11.5332 | 3.5115e-06 | 7.9093e-05 | 0.67469 | CAISO_CCGT2 | Natural Gas Steam Turbine | AES Huntington Beach LLC | 218 | 899.6 | 899.6 | 16.73% | 2 |  | 2.5 |  | 15.9151 | 19.9178 | 1 | Yes | LA Basin | Western | Yes | 16 | 2 | 1141 | High | DAC_Adjacent | 2.3814 | 3 | 0.15819 | 3 | Not Available | 2.5 | 2.5 | NA_Extreme | NA_Moderate | 4 | 4 | 63.0208 | 1
|  |  | ALAMIT_2_PL1X3 | Alamitos Energy Center Unit 7 | 674.7 |  | SCE | AES Alamitos Energy LLC | COMBINED CYCLE | NATURAL GAS | SP15 | 2020-02-06 | Alamitos | 230 | 315 | 958300 | 0 | 12353001 | 12353001 | 0 | 3.817 | 49.845 | 722645.5148 | 3.0899e-07 | 4.0351e-06 | 0.0585 | 12.8905 | 3.9831e-06 | 5.2014e-05 | 0.75409 | CAISO_CCGT2 | Natural Gas Steam Turbine | AES Alamitos LLC | 1115 | 1840.52 | 1840.52 | 9.811% | 1 |  | 2.5 |  | 15.9096 | 19.9123 | 1 | Yes | LA Basin | Western | Yes | 12 | 2 | 1141 | High | DAC_Adjacent | 3.5308 | 3 | 0.10403 | 2 | Not Available | 2.5 | 2.5 | NA_Extreme | NA_Moderate | 4 | 4 | 63.0208 | 1
|  | YES | INDIGO_1_UNIT 1 | INDIGO PEAKER UNIT 1 | 45.3 | 45.3 | SCE | Wildflower Energy LP | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2001-09-19 | Devers | 500 | 55541 | 33376 | 0 | 358256 | 358256 | 0 | 0.107 | 3.955 | 20957.8297 | 2.9867e-07 | 1.104e-05 | 0.0585 | 10.7339 | 3.2059e-06 | 0.0001185 | 0.62793 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Indigo Energy Facility | 149.7 | 126 | 126 | 2.545% | 2 |  | 2 |  | 34.3041 | 38.3068 | 3 | Yes | LA Basin | Eastern, Valley-Devers | No | No Published Factor | 4 | 1141 | High | Outside_DAC | 25.2861 | 1 | 0.237 | 3 | 0.0060319 | 2 | 2 | NA_Severe 15 | A | 3 | 2.25 | 62.5 | 0
|  | YES | INDIGO_1_UNIT 2 | INDIGO PEAKER UNIT 2 | 45.3 | 45.3 | SCE | Wildflower Energy LP | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2001-09-19 | Devers | 500 | 55541 | 33376 | 0 | 358256 | 358256 | 0 | 0.107 | 3.955 | 20957.8297 | 2.9867e-07 | 1.104e-05 | 0.0585 | 10.7339 | 3.2059e-06 | 0.0001185 | 0.62793 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Indigo Energy Facility | 149.7 | 126 | 126 | 2.545% | 2 |  | 2 |  | 34.3041 | 38.3068 | 3 | Yes | LA Basin | Eastern, Valley-Devers | No | No Published Factor | 4 | 1141 | High | Outside_DAC | 25.2861 | 1 | 0.237 | 3 | 0.0060319 | 2 | 2 | NA_Severe 15 | A | 3 | 2.25 | 62.5 | 0
|  | YES | INDIGO_1_UNIT 3 | INDIGO PEAKER UNIT 3 | 45.3 | 45.3 | SCE | Wildflower Energy LP | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2001-09-19 | Devers | 500 | 55541 | 33376 | 0 | 358256 | 358256 | 0 | 0.107 | 3.955 | 20957.8297 | 2.9867e-07 | 1.104e-05 | 0.0585 | 10.7339 | 3.2059e-06 | 0.0001185 | 0.62793 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Indigo Energy Facility | 149.7 | 126 | 126 | 2.545% | 2 |  | 2 |  | 34.3041 | 38.3068 | 3 | Yes | LA Basin | Eastern, Valley-Devers | No | No Published Factor | 4 | 1141 | High | Outside_DAC | 25.2861 | 1 | 0.237 | 3 | 0.0060319 | 2 | 2 | NA_Severe 15 | A | 3 | 2.25 | 62.5 | 0
|  |  | COCOPP_2_CTG1 | Marsh Landing 1 | 204.2 | 222 | PGAE | Marsh Landing LLC | FTUR | NATURAL GAS | NP15 | 2013-05-01 | Contra Costa PP | 230 | 57267 | 219407 | 0 | 2538590 | 2538590 | 0 | 0.776 | 9.163 | 148506.4785 | 3.0568e-07 | 3.6095e-06 | 0.0585 | 11.5702 | 3.5368e-06 | 4.1763e-05 | 0.67685 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Marsh Landing Generating Station | 828 | 757.6 | 764.2 | 3.025% | 2 |  | 4 |  | 22.6822 | 26.6849 | 1 | Yes | Bay Area | Contra Costa | No | No Published Factor | 4 | 2220 | High | DAC_Adjacent | 1.123 | 3 | 0.083525 | 1 | 0.0025266 | 1 | 1 | NA_Marginal | A | 1 | 1.25 | 62.5 | 1
|  |  | COCOPP_2_CTG2 | Marsh Landing 2 | 202.7 | 222 | PGAE | Marsh Landing LLC | FTUR | NATURAL GAS | NP15 | 2013-05-01 | Contra Costa PP | 230 | 57267 | 219407 | 0 | 2538590 | 2538590 | 0 | 0.776 | 9.163 | 148506.4785 | 3.0568e-07 | 3.6095e-06 | 0.0585 | 11.5702 | 3.5368e-06 | 4.1763e-05 | 0.67685 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Marsh Landing Generating Station | 828 | 757.6 | 764.2 | 3.025% | 2 |  | 4 |  | 22.6822 | 26.6849 | 1 | Yes | Bay Area | Contra Costa | No | No Published Factor | 4 | 2220 | High | DAC_Adjacent | 1.123 | 3 | 0.083525 | 1 | 0.0025266 | 1 | 1 | NA_Marginal | A | 1 | 1.25 | 62.5 | 1
|  |  | COCOPP_2_CTG3 | Marsh Landing 3 | 208.96 | 222 | PGAE | Marsh Landing LLC | FTUR | NATURAL GAS | NP15 | 2013-05-01 | Contra Costa PP | 230 | 57267 | 219407 | 0 | 2538590 | 2538590 | 0 | 0.776 | 9.163 | 148506.4785 | 3.0568e-07 | 3.6095e-06 | 0.0585 | 11.5702 | 3.5368e-06 | 4.1763e-05 | 0.67685 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Marsh Landing Generating Station | 828 | 757.6 | 764.2 | 3.025% | 2 |  | 4 |  | 22.6822 | 26.6849 | 1 | Yes | Bay Area | Contra Costa | No | No Published Factor | 4 | 2220 | High | DAC_Adjacent | 1.123 | 3 | 0.083525 | 1 | 0.0025266 | 1 | 1 | NA_Marginal | A | 1 | 1.25 | 62.5 | 1
|  |  | COCOPP_2_CTG4 | Marsh Landing 4 | 204.29 | 222 | PGAE | Marsh Landing LLC | FTUR | NATURAL GAS | NP15 | 2013-05-01 | Contra Costa PP | 230 | 57267 | 219407 | 0 | 2538590 | 2538590 | 0 | 0.776 | 9.163 | 148506.4785 | 3.0568e-07 | 3.6095e-06 | 0.0585 | 11.5702 | 3.5368e-06 | 4.1763e-05 | 0.67685 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Marsh Landing Generating Station | 828 | 757.6 | 764.2 | 3.025% | 2 |  | 4 |  | 22.6822 | 26.6849 | 1 | Yes | Bay Area | Contra Costa | No | No Published Factor | 4 | 2220 | High | DAC_Adjacent | 1.123 | 3 | 0.083525 | 1 | 0.0025266 | 1 | 1 | NA_Marginal | A | 1 | 1.25 | 62.5 | 1
|  |  | MRCHNT_2_PL1X3 | Desert Star Energy Center | 494.58 |  | SCE | San Diego Gas & Electric Company | COMBINED CYCLE | NATURAL GAS | SP15 | 2012-06-18 | Eldorado | 230 | 55077 | 1659922 | 0 | 12788899 | 12788899 | 0 | 3.791 | 82.529 | 748145.3698 | 2.9643e-07 | 6.4532e-06 | 0.0585 | 7.7045 | 2.2838e-06 | 4.9719e-05 | 0.45071 | CAISO_CCGT1 | Natural Gas Fired Combined Cycle | Desert Star Energy Center | 536 | 419.25 | 419.25 | 35.35% | 3 |  | 3 |  | 23.5507 | 27.5534 | 1 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | Outside_DAC | 8229.8474 | 1 | 0.099437 | 1 | 0.035153 | 3 | 4 | A | A | 1 | 1 | 62.5 | 1
|  |  | MALAGA_1_PL1X2 | Malaga Power Aggregate | 96.61 |  | PGAE | Malaga Power, LLC | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2005-09-19 | West Fresno | 115 | 56239 | 27660 | 0 | 287868 | 287868 | 0 | 0.088 | 2.32 | 16840.1605 | 3.057e-07 | 8.0592e-06 | 0.0585 | 10.4074 | 3.1815e-06 | 8.3876e-05 | 0.60883 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Malaga Power LLC | 121 | 96 | 96 | 2.61% | 2 |  | 2 |  | 30.3014 | 34.3041 | 2 | Yes | Fresno | Herndon | Yes | 19 | 2 | 793 | High | In_DAC |  | 4 | 0.16775 | 3 | 0.0043775 | 1 | 1 | NA_Extreme | NA_Moderate | 4 | 4 | 62.5 | 0
|  |  | AGRICO_7_UNIT | Fresno Cogen | 50.6 |  | PGAE | Fresno Cogeneration Partners, LP | OTHER | NATURAL GAS | NP15 | 2023-03-14 | Helm | 230 | 10156 | 5887 | 21636 | 117540 | 57438 | 60102 | 0.011 | 0.178 | 6876.042 | 9.3585e-08 | 1.5144e-06 | 0.0585 | 9.7568 | 9.1309e-07 | 1.4775e-05 | 0.57077 | CAISO_Peaker2 | Natural Gas Fired Combined Cycle | Fresno Cogen Partners | 82.6 | 73.29 | 73.29 | 0.8136% | 1 |  | 1 |  | 12.8082 | 16.811 | 1 | Yes | Fresno | Herndon | Yes | 4 | 3 | 793 | High | In_DAC |  | 4 | 0.029551 | 1 | 0.00024042 | 1 | 1 | NA_Extreme | NA_Moderate | 4 | 4 | 62.5 | 1
|  |  | LMBEPK_2_UNITA1 | Lambie Energy Center, Unit #1 | 47.5 | 49.9 | PGAE | Gilroy Energy Center, LLC | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2003-01-06 | Lambie | 230 | 55626 | 13299 | 0 | 157496 | 157496 | 0 | 0.049 | 1.595 | 9213.4517 | 3.1112e-07 | 1.0127e-05 | 0.0585 | 11.8427 | 3.6845e-06 | 0.00011993 | 0.69279 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Lambie Energy Center | 47 | 47.5 | 47.5 | 3.23% | 2 |  | 3 |  | 33.0055 | 37.0082 | 3 | Yes | Bay Area | Contra Costa | No | No Published Factor | 4 | 2220 | High | Outside_DAC | 10.7271 | 1 | 0.23987 | 3 | 0.007748 | 2 | 2 | NA_Marginal | A | 1 | 1.25 | 61.4583 | 0
|  |  | LMBEPK_2_UNITA2 | Creed Energy Center, Unit #1 | 47.6 | 49.9 | PGAE | Creed Energy Facility, LLC | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2003-01-06 | Lambie | 230 | 55625 | 12968 | 0 | 152402 | 152402 | 0 | 0.051 | 1.612 | 8915.4548 | 3.3464e-07 | 1.0577e-05 | 0.0585 | 11.7522 | 3.9328e-06 | 0.00012431 | 0.6875 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Creed Energy Center | 47 | 47.6 | 47.6 | 3.15% | 2 |  | 3 |  | 33.0055 | 37.0082 | 3 | Yes | Bay Area | Contra Costa | No | No Published Factor | 4 | 2220 | High | Outside_DAC | 12.149 | 1 | 0.24861 | 3 | 0.0078306 | 2 | 2 | NA_Marginal | A | 1 | 1.25 | 61.4583 | 0
|  |  | LMBEPK_2_UNITA3 | Goose Haven Energy Center, Unit #1 | 47.75 | 49.9 | PGAE | Goose Haven Energy Center, LLC | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2003-01-06 | Lambie | 230 | 55627 | 12447 | 0 | 147470 | 147470 | 0 | 0.045 | 1.528 | 8626.9348 | 3.0515e-07 | 1.0361e-05 | 0.0585 | 11.8478 | 3.6153e-06 | 0.00012276 | 0.69309 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Goose Haven Energy Center | 47 | 47.4 | 47.4 | 3.023% | 2 |  | 3 |  | 33.0055 | 37.0082 | 3 | Yes | Bay Area | Contra Costa | No | No Published Factor | 4 | 2220 | High | Outside_DAC | 11.1521 | 1 | 0.24552 | 3 | 0.0074225 | 2 | 2 | NA_Marginal | A | 1 | 1.25 | 61.4583 | 0
|  |  | LECEF_1_UNITS | LOS ESTEROS ENERGY FACILITY AGGREGATE | 309.84 |  | PGAE | Los Esteros Critical Energy Facility, LLC | COMBINED CYCLE | NATURAL GAS | NP15 | 2013-07-31 | Los Esteros | 115 | 55748 | 356431 | 0 | 3006451 | 3006451 | 0 | 0.899 | 8.822 | 175876.156 | 2.9902e-07 | 2.9344e-06 | 0.0585 | 8.4349 | 2.5222e-06 | 2.4751e-05 | 0.49344 | CAISO_CCGT2 | Natural Gas Fired Combined Cycle | Los Esteros Critical Energy Center | 306.1 | 297.54 | 304 | 13.29% | 2 |  | 3 |  | 22.4329 | 26.4356 | 1 | Yes | Bay Area | San Jose, South Bay-Moss Landing | Yes | 7 | 3 | 2220 | High | In_DAC |  | 4 | 0.049502 | 1 | 0.0065801 | 2 | 2 | NA_Marginal | A | 1 | 1.25 | 61.4583 | 1
|  |  | RUSCTY_2_UNITS | Russell City Energy Center | 615.18 |  | PGAE | Russell City Energy Company, LLC | COMBINED CYCLE | NATURAL GAS | NP15 | 2013-08-08 | East Shore | 230 | 56467 | 1010425 | 0 | 7578352 | 7578352 | 0 | 2.221 | 27.581 | 443330.4978 | 2.9307e-07 | 3.6394e-06 | 0.0585 | 7.5002 | 2.1981e-06 | 2.7296e-05 | 0.43876 | CAISO_CCGT1 | Natural Gas Fired Combined Cycle | Russell City Energy Center | 655 | 597.4 | 613.22 | 17.61% | 2 |  | 3 |  | 22.411 | 26.4137 | 1 | Yes | Bay Area | Ames | Yes | 4 | 3 | 2220 | High | In_DAC |  | 4 | 0.054593 | 1 | 0.0096138 | 3 | 2 | NA_Marginal | A | 1 | 1.25 | 61.4583 | 1
|  |  | DELTA_2_PL1X4 | DELTA ENERGY CENTER AGGREGATE | 880 |  | PGAE | Delta Energy Center, LLC | COMBINED CYCLE | NATURAL GAS | NP15 | 2002-06-17 | Delta EC | 230 | 55333 | 3081664 | 0 | 22825752 | 22825752 | 0 | 6.622 | 83.957 | 1335297.1722 | 2.9011e-07 | 3.6782e-06 | 0.0585 | 7.407 | 2.1488e-06 | 2.7244e-05 | 0.4333 | CAISO_CCGT1 | Natural Gas Fired Combined Cycle | Delta Energy Center | 943.5 | 813 | 813 | 37.29% | 3 |  | 2 |  | 33.5616 | 37.5644 | 4 | Yes | Bay Area | Pittsburg | Yes | 15 | 2 | 2220 | High | In_DAC |  | 4 | 0.054488 | 1 | 0.020316 | 3 | 2 | NA_Marginal | A | 1 | 1.25 | 61.4583 | 0
|  |  | GLNARM_2_UNIT 5 | Glenarm Turbine 5 | 65.81 | 71 | SCE | City of Pasadena | COMBINED CYCLE | NATURAL GAS | SP15 | 2016-12-20 | Gould | 230 | 422 | 107233.32 | 0 | 1166292 | 1166292 | 0 | 0.235 | 7.321 | 68227.6058 | 2.0149e-07 | 6.2772e-06 | 0.0585 | 10.8762 | 2.1915e-06 | 6.8272e-05 | 0.63625 | CAISO_CCGT2 | Natural Gas Fired Combustion Turbine | Glenarm | 265.6 | 196.62 | 196.62 | 4.609% | 1 |  | 4 |  | 19.0411 | 23.0438 | 1 | Yes | LA Basin | Western | Yes | 10 | 2 | 1141 | High | DAC_Adjacent | 1.863 | 3 | 0.13654 | 2 | 0.0062932 | 2 | 1 | NA_Extreme | NA_Moderate | 4 | 4 | 61.4583 | 1
|  |  | UNOCAL_1_UNITS | TOSCO (RODEO PLANT) | 49.85 | 57.3 | PGAE | Pacific Gas & Electric Company | FTUR | NATURAL GAS | NP15 | 1987-05-21 | Christie | 115 | 50119 | 390019 | 4046579 | 6966279 | 1778356 | 5187923 | 1.7979 | 855.2419 | 122675.5158 | 2.5809e-07 | 0.00012277 | 0.01761 | 4.5597 | 1.1768e-06 | 0.00055978 | 0.080295 | CAISO_Peaker1 | Other Gases | Phillips 66 Rodeo Refinery | 54.9 | 0.07 | 0.31 | 81.1% | 4 |  | 1 |  | 48.6466 | 52.6493 | 4 | Yes | Bay Area | Pittsburg | Yes | 23 | 1 | 2220 | High | In_DAC |  | 4 | 1.1196 | 3 | 0.90795 | 4 | 4 | NA_Marginal | A | 1 | 1.25 | 60.4167 | 1
|  |  | LODIEC_2_PL1X2 | Lodi Energy Center | 302.58 |  | PGAE | Northern California Power Agency - Lodi Energy Center | COMBINED CYCLE | NATURAL GAS | NP15 | 2012-11-27 | Eight Mile | 230 | 57978 | 1406540 | 0 | 9981568 | 9981568 | 0 | 2.994 | 29.301 | 583917.6525 | 2.9995e-07 | 2.9355e-06 | 0.0585 | 7.0965 | 2.1286e-06 | 2.0832e-05 | 0.41514 | CAISO_CCGT1 | Natural Gas Fired Combined Cycle | Lodi Energy Center | 288.9 | 302.58 | 302.58 | 55.58% | 4 |  | 1 |  | 23.1068 | 27.1096 | 1 | Yes | Sierra | South of Rio Oso, South of Palermo | Yes | 14 | 2 | 75 | Low | DAC_Adjacent | 3.0715 | 3 | 0.041664 | 1 | 0.023156 | 3 | 3 | NA_Extreme | NA_Moderate | 4 | 4 | 60.4167 | 1
|  |  | GOLETA_6_EXGEN | EXXON COMPANY USA | 48.2 | 48.2 | SCE | SOUTHERN CALIFORNIA EDISON COMPANY |  | OTHER | SP15 | 1993-08-19 | Goleta | 230 | 50270 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | CAISO_Peaker1 | Natural Gas Fired Combined Cycle | EXXON COMPANY USA | 49.3 | 0 | 0 | 0% | 1 |  | 1 |  | 42.3945 | 46.3973 | 4 | Yes | BC/Ventura | S.Clara, Moorpark, Goleta | No | No Published Factor | 4 | 657 | High | Outside_DAC | 52.172 | 1 | Not Available | 2.4 | Not Available | 2.5 | 2.5 | A | A | 1 | 1 | 59.375 | 0
|  |  | HUMBPP_1_UNITS3 | Humboldt Bay Generating Station 3 | 65.08 | 83.2 | PGAE | Pacific Gas & Electric Company | RECIPROCATING ENGINE | NATURAL GAS | NP15 | 2010-09-29 | Wildwood Solar | 115 | 246 | 383862 | 0 | 3372675 | 3372675 | 0 | 3.1393 | 4488.9529 | 197650.2736 | 9.3082e-07 | 0.001331 | 0.058603 | 8.7862 | 8.1783e-06 | 0.011694 | 0.5149 | CAISO_Reciprocating_Engine | Natural Gas Internal Combustion Engine | Humboldt Bay | 167 | 162.7 | 162.7 | 26.24% | 4 |  | 1 |  | 25.2712 | 29.274 | 2 | Yes | Humboldt | 0 | No | No Published Factor | 4 | 19 | Low | Outside_DAC | 178.208 | 1 | 23.3884 | 4 | 6.137 | 4 | 4 | A | A | 1 | 1 | 59.375 | 0
|  |  | HUMBPP_6_UNITS | Humboldt Bay Generating Station 1 | 97.62 |  | PGAE | Pacific Gas & Electric Company | RECIPROCATING ENGINE | NATURAL GAS | NP15 | 2010-09-29 | Wildwood Solar | 115 | 246 | 383862 | 0 | 3372675 | 3372675 | 0 | 3.1393 | 4488.9529 | 197650.2736 | 9.3082e-07 | 0.001331 | 0.058603 | 8.7862 | 8.1783e-06 | 0.011694 | 0.5149 | CAISO_Reciprocating_Engine | Natural Gas Internal Combustion Engine | Humboldt Bay | 167 | 162.7 | 162.7 | 26.24% | 4 |  | 1 |  | 25.2712 | 29.274 | 2 | Yes | Humboldt | 0 | No | No Published Factor | 4 | 19 | Low | Outside_DAC | 178.208 | 1 | 23.3884 | 4 | 6.137 | 4 | 4 | A | A | 1 | 1 | 59.375 | 0
|  |  | VACADX_1_UNITA1 | CalPeak Power Vaca Dixon Unit 1 | 51.91 | 57 | PGAE | CalPeak Power - Vaca-Dixon LLC | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2002-06-21 | Vaca Dixon | 500 | 55499 | 11340 | 0 | 124887 | 124887 | 0 | 0.035 | 0.628 | 7305.8385 | 2.8025e-07 | 5.0285e-06 | 0.0585 | 11.013 | 3.0864e-06 | 5.5379e-05 | 0.64425 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | CalPeak Power Vaca Dixon Peaker Plant | 60.5 | 50.61 | 50.61 | 2.14% | 1 |  | 3 |  | 33.5507 | 37.5534 | 3 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | Outside_DAC | 23.3294 | 1 | 0.11076 | 2 | 0.0023699 | 1 | 1 | NA_Moderate | A | 2 | 1.5 | 58.3333 | 0
|  |  | STIGCT_2_LODI | LODI STIG UNIT | 49.9 | 51.2 | PGAE | NCPA (MSS Agreement - S14) | COMBUSTION TURBINE | NATURAL GAS | NP15 | 1996-01-01 | Eight Mile | 230 | 7449 | 11838 | 0 | 111717 | 111717 | 0 | 0.033 | 0.913 | 6535.3989 | 2.9539e-07 | 8.1724e-06 | 0.0585 | 9.4372 | 2.7876e-06 | 7.7125e-05 | 0.55207 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Combustion Turbine Project No 2 | 50 | 49.5 | 49.5 | 2.703% | 2 |  | 1 |  | 40.0247 | 44.0274 | 3 | Yes | Sierra | South of Rio Oso, South of Palermo | Yes | 14 | 2 | 75 | High | DAC_Adjacent | 3.0931 | 3 | 0.15425 | 3 | 0.0041689 | 1 | 1 | NA_Extreme | NA_Moderate | 4 | 4 | 58.3333 | 0
|  |  | WOLFSK_1_UNITA1 | Wolfskill Energy Center | 48.68 | 49.9 | PGAE | Gilroy Energy Center, LLC | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2003-03-22 | Peabody | 230 | 55855 | 9388 | 0 | 111140 | 111140 | 0 | 0.035 | 0.919 | 6501.6446 | 3.1492e-07 | 8.2689e-06 | 0.0585 | 11.8385 | 3.7282e-06 | 9.7891e-05 | 0.69255 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Wolfskill Energy Center | 47 | 46.9 | 46.9 | 2.28% | 2 |  | 3 |  | 32.8 | 36.8027 | 3 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | Outside_DAC | 11.2239 | 1 | 0.19578 | 3 | 0.0044642 | 1 | 1 | NA_Marginal | A | 1 | 1.25 | 57.2917 | 0
|  |  | GILROY_1_UNIT | GILROY COGEN AGGREGATE | 120 |  | PGAE | Calpine Gilroy Cogen, L.P. | COMBINED CYCLE | NATURAL GAS | NP15 | 1987-01-01 | Llagas | 115 | 10034 | 102682 | 57166 | 915492 | 791214 | 124278 | 0.266 | 10.354 | 53555.9082 | 2.9055e-07 | 1.131e-05 | 0.0585 | 7.7055 | 2.2389e-06 | 8.7147e-05 | 0.45077 | CAISO_Peaker1 | Natural Gas Fired Combined Cycle | Gilroy Power Plant | 130 | 105 | 110 | 9.017% | 4 |  | 1 |  | 49.0301 | 53.0329 | 4 | Yes | Bay Area | Llagas, San Jose, South Bay-Moss Landing | Yes | 56 | 1 | 2220 | High | In_DAC |  | 4 | 0.17429 | 3 | 0.015716 | 3 | 3 | NA_Marginal | A | 1 | 1.25 | 56.25 | 1
|  |  | GILRPP_1_PL1X2 | GILROY ENERGY CENTER UNITS 1&2 AGGREGATE | 95.2 |  | PGAE | Gilroy Energy Center, LLC | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2002-01-29 | Llagas | 115 | 55810 | 25659 | 0 | 304435 | 304435 | 0 | 0.093 | 4.683 | 17809.3232 | 3.0548e-07 | 1.5383e-05 | 0.0585 | 11.8646 | 3.6245e-06 | 0.00018251 | 0.69408 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Gilroy Peaking Energy Center | 135 | 141.4 | 141.4 | 2.17% | 2 |  | 3 |  | 33.9425 | 37.9452 | 3 | Yes | Bay Area | Llagas, San Jose, South Bay-Moss Landing | Yes | 56 | 1 | 2220 | High | In_DAC |  | 4 | 0.36502 | 3 | 0.0079198 | 2 | 2 | NA_Marginal | A | 1 | 1.25 | 55.2083 | 1
|  |  | GILRPP_1_PL3X4 | GILROY ENERGY CENTER, UNIT #3 | 46.2 | 49.9 | PGAE | Gilroy Energy Center, LLC | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2002-02-28 | Llagas | 115 | 55810 | 25659 | 0 | 304435 | 304435 | 0 | 0.093 | 4.683 | 17809.3232 | 3.0548e-07 | 1.5383e-05 | 0.0585 | 11.8646 | 3.6245e-06 | 0.00018251 | 0.69408 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Gilroy Peaking Energy Center | 135 | 141.4 | 141.4 | 2.17% | 2 |  | 3 |  | 33.8603 | 37.863 | 3 | Yes | Bay Area | Llagas, San Jose, South Bay-Moss Landing | Yes | 56 | 1 | 2220 | High | In_DAC |  | 4 | 0.36502 | 3 | 0.0079198 | 2 | 2 | NA_Marginal | A | 1 | 1.25 | 55.2083 | 1
|  |  | GRNLF1_1_PL1X2 | Greenleaf 1 | 60 |  | PGAE | Calpine Greenleaf Holdings, Inc. | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2022-06-24 | Pease | 115 | 10350 | 67014 | 28766 | 596062 | 530684 | 65378 | 0.161 | 29.759 | 34869.3836 | 2.7011e-07 | 4.9926e-05 | 0.0585 | 7.919 | 2.139e-06 | 0.00039536 | 0.46326 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Greenleaf 1 Power Plant | 0 | 0 | 0 | Not Available | 2.5 |  | 1 |  | 13.5288 | 17.5315 | 1 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | DAC_Adjacent | 6.5243 | 2 | 0.79073 | 3 | Not Available | 2.5 | 2.5 | A | A | 1 | 1 | 54.1667 | 1
|  |  | BASICE_2_UNITS | King City Cogen | 120 | 120 | PGAE | Calpine King City Cogen | COMBINED CYCLE | NATURAL GAS | NP15 | 1989-03-14 | Coburn | 230 | 10294 | 374693 | 121100 | 3208606 | 2939494 | 269112 | 0.029 | 0.656 | 187702.1409 | 9.0382e-09 | 2.0445e-07 | 0.0585 | 7.8451 | 7.0905e-08 | 1.6039e-06 | 0.45893 | CAISO_Peaker1 | Natural Gas Fired Combined Cycle | King City Power Plant | 133.2 | 0 | 0 | 32.11% | 4 |  | 1 |  | 46.8301 | 50.8329 | 4 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | Outside_DAC | 36.7292 | 1 | 0.0032079 | 1 | 0.0010301 | 1 | 1 | A | A | 1 | 1 | 53.125 | 0
|  |  | MOSSLD_2_PSP1 | MOSS LANDING POWER BLOCK 1 | 510 |  | PGAE | Moss Landing Power Company LLC | COMBINED CYCLE | NATURAL GAS | NP15 | 2002-07-01 | Moss Landing | 115 | 260 | 4178781.84 | 0 | 29433380 | 29433380 | 0 | 9.117 | 126.327 | 1721840.7124 | 3.0975e-07 | 4.292e-06 | 0.0585 | 7.0435 | 2.1817e-06 | 3.0231e-05 | 0.41204 | CAISO_CCGT1 | Natural Gas Fired Combined Cycle | Dynegy Moss Landing Power Plant | 1398 | 1020 | 1020 | 34.12% | 3 |  | 1 |  | 33.5233 | 37.526 | 4 | Yes | Bay Area | South Bay-Moss Landing | Yes | 20 | 2 | 2220 | High | DAC_Adjacent | 1.5306 | 3 | 0.060461 | 1 | 0.020631 | 3 | 2 | A | A | 1 | 1 | 53.125 | 0
|  |  | MOSSLD_2_PSP2 | MOSS LANDING POWER BLOCK 2 | 510 |  | PGAE | Moss Landing Power Company LLC | COMBINED CYCLE | NATURAL GAS | NP15 | 2002-07-11 | Moss Landing | 115 | 260 | 4178781.84 | 0 | 29433380 | 29433380 | 0 | 9.117 | 126.327 | 1721840.7124 | 3.0975e-07 | 4.292e-06 | 0.0585 | 7.0435 | 2.1817e-06 | 3.0231e-05 | 0.41204 | CAISO_CCGT1 | Natural Gas Fired Combined Cycle | Dynegy Moss Landing Power Plant | 1398 | 1020 | 1020 | 34.12% | 3 |  | 1 |  | 33.4959 | 37.4986 | 4 | Yes | Bay Area | South Bay-Moss Landing | Yes | 20 | 2 | 2220 | High | DAC_Adjacent | 1.5306 | 3 | 0.060461 | 1 | 0.020631 | 3 | 2 | A | A | 1 | 1 | 53.125 | 0
|  |  | ELCAJN_6_UNITA1 | Cuyamaca Peak Energy Plant | 45.42 | 48 | SDGE | San Diego Gas & Electric | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2002-05-29 | Santee | 115 | 55512 | 14888 | 0 | 170558 | 170558 | 0 | 0.051 | 0.945 | 9977.5734 | 2.9902e-07 | 5.5406e-06 | 0.0585 | 11.4561 | 3.4256e-06 | 6.3474e-05 | 0.67018 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Cuyamaca Peak Energy Plant | 48.7 | 45.42 | 45.42 | 3.49% | 2 |  | 3 |  | 33.6137 | 37.6164 | 3 | Yes | SD-IV | San Diego, El Cajon | Yes | 22 | 1 | 920 | High | In_DAC |  | 4 | 0.12695 | 2 | 0.0044303 | 1 | 1 | NA_Moderate | A | 2 | 1.5 | 52.0833 | 1
|  |  | COLUSA_2_PL1X3 | Colusa Generating Station | 641 |  | PGAE | Pacific Gas & Electric Company | COMBINED CYCLE | NATURAL GAS | NP15 | 2010-12-22 | Delevan | 230 | 56532 | 2986301 | 0 | 21621556 | 21621556 | 0 | 6.468 | 42.666 | 1264852.1979 | 2.9915e-07 | 1.9733e-06 | 0.0585 | 7.2402 | 2.1659e-06 | 1.4287e-05 | 0.42355 | CAISO_CCGT1 | Natural Gas Fired Combined Cycle | Colusa Generating Station | 712.4 | 594.94 | 607.51 | 47.85% | 4 |  | 1 |  | 25.0411 | 29.0438 | 2 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | Outside_DAC | 38.9593 | 1 | 0.028574 | 1 | 0.013674 | 3 | 2 | A | A | 1 | 1 | 51.0417 | 0
|  |  | BORDER_6_UNITA1 | CalPeak Power Border Unit 1 | 51.25 | 52 | SDGE | CalPeak Power - Border LLC | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2001-10-26 | Otay Mesa | 230 | 55510 | 11381 | 0 | 126107 | 126107 | 0 | 0.036 | 0.701 | 7377.208 | 2.8547e-07 | 5.5588e-06 | 0.0585 | 11.0805 | 3.1632e-06 | 6.1594e-05 | 0.6482 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | CalPeak Power Border Peaker Plant | 60.5 | 51.25 | 51.25 | 2.147% | 2 |  | 3 |  | 34.2027 | 38.2055 | 3 | Yes | SD-IV | San Diego, Border | Yes | 21 | 2 | 920 | High | DAC_Adjacent | 6.0665 | 2 | 0.12319 | 2 | 0.0026454 | 1 | 1 | NA_Moderate | A | 2 | 1.5 | 50 | 0
|  |  | ELCAJN_6_LM6K | El Cajon Energy Center | 48.1 | 49.7 | SDGE | El Cajon Energy, LLC | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2010-06-16 | El Cajon | 69 | 57001 | 16736 | 0 | 187781 | 187781 | 0 | 0.058 | 1.107 | 10985.1118 | 3.0887e-07 | 5.8952e-06 | 0.0585 | 11.2202 | 3.4656e-06 | 6.6145e-05 | 0.65638 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | El Cajon Energy Center | 49.9 | 48.1 | 48.1 | 3.829% | 2 |  | 3 |  | 25.5589 | 29.5616 | 2 | Yes | SD-IV | San Diego, El Cajon | Yes | 22 | 1 | 920 | High | In_DAC |  | 4 | 0.13229 | 2 | 0.0050649 | 1 | 1 | NA_Moderate | A | 2 | 1.5 | 48.9583 | 1
|  |  | OTAY_6_PL1X2 | Chula Vista Energy Center, LLC | 39.57 | 40 | SDGE | Chula Vista Energy Center, LLC | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2006-06-08 | Miguel | 230 | 55540 | 3070 | 0 | 51755 | 51755 | 0 | 0.02 | 0.418 | 3027.6464 | 3.8644e-07 | 8.0765e-06 | 0.0585 | 16.8583 | 6.5147e-06 | 0.00013616 | 0.9862 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Chula Vista Energy Center | 44 | 35.5 | 35.5 | 0.7965% | 1 |  | 4 |  | 29.5836 | 33.5863 | 2 | Yes | SD-IV | San Diego | Yes | 22 | 1 | 920 | High | DAC_Adjacent | 1.0079 | 3 | 0.27231 | 3 | 0.0021689 | 1 | 1 | NA_Moderate | A | 2 | 1.5 | 47.9167 | 1
|  |  | CARLS1_2_CARCT1 | Carlsbad 1 | 422 |  | SDGE | Carlsbad Energy Center LLC | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2018-11-19 | Encina | 230 | 59002 | 132599 | 0 | 1287534 | 1287534 | 0 | 0.37216 | 203.4497 | 75320.2133 | 2.8905e-07 | 0.00015802 | 0.0585 | 9.71 | 2.8067e-06 | 0.0015343 | 0.56803 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Carlsbad Energy Center | 659 | 527.5 | 527.5 | 2.297% | 2 |  | 3 |  | 17.126 | 21.1288 | 1 | Yes | SD-IV | San Diego | Yes | 20 | 2 | 920 | High | Outside_DAC | 31.4204 | 1 | 3.0686 | 4 | 0.070485 | 4 | 3 | NA_Moderate | A | 2 | 1.5 | 47.9167 | 1
|  |  | CARLS2_1_CARCT1 | Carlsbad 2 | 105.5 | 105.5 | SDGE | Carlsbad Energy Center LLC | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2018-11-20 | Encina | 230 | 59002 | 132599 | 0 | 1287534 | 1287534 | 0 | 0.37216 | 203.4497 | 75320.2133 | 2.8905e-07 | 0.00015802 | 0.0585 | 9.71 | 2.8067e-06 | 0.0015343 | 0.56803 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Carlsbad Energy Center | 659 | 527.5 | 527.5 | 2.297% | 2 |  | 3 |  | 17.1233 | 21.126 | 1 | Yes | SD-IV | San Diego | Yes | 21 | 2 | 920 | High | Outside_DAC | 31.4204 | 1 | 3.0686 | 4 | 0.070485 | 4 | 3 | NA_Moderate | A | 2 | 1.5 | 47.9167 | 1
|  |  | METEC_2_PL1X3 | Metcalf Energy Center | 597.05 |  | PGAE | Metcalf Energy Center, LLC | COMBINED CYCLE | NATURAL GAS | NP15 | 2005-05-27 | Metcalf | 115 | 55393 | 2079832 | 0 | 15832385 | 15832385 | 0 | 4.581 | 56.936 | 926188.0581 | 2.8934e-07 | 3.5962e-06 | 0.0585 | 7.6123 | 2.2026e-06 | 2.7375e-05 | 0.44532 | CAISO_CCGT1 | Natural Gas Fired Combined Cycle | Metcalf Energy Center | 635 | 570 | 580 | 37.39% | 3 |  | 2 |  | 30.6164 | 34.6192 | 2 | Yes | Bay Area | South Bay-Moss Landing | Yes | 13 | 2 | 2220 | High | DAC_Adjacent | 8.2664 | 2 | 0.054751 | 1 | 0.020471 | 3 | 2 | NA_Marginal | A | 1 | 1.25 | 46.875 | 0
|  |  | SENTNL_2_CTG1 | Sentinel Unit 1 | 107.68 | 131.8 | SCE | Sentinel Energy Center, LLC | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2013-05-06 | Devers | 500 | 57482 | 485658 | 0 | 4981514 | 4981514 | 0 | 1.498 | 25.839 | 291416.535 | 3.0071e-07 | 5.187e-06 | 0.0585 | 10.2572 | 3.0845e-06 | 5.3204e-05 | 0.60004 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Sentinel Energy Center, LLC | 800 | 802.08 | 802.08 | 6.93% | 3 |  | 1 |  | 22.6685 | 26.6712 | 1 | Yes | LA Basin | Eastern, Valley-Devers | Yes | 7 | 3 | 1141 | High | Outside_DAC | 27.1901 | 1 | 0.10641 | 2 | 0.0073741 | 2 | 2 | NA_Severe 15 | A | 3 | 2.25 | 46.875 | 1
|  |  | SENTNL_2_CTG2 | Sentinel Unit 2 | 104.19 | 131.8 | SCE | Sentinel Energy Center, LLC | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2013-05-06 | Devers | 500 | 57482 | 485658 | 0 | 4981514 | 4981514 | 0 | 1.498 | 25.839 | 291416.535 | 3.0071e-07 | 5.187e-06 | 0.0585 | 10.2572 | 3.0845e-06 | 5.3204e-05 | 0.60004 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Sentinel Energy Center, LLC | 800 | 802.08 | 802.08 | 6.93% | 3 |  | 1 |  | 22.6685 | 26.6712 | 1 | Yes | LA Basin | Eastern, Valley-Devers | Yes | 7 | 3 | 1141 | High | Outside_DAC | 27.1901 | 1 | 0.10641 | 2 | 0.0073741 | 2 | 2 | NA_Severe 15 | A | 3 | 2.25 | 46.875 | 1
|  |  | SENTNL_2_CTG3 | Sentinel Unit 3 | 105.69 | 131.8 | SCE | Sentinel Energy Center, LLC | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2013-05-06 | Devers | 500 | 57482 | 485658 | 0 | 4981514 | 4981514 | 0 | 1.498 | 25.839 | 291416.535 | 3.0071e-07 | 5.187e-06 | 0.0585 | 10.2572 | 3.0845e-06 | 5.3204e-05 | 0.60004 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Sentinel Energy Center, LLC | 800 | 802.08 | 802.08 | 6.93% | 3 |  | 1 |  | 22.6685 | 26.6712 | 1 | Yes | LA Basin | Eastern, Valley-Devers | Yes | 7 | 3 | 1141 | High | Outside_DAC | 27.1901 | 1 | 0.10641 | 2 | 0.0073741 | 2 | 2 | NA_Severe 15 | A | 3 | 2.25 | 46.875 | 1
|  |  | SENTNL_2_CTG4 | Sentinel Unit 4 | 106.55 | 131.8 | SCE | Sentinel Energy Center, LLC | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2013-05-06 | Devers | 500 | 57482 | 485658 | 0 | 4981514 | 4981514 | 0 | 1.498 | 25.839 | 291416.535 | 3.0071e-07 | 5.187e-06 | 0.0585 | 10.2572 | 3.0845e-06 | 5.3204e-05 | 0.60004 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Sentinel Energy Center, LLC | 800 | 802.08 | 802.08 | 6.93% | 3 |  | 1 |  | 22.6685 | 26.6712 | 1 | Yes | LA Basin | Eastern, Valley-Devers | Yes | 7 | 3 | 1141 | High | Outside_DAC | 27.1901 | 1 | 0.10641 | 2 | 0.0073741 | 2 | 2 | NA_Severe 15 | A | 3 | 2.25 | 46.875 | 1
|  |  | SENTNL_2_CTG5 | Sentinel Unit 5 | 107.52 | 131.8 | SCE | Sentinel Energy Center, LLC | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2013-05-06 | Devers | 500 | 57482 | 485658 | 0 | 4981514 | 4981514 | 0 | 1.498 | 25.839 | 291416.535 | 3.0071e-07 | 5.187e-06 | 0.0585 | 10.2572 | 3.0845e-06 | 5.3204e-05 | 0.60004 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Sentinel Energy Center, LLC | 800 | 802.08 | 802.08 | 6.93% | 3 |  | 1 |  | 22.6685 | 26.6712 | 1 | Yes | LA Basin | Eastern, Valley-Devers | Yes | 7 | 3 | 1141 | High | Outside_DAC | 27.1901 | 1 | 0.10641 | 2 | 0.0073741 | 2 | 2 | NA_Severe 15 | A | 3 | 2.25 | 46.875 | 1
|  |  | SENTNL_2_CTG6 | Sentinel Unit 6 | 105 | 131.8 | SCE | Sentinel Energy Center, LLC | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2013-05-06 | Devers | 500 | 57482 | 485658 | 0 | 4981514 | 4981514 | 0 | 1.498 | 25.839 | 291416.535 | 3.0071e-07 | 5.187e-06 | 0.0585 | 10.2572 | 3.0845e-06 | 5.3204e-05 | 0.60004 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Sentinel Energy Center, LLC | 800 | 802.08 | 802.08 | 6.93% | 3 |  | 1 |  | 22.6685 | 26.6712 | 1 | Yes | LA Basin | Eastern, Valley-Devers | Yes | 7 | 3 | 1141 | High | Outside_DAC | 27.1901 | 1 | 0.10641 | 2 | 0.0073741 | 2 | 2 | NA_Severe 15 | A | 3 | 2.25 | 46.875 | 1
|  |  | SENTNL_2_CTG7 | Sentinel Unit 7 | 106.73 | 131.8 | SCE | Sentinel Energy Center, LLC | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2013-05-06 | Devers | 500 | 57482 | 485658 | 0 | 4981514 | 4981514 | 0 | 1.498 | 25.839 | 291416.535 | 3.0071e-07 | 5.187e-06 | 0.0585 | 10.2572 | 3.0845e-06 | 5.3204e-05 | 0.60004 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Sentinel Energy Center, LLC | 800 | 802.08 | 802.08 | 6.93% | 3 |  | 1 |  | 22.6685 | 26.6712 | 1 | Yes | LA Basin | Eastern, Valley-Devers | Yes | 7 | 3 | 1141 | High | Outside_DAC | 27.1901 | 1 | 0.10641 | 2 | 0.0073741 | 2 | 2 | NA_Severe 15 | A | 3 | 2.25 | 46.875 | 1
|  |  | SENTNL_2_CTG8 | Sentinel Unit 8 | 106.85 | 131.8 | SCE | Sentinel Energy Center, LLC | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2013-05-06 | Devers | 500 | 57482 | 485658 | 0 | 4981514 | 4981514 | 0 | 1.498 | 25.839 | 291416.535 | 3.0071e-07 | 5.187e-06 | 0.0585 | 10.2572 | 3.0845e-06 | 5.3204e-05 | 0.60004 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Sentinel Energy Center, LLC | 800 | 802.08 | 802.08 | 6.93% | 3 |  | 1 |  | 22.6685 | 26.6712 | 1 | Yes | LA Basin | Eastern, Valley-Devers | Yes | 7 | 3 | 1141 | High | Outside_DAC | 27.1901 | 1 | 0.10641 | 2 | 0.0073741 | 2 | 2 | NA_Severe 15 | A | 3 | 2.25 | 46.875 | 1
|  |  | ESCNDO_6_UNITB1 | CalPeak Power Enterprise Unit 1 | 48.04 | 52 | SDGE | CalPeak Power - Enterprise LLC | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2001-10-23 | Escondido | 230 | 55513 | 12241 | 0 | 135153 | 135153 | 0 | 0.04 | 0.902 | 7906.3953 | 2.9596e-07 | 6.6739e-06 | 0.0585 | 11.041 | 3.2677e-06 | 7.3687e-05 | 0.64589 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | CalPeak Power Enterprise Peaker Plant | 58.9 | 48.04 | 48.04 | 2.372% | 2 |  | 3 |  | 34.211 | 38.2137 | 3 | Yes | SD-IV | San Diego | Yes | 21 | 2 | 920 | High | Outside_DAC | 22.0442 | 1 | 0.14737 | 3 | 0.0034964 | 1 | 1 | NA_Moderate | A | 2 | 1.5 | 45.8333 | 0
|  |  | MRGT_6_MEF2 | Miramar Energy Facility II | 44 | 67.5 | SDGE | San Diego Gas & Electric | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2009-08-07 | Penasquitos | 230 | 56232 | 92448 | 0 | 929471 | 929471 | 0 | 0.28 | 8.849 | 54373.674 | 3.0125e-07 | 9.5205e-06 | 0.0585 | 10.054 | 3.0287e-06 | 9.5719e-05 | 0.58815 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Miramar Energy Facility | 106 | 89 | 89 | 9.956% | 4 |  | 2 |  | 26.4164 | 30.4192 | 2 | Yes | SD-IV | San Diego | Yes | 23 | 1 | 920 | High | DAC_Adjacent | 9.6766 | 2 | 0.19144 | 3 | 0.01906 | 3 | 3 | NA_Moderate | A | 2 | 1.5 | 45.8333 | 1
|  |  | MRGT_6_MMAREF | Miramar Energy Facility | 45 | 68 | SDGE | San Diego Gas & Electric | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2005-07-27 | Penasquitos | 230 | 56232 | 92448 | 0 | 929471 | 929471 | 0 | 0.28 | 8.849 | 54373.674 | 3.0125e-07 | 9.5205e-06 | 0.0585 | 10.054 | 3.0287e-06 | 9.5719e-05 | 0.58815 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Miramar Energy Facility | 106 | 89 | 89 | 9.956% | 4 |  | 2 |  | 30.4493 | 34.4521 | 2 | Yes | SD-IV | San Diego | Yes | 23 | 1 | 920 | High | DAC_Adjacent | 9.6766 | 2 | 0.19144 | 3 | 0.01906 | 3 | 3 | NA_Moderate | A | 2 | 1.5 | 45.8333 | 1
|  |  | LARKSP_6_UNIT 1 | LARKSPUR PEAKER UNIT 1 | 49 | 49 | SDGE | Wildflower Energy LP | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2001-09-13 | Otay Mesa | 230 | 55542 | 44783 | 0 | 433756 | 433756 | 0 | 0.138 | 4.272 | 25374.5489 | 3.1815e-07 | 9.8489e-06 | 0.0585 | 9.6857 | 3.0815e-06 | 9.5393e-05 | 0.56661 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Larkspur Energy Facility | 99.8 | 92 | 92 | 5.122% | 3 |  | 1 |  | 34.3205 | 38.3233 | 3 | Yes | SD-IV | San Diego, Border | Yes | 22 | 1 | 920 | High | DAC_Adjacent | 6.1273 | 2 | 0.19079 | 3 | 0.009773 | 3 | 3 | NA_Moderate | A | 2 | 1.5 | 45.8333 | 1
|  |  | LARKSP_6_UNIT 2 | LARKSPUR PEAKER UNIT 2 | 49 | 49 | SDGE | Wildflower Energy LP | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2001-09-13 | Otay Mesa | 230 | 55542 | 44783 | 0 | 433756 | 433756 | 0 | 0.138 | 4.272 | 25374.5489 | 3.1815e-07 | 9.8489e-06 | 0.0585 | 9.6857 | 3.0815e-06 | 9.5393e-05 | 0.56661 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Larkspur Energy Facility | 99.8 | 92 | 92 | 5.122% | 3 |  | 1 |  | 34.3205 | 38.3233 | 3 | Yes | SD-IV | San Diego, Border | Yes | 22 | 1 | 920 | High | DAC_Adjacent | 6.1273 | 2 | 0.19079 | 3 | 0.009773 | 3 | 3 | NA_Moderate | A | 2 | 1.5 | 45.8333 | 1
|  |  | TERMEX_2_PL1X3 | TDM | 625 |  | SDGE | Termoelectrica De Mexicali S. de R.L. de C.V. (non-pro forma agreement) | COMBINED CYCLE | NATURAL GAS | SP15 | 2003-07-30 | Imperial Valley | 230 | 55719 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | CAISO_CCGT1 | Not Available | Not Available | Not Available | Not Available | Not Available | Not Available | 2.5 |  | 2.5 |  | 32.4438 | 36.4466 | 3 | Yes | SD-IV | 0 | Yes | 25 | 1 | 920 | High | Not Available | Not Available | 1 | Not Available | 2.4 | Not Available | 2.5 | 2.5 | Not Available | Not Available | 2 | 1.75 | 45.3125 | 1
|  |  | OGROVE_6_PL1X2 | Orange Grove Energy Center | 96 |  | SDGE | Orange Grove Energy, L.P. | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2010-06-16 | Escondido | 230 | 56914 | 33879 | 0 | 377648 | 377648 | 0 | 0.112 | 2.134 | 22092.2538 | 2.9657e-07 | 5.6508e-06 | 0.0585 | 11.147 | 3.3059e-06 | 6.2989e-05 | 0.65209 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Orange Grove Peaking Facility | 118 | 96 | 96 | 3.278% | 2 |  | 3 |  | 25.5589 | 29.5616 | 2 | Yes | SD-IV | San Diego | Yes | 20 | 2 | 920 | High | Outside_DAC | 25.725 | 1 | 0.12598 | 2 | 0.0041289 | 1 | 1 | NA_Moderate | A | 2 | 1.5 | 42.7083 | 0
|  |  | PIOPIC_2_CTG1 | Pio Pico Unit 1 | 111.3 | 111.3 | SDGE | Pio Pico Energy Center | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2016-11-03 | Otay Mesa | 230 | 57555 | 150057 | 0 | 1505278 | 1505278 | 0 | 0.447 | 9.355 | 88058.1484 | 2.9696e-07 | 6.2148e-06 | 0.0585 | 10.0314 | 2.9789e-06 | 6.2343e-05 | 0.58683 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Pio Pico Energy Center | 395.4 | 336 | 336 | 4.332% | 3 |  | 2 |  | 19.1699 | 23.1726 | 1 | Yes | SD-IV | San Diego | Yes | 19 | 2 | 920 | High | DAC_Adjacent | 8.0067 | 2 | 0.12469 | 2 | 0.0054017 | 1 | 1 | NA_Moderate | A | 2 | 1.5 | 40.625 | 1
|  |  | PIOPIC_2_CTG2 | Pio Pico Unit 2 | 112.7 | 112.7 | SDGE | Pio Pico Energy Center | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2016-11-03 | Otay Mesa | 230 | 57555 | 150057 | 0 | 1505278 | 1505278 | 0 | 0.447 | 9.355 | 88058.1484 | 2.9696e-07 | 6.2148e-06 | 0.0585 | 10.0314 | 2.9789e-06 | 6.2343e-05 | 0.58683 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Pio Pico Energy Center | 395.4 | 336 | 336 | 4.332% | 3 |  | 2 |  | 19.1699 | 23.1726 | 1 | Yes | SD-IV | San Diego | Yes | 19 | 2 | 920 | High | DAC_Adjacent | 8.0067 | 2 | 0.12469 | 2 | 0.0054017 | 1 | 1 | NA_Moderate | A | 2 | 1.5 | 40.625 | 1
|  |  | PIOPIC_2_CTG3 | Pio Pico Unit 3 | 112 | 112 | SDGE | Pio Pico Energy Center | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2016-11-03 | Otay Mesa | 230 | 57555 | 150057 | 0 | 1505278 | 1505278 | 0 | 0.447 | 9.355 | 88058.1484 | 2.9696e-07 | 6.2148e-06 | 0.0585 | 10.0314 | 2.9789e-06 | 6.2343e-05 | 0.58683 | CAISO_Peaker1 | Natural Gas Fired Combustion Turbine | Pio Pico Energy Center | 395.4 | 336 | 336 | 4.332% | 3 |  | 2 |  | 19.1699 | 23.1726 | 1 | Yes | SD-IV | San Diego | Yes | 19 | 2 | 920 | High | DAC_Adjacent | 8.0067 | 2 | 0.12469 | 2 | 0.0054017 | 1 | 1 | NA_Moderate | A | 2 | 1.5 | 40.625 | 1
|  |  | OTMESA_2_PL1X3 | OTAY MESA ENERGY CENTER | 603.68 | 689 | SDGE | Otay Mesa Energy Center, LLC | COMBINED CYCLE | NATURAL GAS | SP15 | 2009-10-02 | Otay Mesa | 230 | 55345 | 493151 | 0 | 3707001 | 3707001 | 0 | 1.119 | 18.132 | 216858.0449 | 3.0186e-07 | 4.8913e-06 | 0.0585 | 7.517 | 2.2691e-06 | 3.6768e-05 | 0.43974 | CAISO_CCGT1 | Natural Gas Fired Combined Cycle | Otay Mesa Generating Project | 688.5 | 603.6 | 603.6 | 8.177% | 1 |  | 1 |  | 26.263 | 30.2658 | 2 | Yes | SD-IV | San Diego | Yes | 20 | 2 | 920 | High | DAC_Adjacent | 8.3474 | 2 | 0.073535 | 1 | 0.0060127 | 2 | 1 | NA_Moderate | A | 2 | 1.5 | 40.625 | 0
|  |  | PALOMR_2_PL1X3 | Palomar Energy Center | 588.21 |  | SDGE | San Diego Gas & Electric | COMBINED CYCLE | NATURAL GAS | SP15 | 2005-10-14 | Palomar Energy | 230 | 55985 | 1925066 | 0 | 13759446 | 13759446 | 0 | 4.175 | 45.365 | 804921.973 | 3.0343e-07 | 3.297e-06 | 0.0585 | 7.1475 | 2.1688e-06 | 2.3565e-05 | 0.41813 | CAISO_CCGT1 | Natural Gas Fired Combined Cycle | Palomar Energy | 559 | 565.61 | 565.61 | 39.31% | 3 |  | 1 |  | 30.2329 | 34.2356 | 2 | Yes | SD-IV | San Diego | Yes | 21 | 2 | 920 | High | Outside_DAC | 21.9154 | 1 | 0.047131 | 1 | 0.018528 | 3 | 2 | NA_Moderate | A | 2 | 1.5 | 40.625 | 0
|  |  | ESCNDO_6_PL1X2 | MMC Escondido Aggregate | 48.71 | 49.5 | SDGE | Escondido Energy Center | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2014-01-25 | Escondido | 230 | 55538 | 25261 | 0 | 264756 | 264756 | 0 | 0.08 | 1.17 | 15488.1179 | 3.0217e-07 | 4.4192e-06 | 0.0585 | 10.4808 | 3.1669e-06 | 4.6316e-05 | 0.61312 | CAISO_Peaker2 | Natural Gas Fired Combustion Turbine | Escondido Energy Center | 49.9 | 48.71 | 48.71 | 5.779% | 3 |  | 2 |  | 21.9452 | 25.9479 | 1 | Yes | SD-IV | San Diego | Yes | 21 | 2 | 920 | High | Outside_DAC | 22.2991 | 1 | 0.092633 | 1 | 0.0053532 | 1 | 1 | NA_Moderate | A | 2 | 1.5 | 36.4583 | 1
|  |  | ESCO_6_GLMQF | Goal Line Cogen | 49.9 | 49.9 | SDGE | Goal Line, L.P. | COMBUSTION TURBINE | NATURAL GAS | SP15 | 1994-01-01 | Escondido | 230 | 54749 | 18142 | 13581 | 176484 | 146962 | 29522 | 0.051 | 1.254 | 10324.2419 | 2.8898e-07 | 7.1055e-06 | 0.0585 | 8.1007 | 2.3409e-06 | 5.7559e-05 | 0.47388 | CAISO_Peaker1 | Natural Gas Fired Combined Cycle | Goal Line LP | 51.4 | 36.41 | 34.79 | 4.029% | 3 |  | 1 |  | 42.0247 | 46.0274 | 4 | Yes | SD-IV | San Diego | Yes | 22 | 1 | 920 | High | Outside_DAC | 21.3375 | 1 | 0.11512 | 2 | 0.0046383 | 1 | 1 | NA_Moderate | A | 2 | 1.5 | 36.4583 | 1

## CHPs
|  | Note: | Columns highlighted in blue are the score values for the criteria for each resource.
[37 empty] | *Resources with Not Available CF receive a 2.5 |  | *Resources with Not Available data receive a 2.5 | [9 empty] | *Resources with No published LEF receive a 4 | [7 empty] | *Resources with Not Available data receive a 2.4 |  |  | *Resources with Not Available data receive a 1.75
Selected to be modeled as not retained by portfolio and model year |  | CAISO Master Generator List Information | [9 empty] | IRP Modeled Interconnection Point |  | EIA 2018 Emissions Data | [15 empty] | IRP Info | [10 empty] | Age |  |  | Local Need | [7 empty] | DACs and Air Pollution | [9 empty] | Ranking Score (Highest=100)
Both Portfolios (2034) | Both Portfolios (2039) | RESOURCE_ID | GEN_UNIT_NAME | NET_DEPENDABLE_CAPACITY (MW) | NAMEPLATE_CAPACITY (MW) | PTO_AREA | OWNER_OR_QF | UNIT_TYPE | ENERGY_SOURCE | ZONE | COD | Substation | Voltage | EIA Code | 2018 Generation (MWh) | 2018 Useful Thermal Output (MMBtu) | 2018 Total Fuel Consumption (MMBtu) | 2018 Fuel Consumption for Electric Generation (MMBtu) | 2018 Fuel Consumption for Useful Thermal Output (MMBtu) | 2018 SO2 Emission (Tons) | 2018 NOx Emission (Tons) | 2018 CO2 Emission (Tons) | SO2 Emission Rate (Tons/total MMBtu) | NOx Emission Rate (Tons/total MMBtu) | CO2 Emission Rate (Tons/total MMBtu) | Heat Rate (MMBtu/MWh) | SO2 Emission Rate (Tons/MWh) | NOx Emission Rate (Tons/MWh) | CO2 Emission Rate (Tons/total MWh) | RESOLVE Type | Technology | Plant Name | Nameplate Capacity (MW) | AUG NQC (online 2020) | SEP NQC (online 2020) | Capacity Factor (2018) | Capcity Factor (2018) Quartile* – by Type | CONFIDENTIAL: Heat Rate (2018) (MMBtu/MWh) | Heat Rate (2018) Quartile* – by Type | CONFIDENTIAL: Has Contract past model year | Age in 2035 | Age in 2039 | Age Quartile – by Type | In Local Area | Local Area | Sub Area | Has 2028 LCR Study LEF | 2028 LCR Study Highest Local Effectiveness Factor (%) | LEF Quartile* – All Plants(Highest %=1) | 4-hr Storage able to charge in LCR (MW) | Storage Displacement Potential (High = 4-hr str > plant MW) | DAC Status | If out of DAC, distance to DAC | DAC Rank (4=inDAC to 1=outsideDAC) | NOx Emissions Rate (2018) (lbs/MWh) | CF weighted NOx Rate (CF * NOx Rate) | Nox Emissions Rate Quartile* – All Plants | Ozone Attainment Status (8hr-O3 2015) | PM2.5 Attainment Status (2012 Standard) | Ozone+PM2.5 Rank* | Ozone+PM2.5 Rank (1-4 intergers) | Heat Rate & Age (.25), LEF (.25), DAC, NOx Emissions weighted by CF,and NAZ Combined (.5) | Exclude (1st Quartile Age, 1st Quartile LEF)
YES | YES | DEXZEL_1_UNIT | Western Power and Steam Cogeneration | 20 | 36.8 | PGAE | Western Power and Steam II LLC | COMBUSTION TURBINE | NATURAL GAS | ZP26 | 1989-11-30 | Kern Oil | 115 | 54410 | 148922 | 227303 | 1750887 | 1222274 | 528613 | 0.5076 | 277.4903 | 102426.1746 | 2.8991e-07 | 0.00015849 | 0.0585 | 8.2075 | 2.3795e-06 | 0.0013008 | 0.48013 | CAISO_CHP | Natural Gas Fired Combustion Turbine | Western Power & Steam Inc | 27.7 | 17.78 | 17.43 | 61.37% | 2 |  | 4 |  | 46.1151 | 50.1178 | 2 | Yes | Kern | South Kern PP, Kern Oil | No | No Published Factor | 4 | 270 | High | In_DAC |  | 4 | 2.6015 | 1.5966 | 4 | NA_Extreme | NA_Moderate | 4 | 4 | 93.75 | 0
YES | YES | TXMCKT_6_UNIT | McKittrick Cogen | 11.2 | 11.2 | PGAE | Chevron USA Inc | FTUR | NATURAL GAS | ZP26 | 1994-10-01 | Temblor | 115 | 52076 | 79176 | 10535 | 982409 | 947296 | 35113 | 0.28476 | 155.6667 | 57470.5254 | 2.8985e-07 | 0.00015845 | 0.0585 | 11.9644 | 3.468e-06 | 0.0018958 | 0.69991 | CAISO_CHP | Natural Gas Fired Combustion Turbine | McKittrick Cogen | 12 | 2.08 | 2.13 | 75.32% | 4 |  | 4 |  | 41.2767 | 45.2795 | 2 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | In_DAC |  | 4 | 3.7916 | 2.8558 | 4 | NA_Extreme | NA_Moderate | 4 | 4 | 93.75 | 0
YES | YES | CHEVCY_1_UNIT | CHEVRON USA (CYMRIC) | 24.3 | 24.3 | PGAE | Pacific Gas & Electric Company | COMBUSTION TURBINE | NATURAL GAS | ZP26 | 1982-10-15 | Temblor | 115 | 52081 | 44634 | 382541 | 654763 | 188250 | 466513 | 0.19071 | 104.2537 | 38303.3682 | 2.9126e-07 | 0.00015922 | 0.0585 | 4.2176 | 1.2284e-06 | 0.00067155 | 0.24673 | CAISO_CHP | Natural Gas Fired Combustion Turbine | Cymric 31X Cogen | 6.8 | 2.91 | 2.85 | 74.93% | 3 |  | 4 |  | 53.2466 | 57.2493 | 4 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | In_DAC |  | 4 | 1.3431 | 1.0064 | 2 | NA_Extreme | NA_Moderate | 4 | 4 | 91.6667 | 0
YES | YES | CHEVMN_2_UNITS | CHEVRON U.S.A. UNITS 1 & 2 AGGREGATE | 124.87 | 170.7 | SCE | Chevron U.S.A. Inc. (Chevron CIC) |  | OTHER | SP15 | 1987-12-29 | Chevmain | 230 | 10213 | 1265325 | 344636 | 15508088 | 14359306 | 1148782 | 4.5612 | 1984.9378 | 852984.1261 | 2.9411e-07 | 0.00012799 | 0.055003 | 11.3483 | 3.3377e-06 | 0.0014525 | 0.62419 | CAISO_CHP | Natural Gas Fired Combined Cycle | El Segundo Cogen | 180.1 | 7.54 | 9.78 | 80.2% | 4 |  | 2 |  | 48.0384 | 52.0411 | 3 | Yes | LA Basin | Western, El Nido | No | No Published Factor | 4 | 1141 | High | In_DAC |  | 4 | 2.905 | 2.3299 | 4 | NA_Extreme | NA_Moderate | 4 | 4 | 90.625 | 0
YES | YES | UNVRSY_1_UNIT 1 | Berry Cogen 38 - Unit 1 | 38 | 38 | PGAE | Berry Petroleum Company | FTUR | NATURAL GAS | ZP26 | 1986-01-01 | Taft | 115 | 50170 | 293027 | 1660686 | 3889501 | 1482708 | 2406793 | 1.1278 | 616.5114 | 227534.2204 | 2.8995e-07 | 0.00015851 | 0.0585 | 5.06 | 1.4671e-06 | 0.00080204 | 0.29601 | CAISO_CHP | Natural Gas Fired Combustion Turbine | Berry Cogen | 38.7 | 34.03 | 34.36 | 86.44% | 4 |  | 2 |  | 50.0301 | 54.0329 | 4 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | DAC_Adjacent | 2.5234 | 3 | 1.6041 | 1.3865 | 4 | NA_Extreme | NA_Moderate | 4 | 4 | 89.5833 | 0
YES | YES | TANHIL_6_SOLART | Berry Cogen 18 | 17 | 17 | PGAE | Berry Petroleum Company | FTUR | NATURAL GAS | ZP26 | 1986-01-01 | Taft | 115 | 50170 | 293027 | 1660686 | 3889501 | 1482708 | 2406793 | 1.1278 | 616.5114 | 227534.2204 | 2.8995e-07 | 0.00015851 | 0.0585 | 5.06 | 1.4671e-06 | 0.00080204 | 0.29601 | CAISO_CHP | Natural Gas Fired Combustion Turbine | Berry Cogen | 38.7 | 34.03 | 34.36 | 86.44% | 4 |  | 2 |  | 50.0301 | 54.0329 | 4 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | DAC_Adjacent | 2.5234 | 3 | 1.6041 | 1.3865 | 4 | NA_Extreme | NA_Moderate | 4 | 4 | 89.5833 | 0
YES | YES | CSCCOG_1_UNIT 1 | SANTA CLARA CO-GEN | 7 | 7 | PGAE | City of Santa Clara DBA Silicon Valley Power (MSS Agreement - S14) | FTUR | NATURAL GAS | NP15 | 1981-01-01 | FMC | 115 | 7232 | 45419 | 61225 | 737492 | 533409 | 204083 | 0.21418 | 117.0848 | 43142.9809 | 2.9042e-07 | 0.00015876 | 0.0585 | 11.7442 | 3.4107e-06 | 0.0018645 | 0.68703 | CAISO_CHP | Natural Gas Fired Combustion Turbine | Santa Clara Cogen | 7.8 | 6 | 6 | 66.47% | 3 |  | 4 |  | 55.0329 | 59.0356 | 4 | Yes | Bay Area | San Jose, South Bay-Moss Landing | No | No Published Factor | 4 | 2220 | High | In_DAC |  | 4 | 3.729 | 2.4788 | 4 | NA_Marginal | A | 1.25 | 1 | 88.5417 | 0
YES | YES | CHEVCD_6_UNIT | CHEVRON USA (TAFT/CADET) | 11.5 | 11.5 | PGAE | Pacific Gas & Electric Company | COMBUSTION TURBINE | NATURAL GAS | ZP26 | 1982-07-26 | Taft | 115 | 52085 | 77245 | 748640 | 1197853 | 327341 | 870512 | 0.34957 | 191.0972 | 70073.9114 | 2.9183e-07 | 0.00015953 | 0.0585 | 4.2377 | 1.2367e-06 | 0.00067605 | 0.2479 | CAISO_CHP | Natural Gas Fired Combustion Turbine | Taft 26C Cogen | 12.4 | 1.02 | 1.09 | 71.11% | 3 |  | 3 |  | 53.4685 | 57.4712 | 4 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | DAC_Adjacent | 1.6151 | 3 | 1.3521 | 0.96151 | 2 | NA_Extreme | NA_Moderate | 4 | 4 | 84.375 | 0
YES | YES | DISCOV_1_CHEVRN | CHEVRON USA (EASTRIDGE) | 48.8 | 56.2 | PGAE | Pacific Gas & Electric Company | FTUR | NATURAL GAS | ZP26 | 1988-06-13 | Columbus | 115 | 52107 | 212906 | 1438083 | 2513076 | 860107 | 1652969 | 0.72872 | 398.366 | 147013.9199 | 2.8997e-07 | 0.00015852 | 0.0585 | 4.0398 | 1.1714e-06 | 0.00064039 | 0.23633 | CAISO_CHP | Natural Gas Fired Combustion Turbine | Kern River Eastridge Cogen | 48.8 | 2.58 | 2.34 | 49.8% | 2 |  | 3 |  | 47.5808 | 51.5836 | 2 | Yes | Kern | South Kern PP, Kern Oil | No | No Published Factor | 4 | 270 | High | In_DAC |  | 4 | 1.2808 | 0.63787 | 2 | NA_Extreme | NA_Moderate | 4 | 4 | 82.2917 | 0
YES | YES | CHEVCO_6_UNIT 1 | CHEVRON USA (COALINGA) | 16.5 | 19 | PGAE | Pacific Gas & Electric Company | COMBUSTION TURBINE | NATURAL GAS | ZP26 | 1986-01-17 | Cantua | 115 | 52083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | CAISO_CHP | Natural Gas Fired Combustion Turbine | CHEVRON USA (COALINGA) | 6.8 | 2.09 | 1.94 | 0% | 1 |  | 4 |  | 49.9863 | 53.989 | 4 | Yes | Fresno | Coalinga, Panoche 115 kV | No | No Published Factor | 4 | 793 | High | Outside_DAC | 11.8172 | 1 | Not Available | Not Available | 2.5 | NA_Extreme | NA_Moderate | 4 | 4 | 81.25 | 0
YES | YES | SMPRIP_1_SMPSON | Ripon Cogeneration Unit 1 | 46.05 | 56.9 | PGAE | AltaGas Ripon Energy Inc. | COMBUSTION TURBINE | NATURAL GAS | NP15 | 1988-04-19 | Ripon | 115 | 50299 | 9868 | 0 | 99585 | 99585 | 0 | 0.02869 | 15.6838 | 5825.6818 | 2.8809e-07 | 0.00015749 | 0.0585 | 10.0917 | 2.9074e-06 | 0.0015894 | 0.59036 | CAISO_CHP | Natural Gas Fired Combustion Turbine | AltaGas Ripon Energy Inc. | 49.5 | 46.05 | 46.05 | 2.276% | 1 |  | 4 |  | 47.7315 | 51.7342 | 3 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | DAC_Adjacent | 0.38097 | 3 | 3.1787 | 0.072339 | 1 | NA_Extreme | NA_Moderate | 4 | 4 | 80.2083 | 0
YES | YES | TENGEN_2_PL1X2 | Placerita Canyon Cogen | 37.7 |  | SCE | Shadow Wolf Energy, LLC | COMBUSTION TURBINE | NATURAL GAS | SP15 | 1990-03-06 | Sylmar | 230 | 52096 | 295809 | 1322830 | 3632354 | 1628063 | 2004291 | 1.0531 | 575.6884 | 212491.2259 | 2.8992e-07 | 0.00015849 | 0.0585 | 5.5038 | 1.5956e-06 | 0.00087229 | 0.32197 | CAISO_CHP | Natural Gas Fired Combustion Turbine | Berry Placerita Cogen | 42.8 | 37.6 | 37.59 | 78.9% | 4 |  | 2 |  | 45.8521 | 49.8548 | 2 | Yes | BC/Ventura | 0 | No | No Published Factor | 4 | 657 | High | DAC_Adjacent | 3.2817 | 3 | 1.7446 | 1.3764 | 3 | NA_Extreme | NA_Moderate | 4 | 4 | 79.1667 | 0
YES | YES | SYCAMR_2_UNIT 2 | Sycamore Cogeneration Unit 2 | 76 | 90 | SCE | Chevron Power Holdings | FTUR | NATURAL GAS | SP15 | 1987-01-01 | Dexzel | 115 | 50134 | 1368124 | 4611532 | 17059703 | 8675096 | 8384607 | 4.9688 | 2716.3022 | 997985.66 | 2.9126e-07 | 0.00015922 | 0.0585 | 6.3409 | 1.8469e-06 | 0.0010096 | 0.37094 | CAISO_CHP | Natural Gas Fired Combustion Turbine | Sycamore Cogeneration | 300 | 317.41 | 317.99 | 52.06% | 2 |  | 1 |  | 49.0301 | 53.0329 | 3 | Yes | BC/Ventura | 0 | No | No Published Factor | 4 | 657 | High | In_DAC |  | 4 | 2.0192 | 1.0512 | 2 | NA_Extreme | NA_Moderate | 4 | 4 | 79.1667 | 0
YES | YES | SYCAMR_2_UNIT 1 | Sycamore Cogeneration Unit 1 | 74 | 90 | SCE | Chevron Power Holdings | FTUR | NATURAL GAS | SP15 | 1987-01-01 | Dexzel | 115 | 50134 | 1368124 | 4611532 | 17059703 | 8675096 | 8384607 | 4.9688 | 2716.3022 | 997985.66 | 2.9126e-07 | 0.00015922 | 0.0585 | 6.3409 | 1.8469e-06 | 0.0010096 | 0.37094 | CAISO_CHP | Natural Gas Fired Combustion Turbine | Sycamore Cogeneration | 300 | 317.41 | 317.99 | 52.06% | 2 |  | 1 |  | 49.0301 | 53.0329 | 3 | Yes | BC/Ventura | 0 | No | No Published Factor | 4 | 657 | High | In_DAC |  | 4 | 2.0192 | 1.0512 | 2 | NA_Extreme | NA_Moderate | 4 | 4 | 79.1667 | 0
YES | YES | VEDDER_1_SEKERN | TEXACO EXPLORATION & PROD (SE KERN RIVER | 34.47 | 39.7 | PGAE | Pacific Gas & Electric Company | FTUR | NATURAL GAS | ZP26 | 1989-01-31 | Columbus | 115 | 50751 | 121221 | 558058 | 1451453 | 630778 | 820675 | 0.42072 | 229.9938 | 84909.4079 | 2.8986e-07 | 0.00015846 | 0.0585 | 5.2035 | 1.5083e-06 | 0.00082454 | 0.3044 | CAISO_CHP | Natural Gas Fired Combustion Turbine | Southeast Kern River Cogen | 30.8 | 2.19 | 0.73 | 44.93% | 1 |  | 2 |  | 46.9452 | 50.9479 | 2 | Yes | Kern | South Kern PP, Kern Oil | No | No Published Factor | 4 | 270 | High | In_DAC |  | 4 | 1.6491 | 0.74091 | 2 | NA_Extreme | NA_Moderate | 4 | 4 | 79.1667 | 0
YES | YES | SYCAMR_2_UNIT 3 | Sycamore Cogeneration Unit 3 | 74 | 90 | SCE | Chevron Power Holdings | FTUR | NATURAL GAS | SP15 | 1987-01-01 | Dexzel | 115 | 50134 | 1368124 | 4611532 | 17059703 | 8675096 | 8384607 | 4.9688 | 2716.3022 | 997985.66 | 2.9126e-07 | 0.00015922 | 0.0585 | 6.3409 | 1.8469e-06 | 0.0010096 | 0.37094 | CAISO_CHP | Natural Gas Fired Combustion Turbine | Sycamore Cogeneration | 300 | 317.41 | 317.99 | 52.06% | 2 |  | 1 |  | 49.0301 | 53.0329 | 3 | Yes | BC/Ventura | 0 | No | No Published Factor | 4 | 657 | High | In_DAC |  | 4 | 2.0192 | 1.0512 | 2 | NA_Extreme | NA_Moderate | 4 | 4 | 79.1667 | 0
YES | YES | SYCAMR_2_UNIT 4 | Sycamore Cogeneration Unit 4 | 76 | 90 | SCE | Chevron Power Holdings | FTUR | NATURAL GAS | SP15 | 1987-01-01 | Dexzel | 115 | 50134 | 1368124 | 4611532 | 17059703 | 8675096 | 8384607 | 4.9688 | 2716.3022 | 997985.66 | 2.9126e-07 | 0.00015922 | 0.0585 | 6.3409 | 1.8469e-06 | 0.0010096 | 0.37094 | CAISO_CHP | Natural Gas Fired Combustion Turbine | Sycamore Cogeneration | 300 | 317.41 | 317.99 | 52.06% | 2 |  | 1 |  | 49.0301 | 53.0329 | 3 | Yes | BC/Ventura | 0 | No | No Published Factor | 4 | 657 | High | In_DAC |  | 4 | 2.0192 | 1.0512 | 2 | NA_Extreme | NA_Moderate | 4 | 4 | 79.1667 | 0
YES | YES | SNCLRA_2_UNIT1 | New Indy Oxnard | 27.8 | 29 | SCE | New-Indy Oxnard LLC | FTUR | NATURAL GAS | SP15 | 2016-04-15 | Santa Clara | 230 | 57585 | 189038 | 696758 | 2129815 | 1041131 | 1088684 | 0.62811 | 343.3676 | 124593.3079 | 2.9491e-07 | 0.00016122 | 0.0585 | 5.5075 | 1.6242e-06 | 0.00088792 | 0.32219 | CAISO_CHP | Natural Gas Fired Combustion Turbine | Oxnard Paper Mill | 29 | 15.63 | 15.94 | 74.41% | 3 |  | 4 |  | 19.7233 | 23.726 | 1 | Yes | BC/Ventura | S.Clara, Moorpark | No | No Published Factor | 4 | 657 | High | In_DAC |  | 4 | 1.7758 | 1.3214 | 3 | NA_Serious | A | 2 | 2 | 78.125 | 1
| YES | SNCLRA_6_PROCGN | Procter and Gamble Oxnard 2 | 47.9 | 49.5 | SCE | The Procter & Gamble Paper Products Company | FTUR | NATURAL GAS | SP15 | 1998-11-17 | Santa Clara | 230 | 50464 | 557802 | 807253 | 5547498 | 3932998 | 1614500 | 1.6205 | 885.8709 | 324526.368 | 2.9211e-07 | 0.00015969 | 0.0585 | 7.0509 | 2.0597e-06 | 0.0011259 | 0.41247 | CAISO_CHP | Natural Gas Fired Combustion Turbine | Oxnard | 68.7 | 45.47 | 45.25 | 92.69% | 4 |  | 1 |  | 37.1452 | 41.1479 | 1 | Yes | BC/Ventura | S.Clara, Moorpark | No | No Published Factor | 4 | 657 | High | In_DAC |  | 4 | 2.2519 | 2.0872 | 4 | NA_Serious | A | 2 | 2 | 72.9167 | 1
| YES | CHEVCO_6_UNIT 2 | AERA ENERGY LLC. (COALINGA) | 8.5 | 12.5 | PGAE | Pacific Gas & Electric Company | FTUR | NATURAL GAS | ZP26 | 1988-06-03 | Gates | 115 | 50750 | 48672 | 374654 | 747415 | 241128 | 506287 | 0.21961 | 120.0551 | 43723.4723 | 2.9383e-07 | 0.00016063 | 0.0585 | 4.9541 | 1.4557e-06 | 0.00079577 | 0.28982 | CAISO_CHP | Natural Gas Fired Combustion Turbine | Coalinga Cogeneration Facility | 6.8 | 0.85 | 0.86 | 81.71% | 4 |  | 1 |  | 47.6082 | 51.611 | 3 | Yes | Fresno | Coalinga, Panoche 115 kV | No | No Published Factor | 4 | 793 | High | Outside_DAC | 10.6038 | 1 | 1.5915 | 1.3004 | 3 | NA_Extreme | NA_Moderate | 4 | 4 | 70.8333 | 0
|  | CHINO_6_CIMGEN | Chino Co-Generation | 26 | 31.6 | SCE | O.L.S. Energy - Chino | COMBINED CYCLE | NATURAL GAS | SP15 | 2018-06-27 | Chino | 230 | 50850 | 24709 | 34075 | 247531 | 180717 | 66814 | 0.071818 | 33.5152 | 14480.4624 | 2.9014e-07 | 0.0001354 | 0.0585 | 7.3138 | 2.122e-06 | 0.00099027 | 0.42786 | CAISO_CHP | Natural Gas Fired Combined Cycle | OLS Energy Chino | 30.8 | 26 | 26 | 9.158% | 1 |  | 3 |  | 17.5233 | 21.526 | 1 | Yes | LA Basin | Eastern | No | No Published Factor | 4 | 1141 | High | DAC_Adjacent | 1.5321 | 3 | 1.9805 | 0.18138 | 1 | NA_Extreme | NA_Moderate | 4 | 4 | 70.8333 | 1
|  | SNCLRA_6_OXGEN | OXGEN | 47.7 | 47.7 | SCE | EF Oxnard LLC | COMBUSTION TURBINE | NATURAL GAS | SP15 | 2020-06-01 | Santa Clara | 230 | 10776 | 157062 | 86544 | 1449560 | 1252870 | 196690 | 0.42184 | 230.6055 | 84798.6681 | 2.9101e-07 | 0.00015909 | 0.0585 | 7.9769 | 2.3214e-06 | 0.001269 | 0.46665 | CAISO_CHP | Natural Gas Fired Combustion Turbine | E F Oxnard Energy Facility | 48.5 | 48.13 | 48.13 | 36.97% | 1 |  | 3 |  | 15.5918 | 19.5945 | 1 | Yes | BC/Ventura | S.Clara, Moorpark | No | No Published Factor | 4 | 657 | High | In_DAC |  | 4 | 2.538 | 0.93826 | 2 | NA_Serious | A | 2 | 2 | 70.8333 | 1
| YES | HOLGAT_1_BORAX | U.S. Borax, Unit 1 | 48.2 | 48.2 | SCE | U.S. Borax Inc. |  | OTHER | SP15 | 1984-06-01 | Kramer | 230 | 50115 | 282302 | 1732330 | 3742979 | 1401992 | 2340987 | 1.0827 | 591.8499 | 218962.7432 | 2.8925e-07 | 0.00015812 | 0.0585 | 4.9663 | 1.4365e-06 | 0.00078528 | 0.29053 | CAISO_CHP | Natural Gas Fired Combustion Turbine | US Borax | 48.2 | 12.56 | 11.63 | 66.86% | 3 |  | 2 |  | 51.6164 | 55.6192 | 4 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | DAC_Adjacent | 0.35003 | 3 | 1.5706 | 1.0501 | 2 | NA_Moderate | A | 1.5 | 2 | 70.8333 | 0
| YES | SUNSET_2_UNITS | MIDWAY SUNSET COGENERATION PLANT | 248 | 291 | PGAE | Midway Sunset Cogeneration Company | FTUR | NATURAL GAS | ZP26 | 1989-12-18 | Midway | 230 | 52169 | 850069 | 5237207 | 10249621 | 3703111 | 6546510 | 2.9718 | 1624.6107 | 599598.6436 | 2.8995e-07 | 0.0001585 | 0.0585 | 4.3562 | 1.2631e-06 | 0.00069048 | 0.25484 | CAISO_CHP | Natural Gas Fired Combustion Turbine | Midway Sunset Cogen | 234 | 229.5 | 232.23 | 41.47% | 1 |  | 1 |  | 46.0658 | 50.0685 | 2 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | DAC_Adjacent | 0.0043398 | 3 | 1.381 | 0.57269 | 1 | NA_Extreme | NA_Moderate | 4 | 4 | 67.7083 | 0
| YES | ARCOGN_2_UNITS | WATSON COGENERATION | 305 | 416.6 | SCE | Watson Cogeneration Company | COMBINED CYCLE | NATURAL GAS | SP15 | 1987-12-04 | Hinson | 230 | 50216 | 2988696 | 11797592 | 35475840 | 16447471 | 19028369 | 64.1622 | 4176.9838 | 1736126.8332 | 1.8086e-06 | 0.00011774 | 0.048938 | 5.5032 | 9.9532e-06 | 0.00064796 | 0.26932 | CAISO_CHP | Natural Gas Fired Combined Cycle | Watson Cogeneration | 405 | 259.89 | 256.73 | 84.24% | 4 |  | 2 |  | 48.1068 | 52.1096 | 3 | Yes | LA Basin | Western | Yes | 23 | 1 | 1141 | High | In_DAC |  | 4 | 1.2959 | 1.0917 | 3 | NA_Extreme | NA_Moderate | 4 | 4 | 67.7083 | 1
| YES | SRINTL_6_UNIT | SRI INTERNATIONAL | 6.9 | 6.9 | PGAE | Pacific Gas & Electric Company | COMBUSTION TURBINE | NATURAL GAS | NP15 | 1987-03-10 | Monte Vista | 230 | 50537 | 28860 | 153875 | 459974 | 185197 | 274777 | 0.13339 | 72.9183 | 26908.2912 | 2.8999e-07 | 0.00015853 | 0.0585 | 6.4171 | 1.8609e-06 | 0.0010173 | 0.3754 | CAISO_CHP | Natural Gas Fired Combustion Turbine | SRI International Cogen Project | 6 | 0.78 | 0.75 | 54.91% | 2 |  | 1 |  | 48.8438 | 52.8466 | 3 | Yes | Bay Area | 0 | No | No Published Factor | 4 | 2220 | High | DAC_Adjacent | 1.49 | 3 | 2.0346 | 1.1172 | 3 | NA_Marginal | A | 1.25 | 1 | 67.7083 | 0
|  | PLMSSR_6_HISIER | High Sierra Cogeneration Aggregate | 6 | 6 | PGAE | Plumas Sierra REC | RECIPROCATING ENGINE | NATURAL GAS | NP15 | 2010-04-22 | Caribou | 115 | 57977 | 34849 | 70879 | 366892 | 233162 | 133730 | 0.10533 | 485.9127 | 21463.0322 | 2.8708e-07 | 0.0013244 | 0.0585 | 6.6906 | 1.9208e-06 | 0.0088611 | 0.3914 | CAISO_CHP | Natural Gas Internal Combustion Engine | High Sierra Cogeneration Plant | 6 | 0 | 0 | 66.3% | 3 |  | 4 |  | 25.7096 | 29.7123 | 1 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | Outside_DAC | 8229.8474 | 1 | 17.7222 | 11.7504 | 4 | A | A | 1 | 1 | 65.625 | 1
| YES | CROKET_7_UNIT | CROCKETT COGEN | 240 | 240 | PGAE | Pacific Gas & Electric Company | COMBINED CYCLE | NATURAL GAS | NP15 | 1995-12-20 | Christie | 115 | 55084 | 1372884 | 2369377 | 12598202 | 8441402 | 4156800 | 3.6273 | 1692.7242 | 736989.6732 | 2.8792e-07 | 0.00013436 | 0.0585 | 6.1487 | 1.7703e-06 | 0.00082615 | 0.35969 | CAISO_CHP | Natural Gas Fired Combined Cycle | Crockett Cogen Project | 247.4 | 211.49 | 165.57 | 63.35% | 3 |  | 3 |  | 40.0575 | 44.0603 | 1 | Yes | Bay Area | Pittsburg | No | No Published Factor | 4 | 2220 | High | DAC_Adjacent | 0.6894 | 3 | 1.6523 | 1.0467 | 2 | NA_Marginal | A | 1.25 | 1 | 63.5417 | 1
| YES | OROVIL_6_UNIT | Oroville Cogeneration, LP | 7.5 | 9.8 | PGAE | Oroville Cogeneration, L.P. | RECIPROCATING ENGINE | NATURAL GAS | NP15 | 1989-12-18 | Wyandotte | 115 | 54477 | 156 | 1219 | 2614 | 795 | 1819 | 0.0007614 | 3.5126 | 152.9179 | 2.9128e-07 | 0.0013438 | 0.0585 | 5.0962 | 1.4844e-06 | 0.006848 | 0.29812 | CAISO_CHP | Natural Gas Internal Combustion Engine | Oroville Cogeneration LP | 7.7 | 7.5 | 7.5 | 0.2313% | 1 |  | 4 |  | 46.0658 | 50.0685 | 2 | Yes | Sierra | Drum-Rio Oso | Yes | 6 | 3 | 75 | High | DAC_Adjacent | 1.0652 | 3 | 13.696 | 0.031676 | 1 | NA_Marginal | A | 1.25 | 1 | 59.375 | 0
| YES | UNCHEM_1_UNIT | CONTRA COSTA CARBON PLANT | 19 | 20 | PGAE | Phillips 66 Company | STEAM | COAL | NP15 | 1983-01-01 | Christie | 115 | 50388 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [7 empty] | CAISO_CHP | Petroleum Coke | CONTRA COSTA CARBON PLANT | 27.3 | 13.1 | 10.21 | 0% | 1 |  | 3 |  | 53.0329 | 57.0356 | 4 | Yes | Bay Area | Pittsburg | Yes | 24 | 1 | 2220 | High | DAC_Adjacent | 1.63 | 3 | Not Available | Not Available | 2.5 | NA_Marginal | A | 1.25 | 1 | 56.25 | 1
|  | GRNLF2_1_UNIT | GREENLEAF II COGEN | 49.2 | 63.8 | PGAE | Greenleaf Energy Unit 2 LLC | COMBUSTION TURBINE | NATURAL GAS | NP15 | 2020-06-01 | Pease | 115 | 10349 | 226368 | 202800 | 2198215 | 1747551 | 450664 | 0.111 | 15.553 | 128594.68 | 5.0496e-08 | 7.0753e-06 | 0.0585 | 7.72 | 3.8982e-07 | 5.4621e-05 | 0.45161 | CAISO_CHP | Natural Gas Fired Combustion Turbine | Greenleaf 2 Power Plant | 49.5 | 49.2 | 49.2 | 52.2% | 2 |  | 3 |  | 15.5918 | 19.5945 | 1 | Yes | Sierra | Pease, Drum-Rio Oso | Yes | 17 | 3 | 75 | High | DAC_Adjacent | 1.2135 | 3 | 0.10924 | 0.057029 | 1 | A | A | 1 | 1 | 52.0833 | 1
| YES | SALIRV_2_UNIT | Salinas River Cogeneration | 39 | 57 | PGAE | Chevron Power Holdings, Inc | FTUR | NATURAL GAS | NP15 | 1991-10-11 | Coburn | 230 | 50865 | 301448 | 913626 | 3998386 | 2133843 | 1864543 | 1.234 | 20.526 | 233903.9485 | 3.0862e-07 | 5.1336e-06 | 0.0585 | 7.0786 | 2.1846e-06 | 3.6339e-05 | 0.4141 | CAISO_CHP | Natural Gas Fired Combustion Turbine | Salinas River Cogeneration | 38.9 | 29.35 | 22.68 | 88.46% | 4 |  | 2 |  | 44.2521 | 48.2548 | 2 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | Outside_DAC | 35.6025 | 1 | 0.072677 | 0.064292 | 1 | A | A | 1 | 1 | 50 | 0
|  | SEARLS_7_ARGUS | Argus Cogeneration | 19 | 62.5 | SCE | Searles Valley Minerals Inc. |  | OTHER | SP15 | 2013-11-15 | Inyokern | 115 | 10684 | 295787 | 12407613 | 15313999 | 1372865 | 13941134 | 360.1926 | 914.2492 | 1542119.9368 | 2.352e-05 | 5.97e-05 | 0.1007 | 4.6414 | 0.00010917 | 0.00027709 | 0.46739 | CAISO_CHP | Conventional Steam Coal | Argus Cogen Plant | 62.5 | 4.01 | 3.96 | 54.03% | 2 |  | 3 |  | 22.1397 | 26.1425 | 1 | No | Not_in_LCR | Not_in_LCR | No | No Published Factor | 4 | CAISO_System | High | Outside_DAC | 27.1787 | 1 | 0.55418 | 0.2994 | 1 | A | A | 1 | 1 | 50 | 1
|  | SAMPSN_6_KELCO1 | KELCO QUALIFYING FACILITY | 25 | 28 | SCE | CP Kelco U.S., Inc. | COMBUSTION TURBINE | OTHER | SP15 | 2014-03-05 | Silvergate | 230 | 52147 | 81590 | 346189 | 1012885 | 454517 | 558368 | 0.29801 | 162.9099 | 59253.3589 | 2.9421e-07 | 0.00016084 | 0.0585 | 5.5707 | 1.639e-06 | 0.00089598 | 0.32589 | CAISO_CHP | Natural Gas Fired Combustion Turbine | C P Kelco San Diego Plant | 29.2 | 0.85 | 1.74 | 31.9% | 1 |  | 2 |  | 21.8384 | 25.8411 | 1 | Yes | SD-IV | San Diego | Yes | 22 | 2 | 920 | High | In_DAC |  | 4 | 1.792 | 0.57158 | 1 | NA_Moderate | A | 1.5 | 2 | 48.9583 | 1
|  | STOILS_1_UNITS | Chevron Richmond Refinery | 56.2 |  | PGAE | Chevron Products Company | COMBINED CYCLE | NATURAL GAS | NP15 | 1992-08-31 | Richmond R | 115 | 52109 | 868496 | 6216691 | 11533622 | 3762757 | 7770865 | 3.3675 | 1237.2318 | 525119.3034 | 2.9197e-07 | 0.00010727 | 0.045529 | 4.3325 | 1.265e-06 | 0.00046475 | 0.19726 | CAISO_CHP | Natural Gas Fired Combined Cycle | Richmond Cogen | 155.6 | 5.14 | 0.07 | 63.72% | 3 |  | 1 |  | 43.3616 | 47.3644 | 2 | Yes | Bay Area | Pittsburg | Yes | 25 | 1 | 2220 | High | DAC_Adjacent | 0.78227 | 3 | 0.92951 | 0.59225 | 1 | NA_Marginal | A | 1.25 | 1 | 37.5 | 1

## DataTab_LCR_Battery_Info
2022-23 TPP Appendix J
| Area/Sub-area | Pmax MW | Energy MWh | Max. # of discharge hours | Max. MW of 4 hour battery (1 for 1 MW replacement) | Replacing mostly |  |  |  | Max. 4-hr storage | Replacing Gas? (per 2032 study) | Ozone Attainment Status | Ozone Score | PM2.5 Attainment Status | PM2.5 Score
| Humboldt | 19 | 76 | 11 | 19 | gas |  | Humboldt | Humboldt | 19 | Yes
North Coast/North Bay Overall |  | 410 | 3101 | 12 | 300 | geothermal |  | North Coast/North Bay Overall | North Coast/North Bay Overall | 300 | No | NA_Extreme | 2 | NA_Moderate | 2
| Eagle Rock (Sub) | 75 | 485 | 10 | 25 | geothermal |  | Sierra | Sierra | 75 | No | NA_Severe 15 | 1.75 | A | 0.5
| Fulton (Sub) | 265 | 1550 | 9 | 175 | geothermal |  | Stockton | Stockton | 545 | Yes | NA_Serious | 1.5
Sierra | [7 empty] | Bay Area | Bay Area | 2220 | Yes | NA_Moderate | 1
| Placer | 96 | 477 | 10 | 75 | hydro |  | Fresno | Fresno | 793 | No | NA_Marginal | 0.75
Stockton | [7 empty] | Kern | Kern | 270 | Yes | A | 0.5
| Telsa-Belloa | 546 | 4111 | 16 | 545 | gas |  | Big Creek-Ventura | BC/Ventura | 657 | Yes
Greater Bay Overall |  | 2970 | 15039 | 9 | 2220 | gas |  | LA Basin | LA Basin | 1141 | Yes
| Llagas | 80 | 556 | 10 | 18 | gas |  | San Diego-IV | SD-IV | 920 | Yes
| San Jose | 850 | 2143 | 15 | 536 | gas
| South Bay-Moss Landing | 1010 | 5641 | 19 | 965 | gas
| Oakland |  |  |  |  | distillate | limit reached
Greater Fresno Overall |  | 1223 | 5965 | 10 | 793 | hydro
| Panoche | 120 | 971 | 12 | 53 | gas
| Herndon | 450 | 2531 | 9 | 260 | hydro
| Borden | [5 empty] | Need eliminated
| Hanford | 62 | 433 | 10 | 38 | gas
Coalinga
| Reedley | 85 | 136 | 18 | 34 | none
Kern Overall
| Westpark | 45 | 223 | 8 | 20 | gas
Kern 70 kV
Kern Tevis
| Kern Oil | 130 | 632 | 9 | 100 | gas
| South Kern PP | 323 | 2017 | 10 | 150 | gas
Big Creek/Ventura |  | 743 | 3445 | 19 | 657 | gas
| Vestal | 181 | 851 | 18 | 152 | hydro
LA Basin Overall |  | 2881 | 21215 | 13 | 1141 | gas
| Eastern | 838 | 68232 | 12 | 240 | gas
| Western | 2067 | 13784 | 12 | 1141 | gas
| El Nido | 269 | 2001 | 11 | 68 | gas
San Diego/Imperial Valley Overall |  | 1585 | 8564 | 9 | 920 | gas
| San Diego | 1585 | 8564 | 9 | 920 | gas
| Border | 37 | 200 | 8 | 19 | gas