## README
Workbook Explanation: | This workbook processes the filtered and aggregated outputs of a Python script to evaluate Unforced Capacities (UCAP) for resources. The script combines daily digests of CAISO's OMS data, available from CAISO's website as Prior Trade Day Curtailment Reports, and aggregates seasonal outages coincident with a selected set of demand hours. This workbook further aggregates and evaluates this data to determine the Equivalent Forced Outage Rate during Demand (EFORd) at various levels of aggregation. Each resource has two UCAP values: one applying an individually assessed EFORd and one using a group-assessed EFORd. The individually assessed EFORd values reflect outage rates from the best three of the most recent four years of outage data. In cases where resources don't have four years of historic data because they were constructed more recently, missing data is replaced with capacity-weighted class averages for the relevant years and seasons. Resources are grouped using CPUC's Resource Type field as found in the Master Resource Database. While all outage data is summarized in the input worksheet, the intermediate calculation and results worksheets are filtered to show only the Resource Types to which UCAP applies. EFORd is calculated as the quotient of [outage MWh during demand] / [maximum possible MWh during demand]. Outage MWh during demand are the sum of all products of the magnitude of each outage in MW multiplied by the overlap between the outage and the selected demand hours, excluding any natures-of-work specified on the settings sheet. UCAP MW is each resource's Pmax or Net Dependable Capacity (NDC) multiplied by one minus the applicable EFORd, either individually or group-assessed. The workbook is organized with input data in tabs toward the right and results toward the left, with intermediate calculations in the middle and a single worksheet of settings immediately following the README worksheet. EFORd values for ambient derations due to temperature are presented separately in this workbook, but included in the final calculations of UCAP MW. These EFORd values are calculated the same as other natures-of-work, but will be replaced with weather-normalized outage rates in a later version of this workbook. Their inclusion at this time is intended to provide a sense of the magnitude of their expected contribution toward rating capacities in the eventual UCAP framework. Each group of worksheets is explained in greater detail below.
Settings: | The worksheet named "Settings" contains several parameters that control various aspects of the workbook, including file paths from which data is to be extracted, which nature-of-work codes to exclude from the UCAP evaluation, and how many years to look back and exclude.
Results: | The results consist of two worksheets named "Resource UCAP" and "Resource Type UCAP". The first worksheet presents the UCAP MW values for each resource and season, evaluated based on individually-assessed alongside group-assessed EFORd. The second worksheet presents the total UCAP MW aggregated by Resource Type, again applying both individual and group assessments.
Intermediate Calculations: | This workbook uses Excel's PowerQuery feature to generate indices for multiple tables with varying levels of aggregation based on Resource ID, Year, and Season defined in the outage results file from the Python script, as well as Resource Type, Fuel, and Technology defined in the Resource Database worksheet. Each query is loaded into its own worksheet, where cell formulas process outage data with parameters from the Resource Database and Settings worksheets to calculate aggregate EFORd values. The worksheet named "ResourceYearSeasonNOW" calculates the individual contributions toward each resource's EFORd from every Nature-of-Work code in each year and season. Outage MWh during demand, i.e., the numerator of EFORd, are retrieved directly from the extracted outage data, while the maximum possible MWh during demand are copied from the worksheet "ResourceTypeYearSeason". The worksheet named "ResourceYearSeason" is used primarily to calculate the maximum possible MWh during demand for each resource during each year and season. It also applies a group-averaged EFORd for any resource during years and seasons where it did not show any possible MWh, e.g., before its commercial operation date. This worksheet includes two iterations of evaluating capacity-weighted class average EFORd values--the first iteration includes all available data from individual resources, while the second iteration excludes the worst year or years as specified in the Settings worksheet. The class average calculations are distributed between this worksheet and "ResourceTypeYearSeason". The worksheet named "ResourceYear" calculates each resource's annual EFORd using the EFORd values calculated on the worksheet named "ResourceYearSeason", and determines which years to include in UCAP. The worksheet named "ResourceTypeYearSeason" determines capacity-weighted class average EFORd values for use in replacing missing data at the indivdual resource-season level. This worksheet includes the calculations to aggregate outage and maximum MWh during demand hours by Resource Type which are used in both iterations of assessing capacity-weighted class average EFORd, which is applied to individual resources to replace missing data in the "ResourceYearSeason" worksheet.
Input Data: | Four data sources are input directly into the worksheets named "Resource Database", "Commercial Operation Dates", "DemandHours", and "OutageData". The first two are excerpted from the most recent versions of CPUC's Master Resource Database and CAISO's Master Generation List, respectively.

## Settings
Parameter | Value | Comments
Historic Evaluation Period: | 4 | years
Year Exclusion Count: | 1 | years
Excluded Nature-of-Work Codes: | NEW_GENERATOR_TEST_ENERGY, UNIT_TESTING, RIMS_TESTING, TRANSMISSION_INDUCED | Comma Separated NOW Codes
Nonsummer Months: | 1,2,3,4,5,11,12 | Comma Separated Month Number
Summer Months: | 6,7,8,9,10 | Comma Separated Month Numbers

## Resource UCAP
RESOURCE ID | RESOURCE TYPE | SEASON | PMAX OR NDC MW | INDIVIDUAL EFORD EXCLUDING AMBIENT DUE TO TEMPERATURE | INDIVIDUAL EFORD AMBIENT DUE TO TEMPERATURE | UCAP MW - INDIVIDUAL ASSESSMENT | GROUP EFORD EXCLUDING AMBIENT DUE TO TEMPERATURE | GROUP EFORD AMBIENT DUE TO TEMPERATURE | UCAP MW - GROUP ASSESSMENT
ALAMIT_2_AESBT2 | Battery Storage | nonsummer | 82 | 11% | 0% | 72.9821 | 8.09% | 0% | 75.3659
ALAMIT_2_AESBT2 | Battery Storage | summer | 82 | 9.688% | 0% | 74.0559 | 8.936% | 0% | 74.6725
ALAMIT_7_ES1 | Battery Storage | nonsummer | 100.45 | 19.17% | 0% | 81.1915 | 8.09% | 0% | 92.3232
ALAMIT_7_ES1 | Battery Storage | summer | 100.45 | 16.58% | 0% | 83.796 | 8.936% | 0% | 91.4738
BERCYN_2_BCEBT1 | Battery Storage | nonsummer | 13 | 9.145% | 0% | 11.8112 | 8.09% | 0% | 11.9482
BERCYN_2_BCEBT1 | Battery Storage | summer | 13 | 8.909% | 0% | 11.8418 | 8.936% | 0% | 11.8383
BGROCK_2_BRFBX2 | Battery Storage | nonsummer | 200 | 9.427% | 0% | 181.1467 | 8.09% | 0% | 183.8192
BGROCK_2_BRFBX2 | Battery Storage | summer | 200 | 9.688% | 0% | 180.6242 | 8.936% | 0% | 182.1281
BLKDIA_2_BDEBT1 | Battery Storage | nonsummer | 200 | 3.774% | 0% | 192.4521 | 8.09% | 0% | 183.8192
BLKDIA_2_BDEBT1 | Battery Storage | summer | 200 | 11.5% | 0% | 177.0073 | 8.936% | 0% | 182.1281
BLM W_2_MDRBT1 | Battery Storage | nonsummer | 20 | 9.427% | 0% | 18.1147 | 8.09% | 0% | 18.3819
BLM W_2_MDRBT1 | Battery Storage | summer | 20 | 9.688% | 0% | 18.0624 | 8.936% | 0% | 18.2128
BLVRDE_6_BLVBT1 | Battery Storage | nonsummer | 10 | 9.138% | 0% | 9.0862 | 8.09% | 0% | 9.191
BLVRDE_6_BLVBT1 | Battery Storage | summer | 10 | 15.59% | 0% | 8.4414 | 8.936% | 0% | 9.1064
CABLRO_2_CBSBT1 | Battery Storage | nonsummer | 99.7 | 9.427% | 0% | 90.3016 | 8.09% | 0% | 91.6338
CABLRO_2_CBSBT1 | Battery Storage | summer | 99.7 | 9.688% | 0% | 90.0411 | 8.936% | 0% | 90.7909
CALGEN_1_MDRBT1 | Battery Storage | nonsummer | 25 | 9.427% | 0% | 22.6433 | 8.09% | 0% | 22.9774
CALGEN_1_MDRBT1 | Battery Storage | summer | 25 | 9.688% | 0% | 22.578 | 8.936% | 0% | 22.766
CASCES_6_CESBT1 | Battery Storage | nonsummer | 25 | 8.542% | 0% | 22.8644 | 8.09% | 0% | 22.9774
CASCES_6_CESBT1 | Battery Storage | summer | 25 | 7.457% | 0% | 23.1358 | 8.936% | 0% | 22.766
CASCES_6_CESBT2 | Battery Storage | nonsummer | 20 | 9.427% | 0% | 18.1147 | 8.09% | 0% | 18.3819
CASCES_6_CESBT2 | Battery Storage | summer | 20 | 9.688% | 0% | 18.0624 | 8.936% | 0% | 18.2128
CHINO_2_APEBT1 | Battery Storage | nonsummer | 20 | 6.594% | 0% | 18.6812 | 8.09% | 0% | 18.3819
CHINO_2_APEBT1 | Battery Storage | summer | 20 | 8.741% | 0% | 18.2518 | 8.936% | 0% | 18.2128
CHINO_2_PESBT1 | Battery Storage | nonsummer | 20 | 13.22% | 0% | 17.3564 | 8.09% | 0% | 18.3819
CHINO_2_PESBT1 | Battery Storage | summer | 20 | 10.48% | 0% | 17.9034 | 8.936% | 0% | 18.2128
CLRMNT_6_CLEBT1 | Battery Storage | nonsummer | 9 | 10.89% | 0% | 8.0201 | 8.09% | 0% | 8.2719
CLRMNT_6_CLEBT1 | Battery Storage | summer | 9 | 6.929% | 0% | 8.3764 | 8.936% | 0% | 8.1958
CONDOR_2_CDRBT1 | Battery Storage | nonsummer | 200 | 9.098% | 0% | 181.8031 | 8.09% | 0% | 183.8192
CONDOR_2_CDRBT1 | Battery Storage | summer | 200 | 8.042% | 0% | 183.9158 | 8.936% | 0% | 182.1281
CRIMSN_2_CRMBT1 | Battery Storage | nonsummer | 200 | 10.41% | 0% | 179.1871 | 8.09% | 0% | 183.8192
CRIMSN_2_CRMBT1 | Battery Storage | summer | 200 | 7.907% | 0% | 184.186 | 8.936% | 0% | 182.1281
CRIMSN_2_CRMBT2 | Battery Storage | nonsummer | 150 | 6.558% | 0% | 140.1633 | 8.09% | 0% | 137.8644
CRIMSN_2_CRMBT2 | Battery Storage | summer | 150 | 6.608% | 0% | 140.0878 | 8.936% | 0% | 136.5961
DYLAN_2_BMTBT1 | Battery Storage | nonsummer | 100 | 8.878% | 0% | 91.1222 | 8.09% | 0% | 91.9096
DYLAN_2_BMTBT1 | Battery Storage | summer | 100 | 8.492% | 0% | 91.5082 | 8.936% | 0% | 91.0641
ELCAJN_6_EB1BT1 | Battery Storage | nonsummer | 7.5 | 5.626% | 0% | 7.0781 | 8.09% | 0% | 6.8932
ELCAJN_6_EB1BT1 | Battery Storage | summer | 7.5 | 9.256% | 0% | 6.8058 | 8.936% | 0% | 6.8298
ELKHRN_1_EESX3 | Battery Storage | nonsummer | 182.5 | 17.87% | 0% | 149.879 | 8.09% | 0% | 167.735
ELKHRN_1_EESX3 | Battery Storage | summer | 182.5 | 14.95% | 0% | 155.2157 | 8.936% | 0% | 166.1919
ELLIOT_6_ELIBT1 | Battery Storage | nonsummer | 10 | 9.439% | 0% | 9.0561 | 8.09% | 0% | 9.191
ELLIOT_6_ELIBT1 | Battery Storage | summer | 10 | 8.141% | 0% | 9.1859 | 8.936% | 0% | 9.1064
ESCNDO_6_EB1BT1 | Battery Storage | nonsummer | 10 | 23.91% | 0% | 7.6092 | 8.09% | 0% | 9.191
ESCNDO_6_EB1BT1 | Battery Storage | summer | 10 | 27.19% | 0% | 7.2806 | 8.936% | 0% | 9.1064
ESCNDO_6_EB2BT2 | Battery Storage | nonsummer | 10 | 25.89% | 0% | 7.4113 | 8.09% | 0% | 9.191
ESCNDO_6_EB2BT2 | Battery Storage | summer | 10 | 29.08% | 0% | 7.0921 | 8.936% | 0% | 9.1064
ESCNDO_6_EB3BT3 | Battery Storage | nonsummer | 10 | 28.92% | 0% | 7.1079 | 8.09% | 0% | 9.191
ESCNDO_6_EB3BT3 | Battery Storage | summer | 10 | 29.41% | 0% | 7.0595 | 8.936% | 0% | 9.1064
ESNHWR_2_CS1BT3 | Battery Storage | nonsummer | 10 | 9.427% | 0% | 9.0573 | 8.09% | 0% | 9.191
ESNHWR_2_CS1BT3 | Battery Storage | summer | 10 | 9.688% | 0% | 9.0312 | 8.936% | 0% | 9.1064
ESNHWR_2_HDSBT2 | Battery Storage | nonsummer | 10 | 9.427% | 0% | 9.0573 | 8.09% | 0% | 9.191
ESNHWR_2_HDSBT2 | Battery Storage | summer | 10 | 9.688% | 0% | 9.0312 | 8.936% | 0% | 9.1064
ESNHWR_2_WC1BT1 | Battery Storage | nonsummer | 3 | 4.867% | 0% | 2.854 | 8.09% | 0% | 2.7573
ESNHWR_2_WC1BT1 | Battery Storage | summer | 3 | 14.72% | 0% | 2.5584 | 8.936% | 0% | 2.7319
ETIWND_2_SEPBT1 | Battery Storage | nonsummer | 100 | 13.97% | 0% | 86.0296 | 8.09% | 0% | 91.9096
ETIWND_2_SEPBT1 | Battery Storage | summer | 100 | 11.58% | 0% | 88.4231 | 8.936% | 0% | 91.0641
ETIWND_6_INEBT1 | Battery Storage | nonsummer | 70 | 12.32% | 0% | 61.3758 | 8.09% | 0% | 64.3367
ETIWND_6_INEBT1 | Battery Storage | summer | 70 | 9.258% | 0% | 63.5193 | 8.936% | 0% | 63.7448
FALBRK_6_FESBT1 | Battery Storage | nonsummer | 40 | 9.805% | 0% | 36.0782 | 8.09% | 0% | 36.7638
FALBRK_6_FESBT1 | Battery Storage | summer | 40 | 12.92% | 0% | 34.8324 | 8.936% | 0% | 36.4256
GATEWY_2_GESBT1 | Battery Storage | nonsummer | 250 | 9.427% | 0% | 226.4334 | 8.09% | 0% | 229.7739
GATEWY_2_GESBT1 | Battery Storage | summer | 250 | 9.688% | 0% | 225.7802 | 8.936% | 0% | 227.6601
GOLETA_2_GE2BT3 | Battery Storage | nonsummer | 60 | 7.929% | 0% | 55.2424 | 8.09% | 0% | 55.1457
GOLETA_2_GE2BT3 | Battery Storage | summer | 60 | 7.015% | 0% | 55.7913 | 8.936% | 0% | 54.6384
GOLETA_2_VALBT1 | Battery Storage | nonsummer | 10 | 3.855% | 0% | 9.6145 | 8.09% | 0% | 9.191
GOLETA_2_VALBT1 | Battery Storage | summer | 10 | 0.7207% | 0% | 9.9279 | 8.936% | 0% | 9.1064
HENRTA_6_HDEBT1 | Battery Storage | nonsummer | 10 | 10.27% | 0% | 8.9735 | 8.09% | 0% | 9.191
HENRTA_6_HDEBT1 | Battery Storage | summer | 10 | 21.23% | 0% | 7.8768 | 8.936% | 0% | 9.1064
JOANEC_2_ST3BT3 | Battery Storage | nonsummer | 40 | 6.78% | 0% | 37.2881 | 8.09% | 0% | 36.7638
JOANEC_2_ST3BT3 | Battery Storage | summer | 40 | 4.707% | 0% | 38.1171 | 8.936% | 0% | 36.4256
JOANEC_2_STABT1 | Battery Storage | nonsummer | 20 | 2.232% | 0% | 19.5537 | 8.09% | 0% | 18.3819
JOANEC_2_STABT1 | Battery Storage | summer | 20 | 2.151% | 0% | 19.5699 | 8.936% | 0% | 18.2128
JOANEC_2_STABT2 | Battery Storage | nonsummer | 20 | 3.651% | 0% | 19.2698 | 8.09% | 0% | 18.3819
JOANEC_2_STABT2 | Battery Storage | summer | 20 | 0.6781% | 0% | 19.8644 | 8.936% | 0% | 18.2128
JOHANN_2_JOSBT1 | Battery Storage | nonsummer | 10 | 10.73% | 0% | 8.9273 | 8.09% | 0% | 9.191
JOHANN_2_JOSBT1 | Battery Storage | summer | 10 | 11% | 0% | 8.9004 | 8.936% | 0% | 9.1064
JOHANN_2_JOSBT2 | Battery Storage | nonsummer | 10 | 4.44% | 0% | 9.556 | 8.09% | 0% | 9.191
JOHANN_2_JOSBT2 | Battery Storage | summer | 10 | 5.978% | 0% | 9.4022 | 8.936% | 0% | 9.1064
JOHANN_2_OCEBT2 | Battery Storage | nonsummer | 9 | 11.46% | 0% | 7.9685 | 8.09% | 0% | 8.2719
JOHANN_2_OCEBT2 | Battery Storage | summer | 9 | 26.68% | 0% | 6.5989 | 8.936% | 0% | 8.1958
JOHANN_2_OCEBT3 | Battery Storage | nonsummer | 6 | 11.58% | 0% | 5.3053 | 8.09% | 0% | 5.5146
JOHANN_2_OCEBT3 | Battery Storage | summer | 6 | 23.59% | 0% | 4.5847 | 8.936% | 0% | 5.4638
KEARNY_6_NESBT1 | Battery Storage | nonsummer | 10 | 4.161% | 0% | 9.5839 | 8.09% | 0% | 9.191
KEARNY_6_NESBT1 | Battery Storage | summer | 10 | 4.822% | 0% | 9.5178 | 8.936% | 0% | 9.1064
KEARNY_6_SESBT2 | Battery Storage | nonsummer | 10 | 5.456% | 0% | 9.4544 | 8.09% | 0% | 9.191
KEARNY_6_SESBT2 | Battery Storage | summer | 10 | 11.85% | 0% | 8.8152 | 8.936% | 0% | 9.1064
KOLA_2_KLBBT1 | Battery Storage | nonsummer | 275 | 9.427% | 0% | 249.0768 | 8.09% | 0% | 252.7513
KOLA_2_KLBBT1 | Battery Storage | summer | 275 | 9.688% | 0% | 248.3582 | 8.936% | 0% | 250.4262
KOLA_2_KLBBT2 | Battery Storage | nonsummer | 125 | 9.427% | 0% | 113.2167 | 8.09% | 0% | 114.887
KOLA_2_KLBBT2 | Battery Storage | summer | 125 | 9.688% | 0% | 112.8901 | 8.936% | 0% | 113.8301
KYCORA_6_KMSBT1 | Battery Storage | nonsummer | 1 | 19.35% | 0% | 0.80647 | 8.09% | 0% | 0.9191
KYCORA_6_KMSBT1 | Battery Storage | summer | 1 | 23.82% | 0% | 0.76181 | 8.936% | 0% | 0.91064
LAGBEL_2_CBPBT1 | Battery Storage | nonsummer | 100 | 9.211% | 0% | 90.7889 | 8.09% | 0% | 91.9096
LAGBEL_2_CBPBT1 | Battery Storage | summer | 100 | 8.12% | 0% | 91.8798 | 8.936% | 0% | 91.0641
LCKHT1_2_LH1BT1 | Battery Storage | nonsummer | 45 | 8.831% | 0% | 41.0262 | 8.09% | 0% | 41.3593
LCKHT1_2_LH1BT1 | Battery Storage | summer | 45 | 7.769% | 0% | 41.5042 | 8.936% | 0% | 40.9788
LECONT_2_LESBT1 | Battery Storage | nonsummer | 125 | 5.111% | 0% | 118.6112 | 8.09% | 0% | 114.887
LECONT_2_LESBT1 | Battery Storage | summer | 125 | 7.613% | 0% | 115.4832 | 8.936% | 0% | 113.8301
MARVEL_2_MARBT3 | Battery Storage | nonsummer | 74.94 | 8.873% | 0% | 68.2909 | 8.09% | 0% | 68.877
MARVEL_2_MARBT3 | Battery Storage | summer | 74.94 | 7.846% | 0% | 69.0605 | 8.936% | 0% | 68.2434
MARVEL_2_MARBX2 | Battery Storage | nonsummer | 325 | 8.672% | 0% | 296.8147 | 8.09% | 0% | 298.7061
MARVEL_2_MARBX2 | Battery Storage | summer | 325 | 7.697% | 0% | 299.984 | 8.936% | 0% | 295.9582
MELRSE_6_MELBT1 | Battery Storage | nonsummer | 10 | 8.131% | 0% | 9.1869 | 8.09% | 0% | 9.191
MELRSE_6_MELBT1 | Battery Storage | summer | 10 | 13.58% | 0% | 8.6417 | 8.936% | 0% | 9.1064
MELRSE_6_MELBT2 | Battery Storage | nonsummer | 10 | 9.168% | 0% | 9.0832 | 8.09% | 0% | 9.191
MELRSE_6_MELBT2 | Battery Storage | summer | 10 | 13.32% | 0% | 8.6678 | 8.936% | 0% | 9.1064
MIRLOM_2_MLBBTA | Battery Storage | nonsummer | 10 | 0.3883% | 0% | 9.9612 | 8.09% | 0% | 9.191
MIRLOM_2_MLBBTA | Battery Storage | summer | 10 | 0.7378% | 0% | 9.9262 | 8.936% | 0% | 9.1064
MIRLOM_2_MLBBTB | Battery Storage | nonsummer | 10 | 2.06% | 0% | 9.794 | 8.09% | 0% | 9.191
MIRLOM_2_MLBBTB | Battery Storage | summer | 10 | 3.955% | 0% | 9.6045 | 8.936% | 0% | 9.1064
MOORPK_2_ACOBT1 | Battery Storage | nonsummer | 1.95 | 5.589% | 0% | 1.841 | 8.09% | 0% | 1.7922
MOORPK_2_ACOBT1 | Battery Storage | summer | 1.95 | 5.202% | 0% | 1.8486 | 8.936% | 0% | 1.7757
MRGT_6_TGEBT1 | Battery Storage | nonsummer | 30 | 13.04% | 0% | 26.0889 | 8.09% | 0% | 27.5729
MRGT_6_TGEBT1 | Battery Storage | summer | 30 | 19.16% | 0% | 24.2518 | 8.936% | 0% | 27.3192
MSOLAR_2_MS4BT1 | Battery Storage | nonsummer | 10 | 14.78% | 0% | 8.5221 | 8.09% | 0% | 9.191
MSOLAR_2_MS4BT1 | Battery Storage | summer | 10 | 12.93% | 0% | 8.707 | 8.936% | 0% | 9.1064
NOAKS_2_PESBT1 | Battery Storage | nonsummer | 80 | 8.966% | 0% | 72.8276 | 8.09% | 0% | 73.5277
NOAKS_2_PESBT1 | Battery Storage | summer | 80 | 9.688% | 0% | 72.2497 | 8.936% | 0% | 72.8512
NORCNV_1_NCVBT1 | Battery Storage | nonsummer | 132 | 8.401% | 0% | 120.9109 | 8.09% | 0% | 121.3206
NORCNV_1_NCVBT1 | Battery Storage | summer | 132 | 6.833% | 0% | 122.9805 | 8.936% | 0% | 120.2046
PALA_6_PGCBT1 | Battery Storage | nonsummer | 10 | 10.44% | 0% | 8.9559 | 8.09% | 0% | 9.191
PALA_6_PGCBT1 | Battery Storage | summer | 10 | 13.39% | 0% | 8.6612 | 8.936% | 0% | 9.1064
PARDSE_6_PESBT1 | Battery Storage | nonsummer | 10 | 8.852% | 0% | 9.1148 | 8.09% | 0% | 9.191
PARDSE_6_PESBT1 | Battery Storage | summer | 10 | 9.254% | 0% | 9.0746 | 8.936% | 0% | 9.1064
PEASE_1_TBEBT1 | Battery Storage | nonsummer | 5 | 8.541% | 0% | 4.5729 | 8.09% | 0% | 4.5955
PEASE_1_TBEBT1 | Battery Storage | summer | 5 | 15.68% | 0% | 4.2159 | 8.936% | 0% | 4.5532
PERGRN_2_PRSBT1 | Battery Storage | nonsummer | 200 | 9.427% | 0% | 181.1467 | 8.09% | 0% | 183.8192
PERGRN_2_PRSBT1 | Battery Storage | summer | 200 | 9.688% | 0% | 180.6242 | 8.936% | 0% | 182.1281
RATSKE_2_WAVBT1 | Battery Storage | nonsummer | 125.96 | 9.427% | 0% | 114.0862 | 8.09% | 0% | 115.7693
RATSKE_2_WAVBT1 | Battery Storage | summer | 125.96 | 9.688% | 0% | 113.7571 | 8.936% | 0% | 114.7043
ROMOLA_5_MPBBT1 | Battery Storage | nonsummer | 230 | 8.841% | 0% | 209.6661 | 8.09% | 0% | 211.392
ROMOLA_5_MPBBT1 | Battery Storage | summer | 230 | 8.927% | 0% | 209.4668 | 8.936% | 0% | 209.4473
ROMOLA_5_MPBBT2 | Battery Storage | nonsummer | 230 | 8.831% | 0% | 209.6894 | 8.09% | 0% | 211.392
ROMOLA_5_MPBBT2 | Battery Storage | summer | 230 | 8.96% | 0% | 209.3914 | 8.936% | 0% | 209.4473
ROMOLA_5_MPBBT3 | Battery Storage | nonsummer | 50 | 8.924% | 0% | 45.5378 | 8.09% | 0% | 45.9548
ROMOLA_5_MPBBT3 | Battery Storage | summer | 50 | 9.056% | 0% | 45.4721 | 8.936% | 0% | 45.532
ROMOLA_5_MPBBT4 | Battery Storage | nonsummer | 110 | 8.927% | 0% | 100.1802 | 8.09% | 0% | 101.1005
ROMOLA_5_MPBBT4 | Battery Storage | summer | 110 | 9.469% | 0% | 99.5844 | 8.936% | 0% | 100.1705
SANBRN_2_ESABT1 | Battery Storage | nonsummer | 100 | 0.338% | 0% | 99.662 | 8.09% | 0% | 91.9096
SANBRN_2_ESABT1 | Battery Storage | summer | 100 | 0.6322% | 0% | 99.3678 | 8.936% | 0% | 91.0641
SANBRN_2_ESBBT1 | Battery Storage | nonsummer | 100 | 0.6877% | 0% | 99.3123 | 8.09% | 0% | 91.9096
SANBRN_2_ESBBT1 | Battery Storage | summer | 100 | 0.2853% | 0% | 99.7147 | 8.936% | 0% | 91.0641
SANBRN_2_SS2BT3 | Battery Storage | nonsummer | 169 | 7.304% | 0% | 156.6566 | 8.09% | 0% | 155.3272
SANBRN_2_SS2BT3 | Battery Storage | summer | 169 | 8.623% | 0% | 154.4265 | 8.936% | 0% | 153.8983
SANBRN_2_SS2BT4 | Battery Storage | nonsummer | 47 | 6.859% | 0% | 43.7763 | 8.09% | 0% | 43.1975
SANBRN_2_SS2BT4 | Battery Storage | summer | 47 | 6.913% | 0% | 43.751 | 8.936% | 0% | 42.8001
SAUGUS_2_SPESBT1 | Battery Storage | nonsummer | 30 | 12.17% | 0% | 26.3479 | 8.09% | 0% | 27.5729
SAUGUS_2_SPESBT1 | Battery Storage | summer | 30 | 12.74% | 0% | 26.1782 | 8.936% | 0% | 27.3192
SNCLRA_2_SILBT1 | Battery Storage | nonsummer | 11 | 2.606% | 0% | 10.7133 | 8.09% | 0% | 10.1101
SNCLRA_2_SILBT1 | Battery Storage | summer | 11 | 0.3893% | 0% | 10.9572 | 8.936% | 0% | 10.017
SNCLRA_2_VESBT1 | Battery Storage | nonsummer | 100 | 2.093% | 0% | 97.9069 | 8.09% | 0% | 91.9096
SNCLRA_2_VESBT1 | Battery Storage | summer | 100 | 3.666% | 0% | 96.3341 | 8.936% | 0% | 91.0641
STANTN_2_SBEBX2 | Battery Storage | nonsummer | 68.8 | 6.999% | 0% | 63.985 | 8.09% | 0% | 63.2338
STANTN_2_SBEBX2 | Battery Storage | summer | 68.8 | 7.92% | 0% | 63.3508 | 8.936% | 0% | 62.6521
TAHOE_2_THOBT1 | Battery Storage | nonsummer | 60.04 | 9.427% | 0% | 54.3802 | 8.09% | 0% | 55.1825
TAHOE_2_THOBT1 | Battery Storage | summer | 60.04 | 9.688% | 0% | 54.2234 | 8.936% | 0% | 54.6749
TAHOE_2_THOBT2 | Battery Storage | nonsummer | 109.06 | 9.427% | 0% | 98.7793 | 8.09% | 0% | 100.2366
TAHOE_2_THOBT2 | Battery Storage | summer | 109.06 | 9.688% | 0% | 98.4944 | 8.936% | 0% | 99.3145
TAHOE_2_THOBT3 | Battery Storage | nonsummer | 110.1 | 9.427% | 0% | 99.7213 | 8.09% | 0% | 101.1924
TAHOE_2_THOBT3 | Battery Storage | summer | 110.1 | 9.688% | 0% | 99.4336 | 8.936% | 0% | 100.2615
TUMBWD_2_WISBT3 | Battery Storage | nonsummer | 50 | 8.831% | 0% | 45.5847 | 8.09% | 0% | 45.9548
TUMBWD_2_WISBT3 | Battery Storage | summer | 50 | 9.088% | 0% | 45.4562 | 8.936% | 0% | 45.532
TUMBWD_2_WISBT4 | Battery Storage | nonsummer | 74.97 | 8.831% | 0% | 68.3496 | 8.09% | 0% | 68.9046
TUMBWD_2_WISBT4 | Battery Storage | summer | 74.97 | 8.3% | 0% | 68.7477 | 8.936% | 0% | 68.2707
VALLEY_5_ORTBT1 | Battery Storage | nonsummer | 20 | 9.427% | 0% | 18.1147 | 8.09% | 0% | 18.3819
VALLEY_5_ORTBT1 | Battery Storage | summer | 20 | 9.688% | 0% | 18.0624 | 8.936% | 0% | 18.2128
VESTAL_2_BTNBT1 | Battery Storage | nonsummer | 80 | 10.66% | 0% | 71.475 | 8.09% | 0% | 73.5277
VESTAL_2_BTNBT1 | Battery Storage | summer | 80 | 10.97% | 0% | 71.2239 | 8.936% | 0% | 72.8512
VISTRA_5_DALBT1 | Battery Storage | nonsummer | 100 | 20.97% | 0% | 79.0272 | 8.09% | 0% | 91.9096
VISTRA_5_DALBT1 | Battery Storage | summer | 100 | 8.315% | 0% | 91.6848 | 8.936% | 0% | 91.0641
VISTRA_5_DALBT2 | Battery Storage | nonsummer | 100 | 4.358% | 0% | 95.6416 | 8.09% | 0% | 91.9096
VISTRA_5_DALBT2 | Battery Storage | summer | 100 | 7.769% | 0% | 92.2307 | 8.936% | 0% | 91.0641
VISTRA_5_DALBT3 | Battery Storage | nonsummer | 100 | 3.623% | 0% | 96.3775 | 8.09% | 0% | 91.9096
VISTRA_5_DALBT3 | Battery Storage | summer | 100 | 10.94% | 0% | 89.0587 | 8.936% | 0% | 91.0641
VISTRA_5_DALBT4 | Battery Storage | nonsummer | 100 | 17.42% | 0% | 82.5791 | 8.09% | 0% | 91.9096
VISTRA_5_DALBT4 | Battery Storage | summer | 100 | 4.908% | 0% | 95.0919 | 8.936% | 0% | 91.0641
VISTRA_5_PLABT1 | Battery Storage | nonsummer | 100.4 | 11.79% | 0% | 88.5584 | 8.09% | 0% | 92.2772
VISTRA_5_PLABT1 | Battery Storage | summer | 100.4 | 4.761% | 0% | 95.6198 | 8.936% | 0% | 91.4283
VISTRA_5_PLABT2 | Battery Storage | nonsummer | 100.4 | 7.825% | 0% | 92.5433 | 8.09% | 0% | 92.2772
VISTRA_5_PLABT2 | Battery Storage | summer | 100.4 | 4.786% | 0% | 95.595 | 8.936% | 0% | 91.4283
VISTRA_5_PLABT3 | Battery Storage | nonsummer | 74.6 | 9.333% | 0% | 67.6373 | 8.09% | 0% | 68.5645
VISTRA_5_PLABT3 | Battery Storage | summer | 74.6 | 4.634% | 0% | 71.143 | 8.936% | 0% | 67.9338
VISTRA_5_PLABT4 | Battery Storage | nonsummer | 74.6 | 7.333% | 0% | 69.1296 | 8.09% | 0% | 68.5645
VISTRA_5_PLABT4 | Battery Storage | summer | 74.6 | 4.792% | 0% | 71.0255 | 8.936% | 0% | 67.9338
VSTAES_6_VESBT1 | Battery Storage | nonsummer | 32 | 7.709% | 0% | 29.533 | 8.09% | 0% | 29.4111
VSTAES_6_VESBT1 | Battery Storage | summer | 32 | 2.581% | 0% | 31.174 | 8.936% | 0% | 29.1405
WDFRDF_2_WFFBT1 | Battery Storage | nonsummer | 25 | 9.072% | 0% | 22.7319 | 8.09% | 0% | 22.9774
WDFRDF_2_WFFBT1 | Battery Storage | summer | 25 | 7.838% | 0% | 23.0404 | 8.936% | 0% | 22.766
WESCAN_2_BDSBT1 | Battery Storage | nonsummer | 131 | 7.196% | 0% | 121.573 | 8.09% | 0% | 120.4015
WESCAN_2_BDSBT1 | Battery Storage | summer | 131 | 8.083% | 0% | 120.4118 | 8.936% | 0% | 119.2939
WESCN2_2_BDSBT1 | Battery Storage | nonsummer | 119 | 9.417% | 0% | 107.7939 | 8.09% | 0% | 109.3724
WESCN2_2_BDSBT1 | Battery Storage | summer | 119 | 9.688% | 0% | 107.4714 | 8.936% | 0% | 108.3662
WSTWND_2_SBSBT1 | Battery Storage | nonsummer | 80 | 6.835% | 0% | 74.532 | 8.09% | 0% | 73.5277
WSTWND_2_SBSBT1 | Battery Storage | summer | 80 | 5.063% | 0% | 75.9498 | 8.936% | 0% | 72.8512
WSTWND_2_SBSBT2 | Battery Storage | nonsummer | 40 | 8.85% | 0% | 36.4602 | 8.09% | 0% | 36.7638
WSTWND_2_SBSBT2 | Battery Storage | summer | 40 | 8.861% | 0% | 36.4555 | 8.936% | 0% | 36.4256
WSTWND_2_SBSBT3 | Battery Storage | nonsummer | 59 | 8.831% | 0% | 53.7899 | 8.09% | 0% | 54.2266
WSTWND_2_SBSBT3 | Battery Storage | summer | 59 | 8.51% | 0% | 53.9791 | 8.936% | 0% | 53.7278
CHILLS_7_UNITA1 | Biogas | nonsummer | 2.25 | 16.15% | 2.056% | 1.8404 | 3.533% | 0.2356% | 2.1652
CHILLS_7_UNITA1 | Biogas | summer | 2.25 | 5.521% | 5.118% | 2.0106 | 1.355% | 0.6279% | 2.2054
CSTRVL_7_PL1X2 | Biogas | nonsummer | 4.53 | 2.403% | 0% | 4.4212 | 3.533% | 0.2356% | 4.3593
CSTRVL_7_PL1X2 | Biogas | summer | 4.53 | 0.5689% | 0% | 4.5042 | 1.355% | 0.6279% | 4.4402
GUERNS_6_HD3BM3 | Biogas | nonsummer | 1 | 9.476% | 0% | 0.90524 | 3.533% | 0.2356% | 0.96231
GUERNS_6_HD3BM3 | Biogas | summer | 1 | 2.058% | 0% | 0.97942 | 1.355% | 0.6279% | 0.98017
GUERNS_6_VH2BM1 | Biogas | nonsummer | 1 | 9.048% | 0% | 0.90952 | 3.533% | 0.2356% | 0.96231
GUERNS_6_VH2BM1 | Biogas | summer | 1 | 6.063% | 0% | 0.93937 | 1.355% | 0.6279% | 0.98017
HARDWK_6_STWBM1 | Biogas | nonsummer | 1 | 3.617% | 0% | 0.96383 | 3.533% | 0.2356% | 0.96231
HARDWK_6_STWBM1 | Biogas | summer | 1 | 3.469% | 0.8105% | 0.9572 | 1.355% | 0.6279% | 0.98017
PSWEET_1_STCRUZ | Biogas | nonsummer | 1.6 | 0% | 0% | 1.6 | 3.533% | 0.2356% | 1.5397
PSWEET_1_STCRUZ | Biogas | summer | 1.6 | 0% | 0% | 1.6 | 1.355% | 0.6279% | 1.5683
SANLOB_1_OSFBM1 | Biogas | nonsummer | 0.85 | 0% | 0% | 0.85 | 3.533% | 0.2356% | 0.81796
SANLOB_1_OSFBM1 | Biogas | summer | 0.85 | 0% | 0% | 0.85 | 1.355% | 0.6279% | 0.83315
USWND4_2_UNIT2 | Biogas | nonsummer | 7.4 | 0% | 0% | 7.4 | 3.533% | 0.2356% | 7.1211
USWND4_2_UNIT2 | Biogas | summer | 7.4 | 0% | 0% | 7.4 | 1.355% | 0.6279% | 7.2533
LASSEN_6_UNITS | Biomass/Wood | nonsummer | 30 | 6.536% | 0% | 28.0393 | 6.536% | 0% | 28.0393
LASSEN_6_UNITS | Biomass/Wood | summer | 30 | 4.616% | 0% | 28.6153 | 4.616% | 0% | 28.6153
AGRICO_7_UNIT | CCGT | nonsummer | 59.97 | 3.541% | 0.8563% | 57.3327 | 7.291% | 1.795% | 54.5208
AGRICO_7_UNIT | CCGT | summer | 59.97 | 2.483% | 2.403% | 57.0401 | 5.249% | 4.657% | 54.0291
ALAMIT_2_PL1X3 | CCGT | nonsummer | 674.7 | 6.325% | 0.02477% | 631.8554 | 7.291% | 1.795% | 613.3934
ALAMIT_2_PL1X3 | CCGT | summer | 674.7 | 0.7456% | 1.171% | 661.7658 | 5.249% | 4.657% | 607.8608
BUCKBL_2_PL1X3 | CCGT | nonsummer | 493.63 | 5.396% | 0% | 466.9952 | 7.291% | 1.795% | 448.7763
BUCKBL_2_PL1X3 | CCGT | summer | 493.63 | 1.547% | 0.03268% | 485.8306 | 5.249% | 4.657% | 444.7285
CALPIN_1_AGNEW | CCGT | nonsummer | 28.56 | 15.56% | 0.5455% | 23.9602 | 7.291% | 1.795% | 25.9649
CALPIN_1_AGNEW | CCGT | summer | 28.56 | 5.96% | 1.95% | 26.3008 | 5.249% | 4.657% | 25.7307
COLUSA_2_PL1X3 | CCGT | nonsummer | 641 | 3.188% | 2.496% | 604.5691 | 7.291% | 1.795% | 582.7556
COLUSA_2_PL1X3 | CCGT | summer | 641 | 2.537% | 7.026% | 579.7033 | 5.249% | 4.657% | 577.4993
CORONS_6_CLRWTR | CCGT | nonsummer | 28 | 0% | 0% | 28 | 7.291% | 1.795% | 25.4558
CORONS_6_CLRWTR | CCGT | summer | 28 | 1.435% | 0% | 27.5983 | 5.249% | 4.657% | 25.2262
DELTA_2_PL1X4 | CCGT | nonsummer | 880 | 8.195% | 1.394% | 795.6154 | 7.291% | 1.795% | 800.0389
DELTA_2_PL1X4 | CCGT | summer | 880 | 4.557% | 4.493% | 800.3596 | 5.249% | 4.657% | 792.8227
DUANE_1_PL1X3 | CCGT | nonsummer | 147.8 | 16.08% | 1.976% | 121.1117 | 7.291% | 1.795% | 134.3702
DUANE_1_PL1X3 | CCGT | summer | 147.8 | 7.046% | 3.886% | 131.6423 | 5.249% | 4.657% | 133.1582
ELKHIL_2_PL1X3 | CCGT | nonsummer | 551.7 | 7.535% | 3.628% | 490.1152 | 7.291% | 1.795% | 501.5698
ELKHIL_2_PL1X3 | CCGT | summer | 551.7 | 11.82% | 8.952% | 437.1237 | 5.249% | 4.657% | 497.0458
ELSEGN_2_UN1011 | CCGT | nonsummer | 274.31 | 3.17% | 0.5637% | 264.0685 | 7.291% | 1.795% | 249.3848
ELSEGN_2_UN1011 | CCGT | summer | 274.31 | 8.725% | 0.5749% | 248.7985 | 5.249% | 4.657% | 247.1354
ELSEGN_2_UN2021 | CCGT | nonsummer | 271.74 | 3.025% | 0.2512% | 262.8362 | 7.291% | 1.795% | 247.0484
ELSEGN_2_UN2021 | CCGT | summer | 271.74 | 10.98% | 0.7651% | 239.8169 | 5.249% | 4.657% | 244.82
GATWAY_2_PL1X3 | CCGT | nonsummer | 585 | 4.889% | 6.495% | 518.4032 | 7.291% | 1.795% | 531.844
GATWAY_2_PL1X3 | CCGT | summer | 585 | 1.695% | 15.96% | 481.7458 | 5.249% | 4.657% | 527.0469
GILROY_1_UNIT | CCGT | nonsummer | 120 | 14.94% | 5.554% | 95.4091 | 7.291% | 1.795% | 109.0962
GILROY_1_UNIT | CCGT | summer | 120 | 2.093% | 9.235% | 106.4065 | 5.249% | 4.657% | 108.1122
GLNARM_2_UNIT 5 | CCGT | nonsummer | 65.81 | 39.81% | 0% | 39.6125 | 7.291% | 1.795% | 59.8302
GLNARM_2_UNIT 5 | CCGT | summer | 65.81 | 34.35% | 0.00157% | 43.2064 | 5.249% | 4.657% | 59.2905
GWFPWR_1_LDCTG1 | CCGT | nonsummer | 55.3 | 7.292% | 1.795% | 50.2746 | 7.291% | 1.795% | 50.2752
GWFPWR_1_LDCTG1 | CCGT | summer | 55.3 | 5.249% | 4.659% | 49.8209 | 5.249% | 4.657% | 49.8217
GWFPWR_1_LDCTG2 | CCGT | nonsummer | 55.3 | 7.292% | 1.795% | 50.2746 | 7.291% | 1.795% | 50.2752
GWFPWR_1_LDCTG2 | CCGT | summer | 55.3 | 5.249% | 4.659% | 49.8209 | 5.249% | 4.657% | 49.8217
HARBGN_7_UNITS | CCGT | nonsummer | 109.01 | 8.581% | 0% | 99.6558 | 7.291% | 1.795% | 99.1048
HARBGN_7_UNITS | CCGT | summer | 109.01 | 12.31% | 9.427% | 85.3165 | 5.249% | 4.657% | 98.2109
HIDSRT_2_UNITS | CCGT | nonsummer | 850 | 7.277% | 2.361% | 768.0788 | 7.291% | 1.795% | 772.7648
HIDSRT_2_UNITS | CCGT | summer | 850 | 3.878% | 3.791% | 784.8071 | 5.249% | 4.657% | 765.7947
HNTGBH_2_PL1X3 | CCGT | nonsummer | 673.8 | 3.649% | 0.01709% | 649.0967 | 7.291% | 1.795% | 612.5752
HNTGBH_2_PL1X3 | CCGT | summer | 673.8 | 3.372% | 1.345% | 642.0209 | 5.249% | 4.657% | 607.0499
LAPLMA_2_UNIT 1 | CCGT | nonsummer | 267 | 7.991% | 3.213% | 237.0851 | 7.291% | 1.795% | 242.7391
LAPLMA_2_UNIT 1 | CCGT | summer | 267 | 4.497% | 5.001% | 241.6407 | 5.249% | 4.657% | 240.5496
LAPLMA_2_UNIT 2 | CCGT | nonsummer | 266 | 6.598% | 3.383% | 239.4502 | 7.291% | 1.795% | 241.8299
LAPLMA_2_UNIT 2 | CCGT | summer | 266 | 3.609% | 4.577% | 244.224 | 5.249% | 4.657% | 239.6487
LAPLMA_2_UNIT 3 | CCGT | nonsummer | 266 | 4.753% | 4.171% | 242.2626 | 7.291% | 1.795% | 241.8299
LAPLMA_2_UNIT 3 | CCGT | summer | 266 | 4.001% | 4.949% | 242.1935 | 5.249% | 4.657% | 239.6487
LAPLMA_2_UNIT 4 | CCGT | nonsummer | 267 | 6.161% | 4.847% | 237.6089 | 7.291% | 1.795% | 242.7391
LAPLMA_2_UNIT 4 | CCGT | summer | 267 | 17.98% | 5.287% | 204.8855 | 5.249% | 4.657% | 240.5496
LAROA2_2_UNITA1 | CCGT | nonsummer | 322 | 4.447% | 1.857% | 301.6998 | 7.291% | 1.795% | 292.7415
LAROA2_2_UNITA1 | CCGT | summer | 322 | 5.041% | 6.025% | 286.3678 | 5.249% | 4.657% | 290.101
LEBECS_2_UNITS | CCGT | nonsummer | 799.47 | 9.711% | 0.7461% | 715.8666 | 7.291% | 1.795% | 726.8262
LEBECS_2_UNITS | CCGT | summer | 799.47 | 8.297% | 2.359% | 714.2853 | 5.249% | 4.657% | 720.2704
LECEF_1_UNITS | CCGT | nonsummer | 309.84 | 1.074% | 3.407% | 295.9568 | 7.291% | 1.795% | 281.6864
LECEF_1_UNITS | CCGT | summer | 309.84 | 9.313% | 5.147% | 265.0385 | 5.249% | 4.657% | 279.1457
LGHTHP_6_ICEGEN | CCGT | nonsummer | 48 | 13.86% | 0% | 41.3488 | 7.291% | 1.795% | 43.6385
LGHTHP_6_ICEGEN | CCGT | summer | 48 | 19.95% | 0.09441% | 38.3794 | 5.249% | 4.657% | 43.2449
LMEC_1_PL1X3 | CCGT | nonsummer | 580 | 8.189% | 2.09% | 520.3817 | 7.291% | 1.795% | 527.2983
LMEC_1_PL1X3 | CCGT | summer | 580 | 6.267% | 3.533% | 523.1643 | 5.249% | 4.657% | 522.5422
LODIEC_2_PL1X2 | CCGT | nonsummer | 302.58 | 3.692% | 4.6% | 277.4896 | 7.291% | 1.795% | 275.0861
LODIEC_2_PL1X2 | CCGT | summer | 302.58 | 14.7% | 10.48% | 226.4038 | 5.249% | 4.657% | 272.6049
METEC_2_PL1X3 | CCGT | nonsummer | 597.05 | 17.48% | 1.479% | 483.8411 | 7.291% | 1.795% | 542.7991
METEC_2_PL1X3 | CCGT | summer | 597.05 | 8.542% | 3.294% | 526.3826 | 5.249% | 4.657% | 537.9032
MOSSLD_2_PSP1 | CCGT | nonsummer | 510 | 2.71% | 0.0745% | 495.797 | 7.291% | 1.795% | 463.6589
MOSSLD_2_PSP1 | CCGT | summer | 510 | 1.974% | 0.4662% | 497.5537 | 5.249% | 4.657% | 459.4768
MOSSLD_2_PSP2 | CCGT | nonsummer | 510 | 5.274% | 0.06185% | 482.7866 | 7.291% | 1.795% | 463.6589
MOSSLD_2_PSP2 | CCGT | summer | 510 | 1.363% | 0.3173% | 501.4327 | 5.249% | 4.657% | 459.4768
MRCHNT_2_PL1X3 | CCGT | nonsummer | 494.58 | 3.409% | 3.853% | 458.6618 | 7.291% | 1.795% | 449.64
MRCHNT_2_PL1X3 | CCGT | summer | 494.58 | 2.454% | 15.19% | 407.3044 | 5.249% | 4.657% | 445.5844
OTMESA_2_PL1X3 | CCGT | nonsummer | 603.68 | 9.001% | 1.845% | 538.206 | 7.291% | 1.795% | 548.8267
OTMESA_2_PL1X3 | CCGT | summer | 603.68 | 6.117% | 5.52% | 533.4298 | 5.249% | 4.657% | 543.8764
PALOMR_2_PL1X3 | CCGT | nonsummer | 588.21 | 4.4% | 0% | 562.3269 | 7.291% | 1.795% | 534.7623
PALOMR_2_PL1X3 | CCGT | summer | 588.21 | 9.179% | 0.07395% | 533.7858 | 5.249% | 4.657% | 529.9389
RUSCTY_2_UNITS | CCGT | nonsummer | 615.18 | 27.04% | 1.794% | 437.7668 | 7.291% | 1.795% | 559.2817
RUSCTY_2_UNITS | CCGT | summer | 615.18 | 8.294% | 3.991% | 539.6026 | 5.249% | 4.657% | 554.2371
SBERDO_2_PSP3 | CCGT | nonsummer | 555 | 5.597% | 0.5466% | 520.9046 | 7.291% | 1.795% | 504.57
SBERDO_2_PSP3 | CCGT | summer | 555 | 1.999% | 4.014% | 521.6301 | 5.249% | 4.657% | 500.0189
SBERDO_2_PSP4 | CCGT | nonsummer | 555 | 8.387% | 0.8231% | 503.8867 | 7.291% | 1.795% | 504.57
SBERDO_2_PSP4 | CCGT | summer | 555 | 3.352% | 5.136% | 507.8918 | 5.249% | 4.657% | 500.0189
SCHLTE_1_PL1X3 | CCGT | nonsummer | 336.04 | 0.5971% | 0.9825% | 330.7321 | 7.291% | 1.795% | 305.5057
SCHLTE_1_PL1X3 | CCGT | summer | 336.04 | 0.2525% | 4.05% | 321.5806 | 5.249% | 4.657% | 302.7502
SGREGY_6_SANGER | CCGT | nonsummer | 48.3 | 17.49% | 0% | 39.8503 | 7.291% | 1.795% | 43.9112
SGREGY_6_SANGER | CCGT | summer | 48.3 | 12.07% | 0.02977% | 42.4543 | 5.249% | 4.657% | 43.5152
SUNRIS_2_PL1X3 | CCGT | nonsummer | 586.02 | 6.726% | 4.284% | 521.4981 | 7.291% | 1.795% | 532.7713
SUNRIS_2_PL1X3 | CCGT | summer | 586.02 | 1.551% | 8.126% | 529.3138 | 5.249% | 4.657% | 527.9659
TERMEX_2_PL1X3 | CCGT | nonsummer | 625 | 3.087% | 0.4456% | 602.9222 | 7.291% | 1.795% | 568.2094
TERMEX_2_PL1X3 | CCGT | summer | 625 | 2.345% | 6.029% | 572.6663 | 5.249% | 4.657% | 563.0843
VERNON_6_MALBRG | CCGT | nonsummer | 139 | 7.745% | 0% | 128.2338 | 7.291% | 1.795% | 126.3698
VERNON_6_MALBRG | CCGT | summer | 139 | 2.43% | 0.01411% | 135.6025 | 5.249% | 4.657% | 125.2299
ARCOGN_2_UNITS | CHP | nonsummer | 245 | 12.02% | 0.007176% | 215.5282 | 13.94% | 0.5034% | 209.6069
ARCOGN_2_UNITS | CHP | summer | 245 | 13.12% | 0.06029% | 212.6963 | 11.39% | 1.877% | 212.4837
CHINO_6_CIMGEN | CHP | nonsummer | 26 | 0% | 0% | 26 | 13.94% | 0.5034% | 22.244
CHINO_6_CIMGEN | CHP | summer | 26 | 0% | 0% | 26 | 11.39% | 1.877% | 22.5493
CUMMNG_6_SUNCT1 | CHP | nonsummer | 4 | 0% | 0% | 4 | 13.94% | 0.5034% | 3.4222
CUMMNG_6_SUNCT1 | CHP | summer | 4 | 0% | 0% | 4 | 11.39% | 1.877% | 3.4691
DEXZEL_1_UNIT | CHP | nonsummer | 20 | 37.99% | 0% | 12.4017 | 13.94% | 0.5034% | 17.1108
DEXZEL_1_UNIT | CHP | summer | 20 | 44.08% | 0.06601% | 11.1702 | 11.39% | 1.877% | 17.3456
GRNLF2_1_UNIT | CHP | nonsummer | 49.2 | 50.82% | 0% | 24.1978 | 13.94% | 0.5034% | 42.0925
GRNLF2_1_UNIT | CHP | summer | 49.2 | 46.07% | 0.007404% | 26.5301 | 11.39% | 1.877% | 42.6702
OMAR_2_UNIT 4 | CHP | nonsummer | 75 | 20.12% | 0% | 59.9082 | 13.94% | 0.5034% | 64.1654
OMAR_2_UNIT 4 | CHP | summer | 75 | 6.458% | 0.0316% | 70.1326 | 11.39% | 1.877% | 65.046
OROVIL_6_UNIT | CHP | nonsummer | 7.5 | 9.651% | 0% | 6.7762 | 13.94% | 0.5034% | 6.4165
OROVIL_6_UNIT | CHP | summer | 7.5 | 32% | 0% | 5.0996 | 11.39% | 1.877% | 6.5046
PLMSSR_6_HISIER | CHP | nonsummer | 6 | 6.49% | 0% | 5.6106 | 13.94% | 0.5034% | 5.1332
PLMSSR_6_HISIER | CHP | summer | 6 | 4.918% | 0% | 5.7049 | 11.39% | 1.877% | 5.2037
SALIRV_2_UNIT | CHP | nonsummer | 39 | 14.02% | 0% | 33.5324 | 13.94% | 0.5034% | 33.366
SALIRV_2_UNIT | CHP | summer | 39 | 2.826% | 0% | 37.898 | 11.39% | 1.877% | 33.8239
SMPRIP_1_SMPSON | CHP | nonsummer | 46.05 | 0.5018% | 0% | 45.8189 | 13.94% | 0.5034% | 39.3975
SMPRIP_1_SMPSON | CHP | summer | 46.05 | 16.7% | 0% | 38.3589 | 11.39% | 1.877% | 39.9383
SNCLRA_2_UNIT | CHP | nonsummer | 27.5 | 31.08% | 0% | 18.9521 | 13.94% | 0.5034% | 23.5273
SNCLRA_2_UNIT | CHP | summer | 27.5 | 12.85% | 0% | 23.9651 | 11.39% | 1.877% | 23.8502
SNCLRA_2_UNIT1 | CHP | nonsummer | 27.8 | 14.06% | 0% | 23.892 | 13.94% | 0.5034% | 23.784
SNCLRA_2_UNIT1 | CHP | summer | 27.8 | 23.35% | 0% | 21.3075 | 11.39% | 1.877% | 24.1104
SNCLRA_6_OXGEN | CHP | nonsummer | 47.7 | 10.72% | 0% | 42.5889 | 13.94% | 0.5034% | 40.8092
SNCLRA_6_OXGEN | CHP | summer | 47.7 | 6.91% | 0% | 44.4042 | 11.39% | 1.877% | 41.3693
SUNSET_2_UNITS | CHP | nonsummer | 248 | 7.847% | 2.235% | 222.9966 | 13.94% | 0.5034% | 212.1736
SUNSET_2_UNITS | CHP | summer | 248 | 0.9898% | 8.004% | 225.6952 | 11.39% | 1.877% | 215.0856
SYCAMR_2_UNIT 1 | CHP | nonsummer | 74 | 18.13% | 0% | 60.5823 | 13.94% | 0.5034% | 63.3099
SYCAMR_2_UNIT 1 | CHP | summer | 74 | 12.86% | 0% | 64.4809 | 11.39% | 1.877% | 64.1788
SYCAMR_2_UNIT 3 | CHP | nonsummer | 74 | 7.654% | 0% | 68.3361 | 13.94% | 0.5034% | 63.3099
SYCAMR_2_UNIT 3 | CHP | summer | 74 | 0.8126% | 0% | 73.3986 | 11.39% | 1.877% | 64.1788
TENGEN_2_PL1X2 | CHP | nonsummer | 37.7 | 26.85% | 0% | 27.579 | 13.94% | 0.5034% | 32.2538
TENGEN_2_PL1X2 | CHP | summer | 37.7 | 34.64% | 0.1736% | 24.5753 | 11.39% | 1.877% | 32.6965
YUBACT_1_SUNSWT | CHP | nonsummer | 49.97 | 7.599% | 0% | 46.1727 | 13.94% | 0.5034% | 42.7513
YUBACT_1_SUNSWT | CHP | summer | 49.97 | 13.84% | 1.256% | 42.4245 | 11.39% | 1.877% | 43.338
ADLIN_1_UNITS | Geothermal | nonsummer | 22 | 50.8% | 0% | 10.8234 | 24.78% | 0.05597% | 16.5362
ADLIN_1_UNITS | Geothermal | summer | 22 | 50.37% | 0% | 10.918 | 25.86% | 0.4776% | 16.2055
BLM_2_UNITS | Geothermal | nonsummer | 35 | 16.79% | 0% | 29.1239 | 24.78% | 0.05597% | 26.3076
BLM_2_UNITS | Geothermal | summer | 35 | 7.916% | 0% | 32.2293 | 25.86% | 0.4776% | 25.7815
CALGEN_1_UNITS | Geothermal | nonsummer | 55 | 6.681% | 0% | 51.3257 | 24.78% | 0.05597% | 41.3404
CALGEN_1_UNITS | Geothermal | summer | 55 | 3.309% | 0% | 53.1803 | 25.86% | 0.4776% | 40.5137
CASADB_1_CD4GT1 | Geothermal | nonsummer | 40.7 | 21.17% | 0.8996% | 31.7192 | 24.78% | 0.05597% | 30.5919
CASADB_1_CD4GT1 | Geothermal | summer | 40.7 | 18.13% | 10.45% | 29.0709 | 25.86% | 0.4776% | 29.9802
CONTRL_1_CASAD2 | Geothermal | nonsummer | 10.5 | 10.62% | 3.248% | 9.0443 | 24.78% | 0.05597% | 7.8923
CONTRL_1_CASAD2 | Geothermal | summer | 10.5 | 2.475% | 16.36% | 8.5226 | 25.86% | 0.4776% | 7.7344
GEYS11_7_UNIT11 | Geothermal | nonsummer | 86.8 | 19.32% | 0% | 70.0344 | 24.78% | 0.05597% | 65.2427
GEYS11_7_UNIT11 | Geothermal | summer | 86.8 | 24.74% | 0% | 65.322 | 25.86% | 0.4776% | 63.9381
GEYS12_7_UNIT12 | Geothermal | nonsummer | 57 | 24.84% | 0% | 42.8425 | 24.78% | 0.05597% | 42.8437
GEYS12_7_UNIT12 | Geothermal | summer | 57 | 28.02% | 0% | 41.0275 | 25.86% | 0.4776% | 41.987
GEYS13_7_UNIT13 | Geothermal | nonsummer | 73 | 33.02% | 0% | 48.8989 | 24.78% | 0.05597% | 54.87
GEYS13_7_UNIT13 | Geothermal | summer | 73 | 35.48% | 0% | 47.1021 | 25.86% | 0.4776% | 53.7728
GEYS14_7_UNIT14 | Geothermal | nonsummer | 70 | 17.9% | 0% | 57.4722 | 24.78% | 0.05597% | 52.6151
GEYS14_7_UNIT14 | Geothermal | summer | 70 | 26.67% | 0% | 51.3332 | 25.86% | 0.4776% | 51.5629
GEYS16_7_UNIT16 | Geothermal | nonsummer | 63 | 24.29% | 0% | 47.6969 | 24.78% | 0.05597% | 47.3536
GEYS16_7_UNIT16 | Geothermal | summer | 63 | 27.83% | 0% | 45.4641 | 25.86% | 0.4776% | 46.4067
GEYS17_7_UNIT17 | Geothermal | nonsummer | 75.5 | 19.66% | 0% | 60.6597 | 24.78% | 0.05597% | 56.7491
GEYS17_7_UNIT17 | Geothermal | summer | 75.5 | 29.67% | 0% | 53.1009 | 25.86% | 0.4776% | 55.6143
GEYS18_7_UNIT18 | Geothermal | nonsummer | 72 | 40.78% | 0% | 42.6414 | 24.78% | 0.05597% | 54.1184
GEYS18_7_UNIT18 | Geothermal | summer | 72 | 43.53% | 0% | 40.6553 | 25.86% | 0.4776% | 53.0362
GEYS20_7_UNIT20 | Geothermal | nonsummer | 50 | 28.55% | 0% | 35.7267 | 24.78% | 0.05597% | 37.5822
GEYS20_7_UNIT20 | Geothermal | summer | 50 | 30.77% | 0% | 34.6136 | 25.86% | 0.4776% | 36.8307
GYS5X6_7_UNITS | Geothermal | nonsummer | 98.43 | 32.26% | 0% | 66.6806 | 24.78% | 0.05597% | 73.9844
GYS5X6_7_UNITS | Geothermal | summer | 98.43 | 24.1% | 0% | 74.7104 | 25.86% | 0.4776% | 72.5049
GYS7X8_7_UNITS | Geothermal | nonsummer | 95.8 | 20.48% | 0% | 76.1783 | 24.78% | 0.05597% | 72.0075
GYS7X8_7_UNITS | Geothermal | summer | 95.8 | 19.51% | 0% | 77.1064 | 25.86% | 0.4776% | 70.5676
NAVYII_2_UNITS | Geothermal | nonsummer | 47 | 8.367% | 0% | 43.0677 | 24.78% | 0.05597% | 35.3273
NAVYII_2_UNITS | Geothermal | summer | 47 | 5.558% | 0% | 44.3878 | 25.86% | 0.4776% | 34.6208
NCPA_7_GP1UN1 | Geothermal | nonsummer | 38.85 | 36.42% | 0% | 24.6992 | 24.78% | 0.05597% | 29.2014
NCPA_7_GP1UN1 | Geothermal | summer | 38.85 | 33.33% | 0% | 25.9 | 25.86% | 0.4776% | 28.6174
NCPA_7_GP1UN2 | Geothermal | nonsummer | 50 | 13.48% | 0% | 43.2609 | 24.78% | 0.05597% | 37.5822
NCPA_7_GP1UN2 | Geothermal | summer | 50 | 21.56% | 0% | 39.2222 | 25.86% | 0.4776% | 36.8307
NCPA_7_GP2UN3 | Geothermal | nonsummer | 42.42 | 66.09% | 0% | 14.3842 | 24.78% | 0.05597% | 31.8848
NCPA_7_GP2UN3 | Geothermal | summer | 42.42 | 66.67% | 0% | 14.14 | 25.86% | 0.4776% | 31.2471
NCPA_7_GP2UN4 | Geothermal | nonsummer | 52.73 | 4.105% | 0% | 50.5652 | 24.78% | 0.05597% | 39.6342
NCPA_7_GP2UN4 | Geothermal | summer | 52.73 | 15.11% | 0% | 44.7615 | 25.86% | 0.4776% | 38.8416
SANTFG_7_UNITS | Geothermal | nonsummer | 72 | 19.16% | 0% | 58.202 | 24.78% | 0.05597% | 54.1184
SANTFG_7_UNITS | Geothermal | summer | 72 | 21.76% | 0% | 56.3295 | 25.86% | 0.4776% | 53.0362
SMUDGO_7_UNIT 1 | Geothermal | nonsummer | 64.8 | 36.03% | 0% | 41.4546 | 24.78% | 0.05597% | 48.7066
SMUDGO_7_UNIT 1 | Geothermal | summer | 64.8 | 25.74% | 0% | 48.1201 | 25.86% | 0.4776% | 47.7326
BARRE_2_ALASB1 | Hybrid_BattStorage | nonsummer | 5 | 10.85% | 0.296% | 4.4426 | 26.09% | 0.148% | 3.6879
BARRE_2_ALASB1 | Hybrid_BattStorage | summer | 5 | 7.069% | 0.1756% | 4.6378 | 16.61% | 0.1234% | 4.1636
CUYAMA_6_SB3SB1 | Hybrid_BattStorage | nonsummer | 3 | 11.09% | 0.296% | 2.6585 | 26.09% | 0.148% | 2.2127
CUYAMA_6_SB3SB1 | Hybrid_BattStorage | summer | 3 | 6.764% | 0.1756% | 2.7918 | 16.61% | 0.1234% | 2.4981
DELAMO_2_ALASB2 | Hybrid_BattStorage | nonsummer | 5 | 13.67% | 0.296% | 4.3018 | 26.09% | 0.148% | 3.6879
DELAMO_2_ALASB2 | Hybrid_BattStorage | summer | 5 | 6.764% | 0.1756% | 4.653 | 16.61% | 0.1234% | 4.1636
DSFLWR_2_W9CSB1 | Hybrid_BattStorage | nonsummer | 52 | 23.27% | 0.296% | 39.7458 | 26.09% | 0.148% | 38.3539
DSFLWR_2_W9CSB1 | Hybrid_BattStorage | summer | 52 | 14.63% | 0.1756% | 44.3 | 16.61% | 0.1234% | 43.3009
DSFLWR_2_W9CSB2 | Hybrid_BattStorage | nonsummer | 36 | 23.27% | 0.296% | 27.5163 | 26.09% | 0.148% | 26.5527
DSFLWR_2_W9CSB2 | Hybrid_BattStorage | summer | 36 | 14.63% | 0.1756% | 30.6692 | 16.61% | 0.1234% | 29.9776
EDWARD_2_E21SB1 | Hybrid_BattStorage | nonsummer | 71 | 7.881% | 0.2108% | 65.2548 | 26.09% | 0.148% | 52.3679
EDWARD_2_E21SB1 | Hybrid_BattStorage | summer | 71 | 5.477% | 0.09985% | 67.0402 | 16.61% | 0.1234% | 59.1224
EDWARD_2_E23SB1 | Hybrid_BattStorage | nonsummer | 6 | 12.08% | 0% | 5.275 | 26.09% | 0.148% | 4.4255
EDWARD_2_E23SB1 | Hybrid_BattStorage | summer | 6 | 23.61% | 0% | 4.5831 | 16.61% | 0.1234% | 4.9963
EDWARD_2_ES2BT3 | Hybrid_BattStorage | nonsummer | 66 | 10.91% | 0.1271% | 58.7175 | 26.09% | 0.148% | 48.68
EDWARD_2_ES2BT3 | Hybrid_BattStorage | summer | 66 | 8.01% | 0% | 60.7134 | 16.61% | 0.1234% | 54.9589
EDWARD_2_ESSSB1 | Hybrid_BattStorage | nonsummer | 47 | 23.27% | 0.296% | 35.9241 | 26.09% | 0.148% | 34.6661
EDWARD_2_ESSSB1 | Hybrid_BattStorage | summer | 47 | 14.63% | 0.1756% | 40.0403 | 16.61% | 0.1234% | 39.1374
EDWARD_2_ESSSB2 | Hybrid_BattStorage | nonsummer | 21.5 | 18.07% | 0.296% | 17.5519 | 26.09% | 0.148% | 15.8579
EDWARD_2_ESSSB2 | Hybrid_BattStorage | summer | 21.5 | 6.353% | 0.1756% | 20.0964 | 16.61% | 0.1234% | 17.9033
HAMLIN_1_BLDSB1 | Hybrid_BattStorage | nonsummer | 75 | 32.6% | 0.296% | 50.3277 | 26.09% | 0.148% | 55.3182
HAMLIN_1_BLDSB1 | Hybrid_BattStorage | summer | 75 | 40.47% | 0.1756% | 44.5141 | 16.61% | 0.1234% | 62.4533
HAMLIN_1_BMSBT2 | Hybrid_BattStorage | nonsummer | 25 | 25.12% | 0.296% | 18.6458 | 26.09% | 0.148% | 18.4394
HAMLIN_1_BMSBT2 | Hybrid_BattStorage | summer | 25 | 14.63% | 0.1756% | 21.2981 | 16.61% | 0.1234% | 20.8178
LNCSTR_6_SOLAR2 | Hybrid_BattStorage | nonsummer | 7 | 0% | 0% | 7 | 26.09% | 0.148% | 5.163
LNCSTR_6_SOLAR2 | Hybrid_BattStorage | summer | 7 | 0% | 0% | 7 | 16.61% | 0.1234% | 5.829
MCFLND_5_MBSBX2 | Hybrid_BattStorage | nonsummer | 150 | 26.5% | 0.296% | 109.8023 | 26.09% | 0.148% | 110.6363
MCFLND_5_MBSBX2 | Hybrid_BattStorage | summer | 150 | 17.53% | 0.1756% | 123.442 | 16.61% | 0.1234% | 124.9065
NORORC_2_NOSBX2 | Hybrid_BattStorage | nonsummer | 92 | 23.27% | 0.296% | 70.3194 | 26.09% | 0.148% | 67.857
NORORC_2_NOSBX2 | Hybrid_BattStorage | summer | 92 | 14.63% | 0.1756% | 78.3769 | 16.61% | 0.1234% | 76.6093
PUTHCR_1_PCNSB1 | Hybrid_BattStorage | nonsummer | 3 | 17.71% | 0.2108% | 2.4624 | 26.09% | 0.148% | 2.2127
PUTHCR_1_PCNSB1 | Hybrid_BattStorage | summer | 3 | 10.64% | 0.1561% | 2.676 | 16.61% | 0.1234% | 2.4981
RATSKE_2_RBSSB1 | Hybrid_BattStorage | nonsummer | 7.5 | 15.48% | 0.462% | 6.3046 | 26.09% | 0.148% | 5.5318
RATSKE_2_RBSSB1 | Hybrid_BattStorage | summer | 7.5 | 10.55% | 0.1595% | 6.6966 | 16.61% | 0.1234% | 6.2453
RATSKE_2_RBSSB2 | Hybrid_BattStorage | nonsummer | 5 | 14.92% | 0.9309% | 4.2075 | 26.09% | 0.148% | 3.6879
RATSKE_2_RBSSB2 | Hybrid_BattStorage | summer | 5 | 10.84% | 0.1595% | 4.45 | 16.61% | 0.1234% | 4.1636
SANBRN_2_EESSB2 | Hybrid_BattStorage | nonsummer | 85 | 10.38% | 0.296% | 75.9214 | 26.09% | 0.148% | 62.6939
SANBRN_2_EESSB2 | Hybrid_BattStorage | summer | 85 | 6.506% | 0.1756% | 79.3208 | 16.61% | 0.1234% | 70.7804
SANBRN_2_ES1BT3 | Hybrid_BattStorage | nonsummer | 22 | 5.917% | 0.1424% | 20.667 | 26.09% | 0.148% | 16.2267
SANBRN_2_ES1BT3 | Hybrid_BattStorage | summer | 22 | 3.212% | 0% | 21.2935 | 16.61% | 0.1234% | 18.3196
SANBRN_2_ES2SB3 | Hybrid_BattStorage | nonsummer | 18 | 5.402% | 0.1424% | 17.002 | 26.09% | 0.148% | 13.2764
SANBRN_2_ES2SB3 | Hybrid_BattStorage | summer | 18 | 5.996% | 0% | 16.9207 | 16.61% | 0.1234% | 14.9888
SANBRN_2_SS2SB4 | Hybrid_BattStorage | nonsummer | 18 | 10.59% | 0.296% | 16.0409 | 26.09% | 0.148% | 13.2764
SANBRN_2_SS2SB4 | Hybrid_BattStorage | summer | 18 | 5.584% | 0.1756% | 16.9634 | 16.61% | 0.1234% | 14.9888
SLATE_2_SLASR2 | Hybrid_BattStorage | nonsummer | 46.5 | 35.47% | 0.5423% | 29.755 | 26.09% | 0.148% | 34.2973
SLATE_2_SLASR2 | Hybrid_BattStorage | summer | 46.5 | 5.711% | 0.5365% | 43.595 | 16.61% | 0.1234% | 38.721
SLATE_2_SLASR3 | Hybrid_BattStorage | nonsummer | 33.75 | 37.6% | 0.8954% | 20.7588 | 26.09% | 0.148% | 24.8932
SLATE_2_SLASR3 | Hybrid_BattStorage | summer | 33.75 | 6.747% | 0.7445% | 31.2215 | 16.61% | 0.1234% | 28.104
SLATE_2_SLASR4 | Hybrid_BattStorage | nonsummer | 50 | 16.87% | 0.1019% | 41.5135 | 26.09% | 0.148% | 36.8788
SLATE_2_SLASR4 | Hybrid_BattStorage | summer | 50 | 4.838% | 0% | 47.5809 | 16.61% | 0.1234% | 41.6355
SLATE_2_SLASR5 | Hybrid_BattStorage | nonsummer | 10 | 37.59% | 0.4005% | 6.2008 | 26.09% | 0.148% | 7.3758
SLATE_2_SLASR5 | Hybrid_BattStorage | summer | 10 | 24.16% | 0.1083% | 7.5736 | 16.61% | 0.1234% | 8.3271
BARRE_2_ALASB1_SUN | Hybrid_Solar_1Axis | nonsummer | 10 | 0% | 0% | 10 | 0% | 0% | 10
BARRE_2_ALASB1_SUN | Hybrid_Solar_1Axis | summer | 10 | 0% | 0% | 10 | 0% | 0% | 10
CUYAMA_6_SB3SB1_SUN | Hybrid_Solar_1Axis | nonsummer | 3 | 0% | 0% | 3 | 0% | 0% | 3
CUYAMA_6_SB3SB1_SUN | Hybrid_Solar_1Axis | summer | 3 | 0% | 0% | 3 | 0% | 0% | 3
DELAMO_2_ALASB2_SUN | Hybrid_Solar_1Axis | nonsummer | 10 | 0% | 0% | 10 | 0% | 0% | 10
DELAMO_2_ALASB2_SUN | Hybrid_Solar_1Axis | summer | 10 | 0% | 0% | 10 | 0% | 0% | 10
DSFLWR_2_W9CSB1_SUN | Hybrid_Solar_1Axis | nonsummer | 102 | 0% | 0% | 102 | 0% | 0% | 102
DSFLWR_2_W9CSB1_SUN | Hybrid_Solar_1Axis | summer | 102 | 0% | 0% | 102 | 0% | 0% | 102
DSFLWR_2_W9CSB2_SUN | Hybrid_Solar_1Axis | nonsummer | 72 | 0% | 0% | 72 | 0% | 0% | 72
DSFLWR_2_W9CSB2_SUN | Hybrid_Solar_1Axis | summer | 72 | 0% | 0% | 72 | 0% | 0% | 72
EDWARD_2_E21SB1_SUN | Hybrid_Solar_1Axis | nonsummer | 130 | 0% | 0% | 130 | 0% | 0% | 130
EDWARD_2_E21SB1_SUN | Hybrid_Solar_1Axis | summer | 130 | 0% | 0% | 130 | 0% | 0% | 130
EDWARD_2_E23SB1_SUN | Hybrid_Solar_1Axis | nonsummer | 24 | 0% | 0% | 24 | 0% | 0% | 24
EDWARD_2_E23SB1_SUN | Hybrid_Solar_1Axis | summer | 24 | 0% | 0% | 24 | 0% | 0% | 24
EDWARD_2_ES2BT3_SUN | Hybrid_Solar_1Axis | nonsummer | 118 | 0% | 0% | 118 | 0% | 0% | 118
EDWARD_2_ES2BT3_SUN | Hybrid_Solar_1Axis | summer | 118 | 0% | 0% | 118 | 0% | 0% | 118
EDWARD_2_ESSSB1_SUN | Hybrid_Solar_1Axis | nonsummer | 68 | 0% | 0% | 68 | 0% | 0% | 68
EDWARD_2_ESSSB1_SUN | Hybrid_Solar_1Axis | summer | 68 | 0% | 0% | 68 | 0% | 0% | 68
EDWARD_2_ESSSB2_SUN | Hybrid_Solar_1Axis | nonsummer | 132 | 0% | 0% | 132 | 0% | 0% | 132
EDWARD_2_ESSSB2_SUN | Hybrid_Solar_1Axis | summer | 132 | 0% | 0% | 132 | 0% | 0% | 132
HAMLIN_1_BLDSB1_SUN | Hybrid_Solar_1Axis | nonsummer | 150 | 0% | 0% | 150 | 0% | 0% | 150
HAMLIN_1_BLDSB1_SUN | Hybrid_Solar_1Axis | summer | 150 | 0% | 0% | 150 | 0% | 0% | 150
HAMLIN_1_BMSBT2_SUN | Hybrid_Solar_1Axis | nonsummer | 50 | 0% | 0% | 50 | 0% | 0% | 50
HAMLIN_1_BMSBT2_SUN | Hybrid_Solar_1Axis | summer | 50 | 0% | 0% | 50 | 0% | 0% | 50
LNCSTR_6_SOLAR2_SUN | Hybrid_Solar_1Axis | nonsummer | 3 | 0% | 0% | 3 | 0% | 0% | 3
LNCSTR_6_SOLAR2_SUN | Hybrid_Solar_1Axis | summer | 3 | 0% | 0% | 3 | 0% | 0% | 3
MCFLND_5_MBSBX2_SUN | Hybrid_Solar_1Axis | nonsummer | 300 | 0% | 0% | 300 | 0% | 0% | 300
MCFLND_5_MBSBX2_SUN | Hybrid_Solar_1Axis | summer | 300 | 0% | 0% | 300 | 0% | 0% | 300
NORORC_2_NOSBX2_SUN | Hybrid_Solar_1Axis | nonsummer | 150 | 0% | 0% | 150 | 0% | 0% | 150
NORORC_2_NOSBX2_SUN | Hybrid_Solar_1Axis | summer | 150 | 0% | 0% | 150 | 0% | 0% | 150
PUTHCR_1_PCNSB1_SUN | Hybrid_Solar_1Axis | nonsummer | 3 | 0% | 0% | 3 | 0% | 0% | 3
PUTHCR_1_PCNSB1_SUN | Hybrid_Solar_1Axis | summer | 3 | 0% | 0% | 3 | 0% | 0% | 3
RATSKE_2_RBSSB1_SUN | Hybrid_Solar_1Axis | nonsummer | 60 | 0% | 0% | 60 | 0% | 0% | 60
RATSKE_2_RBSSB1_SUN | Hybrid_Solar_1Axis | summer | 60 | 0% | 0% | 60 | 0% | 0% | 60
RATSKE_2_RBSSB2_SUN | Hybrid_Solar_1Axis | nonsummer | 40 | 0% | 0% | 40 | 0% | 0% | 40
RATSKE_2_RBSSB2_SUN | Hybrid_Solar_1Axis | summer | 40 | 0% | 0% | 40 | 0% | 0% | 40
SANBRN_2_EESSB2_SUN | Hybrid_Solar_1Axis | nonsummer | 130 | 0% | 0% | 130 | 0% | 0% | 130
SANBRN_2_EESSB2_SUN | Hybrid_Solar_1Axis | summer | 130 | 0% | 0% | 130 | 0% | 0% | 130
SANBRN_2_ES1BT3_SUN | Hybrid_Solar_1Axis | nonsummer | 40 | 0% | 0% | 40 | 0% | 0% | 40
SANBRN_2_ES1BT3_SUN | Hybrid_Solar_1Axis | summer | 40 | 0% | 0% | 40 | 0% | 0% | 40
SANBRN_2_ES2SB3_SUN | Hybrid_Solar_1Axis | nonsummer | 33 | 0% | 0% | 33 | 0% | 0% | 33
SANBRN_2_ES2SB3_SUN | Hybrid_Solar_1Axis | summer | 33 | 0% | 0% | 33 | 0% | 0% | 33
SANBRN_2_SS2SB4_SUN | Hybrid_Solar_1Axis | nonsummer | 36 | 0% | 0% | 36 | 0% | 0% | 36
SANBRN_2_SS2SB4_SUN | Hybrid_Solar_1Axis | summer | 36 | 0% | 0% | 36 | 0% | 0% | 36
SLATE_2_SLASR2_SUN | Hybrid_Solar_1Axis | nonsummer | 93 | 0% | 0% | 93 | 0% | 0% | 93
SLATE_2_SLASR2_SUN | Hybrid_Solar_1Axis | summer | 93 | 0% | 0% | 93 | 0% | 0% | 93
SLATE_2_SLASR4_SUN | Hybrid_Solar_1Axis | nonsummer | 63 | 0% | 0% | 63 | 0% | 0% | 63
SLATE_2_SLASR4_SUN | Hybrid_Solar_1Axis | summer | 63 | 0% | 0% | 63 | 0% | 0% | 63
SLATE_2_SLASR5_SUN | Hybrid_Solar_1Axis | nonsummer | 26 | 0% | 0% | 26 | 0% | 0% | 26
SLATE_2_SLASR5_SUN | Hybrid_Solar_1Axis | summer | 26 | 0% | 0% | 26 | 0% | 0% | 26
SLATE_2_SLASR3_SUN | Hybrid_Solar_Fixed | nonsummer | 67.5 | 0% | 0% | 67.5 | 0% | 0% | 67.5
SLATE_2_SLASR3_SUN | Hybrid_Solar_Fixed | summer | 67.5 | 0% | 0% | 67.5 | 0% | 0% | 67.5
ALAMO_6_UNIT | Hydro | nonsummer | 17 | 19.74% | 0% | 13.6439 | 16.13% | 0.1394% | 14.2341
ALAMO_6_UNIT | Hydro | summer | 17 | 3.285% | 0% | 16.4416 | 15.28% | 0.07344% | 14.3896
APLHIL_1_SFKHY1 | Hydro | nonsummer | 2.68 | 22.94% | 0% | 2.0653 | 16.13% | 0.1394% | 2.244
APLHIL_1_SFKHY1 | Hydro | summer | 2.68 | 6.97% | 0% | 2.4932 | 15.28% | 0.07344% | 2.2685
BALCHS_7_UNIT 1 | Hydro | nonsummer | 31 | 3.325% | 0% | 29.9692 | 16.13% | 0.1394% | 25.9564
BALCHS_7_UNIT 1 | Hydro | summer | 31 | 2.18% | 0.0342% | 30.3135 | 15.28% | 0.07344% | 26.2399
BALCHS_7_UNIT 2 | Hydro | nonsummer | 52.5 | 4.382% | 0% | 50.1995 | 16.13% | 0.1394% | 43.9584
BALCHS_7_UNIT 2 | Hydro | summer | 52.5 | 1.917% | 0% | 51.4936 | 15.28% | 0.07344% | 44.4386
BALCHS_7_UNIT 3 | Hydro | nonsummer | 54.6 | 4.281% | 0% | 52.2627 | 16.13% | 0.1394% | 45.7167
BALCHS_7_UNIT 3 | Hydro | summer | 54.6 | 1.993% | 0% | 53.512 | 15.28% | 0.07344% | 46.2161
BEARDS_7_UNIT 1 | Hydro | nonsummer | 11.5 | 0.2531% | 0% | 11.4709 | 16.13% | 0.1394% | 9.629
BEARDS_7_UNIT 1 | Hydro | summer | 11.5 | 0.3798% | 0% | 11.4563 | 15.28% | 0.07344% | 9.7342
BELDEN_7_UNIT 1 | Hydro | nonsummer | 119 | 28.05% | 0% | 85.6194 | 16.13% | 0.1394% | 99.6389
BELDEN_7_UNIT 1 | Hydro | summer | 119 | 56.23% | 0% | 52.0837 | 15.28% | 0.07344% | 100.7274
BIGCRK_2_EXESWD | Hydro | nonsummer | 820 | 27.67% | 0% | 593.1334 | 16.13% | 0.1394% | 686.5877
BIGCRK_2_EXESWD | Hydro | summer | 820 | 22.51% | 0% | 635.4424 | 15.28% | 0.07344% | 694.088
BLACK_7_UNIT 1 | Hydro | nonsummer | 85 | 6.394% | 0.04248% | 79.5287 | 16.13% | 0.1394% | 71.1707
BLACK_7_UNIT 1 | Hydro | summer | 85 | 2.169% | 0% | 83.1567 | 15.28% | 0.07344% | 71.9481
BLACK_7_UNIT 2 | Hydro | nonsummer | 84.1 | 3.971% | 0.01646% | 80.7469 | 16.13% | 0.1394% | 70.4171
BLACK_7_UNIT 2 | Hydro | summer | 84.1 | 2.228% | 0% | 82.2261 | 15.28% | 0.07344% | 71.1863
BLCKBT_2_STONEY | Hydro | nonsummer | 6.2 | 31.61% | 0% | 4.2401 | 16.13% | 0.1394% | 5.1913
BLCKBT_2_STONEY | Hydro | summer | 6.2 | 44.88% | 0% | 3.4172 | 15.28% | 0.07344% | 5.248
BUCKCK_7_PL1X2 | Hydro | nonsummer | 57.25 | 4.844% | 0% | 54.4768 | 16.13% | 0.1394% | 47.9355
BUCKCK_7_PL1X2 | Hydro | summer | 57.25 | 3.611% | 0.04718% | 55.1559 | 15.28% | 0.07344% | 48.4592
BUTTVL_7_UNIT 1 | Hydro | nonsummer | 39.5 | 5.02% | 0% | 37.5171 | 16.13% | 0.1394% | 33.0734
BUTTVL_7_UNIT 1 | Hydro | summer | 39.5 | 1.519% | 0% | 38.9001 | 15.28% | 0.07344% | 33.4347
CAMPFW_7_FARWST | Hydro | nonsummer | 6.8 | 18.84% | 0% | 5.5191 | 16.13% | 0.1394% | 5.6937
CAMPFW_7_FARWST | Hydro | summer | 6.8 | 11.37% | 0% | 6.0267 | 15.28% | 0.07344% | 5.7559
CARBOU_7_PL2X3 | Hydro | nonsummer | 49 | 22.11% | 0% | 38.1638 | 16.13% | 0.1394% | 41.0278
CARBOU_7_PL2X3 | Hydro | summer | 49 | 29.39% | 0% | 34.599 | 15.28% | 0.07344% | 41.476
CARBOU_7_PL4X5 | Hydro | nonsummer | 120 | 29.86% | 0% | 84.1654 | 16.13% | 0.1394% | 100.4762
CARBOU_7_PL4X5 | Hydro | summer | 120 | 23.99% | 0% | 91.2139 | 15.28% | 0.07344% | 101.5739
CARBOU_7_UNIT 1 | Hydro | nonsummer | 24 | 13.36% | 0% | 20.7928 | 16.13% | 0.1394% | 20.0952
CARBOU_7_UNIT 1 | Hydro | summer | 24 | 32.81% | 0% | 16.1246 | 15.28% | 0.07344% | 20.3148
CENTER_2_RHONDO | Hydro | nonsummer | 1.91 | 59.8% | 0% | 0.7679 | 16.13% | 0.1394% | 1.5992
CENTER_2_RHONDO | Hydro | summer | 1.91 | 60.39% | 0% | 0.75662 | 15.28% | 0.07344% | 1.6167
CHICPK_7_UNIT 1 | Hydro | nonsummer | 42 | 47.02% | 0% | 22.2533 | 16.13% | 0.1394% | 35.1667
CHICPK_7_UNIT 1 | Hydro | summer | 42 | 43.46% | 0% | 23.748 | 15.28% | 0.07344% | 35.5508
COLGAT_7_UNIT 1 | Hydro | nonsummer | 176.72 | 13% | 0% | 153.7537 | 16.13% | 0.1394% | 147.968
COLGAT_7_UNIT 1 | Hydro | summer | 176.72 | 11.42% | 0% | 156.5348 | 15.28% | 0.07344% | 149.5844
COLGAT_7_UNIT 2 | Hydro | nonsummer | 175.67 | 11.99% | 0% | 154.6102 | 16.13% | 0.1394% | 147.0888
COLGAT_7_UNIT 2 | Hydro | summer | 175.67 | 11.17% | 0% | 156.0437 | 15.28% | 0.07344% | 148.6957
COLVIL_7_PL1X2 | Hydro | nonsummer | 246.86 | 4.949% | 0% | 234.6428 | 16.13% | 0.1394% | 206.6964
COLVIL_7_PL1X2 | Hydro | summer | 246.86 | 0.8293% | 0% | 244.8129 | 15.28% | 0.07344% | 208.9543
CONTRL_1_POOLE | Hydro | nonsummer | 11.07 | 61.89% | 1.816% | 4.0183 | 16.13% | 0.1394% | 9.2689
CONTRL_1_POOLE | Hydro | summer | 11.07 | 19.79% | 0% | 8.8791 | 15.28% | 0.07344% | 9.3702
CONTRL_1_RUSHCK | Hydro | nonsummer | 12.19 | 47.72% | 2.74% | 6.0388 | 16.13% | 0.1394% | 10.2067
CONTRL_1_RUSHCK | Hydro | summer | 12.19 | 14.16% | 0% | 10.4639 | 15.28% | 0.07344% | 10.3182
COVERD_2_QFUNTS | Hydro | nonsummer | 5.5 | 0.1284% | 0% | 5.4929 | 16.13% | 0.1394% | 4.6052
COVERD_2_QFUNTS | Hydro | summer | 5.5 | 1.479% | 0% | 5.4186 | 15.28% | 0.07344% | 4.6555
CRESTA_7_PL1X2 | Hydro | nonsummer | 70.4 | 14.13% | 0% | 60.455 | 16.13% | 0.1394% | 58.9461
CRESTA_7_PL1X2 | Hydro | summer | 70.4 | 41.27% | 0% | 41.3446 | 15.28% | 0.07344% | 59.59
DONNLS_7_UNIT | Hydro | nonsummer | 72 | 2.968% | 0% | 69.863 | 16.13% | 0.1394% | 60.2857
DONNLS_7_UNIT | Hydro | summer | 72 | 2.189% | 0% | 70.4242 | 15.28% | 0.07344% | 60.9443
DRUM_7_PL1X2 | Hydro | nonsummer | 26 | 33.26% | 0% | 17.3531 | 16.13% | 0.1394% | 21.7699
DRUM_7_PL1X2 | Hydro | summer | 26 | 33.23% | 0% | 17.3595 | 15.28% | 0.07344% | 22.0077
DRUM_7_PL3X4 | Hydro | nonsummer | 28.9 | 48.97% | 0% | 14.7489 | 16.13% | 0.1394% | 24.198
DRUM_7_PL3X4 | Hydro | summer | 28.9 | 43.56% | 0% | 16.3107 | 15.28% | 0.07344% | 24.4624
DRUM_7_UNIT 5 | Hydro | nonsummer | 50 | 19.55% | 0% | 40.226 | 16.13% | 0.1394% | 41.8651
DRUM_7_UNIT 5 | Hydro | summer | 50 | 15.1% | 0% | 42.4478 | 15.28% | 0.07344% | 42.3224
DUTCH1_7_UNIT 1 | Hydro | nonsummer | 22 | 16.1% | 0% | 18.4576 | 16.13% | 0.1394% | 18.4206
DUTCH1_7_UNIT 1 | Hydro | summer | 22 | 28.38% | 0% | 15.7567 | 15.28% | 0.07344% | 18.6219
DUTCH2_7_UNIT 1 | Hydro | nonsummer | 26 | 51.85% | 0.1015% | 12.4923 | 16.13% | 0.1394% | 21.7699
DUTCH2_7_UNIT 1 | Hydro | summer | 26 | 44.17% | 0% | 14.515 | 15.28% | 0.07344% | 22.0077
DVLCYN_1_UNITS | Hydro | nonsummer | 235 | 2.306% | 0% | 229.5801 | 16.13% | 0.1394% | 196.766
DVLCYN_1_UNITS | Hydro | summer | 235 | 1.584% | 0% | 231.2781 | 15.28% | 0.07344% | 198.9155
ELECTR_7_PL1X3 | Hydro | nonsummer | 93 | 11.15% | 0% | 82.6278 | 16.13% | 0.1394% | 77.8691
ELECTR_7_PL1X3 | Hydro | summer | 93 | 5.362% | 0% | 88.0137 | 15.28% | 0.07344% | 78.7197
ELKCRK_6_STONYG | Hydro | nonsummer | 4.9 | 33.01% | 0% | 3.2824 | 16.13% | 0.1394% | 4.1028
ELKCRK_6_STONYG | Hydro | summer | 4.9 | 68.29% | 0% | 1.5537 | 15.28% | 0.07344% | 4.1476
EXCHEC_7_UNIT 1 | Hydro | nonsummer | 94.5 | 13.53% | 0% | 81.7103 | 16.13% | 0.1394% | 79.125
EXCHEC_7_UNIT 1 | Hydro | summer | 94.5 | 19.92% | 0.01089% | 75.6681 | 15.28% | 0.07344% | 79.9894
FMEADO_7_UNIT | Hydro | nonsummer | 16 | 5.884% | 0% | 15.0586 | 16.13% | 0.1394% | 13.3968
FMEADO_7_UNIT | Hydro | summer | 16 | 3.253% | 0% | 15.4796 | 15.28% | 0.07344% | 13.5432
FORBST_7_UNIT 1 | Hydro | nonsummer | 37.5 | 2.432% | 0% | 36.5881 | 16.13% | 0.1394% | 31.3988
FORBST_7_UNIT 1 | Hydro | summer | 37.5 | 0.2676% | 0% | 37.3997 | 15.28% | 0.07344% | 31.7418
GRIZLY_1_UNIT 1 | Hydro | nonsummer | 20 | 7.085% | 0% | 18.583 | 16.13% | 0.1394% | 16.746
GRIZLY_1_UNIT 1 | Hydro | summer | 20 | 0.5174% | 0% | 19.8965 | 15.28% | 0.07344% | 16.929
HAASPH_7_PL1X2 | Hydro | nonsummer | 144 | 4.797% | 0% | 137.0926 | 16.13% | 0.1394% | 120.5715
HAASPH_7_PL1X2 | Hydro | summer | 144 | 3.463% | 0% | 139.0134 | 15.28% | 0.07344% | 121.8886
HALSEY_6_UNIT | Hydro | nonsummer | 13.5 | 5.477% | 0% | 12.7606 | 16.13% | 0.1394% | 11.3036
HALSEY_6_UNIT | Hydro | summer | 13.5 | 5.33% | 0% | 12.7805 | 15.28% | 0.07344% | 11.4271
HYTTHM_2_UNITS | Hydro | nonsummer | 933.1 | 10.52% | 0% | 834.8995 | 16.13% | 0.1394% | 781.2865
HYTTHM_2_UNITS | Hydro | summer | 933.1 | 12.98% | 0% | 811.9955 | 15.28% | 0.07344% | 789.8213
INTKEP_2_UNITS | Hydro | nonsummer | 405 | 24.66% | 0% | 305.137 | 16.13% | 0.1394% | 339.1073
INTKEP_2_UNITS | Hydro | summer | 405 | 15.44% | 0% | 342.4749 | 15.28% | 0.07344% | 342.8117
KELYRG_6_UNIT | Hydro | nonsummer | 11 | 3.754% | 0% | 10.587 | 16.13% | 0.1394% | 9.2103
KELYRG_6_UNIT | Hydro | summer | 11 | 1.438% | 0% | 10.8418 | 15.28% | 0.07344% | 9.3109
KERKH2_7_UNIT 1 | Hydro | nonsummer | 153.9 | 18.07% | 0.1132% | 125.9205 | 16.13% | 0.1394% | 128.8608
KERKH2_7_UNIT 1 | Hydro | summer | 153.9 | 15.28% | 0.4641% | 129.6751 | 15.28% | 0.07344% | 130.2685
KINGRV_7_UNIT 1 | Hydro | nonsummer | 51.2 | 5.135% | 0.01059% | 48.5656 | 16.13% | 0.1394% | 42.8699
KINGRV_7_UNIT 1 | Hydro | summer | 51.2 | 4.656% | 0% | 48.8163 | 15.28% | 0.07344% | 43.3382
MCSWAN_6_UNITS | Hydro | nonsummer | 9 | 17.92% | 0% | 7.3868 | 16.13% | 0.1394% | 7.5357
MCSWAN_6_UNITS | Hydro | summer | 9 | 0.01961% | 0% | 8.9982 | 15.28% | 0.07344% | 7.618
MDFKRL_2_PROJCT | Hydro | nonsummer | 210 | 7.268% | 0% | 194.7369 | 16.13% | 0.1394% | 175.8334
MDFKRL_2_PROJCT | Hydro | summer | 210 | 0.2485% | 0.01342% | 209.4499 | 15.28% | 0.07344% | 177.7542
MERCFL_6_UNIT | Hydro | nonsummer | 3.5 | 25.6% | 0% | 2.6041 | 16.13% | 0.1394% | 2.9306
MERCFL_6_UNIT | Hydro | summer | 3.5 | 0.1511% | 0% | 3.4947 | 15.28% | 0.07344% | 2.9626
MIRLOM_7_MWDLKM | Hydro | nonsummer | 5 | 19.4% | 0% | 4.0298 | 16.13% | 0.1394% | 4.1865
MIRLOM_7_MWDLKM | Hydro | summer | 5 | 11.65% | 0% | 4.4173 | 15.28% | 0.07344% | 4.2322
MOJAVE_1_SIPHON | Hydro | nonsummer | 14.36 | 1.508% | 0% | 14.1435 | 16.13% | 0.1394% | 12.0237
MOJAVE_1_SIPHON | Hydro | summer | 14.36 | 9.034% | 0% | 13.0627 | 15.28% | 0.07344% | 12.155
NAROW1_2_UNIT | Hydro | nonsummer | 12 | 29.28% | 0% | 8.4868 | 16.13% | 0.1394% | 10.0476
NAROW1_2_UNIT | Hydro | summer | 12 | 17.56% | 0% | 9.8929 | 15.28% | 0.07344% | 10.1574
NAROW2_2_UNIT | Hydro | nonsummer | 55 | 60.37% | 0% | 21.7974 | 16.13% | 0.1394% | 46.0516
NAROW2_2_UNIT | Hydro | summer | 55 | 53.65% | 0% | 25.4933 | 15.28% | 0.07344% | 46.5547
OLINDA_2_COYCRK | Hydro | nonsummer | 3.13 | 66.25% | 0% | 1.0564 | 16.13% | 0.1394% | 2.6208
OLINDA_2_COYCRK | Hydro | summer | 3.13 | 66.67% | 0% | 1.0433 | 15.28% | 0.07344% | 2.6494
PADUA_6_MWDSDM | Hydro | nonsummer | 9.9 | 1.099% | 0% | 9.7912 | 16.13% | 0.1394% | 8.2893
PADUA_6_MWDSDM | Hydro | summer | 9.9 | 0.5436% | 0% | 9.8462 | 15.28% | 0.07344% | 8.3798
PADUA_7_SDIMAS | Hydro | nonsummer | 1.05 | 15.23% | 0% | 0.89011 | 16.13% | 0.1394% | 0.87917
PADUA_7_SDIMAS | Hydro | summer | 1.05 | 36.3% | 0% | 0.66881 | 15.28% | 0.07344% | 0.88877
PARDEB_6_UNITS | Hydro | nonsummer | 30 | 19.89% | 0% | 24.0342 | 16.13% | 0.1394% | 25.1191
PARDEB_6_UNITS | Hydro | summer | 30 | 7.092% | 0% | 27.8723 | 15.28% | 0.07344% | 25.3935
PINFLT_7_UNITS | Hydro | nonsummer | 198.51 | 35.34% | 4.253% | 119.9088 | 16.13% | 0.1394% | 166.2128
PINFLT_7_UNITS | Hydro | summer | 198.51 | 40.72% | 2.018% | 113.6695 | 15.28% | 0.07344% | 168.0285
PIT1_7_UNIT 1 | Hydro | nonsummer | 32 | 35.24% | 0% | 20.7231 | 16.13% | 0.1394% | 26.7937
PIT1_7_UNIT 1 | Hydro | summer | 32 | 3.121% | 0% | 31.0013 | 15.28% | 0.07344% | 27.0864
PIT1_7_UNIT 2 | Hydro | nonsummer | 32 | 0.5321% | 0% | 31.8297 | 16.13% | 0.1394% | 26.7937
PIT1_7_UNIT 2 | Hydro | summer | 32 | 0.5359% | 0% | 31.8285 | 15.28% | 0.07344% | 27.0864
PIT3_7_PL1X3 | Hydro | nonsummer | 70.6 | 9.881% | 0% | 63.6239 | 16.13% | 0.1394% | 59.1135
PIT3_7_PL1X3 | Hydro | summer | 70.6 | 2.759% | 0.01263% | 68.6432 | 15.28% | 0.07344% | 59.7593
PIT4_7_PL1X2 | Hydro | nonsummer | 95 | 0.947% | 0% | 94.1003 | 16.13% | 0.1394% | 79.5437
PIT4_7_PL1X2 | Hydro | summer | 95 | 1.097% | 0.002156% | 93.9556 | 15.28% | 0.07344% | 80.4126
PIT5_7_PL1X2 | Hydro | nonsummer | 82 | 2.039% | 0% | 80.3281 | 16.13% | 0.1394% | 68.6588
PIT5_7_PL1X2 | Hydro | summer | 82 | 1.457% | 0.0007085% | 80.8048 | 15.28% | 0.07344% | 69.4088
PIT5_7_PL3X4 | Hydro | nonsummer | 82 | 8.227% | 0% | 75.2538 | 16.13% | 0.1394% | 68.6588
PIT5_7_PL3X4 | Hydro | summer | 82 | 1.745% | 0% | 80.5689 | 15.28% | 0.07344% | 69.4088
PIT6_7_UNIT 1 | Hydro | nonsummer | 39 | 3.837% | 0% | 37.5034 | 16.13% | 0.1394% | 32.6548
PIT6_7_UNIT 1 | Hydro | summer | 39 | 3.367% | 0% | 37.687 | 15.28% | 0.07344% | 33.0115
PIT6_7_UNIT 2 | Hydro | nonsummer | 40 | 5.303% | 0% | 37.8789 | 16.13% | 0.1394% | 33.4921
PIT6_7_UNIT 2 | Hydro | summer | 40 | 5.255% | 0% | 37.8979 | 15.28% | 0.07344% | 33.858
PIT7_7_UNIT 1 | Hydro | nonsummer | 55.7 | 3.241% | 0% | 53.8946 | 16.13% | 0.1394% | 46.6377
PIT7_7_UNIT 1 | Hydro | summer | 55.7 | 3.073% | 0.001842% | 53.9873 | 15.28% | 0.07344% | 47.1472
PIT7_7_UNIT 2 | Hydro | nonsummer | 54.6 | 16.94% | 0% | 45.3487 | 16.13% | 0.1394% | 45.7167
PIT7_7_UNIT 2 | Hydro | summer | 54.6 | 8.113% | 0% | 50.1703 | 15.28% | 0.07344% | 46.2161
POEPH_7_UNIT 1 | Hydro | nonsummer | 68 | 20.76% | 0% | 53.8844 | 16.13% | 0.1394% | 56.9365
POEPH_7_UNIT 1 | Hydro | summer | 68 | 50.97% | 0% | 33.3372 | 15.28% | 0.07344% | 57.5585
POEPH_7_UNIT 2 | Hydro | nonsummer | 68.5 | 19.85% | 0% | 54.9061 | 16.13% | 0.1394% | 57.3552
POEPH_7_UNIT 2 | Hydro | summer | 68.5 | 46.99% | 0.01631% | 36.2987 | 15.28% | 0.07344% | 57.9817
RCKCRK_7_UNIT 1 | Hydro | nonsummer | 57 | 21.55% | 0% | 44.7148 | 16.13% | 0.1394% | 47.7262
RCKCRK_7_UNIT 1 | Hydro | summer | 57 | 43.33% | 0% | 32.2992 | 15.28% | 0.07344% | 48.2476
RCKCRK_7_UNIT 2 | Hydro | nonsummer | 56.9 | 24.41% | 0% | 43.0111 | 16.13% | 0.1394% | 47.6425
RCKCRK_7_UNIT 2 | Hydro | summer | 56.9 | 30.49% | 0% | 39.5487 | 15.28% | 0.07344% | 48.1629
RECTOR_2_QF | Hydro | nonsummer | 20.09 | 63.74% | 0% | 7.2854 | 16.13% | 0.1394% | 16.8214
RECTOR_2_QF | Hydro | summer | 20.09 | 58.38% | 0% | 8.3616 | 15.28% | 0.07344% | 17.0052
ROLLIN_6_UNIT | Hydro | nonsummer | 13.5 | 29.99% | 0% | 9.4514 | 16.13% | 0.1394% | 11.3036
ROLLIN_6_UNIT | Hydro | summer | 13.5 | 33.88% | 0% | 8.9262 | 15.28% | 0.07344% | 11.4271
SALTSP_7_UNITS | Hydro | nonsummer | 46 | 35.03% | 0% | 29.8866 | 16.13% | 0.1394% | 38.5159
SALTSP_7_UNITS | Hydro | summer | 46 | 23.33% | 0% | 35.2694 | 15.28% | 0.07344% | 38.9366
SAUGUS_6_MWDFTH | Hydro | nonsummer | 9.1 | 13.66% | 0% | 7.8571 | 16.13% | 0.1394% | 7.6194
SAUGUS_6_MWDFTH | Hydro | summer | 9.1 | 1.473% | 0% | 8.9659 | 15.28% | 0.07344% | 7.7027
SLYCRK_1_UNIT 1 | Hydro | nonsummer | 13 | 1.111% | 0% | 12.8556 | 16.13% | 0.1394% | 10.8849
SLYCRK_1_UNIT 1 | Hydro | summer | 13 | 3.396% | 0% | 12.5586 | 15.28% | 0.07344% | 11.0038
SPAULD_6_UNIT12 | Hydro | nonsummer | 11.4 | 44.06% | 0% | 6.3769 | 16.13% | 0.1394% | 9.5452
SPAULD_6_UNIT12 | Hydro | summer | 11.4 | 35.77% | 0% | 7.3228 | 15.28% | 0.07344% | 9.6495
SPICER_1_UNITS | Hydro | nonsummer | 6 | 0.9825% | 0% | 5.9411 | 16.13% | 0.1394% | 5.0238
SPICER_1_UNITS | Hydro | summer | 6 | 0.5523% | 0% | 5.9669 | 15.28% | 0.07344% | 5.0787
SPRGVL_2_SUCCES | Hydro | nonsummer | 1.4 | 24.26% | 0.1386% | 1.0584 | 16.13% | 0.1394% | 1.1722
SPRGVL_2_SUCCES | Hydro | summer | 1.4 | 24.41% | 0.06958% | 1.0572 | 15.28% | 0.07344% | 1.185
STANIS_7_UNIT 1 | Hydro | nonsummer | 91 | 6.614% | 0% | 84.9809 | 16.13% | 0.1394% | 76.1945
STANIS_7_UNIT 1 | Hydro | summer | 91 | 1.874% | 0% | 89.2946 | 15.28% | 0.07344% | 77.0268
TIGRCK_7_UNITS | Hydro | nonsummer | 62 | 8.774% | 0% | 56.5601 | 16.13% | 0.1394% | 51.9127
TIGRCK_7_UNITS | Hydro | summer | 62 | 6.295% | 0.01757% | 58.0859 | 15.28% | 0.07344% | 52.4798
TVYVLY_6_KRSHY1 | Hydro | nonsummer | 1.3 | 54.01% | 0% | 0.59789 | 16.13% | 0.1394% | 1.0885
TVYVLY_6_KRSHY1 | Hydro | summer | 1.3 | 59.15% | 0% | 0.53105 | 15.28% | 0.07344% | 1.1004
UKIAH_7_LAKEMN | Hydro | nonsummer | 3.5 | 16.3% | 0% | 2.9296 | 16.13% | 0.1394% | 2.9306
UKIAH_7_LAKEMN | Hydro | summer | 3.5 | 1.413% | 0% | 3.4505 | 15.28% | 0.07344% | 2.9626
VALLEY_5_PERRIS | Hydro | nonsummer | 7.94 | 62.3% | 0% | 2.9931 | 16.13% | 0.1394% | 6.6482
VALLEY_5_PERRIS | Hydro | summer | 7.94 | 65.24% | 0% | 2.7598 | 15.28% | 0.07344% | 6.7208
VILLPK_2_VALLYV | Hydro | nonsummer | 4.1 | 66.25% | 0% | 1.3838 | 16.13% | 0.1394% | 3.4329
VILLPK_2_VALLYV | Hydro | summer | 4.1 | 64.38% | 0% | 1.4603 | 15.28% | 0.07344% | 3.4704
VILLPK_6_MWDYOR | Hydro | nonsummer | 5.1 | 0.4605% | 0% | 5.0765 | 16.13% | 0.1394% | 4.2702
VILLPK_6_MWDYOR | Hydro | summer | 5.1 | 0% | 0.6216% | 5.0683 | 15.28% | 0.07344% | 4.3169
WARNE_2_UNIT | Hydro | nonsummer | 76 | 0.8447% | 0% | 75.358 | 16.13% | 0.1394% | 63.635
WARNE_2_UNIT | Hydro | summer | 76 | 1.298% | 0% | 75.0133 | 15.28% | 0.07344% | 64.3301
WDLEAF_7_UNIT 1 | Hydro | nonsummer | 60 | 5.686% | 0% | 56.5883 | 16.13% | 0.1394% | 50.2381
WDLEAF_7_UNIT 1 | Hydro | summer | 60 | 0.5867% | 0% | 59.648 | 15.28% | 0.07344% | 50.7869
WESTPT_2_UNIT | Hydro | nonsummer | 14 | 1.027% | 0% | 13.8562 | 16.13% | 0.1394% | 11.7222
WESTPT_2_UNIT | Hydro | summer | 14 | 0.6017% | 0.02179% | 13.9127 | 15.28% | 0.07344% | 11.8503
WISE_1_UNIT 1 | Hydro | nonsummer | 14.5 | 23.53% | 0% | 11.0887 | 16.13% | 0.1394% | 12.1409
WISE_1_UNIT 1 | Hydro | summer | 14.5 | 25.71% | 0% | 10.7722 | 15.28% | 0.07344% | 12.2735
WISE_1_UNIT 2 | Hydro | nonsummer | 3.2 | 89.12% | 0% | 0.34813 | 16.13% | 0.1394% | 2.6794
WISE_1_UNIT 2 | Hydro | summer | 3.2 | 96.3% | 0% | 0.11852 | 15.28% | 0.07344% | 2.7086
WISHON_6_UNITS | Hydro | nonsummer | 18.4 | 52.55% | 0% | 8.7314 | 16.13% | 0.1394% | 15.4064
WISHON_6_UNITS | Hydro | summer | 18.4 | 42.83% | 0% | 10.5194 | 15.28% | 0.07344% | 15.5747
DIABLO_7_UNIT 1 | Nuclear | nonsummer | 1150 | 1.143% | 0% | 1136.8514 | 1.735% | 0.05937% | 1129.366
DIABLO_7_UNIT 1 | Nuclear | summer | 1150 | 0.8131% | 0% | 1140.649 | 0.5682% | 0.03299% | 1143.0868
DIABLO_7_UNIT 2 | Nuclear | nonsummer | 1150 | 1.556% | 0.1515% | 1130.3692 | 1.735% | 0.05937% | 1129.366
DIABLO_7_UNIT 2 | Nuclear | summer | 1150 | 0.2528% | 0% | 1147.0932 | 0.5682% | 0.03299% | 1143.0868
PVERDE_5_SCEDYN | Nuclear | nonsummer | 635 | 3.131% | 0% | 615.1178 | 1.735% | 0.05937% | 623.6064
PVERDE_5_SCEDYN | Nuclear | summer | 635 | 0.6957% | 0.1525% | 629.6141 | 0.5682% | 0.03299% | 631.1827
ALMASL_2_AL6BT6 | Paired_BattStorage | nonsummer | 50 | 7.207% | 0% | 46.3964 | 6.409% | 0.001629% | 46.7949
ALMASL_2_AL6BT6 | Paired_BattStorage | summer | 50 | 16.55% | 0% | 41.7238 | 8.917% | 0.0002567% | 45.5412
BIGSKY_2_AS2BT1 | Paired_BattStorage | nonsummer | 127 | 3.441% | 0% | 122.6305 | 6.409% | 0.001629% | 118.8591
BIGSKY_2_AS2BT1 | Paired_BattStorage | summer | 127 | 3.551% | 0% | 122.4903 | 8.917% | 0.0002567% | 115.6746
BIGSKY_2_ASLBT2 | Paired_BattStorage | nonsummer | 100 | 2.979% | 0% | 97.021 | 6.409% | 0.001629% | 93.5898
BIGSKY_2_ASLBT2 | Paired_BattStorage | summer | 100 | 3.46% | 0% | 96.5405 | 8.917% | 0.0002567% | 91.0824
BLKCRK_2_GMCBT1 | Paired_BattStorage | nonsummer | 230 | 4.063% | 0% | 220.6556 | 6.409% | 0.001629% | 215.2566
BLKCRK_2_GMCBT1 | Paired_BattStorage | summer | 230 | 10.2% | 0% | 206.5423 | 8.917% | 0.0002567% | 209.4895
BLM W_2_COSBT1 | Paired_BattStorage | nonsummer | 60 | 7.958% | 0% | 55.2252 | 6.409% | 0.001629% | 56.1539
BLM W_2_COSBT1 | Paired_BattStorage | summer | 60 | 13.68% | 0% | 51.7913 | 8.917% | 0.0002567% | 54.6494
CALFTN_2_CFSBT1 | Paired_BattStorage | nonsummer | 60 | 4.247% | 0% | 57.4521 | 6.409% | 0.001629% | 56.1539
CALFTN_2_CFSBT1 | Paired_BattStorage | summer | 60 | 7.362% | 0% | 55.5826 | 8.917% | 0.0002567% | 54.6494
CENTPD_2_BMSX2 | Paired_BattStorage | nonsummer | 112 | 8.137% | 0% | 102.8867 | 6.409% | 0.001629% | 104.8206
CENTPD_2_BMSX2 | Paired_BattStorage | summer | 112 | 6.544% | 0% | 104.6708 | 8.917% | 0.0002567% | 102.0123
CHESTN_2_CHWBX2 | Paired_BattStorage | nonsummer | 135 | 5.732% | 0% | 127.2624 | 6.409% | 0.001629% | 126.3463
CHESTN_2_CHWBX2 | Paired_BattStorage | summer | 135 | 9.709% | 0% | 121.8931 | 8.917% | 0.0002567% | 122.9612
CMBLND_2_DS2BT1 | Paired_BattStorage | nonsummer | 52 | 6.234% | 0% | 48.7584 | 6.409% | 0.001629% | 48.6667
CMBLND_2_DS2BT1 | Paired_BattStorage | summer | 52 | 10.6% | 0% | 46.4859 | 8.917% | 0.0002567% | 47.3628
CMBLND_2_DS2BT2 | Paired_BattStorage | nonsummer | 33 | 4.993% | 0% | 31.3523 | 6.409% | 0.001629% | 30.8846
CMBLND_2_DS2BT2 | Paired_BattStorage | summer | 33 | 10.78% | 0% | 29.4413 | 8.917% | 0.0002567% | 30.0572
CMBLND_2_DS2BT3 | Paired_BattStorage | nonsummer | 46 | 5.357% | 0% | 43.5358 | 6.409% | 0.001629% | 43.0513
CMBLND_2_DS2BT3 | Paired_BattStorage | summer | 46 | 10.65% | 0% | 41.1005 | 8.917% | 0.0002567% | 41.8979
DRACKR_2_DSUBT1 | Paired_BattStorage | nonsummer | 63 | 8.316% | 0% | 57.7611 | 6.409% | 0.001629% | 58.9616
DRACKR_2_DSUBT1 | Paired_BattStorage | summer | 63 | 16.25% | 0% | 52.7602 | 8.917% | 0.0002567% | 57.3819
DRACKR_2_DSUBT2 | Paired_BattStorage | nonsummer | 115 | 6.869% | 0% | 107.1008 | 6.409% | 0.001629% | 107.6283
DRACKR_2_DSUBT2 | Paired_BattStorage | summer | 115 | 8.176% | 0% | 105.5977 | 8.917% | 0.0002567% | 104.7447
DRACKR_2_DSUBT3 | Paired_BattStorage | nonsummer | 115 | 4.081% | 0% | 110.3072 | 6.409% | 0.001629% | 107.6283
DRACKR_2_DSUBT3 | Paired_BattStorage | summer | 115 | 9.634% | 0% | 103.9215 | 8.917% | 0.0002567% | 104.7447
DRACKR_2_DSUBT4 | Paired_BattStorage | nonsummer | 47 | 10.4% | 0% | 42.1118 | 6.409% | 0.001629% | 43.9872
DRACKR_2_DSUBT4 | Paired_BattStorage | summer | 47 | 18.03% | 0% | 38.5255 | 8.917% | 0.0002567% | 42.8087
DSRTHV_2_DH2BT1 | Paired_BattStorage | nonsummer | 35 | 31.4% | 0% | 24.0113 | 6.409% | 0.001629% | 32.7564
DSRTHV_2_DH2BT1 | Paired_BattStorage | summer | 35 | 39.1% | 0% | 21.3134 | 8.917% | 0.0002567% | 31.8788
DSRTSN_2_DS2BX2 | Paired_BattStorage | nonsummer | 230 | 6.865% | 0.0004832% | 214.2103 | 6.409% | 0.001629% | 215.2566
DSRTSN_2_DS2BX2 | Paired_BattStorage | summer | 230 | 10.43% | 0% | 205.9999 | 8.917% | 0.0002567% | 209.4895
DSRTSN_2_DS2X2 | Paired_BattStorage | nonsummer | 230 | 4.13% | 0% | 220.5003 | 6.409% | 0.001629% | 215.2566
DSRTSN_2_DS2X2 | Paired_BattStorage | summer | 230 | 5.915% | 0% | 216.3948 | 8.917% | 0.0002567% | 209.4895
FIFTHS_2_FSSBT | Paired_BattStorage | nonsummer | 137 | 4.613% | 0% | 130.6806 | 6.409% | 0.001629% | 128.2181
FIFTHS_2_FSSBT | Paired_BattStorage | summer | 137 | 8.616% | 0% | 125.1957 | 8.917% | 0.0002567% | 124.7829
FILIPPI_2_QZSBTX | Paired_BattStorage | nonsummer | 150 | 6.884% | 0.0009665% | 139.6728 | 6.409% | 0.001629% | 140.3848
FILIPPI_2_QZSBTX | Paired_BattStorage | summer | 150 | 11.02% | 0.0001602% | 133.4749 | 8.917% | 0.0002567% | 136.6236
GARLND_2_GARBT1 | Paired_BattStorage | nonsummer | 88 | 14.08% | 0% | 75.611 | 6.409% | 0.001629% | 82.3591
GARLND_2_GARBT1 | Paired_BattStorage | summer | 88 | 21.41% | 0% | 69.1551 | 8.917% | 0.0002567% | 80.1525
GASKW1_2_GW2BT1 | Paired_BattStorage | nonsummer | 20 | 14.19% | 0% | 17.1619 | 6.409% | 0.001629% | 18.718
GASKW1_2_GW2BT1 | Paired_BattStorage | summer | 20 | 21.85% | 0% | 15.6301 | 8.917% | 0.0002567% | 18.2165
HIGHDS_2_H5SBT1 | Paired_BattStorage | nonsummer | 50 | 12.72% | 0% | 43.6391 | 6.409% | 0.001629% | 46.7949
HIGHDS_2_H5SBT1 | Paired_BattStorage | summer | 50 | 11.98% | 0% | 44.0106 | 8.917% | 0.0002567% | 45.5412
KRAMER_1_R1BX3 | Paired_BattStorage | nonsummer | 75 | 6.993% | 0% | 69.7551 | 6.409% | 0.001629% | 70.1924
KRAMER_1_R1BX3 | Paired_BattStorage | summer | 75 | 6.503% | 0% | 70.123 | 8.917% | 0.0002567% | 68.3118
KRAMER_1_R2BX2 | Paired_BattStorage | nonsummer | 40 | 5.176% | 0% | 37.9298 | 6.409% | 0.001629% | 37.4359
KRAMER_1_R2BX2 | Paired_BattStorage | summer | 40 | 8.562% | 0% | 36.5754 | 8.917% | 0.0002567% | 36.433
MCFLND_5_MFSBT1 | Paired_BattStorage | nonsummer | 100 | 6.848% | 0% | 93.1524 | 6.409% | 0.001629% | 93.5898
MCFLND_5_MFSBT1 | Paired_BattStorage | summer | 100 | 14.08% | 0% | 85.9177 | 8.917% | 0.0002567% | 91.0824
MCFLND_5_MSCBT1 | Paired_BattStorage | nonsummer | 185 | 6.986% | 0.00104% | 172.0731 | 6.409% | 0.001629% | 173.1412
MCFLND_5_MSCBT1 | Paired_BattStorage | summer | 185 | 11.02% | 0.0001602% | 164.619 | 8.917% | 0.0002567% | 168.5024
MSTANG_2_MTGBT1 | Paired_BattStorage | nonsummer | 75 | 7.765% | 0% | 69.176 | 6.409% | 0.001629% | 70.1924
MSTANG_2_MTGBT1 | Paired_BattStorage | summer | 75 | 6.142% | 0% | 70.3932 | 8.917% | 0.0002567% | 68.3118
OBERON_5_O1BBX2 | Paired_BattStorage | nonsummer | 125 | 5.496% | 0% | 118.1298 | 6.409% | 0.001629% | 116.9873
OBERON_5_O1BBX2 | Paired_BattStorage | summer | 125 | 10.44% | 0% | 111.9536 | 8.917% | 0.0002567% | 113.853
OBERON_5_O2BBX2 | Paired_BattStorage | nonsummer | 125 | 4.883% | 0% | 118.8966 | 6.409% | 0.001629% | 116.9873
OBERON_5_O2BBX2 | Paired_BattStorage | summer | 125 | 13.11% | 0% | 108.6081 | 8.917% | 0.0002567% | 113.853
PALSEL_6_PLSBT1 | Paired_BattStorage | nonsummer | 15 | 6.77% | 0.0007419% | 13.9844 | 6.409% | 0.001629% | 14.0385
PALSEL_6_PLSBT1 | Paired_BattStorage | summer | 15 | 10.74% | 1.989e-05% | 13.3897 | 8.917% | 0.0002567% | 13.6624
POLRIS_2_ASEBT1 | Paired_BattStorage | nonsummer | 28 | 6.682% | 0% | 26.1292 | 6.409% | 0.001629% | 26.2052
POLRIS_2_ASEBT1 | Paired_BattStorage | summer | 28 | 14.14% | 0% | 24.0411 | 8.917% | 0.0002567% | 25.5031
POLRIS_2_ASRBT1 | Paired_BattStorage | nonsummer | 80 | 9.885% | 0.0004198% | 72.0916 | 6.409% | 0.001629% | 74.8719
POLRIS_2_ASRBT1 | Paired_BattStorage | summer | 80 | 11.02% | 0% | 71.1852 | 8.917% | 0.0002567% | 72.8659
PRIMM_2_SSSBT1 | Paired_BattStorage | nonsummer | 200 | 6.986% | 0.00104% | 186.0249 | 6.409% | 0.001629% | 187.1797
PRIMM_2_SSSBT1 | Paired_BattStorage | summer | 200 | 11.02% | 0.0001602% | 177.9665 | 8.917% | 0.0002567% | 182.1648
PROXSR_2_PS1BT1 | Paired_BattStorage | nonsummer | 40 | 7.556% | 0.0004784% | 36.9774 | 6.409% | 0.001629% | 37.4359
PROXSR_2_PS1BT1 | Paired_BattStorage | summer | 40 | 10.45% | 0% | 35.8188 | 8.917% | 0.0002567% | 36.433
PROXSR_2_PS1BT2 | Paired_BattStorage | nonsummer | 32 | 6.813% | 0.0006199% | 29.8195 | 6.409% | 0.001629% | 29.9487
PROXSR_2_PS1BT2 | Paired_BattStorage | summer | 32 | 9.709% | 0% | 28.8932 | 8.917% | 0.0002567% | 29.1464
PROXSR_2_PS2BT3 | Paired_BattStorage | nonsummer | 90 | 8.388% | 0.000493% | 82.4505 | 6.409% | 0.001629% | 84.2309
PROXSR_2_PS2BT3 | Paired_BattStorage | summer | 90 | 10.99% | 0% | 80.1076 | 8.917% | 0.0002567% | 81.9741
REXFRD_2_RSFBX2 | Paired_BattStorage | nonsummer | 240 | 6.986% | 0.00104% | 223.2299 | 6.409% | 0.001629% | 224.6156
REXFRD_2_RSFBX2 | Paired_BattStorage | summer | 240 | 11.02% | 0.0001602% | 213.5598 | 8.917% | 0.0002567% | 218.5977
RSMNDS_2_CSRBT1 | Paired_BattStorage | nonsummer | 15 | 6.986% | 0.00104% | 13.9519 | 6.409% | 0.001629% | 14.0385
RSMNDS_2_CSRBT1 | Paired_BattStorage | summer | 15 | 11.02% | 0.0001602% | 13.3475 | 8.917% | 0.0002567% | 13.6624
RSMNDS_2_CSRBT2 | Paired_BattStorage | nonsummer | 10 | 6.986% | 0.00104% | 9.3012 | 6.409% | 0.001629% | 9.359
RSMNDS_2_CSRBT2 | Paired_BattStorage | summer | 10 | 11.02% | 0.0001602% | 8.8983 | 8.917% | 0.0002567% | 9.1082
RTEDDY_2_RWSBT1 | Paired_BattStorage | nonsummer | 30 | 6.541% | 0.0005955% | 28.0374 | 6.409% | 0.001629% | 28.077
RTEDDY_2_RWSBT1 | Paired_BattStorage | summer | 30 | 10.43% | 0% | 26.8711 | 8.917% | 0.0002567% | 27.3247
RTEDDY_2_RWSBT2 | Paired_BattStorage | nonsummer | 30 | 7.184% | 0.0005955% | 27.8447 | 6.409% | 0.001629% | 28.077
RTEDDY_2_RWSBT2 | Paired_BattStorage | summer | 30 | 10.56% | 0% | 26.8321 | 8.917% | 0.0002567% | 27.3247
RTEDDY_2_RWSBT3 | Paired_BattStorage | nonsummer | 45 | 6.5% | 0.0006297% | 42.0747 | 6.409% | 0.001629% | 42.1154
RTEDDY_2_RWSBT3 | Paired_BattStorage | summer | 45 | 9.999% | 0% | 40.5005 | 8.917% | 0.0002567% | 40.9871
RTEDDY_2_RWSBT4 | Paired_BattStorage | nonsummer | 30 | 6.549% | 0.0005955% | 28.035 | 6.409% | 0.001629% | 28.077
RTEDDY_2_RWSBT4 | Paired_BattStorage | summer | 30 | 9.81% | 0% | 27.0569 | 8.917% | 0.0002567% | 27.3247
RTEDDY_2_RWSBT5 | Paired_BattStorage | nonsummer | 12 | 6.465% | 0.0006004% | 11.2241 | 6.409% | 0.001629% | 11.2308
RTEDDY_2_RWSBT5 | Paired_BattStorage | summer | 12 | 9.995% | 0% | 10.8006 | 8.917% | 0.0002567% | 10.9299
SCARLT_2_SS2BT1 | Paired_BattStorage | nonsummer | 150 | 9.549% | 0.0009372% | 135.6755 | 6.409% | 0.001629% | 140.3848
SCARLT_2_SS2BT1 | Paired_BattStorage | summer | 150 | 11.02% | 0.0001602% | 133.4749 | 8.917% | 0.0002567% | 136.6236
SCARLT_2_SSABT1 | Paired_BattStorage | nonsummer | 10 | 8.759% | 0.0006004% | 9.124 | 6.409% | 0.001629% | 9.359
SCARLT_2_SSABT1 | Paired_BattStorage | summer | 10 | 18.27% | 0% | 8.1726 | 8.917% | 0.0002567% | 9.1082
SCARLT_2_SSBBT1 | Paired_BattStorage | nonsummer | 30 | 9.093% | 0.0006004% | 27.272 | 6.409% | 0.001629% | 28.077
SCARLT_2_SSBBT1 | Paired_BattStorage | summer | 30 | 19.26% | 0% | 24.2215 | 8.917% | 0.0002567% | 27.3247
SISPRG_2_DS3BT1 | Paired_BattStorage | nonsummer | 61.5 | 5.625% | 0.06637% | 57.9995 | 6.409% | 0.001629% | 57.5577
SISPRG_2_DS3BT1 | Paired_BattStorage | summer | 61.5 | 11.04% | 0% | 54.7116 | 8.917% | 0.0002567% | 56.0157
SISPRG_2_DS3BT2 | Paired_BattStorage | nonsummer | 60 | 4.977% | 0% | 57.0137 | 6.409% | 0.001629% | 56.1539
SISPRG_2_DS3BT2 | Paired_BattStorage | summer | 60 | 9.74% | 0% | 54.1559 | 8.917% | 0.0002567% | 54.6494
SISPRG_2_DS3BT3 | Paired_BattStorage | nonsummer | 12.5 | 6.642% | 0% | 11.6698 | 6.409% | 0.001629% | 11.6987
SISPRG_2_DS3BT3 | Paired_BattStorage | summer | 12.5 | 11.67% | 0% | 11.0407 | 8.917% | 0.0002567% | 11.3853
SISPRG_2_DS3BT4 | Paired_BattStorage | nonsummer | 15 | 5.531% | 0% | 14.1704 | 6.409% | 0.001629% | 14.0385
SISPRG_2_DS3BT4 | Paired_BattStorage | summer | 15 | 8.773% | 0% | 13.684 | 8.917% | 0.0002567% | 13.6624
SOLBLU_2_WSBBX2 | Paired_BattStorage | nonsummer | 225 | 5.812% | 0% | 211.9226 | 6.409% | 0.001629% | 210.5771
SOLBLU_2_WSBBX2 | Paired_BattStorage | summer | 225 | 9.709% | 0% | 203.1551 | 8.917% | 0.0002567% | 204.9354
SUNCAT_2_A1ABT1 | Paired_BattStorage | nonsummer | 47 | 13.54% | 0% | 40.6346 | 6.409% | 0.001629% | 43.9872
SUNCAT_2_A1ABT1 | Paired_BattStorage | summer | 47 | 24.81% | 0% | 35.3406 | 8.917% | 0.0002567% | 42.8087
SUNCAT_2_A1BBT1 | Paired_BattStorage | nonsummer | 63 | 13.61% | 0% | 54.4235 | 6.409% | 0.001629% | 58.9616
SUNCAT_2_A1BBT1 | Paired_BattStorage | summer | 63 | 25.57% | 0% | 46.8887 | 8.917% | 0.0002567% | 57.3819
SUNCAT_2_A2ABT2 | Paired_BattStorage | nonsummer | 132 | 9.108% | 0% | 119.9777 | 6.409% | 0.001629% | 123.5386
SUNCAT_2_A2ABT2 | Paired_BattStorage | summer | 132 | 14.38% | 0% | 113.0164 | 8.917% | 0.0002567% | 120.2287
TRNQLT_2_RETBT1 | Paired_BattStorage | nonsummer | 72 | 12.79% | 0% | 62.788 | 6.409% | 0.001629% | 67.3847
TRNQLT_2_RETBT1 | Paired_BattStorage | summer | 72 | 20.37% | 0% | 57.3342 | 8.917% | 0.0002567% | 65.5793
VALTNE_2_TSBBT1 | Paired_BattStorage | nonsummer | 18 | 6.986% | 0.00104% | 16.7422 | 6.409% | 0.001629% | 16.8462
VALTNE_2_TSBBT1 | Paired_BattStorage | summer | 18 | 11.02% | 0.0001602% | 16.017 | 8.917% | 0.0002567% | 16.3948
VALTNE_2_TSBBT2 | Paired_BattStorage | nonsummer | 22 | 6.986% | 0.00104% | 20.4627 | 6.409% | 0.001629% | 20.5898
VALTNE_2_TSBBT2 | Paired_BattStorage | summer | 22 | 11.02% | 0.0001602% | 19.5763 | 8.917% | 0.0002567% | 20.0381
VICPAS_2_SLOBT1 | Paired_BattStorage | nonsummer | 15 | 6.388% | 0.0004149% | 14.0418 | 6.409% | 0.001629% | 14.0385
VICPAS_2_SLOBT1 | Paired_BattStorage | summer | 15 | 10.81% | 0% | 13.3789 | 8.917% | 0.0002567% | 13.6624
VICPAS_2_SOCBT1 | Paired_BattStorage | nonsummer | 50 | 6.823% | 0.0004149% | 46.5883 | 6.409% | 0.001629% | 46.7949
VICPAS_2_SOCBT1 | Paired_BattStorage | summer | 50 | 12.02% | 0% | 43.9905 | 8.917% | 0.0002567% | 45.5412
VICPAS_2_SOCBT2 | Paired_BattStorage | nonsummer | 71 | 6.964% | 0.0004149% | 66.0551 | 6.409% | 0.001629% | 66.4488
VICPAS_2_SOCBT2 | Paired_BattStorage | summer | 71 | 10.96% | 0% | 63.2162 | 8.917% | 0.0002567% | 64.6685
VICPAS_2_VPSBT1 | Paired_BattStorage | nonsummer | 50 | 6.781% | 0.0004198% | 46.6094 | 6.409% | 0.001629% | 46.7949
VICPAS_2_VPSBT1 | Paired_BattStorage | summer | 50 | 11.31% | 0% | 44.3446 | 8.917% | 0.0002567% | 45.5412
VLCNTR_6_VCEBT1 | Paired_BattStorage | nonsummer | 54 | 5% | 0% | 51.2999 | 6.409% | 0.001629% | 50.5385
VLCNTR_6_VCEBT1 | Paired_BattStorage | summer | 54 | 8.484% | 0.01291% | 49.4115 | 8.917% | 0.0002567% | 49.1845
VLCNTR_6_VCEBT2 | Paired_BattStorage | nonsummer | 85 | 4.305% | 0% | 81.3406 | 6.409% | 0.001629% | 79.5514
VLCNTR_6_VCEBT2 | Paired_BattStorage | summer | 85 | 9.682% | 0% | 76.7704 | 8.917% | 0.0002567% | 77.42
WSTWND_2_M89BT2 | Paired_BattStorage | nonsummer | 70.6 | 8.838% | 0% | 64.3601 | 6.409% | 0.001629% | 66.0744
WSTWND_2_M89BT2 | Paired_BattStorage | summer | 70.6 | 9.646% | 0% | 63.7898 | 8.917% | 0.0002567% | 64.3042
YELPIN_2_YP2BT1 | Paired_BattStorage | nonsummer | 65 | 7.111% | 0% | 60.3782 | 6.409% | 0.001629% | 60.8334
YELPIN_2_YP2BT1 | Paired_BattStorage | summer | 65 | 8.533% | 0% | 59.4537 | 8.917% | 0.0002567% | 59.2036
YELPIN_2_YP2BT2 | Paired_BattStorage | nonsummer | 28 | 8.181% | 0.0007029% | 25.709 | 6.409% | 0.001629% | 26.2052
YELPIN_2_YP2BT2 | Paired_BattStorage | summer | 28 | 10.49% | 0% | 25.0621 | 8.917% | 0.0002567% | 25.5031
YELPIN_2_YP2BT3 | Paired_BattStorage | nonsummer | 32 | 7.556% | 0.0007419% | 29.582 | 6.409% | 0.001629% | 29.9487
YELPIN_2_YP2BT3 | Paired_BattStorage | summer | 32 | 10.06% | 3.14e-06% | 28.7806 | 8.917% | 0.0002567% | 29.1464
PALSEL_6_PLSSR1 | Paired_Solar_1Axis | nonsummer | 20 | #VALUE! | #VALUE! | #VALUE! | 0% | 0% | 20
PALSEL_6_PLSSR1 | Paired_Solar_1Axis | summer | 20 | #VALUE! | #VALUE! | #VALUE! | 2.493% | 0% | 19.5015
AGRICO_6_PL3N5 | Peaker | nonsummer | 22.69 | 1.369% | 0.1208% | 22.352 | 7.047% | 1.211% | 20.8162
AGRICO_6_PL3N5 | Peaker | summer | 22.69 | 0.5722% | 4.397% | 21.5626 | 4.696% | 3.635% | 20.7998
ALMEGT_1_UNIT 1 | Peaker | nonsummer | 25 | 15.12% | 3.793% | 20.2709 | 7.047% | 1.211% | 22.9354
ALMEGT_1_UNIT 1 | Peaker | summer | 25 | 17.97% | 10.54% | 17.8735 | 4.696% | 3.635% | 22.9174
ALMEGT_1_UNIT 2 | Peaker | nonsummer | 25 | 4.764% | 4.388% | 22.712 | 7.047% | 1.211% | 22.9354
ALMEGT_1_UNIT 2 | Peaker | summer | 25 | 10.58% | 10.67% | 19.6886 | 4.696% | 3.635% | 22.9174
ANAHM_2_CANYN1 | Peaker | nonsummer | 49.21 | 47.87% | 0% | 25.6507 | 7.047% | 1.211% | 45.1461
ANAHM_2_CANYN1 | Peaker | summer | 49.21 | 56.43% | 0% | 21.443 | 4.696% | 3.635% | 45.1105
ANAHM_2_CANYN2 | Peaker | nonsummer | 48.04 | 0.2594% | 0% | 47.9154 | 7.047% | 1.211% | 44.0727
ANAHM_2_CANYN2 | Peaker | summer | 48.04 | 0.9775% | 0% | 47.5704 | 4.696% | 3.635% | 44.038
ANAHM_2_CANYN3 | Peaker | nonsummer | 46.49 | 5.237% | 0% | 44.0553 | 7.047% | 1.211% | 42.6507
ANAHM_2_CANYN3 | Peaker | summer | 46.49 | 1.346% | 0% | 45.8644 | 4.696% | 3.635% | 42.6171
ANAHM_2_CANYN4 | Peaker | nonsummer | 49.8 | 1.707% | 0% | 48.9498 | 7.047% | 1.211% | 45.6874
ANAHM_2_CANYN4 | Peaker | summer | 49.8 | 1.207% | 0% | 49.1987 | 4.696% | 3.635% | 45.6514
BARRE_6_PEAKER | Peaker | nonsummer | 49 | 1.786% | 3.269% | 46.5228 | 7.047% | 1.211% | 44.9534
BARRE_6_PEAKER | Peaker | summer | 49 | 0.7788% | 10.86% | 43.2946 | 4.696% | 3.635% | 44.918
BASICE_2_UNITS | Peaker | nonsummer | 120 | 6.61% | 0.7971% | 111.111 | 7.047% | 1.211% | 110.0901
BASICE_2_UNITS | Peaker | summer | 120 | 4.1% | 2.133% | 112.52 | 4.696% | 3.635% | 110.0033
BDGRCK_1_UNITS | Peaker | nonsummer | 48.08 | 0.8638% | 7.184% | 44.2104 | 7.047% | 1.211% | 44.1094
BDGRCK_1_UNITS | Peaker | summer | 48.08 | 4.274% | 7.581% | 42.3801 | 4.696% | 3.635% | 44.0747
BEARMT_1_UNIT | Peaker | nonsummer | 49.21 | 0.3733% | 6.632% | 45.7629 | 7.047% | 1.211% | 45.1461
BEARMT_1_UNIT | Peaker | summer | 49.21 | 0.399% | 9.152% | 44.5098 | 4.696% | 3.635% | 45.1105
BOGUE_1_UNITA1 | Peaker | nonsummer | 48.69 | 1.868% | 0.2876% | 47.6407 | 7.047% | 1.211% | 44.669
BOGUE_1_UNITA1 | Peaker | summer | 48.69 | 1.484% | 2.741% | 46.6328 | 4.696% | 3.635% | 44.6339
BORDER_6_UNITA1 | Peaker | nonsummer | 51.25 | 6.53% | 0% | 47.9036 | 7.047% | 1.211% | 47.0176
BORDER_6_UNITA1 | Peaker | summer | 51.25 | 2.286% | 0.306% | 49.9217 | 4.696% | 3.635% | 46.9806
CARLS1_2_CARCT1 | Peaker | nonsummer | 422 | 7.164% | 0.03333% | 391.6291 | 7.047% | 1.211% | 387.15
CARLS1_2_CARCT1 | Peaker | summer | 422 | 2.291% | 5.524% | 389.0202 | 4.696% | 3.635% | 386.8451
CARLS2_1_CARCT1 | Peaker | nonsummer | 105.5 | 0.46% | 0.02889% | 104.9842 | 7.047% | 1.211% | 96.7875
CARLS2_1_CARCT1 | Peaker | summer | 105.5 | 3.887% | 2.064% | 99.2211 | 4.696% | 3.635% | 96.7113
CENTER_6_PEAKER | Peaker | nonsummer | 47.3 | 5.095% | 0.179% | 44.8056 | 7.047% | 1.211% | 43.3938
CENTER_6_PEAKER | Peaker | summer | 47.3 | 0.8665% | 1.39% | 46.2327 | 4.696% | 3.635% | 43.3597
CENTRY_6_PL1X4 | Peaker | nonsummer | 41.4 | 15.71% | 0% | 34.8963 | 7.047% | 1.211% | 37.9811
CENTRY_6_PL1X4 | Peaker | summer | 41.4 | 5.366% | 1.281% | 38.648 | 4.696% | 3.635% | 37.9512
CHALK_1_UNIT | Peaker | nonsummer | 48.67 | 0% | 6.625% | 45.4458 | 7.047% | 1.211% | 44.6507
CHALK_1_UNIT | Peaker | summer | 48.67 | 0.8995% | 8.799% | 43.9498 | 4.696% | 3.635% | 44.6155
COCOPP_2_CTG1 | Peaker | nonsummer | 204.2 | 0.8543% | 1.583% | 199.2234 | 7.047% | 1.211% | 187.3366
COCOPP_2_CTG1 | Peaker | summer | 204.2 | 0% | 5.06% | 193.8665 | 4.696% | 3.635% | 187.189
COCOPP_2_CTG2 | Peaker | nonsummer | 202.7 | 1.726% | 1.352% | 196.4604 | 7.047% | 1.211% | 185.9605
COCOPP_2_CTG2 | Peaker | summer | 202.7 | 0.2462% | 4.748% | 192.5762 | 4.696% | 3.635% | 185.814
COCOPP_2_CTG3 | Peaker | nonsummer | 208.96 | 1.831% | 4.202% | 196.3533 | 7.047% | 1.211% | 191.7035
COCOPP_2_CTG3 | Peaker | summer | 208.96 | 0.1464% | 7.821% | 192.3114 | 4.696% | 3.635% | 191.5525
COCOPP_2_CTG4 | Peaker | nonsummer | 204.29 | 1.399% | 2.003% | 197.3401 | 7.047% | 1.211% | 187.4192
COCOPP_2_CTG4 | Peaker | summer | 204.29 | 0.4086% | 5.037% | 193.1654 | 4.696% | 3.635% | 187.2715
COLTON_6_AGUAM1 | Peaker | nonsummer | 43 | 0.2117% | 0.4381% | 42.7206 | 7.047% | 1.211% | 39.4489
COLTON_6_AGUAM1 | Peaker | summer | 43 | 6.049% | 1.247% | 39.863 | 4.696% | 3.635% | 39.4179
CSCGNR_1_UNIT 1 | Peaker | nonsummer | 24.75 | 5.495% | 0.01427% | 23.3866 | 7.047% | 1.211% | 22.7061
CSCGNR_1_UNIT 1 | Peaker | summer | 24.75 | 2.23% | 2.887% | 23.4835 | 4.696% | 3.635% | 22.6882
CSCGNR_1_UNIT 2 | Peaker | nonsummer | 24.75 | 23.49% | 0% | 18.9374 | 7.047% | 1.211% | 22.7061
CSCGNR_1_UNIT 2 | Peaker | summer | 24.75 | 11.97% | 3.169% | 21.004 | 4.696% | 3.635% | 22.6882
DOUBLC_1_UNITS | Peaker | nonsummer | 52.23 | 11.76% | 3.543% | 44.2386 | 7.047% | 1.211% | 47.9167
DOUBLC_1_UNITS | Peaker | summer | 52.23 | 1.234% | 5.676% | 48.6211 | 4.696% | 3.635% | 47.879
DREWS_6_PL1X4 | Peaker | nonsummer | 41.4 | 14.71% | 0% | 35.3117 | 7.047% | 1.211% | 37.9811
DREWS_6_PL1X4 | Peaker | summer | 41.4 | 12.72% | 2.065% | 35.2798 | 4.696% | 3.635% | 37.9512
ELCAJN_6_LM6K | Peaker | nonsummer | 48.1 | 2.031% | 0% | 47.1232 | 7.047% | 1.211% | 44.1278
ELCAJN_6_LM6K | Peaker | summer | 48.1 | 15.79% | 0.8984% | 40.0709 | 4.696% | 3.635% | 44.093
ELCAJN_6_UNITA1 | Peaker | nonsummer | 45.42 | 1.6% | 0% | 44.6932 | 7.047% | 1.211% | 41.6691
ELCAJN_6_UNITA1 | Peaker | summer | 45.42 | 10.13% | 0% | 40.8201 | 4.696% | 3.635% | 41.6363
ESCNDO_6_PL1X2 | Peaker | nonsummer | 48.71 | 11.8% | 0% | 42.9638 | 7.047% | 1.211% | 44.6874
ESCNDO_6_PL1X2 | Peaker | summer | 48.71 | 1.493% | 1.066% | 47.4634 | 4.696% | 3.635% | 44.6522
ESCNDO_6_UNITB1 | Peaker | nonsummer | 50.96 | 7.86% | 0.007449% | 46.9507 | 7.047% | 1.211% | 46.7516
ESCNDO_6_UNITB1 | Peaker | summer | 50.96 | 7.34% | 0.1551% | 47.1405 | 4.696% | 3.635% | 46.7148
ESCO_6_GLMQF | Peaker | nonsummer | 49.9 | 8.127% | 0.001258% | 45.844 | 7.047% | 1.211% | 45.7791
ESCO_6_GLMQF | Peaker | summer | 49.9 | 8.055% | 1.241% | 45.261 | 4.696% | 3.635% | 45.7431
ETIWND_2_UNIT1 | Peaker | nonsummer | 33.6 | 24.67% | 0% | 25.3111 | 7.047% | 1.211% | 30.8252
ETIWND_2_UNIT1 | Peaker | summer | 33.6 | 28.7% | 0% | 23.958 | 4.696% | 3.635% | 30.8009
ETIWND_6_GRPLND | Peaker | nonsummer | 45.64 | 1.407% | 0.6404% | 44.7056 | 7.047% | 1.211% | 41.8709
ETIWND_6_GRPLND | Peaker | summer | 45.64 | 3.397% | 2.403% | 42.9928 | 4.696% | 3.635% | 41.8379
GILRPP_1_PL1X2 | Peaker | nonsummer | 95.2 | 0% | 0.01091% | 95.1896 | 7.047% | 1.211% | 87.3381
GILRPP_1_PL1X2 | Peaker | summer | 95.2 | 0.4338% | 0.05178% | 94.7377 | 4.696% | 3.635% | 87.2693
GILRPP_1_PL3X4 | Peaker | nonsummer | 46.2 | 0.5918% | 0% | 45.9266 | 7.047% | 1.211% | 42.3847
GILRPP_1_PL3X4 | Peaker | summer | 46.2 | 0.3417% | 0.005659% | 46.0395 | 4.696% | 3.635% | 42.3513
GLNARM_7_UNIT 1 | Peaker | nonsummer | 22.13 | 10.74% | 0% | 19.7538 | 7.047% | 1.211% | 20.3024
GLNARM_7_UNIT 1 | Peaker | summer | 22.13 | 1.318% | 0% | 21.8383 | 4.696% | 3.635% | 20.2865
GLNARM_7_UNIT 2 | Peaker | nonsummer | 22.38 | 3.914% | 0% | 21.5041 | 7.047% | 1.211% | 20.5318
GLNARM_7_UNIT 2 | Peaker | summer | 22.38 | 3.461% | 0% | 21.6054 | 4.696% | 3.635% | 20.5156
GLNARM_7_UNIT 3 | Peaker | nonsummer | 44.83 | 3.832% | 0.02844% | 43.0994 | 7.047% | 1.211% | 41.1278
GLNARM_7_UNIT 3 | Peaker | summer | 44.83 | 1.034% | 0.05422% | 44.3423 | 4.696% | 3.635% | 41.0954
GLNARM_7_UNIT 4 | Peaker | nonsummer | 42.42 | 4.58% | 0% | 40.4771 | 7.047% | 1.211% | 38.9168
GLNARM_7_UNIT 4 | Peaker | summer | 42.42 | 5.495% | 0.03998% | 40.0721 | 4.696% | 3.635% | 38.8862
GOLETA_6_ELLWOD | Peaker | nonsummer | 54 | 7.785% | 0% | 49.7959 | 7.047% | 1.211% | 49.5405
GOLETA_6_ELLWOD | Peaker | summer | 54 | 1.267% | 0% | 53.3157 | 4.696% | 3.635% | 49.5015
HENRTA_6_ELCTG1 | Peaker | nonsummer | 50 | 7.048% | 1.211% | 45.8706 | 7.047% | 1.211% | 45.8709
HENRTA_6_ELCTG1 | Peaker | summer | 50 | 4.696% | 3.635% | 45.8347 | 4.696% | 3.635% | 45.8347
HENRTA_6_ELCTG2 | Peaker | nonsummer | 50 | 7.048% | 1.211% | 45.8706 | 7.047% | 1.211% | 45.8709
HENRTA_6_ELCTG2 | Peaker | summer | 50 | 4.696% | 3.635% | 45.8347 | 4.696% | 3.635% | 45.8347
HINSON_6_LBECH1 | Peaker | nonsummer | 63 | 0.6044% | 0% | 62.6192 | 7.047% | 1.211% | 57.7973
HINSON_6_LBECH1 | Peaker | summer | 63 | 1.736% | 0.01007% | 61.9002 | 4.696% | 3.635% | 57.7518
HINSON_6_LBECH2 | Peaker | nonsummer | 63 | 0.1334% | 0% | 62.9159 | 7.047% | 1.211% | 57.7973
HINSON_6_LBECH2 | Peaker | summer | 63 | 1.699% | 0.006571% | 61.9253 | 4.696% | 3.635% | 57.7518
HINSON_6_LBECH3 | Peaker | nonsummer | 63 | 18.14% | 0% | 51.5736 | 7.047% | 1.211% | 57.7973
HINSON_6_LBECH3 | Peaker | summer | 63 | 2.686% | 0.02409% | 61.2925 | 4.696% | 3.635% | 57.7518
HINSON_6_LBECH4 | Peaker | nonsummer | 63 | 0.2433% | 0% | 62.8467 | 7.047% | 1.211% | 57.7973
HINSON_6_LBECH4 | Peaker | summer | 63 | 0.07843% | 0.003285% | 62.9485 | 4.696% | 3.635% | 57.7518
INDIGO_1_UNIT 1 | Peaker | nonsummer | 45.3 | 4.751% | 0.2448% | 43.0367 | 7.047% | 1.211% | 41.559
INDIGO_1_UNIT 1 | Peaker | summer | 45.3 | 1.506% | 6.49% | 41.6778 | 4.696% | 3.635% | 41.5263
INDIGO_1_UNIT 2 | Peaker | nonsummer | 45.3 | 7.755% | 0.5504% | 41.5376 | 7.047% | 1.211% | 41.559
INDIGO_1_UNIT 2 | Peaker | summer | 45.3 | 0.6611% | 8.623% | 41.0945 | 4.696% | 3.635% | 41.5263
INDIGO_1_UNIT 3 | Peaker | nonsummer | 45.3 | 9.05% | 0.6178% | 40.9206 | 7.047% | 1.211% | 41.559
INDIGO_1_UNIT 3 | Peaker | summer | 45.3 | 0.7849% | 8.842% | 40.9392 | 4.696% | 3.635% | 41.5263
KELSO_2_UNITS | Peaker | nonsummer | 198.03 | 5.677% | 1.075% | 184.6587 | 7.047% | 1.211% | 181.6761
KELSO_2_UNITS | Peaker | summer | 198.03 | 1.293% | 4.553% | 186.4517 | 4.696% | 3.635% | 181.533
KERNFT_1_UNITS | Peaker | nonsummer | 52.4 | 2.419% | 4.864% | 48.5834 | 7.047% | 1.211% | 48.0727
KERNFT_1_UNITS | Peaker | summer | 52.4 | 15.44% | 6.773% | 40.7592 | 4.696% | 3.635% | 48.0348
KINGCO_1_KINGBR | Peaker | nonsummer | 34.5 | 0.3026% | 0% | 34.3956 | 7.047% | 1.211% | 31.6509
KINGCO_1_KINGBR | Peaker | summer | 34.5 | 2.263% | 0% | 33.7194 | 4.696% | 3.635% | 31.626
KNGCTY_6_UNITA1 | Peaker | nonsummer | 44.6 | 2.268% | 0.2634% | 43.4708 | 7.047% | 1.211% | 40.9168
KNGCTY_6_UNITA1 | Peaker | summer | 44.6 | 0.6338% | 2.686% | 43.1195 | 4.696% | 3.635% | 40.8846
LARKSP_6_UNIT 1 | Peaker | nonsummer | 49 | 8.842% | 0.751% | 44.2994 | 7.047% | 1.211% | 44.9534
LARKSP_6_UNIT 1 | Peaker | summer | 49 | 1.022% | 5.915% | 45.6008 | 4.696% | 3.635% | 44.918
LARKSP_6_UNIT 2 | Peaker | nonsummer | 49 | 7.175% | 0.8201% | 45.0826 | 7.047% | 1.211% | 44.9534
LARKSP_6_UNIT 2 | Peaker | summer | 49 | 1.208% | 4.729% | 46.0908 | 4.696% | 3.635% | 44.918
LIVOAK_1_UNIT 1 | Peaker | nonsummer | 49.7 | 4.535% | 8.934% | 43.0063 | 7.047% | 1.211% | 45.5956
LIVOAK_1_UNIT 1 | Peaker | summer | 49.7 | 2.135% | 14.19% | 41.5842 | 4.696% | 3.635% | 45.5597
LMBEPK_2_UNITA1 | Peaker | nonsummer | 47.5 | 2.318% | 0.1414% | 46.3319 | 7.047% | 1.211% | 43.5773
LMBEPK_2_UNITA1 | Peaker | summer | 47.5 | 1.603% | 0.8752% | 46.3231 | 4.696% | 3.635% | 43.543
LMBEPK_2_UNITA2 | Peaker | nonsummer | 47.6 | 1.686% | 0.507% | 46.5561 | 7.047% | 1.211% | 43.6691
LMBEPK_2_UNITA2 | Peaker | summer | 47.6 | 4.693% | 0.501% | 45.1277 | 4.696% | 3.635% | 43.6347
LMBEPK_2_UNITA3 | Peaker | nonsummer | 47.75 | 1.025% | 0.3857% | 47.0766 | 7.047% | 1.211% | 43.8067
LMBEPK_2_UNITA3 | Peaker | summer | 47.75 | 0.4708% | 1.037% | 47.0299 | 4.696% | 3.635% | 43.7722
LODI25_2_UNIT 1 | Peaker | nonsummer | 25 | 4.862% | 6.9% | 22.0595 | 7.047% | 1.211% | 22.9354
LODI25_2_UNIT 1 | Peaker | summer | 25 | 1.596% | 11.8% | 21.6512 | 4.696% | 3.635% | 22.9174
MALAGA_1_AUCTG1 | Peaker | nonsummer | 55.3 | 8.655% | 1.114% | 49.8979 | 7.047% | 1.211% | 50.7332
MALAGA_1_AUCTG1 | Peaker | summer | 55.3 | 4.696% | 3.635% | 50.6932 | 4.696% | 3.635% | 50.6932
MALAGA_1_AUCTG2 | Peaker | nonsummer | 55.3 | 8.655% | 1.114% | 49.8979 | 7.047% | 1.211% | 50.7332
MALAGA_1_AUCTG2 | Peaker | summer | 55.3 | 4.696% | 3.635% | 50.6932 | 4.696% | 3.635% | 50.6932
MIRLOM_6_PEAKER | Peaker | nonsummer | 47.18 | 0.738% | 1.22% | 46.2562 | 7.047% | 1.211% | 43.2837
MIRLOM_6_PEAKER | Peaker | summer | 47.18 | 2.178% | 7.212% | 42.7501 | 4.696% | 3.635% | 43.2496
MKTRCK_1_UNIT 1 | Peaker | nonsummer | 47.72 | 6.095% | 4.822% | 42.5102 | 7.047% | 1.211% | 43.7791
MKTRCK_1_UNIT 1 | Peaker | summer | 47.72 | 12.43% | 6.547% | 38.6621 | 4.696% | 3.635% | 43.7447
MNDALY_6_MCGRTH | Peaker | nonsummer | 48.56 | 0.3715% | 4.498% | 46.1954 | 7.047% | 1.211% | 44.5498
MNDALY_6_MCGRTH | Peaker | summer | 48.56 | 0.7476% | 13.69% | 41.5486 | 4.696% | 3.635% | 44.5147
MRGT_6_MEF2 | Peaker | nonsummer | 44 | 0.719% | 0% | 43.6836 | 7.047% | 1.211% | 40.3664
MRGT_6_MEF2 | Peaker | summer | 44 | 0.9942% | 0% | 43.5626 | 4.696% | 3.635% | 40.3346
MRGT_6_MMAREF | Peaker | nonsummer | 45 | 0.9356% | 0% | 44.579 | 7.047% | 1.211% | 41.2838
MRGT_6_MMAREF | Peaker | summer | 45 | 0.061% | 0% | 44.9725 | 4.696% | 3.635% | 41.2513
OAK C_7_UNIT 1 | Peaker | nonsummer | 55 | 35.14% | 0% | 35.6729 | 7.047% | 1.211% | 50.4579
OAK C_7_UNIT 1 | Peaker | summer | 55 | 41.39% | 0.02004% | 32.2262 | 4.696% | 3.635% | 50.4182
OAK C_7_UNIT 3 | Peaker | nonsummer | 55 | 7.853% | 0% | 50.6806 | 7.047% | 1.211% | 50.4579
OAK C_7_UNIT 3 | Peaker | summer | 55 | 6.791% | 0.2332% | 51.1369 | 4.696% | 3.635% | 50.4182
OGROVE_6_PL1X2 | Peaker | nonsummer | 96 | 3.435% | 0% | 92.7019 | 7.047% | 1.211% | 88.072
OGROVE_6_PL1X2 | Peaker | summer | 96 | 0.3634% | 0% | 95.6511 | 4.696% | 3.635% | 88.0027
OMAR_2_UNIT 1 | Peaker | nonsummer | 75 | 2.972% | 0% | 72.7708 | 7.047% | 1.211% | 68.8063
OMAR_2_UNIT 1 | Peaker | summer | 75 | 2.108% | 0% | 73.4193 | 4.696% | 3.635% | 68.7521
OMAR_2_UNIT 2 | Peaker | nonsummer | 75 | 5.177% | 0% | 71.1173 | 7.047% | 1.211% | 68.8063
OMAR_2_UNIT 2 | Peaker | summer | 75 | 6.802% | 0% | 69.8981 | 4.696% | 3.635% | 68.7521
OMAR_2_UNIT 3 | Peaker | nonsummer | 75 | 4.636% | 0% | 71.5228 | 7.047% | 1.211% | 68.8063
OMAR_2_UNIT 3 | Peaker | summer | 75 | 2.782% | 0% | 72.9134 | 4.696% | 3.635% | 68.7521
OTAY_6_PL1X2 | Peaker | nonsummer | 39.57 | 1.434% | 0% | 39.0026 | 7.047% | 1.211% | 36.3022
OTAY_6_PL1X2 | Peaker | summer | 39.57 | 1.515% | 0.1166% | 38.9242 | 4.696% | 3.635% | 36.2736
PIOPIC_2_CTG1 | Peaker | nonsummer | 111.3 | 2.525% | 2.147% | 106.1 | 7.047% | 1.211% | 102.1085
PIOPIC_2_CTG1 | Peaker | summer | 111.3 | 0.115% | 5.879% | 104.6289 | 4.696% | 3.635% | 102.0281
PIOPIC_2_CTG2 | Peaker | nonsummer | 112.7 | 0.1323% | 1.082% | 111.3313 | 7.047% | 1.211% | 103.3929
PIOPIC_2_CTG2 | Peaker | summer | 112.7 | 0.3598% | 4.846% | 106.833 | 4.696% | 3.635% | 103.3115
PIOPIC_2_CTG3 | Peaker | nonsummer | 112 | 0.127% | 1.317% | 110.3822 | 7.047% | 1.211% | 102.7507
PIOPIC_2_CTG3 | Peaker | summer | 112 | 0.7726% | 5.694% | 104.7574 | 4.696% | 3.635% | 102.6698
PNCHEG_2_PL1X4 | Peaker | nonsummer | 417 | 25.68% | 0.3444% | 308.4729 | 7.047% | 1.211% | 382.563
PNCHEG_2_PL1X4 | Peaker | summer | 417 | 8.76% | 5.686% | 356.7567 | 4.696% | 3.635% | 382.2616
PNCHPP_1_PL1X2 | Peaker | nonsummer | 119.91 | 3.59% | 2.1% | 113.087 | 7.047% | 1.211% | 110.0075
PNCHPP_1_PL1X2 | Peaker | summer | 119.91 | 2.031% | 6.904% | 109.1966 | 4.696% | 3.635% | 109.9208
PNOCHE_1_PL1X2 | Peaker | nonsummer | 49.97 | 4.36% | 0.1527% | 47.7148 | 7.047% | 1.211% | 45.8433
PNOCHE_1_PL1X2 | Peaker | summer | 49.97 | 0.7264% | 4.1% | 47.558 | 4.696% | 3.635% | 45.8072
PNOCHE_1_UNITA1 | Peaker | nonsummer | 52.3 | 9.577% | 0.03122% | 47.2749 | 7.047% | 1.211% | 47.9809
PNOCHE_1_UNITA1 | Peaker | summer | 52.3 | 1.883% | 0.3234% | 51.146 | 4.696% | 3.635% | 47.9431
RVRVEW_1_UNITA1 | Peaker | nonsummer | 48.7 | 5.391% | 0.1653% | 45.9941 | 7.047% | 1.211% | 44.6782
RVRVEW_1_UNITA1 | Peaker | summer | 48.7 | 3.515% | 1.507% | 46.254 | 4.696% | 3.635% | 44.643
RVSIDE_2_RERCU3 | Peaker | nonsummer | 49 | 0.2959% | 0% | 48.855 | 7.047% | 1.211% | 44.9534
RVSIDE_2_RERCU3 | Peaker | summer | 49 | 1.549% | 0% | 48.241 | 4.696% | 3.635% | 44.918
RVSIDE_2_RERCU4 | Peaker | nonsummer | 49 | 0.0601% | 0% | 48.9705 | 7.047% | 1.211% | 44.9534
RVSIDE_2_RERCU4 | Peaker | summer | 49 | 1.531% | 0% | 48.2497 | 4.696% | 3.635% | 44.918
RVSIDE_6_RERCU1 | Peaker | nonsummer | 48.35 | 8.477% | 0% | 44.2513 | 7.047% | 1.211% | 44.3571
RVSIDE_6_RERCU1 | Peaker | summer | 48.35 | 1.639% | 0% | 47.5576 | 4.696% | 3.635% | 44.3222
RVSIDE_6_RERCU2 | Peaker | nonsummer | 48.5 | 2.578% | 0% | 47.2498 | 7.047% | 1.211% | 44.4947
RVSIDE_6_RERCU2 | Peaker | summer | 48.5 | 1.685% | 0% | 47.683 | 4.696% | 3.635% | 44.4597
RVSIDE_6_SPRING | Peaker | nonsummer | 36 | 0.4205% | 0% | 35.8486 | 7.047% | 1.211% | 33.027
RVSIDE_6_SPRING | Peaker | summer | 36 | 1.712% | 0% | 35.3836 | 4.696% | 3.635% | 33.001
SENTNL_2_CTG1 | Peaker | nonsummer | 107.68 | 5.321% | 3.023% | 98.6953 | 7.047% | 1.211% | 98.7875
SENTNL_2_CTG1 | Peaker | summer | 107.68 | 3.867% | 5.833% | 97.2347 | 4.696% | 3.635% | 98.7097
SENTNL_2_CTG2 | Peaker | nonsummer | 104.19 | 3.254% | 3.507% | 97.1464 | 7.047% | 1.211% | 95.5857
SENTNL_2_CTG2 | Peaker | summer | 104.19 | 0.5433% | 8.104% | 95.1802 | 4.696% | 3.635% | 95.5104
SENTNL_2_CTG3 | Peaker | nonsummer | 105.69 | 44.93% | 1.214% | 56.9183 | 7.047% | 1.211% | 96.9618
SENTNL_2_CTG3 | Peaker | summer | 105.69 | 34.32% | 3.944% | 65.2535 | 4.696% | 3.635% | 96.8854
SENTNL_2_CTG4 | Peaker | nonsummer | 106.55 | 6.865% | 3.581% | 95.4193 | 7.047% | 1.211% | 97.7508
SENTNL_2_CTG4 | Peaker | summer | 106.55 | 0.8555% | 7.303% | 97.857 | 4.696% | 3.635% | 97.6738
SENTNL_2_CTG5 | Peaker | nonsummer | 107.52 | 11.3% | 3.111% | 92.027 | 7.047% | 1.211% | 98.6407
SENTNL_2_CTG5 | Peaker | summer | 107.52 | 1.152% | 7.394% | 98.3311 | 4.696% | 3.635% | 98.563
SENTNL_2_CTG6 | Peaker | nonsummer | 105 | 3.964% | 3.247% | 97.4275 | 7.047% | 1.211% | 96.3288
SENTNL_2_CTG6 | Peaker | summer | 105 | 3.767% | 7.635% | 93.0288 | 4.696% | 3.635% | 96.2529
SENTNL_2_CTG7 | Peaker | nonsummer | 106.73 | 6.295% | 3.214% | 96.5803 | 7.047% | 1.211% | 97.9159
SENTNL_2_CTG7 | Peaker | summer | 106.73 | 13.94% | 5.968% | 85.4786 | 4.696% | 3.635% | 97.8388
SENTNL_2_CTG8 | Peaker | nonsummer | 106.85 | 5.031% | 3.562% | 97.6685 | 7.047% | 1.211% | 98.026
SENTNL_2_CTG8 | Peaker | summer | 106.85 | 0.09379% | 7.547% | 98.6855 | 4.696% | 3.635% | 97.9488
SIERRA_1_UNITS | Peaker | nonsummer | 52.43 | 1.461% | 3.66% | 49.7451 | 7.047% | 1.211% | 48.1002
SIERRA_1_UNITS | Peaker | summer | 52.43 | 1.415% | 5.877% | 48.6069 | 4.696% | 3.635% | 48.0623
STANTN_2_STAGT1 | Peaker | nonsummer | 49.65 | 1.608% | 0.004943% | 48.849 | 7.047% | 1.211% | 45.5498
STANTN_2_STAGT1 | Peaker | summer | 49.65 | 0.285% | 0.0603% | 49.4786 | 4.696% | 3.635% | 45.5139
STANTN_2_STAGT2 | Peaker | nonsummer | 49.65 | 0.8947% | 0.01642% | 49.1976 | 7.047% | 1.211% | 45.5498
STANTN_2_STAGT2 | Peaker | summer | 49.65 | 0.4289% | 1.774% | 48.5562 | 4.696% | 3.635% | 45.5139
STIGCT_2_LODI | Peaker | nonsummer | 49.9 | 10.15% | 7.417% | 41.1329 | 7.047% | 1.211% | 45.7791
STIGCT_2_LODI | Peaker | summer | 49.9 | 8.661% | 8.498% | 41.338 | 4.696% | 3.635% | 45.7431
SYCAMR_2_UNIT 2 | Peaker | nonsummer | 76 | 21.79% | 0% | 59.4389 | 7.047% | 1.211% | 69.7237
SYCAMR_2_UNIT 2 | Peaker | summer | 76 | 4.801% | 0% | 72.3515 | 4.696% | 3.635% | 69.6688
SYCAMR_2_UNIT 4 | Peaker | nonsummer | 76 | 13.92% | 0% | 65.4182 | 7.047% | 1.211% | 69.7237
SYCAMR_2_UNIT 4 | Peaker | summer | 76 | 1.409% | 0% | 74.9291 | 4.696% | 3.635% | 69.6688
VACADX_1_UNITA1 | Peaker | nonsummer | 51.91 | 3.081% | 0% | 50.3105 | 7.047% | 1.211% | 47.6231
VACADX_1_UNITA1 | Peaker | summer | 51.91 | 9.629% | 0.2801% | 46.7662 | 4.696% | 3.635% | 47.5856
VERNON_6_GONZL1 | Peaker | nonsummer | 5.75 | 36.14% | 0% | 3.6721 | 7.047% | 1.211% | 5.2751
VERNON_6_GONZL1 | Peaker | summer | 5.75 | 33.88% | 0% | 3.802 | 4.696% | 3.635% | 5.271
VERNON_6_GONZL2 | Peaker | nonsummer | 5.75 | 7.756% | 0% | 5.3041 | 7.047% | 1.211% | 5.2751
VERNON_6_GONZL2 | Peaker | summer | 5.75 | 0.4444% | 0% | 5.7244 | 4.696% | 3.635% | 5.271
VESTAL_2_WELLHD | Peaker | nonsummer | 49 | 5.085% | 0.1312% | 46.444 | 7.047% | 1.211% | 44.9534
VESTAL_2_WELLHD | Peaker | summer | 49 | 8.773% | 0.5636% | 44.4252 | 4.696% | 3.635% | 44.918
WALCRK_2_CTG1 | Peaker | nonsummer | 100.1 | 2.066% | 0% | 98.0324 | 7.047% | 1.211% | 91.8335
WALCRK_2_CTG1 | Peaker | summer | 100.1 | 6.793% | 0.07374% | 93.2265 | 4.696% | 3.635% | 91.7611
WALCRK_2_CTG2 | Peaker | nonsummer | 100.1 | 27.57% | 0% | 72.5046 | 7.047% | 1.211% | 91.8335
WALCRK_2_CTG2 | Peaker | summer | 100.1 | 9.687% | 0.01557% | 90.3876 | 4.696% | 3.635% | 91.7611
WALCRK_2_CTG3 | Peaker | nonsummer | 100.1 | 4.387% | 0% | 95.709 | 7.047% | 1.211% | 91.8335
WALCRK_2_CTG3 | Peaker | summer | 100.1 | 1.155% | 0.06259% | 98.8816 | 4.696% | 3.635% | 91.7611
WALCRK_2_CTG4 | Peaker | nonsummer | 100.1 | 5.784% | 0% | 94.3102 | 7.047% | 1.211% | 91.8335
WALCRK_2_CTG4 | Peaker | summer | 100.1 | 35.39% | 0% | 64.6733 | 4.696% | 3.635% | 91.7611
WALCRK_2_CTG5 | Peaker | nonsummer | 100.1 | 1.604% | 0% | 98.4941 | 7.047% | 1.211% | 91.8335
WALCRK_2_CTG5 | Peaker | summer | 100.1 | 4.211% | 0.06792% | 95.8172 | 4.696% | 3.635% | 91.7611
WOLFSK_1_UNITA1 | Peaker | nonsummer | 48.68 | 4.455% | 0.3135% | 46.3588 | 7.047% | 1.211% | 44.6599
WOLFSK_1_UNITA1 | Peaker | summer | 48.68 | 0.4172% | 1.743% | 47.6284 | 4.696% | 3.635% | 44.6247
YUBACT_6_UNITA1 | Peaker | nonsummer | 47.16 | 1.094% | 0.136% | 46.58 | 7.047% | 1.211% | 43.2654
YUBACT_6_UNITA1 | Peaker | summer | 47.16 | 0.7573% | 2.132% | 45.7973 | 4.696% | 3.635% | 43.2313
BANKPP_2_NSPIN | Pump | nonsummer | 270 | 0.03925% | 0% | 269.894 | 3.335% | 0% | 260.9944
BANKPP_2_NSPIN | Pump | summer | 270 | 0.2498% | 0% | 269.3255 | 3.826% | 0% | 259.6698
DOSMGO_2_NSPIN | Pump | nonsummer | 159 | 0% | 0% | 159 | 3.335% | 0% | 153.6967
DOSMGO_2_NSPIN | Pump | summer | 159 | 0% | 0% | 159 | 3.826% | 0% | 152.9167
EDMONS_2_NSPIN | Pump | nonsummer | 775.8 | 5.97% | 0% | 729.4875 | 3.335% | 0% | 749.9239
EDMONS_2_NSPIN | Pump | summer | 775.8 | 6.749% | 0% | 723.443 | 3.826% | 0% | 746.1179
OSO_6_NSPIN | Pump | nonsummer | 70 | 0% | 0% | 70 | 3.335% | 0% | 67.6652
OSO_6_NSPIN | Pump | summer | 70 | 0% | 0% | 70 | 3.826% | 0% | 67.3218
PEARBL_2_NSPIN | Pump | nonsummer | 118 | 0.0314% | 0% | 117.963 | 3.335% | 0% | 114.0642
PEARBL_2_NSPIN | Pump | summer | 118 | 0.2179% | 0% | 117.7429 | 3.826% | 0% | 113.4853
EASTWD_7_UNIT | Pumped Hydro | nonsummer | 200 | 1.415% | 0% | 197.169 | 5.887% | 0% | 188.2255
EASTWD_7_UNIT | Pumped Hydro | summer | 200 | 27.08% | 0.03609% | 145.7585 | 5.377% | 0.005091% | 189.2352
HELMPG_7_UNIT 1 | Pumped Hydro | nonsummer | 407 | 6.781% | 0% | 379.4007 | 5.887% | 0% | 383.039
HELMPG_7_UNIT 1 | Pumped Hydro | summer | 407 | 1.877% | 0% | 399.3626 | 5.377% | 0.005091% | 385.0937
HELMPG_7_UNIT 2 | Pumped Hydro | nonsummer | 407 | 5.556% | 0% | 384.3869 | 5.887% | 0% | 383.039
HELMPG_7_UNIT 2 | Pumped Hydro | summer | 407 | 1.677% | 0% | 400.1754 | 5.377% | 0.005091% | 385.0937
HELMPG_7_UNIT 3 | Pumped Hydro | nonsummer | 404 | 7.534% | 0% | 373.5625 | 5.887% | 0% | 380.2156
HELMPG_7_UNIT 3 | Pumped Hydro | summer | 404 | 1.886% | 0% | 396.3813 | 5.377% | 0.005091% | 382.2552
CDWR07_2_GEN | Reciprocating Engine | nonsummer | 415.3 | 0.05039% | 0% | 415.0907 | 1.355% | 0.7877% | 406.402
CDWR07_2_GEN | Reciprocating Engine | summer | 415.3 | 0.2179% | 0% | 414.3952 | 3.075% | 0.101% | 402.1102
CHWCHL_1_UNIT | Reciprocating Engine | nonsummer | 48.6 | 1.675% | 0% | 47.7859 | 1.355% | 0.7877% | 47.5587
CHWCHL_1_UNIT | Reciprocating Engine | summer | 48.6 | 1.023% | 1.239% | 47.5004 | 3.075% | 0.101% | 47.0565
HUMBPP_1_UNITS3 | Reciprocating Engine | nonsummer | 65.08 | 2.919% | 1.758% | 62.0362 | 1.355% | 0.7877% | 63.6856
HUMBPP_1_UNITS3 | Reciprocating Engine | summer | 65.08 | 12.06% | 0% | 57.2296 | 3.075% | 0.101% | 63.0131
HUMBPP_6_UNITS | Reciprocating Engine | nonsummer | 97.62 | 5.626% | 4.239% | 87.9903 | 1.355% | 0.7877% | 95.5284
HUMBPP_6_UNITS | Reciprocating Engine | summer | 97.62 | 11.42% | 0.07262% | 86.3977 | 3.075% | 0.101% | 94.5196
REDBLF_6_UNIT | Reciprocating Engine | nonsummer | 44 | 1.525% | 0% | 43.329 | 1.355% | 0.7877% | 43.0573
REDBLF_6_UNIT | Reciprocating Engine | summer | 44 | 0.4934% | 0.008715% | 43.7791 | 3.075% | 0.101% | 42.6026
CABALO_2_M2WSR2 | Solar_1Axis | nonsummer | 100 | 6.234% | 0% | 93.7661 | 6.234% | 0% | 93.7661
CABALO_2_M2WSR2 | Solar_1Axis | summer | 100 | 3.686% | 0% | 96.3137 | 3.686% | 0% | 96.3137
ELNIDO_1_ECRSR1 | Solar_Fixed | nonsummer | 3 | #VALUE! | #VALUE! | #VALUE! |  |  | #VALUE!
ELNIDO_1_ECRSR1 | Solar_Fixed | summer | 3 | #VALUE! | #VALUE! | #VALUE! |  |  | #VALUE!

## Resource Type UCAP
RESOURCE TYPE | SEASON | MWH AT PMAX DURING DEMAND - GROUP ASSESSMENT | OUTAGE MWH EXCLUDING AMBIENT DUE TO TEMPERATURE - GROUP ASSESSMENT | OUTAGE MWH DURING DEMAND AMBIENT DUE TO TEMPERATURE - GROUP ASSESSMENT | EFORD EXCLUDING AMBIENT DUE TO TEMPERATURE - GROUP ASSESSMENT | EFORD AMBIENT DUE TO TEMPERATURE - GROUP ASSESSMENT | PMAX OR NDC MW | UCAP MW - INDIVIDUAL ASSESSMENT | UCAP MW - GROUP ASSESSMENT
Battery Storage | nonsummer | 8000392.45 | 647265.7068 | 0 | 8.09% | 0% | 7123.97 | 6479.2773 | 6547.6106
Battery Storage | summer | 6567844.25 | 586898.7892 | 0 | 8.936% | 0% | 7123.97 | 6503.3581 | 6487.3761
Biogas | nonsummer | 62521.55 | 2209.05 | 147.33 | 3.533% | 0.2356% | 19.63 | 18.8902 | 18.8902
Biogas | summer | 45050.85 | 610.2583 | 282.8833 | 1.355% | 0.6279% | 19.63 | 19.2408 | 19.2408
Biomass/Wood | nonsummer | 95550 | 6244.8933 | 0 | 6.536% | 0% | 30 | 28.0393 | 28.0393
Biomass/Wood | summer | 68850 | 3178 | 0 | 4.616% | 0% | 30 | 28.6153 | 28.6153
CCGT | nonsummer | 52932288.9 | 3859532.9447 | 950155.944 | 7.291% | 1.795% | 16756.58 | 15233.8291 | 15233.9945
CCGT | summer | 38156647.05 | 2002940.6462 | 1777052.0518 | 5.249% | 4.657% | 16756.58 | 15096.3389 | 15096.5874
CHP | nonsummer | 3517577.7 | 490447.9112 | 17706.5 | 13.94% | 0.5034% | 1104.42 | 944.8739 | 944.8739
CHP | summer | 2534643.9 | 288818.4932 | 47578.1585 | 11.39% | 1.877% | 1104.42 | 957.8419 | 957.8419
Geothermal | nonsummer | 3945153.05 | 977592.9677 | 2208.1017 | 24.78% | 0.05597% | 1272.53 | 956.5017 | 956.49
Geothermal | summer | 2858185.35 | 739156.4858 | 13650.9267 | 25.86% | 0.4776% | 1272.53 | 937.2175 | 937.3628
Hybrid_BattStorage | nonsummer | 1199607.5 | 313031.3267 | 1774.8983 | 26.09% | 0.148% | 960.25 | 758.3173 | 708.257
Hybrid_BattStorage | summer | 951616.25 | 158021.5295 | 1174.1 | 16.61% | 0.1234% | 960.25 | 832.4479 | 799.61
Hybrid_Solar_1Axis | nonsummer | 5879510 | 0 | 0 | 0% | 0% | 1846 | 1846 | 1846
Hybrid_Solar_1Axis | summer | 4236570 | 0 | 0 | 0% | 0% | 1846 | 1846 | 1846
Hybrid_Solar_Fixed | nonsummer | 214987.5 | 0 | 0 | 0% | 0% | 67.5 | 67.5 | 67.5
Hybrid_Solar_Fixed | summer | 154912.5 | 0 | 0 | 0% | 0% | 67.5 | 67.5 | 67.5
Hydro | nonsummer | 21100510.55 | 3403601.691 | 29408.7288 | 16.13% | 0.1394% | 6626.23 | 5548.1542 | 5548.1558
Hydro | summer | 15204502.85 | 2323503.8862 | 11166.526 | 15.28% | 0.07344% | 6626.23 | 5608.7603 | 5608.7641
Nuclear | nonsummer | 9347975 | 162177.4833 | 5549.6667 | 1.735% | 0.05937% | 2935 | 2882.3384 | 2882.3384
Nuclear | summer | 6735825 | 38270.3 | 2221.8667 | 0.5682% | 0.03299% | 2935 | 2917.3564 | 2917.3564
Paired_BattStorage | nonsummer | 7978883 | 511329.6363 | 130 | 6.409% | 0.001629% | 5345.6 | 4972.0746 | 5002.9382
Paired_BattStorage | summer | 6233335.5 | 555848.7865 | 16 | 8.917% | 0.0002567% | 5345.6 | 4756.6885 | 4868.9
Paired_Solar_1Axis | nonsummer | 6100 | 0 | 0 | 0% | 0% | 20 | #VALUE! | 20
Paired_Solar_1Axis | summer | 13400 | 334 | 0 | 2.493% | 0% | 20 | #VALUE! | 19.5015
Peaker | nonsummer | 25047061.55 | 1765169.5157 | 303287.8822 | 7.047% | 1.211% | 8067.03 | 7402.2469 | 7400.8318
Peaker | summer | 18030506.85 | 846662.851 | 655376.2465 | 4.696% | 3.635% | 8067.03 | 7395.0026 | 7395.0026
Pump | nonsummer | 4436068 | 147960.72 | 0 | 3.335% | 0% | 1392.8 | 1346.3445 | 1346.3445
Pump | summer | 3196476 | 122297.3333 | 0 | 3.826% | 0% | 1392.8 | 1339.5114 | 1339.5114
Pumped Hydro | nonsummer | 4516330 | 265886.6167 | 0 | 5.887% | 0% | 1418 | 1334.5191 | 1334.5191
Pumped Hydro | summer | 3254310 | 174993.7833 | 165.6667 | 5.377% | 0.005091% | 1418 | 1341.6778 | 1341.6778
Reciprocating Engine | nonsummer | 2135861 | 28937.4765 | 16824.4147 | 1.355% | 0.7877% | 670.6 | 656.2321 | 656.2321
Reciprocating Engine | summer | 1539027 | 47325.1468 | 1553.715 | 3.075% | 0.101% | 670.6 | 649.302 | 649.302
Solar_1Axis | nonsummer | 318500 | 19854.9158 | 0 | 6.234% | 0% | 100 | 93.7661 | 93.7661
Solar_1Axis | summer | 229500 | 8459.9807 | 0 | 3.686% | 0% | 100 | 96.3137 | 96.3137
Solar_Fixed | nonsummer | 0 | 0 | 0 |  |  | 3 | #VALUE! | #VALUE!
Solar_Fixed | summer | 0 | 0 | 0 |  |  | 3 | #VALUE! | #VALUE!

## ResourceTypeYearSeason
RESOURCE TYPE | YEAR | SEASON | MWH AT PMAX DURING DEMAND - FIRST PASS | OUTAGE MWH DURING DEMAND EXCLUDING AMBIENT DUE TO TEMPERATURE - FIRST PASS | OUTAGE MWH DURING DEMAND AMBIENT DUE TO TEMPERATURE - FIRST PASS | EFORD EXCLUDING AMBIENT DUE TO TEMPERATURE - FIRST PASS | EFORD AMBIENT DUE TO TEMPERATURE - FIRST PASS | MWH AT PMAX DURING DEMAND - SECOND PASS | OUTAGE MWH DURING DEMAND EXCLUDING AMBIENT DUE TO TEMPERATURE - SECOND PASS | OUTAGE MWH DURING DEMAND AMBIENT DUE TO TEMPERATURE - SECOND PASS | EFORD EXCLUDING AMBIENT DUE TO TEMPERATURE - SECOND PASS | EFORD AMBIENT DUE TO TEMPERATURE - SECOND PASS
Battery Storage | 2022 | nonsummer | 1503564 | 230499.0358 | 0 | 15.33% | 0% | 1503564 | 230499.0358 | 0 | 15.33% | 0%
Battery Storage | 2022 | summer | 1203066 | 166393.7857 | 0 | 13.83% | 0% | 1203066 | 166393.7857 | 0 | 13.83% | 0%
Battery Storage | 2023 | nonsummer | 2402824 | 161990.8705 | 0 | 6.742% | 0% | 2402824 | 161990.8705 | 0 | 6.742% | 0%
Battery Storage | 2023 | summer | 2062243 | 137287.7342 | 0 | 6.657% | 0% | 2062243 | 137287.7342 | 0 | 6.657% | 0%
Battery Storage | 2024 | nonsummer | 4094004.45 | 254775.8005 | 0 | 6.223% | 0% | 4094004.45 | 254775.8005 | 0 | 6.223% | 0%
Battery Storage | 2024 | summer | 3302535.25 | 283217.2693 | 0 | 8.576% | 0% | 3302535.25 | 283217.2693 | 0 | 8.576% | 0%
Biogas | 2022 | nonsummer | 20807.8 | 928.3417 | 0 | 4.462% | 0% | 20807.8 | 928.3417 | 0 | 4.462% | 0%
Biogas | 2022 | summer | 15016.95 | 195.7167 | 18.6 | 1.303% | 0.1239% | 15016.95 | 195.7167 | 18.6 | 1.303% | 0.1239%
Biogas | 2023 | nonsummer | 20807.8 | 413.0125 | 0 | 1.985% | 0% | 20807.8 | 413.0125 | 0 | 1.985% | 0%
Biogas | 2023 | summer | 15016.95 | 304.9417 | 0 | 2.031% | 0% | 15016.95 | 304.9417 | 0 | 2.031% | 0%
Biogas | 2024 | nonsummer | 20905.95 | 867.6958 | 147.33 | 4.15% | 0.7047% | 20905.95 | 867.6958 | 147.33 | 4.15% | 0.7047%
Biogas | 2024 | summer | 15016.95 | 109.6 | 264.2833 | 0.7298% | 1.76% | 15016.95 | 109.6 | 264.2833 | 0.7298% | 1.76%
Biomass/Wood | 2022 | nonsummer | 31800 | 4156.2267 | 0 | 13.07% | 0% | 31800 | 4156.2267 | 0 | 13.07% | 0%
Biomass/Wood | 2022 | summer | 22950 | 825.5 | 0 | 3.597% | 0% | 22950 | 825.5 | 0 | 3.597% | 0%
Biomass/Wood | 2023 | nonsummer | 31800 | 891.5 | 0 | 2.803% | 0% | 31800 | 891.5 | 0 | 2.803% | 0%
Biomass/Wood | 2023 | summer | 22950 | 1047.5 | 0 | 4.564% | 0% | 22950 | 1047.5 | 0 | 4.564% | 0%
Biomass/Wood | 2024 | nonsummer | 31950 | 1197.1667 | 0 | 3.747% | 0% | 31950 | 1197.1667 | 0 | 3.747% | 0%
Biomass/Wood | 2024 | summer | 22950 | 1305 | 0 | 5.686% | 0% | 22950 | 1305 | 0 | 5.686% | 0%
CCGT | 2022 | nonsummer | 17581170.6 | 1453406.085 | 329448.6145 | 8.267% | 1.874% | 17581170.6 | 1453406.085 | 329448.6145 | 8.267% | 1.874%
CCGT | 2022 | summer | 12688297.65 | 665398.7837 | 748300.9143 | 5.244% | 5.898% | 12688297.65 | 665398.7837 | 748300.9143 | 5.244% | 5.898%
CCGT | 2023 | nonsummer | 17623149.6 | 1151262.6605 | 330072.2912 | 6.533% | 1.873% | 17623149.6 | 1151262.6605 | 330072.2912 | 6.533% | 1.873%
CCGT | 2023 | summer | 12734174.7 | 787379.4987 | 501027.6635 | 6.183% | 3.935% | 12734174.7 | 787379.4987 | 501027.6635 | 6.183% | 3.935%
CCGT | 2024 | nonsummer | 17727968.7 | 1254864.1992 | 290635.0383 | 7.078% | 1.639% | 17727968.7 | 1254864.1992 | 290635.0383 | 7.078% | 1.639%
CCGT | 2024 | summer | 12734174.7 | 550162.3638 | 527723.474 | 4.32% | 4.144% | 12734174.7 | 550162.3638 | 527723.474 | 4.32% | 4.144%
CHP | 2022 | nonsummer | 1170685.2 | 179445.351 | 7730 | 15.33% | 0.6603% | 1170685.2 | 179445.351 | 7730 | 15.33% | 0.6603%
CHP | 2022 | summer | 844881.3 | 118565.3275 | 16087.4985 | 14.03% | 1.904% | 844881.3 | 118565.3275 | 16087.4985 | 14.03% | 1.904%
CHP | 2023 | nonsummer | 1170685.2 | 183982.1202 | 4179 | 15.72% | 0.357% | 1170685.2 | 183982.1202 | 4179 | 15.72% | 0.357%
CHP | 2023 | summer | 844881.3 | 81458.1477 | 14335 | 9.641% | 1.697% | 844881.3 | 81458.1477 | 14335 | 9.641% | 1.697%
CHP | 2024 | nonsummer | 1176207.3 | 127020.44 | 5797.5 | 10.8% | 0.4929% | 1176207.3 | 127020.44 | 5797.5 | 10.8% | 0.4929%
CHP | 2024 | summer | 844881.3 | 88795.018 | 17155.66 | 10.51% | 2.031% | 844881.3 | 88795.018 | 17155.66 | 10.51% | 2.031%
Geothermal | 2022 | nonsummer | 1305739.8 | 292115.588 | 333.4467 | 22.37% | 0.02554% | 1305739.8 | 292115.588 | 333.4467 | 22.37% | 0.02554%
Geothermal | 2022 | summer | 942349.95 | 213561.2917 | 0 | 22.66% | 0% | 942349.95 | 213561.2917 | 0 | 22.66% | 0%
Geothermal | 2023 | nonsummer | 1305739.8 | 353722.2332 | 185.515 | 27.09% | 0.01421% | 1305739.8 | 353722.2332 | 185.515 | 27.09% | 0.01421%
Geothermal | 2023 | summer | 942349.95 | 291465.3165 | 1466.7167 | 30.93% | 0.1556% | 942349.95 | 291465.3165 | 1466.7167 | 30.93% | 0.1556%
Geothermal | 2024 | nonsummer | 1333673.45 | 331755.1465 | 1689.14 | 24.88% | 0.1267% | 1333673.45 | 331755.1465 | 1689.14 | 24.88% | 0.1267%
Geothermal | 2024 | summer | 973485.45 | 234129.8777 | 12184.21 | 24.05% | 1.252% | 973485.45 | 234129.8777 | 12184.21 | 24.05% | 1.252%
Hybrid_BattStorage | 2022 | nonsummer | 199566.25 | 38491.9148 | 1774.8983 | 19.29% | 0.8894% | 199566.25 | 38491.9148 | 1774.8983 | 19.29% | 0.8894%
Hybrid_BattStorage | 2022 | summer | 222886.25 | 31149.0857 | 1174.1 | 13.98% | 0.5268% | 222886.25 | 31149.0857 | 1174.1 | 13.98% | 0.5268%
Hybrid_BattStorage | 2023 | nonsummer | 402270 | 55738.6945 | 0 | 13.86% | 0% | 402270 | 55738.6945 | 0 | 13.86% | 0%
Hybrid_BattStorage | 2023 | summer | 274668.75 | 13761.8615 | 0 | 5.01% | 0% | 274668.75 | 13761.8615 | 0 | 5.01% | 0%
Hybrid_BattStorage | 2024 | nonsummer | 597771.25 | 218800.7173 | 0 | 36.6% | 0% | 597771.25 | 218800.7173 | 0 | 36.6% | 0%
Hybrid_BattStorage | 2024 | summer | 454061.25 | 113110.5823 | 0 | 24.91% | 0% | 454061.25 | 113110.5823 | 0 | 24.91% | 0%
Hybrid_Solar_1Axis | 2022 | nonsummer | 1956760 | 0 | 0 | 0% | 0% | 1956760 | 0 | 0 | 0% | 0%
Hybrid_Solar_1Axis | 2022 | summer | 1412190 | 0 | 0 | 0% | 0% | 1412190 | 0 | 0 | 0% | 0%
Hybrid_Solar_1Axis | 2023 | nonsummer | 1956760 | 0 | 0 | 0% | 0% | 1956760 | 0 | 0 | 0% | 0%
Hybrid_Solar_1Axis | 2023 | summer | 1412190 | 0 | 0 | 0% | 0% | 1412190 | 0 | 0 | 0% | 0%
Hybrid_Solar_1Axis | 2024 | nonsummer | 1965990 | 0 | 0 | 0% | 0% | 1965990 | 0 | 0 | 0% | 0%
Hybrid_Solar_1Axis | 2024 | summer | 1412190 | 0 | 0 | 0% | 0% | 1412190 | 0 | 0 | 0% | 0%
Hybrid_Solar_Fixed | 2022 | nonsummer | 71550 | 0 | 0 | 0% | 0% | 71550 | 0 | 0 | 0% | 0%
Hybrid_Solar_Fixed | 2022 | summer | 51637.5 | 0 | 0 | 0% | 0% | 51637.5 | 0 | 0 | 0% | 0%
Hybrid_Solar_Fixed | 2023 | nonsummer | 71550 | 0 | 0 | 0% | 0% | 71550 | 0 | 0 | 0% | 0%
Hybrid_Solar_Fixed | 2023 | summer | 51637.5 | 0 | 0 | 0% | 0% | 51637.5 | 0 | 0 | 0% | 0%
Hybrid_Solar_Fixed | 2024 | nonsummer | 71887.5 | 0 | 0 | 0% | 0% | 71887.5 | 0 | 0 | 0% | 0%
Hybrid_Solar_Fixed | 2024 | summer | 51637.5 | 0 | 0 | 0% | 0% | 51637.5 | 0 | 0 | 0% | 0%
Hydro | 2022 | nonsummer | 7022319.8 | 1251108.6842 | 28637.54 | 17.82% | 0.4078% | 7022319.8 | 1251108.6842 | 28637.54 | 17.82% | 0.4078%
Hydro | 2022 | summer | 5067994.95 | 868346.5305 | 9861.8785 | 17.13% | 0.1946% | 5067994.95 | 868346.5305 | 9861.8785 | 17.13% | 0.1946%
Hydro | 2023 | nonsummer | 7022319.8 | 1088469.588 | 199.0667 | 15.5% | 0.002835% | 7022319.8 | 1088469.588 | 199.0667 | 15.5% | 0.002835%
Hydro | 2023 | summer | 5067994.95 | 764557.2732 | 91.0767 | 15.09% | 0.001797% | 5067994.95 | 764557.2732 | 91.0767 | 15.09% | 0.001797%
Hydro | 2024 | nonsummer | 7055870.95 | 1064023.4188 | 572.1222 | 15.08% | 0.008108% | 7055870.95 | 1064023.4188 | 572.1222 | 15.08% | 0.008108%
Hydro | 2024 | summer | 5068512.95 | 690600.0825 | 1213.5708 | 13.63% | 0.02394% | 5068512.95 | 690600.0825 | 1213.5708 | 13.63% | 0.02394%
Nuclear | 2022 | nonsummer | 3111100 | 61916.6667 | 0 | 1.99% | 0% | 3111100 | 61916.6667 | 0 | 1.99% | 0%
Nuclear | 2022 | summer | 2245275 | 0 | 0 | 0% | 0% | 2245275 | 0 | 0 | 0% | 0%
Nuclear | 2023 | nonsummer | 3111100 | 65684.3167 | 5549.6667 | 2.111% | 0.1784% | 3111100 | 65684.3167 | 5549.6667 | 2.111% | 0.1784%
Nuclear | 2023 | summer | 2245275 | 27553.1667 | 150 | 1.227% | 0.006681% | 2245275 | 27553.1667 | 150 | 1.227% | 0.006681%
Nuclear | 2024 | nonsummer | 3125775 | 34576.5 | 0 | 1.106% | 0% | 3125775 | 34576.5 | 0 | 1.106% | 0%
Nuclear | 2024 | summer | 2245275 | 10717.1333 | 2071.8667 | 0.4773% | 0.09228% | 2245275 | 10717.1333 | 2071.8667 | 0.4773% | 0.09228%
Paired_BattStorage | 2022 | nonsummer | 1359820 | 95770.3303 | 0 | 7.043% | 0% | 1359820 | 95770.3303 | 0 | 7.043% | 0%
Paired_BattStorage | 2022 | summer | 1144040 | 162149.5087 | 0 | 14.17% | 0% | 1144040 | 162149.5087 | 0 | 14.17% | 0%
Paired_BattStorage | 2023 | nonsummer | 2438054 | 233339.4885 | 0 | 9.571% | 0% | 2438054 | 233339.4885 | 0 | 9.571% | 0%
Paired_BattStorage | 2023 | summer | 1759166.5 | 263050.3775 | 0 | 14.95% | 0% | 1759166.5 | 263050.3775 | 0 | 14.95% | 0%
Paired_BattStorage | 2024 | nonsummer | 4181009 | 182219.8175 | 130 | 4.358% | 0.003109% | 4181009 | 182219.8175 | 130 | 4.358% | 0.003109%
Paired_BattStorage | 2024 | summer | 3330129 | 130648.9003 | 16 | 3.923% | 0.0004805% | 3330129 | 130648.9003 | 16 | 3.923% | 0.0004805%
Paired_Solar_1Axis | 2022 | nonsummer | 0 | 0 | 0 |  |  | 0 | 0 | 0
Paired_Solar_1Axis | 2022 | summer | 0 | 0 | 0 |  |  | 0 | 0 | 0
Paired_Solar_1Axis | 2023 | nonsummer | 0 | 0 | 0 |  |  | 0 | 0 | 0
Paired_Solar_1Axis | 2023 | summer | 0 | 0 | 0 |  |  | 0 | 0 | 0
Paired_Solar_1Axis | 2024 | nonsummer | 6100 | 0 | 0 | 0% | 0% | 6100 | 0 | 0 | 0% | 0%
Paired_Solar_1Axis | 2024 | summer | 13400 | 334 | 0 | 2.493% | 0% | 13400 | 334 | 0 | 2.493% | 0%
Peaker | 2022 | nonsummer | 8327815.8 | 556507.8958 | 94993.3128 | 6.683% | 1.141% | 8327815.8 | 556507.8958 | 94993.3128 | 6.683% | 1.141%
Peaker | 2022 | summer | 6010168.95 | 213062.407 | 230564.8977 | 3.545% | 3.836% | 6010168.95 | 213062.407 | 230564.8977 | 3.545% | 3.836%
Peaker | 2023 | nonsummer | 8327815.8 | 680898.8572 | 90995.3978 | 8.176% | 1.093% | 8327815.8 | 680898.8572 | 90995.3978 | 8.176% | 1.093%
Peaker | 2023 | summer | 6010168.95 | 296609.1175 | 196201.6072 | 4.935% | 3.264% | 6010168.95 | 296609.1175 | 196201.6072 | 4.935% | 3.264%
Peaker | 2024 | nonsummer | 8391429.95 | 527762.7627 | 117299.1715 | 6.289% | 1.398% | 8391429.95 | 527762.7627 | 117299.1715 | 6.289% | 1.398%
Peaker | 2024 | summer | 6010168.95 | 336991.3265 | 228609.7417 | 5.607% | 3.804% | 6010168.95 | 336991.3265 | 228609.7417 | 5.607% | 3.804%
Pump | 2022 | nonsummer | 1476368 | 46216.22 | 0 | 3.13% | 0% | 1476368 | 46216.22 | 0 | 3.13% | 0%
Pump | 2022 | summer | 1065492 | 45900 | 0 | 4.308% | 0% | 1065492 | 45900 | 0 | 4.308% | 0%
Pump | 2023 | nonsummer | 1476368 | 52466.5 | 0 | 3.554% | 0% | 1476368 | 52466.5 | 0 | 3.554% | 0%
Pump | 2023 | summer | 1065492 | 37120.3333 | 0 | 3.484% | 0% | 1065492 | 37120.3333 | 0 | 3.484% | 0%
Pump | 2024 | nonsummer | 1483332 | 49278 | 0 | 3.322% | 0% | 1483332 | 49278 | 0 | 3.322% | 0%
Pump | 2024 | summer | 1065492 | 39277 | 0 | 3.686% | 0% | 1065492 | 39277 | 0 | 3.686% | 0%
Pumped Hydro | 2022 | nonsummer | 1503080 | 213928.45 | 0 | 14.23% | 0% | 1503080 | 213928.45 | 0 | 14.23% | 0%
Pumped Hydro | 2022 | summer | 1084770 | 34904.6167 | 165.6667 | 3.218% | 0.01527% | 1084770 | 34904.6167 | 165.6667 | 3.218% | 0.01527%
Pumped Hydro | 2023 | nonsummer | 1503080 | 14512.2833 | 0 | 0.9655% | 0% | 1503080 | 14512.2833 | 0 | 0.9655% | 0%
Pumped Hydro | 2023 | summer | 1084770 | 88026 | 0 | 8.115% | 0% | 1084770 | 88026 | 0 | 8.115% | 0%
Pumped Hydro | 2024 | nonsummer | 1510170 | 37445.8833 | 0 | 2.48% | 0% | 1510170 | 37445.8833 | 0 | 2.48% | 0%
Pumped Hydro | 2024 | summer | 1084770 | 52063.1667 | 0 | 4.799% | 0% | 1084770 | 52063.1667 | 0 | 4.799% | 0%
Reciprocating Engine | 2022 | nonsummer | 710836 | 10832.5718 | 0 | 1.524% | 0% | 710836 | 10832.5718 | 0 | 1.524% | 0%
Reciprocating Engine | 2022 | summer | 513009 | 36566.8517 | 136.2167 | 7.128% | 0.02655% | 513009 | 36566.8517 | 136.2167 | 7.128% | 0.02655%
Reciprocating Engine | 2023 | nonsummer | 710836 | 9893.929 | 0 | 1.392% | 0% | 710836 | 9893.929 | 0 | 1.392% | 0%
Reciprocating Engine | 2023 | summer | 513009 | 2027.8477 | 751.675 | 0.3953% | 0.1465% | 513009 | 2027.8477 | 751.675 | 0.3953% | 0.1465%
Reciprocating Engine | 2024 | nonsummer | 714189 | 8210.9757 | 16824.4147 | 1.15% | 2.356% | 714189 | 8210.9757 | 16824.4147 | 1.15% | 2.356%
Reciprocating Engine | 2024 | summer | 513009 | 8730.4475 | 665.8233 | 1.702% | 0.1298% | 513009 | 8730.4475 | 665.8233 | 1.702% | 0.1298%
Solar_1Axis | 2022 | nonsummer | 106000 | 9499.4592 | 0 | 8.962% | 0% | 106000 | 9499.4592 | 0 | 8.962% | 0%
Solar_1Axis | 2022 | summer | 76500 | 5601.3573 | 0 | 7.322% | 0% | 76500 | 5601.3573 | 0 | 7.322% | 0%
Solar_1Axis | 2023 | nonsummer | 106000 | 3410.77 | 0 | 3.218% | 0% | 106000 | 3410.77 | 0 | 3.218% | 0%
Solar_1Axis | 2023 | summer | 76500 | 2478.9433 | 0 | 3.24% | 0% | 76500 | 2478.9433 | 0 | 3.24% | 0%
Solar_1Axis | 2024 | nonsummer | 106500 | 6944.6867 | 0 | 6.521% | 0% | 106500 | 6944.6867 | 0 | 6.521% | 0%
Solar_1Axis | 2024 | summer | 76500 | 379.68 | 0 | 0.4963% | 0% | 76500 | 379.68 | 0 | 0.4963% | 0%
Solar_Fixed | 2022 | nonsummer | 0 | 0 | 0 |  |  | 0 | 0 | 0
Solar_Fixed | 2022 | summer | 0 | 0 | 0 |  |  | 0 | 0 | 0
Solar_Fixed | 2023 | nonsummer | 0 | 0 | 0 |  |  | 0 | 0 | 0
Solar_Fixed | 2023 | summer | 0 | 0 | 0 |  |  | 0 | 0 | 0
Solar_Fixed | 2024 | nonsummer | 0 | 0 | 0 |  |  | 0 | 0 | 0
Solar_Fixed | 2024 | summer | 0 | 0 | 0 |  |  | 0 | 0 | 0

## ResourceYear
RESOURCE ID | RESOURCE TYPE | YEAR | INDIVIDUAL DEMAND HOURS | OUTAGE MWH DURING DEMAND EXCLUDING AMBIENT DUE TO TEMPERATURE | OUTAGE MWH DURING DEMAND AMBIENT DUE TO TEMPERATURE | MWH AT PMAX DURING DEMAND | GROUP DEMAND HOURS | EFORD EXCLUDING AMBIENT DUE TO TEMPERATURE - INDIVIDUAL ASSESSMENT | EFORD AMBIENT DUE TO TEMPERATURE - INDIVIDUAL ASSESSMENT | EFORD EXCLUDING AMBIENT DUE TO TEMPERATURE - GROUP ASSESSMENT | EFORD AMBIENT DUE TO TEMPERATURE - GROUP ASSESSMENT | EFORD EXCLUDING AMBIENT DUE TO TEMPERATURE | EFORD AMBIENT DUE TO TEMPERATURE | TOTAL EFORD | RESOURCE YEAR RANK | INCLUDE RESOURCE YEAR IN UCAP
ALAMIT_2_AESBT2 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 2 | TRUE
ALAMIT_2_AESBT2 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
ALAMIT_2_AESBT2 | Battery Storage | 2024 | 240 | 5327.2667 | 0 | 19680 | 1590 | 27.07% | 0% | 7.274% | 0% | 9.87% | 6.32% | 16.19% | 3 | TRUE
ALAMIT_7_ES1 | Battery Storage | 2022 | 1825 | 31602.6525 | 0 | 183321.25 | 0 | 17.24% | 0% |  |  | 17.24% | 0% | 17.24% | 1 | TRUE
ALAMIT_7_ES1 | Battery Storage | 2023 | 1825 | 33537.6467 | 0 | 183321.25 | 0 | 18.29% | 0% |  |  | 18.29% | 0% | 18.29% | 2 | TRUE
ALAMIT_7_ES1 | Battery Storage | 2024 | 1830 | 34418.9642 | 0 | 183823.5 | 0 | 18.72% | 0% |  |  | 18.72% | 0% | 18.72% | 3 | TRUE
BERCYN_2_BCEBT1 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
BERCYN_2_BCEBT1 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
BERCYN_2_BCEBT1 | Battery Storage | 2024 | 805 | 455 | 0 | 10465 | 1025 | 4.348% | 0% | 7.274% | 0% | 5.987% | 4.074% | 10.06% | 2 | TRUE
BGROCK_2_BRFBX2 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
BGROCK_2_BRFBX2 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
BGROCK_2_BRFBX2 | Battery Storage | 2024 | 0 | 0 | 0 | 0 | 1830 |  |  | 7.274% | 0% | 7.274% | 0% | 7.274% | 2 | TRUE
BLKDIA_2_BDEBT1 | Battery Storage | 2022 | 1450 | 53191.4167 | 0 | 290000 | 375 | 18.34% | 0% | 14.66% | 0% | 17.59% | 3.013% | 20.6% | 3 | TRUE
BLKDIA_2_BDEBT1 | Battery Storage | 2023 | 1825 | 6385.25 | 0 | 365000 | 0 | 1.749% | 0% |  |  | 1.749% | 0% | 1.749% | 2 | TRUE
BLKDIA_2_BDEBT1 | Battery Storage | 2024 | 1830 | 5734.0167 | 0 | 366000 | 0 | 1.567% | 0% |  |  | 1.567% | 0% | 1.567% | 1 | TRUE
BLM W_2_MDRBT1 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
BLM W_2_MDRBT1 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
BLM W_2_MDRBT1 | Battery Storage | 2024 | 0 | 0 | 0 | 0 | 1830 |  |  | 7.274% | 0% | 7.274% | 0% | 7.274% | 2 | TRUE
BLVRDE_6_BLVBT1 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 2 | TRUE
BLVRDE_6_BLVBT1 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
BLVRDE_6_BLVBT1 | Battery Storage | 2024 | 1125 | 2141.5542 | 0 | 11250 | 705 | 19.04% | 0% | 7.274% | 0% | 14.5% | 2.802% | 17.31% | 3 | TRUE
CABLRO_2_CBSBT1 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
CABLRO_2_CBSBT1 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
CABLRO_2_CBSBT1 | Battery Storage | 2024 | 0 | 0 | 0 | 0 | 1830 |  |  | 7.274% | 0% | 7.274% | 0% | 7.274% | 2 | TRUE
CALGEN_1_MDRBT1 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
CALGEN_1_MDRBT1 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
CALGEN_1_MDRBT1 | Battery Storage | 2024 | 0 | 0 | 0 | 0 | 1830 |  |  | 7.274% | 0% | 7.274% | 0% | 7.274% | 2 | TRUE
CASCES_6_CESBT1 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
CASCES_6_CESBT1 | Battery Storage | 2023 | 90 | 0 | 0 | 2250 | 1735 | 0% | 0% | 6.703% | 0% | 6.372% | 6.372% | 12.74% | 2 | TRUE
CASCES_6_CESBT1 | Battery Storage | 2024 | 1830 | 1464.5703 | 0 | 45750 | 0 | 3.201% | 0% |  |  | 3.201% | 0% | 3.201% | 1 | TRUE
CASCES_6_CESBT2 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
CASCES_6_CESBT2 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
CASCES_6_CESBT2 | Battery Storage | 2024 | 0 | 120 | 0 | 0 | 1830 |  |  | 7.274% | 0% | 7.274% | 0% | 7.274% | 2 | TRUE
CHINO_2_APEBT1 | Battery Storage | 2022 | 1825 | 1636.9 | 0 | 36500 | 0 | 4.485% | 0% |  |  | 4.485% | 0% | 4.485% | 1 | TRUE
CHINO_2_APEBT1 | Battery Storage | 2023 | 1825 | 2671.7483 | 0 | 36500 | 0 | 7.32% | 0% |  |  | 7.32% | 0% | 7.32% | 2 | TRUE
CHINO_2_APEBT1 | Battery Storage | 2024 | 1830 | 3903.81 | 0 | 36600 | 0 | 10.67% | 0% |  |  | 10.67% | 0% | 10.67% | 3 | TRUE
CHINO_2_PESBT1 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 2 | TRUE
CHINO_2_PESBT1 | Battery Storage | 2023 | 885 | 4137.6467 | 0 | 17700 | 940 | 23.38% | 0% | 6.703% | 0% | 14.79% | 3.452% | 18.24% | 3 | TRUE
CHINO_2_PESBT1 | Battery Storage | 2024 | 1830 | 2463.48 | 0 | 36600 | 0 | 6.731% | 0% |  |  | 6.731% | 0% | 6.731% | 1 | TRUE
CLRMNT_6_CLEBT1 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
CLRMNT_6_CLEBT1 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
CLRMNT_6_CLEBT1 | Battery Storage | 2024 | 1400 | 794.9 | 0 | 12600 | 430 | 6.309% | 0% | 7.274% | 0% | 6.535% | 1.709% | 8.245% | 2 | TRUE
CONDOR_2_CDRBT1 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
CONDOR_2_CDRBT1 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
CONDOR_2_CDRBT1 | Battery Storage | 2024 | 1125 | 7956.6667 | 0 | 225000 | 705 | 3.536% | 0% | 7.274% | 0% | 4.976% | 2.802% | 7.778% | 2 | TRUE
CRIMSN_2_CRMBT1 | Battery Storage | 2022 | 535 | 6648.5173 | 0 | 107000 | 1290 | 6.214% | 0% | 14.66% | 0% | 12.19% | 10.37% | 22.55% | 3 | TRUE
CRIMSN_2_CRMBT1 | Battery Storage | 2023 | 1825 | 36319.2702 | 0 | 365000 | 0 | 9.95% | 0% |  |  | 9.95% | 0% | 9.95% | 2 | TRUE
CRIMSN_2_CRMBT1 | Battery Storage | 2024 | 1830 | 21666.8417 | 0 | 366000 | 0 | 5.92% | 0% |  |  | 5.92% | 0% | 5.92% | 1 | TRUE
CRIMSN_2_CRMBT2 | Battery Storage | 2022 | 325 | 150 | 0 | 48750 | 1500 | 0.3077% | 0% | 14.66% | 0% | 12.11% | 12.05% | 24.16% | 3 | TRUE
CRIMSN_2_CRMBT2 | Battery Storage | 2023 | 1825 | 11675.947 | 0 | 273750 | 0 | 4.265% | 0% |  |  | 4.265% | 0% | 4.265% | 2 | TRUE
CRIMSN_2_CRMBT2 | Battery Storage | 2024 | 1830 | 9435.125 | 0 | 274500 | 0 | 3.437% | 0% |  |  | 3.437% | 0% | 3.437% | 1 | TRUE
DYLAN_2_BMTBT1 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
DYLAN_2_BMTBT1 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
DYLAN_2_BMTBT1 | Battery Storage | 2024 | 635 | 235 | 0 | 63500 | 1195 | 0.3701% | 0% | 7.274% | 0% | 4.878% | 4.75% | 9.628% | 2 | TRUE
ELCAJN_6_EB1BT1 | Battery Storage | 2022 | 1825 | 582.75 | 0 | 13687.5 | 0 | 4.258% | 0% |  |  | 4.258% | 0% | 4.258% | 1 | TRUE
ELCAJN_6_EB1BT1 | Battery Storage | 2023 | 1825 | 1292.125 | 0 | 13687.5 | 0 | 9.44% | 0% |  |  | 9.44% | 0% | 9.44% | 3 | TRUE
ELCAJN_6_EB1BT1 | Battery Storage | 2024 | 1830 | 1062.15 | 0 | 13725 | 0 | 7.739% | 0% |  |  | 7.739% | 0% | 7.739% | 2 | TRUE
ELKHRN_1_EESX3 | Battery Storage | 2022 | 1345 | 92643 | 0 | 245462.5 | 480 | 37.74% | 0% | 14.66% | 0% | 31.67% | 3.857% | 35.53% | 3 | TRUE
ELKHRN_1_EESX3 | Battery Storage | 2023 | 1825 | 35725.4542 | 0 | 333062.5 | 0 | 10.73% | 0% |  |  | 10.73% | 0% | 10.73% | 2 | TRUE
ELKHRN_1_EESX3 | Battery Storage | 2024 | 1830 | 24717.7555 | 0 | 333975 | 0 | 7.401% | 0% |  |  | 7.401% | 0% | 7.401% | 1 | TRUE
ELLIOT_6_ELIBT1 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
ELLIOT_6_ELIBT1 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
ELLIOT_6_ELIBT1 | Battery Storage | 2024 | 1330 | 656.5667 | 0 | 13300 | 500 | 4.937% | 0% | 7.274% | 0% | 5.575% | 1.987% | 7.562% | 2 | TRUE
ESCNDO_6_EB1BT1 | Battery Storage | 2022 | 1825 | 3371.9083 | 0 | 18250 | 0 | 18.48% | 0% |  |  | 18.48% | 0% | 18.48% | 2 | TRUE
ESCNDO_6_EB1BT1 | Battery Storage | 2023 | 1825 | 2933.3333 | 0 | 18250 | 0 | 16.07% | 0% |  |  | 16.07% | 0% | 16.07% | 1 | TRUE
ESCNDO_6_EB1BT1 | Battery Storage | 2024 | 1830 | 7550.5 | 0 | 18300 | 0 | 41.26% | 0% |  |  | 41.26% | 0% | 41.26% | 3 | TRUE
ESCNDO_6_EB2BT2 | Battery Storage | 2022 | 1825 | 4326.925 | 0 | 18250 | 0 | 23.71% | 0% |  |  | 23.71% | 0% | 23.71% | 2 | TRUE
ESCNDO_6_EB2BT2 | Battery Storage | 2023 | 1825 | 3824.4167 | 0 | 18250 | 0 | 20.96% | 0% |  |  | 20.96% | 0% | 20.96% | 1 | TRUE
ESCNDO_6_EB2BT2 | Battery Storage | 2024 | 1830 | 6767.2167 | 0 | 18300 | 0 | 36.98% | 0% |  |  | 36.98% | 0% | 36.98% | 3 | TRUE
ESCNDO_6_EB3BT3 | Battery Storage | 2022 | 1825 | 4575.5333 | 0 | 18250 | 0 | 25.07% | 0% |  |  | 25.07% | 0% | 25.07% | 2 | TRUE
ESCNDO_6_EB3BT3 | Battery Storage | 2023 | 1825 | 3696.25 | 0 | 18250 | 0 | 20.25% | 0% |  |  | 20.25% | 0% | 20.25% | 1 | TRUE
ESCNDO_6_EB3BT3 | Battery Storage | 2024 | 1830 | 7688 | 0 | 18300 | 0 | 42.01% | 0% |  |  | 42.01% | 0% | 42.01% | 3 | TRUE
ESNHWR_2_CS1BT3 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
ESNHWR_2_CS1BT3 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
ESNHWR_2_CS1BT3 | Battery Storage | 2024 | 0 | 0 | 0 | 0 | 1830 |  |  | 7.274% | 0% | 7.274% | 0% | 7.274% | 2 | TRUE
ESNHWR_2_HDSBT2 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
ESNHWR_2_HDSBT2 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
ESNHWR_2_HDSBT2 | Battery Storage | 2024 | 0 | 0 | 0 | 0 | 1830 |  |  | 7.274% | 0% | 7.274% | 0% | 7.274% | 2 | TRUE
ESNHWR_2_WC1BT1 | Battery Storage | 2022 | 1825 | 464.9833 | 0 | 5475 | 0 | 8.493% | 0% |  |  | 8.493% | 0% | 8.493% | 2 | TRUE
ESNHWR_2_WC1BT1 | Battery Storage | 2023 | 1825 | 631.45 | 0 | 5475 | 0 | 11.53% | 0% |  |  | 11.53% | 0% | 11.53% | 3 | TRUE
ESNHWR_2_WC1BT1 | Battery Storage | 2024 | 1830 | 382.15 | 0 | 5490 | 0 | 6.961% | 0% |  |  | 6.961% | 0% | 6.961% | 1 | TRUE
ETIWND_2_SEPBT1 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 2 | TRUE
ETIWND_2_SEPBT1 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
ETIWND_2_SEPBT1 | Battery Storage | 2024 | 495 | 22334.5833 | 0 | 49500 | 1335 | 45.12% | 0% | 7.274% | 0% | 17.51% | 5.306% | 22.82% | 3 | TRUE
ETIWND_6_INEBT1 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 2 | TRUE
ETIWND_6_INEBT1 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
ETIWND_6_INEBT1 | Battery Storage | 2024 | 420 | 7780.1667 | 0 | 29400 | 1410 | 26.46% | 0% | 7.274% | 0% | 11.68% | 5.604% | 17.28% | 3 | TRUE
FALBRK_6_FESBT1 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 2 | TRUE
FALBRK_6_FESBT1 | Battery Storage | 2023 | 1215 | 8854.6333 | 0 | 48600 | 610 | 18.22% | 0% | 6.703% | 0% | 14.37% | 2.24% | 16.61% | 3 | TRUE
FALBRK_6_FESBT1 | Battery Storage | 2024 | 1830 | 3118.8333 | 0 | 73200 | 0 | 4.261% | 0% |  |  | 4.261% | 0% | 4.261% | 1 | TRUE
GATEWY_2_GESBT1 | Battery Storage | 2022 | 0 | 11102.4083 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
GATEWY_2_GESBT1 | Battery Storage | 2023 | 0 | 7708 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
GATEWY_2_GESBT1 | Battery Storage | 2024 | 0 | 226171.055 | 0 | 0 | 1830 |  |  | 7.274% | 0% | 7.274% | 0% | 7.274% | 2 | TRUE
GOLETA_2_GE2BT3 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
GOLETA_2_GE2BT3 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 2 | TRUE
GOLETA_2_GE2BT3 | Battery Storage | 2024 | 1805 | 1277 | 0 | 108300 | 25 | 1.179% | 0% | 7.274% | 0% | 1.262% | 0.09937% | 1.362% | 1 | TRUE
GOLETA_2_VALBT1 | Battery Storage | 2022 | 1825 | 123.9667 | 0 | 18250 | 0 | 0.6793% | 0% |  |  | 0.6793% | 0% | 0.6793% | 1 | TRUE
GOLETA_2_VALBT1 | Battery Storage | 2023 | 1825 | 1085.8333 | 0 | 18250 | 0 | 5.95% | 0% |  |  | 5.95% | 0% | 5.95% | 3 | TRUE
GOLETA_2_VALBT1 | Battery Storage | 2024 | 1830 | 183.28 | 0 | 18300 | 0 | 1.002% | 0% |  |  | 1.002% | 0% | 1.002% | 2 | TRUE
HENRTA_6_HDEBT1 | Battery Storage | 2022 | 1825 | 130.7333 | 0 | 18250 | 0 | 0.7163% | 0% |  |  | 0.7163% | 0% | 0.7163% | 2 | TRUE
HENRTA_6_HDEBT1 | Battery Storage | 2023 | 1825 | 50.4333 | 0 | 18250 | 0 | 0.2763% | 0% |  |  | 0.2763% | 0% | 0.2763% | 1 | TRUE
HENRTA_6_HDEBT1 | Battery Storage | 2024 | 1830 | 7960.9667 | 0 | 18300 | 0 | 43.5% | 0% |  |  | 43.5% | 0% | 43.5% | 3 | TRUE
JOANEC_2_ST3BT3 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
JOANEC_2_ST3BT3 | Battery Storage | 2023 | 1065 | 41.0333 | 0 | 42600 | 760 | 0.09632% | 0% | 6.703% | 0% | 2.847% | 2.791% | 5.639% | 2 | TRUE
JOANEC_2_ST3BT3 | Battery Storage | 2024 | 1830 | 136 | 0 | 73200 | 0 | 0.1858% | 0% |  |  | 0.1858% | 0% | 0.1858% | 1 | TRUE
JOANEC_2_STABT1 | Battery Storage | 2022 | 1825 | 760.8 | 0 | 36500 | 0 | 2.084% | 0% |  |  | 2.084% | 0% | 2.084% | 2 | TRUE
JOANEC_2_STABT1 | Battery Storage | 2023 | 1825 | 230 | 0 | 36500 | 0 | 0.6301% | 0% |  |  | 0.6301% | 0% | 0.6301% | 1 | TRUE
JOANEC_2_STABT1 | Battery Storage | 2024 | 1830 | 1417.8333 | 0 | 36600 | 0 | 3.874% | 0% |  |  | 3.874% | 0% | 3.874% | 3 | TRUE
JOANEC_2_STABT2 | Battery Storage | 2022 | 1045 | 122.5 | 0 | 20900 | 780 | 0.5861% | 0% | 14.66% | 0% | 6.603% | 6.267% | 12.87% | 3 | TRUE
JOANEC_2_STABT2 | Battery Storage | 2023 | 1825 | 84.5 | 0 | 36500 | 0 | 0.2315% | 0% |  |  | 0.2315% | 0% | 0.2315% | 2 | TRUE
JOANEC_2_STABT2 | Battery Storage | 2024 | 1830 | 45.9333 | 0 | 36600 | 0 | 0.1255% | 0% |  |  | 0.1255% | 0% | 0.1255% | 1 | TRUE
JOHANN_2_JOSBT1 | Battery Storage | 2022 | 1825 | 1111.4133 | 0 | 18250 | 0 | 6.09% | 0% |  |  | 6.09% | 0% | 6.09% | 2 | TRUE
JOHANN_2_JOSBT1 | Battery Storage | 2023 | 1825 | 990.65 | 0 | 18250 | 0 | 5.428% | 0% |  |  | 5.428% | 0% | 5.428% | 1 | TRUE
JOHANN_2_JOSBT1 | Battery Storage | 2024 | 1830 | 3838.2667 | 0 | 18300 | 0 | 20.97% | 0% |  |  | 20.97% | 0% | 20.97% | 3 | TRUE
JOHANN_2_JOSBT2 | Battery Storage | 2022 | 1825 | 1017.2333 | 0 | 18250 | 0 | 5.574% | 0% |  |  | 5.574% | 0% | 5.574% | 2 | TRUE
JOHANN_2_JOSBT2 | Battery Storage | 2023 | 1825 | 576.6167 | 0 | 18250 | 0 | 3.16% | 0% |  |  | 3.16% | 0% | 3.16% | 1 | TRUE
JOHANN_2_JOSBT2 | Battery Storage | 2024 | 1830 | 1192.4167 | 0 | 18300 | 0 | 6.516% | 0% |  |  | 6.516% | 0% | 6.516% | 3 | TRUE
JOHANN_2_OCEBT2 | Battery Storage | 2022 | 1825 | 94.2 | 0 | 16425 | 0 | 0.5735% | 0% |  |  | 0.5735% | 0% | 0.5735% | 1 | TRUE
JOHANN_2_OCEBT2 | Battery Storage | 2023 | 1825 | 422.1833 | 0 | 16425 | 0 | 2.57% | 0% |  |  | 2.57% | 0% | 2.57% | 2 | TRUE
JOHANN_2_OCEBT2 | Battery Storage | 2024 | 1830 | 8279.4333 | 0 | 16470 | 0 | 50.27% | 0% |  |  | 50.27% | 0% | 50.27% | 3 | TRUE
JOHANN_2_OCEBT3 | Battery Storage | 2022 | 1825 | 80.65 | 0 | 10950 | 0 | 0.7365% | 0% |  |  | 0.7365% | 0% | 0.7365% | 1 | TRUE
JOHANN_2_OCEBT3 | Battery Storage | 2023 | 1825 | 245.1333 | 0 | 10950 | 0 | 2.239% | 0% |  |  | 2.239% | 0% | 2.239% | 2 | TRUE
JOHANN_2_OCEBT3 | Battery Storage | 2024 | 1830 | 5134.85 | 0 | 10980 | 0 | 46.77% | 0% |  |  | 46.77% | 0% | 46.77% | 3 | TRUE
KEARNY_6_NESBT1 | Battery Storage | 2022 | 1485 | 826.3167 | 0 | 14850 | 340 | 5.564% | 0% | 14.66% | 0% | 7.26% | 2.732% | 9.992% | 3 | TRUE
KEARNY_6_NESBT1 | Battery Storage | 2023 | 1825 | 892.9 | 0 | 18250 | 0 | 4.893% | 0% |  |  | 4.893% | 0% | 4.893% | 2 | TRUE
KEARNY_6_NESBT1 | Battery Storage | 2024 | 1830 | 191.3333 | 0 | 18300 | 0 | 1.046% | 0% |  |  | 1.046% | 0% | 1.046% | 1 | TRUE
KEARNY_6_SESBT2 | Battery Storage | 2022 | 1485 | 927.75 | 0 | 14850 | 340 | 6.247% | 0% | 14.66% | 0% | 7.815% | 2.732% | 10.55% | 2 | TRUE
KEARNY_6_SESBT2 | Battery Storage | 2023 | 1825 | 67.5 | 0 | 18250 | 0 | 0.3699% | 0% |  |  | 0.3699% | 0% | 0.3699% | 1 | TRUE
KEARNY_6_SESBT2 | Battery Storage | 2024 | 1830 | 2940.5667 | 0 | 18300 | 0 | 16.07% | 0% |  |  | 16.07% | 0% | 16.07% | 3 | TRUE
KOLA_2_KLBBT1 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
KOLA_2_KLBBT1 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
KOLA_2_KLBBT1 | Battery Storage | 2024 | 0 | 0 | 0 | 0 | 1830 |  |  | 7.274% | 0% | 7.274% | 0% | 7.274% | 2 | TRUE
KOLA_2_KLBBT2 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
KOLA_2_KLBBT2 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
KOLA_2_KLBBT2 | Battery Storage | 2024 | 0 | 0 | 0 | 0 | 1830 |  |  | 7.274% | 0% | 7.274% | 0% | 7.274% | 2 | TRUE
KYCORA_6_KMSBT1 | Battery Storage | 2022 | 1825 | 873.3833 | 0 | 1825 | 0 | 47.86% | 0% |  |  | 47.86% | 0% | 47.86% | 3 | TRUE
KYCORA_6_KMSBT1 | Battery Storage | 2023 | 1825 | 196.6667 | 0 | 1825 | 0 | 10.78% | 0% |  |  | 10.78% | 0% | 10.78% | 2 | TRUE
KYCORA_6_KMSBT1 | Battery Storage | 2024 | 1830 | 92.9833 | 0 | 1830 | 0 | 5.081% | 0% |  |  | 5.081% | 0% | 5.081% | 1 | TRUE
LAGBEL_2_CBPBT1 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
LAGBEL_2_CBPBT1 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
LAGBEL_2_CBPBT1 | Battery Storage | 2024 | 915 | 2844.9667 | 0 | 91500 | 915 | 3.109% | 0% | 7.274% | 0% | 5.191% | 3.637% | 8.828% | 2 | TRUE
LCKHT1_2_LH1BT1 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
LCKHT1_2_LH1BT1 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
LCKHT1_2_LH1BT1 | Battery Storage | 2024 | 885 | 256 | 0 | 39825 | 945 | 0.6428% | 0% | 7.274% | 0% | 4.067% | 3.756% | 7.823% | 2 | TRUE
LECONT_2_LESBT1 | Battery Storage | 2022 | 610 | 10595.15 | 0 | 76250 | 1215 | 13.9% | 0% | 14.66% | 0% | 14.41% | 9.762% | 24.17% | 3 | TRUE
LECONT_2_LESBT1 | Battery Storage | 2023 | 1825 | 6376.25 | 0 | 228125 | 0 | 2.795% | 0% |  |  | 2.795% | 0% | 2.795% | 2 | TRUE
LECONT_2_LESBT1 | Battery Storage | 2024 | 1830 | 2797.5667 | 0 | 228750 | 0 | 1.223% | 0% |  |  | 1.223% | 0% | 1.223% | 1 | TRUE
MARVEL_2_MARBT3 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
MARVEL_2_MARBT3 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 2 | TRUE
MARVEL_2_MARBT3 | Battery Storage | 2024 | 1255 | 2710.6358 | 0 | 94049.7 | 575 | 2.882% | 0% | 7.274% | 0% | 4.262% | 2.285% | 6.547% | 1 | TRUE
MARVEL_2_MARBX2 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
MARVEL_2_MARBX2 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 2 | TRUE
MARVEL_2_MARBX2 | Battery Storage | 2024 | 1255 | 8576.4985 | 0 | 407875 | 575 | 2.103% | 0% | 7.274% | 0% | 3.727% | 2.285% | 6.013% | 1 | TRUE
MELRSE_6_MELBT1 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
MELRSE_6_MELBT1 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
MELRSE_6_MELBT1 | Battery Storage | 2024 | 1460 | 1570 | 0 | 14600 | 370 | 10.75% | 0% | 7.274% | 0% | 10.05% | 1.471% | 11.52% | 2 | TRUE
MELRSE_6_MELBT2 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
MELRSE_6_MELBT2 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
MELRSE_6_MELBT2 | Battery Storage | 2024 | 1460 | 1840 | 0 | 14600 | 370 | 12.6% | 0% | 7.274% | 0% | 11.53% | 1.471% | 13% | 2 | TRUE
MIRLOM_2_MLBBTA | Battery Storage | 2022 | 1825 | 175.8333 | 0 | 18250 | 0 | 0.9635% | 0% |  |  | 0.9635% | 0% | 0.9635% | 3 | TRUE
MIRLOM_2_MLBBTA | Battery Storage | 2023 | 1825 | 97.1667 | 0 | 18250 | 0 | 0.5324% | 0% |  |  | 0.5324% | 0% | 0.5324% | 2 | TRUE
MIRLOM_2_MLBBTA | Battery Storage | 2024 | 1830 | 20 | 0 | 18300 | 0 | 0.1093% | 0% |  |  | 0.1093% | 0% | 0.1093% | 1 | TRUE
MIRLOM_2_MLBBTB | Battery Storage | 2022 | 1825 | 755.9267 | 0 | 18250 | 0 | 4.142% | 0% |  |  | 4.142% | 0% | 4.142% | 3 | TRUE
MIRLOM_2_MLBBTB | Battery Storage | 2023 | 1825 | 708.1333 | 0 | 18250 | 0 | 3.88% | 0% |  |  | 3.88% | 0% | 3.88% | 2 | TRUE
MIRLOM_2_MLBBTB | Battery Storage | 2024 | 1830 | 99.6667 | 0 | 18300 | 0 | 0.5446% | 0% |  |  | 0.5446% | 0% | 0.5446% | 1 | TRUE
MOORPK_2_ACOBT1 | Battery Storage | 2022 | 1825 | 300.6117 | 0 | 3558.75 | 0 | 8.447% | 0% |  |  | 8.447% | 0% | 8.447% | 3 | TRUE
MOORPK_2_ACOBT1 | Battery Storage | 2023 | 1825 | 110.3917 | 0 | 3558.75 | 0 | 3.102% | 0% |  |  | 3.102% | 0% | 3.102% | 1 | TRUE
MOORPK_2_ACOBT1 | Battery Storage | 2024 | 1830 | 168.9192 | 0 | 3568.5 | 0 | 4.734% | 0% |  |  | 4.734% | 0% | 4.734% | 2 | TRUE
MRGT_6_TGEBT1 | Battery Storage | 2022 | 1825 | 16146.2083 | 0 | 54750 | 0 | 29.49% | 0% |  |  | 29.49% | 0% | 29.49% | 3 | TRUE
MRGT_6_TGEBT1 | Battery Storage | 2023 | 1825 | 7056.5483 | 0 | 54750 | 0 | 12.89% | 0% |  |  | 12.89% | 0% | 12.89% | 2 | TRUE
MRGT_6_TGEBT1 | Battery Storage | 2024 | 1830 | 2446.0667 | 0 | 54900 | 0 | 4.455% | 0% |  |  | 4.455% | 0% | 4.455% | 1 | TRUE
MSOLAR_2_MS4BT1 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 2 | TRUE
MSOLAR_2_MS4BT1 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
MSOLAR_2_MS4BT1 | Battery Storage | 2024 | 1705 | 3689.7 | 0 | 17050 | 125 | 21.64% | 0% | 7.274% | 0% | 20.66% | 0.4968% | 21.16% | 3 | TRUE
NOAKS_2_PESBT1 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
NOAKS_2_PESBT1 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
NOAKS_2_PESBT1 | Battery Storage | 2024 | 240 | 20 | 0 | 19200 | 1590 | 0.1042% | 0% | 7.274% | 0% | 6.333% | 6.32% | 12.65% | 2 | TRUE
NORCNV_1_NCVBT1 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
NORCNV_1_NCVBT1 | Battery Storage | 2023 | 620 | 2400.5 | 0 | 81840 | 1205 | 2.933% | 0% | 6.703% | 0% | 5.422% | 4.426% | 9.848% | 2 | TRUE
NORCNV_1_NCVBT1 | Battery Storage | 2024 | 1830 | 7528.3165 | 0 | 241560 | 0 | 3.117% | 0% |  |  | 3.117% | 0% | 3.117% | 1 | TRUE
PALA_6_PGCBT1 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 2 | TRUE
PALA_6_PGCBT1 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
PALA_6_PGCBT1 | Battery Storage | 2024 | 1465 | 2264.1 | 0 | 14650 | 365 | 15.45% | 0% | 7.274% | 0% | 13.82% | 1.451% | 15.27% | 3 | TRUE
PARDSE_6_PESBT1 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
PARDSE_6_PESBT1 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
PARDSE_6_PESBT1 | Battery Storage | 2024 | 1125 | 597.2083 | 0 | 11250 | 705 | 5.309% | 0% | 7.274% | 0% | 6.066% | 2.802% | 8.868% | 2 | TRUE
PEASE_1_TBEBT1 | Battery Storage | 2022 | 1070 | 565.7 | 0 | 5350 | 755 | 10.57% | 0% | 14.66% | 0% | 12.27% | 6.066% | 18.33% | 3 | TRUE
PEASE_1_TBEBT1 | Battery Storage | 2023 | 1825 | 1582.7 | 0 | 9125 | 0 | 17.34% | 0% |  |  | 17.34% | 0% | 17.34% | 2 | TRUE
PEASE_1_TBEBT1 | Battery Storage | 2024 | 1830 | 432.6 | 0 | 9150 | 0 | 4.728% | 0% |  |  | 4.728% | 0% | 4.728% | 1 | TRUE
PERGRN_2_PRSBT1 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
PERGRN_2_PRSBT1 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
PERGRN_2_PRSBT1 | Battery Storage | 2024 | 0 | 0 | 0 | 0 | 1830 |  |  | 7.274% | 0% | 7.274% | 0% | 7.274% | 2 | TRUE
RATSKE_2_WAVBT1 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
RATSKE_2_WAVBT1 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
RATSKE_2_WAVBT1 | Battery Storage | 2024 | 0 | 0 | 0 | 0 | 1830 |  |  | 7.274% | 0% | 7.274% | 0% | 7.274% | 2 | TRUE
ROMOLA_5_MPBBT1 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
ROMOLA_5_MPBBT1 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
ROMOLA_5_MPBBT1 | Battery Storage | 2024 | 515 | 202.1667 | 0 | 118450 | 1315 | 0.1707% | 0% | 7.274% | 0% | 5.275% | 5.227% | 10.5% | 2 | TRUE
ROMOLA_5_MPBBT2 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
ROMOLA_5_MPBBT2 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
ROMOLA_5_MPBBT2 | Battery Storage | 2024 | 515 | 301.2 | 0 | 118450 | 1315 | 0.2543% | 0% | 7.274% | 0% | 5.298% | 5.227% | 10.52% | 2 | TRUE
ROMOLA_5_MPBBT3 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
ROMOLA_5_MPBBT3 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
ROMOLA_5_MPBBT3 | Battery Storage | 2024 | 515 | 324.4167 | 0 | 25750 | 1315 | 1.26% | 0% | 7.274% | 0% | 5.581% | 5.227% | 10.81% | 2 | TRUE
ROMOLA_5_MPBBT4 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
ROMOLA_5_MPBBT4 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
ROMOLA_5_MPBBT4 | Battery Storage | 2024 | 515 | 1765.4833 | 0 | 56650 | 1315 | 3.116% | 0% | 7.274% | 0% | 6.104% | 5.227% | 11.33% | 2 | TRUE
SANBRN_2_ESABT1 | Battery Storage | 2022 | 1825 | 1325.8333 | 0 | 182500 | 0 | 0.7265% | 0% |  |  | 0.7265% | 0% | 0.7265% | 3 | TRUE
SANBRN_2_ESABT1 | Battery Storage | 2023 | 1825 | 1175 | 0 | 182500 | 0 | 0.6438% | 0% |  |  | 0.6438% | 0% | 0.6438% | 2 | TRUE
SANBRN_2_ESABT1 | Battery Storage | 2024 | 1830 | 26.6667 | 0 | 183000 | 0 | 0.01457% | 0% |  |  | 0.01457% | 0% | 0.01457% | 1 | TRUE
SANBRN_2_ESBBT1 | Battery Storage | 2022 | 1825 | 361.3 | 0 | 182500 | 0 | 0.198% | 0% |  |  | 0.198% | 0% | 0.198% | 1 | TRUE
SANBRN_2_ESBBT1 | Battery Storage | 2023 | 1825 | 600 | 0 | 182500 | 0 | 0.3288% | 0% |  |  | 0.3288% | 0% | 0.3288% | 2 | TRUE
SANBRN_2_ESBBT1 | Battery Storage | 2024 | 1830 | 1883.8333 | 0 | 183000 | 0 | 1.029% | 0% |  |  | 1.029% | 0% | 1.029% | 3 | TRUE
SANBRN_2_SS2BT3 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
SANBRN_2_SS2BT3 | Battery Storage | 2023 | 410 | 2745.4833 | 0 | 69290 | 1415 | 3.962% | 0% | 6.703% | 0% | 6.087% | 5.197% | 11.28% | 2 | TRUE
SANBRN_2_SS2BT3 | Battery Storage | 2024 | 1830 | 8643.1667 | 0 | 309270 | 0 | 2.795% | 0% |  |  | 2.795% | 0% | 2.795% | 1 | TRUE
SANBRN_2_SS2BT4 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
SANBRN_2_SS2BT4 | Battery Storage | 2023 | 230 | 0 | 0 | 10810 | 1595 | 0% | 0% | 6.703% | 0% | 5.858% | 5.858% | 11.72% | 2 | TRUE
SANBRN_2_SS2BT4 | Battery Storage | 2024 | 1830 | 90.0833 | 0 | 86010 | 0 | 0.1047% | 0% |  |  | 0.1047% | 0% | 0.1047% | 1 | TRUE
SAUGUS_2_SPESBT1 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 2 | TRUE
SAUGUS_2_SPESBT1 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
SAUGUS_2_SPESBT1 | Battery Storage | 2024 | 1455 | 7982.12 | 0 | 43650 | 375 | 18.29% | 0% | 7.274% | 0% | 16.03% | 1.49% | 17.52% | 3 | TRUE
SNCLRA_2_SILBT1 | Battery Storage | 2022 | 1825 | 5.9333 | 0 | 20075 | 0 | 0.02956% | 0% |  |  | 0.02956% | 0% | 0.02956% | 1 | TRUE
SNCLRA_2_SILBT1 | Battery Storage | 2023 | 1825 | 87.9833 | 0 | 20075 | 0 | 0.4383% | 0% |  |  | 0.4383% | 0% | 0.4383% | 2 | TRUE
SNCLRA_2_SILBT1 | Battery Storage | 2024 | 1830 | 917.4533 | 0 | 20130 | 0 | 4.558% | 0% |  |  | 4.558% | 0% | 4.558% | 3 | TRUE
SNCLRA_2_VESBT1 | Battery Storage | 2022 | 1825 | 4030 | 0 | 182500 | 0 | 2.208% | 0% |  |  | 2.208% | 0% | 2.208% | 2 | TRUE
SNCLRA_2_VESBT1 | Battery Storage | 2023 | 1825 | 8250 | 0 | 182500 | 0 | 4.521% | 0% |  |  | 4.521% | 0% | 4.521% | 3 | TRUE
SNCLRA_2_VESBT1 | Battery Storage | 2024 | 1830 | 2800 | 0 | 183000 | 0 | 1.53% | 0% |  |  | 1.53% | 0% | 1.53% | 1 | TRUE
STANTN_2_SBEBX2 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
STANTN_2_SBEBX2 | Battery Storage | 2023 | 830 | 4021.9683 | 0 | 57104 | 995 | 7.043% | 0% | 6.703% | 0% | 6.858% | 3.654% | 10.51% | 2 | TRUE
STANTN_2_SBEBX2 | Battery Storage | 2024 | 1830 | 759.1908 | 0 | 125904 | 0 | 0.603% | 0% |  |  | 0.603% | 0% | 0.603% | 1 | TRUE
TAHOE_2_THOBT1 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
TAHOE_2_THOBT1 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
TAHOE_2_THOBT1 | Battery Storage | 2024 | 0 | 0 | 0 | 0 | 1830 |  |  | 7.274% | 0% | 7.274% | 0% | 7.274% | 2 | TRUE
TAHOE_2_THOBT2 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
TAHOE_2_THOBT2 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
TAHOE_2_THOBT2 | Battery Storage | 2024 | 0 | 0 | 0 | 0 | 1830 |  |  | 7.274% | 0% | 7.274% | 0% | 7.274% | 2 | TRUE
TAHOE_2_THOBT3 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
TAHOE_2_THOBT3 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
TAHOE_2_THOBT3 | Battery Storage | 2024 | 0 | 64.1667 | 0 | 0 | 1830 |  |  | 7.274% | 0% | 7.274% | 0% | 7.274% | 2 | TRUE
TUMBWD_2_WISBT3 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
TUMBWD_2_WISBT3 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
TUMBWD_2_WISBT3 | Battery Storage | 2024 | 845 | 1626.65 | 0 | 42250 | 985 | 3.85% | 0% | 7.274% | 0% | 5.693% | 3.915% | 9.608% | 2 | TRUE
TUMBWD_2_WISBT4 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
TUMBWD_2_WISBT4 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
TUMBWD_2_WISBT4 | Battery Storage | 2024 | 700 | 151.0617 | 0 | 52479 | 1130 | 0.2879% | 0% | 7.274% | 0% | 4.601% | 4.491% | 9.093% | 2 | TRUE
VALLEY_5_ORTBT1 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
VALLEY_5_ORTBT1 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
VALLEY_5_ORTBT1 | Battery Storage | 2024 | 0 | 0 | 0 | 0 | 1830 |  |  | 7.274% | 0% | 7.274% | 0% | 7.274% | 2 | TRUE
VESTAL_2_BTNBT1 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 2 | TRUE
VESTAL_2_BTNBT1 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
VESTAL_2_BTNBT1 | Battery Storage | 2024 | 370 | 7451.4333 | 0 | 29600 | 1460 | 25.17% | 0% | 7.274% | 0% | 10.89% | 5.803% | 16.7% | 3 | TRUE
VISTRA_5_DALBT1 | Battery Storage | 2022 | 1825 | 61346.3167 | 0 | 182500 | 0 | 33.61% | 0% |  |  | 33.61% | 0% | 33.61% | 3 | TRUE
VISTRA_5_DALBT1 | Battery Storage | 2023 | 1825 | 21315.95 | 0 | 182500 | 0 | 11.68% | 0% |  |  | 11.68% | 0% | 11.68% | 2 | TRUE
VISTRA_5_DALBT1 | Battery Storage | 2024 | 1830 | 3219.65 | 0 | 183000 | 0 | 1.759% | 0% |  |  | 1.759% | 0% | 1.759% | 1 | TRUE
VISTRA_5_DALBT2 | Battery Storage | 2022 | 1825 | 7864.6667 | 0 | 182500 | 0 | 4.309% | 0% |  |  | 4.309% | 0% | 4.309% | 2 | TRUE
VISTRA_5_DALBT2 | Battery Storage | 2023 | 1825 | 21795.3333 | 0 | 182500 | 0 | 11.94% | 0% |  |  | 11.94% | 0% | 11.94% | 3 | TRUE
VISTRA_5_DALBT2 | Battery Storage | 2024 | 1830 | 2051.95 | 0 | 183000 | 0 | 1.121% | 0% |  |  | 1.121% | 0% | 1.121% | 1 | TRUE
VISTRA_5_DALBT3 | Battery Storage | 2022 | 1825 | 13109.2 | 0 | 182500 | 0 | 7.183% | 0% |  |  | 7.183% | 0% | 7.183% | 2 | TRUE
VISTRA_5_DALBT3 | Battery Storage | 2023 | 1825 | 21728.2833 | 0 | 182500 | 0 | 11.91% | 0% |  |  | 11.91% | 0% | 11.91% | 3 | TRUE
VISTRA_5_DALBT3 | Battery Storage | 2024 | 1830 | 1810.4833 | 0 | 183000 | 0 | 0.9893% | 0% |  |  | 0.9893% | 0% | 0.9893% | 1 | TRUE
VISTRA_5_DALBT4 | Battery Storage | 2022 | 1825 | 62783 | 0 | 182500 | 0 | 34.4% | 0% |  |  | 34.4% | 0% | 34.4% | 3 | TRUE
VISTRA_5_DALBT4 | Battery Storage | 2023 | 1825 | 3460.0667 | 0 | 182500 | 0 | 1.896% | 0% |  |  | 1.896% | 0% | 1.896% | 2 | TRUE
VISTRA_5_DALBT4 | Battery Storage | 2024 | 1830 | 506.5667 | 0 | 183000 | 0 | 0.2768% | 0% |  |  | 0.2768% | 0% | 0.2768% | 1 | TRUE
VISTRA_5_PLABT1 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
VISTRA_5_PLABT1 | Battery Storage | 2023 | 1165 | 11246.2833 | 0 | 116966 | 660 | 9.615% | 0% | 6.703% | 0% | 8.562% | 2.424% | 10.99% | 2 | TRUE
VISTRA_5_PLABT1 | Battery Storage | 2024 | 1830 | 6034.47 | 0 | 183732 | 0 | 3.284% | 0% |  |  | 3.284% | 0% | 3.284% | 1 | TRUE
VISTRA_5_PLABT2 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
VISTRA_5_PLABT2 | Battery Storage | 2023 | 1070 | 906.7667 | 0 | 107428 | 755 | 0.8441% | 0% | 6.703% | 0% | 3.268% | 2.773% | 6.041% | 2 | TRUE
VISTRA_5_PLABT2 | Battery Storage | 2024 | 1830 | 3096.1233 | 0 | 183732 | 0 | 1.685% | 0% |  |  | 1.685% | 0% | 1.685% | 1 | TRUE
VISTRA_5_PLABT3 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
VISTRA_5_PLABT3 | Battery Storage | 2023 | 1150 | 5635.66 | 0 | 85790 | 675 | 6.569% | 0% | 6.703% | 0% | 6.619% | 2.479% | 9.098% | 2 | TRUE
VISTRA_5_PLABT3 | Battery Storage | 2024 | 1830 | 1063.95 | 0 | 136518 | 0 | 0.7793% | 0% |  |  | 0.7793% | 0% | 0.7793% | 1 | TRUE
VISTRA_5_PLABT4 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
VISTRA_5_PLABT4 | Battery Storage | 2023 | 1065 | 404.39 | 0 | 79449 | 760 | 0.509% | 0% | 6.703% | 0% | 3.088% | 2.791% | 5.88% | 2 | TRUE
VISTRA_5_PLABT4 | Battery Storage | 2024 | 1830 | 1384.8367 | 0 | 136518 | 0 | 1.014% | 0% |  |  | 1.014% | 0% | 1.014% | 1 | TRUE
VSTAES_6_VESBT1 | Battery Storage | 2022 | 1825 | 1161.2 | 0 | 58400 | 0 | 1.988% | 0% |  |  | 1.988% | 0% | 1.988% | 1 | TRUE
VSTAES_6_VESBT1 | Battery Storage | 2023 | 1825 | 2823.9583 | 0 | 58400 | 0 | 4.836% | 0% |  |  | 4.836% | 0% | 4.836% | 2 | TRUE
VSTAES_6_VESBT1 | Battery Storage | 2024 | 1830 | 5767.7498 | 0 | 58560 | 0 | 9.849% | 0% |  |  | 9.849% | 0% | 9.849% | 3 | TRUE
WDFRDF_2_WFFBT1 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
WDFRDF_2_WFFBT1 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
WDFRDF_2_WFFBT1 | Battery Storage | 2024 | 800 | 192.5 | 0 | 20000 | 1030 | 0.9625% | 0% | 7.274% | 0% | 4.515% | 4.094% | 8.609% | 2 | TRUE
WESCAN_2_BDSBT1 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
WESCAN_2_BDSBT1 | Battery Storage | 2023 | 960 | 9087.0333 | 0 | 125760 | 865 | 7.226% | 0% | 6.703% | 0% | 6.978% | 3.177% | 10.15% | 2 | TRUE
WESCAN_2_BDSBT1 | Battery Storage | 2024 | 1830 | 2462.8 | 0 | 239730 | 0 | 1.027% | 0% |  |  | 1.027% | 0% | 1.027% | 1 | TRUE
WESCN2_2_BDSBT1 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
WESCN2_2_BDSBT1 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
WESCN2_2_BDSBT1 | Battery Storage | 2024 | 5 | 0 | 0 | 595 | 1825 | 0% | 0% | 7.274% | 0% | 7.254% | 7.254% | 14.51% | 2 | TRUE
WSTWND_2_SBSBT1 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
WSTWND_2_SBSBT1 | Battery Storage | 2023 | 1115 | 1386.1333 | 0 | 89200 | 710 | 1.554% | 0% | 6.703% | 0% | 3.557% | 2.608% | 6.165% | 2 | TRUE
WSTWND_2_SBSBT1 | Battery Storage | 2024 | 1830 | 30.7167 | 0 | 146400 | 0 | 0.02098% | 0% |  |  | 0.02098% | 0% | 0.02098% | 1 | TRUE
WSTWND_2_SBSBT2 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
WSTWND_2_SBSBT2 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
WSTWND_2_SBSBT2 | Battery Storage | 2024 | 535 | 54 | 0 | 21400 | 1295 | 0.2523% | 0% | 7.274% | 0% | 5.221% | 5.147% | 10.37% | 2 | TRUE
WSTWND_2_SBSBT3 | Battery Storage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 14.66% | 0% | 14.66% | 0% | 14.66% | 3 | TRUE
WSTWND_2_SBSBT3 | Battery Storage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.703% | 0% | 6.703% | 0% | 6.703% | 1 | TRUE
WSTWND_2_SBSBT3 | Battery Storage | 2024 | 705 | 428.9 | 0 | 41595 | 1125 | 1.031% | 0% | 7.274% | 0% | 4.869% | 4.471% | 9.34% | 2 | TRUE
CHILLS_7_UNITA1 | Biogas | 2022 | 1825 | 633 | 0 | 4106.25 | 0 | 15.42% | 0% |  |  | 15.42% | 0% | 15.42% | 2 | TRUE
CHILLS_7_UNITA1 | Biogas | 2023 | 1825 | 401.9792 | 0 | 4106.25 | 0 | 9.789% | 0% |  |  | 9.789% | 0% | 9.789% | 1 | TRUE
CHILLS_7_UNITA1 | Biogas | 2024 | 1830 | 407.3125 | 411.6133 | 4117.5 | 0 | 9.892% | 9.997% |  |  | 9.892% | 9.997% | 19.89% | 3 | TRUE
CSTRVL_7_PL1X2 | Biogas | 2022 | 1825 | 156.65 | 0 | 8267.25 | 0 | 1.895% | 0% |  |  | 1.895% | 0% | 1.895% | 2 | TRUE
CSTRVL_7_PL1X2 | Biogas | 2023 | 1825 | 0 | 0 | 8267.25 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
CSTRVL_7_PL1X2 | Biogas | 2024 | 1830 | 249.15 | 0 | 8289.9 | 0 | 3.005% | 0% |  |  | 3.005% | 0% | 3.005% | 3 | TRUE
GUERNS_6_HD3BM3 | Biogas | 2022 | 1825 | 118.6292 | 0 | 1825 | 0 | 6.5% | 0% |  |  | 6.5% | 0% | 6.5% | 3 | TRUE
GUERNS_6_HD3BM3 | Biogas | 2023 | 1825 | 114.8417 | 0 | 1825 | 0 | 6.293% | 0% |  |  | 6.293% | 0% | 6.293% | 1 | TRUE
GUERNS_6_HD3BM3 | Biogas | 2024 | 1830 | 115.5833 | 0 | 1830 | 0 | 6.316% | 0% |  |  | 6.316% | 0% | 6.316% | 2 | TRUE
GUERNS_6_VH2BM1 | Biogas | 2022 | 1825 | 127.1958 | 0 | 1825 | 0 | 6.97% | 0% |  |  | 6.97% | 0% | 6.97% | 2 | TRUE
GUERNS_6_VH2BM1 | Biogas | 2023 | 1825 | 189.8 | 0 | 1825 | 0 | 10.4% | 0% |  |  | 10.4% | 0% | 10.4% | 3 | TRUE
GUERNS_6_VH2BM1 | Biogas | 2024 | 1830 | 110.3333 | 0 | 1830 | 0 | 6.029% | 0% |  |  | 6.029% | 0% | 6.029% | 1 | TRUE
HARDWK_6_STWBM1 | Biogas | 2022 | 1825 | 88.5833 | 18.6 | 1825 | 0 | 4.854% | 1.019% |  |  | 4.854% | 1.019% | 5.873% | 3 | TRUE
HARDWK_6_STWBM1 | Biogas | 2023 | 1825 | 11.3333 | 0 | 1825 | 0 | 0.621% | 0% |  |  | 0.621% | 0% | 0.621% | 1 | TRUE
HARDWK_6_STWBM1 | Biogas | 2024 | 1830 | 94.9167 | 0 | 1830 | 0 | 5.187% | 0% |  |  | 5.187% | 0% | 5.187% | 2 | TRUE
PSWEET_1_STCRUZ | Biogas | 2022 | 1825 | 0 | 0 | 2920 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
PSWEET_1_STCRUZ | Biogas | 2023 | 1825 | 0 | 0 | 2920 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
PSWEET_1_STCRUZ | Biogas | 2024 | 1830 | 0 | 0 | 2928 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
SANLOB_1_OSFBM1 | Biogas | 2022 | 1825 | 0 | 0 | 1551.25 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
SANLOB_1_OSFBM1 | Biogas | 2023 | 1825 | 0 | 0 | 1551.25 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
SANLOB_1_OSFBM1 | Biogas | 2024 | 1830 | 0 | 0 | 1555.5 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
USWND4_2_UNIT2 | Biogas | 2022 | 1825 | 0 | 0 | 13505 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
USWND4_2_UNIT2 | Biogas | 2023 | 1825 | 0 | 0 | 13505 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
USWND4_2_UNIT2 | Biogas | 2024 | 1830 | 0 | 0 | 13542 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
LASSEN_6_UNITS | Biomass/Wood | 2022 | 1825 | 4981.7267 | 0 | 54750 | 0 | 9.099% | 0% |  |  | 9.099% | 0% | 9.099% | 3 | TRUE
LASSEN_6_UNITS | Biomass/Wood | 2023 | 1825 | 1939 | 0 | 54750 | 0 | 3.542% | 0% |  |  | 3.542% | 0% | 3.542% | 1 | TRUE
LASSEN_6_UNITS | Biomass/Wood | 2024 | 1830 | 2502.1667 | 0 | 54900 | 0 | 4.558% | 0% |  |  | 4.558% | 0% | 4.558% | 2 | TRUE
AGRICO_7_UNIT | CCGT | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 7% | 3.561% | 7% | 3.561% | 10.56% | 3 | TRUE
AGRICO_7_UNIT | CCGT | 2023 | 1465 | 9.13 | 641.2732 | 87856.05 | 360 | 0.01039% | 0.7299% | 6.386% | 2.738% | 1.268% | 1.846% | 3.114% | 2 | TRUE
AGRICO_7_UNIT | CCGT | 2024 | 1830 | 1101.1193 | 0 | 109745.1 | 0 | 1.003% | 0% |  |  | 1.003% | 0% | 1.003% | 1 | TRUE
ALAMIT_2_PL1X3 | CCGT | 2022 | 1825 | 51075.5513 | 7566.9667 | 1231327.5 | 0 | 4.148% | 0.6145% |  |  | 4.148% | 0.6145% | 4.763% | 3 | TRUE
ALAMIT_2_PL1X3 | CCGT | 2023 | 1825 | 44775.716 | 6967 | 1231327.5 | 0 | 3.636% | 0.5658% |  |  | 3.636% | 0.5658% | 4.202% | 1 | TRUE
ALAMIT_2_PL1X3 | CCGT | 2024 | 1830 | 51621.7555 | 4137.1317 | 1234701 | 0 | 4.181% | 0.3351% |  |  | 4.181% | 0.3351% | 4.516% | 2 | TRUE
BUCKBL_2_PL1X3 | CCGT | 2022 | 1825 | 7839.4852 | 370.2225 | 900874.75 | 0 | 0.8702% | 0.0411% |  |  | 0.8702% | 0.0411% | 0.9113% | 1 | TRUE
BUCKBL_2_PL1X3 | CCGT | 2023 | 1825 | 27001.5682 | 0 | 900874.75 | 0 | 2.997% | 0% |  |  | 2.997% | 0% | 2.997% | 2 | TRUE
BUCKBL_2_PL1X3 | CCGT | 2024 | 1830 | 67520.3568 | 0 | 903342.9 | 0 | 7.474% | 0% |  |  | 7.474% | 0% | 7.474% | 3 | TRUE
CALPIN_1_AGNEW | CCGT | 2022 | 1825 | 9076.5493 | 74.134 | 52122 | 0 | 17.41% | 0.1422% |  |  | 17.41% | 0.1422% | 17.56% | 3 | TRUE
CALPIN_1_AGNEW | CCGT | 2023 | 1825 | 4108.7733 | 499.048 | 52122 | 0 | 7.883% | 0.9575% |  |  | 7.883% | 0.9575% | 8.84% | 1 | TRUE
CALPIN_1_AGNEW | CCGT | 2024 | 1830 | 4875.4433 | 1201.3213 | 52264.8 | 0 | 9.328% | 2.299% |  |  | 9.328% | 2.299% | 11.63% | 2 | TRUE
COLUSA_2_PL1X3 | CCGT | 2022 | 1825 | 45397.513 | 53847.0932 | 1169825 | 0 | 3.881% | 4.603% |  |  | 3.881% | 4.603% | 8.484% | 3 | TRUE
COLUSA_2_PL1X3 | CCGT | 2023 | 1825 | 13250.7773 | 46045.8405 | 1169825 | 0 | 1.133% | 3.936% |  |  | 1.133% | 3.936% | 5.069% | 1 | TRUE
COLUSA_2_PL1X3 | CCGT | 2024 | 1830 | 43747.4033 | 54419.5208 | 1173030 | 0 | 3.729% | 4.639% |  |  | 3.729% | 4.639% | 8.369% | 2 | TRUE
CORONS_6_CLRWTR | CCGT | 2022 | 1825 | 145.4127 | 0 | 51100 | 0 | 0.2846% | 0% |  |  | 0.2846% | 0% | 0.2846% | 2 | TRUE
CORONS_6_CLRWTR | CCGT | 2023 | 1825 | 64.4877 | 0 | 51100 | 0 | 0.1262% | 0% |  |  | 0.1262% | 0% | 0.1262% | 1 | TRUE
CORONS_6_CLRWTR | CCGT | 2024 | 1830 | 711.985 | 0 | 51240 | 0 | 1.39% | 0% |  |  | 1.39% | 0% | 1.39% | 3 | TRUE
DELTA_2_PL1X4 | CCGT | 2022 | 1825 | 73112.275 | 44985.1667 | 1606000 | 0 | 4.552% | 2.801% |  |  | 4.552% | 2.801% | 7.354% | 1 | TRUE
DELTA_2_PL1X4 | CCGT | 2023 | 1825 | 105752.1168 | 44671.3803 | 1606000 | 0 | 6.585% | 2.782% |  |  | 6.585% | 2.782% | 9.366% | 2 | TRUE
DELTA_2_PL1X4 | CCGT | 2024 | 1830 | 142863.571 | 40154.985 | 1610400 | 0 | 8.871% | 2.493% |  |  | 8.871% | 2.493% | 11.36% | 3 | TRUE
DUANE_1_PL1X3 | CCGT | 2022 | 1825 | 52837.555 | 9556.4667 | 269735 | 0 | 19.59% | 3.543% |  |  | 19.59% | 3.543% | 23.13% | 3 | TRUE
DUANE_1_PL1X3 | CCGT | 2023 | 1825 | 15678.5833 | 12929.6667 | 269735 | 0 | 5.813% | 4.793% |  |  | 5.813% | 4.793% | 10.61% | 1 | TRUE
DUANE_1_PL1X3 | CCGT | 2024 | 1830 | 31082.1045 | 0 | 270474 | 0 | 11.49% | 0% |  |  | 11.49% | 0% | 11.49% | 2 | TRUE
ELKHIL_2_PL1X3 | CCGT | 2022 | 1825 | 37360.25 | 61895.45 | 1006852.5 | 0 | 3.711% | 6.147% |  |  | 3.711% | 6.147% | 9.858% | 2 | TRUE
ELKHIL_2_PL1X3 | CCGT | 2023 | 1825 | 23434.75 | 62147 | 1006852.5 | 0 | 2.328% | 6.172% |  |  | 2.328% | 6.172% | 8.5% | 1 | TRUE
ELKHIL_2_PL1X3 | CCGT | 2024 | 1830 | 221217.2817 | 53045.325 | 1009611 | 0 | 21.91% | 5.254% |  |  | 21.91% | 5.254% | 27.17% | 3 | TRUE
ELSEGN_2_UN1011 | CCGT | 2022 | 1825 | 38321.4088 | 1805.1528 | 500615.75 | 0 | 7.655% | 0.3606% |  |  | 7.655% | 0.3606% | 8.015% | 3 | TRUE
ELSEGN_2_UN1011 | CCGT | 2023 | 1825 | 21243.0358 | 1341.112 | 500615.75 | 0 | 4.243% | 0.2679% |  |  | 4.243% | 0.2679% | 4.511% | 1 | TRUE
ELSEGN_2_UN1011 | CCGT | 2024 | 1830 | 23059.4225 | 5397.9027 | 501987.3 | 0 | 4.594% | 1.075% |  |  | 4.594% | 1.075% | 5.669% | 2 | TRUE
ELSEGN_2_UN2021 | CCGT | 2022 | 1825 | 46408.907 | 3740.954 | 495925.5 | 0 | 9.358% | 0.7543% |  |  | 9.358% | 0.7543% | 10.11% | 3 | TRUE
ELSEGN_2_UN2021 | CCGT | 2023 | 1825 | 14544.433 | 2004.4687 | 495925.5 | 0 | 2.933% | 0.4042% |  |  | 2.933% | 0.4042% | 3.337% | 1 | TRUE
ELSEGN_2_UN2021 | CCGT | 2024 | 1830 | 33723.085 | 1200.185 | 497284.2 | 0 | 6.781% | 0.2413% |  |  | 6.781% | 0.2413% | 7.023% | 2 | TRUE
GATWAY_2_PL1X3 | CCGT | 2022 | 1825 | 100388.91 | 111121.0203 | 1067625 | 0 | 9.403% | 10.41% |  |  | 9.403% | 10.41% | 19.81% | 3 | TRUE
GATWAY_2_PL1X3 | CCGT | 2023 | 1825 | 10722.5467 | 108148.6983 | 1067625 | 0 | 1.004% | 10.13% |  |  | 1.004% | 10.13% | 11.13% | 2 | TRUE
GATWAY_2_PL1X3 | CCGT | 2024 | 1830 | 2733.3667 | 115964.564 | 1070550 | 0 | 0.2553% | 10.83% |  |  | 0.2553% | 10.83% | 11.09% | 1 | TRUE
GILROY_1_UNIT | CCGT | 2022 | 1825 | 10068.5333 | 17786.3667 | 219000 | 0 | 4.598% | 8.122% |  |  | 4.598% | 8.122% | 12.72% | 1 | TRUE
GILROY_1_UNIT | CCGT | 2023 | 1825 | 21214.0885 | 13545.7 | 219000 | 0 | 9.687% | 6.185% |  |  | 9.687% | 6.185% | 15.87% | 2 | TRUE
GILROY_1_UNIT | CCGT | 2024 | 1830 | 31576.9 | 15327.3 | 219600 | 0 | 14.38% | 6.98% |  |  | 14.38% | 6.98% | 21.36% | 3 | TRUE
GLNARM_2_UNIT 5 | CCGT | 2022 | 1825 | 7409.8303 | 0 | 120103.25 | 0 | 6.17% | 0% |  |  | 6.17% | 0% | 6.17% | 1 | TRUE
GLNARM_2_UNIT 5 | CCGT | 2023 | 1825 | 12405.4423 | 2.3715 | 120103.25 | 0 | 10.33% | 0.001975% |  |  | 10.33% | 0.001975% | 10.33% | 2 | TRUE
GLNARM_2_UNIT 5 | CCGT | 2024 | 1830 | 115496.55 | 0 | 120432.3 | 0 | 95.9% | 0% |  |  | 95.9% | 0% | 95.9% | 3 | TRUE
GWFPWR_1_LDCTG1 | CCGT | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 7% | 3.561% | 7% | 3.561% | 10.56% | 3 | TRUE
GWFPWR_1_LDCTG1 | CCGT | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.386% | 2.738% | 6.386% | 2.738% | 9.124% | 2 | TRUE
GWFPWR_1_LDCTG1 | CCGT | 2024 | 0 | 0 | 0 | 0 | 1830 |  |  | 5.925% | 2.686% | 5.925% | 2.686% | 8.612% | 1 | TRUE
GWFPWR_1_LDCTG2 | CCGT | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 7% | 3.561% | 7% | 3.561% | 10.56% | 3 | TRUE
GWFPWR_1_LDCTG2 | CCGT | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.386% | 2.738% | 6.386% | 2.738% | 9.124% | 2 | TRUE
GWFPWR_1_LDCTG2 | CCGT | 2024 | 0 | 0 | 0 | 0 | 1830 |  |  | 5.925% | 2.686% | 5.925% | 2.686% | 8.612% | 1 | TRUE
HARBGN_7_UNITS | CCGT | 2022 | 1825 | 5633.2088 | 10314.2 | 198943.25 | 0 | 2.832% | 5.184% |  |  | 2.832% | 5.184% | 8.016% | 2 | TRUE
HARBGN_7_UNITS | CCGT | 2023 | 1825 | 2296.6012 | 6140.9 | 198943.25 | 0 | 1.154% | 3.087% |  |  | 1.154% | 3.087% | 4.241% | 1 | TRUE
HARBGN_7_UNITS | CCGT | 2024 | 1830 | 52655.9073 | 7128.75 | 199488.3 | 0 | 26.4% | 3.574% |  |  | 26.4% | 3.574% | 29.97% | 3 | TRUE
HIDSRT_2_UNITS | CCGT | 2022 | 1825 | 18658.425 | 118311.8167 | 1551250 | 0 | 1.203% | 7.627% |  |  | 1.203% | 7.627% | 8.83% | 2 | TRUE
HIDSRT_2_UNITS | CCGT | 2023 | 1825 | 179611 | 17811.5667 | 1551250 | 0 | 11.58% | 1.148% |  |  | 11.58% | 1.148% | 12.73% | 3 | TRUE
HIDSRT_2_UNITS | CCGT | 2024 | 1830 | 74386.6767 | 1757.2167 | 1555500 | 0 | 4.782% | 0.113% |  |  | 4.782% | 0.113% | 4.895% | 1 | TRUE
HNTGBH_2_PL1X3 | CCGT | 2022 | 1825 | 59074.3498 | 9140.6667 | 1229685 | 0 | 4.804% | 0.7433% |  |  | 4.804% | 0.7433% | 5.547% | 2 | TRUE
HNTGBH_2_PL1X3 | CCGT | 2023 | 1825 | 62143.1615 | 9595.8517 | 1229685 | 0 | 5.054% | 0.7804% |  |  | 5.054% | 0.7804% | 5.834% | 3 | TRUE
HNTGBH_2_PL1X3 | CCGT | 2024 | 1830 | 9231.991 | 2427.22 | 1233054 | 0 | 0.7487% | 0.1968% |  |  | 0.7487% | 0.1968% | 0.9456% | 1 | TRUE
LAPLMA_2_UNIT 1 | CCGT | 2022 | 1825 | 11844.5 | 21169.0833 | 487275 | 0 | 2.431% | 4.344% |  |  | 2.431% | 4.344% | 6.775% | 1 | TRUE
LAPLMA_2_UNIT 1 | CCGT | 2023 | 1825 | 55769.8667 | 15678.8833 | 487275 | 0 | 11.45% | 3.218% |  |  | 11.45% | 3.218% | 14.66% | 3 | TRUE
LAPLMA_2_UNIT 1 | CCGT | 2024 | 1830 | 27894.85 | 21121.5 | 488610 | 0 | 5.709% | 4.323% |  |  | 5.709% | 4.323% | 10.03% | 2 | TRUE
LAPLMA_2_UNIT 2 | CCGT | 2022 | 1825 | 18590.6763 | 20939.5 | 485450 | 0 | 3.83% | 4.313% |  |  | 3.83% | 4.313% | 8.143% | 1 | TRUE
LAPLMA_2_UNIT 2 | CCGT | 2023 | 1825 | 26574.75 | 14804 | 485450 | 0 | 5.474% | 3.05% |  |  | 5.474% | 3.05% | 8.524% | 2 | TRUE
LAPLMA_2_UNIT 2 | CCGT | 2024 | 1830 | 32771.65 | 20856.5 | 486780 | 0 | 6.732% | 4.285% |  |  | 6.732% | 4.285% | 11.02% | 3 | TRUE
LAPLMA_2_UNIT 3 | CCGT | 2022 | 1825 | 14634.05 | 20099.2 | 485450 | 0 | 3.015% | 4.14% |  |  | 3.015% | 4.14% | 7.155% | 1 | TRUE
LAPLMA_2_UNIT 3 | CCGT | 2023 | 1825 | 18035.5617 | 19680 | 485450 | 0 | 3.715% | 4.054% |  |  | 3.715% | 4.054% | 7.769% | 2 | TRUE
LAPLMA_2_UNIT 3 | CCGT | 2024 | 1830 | 32017.6302 | 25773 | 486780 | 0 | 6.577% | 5.295% |  |  | 6.577% | 5.295% | 11.87% | 3 | TRUE
LAPLMA_2_UNIT 4 | CCGT | 2022 | 1825 | 18519.7667 | 31101.6667 | 487275 | 0 | 3.801% | 6.383% |  |  | 3.801% | 6.383% | 10.18% | 1 | TRUE
LAPLMA_2_UNIT 4 | CCGT | 2023 | 1825 | 99458.1322 | 18297.1667 | 487275 | 0 | 20.41% | 3.755% |  |  | 20.41% | 3.755% | 24.17% | 3 | TRUE
LAPLMA_2_UNIT 4 | CCGT | 2024 | 1830 | 44566.3833 | 24220.2667 | 488610 | 0 | 9.121% | 4.957% |  |  | 9.121% | 4.957% | 14.08% | 2 | TRUE
LAROA2_2_UNITA1 | CCGT | 2022 | 1825 | 23098.5167 | 12379.5667 | 587650 | 0 | 3.931% | 2.107% |  |  | 3.931% | 2.107% | 6.037% | 1 | TRUE
LAROA2_2_UNITA1 | CCGT | 2023 | 1825 | 23239.9167 | 25973 | 587650 | 0 | 3.955% | 4.42% |  |  | 3.955% | 4.42% | 8.375% | 2 | TRUE
LAROA2_2_UNITA1 | CCGT | 2024 | 1830 | 36526.4867 | 25214.5833 | 589260 | 0 | 6.199% | 4.279% |  |  | 6.199% | 4.279% | 10.48% | 3 | TRUE
LEBECS_2_UNITS | CCGT | 2022 | 1825 | 208925.5375 | 18370.5027 | 1459032.75 | 0 | 14.32% | 1.259% |  |  | 14.32% | 1.259% | 15.58% | 3 | TRUE
LEBECS_2_UNITS | CCGT | 2023 | 1825 | 111309.3987 | 23041.001 | 1459032.75 | 0 | 7.629% | 1.579% |  |  | 7.629% | 1.579% | 9.208% | 2 | TRUE
LEBECS_2_UNITS | CCGT | 2024 | 1830 | 79269.502 | 20859.547 | 1463030.1 | 0 | 5.418% | 1.426% |  |  | 5.418% | 1.426% | 6.844% | 1 | TRUE
LECEF_1_UNITS | CCGT | 2022 | 1825 | 14588.8267 | 25602.76 | 565458 | 0 | 2.58% | 4.528% |  |  | 2.58% | 4.528% | 7.108% | 2 | TRUE
LECEF_1_UNITS | CCGT | 2023 | 1825 | 59641.5558 | 17267.229 | 565458 | 0 | 10.55% | 3.054% |  |  | 10.55% | 3.054% | 13.6% | 3 | TRUE
LECEF_1_UNITS | CCGT | 2024 | 1830 | 2590.902 | 27346.0607 | 567007.2 | 0 | 0.4569% | 4.823% |  |  | 0.4569% | 4.823% | 5.28% | 1 | TRUE
LGHTHP_6_ICEGEN | CCGT | 2022 | 1825 | 5040.8 | 104 | 87600 | 0 | 5.754% | 0.1187% |  |  | 5.754% | 0.1187% | 5.873% | 1 | TRUE
LGHTHP_6_ICEGEN | CCGT | 2023 | 1825 | 16903.98 | 0 | 87600 | 0 | 19.3% | 0% |  |  | 19.3% | 0% | 19.3% | 2 | TRUE
LGHTHP_6_ICEGEN | CCGT | 2024 | 1830 | 21214.4 | 0 | 87840 | 0 | 24.15% | 0% |  |  | 24.15% | 0% | 24.15% | 3 | TRUE
LMEC_1_PL1X3 | CCGT | 2022 | 1825 | 56763.6 | 34643.7667 | 1058500 | 0 | 5.363% | 3.273% |  |  | 5.363% | 3.273% | 8.636% | 2 | TRUE
LMEC_1_PL1X3 | CCGT | 2023 | 1825 | 121154.45 | 31000.4067 | 1058500 | 0 | 11.45% | 2.929% |  |  | 11.45% | 2.929% | 14.37% | 3 | TRUE
LMEC_1_PL1X3 | CCGT | 2024 | 1830 | 56769.71 | 19990.438 | 1061400 | 0 | 5.349% | 1.883% |  |  | 5.349% | 1.883% | 7.232% | 1 | TRUE
LODIEC_2_PL1X2 | CCGT | 2022 | 1825 | 88545.1337 | 42368.2067 | 552208.5 | 0 | 16.03% | 7.673% |  |  | 16.03% | 7.673% | 23.71% | 3 | TRUE
LODIEC_2_PL1X2 | CCGT | 2023 | 1825 | 32250.1947 | 37357.2 | 552208.5 | 0 | 5.84% | 6.765% |  |  | 5.84% | 6.765% | 12.61% | 2 | TRUE
LODIEC_2_PL1X2 | CCGT | 2024 | 1830 | 16859.119 | 37357.5 | 553721.4 | 0 | 3.045% | 6.747% |  |  | 3.045% | 6.747% | 9.791% | 1 | TRUE
METEC_2_PL1X3 | CCGT | 2022 | 1825 | 138875.6323 | 26329.5433 | 1089616.25 | 0 | 12.75% | 2.416% |  |  | 12.75% | 2.416% | 15.16% | 2 | TRUE
METEC_2_PL1X3 | CCGT | 2023 | 1825 | 276550.1047 | 21113.937 | 1089616.25 | 0 | 25.38% | 1.938% |  |  | 25.38% | 1.938% | 27.32% | 3 | TRUE
METEC_2_PL1X3 | CCGT | 2024 | 1830 | 34061.48 | 25821.3667 | 1092601.5 | 0 | 3.117% | 2.363% |  |  | 3.117% | 2.363% | 5.481% | 1 | TRUE
MOSSLD_2_PSP1 | CCGT | 2022 | 1825 | 33712.9167 | 2162.0167 | 930750 | 0 | 3.622% | 0.2323% |  |  | 3.622% | 0.2323% | 3.854% | 3 | TRUE
MOSSLD_2_PSP1 | CCGT | 2023 | 1825 | 14539.9167 | 2849.1 | 930750 | 0 | 1.562% | 0.3061% |  |  | 1.562% | 0.3061% | 1.868% | 1 | TRUE
MOSSLD_2_PSP1 | CCGT | 2024 | 1830 | 18881.15 | 1655.75 | 933300 | 0 | 2.023% | 0.1774% |  |  | 2.023% | 0.1774% | 2.2% | 2 | TRUE
MOSSLD_2_PSP2 | CCGT | 2022 | 1825 | 20098.1667 | 1673.3 | 930750 | 0 | 2.159% | 0.1798% |  |  | 2.159% | 0.1798% | 2.339% | 2 | TRUE
MOSSLD_2_PSP2 | CCGT | 2023 | 1825 | 12468.5 | 1523.8167 | 930750 | 0 | 1.34% | 0.1637% |  |  | 1.34% | 0.1637% | 1.503% | 1 | TRUE
MOSSLD_2_PSP2 | CCGT | 2024 | 1830 | 69051.0833 | 1521.7 | 933300 | 0 | 7.399% | 0.163% |  |  | 7.399% | 0.163% | 7.562% | 3 | TRUE
MRCHNT_2_PL1X3 | CCGT | 2022 | 1825 | 4932.0833 | 95767.5803 | 902608.5 | 0 | 0.5464% | 10.61% |  |  | 0.5464% | 10.61% | 11.16% | 2 | TRUE
MRCHNT_2_PL1X3 | CCGT | 2023 | 1825 | 25687.2167 | 74074.4 | 902608.5 | 0 | 2.846% | 8.207% |  |  | 2.846% | 8.207% | 11.05% | 1 | TRUE
MRCHNT_2_PL1X3 | CCGT | 2024 | 1830 | 50935.15 | 63300.3667 | 905081.4 | 0 | 5.628% | 6.994% |  |  | 5.628% | 6.994% | 12.62% | 3 | TRUE
OTMESA_2_PL1X3 | CCGT | 2022 | 1825 | 64354.05 | 41696.9833 | 1101716 | 0 | 5.841% | 3.785% |  |  | 5.841% | 3.785% | 9.626% | 1 | TRUE
OTMESA_2_PL1X3 | CCGT | 2023 | 1825 | 79394.2167 | 33855.274 | 1101716 | 0 | 7.206% | 3.073% |  |  | 7.206% | 3.073% | 10.28% | 2 | TRUE
OTMESA_2_PL1X3 | CCGT | 2024 | 1830 | 114063.9518 | 36394.425 | 1104734.4 | 0 | 10.33% | 3.294% |  |  | 10.33% | 3.294% | 13.62% | 3 | TRUE
PALOMR_2_PL1X3 | CCGT | 2022 | 1825 | 55285.1827 | 58.0867 | 1073483.25 | 0 | 5.15% | 0.005411% |  |  | 5.15% | 0.005411% | 5.155% | 2 | TRUE
PALOMR_2_PL1X3 | CCGT | 2023 | 1825 | 113693.7035 | 259.5362 | 1073483.25 | 0 | 10.59% | 0.02418% |  |  | 10.59% | 0.02418% | 10.62% | 3 | TRUE
PALOMR_2_PL1X3 | CCGT | 2024 | 1830 | 37363.941 | 680.7127 | 1076424.3 | 0 | 3.471% | 0.06324% |  |  | 3.471% | 0.06324% | 3.534% | 1 | TRUE
RUSCTY_2_UNITS | CCGT | 2022 | 1825 | 551670.1095 | 20002.9555 | 1122703.5 | 0 | 49.14% | 1.782% |  |  | 49.14% | 1.782% | 50.92% | 3 | TRUE
RUSCTY_2_UNITS | CCGT | 2023 | 1825 | 71535.343 | 34787.2833 | 1122703.5 | 0 | 6.372% | 3.099% |  |  | 6.372% | 3.099% | 9.47% | 2 | TRUE
RUSCTY_2_UNITS | CCGT | 2024 | 1830 | 23799.6607 | 36715.8183 | 1125779.4 | 0 | 2.114% | 3.261% |  |  | 2.114% | 3.261% | 5.375% | 1 | TRUE
SBERDO_2_PSP3 | CCGT | 2022 | 1825 | 67580.0565 | 25227.2735 | 1012875 | 0 | 6.672% | 2.491% |  |  | 6.672% | 2.491% | 9.163% | 3 | TRUE
SBERDO_2_PSP3 | CCGT | 2023 | 1825 | 34527.1995 | 19108.3638 | 1012875 | 0 | 3.409% | 1.887% |  |  | 3.409% | 1.887% | 5.295% | 2 | TRUE
SBERDO_2_PSP3 | CCGT | 2024 | 1830 | 22281.9358 | 16452.91 | 1015650 | 0 | 2.194% | 1.62% |  |  | 2.194% | 1.62% | 3.814% | 1 | TRUE
SBERDO_2_PSP4 | CCGT | 2022 | 1825 | 32895.0765 | 27673.8333 | 1012875 | 0 | 3.248% | 2.732% |  |  | 3.248% | 2.732% | 5.98% | 1 | TRUE
SBERDO_2_PSP4 | CCGT | 2023 | 1825 | 96752.0985 | 24515.0415 | 1012875 | 0 | 9.552% | 2.42% |  |  | 9.552% | 2.42% | 11.97% | 3 | TRUE
SBERDO_2_PSP4 | CCGT | 2024 | 1830 | 61295.7165 | 27777.5125 | 1015650 | 0 | 6.035% | 2.735% |  |  | 6.035% | 2.735% | 8.77% | 2 | TRUE
SCHLTE_1_PL1X3 | CCGT | 2022 | 1825 | 214.0057 | 34400.4933 | 613273 | 0 | 0.0349% | 5.609% |  |  | 0.0349% | 5.609% | 5.644% | 3 | TRUE
SCHLTE_1_PL1X3 | CCGT | 2023 | 1825 | 2621.0693 | 2750.5473 | 613273 | 0 | 0.4274% | 0.4485% |  |  | 0.4274% | 0.4485% | 0.8759% | 1 | TRUE
SCHLTE_1_PL1X3 | CCGT | 2024 | 1830 | 5502.5993 | 4601.3027 | 614953.2 | 0 | 0.8948% | 0.7482% |  |  | 0.8948% | 0.7482% | 1.643% | 2 | TRUE
SGREGY_6_SANGER | CCGT | 2022 | 1825 | 31386.95 | 33 | 88147.5 | 0 | 35.61% | 0.03744% |  |  | 35.61% | 0.03744% | 35.64% | 3 | TRUE
SGREGY_6_SANGER | CCGT | 2023 | 1825 | 8299.3917 | 0 | 88147.5 | 0 | 9.415% | 0% |  |  | 9.415% | 0% | 9.415% | 2 | TRUE
SGREGY_6_SANGER | CCGT | 2024 | 1830 | 609.06 | 0 | 88389 | 0 | 0.6891% | 0% |  |  | 0.6891% | 0% | 0.6891% | 1 | TRUE
SUNRIS_2_PL1X3 | CCGT | 2022 | 1825 | 24541.0167 | 68235.6167 | 1069486.5 | 0 | 2.295% | 6.38% |  |  | 2.295% | 6.38% | 8.675% | 1 | TRUE
SUNRIS_2_PL1X3 | CCGT | 2023 | 1825 | 55336.7143 | 61371.124 | 1069486.5 | 0 | 5.174% | 5.738% |  |  | 5.174% | 5.738% | 10.91% | 2 | TRUE
SUNRIS_2_PL1X3 | CCGT | 2024 | 1830 | 66516.47 | 59641.83 | 1072416.6 | 0 | 6.202% | 5.561% |  |  | 6.202% | 5.561% | 11.76% | 3 | TRUE
TERMEX_2_PL1X3 | CCGT | 2022 | 1825 | 43319.2333 | 57149.9167 | 1140625 | 0 | 3.798% | 5.01% |  |  | 3.798% | 5.01% | 8.808% | 3 | TRUE
TERMEX_2_PL1X3 | CCGT | 2023 | 1825 | 19978.6667 | 19300.7667 | 1140625 | 0 | 1.752% | 1.692% |  |  | 1.752% | 1.692% | 3.444% | 1 | TRUE
TERMEX_2_PL1X3 | CCGT | 2024 | 1830 | 31781 | 18894 | 1143750 | 0 | 2.779% | 1.652% |  |  | 2.779% | 1.652% | 4.431% | 2 | TRUE
VERNON_6_MALBRG | CCGT | 2022 | 1825 | 26580.8167 | 45 | 253675 | 0 | 10.48% | 0.01774% |  |  | 10.48% | 0.01774% | 10.5% | 3 | TRUE
VERNON_6_MALBRG | CCGT | 2023 | 1825 | 4664 | 0 | 253675 | 0 | 1.839% | 0% |  |  | 1.839% | 0% | 1.839% | 1 | TRUE
VERNON_6_MALBRG | CCGT | 2024 | 1830 | 10797.8117 | 0 | 254370 | 0 | 4.245% | 0% |  |  | 4.245% | 0% | 4.245% | 2 | TRUE
ARCOGN_2_UNITS | CHP | 2022 | 1825 | 55956.6667 | 180 | 447125 | 0 | 12.51% | 0.04026% |  |  | 12.51% | 0.04026% | 12.56% | 2 | TRUE
ARCOGN_2_UNITS | CHP | 2023 | 1825 | 57765.1667 | 125 | 447125 | 0 | 12.92% | 0.02796% |  |  | 12.92% | 0.02796% | 12.95% | 3 | TRUE
ARCOGN_2_UNITS | CHP | 2024 | 1830 | 53887.8167 | 90 | 448350 | 0 | 12.02% | 0.02007% |  |  | 12.02% | 0.02007% | 12.04% | 1 | TRUE
CHINO_6_CIMGEN | CHP | 2022 | 1825 | 0 | 0 | 47450 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
CHINO_6_CIMGEN | CHP | 2023 | 1825 | 0 | 0 | 47450 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
CHINO_6_CIMGEN | CHP | 2024 | 1830 | 0 | 0 | 47580 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
CUMMNG_6_SUNCT1 | CHP | 2022 | 1825 | 0 | 0 | 7300 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
CUMMNG_6_SUNCT1 | CHP | 2023 | 1825 | 0 | 0 | 7300 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
CUMMNG_6_SUNCT1 | CHP | 2024 | 1830 | 0 | 0 | 7320 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
DEXZEL_1_UNIT | CHP | 2022 | 1825 | 22113.2 | 0 | 36500 | 0 | 60.58% | 0% |  |  | 60.58% | 0% | 60.58% | 3 | TRUE
DEXZEL_1_UNIT | CHP | 2023 | 1825 | 10924.9083 | 0 | 36500 | 0 | 29.93% | 0% |  |  | 29.93% | 0% | 29.93% | 1 | TRUE
DEXZEL_1_UNIT | CHP | 2024 | 1830 | 11396.4903 | 30.3 | 36600 | 0 | 31.14% | 0.08279% |  |  | 31.14% | 0.08279% | 31.22% | 2 | TRUE
GRNLF2_1_UNIT | CHP | 2022 | 1825 | 42558 | 0 | 89790 | 0 | 47.4% | 0% |  |  | 47.4% | 0% | 47.4% | 2 | TRUE
GRNLF2_1_UNIT | CHP | 2023 | 1825 | 75793.95 | 0 | 89790 | 0 | 84.41% | 0% |  |  | 84.41% | 0% | 84.41% | 3 | TRUE
GRNLF2_1_UNIT | CHP | 2024 | 1830 | 13299.0657 | 8.36 | 90036 | 0 | 14.77% | 0.009285% |  |  | 14.77% | 0.009285% | 14.78% | 1 | TRUE
OMAR_2_UNIT 4 | CHP | 2022 | 1825 | 14438.75 | 54.4 | 136875 | 0 | 10.55% | 0.03974% |  |  | 10.55% | 0.03974% | 10.59% | 1 | TRUE
OMAR_2_UNIT 4 | CHP | 2023 | 1825 | 21207.4167 | 0 | 136875 | 0 | 15.49% | 0% |  |  | 15.49% | 0% | 15.49% | 2 | TRUE
OMAR_2_UNIT 4 | CHP | 2024 | 1830 | 23537.5 | 0 | 137250 | 0 | 17.15% | 0% |  |  | 17.15% | 0% | 17.15% | 3 | TRUE
OROVIL_6_UNIT | CHP | 2022 | 1825 | 3927.2 | 0 | 13687.5 | 0 | 28.69% | 0% |  |  | 28.69% | 0% | 28.69% | 3 | TRUE
OROVIL_6_UNIT | CHP | 2023 | 1825 | 2341.92 | 0 | 13687.5 | 0 | 17.11% | 0% |  |  | 17.11% | 0% | 17.11% | 2 | TRUE
OROVIL_6_UNIT | CHP | 2024 | 1830 | 1545 | 0 | 13725 | 0 | 11.26% | 0% |  |  | 11.26% | 0% | 11.26% | 1 | TRUE
PLMSSR_6_HISIER | CHP | 2022 | 1825 | 705.5207 | 0 | 10950 | 0 | 6.443% | 0% |  |  | 6.443% | 0% | 6.443% | 2 | TRUE
PLMSSR_6_HISIER | CHP | 2023 | 1825 | 467.143 | 0 | 10950 | 0 | 4.266% | 0% |  |  | 4.266% | 0% | 4.266% | 1 | TRUE
PLMSSR_6_HISIER | CHP | 2024 | 1830 | 744.7595 | 0 | 10980 | 0 | 6.783% | 0% |  |  | 6.783% | 0% | 6.783% | 3 | TRUE
SALIRV_2_UNIT | CHP | 2022 | 1825 | 259.35 | 0 | 71175 | 0 | 0.3644% | 0% |  |  | 0.3644% | 0% | 0.3644% | 1 | TRUE
SALIRV_2_UNIT | CHP | 2023 | 1825 | 12558.65 | 0 | 71175 | 0 | 17.64% | 0% |  |  | 17.64% | 0% | 17.64% | 3 | TRUE
SALIRV_2_UNIT | CHP | 2024 | 1830 | 7125.3 | 0 | 71370 | 0 | 9.984% | 0% |  |  | 9.984% | 0% | 9.984% | 2 | TRUE
SMPRIP_1_SMPSON | CHP | 2022 | 1825 | 14336.9 | 0 | 84041.25 | 0 | 17.06% | 0% |  |  | 17.06% | 0% | 17.06% | 3 | TRUE
SMPRIP_1_SMPSON | CHP | 2023 | 1825 | 3321.91 | 0 | 84041.25 | 0 | 3.953% | 0% |  |  | 3.953% | 0% | 3.953% | 2 | TRUE
SMPRIP_1_SMPSON | CHP | 2024 | 1830 | 728.2543 | 0 | 84271.5 | 0 | 0.8642% | 0% |  |  | 0.8642% | 0% | 0.8642% | 1 | TRUE
SNCLRA_2_UNIT | CHP | 2022 | 1825 | 21450 | 0 | 50187.5 | 0 | 42.74% | 0% |  |  | 42.74% | 0% | 42.74% | 3 | TRUE
SNCLRA_2_UNIT | CHP | 2023 | 1825 | 13887.5 | 0 | 50187.5 | 0 | 27.67% | 0% |  |  | 27.67% | 0% | 27.67% | 2 | TRUE
SNCLRA_2_UNIT | CHP | 2024 | 1830 | 0 | 0 | 50325 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
SNCLRA_2_UNIT1 | CHP | 2022 | 1825 | 121 | 0 | 50735 | 0 | 0.2385% | 0% |  |  | 0.2385% | 0% | 0.2385% | 1 | TRUE
SNCLRA_2_UNIT1 | CHP | 2023 | 1825 | 16969.9417 | 0 | 50735 | 0 | 33.45% | 0% |  |  | 33.45% | 0% | 33.45% | 3 | TRUE
SNCLRA_2_UNIT1 | CHP | 2024 | 1830 | 10256.1767 | 0 | 50874 | 0 | 20.16% | 0% |  |  | 20.16% | 0% | 20.16% | 2 | TRUE
SNCLRA_6_OXGEN | CHP | 2022 | 1825 | 8728.305 | 0 | 87052.5 | 0 | 10.03% | 0% |  |  | 10.03% | 0% | 10.03% | 2 | TRUE
SNCLRA_6_OXGEN | CHP | 2023 | 1825 | 2432.7 | 0 | 87052.5 | 0 | 2.795% | 0% |  |  | 2.795% | 0% | 2.795% | 1 | TRUE
SNCLRA_6_OXGEN | CHP | 2024 | 1830 | 12681.925 | 0 | 87291 | 0 | 14.53% | 0% |  |  | 14.53% | 0% | 14.53% | 3 | TRUE
SUNSET_2_UNITS | CHP | 2022 | 1825 | 60743.45 | 21993 | 452600 | 0 | 13.42% | 4.859% |  |  | 13.42% | 4.859% | 18.28% | 3 | TRUE
SUNSET_2_UNITS | CHP | 2023 | 1825 | 2696.5667 | 18389 | 452600 | 0 | 0.5958% | 4.063% |  |  | 0.5958% | 4.063% | 4.659% | 1 | TRUE
SUNSET_2_UNITS | CHP | 2024 | 1830 | 4178.9 | 22824.5 | 453840 | 0 | 0.9208% | 5.029% |  |  | 0.9208% | 5.029% | 5.95% | 2 | TRUE
SYCAMR_2_UNIT 1 | CHP | 2022 | 1825 | 20686.5667 | 0 | 135050 | 0 | 15.32% | 0% |  |  | 15.32% | 0% | 15.32% | 1 | TRUE
SYCAMR_2_UNIT 1 | CHP | 2023 | 1825 | 22034.3667 | 0 | 135050 | 0 | 16.32% | 0% |  |  | 16.32% | 0% | 16.32% | 3 | TRUE
SYCAMR_2_UNIT 1 | CHP | 2024 | 1830 | 21860.8333 | 0 | 135420 | 0 | 16.14% | 0% |  |  | 16.14% | 0% | 16.14% | 2 | TRUE
SYCAMR_2_UNIT 3 | CHP | 2022 | 1825 | 4990.7667 | 0 | 135050 | 0 | 3.695% | 0% |  |  | 3.695% | 0% | 3.695% | 2 | TRUE
SYCAMR_2_UNIT 3 | CHP | 2023 | 1825 | 2768.8333 | 0 | 135050 | 0 | 2.05% | 0% |  |  | 2.05% | 0% | 2.05% | 1 | TRUE
SYCAMR_2_UNIT 3 | CHP | 2024 | 1830 | 11659.9333 | 0 | 135420 | 0 | 8.61% | 0% |  |  | 8.61% | 0% | 8.61% | 3 | TRUE
TENGEN_2_PL1X2 | CHP | 2022 | 1825 | 15999.96 | 150.2067 | 68802.5 | 0 | 23.25% | 0.2183% |  |  | 23.25% | 0.2183% | 23.47% | 2 | TRUE
TENGEN_2_PL1X2 | CHP | 2023 | 1825 | 9253.4083 | 0 | 68802.5 | 0 | 13.45% | 0% |  |  | 13.45% | 0% | 13.45% | 1 | TRUE
TENGEN_2_PL1X2 | CHP | 2024 | 1830 | 36952.915 | 0 | 68991 | 0 | 53.56% | 0% |  |  | 53.56% | 0% | 53.56% | 3 | TRUE
YUBACT_1_SUNSWT | CHP | 2022 | 1825 | 10995.0428 | 1439.8918 | 91195.25 | 0 | 12.06% | 1.579% |  |  | 12.06% | 1.579% | 13.64% | 3 | TRUE
YUBACT_1_SUNSWT | CHP | 2023 | 1825 | 11015.8865 | 0 | 91195.25 | 0 | 12.08% | 0% |  |  | 12.08% | 0% | 12.08% | 2 | TRUE
YUBACT_1_SUNSWT | CHP | 2024 | 1830 | 5960.5882 | 0 | 91445.1 | 0 | 6.518% | 0% |  |  | 6.518% | 0% | 6.518% | 1 | TRUE
ADLIN_1_UNITS | Geothermal | 2022 | 1825 | 21078.2805 | 0 | 40150 | 0 | 52.5% | 0% |  |  | 52.5% | 0% | 52.5% | 3 | TRUE
ADLIN_1_UNITS | Geothermal | 2023 | 1825 | 20826.7583 | 0 | 40150 | 0 | 51.87% | 0% |  |  | 51.87% | 0% | 51.87% | 2 | TRUE
ADLIN_1_UNITS | Geothermal | 2024 | 1830 | 19125.6458 | 0 | 40260 | 0 | 47.51% | 0% |  |  | 47.51% | 0% | 47.51% | 1 | TRUE
BLM_2_UNITS | Geothermal | 2022 | 1825 | 6743.6 | 0 | 63875 | 0 | 10.56% | 0% |  |  | 10.56% | 0% | 10.56% | 2 | TRUE
BLM_2_UNITS | Geothermal | 2023 | 1825 | 14126.3333 | 0 | 63875 | 0 | 22.12% | 0% |  |  | 22.12% | 0% | 22.12% | 3 | TRUE
BLM_2_UNITS | Geothermal | 2024 | 1830 | 4204.285 | 0 | 64050 | 0 | 6.564% | 0% |  |  | 6.564% | 0% | 6.564% | 1 | TRUE
CALGEN_1_UNITS | Geothermal | 2022 | 1825 | 1654 | 0 | 100375 | 0 | 1.648% | 0% |  |  | 1.648% | 0% | 1.648% | 1 | TRUE
CALGEN_1_UNITS | Geothermal | 2023 | 1825 | 7417.9333 | 0 | 100375 | 0 | 7.39% | 0% |  |  | 7.39% | 0% | 7.39% | 3 | TRUE
CALGEN_1_UNITS | Geothermal | 2024 | 1830 | 6807.05 | 0 | 100650 | 0 | 6.763% | 0% |  |  | 6.763% | 0% | 6.763% | 2 | TRUE
CASADB_1_CD4GT1 | Geothermal | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 22.49% | 0.01483% | 22.49% | 0.01483% | 22.51% | 1 | TRUE
CASADB_1_CD4GT1 | Geothermal | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 28.7% | 0.07349% | 28.7% | 0.07349% | 28.77% | 2 | TRUE
CASADB_1_CD4GT1 | Geothermal | 2024 | 1300 | 978.0517 | 10831 | 52910 | 530 | 1.849% | 20.47% | 24.53% | 0.6013% | 8.417% | 21.65% | 30.06% | 3 | TRUE
CONTRL_1_CASAD2 | Geothermal | 2022 | 1825 | 291.4367 | 333.4467 | 19162.5 | 0 | 1.521% | 1.74% |  |  | 1.521% | 1.74% | 3.261% | 1 | TRUE
CONTRL_1_CASAD2 | Geothermal | 2023 | 1825 | 3283.0783 | 1652.2317 | 19162.5 | 0 | 17.13% | 8.622% |  |  | 17.13% | 8.622% | 25.76% | 3 | TRUE
CONTRL_1_CASAD2 | Geothermal | 2024 | 1830 | 572.0833 | 3042.35 | 19215 | 0 | 2.977% | 15.83% |  |  | 2.977% | 15.83% | 18.81% | 2 | TRUE
GEYS11_7_UNIT11 | Geothermal | 2022 | 1825 | 30520.2213 | 0 | 158410 | 0 | 19.27% | 0% |  |  | 19.27% | 0% | 19.27% | 2 | TRUE
GEYS11_7_UNIT11 | Geothermal | 2023 | 1825 | 27655.4278 | 0 | 158410 | 0 | 17.46% | 0% |  |  | 17.46% | 0% | 17.46% | 1 | TRUE
GEYS11_7_UNIT11 | Geothermal | 2024 | 1830 | 44514.8667 | 0 | 158844 | 0 | 28.02% | 0% |  |  | 28.02% | 0% | 28.02% | 3 | TRUE
GEYS12_7_UNIT12 | Geothermal | 2022 | 1825 | 24602.3333 | 0 | 104025 | 0 | 23.65% | 0% |  |  | 23.65% | 0% | 23.65% | 1 | TRUE
GEYS12_7_UNIT12 | Geothermal | 2023 | 1825 | 29668 | 0 | 104025 | 0 | 28.52% | 0% |  |  | 28.52% | 0% | 28.52% | 3 | TRUE
GEYS12_7_UNIT12 | Geothermal | 2024 | 1830 | 27478.2782 | 0 | 104310 | 0 | 26.34% | 0% |  |  | 26.34% | 0% | 26.34% | 2 | TRUE
GEYS13_7_UNIT13 | Geothermal | 2022 | 1825 | 40868.9333 | 0 | 133225 | 0 | 30.68% | 0% |  |  | 30.68% | 0% | 30.68% | 1 | TRUE
GEYS13_7_UNIT13 | Geothermal | 2023 | 1825 | 45207.5333 | 0 | 133225 | 0 | 33.93% | 0% |  |  | 33.93% | 0% | 33.93% | 2 | TRUE
GEYS13_7_UNIT13 | Geothermal | 2024 | 1830 | 50121.2167 | 0 | 133590 | 0 | 37.52% | 0% |  |  | 37.52% | 0% | 37.52% | 3 | TRUE
GEYS14_7_UNIT14 | Geothermal | 2022 | 1825 | 20674.2667 | 0 | 127750 | 0 | 16.18% | 0% |  |  | 16.18% | 0% | 16.18% | 1 | TRUE
GEYS14_7_UNIT14 | Geothermal | 2023 | 1825 | 27954 | 0 | 127750 | 0 | 21.88% | 0% |  |  | 21.88% | 0% | 21.88% | 2 | TRUE
GEYS14_7_UNIT14 | Geothermal | 2024 | 1830 | 34113.0833 | 0 | 128100 | 0 | 26.63% | 0% |  |  | 26.63% | 0% | 26.63% | 3 | TRUE
GEYS16_7_UNIT16 | Geothermal | 2022 | 1825 | 29227.9 | 0 | 114975 | 0 | 25.42% | 0% |  |  | 25.42% | 0% | 25.42% | 2 | TRUE
GEYS16_7_UNIT16 | Geothermal | 2023 | 1825 | 28797 | 0 | 114975 | 0 | 25.05% | 0% |  |  | 25.05% | 0% | 25.05% | 1 | TRUE
GEYS16_7_UNIT16 | Geothermal | 2024 | 1830 | 30960.1667 | 0 | 115290 | 0 | 26.85% | 0% |  |  | 26.85% | 0% | 26.85% | 3 | TRUE
GEYS17_7_UNIT17 | Geothermal | 2022 | 1825 | 32664.7367 | 0 | 137787.5 | 0 | 23.71% | 0% |  |  | 23.71% | 0% | 23.71% | 2 | TRUE
GEYS17_7_UNIT17 | Geothermal | 2023 | 1825 | 34112.85 | 0 | 137787.5 | 0 | 24.76% | 0% |  |  | 24.76% | 0% | 24.76% | 3 | TRUE
GEYS17_7_UNIT17 | Geothermal | 2024 | 1830 | 31894.6667 | 0 | 138165 | 0 | 23.08% | 0% |  |  | 23.08% | 0% | 23.08% | 1 | TRUE
GEYS18_7_UNIT18 | Geothermal | 2022 | 1825 | 49931.8333 | 0 | 131400 | 0 | 38% | 0% |  |  | 38% | 0% | 38% | 1 | TRUE
GEYS18_7_UNIT18 | Geothermal | 2023 | 1825 | 58455.5 | 0 | 131400 | 0 | 44.49% | 0% |  |  | 44.49% | 0% | 44.49% | 3 | TRUE
GEYS18_7_UNIT18 | Geothermal | 2024 | 1830 | 57056.0727 | 0 | 131760 | 0 | 43.3% | 0% |  |  | 43.3% | 0% | 43.3% | 2 | TRUE
GEYS20_7_UNIT20 | Geothermal | 2022 | 1825 | 24176.1333 | 0 | 91250 | 0 | 26.49% | 0% |  |  | 26.49% | 0% | 26.49% | 1 | TRUE
GEYS20_7_UNIT20 | Geothermal | 2023 | 1825 | 27191.5652 | 0 | 91250 | 0 | 29.8% | 0% |  |  | 29.8% | 0% | 29.8% | 2 | TRUE
GEYS20_7_UNIT20 | Geothermal | 2024 | 1830 | 29404.6667 | 0 | 91500 | 0 | 32.14% | 0% |  |  | 32.14% | 0% | 32.14% | 3 | TRUE
GYS5X6_7_UNITS | Geothermal | 2022 | 1825 | 32092.335 | 0 | 179634.75 | 0 | 17.87% | 0% |  |  | 17.87% | 0% | 17.87% | 1 | TRUE
GYS5X6_7_UNITS | Geothermal | 2023 | 1825 | 56952.6833 | 0 | 179634.75 | 0 | 31.7% | 0% |  |  | 31.7% | 0% | 31.7% | 2 | TRUE
GYS5X6_7_UNITS | Geothermal | 2024 | 1830 | 66513.2833 | 0 | 180126.9 | 0 | 36.93% | 0% |  |  | 36.93% | 0% | 36.93% | 3 | TRUE
GYS7X8_7_UNITS | Geothermal | 2022 | 1825 | 32890.0495 | 0 | 174835 | 0 | 18.81% | 0% |  |  | 18.81% | 0% | 18.81% | 2 | TRUE
GYS7X8_7_UNITS | Geothermal | 2023 | 1825 | 31854.4167 | 0 | 174835 | 0 | 18.22% | 0% |  |  | 18.22% | 0% | 18.22% | 1 | TRUE
GYS7X8_7_UNITS | Geothermal | 2024 | 1830 | 40652.379 | 0 | 175314 | 0 | 23.19% | 0% |  |  | 23.19% | 0% | 23.19% | 3 | TRUE
NAVYII_2_UNITS | Geothermal | 2022 | 1825 | 1307 | 0 | 85775 | 0 | 1.524% | 0% |  |  | 1.524% | 0% | 1.524% | 1 | TRUE
NAVYII_2_UNITS | Geothermal | 2023 | 1825 | 8095 | 0 | 85775 | 0 | 9.437% | 0% |  |  | 9.437% | 0% | 9.437% | 2 | TRUE
NAVYII_2_UNITS | Geothermal | 2024 | 1830 | 9117.485 | 0 | 86010 | 0 | 10.6% | 0% |  |  | 10.6% | 0% | 10.6% | 3 | TRUE
NCPA_7_GP1UN1 | Geothermal | 2022 | 1825 | 618.72 | 0 | 70901.25 | 0 | 0.8727% | 0% |  |  | 0.8727% | 0% | 0.8727% | 1 | TRUE
NCPA_7_GP1UN1 | Geothermal | 2023 | 1825 | 56313.075 | 0 | 70901.25 | 0 | 79.42% | 0% |  |  | 79.42% | 0% | 79.42% | 3 | TRUE
NCPA_7_GP1UN1 | Geothermal | 2024 | 1830 | 17858.6975 | 0 | 71095.5 | 0 | 25.12% | 0% |  |  | 25.12% | 0% | 25.12% | 2 | TRUE
NCPA_7_GP1UN2 | Geothermal | 2022 | 1825 | 306.78 | 0 | 91250 | 0 | 0.3362% | 0% |  |  | 0.3362% | 0% | 0.3362% | 1 | TRUE
NCPA_7_GP1UN2 | Geothermal | 2023 | 1825 | 9392.2607 | 0 | 91250 | 0 | 10.29% | 0% |  |  | 10.29% | 0% | 10.29% | 2 | TRUE
NCPA_7_GP1UN2 | Geothermal | 2024 | 1830 | 36500 | 0 | 91500 | 0 | 39.89% | 0% |  |  | 39.89% | 0% | 39.89% | 3 | TRUE
NCPA_7_GP2UN3 | Geothermal | 2022 | 1825 | 77204.4 | 0 | 77416.5 | 0 | 99.73% | 0% |  |  | 99.73% | 0% | 99.73% | 3 | TRUE
NCPA_7_GP2UN3 | Geothermal | 2023 | 1825 | 76992.3 | 0 | 77416.5 | 0 | 99.45% | 0% |  |  | 99.45% | 0% | 99.45% | 2 | TRUE
NCPA_7_GP2UN3 | Geothermal | 2024 | 1830 | 0 | 0 | 77628.6 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
NCPA_7_GP2UN4 | Geothermal | 2022 | 1825 | 0 | 0 | 96232.25 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
NCPA_7_GP2UN4 | Geothermal | 2023 | 1825 | 25097.0343 | 0 | 96232.25 | 0 | 26.08% | 0% |  |  | 26.08% | 0% | 26.08% | 3 | TRUE
NCPA_7_GP2UN4 | Geothermal | 2024 | 1830 | 85.46 | 0 | 96495.9 | 0 | 0.08856% | 0% |  |  | 0.08856% | 0% | 0.08856% | 2 | TRUE
SANTFG_7_UNITS | Geothermal | 2022 | 1825 | 18241.5 | 0 | 131400 | 0 | 13.88% | 0% |  |  | 13.88% | 0% | 13.88% | 1 | TRUE
SANTFG_7_UNITS | Geothermal | 2023 | 1825 | 28946.9333 | 0 | 131400 | 0 | 22.03% | 0% |  |  | 22.03% | 0% | 22.03% | 2 | TRUE
SANTFG_7_UNITS | Geothermal | 2024 | 1830 | 32722.186 | 0 | 131760 | 0 | 24.83% | 0% |  |  | 24.83% | 0% | 24.83% | 3 | TRUE
SMUDGO_7_UNIT 1 | Geothermal | 2022 | 1825 | 60582.42 | 0 | 118260 | 0 | 51.23% | 0% |  |  | 51.23% | 0% | 51.23% | 3 | TRUE
SMUDGO_7_UNIT 1 | Geothermal | 2023 | 1825 | 26847.8667 | 0 | 118260 | 0 | 22.7% | 0% |  |  | 22.7% | 0% | 22.7% | 2 | TRUE
SMUDGO_7_UNIT 1 | Geothermal | 2024 | 1830 | 25205.4 | 0 | 118584 | 0 | 21.26% | 0% |  |  | 21.26% | 0% | 21.26% | 1 | TRUE
BARRE_2_ALASB1 | Hybrid_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 16.48% | 0.6981% | 16.48% | 0.6981% | 17.18% | 2 | TRUE
BARRE_2_ALASB1 | Hybrid_BattStorage | 2023 | 260 | 0 | 0 | 1300 | 1565 | 0% | 0% | 10.27% | 0% | 8.804% | 8.804% | 17.61% | 3 | TRUE
BARRE_2_ALASB1 | Hybrid_BattStorage | 2024 | 1830 | 236.6667 | 0 | 9150 | 0 | 2.587% | 0% |  |  | 2.587% | 0% | 2.587% | 1 | TRUE
CUYAMA_6_SB3SB1 | Hybrid_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 16.48% | 0.6981% | 16.48% | 0.6981% | 17.18% | 3 | TRUE
CUYAMA_6_SB3SB1 | Hybrid_BattStorage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.27% | 0% | 10.27% | 0% | 10.27% | 2 | TRUE
CUYAMA_6_SB3SB1 | Hybrid_BattStorage | 2024 | 1825 | 30 | 0 | 5475 | 5 | 0.5479% | 0% | 31.56% | 0% | 0.6327% | 0.08622% | 0.7189% | 1 | TRUE
DELAMO_2_ALASB2 | Hybrid_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 16.48% | 0.6981% | 16.48% | 0.6981% | 17.18% | 2 | TRUE
DELAMO_2_ALASB2 | Hybrid_BattStorage | 2023 | 260 | 200 | 0 | 1300 | 1565 | 15.38% | 0% | 10.27% | 0% | 11% | 8.804% | 19.8% | 3 | TRUE
DELAMO_2_ALASB2 | Hybrid_BattStorage | 2024 | 1830 | 450 | 0 | 9150 | 0 | 4.918% | 0% |  |  | 4.918% | 0% | 4.918% | 1 | TRUE
DSFLWR_2_W9CSB1 | Hybrid_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 16.48% | 0.6981% | 16.48% | 0.6981% | 17.18% | 2 | TRUE
DSFLWR_2_W9CSB1 | Hybrid_BattStorage | 2023 | 0 | 6391.22 | 0 | 0 | 1825 |  |  | 10.27% | 0% | 10.27% | 0% | 10.27% | 1 | TRUE
DSFLWR_2_W9CSB1 | Hybrid_BattStorage | 2024 | 0 | 36257 | 0 | 0 | 1830 |  |  | 31.56% | 0% | 31.56% | 0% | 31.56% | 3 | TRUE
DSFLWR_2_W9CSB2 | Hybrid_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 16.48% | 0.6981% | 16.48% | 0.6981% | 17.18% | 2 | TRUE
DSFLWR_2_W9CSB2 | Hybrid_BattStorage | 2023 | 0 | 5618.6733 | 0 | 0 | 1825 |  |  | 10.27% | 0% | 10.27% | 0% | 10.27% | 1 | TRUE
DSFLWR_2_W9CSB2 | Hybrid_BattStorage | 2024 | 0 | 31573 | 0 | 0 | 1830 |  |  | 31.56% | 0% | 31.56% | 0% | 31.56% | 3 | TRUE
EDWARD_2_E21SB1 | Hybrid_BattStorage | 2022 | 635 | 6393.3 | 0 | 45085 | 1190 | 14.18% | 0% | 16.48% | 0.6981% | 15.68% | 10.75% | 26.43% | 3 | TRUE
EDWARD_2_E21SB1 | Hybrid_BattStorage | 2023 | 1825 | 5054 | 0 | 129575 | 0 | 3.9% | 0% |  |  | 3.9% | 0% | 3.9% | 2 | TRUE
EDWARD_2_E21SB1 | Hybrid_BattStorage | 2024 | 1830 | 644.0667 | 0 | 129930 | 0 | 0.4957% | 0% |  |  | 0.4957% | 0% | 0.4957% | 1 | TRUE
EDWARD_2_E23SB1 | Hybrid_BattStorage | 2022 | 1825 | 2439.7 | 0 | 10950 | 0 | 22.28% | 0% |  |  | 22.28% | 0% | 22.28% | 3 | TRUE
EDWARD_2_E23SB1 | Hybrid_BattStorage | 2023 | 1825 | 756.2667 | 0 | 10950 | 0 | 6.907% | 0% |  |  | 6.907% | 0% | 6.907% | 1 | TRUE
EDWARD_2_E23SB1 | Hybrid_BattStorage | 2024 | 1830 | 2364.75 | 0 | 10980 | 0 | 21.54% | 0% |  |  | 21.54% | 0% | 21.54% | 2 | TRUE
EDWARD_2_ES2BT3 | Hybrid_BattStorage | 2022 | 1370 | 8315.8 | 0 | 90420 | 455 | 9.197% | 0% | 16.48% | 0.6981% | 11.01% | 4.11% | 15.12% | 3 | TRUE
EDWARD_2_ES2BT3 | Hybrid_BattStorage | 2023 | 1825 | 3999.2 | 0 | 120450 | 0 | 3.32% | 0% |  |  | 3.32% | 0% | 3.32% | 1 | TRUE
EDWARD_2_ES2BT3 | Hybrid_BattStorage | 2024 | 1830 | 16953.4167 | 0 | 120780 | 0 | 14.04% | 0% |  |  | 14.04% | 0% | 14.04% | 2 | TRUE
EDWARD_2_ESSSB1 | Hybrid_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 16.48% | 0.6981% | 16.48% | 0.6981% | 17.18% | 2 | TRUE
EDWARD_2_ESSSB1 | Hybrid_BattStorage | 2023 | 0 | 334.4667 | 0 | 0 | 1825 |  |  | 10.27% | 0% | 10.27% | 0% | 10.27% | 1 | TRUE
EDWARD_2_ESSSB1 | Hybrid_BattStorage | 2024 | 0 | 24039.0367 | 0 | 0 | 1830 |  |  | 31.56% | 0% | 31.56% | 0% | 31.56% | 3 | TRUE
EDWARD_2_ESSSB2 | Hybrid_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 16.48% | 0.6981% | 16.48% | 0.6981% | 17.18% | 2 | TRUE
EDWARD_2_ESSSB2 | Hybrid_BattStorage | 2023 | 240 | 132 | 0 | 5160 | 1585 | 2.558% | 0% | 10.27% | 0% | 9.253% | 8.917% | 18.17% | 3 | TRUE
EDWARD_2_ESSSB2 | Hybrid_BattStorage | 2024 | 1830 | 5413.5833 | 0 | 39345 | 0 | 13.76% | 0% |  |  | 13.76% | 0% | 13.76% | 1 | TRUE
HAMLIN_1_BLDSB1 | Hybrid_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 16.48% | 0.6981% | 16.48% | 0.6981% | 17.18% | 2 | TRUE
HAMLIN_1_BLDSB1 | Hybrid_BattStorage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.27% | 0% | 10.27% | 0% | 10.27% | 1 | TRUE
HAMLIN_1_BLDSB1 | Hybrid_BattStorage | 2024 | 1230 | 93823.55 | 0 | 92250 | 600 | 101.7% | 0% | 31.56% | 0% | 78.71% | 10.35% | 89.05% | 3 | TRUE
HAMLIN_1_BMSBT2 | Hybrid_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 16.48% | 0.6981% | 16.48% | 0.6981% | 17.18% | 2 | TRUE
HAMLIN_1_BMSBT2 | Hybrid_BattStorage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.27% | 0% | 10.27% | 0% | 10.27% | 1 | TRUE
HAMLIN_1_BMSBT2 | Hybrid_BattStorage | 2024 | 100 | 2388.8333 | 0 | 2500 | 1730 | 95.55% | 0% | 31.56% | 0% | 35.05% | 29.83% | 64.88% | 3 | TRUE
LNCSTR_6_SOLAR2 | Hybrid_BattStorage | 2022 | 1825 | 0 | 0 | 12775 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
LNCSTR_6_SOLAR2 | Hybrid_BattStorage | 2023 | 1825 | 0 | 0 | 12775 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
LNCSTR_6_SOLAR2 | Hybrid_BattStorage | 2024 | 1830 | 0 | 0 | 12810 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
MCFLND_5_MBSBX2 | Hybrid_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 16.48% | 0.6981% | 16.48% | 0.6981% | 17.18% | 2 | TRUE
MCFLND_5_MBSBX2 | Hybrid_BattStorage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.27% | 0% | 10.27% | 0% | 10.27% | 1 | TRUE
MCFLND_5_MBSBX2 | Hybrid_BattStorage | 2024 | 485 | 48890.4833 | 0 | 72750 | 1345 | 67.2% | 0% | 31.56% | 0% | 41% | 23.19% | 64.2% | 3 | TRUE
NORORC_2_NOSBX2 | Hybrid_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 16.48% | 0.6981% | 16.48% | 0.6981% | 17.18% | 2 | TRUE
NORORC_2_NOSBX2 | Hybrid_BattStorage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.27% | 0% | 10.27% | 0% | 10.27% | 1 | TRUE
NORORC_2_NOSBX2 | Hybrid_BattStorage | 2024 | 0 | 6390.95 | 0 | 0 | 1830 |  |  | 31.56% | 0% | 31.56% | 0% | 31.56% | 3 | TRUE
PUTHCR_1_PCNSB1 | Hybrid_BattStorage | 2022 | 390 | 0 | 0 | 1170 | 1435 | 0% | 0% | 16.48% | 0.6981% | 12.96% | 12.96% | 25.92% | 3 | TRUE
PUTHCR_1_PCNSB1 | Hybrid_BattStorage | 2023 | 1825 | 505.35 | 0 | 5475 | 0 | 9.23% | 0% |  |  | 9.23% | 0% | 9.23% | 1 | TRUE
PUTHCR_1_PCNSB1 | Hybrid_BattStorage | 2024 | 1830 | 1197.65 | 0 | 5490 | 0 | 21.82% | 0% |  |  | 21.82% | 0% | 21.82% | 2 | TRUE
RATSKE_2_RBSSB1 | Hybrid_BattStorage | 2022 | 375 | 2223.0333 | 60 | 2812.5 | 1450 | 79.04% | 2.133% | 16.48% | 0.6981% | 29.34% | 13.54% | 42.87% | 3 | TRUE
RATSKE_2_RBSSB1 | Hybrid_BattStorage | 2023 | 1825 | 289.8083 | 0 | 13687.5 | 0 | 2.117% | 0% |  |  | 2.117% | 0% | 2.117% | 1 | TRUE
RATSKE_2_RBSSB1 | Hybrid_BattStorage | 2024 | 1830 | 1180 | 0 | 13725 | 0 | 8.597% | 0% |  |  | 8.597% | 0% | 8.597% | 2 | TRUE
RATSKE_2_RBSSB2 | Hybrid_BattStorage | 2022 | 375 | 1578.1333 | 114.6667 | 1875 | 1450 | 84.17% | 6.116% | 16.48% | 0.6981% | 30.39% | 14.35% | 44.75% | 3 | TRUE
RATSKE_2_RBSSB2 | Hybrid_BattStorage | 2023 | 1825 | 288.0667 | 0 | 9125 | 0 | 3.157% | 0% |  |  | 3.157% | 0% | 3.157% | 1 | TRUE
RATSKE_2_RBSSB2 | Hybrid_BattStorage | 2024 | 1830 | 540 | 0 | 9150 | 0 | 5.902% | 0% |  |  | 5.902% | 0% | 5.902% | 2 | TRUE
SANBRN_2_EESSB2 | Hybrid_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 16.48% | 0.6981% | 16.48% | 0.6981% | 17.18% | 2 | TRUE
SANBRN_2_EESSB2 | Hybrid_BattStorage | 2023 | 265 | 499.3333 | 0 | 22525 | 1560 | 2.217% | 0% | 10.27% | 0% | 9.098% | 8.776% | 17.87% | 3 | TRUE
SANBRN_2_EESSB2 | Hybrid_BattStorage | 2024 | 1830 | 1218.85 | 0 | 155550 | 0 | 0.7836% | 0% |  |  | 0.7836% | 0% | 0.7836% | 1 | TRUE
SANBRN_2_ES1BT3 | Hybrid_BattStorage | 2022 | 1315 | 2227.325 | 0 | 28930 | 510 | 7.699% | 0% | 16.48% | 0.6981% | 10.15% | 4.607% | 14.76% | 3 | TRUE
SANBRN_2_ES1BT3 | Hybrid_BattStorage | 2023 | 1825 | 903.5375 | 0 | 40150 | 0 | 2.25% | 0% |  |  | 2.25% | 0% | 2.25% | 2 | TRUE
SANBRN_2_ES1BT3 | Hybrid_BattStorage | 2024 | 1830 | 472.5407 | 0 | 40260 | 0 | 1.174% | 0% |  |  | 1.174% | 0% | 1.174% | 1 | TRUE
SANBRN_2_ES2SB3 | Hybrid_BattStorage | 2022 | 1315 | 2892.9 | 0 | 23670 | 510 | 12.22% | 0% | 16.48% | 0.6981% | 13.41% | 4.607% | 18.02% | 3 | TRUE
SANBRN_2_ES2SB3 | Hybrid_BattStorage | 2023 | 1825 | 767.2 | 0 | 32850 | 0 | 2.335% | 0% |  |  | 2.335% | 0% | 2.335% | 2 | TRUE
SANBRN_2_ES2SB3 | Hybrid_BattStorage | 2024 | 1830 | 143.5 | 0 | 32940 | 0 | 0.4356% | 0% |  |  | 0.4356% | 0% | 0.4356% | 1 | TRUE
SANBRN_2_SS2SB4 | Hybrid_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 16.48% | 0.6981% | 16.48% | 0.6981% | 17.18% | 3 | TRUE
SANBRN_2_SS2SB4 | Hybrid_BattStorage | 2023 | 870 | 198 | 0 | 15660 | 955 | 1.264% | 0% | 10.27% | 0% | 5.975% | 5.373% | 11.35% | 2 | TRUE
SANBRN_2_SS2SB4 | Hybrid_BattStorage | 2024 | 1830 | 510.8 | 0 | 32940 | 0 | 1.551% | 0% |  |  | 1.551% | 0% | 1.551% | 1 | TRUE
SLATE_2_SLASR2 | Hybrid_BattStorage | 2022 | 1460 | 10963.545 | 1224.7733 | 67890 | 365 | 16.15% | 1.804% | 16.48% | 0.6981% | 16.22% | 4.74% | 20.96% | 2 | TRUE
SLATE_2_SLASR2 | Hybrid_BattStorage | 2023 | 1825 | 16082.275 | 0 | 84862.5 | 0 | 18.95% | 0% |  |  | 18.95% | 0% | 18.95% | 1 | TRUE
SLATE_2_SLASR2 | Hybrid_BattStorage | 2024 | 1830 | 28304.6067 | 0 | 85095 | 0 | 33.26% | 0% |  |  | 33.26% | 0% | 33.26% | 3 | TRUE
SLATE_2_SLASR3 | Hybrid_BattStorage | 2022 | 1460 | 7211.5817 | 1429.6217 | 49275 | 365 | 14.64% | 2.901% | 16.48% | 0.6981% | 15.01% | 5.618% | 20.62% | 1 | TRUE
SLATE_2_SLASR3 | Hybrid_BattStorage | 2023 | 1825 | 13264.9267 | 0 | 61593.75 | 0 | 21.54% | 0% |  |  | 21.54% | 0% | 21.54% | 2 | TRUE
SLATE_2_SLASR3 | Hybrid_BattStorage | 2024 | 1830 | 22788.1467 | 0 | 61762.5 | 0 | 36.9% | 0% |  |  | 36.9% | 0% | 36.9% | 3 | TRUE
SLATE_2_SLASR4 | Hybrid_BattStorage | 2022 | 1460 | 19390.6997 | 0 | 73000 | 365 | 26.56% | 0% | 16.48% | 0.6981% | 24.55% | 3.297% | 27.84% | 3 | TRUE
SLATE_2_SLASR4 | Hybrid_BattStorage | 2023 | 1825 | 8087.852 | 0 | 91250 | 0 | 8.863% | 0% |  |  | 8.863% | 0% | 8.863% | 2 | TRUE
SLATE_2_SLASR4 | Hybrid_BattStorage | 2024 | 1830 | 1420.6233 | 0 | 91500 | 0 | 1.553% | 0% |  |  | 1.553% | 0% | 1.553% | 1 | TRUE
SLATE_2_SLASR5 | Hybrid_BattStorage | 2022 | 1460 | 6004.9825 | 119.9367 | 14600 | 365 | 41.13% | 0.8215% | 16.48% | 0.6981% | 36.2% | 3.954% | 40.16% | 3 | TRUE
SLATE_2_SLASR5 | Hybrid_BattStorage | 2023 | 1825 | 6128.3798 | 0 | 18250 | 0 | 33.58% | 0% |  |  | 33.58% | 0% | 33.58% | 2 | TRUE
SLATE_2_SLASR5 | Hybrid_BattStorage | 2024 | 1830 | 4679.2457 | 0 | 18300 | 0 | 25.57% | 0% |  |  | 25.57% | 0% | 25.57% | 1 | TRUE
BARRE_2_ALASB1_SUN | Hybrid_Solar_1Axis | 2022 | 1825 | 0 | 0 | 18250 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
BARRE_2_ALASB1_SUN | Hybrid_Solar_1Axis | 2023 | 1825 | 0 | 0 | 18250 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
BARRE_2_ALASB1_SUN | Hybrid_Solar_1Axis | 2024 | 1830 | 0 | 0 | 18300 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
CUYAMA_6_SB3SB1_SUN | Hybrid_Solar_1Axis | 2022 | 1825 | 0 | 0 | 5475 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
CUYAMA_6_SB3SB1_SUN | Hybrid_Solar_1Axis | 2023 | 1825 | 0 | 0 | 5475 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
CUYAMA_6_SB3SB1_SUN | Hybrid_Solar_1Axis | 2024 | 1830 | 0 | 0 | 5490 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
DELAMO_2_ALASB2_SUN | Hybrid_Solar_1Axis | 2022 | 1825 | 0 | 0 | 18250 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
DELAMO_2_ALASB2_SUN | Hybrid_Solar_1Axis | 2023 | 1825 | 0 | 0 | 18250 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
DELAMO_2_ALASB2_SUN | Hybrid_Solar_1Axis | 2024 | 1830 | 0 | 0 | 18300 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
DSFLWR_2_W9CSB1_SUN | Hybrid_Solar_1Axis | 2022 | 1825 | 0 | 0 | 186150 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
DSFLWR_2_W9CSB1_SUN | Hybrid_Solar_1Axis | 2023 | 1825 | 0 | 0 | 186150 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
DSFLWR_2_W9CSB1_SUN | Hybrid_Solar_1Axis | 2024 | 1830 | 0 | 0 | 186660 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
DSFLWR_2_W9CSB2_SUN | Hybrid_Solar_1Axis | 2022 | 1825 | 0 | 0 | 131400 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
DSFLWR_2_W9CSB2_SUN | Hybrid_Solar_1Axis | 2023 | 1825 | 0 | 0 | 131400 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
DSFLWR_2_W9CSB2_SUN | Hybrid_Solar_1Axis | 2024 | 1830 | 0 | 0 | 131760 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
EDWARD_2_E21SB1_SUN | Hybrid_Solar_1Axis | 2022 | 1825 | 0 | 0 | 237250 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
EDWARD_2_E21SB1_SUN | Hybrid_Solar_1Axis | 2023 | 1825 | 0 | 0 | 237250 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
EDWARD_2_E21SB1_SUN | Hybrid_Solar_1Axis | 2024 | 1830 | 0 | 0 | 237900 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
EDWARD_2_E23SB1_SUN | Hybrid_Solar_1Axis | 2022 | 1825 | 0 | 0 | 43800 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
EDWARD_2_E23SB1_SUN | Hybrid_Solar_1Axis | 2023 | 1825 | 0 | 0 | 43800 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
EDWARD_2_E23SB1_SUN | Hybrid_Solar_1Axis | 2024 | 1830 | 0 | 0 | 43920 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
EDWARD_2_ES2BT3_SUN | Hybrid_Solar_1Axis | 2022 | 1825 | 0 | 0 | 215350 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
EDWARD_2_ES2BT3_SUN | Hybrid_Solar_1Axis | 2023 | 1825 | 0 | 0 | 215350 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
EDWARD_2_ES2BT3_SUN | Hybrid_Solar_1Axis | 2024 | 1830 | 0 | 0 | 215940 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
EDWARD_2_ESSSB1_SUN | Hybrid_Solar_1Axis | 2022 | 1825 | 0 | 0 | 124100 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
EDWARD_2_ESSSB1_SUN | Hybrid_Solar_1Axis | 2023 | 1825 | 0 | 0 | 124100 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
EDWARD_2_ESSSB1_SUN | Hybrid_Solar_1Axis | 2024 | 1830 | 0 | 0 | 124440 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
EDWARD_2_ESSSB2_SUN | Hybrid_Solar_1Axis | 2022 | 1825 | 0 | 0 | 240900 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
EDWARD_2_ESSSB2_SUN | Hybrid_Solar_1Axis | 2023 | 1825 | 0 | 0 | 240900 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
EDWARD_2_ESSSB2_SUN | Hybrid_Solar_1Axis | 2024 | 1830 | 0 | 0 | 241560 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
HAMLIN_1_BLDSB1_SUN | Hybrid_Solar_1Axis | 2022 | 1825 | 0 | 0 | 273750 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
HAMLIN_1_BLDSB1_SUN | Hybrid_Solar_1Axis | 2023 | 1825 | 0 | 0 | 273750 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
HAMLIN_1_BLDSB1_SUN | Hybrid_Solar_1Axis | 2024 | 1830 | 0 | 0 | 274500 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
HAMLIN_1_BMSBT2_SUN | Hybrid_Solar_1Axis | 2022 | 1825 | 0 | 0 | 91250 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
HAMLIN_1_BMSBT2_SUN | Hybrid_Solar_1Axis | 2023 | 1825 | 0 | 0 | 91250 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
HAMLIN_1_BMSBT2_SUN | Hybrid_Solar_1Axis | 2024 | 1830 | 0 | 0 | 91500 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
LNCSTR_6_SOLAR2_SUN | Hybrid_Solar_1Axis | 2022 | 1825 | 0 | 0 | 5475 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
LNCSTR_6_SOLAR2_SUN | Hybrid_Solar_1Axis | 2023 | 1825 | 0 | 0 | 5475 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
LNCSTR_6_SOLAR2_SUN | Hybrid_Solar_1Axis | 2024 | 1830 | 0 | 0 | 5490 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
MCFLND_5_MBSBX2_SUN | Hybrid_Solar_1Axis | 2022 | 1825 | 0 | 0 | 547500 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
MCFLND_5_MBSBX2_SUN | Hybrid_Solar_1Axis | 2023 | 1825 | 0 | 0 | 547500 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
MCFLND_5_MBSBX2_SUN | Hybrid_Solar_1Axis | 2024 | 1830 | 0 | 0 | 549000 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
NORORC_2_NOSBX2_SUN | Hybrid_Solar_1Axis | 2022 | 1825 | 0 | 0 | 273750 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
NORORC_2_NOSBX2_SUN | Hybrid_Solar_1Axis | 2023 | 1825 | 0 | 0 | 273750 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
NORORC_2_NOSBX2_SUN | Hybrid_Solar_1Axis | 2024 | 1830 | 0 | 0 | 274500 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
PUTHCR_1_PCNSB1_SUN | Hybrid_Solar_1Axis | 2022 | 1825 | 0 | 0 | 5475 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
PUTHCR_1_PCNSB1_SUN | Hybrid_Solar_1Axis | 2023 | 1825 | 0 | 0 | 5475 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
PUTHCR_1_PCNSB1_SUN | Hybrid_Solar_1Axis | 2024 | 1830 | 0 | 0 | 5490 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
RATSKE_2_RBSSB1_SUN | Hybrid_Solar_1Axis | 2022 | 1825 | 0 | 0 | 109500 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
RATSKE_2_RBSSB1_SUN | Hybrid_Solar_1Axis | 2023 | 1825 | 0 | 0 | 109500 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
RATSKE_2_RBSSB1_SUN | Hybrid_Solar_1Axis | 2024 | 1830 | 0 | 0 | 109800 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
RATSKE_2_RBSSB2_SUN | Hybrid_Solar_1Axis | 2022 | 1825 | 0 | 0 | 73000 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
RATSKE_2_RBSSB2_SUN | Hybrid_Solar_1Axis | 2023 | 1825 | 0 | 0 | 73000 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
RATSKE_2_RBSSB2_SUN | Hybrid_Solar_1Axis | 2024 | 1830 | 0 | 0 | 73200 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
SANBRN_2_EESSB2_SUN | Hybrid_Solar_1Axis | 2022 | 1825 | 0 | 0 | 237250 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
SANBRN_2_EESSB2_SUN | Hybrid_Solar_1Axis | 2023 | 1825 | 0 | 0 | 237250 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
SANBRN_2_EESSB2_SUN | Hybrid_Solar_1Axis | 2024 | 1830 | 0 | 0 | 237900 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
SANBRN_2_ES1BT3_SUN | Hybrid_Solar_1Axis | 2022 | 1825 | 0 | 0 | 73000 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
SANBRN_2_ES1BT3_SUN | Hybrid_Solar_1Axis | 2023 | 1825 | 0 | 0 | 73000 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
SANBRN_2_ES1BT3_SUN | Hybrid_Solar_1Axis | 2024 | 1830 | 0 | 0 | 73200 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
SANBRN_2_ES2SB3_SUN | Hybrid_Solar_1Axis | 2022 | 1825 | 0 | 0 | 60225 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
SANBRN_2_ES2SB3_SUN | Hybrid_Solar_1Axis | 2023 | 1825 | 0 | 0 | 60225 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
SANBRN_2_ES2SB3_SUN | Hybrid_Solar_1Axis | 2024 | 1830 | 0 | 0 | 60390 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
SANBRN_2_SS2SB4_SUN | Hybrid_Solar_1Axis | 2022 | 1825 | 0 | 0 | 65700 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
SANBRN_2_SS2SB4_SUN | Hybrid_Solar_1Axis | 2023 | 1825 | 0 | 0 | 65700 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
SANBRN_2_SS2SB4_SUN | Hybrid_Solar_1Axis | 2024 | 1830 | 0 | 0 | 65880 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
SLATE_2_SLASR2_SUN | Hybrid_Solar_1Axis | 2022 | 1825 | 0 | 0 | 169725 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
SLATE_2_SLASR2_SUN | Hybrid_Solar_1Axis | 2023 | 1825 | 0 | 0 | 169725 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
SLATE_2_SLASR2_SUN | Hybrid_Solar_1Axis | 2024 | 1830 | 0 | 0 | 170190 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
SLATE_2_SLASR4_SUN | Hybrid_Solar_1Axis | 2022 | 1825 | 0 | 0 | 114975 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
SLATE_2_SLASR4_SUN | Hybrid_Solar_1Axis | 2023 | 1825 | 0 | 0 | 114975 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
SLATE_2_SLASR4_SUN | Hybrid_Solar_1Axis | 2024 | 1830 | 0 | 0 | 115290 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
SLATE_2_SLASR5_SUN | Hybrid_Solar_1Axis | 2022 | 1825 | 0 | 0 | 47450 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
SLATE_2_SLASR5_SUN | Hybrid_Solar_1Axis | 2023 | 1825 | 0 | 0 | 47450 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
SLATE_2_SLASR5_SUN | Hybrid_Solar_1Axis | 2024 | 1830 | 0 | 0 | 47580 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
SLATE_2_SLASR3_SUN | Hybrid_Solar_Fixed | 2022 | 1825 | 0 | 0 | 123187.5 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
SLATE_2_SLASR3_SUN | Hybrid_Solar_Fixed | 2023 | 1825 | 0 | 0 | 123187.5 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
SLATE_2_SLASR3_SUN | Hybrid_Solar_Fixed | 2024 | 1830 | 0 | 0 | 123525 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
ALAMO_6_UNIT | Hydro | 2022 | 1825 | 3376.2 | 0 | 31025 | 0 | 10.88% | 0% |  |  | 10.88% | 0% | 10.88% | 2 | TRUE
ALAMO_6_UNIT | Hydro | 2023 | 1825 | 27.2 | 0 | 31025 | 0 | 0.08767% | 0% |  |  | 0.08767% | 0% | 0.08767% | 1 | TRUE
ALAMO_6_UNIT | Hydro | 2024 | 1830 | 8567.15 | 0 | 31110 | 0 | 27.54% | 0% |  |  | 27.54% | 0% | 27.54% | 3 | TRUE
APLHIL_1_SFKHY1 | Hydro | 2022 | 1825 | 1876 | 0 | 4891 | 0 | 38.36% | 0% |  |  | 38.36% | 0% | 38.36% | 3 | TRUE
APLHIL_1_SFKHY1 | Hydro | 2023 | 1825 | 383.1507 | 0 | 4891 | 0 | 7.834% | 0% |  |  | 7.834% | 0% | 7.834% | 2 | TRUE
APLHIL_1_SFKHY1 | Hydro | 2024 | 1830 | 127.434 | 0 | 4904.4 | 0 | 2.598% | 0% |  |  | 2.598% | 0% | 2.598% | 1 | TRUE
BALCHS_7_UNIT 1 | Hydro | 2022 | 1825 | 1841.0367 | 0 | 56575 | 0 | 3.254% | 0% |  |  | 3.254% | 0% | 3.254% | 2 | TRUE
BALCHS_7_UNIT 1 | Hydro | 2023 | 1825 | 1090.4667 | 2.2333 | 56575 | 0 | 1.927% | 0.003948% |  |  | 1.927% | 0.003948% | 1.931% | 1 | TRUE
BALCHS_7_UNIT 1 | Hydro | 2024 | 1830 | 1902.8367 | 22.1 | 56730 | 0 | 3.354% | 0.03896% |  |  | 3.354% | 0.03896% | 3.393% | 3 | TRUE
BALCHS_7_UNIT 2 | Hydro | 2022 | 1825 | 5058.7867 | 0 | 95812.5 | 0 | 5.28% | 0% |  |  | 5.28% | 0% | 5.28% | 3 | TRUE
BALCHS_7_UNIT 2 | Hydro | 2023 | 1825 | 2797.1792 | 0 | 95812.5 | 0 | 2.919% | 0% |  |  | 2.919% | 0% | 2.919% | 2 | TRUE
BALCHS_7_UNIT 2 | Hydro | 2024 | 1830 | 1780.9167 | 0 | 96075 | 0 | 1.854% | 0% |  |  | 1.854% | 0% | 1.854% | 1 | TRUE
BALCHS_7_UNIT 3 | Hydro | 2022 | 1825 | 4527.7167 | 0 | 99645 | 0 | 4.544% | 0% |  |  | 4.544% | 0% | 4.544% | 3 | TRUE
BALCHS_7_UNIT 3 | Hydro | 2023 | 1825 | 3319.3333 | 0 | 99645 | 0 | 3.331% | 0% |  |  | 3.331% | 0% | 3.331% | 2 | TRUE
BALCHS_7_UNIT 3 | Hydro | 2024 | 1830 | 2094.0033 | 0 | 99918 | 0 | 2.096% | 0% |  |  | 2.096% | 0% | 2.096% | 1 | TRUE
BEARDS_7_UNIT 1 | Hydro | 2022 | 1825 | 69.4083 | 0 | 20987.5 | 0 | 0.3307% | 0% |  |  | 0.3307% | 0% | 0.3307% | 3 | TRUE
BEARDS_7_UNIT 1 | Hydro | 2023 | 1825 | 66.0233 | 0 | 20987.5 | 0 | 0.3146% | 0% |  |  | 0.3146% | 0% | 0.3146% | 2 | TRUE
BEARDS_7_UNIT 1 | Hydro | 2024 | 1830 | 57.5 | 0 | 21045 | 0 | 0.2732% | 0% |  |  | 0.2732% | 0% | 0.2732% | 1 | TRUE
BELDEN_7_UNIT 1 | Hydro | 2022 | 1825 | 74656.2753 | 0 | 217175 | 0 | 34.38% | 0% |  |  | 34.38% | 0% | 34.38% | 2 | TRUE
BELDEN_7_UNIT 1 | Hydro | 2023 | 1825 | 124228.9447 | 0 | 217175 | 0 | 57.2% | 0% |  |  | 57.2% | 0% | 57.2% | 3 | TRUE
BELDEN_7_UNIT 1 | Hydro | 2024 | 1830 | 61004.9995 | 0 | 217770 | 0 | 28.01% | 0% |  |  | 28.01% | 0% | 28.01% | 1 | TRUE
BIGCRK_2_EXESWD | Hydro | 2022 | 1825 | 392927.3667 | 0 | 1496500 | 0 | 26.26% | 0% |  |  | 26.26% | 0% | 26.26% | 2 | TRUE
BIGCRK_2_EXESWD | Hydro | 2023 | 1825 | 419525.605 | 0 | 1496500 | 0 | 28.03% | 0% |  |  | 28.03% | 0% | 28.03% | 3 | TRUE
BIGCRK_2_EXESWD | Hydro | 2024 | 1830 | 333676.8833 | 0 | 1500600 | 0 | 22.24% | 0% |  |  | 22.24% | 0% | 22.24% | 1 | TRUE
BLACK_7_UNIT 1 | Hydro | 2022 | 1825 | 4749.0733 | 0 | 155125 | 0 | 3.061% | 0% |  |  | 3.061% | 0% | 3.061% | 1 | TRUE
BLACK_7_UNIT 1 | Hydro | 2023 | 1825 | 9088.9333 | 115 | 155125 | 0 | 5.859% | 0.07413% |  |  | 5.859% | 0.07413% | 5.933% | 3 | TRUE
BLACK_7_UNIT 1 | Hydro | 2024 | 1830 | 7703.4383 | 0 | 155550 | 0 | 4.952% | 0% |  |  | 4.952% | 0% | 4.952% | 2 | TRUE
BLACK_7_UNIT 2 | Hydro | 2022 | 1825 | 4494.4067 | 44.1 | 153482.5 | 0 | 2.928% | 0.02873% |  |  | 2.928% | 0.02873% | 2.957% | 2 | TRUE
BLACK_7_UNIT 2 | Hydro | 2023 | 1825 | 4375.7183 | 0 | 153482.5 | 0 | 2.851% | 0% |  |  | 2.851% | 0% | 2.851% | 1 | TRUE
BLACK_7_UNIT 2 | Hydro | 2024 | 1830 | 6065.9567 | 0 | 153903 | 0 | 3.941% | 0% |  |  | 3.941% | 0% | 3.941% | 3 | TRUE
BLCKBT_2_STONEY | Hydro | 2022 | 1825 | 5806.0933 | 0 | 11315 | 0 | 51.31% | 0% |  |  | 51.31% | 0% | 51.31% | 3 | TRUE
BLCKBT_2_STONEY | Hydro | 2023 | 1825 | 1653.23 | 0 | 11315 | 0 | 14.61% | 0% |  |  | 14.61% | 0% | 14.61% | 1 | TRUE
BLCKBT_2_STONEY | Hydro | 2024 | 1830 | 5169.25 | 0 | 11346 | 0 | 45.56% | 0% |  |  | 45.56% | 0% | 45.56% | 2 | TRUE
BUCKCK_7_PL1X2 | Hydro | 2022 | 1825 | 3865.4067 | 47.2452 | 104481.25 | 0 | 3.7% | 0.04522% |  |  | 3.7% | 0.04522% | 3.745% | 1 | TRUE
BUCKCK_7_PL1X2 | Hydro | 2023 | 1825 | 4020.2267 | 14.75 | 104481.25 | 0 | 3.848% | 0.01412% |  |  | 3.848% | 0.01412% | 3.862% | 2 | TRUE
BUCKCK_7_PL1X2 | Hydro | 2024 | 1830 | 5690.8867 | 0 | 104767.5 | 0 | 5.432% | 0% |  |  | 5.432% | 0% | 5.432% | 3 | TRUE
BUTTVL_7_UNIT 1 | Hydro | 2022 | 1825 | 650.0017 | 0 | 72087.5 | 0 | 0.9017% | 0% |  |  | 0.9017% | 0% | 0.9017% | 1 | TRUE
BUTTVL_7_UNIT 1 | Hydro | 2023 | 1825 | 6183.725 | 0 | 72087.5 | 0 | 8.578% | 0% |  |  | 8.578% | 0% | 8.578% | 3 | TRUE
BUTTVL_7_UNIT 1 | Hydro | 2024 | 1830 | 858.4667 | 0 | 72285 | 0 | 1.188% | 0% |  |  | 1.188% | 0% | 1.188% | 2 | TRUE
CAMPFW_7_FARWST | Hydro | 2022 | 1825 | 1332.8 | 0 | 12410 | 0 | 10.74% | 0% |  |  | 10.74% | 0% | 10.74% | 2 | TRUE
CAMPFW_7_FARWST | Hydro | 2023 | 1825 | 3739.5467 | 0 | 12410 | 0 | 30.13% | 0% |  |  | 30.13% | 0% | 30.13% | 3 | TRUE
CAMPFW_7_FARWST | Hydro | 2024 | 1830 | 782 | 0 | 12444 | 0 | 6.284% | 0% |  |  | 6.284% | 0% | 6.284% | 1 | TRUE
CARBOU_7_PL2X3 | Hydro | 2022 | 1825 | 40591.67 | 0 | 89425 | 0 | 45.39% | 0% |  |  | 45.39% | 0% | 45.39% | 3 | TRUE
CARBOU_7_PL2X3 | Hydro | 2023 | 1825 | 11222.806 | 0 | 89425 | 0 | 12.55% | 0% |  |  | 12.55% | 0% | 12.55% | 1 | TRUE
CARBOU_7_PL2X3 | Hydro | 2024 | 1830 | 15749.1527 | 0 | 89670 | 0 | 17.56% | 0% |  |  | 17.56% | 0% | 17.56% | 2 | TRUE
CARBOU_7_PL4X5 | Hydro | 2022 | 1825 | 73530.3747 | 0 | 219000 | 0 | 33.58% | 0% |  |  | 33.58% | 0% | 33.58% | 2 | TRUE
CARBOU_7_PL4X5 | Hydro | 2023 | 1825 | 21641.8125 | 0 | 219000 | 0 | 9.882% | 0% |  |  | 9.882% | 0% | 9.882% | 1 | TRUE
CARBOU_7_PL4X5 | Hydro | 2024 | 1830 | 85025.2193 | 0 | 219600 | 0 | 38.72% | 0% |  |  | 38.72% | 0% | 38.72% | 3 | TRUE
CARBOU_7_UNIT 1 | Hydro | 2022 | 1825 | 8425.9667 | 0 | 43800 | 0 | 19.24% | 0% |  |  | 19.24% | 0% | 19.24% | 2 | TRUE
CARBOU_7_UNIT 1 | Hydro | 2023 | 1825 | 16400.5 | 0 | 43800 | 0 | 37.44% | 0% |  |  | 37.44% | 0% | 37.44% | 3 | TRUE
CARBOU_7_UNIT 1 | Hydro | 2024 | 1830 | 3462.4733 | 0 | 43920 | 0 | 7.884% | 0% |  |  | 7.884% | 0% | 7.884% | 1 | TRUE
CENTER_2_RHONDO | Hydro | 2022 | 1825 | 3025.7 | 0 | 3485.75 | 0 | 86.8% | 0% |  |  | 86.8% | 0% | 86.8% | 2 | TRUE
CENTER_2_RHONDO | Hydro | 2023 | 1825 | 3258.9083 | 0 | 3485.75 | 0 | 93.49% | 0% |  |  | 93.49% | 0% | 93.49% | 3 | TRUE
CENTER_2_RHONDO | Hydro | 2024 | 1830 | 0 | 0 | 3495.3 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
CHICPK_7_UNIT 1 | Hydro | 2022 | 1825 | 30203.3017 | 0 | 76650 | 0 | 39.4% | 0% |  |  | 39.4% | 0% | 39.4% | 2 | TRUE
CHICPK_7_UNIT 1 | Hydro | 2023 | 1825 | 27219.3402 | 0 | 76650 | 0 | 35.51% | 0% |  |  | 35.51% | 0% | 35.51% | 1 | TRUE
CHICPK_7_UNIT 1 | Hydro | 2024 | 1830 | 47358.9 | 0 | 76860 | 0 | 61.62% | 0% |  |  | 61.62% | 0% | 61.62% | 3 | TRUE
COLGAT_7_UNIT 1 | Hydro | 2022 | 1825 | 43391.2033 | 0 | 322514 | 0 | 13.45% | 0% |  |  | 13.45% | 0% | 13.45% | 3 | TRUE
COLGAT_7_UNIT 1 | Hydro | 2023 | 1825 | 35707.4433 | 0 | 322514 | 0 | 11.07% | 0% |  |  | 11.07% | 0% | 11.07% | 1 | TRUE
COLGAT_7_UNIT 1 | Hydro | 2024 | 1830 | 40374.2 | 0 | 323397.6 | 0 | 12.48% | 0% |  |  | 12.48% | 0% | 12.48% | 2 | TRUE
COLGAT_7_UNIT 2 | Hydro | 2022 | 1825 | 38678.5167 | 0 | 320597.75 | 0 | 12.06% | 0% |  |  | 12.06% | 0% | 12.06% | 3 | TRUE
COLGAT_7_UNIT 2 | Hydro | 2023 | 1825 | 36151.1067 | 0 | 320597.75 | 0 | 11.28% | 0% |  |  | 11.28% | 0% | 11.28% | 1 | TRUE
COLGAT_7_UNIT 2 | Hydro | 2024 | 1830 | 37288.2167 | 0 | 321476.1 | 0 | 11.6% | 0% |  |  | 11.6% | 0% | 11.6% | 2 | TRUE
COLVIL_7_PL1X2 | Hydro | 2022 | 1825 | 2088.5857 | 0 | 450519.5 | 0 | 0.4636% | 0% |  |  | 0.4636% | 0% | 0.4636% | 1 | TRUE
COLVIL_7_PL1X2 | Hydro | 2023 | 1825 | 2115.3647 | 0 | 450519.5 | 0 | 0.4695% | 0% |  |  | 0.4695% | 0% | 0.4695% | 2 | TRUE
COLVIL_7_PL1X2 | Hydro | 2024 | 1830 | 39406.016 | 0 | 451753.8 | 0 | 8.723% | 0% |  |  | 8.723% | 0% | 8.723% | 3 | TRUE
CONTRL_1_POOLE | Hydro | 2022 | 1825 | 12341.7233 | 640.24 | 20202.75 | 0 | 61.09% | 3.169% |  |  | 61.09% | 3.169% | 64.26% | 3 | TRUE
CONTRL_1_POOLE | Hydro | 2023 | 1825 | 9149.3883 | 0 | 20202.75 | 0 | 45.29% | 0% |  |  | 45.29% | 0% | 45.29% | 2 | TRUE
CONTRL_1_POOLE | Hydro | 2024 | 1830 | 5356.56 | 0 | 20258.1 | 0 | 26.44% | 0% |  |  | 26.44% | 0% | 26.44% | 1 | TRUE
CONTRL_1_RUSHCK | Hydro | 2022 | 1825 | 8038.02 | 1063.9 | 22246.75 | 0 | 36.13% | 4.782% |  |  | 36.13% | 4.782% | 40.91% | 2 | TRUE
CONTRL_1_RUSHCK | Hydro | 2023 | 1825 | 10950.37 | 0 | 22246.75 | 0 | 49.22% | 0% |  |  | 49.22% | 0% | 49.22% | 3 | TRUE
CONTRL_1_RUSHCK | Hydro | 2024 | 1830 | 3500.8 | 0 | 22307.7 | 0 | 15.69% | 0% |  |  | 15.69% | 0% | 15.69% | 1 | TRUE
COVERD_2_QFUNTS | Hydro | 2022 | 1825 | 62.8833 | 0 | 10037.5 | 0 | 0.6265% | 0% |  |  | 0.6265% | 0% | 0.6265% | 2 | TRUE
COVERD_2_QFUNTS | Hydro | 2023 | 1825 | 93.8667 | 0 | 10037.5 | 0 | 0.9352% | 0% |  |  | 0.9352% | 0% | 0.9352% | 3 | TRUE
COVERD_2_QFUNTS | Hydro | 2024 | 1830 | 52.475 | 0 | 10065 | 0 | 0.5214% | 0% |  |  | 0.5214% | 0% | 0.5214% | 1 | TRUE
CRESTA_7_PL1X2 | Hydro | 2022 | 1825 | 40503.0162 | 0 | 128480 | 0 | 31.52% | 0% |  |  | 31.52% | 0% | 31.52% | 3 | TRUE
CRESTA_7_PL1X2 | Hydro | 2023 | 1825 | 21262.855 | 0 | 128480 | 0 | 16.55% | 0% |  |  | 16.55% | 0% | 16.55% | 1 | TRUE
CRESTA_7_PL1X2 | Hydro | 2024 | 1830 | 36591.1652 | 0 | 128832 | 0 | 28.4% | 0% |  |  | 28.4% | 0% | 28.4% | 2 | TRUE
DONNLS_7_UNIT | Hydro | 2022 | 1825 | 1145 | 0 | 131400 | 0 | 0.8714% | 0% |  |  | 0.8714% | 0% | 0.8714% | 1 | TRUE
DONNLS_7_UNIT | Hydro | 2023 | 1825 | 5426.7 | 0 | 131400 | 0 | 4.13% | 0% |  |  | 4.13% | 0% | 4.13% | 3 | TRUE
DONNLS_7_UNIT | Hydro | 2024 | 1830 | 3851.0167 | 0 | 131760 | 0 | 2.923% | 0% |  |  | 2.923% | 0% | 2.923% | 2 | TRUE
DRUM_7_PL1X2 | Hydro | 2022 | 1825 | 13719.7167 | 0 | 47450 | 0 | 28.91% | 0% |  |  | 28.91% | 0% | 28.91% | 2 | TRUE
DRUM_7_PL1X2 | Hydro | 2023 | 1825 | 4414.2 | 0 | 47450 | 0 | 9.303% | 0% |  |  | 9.303% | 0% | 9.303% | 1 | TRUE
DRUM_7_PL1X2 | Hydro | 2024 | 1830 | 29236.5167 | 0 | 47580 | 0 | 61.45% | 0% |  |  | 61.45% | 0% | 61.45% | 3 | TRUE
DRUM_7_PL3X4 | Hydro | 2022 | 1825 | 23465.2833 | 0 | 52742.5 | 0 | 44.49% | 0% |  |  | 44.49% | 0% | 44.49% | 2 | TRUE
DRUM_7_PL3X4 | Hydro | 2023 | 1825 | 17922.2683 | 0 | 52742.5 | 0 | 33.98% | 0% |  |  | 33.98% | 0% | 33.98% | 1 | TRUE
DRUM_7_PL3X4 | Hydro | 2024 | 1830 | 32576.2133 | 0 | 52887 | 0 | 61.6% | 0% |  |  | 61.6% | 0% | 61.6% | 3 | TRUE
DRUM_7_UNIT 5 | Hydro | 2022 | 1825 | 6770.7467 | 0 | 91250 | 0 | 7.42% | 0% |  |  | 7.42% | 0% | 7.42% | 2 | TRUE
DRUM_7_UNIT 5 | Hydro | 2023 | 1825 | 3786.5 | 0 | 91250 | 0 | 4.15% | 0% |  |  | 4.15% | 0% | 4.15% | 1 | TRUE
DRUM_7_UNIT 5 | Hydro | 2024 | 1830 | 37905.2333 | 0 | 91500 | 0 | 41.43% | 0% |  |  | 41.43% | 0% | 41.43% | 3 | TRUE
DUTCH1_7_UNIT 1 | Hydro | 2022 | 1825 | 5603.79 | 0 | 40150 | 0 | 13.96% | 0% |  |  | 13.96% | 0% | 13.96% | 2 | TRUE
DUTCH1_7_UNIT 1 | Hydro | 2023 | 1825 | 5291.6367 | 0 | 40150 | 0 | 13.18% | 0% |  |  | 13.18% | 0% | 13.18% | 1 | TRUE
DUTCH1_7_UNIT 1 | Hydro | 2024 | 1830 | 14715.4817 | 0 | 40260 | 0 | 36.55% | 0% |  |  | 36.55% | 0% | 36.55% | 3 | TRUE
DUTCH2_7_UNIT 1 | Hydro | 2022 | 1825 | 22756.6167 | 0 | 47450 | 0 | 47.96% | 0% |  |  | 47.96% | 0% | 47.96% | 2 | TRUE
DUTCH2_7_UNIT 1 | Hydro | 2023 | 1825 | 17204.0667 | 84.0667 | 47450 | 0 | 36.26% | 0.1772% |  |  | 36.26% | 0.1772% | 36.43% | 1 | TRUE
DUTCH2_7_UNIT 1 | Hydro | 2024 | 1830 | 29335.4667 | 0 | 47580 | 0 | 61.66% | 0% |  |  | 61.66% | 0% | 61.66% | 3 | TRUE
DVLCYN_1_UNITS | Hydro | 2022 | 1825 | 7772.3333 | 0 | 428875 | 0 | 1.812% | 0% |  |  | 1.812% | 0% | 1.812% | 2 | TRUE
DVLCYN_1_UNITS | Hydro | 2023 | 1825 | 4792.15 | 0 | 428875 | 0 | 1.117% | 0% |  |  | 1.117% | 0% | 1.117% | 1 | TRUE
DVLCYN_1_UNITS | Hydro | 2024 | 1830 | 13239.6333 | 0 | 430050 | 0 | 3.079% | 0% |  |  | 3.079% | 0% | 3.079% | 3 | TRUE
ELECTR_7_PL1X3 | Hydro | 2022 | 1825 | 10627.03 | 0 | 169725 | 0 | 6.261% | 0% |  |  | 6.261% | 0% | 6.261% | 1 | TRUE
ELECTR_7_PL1X3 | Hydro | 2023 | 1825 | 18242.2183 | 0 | 169725 | 0 | 10.75% | 0% |  |  | 10.75% | 0% | 10.75% | 3 | TRUE
ELECTR_7_PL1X3 | Hydro | 2024 | 1830 | 15609.6533 | 0 | 170190 | 0 | 9.172% | 0% |  |  | 9.172% | 0% | 9.172% | 2 | TRUE
ELKCRK_6_STONYG | Hydro | 2022 | 1825 | 5303.3517 | 0 | 8942.5 | 0 | 59.31% | 0% |  |  | 59.31% | 0% | 59.31% | 3 | TRUE
ELKCRK_6_STONYG | Hydro | 2023 | 1825 | 3796.0367 | 0 | 8942.5 | 0 | 42.45% | 0% |  |  | 42.45% | 0% | 42.45% | 2 | TRUE
ELKCRK_6_STONYG | Hydro | 2024 | 1830 | 3732.4983 | 0 | 8967 | 0 | 41.62% | 0% |  |  | 41.62% | 0% | 41.62% | 1 | TRUE
EXCHEC_7_UNIT 1 | Hydro | 2022 | 1825 | 52437.95 | 0 | 172462.5 | 0 | 30.41% | 0% |  |  | 30.41% | 0% | 30.41% | 3 | TRUE
EXCHEC_7_UNIT 1 | Hydro | 2023 | 1825 | 31406.3 | 0 | 172462.5 | 0 | 18.21% | 0% |  |  | 18.21% | 0% | 18.21% | 2 | TRUE
EXCHEC_7_UNIT 1 | Hydro | 2024 | 1830 | 86.625 | 23.625 | 172935 | 0 | 0.05009% | 0.01366% |  |  | 0.05009% | 0.01366% | 0.06375% | 1 | TRUE
FMEADO_7_UNIT | Hydro | 2022 | 1825 | 59.2 | 0 | 29200 | 0 | 0.2027% | 0% |  |  | 0.2027% | 0% | 0.2027% | 1 | TRUE
FMEADO_7_UNIT | Hydro | 2023 | 1825 | 2300.7 | 0 | 29200 | 0 | 7.879% | 0% |  |  | 7.879% | 0% | 7.879% | 3 | TRUE
FMEADO_7_UNIT | Hydro | 2024 | 1830 | 1832.8 | 0 | 29280 | 0 | 6.26% | 0% |  |  | 6.26% | 0% | 6.26% | 2 | TRUE
FORBST_7_UNIT 1 | Hydro | 2022 | 1825 | 32.75 | 0 | 68437.5 | 0 | 0.04785% | 0% |  |  | 0.04785% | 0% | 0.04785% | 1 | TRUE
FORBST_7_UNIT 1 | Hydro | 2023 | 1825 | 2817.5333 | 0 | 68437.5 | 0 | 4.117% | 0% |  |  | 4.117% | 0% | 4.117% | 3 | TRUE
FORBST_7_UNIT 1 | Hydro | 2024 | 1830 | 284.375 | 0 | 68625 | 0 | 0.4144% | 0% |  |  | 0.4144% | 0% | 0.4144% | 2 | TRUE
GRIZLY_1_UNIT 1 | Hydro | 2022 | 1825 | 0 | 0 | 36500 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
GRIZLY_1_UNIT 1 | Hydro | 2023 | 1825 | 3 | 0 | 36500 | 0 | 0.008219% | 0% |  |  | 0.008219% | 0% | 0.008219% | 2 | TRUE
GRIZLY_1_UNIT 1 | Hydro | 2024 | 1830 | 4747.51 | 0 | 36600 | 0 | 12.97% | 0% |  |  | 12.97% | 0% | 12.97% | 3 | TRUE
HAASPH_7_PL1X2 | Hydro | 2022 | 1825 | 14859.7 | 0 | 262800 | 0 | 5.654% | 0% |  |  | 5.654% | 0% | 5.654% | 3 | TRUE
HAASPH_7_PL1X2 | Hydro | 2023 | 1825 | 10851.85 | 0 | 262800 | 0 | 4.129% | 0% |  |  | 4.129% | 0% | 4.129% | 2 | TRUE
HAASPH_7_PL1X2 | Hydro | 2024 | 1830 | 7732.6333 | 0 | 263520 | 0 | 2.934% | 0% |  |  | 2.934% | 0% | 2.934% | 1 | TRUE
HALSEY_6_UNIT | Hydro | 2022 | 1825 | 2355.008 | 0 | 24637.5 | 0 | 9.559% | 0% |  |  | 9.559% | 0% | 9.559% | 3 | TRUE
HALSEY_6_UNIT | Hydro | 2023 | 1825 | 0 | 0 | 24637.5 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
HALSEY_6_UNIT | Hydro | 2024 | 1830 | 1651.325 | 0 | 24705 | 0 | 6.684% | 0% |  |  | 6.684% | 0% | 6.684% | 2 | TRUE
HYTTHM_2_UNITS | Hydro | 2022 | 1825 | 208433.2633 | 0 | 1702907.5 | 0 | 12.24% | 0% |  |  | 12.24% | 0% | 12.24% | 2 | TRUE
HYTTHM_2_UNITS | Hydro | 2023 | 1825 | 210071.0983 | 0 | 1702907.5 | 0 | 12.34% | 0% |  |  | 12.34% | 0% | 12.34% | 3 | TRUE
HYTTHM_2_UNITS | Hydro | 2024 | 1830 | 172199.0317 | 0 | 1707573 | 0 | 10.08% | 0% |  |  | 10.08% | 0% | 10.08% | 1 | TRUE
INTKEP_2_UNITS | Hydro | 2022 | 1825 | 112025.8667 | 0 | 739125 | 0 | 15.16% | 0% |  |  | 15.16% | 0% | 15.16% | 1 | TRUE
INTKEP_2_UNITS | Hydro | 2023 | 1825 | 174937.8667 | 0 | 739125 | 0 | 23.67% | 0% |  |  | 23.67% | 0% | 23.67% | 3 | TRUE
INTKEP_2_UNITS | Hydro | 2024 | 1830 | 174595.1833 | 0 | 741150 | 0 | 23.56% | 0% |  |  | 23.56% | 0% | 23.56% | 2 | TRUE
KELYRG_6_UNIT | Hydro | 2022 | 1825 | 171.125 | 0 | 20075 | 0 | 0.8524% | 0% |  |  | 0.8524% | 0% | 0.8524% | 1 | TRUE
KELYRG_6_UNIT | Hydro | 2023 | 1825 | 1309.22 | 0 | 20075 | 0 | 6.522% | 0% |  |  | 6.522% | 0% | 6.522% | 3 | TRUE
KELYRG_6_UNIT | Hydro | 2024 | 1830 | 198 | 0 | 20130 | 0 | 0.9836% | 0% |  |  | 0.9836% | 0% | 0.9836% | 2 | TRUE
KERKH2_7_UNIT 1 | Hydro | 2022 | 1825 | 40286.3205 | 575.94 | 280867.5 | 0 | 14.34% | 0.2051% |  |  | 14.34% | 0.2051% | 14.55% | 1 | TRUE
KERKH2_7_UNIT 1 | Hydro | 2023 | 1825 | 53095.3502 | 0 | 280867.5 | 0 | 18.9% | 0% |  |  | 18.9% | 0% | 18.9% | 3 | TRUE
KERKH2_7_UNIT 1 | Hydro | 2024 | 1830 | 49135.1372 | 1618.0922 | 281637 | 0 | 17.45% | 0.5745% |  |  | 17.45% | 0.5745% | 18.02% | 2 | TRUE
KINGRV_7_UNIT 1 | Hydro | 2022 | 1825 | 3689.65 | 0 | 93440 | 0 | 3.949% | 0% |  |  | 3.949% | 0% | 3.949% | 1 | TRUE
KINGRV_7_UNIT 1 | Hydro | 2023 | 1825 | 4452.95 | 0 | 93440 | 0 | 4.766% | 0% |  |  | 4.766% | 0% | 4.766% | 2 | TRUE
KINGRV_7_UNIT 1 | Hydro | 2024 | 1830 | 5701.2833 | 17.2667 | 93696 | 0 | 6.085% | 0.01843% |  |  | 6.085% | 0.01843% | 6.103% | 3 | TRUE
MCSWAN_6_UNITS | Hydro | 2022 | 1825 | 4936.35 | 0 | 16425 | 0 | 30.05% | 0% |  |  | 30.05% | 0% | 30.05% | 3 | TRUE
MCSWAN_6_UNITS | Hydro | 2023 | 1825 | 180 | 0 | 16425 | 0 | 1.096% | 0% |  |  | 1.096% | 0% | 1.096% | 2 | TRUE
MCSWAN_6_UNITS | Hydro | 2024 | 1830 | 25.65 | 0 | 16470 | 0 | 0.1557% | 0% |  |  | 0.1557% | 0% | 0.1557% | 1 | TRUE
MDFKRL_2_PROJCT | Hydro | 2022 | 1825 | 13928.1 | 0 | 383250 | 0 | 3.634% | 0% |  |  | 3.634% | 0% | 3.634% | 2 | TRUE
MDFKRL_2_PROJCT | Hydro | 2023 | 1825 | 27363.7833 | 0 | 383250 | 0 | 7.14% | 0% |  |  | 7.14% | 0% | 7.14% | 3 | TRUE
MDFKRL_2_PROJCT | Hydro | 2024 | 1830 | 8518.8167 | 64.6667 | 384300 | 0 | 2.217% | 0.01683% |  |  | 2.217% | 0.01683% | 2.234% | 1 | TRUE
MERCFL_6_UNIT | Hydro | 2022 | 1825 | 995.6333 | 0 | 6387.5 | 0 | 15.59% | 0% |  |  | 15.59% | 0% | 15.59% | 2 | TRUE
MERCFL_6_UNIT | Hydro | 2023 | 1825 | 820.0917 | 0 | 6387.5 | 0 | 12.84% | 0% |  |  | 12.84% | 0% | 12.84% | 1 | TRUE
MERCFL_6_UNIT | Hydro | 2024 | 1830 | 1050 | 0 | 6405 | 0 | 16.39% | 0% |  |  | 16.39% | 0% | 16.39% | 3 | TRUE
MIRLOM_7_MWDLKM | Hydro | 2022 | 1825 | 77.1667 | 0 | 9125 | 0 | 0.8457% | 0% |  |  | 0.8457% | 0% | 0.8457% | 1 | TRUE
MIRLOM_7_MWDLKM | Hydro | 2023 | 1825 | 3894.9167 | 0 | 9125 | 0 | 42.68% | 0% |  |  | 42.68% | 0% | 42.68% | 3 | TRUE
MIRLOM_7_MWDLKM | Hydro | 2024 | 1830 | 455.4167 | 0 | 9150 | 0 | 4.977% | 0% |  |  | 4.977% | 0% | 4.977% | 2 | TRUE
MOJAVE_1_SIPHON | Hydro | 2022 | 1825 | 188.8567 | 0 | 26207 | 0 | 0.7206% | 0% |  |  | 0.7206% | 0% | 0.7206% | 1 | TRUE
MOJAVE_1_SIPHON | Hydro | 2023 | 1825 | 2795.02 | 0 | 26207 | 0 | 10.67% | 0% |  |  | 10.67% | 0% | 10.67% | 3 | TRUE
MOJAVE_1_SIPHON | Hydro | 2024 | 1830 | 683.0553 | 0 | 26278.8 | 0 | 2.599% | 0% |  |  | 2.599% | 0% | 2.599% | 2 | TRUE
NAROW1_2_UNIT | Hydro | 2022 | 1825 | 6159.1267 | 0 | 21900 | 0 | 28.12% | 0% |  |  | 28.12% | 0% | 28.12% | 3 | TRUE
NAROW1_2_UNIT | Hydro | 2023 | 1825 | 4830.9683 | 0 | 21900 | 0 | 22.06% | 0% |  |  | 22.06% | 0% | 22.06% | 1 | TRUE
NAROW1_2_UNIT | Hydro | 2024 | 1830 | 5035.2667 | 0 | 21960 | 0 | 22.93% | 0% |  |  | 22.93% | 0% | 22.93% | 2 | TRUE
NAROW2_2_UNIT | Hydro | 2022 | 1825 | 81322.575 | 0 | 100375 | 0 | 81.02% | 0% |  |  | 81.02% | 0% | 81.02% | 3 | TRUE
NAROW2_2_UNIT | Hydro | 2023 | 1825 | 39986.02 | 0 | 100375 | 0 | 39.84% | 0% |  |  | 39.84% | 0% | 39.84% | 1 | TRUE
NAROW2_2_UNIT | Hydro | 2024 | 1830 | 52159.655 | 0 | 100650 | 0 | 51.82% | 0% |  |  | 51.82% | 0% | 51.82% | 2 | TRUE
OLINDA_2_COYCRK | Hydro | 2022 | 1825 | 5696.6 | 0 | 5712.25 | 0 | 99.73% | 0% |  |  | 99.73% | 0% | 99.73% | 2 | TRUE
OLINDA_2_COYCRK | Hydro | 2023 | 1825 | 5696.6 | 0 | 5712.25 | 0 | 99.73% | 0% |  |  | 99.73% | 0% | 99.73% | 2 | TRUE
OLINDA_2_COYCRK | Hydro | 2024 | 1830 | 0 | 0 | 5727.9 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
PADUA_6_MWDSDM | Hydro | 2022 | 1825 | 49.5 | 0 | 18067.5 | 0 | 0.274% | 0% |  |  | 0.274% | 0% | 0.274% | 2 | TRUE
PADUA_6_MWDSDM | Hydro | 2023 | 1825 | 420.5 | 0 | 18067.5 | 0 | 2.327% | 0% |  |  | 2.327% | 0% | 2.327% | 3 | TRUE
PADUA_6_MWDSDM | Hydro | 2024 | 1830 | 0 | 0 | 18117 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
PADUA_7_SDIMAS | Hydro | 2022 | 1825 | 0 | 0 | 1916.25 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
PADUA_7_SDIMAS | Hydro | 2023 | 1825 | 381.325 | 0 | 1916.25 | 0 | 19.9% | 0% |  |  | 19.9% | 0% | 19.9% | 2 | TRUE
PADUA_7_SDIMAS | Hydro | 2024 | 1830 | 1002.75 | 0 | 1921.5 | 0 | 52.19% | 0% |  |  | 52.19% | 0% | 52.19% | 3 | TRUE
PARDEB_6_UNITS | Hydro | 2022 | 1825 | 13988.6 | 0 | 54750 | 0 | 25.55% | 0% |  |  | 25.55% | 0% | 25.55% | 3 | TRUE
PARDEB_6_UNITS | Hydro | 2023 | 1825 | 5253.2917 | 0 | 54750 | 0 | 9.595% | 0% |  |  | 9.595% | 0% | 9.595% | 2 | TRUE
PARDEB_6_UNITS | Hydro | 2024 | 1830 | 4642.3967 | 0 | 54900 | 0 | 8.456% | 0% |  |  | 8.456% | 0% | 8.456% | 1 | TRUE
PINFLT_7_UNITS | Hydro | 2022 | 1825 | 219041.736 | 36082.7833 | 362280.75 | 0 | 60.46% | 9.96% |  |  | 60.46% | 9.96% | 70.42% | 3 | TRUE
PINFLT_7_UNITS | Hydro | 2023 | 1825 | 115477.8283 | 0 | 362280.75 | 0 | 31.88% | 0% |  |  | 31.88% | 0% | 31.88% | 2 | TRUE
PINFLT_7_UNITS | Hydro | 2024 | 1830 | 74451.4835 | 0 | 363273.3 | 0 | 20.49% | 0% |  |  | 20.49% | 0% | 20.49% | 1 | TRUE
PIT1_7_UNIT 1 | Hydro | 2022 | 1825 | 12514 | 0 | 58400 | 0 | 21.43% | 0% |  |  | 21.43% | 0% | 21.43% | 2 | TRUE
PIT1_7_UNIT 1 | Hydro | 2023 | 1825 | 25087.5667 | 0 | 58400 | 0 | 42.96% | 0% |  |  | 42.96% | 0% | 42.96% | 3 | TRUE
PIT1_7_UNIT 1 | Hydro | 2024 | 1830 | 607.3 | 0 | 58560 | 0 | 1.037% | 0% |  |  | 1.037% | 0% | 1.037% | 1 | TRUE
PIT1_7_UNIT 2 | Hydro | 2022 | 1825 | 209.0333 | 0 | 58400 | 0 | 0.3579% | 0% |  |  | 0.3579% | 0% | 0.3579% | 1 | TRUE
PIT1_7_UNIT 2 | Hydro | 2023 | 1825 | 259.3833 | 0 | 58400 | 0 | 0.4441% | 0% |  |  | 0.4441% | 0% | 0.4441% | 2 | TRUE
PIT1_7_UNIT 2 | Hydro | 2024 | 1830 | 467.455 | 0 | 58560 | 0 | 0.7982% | 0% |  |  | 0.7982% | 0% | 0.7982% | 3 | TRUE
PIT3_7_PL1X3 | Hydro | 2022 | 1825 | 24822.5533 | 8.51 | 128845 | 0 | 19.27% | 0.006605% |  |  | 19.27% | 0.006605% | 19.27% | 3 | TRUE
PIT3_7_PL1X3 | Hydro | 2023 | 1825 | 1032.4933 | 0 | 128845 | 0 | 0.8013% | 0% |  |  | 0.8013% | 0% | 0.8013% | 2 | TRUE
PIT3_7_PL1X3 | Hydro | 2024 | 1830 | 833.9867 | 11.9467 | 129198 | 0 | 0.6455% | 0.009247% |  |  | 0.6455% | 0.009247% | 0.6548% | 1 | TRUE
PIT4_7_PL1X2 | Hydro | 2022 | 1825 | 2113.65 | 4.7 | 173375 | 0 | 1.219% | 0.002711% |  |  | 1.219% | 0.002711% | 1.222% | 3 | TRUE
PIT4_7_PL1X2 | Hydro | 2023 | 1825 | 1583.65 | 0 | 173375 | 0 | 0.9134% | 0% |  |  | 0.9134% | 0% | 0.9134% | 2 | TRUE
PIT4_7_PL1X2 | Hydro | 2024 | 1830 | 1560.3783 | 0 | 173850 | 0 | 0.8975% | 0% |  |  | 0.8975% | 0% | 0.8975% | 1 | TRUE
PIT5_7_PL1X2 | Hydro | 2022 | 1825 | 1312.2833 | 0 | 149650 | 0 | 0.8769% | 0% |  |  | 0.8769% | 0% | 0.8769% | 1 | TRUE
PIT5_7_PL1X2 | Hydro | 2023 | 1825 | 3024.45 | 1.3333 | 149650 | 0 | 2.021% | 0.000891% |  |  | 2.021% | 0.000891% | 2.022% | 2 | TRUE
PIT5_7_PL1X2 | Hydro | 2024 | 1830 | 3729.8833 | 0 | 150060 | 0 | 2.486% | 0% |  |  | 2.486% | 0% | 2.486% | 3 | TRUE
PIT5_7_PL3X4 | Hydro | 2022 | 1825 | 20582.03 | 0 | 149650 | 0 | 13.75% | 0% |  |  | 13.75% | 0% | 13.75% | 3 | TRUE
PIT5_7_PL3X4 | Hydro | 2023 | 1825 | 2744.6833 | 0 | 149650 | 0 | 1.834% | 0% |  |  | 1.834% | 0% | 1.834% | 2 | TRUE
PIT5_7_PL3X4 | Hydro | 2024 | 1830 | 1444.3667 | 0 | 150060 | 0 | 0.9625% | 0% |  |  | 0.9625% | 0% | 0.9625% | 1 | TRUE
PIT6_7_UNIT 1 | Hydro | 2022 | 1825 | 2314.4075 | 0 | 71175 | 0 | 3.252% | 0% |  |  | 3.252% | 0% | 3.252% | 1 | TRUE
PIT6_7_UNIT 1 | Hydro | 2023 | 1825 | 2410.5418 | 0 | 71175 | 0 | 3.387% | 0% |  |  | 3.387% | 0% | 3.387% | 2 | TRUE
PIT6_7_UNIT 1 | Hydro | 2024 | 1830 | 3054.8628 | 0 | 71370 | 0 | 4.28% | 0% |  |  | 4.28% | 0% | 4.28% | 3 | TRUE
PIT6_7_UNIT 2 | Hydro | 2022 | 1825 | 4114.1565 | 0 | 73000 | 0 | 5.636% | 0% |  |  | 5.636% | 0% | 5.636% | 2 | TRUE
PIT6_7_UNIT 2 | Hydro | 2023 | 1825 | 3234.1732 | 0 | 73000 | 0 | 4.43% | 0% |  |  | 4.43% | 0% | 4.43% | 1 | TRUE
PIT6_7_UNIT 2 | Hydro | 2024 | 1830 | 4231.62 | 0 | 73200 | 0 | 5.781% | 0% |  |  | 5.781% | 0% | 5.781% | 3 | TRUE
PIT7_7_UNIT 1 | Hydro | 2022 | 1825 | 3116.6828 | 0 | 101652.5 | 0 | 3.066% | 0% |  |  | 3.066% | 0% | 3.066% | 2 | TRUE
PIT7_7_UNIT 1 | Hydro | 2023 | 1825 | 2743.0242 | 0 | 101652.5 | 0 | 2.698% | 0% |  |  | 2.698% | 0% | 2.698% | 1 | TRUE
PIT7_7_UNIT 1 | Hydro | 2024 | 1830 | 3818.9457 | 2.3542 | 101931 | 0 | 3.747% | 0.00231% |  |  | 3.747% | 0.00231% | 3.749% | 3 | TRUE
PIT7_7_UNIT 2 | Hydro | 2022 | 1825 | 33530.8767 | 0 | 99645 | 0 | 33.65% | 0% |  |  | 33.65% | 0% | 33.65% | 3 | TRUE
PIT7_7_UNIT 2 | Hydro | 2023 | 1825 | 3922.0845 | 0 | 99645 | 0 | 3.936% | 0% |  |  | 3.936% | 0% | 3.936% | 2 | TRUE
PIT7_7_UNIT 2 | Hydro | 2024 | 1830 | 2178.6097 | 0 | 99918 | 0 | 2.18% | 0% |  |  | 2.18% | 0% | 2.18% | 1 | TRUE
POEPH_7_UNIT 1 | Hydro | 2022 | 1825 | 52645.4828 | 0 | 124100 | 0 | 42.42% | 0% |  |  | 42.42% | 0% | 42.42% | 3 | TRUE
POEPH_7_UNIT 1 | Hydro | 2023 | 1825 | 38979.9145 | 0 | 124100 | 0 | 31.41% | 0% |  |  | 31.41% | 0% | 31.41% | 2 | TRUE
POEPH_7_UNIT 1 | Hydro | 2024 | 1830 | 32884.1312 | 0 | 124440 | 0 | 26.43% | 0% |  |  | 26.43% | 0% | 26.43% | 1 | TRUE
POEPH_7_UNIT 2 | Hydro | 2022 | 1825 | 50088.6172 | 0 | 125012.5 | 0 | 40.07% | 0% |  |  | 40.07% | 0% | 40.07% | 3 | TRUE
POEPH_7_UNIT 2 | Hydro | 2023 | 1825 | 41483.9123 | 0 | 125012.5 | 0 | 33.18% | 0% |  |  | 33.18% | 0% | 33.18% | 2 | TRUE
POEPH_7_UNIT 2 | Hydro | 2024 | 1830 | 25600.3317 | 25.6417 | 125355 | 0 | 20.42% | 0.02046% |  |  | 20.42% | 0.02046% | 20.44% | 1 | TRUE
RCKCRK_7_UNIT 1 | Hydro | 2022 | 1825 | 36082.4905 | 0 | 104025 | 0 | 34.69% | 0% |  |  | 34.69% | 0% | 34.69% | 3 | TRUE
RCKCRK_7_UNIT 1 | Hydro | 2023 | 1825 | 34662.856 | 0 | 104025 | 0 | 33.32% | 0% |  |  | 33.32% | 0% | 33.32% | 2 | TRUE
RCKCRK_7_UNIT 1 | Hydro | 2024 | 1830 | 25071.414 | 0 | 104310 | 0 | 24.04% | 0% |  |  | 24.04% | 0% | 24.04% | 1 | TRUE
RCKCRK_7_UNIT 2 | Hydro | 2022 | 1825 | 52123.3775 | 0 | 103842.5 | 0 | 50.19% | 0% |  |  | 50.19% | 0% | 50.19% | 3 | TRUE
RCKCRK_7_UNIT 2 | Hydro | 2023 | 1825 | 10889.6042 | 0 | 103842.5 | 0 | 10.49% | 0% |  |  | 10.49% | 0% | 10.49% | 1 | TRUE
RCKCRK_7_UNIT 2 | Hydro | 2024 | 1830 | 21044.4982 | 0 | 104127 | 0 | 20.21% | 0% |  |  | 20.21% | 0% | 20.21% | 2 | TRUE
RECTOR_2_QF | Hydro | 2022 | 1825 | 22500.8 | 0 | 36664.25 | 0 | 61.37% | 0% |  |  | 61.37% | 0% | 61.37% | 2 | TRUE
RECTOR_2_QF | Hydro | 2023 | 1825 | 14380.7568 | 0 | 36664.25 | 0 | 39.22% | 0% |  |  | 39.22% | 0% | 39.22% | 1 | TRUE
RECTOR_2_QF | Hydro | 2024 | 1830 | 30817.7252 | 0 | 36764.7 | 0 | 83.82% | 0% |  |  | 83.82% | 0% | 83.82% | 3 | TRUE
ROLLIN_6_UNIT | Hydro | 2022 | 1825 | 8978.6393 | 0 | 24637.5 | 0 | 36.44% | 0% |  |  | 36.44% | 0% | 36.44% | 2 | TRUE
ROLLIN_6_UNIT | Hydro | 2023 | 1825 | 1855.9 | 0 | 24637.5 | 0 | 7.533% | 0% |  |  | 7.533% | 0% | 7.533% | 1 | TRUE
ROLLIN_6_UNIT | Hydro | 2024 | 1830 | 12557.1405 | 0 | 24705 | 0 | 50.83% | 0% |  |  | 50.83% | 0% | 50.83% | 3 | TRUE
SALTSP_7_UNITS | Hydro | 2022 | 1825 | 23398.8317 | 0 | 83950 | 0 | 27.87% | 0% |  |  | 27.87% | 0% | 27.87% | 1 | TRUE
SALTSP_7_UNITS | Hydro | 2023 | 1825 | 24384.3 | 0 | 83950 | 0 | 29.05% | 0% |  |  | 29.05% | 0% | 29.05% | 2 | TRUE
SALTSP_7_UNITS | Hydro | 2024 | 1830 | 28164.7167 | 0 | 84180 | 0 | 33.46% | 0% |  |  | 33.46% | 0% | 33.46% | 3 | TRUE
SAUGUS_6_MWDFTH | Hydro | 2022 | 1825 | 0 | 0 | 16607.5 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
SAUGUS_6_MWDFTH | Hydro | 2023 | 1825 | 944.7317 | 0 | 16607.5 | 0 | 5.689% | 0% |  |  | 5.689% | 0% | 5.689% | 2 | TRUE
SAUGUS_6_MWDFTH | Hydro | 2024 | 1830 | 3321.5 | 0 | 16653 | 0 | 19.95% | 0% |  |  | 19.95% | 0% | 19.95% | 3 | TRUE
SLYCRK_1_UNIT 1 | Hydro | 2022 | 1825 | 1269.4433 | 0 | 23725 | 0 | 5.351% | 0% |  |  | 5.351% | 0% | 5.351% | 3 | TRUE
SLYCRK_1_UNIT 1 | Hydro | 2023 | 1825 | 131.0833 | 0 | 23725 | 0 | 0.5525% | 0% |  |  | 0.5525% | 0% | 0.5525% | 2 | TRUE
SLYCRK_1_UNIT 1 | Hydro | 2024 | 1830 | 72.5833 | 0 | 23790 | 0 | 0.3051% | 0% |  |  | 0.3051% | 0% | 0.3051% | 1 | TRUE
SPAULD_6_UNIT12 | Hydro | 2022 | 1825 | 4608.5983 | 0 | 20805 | 0 | 22.15% | 0% |  |  | 22.15% | 0% | 22.15% | 1 | TRUE
SPAULD_6_UNIT12 | Hydro | 2023 | 1825 | 5867.5667 | 0 | 20805 | 0 | 28.2% | 0% |  |  | 28.2% | 0% | 28.2% | 2 | TRUE
SPAULD_6_UNIT12 | Hydro | 2024 | 1830 | 14879.7167 | 0 | 20862 | 0 | 71.32% | 0% |  |  | 71.32% | 0% | 71.32% | 3 | TRUE
SPICER_1_UNITS | Hydro | 2022 | 1825 | 5.55 | 0 | 10950 | 0 | 0.05068% | 0% |  |  | 0.05068% | 0% | 0.05068% | 1 | TRUE
SPICER_1_UNITS | Hydro | 2023 | 1825 | 156.45 | 0 | 10950 | 0 | 1.429% | 0% |  |  | 1.429% | 0% | 1.429% | 3 | TRUE
SPICER_1_UNITS | Hydro | 2024 | 1830 | 101.8 | 0 | 10980 | 0 | 0.9271% | 0% |  |  | 0.9271% | 0% | 0.9271% | 2 | TRUE
SPRGVL_2_SUCCES | Hydro | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 17.53% | 0.3184% | 17.53% | 0.3184% | 17.85% | 2 | TRUE
SPRGVL_2_SUCCES | Hydro | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 15.33% | 0.0024% | 15.33% | 0.0024% | 15.33% | 1 | TRUE
SPRGVL_2_SUCCES | Hydro | 2024 | 675 | 791 | 0 | 945 | 1155 | 83.7% | 0% | 14.47% | 0.01473% | 40.01% | 9.134% | 49.14% | 3 | TRUE
STANIS_7_UNIT 1 | Hydro | 2022 | 1825 | 20266.0117 | 0 | 166075 | 0 | 12.2% | 0% |  |  | 12.2% | 0% | 12.2% | 3 | TRUE
STANIS_7_UNIT 1 | Hydro | 2023 | 1825 | 2273.8733 | 0 | 166075 | 0 | 1.369% | 0% |  |  | 1.369% | 0% | 1.369% | 2 | TRUE
STANIS_7_UNIT 1 | Hydro | 2024 | 1830 | 544.804 | 0 | 166530 | 0 | 0.3272% | 0% |  |  | 0.3272% | 0% | 0.3272% | 1 | TRUE
TIGRCK_7_UNITS | Hydro | 2022 | 1825 | 6432.8483 | 25 | 113150 | 0 | 5.685% | 0.02209% |  |  | 5.685% | 0.02209% | 5.707% | 2 | TRUE
TIGRCK_7_UNITS | Hydro | 2023 | 1825 | 18375.6083 | 0 | 113150 | 0 | 16.24% | 0% |  |  | 16.24% | 0% | 16.24% | 3 | TRUE
TIGRCK_7_UNITS | Hydro | 2024 | 1830 | 1475.3667 | 0 | 113460 | 0 | 1.3% | 0% |  |  | 1.3% | 0% | 1.3% | 1 | TRUE
TVYVLY_6_KRSHY1 | Hydro | 2022 | 1825 | 721.5 | 0 | 2372.5 | 0 | 30.41% | 0% |  |  | 30.41% | 0% | 30.41% | 1 | TRUE
TVYVLY_6_KRSHY1 | Hydro | 2023 | 1825 | 1975.9 | 0 | 2372.5 | 0 | 83.28% | 0% |  |  | 83.28% | 0% | 83.28% | 3 | TRUE
TVYVLY_6_KRSHY1 | Hydro | 2024 | 1830 | 1303.575 | 0 | 2379 | 0 | 54.8% | 0% |  |  | 54.8% | 0% | 54.8% | 2 | TRUE
UKIAH_7_LAKEMN | Hydro | 2022 | 1825 | 1299.8083 | 0 | 6387.5 | 0 | 20.35% | 0% |  |  | 20.35% | 0% | 20.35% | 3 | TRUE
UKIAH_7_LAKEMN | Hydro | 2023 | 1825 | 464.7917 | 0 | 6387.5 | 0 | 7.277% | 0% |  |  | 7.277% | 0% | 7.277% | 2 | TRUE
UKIAH_7_LAKEMN | Hydro | 2024 | 1830 | 165.6583 | 0 | 6405 | 0 | 2.586% | 0% |  |  | 2.586% | 0% | 2.586% | 1 | TRUE
VALLEY_5_PERRIS | Hydro | 2022 | 1825 | 14450.8 | 0 | 14490.5 | 0 | 99.73% | 0% |  |  | 99.73% | 0% | 99.73% | 3 | TRUE
VALLEY_5_PERRIS | Hydro | 2023 | 1825 | 13193.5407 | 0 | 14490.5 | 0 | 91.05% | 0% |  |  | 91.05% | 0% | 91.05% | 2 | TRUE
VALLEY_5_PERRIS | Hydro | 2024 | 1830 | 0 | 0 | 14530.2 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
VILLPK_2_VALLYV | Hydro | 2022 | 1825 | 7247 | 0 | 7482.5 | 0 | 96.85% | 0% |  |  | 96.85% | 0% | 96.85% | 2 | TRUE
VILLPK_2_VALLYV | Hydro | 2023 | 1825 | 7462 | 0 | 7482.5 | 0 | 99.73% | 0% |  |  | 99.73% | 0% | 99.73% | 3 | TRUE
VILLPK_2_VALLYV | Hydro | 2024 | 1830 | 0 | 0 | 7503 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
VILLPK_6_MWDYOR | Hydro | 2022 | 1825 | 25.5 | 0 | 9307.5 | 0 | 0.274% | 0% |  |  | 0.274% | 0% | 0.274% | 2 | TRUE
VILLPK_6_MWDYOR | Hydro | 2023 | 1825 | 49.3 | 72.76 | 9307.5 | 0 | 0.5297% | 0.7817% |  |  | 0.5297% | 0.7817% | 1.311% | 3 | TRUE
VILLPK_6_MWDYOR | Hydro | 2024 | 1830 | 0 | 0 | 9333 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
WARNE_2_UNIT | Hydro | 2022 | 1825 | 104.5 | 0 | 138700 | 0 | 0.07534% | 0% |  |  | 0.07534% | 0% | 0.07534% | 1 | TRUE
WARNE_2_UNIT | Hydro | 2023 | 1825 | 1858.2 | 0 | 138700 | 0 | 1.34% | 0% |  |  | 1.34% | 0% | 1.34% | 2 | TRUE
WARNE_2_UNIT | Hydro | 2024 | 1830 | 2346.5333 | 0 | 139080 | 0 | 1.687% | 0% |  |  | 1.687% | 0% | 1.687% | 3 | TRUE
WDLEAF_7_UNIT 1 | Hydro | 2022 | 1825 | 1447.9167 | 0 | 109500 | 0 | 1.322% | 0% |  |  | 1.322% | 0% | 1.322% | 1 | TRUE
WDLEAF_7_UNIT 1 | Hydro | 2023 | 1825 | 7334.75 | 0 | 109500 | 0 | 6.698% | 0% |  |  | 6.698% | 0% | 6.698% | 3 | TRUE
WDLEAF_7_UNIT 1 | Hydro | 2024 | 1830 | 2891.55 | 0 | 109800 | 0 | 2.633% | 0% |  |  | 2.633% | 0% | 2.633% | 2 | TRUE
WESTPT_2_UNIT | Hydro | 2022 | 1825 | 234.5733 | 7 | 25550 | 0 | 0.9181% | 0.0274% |  |  | 0.9181% | 0.0274% | 0.9455% | 2 | TRUE
WESTPT_2_UNIT | Hydro | 2023 | 1825 | 378.4833 | 0 | 25550 | 0 | 1.481% | 0% |  |  | 1.481% | 0% | 1.481% | 3 | TRUE
WESTPT_2_UNIT | Hydro | 2024 | 1830 | 38.3167 | 0 | 25620 | 0 | 0.1496% | 0% |  |  | 0.1496% | 0% | 0.1496% | 1 | TRUE
WISE_1_UNIT 1 | Hydro | 2022 | 1825 | 5348.8375 | 0 | 26462.5 | 0 | 20.21% | 0% |  |  | 20.21% | 0% | 20.21% | 2 | TRUE
WISE_1_UNIT 1 | Hydro | 2023 | 1825 | 2188.4783 | 0 | 26462.5 | 0 | 8.27% | 0% |  |  | 8.27% | 0% | 8.27% | 1 | TRUE
WISE_1_UNIT 1 | Hydro | 2024 | 1830 | 11882.8392 | 0 | 26535 | 0 | 44.78% | 0% |  |  | 44.78% | 0% | 44.78% | 3 | TRUE
WISE_1_UNIT 2 | Hydro | 2022 | 1825 | 5744 | 0 | 5840 | 0 | 98.36% | 0% |  |  | 98.36% | 0% | 98.36% | 2 | TRUE
WISE_1_UNIT 2 | Hydro | 2023 | 1825 | 5819.2 | 0 | 5840 | 0 | 99.64% | 0% |  |  | 99.64% | 0% | 99.64% | 3 | TRUE
WISE_1_UNIT 2 | Hydro | 2024 | 1830 | 4592 | 0 | 5856 | 0 | 78.42% | 0% |  |  | 78.42% | 0% | 78.42% | 1 | TRUE
WISHON_6_UNITS | Hydro | 2022 | 1825 | 15789.935 | 0 | 33580 | 0 | 47.02% | 0% |  |  | 47.02% | 0% | 47.02% | 1 | TRUE
WISHON_6_UNITS | Hydro | 2023 | 1825 | 16978.575 | 0 | 33580 | 0 | 50.56% | 0% |  |  | 50.56% | 0% | 50.56% | 3 | TRUE
WISHON_6_UNITS | Hydro | 2024 | 1830 | 16111.885 | 0 | 33672 | 0 | 47.85% | 0% |  |  | 47.85% | 0% | 47.85% | 2 | TRUE
DIABLO_7_UNIT 1 | Nuclear | 2022 | 1825 | 21490 | 0 | 2098750 | 0 | 1.024% | 0% |  |  | 1.024% | 0% | 1.024% | 2 | TRUE
DIABLO_7_UNIT 1 | Nuclear | 2023 | 1825 | 31353.8333 | 0 | 2098750 | 0 | 1.494% | 0% |  |  | 1.494% | 0% | 1.494% | 3 | TRUE
DIABLO_7_UNIT 1 | Nuclear | 2024 | 1830 | 10495.1333 | 0 | 2104500 | 0 | 0.4987% | 0% |  |  | 0.4987% | 0% | 0.4987% | 1 | TRUE
DIABLO_7_UNIT 2 | Nuclear | 2022 | 1825 | 25561.6667 | 0 | 2098750 | 0 | 1.218% | 0% |  |  | 1.218% | 0% | 1.218% | 2 | TRUE
DIABLO_7_UNIT 2 | Nuclear | 2023 | 1825 | 24463.8 | 5549.6667 | 2098750 | 0 | 1.166% | 0.2644% |  |  | 1.166% | 0.2644% | 1.43% | 3 | TRUE
DIABLO_7_UNIT 2 | Nuclear | 2024 | 1830 | 13620 | 0 | 2104500 | 0 | 0.6472% | 0% |  |  | 0.6472% | 0% | 0.6472% | 1 | TRUE
PVERDE_5_SCEDYN | Nuclear | 2022 | 1825 | 14865 | 0 | 1158875 | 0 | 1.283% | 0% |  |  | 1.283% | 0% | 1.283% | 1 | TRUE
PVERDE_5_SCEDYN | Nuclear | 2023 | 1825 | 37419.85 | 150 | 1158875 | 0 | 3.229% | 0.01294% |  |  | 3.229% | 0.01294% | 3.242% | 3 | TRUE
PVERDE_5_SCEDYN | Nuclear | 2024 | 1830 | 21178.5 | 2071.8667 | 1162050 | 0 | 1.823% | 0.1783% |  |  | 1.823% | 0.1783% | 2.001% | 2 | TRUE
ALMASL_2_AL6BT6 | Paired_BattStorage | 2022 | 940 | 3037.6 | 0 | 47000 | 885 | 6.463% | 0% | 10.3% | 0% | 8.324% | 4.995% | 13.32% | 2 | TRUE
ALMASL_2_AL6BT6 | Paired_BattStorage | 2023 | 1825 | 13522.85 | 0 | 91250 | 0 | 14.82% | 0% |  |  | 14.82% | 0% | 14.82% | 3 | TRUE
ALMASL_2_AL6BT6 | Paired_BattStorage | 2024 | 1830 | 10330.8425 | 0 | 91500 | 0 | 11.29% | 0% |  |  | 11.29% | 0% | 11.29% | 1 | TRUE
BIGSKY_2_AS2BT1 | Paired_BattStorage | 2022 | 605 | 2939.4167 | 0 | 76835 | 1220 | 3.826% | 0% | 10.3% | 0% | 8.154% | 6.886% | 15.04% | 3 | TRUE
BIGSKY_2_AS2BT1 | Paired_BattStorage | 2023 | 1825 | 5995.4333 | 0 | 231775 | 0 | 2.587% | 0% |  |  | 2.587% | 0% | 2.587% | 2 | TRUE
BIGSKY_2_AS2BT1 | Paired_BattStorage | 2024 | 1830 | 208.7 | 0 | 232410 | 0 | 0.0898% | 0% |  |  | 0.0898% | 0% | 0.0898% | 1 | TRUE
BIGSKY_2_ASLBT2 | Paired_BattStorage | 2022 | 775 | 4883.2 | 0 | 77500 | 1050 | 6.301% | 0% | 10.3% | 0% | 8.602% | 5.927% | 14.53% | 3 | TRUE
BIGSKY_2_ASLBT2 | Paired_BattStorage | 2023 | 1825 | 2449.5 | 0 | 182500 | 0 | 1.342% | 0% |  |  | 1.342% | 0% | 1.342% | 2 | TRUE
BIGSKY_2_ASLBT2 | Paired_BattStorage | 2024 | 1830 | 596.5167 | 0 | 183000 | 0 | 0.326% | 0% |  |  | 0.326% | 0% | 0.326% | 1 | TRUE
BLKCRK_2_GMCBT1 | Paired_BattStorage | 2022 | 1825 | 16148.2028 | 0 | 419750 | 0 | 3.847% | 0% |  |  | 3.847% | 0% | 3.847% | 2 | TRUE
BLKCRK_2_GMCBT1 | Paired_BattStorage | 2023 | 1825 | 61529.09 | 0 | 419750 | 0 | 14.66% | 0% |  |  | 14.66% | 0% | 14.66% | 3 | TRUE
BLKCRK_2_GMCBT1 | Paired_BattStorage | 2024 | 1830 | 5920.1992 | 0 | 420900 | 0 | 1.407% | 0% |  |  | 1.407% | 0% | 1.407% | 1 | TRUE
BLM W_2_COSBT1 | Paired_BattStorage | 2022 | 1535 | 14291.571 | 0 | 92100 | 290 | 15.52% | 0% | 10.3% | 0% | 14.69% | 1.637% | 16.33% | 3 | TRUE
BLM W_2_COSBT1 | Paired_BattStorage | 2023 | 1825 | 12435.4508 | 0 | 109500 | 0 | 11.36% | 0% |  |  | 11.36% | 0% | 11.36% | 2 | TRUE
BLM W_2_COSBT1 | Paired_BattStorage | 2024 | 1830 | 6094.2092 | 0 | 109800 | 0 | 5.55% | 0% |  |  | 5.55% | 0% | 5.55% | 1 | TRUE
CALFTN_2_CFSBT1 | Paired_BattStorage | 2022 | 1825 | 2691 | 0 | 109500 | 0 | 2.458% | 0% |  |  | 2.458% | 0% | 2.458% | 1 | TRUE
CALFTN_2_CFSBT1 | Paired_BattStorage | 2023 | 1825 | 4300.2 | 0 | 109500 | 0 | 3.927% | 0% |  |  | 3.927% | 0% | 3.927% | 2 | TRUE
CALFTN_2_CFSBT1 | Paired_BattStorage | 2024 | 1830 | 11262 | 0 | 109800 | 0 | 10.26% | 0% |  |  | 10.26% | 0% | 10.26% | 3 | TRUE
CENTPD_2_BMSX2 | Paired_BattStorage | 2022 | 55 | 0 | 0 | 6160 | 1770 | 0% | 0% | 10.3% | 0% | 9.99% | 9.99% | 19.98% | 3 | TRUE
CENTPD_2_BMSX2 | Paired_BattStorage | 2023 | 1825 | 16989.5667 | 0 | 204400 | 0 | 8.312% | 0% |  |  | 8.312% | 0% | 8.312% | 2 | TRUE
CENTPD_2_BMSX2 | Paired_BattStorage | 2024 | 1830 | 8785.5 | 0 | 204960 | 0 | 4.286% | 0% |  |  | 4.286% | 0% | 4.286% | 1 | TRUE
CHESTN_2_CHWBX2 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 2 | TRUE
CHESTN_2_CHWBX2 | Paired_BattStorage | 2023 | 90 | 985.5 | 0 | 12150 | 1735 | 8.111% | 0% | 11.83% | 0% | 11.64% | 11.24% | 22.89% | 3 | TRUE
CHESTN_2_CHWBX2 | Paired_BattStorage | 2024 | 1830 | 1047.6 | 0 | 247050 | 0 | 0.424% | 0% |  |  | 0.424% | 0% | 0.424% | 1 | TRUE
CMBLND_2_DS2BT1 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 2 | TRUE
CMBLND_2_DS2BT1 | Paired_BattStorage | 2023 | 200 | 1008.85 | 0 | 10400 | 1625 | 9.7% | 0% | 11.83% | 0% | 11.59% | 10.53% | 22.12% | 3 | TRUE
CMBLND_2_DS2BT1 | Paired_BattStorage | 2024 | 1830 | 2221.8167 | 0 | 95160 | 0 | 2.335% | 0% |  |  | 2.335% | 0% | 2.335% | 1 | TRUE
CMBLND_2_DS2BT2 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 2 | TRUE
CMBLND_2_DS2BT2 | Paired_BattStorage | 2023 | 200 | 14 | 0 | 6600 | 1625 | 0.2121% | 0% | 11.83% | 0% | 10.55% | 10.53% | 21.08% | 3 | TRUE
CMBLND_2_DS2BT2 | Paired_BattStorage | 2024 | 1830 | 868.4167 | 0 | 60390 | 0 | 1.438% | 0% |  |  | 1.438% | 0% | 1.438% | 1 | TRUE
CMBLND_2_DS2BT3 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 2 | TRUE
CMBLND_2_DS2BT3 | Paired_BattStorage | 2023 | 155 | 30 | 0 | 7130 | 1670 | 0.4208% | 0% | 11.83% | 0% | 10.86% | 10.82% | 21.68% | 3 | TRUE
CMBLND_2_DS2BT3 | Paired_BattStorage | 2024 | 1830 | 1394.6417 | 0 | 84180 | 0 | 1.657% | 0% |  |  | 1.657% | 0% | 1.657% | 1 | TRUE
DRACKR_2_DSUBT1 | Paired_BattStorage | 2022 | 1825 | 17331.4497 | 0 | 114975 | 0 | 15.07% | 0% |  |  | 15.07% | 0% | 15.07% | 2 | TRUE
DRACKR_2_DSUBT1 | Paired_BattStorage | 2023 | 1825 | 19988.057 | 0 | 114975 | 0 | 17.38% | 0% |  |  | 17.38% | 0% | 17.38% | 3 | TRUE
DRACKR_2_DSUBT1 | Paired_BattStorage | 2024 | 1830 | 2866.6168 | 0 | 115290 | 0 | 2.486% | 0% |  |  | 2.486% | 0% | 2.486% | 1 | TRUE
DRACKR_2_DSUBT2 | Paired_BattStorage | 2022 | 1825 | 16924.3583 | 0 | 209875 | 0 | 8.064% | 0% |  |  | 8.064% | 0% | 8.064% | 2 | TRUE
DRACKR_2_DSUBT2 | Paired_BattStorage | 2023 | 1825 | 26210.104 | 0 | 209875 | 0 | 12.49% | 0% |  |  | 12.49% | 0% | 12.49% | 3 | TRUE
DRACKR_2_DSUBT2 | Paired_BattStorage | 2024 | 1830 | 3602.8265 | 0 | 210450 | 0 | 1.712% | 0% |  |  | 1.712% | 0% | 1.712% | 1 | TRUE
DRACKR_2_DSUBT3 | Paired_BattStorage | 2022 | 1825 | 10894.6875 | 0 | 209875 | 0 | 5.191% | 0% |  |  | 5.191% | 0% | 5.191% | 2 | TRUE
DRACKR_2_DSUBT3 | Paired_BattStorage | 2023 | 1825 | 27284.2193 | 0 | 209875 | 0 | 13% | 0% |  |  | 13% | 0% | 13% | 3 | TRUE
DRACKR_2_DSUBT3 | Paired_BattStorage | 2024 | 1830 | 2192.8723 | 0 | 210450 | 0 | 1.042% | 0% |  |  | 1.042% | 0% | 1.042% | 1 | TRUE
DRACKR_2_DSUBT4 | Paired_BattStorage | 2022 | 475 | 9294.5775 | 0 | 22325 | 1350 | 41.63% | 0% | 10.3% | 0% | 18.46% | 7.62% | 26.08% | 3 | TRUE
DRACKR_2_DSUBT4 | Paired_BattStorage | 2023 | 1825 | 17721.9975 | 0 | 85775 | 0 | 20.66% | 0% |  |  | 20.66% | 0% | 20.66% | 2 | TRUE
DRACKR_2_DSUBT4 | Paired_BattStorage | 2024 | 1830 | 1538.4898 | 0 | 86010 | 0 | 1.789% | 0% |  |  | 1.789% | 0% | 1.789% | 1 | TRUE
DSRTHV_2_DH2BT1 | Paired_BattStorage | 2022 | 1825 | 11936.213 | 0 | 63875 | 0 | 18.69% | 0% |  |  | 18.69% | 0% | 18.69% | 1 | TRUE
DSRTHV_2_DH2BT1 | Paired_BattStorage | 2023 | 1825 | 38937.502 | 0 | 63875 | 0 | 60.96% | 0% |  |  | 60.96% | 0% | 60.96% | 3 | TRUE
DSRTHV_2_DH2BT1 | Paired_BattStorage | 2024 | 1830 | 15536.1258 | 0 | 64050 | 0 | 24.26% | 0% |  |  | 24.26% | 0% | 24.26% | 2 | TRUE
DSRTSN_2_DS2BX2 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 2 | TRUE
DSRTSN_2_DS2BX2 | Paired_BattStorage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 11.83% | 0% | 11.83% | 0% | 11.83% | 3 | TRUE
DSRTSN_2_DS2BX2 | Paired_BattStorage | 2024 | 1335 | 8652.953 | 0 | 307050 | 495 | 2.818% | 0% | 4.165% | 0.001944% | 3.183% | 1.127% | 4.309% | 1 | TRUE
DSRTSN_2_DS2X2 | Paired_BattStorage | 2022 | 630 | 6881.905 | 0 | 144900 | 1195 | 4.749% | 0% | 10.3% | 0% | 8.384% | 6.745% | 15.13% | 3 | TRUE
DSRTSN_2_DS2X2 | Paired_BattStorage | 2023 | 1825 | 18044.2718 | 0 | 419750 | 0 | 4.299% | 0% |  |  | 4.299% | 0% | 4.299% | 2 | TRUE
DSRTSN_2_DS2X2 | Paired_BattStorage | 2024 | 1830 | 9980.938 | 0 | 420900 | 0 | 2.371% | 0% |  |  | 2.371% | 0% | 2.371% | 1 | TRUE
FIFTHS_2_FSSBT | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 2 | TRUE
FIFTHS_2_FSSBT | Paired_BattStorage | 2023 | 540 | 1379 | 0 | 73980 | 1285 | 1.864% | 0% | 11.83% | 0% | 8.879% | 8.327% | 17.21% | 3 | TRUE
FIFTHS_2_FSSBT | Paired_BattStorage | 2024 | 1830 | 0 | 0 | 250710 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
FILIPPI_2_QZSBTX | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 2 | TRUE
FILIPPI_2_QZSBTX | Paired_BattStorage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 11.83% | 0% | 11.83% | 0% | 11.83% | 3 | TRUE
FILIPPI_2_QZSBTX | Paired_BattStorage | 2024 | 75 | 0 | 0 | 11250 | 1755 | 0% | 0% | 4.165% | 0.001944% | 3.995% | 3.995% | 7.989% | 1 | TRUE
GARLND_2_GARBT1 | Paired_BattStorage | 2022 | 1675 | 23632.4833 | 0 | 147400 | 150 | 16.03% | 0% | 10.3% | 0% | 15.56% | 0.8466% | 16.41% | 2 | TRUE
GARLND_2_GARBT1 | Paired_BattStorage | 2023 | 1825 | 32729.4833 | 0 | 160600 | 0 | 20.38% | 0% |  |  | 20.38% | 0% | 20.38% | 3 | TRUE
GARLND_2_GARBT1 | Paired_BattStorage | 2024 | 1830 | 25416.5167 | 0 | 161040 | 0 | 15.78% | 0% |  |  | 15.78% | 0% | 15.78% | 1 | TRUE
GASKW1_2_GW2BT1 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 1 | TRUE
GASKW1_2_GW2BT1 | Paired_BattStorage | 2023 | 1205 | 3254.865 | 0 | 24100 | 620 | 13.51% | 0% | 11.83% | 0% | 12.94% | 4.018% | 16.95% | 2 | TRUE
GASKW1_2_GW2BT1 | Paired_BattStorage | 2024 | 1830 | 10964.8037 | 0 | 36600 | 0 | 29.96% | 0% |  |  | 29.96% | 0% | 29.96% | 3 | TRUE
HIGHDS_2_H5SBT1 | Paired_BattStorage | 2022 | 1825 | 14098.8993 | 0 | 91250 | 0 | 15.45% | 0% |  |  | 15.45% | 0% | 15.45% | 3 | TRUE
HIGHDS_2_H5SBT1 | Paired_BattStorage | 2023 | 1825 | 10454.8653 | 0 | 91250 | 0 | 11.46% | 0% |  |  | 11.46% | 0% | 11.46% | 2 | TRUE
HIGHDS_2_H5SBT1 | Paired_BattStorage | 2024 | 1830 | 9451.3473 | 0 | 91500 | 0 | 10.33% | 0% |  |  | 10.33% | 0% | 10.33% | 1 | TRUE
KRAMER_1_R1BX3 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 2 | TRUE
KRAMER_1_R1BX3 | Paired_BattStorage | 2023 | 920 | 2036.8 | 0 | 69000 | 905 | 2.952% | 0% | 11.83% | 0% | 7.353% | 5.865% | 13.22% | 3 | TRUE
KRAMER_1_R1BX3 | Paired_BattStorage | 2024 | 1830 | 5028.0833 | 0 | 137250 | 0 | 3.663% | 0% |  |  | 3.663% | 0% | 3.663% | 1 | TRUE
KRAMER_1_R2BX2 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 2 | TRUE
KRAMER_1_R2BX2 | Paired_BattStorage | 2023 | 620 | 406.772 | 0 | 24800 | 1205 | 1.64% | 0% | 11.83% | 0% | 8.366% | 7.809% | 16.17% | 3 | TRUE
KRAMER_1_R2BX2 | Paired_BattStorage | 2024 | 1830 | 1141.2367 | 0 | 73200 | 0 | 1.559% | 0% |  |  | 1.559% | 0% | 1.559% | 1 | TRUE
MCFLND_5_MFSBT1 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 2 | TRUE
MCFLND_5_MFSBT1 | Paired_BattStorage | 2023 | 50 | 133.825 | 0 | 5000 | 1775 | 2.676% | 0% | 11.83% | 0% | 11.58% | 11.5% | 23.08% | 3 | TRUE
MCFLND_5_MFSBT1 | Paired_BattStorage | 2024 | 1830 | 14581.0667 | 0 | 183000 | 0 | 7.968% | 0% |  |  | 7.968% | 0% | 7.968% | 1 | TRUE
MCFLND_5_MSCBT1 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 2 | TRUE
MCFLND_5_MSCBT1 | Paired_BattStorage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 11.83% | 0% | 11.83% | 0% | 11.83% | 3 | TRUE
MCFLND_5_MSCBT1 | Paired_BattStorage | 2024 | 0 | 0 | 0 | 0 | 1830 |  |  | 4.165% | 0.001944% | 4.165% | 0.001944% | 4.167% | 1 | TRUE
MSTANG_2_MTGBT1 | Paired_BattStorage | 2022 | 1825 | 5203.7082 | 0 | 136875 | 0 | 3.802% | 0% |  |  | 3.802% | 0% | 3.802% | 1 | TRUE
MSTANG_2_MTGBT1 | Paired_BattStorage | 2023 | 1825 | 12969.4158 | 0 | 136875 | 0 | 9.475% | 0% |  |  | 9.475% | 0% | 9.475% | 3 | TRUE
MSTANG_2_MTGBT1 | Paired_BattStorage | 2024 | 1830 | 10948.7718 | 0 | 137250 | 0 | 7.977% | 0% |  |  | 7.977% | 0% | 7.977% | 2 | TRUE
OBERON_5_O1BBX2 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 2 | TRUE
OBERON_5_O1BBX2 | Paired_BattStorage | 2023 | 295 | 0 | 0 | 36875 | 1530 | 0% | 0% | 11.83% | 0% | 9.915% | 9.915% | 19.83% | 3 | TRUE
OBERON_5_O1BBX2 | Paired_BattStorage | 2024 | 1830 | 5487.0833 | 0 | 228750 | 0 | 2.399% | 0% |  |  | 2.399% | 0% | 2.399% | 1 | TRUE
OBERON_5_O2BBX2 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 2 | TRUE
OBERON_5_O2BBX2 | Paired_BattStorage | 2023 | 295 | 0 | 0 | 36875 | 1530 | 0% | 0% | 11.83% | 0% | 9.915% | 9.915% | 19.83% | 3 | TRUE
OBERON_5_O2BBX2 | Paired_BattStorage | 2024 | 1830 | 10722.7 | 0 | 228750 | 0 | 4.688% | 0% |  |  | 4.688% | 0% | 4.688% | 1 | TRUE
PALSEL_6_PLSBT1 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 2 | TRUE
PALSEL_6_PLSBT1 | Paired_BattStorage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 11.83% | 0% | 11.83% | 0% | 11.83% | 3 | TRUE
PALSEL_6_PLSBT1 | Paired_BattStorage | 2024 | 975 | 393.5167 | 0 | 14625 | 855 | 2.691% | 0% | 4.165% | 0.001944% | 3.38% | 1.946% | 5.326% | 1 | TRUE
POLRIS_2_ASEBT1 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 2 | TRUE
POLRIS_2_ASEBT1 | Paired_BattStorage | 2023 | 15 | 0 | 0 | 420 | 1810 | 0% | 0% | 11.83% | 0% | 11.73% | 11.73% | 23.46% | 3 | TRUE
POLRIS_2_ASEBT1 | Paired_BattStorage | 2024 | 1830 | 3914.6833 | 0 | 51240 | 0 | 7.64% | 0% |  |  | 7.64% | 0% | 7.64% | 1 | TRUE
POLRIS_2_ASRBT1 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 2 | TRUE
POLRIS_2_ASRBT1 | Paired_BattStorage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 11.83% | 0% | 11.83% | 0% | 11.83% | 3 | TRUE
POLRIS_2_ASRBT1 | Paired_BattStorage | 2024 | 1400 | 12004.1833 | 0 | 112000 | 430 | 10.72% | 0% | 4.165% | 0.001944% | 9.178% | 0.9788% | 10.16% | 1 | TRUE
PRIMM_2_SSSBT1 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 2 | TRUE
PRIMM_2_SSSBT1 | Paired_BattStorage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 11.83% | 0% | 11.83% | 0% | 11.83% | 3 | TRUE
PRIMM_2_SSSBT1 | Paired_BattStorage | 2024 | 0 | 0 | 0 | 0 | 1830 |  |  | 4.165% | 0.001944% | 4.165% | 0.001944% | 4.167% | 1 | TRUE
PROXSR_2_PS1BT1 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 2 | TRUE
PROXSR_2_PS1BT1 | Paired_BattStorage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 11.83% | 0% | 11.83% | 0% | 11.83% | 3 | TRUE
PROXSR_2_PS1BT1 | Paired_BattStorage | 2024 | 1340 | 2411.0485 | 0 | 53600 | 490 | 4.498% | 0% | 4.165% | 0.001944% | 4.409% | 1.115% | 5.524% | 1 | TRUE
PROXSR_2_PS1BT2 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 2 | TRUE
PROXSR_2_PS1BT2 | Paired_BattStorage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 11.83% | 0% | 11.83% | 0% | 11.83% | 3 | TRUE
PROXSR_2_PS1BT2 | Paired_BattStorage | 2024 | 1195 | 423.3333 | 0 | 38240 | 635 | 1.107% | 0% | 4.165% | 0.001944% | 2.168% | 1.445% | 3.614% | 1 | TRUE
PROXSR_2_PS2BT3 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 2 | TRUE
PROXSR_2_PS2BT3 | Paired_BattStorage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 11.83% | 0% | 11.83% | 0% | 11.83% | 3 | TRUE
PROXSR_2_PS2BT3 | Paired_BattStorage | 2024 | 1325 | 8863.024 | 0 | 119250 | 505 | 7.432% | 0% | 4.165% | 0.001944% | 6.531% | 1.149% | 7.68% | 1 | TRUE
REXFRD_2_RSFBX2 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 2 | TRUE
REXFRD_2_RSFBX2 | Paired_BattStorage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 11.83% | 0% | 11.83% | 0% | 11.83% | 3 | TRUE
REXFRD_2_RSFBX2 | Paired_BattStorage | 2024 | 0 | 0 | 0 | 0 | 1830 |  |  | 4.165% | 0.001944% | 4.165% | 0.001944% | 4.167% | 1 | TRUE
RSMNDS_2_CSRBT1 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 2 | TRUE
RSMNDS_2_CSRBT1 | Paired_BattStorage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 11.83% | 0% | 11.83% | 0% | 11.83% | 3 | TRUE
RSMNDS_2_CSRBT1 | Paired_BattStorage | 2024 | 0 | 0 | 0 | 0 | 1830 |  |  | 4.165% | 0.001944% | 4.165% | 0.001944% | 4.167% | 1 | TRUE
RSMNDS_2_CSRBT2 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 2 | TRUE
RSMNDS_2_CSRBT2 | Paired_BattStorage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 11.83% | 0% | 11.83% | 0% | 11.83% | 3 | TRUE
RSMNDS_2_CSRBT2 | Paired_BattStorage | 2024 | 0 | 0 | 0 | 0 | 1830 |  |  | 4.165% | 0.001944% | 4.165% | 0.001944% | 4.167% | 1 | TRUE
RTEDDY_2_RWSBT1 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 2 | TRUE
RTEDDY_2_RWSBT1 | Paired_BattStorage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 11.83% | 0% | 11.83% | 0% | 11.83% | 3 | TRUE
RTEDDY_2_RWSBT1 | Paired_BattStorage | 2024 | 1220 | 665.8833 | 0 | 36600 | 610 | 1.819% | 0% | 4.165% | 0.001944% | 2.601% | 1.388% | 3.99% | 1 | TRUE
RTEDDY_2_RWSBT2 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 2 | TRUE
RTEDDY_2_RWSBT2 | Paired_BattStorage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 11.83% | 0% | 11.83% | 0% | 11.83% | 3 | TRUE
RTEDDY_2_RWSBT2 | Paired_BattStorage | 2024 | 1220 | 1369.0667 | 0 | 36600 | 610 | 3.741% | 0% | 4.165% | 0.001944% | 3.882% | 1.388% | 5.271% | 1 | TRUE
RTEDDY_2_RWSBT3 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 2 | TRUE
RTEDDY_2_RWSBT3 | Paired_BattStorage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 11.83% | 0% | 11.83% | 0% | 11.83% | 3 | TRUE
RTEDDY_2_RWSBT3 | Paired_BattStorage | 2024 | 1185 | 426.0667 | 0 | 53325 | 645 | 0.799% | 0% | 4.165% | 0.001944% | 1.986% | 1.468% | 3.454% | 1 | TRUE
RTEDDY_2_RWSBT4 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 2 | TRUE
RTEDDY_2_RWSBT4 | Paired_BattStorage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 11.83% | 0% | 11.83% | 0% | 11.83% | 3 | TRUE
RTEDDY_2_RWSBT4 | Paired_BattStorage | 2024 | 1220 | 247.15 | 0 | 36600 | 610 | 0.6753% | 0% | 4.165% | 0.001944% | 1.839% | 1.388% | 3.227% | 1 | TRUE
RTEDDY_2_RWSBT5 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 2 | TRUE
RTEDDY_2_RWSBT5 | Paired_BattStorage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 11.83% | 0% | 11.83% | 0% | 11.83% | 3 | TRUE
RTEDDY_2_RWSBT5 | Paired_BattStorage | 2024 | 1215 | 114.7333 | 0 | 14580 | 615 | 0.7869% | 0% | 4.165% | 0.001944% | 1.922% | 1.4% | 3.322% | 1 | TRUE
SCARLT_2_SS2BT1 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 1 | TRUE
SCARLT_2_SS2BT1 | Paired_BattStorage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 11.83% | 0% | 11.83% | 0% | 11.83% | 2 | TRUE
SCARLT_2_SS2BT1 | Paired_BattStorage | 2024 | 105 | 12927.5 | 0 | 15750 | 1725 | 82.08% | 0% | 4.165% | 0.001944% | 8.636% | 3.926% | 12.56% | 3 | TRUE
SCARLT_2_SSABT1 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 1 | TRUE
SCARLT_2_SSABT1 | Paired_BattStorage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 11.83% | 0% | 11.83% | 0% | 11.83% | 2 | TRUE
SCARLT_2_SSABT1 | Paired_BattStorage | 2024 | 1215 | 2726.4685 | 0 | 12150 | 615 | 22.44% | 0% | 4.165% | 0.001944% | 16.3% | 1.4% | 17.7% | 3 | TRUE
SCARLT_2_SSBBT1 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 1 | TRUE
SCARLT_2_SSBBT1 | Paired_BattStorage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 11.83% | 0% | 11.83% | 0% | 11.83% | 2 | TRUE
SCARLT_2_SSBBT1 | Paired_BattStorage | 2024 | 1215 | 9177.7832 | 0 | 36450 | 615 | 25.18% | 0% | 4.165% | 0.001944% | 18.12% | 1.4% | 19.52% | 3 | TRUE
SISPRG_2_DS3BT1 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 2 | TRUE
SISPRG_2_DS3BT1 | Paired_BattStorage | 2023 | 235 | 352.35 | 0 | 14452.5 | 1590 | 2.438% | 0% | 11.83% | 0% | 10.62% | 10.3% | 20.92% | 3 | TRUE
SISPRG_2_DS3BT1 | Paired_BattStorage | 2024 | 1830 | 3095.5433 | 130 | 112545 | 0 | 2.75% | 0.1155% |  |  | 2.75% | 0.1155% | 2.866% | 1 | TRUE
SISPRG_2_DS3BT2 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 2 | TRUE
SISPRG_2_DS3BT2 | Paired_BattStorage | 2023 | 650 | 571.6667 | 0 | 39000 | 1175 | 1.466% | 0% | 11.83% | 0% | 8.136% | 7.614% | 15.75% | 3 | TRUE
SISPRG_2_DS3BT2 | Paired_BattStorage | 2024 | 1830 | 3263.2717 | 0 | 109800 | 0 | 2.972% | 0% |  |  | 2.972% | 0% | 2.972% | 1 | TRUE
SISPRG_2_DS3BT3 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 2 | TRUE
SISPRG_2_DS3BT3 | Paired_BattStorage | 2023 | 590 | 1096.8417 | 0 | 7375 | 1235 | 14.87% | 0% | 11.83% | 0% | 12.81% | 8.003% | 20.81% | 3 | TRUE
SISPRG_2_DS3BT3 | Paired_BattStorage | 2024 | 1830 | 807.5167 | 0 | 22875 | 0 | 3.53% | 0% |  |  | 3.53% | 0% | 3.53% | 1 | TRUE
SISPRG_2_DS3BT4 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 2 | TRUE
SISPRG_2_DS3BT4 | Paired_BattStorage | 2023 | 650 | 383.3033 | 0 | 9750 | 1175 | 3.931% | 0% | 11.83% | 0% | 9.015% | 7.614% | 16.63% | 3 | TRUE
SISPRG_2_DS3BT4 | Paired_BattStorage | 2024 | 1830 | 506.8833 | 0 | 27450 | 0 | 1.847% | 0% |  |  | 1.847% | 0% | 1.847% | 1 | TRUE
SOLBLU_2_WSBBX2 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 2 | TRUE
SOLBLU_2_WSBBX2 | Paired_BattStorage | 2023 | 95 | 1877.15 | 0 | 21375 | 1730 | 8.782% | 0% | 11.83% | 0% | 11.67% | 11.21% | 22.88% | 3 | TRUE
SOLBLU_2_WSBBX2 | Paired_BattStorage | 2024 | 1830 | 2196.7633 | 0 | 411750 | 0 | 0.5335% | 0% |  |  | 0.5335% | 0% | 0.5335% | 1 | TRUE
SUNCAT_2_A1ABT1 | Paired_BattStorage | 2022 | 765 | 16748.0117 | 0 | 35955 | 1060 | 46.58% | 0% | 10.3% | 0% | 25.51% | 5.983% | 31.49% | 3 | TRUE
SUNCAT_2_A1ABT1 | Paired_BattStorage | 2023 | 1825 | 23806.0423 | 0 | 85775 | 0 | 27.75% | 0% |  |  | 27.75% | 0% | 27.75% | 2 | TRUE
SUNCAT_2_A1ABT1 | Paired_BattStorage | 2024 | 1830 | 1947.0235 | 0 | 86010 | 0 | 2.264% | 0% |  |  | 2.264% | 0% | 2.264% | 1 | TRUE
SUNCAT_2_A1BBT1 | Paired_BattStorage | 2022 | 765 | 18050.4833 | 0 | 48195 | 1060 | 37.45% | 0% | 10.3% | 0% | 21.68% | 5.983% | 27.67% | 2 | TRUE
SUNCAT_2_A1BBT1 | Paired_BattStorage | 2023 | 1825 | 35780.538 | 0 | 114975 | 0 | 31.12% | 0% |  |  | 31.12% | 0% | 31.12% | 3 | TRUE
SUNCAT_2_A1BBT1 | Paired_BattStorage | 2024 | 1830 | 4387.008 | 0 | 115290 | 0 | 3.805% | 0% |  |  | 3.805% | 0% | 3.805% | 1 | TRUE
SUNCAT_2_A2ABT2 | Paired_BattStorage | 2022 | 690 | 23914.1333 | 0 | 91080 | 1135 | 26.26% | 0% | 10.3% | 0% | 16.33% | 6.406% | 22.74% | 3 | TRUE
SUNCAT_2_A2ABT2 | Paired_BattStorage | 2023 | 1825 | 36859.205 | 0 | 240900 | 0 | 15.3% | 0% |  |  | 15.3% | 0% | 15.3% | 2 | TRUE
SUNCAT_2_A2ABT2 | Paired_BattStorage | 2024 | 1830 | 6956.8378 | 0 | 241560 | 0 | 2.88% | 0% |  |  | 2.88% | 0% | 2.88% | 1 | TRUE
TRNQLT_2_RETBT1 | Paired_BattStorage | 2022 | 1455 | 21031.005 | 0 | 104760 | 370 | 20.08% | 0% | 10.3% | 0% | 18.09% | 2.088% | 20.18% | 2 | TRUE
TRNQLT_2_RETBT1 | Paired_BattStorage | 2023 | 1825 | 28643.9833 | 0 | 131400 | 0 | 21.8% | 0% |  |  | 21.8% | 0% | 21.8% | 3 | TRUE
TRNQLT_2_RETBT1 | Paired_BattStorage | 2024 | 1830 | 11447.0833 | 0 | 131760 | 0 | 8.688% | 0% |  |  | 8.688% | 0% | 8.688% | 1 | TRUE
VALTNE_2_TSBBT1 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 2 | TRUE
VALTNE_2_TSBBT1 | Paired_BattStorage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 11.83% | 0% | 11.83% | 0% | 11.83% | 3 | TRUE
VALTNE_2_TSBBT1 | Paired_BattStorage | 2024 | 0 | 0 | 0 | 0 | 1830 |  |  | 4.165% | 0.001944% | 4.165% | 0.001944% | 4.167% | 1 | TRUE
VALTNE_2_TSBBT2 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 2 | TRUE
VALTNE_2_TSBBT2 | Paired_BattStorage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 11.83% | 0% | 11.83% | 0% | 11.83% | 3 | TRUE
VALTNE_2_TSBBT2 | Paired_BattStorage | 2024 | 0 | 0 | 0 | 0 | 1830 |  |  | 4.165% | 0.001944% | 4.165% | 0.001944% | 4.167% | 1 | TRUE
VICPAS_2_SLOBT1 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 2 | TRUE
VICPAS_2_SLOBT1 | Paired_BattStorage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 11.83% | 0% | 11.83% | 0% | 11.83% | 3 | TRUE
VICPAS_2_SLOBT1 | Paired_BattStorage | 2024 | 1405 | 510.325 | 0 | 21075 | 425 | 2.421% | 0% | 4.165% | 0.001944% | 2.826% | 0.9674% | 3.794% | 1 | TRUE
VICPAS_2_SOCBT1 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 2 | TRUE
VICPAS_2_SOCBT1 | Paired_BattStorage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 11.83% | 0% | 11.83% | 0% | 11.83% | 3 | TRUE
VICPAS_2_SOCBT1 | Paired_BattStorage | 2024 | 1405 | 3785.1333 | 0 | 70250 | 425 | 5.388% | 0% | 4.165% | 0.001944% | 5.104% | 0.9674% | 6.072% | 1 | TRUE
VICPAS_2_SOCBT2 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 2 | TRUE
VICPAS_2_SOCBT2 | Paired_BattStorage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 11.83% | 0% | 11.83% | 0% | 11.83% | 3 | TRUE
VICPAS_2_SOCBT2 | Paired_BattStorage | 2024 | 1405 | 3973.6833 | 0 | 99755 | 425 | 3.983% | 0% | 4.165% | 0.001944% | 4.026% | 0.9674% | 4.993% | 1 | TRUE
VICPAS_2_VPSBT1 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 2 | TRUE
VICPAS_2_VPSBT1 | Paired_BattStorage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 11.83% | 0% | 11.83% | 0% | 11.83% | 3 | TRUE
VICPAS_2_VPSBT1 | Paired_BattStorage | 2024 | 1400 | 2894.5167 | 0 | 70000 | 430 | 4.135% | 0% | 4.165% | 0.001944% | 4.142% | 0.9788% | 5.121% | 1 | TRUE
VLCNTR_6_VCEBT1 | Paired_BattStorage | 2022 | 1825 | 3553.1 | 0 | 98550 | 0 | 3.605% | 0% |  |  | 3.605% | 0% | 3.605% | 2 | TRUE
VLCNTR_6_VCEBT1 | Paired_BattStorage | 2023 | 1825 | 14363.6 | 0 | 98550 | 0 | 14.57% | 0% |  |  | 14.57% | 0% | 14.57% | 3 | TRUE
VLCNTR_6_VCEBT1 | Paired_BattStorage | 2024 | 1830 | 1197.6667 | 16 | 98820 | 0 | 1.212% | 0.01619% |  |  | 1.212% | 0.01619% | 1.228% | 1 | TRUE
VLCNTR_6_VCEBT2 | Paired_BattStorage | 2022 | 1825 | 14433.8333 | 0 | 155125 | 0 | 9.305% | 0% |  |  | 9.305% | 0% | 9.305% | 3 | TRUE
VLCNTR_6_VCEBT2 | Paired_BattStorage | 2023 | 1825 | 14161.2333 | 0 | 155125 | 0 | 9.129% | 0% |  |  | 9.129% | 0% | 9.129% | 2 | TRUE
VLCNTR_6_VCEBT2 | Paired_BattStorage | 2024 | 1830 | 1947 | 0 | 155550 | 0 | 1.252% | 0% |  |  | 1.252% | 0% | 1.252% | 1 | TRUE
WSTWND_2_M89BT2 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 1 | TRUE
WSTWND_2_M89BT2 | Paired_BattStorage | 2023 | 1105 | 2267.64 | 0 | 78013 | 720 | 2.907% | 0% | 11.83% | 0% | 6.426% | 4.666% | 11.09% | 2 | TRUE
WSTWND_2_M89BT2 | Paired_BattStorage | 2024 | 1830 | 15445.4267 | 0 | 129198 | 0 | 11.95% | 0% |  |  | 11.95% | 0% | 11.95% | 3 | TRUE
YELPIN_2_YP2BT1 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 2 | TRUE
YELPIN_2_YP2BT1 | Paired_BattStorage | 2023 | 795 | 5414.6933 | 0 | 51675 | 1030 | 10.48% | 0% | 11.83% | 0% | 11.24% | 6.675% | 17.91% | 3 | TRUE
YELPIN_2_YP2BT1 | Paired_BattStorage | 2024 | 1830 | 2764.6533 | 0 | 118950 | 0 | 2.324% | 0% |  |  | 2.324% | 0% | 2.324% | 1 | TRUE
YELPIN_2_YP2BT2 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 2 | TRUE
YELPIN_2_YP2BT2 | Paired_BattStorage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 11.83% | 0% | 11.83% | 0% | 11.83% | 3 | TRUE
YELPIN_2_YP2BT2 | Paired_BattStorage | 2024 | 1110 | 1990.15 | 0 | 31080 | 720 | 6.403% | 0% | 4.165% | 0.001944% | 5.523% | 1.639% | 7.162% | 1 | TRUE
YELPIN_2_YP2BT3 | Paired_BattStorage | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 10.3% | 0% | 10.3% | 0% | 10.3% | 2 | TRUE
YELPIN_2_YP2BT3 | Paired_BattStorage | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 11.83% | 0% | 11.83% | 0% | 11.83% | 3 | TRUE
YELPIN_2_YP2BT3 | Paired_BattStorage | 2024 | 1055 | 1244.9167 | 0 | 33760 | 775 | 3.688% | 0% | 4.165% | 0.001944% | 3.89% | 1.764% | 5.654% | 1 | TRUE
PALSEL_6_PLSSR1 | Paired_Solar_1Axis | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3 | TRUE
PALSEL_6_PLSSR1 | Paired_Solar_1Axis | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 3 | TRUE
PALSEL_6_PLSSR1 | Paired_Solar_1Axis | 2024 | 975 | 334 | 0 | 19500 | 855 | 1.713% | 0% | 1.713% | 0% | 1.713% | 0.8003% | 2.513% | 1 | TRUE
AGRICO_6_PL3N5 | Peaker | 2022 | 1825 | 568.3533 | 730.7462 | 41409.25 | 0 | 1.373% | 1.765% |  |  | 1.373% | 1.765% | 3.137% | 2 | TRUE
AGRICO_6_PL3N5 | Peaker | 2023 | 1825 | 490.833 | 500.39 | 41409.25 | 0 | 1.185% | 1.208% |  |  | 1.185% | 1.208% | 2.394% | 1 | TRUE
AGRICO_6_PL3N5 | Peaker | 2024 | 1830 | 228.0787 | 1145.61 | 41522.7 | 0 | 0.5493% | 2.759% |  |  | 0.5493% | 2.759% | 3.308% | 3 | TRUE
ALMEGT_1_UNIT 1 | Peaker | 2022 | 1825 | 16021.7333 | 2076 | 45625 | 0 | 35.12% | 4.55% |  |  | 35.12% | 4.55% | 39.67% | 3 | TRUE
ALMEGT_1_UNIT 1 | Peaker | 2023 | 1825 | 6049.3833 | 4814.6167 | 45625 | 0 | 13.26% | 10.55% |  |  | 13.26% | 10.55% | 23.81% | 2 | TRUE
ALMEGT_1_UNIT 1 | Peaker | 2024 | 1830 | 280.4333 | 2175.4 | 45750 | 0 | 0.613% | 4.755% |  |  | 0.613% | 4.755% | 5.368% | 1 | TRUE
ALMEGT_1_UNIT 2 | Peaker | 2022 | 1825 | 3397.75 | 2765 | 45625 | 0 | 7.447% | 6.06% |  |  | 7.447% | 6.06% | 13.51% | 2 | TRUE
ALMEGT_1_UNIT 2 | Peaker | 2023 | 1825 | 6184.1 | 4718.6167 | 45625 | 0 | 13.55% | 10.34% |  |  | 13.55% | 10.34% | 23.9% | 3 | TRUE
ALMEGT_1_UNIT 2 | Peaker | 2024 | 1830 | 280.4333 | 2131 | 45750 | 0 | 0.613% | 4.658% |  |  | 0.613% | 4.658% | 5.271% | 1 | TRUE
ANAHM_2_CANYN1 | Peaker | 2022 | 1825 | 1664.911 | 0 | 89808.25 | 0 | 1.854% | 0% |  |  | 1.854% | 0% | 1.854% | 1 | TRUE
ANAHM_2_CANYN1 | Peaker | 2023 | 1825 | 54471.3692 | 0 | 89808.25 | 0 | 60.65% | 0% |  |  | 60.65% | 0% | 60.65% | 2 | TRUE
ANAHM_2_CANYN1 | Peaker | 2024 | 1830 | 82625.2303 | 0 | 90054.3 | 0 | 91.75% | 0% |  |  | 91.75% | 0% | 91.75% | 3 | TRUE
ANAHM_2_CANYN2 | Peaker | 2022 | 1825 | 1276.816 | 0 | 87673 | 0 | 1.456% | 0% |  |  | 1.456% | 0% | 1.456% | 3 | TRUE
ANAHM_2_CANYN2 | Peaker | 2023 | 1825 | 144.12 | 0 | 87673 | 0 | 0.1644% | 0% |  |  | 0.1644% | 0% | 0.1644% | 2 | TRUE
ANAHM_2_CANYN2 | Peaker | 2024 | 1830 | 53.6447 | 0 | 87913.2 | 0 | 0.06102% | 0% |  |  | 0.06102% | 0% | 0.06102% | 1 | TRUE
ANAHM_2_CANYN3 | Peaker | 2022 | 1825 | 2010.0023 | 0 | 84844.25 | 0 | 2.369% | 0% |  |  | 2.369% | 0% | 2.369% | 1 | TRUE
ANAHM_2_CANYN3 | Peaker | 2023 | 1825 | 2789.4 | 0 | 84844.25 | 0 | 3.288% | 0% |  |  | 3.288% | 0% | 3.288% | 2 | TRUE
ANAHM_2_CANYN3 | Peaker | 2024 | 1830 | 4390.9805 | 0 | 85076.7 | 0 | 5.161% | 0% |  |  | 5.161% | 0% | 5.161% | 3 | TRUE
ANAHM_2_CANYN4 | Peaker | 2022 | 1825 | 1482.097 | 0 | 90885 | 0 | 1.631% | 0% |  |  | 1.631% | 0% | 1.631% | 2 | TRUE
ANAHM_2_CANYN4 | Peaker | 2023 | 1825 | 1766.7 | 0 | 90885 | 0 | 1.944% | 0% |  |  | 1.944% | 0% | 1.944% | 3 | TRUE
ANAHM_2_CANYN4 | Peaker | 2024 | 1830 | 839.13 | 0 | 91134 | 0 | 0.9208% | 0% |  |  | 0.9208% | 0% | 0.9208% | 1 | TRUE
BARRE_6_PEAKER | Peaker | 2022 | 1825 | 502.5093 | 5221.3375 | 89425 | 0 | 0.5619% | 5.839% |  |  | 0.5619% | 5.839% | 6.401% | 1 | TRUE
BARRE_6_PEAKER | Peaker | 2023 | 1825 | 2313.7982 | 6401.0867 | 89425 | 0 | 2.587% | 7.158% |  |  | 2.587% | 7.158% | 9.745% | 3 | TRUE
BARRE_6_PEAKER | Peaker | 2024 | 1830 | 847.4567 | 5697.3787 | 89670 | 0 | 0.9451% | 6.354% |  |  | 0.9451% | 6.354% | 7.299% | 2 | TRUE
BASICE_2_UNITS | Peaker | 2022 | 1825 | 12564.5 | 4576.1567 | 219000 | 0 | 5.737% | 2.09% |  |  | 5.737% | 2.09% | 7.827% | 2 | TRUE
BASICE_2_UNITS | Peaker | 2023 | 1825 | 2880.0592 | 2120.4602 | 219000 | 0 | 1.315% | 0.9682% |  |  | 1.315% | 0.9682% | 2.283% | 1 | TRUE
BASICE_2_UNITS | Peaker | 2024 | 1830 | 21112.6 | 2224.3667 | 219600 | 0 | 9.614% | 1.013% |  |  | 9.614% | 1.013% | 10.63% | 3 | TRUE
BDGRCK_1_UNITS | Peaker | 2022 | 1825 | 248.62 | 7047.78 | 87746 | 0 | 0.2833% | 8.032% |  |  | 0.2833% | 8.032% | 8.315% | 1 | TRUE
BDGRCK_1_UNITS | Peaker | 2023 | 1825 | 3801.275 | 5815.82 | 87746 | 0 | 4.332% | 6.628% |  |  | 4.332% | 6.628% | 10.96% | 3 | TRUE
BDGRCK_1_UNITS | Peaker | 2024 | 1830 | 1988.9667 | 6503.28 | 87986.4 | 0 | 2.261% | 7.391% |  |  | 2.261% | 7.391% | 9.652% | 2 | TRUE
BEARMT_1_UNIT | Peaker | 2022 | 1825 | 3.8 | 6011.86 | 89808.25 | 0 | 0.004231% | 6.694% |  |  | 0.004231% | 6.694% | 6.698% | 1 | TRUE
BEARMT_1_UNIT | Peaker | 2023 | 1825 | 796.3083 | 7565.42 | 89808.25 | 0 | 0.8867% | 8.424% |  |  | 0.8867% | 8.424% | 9.311% | 3 | TRUE
BEARMT_1_UNIT | Peaker | 2024 | 1830 | 235.6333 | 7152.9883 | 90054.3 | 0 | 0.2617% | 7.943% |  |  | 0.2617% | 7.943% | 8.205% | 2 | TRUE
BOGUE_1_UNITA1 | Peaker | 2022 | 1825 | 2433.231 | 792.527 | 88859.25 | 0 | 2.738% | 0.8919% |  |  | 2.738% | 0.8919% | 3.63% | 2 | TRUE
BOGUE_1_UNITA1 | Peaker | 2023 | 1825 | 497.5502 | 506.0497 | 88859.25 | 0 | 0.5599% | 0.5695% |  |  | 0.5599% | 0.5695% | 1.129% | 1 | TRUE
BOGUE_1_UNITA1 | Peaker | 2024 | 1830 | 1623.6662 | 2210.1625 | 89102.7 | 0 | 1.822% | 2.48% |  |  | 1.822% | 2.48% | 4.303% | 3 | TRUE
BORDER_6_UNITA1 | Peaker | 2022 | 1825 | 6295.6698 | 353.5093 | 93531.25 | 0 | 6.731% | 0.378% |  |  | 6.731% | 0.378% | 7.109% | 3 | TRUE
BORDER_6_UNITA1 | Peaker | 2023 | 1825 | 2674.2067 | 6.375 | 93531.25 | 0 | 2.859% | 0.006816% |  |  | 2.859% | 0.006816% | 2.866% | 1 | TRUE
BORDER_6_UNITA1 | Peaker | 2024 | 1830 | 4377.06 | 0 | 93787.5 | 0 | 4.667% | 0% |  |  | 4.667% | 0% | 4.667% | 2 | TRUE
CARLS1_2_CARCT1 | Peaker | 2022 | 1825 | 105427.8475 | 40299.7917 | 770150 | 0 | 13.69% | 5.233% |  |  | 13.69% | 5.233% | 18.92% | 3 | TRUE
CARLS1_2_CARCT1 | Peaker | 2023 | 1825 | 6464.6767 | 9256.8 | 770150 | 0 | 0.8394% | 1.202% |  |  | 0.8394% | 1.202% | 2.041% | 2 | TRUE
CARLS1_2_CARCT1 | Peaker | 2024 | 1830 | 6580.7483 | 4390.2 | 772260 | 0 | 0.8521% | 0.5685% |  |  | 0.8521% | 0.5685% | 1.421% | 1 | TRUE
CARLS2_1_CARCT1 | Peaker | 2022 | 1825 | 1566.162 | 1753.57 | 192537.5 | 0 | 0.8134% | 0.9108% |  |  | 0.8134% | 0.9108% | 1.724% | 2 | TRUE
CARLS2_1_CARCT1 | Peaker | 2023 | 1825 | 248.2663 | 811.9017 | 192537.5 | 0 | 0.1289% | 0.4217% |  |  | 0.1289% | 0.4217% | 0.5506% | 1 | TRUE
CARLS2_1_CARCT1 | Peaker | 2024 | 1830 | 9143.645 | 2529.41 | 193065 | 0 | 4.736% | 1.31% |  |  | 4.736% | 1.31% | 6.046% | 3 | TRUE
CENTER_6_PEAKER | Peaker | 2022 | 1825 | 1251.195 | 552.83 | 86322.5 | 0 | 1.449% | 0.6404% |  |  | 1.449% | 0.6404% | 2.09% | 1 | TRUE
CENTER_6_PEAKER | Peaker | 2023 | 1825 | 5212.0317 | 608.21 | 86322.5 | 0 | 6.038% | 0.7046% |  |  | 6.038% | 0.7046% | 6.742% | 3 | TRUE
CENTER_6_PEAKER | Peaker | 2024 | 1830 | 2152.5077 | 617.4 | 86559 | 0 | 2.487% | 0.7133% |  |  | 2.487% | 0.7133% | 3.2% | 2 | TRUE
CENTRY_6_PL1X4 | Peaker | 2022 | 1825 | 7397.9833 | 1217 | 75555 | 0 | 9.792% | 1.611% |  |  | 9.792% | 1.611% | 11.4% | 2 | TRUE
CENTRY_6_PL1X4 | Peaker | 2023 | 1825 | 5120.6 | 0 | 75555 | 0 | 6.777% | 0% |  |  | 6.777% | 0% | 6.777% | 1 | TRUE
CENTRY_6_PL1X4 | Peaker | 2024 | 1830 | 13294.35 | 0 | 75762 | 0 | 17.55% | 0% |  |  | 17.55% | 0% | 17.55% | 3 | TRUE
CHALK_1_UNIT | Peaker | 2022 | 1825 | 720.6233 | 6141.9385 | 88822.75 | 0 | 0.8113% | 6.915% |  |  | 0.8113% | 6.915% | 7.726% | 2 | TRUE
CHALK_1_UNIT | Peaker | 2023 | 1825 | 196.0567 | 7267.615 | 88822.75 | 0 | 0.2207% | 8.182% |  |  | 0.2207% | 8.182% | 8.403% | 3 | TRUE
CHALK_1_UNIT | Peaker | 2024 | 1830 | 88 | 6687.5 | 89066.1 | 0 | 0.0988% | 7.508% |  |  | 0.0988% | 7.508% | 7.607% | 1 | TRUE
COCOPP_2_CTG1 | Peaker | 2022 | 1825 | 0 | 11552.8073 | 372665 | 0 | 0% | 3.1% |  |  | 0% | 3.1% | 3.1% | 2 | TRUE
COCOPP_2_CTG1 | Peaker | 2023 | 1825 | 5555.8867 | 11132.31 | 372665 | 0 | 1.491% | 2.987% |  |  | 1.491% | 2.987% | 4.478% | 3 | TRUE
COCOPP_2_CTG1 | Peaker | 2024 | 1830 | 0 | 11324.81 | 373686 | 0 | 0% | 3.031% |  |  | 0% | 3.031% | 3.031% | 1 | TRUE
COCOPP_2_CTG2 | Peaker | 2022 | 1825 | 962.24 | 10388.3055 | 369927.5 | 0 | 0.2601% | 2.808% |  |  | 0.2601% | 2.808% | 3.068% | 2 | TRUE
COCOPP_2_CTG2 | Peaker | 2023 | 1825 | 11145.29 | 10073.09 | 369927.5 | 0 | 3.013% | 2.723% |  |  | 3.013% | 2.723% | 5.736% | 3 | TRUE
COCOPP_2_CTG2 | Peaker | 2024 | 1830 | 182.8933 | 10355.36 | 370941 | 0 | 0.04931% | 2.792% |  |  | 0.04931% | 2.792% | 2.841% | 1 | TRUE
COCOPP_2_CTG3 | Peaker | 2022 | 1825 | 1077.9 | 22773.3557 | 381352 | 0 | 0.2827% | 5.972% |  |  | 0.2827% | 5.972% | 6.254% | 1 | TRUE
COCOPP_2_CTG3 | Peaker | 2023 | 1825 | 5347.7723 | 22746.0767 | 381352 | 0 | 1.402% | 5.965% |  |  | 1.402% | 5.965% | 7.367% | 3 | TRUE
COCOPP_2_CTG3 | Peaker | 2024 | 1830 | 6459.8593 | 19955.8495 | 382396.8 | 0 | 1.689% | 5.219% |  |  | 1.689% | 5.219% | 6.908% | 2 | TRUE
COCOPP_2_CTG4 | Peaker | 2022 | 1825 | 2013.475 | 13270.9023 | 372829.25 | 0 | 0.5401% | 3.56% |  |  | 0.5401% | 3.56% | 4.1% | 1 | TRUE
COCOPP_2_CTG4 | Peaker | 2023 | 1825 | 3714.2415 | 12826.4432 | 372829.25 | 0 | 0.9962% | 3.44% |  |  | 0.9962% | 3.44% | 4.437% | 3 | TRUE
COCOPP_2_CTG4 | Peaker | 2024 | 1830 | 5288.7945 | 10552.7347 | 373850.7 | 0 | 1.415% | 2.823% |  |  | 1.415% | 2.823% | 4.237% | 2 | TRUE
COLTON_6_AGUAM1 | Peaker | 2022 | 1825 | 0 | 1827.1603 | 78475 | 0 | 0% | 2.328% |  |  | 0% | 2.328% | 2.328% | 2 | TRUE
COLTON_6_AGUAM1 | Peaker | 2023 | 1825 | 781.1833 | 0 | 78475 | 0 | 0.9955% | 0% |  |  | 0.9955% | 0% | 0.9955% | 1 | TRUE
COLTON_6_AGUAM1 | Peaker | 2024 | 1830 | 5478 | 3 | 78690 | 0 | 6.961% | 0.003812% |  |  | 6.961% | 0.003812% | 6.965% | 3 | TRUE
CSCGNR_1_UNIT 1 | Peaker | 2022 | 1825 | 459.3475 | 11.25 | 45168.75 | 0 | 1.017% | 0.02491% |  |  | 1.017% | 0.02491% | 1.042% | 1 | TRUE
CSCGNR_1_UNIT 1 | Peaker | 2023 | 1825 | 1732.5 | 0 | 45168.75 | 0 | 3.836% | 0% |  |  | 3.836% | 0% | 3.836% | 2 | TRUE
CSCGNR_1_UNIT 1 | Peaker | 2024 | 1830 | 3406.0125 | 1640.0825 | 45292.5 | 0 | 7.52% | 3.621% |  |  | 7.52% | 3.621% | 11.14% | 3 | TRUE
CSCGNR_1_UNIT 2 | Peaker | 2022 | 1825 | 14727.7365 | 0 | 45168.75 | 0 | 32.61% | 0% |  |  | 32.61% | 0% | 32.61% | 3 | TRUE
CSCGNR_1_UNIT 2 | Peaker | 2023 | 1825 | 9715.6793 | 0 | 45168.75 | 0 | 21.51% | 0% |  |  | 21.51% | 0% | 21.51% | 2 | TRUE
CSCGNR_1_UNIT 2 | Peaker | 2024 | 1830 | 866.6625 | 1800.0492 | 45292.5 | 0 | 1.913% | 3.974% |  |  | 1.913% | 3.974% | 5.888% | 1 | TRUE
DOUBLC_1_UNITS | Peaker | 2022 | 1825 | 852.41 | 3668.41 | 95319.75 | 0 | 0.8943% | 3.849% |  |  | 0.8943% | 3.849% | 4.743% | 1 | TRUE
DOUBLC_1_UNITS | Peaker | 2023 | 1825 | 6338.2617 | 4058.62 | 95319.75 | 0 | 6.649% | 4.258% |  |  | 6.649% | 4.258% | 10.91% | 2 | TRUE
DOUBLC_1_UNITS | Peaker | 2024 | 1830 | 13846.7793 | 4970.6038 | 95580.9 | 0 | 14.49% | 5.2% |  |  | 14.49% | 5.2% | 19.69% | 3 | TRUE
DREWS_6_PL1X4 | Peaker | 2022 | 1825 | 18908.5 | 1962 | 75555 | 0 | 25.03% | 2.597% |  |  | 25.03% | 2.597% | 27.62% | 3 | TRUE
DREWS_6_PL1X4 | Peaker | 2023 | 1825 | 7816.2225 | 0 | 75555 | 0 | 10.35% | 0% |  |  | 10.35% | 0% | 10.35% | 2 | TRUE
DREWS_6_PL1X4 | Peaker | 2024 | 1830 | 4750.2 | 0 | 75762 | 0 | 6.27% | 0% |  |  | 6.27% | 0% | 6.27% | 1 | TRUE
ELCAJN_6_LM6K | Peaker | 2022 | 1825 | 4333.54 | 488.3 | 87782.5 | 0 | 4.937% | 0.5563% |  |  | 4.937% | 0.5563% | 5.493% | 2 | TRUE
ELCAJN_6_LM6K | Peaker | 2023 | 1825 | 14470.015 | 13 | 87782.5 | 0 | 16.48% | 0.01481% |  |  | 16.48% | 0.01481% | 16.5% | 3 | TRUE
ELCAJN_6_LM6K | Peaker | 2024 | 1830 | 1742.6433 | 490.4 | 88023 | 0 | 1.98% | 0.5571% |  |  | 1.98% | 0.5571% | 2.537% | 1 | TRUE
ELCAJN_6_UNITA1 | Peaker | 2022 | 1825 | 6009.3527 | 0 | 82891.5 | 0 | 7.25% | 0% |  |  | 7.25% | 0% | 7.25% | 3 | TRUE
ELCAJN_6_UNITA1 | Peaker | 2023 | 1825 | 3515.8047 | 0 | 82891.5 | 0 | 4.241% | 0% |  |  | 4.241% | 0% | 4.241% | 2 | TRUE
ELCAJN_6_UNITA1 | Peaker | 2024 | 1830 | 3346.4127 | 0 | 83118.6 | 0 | 4.026% | 0% |  |  | 4.026% | 0% | 4.026% | 1 | TRUE
ESCNDO_6_PL1X2 | Peaker | 2022 | 1825 | 5882.2068 | 587.76 | 88895.75 | 0 | 6.617% | 0.6612% |  |  | 6.617% | 0.6612% | 7.278% | 2 | TRUE
ESCNDO_6_PL1X2 | Peaker | 2023 | 1825 | 8501.196 | 279.87 | 88895.75 | 0 | 9.563% | 0.3148% |  |  | 9.563% | 0.3148% | 9.878% | 3 | TRUE
ESCNDO_6_PL1X2 | Peaker | 2024 | 1830 | 5587.1767 | 324.3 | 89139.3 | 0 | 6.268% | 0.3638% |  |  | 6.268% | 0.3638% | 6.632% | 1 | TRUE
ESCNDO_6_UNITB1 | Peaker | 2022 | 1825 | 11757.3665 | 193.44 | 93002 | 0 | 12.64% | 0.208% |  |  | 12.64% | 0.208% | 12.85% | 3 | TRUE
ESCNDO_6_UNITB1 | Peaker | 2023 | 1825 | 7274.4427 | 0 | 93002 | 0 | 7.822% | 0% |  |  | 7.822% | 0% | 7.822% | 2 | TRUE
ESCNDO_6_UNITB1 | Peaker | 2024 | 1830 | 2310.062 | 0 | 93256.8 | 0 | 2.477% | 0% |  |  | 2.477% | 0% | 2.477% | 1 | TRUE
ESCO_6_GLMQF | Peaker | 2022 | 1825 | 11186.1247 | 0 | 91067.5 | 0 | 12.28% | 0% |  |  | 12.28% | 0% | 12.28% | 3 | TRUE
ESCO_6_GLMQF | Peaker | 2023 | 1825 | 9582.93 | 0.69 | 91067.5 | 0 | 10.52% | 0.0007577% |  |  | 10.52% | 0.0007577% | 10.52% | 2 | TRUE
ESCO_6_GLMQF | Peaker | 2024 | 1830 | 1372.2567 | 1422.95 | 91317 | 0 | 1.503% | 1.558% |  |  | 1.503% | 1.558% | 3.061% | 1 | TRUE
ETIWND_2_UNIT1 | Peaker | 2022 | 1825 | 0 | 0 | 61320 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
ETIWND_2_UNIT1 | Peaker | 2023 | 1825 | 45425.34 | 0 | 61320 | 0 | 74.08% | 0% |  |  | 74.08% | 0% | 74.08% | 3 | TRUE
ETIWND_2_UNIT1 | Peaker | 2024 | 1830 | 3102.96 | 0 | 61488 | 0 | 5.046% | 0% |  |  | 5.046% | 0% | 5.046% | 2 | TRUE
ETIWND_6_GRPLND | Peaker | 2022 | 1825 | 1165.8355 | 1124.7367 | 83293 | 0 | 1.4% | 1.35% |  |  | 1.4% | 1.35% | 2.75% | 1 | TRUE
ETIWND_6_GRPLND | Peaker | 2023 | 1825 | 2716.2303 | 1225.4233 | 83293 | 0 | 3.261% | 1.471% |  |  | 3.261% | 1.471% | 4.732% | 3 | TRUE
ETIWND_6_GRPLND | Peaker | 2024 | 1830 | 1721.233 | 1097.99 | 83521.2 | 0 | 2.061% | 1.315% |  |  | 2.061% | 1.315% | 3.375% | 2 | TRUE
GILRPP_1_PL1X2 | Peaker | 2022 | 1825 | 411.6667 | 88.24 | 173740 | 0 | 0.2369% | 0.05079% |  |  | 0.2369% | 0.05079% | 0.2877% | 2 | TRUE
GILRPP_1_PL1X2 | Peaker | 2023 | 1825 | 56.2083 | 0 | 173740 | 0 | 0.03235% | 0% |  |  | 0.03235% | 0% | 0.03235% | 1 | TRUE
GILRPP_1_PL1X2 | Peaker | 2024 | 1830 | 479.8767 | 57.9867 | 174216 | 0 | 0.2754% | 0.03328% |  |  | 0.2754% | 0.03328% | 0.3087% | 3 | TRUE
GILRPP_1_PL3X4 | Peaker | 2022 | 1825 | 1233.1667 | 6 | 84315 | 0 | 1.463% | 0.007116% |  |  | 1.463% | 0.007116% | 1.47% | 3 | TRUE
GILRPP_1_PL3X4 | Peaker | 2023 | 1825 | 0 | 0 | 84315 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
GILRPP_1_PL3X4 | Peaker | 2024 | 1830 | 0 | 0 | 84546 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
GLNARM_7_UNIT 1 | Peaker | 2022 | 1825 | 511.8 | 0 | 40387.25 | 0 | 1.267% | 0% |  |  | 1.267% | 0% | 1.267% | 2 | TRUE
GLNARM_7_UNIT 1 | Peaker | 2023 | 1825 | 7368.1835 | 0 | 40387.25 | 0 | 18.24% | 0% |  |  | 18.24% | 0% | 18.24% | 3 | TRUE
GLNARM_7_UNIT 1 | Peaker | 2024 | 1830 | 357.7407 | 0 | 40497.9 | 0 | 0.8834% | 0% |  |  | 0.8834% | 0% | 0.8834% | 1 | TRUE
GLNARM_7_UNIT 2 | Peaker | 2022 | 1825 | 2037.3733 | 0 | 40843.5 | 0 | 4.988% | 0% |  |  | 4.988% | 0% | 4.988% | 3 | TRUE
GLNARM_7_UNIT 2 | Peaker | 2023 | 1825 | 988.45 | 0 | 40843.5 | 0 | 2.42% | 0% |  |  | 2.42% | 0% | 2.42% | 1 | TRUE
GLNARM_7_UNIT 2 | Peaker | 2024 | 1830 | 1541.6445 | 0 | 40955.4 | 0 | 3.764% | 0% |  |  | 3.764% | 0% | 3.764% | 2 | TRUE
GLNARM_7_UNIT 3 | Peaker | 2022 | 1825 | 1338.1188 | 0 | 81814.75 | 0 | 1.636% | 0% |  |  | 1.636% | 0% | 1.636% | 2 | TRUE
GLNARM_7_UNIT 3 | Peaker | 2023 | 1825 | 4634.4527 | 0 | 81814.75 | 0 | 5.665% | 0% |  |  | 5.665% | 0% | 5.665% | 3 | TRUE
GLNARM_7_UNIT 3 | Peaker | 2024 | 1830 | 562.2245 | 96.3933 | 82038.9 | 0 | 0.6853% | 0.1175% |  |  | 0.6853% | 0.1175% | 0.8028% | 1 | TRUE
GLNARM_7_UNIT 4 | Peaker | 2022 | 1825 | 7552.1203 | 0 | 77416.5 | 0 | 9.755% | 0% |  |  | 9.755% | 0% | 9.755% | 3 | TRUE
GLNARM_7_UNIT 4 | Peaker | 2023 | 1825 | 3495.98 | 0 | 77416.5 | 0 | 4.516% | 0% |  |  | 4.516% | 0% | 4.516% | 2 | TRUE
GLNARM_7_UNIT 4 | Peaker | 2024 | 1830 | 489.649 | 38.9217 | 77628.6 | 0 | 0.6308% | 0.05014% |  |  | 0.6308% | 0.05014% | 0.6809% | 1 | TRUE
GOLETA_6_ELLWOD | Peaker | 2022 | 1825 | 6499.8 | 0 | 98550 | 0 | 6.595% | 0% |  |  | 6.595% | 0% | 6.595% | 2 | TRUE
GOLETA_6_ELLWOD | Peaker | 2023 | 1825 | 648.9 | 0 | 98550 | 0 | 0.6584% | 0% |  |  | 0.6584% | 0% | 0.6584% | 1 | TRUE
GOLETA_6_ELLWOD | Peaker | 2024 | 1830 | 7812 | 0 | 98820 | 0 | 7.905% | 0% |  |  | 7.905% | 0% | 7.905% | 3 | TRUE
HENRTA_6_ELCTG1 | Peaker | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 5.367% | 2.271% | 5.367% | 2.271% | 7.638% | 1 | TRUE
HENRTA_6_ELCTG1 | Peaker | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.818% | 2.003% | 6.818% | 2.003% | 8.821% | 3 | TRUE
HENRTA_6_ELCTG1 | Peaker | 2024 | 0 | 2325 | 0 | 0 | 1830 |  |  | 6.005% | 2.402% | 6.005% | 2.402% | 8.406% | 2 | TRUE
HENRTA_6_ELCTG2 | Peaker | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 5.367% | 2.271% | 5.367% | 2.271% | 7.638% | 1 | TRUE
HENRTA_6_ELCTG2 | Peaker | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.818% | 2.003% | 6.818% | 2.003% | 8.821% | 3 | TRUE
HENRTA_6_ELCTG2 | Peaker | 2024 | 0 | 2325 | 0 | 0 | 1830 |  |  | 6.005% | 2.402% | 6.005% | 2.402% | 8.406% | 2 | TRUE
HINSON_6_LBECH1 | Peaker | 2022 | 1825 | 378 | 14.5667 | 114975 | 0 | 0.3288% | 0.01267% |  |  | 0.3288% | 0.01267% | 0.3414% | 2 | TRUE
HINSON_6_LBECH1 | Peaker | 2023 | 1825 | 3344.25 | 0 | 114975 | 0 | 2.909% | 0% |  |  | 2.909% | 0% | 2.909% | 3 | TRUE
HINSON_6_LBECH1 | Peaker | 2024 | 1830 | 0 | 0 | 115290 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
HINSON_6_LBECH2 | Peaker | 2022 | 1825 | 0 | 9.5 | 114975 | 0 | 0% | 0.008263% |  |  | 0% | 0.008263% | 0.008263% | 2 | TRUE
HINSON_6_LBECH2 | Peaker | 2023 | 1825 | 2724.75 | 0 | 114975 | 0 | 2.37% | 0% |  |  | 2.37% | 0% | 2.37% | 3 | TRUE
HINSON_6_LBECH2 | Peaker | 2024 | 1830 | 0 | 0 | 115290 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
HINSON_6_LBECH3 | Peaker | 2022 | 1825 | 0 | 34.8333 | 114975 | 0 | 0% | 0.0303% |  |  | 0% | 0.0303% | 0.0303% | 1 | TRUE
HINSON_6_LBECH3 | Peaker | 2023 | 1825 | 157.5 | 0 | 114975 | 0 | 0.137% | 0% |  |  | 0.137% | 0% | 0.137% | 2 | TRUE
HINSON_6_LBECH3 | Peaker | 2024 | 1830 | 40119.45 | 0 | 115290 | 0 | 34.8% | 0% |  |  | 34.8% | 0% | 34.8% | 3 | TRUE
HINSON_6_LBECH4 | Peaker | 2022 | 1825 | 0 | 4.75 | 114975 | 0 | 0% | 0.004131% |  |  | 0% | 0.004131% | 0.004131% | 2 | TRUE
HINSON_6_LBECH4 | Peaker | 2023 | 1825 | 601.65 | 0 | 114975 | 0 | 0.5233% | 0% |  |  | 0.5233% | 0% | 0.5233% | 3 | TRUE
HINSON_6_LBECH4 | Peaker | 2024 | 1830 | 0 | 0 | 115290 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
INDIGO_1_UNIT 1 | Peaker | 2022 | 1825 | 871.94 | 2818.475 | 82672.5 | 0 | 1.055% | 3.409% |  |  | 1.055% | 3.409% | 4.464% | 2 | TRUE
INDIGO_1_UNIT 1 | Peaker | 2023 | 1825 | 6693.195 | 1751.7317 | 82672.5 | 0 | 8.096% | 2.119% |  |  | 8.096% | 2.119% | 10.21% | 3 | TRUE
INDIGO_1_UNIT 1 | Peaker | 2024 | 1830 | 856.2767 | 2530 | 82899 | 0 | 1.033% | 3.052% |  |  | 1.033% | 3.052% | 4.085% | 1 | TRUE
INDIGO_1_UNIT 2 | Peaker | 2022 | 1825 | 541.42 | 3998.5 | 82672.5 | 0 | 0.6549% | 4.837% |  |  | 0.6549% | 4.837% | 5.491% | 2 | TRUE
INDIGO_1_UNIT 2 | Peaker | 2023 | 1825 | 11289.6983 | 2355.955 | 82672.5 | 0 | 13.66% | 2.85% |  |  | 13.66% | 2.85% | 16.51% | 3 | TRUE
INDIGO_1_UNIT 2 | Peaker | 2024 | 1830 | 45.3 | 3404 | 82899 | 0 | 0.05464% | 4.106% |  |  | 0.05464% | 4.106% | 4.161% | 1 | TRUE
INDIGO_1_UNIT 3 | Peaker | 2022 | 1825 | 3736.6833 | 3730.5 | 82672.5 | 0 | 4.52% | 4.512% |  |  | 4.52% | 4.512% | 9.032% | 2 | TRUE
INDIGO_1_UNIT 3 | Peaker | 2023 | 1825 | 9831.9733 | 2684.0583 | 82672.5 | 0 | 11.89% | 3.247% |  |  | 11.89% | 3.247% | 15.14% | 3 | TRUE
INDIGO_1_UNIT 3 | Peaker | 2024 | 1830 | 304.3583 | 3668.8 | 82899 | 0 | 0.3671% | 4.426% |  |  | 0.3671% | 4.426% | 4.793% | 1 | TRUE
KELSO_2_UNITS | Peaker | 2022 | 1825 | 388.028 | 7852.82 | 361404.75 | 0 | 0.1074% | 2.173% |  |  | 0.1074% | 2.173% | 2.28% | 1 | TRUE
KELSO_2_UNITS | Peaker | 2023 | 1825 | 14696.7098 | 10429.1267 | 361404.75 | 0 | 4.067% | 2.886% |  |  | 4.067% | 2.886% | 6.952% | 2 | TRUE
KELSO_2_UNITS | Peaker | 2024 | 1830 | 26602.4592 | 9190.57 | 362394.9 | 0 | 7.341% | 2.536% |  |  | 7.341% | 2.536% | 9.877% | 3 | TRUE
KERNFT_1_UNITS | Peaker | 2022 | 1825 | 17855.6433 | 6090.26 | 95630 | 0 | 18.67% | 6.369% |  |  | 18.67% | 6.369% | 25.04% | 3 | TRUE
KERNFT_1_UNITS | Peaker | 2023 | 1825 | 2247.36 | 5336.5 | 95630 | 0 | 2.35% | 5.58% |  |  | 2.35% | 5.58% | 7.93% | 2 | TRUE
KERNFT_1_UNITS | Peaker | 2024 | 1830 | 2505.05 | 4836.7367 | 95892 | 0 | 2.612% | 5.044% |  |  | 2.612% | 5.044% | 7.656% | 1 | TRUE
KINGCO_1_KINGBR | Peaker | 2022 | 1825 | 196.65 | 0 | 62962.5 | 0 | 0.3123% | 0% |  |  | 0.3123% | 0% | 0.3123% | 2 | TRUE
KINGCO_1_KINGBR | Peaker | 2023 | 1825 | 150.075 | 0 | 62962.5 | 0 | 0.2384% | 0% |  |  | 0.2384% | 0% | 0.2384% | 1 | TRUE
KINGCO_1_KINGBR | Peaker | 2024 | 1830 | 1777.26 | 0 | 63135 | 0 | 2.815% | 0% |  |  | 2.815% | 0% | 2.815% | 3 | TRUE
KNGCTY_6_UNITA1 | Peaker | 2022 | 1825 | 1843.8357 | 839.1 | 81395 | 0 | 2.265% | 1.031% |  |  | 2.265% | 1.031% | 3.296% | 2 | TRUE
KNGCTY_6_UNITA1 | Peaker | 2023 | 1825 | 1594.02 | 0 | 81395 | 0 | 1.958% | 0% |  |  | 1.958% | 0% | 1.958% | 1 | TRUE
KNGCTY_6_UNITA1 | Peaker | 2024 | 1830 | 433.2533 | 2284 | 81618 | 0 | 0.5308% | 2.798% |  |  | 0.5308% | 2.798% | 3.329% | 3 | TRUE
LARKSP_6_UNIT 1 | Peaker | 2022 | 1825 | 3224.9317 | 2608.5 | 89425 | 0 | 3.606% | 2.917% |  |  | 3.606% | 2.917% | 6.523% | 1 | TRUE
LARKSP_6_UNIT 1 | Peaker | 2023 | 1825 | 6438.9333 | 2661.51 | 89425 | 0 | 7.2% | 2.976% |  |  | 7.2% | 2.976% | 10.18% | 3 | TRUE
LARKSP_6_UNIT 1 | Peaker | 2024 | 1830 | 5285.1 | 2553.5 | 89670 | 0 | 5.894% | 2.848% |  |  | 5.894% | 2.848% | 8.742% | 2 | TRUE
LARKSP_6_UNIT 2 | Peaker | 2022 | 1825 | 3252.6477 | 2356 | 89425 | 0 | 3.637% | 2.635% |  |  | 3.637% | 2.635% | 6.272% | 2 | TRUE
LARKSP_6_UNIT 2 | Peaker | 2023 | 1825 | 8589.6233 | 1688.9317 | 89425 | 0 | 9.605% | 1.889% |  |  | 9.605% | 1.889% | 11.49% | 3 | TRUE
LARKSP_6_UNIT 2 | Peaker | 2024 | 1830 | 712.9 | 2553.5 | 89670 | 0 | 0.795% | 2.848% |  |  | 0.795% | 2.848% | 3.643% | 1 | TRUE
LIVOAK_1_UNIT 1 | Peaker | 2022 | 1825 | 633.3567 | 12209.9667 | 90702.5 | 0 | 0.6983% | 13.46% |  |  | 0.6983% | 13.46% | 14.16% | 2 | TRUE
LIVOAK_1_UNIT 1 | Peaker | 2023 | 1825 | 7318.545 | 9645.9 | 90702.5 | 0 | 8.069% | 10.63% |  |  | 8.069% | 10.63% | 18.7% | 3 | TRUE
LIVOAK_1_UNIT 1 | Peaker | 2024 | 1830 | 1660.95 | 8476.46 | 90951 | 0 | 1.826% | 9.32% |  |  | 1.826% | 9.32% | 11.15% | 1 | TRUE
LMBEPK_2_UNITA1 | Peaker | 2022 | 1825 | 3134.3983 | 28.5 | 86687.5 | 0 | 3.616% | 0.03288% |  |  | 3.616% | 0.03288% | 3.649% | 3 | TRUE
LMBEPK_2_UNITA1 | Peaker | 2023 | 1825 | 1559.3592 | 0 | 86687.5 | 0 | 1.799% | 0% |  |  | 1.799% | 0% | 1.799% | 1 | TRUE
LMBEPK_2_UNITA1 | Peaker | 2024 | 1830 | 559.7083 | 1139.4833 | 86925 | 0 | 0.6439% | 1.311% |  |  | 0.6439% | 1.311% | 1.955% | 2 | TRUE
LMBEPK_2_UNITA2 | Peaker | 2022 | 1825 | 919.9738 | 117.1933 | 86870 | 0 | 1.059% | 0.1349% |  |  | 1.059% | 0.1349% | 1.194% | 1 | TRUE
LMBEPK_2_UNITA2 | Peaker | 2023 | 1825 | 6616.1958 | 6.11 | 86870 | 0 | 7.616% | 0.007033% |  |  | 7.616% | 0.007033% | 7.623% | 3 | TRUE
LMBEPK_2_UNITA2 | Peaker | 2024 | 1830 | 146.4933 | 1192.6933 | 87108 | 0 | 0.1682% | 1.369% |  |  | 0.1682% | 1.369% | 1.537% | 2 | TRUE
LMBEPK_2_UNITA3 | Peaker | 2022 | 1825 | 871.0708 | 69.3125 | 87143.75 | 0 | 0.9996% | 0.07954% |  |  | 0.9996% | 0.07954% | 1.079% | 2 | TRUE
LMBEPK_2_UNITA3 | Peaker | 2023 | 1825 | 448.0542 | 89.4417 | 87143.75 | 0 | 0.5142% | 0.1026% |  |  | 0.5142% | 0.1026% | 0.6168% | 1 | TRUE
LMBEPK_2_UNITA3 | Peaker | 2024 | 1830 | 754.9625 | 1564.55 | 87382.5 | 0 | 0.864% | 1.79% |  |  | 0.864% | 1.79% | 2.654% | 3 | TRUE
LODI25_2_UNIT 1 | Peaker | 2022 | 1825 | 562.3167 | 4594.85 | 45625 | 0 | 1.232% | 10.07% |  |  | 1.232% | 10.07% | 11.3% | 2 | TRUE
LODI25_2_UNIT 1 | Peaker | 2023 | 1825 | 3318 | 3736 | 45625 | 0 | 7.272% | 8.188% |  |  | 7.272% | 8.188% | 15.46% | 3 | TRUE
LODI25_2_UNIT 1 | Peaker | 2024 | 1830 | 906.75 | 3933 | 45750 | 0 | 1.982% | 8.597% |  |  | 1.982% | 8.597% | 10.58% | 1 | TRUE
MALAGA_1_AUCTG1 | Peaker | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 5.367% | 2.271% | 5.367% | 2.271% | 7.638% | 1 | TRUE
MALAGA_1_AUCTG1 | Peaker | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.818% | 2.003% | 6.818% | 2.003% | 8.821% | 2 | TRUE
MALAGA_1_AUCTG1 | Peaker | 2024 | 220 | 3594.5 | 0 | 12166 | 1610 | 29.55% | 0% | 6.005% | 2.402% | 8.835% | 5.283% | 14.12% | 3 | TRUE
MALAGA_1_AUCTG2 | Peaker | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | 5.367% | 2.271% | 5.367% | 2.271% | 7.638% | 1 | TRUE
MALAGA_1_AUCTG2 | Peaker | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | 6.818% | 2.003% | 6.818% | 2.003% | 8.821% | 2 | TRUE
MALAGA_1_AUCTG2 | Peaker | 2024 | 220 | 3594.5 | 0 | 12166 | 1610 | 29.55% | 0% | 6.005% | 2.402% | 8.835% | 5.283% | 14.12% | 3 | TRUE
MIRLOM_6_PEAKER | Peaker | 2022 | 1825 | 337.4373 | 3555.0933 | 86103.5 | 0 | 0.3919% | 4.129% |  |  | 0.3919% | 4.129% | 4.521% | 2 | TRUE
MIRLOM_6_PEAKER | Peaker | 2023 | 1825 | 859.8183 | 2896.98 | 86103.5 | 0 | 0.9986% | 3.365% |  |  | 0.9986% | 3.365% | 4.363% | 1 | TRUE
MIRLOM_6_PEAKER | Peaker | 2024 | 1830 | 2269.7918 | 3189.91 | 86339.4 | 0 | 2.629% | 3.695% |  |  | 2.629% | 3.695% | 6.324% | 3 | TRUE
MKTRCK_1_UNIT 1 | Peaker | 2022 | 1825 | 8642.155 | 3196.59 | 87089 | 0 | 9.923% | 3.67% |  |  | 9.923% | 3.67% | 13.59% | 1 | TRUE
MKTRCK_1_UNIT 1 | Peaker | 2023 | 1825 | 6771.15 | 5413.28 | 87089 | 0 | 7.775% | 6.216% |  |  | 7.775% | 6.216% | 13.99% | 2 | TRUE
MKTRCK_1_UNIT 1 | Peaker | 2024 | 1830 | 7468.9033 | 5888.86 | 87327.6 | 0 | 8.553% | 6.743% |  |  | 8.553% | 6.743% | 15.3% | 3 | TRUE
MNDALY_6_MCGRTH | Peaker | 2022 | 1825 | 685.2107 | 6748.5957 | 88622 | 0 | 0.7732% | 7.615% |  |  | 0.7732% | 7.615% | 8.388% | 1 | TRUE
MNDALY_6_MCGRTH | Peaker | 2023 | 1825 | 523.0057 | 7213.83 | 88622 | 0 | 0.5902% | 8.14% |  |  | 0.5902% | 8.14% | 8.73% | 2 | TRUE
MNDALY_6_MCGRTH | Peaker | 2024 | 1830 | 199.515 | 8252.08 | 88864.8 | 0 | 0.2245% | 9.286% |  |  | 0.2245% | 9.286% | 9.511% | 3 | TRUE
MRGT_6_MEF2 | Peaker | 2022 | 1825 | 392.3333 | 0 | 80300 | 0 | 0.4886% | 0% |  |  | 0.4886% | 0% | 0.4886% | 2 | TRUE
MRGT_6_MEF2 | Peaker | 2023 | 1825 | 1399.2 | 0 | 80300 | 0 | 1.742% | 0% |  |  | 1.742% | 0% | 1.742% | 3 | TRUE
MRGT_6_MEF2 | Peaker | 2024 | 1830 | 220 | 0 | 80520 | 0 | 0.2732% | 0% |  |  | 0.2732% | 0% | 0.2732% | 1 | TRUE
MRGT_6_MMAREF | Peaker | 2022 | 1825 | 471.75 | 0 | 82125 | 0 | 0.5744% | 0% |  |  | 0.5744% | 0% | 0.5744% | 2 | TRUE
MRGT_6_MMAREF | Peaker | 2023 | 1825 | 932.25 | 0 | 82125 | 0 | 1.135% | 0% |  |  | 1.135% | 0% | 1.135% | 3 | TRUE
MRGT_6_MMAREF | Peaker | 2024 | 1830 | 0 | 0 | 82350 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
OAK C_7_UNIT 1 | Peaker | 2022 | 1825 | 51291.1317 | 25.2917 | 100375 | 0 | 51.1% | 0.0252% |  |  | 51.1% | 0.0252% | 51.12% | 2 | TRUE
OAK C_7_UNIT 1 | Peaker | 2023 | 1825 | 54252.7167 | 0 | 100375 | 0 | 54.05% | 0% |  |  | 54.05% | 0% | 54.05% | 3 | TRUE
OAK C_7_UNIT 1 | Peaker | 2024 | 1830 | 8253.5083 | 0 | 100650 | 0 | 8.2% | 0% |  |  | 8.2% | 0% | 8.2% | 1 | TRUE
OAK C_7_UNIT 3 | Peaker | 2022 | 1825 | 7443.8317 | 294.4 | 100375 | 0 | 7.416% | 0.2933% |  |  | 7.416% | 0.2933% | 7.709% | 2 | TRUE
OAK C_7_UNIT 3 | Peaker | 2023 | 1825 | 9630.15 | 0 | 100375 | 0 | 9.594% | 0% |  |  | 9.594% | 0% | 9.594% | 3 | TRUE
OAK C_7_UNIT 3 | Peaker | 2024 | 1830 | 5254.6833 | 0 | 100650 | 0 | 5.221% | 0% |  |  | 5.221% | 0% | 5.221% | 1 | TRUE
OGROVE_6_PL1X2 | Peaker | 2022 | 1825 | 8660 | 0 | 175200 | 0 | 4.943% | 0% |  |  | 4.943% | 0% | 4.943% | 3 | TRUE
OGROVE_6_PL1X2 | Peaker | 2023 | 1825 | 2085.7667 | 0 | 175200 | 0 | 1.191% | 0% |  |  | 1.191% | 0% | 1.191% | 2 | TRUE
OGROVE_6_PL1X2 | Peaker | 2024 | 1830 | 559.2233 | 0 | 175680 | 0 | 0.3183% | 0% |  |  | 0.3183% | 0% | 0.3183% | 1 | TRUE
OMAR_2_UNIT 1 | Peaker | 2022 | 1825 | 8673.75 | 0 | 136875 | 0 | 6.337% | 0% |  |  | 6.337% | 0% | 6.337% | 3 | TRUE
OMAR_2_UNIT 1 | Peaker | 2023 | 1825 | 1210 | 0 | 136875 | 0 | 0.884% | 0% |  |  | 0.884% | 0% | 0.884% | 2 | TRUE
OMAR_2_UNIT 1 | Peaker | 2024 | 1830 | 844 | 0 | 137250 | 0 | 0.6149% | 0% |  |  | 0.6149% | 0% | 0.6149% | 1 | TRUE
OMAR_2_UNIT 2 | Peaker | 2022 | 1825 | 3322.5 | 0 | 136875 | 0 | 2.427% | 0% |  |  | 2.427% | 0% | 2.427% | 2 | TRUE
OMAR_2_UNIT 2 | Peaker | 2023 | 1825 | 18843.75 | 0 | 136875 | 0 | 13.77% | 0% |  |  | 13.77% | 0% | 13.77% | 3 | TRUE
OMAR_2_UNIT 2 | Peaker | 2024 | 1830 | 1908.75 | 0 | 137250 | 0 | 1.391% | 0% |  |  | 1.391% | 0% | 1.391% | 1 | TRUE
OMAR_2_UNIT 3 | Peaker | 2022 | 1825 | 9482.5 | 0 | 136875 | 0 | 6.928% | 0% |  |  | 6.928% | 0% | 6.928% | 3 | TRUE
OMAR_2_UNIT 3 | Peaker | 2023 | 1825 | 2340 | 0 | 136875 | 0 | 1.71% | 0% |  |  | 1.71% | 0% | 1.71% | 1 | TRUE
OMAR_2_UNIT 3 | Peaker | 2024 | 1830 | 4041.25 | 0 | 137250 | 0 | 2.944% | 0% |  |  | 2.944% | 0% | 2.944% | 2 | TRUE
OTAY_6_PL1X2 | Peaker | 2022 | 1825 | 807.228 | 4.78 | 72215.25 | 0 | 1.118% | 0.006619% |  |  | 1.118% | 0.006619% | 1.124% | 1 | TRUE
OTAY_6_PL1X2 | Peaker | 2023 | 1825 | 1518.169 | 53.55 | 72215.25 | 0 | 2.102% | 0.07415% |  |  | 2.102% | 0.07415% | 2.176% | 3 | TRUE
OTAY_6_PL1X2 | Peaker | 2024 | 1830 | 857.7638 | 47.55 | 72413.1 | 0 | 1.185% | 0.06566% |  |  | 1.185% | 0.06566% | 1.25% | 2 | TRUE
PIOPIC_2_CTG1 | Peaker | 2022 | 1825 | 9033.9747 | 8191.44 | 203122.5 | 0 | 4.448% | 4.033% |  |  | 4.448% | 4.033% | 8.48% | 3 | TRUE
PIOPIC_2_CTG1 | Peaker | 2023 | 1825 | 116.4183 | 7459.27 | 203122.5 | 0 | 0.05731% | 3.672% |  |  | 0.05731% | 3.672% | 3.73% | 2 | TRUE
PIOPIC_2_CTG1 | Peaker | 2024 | 1830 | 94.9063 | 6975.98 | 203679 | 0 | 0.0466% | 3.425% |  |  | 0.0466% | 3.425% | 3.472% | 1 | TRUE
PIOPIC_2_CTG2 | Peaker | 2022 | 1825 | 223.8717 | 6116.98 | 205677.5 | 0 | 0.1088% | 2.974% |  |  | 0.1088% | 2.974% | 3.083% | 3 | TRUE
PIOPIC_2_CTG2 | Peaker | 2023 | 1825 | 539.0317 | 5321.775 | 205677.5 | 0 | 0.2621% | 2.587% |  |  | 0.2621% | 2.587% | 2.85% | 2 | TRUE
PIOPIC_2_CTG2 | Peaker | 2024 | 1830 | 642.8192 | 4979.52 | 206241 | 0 | 0.3117% | 2.414% |  |  | 0.3117% | 2.414% | 2.726% | 1 | TRUE
PIOPIC_2_CTG3 | Peaker | 2022 | 1825 | 728.2695 | 6411.96 | 204400 | 0 | 0.3563% | 3.137% |  |  | 0.3563% | 3.137% | 3.493% | 2 | TRUE
PIOPIC_2_CTG3 | Peaker | 2023 | 1825 | 526.2208 | 5759.4467 | 204400 | 0 | 0.2574% | 2.818% |  |  | 0.2574% | 2.818% | 3.075% | 1 | TRUE
PIOPIC_2_CTG3 | Peaker | 2024 | 1830 | 1184.4915 | 7164 | 204960 | 0 | 0.5779% | 3.495% |  |  | 0.5779% | 3.495% | 4.073% | 3 | TRUE
PNCHEG_2_PL1X4 | Peaker | 2022 | 1825 | 127184.92 | 19460.4933 | 761025 | 0 | 16.71% | 2.557% |  |  | 16.71% | 2.557% | 19.27% | 2 | TRUE
PNCHEG_2_PL1X4 | Peaker | 2023 | 1825 | 215355.775 | 14041.1567 | 761025 | 0 | 28.3% | 1.845% |  |  | 28.3% | 1.845% | 30.14% | 3 | TRUE
PNCHEG_2_PL1X4 | Peaker | 2024 | 1830 | 82381.645 | 25493.1683 | 763110 | 0 | 10.8% | 3.341% |  |  | 10.8% | 3.341% | 14.14% | 1 | TRUE
PNCHPP_1_PL1X2 | Peaker | 2022 | 1825 | 4232.13 | 12926.37 | 218835.75 | 0 | 1.934% | 5.907% |  |  | 1.934% | 5.907% | 7.841% | 2 | TRUE
PNCHPP_1_PL1X2 | Peaker | 2023 | 1825 | 9912.703 | 12408.6835 | 218835.75 | 0 | 4.53% | 5.67% |  |  | 4.53% | 5.67% | 10.2% | 3 | TRUE
PNCHPP_1_PL1X2 | Peaker | 2024 | 1830 | 5154.7162 | 1683.655 | 219435.3 | 0 | 2.349% | 0.7673% |  |  | 2.349% | 0.7673% | 3.116% | 1 | TRUE
PNOCHE_1_PL1X2 | Peaker | 2022 | 1825 | 1081.3278 | 1550.411 | 91195.25 | 0 | 1.186% | 1.7% |  |  | 1.186% | 1.7% | 2.886% | 1 | TRUE
PNOCHE_1_PL1X2 | Peaker | 2023 | 1825 | 4695.426 | 1542.3732 | 91195.25 | 0 | 5.149% | 1.691% |  |  | 5.149% | 1.691% | 6.84% | 3 | TRUE
PNOCHE_1_PL1X2 | Peaker | 2024 | 1830 | 1995.9792 | 1852.6048 | 91445.1 | 0 | 2.183% | 2.026% |  |  | 2.183% | 2.026% | 4.209% | 2 | TRUE
PNOCHE_1_UNITA1 | Peaker | 2022 | 1825 | 1404.3933 | 412.01 | 95447.5 | 0 | 1.471% | 0.4317% |  |  | 1.471% | 0.4317% | 1.903% | 1 | TRUE
PNOCHE_1_UNITA1 | Peaker | 2023 | 1825 | 10672.925 | 28.21 | 95447.5 | 0 | 11.18% | 0.02956% |  |  | 11.18% | 0.02956% | 11.21% | 3 | TRUE
PNOCHE_1_UNITA1 | Peaker | 2024 | 1830 | 6136.04 | 0 | 95709 | 0 | 6.411% | 0% |  |  | 6.411% | 0% | 6.411% | 2 | TRUE
RVRVEW_1_UNITA1 | Peaker | 2022 | 1825 | 7315.2667 | 98.45 | 88877.5 | 0 | 8.231% | 0.1108% |  |  | 8.231% | 0.1108% | 8.342% | 3 | TRUE
RVRVEW_1_UNITA1 | Peaker | 2023 | 1825 | 3562.945 | 76.6317 | 88877.5 | 0 | 4.009% | 0.08622% |  |  | 4.009% | 0.08622% | 4.095% | 2 | TRUE
RVRVEW_1_UNITA1 | Peaker | 2024 | 1830 | 1412.7483 | 1765.89 | 89121 | 0 | 1.585% | 1.981% |  |  | 1.585% | 1.981% | 3.567% | 1 | TRUE
RVSIDE_2_RERCU3 | Peaker | 2022 | 1825 | 0 | 0 | 89425 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
RVSIDE_2_RERCU3 | Peaker | 2023 | 1825 | 245 | 0 | 89425 | 0 | 0.274% | 0% |  |  | 0.274% | 0% | 0.274% | 2 | TRUE
RVSIDE_2_RERCU3 | Peaker | 2024 | 1830 | 1958.7833 | 0 | 89670 | 0 | 2.184% | 0% |  |  | 2.184% | 0% | 2.184% | 3 | TRUE
RVSIDE_2_RERCU4 | Peaker | 2022 | 1825 | 0 | 0 | 89425 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
RVSIDE_2_RERCU4 | Peaker | 2023 | 1825 | 7 | 0 | 89425 | 0 | 0.007828% | 0% |  |  | 0.007828% | 0% | 0.007828% | 2 | TRUE
RVSIDE_2_RERCU4 | Peaker | 2024 | 1830 | 1808.8 | 0 | 89670 | 0 | 2.017% | 0% |  |  | 2.017% | 0% | 2.017% | 3 | TRUE
RVSIDE_6_RERCU1 | Peaker | 2022 | 1825 | 11684.43 | 0 | 88238.75 | 0 | 13.24% | 0% |  |  | 13.24% | 0% | 13.24% | 3 | TRUE
RVSIDE_6_RERCU1 | Peaker | 2023 | 1825 | 1450.5 | 0 | 88238.75 | 0 | 1.644% | 0% |  |  | 1.644% | 0% | 1.644% | 1 | TRUE
RVSIDE_6_RERCU1 | Peaker | 2024 | 1830 | 1738.125 | 0 | 88480.5 | 0 | 1.964% | 0% |  |  | 1.964% | 0% | 1.964% | 2 | TRUE
RVSIDE_6_RERCU2 | Peaker | 2022 | 1825 | 231.1833 | 0 | 88512.5 | 0 | 0.2612% | 0% |  |  | 0.2612% | 0% | 0.2612% | 2 | TRUE
RVSIDE_6_RERCU2 | Peaker | 2023 | 1825 | 0 | 0 | 88512.5 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
RVSIDE_6_RERCU2 | Peaker | 2024 | 1830 | 5625.75 | 0 | 88755 | 0 | 6.339% | 0% |  |  | 6.339% | 0% | 6.339% | 3 | TRUE
RVSIDE_6_SPRING | Peaker | 2022 | 1825 | 66.1333 | 0 | 65700 | 0 | 0.1007% | 0% |  |  | 0.1007% | 0% | 0.1007% | 1 | TRUE
RVSIDE_6_SPRING | Peaker | 2023 | 1825 | 486.6667 | 0 | 65700 | 0 | 0.7407% | 0% |  |  | 0.7407% | 0% | 0.7407% | 2 | TRUE
RVSIDE_6_SPRING | Peaker | 2024 | 1830 | 1344 | 0 | 65880 | 0 | 2.04% | 0% |  |  | 2.04% | 0% | 2.04% | 3 | TRUE
SENTNL_2_CTG1 | Peaker | 2022 | 1825 | 5960.894 | 5751.92 | 196516 | 0 | 3.033% | 2.927% |  |  | 3.033% | 2.927% | 5.96% | 1 | TRUE
SENTNL_2_CTG1 | Peaker | 2023 | 1825 | 21212.5873 | 3579.66 | 196516 | 0 | 10.79% | 1.822% |  |  | 10.79% | 1.822% | 12.62% | 3 | TRUE
SENTNL_2_CTG1 | Peaker | 2024 | 1830 | 630.3083 | 15452.7032 | 197054.4 | 0 | 0.3199% | 7.842% |  |  | 0.3199% | 7.842% | 8.162% | 2 | TRUE
SENTNL_2_CTG2 | Peaker | 2022 | 1825 | 8153.2802 | 7553.556 | 190146.75 | 0 | 4.288% | 3.972% |  |  | 4.288% | 3.972% | 8.26% | 2 | TRUE
SENTNL_2_CTG2 | Peaker | 2023 | 1825 | 2852.1153 | 8221.0133 | 190146.75 | 0 | 1.5% | 4.324% |  |  | 1.5% | 4.324% | 5.823% | 1 | TRUE
SENTNL_2_CTG2 | Peaker | 2024 | 1830 | 1090.525 | 15240.8553 | 190667.7 | 0 | 0.572% | 7.993% |  |  | 0.572% | 7.993% | 8.565% | 3 | TRUE
SENTNL_2_CTG3 | Peaker | 2022 | 1825 | 8683.1843 | 5809.9377 | 192884.25 | 0 | 4.502% | 3.012% |  |  | 4.502% | 3.012% | 7.514% | 1 | TRUE
SENTNL_2_CTG3 | Peaker | 2023 | 1825 | 39260.6775 | 7842.7233 | 192884.25 | 0 | 20.35% | 4.066% |  |  | 20.35% | 4.066% | 24.42% | 2 | TRUE
SENTNL_2_CTG3 | Peaker | 2024 | 1830 | 186542.85 | 0 | 193412.7 | 0 | 96.45% | 0% |  |  | 96.45% | 0% | 96.45% | 3 | TRUE
SENTNL_2_CTG4 | Peaker | 2022 | 1825 | 9464.6522 | 5707.046 | 194453.75 | 0 | 4.867% | 2.935% |  |  | 4.867% | 2.935% | 7.802% | 1 | TRUE
SENTNL_2_CTG4 | Peaker | 2023 | 1825 | 7240.515 | 8569.8933 | 194453.75 | 0 | 3.724% | 4.407% |  |  | 3.724% | 4.407% | 8.131% | 2 | TRUE
SENTNL_2_CTG4 | Peaker | 2024 | 1830 | 8684.8633 | 15734.9 | 194986.5 | 0 | 4.454% | 8.07% |  |  | 4.454% | 8.07% | 12.52% | 3 | TRUE
SENTNL_2_CTG5 | Peaker | 2022 | 1825 | 5444.8027 | 5778.84 | 196224 | 0 | 2.775% | 2.945% |  |  | 2.775% | 2.945% | 5.72% | 1 | TRUE
SENTNL_2_CTG5 | Peaker | 2023 | 1825 | 33768.129 | 7458.5367 | 196224 | 0 | 17.21% | 3.801% |  |  | 17.21% | 3.801% | 21.01% | 3 | TRUE
SENTNL_2_CTG5 | Peaker | 2024 | 1830 | 2320.75 | 15662.57 | 196761.6 | 0 | 1.179% | 7.96% |  |  | 1.179% | 7.96% | 9.14% | 2 | TRUE
SENTNL_2_CTG6 | Peaker | 2022 | 1825 | 14288.9528 | 5802.8137 | 191625 | 0 | 7.457% | 3.028% |  |  | 7.457% | 3.028% | 10.48% | 2 | TRUE
SENTNL_2_CTG6 | Peaker | 2023 | 1825 | 2957.2477 | 7929.05 | 191625 | 0 | 1.543% | 4.138% |  |  | 1.543% | 4.138% | 5.681% | 1 | TRUE
SENTNL_2_CTG6 | Peaker | 2024 | 1830 | 5088.4417 | 15525.71 | 192150 | 0 | 2.648% | 8.08% |  |  | 2.648% | 8.08% | 10.73% | 3 | TRUE
SENTNL_2_CTG7 | Peaker | 2022 | 1825 | 11531.207 | 5591.634 | 194782.25 | 0 | 5.92% | 2.871% |  |  | 5.92% | 2.871% | 8.791% | 1 | TRUE
SENTNL_2_CTG7 | Peaker | 2023 | 1825 | 33915.4172 | 4488.7 | 194782.25 | 0 | 17.41% | 2.304% |  |  | 17.41% | 2.304% | 19.72% | 3 | TRUE
SENTNL_2_CTG7 | Peaker | 2024 | 1830 | 10106.9933 | 15464.75 | 195315.9 | 0 | 5.175% | 7.918% |  |  | 5.175% | 7.918% | 13.09% | 2 | TRUE
SENTNL_2_CTG8 | Peaker | 2022 | 1825 | 9483.9622 | 5890.206 | 195001.25 | 0 | 4.864% | 3.021% |  |  | 4.864% | 3.021% | 7.884% | 1 | TRUE
SENTNL_2_CTG8 | Peaker | 2023 | 1825 | 7866.7008 | 8777.7833 | 195001.25 | 0 | 4.034% | 4.501% |  |  | 4.034% | 4.501% | 8.536% | 3 | TRUE
SENTNL_2_CTG8 | Peaker | 2024 | 1830 | 0 | 15961.8 | 195535.5 | 0 | 0% | 8.163% |  |  | 0% | 8.163% | 8.163% | 2 | TRUE
SIERRA_1_UNITS | Peaker | 2022 | 1825 | 2709.78 | 3826.98 | 95684.75 | 0 | 2.832% | 4% |  |  | 2.832% | 4% | 6.832% | 3 | TRUE
SIERRA_1_UNITS | Peaker | 2023 | 1825 | 1196 | 4779.9327 | 95684.75 | 0 | 1.25% | 4.996% |  |  | 1.25% | 4.996% | 6.245% | 2 | TRUE
SIERRA_1_UNITS | Peaker | 2024 | 1830 | 237.1333 | 4575.5267 | 95946.9 | 0 | 0.2472% | 4.769% |  |  | 0.2472% | 4.769% | 5.016% | 1 | TRUE
STANTN_2_STAGT1 | Peaker | 2022 | 1825 | 329.01 | 33.0148 | 90611.25 | 0 | 0.3631% | 0.03644% |  |  | 0.3631% | 0.03644% | 0.3995% | 1 | TRUE
STANTN_2_STAGT1 | Peaker | 2023 | 1825 | 741.0017 | 4.2592 | 90611.25 | 0 | 0.8178% | 0.0047% |  |  | 0.8178% | 0.0047% | 0.8225% | 2 | TRUE
STANTN_2_STAGT1 | Peaker | 2024 | 1830 | 1798.1575 | 39.2488 | 90859.5 | 0 | 1.979% | 0.0432% |  |  | 1.979% | 0.0432% | 2.022% | 3 | TRUE
STANTN_2_STAGT2 | Peaker | 2022 | 1825 | 629.0793 | 686.6732 | 90611.25 | 0 | 0.6943% | 0.7578% |  |  | 0.6943% | 0.7578% | 1.452% | 2 | TRUE
STANTN_2_STAGT2 | Peaker | 2023 | 1825 | 924.9122 | 772.4275 | 90611.25 | 0 | 1.021% | 0.8525% |  |  | 1.021% | 0.8525% | 1.873% | 3 | TRUE
STANTN_2_STAGT2 | Peaker | 2024 | 1830 | 349.5757 | 588.3727 | 90859.5 | 0 | 0.3847% | 0.6476% |  |  | 0.3847% | 0.6476% | 1.032% | 1 | TRUE
STIGCT_2_LODI | Peaker | 2022 | 1825 | 4050.5897 | 7643 | 91067.5 | 0 | 4.448% | 8.393% |  |  | 4.448% | 8.393% | 12.84% | 2 | TRUE
STIGCT_2_LODI | Peaker | 2023 | 1825 | 349.75 | 8834.4 | 91067.5 | 0 | 0.3841% | 9.701% |  |  | 0.3841% | 9.701% | 10.08% | 1 | TRUE
STIGCT_2_LODI | Peaker | 2024 | 1830 | 21653.3667 | 5042 | 91317 | 0 | 23.71% | 5.521% |  |  | 23.71% | 5.521% | 29.23% | 3 | TRUE
SYCAMR_2_UNIT 2 | Peaker | 2022 | 1825 | 4492 | 0 | 138700 | 0 | 3.239% | 0% |  |  | 3.239% | 0% | 3.239% | 1 | TRUE
SYCAMR_2_UNIT 2 | Peaker | 2023 | 1825 | 28039.7333 | 0 | 138700 | 0 | 20.22% | 0% |  |  | 20.22% | 0% | 20.22% | 2 | TRUE
SYCAMR_2_UNIT 2 | Peaker | 2024 | 1830 | 28588.6667 | 0 | 139080 | 0 | 20.56% | 0% |  |  | 20.56% | 0% | 20.56% | 3 | TRUE
SYCAMR_2_UNIT 4 | Peaker | 2022 | 1825 | 15164.5667 | 0 | 138700 | 0 | 10.93% | 0% |  |  | 10.93% | 0% | 10.93% | 3 | TRUE
SYCAMR_2_UNIT 4 | Peaker | 2023 | 1825 | 9781.2333 | 0 | 138700 | 0 | 7.052% | 0% |  |  | 7.052% | 0% | 7.052% | 1 | TRUE
SYCAMR_2_UNIT 4 | Peaker | 2024 | 1830 | 11215.0667 | 0 | 139080 | 0 | 8.064% | 0% |  |  | 8.064% | 0% | 8.064% | 2 | TRUE
VACADX_1_UNITA1 | Peaker | 2022 | 1825 | 3677.2945 | 316.8 | 94735.75 | 0 | 3.882% | 0.3344% |  |  | 3.882% | 0.3344% | 4.216% | 1 | TRUE
VACADX_1_UNITA1 | Peaker | 2023 | 1825 | 5184.1557 | 0 | 94735.75 | 0 | 5.472% | 0% |  |  | 5.472% | 0% | 5.472% | 2 | TRUE
VACADX_1_UNITA1 | Peaker | 2024 | 1830 | 7704.4327 | 16.8533 | 94995.3 | 0 | 8.11% | 0.01774% |  |  | 8.11% | 0.01774% | 8.128% | 3 | TRUE
VERNON_6_GONZL1 | Peaker | 2022 | 1825 | 10465 | 0 | 10493.75 | 0 | 99.73% | 0% |  |  | 99.73% | 0% | 99.73% | 3 | TRUE
VERNON_6_GONZL1 | Peaker | 2023 | 1825 | 569.25 | 0 | 10493.75 | 0 | 5.425% | 0% |  |  | 5.425% | 0% | 5.425% | 2 | TRUE
VERNON_6_GONZL1 | Peaker | 2024 | 1830 | 54.625 | 0 | 10522.5 | 0 | 0.5191% | 0% |  |  | 0.5191% | 0% | 0.5191% | 1 | TRUE
VERNON_6_GONZL2 | Peaker | 2022 | 1825 | 231.3417 | 0 | 10493.75 | 0 | 2.205% | 0% |  |  | 2.205% | 0% | 2.205% | 1 | TRUE
VERNON_6_GONZL2 | Peaker | 2023 | 1825 | 488.75 | 0 | 10493.75 | 0 | 4.658% | 0% |  |  | 4.658% | 0% | 4.658% | 2 | TRUE
VERNON_6_GONZL2 | Peaker | 2024 | 1830 | 758.9042 | 0 | 10522.5 | 0 | 7.212% | 0% |  |  | 7.212% | 0% | 7.212% | 3 | TRUE
VESTAL_2_WELLHD | Peaker | 2022 | 1825 | 4568.0833 | 32.245 | 89425 | 0 | 5.108% | 0.03606% |  |  | 5.108% | 0.03606% | 5.144% | 1 | TRUE
VESTAL_2_WELLHD | Peaker | 2023 | 1825 | 9315.7333 | 0 | 89425 | 0 | 10.42% | 0% |  |  | 10.42% | 0% | 10.42% | 3 | TRUE
VESTAL_2_WELLHD | Peaker | 2024 | 1830 | 3917.6627 | 806.26 | 89670 | 0 | 4.369% | 0.8991% |  |  | 4.369% | 0.8991% | 5.268% | 2 | TRUE
WALCRK_2_CTG1 | Peaker | 2022 | 1825 | 7913.1127 | 0 | 182682.5 | 0 | 4.332% | 0% |  |  | 4.332% | 0% | 4.332% | 2 | TRUE
WALCRK_2_CTG1 | Peaker | 2023 | 1825 | 2534.786 | 0 | 182682.5 | 0 | 1.388% | 0% |  |  | 1.388% | 0% | 1.388% | 1 | TRUE
WALCRK_2_CTG1 | Peaker | 2024 | 1830 | 11742.745 | 169.4033 | 183183 | 0 | 6.41% | 0.09248% |  |  | 6.41% | 0.09248% | 6.503% | 3 | TRUE
WALCRK_2_CTG2 | Peaker | 2022 | 1825 | 51921.8058 | 0 | 182682.5 | 0 | 28.42% | 0% |  |  | 28.42% | 0% | 28.42% | 2 | TRUE
WALCRK_2_CTG2 | Peaker | 2023 | 1825 | 54159.0032 | 0 | 182682.5 | 0 | 29.65% | 0% |  |  | 29.65% | 0% | 29.65% | 3 | TRUE
WALCRK_2_CTG2 | Peaker | 2024 | 1830 | 4064.7383 | 35.775 | 183183 | 0 | 2.219% | 0.01953% |  |  | 2.219% | 0.01953% | 2.238% | 1 | TRUE
WALCRK_2_CTG3 | Peaker | 2022 | 1825 | 2760.9033 | 18.625 | 182682.5 | 0 | 1.511% | 0.0102% |  |  | 1.511% | 0.0102% | 1.522% | 2 | TRUE
WALCRK_2_CTG3 | Peaker | 2023 | 1825 | 2548.7425 | 0 | 182682.5 | 0 | 1.395% | 0% |  |  | 1.395% | 0% | 1.395% | 1 | TRUE
WALCRK_2_CTG3 | Peaker | 2024 | 1830 | 11328.1967 | 125.1683 | 183183 | 0 | 6.184% | 0.06833% |  |  | 6.184% | 0.06833% | 6.252% | 3 | TRUE
WALCRK_2_CTG4 | Peaker | 2022 | 1825 | 12026.1033 | 0 | 182682.5 | 0 | 6.583% | 0% |  |  | 6.583% | 0% | 6.583% | 2 | TRUE
WALCRK_2_CTG4 | Peaker | 2023 | 1825 | 10524.815 | 0 | 182682.5 | 0 | 5.761% | 0% |  |  | 5.761% | 0% | 5.761% | 1 | TRUE
WALCRK_2_CTG4 | Peaker | 2024 | 1830 | 77193.9 | 0 | 183183 | 0 | 42.14% | 0% |  |  | 42.14% | 0% | 42.14% | 3 | TRUE
WALCRK_2_CTG5 | Peaker | 2022 | 1825 | 3609.0958 | 0 | 182682.5 | 0 | 1.976% | 0% |  |  | 1.976% | 0% | 1.976% | 2 | TRUE
WALCRK_2_CTG5 | Peaker | 2023 | 1825 | 1847.0042 | 0 | 182682.5 | 0 | 1.011% | 0% |  |  | 1.011% | 0% | 1.011% | 1 | TRUE
WALCRK_2_CTG5 | Peaker | 2024 | 1830 | 9331.6967 | 156.0317 | 183183 | 0 | 5.094% | 0.08518% |  |  | 5.094% | 0.08518% | 5.179% | 3 | TRUE
WOLFSK_1_UNITA1 | Peaker | 2022 | 1825 | 5983.9067 | 501.55 | 88841 | 0 | 6.736% | 0.5645% |  |  | 6.736% | 0.5645% | 7.3% | 3 | TRUE
WOLFSK_1_UNITA1 | Peaker | 2023 | 1825 | 1049.3615 | 366.4453 | 88841 | 0 | 1.181% | 0.4125% |  |  | 1.181% | 0.4125% | 1.594% | 1 | TRUE
WOLFSK_1_UNITA1 | Peaker | 2024 | 1830 | 339.9487 | 1565.4058 | 89084.4 | 0 | 0.3816% | 1.757% |  |  | 0.3816% | 1.757% | 2.139% | 2 | TRUE
YUBACT_6_UNITA1 | Peaker | 2022 | 1825 | 467.1853 | 760.162 | 86067 | 0 | 0.5428% | 0.8832% |  |  | 0.5428% | 0.8832% | 1.426% | 2 | TRUE
YUBACT_6_UNITA1 | Peaker | 2023 | 1825 | 697.968 | 222.844 | 86067 | 0 | 0.811% | 0.2589% |  |  | 0.811% | 0.2589% | 1.07% | 1 | TRUE
YUBACT_6_UNITA1 | Peaker | 2024 | 1830 | 1297.4307 | 1528.94 | 86302.8 | 0 | 1.503% | 1.772% |  |  | 1.503% | 1.772% | 3.275% | 3 | TRUE
BANKPP_2_NSPIN | Pump | 2022 | 1825 | 0 | 0 | 492750 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
BANKPP_2_NSPIN | Pump | 2023 | 1825 | 1885.5 | 0 | 492750 | 0 | 0.3826% | 0% |  |  | 0.3826% | 0% | 0.3826% | 3 | TRUE
BANKPP_2_NSPIN | Pump | 2024 | 1830 | 0 | 0 | 494100 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
DOSMGO_2_NSPIN | Pump | 2022 | 1825 | 0 | 0 | 290175 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
DOSMGO_2_NSPIN | Pump | 2023 | 1825 | 0 | 0 | 290175 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
DOSMGO_2_NSPIN | Pump | 2024 | 1830 | 0 | 0 | 290970 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
EDMONS_2_NSPIN | Pump | 2022 | 1825 | 92116.22 | 0 | 1415835 | 0 | 6.506% | 0% |  |  | 6.506% | 0% | 6.506% | 3 | TRUE
EDMONS_2_NSPIN | Pump | 2023 | 1825 | 87583.3333 | 0 | 1415835 | 0 | 6.186% | 0% |  |  | 6.186% | 0% | 6.186% | 1 | TRUE
EDMONS_2_NSPIN | Pump | 2024 | 1830 | 87965 | 0 | 1419714 | 0 | 6.196% | 0% |  |  | 6.196% | 0% | 6.196% | 2 | TRUE
OSO_6_NSPIN | Pump | 2022 | 1825 | 0 | 0 | 127750 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
OSO_6_NSPIN | Pump | 2023 | 1825 | 0 | 0 | 127750 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
OSO_6_NSPIN | Pump | 2024 | 1830 | 0 | 0 | 128100 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
PEARBL_2_NSPIN | Pump | 2022 | 1825 | 0 | 0 | 215350 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
PEARBL_2_NSPIN | Pump | 2023 | 1825 | 118 | 0 | 215350 | 0 | 0.05479% | 0% |  |  | 0.05479% | 0% | 0.05479% | 2 | TRUE
PEARBL_2_NSPIN | Pump | 2024 | 1830 | 590 | 0 | 215940 | 0 | 0.2732% | 0% |  |  | 0.2732% | 0% | 0.2732% | 3 | TRUE
EASTWD_7_UNIT | Pumped Hydro | 2022 | 1825 | 32400 | 165.6667 | 365000 | 0 | 8.877% | 0.04539% |  |  | 8.877% | 0.04539% | 8.922% | 1 | TRUE
EASTWD_7_UNIT | Pumped Hydro | 2023 | 1825 | 65400 | 0 | 365000 | 0 | 17.92% | 0% |  |  | 17.92% | 0% | 17.92% | 3 | TRUE
EASTWD_7_UNIT | Pumped Hydro | 2024 | 1830 | 35535.3333 | 0 | 366000 | 0 | 9.709% | 0% |  |  | 9.709% | 0% | 9.709% | 2 | TRUE
HELMPG_7_UNIT 1 | Pumped Hydro | 2022 | 1825 | 73156.7333 | 0 | 742775 | 0 | 9.849% | 0% |  |  | 9.849% | 0% | 9.849% | 3 | TRUE
HELMPG_7_UNIT 1 | Pumped Hydro | 2023 | 1825 | 7549.95 | 0 | 742775 | 0 | 1.016% | 0% |  |  | 1.016% | 0% | 1.016% | 1 | TRUE
HELMPG_7_UNIT 1 | Pumped Hydro | 2024 | 1830 | 24724.8833 | 0 | 744810 | 0 | 3.32% | 0% |  |  | 3.32% | 0% | 3.32% | 2 | TRUE
HELMPG_7_UNIT 2 | Pumped Hydro | 2022 | 1825 | 60769.1333 | 0 | 742775 | 0 | 8.181% | 0% |  |  | 8.181% | 0% | 8.181% | 3 | TRUE
HELMPG_7_UNIT 2 | Pumped Hydro | 2023 | 1825 | 12155.7333 | 0 | 742775 | 0 | 1.637% | 0% |  |  | 1.637% | 0% | 1.637% | 1 | TRUE
HELMPG_7_UNIT 2 | Pumped Hydro | 2024 | 1830 | 14760.1667 | 0 | 744810 | 0 | 1.982% | 0% |  |  | 1.982% | 0% | 1.982% | 2 | TRUE
HELMPG_7_UNIT 3 | Pumped Hydro | 2022 | 1825 | 82507.2 | 0 | 737300 | 0 | 11.19% | 0% |  |  | 11.19% | 0% | 11.19% | 3 | TRUE
HELMPG_7_UNIT 3 | Pumped Hydro | 2023 | 1825 | 17432.6 | 0 | 737300 | 0 | 2.364% | 0% |  |  | 2.364% | 0% | 2.364% | 2 | TRUE
HELMPG_7_UNIT 3 | Pumped Hydro | 2024 | 1830 | 14488.6667 | 0 | 739320 | 0 | 1.96% | 0% |  |  | 1.96% | 0% | 1.96% | 1 | TRUE
CDWR07_2_GEN | Reciprocating Engine | 2022 | 1825 | 0 | 0 | 757922.5 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
CDWR07_2_GEN | Reciprocating Engine | 2023 | 1825 | 264.225 | 0 | 757922.5 | 0 | 0.03486% | 0% |  |  | 0.03486% | 0% | 0.03486% | 2 | TRUE
CDWR07_2_GEN | Reciprocating Engine | 2024 | 1830 | 2478.8 | 0 | 759999 | 0 | 0.3262% | 0% |  |  | 0.3262% | 0% | 0.3262% | 3 | TRUE
CHWCHL_1_UNIT | Reciprocating Engine | 2022 | 1825 | 2079.4 | 136.2167 | 88695 | 0 | 2.344% | 0.1536% |  |  | 2.344% | 0.1536% | 2.498% | 3 | TRUE
CHWCHL_1_UNIT | Reciprocating Engine | 2023 | 1825 | 1192.0333 | 742.875 | 88695 | 0 | 1.344% | 0.8376% |  |  | 1.344% | 0.8376% | 2.182% | 2 | TRUE
CHWCHL_1_UNIT | Reciprocating Engine | 2024 | 1830 | 462.72 | 503.1233 | 88938 | 0 | 0.5203% | 0.5657% |  |  | 0.5203% | 0.5657% | 1.086% | 1 | TRUE
HUMBPP_1_UNITS3 | Reciprocating Engine | 2022 | 1825 | 17081.1598 | 0 | 118771 | 0 | 14.38% | 0% |  |  | 14.38% | 0% | 14.38% | 3 | TRUE
HUMBPP_1_UNITS3 | Reciprocating Engine | 2023 | 1825 | 3808.7438 | 0 | 118771 | 0 | 3.207% | 0% |  |  | 3.207% | 0% | 3.207% | 1 | TRUE
HUMBPP_1_UNITS3 | Reciprocating Engine | 2024 | 1830 | 3176.7175 | 3644.48 | 119096.4 | 0 | 2.667% | 3.06% |  |  | 2.667% | 3.06% | 5.727% | 2 | TRUE
HUMBPP_6_UNITS | Reciprocating Engine | 2022 | 1825 | 28238.8637 | 0 | 178156.5 | 0 | 15.85% | 0% |  |  | 15.85% | 0% | 15.85% | 3 | TRUE
HUMBPP_6_UNITS | Reciprocating Engine | 2023 | 1825 | 6063.5578 | 0 | 178156.5 | 0 | 3.404% | 0% |  |  | 3.404% | 0% | 3.404% | 1 | TRUE
HUMBPP_6_UNITS | Reciprocating Engine | 2024 | 1830 | 8780.919 | 13342.6347 | 178644.6 | 0 | 4.915% | 7.469% |  |  | 4.915% | 7.469% | 12.38% | 2 | TRUE
REDBLF_6_UNIT | Reciprocating Engine | 2022 | 1825 | 0 | 0 | 80300 | 0 | 0% | 0% |  |  | 0% | 0% | 0% | 1 | TRUE
REDBLF_6_UNIT | Reciprocating Engine | 2023 | 1825 | 593.2167 | 8.8 | 80300 | 0 | 0.7388% | 0.01096% |  |  | 0.7388% | 0.01096% | 0.7497% | 2 | TRUE
REDBLF_6_UNIT | Reciprocating Engine | 2024 | 1830 | 2042.2667 | 0 | 80520 | 0 | 2.536% | 0% |  |  | 2.536% | 0% | 2.536% | 3 | TRUE
CABALO_2_M2WSR2 | Solar_1Axis | 2022 | 1825 | 15100.8165 | 0 | 182500 | 0 | 8.274% | 0% |  |  | 8.274% | 0% | 8.274% | 3 | TRUE
CABALO_2_M2WSR2 | Solar_1Axis | 2023 | 1825 | 5889.7133 | 0 | 182500 | 0 | 3.227% | 0% |  |  | 3.227% | 0% | 3.227% | 1 | TRUE
CABALO_2_M2WSR2 | Solar_1Axis | 2024 | 1830 | 7324.3667 | 0 | 183000 | 0 | 4.002% | 0% |  |  | 4.002% | 0% | 4.002% | 2 | TRUE
ELNIDO_1_ECRSR1 | Solar_Fixed | 2022 | 0 | 0 | 0 | 0 | 1825 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 4 | FALSE
ELNIDO_1_ECRSR1 | Solar_Fixed | 2023 | 0 | 0 | 0 | 0 | 1825 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 4 | FALSE
ELNIDO_1_ECRSR1 | Solar_Fixed | 2024 | 0 | 0 | 0 | 0 | 1830 |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | 4 | FALSE

## ResourceYearSeason
RESOURCE ID | RESOURCE TYPE | YEAR | SEASON | COMMERCIAL OPERATION DATE | OUTAGE MWH DURING DEMAND EXCLUDING AMBIENT DUE TO TEMPERATURE | OUTAGE MWH DURING DEMAND AMBIENT DUE TO TEMPERATURE | INDIVIDUAL DEMAND HOURS | PMAX OR NDC MW | MWH AT PMAX DURING DEMAND | GROUP DEMAND HOURS | EFORD ASSESSMENT | EFORD EXCLUDING AMBIENT DUE TO TEMPERATURE - INDIVIDUAL ASSESSMENT | EFORD AMBIENT DUE TO TEMPERATURE - INDIVIDUAL ASSESSMENT | EFORD EXCLUDING AMBIENT DUE TO TEMPERATURE - GROUP ASSESSMENT - FIRST PASS | EFORD AMBIENT DUE TO TEMPERATURE - GROUP ASSESSMENT - FIRST PASS | EFORD EXCLUDING AMBIENT DUE TO TEMPERATURE - FIRST PASS | EFORD AMBIENT DUE TO TEMPERATURE - FIRST PASS | INCLUDE RESOURCE YEAR SEASON IN UCAP | EFORD EXCLUDING AMBIENT DUE TO TEMPERATURE - GROUP ASSESSMENT - SECOND PASS | EFORD AMBIENT DUE TO TEMPERATURE - GROUP ASSESSMENT - SECOND PASS | EFORD EXCLUDING AMBIENT DUE TO TEMPERATURE - SECOND PASS | EFORD AMBIENT DUE TO TEMPERATURE - SECOND PASS
ALAMIT_2_AESBT2 | Battery Storage | 2022 | nonsummer | 2024-11-14 | 0 | 0 | 0 | 82 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
ALAMIT_2_AESBT2 | Battery Storage | 2022 | summer | 2024-11-14 | 0 | 0 | 0 | 82 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
ALAMIT_2_AESBT2 | Battery Storage | 2023 | nonsummer | 2024-11-14 | 0 | 0 | 0 | 82 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
ALAMIT_2_AESBT2 | Battery Storage | 2023 | summer | 2024-11-14 | 0 | 0 | 0 | 82 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
ALAMIT_2_AESBT2 | Battery Storage | 2024 | nonsummer | 2024-11-14 | 5327.2667 | 0 | 240 | 82 | 19680 | 825 | Blended | 27.07% | 0% | 6.223% | 0% | 10.92% | 0% | TRUE | 6.223% | 0% | 10.92% | 0%
ALAMIT_2_AESBT2 | Battery Storage | 2024 | summer | 2024-11-14 | 0 | 0 | 0 | 82 | 0 | 765 | Group |  |  | 8.576% | 0% | 8.576% | 0% | TRUE | 8.576% | 0% | 8.576% | 0%
ALAMIT_7_ES1 | Battery Storage | 2022 | nonsummer | 2020-12-04 | 18641.0267 | 0 | 1060 | 100.45 | 106477 | 0 | Individual | 17.51% | 0% |  |  | 17.51% | 0% | TRUE |  |  | 17.51% | 0%
ALAMIT_7_ES1 | Battery Storage | 2022 | summer | 2020-12-04 | 12961.6258 | 0 | 765 | 100.45 | 76844.25 | 0 | Individual | 16.87% | 0% |  |  | 16.87% | 0% | TRUE |  |  | 16.87% | 0%
ALAMIT_7_ES1 | Battery Storage | 2023 | nonsummer | 2020-12-04 | 19925.2625 | 0 | 1060 | 100.45 | 106477 | 0 | Individual | 18.71% | 0% |  |  | 18.71% | 0% | TRUE |  |  | 18.71% | 0%
ALAMIT_7_ES1 | Battery Storage | 2023 | summer | 2020-12-04 | 13612.3842 | 0 | 765 | 100.45 | 76844.25 | 0 | Individual | 17.71% | 0% |  |  | 17.71% | 0% | TRUE |  |  | 17.71% | 0%
ALAMIT_7_ES1 | Battery Storage | 2024 | nonsummer | 2020-12-04 | 22772.1058 | 0 | 1065 | 100.45 | 106979.25 | 0 | Individual | 21.29% | 0% |  |  | 21.29% | 0% | TRUE |  |  | 21.29% | 0%
ALAMIT_7_ES1 | Battery Storage | 2024 | summer | 2020-12-04 | 11646.8583 | 0 | 765 | 100.45 | 76844.25 | 0 | Individual | 15.16% | 0% |  |  | 15.16% | 0% | TRUE |  |  | 15.16% | 0%
BERCYN_2_BCEBT1 | Battery Storage | 2022 | nonsummer | 2024-07-24 | 0 | 0 | 0 | 13 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
BERCYN_2_BCEBT1 | Battery Storage | 2022 | summer | 2024-07-24 | 0 | 0 | 0 | 13 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
BERCYN_2_BCEBT1 | Battery Storage | 2023 | nonsummer | 2024-07-24 | 0 | 0 | 0 | 13 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
BERCYN_2_BCEBT1 | Battery Storage | 2023 | summer | 2024-07-24 | 0 | 0 | 0 | 13 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
BERCYN_2_BCEBT1 | Battery Storage | 2024 | nonsummer | 2024-07-24 | 130 | 0 | 305 | 13 | 3965 | 760 | Blended | 3.279% | 0% | 6.223% | 0% | 5.38% | 0% | TRUE | 6.223% | 0% | 5.38% | 0%
BERCYN_2_BCEBT1 | Battery Storage | 2024 | summer | 2024-07-24 | 325 | 0 | 500 | 13 | 6500 | 265 | Blended | 5% | 0% | 8.576% | 0% | 6.239% | 0% | TRUE | 8.576% | 0% | 6.239% | 0%
BGROCK_2_BRFBX2 | Battery Storage | 2022 | nonsummer | 2025-05-28 | 0 | 0 | 0 | 200 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
BGROCK_2_BRFBX2 | Battery Storage | 2022 | summer | 2025-05-28 | 0 | 0 | 0 | 200 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
BGROCK_2_BRFBX2 | Battery Storage | 2023 | nonsummer | 2025-05-28 | 0 | 0 | 0 | 200 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
BGROCK_2_BRFBX2 | Battery Storage | 2023 | summer | 2025-05-28 | 0 | 0 | 0 | 200 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
BGROCK_2_BRFBX2 | Battery Storage | 2024 | nonsummer | 2025-05-28 | 0 | 0 | 0 | 200 | 0 | 1065 | Group |  |  | 6.223% | 0% | 6.223% | 0% | TRUE | 6.223% | 0% | 6.223% | 0%
BGROCK_2_BRFBX2 | Battery Storage | 2024 | summer | 2025-05-28 | 0 | 0 | 0 | 200 | 0 | 765 | Group |  |  | 8.576% | 0% | 8.576% | 0% | TRUE | 8.576% | 0% | 8.576% | 0%
BLKDIA_2_BDEBT1 | Battery Storage | 2022 | nonsummer | 2022-03-17 | 8648.7667 | 0 | 685 | 200 | 137000 | 375 | Blended | 6.313% | 0% | 15.33% | 0% | 9.503% | 0% | TRUE | 15.33% | 0% | 9.503% | 0%
BLKDIA_2_BDEBT1 | Battery Storage | 2022 | summer | 2022-03-17 | 44542.65 | 0 | 765 | 200 | 153000 | 0 | Individual | 29.11% | 0% |  |  | 29.11% | 0% | TRUE |  |  | 29.11% | 0%
BLKDIA_2_BDEBT1 | Battery Storage | 2023 | nonsummer | 2022-03-17 | 1577.1167 | 0 | 1060 | 200 | 212000 | 0 | Individual | 0.7439% | 0% |  |  | 0.7439% | 0% | TRUE |  |  | 0.7439% | 0%
BLKDIA_2_BDEBT1 | Battery Storage | 2023 | summer | 2022-03-17 | 4808.1333 | 0 | 765 | 200 | 153000 | 0 | Individual | 3.143% | 0% |  |  | 3.143% | 0% | TRUE |  |  | 3.143% | 0%
BLKDIA_2_BDEBT1 | Battery Storage | 2024 | nonsummer | 2022-03-17 | 2316.6667 | 0 | 1065 | 200 | 213000 | 0 | Individual | 1.088% | 0% |  |  | 1.088% | 0% | TRUE |  |  | 1.088% | 0%
BLKDIA_2_BDEBT1 | Battery Storage | 2024 | summer | 2022-03-17 | 3417.35 | 0 | 765 | 200 | 153000 | 0 | Individual | 2.234% | 0% |  |  | 2.234% | 0% | TRUE |  |  | 2.234% | 0%
BLM W_2_MDRBT1 | Battery Storage | 2022 | nonsummer | 2025-04-29 | 0 | 0 | 0 | 20 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
BLM W_2_MDRBT1 | Battery Storage | 2022 | summer | 2025-04-29 | 0 | 0 | 0 | 20 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
BLM W_2_MDRBT1 | Battery Storage | 2023 | nonsummer | 2025-04-29 | 0 | 0 | 0 | 20 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
BLM W_2_MDRBT1 | Battery Storage | 2023 | summer | 2025-04-29 | 0 | 0 | 0 | 20 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
BLM W_2_MDRBT1 | Battery Storage | 2024 | nonsummer | 2025-04-29 | 0 | 0 | 0 | 20 | 0 | 1065 | Group |  |  | 6.223% | 0% | 6.223% | 0% | TRUE | 6.223% | 0% | 6.223% | 0%
BLM W_2_MDRBT1 | Battery Storage | 2024 | summer | 2025-04-29 | 0 | 0 | 0 | 20 | 0 | 765 | Group |  |  | 8.576% | 0% | 8.576% | 0% | TRUE | 8.576% | 0% | 8.576% | 0%
BLVRDE_6_BLVBT1 | Battery Storage | 2022 | nonsummer | 2024-05-21 | 0 | 0 | 0 | 10 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
BLVRDE_6_BLVBT1 | Battery Storage | 2022 | summer | 2024-05-21 | 0 | 0 | 0 | 10 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
BLVRDE_6_BLVBT1 | Battery Storage | 2023 | nonsummer | 2024-05-21 | 0 | 0 | 0 | 10 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
BLVRDE_6_BLVBT1 | Battery Storage | 2023 | summer | 2024-05-21 | 0 | 0 | 0 | 10 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
BLVRDE_6_BLVBT1 | Battery Storage | 2024 | nonsummer | 2024-05-21 | 132 | 0 | 360 | 10 | 3600 | 705 | Blended | 3.667% | 0% | 6.223% | 0% | 5.359% | 0% | TRUE | 6.223% | 0% | 5.359% | 0%
BLVRDE_6_BLVBT1 | Battery Storage | 2024 | summer | 2024-05-21 | 2009.5542 | 0 | 765 | 10 | 7650 | 0 | Individual | 26.27% | 0% |  |  | 26.27% | 0% | TRUE |  |  | 26.27% | 0%
CABLRO_2_CBSBT1 | Battery Storage | 2022 | nonsummer | 2025-02-05 | 0 | 0 | 0 | 99.7 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
CABLRO_2_CBSBT1 | Battery Storage | 2022 | summer | 2025-02-05 | 0 | 0 | 0 | 99.7 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
CABLRO_2_CBSBT1 | Battery Storage | 2023 | nonsummer | 2025-02-05 | 0 | 0 | 0 | 99.7 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
CABLRO_2_CBSBT1 | Battery Storage | 2023 | summer | 2025-02-05 | 0 | 0 | 0 | 99.7 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
CABLRO_2_CBSBT1 | Battery Storage | 2024 | nonsummer | 2025-02-05 | 0 | 0 | 0 | 99.7 | 0 | 1065 | Group |  |  | 6.223% | 0% | 6.223% | 0% | TRUE | 6.223% | 0% | 6.223% | 0%
CABLRO_2_CBSBT1 | Battery Storage | 2024 | summer | 2025-02-05 | 0 | 0 | 0 | 99.7 | 0 | 765 | Group |  |  | 8.576% | 0% | 8.576% | 0% | TRUE | 8.576% | 0% | 8.576% | 0%
CALGEN_1_MDRBT1 | Battery Storage | 2022 | nonsummer | 2025-04-29 | 0 | 0 | 0 | 25 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
CALGEN_1_MDRBT1 | Battery Storage | 2022 | summer | 2025-04-29 | 0 | 0 | 0 | 25 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
CALGEN_1_MDRBT1 | Battery Storage | 2023 | nonsummer | 2025-04-29 | 0 | 0 | 0 | 25 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
CALGEN_1_MDRBT1 | Battery Storage | 2023 | summer | 2025-04-29 | 0 | 0 | 0 | 25 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
CALGEN_1_MDRBT1 | Battery Storage | 2024 | nonsummer | 2025-04-29 | 0 | 0 | 0 | 25 | 0 | 1065 | Group |  |  | 6.223% | 0% | 6.223% | 0% | TRUE | 6.223% | 0% | 6.223% | 0%
CALGEN_1_MDRBT1 | Battery Storage | 2024 | summer | 2025-04-29 | 0 | 0 | 0 | 25 | 0 | 765 | Group |  |  | 8.576% | 0% | 8.576% | 0% | TRUE | 8.576% | 0% | 8.576% | 0%
CASCES_6_CESBT1 | Battery Storage | 2022 | nonsummer | 2023-12-14 | 0 | 0 | 0 | 25 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
CASCES_6_CESBT1 | Battery Storage | 2022 | summer | 2023-12-14 | 0 | 0 | 0 | 25 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
CASCES_6_CESBT1 | Battery Storage | 2023 | nonsummer | 2023-12-14 | 0 | 0 | 90 | 25 | 2250 | 970 | Blended | 0% | 0% | 6.742% | 0% | 6.169% | 0% | TRUE | 6.742% | 0% | 6.169% | 0%
CASCES_6_CESBT1 | Battery Storage | 2023 | summer | 2023-12-14 | 0 | 0 | 0 | 25 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
CASCES_6_CESBT1 | Battery Storage | 2024 | nonsummer | 2023-12-14 | 1104.475 | 0 | 1065 | 25 | 26625 | 0 | Individual | 4.148% | 0% |  |  | 4.148% | 0% | TRUE |  |  | 4.148% | 0%
CASCES_6_CESBT1 | Battery Storage | 2024 | summer | 2023-12-14 | 360.0953 | 0 | 765 | 25 | 19125 | 0 | Individual | 1.883% | 0% |  |  | 1.883% | 0% | TRUE |  |  | 1.883% | 0%
CASCES_6_CESBT2 | Battery Storage | 2022 | nonsummer | 2025-03-15 | 0 | 0 | 0 | 20 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
CASCES_6_CESBT2 | Battery Storage | 2022 | summer | 2025-03-15 | 0 | 0 | 0 | 20 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
CASCES_6_CESBT2 | Battery Storage | 2023 | nonsummer | 2025-03-15 | 0 | 0 | 0 | 20 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
CASCES_6_CESBT2 | Battery Storage | 2023 | summer | 2025-03-15 | 0 | 0 | 0 | 20 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
CASCES_6_CESBT2 | Battery Storage | 2024 | nonsummer | 2025-03-15 | 120 | 0 | 0 | 20 | 0 | 1065 | Group |  |  | 6.223% | 0% | 6.223% | 0% | TRUE | 6.223% | 0% | 6.223% | 0%
CASCES_6_CESBT2 | Battery Storage | 2024 | summer | 2025-03-15 | 0 | 0 | 0 | 20 | 0 | 765 | Group |  |  | 8.576% | 0% | 8.576% | 0% | TRUE | 8.576% | 0% | 8.576% | 0%
CHINO_2_APEBT1 | Battery Storage | 2022 | nonsummer | 2016-12-31 | 980.4233 | 0 | 1060 | 20 | 21200 | 0 | Individual | 4.625% | 0% |  |  | 4.625% | 0% | TRUE |  |  | 4.625% | 0%
CHINO_2_APEBT1 | Battery Storage | 2022 | summer | 2016-12-31 | 656.4767 | 0 | 765 | 20 | 15300 | 0 | Individual | 4.291% | 0% |  |  | 4.291% | 0% | TRUE |  |  | 4.291% | 0%
CHINO_2_APEBT1 | Battery Storage | 2023 | nonsummer | 2016-12-31 | 1011.3233 | 0 | 1060 | 20 | 21200 | 0 | Individual | 4.77% | 0% |  |  | 4.77% | 0% | TRUE |  |  | 4.77% | 0%
CHINO_2_APEBT1 | Battery Storage | 2023 | summer | 2016-12-31 | 1660.425 | 0 | 765 | 20 | 15300 | 0 | Individual | 10.85% | 0% |  |  | 10.85% | 0% | TRUE |  |  | 10.85% | 0%
CHINO_2_APEBT1 | Battery Storage | 2024 | nonsummer | 2016-12-31 | 2208.68 | 0 | 1065 | 20 | 21300 | 0 | Individual | 10.37% | 0% |  |  | 10.37% | 0% | TRUE |  |  | 10.37% | 0%
CHINO_2_APEBT1 | Battery Storage | 2024 | summer | 2016-12-31 | 1695.13 | 0 | 765 | 20 | 15300 | 0 | Individual | 11.08% | 0% |  |  | 11.08% | 0% | TRUE |  |  | 11.08% | 0%
CHINO_2_PESBT1 | Battery Storage | 2022 | nonsummer | 2023-07-08 | 0 | 0 | 0 | 20 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
CHINO_2_PESBT1 | Battery Storage | 2022 | summer | 2023-07-08 | 0 | 0 | 0 | 20 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
CHINO_2_PESBT1 | Battery Storage | 2023 | nonsummer | 2023-07-08 | 2301.25 | 0 | 305 | 20 | 6100 | 755 | Blended | 37.73% | 0% | 6.742% | 0% | 15.66% | 0% | TRUE | 6.742% | 0% | 15.66% | 0%
CHINO_2_PESBT1 | Battery Storage | 2023 | summer | 2023-07-08 | 1836.3967 | 0 | 580 | 20 | 11600 | 185 | Blended | 15.83% | 0% | 6.657% | 0% | 13.61% | 0% | TRUE | 6.657% | 0% | 13.61% | 0%
CHINO_2_PESBT1 | Battery Storage | 2024 | nonsummer | 2023-07-08 | 1850.68 | 0 | 1065 | 20 | 21300 | 0 | Individual | 8.689% | 0% |  |  | 8.689% | 0% | TRUE |  |  | 8.689% | 0%
CHINO_2_PESBT1 | Battery Storage | 2024 | summer | 2023-07-08 | 612.8 | 0 | 765 | 20 | 15300 | 0 | Individual | 4.005% | 0% |  |  | 4.005% | 0% | TRUE |  |  | 4.005% | 0%
CLRMNT_6_CLEBT1 | Battery Storage | 2022 | nonsummer | 2024-03-27 | 0 | 0 | 0 | 9 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
CLRMNT_6_CLEBT1 | Battery Storage | 2022 | summer | 2024-03-27 | 0 | 0 | 0 | 9 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
CLRMNT_6_CLEBT1 | Battery Storage | 2023 | nonsummer | 2024-03-27 | 0 | 0 | 0 | 9 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
CLRMNT_6_CLEBT1 | Battery Storage | 2023 | summer | 2024-03-27 | 0 | 0 | 0 | 9 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
CLRMNT_6_CLEBT1 | Battery Storage | 2024 | nonsummer | 2024-03-27 | 774.4 | 0 | 635 | 9 | 5715 | 430 | Blended | 13.55% | 0% | 6.223% | 0% | 10.59% | 0% | TRUE | 6.223% | 0% | 10.59% | 0%
CLRMNT_6_CLEBT1 | Battery Storage | 2024 | summer | 2024-03-27 | 20.5 | 0 | 765 | 9 | 6885 | 0 | Individual | 0.2977% | 0% |  |  | 0.2977% | 0% | TRUE |  |  | 0.2977% | 0%
CONDOR_2_CDRBT1 | Battery Storage | 2022 | nonsummer | 2024-05-21 | 0 | 0 | 0 | 200 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
CONDOR_2_CDRBT1 | Battery Storage | 2022 | summer | 2024-05-21 | 0 | 0 | 0 | 200 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
CONDOR_2_CDRBT1 | Battery Storage | 2023 | nonsummer | 2024-05-21 | 0 | 0 | 0 | 200 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
CONDOR_2_CDRBT1 | Battery Storage | 2023 | summer | 2024-05-21 | 0 | 0 | 0 | 200 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
CONDOR_2_CDRBT1 | Battery Storage | 2024 | nonsummer | 2024-05-21 | 2390 | 0 | 360 | 200 | 72000 | 705 | Blended | 3.319% | 0% | 6.223% | 0% | 5.242% | 0% | TRUE | 6.223% | 0% | 5.242% | 0%
CONDOR_2_CDRBT1 | Battery Storage | 2024 | summer | 2024-05-21 | 5566.6667 | 0 | 765 | 200 | 153000 | 0 | Individual | 3.638% | 0% |  |  | 3.638% | 0% | TRUE |  |  | 3.638% | 0%
CRIMSN_2_CRMBT1 | Battery Storage | 2022 | nonsummer | 2022-09-16 | 3990.3333 | 0 | 305 | 200 | 61000 | 755 | Blended | 6.542% | 0% | 15.33% | 0% | 12.8% | 0% | TRUE | 15.33% | 0% | 12.8% | 0%
CRIMSN_2_CRMBT1 | Battery Storage | 2022 | summer | 2022-09-16 | 2658.184 | 0 | 230 | 200 | 46000 | 535 | Blended | 5.779% | 0% | 13.83% | 0% | 11.41% | 0% | TRUE | 13.83% | 0% | 11.41% | 0%
CRIMSN_2_CRMBT1 | Battery Storage | 2023 | nonsummer | 2022-09-16 | 30963.5285 | 0 | 1060 | 200 | 212000 | 0 | Individual | 14.61% | 0% |  |  | 14.61% | 0% | TRUE |  |  | 14.61% | 0%
CRIMSN_2_CRMBT1 | Battery Storage | 2023 | summer | 2022-09-16 | 5355.7417 | 0 | 765 | 200 | 153000 | 0 | Individual | 3.5% | 0% |  |  | 3.5% | 0% | TRUE |  |  | 3.5% | 0%
CRIMSN_2_CRMBT1 | Battery Storage | 2024 | nonsummer | 2022-09-16 | 8186.5833 | 0 | 1065 | 200 | 213000 | 0 | Individual | 3.843% | 0% |  |  | 3.843% | 0% | TRUE |  |  | 3.843% | 0%
CRIMSN_2_CRMBT1 | Battery Storage | 2024 | summer | 2022-09-16 | 13480.2583 | 0 | 765 | 200 | 153000 | 0 | Individual | 8.811% | 0% |  |  | 8.811% | 0% | TRUE |  |  | 8.811% | 0%
CRIMSN_2_CRMBT2 | Battery Storage | 2022 | nonsummer | 2022-10-28 | 0 | 0 | 305 | 150 | 45750 | 755 | Blended | 0% | 0% | 15.33% | 0% | 10.92% | 0% | TRUE | 15.33% | 0% | 10.92% | 0%
CRIMSN_2_CRMBT2 | Battery Storage | 2022 | summer | 2022-10-28 | 150 | 0 | 20 | 150 | 3000 | 745 | Blended | 5% | 0% | 13.83% | 0% | 13.6% | 0% | TRUE | 13.83% | 0% | 13.6% | 0%
CRIMSN_2_CRMBT2 | Battery Storage | 2023 | nonsummer | 2022-10-28 | 9730.9553 | 0 | 1060 | 150 | 159000 | 0 | Individual | 6.12% | 0% |  |  | 6.12% | 0% | TRUE |  |  | 6.12% | 0%
CRIMSN_2_CRMBT2 | Battery Storage | 2023 | summer | 2022-10-28 | 1944.9917 | 0 | 765 | 150 | 114750 | 0 | Individual | 1.695% | 0% |  |  | 1.695% | 0% | TRUE |  |  | 1.695% | 0%
CRIMSN_2_CRMBT2 | Battery Storage | 2024 | nonsummer | 2022-10-28 | 4237.475 | 0 | 1065 | 150 | 159750 | 0 | Individual | 2.653% | 0% |  |  | 2.653% | 0% | TRUE |  |  | 2.653% | 0%
CRIMSN_2_CRMBT2 | Battery Storage | 2024 | summer | 2022-10-28 | 5197.65 | 0 | 765 | 150 | 114750 | 0 | Individual | 4.53% | 0% |  |  | 4.53% | 0% | TRUE |  |  | 4.53% | 0%
DYLAN_2_BMTBT1 | Battery Storage | 2022 | nonsummer | 2024-08-27 | 0 | 0 | 0 | 100 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
DYLAN_2_BMTBT1 | Battery Storage | 2022 | summer | 2024-08-27 | 0 | 0 | 0 | 100 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
DYLAN_2_BMTBT1 | Battery Storage | 2023 | nonsummer | 2024-08-27 | 0 | 0 | 0 | 100 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
DYLAN_2_BMTBT1 | Battery Storage | 2023 | summer | 2024-08-27 | 0 | 0 | 0 | 100 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
DYLAN_2_BMTBT1 | Battery Storage | 2024 | nonsummer | 2024-08-27 | 150 | 0 | 305 | 100 | 30500 | 760 | Blended | 0.4918% | 0% | 6.223% | 0% | 4.582% | 0% | TRUE | 6.223% | 0% | 4.582% | 0%
DYLAN_2_BMTBT1 | Battery Storage | 2024 | summer | 2024-08-27 | 85 | 0 | 330 | 100 | 33000 | 435 | Blended | 0.2576% | 0% | 8.576% | 0% | 4.988% | 0% | TRUE | 8.576% | 0% | 4.988% | 0%
ELCAJN_6_EB1BT1 | Battery Storage | 2022 | nonsummer | 2017-02-18 | 170.625 | 0 | 1060 | 7.5 | 7950 | 0 | Individual | 2.146% | 0% |  |  | 2.146% | 0% | TRUE |  |  | 2.146% | 0%
ELCAJN_6_EB1BT1 | Battery Storage | 2022 | summer | 2017-02-18 | 412.125 | 0 | 765 | 7.5 | 5737.5 | 0 | Individual | 7.183% | 0% |  |  | 7.183% | 0% | TRUE |  |  | 7.183% | 0%
ELCAJN_6_EB1BT1 | Battery Storage | 2023 | nonsummer | 2017-02-18 | 602.125 | 0 | 1060 | 7.5 | 7950 | 0 | Individual | 7.574% | 0% |  |  | 7.574% | 0% | TRUE |  |  | 7.574% | 0%
ELCAJN_6_EB1BT1 | Battery Storage | 2023 | summer | 2017-02-18 | 690 | 0 | 765 | 7.5 | 5737.5 | 0 | Individual | 12.03% | 0% |  |  | 12.03% | 0% | TRUE |  |  | 12.03% | 0%
ELCAJN_6_EB1BT1 | Battery Storage | 2024 | nonsummer | 2017-02-18 | 571.15 | 0 | 1065 | 7.5 | 7987.5 | 0 | Individual | 7.151% | 0% |  |  | 7.151% | 0% | TRUE |  |  | 7.151% | 0%
ELCAJN_6_EB1BT1 | Battery Storage | 2024 | summer | 2017-02-18 | 491 | 0 | 765 | 7.5 | 5737.5 | 0 | Individual | 8.558% | 0% |  |  | 8.558% | 0% | TRUE |  |  | 8.558% | 0%
ELKHRN_1_EESX3 | Battery Storage | 2022 | nonsummer | 2022-04-07 | 54062.5 | 0 | 580 | 182.5 | 105850 | 480 | Blended | 51.07% | 0% | 15.33% | 0% | 34.89% | 0% | TRUE | 15.33% | 0% | 34.89% | 0%
ELKHRN_1_EESX3 | Battery Storage | 2022 | summer | 2022-04-07 | 38580.5 | 0 | 765 | 182.5 | 139612.5 | 0 | Individual | 27.63% | 0% |  |  | 27.63% | 0% | TRUE |  |  | 27.63% | 0%
ELKHRN_1_EESX3 | Battery Storage | 2023 | nonsummer | 2022-04-07 | 21117.1542 | 0 | 1060 | 182.5 | 193450 | 0 | Individual | 10.92% | 0% |  |  | 10.92% | 0% | TRUE |  |  | 10.92% | 0%
ELKHRN_1_EESX3 | Battery Storage | 2023 | summer | 2022-04-07 | 14608.3 | 0 | 765 | 182.5 | 139612.5 | 0 | Individual | 10.46% | 0% |  |  | 10.46% | 0% | TRUE |  |  | 10.46% | 0%
ELKHRN_1_EESX3 | Battery Storage | 2024 | nonsummer | 2022-04-07 | 15288.977 | 0 | 1065 | 182.5 | 194362.5 | 0 | Individual | 7.866% | 0% |  |  | 7.866% | 0% | TRUE |  |  | 7.866% | 0%
ELKHRN_1_EESX3 | Battery Storage | 2024 | summer | 2022-04-07 | 9428.7785 | 0 | 765 | 182.5 | 139612.5 | 0 | Individual | 6.754% | 0% |  |  | 6.754% | 0% | TRUE |  |  | 6.754% | 0%
ELLIOT_6_ELIBT1 | Battery Storage | 2022 | nonsummer | 2024-04-10 | 0 | 0 | 0 | 10 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
ELLIOT_6_ELIBT1 | Battery Storage | 2022 | summer | 2024-04-10 | 0 | 0 | 0 | 10 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
ELLIOT_6_ELIBT1 | Battery Storage | 2023 | nonsummer | 2024-04-10 | 0 | 0 | 0 | 10 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
ELLIOT_6_ELIBT1 | Battery Storage | 2023 | summer | 2024-04-10 | 0 | 0 | 0 | 10 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
ELLIOT_6_ELIBT1 | Battery Storage | 2024 | nonsummer | 2024-04-10 | 355.5667 | 0 | 565 | 10 | 5650 | 500 | Blended | 6.293% | 0% | 6.223% | 0% | 6.26% | 0% | TRUE | 6.223% | 0% | 6.26% | 0%
ELLIOT_6_ELIBT1 | Battery Storage | 2024 | summer | 2024-04-10 | 301 | 0 | 765 | 10 | 7650 | 0 | Individual | 3.935% | 0% |  |  | 3.935% | 0% | TRUE |  |  | 3.935% | 0%
ESCNDO_6_EB1BT1 | Battery Storage | 2022 | nonsummer | 2017-03-06 | 1100 | 0 | 1060 | 10 | 10600 | 0 | Individual | 10.38% | 0% |  |  | 10.38% | 0% | TRUE |  |  | 10.38% | 0%
ESCNDO_6_EB1BT1 | Battery Storage | 2022 | summer | 2017-03-06 | 2271.9083 | 0 | 765 | 10 | 7650 | 0 | Individual | 29.7% | 0% |  |  | 29.7% | 0% | TRUE |  |  | 29.7% | 0%
ESCNDO_6_EB1BT1 | Battery Storage | 2023 | nonsummer | 2017-03-06 | 2169.3333 | 0 | 1060 | 10 | 10600 | 0 | Individual | 20.47% | 0% |  |  | 20.47% | 0% | TRUE |  |  | 20.47% | 0%
ESCNDO_6_EB1BT1 | Battery Storage | 2023 | summer | 2017-03-06 | 764 | 0 | 765 | 10 | 7650 | 0 | Individual | 9.987% | 0% |  |  | 9.987% | 0% | TRUE |  |  | 9.987% | 0%
ESCNDO_6_EB1BT1 | Battery Storage | 2024 | nonsummer | 2017-03-06 | 4345.5 | 0 | 1065 | 10 | 10650 | 0 | Individual | 40.8% | 0% |  |  | 40.8% | 0% | TRUE |  |  | 40.8% | 0%
ESCNDO_6_EB1BT1 | Battery Storage | 2024 | summer | 2017-03-06 | 3205 | 0 | 765 | 10 | 7650 | 0 | Individual | 41.9% | 0% |  |  | 41.9% | 0% | TRUE |  |  | 41.9% | 0%
ESCNDO_6_EB2BT2 | Battery Storage | 2022 | nonsummer | 2017-03-06 | 1655 | 0 | 1060 | 10 | 10600 | 0 | Individual | 15.61% | 0% |  |  | 15.61% | 0% | TRUE |  |  | 15.61% | 0%
ESCNDO_6_EB2BT2 | Battery Storage | 2022 | summer | 2017-03-06 | 2671.925 | 0 | 765 | 10 | 7650 | 0 | Individual | 34.93% | 0% |  |  | 34.93% | 0% | TRUE |  |  | 34.93% | 0%
ESCNDO_6_EB2BT2 | Battery Storage | 2023 | nonsummer | 2017-03-06 | 2351.9167 | 0 | 1060 | 10 | 10600 | 0 | Individual | 22.19% | 0% |  |  | 22.19% | 0% | TRUE |  |  | 22.19% | 0%
ESCNDO_6_EB2BT2 | Battery Storage | 2023 | summer | 2017-03-06 | 1472.5 | 0 | 765 | 10 | 7650 | 0 | Individual | 19.25% | 0% |  |  | 19.25% | 0% | TRUE |  |  | 19.25% | 0%
ESCNDO_6_EB2BT2 | Battery Storage | 2024 | nonsummer | 2017-03-06 | 4237.9667 | 0 | 1065 | 10 | 10650 | 0 | Individual | 39.79% | 0% |  |  | 39.79% | 0% | TRUE |  |  | 39.79% | 0%
ESCNDO_6_EB2BT2 | Battery Storage | 2024 | summer | 2017-03-06 | 2529.25 | 0 | 765 | 10 | 7650 | 0 | Individual | 33.06% | 0% |  |  | 33.06% | 0% | TRUE |  |  | 33.06% | 0%
ESCNDO_6_EB3BT3 | Battery Storage | 2022 | nonsummer | 2017-03-06 | 1677.5 | 0 | 1060 | 10 | 10600 | 0 | Individual | 15.83% | 0% |  |  | 15.83% | 0% | TRUE |  |  | 15.83% | 0%
ESCNDO_6_EB3BT3 | Battery Storage | 2022 | summer | 2017-03-06 | 2898.0333 | 0 | 765 | 10 | 7650 | 0 | Individual | 37.88% | 0% |  |  | 37.88% | 0% | TRUE |  |  | 37.88% | 0%
ESCNDO_6_EB3BT3 | Battery Storage | 2023 | nonsummer | 2017-03-06 | 2708.25 | 0 | 1060 | 10 | 10600 | 0 | Individual | 25.55% | 0% |  |  | 25.55% | 0% | TRUE |  |  | 25.55% | 0%
ESCNDO_6_EB3BT3 | Battery Storage | 2023 | summer | 2017-03-06 | 988 | 0 | 765 | 10 | 7650 | 0 | Individual | 12.92% | 0% |  |  | 12.92% | 0% | TRUE |  |  | 12.92% | 0%
ESCNDO_6_EB3BT3 | Battery Storage | 2024 | nonsummer | 2017-03-06 | 4825.5 | 0 | 1065 | 10 | 10650 | 0 | Individual | 45.31% | 0% |  |  | 45.31% | 0% | TRUE |  |  | 45.31% | 0%
ESCNDO_6_EB3BT3 | Battery Storage | 2024 | summer | 2017-03-06 | 2862.5 | 0 | 765 | 10 | 7650 | 0 | Individual | 37.42% | 0% |  |  | 37.42% | 0% | TRUE |  |  | 37.42% | 0%
ESNHWR_2_CS1BT3 | Battery Storage | 2022 | nonsummer | 2025-05-13 | 0 | 0 | 0 | 10 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
ESNHWR_2_CS1BT3 | Battery Storage | 2022 | summer | 2025-05-13 | 0 | 0 | 0 | 10 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
ESNHWR_2_CS1BT3 | Battery Storage | 2023 | nonsummer | 2025-05-13 | 0 | 0 | 0 | 10 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
ESNHWR_2_CS1BT3 | Battery Storage | 2023 | summer | 2025-05-13 | 0 | 0 | 0 | 10 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
ESNHWR_2_CS1BT3 | Battery Storage | 2024 | nonsummer | 2025-05-13 | 0 | 0 | 0 | 10 | 0 | 1065 | Group |  |  | 6.223% | 0% | 6.223% | 0% | TRUE | 6.223% | 0% | 6.223% | 0%
ESNHWR_2_CS1BT3 | Battery Storage | 2024 | summer | 2025-05-13 | 0 | 0 | 0 | 10 | 0 | 765 | Group |  |  | 8.576% | 0% | 8.576% | 0% | TRUE | 8.576% | 0% | 8.576% | 0%
ESNHWR_2_HDSBT2 | Battery Storage | 2022 | nonsummer | 2025-05-16 | 0 | 0 | 0 | 10 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
ESNHWR_2_HDSBT2 | Battery Storage | 2022 | summer | 2025-05-16 | 0 | 0 | 0 | 10 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
ESNHWR_2_HDSBT2 | Battery Storage | 2023 | nonsummer | 2025-05-16 | 0 | 0 | 0 | 10 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
ESNHWR_2_HDSBT2 | Battery Storage | 2023 | summer | 2025-05-16 | 0 | 0 | 0 | 10 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
ESNHWR_2_HDSBT2 | Battery Storage | 2024 | nonsummer | 2025-05-16 | 0 | 0 | 0 | 10 | 0 | 1065 | Group |  |  | 6.223% | 0% | 6.223% | 0% | TRUE | 6.223% | 0% | 6.223% | 0%
ESNHWR_2_HDSBT2 | Battery Storage | 2024 | summer | 2025-05-16 | 0 | 0 | 0 | 10 | 0 | 765 | Group |  |  | 8.576% | 0% | 8.576% | 0% | TRUE | 8.576% | 0% | 8.576% | 0%
ESNHWR_2_WC1BT1 | Battery Storage | 2022 | nonsummer | 2021-10-13 | 201.8333 | 0 | 1060 | 3 | 3180 | 0 | Individual | 6.347% | 0% |  |  | 6.347% | 0% | TRUE |  |  | 6.347% | 0%
ESNHWR_2_WC1BT1 | Battery Storage | 2022 | summer | 2021-10-13 | 263.15 | 0 | 765 | 3 | 2295 | 0 | Individual | 11.47% | 0% |  |  | 11.47% | 0% | TRUE |  |  | 11.47% | 0%
ESNHWR_2_WC1BT1 | Battery Storage | 2023 | nonsummer | 2021-10-13 | 210 | 0 | 1060 | 3 | 3180 | 0 | Individual | 6.604% | 0% |  |  | 6.604% | 0% | TRUE |  |  | 6.604% | 0%
ESNHWR_2_WC1BT1 | Battery Storage | 2023 | summer | 2021-10-13 | 421.45 | 0 | 765 | 3 | 2295 | 0 | Individual | 18.36% | 0% |  |  | 18.36% | 0% | TRUE |  |  | 18.36% | 0%
ESNHWR_2_WC1BT1 | Battery Storage | 2024 | nonsummer | 2021-10-13 | 53.25 | 0 | 1065 | 3 | 3195 | 0 | Individual | 1.667% | 0% |  |  | 1.667% | 0% | TRUE |  |  | 1.667% | 0%
ESNHWR_2_WC1BT1 | Battery Storage | 2024 | summer | 2021-10-13 | 328.9 | 0 | 765 | 3 | 2295 | 0 | Individual | 14.33% | 0% |  |  | 14.33% | 0% | TRUE |  |  | 14.33% | 0%
ETIWND_2_SEPBT1 | Battery Storage | 2022 | nonsummer | 2024-09-24 | 0 | 0 | 0 | 100 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
ETIWND_2_SEPBT1 | Battery Storage | 2022 | summer | 2024-09-24 | 0 | 0 | 0 | 100 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
ETIWND_2_SEPBT1 | Battery Storage | 2023 | nonsummer | 2024-09-24 | 0 | 0 | 0 | 100 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
ETIWND_2_SEPBT1 | Battery Storage | 2023 | summer | 2024-09-24 | 0 | 0 | 0 | 100 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
ETIWND_2_SEPBT1 | Battery Storage | 2024 | nonsummer | 2024-09-24 | 16369.9167 | 0 | 305 | 100 | 30500 | 760 | Blended | 53.67% | 0% | 6.223% | 0% | 19.81% | 0% | TRUE | 6.223% | 0% | 19.81% | 0%
ETIWND_2_SEPBT1 | Battery Storage | 2024 | summer | 2024-09-24 | 5964.6667 | 0 | 190 | 100 | 19000 | 575 | Blended | 31.39% | 0% | 8.576% | 0% | 14.24% | 0% | TRUE | 8.576% | 0% | 14.24% | 0%
ETIWND_6_INEBT1 | Battery Storage | 2022 | nonsummer | 2024-10-09 | 0 | 0 | 0 | 70 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
ETIWND_6_INEBT1 | Battery Storage | 2022 | summer | 2024-10-09 | 0 | 0 | 0 | 70 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
ETIWND_6_INEBT1 | Battery Storage | 2023 | nonsummer | 2024-10-09 | 0 | 0 | 0 | 70 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
ETIWND_6_INEBT1 | Battery Storage | 2023 | summer | 2024-10-09 | 0 | 0 | 0 | 70 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
ETIWND_6_INEBT1 | Battery Storage | 2024 | nonsummer | 2024-10-09 | 7780.1667 | 0 | 305 | 70 | 21350 | 760 | Blended | 36.44% | 0% | 6.223% | 0% | 14.88% | 0% | TRUE | 6.223% | 0% | 14.88% | 0%
ETIWND_6_INEBT1 | Battery Storage | 2024 | summer | 2024-10-09 | 0 | 0 | 115 | 70 | 8050 | 650 | Blended | 0% | 0% | 8.576% | 0% | 7.287% | 0% | TRUE | 8.576% | 0% | 7.287% | 0%
FALBRK_6_FESBT1 | Battery Storage | 2022 | nonsummer | 2023-05-03 | 0 | 0 | 0 | 40 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
FALBRK_6_FESBT1 | Battery Storage | 2022 | summer | 2023-05-03 | 0 | 0 | 0 | 40 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
FALBRK_6_FESBT1 | Battery Storage | 2023 | nonsummer | 2023-05-03 | 2686 | 0 | 450 | 40 | 18000 | 610 | Blended | 14.92% | 0% | 6.742% | 0% | 10.21% | 0% | TRUE | 6.742% | 0% | 10.21% | 0%
FALBRK_6_FESBT1 | Battery Storage | 2023 | summer | 2023-05-03 | 6168.6333 | 0 | 765 | 40 | 30600 | 0 | Individual | 20.16% | 0% |  |  | 20.16% | 0% | TRUE |  |  | 20.16% | 0%
FALBRK_6_FESBT1 | Battery Storage | 2024 | nonsummer | 2023-05-03 | 1660 | 0 | 1065 | 40 | 42600 | 0 | Individual | 3.897% | 0% |  |  | 3.897% | 0% | TRUE |  |  | 3.897% | 0%
FALBRK_6_FESBT1 | Battery Storage | 2024 | summer | 2023-05-03 | 1458.8333 | 0 | 765 | 40 | 30600 | 0 | Individual | 4.767% | 0% |  |  | 4.767% | 0% | TRUE |  |  | 4.767% | 0%
GATEWY_2_GESBT1 | Battery Storage | 2022 | nonsummer | 2025-04-22 | 9500.225 | 0 | 0 | 250 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
GATEWY_2_GESBT1 | Battery Storage | 2022 | summer | 2025-04-22 | 1602.1833 | 0 | 0 | 250 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
GATEWY_2_GESBT1 | Battery Storage | 2023 | nonsummer | 2025-04-22 | 903.8333 | 0 | 0 | 250 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
GATEWY_2_GESBT1 | Battery Storage | 2023 | summer | 2025-04-22 | 6804.1667 | 0 | 0 | 250 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
GATEWY_2_GESBT1 | Battery Storage | 2024 | nonsummer | 2025-04-22 | 75017.85 | 0 | 0 | 250 | 0 | 1065 | Group |  |  | 6.223% | 0% | 6.223% | 0% | TRUE | 6.223% | 0% | 6.223% | 0%
GATEWY_2_GESBT1 | Battery Storage | 2024 | summer | 2025-04-22 | 151153.205 | 0 | 0 | 250 | 0 | 765 | Group |  |  | 8.576% | 0% | 8.576% | 0% | TRUE | 8.576% | 0% | 8.576% | 0%
GOLETA_2_GE2BT3 | Battery Storage | 2022 | nonsummer | 2024-01-06 | 0 | 0 | 0 | 60 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
GOLETA_2_GE2BT3 | Battery Storage | 2022 | summer | 2024-01-06 | 0 | 0 | 0 | 60 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
GOLETA_2_GE2BT3 | Battery Storage | 2023 | nonsummer | 2024-01-06 | 0 | 0 | 0 | 60 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
GOLETA_2_GE2BT3 | Battery Storage | 2023 | summer | 2024-01-06 | 0 | 0 | 0 | 60 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
GOLETA_2_GE2BT3 | Battery Storage | 2024 | nonsummer | 2024-01-06 | 1022 | 0 | 1040 | 60 | 62400 | 25 | Blended | 1.638% | 0% | 6.223% | 0% | 1.745% | 0% | TRUE | 6.223% | 0% | 1.745% | 0%
GOLETA_2_GE2BT3 | Battery Storage | 2024 | summer | 2024-01-06 | 255 | 0 | 765 | 60 | 45900 | 0 | Individual | 0.5556% | 0% |  |  | 0.5556% | 0% | TRUE |  |  | 0.5556% | 0%
GOLETA_2_VALBT1 | Battery Storage | 2022 | nonsummer | 2021-02-04 | 108.1333 | 0 | 1060 | 10 | 10600 | 0 | Individual | 1.02% | 0% |  |  | 1.02% | 0% | TRUE |  |  | 1.02% | 0%
GOLETA_2_VALBT1 | Battery Storage | 2022 | summer | 2021-02-04 | 15.8333 | 0 | 765 | 10 | 7650 | 0 | Individual | 0.207% | 0% |  |  | 0.207% | 0% | TRUE |  |  | 0.207% | 0%
GOLETA_2_VALBT1 | Battery Storage | 2023 | nonsummer | 2021-02-04 | 970.3717 | 0 | 1060 | 10 | 10600 | 0 | Individual | 9.154% | 0% |  |  | 9.154% | 0% | TRUE |  |  | 9.154% | 0%
GOLETA_2_VALBT1 | Battery Storage | 2023 | summer | 2021-02-04 | 115.4617 | 0 | 765 | 10 | 7650 | 0 | Individual | 1.509% | 0% |  |  | 1.509% | 0% | TRUE |  |  | 1.509% | 0%
GOLETA_2_VALBT1 | Battery Storage | 2024 | nonsummer | 2021-02-04 | 149.1667 | 0 | 1065 | 10 | 10650 | 0 | Individual | 1.401% | 0% |  |  | 1.401% | 0% | TRUE |  |  | 1.401% | 0%
GOLETA_2_VALBT1 | Battery Storage | 2024 | summer | 2021-02-04 | 34.1133 | 0 | 765 | 10 | 7650 | 0 | Individual | 0.4459% | 0% |  |  | 0.4459% | 0% | TRUE |  |  | 0.4459% | 0%
HENRTA_6_HDEBT1 | Battery Storage | 2022 | nonsummer | 2021-11-04 | 128.7333 | 0 | 1060 | 10 | 10600 | 0 | Individual | 1.214% | 0% |  |  | 1.214% | 0% | TRUE |  |  | 1.214% | 0%
HENRTA_6_HDEBT1 | Battery Storage | 2022 | summer | 2021-11-04 | 2 | 0 | 765 | 10 | 7650 | 0 | Individual | 0.02614% | 0% |  |  | 0.02614% | 0% | TRUE |  |  | 0.02614% | 0%
HENRTA_6_HDEBT1 | Battery Storage | 2023 | nonsummer | 2021-11-04 | 42.7667 | 0 | 1060 | 10 | 10600 | 0 | Individual | 0.4035% | 0% |  |  | 0.4035% | 0% | TRUE |  |  | 0.4035% | 0%
HENRTA_6_HDEBT1 | Battery Storage | 2023 | summer | 2021-11-04 | 7.6667 | 0 | 765 | 10 | 7650 | 0 | Individual | 0.1002% | 0% |  |  | 0.1002% | 0% | TRUE |  |  | 0.1002% | 0%
HENRTA_6_HDEBT1 | Battery Storage | 2024 | nonsummer | 2021-11-04 | 3097.9667 | 0 | 1065 | 10 | 10650 | 0 | Individual | 29.09% | 0% |  |  | 29.09% | 0% | TRUE |  |  | 29.09% | 0%
HENRTA_6_HDEBT1 | Battery Storage | 2024 | summer | 2021-11-04 | 4863 | 0 | 765 | 10 | 7650 | 0 | Individual | 63.57% | 0% |  |  | 63.57% | 0% | TRUE |  |  | 63.57% | 0%
JOANEC_2_ST3BT3 | Battery Storage | 2022 | nonsummer | 2023-06-02 | 0 | 0 | 0 | 40 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
JOANEC_2_ST3BT3 | Battery Storage | 2022 | summer | 2023-06-02 | 0 | 0 | 0 | 40 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
JOANEC_2_ST3BT3 | Battery Storage | 2023 | nonsummer | 2023-06-02 | 2 | 0 | 305 | 40 | 12200 | 755 | Blended | 0.01639% | 0% | 6.742% | 0% | 4.807% | 0% | TRUE | 6.742% | 0% | 4.807% | 0%
JOANEC_2_ST3BT3 | Battery Storage | 2023 | summer | 2023-06-02 | 39.0333 | 0 | 760 | 40 | 30400 | 5 | Blended | 0.1284% | 0% | 6.657% | 0% | 0.1711% | 0% | TRUE | 6.657% | 0% | 0.1711% | 0%
JOANEC_2_ST3BT3 | Battery Storage | 2024 | nonsummer | 2023-06-02 | 99.3333 | 0 | 1065 | 40 | 42600 | 0 | Individual | 0.2332% | 0% |  |  | 0.2332% | 0% | TRUE |  |  | 0.2332% | 0%
JOANEC_2_ST3BT3 | Battery Storage | 2024 | summer | 2023-06-02 | 36.6667 | 0 | 765 | 40 | 30600 | 0 | Individual | 0.1198% | 0% |  |  | 0.1198% | 0% | TRUE |  |  | 0.1198% | 0%
JOANEC_2_STABT1 | Battery Storage | 2022 | nonsummer | 2021-06-11 | 193.1333 | 0 | 1060 | 20 | 21200 | 0 | Individual | 0.911% | 0% |  |  | 0.911% | 0% | TRUE |  |  | 0.911% | 0%
JOANEC_2_STABT1 | Battery Storage | 2022 | summer | 2021-06-11 | 567.6667 | 0 | 765 | 20 | 15300 | 0 | Individual | 3.71% | 0% |  |  | 3.71% | 0% | TRUE |  |  | 3.71% | 0%
JOANEC_2_STABT1 | Battery Storage | 2023 | nonsummer | 2021-06-11 | 230 | 0 | 1060 | 20 | 21200 | 0 | Individual | 1.085% | 0% |  |  | 1.085% | 0% | TRUE |  |  | 1.085% | 0%
JOANEC_2_STABT1 | Battery Storage | 2023 | summer | 2021-06-11 | 0 | 0 | 765 | 20 | 15300 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
JOANEC_2_STABT1 | Battery Storage | 2024 | nonsummer | 2021-06-11 | 998.3333 | 0 | 1065 | 20 | 21300 | 0 | Individual | 4.687% | 0% |  |  | 4.687% | 0% | TRUE |  |  | 4.687% | 0%
JOANEC_2_STABT1 | Battery Storage | 2024 | summer | 2021-06-11 | 419.5 | 0 | 765 | 20 | 15300 | 0 | Individual | 2.742% | 0% |  |  | 2.742% | 0% | TRUE |  |  | 2.742% | 0%
JOANEC_2_STABT2 | Battery Storage | 2022 | nonsummer | 2022-06-06 | 0 | 0 | 305 | 20 | 6100 | 755 | Blended | 0% | 0% | 15.33% | 0% | 10.92% | 0% | TRUE | 15.33% | 0% | 10.92% | 0%
JOANEC_2_STABT2 | Battery Storage | 2022 | summer | 2022-06-06 | 122.5 | 0 | 740 | 20 | 14800 | 25 | Blended | 0.8277% | 0% | 13.83% | 0% | 1.253% | 0% | TRUE | 13.83% | 0% | 1.253% | 0%
JOANEC_2_STABT2 | Battery Storage | 2023 | nonsummer | 2022-06-06 | 8.5 | 0 | 1060 | 20 | 21200 | 0 | Individual | 0.04009% | 0% |  |  | 0.04009% | 0% | TRUE |  |  | 0.04009% | 0%
JOANEC_2_STABT2 | Battery Storage | 2023 | summer | 2022-06-06 | 76 | 0 | 765 | 20 | 15300 | 0 | Individual | 0.4967% | 0% |  |  | 0.4967% | 0% | TRUE |  |  | 0.4967% | 0%
JOANEC_2_STABT2 | Battery Storage | 2024 | nonsummer | 2022-06-06 | 2.3333 | 0 | 1065 | 20 | 21300 | 0 | Individual | 0.01095% | 0% |  |  | 0.01095% | 0% | TRUE |  |  | 0.01095% | 0%
JOANEC_2_STABT2 | Battery Storage | 2024 | summer | 2022-06-06 | 43.6 | 0 | 765 | 20 | 15300 | 0 | Individual | 0.285% | 0% |  |  | 0.285% | 0% | TRUE |  |  | 0.285% | 0%
JOHANN_2_JOSBT1 | Battery Storage | 2022 | nonsummer | 2021-10-29 | 539.9133 | 0 | 1060 | 10 | 10600 | 0 | Individual | 5.094% | 0% |  |  | 5.094% | 0% | TRUE |  |  | 5.094% | 0%
JOHANN_2_JOSBT1 | Battery Storage | 2022 | summer | 2021-10-29 | 571.5 | 0 | 765 | 10 | 7650 | 0 | Individual | 7.471% | 0% |  |  | 7.471% | 0% | TRUE |  |  | 7.471% | 0%
JOHANN_2_JOSBT1 | Battery Storage | 2023 | nonsummer | 2021-10-29 | 699.8833 | 0 | 1060 | 10 | 10600 | 0 | Individual | 6.603% | 0% |  |  | 6.603% | 0% | TRUE |  |  | 6.603% | 0%
JOHANN_2_JOSBT1 | Battery Storage | 2023 | summer | 2021-10-29 | 290.7667 | 0 | 765 | 10 | 7650 | 0 | Individual | 3.801% | 0% |  |  | 3.801% | 0% | TRUE |  |  | 3.801% | 0%
JOHANN_2_JOSBT1 | Battery Storage | 2024 | nonsummer | 2021-10-29 | 2176.85 | 0 | 1065 | 10 | 10650 | 0 | Individual | 20.44% | 0% |  |  | 20.44% | 0% | TRUE |  |  | 20.44% | 0%
JOHANN_2_JOSBT1 | Battery Storage | 2024 | summer | 2021-10-29 | 1661.4167 | 0 | 765 | 10 | 7650 | 0 | Individual | 21.72% | 0% |  |  | 21.72% | 0% | TRUE |  |  | 21.72% | 0%
JOHANN_2_JOSBT2 | Battery Storage | 2022 | nonsummer | 2021-10-29 | 633.7333 | 0 | 1060 | 10 | 10600 | 0 | Individual | 5.979% | 0% |  |  | 5.979% | 0% | TRUE |  |  | 5.979% | 0%
JOHANN_2_JOSBT2 | Battery Storage | 2022 | summer | 2021-10-29 | 383.5 | 0 | 765 | 10 | 7650 | 0 | Individual | 5.013% | 0% |  |  | 5.013% | 0% | TRUE |  |  | 5.013% | 0%
JOHANN_2_JOSBT2 | Battery Storage | 2023 | nonsummer | 2021-10-29 | 260.7 | 0 | 1060 | 10 | 10600 | 0 | Individual | 2.459% | 0% |  |  | 2.459% | 0% | TRUE |  |  | 2.459% | 0%
JOHANN_2_JOSBT2 | Battery Storage | 2023 | summer | 2021-10-29 | 315.9167 | 0 | 765 | 10 | 7650 | 0 | Individual | 4.13% | 0% |  |  | 4.13% | 0% | TRUE |  |  | 4.13% | 0%
JOHANN_2_JOSBT2 | Battery Storage | 2024 | nonsummer | 2021-10-29 | 519.8 | 0 | 1065 | 10 | 10650 | 0 | Individual | 4.881% | 0% |  |  | 4.881% | 0% | TRUE |  |  | 4.881% | 0%
JOHANN_2_JOSBT2 | Battery Storage | 2024 | summer | 2021-10-29 | 672.6167 | 0 | 765 | 10 | 7650 | 0 | Individual | 8.792% | 0% |  |  | 8.792% | 0% | TRUE |  |  | 8.792% | 0%
JOHANN_2_OCEBT2 | Battery Storage | 2022 | nonsummer | 2021-12-07 | 94.2 | 0 | 1060 | 9 | 9540 | 0 | Individual | 0.9874% | 0% |  |  | 0.9874% | 0% | TRUE |  |  | 0.9874% | 0%
JOHANN_2_OCEBT2 | Battery Storage | 2022 | summer | 2021-12-07 | 0 | 0 | 765 | 9 | 6885 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
JOHANN_2_OCEBT2 | Battery Storage | 2023 | nonsummer | 2021-12-07 | 327.8333 | 0 | 1060 | 9 | 9540 | 0 | Individual | 3.436% | 0% |  |  | 3.436% | 0% | TRUE |  |  | 3.436% | 0%
JOHANN_2_OCEBT2 | Battery Storage | 2023 | summer | 2021-12-07 | 94.35 | 0 | 765 | 9 | 6885 | 0 | Individual | 1.37% | 0% |  |  | 1.37% | 0% | TRUE |  |  | 1.37% | 0%
JOHANN_2_OCEBT2 | Battery Storage | 2024 | nonsummer | 2021-12-07 | 2863.3167 | 0 | 1065 | 9 | 9585 | 0 | Individual | 29.87% | 0% |  |  | 29.87% | 0% | TRUE |  |  | 29.87% | 0%
JOHANN_2_OCEBT2 | Battery Storage | 2024 | summer | 2021-12-07 | 5416.1167 | 0 | 765 | 9 | 6885 | 0 | Individual | 78.67% | 0% |  |  | 78.67% | 0% | TRUE |  |  | 78.67% | 0%
JOHANN_2_OCEBT3 | Battery Storage | 2022 | nonsummer | 2021-12-07 | 77.55 | 0 | 1060 | 6 | 6360 | 0 | Individual | 1.219% | 0% |  |  | 1.219% | 0% | TRUE |  |  | 1.219% | 0%
JOHANN_2_OCEBT3 | Battery Storage | 2022 | summer | 2021-12-07 | 3.1 | 0 | 765 | 6 | 4590 | 0 | Individual | 0.06754% | 0% |  |  | 0.06754% | 0% | TRUE |  |  | 0.06754% | 0%
JOHANN_2_OCEBT3 | Battery Storage | 2023 | nonsummer | 2021-12-07 | 242.25 | 0 | 1060 | 6 | 6360 | 0 | Individual | 3.809% | 0% |  |  | 3.809% | 0% | TRUE |  |  | 3.809% | 0%
JOHANN_2_OCEBT3 | Battery Storage | 2023 | summer | 2021-12-07 | 2.8833 | 0 | 765 | 6 | 4590 | 0 | Individual | 0.06282% | 0% |  |  | 0.06282% | 0% | TRUE |  |  | 0.06282% | 0%
JOHANN_2_OCEBT3 | Battery Storage | 2024 | nonsummer | 2021-12-07 | 1892.8 | 0 | 1065 | 6 | 6390 | 0 | Individual | 29.62% | 0% |  |  | 29.62% | 0% | TRUE |  |  | 29.62% | 0%
JOHANN_2_OCEBT3 | Battery Storage | 2024 | summer | 2021-12-07 | 3242.05 | 0 | 765 | 6 | 4590 | 0 | Individual | 70.63% | 0% |  |  | 70.63% | 0% | TRUE |  |  | 70.63% | 0%
KEARNY_6_NESBT1 | Battery Storage | 2022 | nonsummer | 2022-03-10 | 512.6167 | 0 | 720 | 10 | 7200 | 340 | Blended | 7.12% | 0% | 15.33% | 0% | 9.753% | 0% | TRUE | 15.33% | 0% | 9.753% | 0%
KEARNY_6_NESBT1 | Battery Storage | 2022 | summer | 2022-03-10 | 313.7 | 0 | 765 | 10 | 7650 | 0 | Individual | 4.101% | 0% |  |  | 4.101% | 0% | TRUE |  |  | 4.101% | 0%
KEARNY_6_NESBT1 | Battery Storage | 2023 | nonsummer | 2022-03-10 | 100 | 0 | 1060 | 10 | 10600 | 0 | Individual | 0.9434% | 0% |  |  | 0.9434% | 0% | TRUE |  |  | 0.9434% | 0%
KEARNY_6_NESBT1 | Battery Storage | 2023 | summer | 2022-03-10 | 792.9 | 0 | 765 | 10 | 7650 | 0 | Individual | 10.36% | 0% |  |  | 10.36% | 0% | TRUE |  |  | 10.36% | 0%
KEARNY_6_NESBT1 | Battery Storage | 2024 | nonsummer | 2022-03-10 | 191.3333 | 0 | 1065 | 10 | 10650 | 0 | Individual | 1.797% | 0% |  |  | 1.797% | 0% | TRUE |  |  | 1.797% | 0%
KEARNY_6_NESBT1 | Battery Storage | 2024 | summer | 2022-03-10 | 0 | 0 | 765 | 10 | 7650 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
KEARNY_6_SESBT2 | Battery Storage | 2022 | nonsummer | 2022-03-10 | 365 | 0 | 720 | 10 | 7200 | 340 | Blended | 5.069% | 0% | 15.33% | 0% | 8.361% | 0% | TRUE | 15.33% | 0% | 8.361% | 0%
KEARNY_6_SESBT2 | Battery Storage | 2022 | summer | 2022-03-10 | 562.75 | 0 | 765 | 10 | 7650 | 0 | Individual | 7.356% | 0% |  |  | 7.356% | 0% | TRUE |  |  | 7.356% | 0%
KEARNY_6_SESBT2 | Battery Storage | 2023 | nonsummer | 2022-03-10 | 65 | 0 | 1060 | 10 | 10600 | 0 | Individual | 0.6132% | 0% |  |  | 0.6132% | 0% | TRUE |  |  | 0.6132% | 0%
KEARNY_6_SESBT2 | Battery Storage | 2023 | summer | 2022-03-10 | 2.5 | 0 | 765 | 10 | 7650 | 0 | Individual | 0.03268% | 0% |  |  | 0.03268% | 0% | TRUE |  |  | 0.03268% | 0%
KEARNY_6_SESBT2 | Battery Storage | 2024 | nonsummer | 2022-03-10 | 786.6667 | 0 | 1065 | 10 | 10650 | 0 | Individual | 7.387% | 0% |  |  | 7.387% | 0% | TRUE |  |  | 7.387% | 0%
KEARNY_6_SESBT2 | Battery Storage | 2024 | summer | 2022-03-10 | 2153.9 | 0 | 765 | 10 | 7650 | 0 | Individual | 28.16% | 0% |  |  | 28.16% | 0% | TRUE |  |  | 28.16% | 0%
KOLA_2_KLBBT1 | Battery Storage | 2022 | nonsummer | 2025-08-01 | 0 | 0 | 0 | 275 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
KOLA_2_KLBBT1 | Battery Storage | 2022 | summer | 2025-08-01 | 0 | 0 | 0 | 275 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
KOLA_2_KLBBT1 | Battery Storage | 2023 | nonsummer | 2025-08-01 | 0 | 0 | 0 | 275 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
KOLA_2_KLBBT1 | Battery Storage | 2023 | summer | 2025-08-01 | 0 | 0 | 0 | 275 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
KOLA_2_KLBBT1 | Battery Storage | 2024 | nonsummer | 2025-08-01 | 0 | 0 | 0 | 275 | 0 | 1065 | Group |  |  | 6.223% | 0% | 6.223% | 0% | TRUE | 6.223% | 0% | 6.223% | 0%
KOLA_2_KLBBT1 | Battery Storage | 2024 | summer | 2025-08-01 | 0 | 0 | 0 | 275 | 0 | 765 | Group |  |  | 8.576% | 0% | 8.576% | 0% | TRUE | 8.576% | 0% | 8.576% | 0%
KOLA_2_KLBBT2 | Battery Storage | 2022 | nonsummer | 2025-08-01 | 0 | 0 | 0 | 125 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
KOLA_2_KLBBT2 | Battery Storage | 2022 | summer | 2025-08-01 | 0 | 0 | 0 | 125 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
KOLA_2_KLBBT2 | Battery Storage | 2023 | nonsummer | 2025-08-01 | 0 | 0 | 0 | 125 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
KOLA_2_KLBBT2 | Battery Storage | 2023 | summer | 2025-08-01 | 0 | 0 | 0 | 125 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
KOLA_2_KLBBT2 | Battery Storage | 2024 | nonsummer | 2025-08-01 | 0 | 0 | 0 | 125 | 0 | 1065 | Group |  |  | 6.223% | 0% | 6.223% | 0% | TRUE | 6.223% | 0% | 6.223% | 0%
KOLA_2_KLBBT2 | Battery Storage | 2024 | summer | 2025-08-01 | 0 | 0 | 0 | 125 | 0 | 765 | Group |  |  | 8.576% | 0% | 8.576% | 0% | TRUE | 8.576% | 0% | 8.576% | 0%
KYCORA_6_KMSBT1 | Battery Storage | 2022 | nonsummer | 2020-02-13 | 486.4083 | 0 | 1060 | 1 | 1060 | 0 | Individual | 45.89% | 0% |  |  | 45.89% | 0% | TRUE |  |  | 45.89% | 0%
KYCORA_6_KMSBT1 | Battery Storage | 2022 | summer | 2020-02-13 | 386.975 | 0 | 765 | 1 | 765 | 0 | Individual | 50.58% | 0% |  |  | 50.58% | 0% | TRUE |  |  | 50.58% | 0%
KYCORA_6_KMSBT1 | Battery Storage | 2023 | nonsummer | 2020-02-13 | 111.5583 | 0 | 1060 | 1 | 1060 | 0 | Individual | 10.52% | 0% |  |  | 10.52% | 0% | TRUE |  |  | 10.52% | 0%
KYCORA_6_KMSBT1 | Battery Storage | 2023 | summer | 2020-02-13 | 85.1083 | 0 | 765 | 1 | 765 | 0 | Individual | 11.13% | 0% |  |  | 11.13% | 0% | TRUE |  |  | 11.13% | 0%
KYCORA_6_KMSBT1 | Battery Storage | 2024 | nonsummer | 2020-02-13 | 18.4167 | 0 | 1065 | 1 | 1065 | 0 | Individual | 1.729% | 0% |  |  | 1.729% | 0% | TRUE |  |  | 1.729% | 0%
KYCORA_6_KMSBT1 | Battery Storage | 2024 | summer | 2020-02-13 | 74.5667 | 0 | 765 | 1 | 765 | 0 | Individual | 9.747% | 0% |  |  | 9.747% | 0% | TRUE |  |  | 9.747% | 0%
LAGBEL_2_CBPBT1 | Battery Storage | 2022 | nonsummer | 2024-07-02 | 0 | 0 | 0 | 100 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
LAGBEL_2_CBPBT1 | Battery Storage | 2022 | summer | 2024-07-02 | 0 | 0 | 0 | 100 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
LAGBEL_2_CBPBT1 | Battery Storage | 2023 | nonsummer | 2024-07-02 | 0 | 0 | 0 | 100 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
LAGBEL_2_CBPBT1 | Battery Storage | 2023 | summer | 2024-07-02 | 0 | 0 | 0 | 100 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
LAGBEL_2_CBPBT1 | Battery Storage | 2024 | nonsummer | 2024-07-02 | 1211.6333 | 0 | 305 | 100 | 30500 | 760 | Blended | 3.973% | 0% | 6.223% | 0% | 5.579% | 0% | TRUE | 6.223% | 0% | 5.579% | 0%
LAGBEL_2_CBPBT1 | Battery Storage | 2024 | summer | 2024-07-02 | 1633.3333 | 0 | 610 | 100 | 61000 | 155 | Blended | 2.678% | 0% | 8.576% | 0% | 3.873% | 0% | TRUE | 8.576% | 0% | 3.873% | 0%
LCKHT1_2_LH1BT1 | Battery Storage | 2022 | nonsummer | 2024-07-08 | 0 | 0 | 0 | 45 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
LCKHT1_2_LH1BT1 | Battery Storage | 2022 | summer | 2024-07-08 | 0 | 0 | 0 | 45 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
LCKHT1_2_LH1BT1 | Battery Storage | 2023 | nonsummer | 2024-07-08 | 0 | 0 | 0 | 45 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
LCKHT1_2_LH1BT1 | Battery Storage | 2023 | summer | 2024-07-08 | 0 | 0 | 0 | 45 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
LCKHT1_2_LH1BT1 | Battery Storage | 2024 | nonsummer | 2024-07-08 | 0 | 0 | 305 | 45 | 13725 | 760 | Blended | 0% | 0% | 6.223% | 0% | 4.441% | 0% | TRUE | 6.223% | 0% | 4.441% | 0%
LCKHT1_2_LH1BT1 | Battery Storage | 2024 | summer | 2024-07-08 | 256 | 0 | 580 | 45 | 26100 | 185 | Blended | 0.9808% | 0% | 8.576% | 0% | 2.818% | 0% | TRUE | 8.576% | 0% | 2.818% | 0%
LECONT_2_LESBT1 | Battery Storage | 2022 | nonsummer | 2022-09-01 | 602.0833 | 0 | 305 | 125 | 38125 | 755 | Blended | 1.579% | 0% | 15.33% | 0% | 11.37% | 0% | TRUE | 15.33% | 0% | 11.37% | 0%
LECONT_2_LESBT1 | Battery Storage | 2022 | summer | 2022-09-01 | 9993.0667 | 0 | 305 | 125 | 38125 | 460 | Blended | 26.21% | 0% | 13.83% | 0% | 18.77% | 0% | TRUE | 13.83% | 0% | 18.77% | 0%
LECONT_2_LESBT1 | Battery Storage | 2023 | nonsummer | 2022-09-01 | 2987.2167 | 0 | 1060 | 125 | 132500 | 0 | Individual | 2.255% | 0% |  |  | 2.255% | 0% | TRUE |  |  | 2.255% | 0%
LECONT_2_LESBT1 | Battery Storage | 2023 | summer | 2022-09-01 | 3389.0333 | 0 | 765 | 125 | 95625 | 0 | Individual | 3.544% | 0% |  |  | 3.544% | 0% | TRUE |  |  | 3.544% | 0%
LECONT_2_LESBT1 | Battery Storage | 2024 | nonsummer | 2022-09-01 | 2291.3 | 0 | 1065 | 125 | 133125 | 0 | Individual | 1.721% | 0% |  |  | 1.721% | 0% | TRUE |  |  | 1.721% | 0%
LECONT_2_LESBT1 | Battery Storage | 2024 | summer | 2022-09-01 | 506.2667 | 0 | 765 | 125 | 95625 | 0 | Individual | 0.5294% | 0% |  |  | 0.5294% | 0% | TRUE |  |  | 0.5294% | 0%
MARVEL_2_MARBT3 | Battery Storage | 2022 | nonsummer | 2024-04-25 | 0 | 0 | 0 | 74.94 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
MARVEL_2_MARBT3 | Battery Storage | 2022 | summer | 2024-04-25 | 0 | 0 | 0 | 74.94 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
MARVEL_2_MARBT3 | Battery Storage | 2023 | nonsummer | 2024-04-25 | 0 | 0 | 0 | 74.94 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
MARVEL_2_MARBT3 | Battery Storage | 2023 | summer | 2024-04-25 | 0 | 0 | 0 | 74.94 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
MARVEL_2_MARBT3 | Battery Storage | 2024 | nonsummer | 2024-04-25 | 962.7858 | 0 | 490 | 74.94 | 36720.6 | 575 | Blended | 2.622% | 0% | 6.223% | 0% | 4.566% | 0% | TRUE | 6.223% | 0% | 4.566% | 0%
MARVEL_2_MARBT3 | Battery Storage | 2024 | summer | 2024-04-25 | 1747.85 | 0 | 765 | 74.94 | 57329.1 | 0 | Individual | 3.049% | 0% |  |  | 3.049% | 0% | TRUE |  |  | 3.049% | 0%
MARVEL_2_MARBX2 | Battery Storage | 2022 | nonsummer | 2024-04-25 | 0 | 0 | 0 | 325 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
MARVEL_2_MARBX2 | Battery Storage | 2022 | summer | 2024-04-25 | 0 | 0 | 0 | 325 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
MARVEL_2_MARBX2 | Battery Storage | 2023 | nonsummer | 2024-04-25 | 0 | 0 | 0 | 325 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
MARVEL_2_MARBX2 | Battery Storage | 2023 | summer | 2024-04-25 | 0 | 0 | 0 | 325 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
MARVEL_2_MARBX2 | Battery Storage | 2024 | nonsummer | 2024-04-25 | 2103.0787 | 0 | 490 | 325 | 159250 | 575 | Blended | 1.321% | 0% | 6.223% | 0% | 3.968% | 0% | TRUE | 6.223% | 0% | 3.968% | 0%
MARVEL_2_MARBX2 | Battery Storage | 2024 | summer | 2024-04-25 | 6473.4198 | 0 | 765 | 325 | 248625 | 0 | Individual | 2.604% | 0% |  |  | 2.604% | 0% | TRUE |  |  | 2.604% | 0%
MELRSE_6_MELBT1 | Battery Storage | 2022 | nonsummer | 2024-03-15 | 0 | 0 | 0 | 10 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
MELRSE_6_MELBT1 | Battery Storage | 2022 | summer | 2024-03-15 | 0 | 0 | 0 | 10 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
MELRSE_6_MELBT1 | Battery Storage | 2023 | nonsummer | 2024-03-15 | 0 | 0 | 0 | 10 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
MELRSE_6_MELBT1 | Battery Storage | 2023 | summer | 2024-03-15 | 0 | 0 | 0 | 10 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
MELRSE_6_MELBT1 | Battery Storage | 2024 | nonsummer | 2024-03-15 | 20 | 0 | 695 | 10 | 6950 | 370 | Blended | 0.2878% | 0% | 6.223% | 0% | 2.35% | 0% | TRUE | 6.223% | 0% | 2.35% | 0%
MELRSE_6_MELBT1 | Battery Storage | 2024 | summer | 2024-03-15 | 1550 | 0 | 765 | 10 | 7650 | 0 | Individual | 20.26% | 0% |  |  | 20.26% | 0% | TRUE |  |  | 20.26% | 0%
MELRSE_6_MELBT2 | Battery Storage | 2022 | nonsummer | 2024-03-15 | 0 | 0 | 0 | 10 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
MELRSE_6_MELBT2 | Battery Storage | 2022 | summer | 2024-03-15 | 0 | 0 | 0 | 10 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
MELRSE_6_MELBT2 | Battery Storage | 2023 | nonsummer | 2024-03-15 | 0 | 0 | 0 | 10 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
MELRSE_6_MELBT2 | Battery Storage | 2023 | summer | 2024-03-15 | 0 | 0 | 0 | 10 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
MELRSE_6_MELBT2 | Battery Storage | 2024 | nonsummer | 2024-03-15 | 350 | 0 | 695 | 10 | 6950 | 370 | Blended | 5.036% | 0% | 6.223% | 0% | 5.448% | 0% | TRUE | 6.223% | 0% | 5.448% | 0%
MELRSE_6_MELBT2 | Battery Storage | 2024 | summer | 2024-03-15 | 1490 | 0 | 765 | 10 | 7650 | 0 | Individual | 19.48% | 0% |  |  | 19.48% | 0% | TRUE |  |  | 19.48% | 0%
MIRLOM_2_MLBBTA | Battery Storage | 2022 | nonsummer | 2016-12-30 | 75.8333 | 0 | 1060 | 10 | 10600 | 0 | Individual | 0.7154% | 0% |  |  | 0.7154% | 0% | TRUE |  |  | 0.7154% | 0%
MIRLOM_2_MLBBTA | Battery Storage | 2022 | summer | 2016-12-30 | 100 | 0 | 765 | 10 | 7650 | 0 | Individual | 1.307% | 0% |  |  | 1.307% | 0% | TRUE |  |  | 1.307% | 0%
MIRLOM_2_MLBBTA | Battery Storage | 2023 | nonsummer | 2016-12-30 | 47.8333 | 0 | 1060 | 10 | 10600 | 0 | Individual | 0.4513% | 0% |  |  | 0.4513% | 0% | TRUE |  |  | 0.4513% | 0%
MIRLOM_2_MLBBTA | Battery Storage | 2023 | summer | 2016-12-30 | 49.3333 | 0 | 765 | 10 | 7650 | 0 | Individual | 0.6449% | 0% |  |  | 0.6449% | 0% | TRUE |  |  | 0.6449% | 0%
MIRLOM_2_MLBBTA | Battery Storage | 2024 | nonsummer | 2016-12-30 | 0 | 0 | 1065 | 10 | 10650 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
MIRLOM_2_MLBBTA | Battery Storage | 2024 | summer | 2016-12-30 | 20 | 0 | 765 | 10 | 7650 | 0 | Individual | 0.2614% | 0% |  |  | 0.2614% | 0% | TRUE |  |  | 0.2614% | 0%
MIRLOM_2_MLBBTB | Battery Storage | 2022 | nonsummer | 2016-12-30 | 322 | 0 | 1060 | 10 | 10600 | 0 | Individual | 3.038% | 0% |  |  | 3.038% | 0% | TRUE |  |  | 3.038% | 0%
MIRLOM_2_MLBBTB | Battery Storage | 2022 | summer | 2016-12-30 | 433.9267 | 0 | 765 | 10 | 7650 | 0 | Individual | 5.672% | 0% |  |  | 5.672% | 0% | TRUE |  |  | 5.672% | 0%
MIRLOM_2_MLBBTB | Battery Storage | 2023 | nonsummer | 2016-12-30 | 283.9667 | 0 | 1060 | 10 | 10600 | 0 | Individual | 2.679% | 0% |  |  | 2.679% | 0% | TRUE |  |  | 2.679% | 0%
MIRLOM_2_MLBBTB | Battery Storage | 2023 | summer | 2016-12-30 | 424.1667 | 0 | 765 | 10 | 7650 | 0 | Individual | 5.545% | 0% |  |  | 5.545% | 0% | TRUE |  |  | 5.545% | 0%
MIRLOM_2_MLBBTB | Battery Storage | 2024 | nonsummer | 2016-12-30 | 50 | 0 | 1065 | 10 | 10650 | 0 | Individual | 0.4695% | 0% |  |  | 0.4695% | 0% | TRUE |  |  | 0.4695% | 0%
MIRLOM_2_MLBBTB | Battery Storage | 2024 | summer | 2016-12-30 | 49.6667 | 0 | 765 | 10 | 7650 | 0 | Individual | 0.6492% | 0% |  |  | 0.6492% | 0% | TRUE |  |  | 0.6492% | 0%
MOORPK_2_ACOBT1 | Battery Storage | 2022 | nonsummer | 2021-03-31 | 181.7892 | 0 | 1060 | 1.95 | 2067 | 0 | Individual | 8.795% | 0% |  |  | 8.795% | 0% | TRUE |  |  | 8.795% | 0%
MOORPK_2_ACOBT1 | Battery Storage | 2022 | summer | 2021-03-31 | 118.8225 | 0 | 765 | 1.95 | 1491.75 | 0 | Individual | 7.965% | 0% |  |  | 7.965% | 0% | TRUE |  |  | 7.965% | 0%
MOORPK_2_ACOBT1 | Battery Storage | 2023 | nonsummer | 2021-03-31 | 34.84 | 0 | 1060 | 1.95 | 2067 | 0 | Individual | 1.686% | 0% |  |  | 1.686% | 0% | TRUE |  |  | 1.686% | 0%
MOORPK_2_ACOBT1 | Battery Storage | 2023 | summer | 2021-03-31 | 75.5517 | 0 | 765 | 1.95 | 1491.75 | 0 | Individual | 5.065% | 0% |  |  | 5.065% | 0% | TRUE |  |  | 5.065% | 0%
MOORPK_2_ACOBT1 | Battery Storage | 2024 | nonsummer | 2021-03-31 | 130.4875 | 0 | 1065 | 1.95 | 2076.75 | 0 | Individual | 6.283% | 0% |  |  | 6.283% | 0% | TRUE |  |  | 6.283% | 0%
MOORPK_2_ACOBT1 | Battery Storage | 2024 | summer | 2021-03-31 | 38.4317 | 0 | 765 | 1.95 | 1491.75 | 0 | Individual | 2.576% | 0% |  |  | 2.576% | 0% | TRUE |  |  | 2.576% | 0%
MRGT_6_TGEBT1 | Battery Storage | 2022 | nonsummer | 2021-06-30 | 8700.7083 | 0 | 1060 | 30 | 31800 | 0 | Individual | 27.36% | 0% |  |  | 27.36% | 0% | TRUE |  |  | 27.36% | 0%
MRGT_6_TGEBT1 | Battery Storage | 2022 | summer | 2021-06-30 | 7445.5 | 0 | 765 | 30 | 22950 | 0 | Individual | 32.44% | 0% |  |  | 32.44% | 0% | TRUE |  |  | 32.44% | 0%
MRGT_6_TGEBT1 | Battery Storage | 2023 | nonsummer | 2021-06-30 | 3262.9917 | 0 | 1060 | 30 | 31800 | 0 | Individual | 10.26% | 0% |  |  | 10.26% | 0% | TRUE |  |  | 10.26% | 0%
MRGT_6_TGEBT1 | Battery Storage | 2023 | summer | 2021-06-30 | 3793.5567 | 0 | 765 | 30 | 22950 | 0 | Individual | 16.53% | 0% |  |  | 16.53% | 0% | TRUE |  |  | 16.53% | 0%
MRGT_6_TGEBT1 | Battery Storage | 2024 | nonsummer | 2021-06-30 | 493 | 0 | 1065 | 30 | 31950 | 0 | Individual | 1.543% | 0% |  |  | 1.543% | 0% | TRUE |  |  | 1.543% | 0%
MRGT_6_TGEBT1 | Battery Storage | 2024 | summer | 2021-06-30 | 1953.0667 | 0 | 765 | 30 | 22950 | 0 | Individual | 8.51% | 0% |  |  | 8.51% | 0% | TRUE |  |  | 8.51% | 0%
MSOLAR_2_MS4BT1 | Battery Storage | 2022 | nonsummer | 2024-01-26 | 0 | 0 | 0 | 10 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
MSOLAR_2_MS4BT1 | Battery Storage | 2022 | summer | 2024-01-26 | 0 | 0 | 0 | 10 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
MSOLAR_2_MS4BT1 | Battery Storage | 2023 | nonsummer | 2024-01-26 | 0 | 0 | 0 | 10 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
MSOLAR_2_MS4BT1 | Battery Storage | 2023 | summer | 2024-01-26 | 0 | 0 | 0 | 10 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
MSOLAR_2_MS4BT1 | Battery Storage | 2024 | nonsummer | 2024-01-26 | 2289.7 | 0 | 940 | 10 | 9400 | 125 | Blended | 24.36% | 0% | 6.223% | 0% | 22.23% | 0% | TRUE | 6.223% | 0% | 22.23% | 0%
MSOLAR_2_MS4BT1 | Battery Storage | 2024 | summer | 2024-01-26 | 1400 | 0 | 765 | 10 | 7650 | 0 | Individual | 18.3% | 0% |  |  | 18.3% | 0% | TRUE |  |  | 18.3% | 0%
NOAKS_2_PESBT1 | Battery Storage | 2022 | nonsummer | 2024-11-14 | 0 | 0 | 0 | 80 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
NOAKS_2_PESBT1 | Battery Storage | 2022 | summer | 2024-11-14 | 0 | 0 | 0 | 80 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
NOAKS_2_PESBT1 | Battery Storage | 2023 | nonsummer | 2024-11-14 | 0 | 0 | 0 | 80 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
NOAKS_2_PESBT1 | Battery Storage | 2023 | summer | 2024-11-14 | 0 | 0 | 0 | 80 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
NOAKS_2_PESBT1 | Battery Storage | 2024 | nonsummer | 2024-11-14 | 20 | 0 | 240 | 80 | 19200 | 825 | Blended | 0.1042% | 0% | 6.223% | 0% | 4.844% | 0% | TRUE | 6.223% | 0% | 4.844% | 0%
NOAKS_2_PESBT1 | Battery Storage | 2024 | summer | 2024-11-14 | 0 | 0 | 0 | 80 | 0 | 765 | Group |  |  | 8.576% | 0% | 8.576% | 0% | TRUE | 8.576% | 0% | 8.576% | 0%
NORCNV_1_NCVBT1 | Battery Storage | 2022 | nonsummer | 2023-08-30 | 0 | 0 | 0 | 132 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
NORCNV_1_NCVBT1 | Battery Storage | 2022 | summer | 2023-08-30 | 0 | 0 | 0 | 132 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
NORCNV_1_NCVBT1 | Battery Storage | 2023 | nonsummer | 2023-08-30 | 17.9 | 0 | 305 | 132 | 40260 | 755 | Blended | 0.04446% | 0% | 6.742% | 0% | 4.815% | 0% | TRUE | 6.742% | 0% | 4.815% | 0%
NORCNV_1_NCVBT1 | Battery Storage | 2023 | summer | 2023-08-30 | 2382.6 | 0 | 315 | 132 | 41580 | 450 | Blended | 5.73% | 0% | 6.657% | 0% | 6.275% | 0% | TRUE | 6.657% | 0% | 6.275% | 0%
NORCNV_1_NCVBT1 | Battery Storage | 2024 | nonsummer | 2023-08-30 | 7131.9917 | 0 | 1065 | 132 | 140580 | 0 | Individual | 5.073% | 0% |  |  | 5.073% | 0% | TRUE |  |  | 5.073% | 0%
NORCNV_1_NCVBT1 | Battery Storage | 2024 | summer | 2023-08-30 | 396.3248 | 0 | 765 | 132 | 100980 | 0 | Individual | 0.3925% | 0% |  |  | 0.3925% | 0% | TRUE |  |  | 0.3925% | 0%
PALA_6_PGCBT1 | Battery Storage | 2022 | nonsummer | 2024-03-14 | 0 | 0 | 0 | 10 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
PALA_6_PGCBT1 | Battery Storage | 2022 | summer | 2024-03-14 | 0 | 0 | 0 | 10 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
PALA_6_PGCBT1 | Battery Storage | 2023 | nonsummer | 2024-03-14 | 0 | 0 | 0 | 10 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
PALA_6_PGCBT1 | Battery Storage | 2023 | summer | 2024-03-14 | 0 | 0 | 0 | 10 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
PALA_6_PGCBT1 | Battery Storage | 2024 | nonsummer | 2024-03-14 | 758.8 | 0 | 700 | 10 | 7000 | 365 | Blended | 10.84% | 0% | 6.223% | 0% | 9.258% | 0% | TRUE | 6.223% | 0% | 9.258% | 0%
PALA_6_PGCBT1 | Battery Storage | 2024 | summer | 2024-03-14 | 1505.3 | 0 | 765 | 10 | 7650 | 0 | Individual | 19.68% | 0% |  |  | 19.68% | 0% | TRUE |  |  | 19.68% | 0%
PARDSE_6_PESBT1 | Battery Storage | 2022 | nonsummer | 2024-05-21 | 0 | 0 | 0 | 10 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
PARDSE_6_PESBT1 | Battery Storage | 2022 | summer | 2024-05-21 | 0 | 0 | 0 | 10 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
PARDSE_6_PESBT1 | Battery Storage | 2023 | nonsummer | 2024-05-21 | 0 | 0 | 0 | 10 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
PARDSE_6_PESBT1 | Battery Storage | 2023 | summer | 2024-05-21 | 0 | 0 | 0 | 10 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
PARDSE_6_PESBT1 | Battery Storage | 2024 | nonsummer | 2024-05-21 | 40.8583 | 0 | 360 | 10 | 3600 | 705 | Blended | 1.135% | 0% | 6.223% | 0% | 4.503% | 0% | TRUE | 6.223% | 0% | 4.503% | 0%
PARDSE_6_PESBT1 | Battery Storage | 2024 | summer | 2024-05-21 | 556.35 | 0 | 765 | 10 | 7650 | 0 | Individual | 7.273% | 0% |  |  | 7.273% | 0% | TRUE |  |  | 7.273% | 0%
PEASE_1_TBEBT1 | Battery Storage | 2022 | nonsummer | 2022-06-01 | 0 | 0 | 305 | 5 | 1525 | 755 | Blended | 0% | 0% | 15.33% | 0% | 10.92% | 0% | TRUE | 15.33% | 0% | 10.92% | 0%
PEASE_1_TBEBT1 | Battery Storage | 2022 | summer | 2022-06-01 | 565.7 | 0 | 765 | 5 | 3825 | 0 | Individual | 14.79% | 0% |  |  | 14.79% | 0% | TRUE |  |  | 14.79% | 0%
PEASE_1_TBEBT1 | Battery Storage | 2023 | nonsummer | 2022-06-01 | 633.2 | 0 | 1060 | 5 | 5300 | 0 | Individual | 11.95% | 0% |  |  | 11.95% | 0% | TRUE |  |  | 11.95% | 0%
PEASE_1_TBEBT1 | Battery Storage | 2023 | summer | 2022-06-01 | 949.5 | 0 | 765 | 5 | 3825 | 0 | Individual | 24.82% | 0% |  |  | 24.82% | 0% | TRUE |  |  | 24.82% | 0%
PEASE_1_TBEBT1 | Battery Storage | 2024 | nonsummer | 2022-06-01 | 148.3 | 0 | 1065 | 5 | 5325 | 0 | Individual | 2.785% | 0% |  |  | 2.785% | 0% | TRUE |  |  | 2.785% | 0%
PEASE_1_TBEBT1 | Battery Storage | 2024 | summer | 2022-06-01 | 284.3 | 0 | 765 | 5 | 3825 | 0 | Individual | 7.433% | 0% |  |  | 7.433% | 0% | TRUE |  |  | 7.433% | 0%
PERGRN_2_PRSBT1 | Battery Storage | 2022 | nonsummer | 2025-04-09 | 0 | 0 | 0 | 200 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
PERGRN_2_PRSBT1 | Battery Storage | 2022 | summer | 2025-04-09 | 0 | 0 | 0 | 200 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
PERGRN_2_PRSBT1 | Battery Storage | 2023 | nonsummer | 2025-04-09 | 0 | 0 | 0 | 200 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
PERGRN_2_PRSBT1 | Battery Storage | 2023 | summer | 2025-04-09 | 0 | 0 | 0 | 200 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
PERGRN_2_PRSBT1 | Battery Storage | 2024 | nonsummer | 2025-04-09 | 0 | 0 | 0 | 200 | 0 | 1065 | Group |  |  | 6.223% | 0% | 6.223% | 0% | TRUE | 6.223% | 0% | 6.223% | 0%
PERGRN_2_PRSBT1 | Battery Storage | 2024 | summer | 2025-04-09 | 0 | 0 | 0 | 200 | 0 | 765 | Group |  |  | 8.576% | 0% | 8.576% | 0% | TRUE | 8.576% | 0% | 8.576% | 0%
RATSKE_2_WAVBT1 | Battery Storage | 2022 | nonsummer | 2025-04-16 | 0 | 0 | 0 | 125.96 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
RATSKE_2_WAVBT1 | Battery Storage | 2022 | summer | 2025-04-16 | 0 | 0 | 0 | 125.96 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
RATSKE_2_WAVBT1 | Battery Storage | 2023 | nonsummer | 2025-04-16 | 0 | 0 | 0 | 125.96 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
RATSKE_2_WAVBT1 | Battery Storage | 2023 | summer | 2025-04-16 | 0 | 0 | 0 | 125.96 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
RATSKE_2_WAVBT1 | Battery Storage | 2024 | nonsummer | 2025-04-16 | 0 | 0 | 0 | 125.96 | 0 | 1065 | Group |  |  | 6.223% | 0% | 6.223% | 0% | TRUE | 6.223% | 0% | 6.223% | 0%
RATSKE_2_WAVBT1 | Battery Storage | 2024 | summer | 2025-04-16 | 0 | 0 | 0 | 125.96 | 0 | 765 | Group |  |  | 8.576% | 0% | 8.576% | 0% | TRUE | 8.576% | 0% | 8.576% | 0%
ROMOLA_5_MPBBT1 | Battery Storage | 2022 | nonsummer | 2024-09-20 | 0 | 0 | 0 | 230 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
ROMOLA_5_MPBBT1 | Battery Storage | 2022 | summer | 2024-09-20 | 0 | 0 | 0 | 230 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
ROMOLA_5_MPBBT1 | Battery Storage | 2023 | nonsummer | 2024-09-20 | 0 | 0 | 0 | 230 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
ROMOLA_5_MPBBT1 | Battery Storage | 2023 | summer | 2024-09-20 | 0 | 0 | 0 | 230 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
ROMOLA_5_MPBBT1 | Battery Storage | 2024 | nonsummer | 2024-09-20 | 74.1667 | 0 | 305 | 230 | 70150 | 760 | Blended | 0.1057% | 0% | 6.223% | 0% | 4.471% | 0% | TRUE | 6.223% | 0% | 4.471% | 0%
ROMOLA_5_MPBBT1 | Battery Storage | 2024 | summer | 2024-09-20 | 128 | 0 | 210 | 230 | 48300 | 555 | Blended | 0.265% | 0% | 8.576% | 0% | 6.294% | 0% | TRUE | 8.576% | 0% | 6.294% | 0%
ROMOLA_5_MPBBT2 | Battery Storage | 2022 | nonsummer | 2024-09-20 | 0 | 0 | 0 | 230 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
ROMOLA_5_MPBBT2 | Battery Storage | 2022 | summer | 2024-09-20 | 0 | 0 | 0 | 230 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
ROMOLA_5_MPBBT2 | Battery Storage | 2023 | nonsummer | 2024-09-20 | 0 | 0 | 0 | 230 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
ROMOLA_5_MPBBT2 | Battery Storage | 2023 | summer | 2024-09-20 | 0 | 0 | 0 | 230 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
ROMOLA_5_MPBBT2 | Battery Storage | 2024 | nonsummer | 2024-09-20 | 0 | 0 | 305 | 230 | 70150 | 760 | Blended | 0% | 0% | 6.223% | 0% | 4.441% | 0% | TRUE | 6.223% | 0% | 4.441% | 0%
ROMOLA_5_MPBBT2 | Battery Storage | 2024 | summer | 2024-09-20 | 301.2 | 0 | 210 | 230 | 48300 | 555 | Blended | 0.6236% | 0% | 8.576% | 0% | 6.393% | 0% | TRUE | 8.576% | 0% | 6.393% | 0%
ROMOLA_5_MPBBT3 | Battery Storage | 2022 | nonsummer | 2024-09-20 | 0 | 0 | 0 | 50 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
ROMOLA_5_MPBBT3 | Battery Storage | 2022 | summer | 2024-09-20 | 0 | 0 | 0 | 50 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
ROMOLA_5_MPBBT3 | Battery Storage | 2023 | nonsummer | 2024-09-20 | 0 | 0 | 0 | 50 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
ROMOLA_5_MPBBT3 | Battery Storage | 2023 | summer | 2024-09-20 | 0 | 0 | 0 | 50 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
ROMOLA_5_MPBBT3 | Battery Storage | 2024 | nonsummer | 2024-09-20 | 149.25 | 0 | 305 | 50 | 15250 | 760 | Blended | 0.9787% | 0% | 6.223% | 0% | 4.721% | 0% | TRUE | 6.223% | 0% | 4.721% | 0%
ROMOLA_5_MPBBT3 | Battery Storage | 2024 | summer | 2024-09-20 | 175.1667 | 0 | 210 | 50 | 10500 | 555 | Blended | 1.668% | 0% | 8.576% | 0% | 6.68% | 0% | TRUE | 8.576% | 0% | 6.68% | 0%
ROMOLA_5_MPBBT4 | Battery Storage | 2022 | nonsummer | 2024-09-20 | 0 | 0 | 0 | 110 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
ROMOLA_5_MPBBT4 | Battery Storage | 2022 | summer | 2024-09-20 | 0 | 0 | 0 | 110 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
ROMOLA_5_MPBBT4 | Battery Storage | 2023 | nonsummer | 2024-09-20 | 0 | 0 | 0 | 110 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
ROMOLA_5_MPBBT4 | Battery Storage | 2023 | summer | 2024-09-20 | 0 | 0 | 0 | 110 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
ROMOLA_5_MPBBT4 | Battery Storage | 2024 | nonsummer | 2024-09-20 | 337.75 | 0 | 305 | 110 | 33550 | 760 | Blended | 1.007% | 0% | 6.223% | 0% | 4.729% | 0% | TRUE | 6.223% | 0% | 4.729% | 0%
ROMOLA_5_MPBBT4 | Battery Storage | 2024 | summer | 2024-09-20 | 1427.7333 | 0 | 210 | 110 | 23100 | 555 | Blended | 6.181% | 0% | 8.576% | 0% | 7.918% | 0% | TRUE | 8.576% | 0% | 7.918% | 0%
SANBRN_2_ESABT1 | Battery Storage | 2022 | nonsummer | 2021-11-19 | 0 | 0 | 1060 | 100 | 106000 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SANBRN_2_ESABT1 | Battery Storage | 2022 | summer | 2021-11-19 | 1325.8333 | 0 | 765 | 100 | 76500 | 0 | Individual | 1.733% | 0% |  |  | 1.733% | 0% | TRUE |  |  | 1.733% | 0%
SANBRN_2_ESABT1 | Battery Storage | 2023 | nonsummer | 2021-11-19 | 1050 | 0 | 1060 | 100 | 106000 | 0 | Individual | 0.9906% | 0% |  |  | 0.9906% | 0% | TRUE |  |  | 0.9906% | 0%
SANBRN_2_ESABT1 | Battery Storage | 2023 | summer | 2021-11-19 | 125 | 0 | 765 | 100 | 76500 | 0 | Individual | 0.1634% | 0% |  |  | 0.1634% | 0% | TRUE |  |  | 0.1634% | 0%
SANBRN_2_ESABT1 | Battery Storage | 2024 | nonsummer | 2021-11-19 | 26.6667 | 0 | 1065 | 100 | 106500 | 0 | Individual | 0.02504% | 0% |  |  | 0.02504% | 0% | TRUE |  |  | 0.02504% | 0%
SANBRN_2_ESABT1 | Battery Storage | 2024 | summer | 2021-11-19 | 0 | 0 | 765 | 100 | 76500 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SANBRN_2_ESBBT1 | Battery Storage | 2022 | nonsummer | 2021-11-01 | 0 | 0 | 1060 | 100 | 106000 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SANBRN_2_ESBBT1 | Battery Storage | 2022 | summer | 2021-11-01 | 361.3 | 0 | 765 | 100 | 76500 | 0 | Individual | 0.4723% | 0% |  |  | 0.4723% | 0% | TRUE |  |  | 0.4723% | 0%
SANBRN_2_ESBBT1 | Battery Storage | 2023 | nonsummer | 2021-11-01 | 425 | 0 | 1060 | 100 | 106000 | 0 | Individual | 0.4009% | 0% |  |  | 0.4009% | 0% | TRUE |  |  | 0.4009% | 0%
SANBRN_2_ESBBT1 | Battery Storage | 2023 | summer | 2021-11-01 | 175 | 0 | 765 | 100 | 76500 | 0 | Individual | 0.2288% | 0% |  |  | 0.2288% | 0% | TRUE |  |  | 0.2288% | 0%
SANBRN_2_ESBBT1 | Battery Storage | 2024 | nonsummer | 2021-11-01 | 1765.3333 | 0 | 1065 | 100 | 106500 | 0 | Individual | 1.658% | 0% |  |  | 1.658% | 0% | TRUE |  |  | 1.658% | 0%
SANBRN_2_ESBBT1 | Battery Storage | 2024 | summer | 2021-11-01 | 118.5 | 0 | 765 | 100 | 76500 | 0 | Individual | 0.1549% | 0% |  |  | 0.1549% | 0% | TRUE |  |  | 0.1549% | 0%
SANBRN_2_SS2BT3 | Battery Storage | 2022 | nonsummer | 2023-10-11 | 0 | 0 | 0 | 169 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
SANBRN_2_SS2BT3 | Battery Storage | 2022 | summer | 2023-10-11 | 0 | 0 | 0 | 169 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
SANBRN_2_SS2BT3 | Battery Storage | 2023 | nonsummer | 2023-10-11 | 348.7 | 0 | 305 | 169 | 51545 | 755 | Blended | 0.6765% | 0% | 6.742% | 0% | 4.997% | 0% | TRUE | 6.742% | 0% | 4.997% | 0%
SANBRN_2_SS2BT3 | Battery Storage | 2023 | summer | 2023-10-11 | 2396.7833 | 0 | 105 | 169 | 17745 | 660 | Blended | 13.51% | 0% | 6.657% | 0% | 7.597% | 0% | TRUE | 6.657% | 0% | 7.597% | 0%
SANBRN_2_SS2BT3 | Battery Storage | 2024 | nonsummer | 2023-10-11 | 2900.3833 | 0 | 1065 | 169 | 179985 | 0 | Individual | 1.611% | 0% |  |  | 1.611% | 0% | TRUE |  |  | 1.611% | 0%
SANBRN_2_SS2BT3 | Battery Storage | 2024 | summer | 2023-10-11 | 5742.7833 | 0 | 765 | 169 | 129285 | 0 | Individual | 4.442% | 0% |  |  | 4.442% | 0% | TRUE |  |  | 4.442% | 0%
SANBRN_2_SS2BT4 | Battery Storage | 2022 | nonsummer | 2023-11-16 | 0 | 0 | 0 | 47 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
SANBRN_2_SS2BT4 | Battery Storage | 2022 | summer | 2023-11-16 | 0 | 0 | 0 | 47 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
SANBRN_2_SS2BT4 | Battery Storage | 2023 | nonsummer | 2023-11-16 | 0 | 0 | 230 | 47 | 10810 | 830 | Blended | 0% | 0% | 6.742% | 0% | 5.279% | 0% | TRUE | 6.742% | 0% | 5.279% | 0%
SANBRN_2_SS2BT4 | Battery Storage | 2023 | summer | 2023-11-16 | 0 | 0 | 0 | 47 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
SANBRN_2_SS2BT4 | Battery Storage | 2024 | nonsummer | 2023-11-16 | 0 | 0 | 1065 | 47 | 50055 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SANBRN_2_SS2BT4 | Battery Storage | 2024 | summer | 2023-11-16 | 90.0833 | 0 | 765 | 47 | 35955 | 0 | Individual | 0.2505% | 0% |  |  | 0.2505% | 0% | TRUE |  |  | 0.2505% | 0%
SAUGUS_2_SPESBT1 | Battery Storage | 2022 | nonsummer | 2024-03-16 | 0 | 0 | 0 | 30 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
SAUGUS_2_SPESBT1 | Battery Storage | 2022 | summer | 2024-03-16 | 0 | 0 | 0 | 30 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
SAUGUS_2_SPESBT1 | Battery Storage | 2023 | nonsummer | 2024-03-16 | 0 | 0 | 0 | 30 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
SAUGUS_2_SPESBT1 | Battery Storage | 2023 | summer | 2024-03-16 | 0 | 0 | 0 | 30 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
SAUGUS_2_SPESBT1 | Battery Storage | 2024 | nonsummer | 2024-03-16 | 3913 | 0 | 690 | 30 | 20700 | 375 | Blended | 18.9% | 0% | 6.223% | 0% | 14.44% | 0% | TRUE | 6.223% | 0% | 14.44% | 0%
SAUGUS_2_SPESBT1 | Battery Storage | 2024 | summer | 2024-03-16 | 4069.12 | 0 | 765 | 30 | 22950 | 0 | Individual | 17.73% | 0% |  |  | 17.73% | 0% | TRUE |  |  | 17.73% | 0%
SNCLRA_2_SILBT1 | Battery Storage | 2022 | nonsummer | 2021-04-01 | 5.9333 | 0 | 1060 | 11 | 11660 | 0 | Individual | 0.05089% | 0% |  |  | 0.05089% | 0% | TRUE |  |  | 0.05089% | 0%
SNCLRA_2_SILBT1 | Battery Storage | 2022 | summer | 2021-04-01 | 0 | 0 | 765 | 11 | 8415 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SNCLRA_2_SILBT1 | Battery Storage | 2023 | nonsummer | 2021-04-01 | 11.1833 | 0 | 1060 | 11 | 11660 | 0 | Individual | 0.09591% | 0% |  |  | 0.09591% | 0% | TRUE |  |  | 0.09591% | 0%
SNCLRA_2_SILBT1 | Battery Storage | 2023 | summer | 2021-04-01 | 76.8 | 0 | 765 | 11 | 8415 | 0 | Individual | 0.9127% | 0% |  |  | 0.9127% | 0% | TRUE |  |  | 0.9127% | 0%
SNCLRA_2_SILBT1 | Battery Storage | 2024 | nonsummer | 2021-04-01 | 895.9667 | 0 | 1065 | 11 | 11715 | 0 | Individual | 7.648% | 0% |  |  | 7.648% | 0% | TRUE |  |  | 7.648% | 0%
SNCLRA_2_SILBT1 | Battery Storage | 2024 | summer | 2021-04-01 | 21.4867 | 0 | 765 | 11 | 8415 | 0 | Individual | 0.2553% | 0% |  |  | 0.2553% | 0% | TRUE |  |  | 0.2553% | 0%
SNCLRA_2_VESBT1 | Battery Storage | 2022 | nonsummer | 2021-04-20 | 2916.6667 | 0 | 1060 | 100 | 106000 | 0 | Individual | 2.752% | 0% |  |  | 2.752% | 0% | TRUE |  |  | 2.752% | 0%
SNCLRA_2_VESBT1 | Battery Storage | 2022 | summer | 2021-04-20 | 1113.3333 | 0 | 765 | 100 | 76500 | 0 | Individual | 1.455% | 0% |  |  | 1.455% | 0% | TRUE |  |  | 1.455% | 0%
SNCLRA_2_VESBT1 | Battery Storage | 2023 | nonsummer | 2021-04-20 | 3750 | 0 | 1060 | 100 | 106000 | 0 | Individual | 3.538% | 0% |  |  | 3.538% | 0% | TRUE |  |  | 3.538% | 0%
SNCLRA_2_VESBT1 | Battery Storage | 2023 | summer | 2021-04-20 | 4500 | 0 | 765 | 100 | 76500 | 0 | Individual | 5.882% | 0% |  |  | 5.882% | 0% | TRUE |  |  | 5.882% | 0%
SNCLRA_2_VESBT1 | Battery Storage | 2024 | nonsummer | 2021-04-20 | 0 | 0 | 1065 | 100 | 106500 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SNCLRA_2_VESBT1 | Battery Storage | 2024 | summer | 2021-04-20 | 2800 | 0 | 765 | 100 | 76500 | 0 | Individual | 3.66% | 0% |  |  | 3.66% | 0% | TRUE |  |  | 3.66% | 0%
STANTN_2_SBEBX2 | Battery Storage | 2022 | nonsummer | 2023-07-19 | 0 | 0 | 0 | 68.8 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
STANTN_2_SBEBX2 | Battery Storage | 2022 | summer | 2023-07-19 | 0 | 0 | 0 | 68.8 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
STANTN_2_SBEBX2 | Battery Storage | 2023 | nonsummer | 2023-07-19 | 0 | 0 | 305 | 68.8 | 20984 | 755 | Blended | 0% | 0% | 6.742% | 0% | 4.802% | 0% | TRUE | 6.742% | 0% | 4.802% | 0%
STANTN_2_SBEBX2 | Battery Storage | 2023 | summer | 2023-07-19 | 4021.9683 | 0 | 525 | 68.8 | 36120 | 240 | Blended | 11.14% | 0% | 6.657% | 0% | 9.73% | 0% | TRUE | 6.657% | 0% | 9.73% | 0%
STANTN_2_SBEBX2 | Battery Storage | 2024 | nonsummer | 2023-07-19 | 653.8575 | 0 | 1065 | 68.8 | 73272 | 0 | Individual | 0.8924% | 0% |  |  | 0.8924% | 0% | TRUE |  |  | 0.8924% | 0%
STANTN_2_SBEBX2 | Battery Storage | 2024 | summer | 2023-07-19 | 105.3333 | 0 | 765 | 68.8 | 52632 | 0 | Individual | 0.2001% | 0% |  |  | 0.2001% | 0% | TRUE |  |  | 0.2001% | 0%
TAHOE_2_THOBT1 | Battery Storage | 2022 | nonsummer | 2025-06-05 | 0 | 0 | 0 | 60.04 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
TAHOE_2_THOBT1 | Battery Storage | 2022 | summer | 2025-06-05 | 0 | 0 | 0 | 60.04 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
TAHOE_2_THOBT1 | Battery Storage | 2023 | nonsummer | 2025-06-05 | 0 | 0 | 0 | 60.04 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
TAHOE_2_THOBT1 | Battery Storage | 2023 | summer | 2025-06-05 | 0 | 0 | 0 | 60.04 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
TAHOE_2_THOBT1 | Battery Storage | 2024 | nonsummer | 2025-06-05 | 0 | 0 | 0 | 60.04 | 0 | 1065 | Group |  |  | 6.223% | 0% | 6.223% | 0% | TRUE | 6.223% | 0% | 6.223% | 0%
TAHOE_2_THOBT1 | Battery Storage | 2024 | summer | 2025-06-05 | 0 | 0 | 0 | 60.04 | 0 | 765 | Group |  |  | 8.576% | 0% | 8.576% | 0% | TRUE | 8.576% | 0% | 8.576% | 0%
TAHOE_2_THOBT2 | Battery Storage | 2022 | nonsummer | 2025-06-02 | 0 | 0 | 0 | 109.06 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
TAHOE_2_THOBT2 | Battery Storage | 2022 | summer | 2025-06-02 | 0 | 0 | 0 | 109.06 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
TAHOE_2_THOBT2 | Battery Storage | 2023 | nonsummer | 2025-06-02 | 0 | 0 | 0 | 109.06 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
TAHOE_2_THOBT2 | Battery Storage | 2023 | summer | 2025-06-02 | 0 | 0 | 0 | 109.06 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
TAHOE_2_THOBT2 | Battery Storage | 2024 | nonsummer | 2025-06-02 | 0 | 0 | 0 | 109.06 | 0 | 1065 | Group |  |  | 6.223% | 0% | 6.223% | 0% | TRUE | 6.223% | 0% | 6.223% | 0%
TAHOE_2_THOBT2 | Battery Storage | 2024 | summer | 2025-06-02 | 0 | 0 | 0 | 109.06 | 0 | 765 | Group |  |  | 8.576% | 0% | 8.576% | 0% | TRUE | 8.576% | 0% | 8.576% | 0%
TAHOE_2_THOBT3 | Battery Storage | 2022 | nonsummer | 2025-06-02 | 0 | 0 | 0 | 110.1 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
TAHOE_2_THOBT3 | Battery Storage | 2022 | summer | 2025-06-02 | 0 | 0 | 0 | 110.1 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
TAHOE_2_THOBT3 | Battery Storage | 2023 | nonsummer | 2025-06-02 | 0 | 0 | 0 | 110.1 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
TAHOE_2_THOBT3 | Battery Storage | 2023 | summer | 2025-06-02 | 0 | 0 | 0 | 110.1 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
TAHOE_2_THOBT3 | Battery Storage | 2024 | nonsummer | 2025-06-02 | 0 | 0 | 0 | 110.1 | 0 | 1065 | Group |  |  | 6.223% | 0% | 6.223% | 0% | TRUE | 6.223% | 0% | 6.223% | 0%
TAHOE_2_THOBT3 | Battery Storage | 2024 | summer | 2025-06-02 | 64.1667 | 0 | 0 | 110.1 | 0 | 765 | Group |  |  | 8.576% | 0% | 8.576% | 0% | TRUE | 8.576% | 0% | 8.576% | 0%
TUMBWD_2_WISBT3 | Battery Storage | 2022 | nonsummer | 2024-07-16 | 0 | 0 | 0 | 50 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
TUMBWD_2_WISBT3 | Battery Storage | 2022 | summer | 2024-07-16 | 0 | 0 | 0 | 50 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
TUMBWD_2_WISBT3 | Battery Storage | 2023 | nonsummer | 2024-07-16 | 0 | 0 | 0 | 50 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
TUMBWD_2_WISBT3 | Battery Storage | 2023 | summer | 2024-07-16 | 0 | 0 | 0 | 50 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
TUMBWD_2_WISBT3 | Battery Storage | 2024 | nonsummer | 2024-07-16 | 0 | 0 | 305 | 50 | 15250 | 760 | Blended | 0% | 0% | 6.223% | 0% | 4.441% | 0% | TRUE | 6.223% | 0% | 4.441% | 0%
TUMBWD_2_WISBT3 | Battery Storage | 2024 | summer | 2024-07-16 | 1626.65 | 0 | 540 | 50 | 27000 | 225 | Blended | 6.025% | 0% | 8.576% | 0% | 6.775% | 0% | TRUE | 8.576% | 0% | 6.775% | 0%
TUMBWD_2_WISBT4 | Battery Storage | 2022 | nonsummer | 2024-08-14 | 0 | 0 | 0 | 74.97 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
TUMBWD_2_WISBT4 | Battery Storage | 2022 | summer | 2024-08-14 | 0 | 0 | 0 | 74.97 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
TUMBWD_2_WISBT4 | Battery Storage | 2023 | nonsummer | 2024-08-14 | 0 | 0 | 0 | 74.97 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
TUMBWD_2_WISBT4 | Battery Storage | 2023 | summer | 2024-08-14 | 0 | 0 | 0 | 74.97 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
TUMBWD_2_WISBT4 | Battery Storage | 2024 | nonsummer | 2024-08-14 | 0 | 0 | 305 | 74.97 | 22865.85 | 760 | Blended | 0% | 0% | 6.223% | 0% | 4.441% | 0% | TRUE | 6.223% | 0% | 4.441% | 0%
TUMBWD_2_WISBT4 | Battery Storage | 2024 | summer | 2024-08-14 | 151.0617 | 0 | 395 | 74.97 | 29613.15 | 370 | Blended | 0.5101% | 0% | 8.576% | 0% | 4.411% | 0% | TRUE | 8.576% | 0% | 4.411% | 0%
VALLEY_5_ORTBT1 | Battery Storage | 2022 | nonsummer | 2025-06-16 | 0 | 0 | 0 | 20 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
VALLEY_5_ORTBT1 | Battery Storage | 2022 | summer | 2025-06-16 | 0 | 0 | 0 | 20 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
VALLEY_5_ORTBT1 | Battery Storage | 2023 | nonsummer | 2025-06-16 | 0 | 0 | 0 | 20 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
VALLEY_5_ORTBT1 | Battery Storage | 2023 | summer | 2025-06-16 | 0 | 0 | 0 | 20 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
VALLEY_5_ORTBT1 | Battery Storage | 2024 | nonsummer | 2025-06-16 | 0 | 0 | 0 | 20 | 0 | 1065 | Group |  |  | 6.223% | 0% | 6.223% | 0% | TRUE | 6.223% | 0% | 6.223% | 0%
VALLEY_5_ORTBT1 | Battery Storage | 2024 | summer | 2025-06-16 | 0 | 0 | 0 | 20 | 0 | 765 | Group |  |  | 8.576% | 0% | 8.576% | 0% | TRUE | 8.576% | 0% | 8.576% | 0%
VESTAL_2_BTNBT1 | Battery Storage | 2022 | nonsummer | 2024-10-19 | 0 | 0 | 0 | 80 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
VESTAL_2_BTNBT1 | Battery Storage | 2022 | summer | 2024-10-19 | 0 | 0 | 0 | 80 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
VESTAL_2_BTNBT1 | Battery Storage | 2023 | nonsummer | 2024-10-19 | 0 | 0 | 0 | 80 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
VESTAL_2_BTNBT1 | Battery Storage | 2023 | summer | 2024-10-19 | 0 | 0 | 0 | 80 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
VESTAL_2_BTNBT1 | Battery Storage | 2024 | nonsummer | 2024-10-19 | 4651.4333 | 0 | 305 | 80 | 24400 | 760 | Blended | 19.06% | 0% | 6.223% | 0% | 9.9% | 0% | TRUE | 6.223% | 0% | 9.9% | 0%
VESTAL_2_BTNBT1 | Battery Storage | 2024 | summer | 2024-10-19 | 2800 | 0 | 65 | 80 | 5200 | 700 | Blended | 53.85% | 0% | 8.576% | 0% | 12.42% | 0% | TRUE | 8.576% | 0% | 12.42% | 0%
VISTRA_5_DALBT1 | Battery Storage | 2022 | nonsummer | 2021-03-23 | 55922.5167 | 0 | 1060 | 100 | 106000 | 0 | Individual | 52.76% | 0% |  |  | 52.76% | 0% | TRUE |  |  | 52.76% | 0%
VISTRA_5_DALBT1 | Battery Storage | 2022 | summer | 2021-03-23 | 5423.8 | 0 | 765 | 100 | 76500 | 0 | Individual | 7.09% | 0% |  |  | 7.09% | 0% | TRUE |  |  | 7.09% | 0%
VISTRA_5_DALBT1 | Battery Storage | 2023 | nonsummer | 2021-03-23 | 7890.95 | 0 | 1060 | 100 | 106000 | 0 | Individual | 7.444% | 0% |  |  | 7.444% | 0% | TRUE |  |  | 7.444% | 0%
VISTRA_5_DALBT1 | Battery Storage | 2023 | summer | 2021-03-23 | 13425 | 0 | 765 | 100 | 76500 | 0 | Individual | 17.55% | 0% |  |  | 17.55% | 0% | TRUE |  |  | 17.55% | 0%
VISTRA_5_DALBT1 | Battery Storage | 2024 | nonsummer | 2021-03-23 | 2984.9667 | 0 | 1065 | 100 | 106500 | 0 | Individual | 2.803% | 0% |  |  | 2.803% | 0% | TRUE |  |  | 2.803% | 0%
VISTRA_5_DALBT1 | Battery Storage | 2024 | summer | 2021-03-23 | 234.6833 | 0 | 765 | 100 | 76500 | 0 | Individual | 0.3068% | 0% |  |  | 0.3068% | 0% | TRUE |  |  | 0.3068% | 0%
VISTRA_5_DALBT2 | Battery Storage | 2022 | nonsummer | 2021-03-23 | 1825.0333 | 0 | 1060 | 100 | 106000 | 0 | Individual | 1.722% | 0% |  |  | 1.722% | 0% | TRUE |  |  | 1.722% | 0%
VISTRA_5_DALBT2 | Battery Storage | 2022 | summer | 2021-03-23 | 6039.6333 | 0 | 765 | 100 | 76500 | 0 | Individual | 7.895% | 0% |  |  | 7.895% | 0% | TRUE |  |  | 7.895% | 0%
VISTRA_5_DALBT2 | Battery Storage | 2023 | nonsummer | 2021-03-23 | 10044.5 | 0 | 1060 | 100 | 106000 | 0 | Individual | 9.476% | 0% |  |  | 9.476% | 0% | TRUE |  |  | 9.476% | 0%
VISTRA_5_DALBT2 | Battery Storage | 2023 | summer | 2021-03-23 | 11750.8333 | 0 | 765 | 100 | 76500 | 0 | Individual | 15.36% | 0% |  |  | 15.36% | 0% | TRUE |  |  | 15.36% | 0%
VISTRA_5_DALBT2 | Battery Storage | 2024 | nonsummer | 2021-03-23 | 2011.95 | 0 | 1065 | 100 | 106500 | 0 | Individual | 1.889% | 0% |  |  | 1.889% | 0% | TRUE |  |  | 1.889% | 0%
VISTRA_5_DALBT2 | Battery Storage | 2024 | summer | 2021-03-23 | 40 | 0 | 765 | 100 | 76500 | 0 | Individual | 0.05229% | 0% |  |  | 0.05229% | 0% | TRUE |  |  | 0.05229% | 0%
VISTRA_5_DALBT3 | Battery Storage | 2022 | nonsummer | 2021-04-06 | 2062.6333 | 0 | 1060 | 100 | 106000 | 0 | Individual | 1.946% | 0% |  |  | 1.946% | 0% | TRUE |  |  | 1.946% | 0%
VISTRA_5_DALBT3 | Battery Storage | 2022 | summer | 2021-04-06 | 11046.5667 | 0 | 765 | 100 | 76500 | 0 | Individual | 14.44% | 0% |  |  | 14.44% | 0% | TRUE |  |  | 14.44% | 0%
VISTRA_5_DALBT3 | Battery Storage | 2023 | nonsummer | 2021-04-06 | 7744.5667 | 0 | 1060 | 100 | 106000 | 0 | Individual | 7.306% | 0% |  |  | 7.306% | 0% | TRUE |  |  | 7.306% | 0%
VISTRA_5_DALBT3 | Battery Storage | 2023 | summer | 2021-04-06 | 13983.7167 | 0 | 765 | 100 | 76500 | 0 | Individual | 18.28% | 0% |  |  | 18.28% | 0% | TRUE |  |  | 18.28% | 0%
VISTRA_5_DALBT3 | Battery Storage | 2024 | nonsummer | 2021-04-06 | 1730.4833 | 0 | 1065 | 100 | 106500 | 0 | Individual | 1.625% | 0% |  |  | 1.625% | 0% | TRUE |  |  | 1.625% | 0%
VISTRA_5_DALBT3 | Battery Storage | 2024 | summer | 2021-04-06 | 80 | 0 | 765 | 100 | 76500 | 0 | Individual | 0.1046% | 0% |  |  | 0.1046% | 0% | TRUE |  |  | 0.1046% | 0%
VISTRA_5_DALBT4 | Battery Storage | 2022 | nonsummer | 2021-07-28 | 53228.6833 | 0 | 1060 | 100 | 106000 | 0 | Individual | 50.22% | 0% |  |  | 50.22% | 0% | TRUE |  |  | 50.22% | 0%
VISTRA_5_DALBT4 | Battery Storage | 2022 | summer | 2021-07-28 | 9554.3167 | 0 | 765 | 100 | 76500 | 0 | Individual | 12.49% | 0% |  |  | 12.49% | 0% | TRUE |  |  | 12.49% | 0%
VISTRA_5_DALBT4 | Battery Storage | 2023 | nonsummer | 2021-07-28 | 1817.75 | 0 | 1060 | 100 | 106000 | 0 | Individual | 1.715% | 0% |  |  | 1.715% | 0% | TRUE |  |  | 1.715% | 0%
VISTRA_5_DALBT4 | Battery Storage | 2023 | summer | 2021-07-28 | 1642.3167 | 0 | 765 | 100 | 76500 | 0 | Individual | 2.147% | 0% |  |  | 2.147% | 0% | TRUE |  |  | 2.147% | 0%
VISTRA_5_DALBT4 | Battery Storage | 2024 | nonsummer | 2021-07-28 | 439.1667 | 0 | 1065 | 100 | 106500 | 0 | Individual | 0.4124% | 0% |  |  | 0.4124% | 0% | TRUE |  |  | 0.4124% | 0%
VISTRA_5_DALBT4 | Battery Storage | 2024 | summer | 2021-07-28 | 67.4 | 0 | 765 | 100 | 76500 | 0 | Individual | 0.0881% | 0% |  |  | 0.0881% | 0% | TRUE |  |  | 0.0881% | 0%
VISTRA_5_PLABT1 | Battery Storage | 2022 | nonsummer | 2023-05-13 | 0 | 0 | 0 | 100.4 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
VISTRA_5_PLABT1 | Battery Storage | 2022 | summer | 2023-05-13 | 0 | 0 | 0 | 100.4 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
VISTRA_5_PLABT1 | Battery Storage | 2023 | nonsummer | 2023-05-13 | 10898.67 | 0 | 400 | 100.4 | 40160 | 660 | Blended | 27.14% | 0% | 6.742% | 0% | 14.44% | 0% | TRUE | 6.742% | 0% | 14.44% | 0%
VISTRA_5_PLABT1 | Battery Storage | 2023 | summer | 2023-05-13 | 347.6133 | 0 | 765 | 100.4 | 76806 | 0 | Individual | 0.4526% | 0% |  |  | 0.4526% | 0% | TRUE |  |  | 0.4526% | 0%
VISTRA_5_PLABT1 | Battery Storage | 2024 | nonsummer | 2023-05-13 | 6034.47 | 0 | 1065 | 100.4 | 106926 | 0 | Individual | 5.644% | 0% |  |  | 5.644% | 0% | TRUE |  |  | 5.644% | 0%
VISTRA_5_PLABT1 | Battery Storage | 2024 | summer | 2023-05-13 | 0 | 0 | 765 | 100.4 | 76806 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
VISTRA_5_PLABT2 | Battery Storage | 2022 | nonsummer | 2023-06-01 | 0 | 0 | 0 | 100.4 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
VISTRA_5_PLABT2 | Battery Storage | 2022 | summer | 2023-06-01 | 0 | 0 | 0 | 100.4 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
VISTRA_5_PLABT2 | Battery Storage | 2023 | nonsummer | 2023-06-01 | 631.3333 | 0 | 305 | 100.4 | 30622 | 755 | Blended | 2.062% | 0% | 6.742% | 0% | 5.395% | 0% | TRUE | 6.742% | 0% | 5.395% | 0%
VISTRA_5_PLABT2 | Battery Storage | 2023 | summer | 2023-06-01 | 275.4333 | 0 | 765 | 100.4 | 76806 | 0 | Individual | 0.3586% | 0% |  |  | 0.3586% | 0% | TRUE |  |  | 0.3586% | 0%
VISTRA_5_PLABT2 | Battery Storage | 2024 | nonsummer | 2023-06-01 | 2967.05 | 0 | 1065 | 100.4 | 106926 | 0 | Individual | 2.775% | 0% |  |  | 2.775% | 0% | TRUE |  |  | 2.775% | 0%
VISTRA_5_PLABT2 | Battery Storage | 2024 | summer | 2023-06-01 | 129.0733 | 0 | 765 | 100.4 | 76806 | 0 | Individual | 0.1681% | 0% |  |  | 0.1681% | 0% | TRUE |  |  | 0.1681% | 0%
VISTRA_5_PLABT3 | Battery Storage | 2022 | nonsummer | 2023-05-16 | 0 | 0 | 0 | 74.6 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
VISTRA_5_PLABT3 | Battery Storage | 2022 | summer | 2023-05-16 | 0 | 0 | 0 | 74.6 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
VISTRA_5_PLABT3 | Battery Storage | 2023 | nonsummer | 2023-05-16 | 5613.66 | 0 | 385 | 74.6 | 28721 | 675 | Blended | 19.55% | 0% | 6.742% | 0% | 11.39% | 0% | TRUE | 6.742% | 0% | 11.39% | 0%
VISTRA_5_PLABT3 | Battery Storage | 2023 | summer | 2023-05-16 | 22 | 0 | 765 | 74.6 | 57069 | 0 | Individual | 0.03855% | 0% |  |  | 0.03855% | 0% | TRUE |  |  | 0.03855% | 0%
VISTRA_5_PLABT3 | Battery Storage | 2024 | nonsummer | 2023-05-16 | 1045.1667 | 0 | 1065 | 74.6 | 79449 | 0 | Individual | 1.316% | 0% |  |  | 1.316% | 0% | TRUE |  |  | 1.316% | 0%
VISTRA_5_PLABT3 | Battery Storage | 2024 | summer | 2023-05-16 | 18.7833 | 0 | 765 | 74.6 | 57069 | 0 | Individual | 0.03291% | 0% |  |  | 0.03291% | 0% | TRUE |  |  | 0.03291% | 0%
VISTRA_5_PLABT4 | Battery Storage | 2022 | nonsummer | 2023-06-02 | 0 | 0 | 0 | 74.6 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
VISTRA_5_PLABT4 | Battery Storage | 2022 | summer | 2023-06-02 | 0 | 0 | 0 | 74.6 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
VISTRA_5_PLABT4 | Battery Storage | 2023 | nonsummer | 2023-06-02 | 118.93 | 0 | 305 | 74.6 | 22753 | 755 | Blended | 0.5227% | 0% | 6.742% | 0% | 4.952% | 0% | TRUE | 6.742% | 0% | 4.952% | 0%
VISTRA_5_PLABT4 | Battery Storage | 2023 | summer | 2023-06-02 | 285.46 | 0 | 760 | 74.6 | 56696 | 5 | Blended | 0.5035% | 0% | 6.657% | 0% | 0.5437% | 0% | TRUE | 6.657% | 0% | 0.5437% | 0%
VISTRA_5_PLABT4 | Battery Storage | 2024 | nonsummer | 2023-06-02 | 1384.8367 | 0 | 1065 | 74.6 | 79449 | 0 | Individual | 1.743% | 0% |  |  | 1.743% | 0% | TRUE |  |  | 1.743% | 0%
VISTRA_5_PLABT4 | Battery Storage | 2024 | summer | 2023-06-02 | 0 | 0 | 765 | 74.6 | 57069 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
VSTAES_6_VESBT1 | Battery Storage | 2022 | nonsummer | 2018-06-26 | 887.5 | 0 | 1060 | 32 | 33920 | 0 | Individual | 2.616% | 0% |  |  | 2.616% | 0% | TRUE |  |  | 2.616% | 0%
VSTAES_6_VESBT1 | Battery Storage | 2022 | summer | 2018-06-26 | 273.7 | 0 | 765 | 32 | 24480 | 0 | Individual | 1.118% | 0% |  |  | 1.118% | 0% | TRUE |  |  | 1.118% | 0%
VSTAES_6_VESBT1 | Battery Storage | 2023 | nonsummer | 2018-06-26 | 2503.3 | 0 | 1060 | 32 | 33920 | 0 | Individual | 7.38% | 0% |  |  | 7.38% | 0% | TRUE |  |  | 7.38% | 0%
VSTAES_6_VESBT1 | Battery Storage | 2023 | summer | 2018-06-26 | 320.6583 | 0 | 765 | 32 | 24480 | 0 | Individual | 1.31% | 0% |  |  | 1.31% | 0% | TRUE |  |  | 1.31% | 0%
VSTAES_6_VESBT1 | Battery Storage | 2024 | nonsummer | 2018-06-26 | 4466.4582 | 0 | 1065 | 32 | 34080 | 0 | Individual | 13.11% | 0% |  |  | 13.11% | 0% | TRUE |  |  | 13.11% | 0%
VSTAES_6_VESBT1 | Battery Storage | 2024 | summer | 2018-06-26 | 1301.2917 | 0 | 765 | 32 | 24480 | 0 | Individual | 5.316% | 0% |  |  | 5.316% | 0% | TRUE |  |  | 5.316% | 0%
WDFRDF_2_WFFBT1 | Battery Storage | 2022 | nonsummer | 2024-07-25 | 0 | 0 | 0 | 25 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
WDFRDF_2_WFFBT1 | Battery Storage | 2022 | summer | 2024-07-25 | 0 | 0 | 0 | 25 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
WDFRDF_2_WFFBT1 | Battery Storage | 2023 | nonsummer | 2024-07-25 | 0 | 0 | 0 | 25 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
WDFRDF_2_WFFBT1 | Battery Storage | 2023 | summer | 2024-07-25 | 0 | 0 | 0 | 25 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
WDFRDF_2_WFFBT1 | Battery Storage | 2024 | nonsummer | 2024-07-25 | 192.5 | 0 | 305 | 25 | 7625 | 760 | Blended | 2.525% | 0% | 6.223% | 0% | 5.164% | 0% | TRUE | 6.223% | 0% | 5.164% | 0%
WDFRDF_2_WFFBT1 | Battery Storage | 2024 | summer | 2024-07-25 | 0 | 0 | 495 | 25 | 12375 | 270 | Blended | 0% | 0% | 8.576% | 0% | 3.027% | 0% | TRUE | 8.576% | 0% | 3.027% | 0%
WESCAN_2_BDSBT1 | Battery Storage | 2022 | nonsummer | 2023-06-23 | 0 | 0 | 0 | 131 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
WESCAN_2_BDSBT1 | Battery Storage | 2022 | summer | 2023-06-23 | 0 | 0 | 0 | 131 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
WESCAN_2_BDSBT1 | Battery Storage | 2023 | nonsummer | 2023-06-23 | 0 | 0 | 305 | 131 | 39955 | 755 | Blended | 0% | 0% | 6.742% | 0% | 4.802% | 0% | TRUE | 6.742% | 0% | 4.802% | 0%
WESCAN_2_BDSBT1 | Battery Storage | 2023 | summer | 2023-06-23 | 9087.0333 | 0 | 655 | 131 | 85805 | 110 | Blended | 10.59% | 0% | 6.657% | 0% | 10.02% | 0% | TRUE | 6.657% | 0% | 10.02% | 0%
WESCAN_2_BDSBT1 | Battery Storage | 2024 | nonsummer | 2023-06-23 | 2069.8 | 0 | 1065 | 131 | 139515 | 0 | Individual | 1.484% | 0% |  |  | 1.484% | 0% | TRUE |  |  | 1.484% | 0%
WESCAN_2_BDSBT1 | Battery Storage | 2024 | summer | 2023-06-23 | 393 | 0 | 765 | 131 | 100215 | 0 | Individual | 0.3922% | 0% |  |  | 0.3922% | 0% | TRUE |  |  | 0.3922% | 0%
WESCN2_2_BDSBT1 | Battery Storage | 2022 | nonsummer | 2024-12-31 | 0 | 0 | 0 | 119 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
WESCN2_2_BDSBT1 | Battery Storage | 2022 | summer | 2024-12-31 | 0 | 0 | 0 | 119 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
WESCN2_2_BDSBT1 | Battery Storage | 2023 | nonsummer | 2024-12-31 | 0 | 0 | 0 | 119 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
WESCN2_2_BDSBT1 | Battery Storage | 2023 | summer | 2024-12-31 | 0 | 0 | 0 | 119 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
WESCN2_2_BDSBT1 | Battery Storage | 2024 | nonsummer | 2024-12-31 | 0 | 0 | 5 | 119 | 595 | 1060 | Blended | 0% | 0% | 6.223% | 0% | 6.194% | 0% | TRUE | 6.223% | 0% | 6.194% | 0%
WESCN2_2_BDSBT1 | Battery Storage | 2024 | summer | 2024-12-31 | 0 | 0 | 0 | 119 | 0 | 765 | Group |  |  | 8.576% | 0% | 8.576% | 0% | TRUE | 8.576% | 0% | 8.576% | 0%
WSTWND_2_SBSBT1 | Battery Storage | 2022 | nonsummer | 2023-05-23 | 0 | 0 | 0 | 80 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
WSTWND_2_SBSBT1 | Battery Storage | 2022 | summer | 2023-05-23 | 0 | 0 | 0 | 80 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
WSTWND_2_SBSBT1 | Battery Storage | 2023 | nonsummer | 2023-05-23 | 555.4667 | 0 | 350 | 80 | 28000 | 710 | Blended | 1.984% | 0% | 6.742% | 0% | 5.171% | 0% | TRUE | 6.742% | 0% | 5.171% | 0%
WSTWND_2_SBSBT1 | Battery Storage | 2023 | summer | 2023-05-23 | 830.6667 | 0 | 765 | 80 | 61200 | 0 | Individual | 1.357% | 0% |  |  | 1.357% | 0% | TRUE |  |  | 1.357% | 0%
WSTWND_2_SBSBT1 | Battery Storage | 2024 | nonsummer | 2023-05-23 | 30.7167 | 0 | 1065 | 80 | 85200 | 0 | Individual | 0.03605% | 0% |  |  | 0.03605% | 0% | TRUE |  |  | 0.03605% | 0%
WSTWND_2_SBSBT1 | Battery Storage | 2024 | summer | 2023-05-23 | 0 | 0 | 765 | 80 | 61200 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
WSTWND_2_SBSBT2 | Battery Storage | 2022 | nonsummer | 2024-09-16 | 0 | 0 | 0 | 40 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
WSTWND_2_SBSBT2 | Battery Storage | 2022 | summer | 2024-09-16 | 0 | 0 | 0 | 40 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
WSTWND_2_SBSBT2 | Battery Storage | 2023 | nonsummer | 2024-09-16 | 0 | 0 | 0 | 40 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
WSTWND_2_SBSBT2 | Battery Storage | 2023 | summer | 2024-09-16 | 0 | 0 | 0 | 40 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
WSTWND_2_SBSBT2 | Battery Storage | 2024 | nonsummer | 2024-09-16 | 24 | 0 | 305 | 40 | 12200 | 760 | Blended | 0.1967% | 0% | 6.223% | 0% | 4.497% | 0% | TRUE | 6.223% | 0% | 4.497% | 0%
WSTWND_2_SBSBT2 | Battery Storage | 2024 | summer | 2024-09-16 | 30 | 0 | 230 | 40 | 9200 | 535 | Blended | 0.3261% | 0% | 8.576% | 0% | 6.095% | 0% | TRUE | 8.576% | 0% | 6.095% | 0%
WSTWND_2_SBSBT3 | Battery Storage | 2022 | nonsummer | 2024-08-13 | 0 | 0 | 0 | 59 | 0 | 1060 | Group |  |  | 15.33% | 0% | 15.33% | 0% | TRUE | 15.33% | 0% | 15.33% | 0%
WSTWND_2_SBSBT3 | Battery Storage | 2022 | summer | 2024-08-13 | 0 | 0 | 0 | 59 | 0 | 765 | Group |  |  | 13.83% | 0% | 13.83% | 0% | TRUE | 13.83% | 0% | 13.83% | 0%
WSTWND_2_SBSBT3 | Battery Storage | 2023 | nonsummer | 2024-08-13 | 0 | 0 | 0 | 59 | 0 | 1060 | Group |  |  | 6.742% | 0% | 6.742% | 0% | TRUE | 6.742% | 0% | 6.742% | 0%
WSTWND_2_SBSBT3 | Battery Storage | 2023 | summer | 2024-08-13 | 0 | 0 | 0 | 59 | 0 | 765 | Group |  |  | 6.657% | 0% | 6.657% | 0% | TRUE | 6.657% | 0% | 6.657% | 0%
WSTWND_2_SBSBT3 | Battery Storage | 2024 | nonsummer | 2024-08-13 | 0 | 0 | 305 | 59 | 17995 | 760 | Blended | 0% | 0% | 6.223% | 0% | 4.441% | 0% | TRUE | 6.223% | 0% | 4.441% | 0%
WSTWND_2_SBSBT3 | Battery Storage | 2024 | summer | 2024-08-13 | 428.9 | 0 | 400 | 59 | 23600 | 365 | Blended | 1.817% | 0% | 8.576% | 0% | 5.042% | 0% | TRUE | 8.576% | 0% | 5.042% | 0%
CHILLS_7_UNITA1 | Biogas | 2022 | nonsummer | 2004-07-14 | 552.75 | 0 | 1060 | 2.25 | 2385 | 0 | Individual | 23.18% | 0% |  |  | 23.18% | 0% | TRUE |  |  | 23.18% | 0%
CHILLS_7_UNITA1 | Biogas | 2022 | summer | 2004-07-14 | 80.25 | 0 | 765 | 2.25 | 1721.25 | 0 | Individual | 4.662% | 0% |  |  | 4.662% | 0% | TRUE |  |  | 4.662% | 0%
CHILLS_7_UNITA1 | Biogas | 2023 | nonsummer | 2004-07-14 | 218.3625 | 0 | 1060 | 2.25 | 2385 | 0 | Individual | 9.156% | 0% |  |  | 9.156% | 0% | TRUE |  |  | 9.156% | 0%
CHILLS_7_UNITA1 | Biogas | 2023 | summer | 2004-07-14 | 183.6167 | 0 | 765 | 2.25 | 1721.25 | 0 | Individual | 10.67% | 0% |  |  | 10.67% | 0% | TRUE |  |  | 10.67% | 0%
CHILLS_7_UNITA1 | Biogas | 2024 | nonsummer | 2004-07-14 | 386.0792 | 147.33 | 1065 | 2.25 | 2396.25 | 0 | Individual | 16.11% | 6.148% |  |  | 16.11% | 6.148% | TRUE |  |  | 16.11% | 6.148%
CHILLS_7_UNITA1 | Biogas | 2024 | summer | 2004-07-14 | 21.2333 | 264.2833 | 765 | 2.25 | 1721.25 | 0 | Individual | 1.234% | 15.35% |  |  | 1.234% | 15.35% | TRUE |  |  | 1.234% | 15.35%
CSTRVL_7_PL1X2 | Biogas | 2022 | nonsummer | 2007-09-01 | 97.5 | 0 | 1060 | 4.53 | 4801.8 | 0 | Individual | 2.03% | 0% |  |  | 2.03% | 0% | TRUE |  |  | 2.03% | 0%
CSTRVL_7_PL1X2 | Biogas | 2022 | summer | 2007-09-01 | 59.15 | 0 | 765 | 4.53 | 3465.45 | 0 | Individual | 1.707% | 0% |  |  | 1.707% | 0% | TRUE |  |  | 1.707% | 0%
CSTRVL_7_PL1X2 | Biogas | 2023 | nonsummer | 2007-09-01 | 0 | 0 | 1060 | 4.53 | 4801.8 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
CSTRVL_7_PL1X2 | Biogas | 2023 | summer | 2007-09-01 | 0 | 0 | 765 | 4.53 | 3465.45 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
CSTRVL_7_PL1X2 | Biogas | 2024 | nonsummer | 2007-09-01 | 249.15 | 0 | 1065 | 4.53 | 4824.45 | 0 | Individual | 5.164% | 0% |  |  | 5.164% | 0% | TRUE |  |  | 5.164% | 0%
CSTRVL_7_PL1X2 | Biogas | 2024 | summer | 2007-09-01 | 0 | 0 | 765 | 4.53 | 3465.45 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
GUERNS_6_HD3BM3 | Biogas | 2022 | nonsummer | 2019-07-01 | 110.8792 | 0 | 1060 | 1 | 1060 | 0 | Individual | 10.46% | 0% |  |  | 10.46% | 0% | TRUE |  |  | 10.46% | 0%
GUERNS_6_HD3BM3 | Biogas | 2022 | summer | 2019-07-01 | 7.75 | 0 | 765 | 1 | 765 | 0 | Individual | 1.013% | 0% |  |  | 1.013% | 0% | TRUE |  |  | 1.013% | 0%
GUERNS_6_HD3BM3 | Biogas | 2023 | nonsummer | 2019-07-01 | 92.1 | 0 | 1060 | 1 | 1060 | 0 | Individual | 8.689% | 0% |  |  | 8.689% | 0% | TRUE |  |  | 8.689% | 0%
GUERNS_6_HD3BM3 | Biogas | 2023 | summer | 2019-07-01 | 22.7417 | 0 | 765 | 1 | 765 | 0 | Individual | 2.973% | 0% |  |  | 2.973% | 0% | TRUE |  |  | 2.973% | 0%
GUERNS_6_HD3BM3 | Biogas | 2024 | nonsummer | 2019-07-01 | 98.8333 | 0 | 1065 | 1 | 1065 | 0 | Individual | 9.28% | 0% |  |  | 9.28% | 0% | TRUE |  |  | 9.28% | 0%
GUERNS_6_HD3BM3 | Biogas | 2024 | summer | 2019-07-01 | 16.75 | 0 | 765 | 1 | 765 | 0 | Individual | 2.19% | 0% |  |  | 2.19% | 0% | TRUE |  |  | 2.19% | 0%
GUERNS_6_VH2BM1 | Biogas | 2022 | nonsummer | 2019-07-01 | 98.7958 | 0 | 1060 | 1 | 1060 | 0 | Individual | 9.32% | 0% |  |  | 9.32% | 0% | TRUE |  |  | 9.32% | 0%
GUERNS_6_VH2BM1 | Biogas | 2022 | summer | 2019-07-01 | 28.4 | 0 | 765 | 1 | 765 | 0 | Individual | 3.712% | 0% |  |  | 3.712% | 0% | TRUE |  |  | 3.712% | 0%
GUERNS_6_VH2BM1 | Biogas | 2023 | nonsummer | 2019-07-01 | 102.55 | 0 | 1060 | 1 | 1060 | 0 | Individual | 9.675% | 0% |  |  | 9.675% | 0% | TRUE |  |  | 9.675% | 0%
GUERNS_6_VH2BM1 | Biogas | 2023 | summer | 2019-07-01 | 87.25 | 0 | 765 | 1 | 765 | 0 | Individual | 11.41% | 0% |  |  | 11.41% | 0% | TRUE |  |  | 11.41% | 0%
GUERNS_6_VH2BM1 | Biogas | 2024 | nonsummer | 2019-07-01 | 86.8333 | 0 | 1065 | 1 | 1065 | 0 | Individual | 8.153% | 0% |  |  | 8.153% | 0% | TRUE |  |  | 8.153% | 0%
GUERNS_6_VH2BM1 | Biogas | 2024 | summer | 2019-07-01 | 23.5 | 0 | 765 | 1 | 765 | 0 | Individual | 3.072% | 0% |  |  | 3.072% | 0% | TRUE |  |  | 3.072% | 0%
HARDWK_6_STWBM1 | Biogas | 2022 | nonsummer | 2020-05-26 | 68.4167 | 0 | 1060 | 1 | 1060 | 0 | Individual | 6.454% | 0% |  |  | 6.454% | 0% | TRUE |  |  | 6.454% | 0%
HARDWK_6_STWBM1 | Biogas | 2022 | summer | 2020-05-26 | 20.1667 | 18.6 | 765 | 1 | 765 | 0 | Individual | 2.636% | 2.431% |  |  | 2.636% | 2.431% | TRUE |  |  | 2.636% | 2.431%
HARDWK_6_STWBM1 | Biogas | 2023 | nonsummer | 2020-05-26 | 0 | 0 | 1060 | 1 | 1060 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
HARDWK_6_STWBM1 | Biogas | 2023 | summer | 2020-05-26 | 11.3333 | 0 | 765 | 1 | 765 | 0 | Individual | 1.481% | 0% |  |  | 1.481% | 0% | TRUE |  |  | 1.481% | 0%
HARDWK_6_STWBM1 | Biogas | 2024 | nonsummer | 2020-05-26 | 46.8 | 0 | 1065 | 1 | 1065 | 0 | Individual | 4.394% | 0% |  |  | 4.394% | 0% | TRUE |  |  | 4.394% | 0%
HARDWK_6_STWBM1 | Biogas | 2024 | summer | 2020-05-26 | 48.1167 | 0 | 765 | 1 | 765 | 0 | Individual | 6.29% | 0% |  |  | 6.29% | 0% | TRUE |  |  | 6.29% | 0%
PSWEET_1_STCRUZ | Biogas | 2022 | nonsummer | 2010-02-06 | 0 | 0 | 1060 | 1.6 | 1696 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
PSWEET_1_STCRUZ | Biogas | 2022 | summer | 2010-02-06 | 0 | 0 | 765 | 1.6 | 1224 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
PSWEET_1_STCRUZ | Biogas | 2023 | nonsummer | 2010-02-06 | 0 | 0 | 1060 | 1.6 | 1696 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
PSWEET_1_STCRUZ | Biogas | 2023 | summer | 2010-02-06 | 0 | 0 | 765 | 1.6 | 1224 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
PSWEET_1_STCRUZ | Biogas | 2024 | nonsummer | 2010-02-06 | 0 | 0 | 1065 | 1.6 | 1704 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
PSWEET_1_STCRUZ | Biogas | 2024 | summer | 2010-02-06 | 0 | 0 | 765 | 1.6 | 1224 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SANLOB_1_OSFBM1 | Biogas | 2022 | nonsummer | 2019-07-11 | 0 | 0 | 1060 | 0.85 | 901 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SANLOB_1_OSFBM1 | Biogas | 2022 | summer | 2019-07-11 | 0 | 0 | 765 | 0.85 | 650.25 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SANLOB_1_OSFBM1 | Biogas | 2023 | nonsummer | 2019-07-11 | 0 | 0 | 1060 | 0.85 | 901 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SANLOB_1_OSFBM1 | Biogas | 2023 | summer | 2019-07-11 | 0 | 0 | 765 | 0.85 | 650.25 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SANLOB_1_OSFBM1 | Biogas | 2024 | nonsummer | 2019-07-11 | 0 | 0 | 1065 | 0.85 | 905.25 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SANLOB_1_OSFBM1 | Biogas | 2024 | summer | 2019-07-11 | 0 | 0 | 765 | 0.85 | 650.25 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
USWND4_2_UNIT2 | Biogas | 2022 | nonsummer | 2018-02-01 | 0 | 0 | 1060 | 7.4 | 7844 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
USWND4_2_UNIT2 | Biogas | 2022 | summer | 2018-02-01 | 0 | 0 | 765 | 7.4 | 5661 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
USWND4_2_UNIT2 | Biogas | 2023 | nonsummer | 2018-02-01 | 0 | 0 | 1060 | 7.4 | 7844 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
USWND4_2_UNIT2 | Biogas | 2023 | summer | 2018-02-01 | 0 | 0 | 765 | 7.4 | 5661 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
USWND4_2_UNIT2 | Biogas | 2024 | nonsummer | 2018-02-01 | 0 | 0 | 1065 | 7.4 | 7881 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
USWND4_2_UNIT2 | Biogas | 2024 | summer | 2018-02-01 | 0 | 0 | 765 | 7.4 | 5661 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
LASSEN_6_UNITS | Biomass/Wood | 2022 | nonsummer | 2017-06-27 | 4156.2267 | 0 | 1060 | 30 | 31800 | 0 | Individual | 13.07% | 0% |  |  | 13.07% | 0% | TRUE |  |  | 13.07% | 0%
LASSEN_6_UNITS | Biomass/Wood | 2022 | summer | 2017-06-27 | 825.5 | 0 | 765 | 30 | 22950 | 0 | Individual | 3.597% | 0% |  |  | 3.597% | 0% | TRUE |  |  | 3.597% | 0%
LASSEN_6_UNITS | Biomass/Wood | 2023 | nonsummer | 2017-06-27 | 891.5 | 0 | 1060 | 30 | 31800 | 0 | Individual | 2.803% | 0% |  |  | 2.803% | 0% | TRUE |  |  | 2.803% | 0%
LASSEN_6_UNITS | Biomass/Wood | 2023 | summer | 2017-06-27 | 1047.5 | 0 | 765 | 30 | 22950 | 0 | Individual | 4.564% | 0% |  |  | 4.564% | 0% | TRUE |  |  | 4.564% | 0%
LASSEN_6_UNITS | Biomass/Wood | 2024 | nonsummer | 2017-06-27 | 1197.1667 | 0 | 1065 | 30 | 31950 | 0 | Individual | 3.747% | 0% |  |  | 3.747% | 0% | TRUE |  |  | 3.747% | 0%
LASSEN_6_UNITS | Biomass/Wood | 2024 | summer | 2017-06-27 | 1305 | 0 | 765 | 30 | 22950 | 0 | Individual | 5.686% | 0% |  |  | 5.686% | 0% | TRUE |  |  | 5.686% | 0%
AGRICO_7_UNIT | CCGT | 2022 | nonsummer | 2023-03-14 | 0 | 0 | 0 | 59.97 | 0 | 1060 | Group |  |  | 8.267% | 1.874% | 8.267% | 1.874% | TRUE | 8.267% | 1.874% | 8.267% | 1.874%
AGRICO_7_UNIT | CCGT | 2022 | summer | 2023-03-14 | 0 | 0 | 0 | 59.97 | 0 | 765 | Group |  |  | 5.244% | 5.898% | 5.244% | 5.898% | TRUE | 5.244% | 5.898% | 5.244% | 5.898%
AGRICO_7_UNIT | CCGT | 2023 | nonsummer | 2023-03-14 | 0 | 39.97 | 700 | 59.97 | 41979 | 360 | Blended | 0% | 0.09521% | 6.533% | 1.873% | 2.219% | 0.699% | TRUE | 6.533% | 1.873% | 2.219% | 0.699%
AGRICO_7_UNIT | CCGT | 2023 | summer | 2023-03-14 | 9.13 | 601.3032 | 765 | 59.97 | 45877.05 | 0 | Individual | 0.0199% | 1.311% |  |  | 0.0199% | 1.311% | TRUE |  |  | 0.0199% | 1.311%
AGRICO_7_UNIT | CCGT | 2024 | nonsummer | 2023-03-14 | 98.9818 | 0 | 1065 | 59.97 | 63868.05 | 0 | Individual | 0.155% | 0% |  |  | 0.155% | 0% | TRUE |  |  | 0.155% | 0%
AGRICO_7_UNIT | CCGT | 2024 | summer | 2023-03-14 | 1002.1375 | 0 | 765 | 59.97 | 45877.05 | 0 | Individual | 2.184% | 0% |  |  | 2.184% | 0% | TRUE |  |  | 2.184% | 0%
ALAMIT_2_PL1X3 | CCGT | 2022 | nonsummer | 2020-02-06 | 45345.5022 | 36.8 | 1060 | 674.7 | 715182 | 0 | Individual | 6.34% | 0.005146% |  |  | 6.34% | 0.005146% | TRUE |  |  | 6.34% | 0.005146%
ALAMIT_2_PL1X3 | CCGT | 2022 | summer | 2020-02-06 | 5730.0492 | 7530.1667 | 765 | 674.7 | 516145.5 | 0 | Individual | 1.11% | 1.459% |  |  | 1.11% | 1.459% | TRUE |  |  | 1.11% | 1.459%
ALAMIT_2_PL1X3 | CCGT | 2023 | nonsummer | 2020-02-06 | 40688.6635 | 409.5 | 1060 | 674.7 | 715182 | 0 | Individual | 5.689% | 0.05726% |  |  | 5.689% | 0.05726% | TRUE |  |  | 5.689% | 0.05726%
ALAMIT_2_PL1X3 | CCGT | 2023 | summer | 2020-02-06 | 4087.0525 | 6557.5 | 765 | 674.7 | 516145.5 | 0 | Individual | 0.7918% | 1.27% |  |  | 0.7918% | 1.27% | TRUE |  |  | 0.7918% | 1.27%
ALAMIT_2_PL1X3 | CCGT | 2024 | nonsummer | 2020-02-06 | 49893.6055 | 85.965 | 1065 | 674.7 | 718555.5 | 0 | Individual | 6.944% | 0.01196% |  |  | 6.944% | 0.01196% | TRUE |  |  | 6.944% | 0.01196%
ALAMIT_2_PL1X3 | CCGT | 2024 | summer | 2020-02-06 | 1728.15 | 4051.1667 | 765 | 674.7 | 516145.5 | 0 | Individual | 0.3348% | 0.7849% |  |  | 0.3348% | 0.7849% | TRUE |  |  | 0.3348% | 0.7849%
BUCKBL_2_PL1X3 | CCGT | 2022 | nonsummer | 2010-07-31 | 1554.3443 | 0 | 1060 | 493.63 | 523247.8 | 0 | Individual | 0.2971% | 0% |  |  | 0.2971% | 0% | TRUE |  |  | 0.2971% | 0%
BUCKBL_2_PL1X3 | CCGT | 2022 | summer | 2010-07-31 | 6285.1408 | 370.2225 | 765 | 493.63 | 377626.95 | 0 | Individual | 1.664% | 0.09804% |  |  | 1.664% | 0.09804% | TRUE |  |  | 1.664% | 0.09804%
BUCKBL_2_PL1X3 | CCGT | 2023 | nonsummer | 2010-07-31 | 18924.659 | 0 | 1060 | 493.63 | 523247.8 | 0 | Individual | 3.617% | 0% |  |  | 3.617% | 0% | TRUE |  |  | 3.617% | 0%
BUCKBL_2_PL1X3 | CCGT | 2023 | summer | 2010-07-31 | 8076.9092 | 0 | 765 | 493.63 | 377626.95 | 0 | Individual | 2.139% | 0% |  |  | 2.139% | 0% | TRUE |  |  | 2.139% | 0%
BUCKBL_2_PL1X3 | CCGT | 2024 | nonsummer | 2010-07-31 | 64352.8977 | 0 | 1065 | 493.63 | 525715.95 | 0 | Individual | 12.24% | 0% |  |  | 12.24% | 0% | TRUE |  |  | 12.24% | 0%
BUCKBL_2_PL1X3 | CCGT | 2024 | summer | 2010-07-31 | 3167.4592 | 0 | 765 | 493.63 | 377626.95 | 0 | Individual | 0.8388% | 0% |  |  | 0.8388% | 0% | TRUE |  |  | 0.8388% | 0%
CALPIN_1_AGNEW | CCGT | 2022 | nonsummer | 1990-10-19 | 7303.1227 | 17.94 | 1060 | 28.56 | 30273.6 | 0 | Individual | 24.12% | 0.05926% |  |  | 24.12% | 0.05926% | TRUE |  |  | 24.12% | 0.05926%
CALPIN_1_AGNEW | CCGT | 2022 | summer | 1990-10-19 | 1773.4267 | 56.194 | 765 | 28.56 | 21848.4 | 0 | Individual | 8.117% | 0.2572% |  |  | 8.117% | 0.2572% | TRUE |  |  | 8.117% | 0.2572%
CALPIN_1_AGNEW | CCGT | 2023 | nonsummer | 1990-10-19 | 2302.216 | 239.848 | 1060 | 28.56 | 30273.6 | 0 | Individual | 7.605% | 0.7923% |  |  | 7.605% | 0.7923% | TRUE |  |  | 7.605% | 0.7923%
CALPIN_1_AGNEW | CCGT | 2023 | summer | 1990-10-19 | 1806.5573 | 259.2 | 765 | 28.56 | 21848.4 | 0 | Individual | 8.269% | 1.186% |  |  | 8.269% | 1.186% | TRUE |  |  | 8.269% | 1.186%
CALPIN_1_AGNEW | CCGT | 2024 | nonsummer | 1990-10-19 | 4548.9333 | 238.44 | 1065 | 28.56 | 30416.4 | 0 | Individual | 14.96% | 0.7839% |  |  | 14.96% | 0.7839% | TRUE |  |  | 14.96% | 0.7839%
CALPIN_1_AGNEW | CCGT | 2024 | summer | 1990-10-19 | 326.51 | 962.8813 | 765 | 28.56 | 21848.4 | 0 | Individual | 1.494% | 4.407% |  |  | 1.494% | 4.407% | TRUE |  |  | 1.494% | 4.407%
COLUSA_2_PL1X3 | CCGT | 2022 | nonsummer | 2010-12-22 | 24654.9847 | 16284.4 | 1060 | 641 | 679460 | 0 | Individual | 3.629% | 2.397% |  |  | 3.629% | 2.397% | TRUE |  |  | 3.629% | 2.397%
COLUSA_2_PL1X3 | CCGT | 2022 | summer | 2010-12-22 | 20742.5283 | 37562.6932 | 765 | 641 | 490365 | 0 | Individual | 4.23% | 7.66% |  |  | 4.23% | 7.66% | TRUE |  |  | 4.23% | 7.66%
COLUSA_2_PL1X3 | CCGT | 2023 | nonsummer | 2010-12-22 | 4784.0533 | 15947.1455 | 1060 | 641 | 679460 | 0 | Individual | 0.7041% | 2.347% |  |  | 0.7041% | 2.347% | TRUE |  |  | 0.7041% | 2.347%
COLUSA_2_PL1X3 | CCGT | 2023 | summer | 2010-12-22 | 8466.724 | 30098.695 | 765 | 641 | 490365 | 0 | Individual | 1.727% | 6.138% |  |  | 1.727% | 6.138% | TRUE |  |  | 1.727% | 6.138%
COLUSA_2_PL1X3 | CCGT | 2024 | nonsummer | 2010-12-22 | 35637.6617 | 18724.0133 | 1065 | 641 | 682665 | 0 | Individual | 5.22% | 2.743% |  |  | 5.22% | 2.743% | TRUE |  |  | 5.22% | 2.743%
COLUSA_2_PL1X3 | CCGT | 2024 | summer | 2010-12-22 | 8109.7417 | 35695.5075 | 765 | 641 | 490365 | 0 | Individual | 1.654% | 7.279% |  |  | 1.654% | 7.279% | TRUE |  |  | 1.654% | 7.279%
CORONS_6_CLRWTR | CCGT | 2022 | nonsummer | 2005-02-28 | 0 | 0 | 1060 | 28 | 29680 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
CORONS_6_CLRWTR | CCGT | 2022 | summer | 2005-02-28 | 145.4127 | 0 | 765 | 28 | 21420 | 0 | Individual | 0.6789% | 0% |  |  | 0.6789% | 0% | TRUE |  |  | 0.6789% | 0%
CORONS_6_CLRWTR | CCGT | 2023 | nonsummer | 2005-02-28 | 0 | 0 | 1060 | 28 | 29680 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
CORONS_6_CLRWTR | CCGT | 2023 | summer | 2005-02-28 | 64.4877 | 0 | 765 | 28 | 21420 | 0 | Individual | 0.3011% | 0% |  |  | 0.3011% | 0% | TRUE |  |  | 0.3011% | 0%
CORONS_6_CLRWTR | CCGT | 2024 | nonsummer | 2005-02-28 | 0 | 0 | 1065 | 28 | 29820 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
CORONS_6_CLRWTR | CCGT | 2024 | summer | 2005-02-28 | 711.985 | 0 | 765 | 28 | 21420 | 0 | Individual | 3.324% | 0% |  |  | 3.324% | 0% | TRUE |  |  | 3.324% | 0%
DELTA_2_PL1X4 | CCGT | 2022 | nonsummer | 2002-06-17 | 50729.9833 | 8980 | 1060 | 880 | 932800 | 0 | Individual | 5.438% | 0.9627% |  |  | 5.438% | 0.9627% | TRUE |  |  | 5.438% | 0.9627%
DELTA_2_PL1X4 | CCGT | 2022 | summer | 2002-06-17 | 22382.2917 | 36005.1667 | 765 | 880 | 673200 | 0 | Individual | 3.325% | 5.348% |  |  | 3.325% | 5.348% | TRUE |  |  | 3.325% | 5.348%
DELTA_2_PL1X4 | CCGT | 2023 | nonsummer | 2002-06-17 | 41494.8502 | 15827.3967 | 1060 | 880 | 932800 | 0 | Individual | 4.448% | 1.697% |  |  | 4.448% | 1.697% | TRUE |  |  | 4.448% | 1.697%
DELTA_2_PL1X4 | CCGT | 2023 | summer | 2002-06-17 | 64257.2667 | 28843.9837 | 765 | 880 | 673200 | 0 | Individual | 9.545% | 4.285% |  |  | 9.545% | 4.285% | TRUE |  |  | 9.545% | 4.285%
DELTA_2_PL1X4 | CCGT | 2024 | nonsummer | 2002-06-17 | 137474.2533 | 14258.4 | 1065 | 880 | 937200 | 0 | Individual | 14.67% | 1.521% |  |  | 14.67% | 1.521% | TRUE |  |  | 14.67% | 1.521%
DELTA_2_PL1X4 | CCGT | 2024 | summer | 2002-06-17 | 5389.3177 | 25896.585 | 765 | 880 | 673200 | 0 | Individual | 0.8006% | 3.847% |  |  | 0.8006% | 3.847% | TRUE |  |  | 0.8006% | 3.847%
DUANE_1_PL1X3 | CCGT | 2022 | nonsummer | 2005-03-24 | 43298.8817 | 2341 | 1060 | 147.8 | 156668 | 0 | Individual | 27.64% | 1.494% |  |  | 27.64% | 1.494% | TRUE |  |  | 27.64% | 1.494%
DUANE_1_PL1X3 | CCGT | 2022 | summer | 2005-03-24 | 9538.6733 | 7215.4667 | 765 | 147.8 | 113067 | 0 | Individual | 8.436% | 6.382% |  |  | 8.436% | 6.382% | TRUE |  |  | 8.436% | 6.382%
DUANE_1_PL1X3 | CCGT | 2023 | nonsummer | 2005-03-24 | 9499.5333 | 6962.6667 | 1060 | 147.8 | 156668 | 0 | Individual | 6.063% | 4.444% |  |  | 6.063% | 4.444% | TRUE |  |  | 6.063% | 4.444%
DUANE_1_PL1X3 | CCGT | 2023 | summer | 2005-03-24 | 6179.05 | 5967 | 765 | 147.8 | 113067 | 0 | Individual | 5.465% | 5.277% |  |  | 5.465% | 5.277% | TRUE |  |  | 5.465% | 5.277%
DUANE_1_PL1X3 | CCGT | 2024 | nonsummer | 2005-03-24 | 22900.29 | 0 | 1065 | 147.8 | 157407 | 0 | Individual | 14.55% | 0% |  |  | 14.55% | 0% | TRUE |  |  | 14.55% | 0%
DUANE_1_PL1X3 | CCGT | 2024 | summer | 2005-03-24 | 8181.8145 | 0 | 765 | 147.8 | 113067 | 0 | Individual | 7.236% | 0% |  |  | 7.236% | 0% | TRUE |  |  | 7.236% | 0%
ELKHIL_2_PL1X3 | CCGT | 2022 | nonsummer | 2003-07-24 | 17124.8333 | 23067.5 | 1060 | 551.7 | 584802 | 0 | Individual | 2.928% | 3.944% |  |  | 2.928% | 3.944% | TRUE |  |  | 2.928% | 3.944%
ELKHIL_2_PL1X3 | CCGT | 2022 | summer | 2003-07-24 | 20235.4167 | 38827.95 | 765 | 551.7 | 422050.5 | 0 | Individual | 4.795% | 9.2% |  |  | 4.795% | 9.2% | TRUE |  |  | 4.795% | 9.2%
ELKHIL_2_PL1X3 | CCGT | 2023 | nonsummer | 2003-07-24 | 20547.4167 | 22282.5 | 1060 | 551.7 | 584802 | 0 | Individual | 3.514% | 3.81% |  |  | 3.514% | 3.81% | TRUE |  |  | 3.514% | 3.81%
ELKHIL_2_PL1X3 | CCGT | 2023 | summer | 2003-07-24 | 2887.3333 | 39864.5 | 765 | 551.7 | 422050.5 | 0 | Individual | 0.6841% | 9.445% |  |  | 0.6841% | 9.445% | TRUE |  |  | 0.6841% | 9.445%
ELKHIL_2_PL1X3 | CCGT | 2024 | nonsummer | 2003-07-24 | 94732.4817 | 18392.7417 | 1065 | 551.7 | 587560.5 | 0 | Individual | 16.12% | 3.13% |  |  | 16.12% | 3.13% | TRUE |  |  | 16.12% | 3.13%
ELKHIL_2_PL1X3 | CCGT | 2024 | summer | 2003-07-24 | 126484.8 | 34652.5833 | 765 | 551.7 | 422050.5 | 0 | Individual | 29.97% | 8.211% |  |  | 29.97% | 8.211% | TRUE |  |  | 29.97% | 8.211%
ELSEGN_2_UN1011 | CCGT | 2022 | nonsummer | 2013-06-29 | 11094.2572 | 1412.4528 | 1060 | 274.31 | 290768.6 | 0 | Individual | 3.815% | 0.4858% |  |  | 3.815% | 0.4858% | TRUE |  |  | 3.815% | 0.4858%
ELSEGN_2_UN1011 | CCGT | 2022 | summer | 2013-06-29 | 27227.1517 | 392.7 | 765 | 274.31 | 209847.15 | 0 | Individual | 12.97% | 0.1871% |  |  | 12.97% | 0.1871% | TRUE |  |  | 12.97% | 0.1871%
ELSEGN_2_UN1011 | CCGT | 2023 | nonsummer | 2013-06-29 | 4549.7233 | 8.15 | 1060 | 274.31 | 290768.6 | 0 | Individual | 1.565% | 0.002803% |  |  | 1.565% | 0.002803% | TRUE |  |  | 1.565% | 0.002803%
ELSEGN_2_UN1011 | CCGT | 2023 | summer | 2013-06-29 | 16693.3125 | 1332.962 | 765 | 274.31 | 209847.15 | 0 | Individual | 7.955% | 0.6352% |  |  | 7.955% | 0.6352% | TRUE |  |  | 7.955% | 0.6352%
ELSEGN_2_UN1011 | CCGT | 2024 | nonsummer | 2013-06-29 | 12050.463 | 3504.1237 | 1065 | 274.31 | 292140.15 | 0 | Individual | 4.125% | 1.199% |  |  | 4.125% | 1.199% | TRUE |  |  | 4.125% | 1.199%
ELSEGN_2_UN1011 | CCGT | 2024 | summer | 2013-06-29 | 11008.9595 | 1893.779 | 765 | 274.31 | 209847.15 | 0 | Individual | 5.246% | 0.9025% |  |  | 5.246% | 0.9025% | TRUE |  |  | 5.246% | 0.9025%
ELSEGN_2_UN2021 | CCGT | 2022 | nonsummer | 2013-06-29 | 9678.473 | 0 | 1060 | 271.74 | 288044.4 | 0 | Individual | 3.36% | 0% |  |  | 3.36% | 0% | TRUE |  |  | 3.36% | 0%
ELSEGN_2_UN2021 | CCGT | 2022 | summer | 2013-06-29 | 36730.434 | 3740.954 | 765 | 271.74 | 207881.1 | 0 | Individual | 17.67% | 1.8% |  |  | 17.67% | 1.8% | TRUE |  |  | 17.67% | 1.8%
ELSEGN_2_UN2021 | CCGT | 2023 | nonsummer | 2013-06-29 | 9404.018 | 1123.1277 | 1060 | 271.74 | 288044.4 | 0 | Individual | 3.265% | 0.3899% |  |  | 3.265% | 0.3899% | TRUE |  |  | 3.265% | 0.3899%
ELSEGN_2_UN2021 | CCGT | 2023 | summer | 2013-06-29 | 5140.415 | 881.341 | 765 | 271.74 | 207881.1 | 0 | Individual | 2.473% | 0.424% |  |  | 2.473% | 0.424% | TRUE |  |  | 2.473% | 0.424%
ELSEGN_2_UN2021 | CCGT | 2024 | nonsummer | 2013-06-29 | 7102.13 | 1050.728 | 1065 | 271.74 | 289403.1 | 0 | Individual | 2.454% | 0.3631% |  |  | 2.454% | 0.3631% | TRUE |  |  | 2.454% | 0.3631%
ELSEGN_2_UN2021 | CCGT | 2024 | summer | 2013-06-29 | 26620.955 | 149.457 | 765 | 271.74 | 207881.1 | 0 | Individual | 12.81% | 0.0719% |  |  | 12.81% | 0.0719% | TRUE |  |  | 12.81% | 0.0719%
GATWAY_2_PL1X3 | CCGT | 2022 | nonsummer | 2009-01-06 | 86348.765 | 34306.92 | 1060 | 585 | 620100 | 0 | Individual | 13.92% | 5.532% |  |  | 13.92% | 5.532% | TRUE |  |  | 13.92% | 5.532%
GATWAY_2_PL1X3 | CCGT | 2022 | summer | 2009-01-06 | 14040.145 | 76814.1003 | 765 | 585 | 447525 | 0 | Individual | 3.137% | 17.16% |  |  | 3.137% | 17.16% | TRUE |  |  | 3.137% | 17.16%
GATWAY_2_PL1X3 | CCGT | 2023 | nonsummer | 2009-01-06 | 2299.4 | 41476.5833 | 1060 | 585 | 620100 | 0 | Individual | 0.3708% | 6.689% |  |  | 0.3708% | 6.689% | TRUE |  |  | 0.3708% | 6.689%
GATWAY_2_PL1X3 | CCGT | 2023 | summer | 2009-01-06 | 8423.1467 | 66672.115 | 765 | 585 | 447525 | 0 | Individual | 1.882% | 14.9% |  |  | 1.882% | 14.9% | TRUE |  |  | 1.882% | 14.9%
GATWAY_2_PL1X3 | CCGT | 2024 | nonsummer | 2009-01-06 | 2439.0667 | 45240.0083 | 1065 | 585 | 623025 | 0 | Individual | 0.3915% | 7.261% |  |  | 0.3915% | 7.261% | TRUE |  |  | 0.3915% | 7.261%
GATWAY_2_PL1X3 | CCGT | 2024 | summer | 2009-01-06 | 294.3 | 70724.5557 | 765 | 585 | 447525 | 0 | Individual | 0.06576% | 15.8% |  |  | 0.06576% | 15.8% | TRUE |  |  | 0.06576% | 15.8%
GILROY_1_UNIT | CCGT | 2022 | nonsummer | 1987-01-01 | 5311.9167 | 9049 | 1060 | 120 | 127200 | 0 | Individual | 4.176% | 7.114% |  |  | 4.176% | 7.114% | TRUE |  |  | 4.176% | 7.114%
GILROY_1_UNIT | CCGT | 2022 | summer | 1987-01-01 | 4756.6167 | 8737.3667 | 765 | 120 | 91800 | 0 | Individual | 5.181% | 9.518% |  |  | 5.181% | 9.518% | TRUE |  |  | 5.181% | 9.518%
GILROY_1_UNIT | CCGT | 2023 | nonsummer | 1987-01-01 | 21165 | 6084 | 1060 | 120 | 127200 | 0 | Individual | 16.64% | 4.783% |  |  | 16.64% | 4.783% | TRUE |  |  | 16.64% | 4.783%
GILROY_1_UNIT | CCGT | 2023 | summer | 1987-01-01 | 49.0885 | 7461.7 | 765 | 120 | 91800 | 0 | Individual | 0.05347% | 8.128% |  |  | 0.05347% | 8.128% | TRUE |  |  | 0.05347% | 8.128%
GILROY_1_UNIT | CCGT | 2024 | nonsummer | 1987-01-01 | 30618 | 6094 | 1065 | 120 | 127800 | 0 | Individual | 23.96% | 4.768% |  |  | 23.96% | 4.768% | TRUE |  |  | 23.96% | 4.768%
GILROY_1_UNIT | CCGT | 2024 | summer | 1987-01-01 | 958.9 | 9233.3 | 765 | 120 | 91800 | 0 | Individual | 1.045% | 10.06% |  |  | 1.045% | 10.06% | TRUE |  |  | 1.045% | 10.06%
GLNARM_2_UNIT 5 | CCGT | 2022 | nonsummer | 2016-12-20 | 6472.9572 | 0 | 1060 | 65.81 | 69758.6 | 0 | Individual | 9.279% | 0% |  |  | 9.279% | 0% | TRUE |  |  | 9.279% | 0%
GLNARM_2_UNIT 5 | CCGT | 2022 | summer | 2016-12-20 | 936.8732 | 0 | 765 | 65.81 | 50344.65 | 0 | Individual | 1.861% | 0% |  |  | 1.861% | 0% | TRUE |  |  | 1.861% | 0%
GLNARM_2_UNIT 5 | CCGT | 2023 | nonsummer | 2016-12-20 | 11814.1478 | 0 | 1060 | 65.81 | 69758.6 | 0 | Individual | 16.94% | 0% |  |  | 16.94% | 0% | TRUE |  |  | 16.94% | 0%
GLNARM_2_UNIT 5 | CCGT | 2023 | summer | 2016-12-20 | 591.2945 | 2.3715 | 765 | 65.81 | 50344.65 | 0 | Individual | 1.174% | 0.004711% |  |  | 1.174% | 0.004711% | TRUE |  |  | 1.174% | 0.004711%
GLNARM_2_UNIT 5 | CCGT | 2024 | nonsummer | 2016-12-20 | 65151.9 | 0 | 1065 | 65.81 | 70087.65 | 0 | Individual | 92.96% | 0% |  |  | 92.96% | 0% | TRUE |  |  | 92.96% | 0%
GLNARM_2_UNIT 5 | CCGT | 2024 | summer | 2016-12-20 | 50344.65 | 0 | 765 | 65.81 | 50344.65 | 0 | Individual | 100% | 0% |  |  | 100% | 0% | TRUE |  |  | 100% | 0%
GWFPWR_1_LDCTG1 | CCGT | 2022 | nonsummer | 2025-07-25 | 0 | 0 | 0 | 55.3 | 0 | 1060 | Group |  |  | 8.267% | 1.874% | 8.267% | 1.874% | TRUE | 8.267% | 1.874% | 8.267% | 1.874%
GWFPWR_1_LDCTG1 | CCGT | 2022 | summer | 2025-07-25 | 0 | 0 | 0 | 55.3 | 0 | 765 | Group |  |  | 5.244% | 5.898% | 5.244% | 5.898% | TRUE | 5.244% | 5.898% | 5.244% | 5.898%
GWFPWR_1_LDCTG1 | CCGT | 2023 | nonsummer | 2025-07-25 | 0 | 0 | 0 | 55.3 | 0 | 1060 | Group |  |  | 6.533% | 1.873% | 6.533% | 1.873% | TRUE | 6.533% | 1.873% | 6.533% | 1.873%
GWFPWR_1_LDCTG1 | CCGT | 2023 | summer | 2025-07-25 | 0 | 0 | 0 | 55.3 | 0 | 765 | Group |  |  | 6.183% | 3.935% | 6.183% | 3.935% | TRUE | 6.183% | 3.935% | 6.183% | 3.935%
GWFPWR_1_LDCTG1 | CCGT | 2024 | nonsummer | 2025-07-25 | 0 | 0 | 0 | 55.3 | 0 | 1065 | Group |  |  | 7.078% | 1.639% | 7.078% | 1.639% | TRUE | 7.078% | 1.639% | 7.078% | 1.639%
GWFPWR_1_LDCTG1 | CCGT | 2024 | summer | 2025-07-25 | 0 | 0 | 0 | 55.3 | 0 | 765 | Group |  |  | 4.32% | 4.144% | 4.32% | 4.144% | TRUE | 4.32% | 4.144% | 4.32% | 4.144%
GWFPWR_1_LDCTG2 | CCGT | 2022 | nonsummer | 2025-07-25 | 0 | 0 | 0 | 55.3 | 0 | 1060 | Group |  |  | 8.267% | 1.874% | 8.267% | 1.874% | TRUE | 8.267% | 1.874% | 8.267% | 1.874%
GWFPWR_1_LDCTG2 | CCGT | 2022 | summer | 2025-07-25 | 0 | 0 | 0 | 55.3 | 0 | 765 | Group |  |  | 5.244% | 5.898% | 5.244% | 5.898% | TRUE | 5.244% | 5.898% | 5.244% | 5.898%
GWFPWR_1_LDCTG2 | CCGT | 2023 | nonsummer | 2025-07-25 | 0 | 0 | 0 | 55.3 | 0 | 1060 | Group |  |  | 6.533% | 1.873% | 6.533% | 1.873% | TRUE | 6.533% | 1.873% | 6.533% | 1.873%
GWFPWR_1_LDCTG2 | CCGT | 2023 | summer | 2025-07-25 | 0 | 0 | 0 | 55.3 | 0 | 765 | Group |  |  | 6.183% | 3.935% | 6.183% | 3.935% | TRUE | 6.183% | 3.935% | 6.183% | 3.935%
GWFPWR_1_LDCTG2 | CCGT | 2024 | nonsummer | 2025-07-25 | 0 | 0 | 0 | 55.3 | 0 | 1065 | Group |  |  | 7.078% | 1.639% | 7.078% | 1.639% | TRUE | 7.078% | 1.639% | 7.078% | 1.639%
GWFPWR_1_LDCTG2 | CCGT | 2024 | summer | 2025-07-25 | 0 | 0 | 0 | 55.3 | 0 | 765 | Group |  |  | 4.32% | 4.144% | 4.32% | 4.144% | TRUE | 4.32% | 4.144% | 4.32% | 4.144%
HARBGN_7_UNITS | CCGT | 2022 | nonsummer | 2001-06-14 | 2997.775 | 0 | 1060 | 109.01 | 115550.6 | 0 | Individual | 2.594% | 0% |  |  | 2.594% | 0% | TRUE |  |  | 2.594% | 0%
HARBGN_7_UNITS | CCGT | 2022 | summer | 2001-06-14 | 2635.4338 | 10314.2 | 765 | 109.01 | 83392.65 | 0 | Individual | 3.16% | 12.37% |  |  | 3.16% | 12.37% | TRUE |  |  | 3.16% | 12.37%
HARBGN_7_UNITS | CCGT | 2023 | nonsummer | 2001-06-14 | 436.04 | 0 | 1060 | 109.01 | 115550.6 | 0 | Individual | 0.3774% | 0% |  |  | 0.3774% | 0% | TRUE |  |  | 0.3774% | 0%
HARBGN_7_UNITS | CCGT | 2023 | summer | 2001-06-14 | 1860.5612 | 6140.9 | 765 | 109.01 | 83392.65 | 0 | Individual | 2.231% | 7.364% |  |  | 2.231% | 7.364% | TRUE |  |  | 2.231% | 7.364%
HARBGN_7_UNITS | CCGT | 2024 | nonsummer | 2001-06-14 | 26359.193 | 0 | 1065 | 109.01 | 116095.65 | 0 | Individual | 22.7% | 0% |  |  | 22.7% | 0% | TRUE |  |  | 22.7% | 0%
HARBGN_7_UNITS | CCGT | 2024 | summer | 2001-06-14 | 26296.7143 | 7128.75 | 765 | 109.01 | 83392.65 | 0 | Individual | 31.53% | 8.548% |  |  | 31.53% | 8.548% | TRUE |  |  | 31.53% | 8.548%
HIDSRT_2_UNITS | CCGT | 2022 | nonsummer | 2003-04-21 | 12359.125 | 47457.4167 | 1060 | 850 | 901000 | 0 | Individual | 1.372% | 5.267% |  |  | 1.372% | 5.267% | TRUE |  |  | 1.372% | 5.267%
HIDSRT_2_UNITS | CCGT | 2022 | summer | 2003-04-21 | 6299.3 | 70854.4 | 765 | 850 | 650250 | 0 | Individual | 0.9688% | 10.9% |  |  | 0.9688% | 10.9% | TRUE |  |  | 0.9688% | 10.9%
HIDSRT_2_UNITS | CCGT | 2023 | nonsummer | 2003-04-21 | 131982.5 | 15160.1667 | 1060 | 850 | 901000 | 0 | Individual | 14.65% | 1.683% |  |  | 14.65% | 1.683% | TRUE |  |  | 14.65% | 1.683%
HIDSRT_2_UNITS | CCGT | 2023 | summer | 2003-04-21 | 47628.5 | 2651.4 | 765 | 850 | 650250 | 0 | Individual | 7.325% | 0.4078% |  |  | 7.325% | 0.4078% | TRUE |  |  | 7.325% | 0.4078%
HIDSRT_2_UNITS | CCGT | 2024 | nonsummer | 2003-04-21 | 52656.1167 | 1303.6 | 1065 | 850 | 905250 | 0 | Individual | 5.817% | 0.144% |  |  | 5.817% | 0.144% | TRUE |  |  | 5.817% | 0.144%
HIDSRT_2_UNITS | CCGT | 2024 | summer | 2003-04-21 | 21730.56 | 453.6167 | 765 | 850 | 650250 | 0 | Individual | 3.342% | 0.06976% |  |  | 3.342% | 0.06976% | TRUE |  |  | 3.342% | 0.06976%
HNTGBH_2_PL1X3 | CCGT | 2022 | nonsummer | 2020-02-04 | 58640.0165 | 87.1333 | 1060 | 673.8 | 714228 | 0 | Individual | 8.21% | 0.0122% |  |  | 8.21% | 0.0122% | TRUE |  |  | 8.21% | 0.0122%
HNTGBH_2_PL1X3 | CCGT | 2022 | summer | 2020-02-04 | 434.3333 | 9053.5333 | 765 | 673.8 | 515457 | 0 | Individual | 0.08426% | 1.756% |  |  | 0.08426% | 1.756% | TRUE |  |  | 0.08426% | 1.756%
HNTGBH_2_PL1X3 | CCGT | 2023 | nonsummer | 2020-02-04 | 17854.5045 | 69 | 1060 | 673.8 | 714228 | 0 | Individual | 2.5% | 0.009661% |  |  | 2.5% | 0.009661% | TRUE |  |  | 2.5% | 0.009661%
HNTGBH_2_PL1X3 | CCGT | 2023 | summer | 2020-02-04 | 44288.657 | 9526.8517 | 765 | 673.8 | 515457 | 0 | Individual | 8.592% | 1.848% |  |  | 8.592% | 1.848% | TRUE |  |  | 8.592% | 1.848%
HNTGBH_2_PL1X3 | CCGT | 2024 | nonsummer | 2020-02-04 | 1818.8445 | 210.6633 | 1065 | 673.8 | 717597 | 0 | Individual | 0.2535% | 0.02936% |  |  | 0.2535% | 0.02936% | TRUE |  |  | 0.2535% | 0.02936%
HNTGBH_2_PL1X3 | CCGT | 2024 | summer | 2020-02-04 | 7413.1465 | 2216.5567 | 765 | 673.8 | 515457 | 0 | Individual | 1.438% | 0.43% |  |  | 1.438% | 0.43% | TRUE |  |  | 1.438% | 0.43%
LAPLMA_2_UNIT 1 | CCGT | 2022 | nonsummer | 2003-01-10 | 3137.4 | 10809 | 1060 | 267 | 283020 | 0 | Individual | 1.109% | 3.819% |  |  | 1.109% | 3.819% | TRUE |  |  | 1.109% | 3.819%
LAPLMA_2_UNIT 1 | CCGT | 2022 | summer | 2003-01-10 | 8707.1 | 10360.0833 | 765 | 267 | 204255 | 0 | Individual | 4.263% | 5.072% |  |  | 4.263% | 5.072% | TRUE |  |  | 4.263% | 5.072%
LAPLMA_2_UNIT 1 | CCGT | 2023 | nonsummer | 2003-01-10 | 43808.65 | 6347.8833 | 1060 | 267 | 283020 | 0 | Individual | 15.48% | 2.243% |  |  | 15.48% | 2.243% | TRUE |  |  | 15.48% | 2.243%
LAPLMA_2_UNIT 1 | CCGT | 2023 | summer | 2003-01-10 | 11961.2167 | 9331 | 765 | 267 | 204255 | 0 | Individual | 5.856% | 4.568% |  |  | 5.856% | 4.568% | TRUE |  |  | 5.856% | 4.568%
LAPLMA_2_UNIT 1 | CCGT | 2024 | nonsummer | 2003-01-10 | 21005.6333 | 10170.5 | 1065 | 267 | 284355 | 0 | Individual | 7.387% | 3.577% |  |  | 7.387% | 3.577% | TRUE |  |  | 7.387% | 3.577%
LAPLMA_2_UNIT 1 | CCGT | 2024 | summer | 2003-01-10 | 6889.2167 | 10951 | 765 | 267 | 204255 | 0 | Individual | 3.373% | 5.361% |  |  | 3.373% | 5.361% | TRUE |  |  | 3.373% | 5.361%
LAPLMA_2_UNIT 2 | CCGT | 2022 | nonsummer | 2003-03-05 | 13174.443 | 8326.5 | 1060 | 266 | 281960 | 0 | Individual | 4.672% | 2.953% |  |  | 4.672% | 2.953% | TRUE |  |  | 4.672% | 2.953%
LAPLMA_2_UNIT 2 | CCGT | 2022 | summer | 2003-03-05 | 5416.2333 | 12613 | 765 | 266 | 203490 | 0 | Individual | 2.662% | 6.198% |  |  | 2.662% | 6.198% | TRUE |  |  | 2.662% | 6.198%
LAPLMA_2_UNIT 2 | CCGT | 2023 | nonsummer | 2003-03-05 | 21533.0667 | 9354 | 1060 | 266 | 281960 | 0 | Individual | 7.637% | 3.317% |  |  | 7.637% | 3.317% | TRUE |  |  | 7.637% | 3.317%
LAPLMA_2_UNIT 2 | CCGT | 2023 | summer | 2003-03-05 | 5041.6833 | 5450 | 765 | 266 | 203490 | 0 | Individual | 2.478% | 2.678% |  |  | 2.478% | 2.678% | TRUE |  |  | 2.478% | 2.678%
LAPLMA_2_UNIT 2 | CCGT | 2024 | nonsummer | 2003-03-05 | 21194.7167 | 10978.5 | 1065 | 266 | 283290 | 0 | Individual | 7.482% | 3.875% |  |  | 7.482% | 3.875% | TRUE |  |  | 7.482% | 3.875%
LAPLMA_2_UNIT 2 | CCGT | 2024 | summer | 2003-03-05 | 11576.9333 | 9878 | 765 | 266 | 203490 | 0 | Individual | 5.689% | 4.854% |  |  | 5.689% | 4.854% | TRUE |  |  | 5.689% | 4.854%
LAPLMA_2_UNIT 3 | CCGT | 2022 | nonsummer | 2003-01-13 | 6026.3167 | 10834.7667 | 1060 | 266 | 281960 | 0 | Individual | 2.137% | 3.843% |  |  | 2.137% | 3.843% | TRUE |  |  | 2.137% | 3.843%
LAPLMA_2_UNIT 3 | CCGT | 2022 | summer | 2003-01-13 | 8607.7333 | 9264.4333 | 765 | 266 | 203490 | 0 | Individual | 4.23% | 4.553% |  |  | 4.23% | 4.553% | TRUE |  |  | 4.23% | 4.553%
LAPLMA_2_UNIT 3 | CCGT | 2023 | nonsummer | 2003-01-13 | 16649.3283 | 9938 | 1060 | 266 | 281960 | 0 | Individual | 5.905% | 3.525% |  |  | 5.905% | 3.525% | TRUE |  |  | 5.905% | 3.525%
LAPLMA_2_UNIT 3 | CCGT | 2023 | summer | 2003-01-13 | 1386.2333 | 9742 | 765 | 266 | 203490 | 0 | Individual | 0.6812% | 4.787% |  |  | 0.6812% | 4.787% | TRUE |  |  | 0.6812% | 4.787%
LAPLMA_2_UNIT 3 | CCGT | 2024 | nonsummer | 2003-01-13 | 17589.1833 | 14566 | 1065 | 266 | 283290 | 0 | Individual | 6.209% | 5.142% |  |  | 6.209% | 5.142% | TRUE |  |  | 6.209% | 5.142%
LAPLMA_2_UNIT 3 | CCGT | 2024 | summer | 2003-01-13 | 14428.4468 | 11207 | 765 | 266 | 203490 | 0 | Individual | 7.09% | 5.507% |  |  | 7.09% | 5.507% | TRUE |  |  | 7.09% | 5.507%
LAPLMA_2_UNIT 4 | CCGT | 2022 | nonsummer | 2003-03-05 | 14090.3167 | 16576 | 1060 | 267 | 283020 | 0 | Individual | 4.979% | 5.857% |  |  | 4.979% | 5.857% | TRUE |  |  | 4.979% | 5.857%
LAPLMA_2_UNIT 4 | CCGT | 2022 | summer | 2003-03-05 | 4429.45 | 14525.6667 | 765 | 267 | 204255 | 0 | Individual | 2.169% | 7.112% |  |  | 2.169% | 7.112% | TRUE |  |  | 2.169% | 7.112%
LAPLMA_2_UNIT 4 | CCGT | 2023 | nonsummer | 2003-03-05 | 20600.4488 | 10878 | 1060 | 267 | 283020 | 0 | Individual | 7.279% | 3.844% |  |  | 7.279% | 3.844% | TRUE |  |  | 7.279% | 3.844%
LAPLMA_2_UNIT 4 | CCGT | 2023 | summer | 2003-03-05 | 78857.6833 | 7419.1667 | 765 | 267 | 204255 | 0 | Individual | 38.61% | 3.632% |  |  | 38.61% | 3.632% | TRUE |  |  | 38.61% | 3.632%
LAPLMA_2_UNIT 4 | CCGT | 2024 | nonsummer | 2003-03-05 | 17697.8833 | 13768 | 1065 | 267 | 284355 | 0 | Individual | 6.224% | 4.842% |  |  | 6.224% | 4.842% | TRUE |  |  | 6.224% | 4.842%
LAPLMA_2_UNIT 4 | CCGT | 2024 | summer | 2003-03-05 | 26868.5 | 10452.2667 | 765 | 267 | 204255 | 0 | Individual | 13.15% | 5.117% |  |  | 13.15% | 5.117% | TRUE |  |  | 13.15% | 5.117%
LAROA2_2_UNITA1 | CCGT | 2022 | nonsummer | 2003-07-22 | 9222.1333 | 1402 | 1060 | 322 | 341320 | 0 | Individual | 2.702% | 0.4108% |  |  | 2.702% | 0.4108% | TRUE |  |  | 2.702% | 0.4108%
LAROA2_2_UNITA1 | CCGT | 2022 | summer | 2003-07-22 | 13876.3833 | 10977.5667 | 765 | 322 | 246330 | 0 | Individual | 5.633% | 4.456% |  |  | 5.633% | 4.456% | TRUE |  |  | 5.633% | 4.456%
LAROA2_2_UNITA1 | CCGT | 2023 | nonsummer | 2003-07-22 | 13755.5 | 8971.0833 | 1060 | 322 | 341320 | 0 | Individual | 4.03% | 2.628% |  |  | 4.03% | 2.628% | TRUE |  |  | 4.03% | 2.628%
LAROA2_2_UNITA1 | CCGT | 2023 | summer | 2003-07-22 | 9484.4167 | 17001.9167 | 765 | 322 | 246330 | 0 | Individual | 3.85% | 6.902% |  |  | 3.85% | 6.902% | TRUE |  |  | 3.85% | 6.902%
LAROA2_2_UNITA1 | CCGT | 2024 | nonsummer | 2003-07-22 | 22632.4333 | 8673 | 1065 | 322 | 342930 | 0 | Individual | 6.6% | 2.529% |  |  | 6.6% | 2.529% | TRUE |  |  | 6.6% | 2.529%
LAROA2_2_UNITA1 | CCGT | 2024 | summer | 2003-07-22 | 13894.0533 | 16541.5833 | 765 | 322 | 246330 | 0 | Individual | 5.64% | 6.715% |  |  | 5.64% | 6.715% | TRUE |  |  | 5.64% | 6.715%
LEBECS_2_UNITS | CCGT | 2022 | nonsummer | 2005-05-04 | 122182.754 | 3396.706 | 1060 | 799.47 | 847438.2 | 0 | Individual | 14.42% | 0.4008% |  |  | 14.42% | 0.4008% | TRUE |  |  | 14.42% | 0.4008%
LEBECS_2_UNITS | CCGT | 2022 | summer | 2005-05-04 | 86742.7835 | 14973.7967 | 765 | 799.47 | 611594.55 | 0 | Individual | 14.18% | 2.448% |  |  | 14.18% | 2.448% | TRUE |  |  | 14.18% | 2.448%
LEBECS_2_UNITS | CCGT | 2023 | nonsummer | 2005-05-04 | 70346.837 | 11222.0032 | 1060 | 799.47 | 847438.2 | 0 | Individual | 8.301% | 1.324% |  |  | 8.301% | 1.324% | TRUE |  |  | 8.301% | 1.324%
LEBECS_2_UNITS | CCGT | 2023 | summer | 2005-05-04 | 40962.5617 | 11818.9978 | 765 | 799.47 | 611594.55 | 0 | Individual | 6.698% | 1.932% |  |  | 6.698% | 1.932% | TRUE |  |  | 6.698% | 1.932%
LEBECS_2_UNITS | CCGT | 2024 | nonsummer | 2005-05-04 | 54750.0563 | 4378.3217 | 1065 | 799.47 | 851435.55 | 0 | Individual | 6.43% | 0.5142% |  |  | 6.43% | 0.5142% | TRUE |  |  | 6.43% | 0.5142%
LEBECS_2_UNITS | CCGT | 2024 | summer | 2005-05-04 | 24519.4457 | 16481.2253 | 765 | 799.47 | 611594.55 | 0 | Individual | 4.009% | 2.695% |  |  | 4.009% | 2.695% | TRUE |  |  | 4.009% | 2.695%
LECEF_1_UNITS | CCGT | 2022 | nonsummer | 2013-07-31 | 5379.48 | 11178.24 | 1060 | 309.84 | 328430.4 | 0 | Individual | 1.638% | 3.404% |  |  | 1.638% | 3.404% | TRUE |  |  | 1.638% | 3.404%
LECEF_1_UNITS | CCGT | 2022 | summer | 2013-07-31 | 9209.3467 | 14424.52 | 765 | 309.84 | 237027.6 | 0 | Individual | 3.885% | 6.086% |  |  | 3.885% | 6.086% | TRUE |  |  | 3.885% | 6.086%
LECEF_1_UNITS | CCGT | 2023 | nonsummer | 2013-07-31 | 3114.3467 | 9229.4867 | 1060 | 309.84 | 328430.4 | 0 | Individual | 0.9483% | 2.81% |  |  | 0.9483% | 2.81% | TRUE |  |  | 0.9483% | 2.81%
LECEF_1_UNITS | CCGT | 2023 | summer | 2013-07-31 | 56527.2092 | 8037.7423 | 765 | 309.84 | 237027.6 | 0 | Individual | 23.85% | 3.391% |  |  | 23.85% | 3.391% | TRUE |  |  | 23.85% | 3.391%
LECEF_1_UNITS | CCGT | 2024 | nonsummer | 2013-07-31 | 2105.9353 | 13210.432 | 1065 | 309.84 | 329979.6 | 0 | Individual | 0.6382% | 4.003% |  |  | 0.6382% | 4.003% | TRUE |  |  | 0.6382% | 4.003%
LECEF_1_UNITS | CCGT | 2024 | summer | 2013-07-31 | 484.9667 | 14135.6287 | 765 | 309.84 | 237027.6 | 0 | Individual | 0.2046% | 5.964% |  |  | 0.2046% | 5.964% | TRUE |  |  | 0.2046% | 5.964%
LGHTHP_6_ICEGEN | CCGT | 2022 | nonsummer | 1989-12-22 | 0 | 0 | 1060 | 48 | 50880 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
LGHTHP_6_ICEGEN | CCGT | 2022 | summer | 1989-12-22 | 5040.8 | 104 | 765 | 48 | 36720 | 0 | Individual | 13.73% | 0.2832% |  |  | 13.73% | 0.2832% | TRUE |  |  | 13.73% | 0.2832%
LGHTHP_6_ICEGEN | CCGT | 2023 | nonsummer | 1989-12-22 | 15019.98 | 0 | 1060 | 48 | 50880 | 0 | Individual | 29.52% | 0% |  |  | 29.52% | 0% | TRUE |  |  | 29.52% | 0%
LGHTHP_6_ICEGEN | CCGT | 2023 | summer | 1989-12-22 | 1884 | 0 | 765 | 48 | 36720 | 0 | Individual | 5.131% | 0% |  |  | 5.131% | 0% | TRUE |  |  | 5.131% | 0%
LGHTHP_6_ICEGEN | CCGT | 2024 | nonsummer | 1989-12-22 | 6164 | 0 | 1065 | 48 | 51120 | 0 | Individual | 12.06% | 0% |  |  | 12.06% | 0% | TRUE |  |  | 12.06% | 0%
LGHTHP_6_ICEGEN | CCGT | 2024 | summer | 1989-12-22 | 15050.4 | 0 | 765 | 48 | 36720 | 0 | Individual | 40.99% | 0% |  |  | 40.99% | 0% | TRUE |  |  | 40.99% | 0%
LMEC_1_PL1X3 | CCGT | 2022 | nonsummer | 2001-06-09 | 33382.6333 | 15067.15 | 1060 | 580 | 614800 | 0 | Individual | 5.43% | 2.451% |  |  | 5.43% | 2.451% | TRUE |  |  | 5.43% | 2.451%
LMEC_1_PL1X3 | CCGT | 2022 | summer | 2001-06-09 | 23380.9667 | 19576.6167 | 765 | 580 | 443700 | 0 | Individual | 5.27% | 4.412% |  |  | 5.27% | 4.412% | TRUE |  |  | 5.27% | 4.412%
LMEC_1_PL1X3 | CCGT | 2023 | nonsummer | 2001-06-09 | 77128.5 | 14463.59 | 1060 | 580 | 614800 | 0 | Individual | 12.55% | 2.353% |  |  | 12.55% | 2.353% | TRUE |  |  | 12.55% | 2.353%
LMEC_1_PL1X3 | CCGT | 2023 | summer | 2001-06-09 | 44025.95 | 16536.8167 | 765 | 580 | 443700 | 0 | Individual | 9.922% | 3.727% |  |  | 9.922% | 3.727% | TRUE |  |  | 9.922% | 3.727%
LMEC_1_PL1X3 | CCGT | 2024 | nonsummer | 2001-06-09 | 40762.21 | 9080.3047 | 1065 | 580 | 617700 | 0 | Individual | 6.599% | 1.47% |  |  | 6.599% | 1.47% | TRUE |  |  | 6.599% | 1.47%
LMEC_1_PL1X3 | CCGT | 2024 | summer | 2001-06-09 | 16007.5 | 10910.1333 | 765 | 580 | 443700 | 0 | Individual | 3.608% | 2.459% |  |  | 3.608% | 2.459% | TRUE |  |  | 3.608% | 2.459%
LODIEC_2_PL1X2 | CCGT | 2022 | nonsummer | 2012-11-27 | 2003.03 | 11657.1 | 1060 | 302.58 | 320734.8 | 0 | Individual | 0.6245% | 3.634% |  |  | 0.6245% | 3.634% | TRUE |  |  | 0.6245% | 3.634%
LODIEC_2_PL1X2 | CCGT | 2022 | summer | 2012-11-27 | 86542.1037 | 30711.1067 | 765 | 302.58 | 231473.7 | 0 | Individual | 37.39% | 13.27% |  |  | 37.39% | 13.27% | TRUE |  |  | 37.39% | 13.27%
LODIEC_2_PL1X2 | CCGT | 2023 | nonsummer | 2012-11-27 | 19208 | 16795.9 | 1060 | 302.58 | 320734.8 | 0 | Individual | 5.989% | 5.237% |  |  | 5.989% | 5.237% | TRUE |  |  | 5.989% | 5.237%
LODIEC_2_PL1X2 | CCGT | 2023 | summer | 2012-11-27 | 13042.1947 | 20561.3 | 765 | 302.58 | 231473.7 | 0 | Individual | 5.634% | 8.883% |  |  | 5.634% | 8.883% | TRUE |  |  | 5.634% | 8.883%
LODIEC_2_PL1X2 | CCGT | 2024 | nonsummer | 2012-11-27 | 14374.164 | 15874.7 | 1065 | 302.58 | 322247.7 | 0 | Individual | 4.461% | 4.926% |  |  | 4.461% | 4.926% | TRUE |  |  | 4.461% | 4.926%
LODIEC_2_PL1X2 | CCGT | 2024 | summer | 2012-11-27 | 2484.955 | 21482.8 | 765 | 302.58 | 231473.7 | 0 | Individual | 1.074% | 9.281% |  |  | 1.074% | 9.281% | TRUE |  |  | 1.074% | 9.281%
METEC_2_PL1X3 | CCGT | 2022 | nonsummer | 2005-05-27 | 117761.5967 | 6623.0167 | 1060 | 597.05 | 632873 | 0 | Individual | 18.61% | 1.047% |  |  | 18.61% | 1.047% | TRUE |  |  | 18.61% | 1.047%
METEC_2_PL1X3 | CCGT | 2022 | summer | 2005-05-27 | 21114.0357 | 19706.5267 | 765 | 597.05 | 456743.25 | 0 | Individual | 4.623% | 4.315% |  |  | 4.623% | 4.315% | TRUE |  |  | 4.623% | 4.315%
METEC_2_PL1X3 | CCGT | 2023 | nonsummer | 2005-05-27 | 200989.6748 | 10239.5817 | 1060 | 597.05 | 632873 | 0 | Individual | 31.76% | 1.618% |  |  | 31.76% | 1.618% | TRUE |  |  | 31.76% | 1.618%
METEC_2_PL1X3 | CCGT | 2023 | summer | 2005-05-27 | 75560.4298 | 10874.3553 | 765 | 597.05 | 456743.25 | 0 | Individual | 16.54% | 2.381% |  |  | 16.54% | 2.381% | TRUE |  |  | 16.54% | 2.381%
METEC_2_PL1X3 | CCGT | 2024 | nonsummer | 2005-05-27 | 13692.2333 | 11264.3167 | 1065 | 597.05 | 635858.25 | 0 | Individual | 2.153% | 1.772% |  |  | 2.153% | 1.772% | TRUE |  |  | 2.153% | 1.772%
METEC_2_PL1X3 | CCGT | 2024 | summer | 2005-05-27 | 20369.2467 | 14557.05 | 765 | 597.05 | 456743.25 | 0 | Individual | 4.46% | 3.187% |  |  | 4.46% | 3.187% | TRUE |  |  | 4.46% | 3.187%
MOSSLD_2_PSP1 | CCGT | 2022 | nonsummer | 2002-07-01 | 21128.5833 | 490.25 | 1060 | 510 | 540600 | 0 | Individual | 3.908% | 0.09069% |  |  | 3.908% | 0.09069% | TRUE |  |  | 3.908% | 0.09069%
MOSSLD_2_PSP1 | CCGT | 2022 | summer | 2002-07-01 | 12584.3333 | 1671.7667 | 765 | 510 | 390150 | 0 | Individual | 3.226% | 0.4285% |  |  | 3.226% | 0.4285% | TRUE |  |  | 3.226% | 0.4285%
MOSSLD_2_PSP1 | CCGT | 2023 | nonsummer | 2002-07-01 | 8635.0333 | 324.1333 | 1060 | 510 | 540600 | 0 | Individual | 1.597% | 0.05996% |  |  | 1.597% | 0.05996% | TRUE |  |  | 1.597% | 0.05996%
MOSSLD_2_PSP1 | CCGT | 2023 | summer | 2002-07-01 | 5904.8833 | 2524.9667 | 765 | 510 | 390150 | 0 | Individual | 1.513% | 0.6472% |  |  | 1.513% | 0.6472% | TRUE |  |  | 1.513% | 0.6472%
MOSSLD_2_PSP1 | CCGT | 2024 | nonsummer | 2002-07-01 | 14262.85 | 395.7167 | 1065 | 510 | 543150 | 0 | Individual | 2.626% | 0.07286% |  |  | 2.626% | 0.07286% | TRUE |  |  | 2.626% | 0.07286%
MOSSLD_2_PSP1 | CCGT | 2024 | summer | 2002-07-01 | 4618.3 | 1260.0333 | 765 | 510 | 390150 | 0 | Individual | 1.184% | 0.323% |  |  | 1.184% | 0.323% | TRUE |  |  | 1.184% | 0.323%
MOSSLD_2_PSP2 | CCGT | 2022 | nonsummer | 2002-07-11 | 14168.9167 | 178.6833 | 1060 | 510 | 540600 | 0 | Individual | 2.621% | 0.03305% |  |  | 2.621% | 0.03305% | TRUE |  |  | 2.621% | 0.03305%
MOSSLD_2_PSP2 | CCGT | 2022 | summer | 2002-07-11 | 5929.25 | 1494.6167 | 765 | 510 | 390150 | 0 | Individual | 1.52% | 0.3831% |  |  | 1.52% | 0.3831% | TRUE |  |  | 1.52% | 0.3831%
MOSSLD_2_PSP2 | CCGT | 2023 | nonsummer | 2002-07-11 | 9943.5 | 504.9333 | 1060 | 510 | 540600 | 0 | Individual | 1.839% | 0.0934% |  |  | 1.839% | 0.0934% | TRUE |  |  | 1.839% | 0.0934%
MOSSLD_2_PSP2 | CCGT | 2023 | summer | 2002-07-11 | 2525 | 1018.8833 | 765 | 510 | 390150 | 0 | Individual | 0.6472% | 0.2612% |  |  | 0.6472% | 0.2612% | TRUE |  |  | 0.6472% | 0.2612%
MOSSLD_2_PSP2 | CCGT | 2024 | nonsummer | 2002-07-11 | 61557.5167 | 321.0167 | 1065 | 510 | 543150 | 0 | Individual | 11.33% | 0.0591% |  |  | 11.33% | 0.0591% | TRUE |  |  | 11.33% | 0.0591%
MOSSLD_2_PSP2 | CCGT | 2024 | summer | 2002-07-11 | 7493.5667 | 1200.6833 | 765 | 510 | 390150 | 0 | Individual | 1.921% | 0.3077% |  |  | 1.921% | 0.3077% | TRUE |  |  | 1.921% | 0.3077%
MRCHNT_2_PL1X3 | CCGT | 2022 | nonsummer | 2012-06-18 | 1667.0833 | 23965.7137 | 1060 | 494.58 | 524254.8 | 0 | Individual | 0.318% | 4.571% |  |  | 0.318% | 4.571% | TRUE |  |  | 0.318% | 4.571%
MRCHNT_2_PL1X3 | CCGT | 2022 | summer | 2012-06-18 | 3265 | 71801.8667 | 765 | 494.58 | 378353.7 | 0 | Individual | 0.8629% | 18.98% |  |  | 0.8629% | 18.98% | TRUE |  |  | 0.8629% | 18.98%
MRCHNT_2_PL1X3 | CCGT | 2023 | nonsummer | 2012-06-18 | 6714.2167 | 26471.7667 | 1060 | 494.58 | 524254.8 | 0 | Individual | 1.281% | 5.049% |  |  | 1.281% | 5.049% | TRUE |  |  | 1.281% | 5.049%
MRCHNT_2_PL1X3 | CCGT | 2023 | summer | 2012-06-18 | 18973 | 47602.6333 | 765 | 494.58 | 378353.7 | 0 | Individual | 5.015% | 12.58% |  |  | 5.015% | 12.58% | TRUE |  |  | 5.015% | 12.58%
MRCHNT_2_PL1X3 | CCGT | 2024 | nonsummer | 2012-06-18 | 45320.15 | 10260.4667 | 1065 | 494.58 | 526727.7 | 0 | Individual | 8.604% | 1.948% |  |  | 8.604% | 1.948% | TRUE |  |  | 8.604% | 1.948%
MRCHNT_2_PL1X3 | CCGT | 2024 | summer | 2012-06-18 | 5615 | 53039.9 | 765 | 494.58 | 378353.7 | 0 | Individual | 1.484% | 14.02% |  |  | 1.484% | 14.02% | TRUE |  |  | 1.484% | 14.02%
OTMESA_2_PL1X3 | CCGT | 2022 | nonsummer | 2009-10-02 | 20929.6 | 12339.7833 | 1060 | 603.68 | 639900.8 | 0 | Individual | 3.271% | 1.928% |  |  | 3.271% | 1.928% | TRUE |  |  | 3.271% | 1.928%
OTMESA_2_PL1X3 | CCGT | 2022 | summer | 2009-10-02 | 43424.45 | 29357.2 | 765 | 603.68 | 461815.2 | 0 | Individual | 9.403% | 6.357% |  |  | 9.403% | 6.357% | TRUE |  |  | 9.403% | 6.357%
OTMESA_2_PL1X3 | CCGT | 2023 | nonsummer | 2009-10-02 | 40023.3833 | 12882.5793 | 1060 | 603.68 | 639900.8 | 0 | Individual | 6.255% | 2.013% |  |  | 6.255% | 2.013% | TRUE |  |  | 6.255% | 2.013%
OTMESA_2_PL1X3 | CCGT | 2023 | summer | 2009-10-02 | 39370.8333 | 20972.6947 | 765 | 603.68 | 461815.2 | 0 | Individual | 8.525% | 4.541% |  |  | 8.525% | 4.541% | TRUE |  |  | 8.525% | 4.541%
OTMESA_2_PL1X3 | CCGT | 2024 | nonsummer | 2009-10-02 | 112105.282 | 10254.1433 | 1065 | 603.68 | 642919.2 | 0 | Individual | 17.44% | 1.595% |  |  | 17.44% | 1.595% | TRUE |  |  | 17.44% | 1.595%
OTMESA_2_PL1X3 | CCGT | 2024 | summer | 2009-10-02 | 1958.6698 | 26140.2817 | 765 | 603.68 | 461815.2 | 0 | Individual | 0.4241% | 5.66% |  |  | 0.4241% | 5.66% | TRUE |  |  | 0.4241% | 5.66%
PALOMR_2_PL1X3 | CCGT | 2022 | nonsummer | 2005-10-14 | 50355.2083 | 0 | 1060 | 588.21 | 623502.6 | 0 | Individual | 8.076% | 0% |  |  | 8.076% | 0% | TRUE |  |  | 8.076% | 0%
PALOMR_2_PL1X3 | CCGT | 2022 | summer | 2005-10-14 | 4929.9743 | 58.0867 | 765 | 588.21 | 449980.65 | 0 | Individual | 1.096% | 0.01291% |  |  | 1.096% | 0.01291% | TRUE |  |  | 1.096% | 0.01291%
PALOMR_2_PL1X3 | CCGT | 2023 | nonsummer | 2005-10-14 | 4628.9067 | 0 | 1060 | 588.21 | 623502.6 | 0 | Individual | 0.7424% | 0% |  |  | 0.7424% | 0% | TRUE |  |  | 0.7424% | 0%
PALOMR_2_PL1X3 | CCGT | 2023 | summer | 2005-10-14 | 109064.7968 | 259.5362 | 765 | 588.21 | 449980.65 | 0 | Individual | 24.24% | 0.05768% |  |  | 24.24% | 0.05768% | TRUE |  |  | 24.24% | 0.05768%
PALOMR_2_PL1X3 | CCGT | 2024 | nonsummer | 2005-10-14 | 27453.5535 | 0 | 1065 | 588.21 | 626443.65 | 0 | Individual | 4.382% | 0% |  |  | 4.382% | 0% | TRUE |  |  | 4.382% | 0%
PALOMR_2_PL1X3 | CCGT | 2024 | summer | 2005-10-14 | 9910.3875 | 680.7127 | 765 | 588.21 | 449980.65 | 0 | Individual | 2.202% | 0.1513% |  |  | 2.202% | 0.1513% | TRUE |  |  | 2.202% | 0.1513%
RUSCTY_2_UNITS | CCGT | 2022 | nonsummer | 2013-08-08 | 462411.757 | 850.512 | 1060 | 615.18 | 652090.8 | 0 | Individual | 70.91% | 0.1304% |  |  | 70.91% | 0.1304% | TRUE |  |  | 70.91% | 0.1304%
RUSCTY_2_UNITS | CCGT | 2022 | summer | 2013-08-08 | 89258.3525 | 19152.4435 | 765 | 615.18 | 470612.7 | 0 | Individual | 18.97% | 4.07% |  |  | 18.97% | 4.07% | TRUE |  |  | 18.97% | 4.07%
RUSCTY_2_UNITS | CCGT | 2023 | nonsummer | 2013-08-08 | 64580.4902 | 17117.2033 | 1060 | 615.18 | 652090.8 | 0 | Individual | 9.904% | 2.625% |  |  | 9.904% | 2.625% | TRUE |  |  | 9.904% | 2.625%
RUSCTY_2_UNITS | CCGT | 2023 | summer | 2013-08-08 | 6954.8528 | 17670.08 | 765 | 615.18 | 470612.7 | 0 | Individual | 1.478% | 3.755% |  |  | 1.478% | 3.755% | TRUE |  |  | 1.478% | 3.755%
RUSCTY_2_UNITS | CCGT | 2024 | nonsummer | 2013-08-08 | 2909.915 | 17191.2517 | 1065 | 615.18 | 655166.7 | 0 | Individual | 0.4441% | 2.624% |  |  | 0.4441% | 2.624% | TRUE |  |  | 0.4441% | 2.624%
RUSCTY_2_UNITS | CCGT | 2024 | summer | 2013-08-08 | 20889.7457 | 19524.5667 | 765 | 615.18 | 470612.7 | 0 | Individual | 4.439% | 4.149% |  |  | 4.439% | 4.149% | TRUE |  |  | 4.439% | 4.149%
SBERDO_2_PSP3 | CCGT | 2022 | nonsummer | 2005-12-10 | 56493.3167 | 4807.62 | 1060 | 555 | 588300 | 0 | Individual | 9.603% | 0.8172% |  |  | 9.603% | 0.8172% | TRUE |  |  | 9.603% | 0.8172%
SBERDO_2_PSP3 | CCGT | 2022 | summer | 2005-12-10 | 11086.7398 | 20419.6535 | 765 | 555 | 424575 | 0 | Individual | 2.611% | 4.809% |  |  | 2.611% | 4.809% | TRUE |  |  | 2.611% | 4.809%
SBERDO_2_PSP3 | CCGT | 2023 | nonsummer | 2005-12-10 | 22739.6358 | 4097.8503 | 1060 | 555 | 588300 | 0 | Individual | 3.865% | 0.6966% |  |  | 3.865% | 0.6966% | TRUE |  |  | 3.865% | 0.6966%
SBERDO_2_PSP3 | CCGT | 2023 | summer | 2005-12-10 | 11787.5637 | 15010.5135 | 765 | 555 | 424575 | 0 | Individual | 2.776% | 3.535% |  |  | 2.776% | 3.535% | TRUE |  |  | 2.776% | 3.535%
SBERDO_2_PSP3 | CCGT | 2024 | nonsummer | 2005-12-10 | 19698.9167 | 756.43 | 1065 | 555 | 591075 | 0 | Individual | 3.333% | 0.128% |  |  | 3.333% | 0.128% | TRUE |  |  | 3.333% | 0.128%
SBERDO_2_PSP3 | CCGT | 2024 | summer | 2005-12-10 | 2583.0192 | 15696.48 | 765 | 555 | 424575 | 0 | Individual | 0.6084% | 3.697% |  |  | 0.6084% | 3.697% | TRUE |  |  | 0.6084% | 3.697%
SBERDO_2_PSP4 | CCGT | 2022 | nonsummer | 2006-01-19 | 25573.6143 | 4013.6433 | 1060 | 555 | 588300 | 0 | Individual | 4.347% | 0.6822% |  |  | 4.347% | 0.6822% | TRUE |  |  | 4.347% | 0.6822%
SBERDO_2_PSP4 | CCGT | 2022 | summer | 2006-01-19 | 7321.4622 | 23660.19 | 765 | 555 | 424575 | 0 | Individual | 1.724% | 5.573% |  |  | 1.724% | 5.573% | TRUE |  |  | 1.724% | 5.573%
SBERDO_2_PSP4 | CCGT | 2023 | nonsummer | 2006-01-19 | 82416.8112 | 6476.6315 | 1060 | 555 | 588300 | 0 | Individual | 14.01% | 1.101% |  |  | 14.01% | 1.101% | TRUE |  |  | 14.01% | 1.101%
SBERDO_2_PSP4 | CCGT | 2023 | summer | 2006-01-19 | 14335.2873 | 18038.41 | 765 | 555 | 424575 | 0 | Individual | 3.376% | 4.249% |  |  | 3.376% | 4.249% | TRUE |  |  | 3.376% | 4.249%
SBERDO_2_PSP4 | CCGT | 2024 | nonsummer | 2006-01-19 | 40256.418 | 4058.7543 | 1065 | 555 | 591075 | 0 | Individual | 6.811% | 0.6867% |  |  | 6.811% | 0.6867% | TRUE |  |  | 6.811% | 0.6867%
SBERDO_2_PSP4 | CCGT | 2024 | summer | 2006-01-19 | 21039.2985 | 23718.7582 | 765 | 555 | 424575 | 0 | Individual | 4.955% | 5.586% |  |  | 4.955% | 5.586% | TRUE |  |  | 4.955% | 5.586%
SCHLTE_1_PL1X3 | CCGT | 2022 | nonsummer | 2012-10-31 | 214.0057 | 8853.05 | 1060 | 336.04 | 356202.4 | 0 | Individual | 0.06008% | 2.485% |  |  | 0.06008% | 2.485% | TRUE |  |  | 0.06008% | 2.485%
SCHLTE_1_PL1X3 | CCGT | 2022 | summer | 2012-10-31 | 0 | 25547.4433 | 765 | 336.04 | 257070.6 | 0 | Individual | 0% | 9.938% |  |  | 0% | 9.938% | TRUE |  |  | 0% | 9.938%
SCHLTE_1_PL1X3 | CCGT | 2023 | nonsummer | 2012-10-31 | 1108.8893 | 679.68 | 1060 | 336.04 | 356202.4 | 0 | Individual | 0.3113% | 0.1908% |  |  | 0.3113% | 0.1908% | TRUE |  |  | 0.3113% | 0.1908%
SCHLTE_1_PL1X3 | CCGT | 2023 | summer | 2012-10-31 | 1512.18 | 2070.8673 | 765 | 336.04 | 257070.6 | 0 | Individual | 0.5882% | 0.8056% |  |  | 0.5882% | 0.8056% | TRUE |  |  | 0.5882% | 0.8056%
SCHLTE_1_PL1X3 | CCGT | 2024 | nonsummer | 2012-10-31 | 5067.3047 | 982.7707 | 1065 | 336.04 | 357882.6 | 0 | Individual | 1.416% | 0.2746% |  |  | 1.416% | 0.2746% | TRUE |  |  | 1.416% | 0.2746%
SCHLTE_1_PL1X3 | CCGT | 2024 | summer | 2012-10-31 | 435.2947 | 3618.532 | 765 | 336.04 | 257070.6 | 0 | Individual | 0.1693% | 1.408% |  |  | 0.1693% | 1.408% | TRUE |  |  | 0.1693% | 1.408%
SGREGY_6_SANGER | CCGT | 2022 | nonsummer | 2017-06-01 | 18422.425 | 0 | 1060 | 48.3 | 51198 | 0 | Individual | 35.98% | 0% |  |  | 35.98% | 0% | TRUE |  |  | 35.98% | 0%
SGREGY_6_SANGER | CCGT | 2022 | summer | 2017-06-01 | 12964.525 | 33 | 765 | 48.3 | 36949.5 | 0 | Individual | 35.09% | 0.08931% |  |  | 35.09% | 0.08931% | TRUE |  |  | 35.09% | 0.08931%
SGREGY_6_SANGER | CCGT | 2023 | nonsummer | 2017-06-01 | 8170.75 | 0 | 1060 | 48.3 | 51198 | 0 | Individual | 15.96% | 0% |  |  | 15.96% | 0% | TRUE |  |  | 15.96% | 0%
SGREGY_6_SANGER | CCGT | 2023 | summer | 2017-06-01 | 128.6417 | 0 | 765 | 48.3 | 36949.5 | 0 | Individual | 0.3482% | 0% |  |  | 0.3482% | 0% | TRUE |  |  | 0.3482% | 0%
SGREGY_6_SANGER | CCGT | 2024 | nonsummer | 2017-06-01 | 319.26 | 0 | 1065 | 48.3 | 51439.5 | 0 | Individual | 0.6207% | 0% |  |  | 0.6207% | 0% | TRUE |  |  | 0.6207% | 0%
SGREGY_6_SANGER | CCGT | 2024 | summer | 2017-06-01 | 289.8 | 0 | 765 | 48.3 | 36949.5 | 0 | Individual | 0.7843% | 0% |  |  | 0.7843% | 0% | TRUE |  |  | 0.7843% | 0%
SUNRIS_2_PL1X3 | CCGT | 2022 | nonsummer | 2001-06-07 | 22534.1667 | 30698.3167 | 1060 | 586.02 | 621181.2 | 0 | Individual | 3.628% | 4.942% |  |  | 3.628% | 4.942% | TRUE |  |  | 3.628% | 4.942%
SUNRIS_2_PL1X3 | CCGT | 2022 | summer | 2001-06-07 | 2006.85 | 37537.3 | 765 | 586.02 | 448305.3 | 0 | Individual | 0.4477% | 8.373% |  |  | 0.4477% | 8.373% | TRUE |  |  | 0.4477% | 8.373%
SUNRIS_2_PL1X3 | CCGT | 2023 | nonsummer | 2001-06-07 | 41031.8193 | 26101.9307 | 1060 | 586.02 | 621181.2 | 0 | Individual | 6.605% | 4.202% |  |  | 6.605% | 4.202% | TRUE |  |  | 6.605% | 4.202%
SUNRIS_2_PL1X3 | CCGT | 2023 | summer | 2001-06-07 | 14304.895 | 35269.1933 | 765 | 586.02 | 448305.3 | 0 | Individual | 3.191% | 7.867% |  |  | 3.191% | 7.867% | TRUE |  |  | 3.191% | 7.867%
SUNRIS_2_PL1X3 | CCGT | 2024 | nonsummer | 2001-06-07 | 61972.1482 | 23163.73 | 1065 | 586.02 | 624111.3 | 0 | Individual | 9.93% | 3.711% |  |  | 9.93% | 3.711% | TRUE |  |  | 9.93% | 3.711%
SUNRIS_2_PL1X3 | CCGT | 2024 | summer | 2001-06-07 | 4544.3218 | 36478.1 | 765 | 586.02 | 448305.3 | 0 | Individual | 1.014% | 8.137% |  |  | 1.014% | 8.137% | TRUE |  |  | 1.014% | 8.137%
TERMEX_2_PL1X3 | CCGT | 2022 | nonsummer | 2003-07-30 | 27257.6667 | 4340 | 1060 | 625 | 662500 | 0 | Individual | 4.114% | 0.6551% |  |  | 4.114% | 0.6551% | TRUE |  |  | 4.114% | 0.6551%
TERMEX_2_PL1X3 | CCGT | 2022 | summer | 2003-07-30 | 16061.5667 | 52809.9167 | 765 | 625 | 478125 | 0 | Individual | 3.359% | 11.05% |  |  | 3.359% | 11.05% | TRUE |  |  | 3.359% | 11.05%
TERMEX_2_PL1X3 | CCGT | 2023 | nonsummer | 2003-07-30 | 16843.1667 | 2346 | 1060 | 625 | 662500 | 0 | Individual | 2.542% | 0.3541% |  |  | 2.542% | 0.3541% | TRUE |  |  | 2.542% | 0.3541%
TERMEX_2_PL1X3 | CCGT | 2023 | summer | 2003-07-30 | 3135.5 | 16954.7667 | 765 | 625 | 478125 | 0 | Individual | 0.6558% | 3.546% |  |  | 0.6558% | 3.546% | TRUE |  |  | 0.6558% | 3.546%
TERMEX_2_PL1X3 | CCGT | 2024 | nonsummer | 2003-07-30 | 17346.9833 | 2184 | 1065 | 625 | 665625 | 0 | Individual | 2.606% | 0.3281% |  |  | 2.606% | 0.3281% | TRUE |  |  | 2.606% | 0.3281%
TERMEX_2_PL1X3 | CCGT | 2024 | summer | 2003-07-30 | 14434.0167 | 16710 | 765 | 625 | 478125 | 0 | Individual | 3.019% | 3.495% |  |  | 3.019% | 3.495% | TRUE |  |  | 3.019% | 3.495%
VERNON_6_MALBRG | CCGT | 2022 | nonsummer | 2005-10-17 | 22974.7 | 0 | 1060 | 139 | 147340 | 0 | Individual | 15.59% | 0% |  |  | 15.59% | 0% | TRUE |  |  | 15.59% | 0%
VERNON_6_MALBRG | CCGT | 2022 | summer | 2005-10-17 | 3606.1167 | 45 | 765 | 139 | 106335 | 0 | Individual | 3.391% | 0.04232% |  |  | 3.391% | 0.04232% | TRUE |  |  | 3.391% | 0.04232%
VERNON_6_MALBRG | CCGT | 2023 | nonsummer | 2005-10-17 | 4525 | 0 | 1060 | 139 | 147340 | 0 | Individual | 3.071% | 0% |  |  | 3.071% | 0% | TRUE |  |  | 3.071% | 0%
VERNON_6_MALBRG | CCGT | 2023 | summer | 2005-10-17 | 139 | 0 | 765 | 139 | 106335 | 0 | Individual | 0.1307% | 0% |  |  | 0.1307% | 0% | TRUE |  |  | 0.1307% | 0%
VERNON_6_MALBRG | CCGT | 2024 | nonsummer | 2005-10-17 | 6790.6333 | 0 | 1065 | 139 | 148035 | 0 | Individual | 4.587% | 0% |  |  | 4.587% | 0% | TRUE |  |  | 4.587% | 0%
VERNON_6_MALBRG | CCGT | 2024 | summer | 2005-10-17 | 4007.1783 | 0 | 765 | 139 | 106335 | 0 | Individual | 3.768% | 0% |  |  | 3.768% | 0% | TRUE |  |  | 3.768% | 0%
ARCOGN_2_UNITS | CHP | 2022 | nonsummer | 1987-12-04 | 38482.5 | 0 | 1060 | 245 | 259700 | 0 | Individual | 14.82% | 0% |  |  | 14.82% | 0% | TRUE |  |  | 14.82% | 0%
ARCOGN_2_UNITS | CHP | 2022 | summer | 1987-12-04 | 17474.1667 | 180 | 765 | 245 | 187425 | 0 | Individual | 9.323% | 0.09604% |  |  | 9.323% | 0.09604% | TRUE |  |  | 9.323% | 0.09604%
ARCOGN_2_UNITS | CHP | 2023 | nonsummer | 1987-12-04 | 38131.5 | 0 | 1060 | 245 | 259700 | 0 | Individual | 14.68% | 0% |  |  | 14.68% | 0% | TRUE |  |  | 14.68% | 0%
ARCOGN_2_UNITS | CHP | 2023 | summer | 1987-12-04 | 19633.6667 | 125 | 765 | 245 | 187425 | 0 | Individual | 10.48% | 0.06669% |  |  | 10.48% | 0.06669% | TRUE |  |  | 10.48% | 0.06669%
ARCOGN_2_UNITS | CHP | 2024 | nonsummer | 1987-12-04 | 17197.5667 | 56 | 1065 | 245 | 260925 | 0 | Individual | 6.591% | 0.02146% |  |  | 6.591% | 0.02146% | TRUE |  |  | 6.591% | 0.02146%
ARCOGN_2_UNITS | CHP | 2024 | summer | 1987-12-04 | 36690.25 | 34 | 765 | 245 | 187425 | 0 | Individual | 19.58% | 0.01814% |  |  | 19.58% | 0.01814% | TRUE |  |  | 19.58% | 0.01814%
CHINO_6_CIMGEN | CHP | 2022 | nonsummer | 2018-06-27 | 0 | 0 | 1060 | 26 | 27560 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
CHINO_6_CIMGEN | CHP | 2022 | summer | 2018-06-27 | 0 | 0 | 765 | 26 | 19890 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
CHINO_6_CIMGEN | CHP | 2023 | nonsummer | 2018-06-27 | 0 | 0 | 1060 | 26 | 27560 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
CHINO_6_CIMGEN | CHP | 2023 | summer | 2018-06-27 | 0 | 0 | 765 | 26 | 19890 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
CHINO_6_CIMGEN | CHP | 2024 | nonsummer | 2018-06-27 | 0 | 0 | 1065 | 26 | 27690 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
CHINO_6_CIMGEN | CHP | 2024 | summer | 2018-06-27 | 0 | 0 | 765 | 26 | 19890 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
CUMMNG_6_SUNCT1 | CHP | 2022 | nonsummer | 2018-05-31 | 0 | 0 | 1060 | 4 | 4240 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
CUMMNG_6_SUNCT1 | CHP | 2022 | summer | 2018-05-31 | 0 | 0 | 765 | 4 | 3060 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
CUMMNG_6_SUNCT1 | CHP | 2023 | nonsummer | 2018-05-31 | 0 | 0 | 1060 | 4 | 4240 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
CUMMNG_6_SUNCT1 | CHP | 2023 | summer | 2018-05-31 | 0 | 0 | 765 | 4 | 3060 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
CUMMNG_6_SUNCT1 | CHP | 2024 | nonsummer | 2018-05-31 | 0 | 0 | 1065 | 4 | 4260 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
CUMMNG_6_SUNCT1 | CHP | 2024 | summer | 2018-05-31 | 0 | 0 | 765 | 4 | 3060 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
DEXZEL_1_UNIT | CHP | 2022 | nonsummer | 1989-11-30 | 9106.95 | 0 | 1060 | 20 | 21200 | 0 | Individual | 42.96% | 0% |  |  | 42.96% | 0% | TRUE |  |  | 42.96% | 0%
DEXZEL_1_UNIT | CHP | 2022 | summer | 1989-11-30 | 13006.25 | 0 | 765 | 20 | 15300 | 0 | Individual | 85.01% | 0% |  |  | 85.01% | 0% | TRUE |  |  | 85.01% | 0%
DEXZEL_1_UNIT | CHP | 2023 | nonsummer | 1989-11-30 | 10416.9083 | 0 | 1060 | 20 | 21200 | 0 | Individual | 49.14% | 0% |  |  | 49.14% | 0% | TRUE |  |  | 49.14% | 0%
DEXZEL_1_UNIT | CHP | 2023 | summer | 1989-11-30 | 508 | 0 | 765 | 20 | 15300 | 0 | Individual | 3.32% | 0% |  |  | 3.32% | 0% | TRUE |  |  | 3.32% | 0%
DEXZEL_1_UNIT | CHP | 2024 | nonsummer | 1989-11-30 | 4676.5872 | 0 | 1065 | 20 | 21300 | 0 | Individual | 21.96% | 0% |  |  | 21.96% | 0% | TRUE |  |  | 21.96% | 0%
DEXZEL_1_UNIT | CHP | 2024 | summer | 1989-11-30 | 6719.9032 | 30.3 | 765 | 20 | 15300 | 0 | Individual | 43.92% | 0.198% |  |  | 43.92% | 0.198% | TRUE |  |  | 43.92% | 0.198%
GRNLF2_1_UNIT | CHP | 2022 | nonsummer | 2020-06-01 | 15990 | 0 | 1060 | 49.2 | 52152 | 0 | Individual | 30.66% | 0% |  |  | 30.66% | 0% | TRUE |  |  | 30.66% | 0%
GRNLF2_1_UNIT | CHP | 2022 | summer | 2020-06-01 | 26568 | 0 | 765 | 49.2 | 37638 | 0 | Individual | 70.59% | 0% |  |  | 70.59% | 0% | TRUE |  |  | 70.59% | 0%
GRNLF2_1_UNIT | CHP | 2023 | nonsummer | 2020-06-01 | 51292.81 | 0 | 1060 | 49.2 | 52152 | 0 | Individual | 98.35% | 0% |  |  | 98.35% | 0% | TRUE |  |  | 98.35% | 0%
GRNLF2_1_UNIT | CHP | 2023 | summer | 2020-06-01 | 24501.14 | 0 | 765 | 49.2 | 37638 | 0 | Individual | 65.1% | 0% |  |  | 65.1% | 0% | TRUE |  |  | 65.1% | 0%
GRNLF2_1_UNIT | CHP | 2024 | nonsummer | 2020-06-01 | 12349.2 | 0 | 1065 | 49.2 | 52398 | 0 | Individual | 23.57% | 0% |  |  | 23.57% | 0% | TRUE |  |  | 23.57% | 0%
GRNLF2_1_UNIT | CHP | 2024 | summer | 2020-06-01 | 949.8657 | 8.36 | 765 | 49.2 | 37638 | 0 | Individual | 2.524% | 0.02221% |  |  | 2.524% | 0.02221% | TRUE |  |  | 2.524% | 0.02221%
OMAR_2_UNIT 4 | CHP | 2022 | nonsummer | 1985-05-01 | 13312.5 | 0 | 1060 | 75 | 79500 | 0 | Individual | 16.75% | 0% |  |  | 16.75% | 0% | TRUE |  |  | 16.75% | 0%
OMAR_2_UNIT 4 | CHP | 2022 | summer | 1985-05-01 | 1126.25 | 54.4 | 765 | 75 | 57375 | 0 | Individual | 1.963% | 0.09481% |  |  | 1.963% | 0.09481% | TRUE |  |  | 1.963% | 0.09481%
OMAR_2_UNIT 4 | CHP | 2023 | nonsummer | 1985-05-01 | 18582.4167 | 0 | 1060 | 75 | 79500 | 0 | Individual | 23.37% | 0% |  |  | 23.37% | 0% | TRUE |  |  | 23.37% | 0%
OMAR_2_UNIT 4 | CHP | 2023 | summer | 1985-05-01 | 2625 | 0 | 765 | 75 | 57375 | 0 | Individual | 4.575% | 0% |  |  | 4.575% | 0% | TRUE |  |  | 4.575% | 0%
OMAR_2_UNIT 4 | CHP | 2024 | nonsummer | 1985-05-01 | 16172.5 | 0 | 1065 | 75 | 79875 | 0 | Individual | 20.25% | 0% |  |  | 20.25% | 0% | TRUE |  |  | 20.25% | 0%
OMAR_2_UNIT 4 | CHP | 2024 | summer | 1985-05-01 | 7365 | 0 | 765 | 75 | 57375 | 0 | Individual | 12.84% | 0% |  |  | 12.84% | 0% | TRUE |  |  | 12.84% | 0%
OROVIL_6_UNIT | CHP | 2022 | nonsummer | 1989-12-18 | 395 | 0 | 1060 | 7.5 | 7950 | 0 | Individual | 4.969% | 0% |  |  | 4.969% | 0% | TRUE |  |  | 4.969% | 0%
OROVIL_6_UNIT | CHP | 2022 | summer | 1989-12-18 | 3532.2 | 0 | 765 | 7.5 | 5737.5 | 0 | Individual | 61.56% | 0% |  |  | 61.56% | 0% | TRUE |  |  | 61.56% | 0%
OROVIL_6_UNIT | CHP | 2023 | nonsummer | 1989-12-18 | 1527.8 | 0 | 1060 | 7.5 | 7950 | 0 | Individual | 19.22% | 0% |  |  | 19.22% | 0% | TRUE |  |  | 19.22% | 0%
OROVIL_6_UNIT | CHP | 2023 | summer | 1989-12-18 | 814.12 | 0 | 765 | 7.5 | 5737.5 | 0 | Individual | 14.19% | 0% |  |  | 14.19% | 0% | TRUE |  |  | 14.19% | 0%
OROVIL_6_UNIT | CHP | 2024 | nonsummer | 1989-12-18 | 382.5 | 0 | 1065 | 7.5 | 7987.5 | 0 | Individual | 4.789% | 0% |  |  | 4.789% | 0% | TRUE |  |  | 4.789% | 0%
OROVIL_6_UNIT | CHP | 2024 | summer | 1989-12-18 | 1162.5 | 0 | 765 | 7.5 | 5737.5 | 0 | Individual | 20.26% | 0% |  |  | 20.26% | 0% | TRUE |  |  | 20.26% | 0%
PLMSSR_6_HISIER | CHP | 2022 | nonsummer | 2010-04-22 | 505.5893 | 0 | 1060 | 6 | 6360 | 0 | Individual | 7.95% | 0% |  |  | 7.95% | 0% | TRUE |  |  | 7.95% | 0%
PLMSSR_6_HISIER | CHP | 2022 | summer | 2010-04-22 | 199.9313 | 0 | 765 | 6 | 4590 | 0 | Individual | 4.356% | 0% |  |  | 4.356% | 0% | TRUE |  |  | 4.356% | 0%
PLMSSR_6_HISIER | CHP | 2023 | nonsummer | 2010-04-22 | 361.1243 | 0 | 1060 | 6 | 6360 | 0 | Individual | 5.678% | 0% |  |  | 5.678% | 0% | TRUE |  |  | 5.678% | 0%
PLMSSR_6_HISIER | CHP | 2023 | summer | 2010-04-22 | 106.0187 | 0 | 765 | 6 | 4590 | 0 | Individual | 2.31% | 0% |  |  | 2.31% | 0% | TRUE |  |  | 2.31% | 0%
PLMSSR_6_HISIER | CHP | 2024 | nonsummer | 2010-04-22 | 373.5403 | 0 | 1065 | 6 | 6390 | 0 | Individual | 5.846% | 0% |  |  | 5.846% | 0% | TRUE |  |  | 5.846% | 0%
PLMSSR_6_HISIER | CHP | 2024 | summer | 2010-04-22 | 371.2192 | 0 | 765 | 6 | 4590 | 0 | Individual | 8.088% | 0% |  |  | 8.088% | 0% | TRUE |  |  | 8.088% | 0%
SALIRV_2_UNIT | CHP | 2022 | nonsummer | 1991-10-11 | 195 | 0 | 1060 | 39 | 41340 | 0 | Individual | 0.4717% | 0% |  |  | 0.4717% | 0% | TRUE |  |  | 0.4717% | 0%
SALIRV_2_UNIT | CHP | 2022 | summer | 1991-10-11 | 64.35 | 0 | 765 | 39 | 29835 | 0 | Individual | 0.2157% | 0% |  |  | 0.2157% | 0% | TRUE |  |  | 0.2157% | 0%
SALIRV_2_UNIT | CHP | 2023 | nonsummer | 1991-10-11 | 10870.6 | 0 | 1060 | 39 | 41340 | 0 | Individual | 26.3% | 0% |  |  | 26.3% | 0% | TRUE |  |  | 26.3% | 0%
SALIRV_2_UNIT | CHP | 2023 | summer | 1991-10-11 | 1688.05 | 0 | 765 | 39 | 29835 | 0 | Individual | 5.658% | 0% |  |  | 5.658% | 0% | TRUE |  |  | 5.658% | 0%
SALIRV_2_UNIT | CHP | 2024 | nonsummer | 1991-10-11 | 6348.55 | 0 | 1065 | 39 | 41535 | 0 | Individual | 15.28% | 0% |  |  | 15.28% | 0% | TRUE |  |  | 15.28% | 0%
SALIRV_2_UNIT | CHP | 2024 | summer | 1991-10-11 | 776.75 | 0 | 765 | 39 | 29835 | 0 | Individual | 2.603% | 0% |  |  | 2.603% | 0% | TRUE |  |  | 2.603% | 0%
SMPRIP_1_SMPSON | CHP | 2022 | nonsummer | 1988-04-19 | 690.75 | 0 | 1060 | 46.05 | 48813 | 0 | Individual | 1.415% | 0% |  |  | 1.415% | 0% | TRUE |  |  | 1.415% | 0%
SMPRIP_1_SMPSON | CHP | 2022 | summer | 1988-04-19 | 13646.15 | 0 | 765 | 46.05 | 35228.25 | 0 | Individual | 38.74% | 0% |  |  | 38.74% | 0% | TRUE |  |  | 38.74% | 0%
SMPRIP_1_SMPSON | CHP | 2023 | nonsummer | 1988-04-19 | 0 | 0 | 1060 | 46.05 | 48813 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SMPRIP_1_SMPSON | CHP | 2023 | summer | 1988-04-19 | 3321.91 | 0 | 765 | 46.05 | 35228.25 | 0 | Individual | 9.43% | 0% |  |  | 9.43% | 0% | TRUE |  |  | 9.43% | 0%
SMPRIP_1_SMPSON | CHP | 2024 | nonsummer | 1988-04-19 | 45.1793 | 0 | 1065 | 46.05 | 49043.25 | 0 | Individual | 0.09212% | 0% |  |  | 0.09212% | 0% | TRUE |  |  | 0.09212% | 0%
SMPRIP_1_SMPSON | CHP | 2024 | summer | 1988-04-19 | 683.075 | 0 | 765 | 46.05 | 35228.25 | 0 | Individual | 1.939% | 0% |  |  | 1.939% | 0% | TRUE |  |  | 1.939% | 0%
SNCLRA_2_UNIT | CHP | 2022 | nonsummer | 2018-04-26 | 15812.5 | 0 | 1060 | 27.5 | 29150 | 0 | Individual | 54.25% | 0% |  |  | 54.25% | 0% | TRUE |  |  | 54.25% | 0%
SNCLRA_2_UNIT | CHP | 2022 | summer | 2018-04-26 | 5637.5 | 0 | 765 | 27.5 | 21037.5 | 0 | Individual | 26.8% | 0% |  |  | 26.8% | 0% | TRUE |  |  | 26.8% | 0%
SNCLRA_2_UNIT | CHP | 2023 | nonsummer | 2018-04-26 | 11412.5 | 0 | 1060 | 27.5 | 29150 | 0 | Individual | 39.15% | 0% |  |  | 39.15% | 0% | TRUE |  |  | 39.15% | 0%
SNCLRA_2_UNIT | CHP | 2023 | summer | 2018-04-26 | 2475 | 0 | 765 | 27.5 | 21037.5 | 0 | Individual | 11.76% | 0% |  |  | 11.76% | 0% | TRUE |  |  | 11.76% | 0%
SNCLRA_2_UNIT | CHP | 2024 | nonsummer | 2018-04-26 | 0 | 0 | 1065 | 27.5 | 29287.5 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SNCLRA_2_UNIT | CHP | 2024 | summer | 2018-04-26 | 0 | 0 | 765 | 27.5 | 21037.5 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SNCLRA_2_UNIT1 | CHP | 2022 | nonsummer | 2016-04-15 | 0 | 0 | 1060 | 27.8 | 29468 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SNCLRA_2_UNIT1 | CHP | 2022 | summer | 2016-04-15 | 121 | 0 | 765 | 27.8 | 21267 | 0 | Individual | 0.569% | 0% |  |  | 0.569% | 0% | TRUE |  |  | 0.569% | 0%
SNCLRA_2_UNIT1 | CHP | 2023 | nonsummer | 2016-04-15 | 5730.7333 | 0 | 1060 | 27.8 | 29468 | 0 | Individual | 19.45% | 0% |  |  | 19.45% | 0% | TRUE |  |  | 19.45% | 0%
SNCLRA_2_UNIT1 | CHP | 2023 | summer | 2016-04-15 | 11239.2083 | 0 | 765 | 27.8 | 21267 | 0 | Individual | 52.85% | 0% |  |  | 52.85% | 0% | TRUE |  |  | 52.85% | 0%
SNCLRA_2_UNIT1 | CHP | 2024 | nonsummer | 2016-04-15 | 6716.14 | 0 | 1065 | 27.8 | 29607 | 0 | Individual | 22.68% | 0% |  |  | 22.68% | 0% | TRUE |  |  | 22.68% | 0%
SNCLRA_2_UNIT1 | CHP | 2024 | summer | 2016-04-15 | 3540.0367 | 0 | 765 | 27.8 | 21267 | 0 | Individual | 16.65% | 0% |  |  | 16.65% | 0% | TRUE |  |  | 16.65% | 0%
SNCLRA_6_OXGEN | CHP | 2022 | nonsummer | 2020-06-01 | 8728.305 | 0 | 1060 | 47.7 | 50562 | 0 | Individual | 17.26% | 0% |  |  | 17.26% | 0% | TRUE |  |  | 17.26% | 0%
SNCLRA_6_OXGEN | CHP | 2022 | summer | 2020-06-01 | 0 | 0 | 765 | 47.7 | 36490.5 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SNCLRA_6_OXGEN | CHP | 2023 | nonsummer | 2020-06-01 | 2051.1 | 0 | 1060 | 47.7 | 50562 | 0 | Individual | 4.057% | 0% |  |  | 4.057% | 0% | TRUE |  |  | 4.057% | 0%
SNCLRA_6_OXGEN | CHP | 2023 | summer | 2020-06-01 | 381.6 | 0 | 765 | 47.7 | 36490.5 | 0 | Individual | 1.046% | 0% |  |  | 1.046% | 0% | TRUE |  |  | 1.046% | 0%
SNCLRA_6_OXGEN | CHP | 2024 | nonsummer | 2020-06-01 | 5499.59 | 0 | 1065 | 47.7 | 50800.5 | 0 | Individual | 10.83% | 0% |  |  | 10.83% | 0% | TRUE |  |  | 10.83% | 0%
SNCLRA_6_OXGEN | CHP | 2024 | summer | 2020-06-01 | 7182.335 | 0 | 765 | 47.7 | 36490.5 | 0 | Individual | 19.68% | 0% |  |  | 19.68% | 0% | TRUE |  |  | 19.68% | 0%
SUNSET_2_UNITS | CHP | 2022 | nonsummer | 1989-12-18 | 55831.5167 | 7730 | 1060 | 248 | 262880 | 0 | Individual | 21.24% | 2.941% |  |  | 21.24% | 2.941% | TRUE |  |  | 21.24% | 2.941%
SUNSET_2_UNITS | CHP | 2022 | summer | 1989-12-18 | 4911.9333 | 14263 | 765 | 248 | 189720 | 0 | Individual | 2.589% | 7.518% |  |  | 2.589% | 7.518% | TRUE |  |  | 2.589% | 7.518%
SUNSET_2_UNITS | CHP | 2023 | nonsummer | 1989-12-18 | 2310 | 4179 | 1060 | 248 | 262880 | 0 | Individual | 0.8787% | 1.59% |  |  | 0.8787% | 1.59% | TRUE |  |  | 0.8787% | 1.59%
SUNSET_2_UNITS | CHP | 2023 | summer | 1989-12-18 | 386.5667 | 14210 | 765 | 248 | 189720 | 0 | Individual | 0.2038% | 7.49% |  |  | 0.2038% | 7.49% | TRUE |  |  | 0.2038% | 7.49%
SUNSET_2_UNITS | CHP | 2024 | nonsummer | 1989-12-18 | 3843.9 | 5741.5 | 1065 | 248 | 264120 | 0 | Individual | 1.455% | 2.174% |  |  | 1.455% | 2.174% | TRUE |  |  | 1.455% | 2.174%
SUNSET_2_UNITS | CHP | 2024 | summer | 1989-12-18 | 335 | 17083 | 765 | 248 | 189720 | 0 | Individual | 0.1766% | 9.004% |  |  | 0.1766% | 9.004% | TRUE |  |  | 0.1766% | 9.004%
SYCAMR_2_UNIT 1 | CHP | 2022 | nonsummer | 1987-01-01 | 5645.7333 | 0 | 1060 | 74 | 78440 | 0 | Individual | 7.198% | 0% |  |  | 7.198% | 0% | TRUE |  |  | 7.198% | 0%
SYCAMR_2_UNIT 1 | CHP | 2022 | summer | 1987-01-01 | 15040.8333 | 0 | 765 | 74 | 56610 | 0 | Individual | 26.57% | 0% |  |  | 26.57% | 0% | TRUE |  |  | 26.57% | 0%
SYCAMR_2_UNIT 1 | CHP | 2023 | nonsummer | 1987-01-01 | 15919.5 | 0 | 1060 | 74 | 78440 | 0 | Individual | 20.3% | 0% |  |  | 20.3% | 0% | TRUE |  |  | 20.3% | 0%
SYCAMR_2_UNIT 1 | CHP | 2023 | summer | 1987-01-01 | 6114.8667 | 0 | 765 | 74 | 56610 | 0 | Individual | 10.8% | 0% |  |  | 10.8% | 0% | TRUE |  |  | 10.8% | 0%
SYCAMR_2_UNIT 1 | CHP | 2024 | nonsummer | 1987-01-01 | 21170.1667 | 0 | 1065 | 74 | 78810 | 0 | Individual | 26.86% | 0% |  |  | 26.86% | 0% | TRUE |  |  | 26.86% | 0%
SYCAMR_2_UNIT 1 | CHP | 2024 | summer | 1987-01-01 | 690.6667 | 0 | 765 | 74 | 56610 | 0 | Individual | 1.22% | 0% |  |  | 1.22% | 0% | TRUE |  |  | 1.22% | 0%
SYCAMR_2_UNIT 3 | CHP | 2022 | nonsummer | 1987-01-01 | 4620.7667 | 0 | 1060 | 74 | 78440 | 0 | Individual | 5.891% | 0% |  |  | 5.891% | 0% | TRUE |  |  | 5.891% | 0%
SYCAMR_2_UNIT 3 | CHP | 2022 | summer | 1987-01-01 | 370 | 0 | 765 | 74 | 56610 | 0 | Individual | 0.6536% | 0% |  |  | 0.6536% | 0% | TRUE |  |  | 0.6536% | 0%
SYCAMR_2_UNIT 3 | CHP | 2023 | nonsummer | 1987-01-01 | 2146 | 0 | 1060 | 74 | 78440 | 0 | Individual | 2.736% | 0% |  |  | 2.736% | 0% | TRUE |  |  | 2.736% | 0%
SYCAMR_2_UNIT 3 | CHP | 2023 | summer | 1987-01-01 | 622.8333 | 0 | 765 | 74 | 56610 | 0 | Individual | 1.1% | 0% |  |  | 1.1% | 0% | TRUE |  |  | 1.1% | 0%
SYCAMR_2_UNIT 3 | CHP | 2024 | nonsummer | 1987-01-01 | 11272.6667 | 0 | 1065 | 74 | 78810 | 0 | Individual | 14.3% | 0% |  |  | 14.3% | 0% | TRUE |  |  | 14.3% | 0%
SYCAMR_2_UNIT 3 | CHP | 2024 | summer | 1987-01-01 | 387.2667 | 0 | 765 | 74 | 56610 | 0 | Individual | 0.6841% | 0% |  |  | 0.6841% | 0% | TRUE |  |  | 0.6841% | 0%
TENGEN_2_PL1X2 | CHP | 2022 | nonsummer | 1990-03-06 | 8029.5 | 0 | 1060 | 37.7 | 39962 | 0 | Individual | 20.09% | 0% |  |  | 20.09% | 0% | TRUE |  |  | 20.09% | 0%
TENGEN_2_PL1X2 | CHP | 2022 | summer | 1990-03-06 | 7970.46 | 150.2067 | 765 | 37.7 | 28840.5 | 0 | Individual | 27.64% | 0.5208% |  |  | 27.64% | 0.5208% | TRUE |  |  | 27.64% | 0.5208%
TENGEN_2_PL1X2 | CHP | 2023 | nonsummer | 1990-03-06 | 5946 | 0 | 1060 | 37.7 | 39962 | 0 | Individual | 14.88% | 0% |  |  | 14.88% | 0% | TRUE |  |  | 14.88% | 0%
TENGEN_2_PL1X2 | CHP | 2023 | summer | 1990-03-06 | 3307.4083 | 0 | 765 | 37.7 | 28840.5 | 0 | Individual | 11.47% | 0% |  |  | 11.47% | 0% | TRUE |  |  | 11.47% | 0%
TENGEN_2_PL1X2 | CHP | 2024 | nonsummer | 1990-03-06 | 18259.815 | 0 | 1065 | 37.7 | 40150.5 | 0 | Individual | 45.48% | 0% |  |  | 45.48% | 0% | TRUE |  |  | 45.48% | 0%
TENGEN_2_PL1X2 | CHP | 2024 | summer | 1990-03-06 | 18693.1 | 0 | 765 | 37.7 | 28840.5 | 0 | Individual | 64.82% | 0% |  |  | 64.82% | 0% | TRUE |  |  | 64.82% | 0%
YUBACT_1_SUNSWT | CHP | 2022 | nonsummer | 1990-12-27 | 2098.74 | 0 | 1060 | 49.97 | 52968.2 | 0 | Individual | 3.962% | 0% |  |  | 3.962% | 0% | TRUE |  |  | 3.962% | 0%
YUBACT_1_SUNSWT | CHP | 2022 | summer | 1990-12-27 | 8896.3028 | 1439.8918 | 765 | 49.97 | 38227.05 | 0 | Individual | 23.27% | 3.767% |  |  | 23.27% | 3.767% | TRUE |  |  | 23.27% | 3.767%
YUBACT_1_SUNSWT | CHP | 2023 | nonsummer | 1990-12-27 | 7283.1275 | 0 | 1060 | 49.97 | 52968.2 | 0 | Individual | 13.75% | 0% |  |  | 13.75% | 0% | TRUE |  |  | 13.75% | 0%
YUBACT_1_SUNSWT | CHP | 2023 | summer | 1990-12-27 | 3732.759 | 0 | 765 | 49.97 | 38227.05 | 0 | Individual | 9.765% | 0% |  |  | 9.765% | 0% | TRUE |  |  | 9.765% | 0%
YUBACT_1_SUNSWT | CHP | 2024 | nonsummer | 1990-12-27 | 2712.5382 | 0 | 1065 | 49.97 | 53218.05 | 0 | Individual | 5.097% | 0% |  |  | 5.097% | 0% | TRUE |  |  | 5.097% | 0%
YUBACT_1_SUNSWT | CHP | 2024 | summer | 1990-12-27 | 3248.05 | 0 | 765 | 49.97 | 38227.05 | 0 | Individual | 8.497% | 0% |  |  | 8.497% | 0% | TRUE |  |  | 8.497% | 0%
ADLIN_1_UNITS | Geothermal | 2022 | nonsummer | 2008-07-28 | 13286.7238 | 0 | 1060 | 22 | 23320 | 0 | Individual | 56.98% | 0% |  |  | 56.98% | 0% | TRUE |  |  | 56.98% | 0%
ADLIN_1_UNITS | Geothermal | 2022 | summer | 2008-07-28 | 7791.5567 | 0 | 765 | 22 | 16830 | 0 | Individual | 46.3% | 0% |  |  | 46.3% | 0% | TRUE |  |  | 46.3% | 0%
ADLIN_1_UNITS | Geothermal | 2023 | nonsummer | 2008-07-28 | 11906.8862 | 0 | 1060 | 22 | 23320 | 0 | Individual | 51.06% | 0% |  |  | 51.06% | 0% | TRUE |  |  | 51.06% | 0%
ADLIN_1_UNITS | Geothermal | 2023 | summer | 2008-07-28 | 8919.8722 | 0 | 765 | 22 | 16830 | 0 | Individual | 53% | 0% |  |  | 53% | 0% | TRUE |  |  | 53% | 0%
ADLIN_1_UNITS | Geothermal | 2024 | nonsummer | 2008-07-28 | 10403.9923 | 0 | 1065 | 22 | 23430 | 0 | Individual | 44.4% | 0% |  |  | 44.4% | 0% | TRUE |  |  | 44.4% | 0%
ADLIN_1_UNITS | Geothermal | 2024 | summer | 2008-07-28 | 8721.6535 | 0 | 765 | 22 | 16830 | 0 | Individual | 51.82% | 0% |  |  | 51.82% | 0% | TRUE |  |  | 51.82% | 0%
BLM_2_UNITS | Geothermal | 2022 | nonsummer | 1988-12-05 | 1393.6 | 0 | 1060 | 35 | 37100 | 0 | Individual | 3.756% | 0% |  |  | 3.756% | 0% | TRUE |  |  | 3.756% | 0%
BLM_2_UNITS | Geothermal | 2022 | summer | 1988-12-05 | 5350 | 0 | 765 | 35 | 26775 | 0 | Individual | 19.98% | 0% |  |  | 19.98% | 0% | TRUE |  |  | 19.98% | 0%
BLM_2_UNITS | Geothermal | 2023 | nonsummer | 1988-12-05 | 14126.3333 | 0 | 1060 | 35 | 37100 | 0 | Individual | 38.08% | 0% |  |  | 38.08% | 0% | TRUE |  |  | 38.08% | 0%
BLM_2_UNITS | Geothermal | 2023 | summer | 1988-12-05 | 0 | 0 | 765 | 35 | 26775 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
BLM_2_UNITS | Geothermal | 2024 | nonsummer | 1988-12-05 | 3195.485 | 0 | 1065 | 35 | 37275 | 0 | Individual | 8.573% | 0% |  |  | 8.573% | 0% | TRUE |  |  | 8.573% | 0%
BLM_2_UNITS | Geothermal | 2024 | summer | 1988-12-05 | 1008.8 | 0 | 765 | 35 | 26775 | 0 | Individual | 3.768% | 0% |  |  | 3.768% | 0% | TRUE |  |  | 3.768% | 0%
CALGEN_1_UNITS | Geothermal | 2022 | nonsummer | 1987-07-13 | 770 | 0 | 1060 | 55 | 58300 | 0 | Individual | 1.321% | 0% |  |  | 1.321% | 0% | TRUE |  |  | 1.321% | 0%
CALGEN_1_UNITS | Geothermal | 2022 | summer | 1987-07-13 | 884 | 0 | 765 | 55 | 42075 | 0 | Individual | 2.101% | 0% |  |  | 2.101% | 0% | TRUE |  |  | 2.101% | 0%
CALGEN_1_UNITS | Geothermal | 2023 | nonsummer | 1987-07-13 | 4450.7333 | 0 | 1060 | 55 | 58300 | 0 | Individual | 7.634% | 0% |  |  | 7.634% | 0% | TRUE |  |  | 7.634% | 0%
CALGEN_1_UNITS | Geothermal | 2023 | summer | 1987-07-13 | 2967.2 | 0 | 765 | 55 | 42075 | 0 | Individual | 7.052% | 0% |  |  | 7.052% | 0% | TRUE |  |  | 7.052% | 0%
CALGEN_1_UNITS | Geothermal | 2024 | nonsummer | 1987-07-13 | 6482.05 | 0 | 1065 | 55 | 58575 | 0 | Individual | 11.07% | 0% |  |  | 11.07% | 0% | TRUE |  |  | 11.07% | 0%
CALGEN_1_UNITS | Geothermal | 2024 | summer | 1987-07-13 | 325 | 0 | 765 | 55 | 42075 | 0 | Individual | 0.7724% | 0% |  |  | 0.7724% | 0% | TRUE |  |  | 0.7724% | 0%
CASADB_1_CD4GT1 | Geothermal | 2022 | nonsummer | 2024-04-16 | 0 | 0 | 0 | 40.7 | 0 | 1060 | Group |  |  | 22.37% | 0.02554% | 22.37% | 0.02554% | TRUE | 22.37% | 0.02554% | 22.37% | 0.02554%
CASADB_1_CD4GT1 | Geothermal | 2022 | summer | 2024-04-16 | 0 | 0 | 0 | 40.7 | 0 | 765 | Group |  |  | 22.66% | 0% | 22.66% | 0% | TRUE | 22.66% | 0% | 22.66% | 0%
CASADB_1_CD4GT1 | Geothermal | 2023 | nonsummer | 2024-04-16 | 0 | 0 | 0 | 40.7 | 0 | 1060 | Group |  |  | 27.09% | 0.01421% | 27.09% | 0.01421% | TRUE | 27.09% | 0.01421% | 27.09% | 0.01421%
CASADB_1_CD4GT1 | Geothermal | 2023 | summer | 2024-04-16 | 0 | 0 | 0 | 40.7 | 0 | 765 | Group |  |  | 30.93% | 0.1556% | 30.93% | 0.1556% | TRUE | 30.93% | 0.1556% | 30.93% | 0.1556%
CASADB_1_CD4GT1 | Geothermal | 2024 | nonsummer | 2024-04-16 | 733.2833 | 1121.74 | 535 | 40.7 | 21774.5 | 530 | Blended | 3.368% | 5.152% | 24.88% | 0.1267% | 14.07% | 2.651% | TRUE | 24.88% | 0.1267% | 14.07% | 2.651%
CASADB_1_CD4GT1 | Geothermal | 2024 | summer | 2024-04-16 | 244.7683 | 9709.26 | 765 | 40.7 | 31135.5 | 0 | Individual | 0.7861% | 31.18% |  |  | 0.7861% | 31.18% | TRUE |  |  | 0.7861% | 31.18%
CONTRL_1_CASAD2 | Geothermal | 2022 | nonsummer | 2020-12-08 | 102.3217 | 333.4467 | 1060 | 10.5 | 11130 | 0 | Individual | 0.9193% | 2.996% |  |  | 0.9193% | 2.996% | TRUE |  |  | 0.9193% | 2.996%
CONTRL_1_CASAD2 | Geothermal | 2022 | summer | 2020-12-08 | 189.115 | 0 | 765 | 10.5 | 8032.5 | 0 | Individual | 2.354% | 0% |  |  | 2.354% | 0% | TRUE |  |  | 2.354% | 0%
CONTRL_1_CASAD2 | Geothermal | 2023 | nonsummer | 2020-12-08 | 3238.4033 | 185.515 | 1060 | 10.5 | 11130 | 0 | Individual | 29.1% | 1.667% |  |  | 29.1% | 1.667% | TRUE |  |  | 29.1% | 1.667%
CONTRL_1_CASAD2 | Geothermal | 2023 | summer | 2020-12-08 | 44.675 | 1466.7167 | 765 | 10.5 | 8032.5 | 0 | Individual | 0.5562% | 18.26% |  |  | 0.5562% | 18.26% | TRUE |  |  | 0.5562% | 18.26%
CONTRL_1_CASAD2 | Geothermal | 2024 | nonsummer | 2020-12-08 | 209.3833 | 567.4 | 1065 | 10.5 | 11182.5 | 0 | Individual | 1.872% | 5.074% |  |  | 1.872% | 5.074% | TRUE |  |  | 1.872% | 5.074%
CONTRL_1_CASAD2 | Geothermal | 2024 | summer | 2020-12-08 | 362.7 | 2474.95 | 765 | 10.5 | 8032.5 | 0 | Individual | 4.515% | 30.81% |  |  | 4.515% | 30.81% | TRUE |  |  | 4.515% | 30.81%
GEYS11_7_UNIT11 | Geothermal | 2022 | nonsummer | 1975-01-01 | 20775.8047 | 0 | 1060 | 86.8 | 92008 | 0 | Individual | 22.58% | 0% |  |  | 22.58% | 0% | TRUE |  |  | 22.58% | 0%
GEYS11_7_UNIT11 | Geothermal | 2022 | summer | 1975-01-01 | 9744.4167 | 0 | 765 | 86.8 | 66402 | 0 | Individual | 14.67% | 0% |  |  | 14.67% | 0% | TRUE |  |  | 14.67% | 0%
GEYS11_7_UNIT11 | Geothermal | 2023 | nonsummer | 1975-01-01 | 12796.058 | 0 | 1060 | 86.8 | 92008 | 0 | Individual | 13.91% | 0% |  |  | 13.91% | 0% | TRUE |  |  | 13.91% | 0%
GEYS11_7_UNIT11 | Geothermal | 2023 | summer | 1975-01-01 | 14859.3698 | 0 | 765 | 86.8 | 66402 | 0 | Individual | 22.38% | 0% |  |  | 22.38% | 0% | TRUE |  |  | 22.38% | 0%
GEYS11_7_UNIT11 | Geothermal | 2024 | nonsummer | 1975-01-01 | 19826.6133 | 0 | 1065 | 86.8 | 92442 | 0 | Individual | 21.45% | 0% |  |  | 21.45% | 0% | TRUE |  |  | 21.45% | 0%
GEYS11_7_UNIT11 | Geothermal | 2024 | summer | 1975-01-01 | 24688.2533 | 0 | 765 | 86.8 | 66402 | 0 | Individual | 37.18% | 0% |  |  | 37.18% | 0% | TRUE |  |  | 37.18% | 0%
GEYS12_7_UNIT12 | Geothermal | 2022 | nonsummer | 1979-01-01 | 13347.1333 | 0 | 1060 | 57 | 60420 | 0 | Individual | 22.09% | 0% |  |  | 22.09% | 0% | TRUE |  |  | 22.09% | 0%
GEYS12_7_UNIT12 | Geothermal | 2022 | summer | 1979-01-01 | 11255.2 | 0 | 765 | 57 | 43605 | 0 | Individual | 25.81% | 0% |  |  | 25.81% | 0% | TRUE |  |  | 25.81% | 0%
GEYS12_7_UNIT12 | Geothermal | 2023 | nonsummer | 1979-01-01 | 16753 | 0 | 1060 | 57 | 60420 | 0 | Individual | 27.73% | 0% |  |  | 27.73% | 0% | TRUE |  |  | 27.73% | 0%
GEYS12_7_UNIT12 | Geothermal | 2023 | summer | 1979-01-01 | 12915 | 0 | 765 | 57 | 43605 | 0 | Individual | 29.62% | 0% |  |  | 29.62% | 0% | TRUE |  |  | 29.62% | 0%
GEYS12_7_UNIT12 | Geothermal | 2024 | nonsummer | 1979-01-01 | 14991.5 | 0 | 1065 | 57 | 60705 | 0 | Individual | 24.7% | 0% |  |  | 24.7% | 0% | TRUE |  |  | 24.7% | 0%
GEYS12_7_UNIT12 | Geothermal | 2024 | summer | 1979-01-01 | 12486.7782 | 0 | 765 | 57 | 43605 | 0 | Individual | 28.64% | 0% |  |  | 28.64% | 0% | TRUE |  |  | 28.64% | 0%
GEYS13_7_UNIT13 | Geothermal | 2022 | nonsummer | 1980-01-01 | 22803.7333 | 0 | 1060 | 73 | 77380 | 0 | Individual | 29.47% | 0% |  |  | 29.47% | 0% | TRUE |  |  | 29.47% | 0%
GEYS13_7_UNIT13 | Geothermal | 2022 | summer | 1980-01-01 | 18065.2 | 0 | 765 | 73 | 55845 | 0 | Individual | 32.35% | 0% |  |  | 32.35% | 0% | TRUE |  |  | 32.35% | 0%
GEYS13_7_UNIT13 | Geothermal | 2023 | nonsummer | 1980-01-01 | 23982.8 | 0 | 1060 | 73 | 77380 | 0 | Individual | 30.99% | 0% |  |  | 30.99% | 0% | TRUE |  |  | 30.99% | 0%
GEYS13_7_UNIT13 | Geothermal | 2023 | summer | 1980-01-01 | 21224.7333 | 0 | 765 | 73 | 55845 | 0 | Individual | 38.01% | 0% |  |  | 38.01% | 0% | TRUE |  |  | 38.01% | 0%
GEYS13_7_UNIT13 | Geothermal | 2024 | nonsummer | 1980-01-01 | 29975.4167 | 0 | 1065 | 73 | 77745 | 0 | Individual | 38.56% | 0% |  |  | 38.56% | 0% | TRUE |  |  | 38.56% | 0%
GEYS13_7_UNIT13 | Geothermal | 2024 | summer | 1980-01-01 | 20145.8 | 0 | 765 | 73 | 55845 | 0 | Individual | 36.07% | 0% |  |  | 36.07% | 0% | TRUE |  |  | 36.07% | 0%
GEYS14_7_UNIT14 | Geothermal | 2022 | nonsummer | 1980-01-01 | 9732.1167 | 0 | 1060 | 70 | 74200 | 0 | Individual | 13.12% | 0% |  |  | 13.12% | 0% | TRUE |  |  | 13.12% | 0%
GEYS14_7_UNIT14 | Geothermal | 2022 | summer | 1980-01-01 | 10942.15 | 0 | 765 | 70 | 53550 | 0 | Individual | 20.43% | 0% |  |  | 20.43% | 0% | TRUE |  |  | 20.43% | 0%
GEYS14_7_UNIT14 | Geothermal | 2023 | nonsummer | 1980-01-01 | 14967 | 0 | 1060 | 70 | 74200 | 0 | Individual | 20.17% | 0% |  |  | 20.17% | 0% | TRUE |  |  | 20.17% | 0%
GEYS14_7_UNIT14 | Geothermal | 2023 | summer | 1980-01-01 | 12987 | 0 | 765 | 70 | 53550 | 0 | Individual | 24.25% | 0% |  |  | 24.25% | 0% | TRUE |  |  | 24.25% | 0%
GEYS14_7_UNIT14 | Geothermal | 2024 | nonsummer | 1980-01-01 | 15201.8167 | 0 | 1065 | 70 | 74550 | 0 | Individual | 20.39% | 0% |  |  | 20.39% | 0% | TRUE |  |  | 20.39% | 0%
GEYS14_7_UNIT14 | Geothermal | 2024 | summer | 1980-01-01 | 18911.2667 | 0 | 765 | 70 | 53550 | 0 | Individual | 35.32% | 0% |  |  | 35.32% | 0% | TRUE |  |  | 35.32% | 0%
GEYS16_7_UNIT16 | Geothermal | 2022 | nonsummer | 1985-01-01 | 17322.1 | 0 | 1060 | 63 | 66780 | 0 | Individual | 25.94% | 0% |  |  | 25.94% | 0% | TRUE |  |  | 25.94% | 0%
GEYS16_7_UNIT16 | Geothermal | 2022 | summer | 1985-01-01 | 11905.8 | 0 | 765 | 63 | 48195 | 0 | Individual | 24.7% | 0% |  |  | 24.7% | 0% | TRUE |  |  | 24.7% | 0%
GEYS16_7_UNIT16 | Geothermal | 2023 | nonsummer | 1985-01-01 | 14685 | 0 | 1060 | 63 | 66780 | 0 | Individual | 21.99% | 0% |  |  | 21.99% | 0% | TRUE |  |  | 21.99% | 0%
GEYS16_7_UNIT16 | Geothermal | 2023 | summer | 1985-01-01 | 14112 | 0 | 765 | 63 | 48195 | 0 | Individual | 29.28% | 0% |  |  | 29.28% | 0% | TRUE |  |  | 29.28% | 0%
GEYS16_7_UNIT16 | Geothermal | 2024 | nonsummer | 1985-01-01 | 16733.1667 | 0 | 1065 | 63 | 67095 | 0 | Individual | 24.94% | 0% |  |  | 24.94% | 0% | TRUE |  |  | 24.94% | 0%
GEYS16_7_UNIT16 | Geothermal | 2024 | summer | 1985-01-01 | 14227 | 0 | 765 | 63 | 48195 | 0 | Individual | 29.52% | 0% |  |  | 29.52% | 0% | TRUE |  |  | 29.52% | 0%
GEYS17_7_UNIT17 | Geothermal | 2022 | nonsummer | 1982-01-01 | 15473.2533 | 0 | 1060 | 75.5 | 80030 | 0 | Individual | 19.33% | 0% |  |  | 19.33% | 0% | TRUE |  |  | 19.33% | 0%
GEYS17_7_UNIT17 | Geothermal | 2022 | summer | 1982-01-01 | 17191.4833 | 0 | 765 | 75.5 | 57757.5 | 0 | Individual | 29.76% | 0% |  |  | 29.76% | 0% | TRUE |  |  | 29.76% | 0%
GEYS17_7_UNIT17 | Geothermal | 2023 | nonsummer | 1982-01-01 | 17446.9667 | 0 | 1060 | 75.5 | 80030 | 0 | Individual | 21.8% | 0% |  |  | 21.8% | 0% | TRUE |  |  | 21.8% | 0%
GEYS17_7_UNIT17 | Geothermal | 2023 | summer | 1982-01-01 | 16665.8833 | 0 | 765 | 75.5 | 57757.5 | 0 | Individual | 28.85% | 0% |  |  | 28.85% | 0% | TRUE |  |  | 28.85% | 0%
GEYS17_7_UNIT17 | Geothermal | 2024 | nonsummer | 1982-01-01 | 14346.1167 | 0 | 1065 | 75.5 | 80407.5 | 0 | Individual | 17.84% | 0% |  |  | 17.84% | 0% | TRUE |  |  | 17.84% | 0%
GEYS17_7_UNIT17 | Geothermal | 2024 | summer | 1982-01-01 | 17548.55 | 0 | 765 | 75.5 | 57757.5 | 0 | Individual | 30.38% | 0% |  |  | 30.38% | 0% | TRUE |  |  | 30.38% | 0%
GEYS18_7_UNIT18 | Geothermal | 2022 | nonsummer | 1983-01-01 | 27970.3333 | 0 | 1060 | 72 | 76320 | 0 | Individual | 36.65% | 0% |  |  | 36.65% | 0% | TRUE |  |  | 36.65% | 0%
GEYS18_7_UNIT18 | Geothermal | 2022 | summer | 1983-01-01 | 21961.5 | 0 | 765 | 72 | 55080 | 0 | Individual | 39.87% | 0% |  |  | 39.87% | 0% | TRUE |  |  | 39.87% | 0%
GEYS18_7_UNIT18 | Geothermal | 2023 | nonsummer | 1983-01-01 | 32164.5 | 0 | 1060 | 72 | 76320 | 0 | Individual | 42.14% | 0% |  |  | 42.14% | 0% | TRUE |  |  | 42.14% | 0%
GEYS18_7_UNIT18 | Geothermal | 2023 | summer | 1983-01-01 | 26291 | 0 | 765 | 72 | 55080 | 0 | Individual | 47.73% | 0% |  |  | 47.73% | 0% | TRUE |  |  | 47.73% | 0%
GEYS18_7_UNIT18 | Geothermal | 2024 | nonsummer | 1983-01-01 | 33372.4 | 0 | 1065 | 72 | 76680 | 0 | Individual | 43.52% | 0% |  |  | 43.52% | 0% | TRUE |  |  | 43.52% | 0%
GEYS18_7_UNIT18 | Geothermal | 2024 | summer | 1983-01-01 | 23683.6727 | 0 | 765 | 72 | 55080 | 0 | Individual | 43% | 0% |  |  | 43% | 0% | TRUE |  |  | 43% | 0%
GEYS20_7_UNIT20 | Geothermal | 2022 | nonsummer | 1985-01-01 | 12997.75 | 0 | 1060 | 50 | 53000 | 0 | Individual | 24.52% | 0% |  |  | 24.52% | 0% | TRUE |  |  | 24.52% | 0%
GEYS20_7_UNIT20 | Geothermal | 2022 | summer | 1985-01-01 | 11178.3833 | 0 | 765 | 50 | 38250 | 0 | Individual | 29.22% | 0% |  |  | 29.22% | 0% | TRUE |  |  | 29.22% | 0%
GEYS20_7_UNIT20 | Geothermal | 2023 | nonsummer | 1985-01-01 | 15690.2652 | 0 | 1060 | 50 | 53000 | 0 | Individual | 29.6% | 0% |  |  | 29.6% | 0% | TRUE |  |  | 29.6% | 0%
GEYS20_7_UNIT20 | Geothermal | 2023 | summer | 1985-01-01 | 11501.3 | 0 | 765 | 50 | 38250 | 0 | Individual | 30.07% | 0% |  |  | 30.07% | 0% | TRUE |  |  | 30.07% | 0%
GEYS20_7_UNIT20 | Geothermal | 2024 | nonsummer | 1985-01-01 | 16772.5333 | 0 | 1065 | 50 | 53250 | 0 | Individual | 31.5% | 0% |  |  | 31.5% | 0% | TRUE |  |  | 31.5% | 0%
GEYS20_7_UNIT20 | Geothermal | 2024 | summer | 1985-01-01 | 12632.1333 | 0 | 765 | 50 | 38250 | 0 | Individual | 33.03% | 0% |  |  | 33.03% | 0% | TRUE |  |  | 33.03% | 0%
GYS5X6_7_UNITS | Geothermal | 2022 | nonsummer | 1971-01-01 | 17217.2017 | 0 | 1060 | 98.43 | 104335.8 | 0 | Individual | 16.5% | 0% |  |  | 16.5% | 0% | TRUE |  |  | 16.5% | 0%
GYS5X6_7_UNITS | Geothermal | 2022 | summer | 1971-01-01 | 14875.1333 | 0 | 765 | 98.43 | 75298.95 | 0 | Individual | 19.75% | 0% |  |  | 19.75% | 0% | TRUE |  |  | 19.75% | 0%
GYS5X6_7_UNITS | Geothermal | 2023 | nonsummer | 1971-01-01 | 34687.7333 | 0 | 1060 | 98.43 | 104335.8 | 0 | Individual | 33.25% | 0% |  |  | 33.25% | 0% | TRUE |  |  | 33.25% | 0%
GYS5X6_7_UNITS | Geothermal | 2023 | summer | 1971-01-01 | 22264.95 | 0 | 765 | 98.43 | 75298.95 | 0 | Individual | 29.57% | 0% |  |  | 29.57% | 0% | TRUE |  |  | 29.57% | 0%
GYS5X6_7_UNITS | Geothermal | 2024 | nonsummer | 1971-01-01 | 49216.7833 | 0 | 1065 | 98.43 | 104827.95 | 0 | Individual | 46.95% | 0% |  |  | 46.95% | 0% | TRUE |  |  | 46.95% | 0%
GYS5X6_7_UNITS | Geothermal | 2024 | summer | 1971-01-01 | 17296.5 | 0 | 765 | 98.43 | 75298.95 | 0 | Individual | 22.97% | 0% |  |  | 22.97% | 0% | TRUE |  |  | 22.97% | 0%
GYS7X8_7_UNITS | Geothermal | 2022 | nonsummer | 1972-01-01 | 19603.7162 | 0 | 1060 | 95.8 | 101548 | 0 | Individual | 19.3% | 0% |  |  | 19.3% | 0% | TRUE |  |  | 19.3% | 0%
GYS7X8_7_UNITS | Geothermal | 2022 | summer | 1972-01-01 | 13286.3333 | 0 | 765 | 95.8 | 73287 | 0 | Individual | 18.13% | 0% |  |  | 18.13% | 0% | TRUE |  |  | 18.13% | 0%
GYS7X8_7_UNITS | Geothermal | 2023 | nonsummer | 1972-01-01 | 17465.4167 | 0 | 1060 | 95.8 | 101548 | 0 | Individual | 17.2% | 0% |  |  | 17.2% | 0% | TRUE |  |  | 17.2% | 0%
GYS7X8_7_UNITS | Geothermal | 2023 | summer | 1972-01-01 | 14389 | 0 | 765 | 95.8 | 73287 | 0 | Individual | 19.63% | 0% |  |  | 19.63% | 0% | TRUE |  |  | 19.63% | 0%
GYS7X8_7_UNITS | Geothermal | 2024 | nonsummer | 1972-01-01 | 25425.9467 | 0 | 1065 | 95.8 | 102027 | 0 | Individual | 24.92% | 0% |  |  | 24.92% | 0% | TRUE |  |  | 24.92% | 0%
GYS7X8_7_UNITS | Geothermal | 2024 | summer | 1972-01-01 | 15226.4323 | 0 | 765 | 95.8 | 73287 | 0 | Individual | 20.78% | 0% |  |  | 20.78% | 0% | TRUE |  |  | 20.78% | 0%
NAVYII_2_UNITS | Geothermal | 2022 | nonsummer | 1989-12-23 | 1307 | 0 | 1060 | 47 | 49820 | 0 | Individual | 2.623% | 0% |  |  | 2.623% | 0% | TRUE |  |  | 2.623% | 0%
NAVYII_2_UNITS | Geothermal | 2022 | summer | 1989-12-23 | 0 | 0 | 765 | 47 | 35955 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
NAVYII_2_UNITS | Geothermal | 2023 | nonsummer | 1989-12-23 | 2550 | 0 | 1060 | 47 | 49820 | 0 | Individual | 5.118% | 0% |  |  | 5.118% | 0% | TRUE |  |  | 5.118% | 0%
NAVYII_2_UNITS | Geothermal | 2023 | summer | 1989-12-23 | 5545 | 0 | 765 | 47 | 35955 | 0 | Individual | 15.42% | 0% |  |  | 15.42% | 0% | TRUE |  |  | 15.42% | 0%
NAVYII_2_UNITS | Geothermal | 2024 | nonsummer | 1989-12-23 | 8667.485 | 0 | 1065 | 47 | 50055 | 0 | Individual | 17.32% | 0% |  |  | 17.32% | 0% | TRUE |  |  | 17.32% | 0%
NAVYII_2_UNITS | Geothermal | 2024 | summer | 1989-12-23 | 450 | 0 | 765 | 47 | 35955 | 0 | Individual | 1.252% | 0% |  |  | 1.252% | 0% | TRUE |  |  | 1.252% | 0%
NCPA_7_GP1UN1 | Geothermal | 2022 | nonsummer | 1983-01-01 | 618.72 | 0 | 1060 | 38.85 | 41181 | 0 | Individual | 1.502% | 0% |  |  | 1.502% | 0% | TRUE |  |  | 1.502% | 0%
NCPA_7_GP1UN1 | Geothermal | 2022 | summer | 1983-01-01 | 0 | 0 | 765 | 38.85 | 29720.25 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
NCPA_7_GP1UN1 | Geothermal | 2023 | nonsummer | 1983-01-01 | 26592.825 | 0 | 1060 | 38.85 | 41181 | 0 | Individual | 64.58% | 0% |  |  | 64.58% | 0% | TRUE |  |  | 64.58% | 0%
NCPA_7_GP1UN1 | Geothermal | 2023 | summer | 1983-01-01 | 29720.25 | 0 | 765 | 38.85 | 29720.25 | 0 | Individual | 100% | 0% |  |  | 100% | 0% | TRUE |  |  | 100% | 0%
NCPA_7_GP1UN1 | Geothermal | 2024 | nonsummer | 1983-01-01 | 17858.6975 | 0 | 1065 | 38.85 | 41375.25 | 0 | Individual | 43.16% | 0% |  |  | 43.16% | 0% | TRUE |  |  | 43.16% | 0%
NCPA_7_GP1UN1 | Geothermal | 2024 | summer | 1983-01-01 | 0 | 0 | 765 | 38.85 | 29720.25 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
NCPA_7_GP1UN2 | Geothermal | 2022 | nonsummer | 1983-01-01 | 306.78 | 0 | 1060 | 50 | 53000 | 0 | Individual | 0.5788% | 0% |  |  | 0.5788% | 0% | TRUE |  |  | 0.5788% | 0%
NCPA_7_GP1UN2 | Geothermal | 2022 | summer | 1983-01-01 | 0 | 0 | 765 | 50 | 38250 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
NCPA_7_GP1UN2 | Geothermal | 2023 | nonsummer | 1983-01-01 | 6157.1207 | 0 | 1060 | 50 | 53000 | 0 | Individual | 11.62% | 0% |  |  | 11.62% | 0% | TRUE |  |  | 11.62% | 0%
NCPA_7_GP1UN2 | Geothermal | 2023 | summer | 1983-01-01 | 3235.14 | 0 | 765 | 50 | 38250 | 0 | Individual | 8.458% | 0% |  |  | 8.458% | 0% | TRUE |  |  | 8.458% | 0%
NCPA_7_GP1UN2 | Geothermal | 2024 | nonsummer | 1983-01-01 | 15000 | 0 | 1065 | 50 | 53250 | 0 | Individual | 28.17% | 0% |  |  | 28.17% | 0% | TRUE |  |  | 28.17% | 0%
NCPA_7_GP1UN2 | Geothermal | 2024 | summer | 1983-01-01 | 21500 | 0 | 765 | 50 | 38250 | 0 | Individual | 56.21% | 0% |  |  | 56.21% | 0% | TRUE |  |  | 56.21% | 0%
NCPA_7_GP2UN3 | Geothermal | 2022 | nonsummer | 1985-01-01 | 44753.1 | 0 | 1060 | 42.42 | 44965.2 | 0 | Individual | 99.53% | 0% |  |  | 99.53% | 0% | TRUE |  |  | 99.53% | 0%
NCPA_7_GP2UN3 | Geothermal | 2022 | summer | 1985-01-01 | 32451.3 | 0 | 765 | 42.42 | 32451.3 | 0 | Individual | 100% | 0% |  |  | 100% | 0% | TRUE |  |  | 100% | 0%
NCPA_7_GP2UN3 | Geothermal | 2023 | nonsummer | 1985-01-01 | 44541 | 0 | 1060 | 42.42 | 44965.2 | 0 | Individual | 99.06% | 0% |  |  | 99.06% | 0% | TRUE |  |  | 99.06% | 0%
NCPA_7_GP2UN3 | Geothermal | 2023 | summer | 1985-01-01 | 32451.3 | 0 | 765 | 42.42 | 32451.3 | 0 | Individual | 100% | 0% |  |  | 100% | 0% | TRUE |  |  | 100% | 0%
NCPA_7_GP2UN3 | Geothermal | 2024 | nonsummer | 1985-01-01 | 0 | 0 | 1065 | 42.42 | 45177.3 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
NCPA_7_GP2UN3 | Geothermal | 2024 | summer | 1985-01-01 | 0 | 0 | 765 | 42.42 | 32451.3 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
NCPA_7_GP2UN4 | Geothermal | 2022 | nonsummer | 1986-01-01 | 0 | 0 | 1060 | 52.73 | 55893.8 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
NCPA_7_GP2UN4 | Geothermal | 2022 | summer | 1986-01-01 | 0 | 0 | 765 | 52.73 | 40338.45 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
NCPA_7_GP2UN4 | Geothermal | 2023 | nonsummer | 1986-01-01 | 6809.3915 | 0 | 1060 | 52.73 | 55893.8 | 0 | Individual | 12.18% | 0% |  |  | 12.18% | 0% | TRUE |  |  | 12.18% | 0%
NCPA_7_GP2UN4 | Geothermal | 2023 | summer | 1986-01-01 | 18287.6428 | 0 | 765 | 52.73 | 40338.45 | 0 | Individual | 45.34% | 0% |  |  | 45.34% | 0% | TRUE |  |  | 45.34% | 0%
NCPA_7_GP2UN4 | Geothermal | 2024 | nonsummer | 1986-01-01 | 85.46 | 0 | 1065 | 52.73 | 56157.45 | 0 | Individual | 0.1522% | 0% |  |  | 0.1522% | 0% | TRUE |  |  | 0.1522% | 0%
NCPA_7_GP2UN4 | Geothermal | 2024 | summer | 1986-01-01 | 0 | 0 | 765 | 52.73 | 40338.45 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SANTFG_7_UNITS | Geothermal | 2022 | nonsummer | 1984-03-14 | 8975.5 | 0 | 1060 | 72 | 76320 | 0 | Individual | 11.76% | 0% |  |  | 11.76% | 0% | TRUE |  |  | 11.76% | 0%
SANTFG_7_UNITS | Geothermal | 2022 | summer | 1984-03-14 | 9266 | 0 | 765 | 72 | 55080 | 0 | Individual | 16.82% | 0% |  |  | 16.82% | 0% | TRUE |  |  | 16.82% | 0%
SANTFG_7_UNITS | Geothermal | 2023 | nonsummer | 1984-03-14 | 16016.9333 | 0 | 1060 | 72 | 76320 | 0 | Individual | 20.99% | 0% |  |  | 20.99% | 0% | TRUE |  |  | 20.99% | 0%
SANTFG_7_UNITS | Geothermal | 2023 | summer | 1984-03-14 | 12930 | 0 | 765 | 72 | 55080 | 0 | Individual | 23.47% | 0% |  |  | 23.47% | 0% | TRUE |  |  | 23.47% | 0%
SANTFG_7_UNITS | Geothermal | 2024 | nonsummer | 1984-03-14 | 18954.35 | 0 | 1065 | 72 | 76680 | 0 | Individual | 24.72% | 0% |  |  | 24.72% | 0% | TRUE |  |  | 24.72% | 0%
SANTFG_7_UNITS | Geothermal | 2024 | summer | 1984-03-14 | 13767.836 | 0 | 765 | 72 | 55080 | 0 | Individual | 25% | 0% |  |  | 25% | 0% | TRUE |  |  | 25% | 0%
SMUDGO_7_UNIT 1 | Geothermal | 2022 | nonsummer | 1983-01-01 | 43358.7 | 0 | 1060 | 64.8 | 68688 | 0 | Individual | 63.12% | 0% |  |  | 63.12% | 0% | TRUE |  |  | 63.12% | 0%
SMUDGO_7_UNIT 1 | Geothermal | 2022 | summer | 1983-01-01 | 17223.72 | 0 | 765 | 64.8 | 49572 | 0 | Individual | 34.74% | 0% |  |  | 34.74% | 0% | TRUE |  |  | 34.74% | 0%
SMUDGO_7_UNIT 1 | Geothermal | 2023 | nonsummer | 1983-01-01 | 16693.8667 | 0 | 1060 | 64.8 | 68688 | 0 | Individual | 24.3% | 0% |  |  | 24.3% | 0% | TRUE |  |  | 24.3% | 0%
SMUDGO_7_UNIT 1 | Geothermal | 2023 | summer | 1983-01-01 | 10154 | 0 | 765 | 64.8 | 49572 | 0 | Individual | 20.48% | 0% |  |  | 20.48% | 0% | TRUE |  |  | 20.48% | 0%
SMUDGO_7_UNIT 1 | Geothermal | 2024 | nonsummer | 1983-01-01 | 14302.6667 | 0 | 1065 | 64.8 | 69012 | 0 | Individual | 20.72% | 0% |  |  | 20.72% | 0% | TRUE |  |  | 20.72% | 0%
SMUDGO_7_UNIT 1 | Geothermal | 2024 | summer | 1983-01-01 | 10902.7333 | 0 | 765 | 64.8 | 49572 | 0 | Individual | 21.99% | 0% |  |  | 21.99% | 0% | TRUE |  |  | 21.99% | 0%
BARRE_2_ALASB1 | Hybrid_BattStorage | 2022 | nonsummer | 45240 | 0 | 0 | 0 | 5 | 0 | 1060 | Group |  |  | 19.29% | 0.8894% | 19.29% | 0.8894% | TRUE | 19.29% | 0.8894% | 19.29% | 0.8894%
BARRE_2_ALASB1 | Hybrid_BattStorage | 2022 | summer | 45240 | 0 | 0 | 0 | 5 | 0 | 765 | Group |  |  | 13.98% | 0.5268% | 13.98% | 0.5268% | TRUE | 13.98% | 0.5268% | 13.98% | 0.5268%
BARRE_2_ALASB1 | Hybrid_BattStorage | 2023 | nonsummer | 45240 | 0 | 0 | 260 | 5 | 1300 | 800 | Blended | 0% | 0% | 13.86% | 0% | 10.46% | 0% | TRUE | 13.86% | 0% | 10.46% | 0%
BARRE_2_ALASB1 | Hybrid_BattStorage | 2023 | summer | 45240 | 0 | 0 | 0 | 5 | 0 | 765 | Group |  |  | 5.01% | 0% | 5.01% | 0% | TRUE | 5.01% | 0% | 5.01% | 0%
BARRE_2_ALASB1 | Hybrid_BattStorage | 2024 | nonsummer | 45240 | 151.6667 | 0 | 1065 | 5 | 5325 | 0 | Individual | 2.848% | 0% |  |  | 2.848% | 0% | TRUE |  |  | 2.848% | 0%
BARRE_2_ALASB1 | Hybrid_BattStorage | 2024 | summer | 45240 | 85 | 0 | 765 | 5 | 3825 | 0 | Individual | 2.222% | 0% |  |  | 2.222% | 0% | TRUE |  |  | 2.222% | 0%
CUYAMA_6_SB3SB1 | Hybrid_BattStorage | 2022 | nonsummer | 45293 | 0 | 0 | 0 | 3 | 0 | 1060 | Group |  |  | 19.29% | 0.8894% | 19.29% | 0.8894% | TRUE | 19.29% | 0.8894% | 19.29% | 0.8894%
CUYAMA_6_SB3SB1 | Hybrid_BattStorage | 2022 | summer | 45293 | 0 | 0 | 0 | 3 | 0 | 765 | Group |  |  | 13.98% | 0.5268% | 13.98% | 0.5268% | TRUE | 13.98% | 0.5268% | 13.98% | 0.5268%
CUYAMA_6_SB3SB1 | Hybrid_BattStorage | 2023 | nonsummer | 45293 | 0 | 0 | 0 | 3 | 0 | 1060 | Group |  |  | 13.86% | 0% | 13.86% | 0% | TRUE | 13.86% | 0% | 13.86% | 0%
CUYAMA_6_SB3SB1 | Hybrid_BattStorage | 2023 | summer | 45293 | 0 | 0 | 0 | 3 | 0 | 765 | Group |  |  | 5.01% | 0% | 5.01% | 0% | TRUE | 5.01% | 0% | 5.01% | 0%
CUYAMA_6_SB3SB1 | Hybrid_BattStorage | 2024 | nonsummer | 45293 | 0 | 0 | 1060 | 3 | 3180 | 5 | Blended | 0% | 0% | 36.6% | 0% | 0.1718% | 0% | TRUE | 36.6% | 0% | 0.1718% | 0%
CUYAMA_6_SB3SB1 | Hybrid_BattStorage | 2024 | summer | 45293 | 30 | 0 | 765 | 3 | 2295 | 0 | Individual | 1.307% | 0% |  |  | 1.307% | 0% | TRUE |  |  | 1.307% | 0%
DELAMO_2_ALASB2 | Hybrid_BattStorage | 2022 | nonsummer | 45240 | 0 | 0 | 0 | 5 | 0 | 1060 | Group |  |  | 19.29% | 0.8894% | 19.29% | 0.8894% | TRUE | 19.29% | 0.8894% | 19.29% | 0.8894%
DELAMO_2_ALASB2 | Hybrid_BattStorage | 2022 | summer | 45240 | 0 | 0 | 0 | 5 | 0 | 765 | Group |  |  | 13.98% | 0.5268% | 13.98% | 0.5268% | TRUE | 13.98% | 0.5268% | 13.98% | 0.5268%
DELAMO_2_ALASB2 | Hybrid_BattStorage | 2023 | nonsummer | 45240 | 200 | 0 | 260 | 5 | 1300 | 800 | Blended | 15.38% | 0% | 13.86% | 0% | 14.23% | 0% | TRUE | 13.86% | 0% | 14.23% | 0%
DELAMO_2_ALASB2 | Hybrid_BattStorage | 2023 | summer | 45240 | 0 | 0 | 0 | 5 | 0 | 765 | Group |  |  | 5.01% | 0% | 5.01% | 0% | TRUE | 5.01% | 0% | 5.01% | 0%
DELAMO_2_ALASB2 | Hybrid_BattStorage | 2024 | nonsummer | 45240 | 400 | 0 | 1065 | 5 | 5325 | 0 | Individual | 7.512% | 0% |  |  | 7.512% | 0% | TRUE |  |  | 7.512% | 0%
DELAMO_2_ALASB2 | Hybrid_BattStorage | 2024 | summer | 45240 | 50 | 0 | 765 | 5 | 3825 | 0 | Individual | 1.307% | 0% |  |  | 1.307% | 0% | TRUE |  |  | 1.307% | 0%
DSFLWR_2_W9CSB1 | Hybrid_BattStorage | 2022 | nonsummer | 45785 | 0 | 0 | 0 | 52 | 0 | 1060 | Group |  |  | 19.29% | 0.8894% | 19.29% | 0.8894% | TRUE | 19.29% | 0.8894% | 19.29% | 0.8894%
DSFLWR_2_W9CSB1 | Hybrid_BattStorage | 2022 | summer | 45785 | 0 | 0 | 0 | 52 | 0 | 765 | Group |  |  | 13.98% | 0.5268% | 13.98% | 0.5268% | TRUE | 13.98% | 0.5268% | 13.98% | 0.5268%
DSFLWR_2_W9CSB1 | Hybrid_BattStorage | 2023 | nonsummer | 45785 | 3655.62 | 0 | 0 | 52 | 0 | 1060 | Group |  |  | 13.86% | 0% | 13.86% | 0% | TRUE | 13.86% | 0% | 13.86% | 0%
DSFLWR_2_W9CSB1 | Hybrid_BattStorage | 2023 | summer | 45785 | 2735.6 | 0 | 0 | 52 | 0 | 765 | Group |  |  | 5.01% | 0% | 5.01% | 0% | TRUE | 5.01% | 0% | 5.01% | 0%
DSFLWR_2_W9CSB1 | Hybrid_BattStorage | 2024 | nonsummer | 45785 | 35798 | 0 | 0 | 52 | 0 | 1065 | Group |  |  | 36.6% | 0% | 36.6% | 0% | TRUE | 36.6% | 0% | 36.6% | 0%
DSFLWR_2_W9CSB1 | Hybrid_BattStorage | 2024 | summer | 45785 | 459 | 0 | 0 | 52 | 0 | 765 | Group |  |  | 24.91% | 0% | 24.91% | 0% | TRUE | 24.91% | 0% | 24.91% | 0%
DSFLWR_2_W9CSB2 | Hybrid_BattStorage | 2022 | nonsummer | 45785 | 0 | 0 | 0 | 36 | 0 | 1060 | Group |  |  | 19.29% | 0.8894% | 19.29% | 0.8894% | TRUE | 19.29% | 0.8894% | 19.29% | 0.8894%
DSFLWR_2_W9CSB2 | Hybrid_BattStorage | 2022 | summer | 45785 | 0 | 0 | 0 | 36 | 0 | 765 | Group |  |  | 13.98% | 0.5268% | 13.98% | 0.5268% | TRUE | 13.98% | 0.5268% | 13.98% | 0.5268%
DSFLWR_2_W9CSB2 | Hybrid_BattStorage | 2023 | nonsummer | 45785 | 2776.19 | 0 | 0 | 36 | 0 | 1060 | Group |  |  | 13.86% | 0% | 13.86% | 0% | TRUE | 13.86% | 0% | 13.86% | 0%
DSFLWR_2_W9CSB2 | Hybrid_BattStorage | 2023 | summer | 45785 | 2842.4833 | 0 | 0 | 36 | 0 | 765 | Group |  |  | 5.01% | 0% | 5.01% | 0% | TRUE | 5.01% | 0% | 5.01% | 0%
DSFLWR_2_W9CSB2 | Hybrid_BattStorage | 2024 | nonsummer | 45785 | 25525 | 0 | 0 | 36 | 0 | 1065 | Group |  |  | 36.6% | 0% | 36.6% | 0% | TRUE | 36.6% | 0% | 36.6% | 0%
DSFLWR_2_W9CSB2 | Hybrid_BattStorage | 2024 | summer | 45785 | 6048 | 0 | 0 | 36 | 0 | 765 | Group |  |  | 24.91% | 0% | 24.91% | 0% | TRUE | 24.91% | 0% | 24.91% | 0%
EDWARD_2_E21SB1 | Hybrid_BattStorage | 2022 | nonsummer | 44800 | 2708.5667 | 0 | 305 | 71 | 21655 | 755 | Blended | 12.51% | 0% | 19.29% | 0.8894% | 17.34% | 0.6335% | TRUE | 19.29% | 0.8894% | 17.34% | 0.6335%
EDWARD_2_E21SB1 | Hybrid_BattStorage | 2022 | summer | 44800 | 3684.7333 | 0 | 330 | 71 | 23430 | 435 | Blended | 15.73% | 0% | 13.98% | 0.5268% | 14.73% | 0.2995% | TRUE | 13.98% | 0.5268% | 14.73% | 0.2995%
EDWARD_2_E21SB1 | Hybrid_BattStorage | 2023 | nonsummer | 44800 | 4597.5 | 0 | 1060 | 71 | 75260 | 0 | Individual | 6.109% | 0% |  |  | 6.109% | 0% | TRUE |  |  | 6.109% | 0%
EDWARD_2_E21SB1 | Hybrid_BattStorage | 2023 | summer | 44800 | 456.5 | 0 | 765 | 71 | 54315 | 0 | Individual | 0.8405% | 0% |  |  | 0.8405% | 0% | TRUE |  |  | 0.8405% | 0%
EDWARD_2_E21SB1 | Hybrid_BattStorage | 2024 | nonsummer | 44800 | 176.5 | 0 | 1065 | 71 | 75615 | 0 | Individual | 0.2334% | 0% |  |  | 0.2334% | 0% | TRUE |  |  | 0.2334% | 0%
EDWARD_2_E21SB1 | Hybrid_BattStorage | 2024 | summer | 44800 | 467.5667 | 0 | 765 | 71 | 54315 | 0 | Individual | 0.8608% | 0% |  |  | 0.8608% | 0% | TRUE |  |  | 0.8608% | 0%
EDWARD_2_E23SB1 | Hybrid_BattStorage | 2022 | nonsummer | 44560 | 1048.6 | 0 | 1060 | 6 | 6360 | 0 | Individual | 16.49% | 0% |  |  | 16.49% | 0% | TRUE |  |  | 16.49% | 0%
EDWARD_2_E23SB1 | Hybrid_BattStorage | 2022 | summer | 44560 | 1391.1 | 0 | 765 | 6 | 4590 | 0 | Individual | 30.31% | 0% |  |  | 30.31% | 0% | TRUE |  |  | 30.31% | 0%
EDWARD_2_E23SB1 | Hybrid_BattStorage | 2023 | nonsummer | 44560 | 686 | 0 | 1060 | 6 | 6360 | 0 | Individual | 10.79% | 0% |  |  | 10.79% | 0% | TRUE |  |  | 10.79% | 0%
EDWARD_2_E23SB1 | Hybrid_BattStorage | 2023 | summer | 44560 | 70.2667 | 0 | 765 | 6 | 4590 | 0 | Individual | 1.531% | 0% |  |  | 1.531% | 0% | TRUE |  |  | 1.531% | 0%
EDWARD_2_E23SB1 | Hybrid_BattStorage | 2024 | nonsummer | 44560 | 574.4 | 0 | 1065 | 6 | 6390 | 0 | Individual | 8.989% | 0% |  |  | 8.989% | 0% | TRUE |  |  | 8.989% | 0%
EDWARD_2_E23SB1 | Hybrid_BattStorage | 2024 | summer | 44560 | 1790.35 | 0 | 765 | 6 | 4590 | 0 | Individual | 39.01% | 0% |  |  | 39.01% | 0% | TRUE |  |  | 39.01% | 0%
EDWARD_2_ES2BT3 | Hybrid_BattStorage | 2022 | nonsummer | 44653 | 1152.6333 | 0 | 605 | 66 | 39930 | 455 | Blended | 2.887% | 0% | 19.29% | 0.8894% | 9.927% | 0.3818% | TRUE | 19.29% | 0.8894% | 9.927% | 0.3818%
EDWARD_2_ES2BT3 | Hybrid_BattStorage | 2022 | summer | 44653 | 7163.1667 | 0 | 765 | 66 | 50490 | 0 | Individual | 14.19% | 0% |  |  | 14.19% | 0% | TRUE |  |  | 14.19% | 0%
EDWARD_2_ES2BT3 | Hybrid_BattStorage | 2023 | nonsummer | 44653 | 3428 | 0 | 1060 | 66 | 69960 | 0 | Individual | 4.9% | 0% |  |  | 4.9% | 0% | TRUE |  |  | 4.9% | 0%
EDWARD_2_ES2BT3 | Hybrid_BattStorage | 2023 | summer | 44653 | 571.2 | 0 | 765 | 66 | 50490 | 0 | Individual | 1.131% | 0% |  |  | 1.131% | 0% | TRUE |  |  | 1.131% | 0%
EDWARD_2_ES2BT3 | Hybrid_BattStorage | 2024 | nonsummer | 44653 | 12554.9333 | 0 | 1065 | 66 | 70290 | 0 | Individual | 17.86% | 0% |  |  | 17.86% | 0% | TRUE |  |  | 17.86% | 0%
EDWARD_2_ES2BT3 | Hybrid_BattStorage | 2024 | summer | 44653 | 4398.4833 | 0 | 765 | 66 | 50490 | 0 | Individual | 8.712% | 0% |  |  | 8.712% | 0% | TRUE |  |  | 8.712% | 0%
EDWARD_2_ESSSB1 | Hybrid_BattStorage | 2022 | nonsummer | 45664 | 0 | 0 | 0 | 47 | 0 | 1060 | Group |  |  | 19.29% | 0.8894% | 19.29% | 0.8894% | TRUE | 19.29% | 0.8894% | 19.29% | 0.8894%
EDWARD_2_ESSSB1 | Hybrid_BattStorage | 2022 | summer | 45664 | 0 | 0 | 0 | 47 | 0 | 765 | Group |  |  | 13.98% | 0.5268% | 13.98% | 0.5268% | TRUE | 13.98% | 0.5268% | 13.98% | 0.5268%
EDWARD_2_ESSSB1 | Hybrid_BattStorage | 2023 | nonsummer | 45664 | 334.4667 | 0 | 0 | 47 | 0 | 1060 | Group |  |  | 13.86% | 0% | 13.86% | 0% | TRUE | 13.86% | 0% | 13.86% | 0%
EDWARD_2_ESSSB1 | Hybrid_BattStorage | 2023 | summer | 45664 | 0 | 0 | 0 | 47 | 0 | 765 | Group |  |  | 5.01% | 0% | 5.01% | 0% | TRUE | 5.01% | 0% | 5.01% | 0%
EDWARD_2_ESSSB1 | Hybrid_BattStorage | 2024 | nonsummer | 45664 | 9491.0367 | 0 | 0 | 47 | 0 | 1065 | Group |  |  | 36.6% | 0% | 36.6% | 0% | TRUE | 36.6% | 0% | 36.6% | 0%
EDWARD_2_ESSSB1 | Hybrid_BattStorage | 2024 | summer | 45664 | 14548 | 0 | 0 | 47 | 0 | 765 | Group |  |  | 24.91% | 0% | 24.91% | 0% | TRUE | 24.91% | 0% | 24.91% | 0%
EDWARD_2_ESSSB2 | Hybrid_BattStorage | 2022 | nonsummer | 45244 | 0 | 0 | 0 | 21.5 | 0 | 1060 | Group |  |  | 19.29% | 0.8894% | 19.29% | 0.8894% | TRUE | 19.29% | 0.8894% | 19.29% | 0.8894%
EDWARD_2_ESSSB2 | Hybrid_BattStorage | 2022 | summer | 45244 | 0 | 0 | 0 | 21.5 | 0 | 765 | Group |  |  | 13.98% | 0.5268% | 13.98% | 0.5268% | TRUE | 13.98% | 0.5268% | 13.98% | 0.5268%
EDWARD_2_ESSSB2 | Hybrid_BattStorage | 2023 | nonsummer | 45244 | 132 | 0 | 240 | 21.5 | 5160 | 820 | Blended | 2.558% | 0% | 13.86% | 0% | 11.3% | 0% | TRUE | 13.86% | 0% | 11.3% | 0%
EDWARD_2_ESSSB2 | Hybrid_BattStorage | 2023 | summer | 45244 | 0 | 0 | 0 | 21.5 | 0 | 765 | Group |  |  | 5.01% | 0% | 5.01% | 0% | TRUE | 5.01% | 0% | 5.01% | 0%
EDWARD_2_ESSSB2 | Hybrid_BattStorage | 2024 | nonsummer | 45244 | 5401.5833 | 0 | 1065 | 21.5 | 22897.5 | 0 | Individual | 23.59% | 0% |  |  | 23.59% | 0% | TRUE |  |  | 23.59% | 0%
EDWARD_2_ESSSB2 | Hybrid_BattStorage | 2024 | summer | 45244 | 12 | 0 | 765 | 21.5 | 16447.5 | 0 | Individual | 0.07296% | 0% |  |  | 0.07296% | 0% | TRUE |  |  | 0.07296% | 0%
HAMLIN_1_BLDSB1 | Hybrid_BattStorage | 2022 | nonsummer | 45412 | 0 | 0 | 0 | 75 | 0 | 1060 | Group |  |  | 19.29% | 0.8894% | 19.29% | 0.8894% | TRUE | 19.29% | 0.8894% | 19.29% | 0.8894%
HAMLIN_1_BLDSB1 | Hybrid_BattStorage | 2022 | summer | 45412 | 0 | 0 | 0 | 75 | 0 | 765 | Group |  |  | 13.98% | 0.5268% | 13.98% | 0.5268% | TRUE | 13.98% | 0.5268% | 13.98% | 0.5268%
HAMLIN_1_BLDSB1 | Hybrid_BattStorage | 2023 | nonsummer | 45412 | 0 | 0 | 0 | 75 | 0 | 1060 | Group |  |  | 13.86% | 0% | 13.86% | 0% | TRUE | 13.86% | 0% | 13.86% | 0%
HAMLIN_1_BLDSB1 | Hybrid_BattStorage | 2023 | summer | 45412 | 0 | 0 | 0 | 75 | 0 | 765 | Group |  |  | 5.01% | 0% | 5.01% | 0% | TRUE | 5.01% | 0% | 5.01% | 0%
HAMLIN_1_BLDSB1 | Hybrid_BattStorage | 2024 | nonsummer | 45412 | 35053.6833 | 0 | 465 | 75 | 34875 | 600 | Blended | 100.5% | 0% | 36.6% | 0% | 64.51% | 0% | TRUE | 36.6% | 0% | 64.51% | 0%
HAMLIN_1_BLDSB1 | Hybrid_BattStorage | 2024 | summer | 45412 | 58769.8667 | 0 | 765 | 75 | 57375 | 0 | Individual | 102.4% | 0% |  |  | 102.4% | 0% | TRUE |  |  | 102.4% | 0%
HAMLIN_1_BMSBT2 | Hybrid_BattStorage | 2022 | nonsummer | 45638 | 0 | 0 | 0 | 25 | 0 | 1060 | Group |  |  | 19.29% | 0.8894% | 19.29% | 0.8894% | TRUE | 19.29% | 0.8894% | 19.29% | 0.8894%
HAMLIN_1_BMSBT2 | Hybrid_BattStorage | 2022 | summer | 45638 | 0 | 0 | 0 | 25 | 0 | 765 | Group |  |  | 13.98% | 0.5268% | 13.98% | 0.5268% | TRUE | 13.98% | 0.5268% | 13.98% | 0.5268%
HAMLIN_1_BMSBT2 | Hybrid_BattStorage | 2023 | nonsummer | 45638 | 0 | 0 | 0 | 25 | 0 | 1060 | Group |  |  | 13.86% | 0% | 13.86% | 0% | TRUE | 13.86% | 0% | 13.86% | 0%
HAMLIN_1_BMSBT2 | Hybrid_BattStorage | 2023 | summer | 45638 | 0 | 0 | 0 | 25 | 0 | 765 | Group |  |  | 5.01% | 0% | 5.01% | 0% | TRUE | 5.01% | 0% | 5.01% | 0%
HAMLIN_1_BMSBT2 | Hybrid_BattStorage | 2024 | nonsummer | 45638 | 2388.8333 | 0 | 100 | 25 | 2500 | 965 | Blended | 95.55% | 0% | 36.6% | 0% | 42.14% | 0% | TRUE | 36.6% | 0% | 42.14% | 0%
HAMLIN_1_BMSBT2 | Hybrid_BattStorage | 2024 | summer | 45638 | 0 | 0 | 0 | 25 | 0 | 765 | Group |  |  | 24.91% | 0% | 24.91% | 0% | TRUE | 24.91% | 0% | 24.91% | 0%
LNCSTR_6_SOLAR2 | Hybrid_BattStorage | 2022 | nonsummer | 44552 | 0 | 0 | 1060 | 7 | 7420 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
LNCSTR_6_SOLAR2 | Hybrid_BattStorage | 2022 | summer | 44552 | 0 | 0 | 765 | 7 | 5355 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
LNCSTR_6_SOLAR2 | Hybrid_BattStorage | 2023 | nonsummer | 44552 | 0 | 0 | 1060 | 7 | 7420 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
LNCSTR_6_SOLAR2 | Hybrid_BattStorage | 2023 | summer | 44552 | 0 | 0 | 765 | 7 | 5355 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
LNCSTR_6_SOLAR2 | Hybrid_BattStorage | 2024 | nonsummer | 44552 | 0 | 0 | 1065 | 7 | 7455 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
LNCSTR_6_SOLAR2 | Hybrid_BattStorage | 2024 | summer | 44552 | 0 | 0 | 765 | 7 | 5355 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
MCFLND_5_MBSBX2 | Hybrid_BattStorage | 2022 | nonsummer | 45561 | 0 | 0 | 0 | 150 | 0 | 1060 | Group |  |  | 19.29% | 0.8894% | 19.29% | 0.8894% | TRUE | 19.29% | 0.8894% | 19.29% | 0.8894%
MCFLND_5_MBSBX2 | Hybrid_BattStorage | 2022 | summer | 45561 | 0 | 0 | 0 | 150 | 0 | 765 | Group |  |  | 13.98% | 0.5268% | 13.98% | 0.5268% | TRUE | 13.98% | 0.5268% | 13.98% | 0.5268%
MCFLND_5_MBSBX2 | Hybrid_BattStorage | 2023 | nonsummer | 45561 | 0 | 0 | 0 | 150 | 0 | 1060 | Group |  |  | 13.86% | 0% | 13.86% | 0% | TRUE | 13.86% | 0% | 13.86% | 0%
MCFLND_5_MBSBX2 | Hybrid_BattStorage | 2023 | summer | 45561 | 0 | 0 | 0 | 150 | 0 | 765 | Group |  |  | 5.01% | 0% | 5.01% | 0% | TRUE | 5.01% | 0% | 5.01% | 0%
MCFLND_5_MBSBX2 | Hybrid_BattStorage | 2024 | nonsummer | 45561 | 32189.7333 | 0 | 305 | 150 | 45750 | 760 | Blended | 70.36% | 0% | 36.6% | 0% | 46.27% | 0% | TRUE | 36.6% | 0% | 46.27% | 0%
MCFLND_5_MBSBX2 | Hybrid_BattStorage | 2024 | summer | 45561 | 16700.75 | 0 | 180 | 150 | 27000 | 585 | Blended | 61.85% | 0% | 24.91% | 0% | 33.6% | 0% | TRUE | 24.91% | 0% | 33.6% | 0%
NORORC_2_NOSBX2 | Hybrid_BattStorage | 2022 | nonsummer | 45769 | 0 | 0 | 0 | 92 | 0 | 1060 | Group |  |  | 19.29% | 0.8894% | 19.29% | 0.8894% | TRUE | 19.29% | 0.8894% | 19.29% | 0.8894%
NORORC_2_NOSBX2 | Hybrid_BattStorage | 2022 | summer | 45769 | 0 | 0 | 0 | 92 | 0 | 765 | Group |  |  | 13.98% | 0.5268% | 13.98% | 0.5268% | TRUE | 13.98% | 0.5268% | 13.98% | 0.5268%
NORORC_2_NOSBX2 | Hybrid_BattStorage | 2023 | nonsummer | 45769 | 0 | 0 | 0 | 92 | 0 | 1060 | Group |  |  | 13.86% | 0% | 13.86% | 0% | TRUE | 13.86% | 0% | 13.86% | 0%
NORORC_2_NOSBX2 | Hybrid_BattStorage | 2023 | summer | 45769 | 0 | 0 | 0 | 92 | 0 | 765 | Group |  |  | 5.01% | 0% | 5.01% | 0% | TRUE | 5.01% | 0% | 5.01% | 0%
NORORC_2_NOSBX2 | Hybrid_BattStorage | 2024 | nonsummer | 45769 | 0 | 0 | 0 | 92 | 0 | 1065 | Group |  |  | 36.6% | 0% | 36.6% | 0% | TRUE | 36.6% | 0% | 36.6% | 0%
NORORC_2_NOSBX2 | Hybrid_BattStorage | 2024 | summer | 45769 | 6390.95 | 0 | 0 | 92 | 0 | 765 | Group |  |  | 24.91% | 0% | 24.91% | 0% | TRUE | 24.91% | 0% | 24.91% | 0%
PUTHCR_1_PCNSB1 | Hybrid_BattStorage | 2022 | nonsummer | 44849 | 0 | 0 | 305 | 3 | 915 | 755 | Blended | 0% | 0% | 19.29% | 0.8894% | 13.74% | 0.6335% | TRUE | 19.29% | 0.8894% | 13.74% | 0.6335%
PUTHCR_1_PCNSB1 | Hybrid_BattStorage | 2022 | summer | 44849 | 0 | 0 | 85 | 3 | 255 | 680 | Blended | 0% | 0% | 13.98% | 0.5268% | 12.42% | 0.4682% | TRUE | 13.98% | 0.5268% | 12.42% | 0.4682%
PUTHCR_1_PCNSB1 | Hybrid_BattStorage | 2023 | nonsummer | 44849 | 322.05 | 0 | 1060 | 3 | 3180 | 0 | Individual | 10.13% | 0% |  |  | 10.13% | 0% | TRUE |  |  | 10.13% | 0%
PUTHCR_1_PCNSB1 | Hybrid_BattStorage | 2023 | summer | 44849 | 183.3 | 0 | 765 | 3 | 2295 | 0 | Individual | 7.987% | 0% |  |  | 7.987% | 0% | TRUE |  |  | 7.987% | 0%
PUTHCR_1_PCNSB1 | Hybrid_BattStorage | 2024 | nonsummer | 44849 | 933.3 | 0 | 1065 | 3 | 3195 | 0 | Individual | 29.21% | 0% |  |  | 29.21% | 0% | TRUE |  |  | 29.21% | 0%
PUTHCR_1_PCNSB1 | Hybrid_BattStorage | 2024 | summer | 44849 | 264.35 | 0 | 765 | 3 | 2295 | 0 | Individual | 11.52% | 0% |  |  | 11.52% | 0% | TRUE |  |  | 11.52% | 0%
RATSKE_2_RBSSB1 | Hybrid_BattStorage | 2022 | nonsummer | 44852 | 1475.1 | 60 | 305 | 7.5 | 2287.5 | 755 | Blended | 64.49% | 2.623% | 19.29% | 0.8894% | 32.29% | 1.388% | TRUE | 19.29% | 0.8894% | 32.29% | 1.388%
RATSKE_2_RBSSB1 | Hybrid_BattStorage | 2022 | summer | 44852 | 747.9333 | 0 | 70 | 7.5 | 525 | 695 | Blended | 142.5% | 0% | 13.98% | 0.5268% | 25.73% | 0.4786% | TRUE | 13.98% | 0.5268% | 25.73% | 0.4786%
RATSKE_2_RBSSB1 | Hybrid_BattStorage | 2023 | nonsummer | 44852 | 169.8083 | 0 | 1060 | 7.5 | 7950 | 0 | Individual | 2.136% | 0% |  |  | 2.136% | 0% | TRUE |  |  | 2.136% | 0%
RATSKE_2_RBSSB1 | Hybrid_BattStorage | 2023 | summer | 44852 | 120 | 0 | 765 | 7.5 | 5737.5 | 0 | Individual | 2.092% | 0% |  |  | 2.092% | 0% | TRUE |  |  | 2.092% | 0%
RATSKE_2_RBSSB1 | Hybrid_BattStorage | 2024 | nonsummer | 44852 | 960 | 0 | 1065 | 7.5 | 7987.5 | 0 | Individual | 12.02% | 0% |  |  | 12.02% | 0% | TRUE |  |  | 12.02% | 0%
RATSKE_2_RBSSB1 | Hybrid_BattStorage | 2024 | summer | 44852 | 220 | 0 | 765 | 7.5 | 5737.5 | 0 | Individual | 3.834% | 0% |  |  | 3.834% | 0% | TRUE |  |  | 3.834% | 0%
RATSKE_2_RBSSB2 | Hybrid_BattStorage | 2022 | nonsummer | 44852 | 1080.4667 | 114.6667 | 305 | 5 | 1525 | 755 | Blended | 70.85% | 7.519% | 19.29% | 0.8894% | 34.12% | 2.797% | TRUE | 19.29% | 0.8894% | 34.12% | 2.797%
RATSKE_2_RBSSB2 | Hybrid_BattStorage | 2022 | summer | 44852 | 497.6667 | 0 | 70 | 5 | 350 | 695 | Blended | 142.2% | 0% | 13.98% | 0.5268% | 25.71% | 0.4786% | TRUE | 13.98% | 0.5268% | 25.71% | 0.4786%
RATSKE_2_RBSSB2 | Hybrid_BattStorage | 2023 | nonsummer | 44852 | 87.4 | 0 | 1060 | 5 | 5300 | 0 | Individual | 1.649% | 0% |  |  | 1.649% | 0% | TRUE |  |  | 1.649% | 0%
RATSKE_2_RBSSB2 | Hybrid_BattStorage | 2023 | summer | 44852 | 200.6667 | 0 | 765 | 5 | 3825 | 0 | Individual | 5.246% | 0% |  |  | 5.246% | 0% | TRUE |  |  | 5.246% | 0%
RATSKE_2_RBSSB2 | Hybrid_BattStorage | 2024 | nonsummer | 44852 | 480 | 0 | 1065 | 5 | 5325 | 0 | Individual | 9.014% | 0% |  |  | 9.014% | 0% | TRUE |  |  | 9.014% | 0%
RATSKE_2_RBSSB2 | Hybrid_BattStorage | 2024 | summer | 44852 | 60 | 0 | 765 | 5 | 3825 | 0 | Individual | 1.569% | 0% |  |  | 1.569% | 0% | TRUE |  |  | 1.569% | 0%
SANBRN_2_EESSB2 | Hybrid_BattStorage | 2022 | nonsummer | 45239 | 0 | 0 | 0 | 85 | 0 | 1060 | Group |  |  | 19.29% | 0.8894% | 19.29% | 0.8894% | TRUE | 19.29% | 0.8894% | 19.29% | 0.8894%
SANBRN_2_EESSB2 | Hybrid_BattStorage | 2022 | summer | 45239 | 0 | 0 | 0 | 85 | 0 | 765 | Group |  |  | 13.98% | 0.5268% | 13.98% | 0.5268% | TRUE | 13.98% | 0.5268% | 13.98% | 0.5268%
SANBRN_2_EESSB2 | Hybrid_BattStorage | 2023 | nonsummer | 45239 | 499.3333 | 0 | 265 | 85 | 22525 | 795 | Blended | 2.217% | 0% | 13.86% | 0% | 10.95% | 0% | TRUE | 13.86% | 0% | 10.95% | 0%
SANBRN_2_EESSB2 | Hybrid_BattStorage | 2023 | summer | 45239 | 0 | 0 | 0 | 85 | 0 | 765 | Group |  |  | 5.01% | 0% | 5.01% | 0% | TRUE | 5.01% | 0% | 5.01% | 0%
SANBRN_2_EESSB2 | Hybrid_BattStorage | 2024 | nonsummer | 45239 | 873.0167 | 0 | 1065 | 85 | 90525 | 0 | Individual | 0.9644% | 0% |  |  | 0.9644% | 0% | TRUE |  |  | 0.9644% | 0%
SANBRN_2_EESSB2 | Hybrid_BattStorage | 2024 | summer | 45239 | 345.8333 | 0 | 765 | 85 | 65025 | 0 | Individual | 0.5318% | 0% |  |  | 0.5318% | 0% | TRUE |  |  | 0.5318% | 0%
SANBRN_2_ES1BT3 | Hybrid_BattStorage | 2022 | nonsummer | 44664 | 711.9035 | 0 | 550 | 22 | 12100 | 510 | Blended | 5.883% | 0% | 19.29% | 0.8894% | 12.33% | 0.4279% | TRUE | 19.29% | 0.8894% | 12.33% | 0.4279%
SANBRN_2_ES1BT3 | Hybrid_BattStorage | 2022 | summer | 44664 | 1515.4215 | 0 | 765 | 22 | 16830 | 0 | Individual | 9.004% | 0% |  |  | 9.004% | 0% | TRUE |  |  | 9.004% | 0%
SANBRN_2_ES1BT3 | Hybrid_BattStorage | 2023 | nonsummer | 44664 | 903.5375 | 0 | 1060 | 22 | 23320 | 0 | Individual | 3.875% | 0% |  |  | 3.875% | 0% | TRUE |  |  | 3.875% | 0%
SANBRN_2_ES1BT3 | Hybrid_BattStorage | 2023 | summer | 44664 | 0 | 0 | 765 | 22 | 16830 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SANBRN_2_ES1BT3 | Hybrid_BattStorage | 2024 | nonsummer | 44664 | 366.439 | 0 | 1065 | 22 | 23430 | 0 | Individual | 1.564% | 0% |  |  | 1.564% | 0% | TRUE |  |  | 1.564% | 0%
SANBRN_2_ES1BT3 | Hybrid_BattStorage | 2024 | summer | 44664 | 106.1017 | 0 | 765 | 22 | 16830 | 0 | Individual | 0.6304% | 0% |  |  | 0.6304% | 0% | TRUE |  |  | 0.6304% | 0%
SANBRN_2_ES2SB3 | Hybrid_BattStorage | 2022 | nonsummer | 44664 | 503.3 | 0 | 550 | 18 | 9900 | 510 | Blended | 5.084% | 0% | 19.29% | 0.8894% | 11.92% | 0.4279% | TRUE | 19.29% | 0.8894% | 11.92% | 0.4279%
SANBRN_2_ES2SB3 | Hybrid_BattStorage | 2022 | summer | 44664 | 2389.6 | 0 | 765 | 18 | 13770 | 0 | Individual | 17.35% | 0% |  |  | 17.35% | 0% | TRUE |  |  | 17.35% | 0%
SANBRN_2_ES2SB3 | Hybrid_BattStorage | 2023 | nonsummer | 44664 | 767.2 | 0 | 1060 | 18 | 19080 | 0 | Individual | 4.021% | 0% |  |  | 4.021% | 0% | TRUE |  |  | 4.021% | 0%
SANBRN_2_ES2SB3 | Hybrid_BattStorage | 2023 | summer | 44664 | 0 | 0 | 765 | 18 | 13770 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SANBRN_2_ES2SB3 | Hybrid_BattStorage | 2024 | nonsummer | 44664 | 56 | 0 | 1065 | 18 | 19170 | 0 | Individual | 0.2921% | 0% |  |  | 0.2921% | 0% | TRUE |  |  | 0.2921% | 0%
SANBRN_2_ES2SB3 | Hybrid_BattStorage | 2024 | summer | 44664 | 87.5 | 0 | 765 | 18 | 13770 | 0 | Individual | 0.6354% | 0% |  |  | 0.6354% | 0% | TRUE |  |  | 0.6354% | 0%
SANBRN_2_SS2SB4 | Hybrid_BattStorage | 2022 | nonsummer | 45118 | 0 | 0 | 0 | 18 | 0 | 1060 | Group |  |  | 19.29% | 0.8894% | 19.29% | 0.8894% | TRUE | 19.29% | 0.8894% | 19.29% | 0.8894%
SANBRN_2_SS2SB4 | Hybrid_BattStorage | 2022 | summer | 45118 | 0 | 0 | 0 | 18 | 0 | 765 | Group |  |  | 13.98% | 0.5268% | 13.98% | 0.5268% | TRUE | 13.98% | 0.5268% | 13.98% | 0.5268%
SANBRN_2_SS2SB4 | Hybrid_BattStorage | 2023 | nonsummer | 45118 | 144 | 0 | 305 | 18 | 5490 | 755 | Blended | 2.623% | 0% | 13.86% | 0% | 10.62% | 0% | TRUE | 13.86% | 0% | 10.62% | 0%
SANBRN_2_SS2SB4 | Hybrid_BattStorage | 2023 | summer | 45118 | 54 | 0 | 565 | 18 | 10170 | 200 | Blended | 0.531% | 0% | 5.01% | 0% | 1.702% | 0% | TRUE | 5.01% | 0% | 1.702% | 0%
SANBRN_2_SS2SB4 | Hybrid_BattStorage | 2024 | nonsummer | 45118 | 363 | 0 | 1065 | 18 | 19170 | 0 | Individual | 1.894% | 0% |  |  | 1.894% | 0% | TRUE |  |  | 1.894% | 0%
SANBRN_2_SS2SB4 | Hybrid_BattStorage | 2024 | summer | 45118 | 147.8 | 0 | 765 | 18 | 13770 | 0 | Individual | 1.073% | 0% |  |  | 1.073% | 0% | TRUE |  |  | 1.073% | 0%
SLATE_2_SLASR2 | Hybrid_BattStorage | 2022 | nonsummer | 44635 | 7458.0108 | 652.19 | 695 | 46.5 | 32317.5 | 365 | Blended | 23.08% | 2.018% | 19.29% | 0.8894% | 21.77% | 1.629% | TRUE | 19.29% | 0.8894% | 21.77% | 1.629%
SLATE_2_SLASR2 | Hybrid_BattStorage | 2022 | summer | 44635 | 3505.5342 | 572.5833 | 765 | 46.5 | 35572.5 | 0 | Individual | 9.855% | 1.61% |  |  | 9.855% | 1.61% | TRUE |  |  | 9.855% | 1.61%
SLATE_2_SLASR2 | Hybrid_BattStorage | 2023 | nonsummer | 44635 | 13799.475 | 0 | 1060 | 46.5 | 49290 | 0 | Individual | 28% | 0% |  |  | 28% | 0% | TRUE |  |  | 28% | 0%
SLATE_2_SLASR2 | Hybrid_BattStorage | 2023 | summer | 44635 | 2282.8 | 0 | 765 | 46.5 | 35572.5 | 0 | Individual | 6.417% | 0% |  |  | 6.417% | 0% | TRUE |  |  | 6.417% | 0%
SLATE_2_SLASR2 | Hybrid_BattStorage | 2024 | nonsummer | 44635 | 27998.54 | 0 | 1065 | 46.5 | 49522.5 | 0 | Individual | 56.54% | 0% |  |  | 56.54% | 0% | TRUE |  |  | 56.54% | 0%
SLATE_2_SLASR2 | Hybrid_BattStorage | 2024 | summer | 44635 | 306.0667 | 0 | 765 | 46.5 | 35572.5 | 0 | Individual | 0.8604% | 0% |  |  | 0.8604% | 0% | TRUE |  |  | 0.8604% | 0%
SLATE_2_SLASR3 | Hybrid_BattStorage | 2022 | nonsummer | 44635 | 4555.6733 | 852.955 | 695 | 33.75 | 23456.25 | 365 | Blended | 19.42% | 3.636% | 19.29% | 0.8894% | 19.38% | 2.69% | TRUE | 19.29% | 0.8894% | 19.38% | 2.69%
SLATE_2_SLASR3 | Hybrid_BattStorage | 2022 | summer | 44635 | 2655.9083 | 576.6667 | 765 | 33.75 | 25818.75 | 0 | Individual | 10.29% | 2.234% |  |  | 10.29% | 2.234% | TRUE |  |  | 10.29% | 2.234%
SLATE_2_SLASR3 | Hybrid_BattStorage | 2023 | nonsummer | 44635 | 10890.95 | 0 | 1060 | 33.75 | 35775 | 0 | Individual | 30.44% | 0% |  |  | 30.44% | 0% | TRUE |  |  | 30.44% | 0%
SLATE_2_SLASR3 | Hybrid_BattStorage | 2023 | summer | 44635 | 2373.9767 | 0 | 765 | 33.75 | 25818.75 | 0 | Individual | 9.195% | 0% |  |  | 9.195% | 0% | TRUE |  |  | 9.195% | 0%
SLATE_2_SLASR3 | Hybrid_BattStorage | 2024 | nonsummer | 44635 | 22591.825 | 0 | 1065 | 33.75 | 35943.75 | 0 | Individual | 62.85% | 0% |  |  | 62.85% | 0% | TRUE |  |  | 62.85% | 0%
SLATE_2_SLASR3 | Hybrid_BattStorage | 2024 | summer | 44635 | 196.3217 | 0 | 765 | 33.75 | 25818.75 | 0 | Individual | 0.7604% | 0% |  |  | 0.7604% | 0% | TRUE |  |  | 0.7604% | 0%
SLATE_2_SLASR4 | Hybrid_BattStorage | 2022 | nonsummer | 44635 | 14040.558 | 0 | 695 | 50 | 34750 | 365 | Blended | 40.4% | 0% | 19.29% | 0.8894% | 33.13% | 0.3062% | TRUE | 19.29% | 0.8894% | 33.13% | 0.3062%
SLATE_2_SLASR4 | Hybrid_BattStorage | 2022 | summer | 44635 | 5350.1417 | 0 | 765 | 50 | 38250 | 0 | Individual | 13.99% | 0% |  |  | 13.99% | 0% | TRUE |  |  | 13.99% | 0%
SLATE_2_SLASR4 | Hybrid_BattStorage | 2023 | nonsummer | 44635 | 7904.102 | 0 | 1060 | 50 | 53000 | 0 | Individual | 14.91% | 0% |  |  | 14.91% | 0% | TRUE |  |  | 14.91% | 0%
SLATE_2_SLASR4 | Hybrid_BattStorage | 2023 | summer | 44635 | 183.75 | 0 | 765 | 50 | 38250 | 0 | Individual | 0.4804% | 0% |  |  | 0.4804% | 0% | TRUE |  |  | 0.4804% | 0%
SLATE_2_SLASR4 | Hybrid_BattStorage | 2024 | nonsummer | 44635 | 1402.6067 | 0 | 1065 | 50 | 53250 | 0 | Individual | 2.634% | 0% |  |  | 2.634% | 0% | TRUE |  |  | 2.634% | 0%
SLATE_2_SLASR4 | Hybrid_BattStorage | 2024 | summer | 44635 | 18.0167 | 0 | 765 | 50 | 38250 | 0 | Individual | 0.0471% | 0% |  |  | 0.0471% | 0% | TRUE |  |  | 0.0471% | 0%
SLATE_2_SLASR5 | Hybrid_BattStorage | 2022 | nonsummer | 44635 | 3757.1025 | 95.0867 | 695 | 10 | 6950 | 365 | Blended | 54.06% | 1.368% | 19.29% | 0.8894% | 42.09% | 1.203% | TRUE | 19.29% | 0.8894% | 42.09% | 1.203%
SLATE_2_SLASR5 | Hybrid_BattStorage | 2022 | summer | 44635 | 2247.88 | 24.85 | 765 | 10 | 7650 | 0 | Individual | 29.38% | 0.3248% |  |  | 29.38% | 0.3248% | TRUE |  |  | 29.38% | 0.3248%
SLATE_2_SLASR5 | Hybrid_BattStorage | 2023 | nonsummer | 44635 | 4441.0617 | 0 | 1060 | 10 | 10600 | 0 | Individual | 41.9% | 0% |  |  | 41.9% | 0% | TRUE |  |  | 41.9% | 0%
SLATE_2_SLASR5 | Hybrid_BattStorage | 2023 | summer | 44635 | 1687.3182 | 0 | 765 | 10 | 7650 | 0 | Individual | 22.06% | 0% |  |  | 22.06% | 0% | TRUE |  |  | 22.06% | 0%
SLATE_2_SLASR5 | Hybrid_BattStorage | 2024 | nonsummer | 44635 | 3070.62 | 0 | 1065 | 10 | 10650 | 0 | Individual | 28.83% | 0% |  |  | 28.83% | 0% | TRUE |  |  | 28.83% | 0%
SLATE_2_SLASR5 | Hybrid_BattStorage | 2024 | summer | 44635 | 1608.6257 | 0 | 765 | 10 | 7650 | 0 | Individual | 21.03% | 0% |  |  | 21.03% | 0% | TRUE |  |  | 21.03% | 0%
BARRE_2_ALASB1_SUN | Hybrid_Solar_1Axis | 2022 | nonsummer | 1 | 0 | 0 | 1060 | 10 | 10600 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
BARRE_2_ALASB1_SUN | Hybrid_Solar_1Axis | 2022 | summer | 1 | 0 | 0 | 765 | 10 | 7650 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
BARRE_2_ALASB1_SUN | Hybrid_Solar_1Axis | 2023 | nonsummer | 1 | 0 | 0 | 1060 | 10 | 10600 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
BARRE_2_ALASB1_SUN | Hybrid_Solar_1Axis | 2023 | summer | 1 | 0 | 0 | 765 | 10 | 7650 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
BARRE_2_ALASB1_SUN | Hybrid_Solar_1Axis | 2024 | nonsummer | 1 | 0 | 0 | 1065 | 10 | 10650 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
BARRE_2_ALASB1_SUN | Hybrid_Solar_1Axis | 2024 | summer | 1 | 0 | 0 | 765 | 10 | 7650 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
CUYAMA_6_SB3SB1_SUN | Hybrid_Solar_1Axis | 2022 | nonsummer | 1 | 0 | 0 | 1060 | 3 | 3180 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
CUYAMA_6_SB3SB1_SUN | Hybrid_Solar_1Axis | 2022 | summer | 1 | 0 | 0 | 765 | 3 | 2295 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
CUYAMA_6_SB3SB1_SUN | Hybrid_Solar_1Axis | 2023 | nonsummer | 1 | 0 | 0 | 1060 | 3 | 3180 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
CUYAMA_6_SB3SB1_SUN | Hybrid_Solar_1Axis | 2023 | summer | 1 | 0 | 0 | 765 | 3 | 2295 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
CUYAMA_6_SB3SB1_SUN | Hybrid_Solar_1Axis | 2024 | nonsummer | 1 | 0 | 0 | 1065 | 3 | 3195 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
CUYAMA_6_SB3SB1_SUN | Hybrid_Solar_1Axis | 2024 | summer | 1 | 0 | 0 | 765 | 3 | 2295 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
DELAMO_2_ALASB2_SUN | Hybrid_Solar_1Axis | 2022 | nonsummer | 1 | 0 | 0 | 1060 | 10 | 10600 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
DELAMO_2_ALASB2_SUN | Hybrid_Solar_1Axis | 2022 | summer | 1 | 0 | 0 | 765 | 10 | 7650 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
DELAMO_2_ALASB2_SUN | Hybrid_Solar_1Axis | 2023 | nonsummer | 1 | 0 | 0 | 1060 | 10 | 10600 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
DELAMO_2_ALASB2_SUN | Hybrid_Solar_1Axis | 2023 | summer | 1 | 0 | 0 | 765 | 10 | 7650 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
DELAMO_2_ALASB2_SUN | Hybrid_Solar_1Axis | 2024 | nonsummer | 1 | 0 | 0 | 1065 | 10 | 10650 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
DELAMO_2_ALASB2_SUN | Hybrid_Solar_1Axis | 2024 | summer | 1 | 0 | 0 | 765 | 10 | 7650 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
DSFLWR_2_W9CSB1_SUN | Hybrid_Solar_1Axis | 2022 | nonsummer | 1 | 0 | 0 | 1060 | 102 | 108120 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
DSFLWR_2_W9CSB1_SUN | Hybrid_Solar_1Axis | 2022 | summer | 1 | 0 | 0 | 765 | 102 | 78030 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
DSFLWR_2_W9CSB1_SUN | Hybrid_Solar_1Axis | 2023 | nonsummer | 1 | 0 | 0 | 1060 | 102 | 108120 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
DSFLWR_2_W9CSB1_SUN | Hybrid_Solar_1Axis | 2023 | summer | 1 | 0 | 0 | 765 | 102 | 78030 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
DSFLWR_2_W9CSB1_SUN | Hybrid_Solar_1Axis | 2024 | nonsummer | 1 | 0 | 0 | 1065 | 102 | 108630 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
DSFLWR_2_W9CSB1_SUN | Hybrid_Solar_1Axis | 2024 | summer | 1 | 0 | 0 | 765 | 102 | 78030 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
DSFLWR_2_W9CSB2_SUN | Hybrid_Solar_1Axis | 2022 | nonsummer | 1 | 0 | 0 | 1060 | 72 | 76320 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
DSFLWR_2_W9CSB2_SUN | Hybrid_Solar_1Axis | 2022 | summer | 1 | 0 | 0 | 765 | 72 | 55080 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
DSFLWR_2_W9CSB2_SUN | Hybrid_Solar_1Axis | 2023 | nonsummer | 1 | 0 | 0 | 1060 | 72 | 76320 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
DSFLWR_2_W9CSB2_SUN | Hybrid_Solar_1Axis | 2023 | summer | 1 | 0 | 0 | 765 | 72 | 55080 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
DSFLWR_2_W9CSB2_SUN | Hybrid_Solar_1Axis | 2024 | nonsummer | 1 | 0 | 0 | 1065 | 72 | 76680 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
DSFLWR_2_W9CSB2_SUN | Hybrid_Solar_1Axis | 2024 | summer | 1 | 0 | 0 | 765 | 72 | 55080 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
EDWARD_2_E21SB1_SUN | Hybrid_Solar_1Axis | 2022 | nonsummer | 1 | 0 | 0 | 1060 | 130 | 137800 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
EDWARD_2_E21SB1_SUN | Hybrid_Solar_1Axis | 2022 | summer | 1 | 0 | 0 | 765 | 130 | 99450 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
EDWARD_2_E21SB1_SUN | Hybrid_Solar_1Axis | 2023 | nonsummer | 1 | 0 | 0 | 1060 | 130 | 137800 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
EDWARD_2_E21SB1_SUN | Hybrid_Solar_1Axis | 2023 | summer | 1 | 0 | 0 | 765 | 130 | 99450 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
EDWARD_2_E21SB1_SUN | Hybrid_Solar_1Axis | 2024 | nonsummer | 1 | 0 | 0 | 1065 | 130 | 138450 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
EDWARD_2_E21SB1_SUN | Hybrid_Solar_1Axis | 2024 | summer | 1 | 0 | 0 | 765 | 130 | 99450 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
EDWARD_2_E23SB1_SUN | Hybrid_Solar_1Axis | 2022 | nonsummer | 1 | 0 | 0 | 1060 | 24 | 25440 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
EDWARD_2_E23SB1_SUN | Hybrid_Solar_1Axis | 2022 | summer | 1 | 0 | 0 | 765 | 24 | 18360 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
EDWARD_2_E23SB1_SUN | Hybrid_Solar_1Axis | 2023 | nonsummer | 1 | 0 | 0 | 1060 | 24 | 25440 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
EDWARD_2_E23SB1_SUN | Hybrid_Solar_1Axis | 2023 | summer | 1 | 0 | 0 | 765 | 24 | 18360 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
EDWARD_2_E23SB1_SUN | Hybrid_Solar_1Axis | 2024 | nonsummer | 1 | 0 | 0 | 1065 | 24 | 25560 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
EDWARD_2_E23SB1_SUN | Hybrid_Solar_1Axis | 2024 | summer | 1 | 0 | 0 | 765 | 24 | 18360 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
EDWARD_2_ES2BT3_SUN | Hybrid_Solar_1Axis | 2022 | nonsummer | 1 | 0 | 0 | 1060 | 118 | 125080 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
EDWARD_2_ES2BT3_SUN | Hybrid_Solar_1Axis | 2022 | summer | 1 | 0 | 0 | 765 | 118 | 90270 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
EDWARD_2_ES2BT3_SUN | Hybrid_Solar_1Axis | 2023 | nonsummer | 1 | 0 | 0 | 1060 | 118 | 125080 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
EDWARD_2_ES2BT3_SUN | Hybrid_Solar_1Axis | 2023 | summer | 1 | 0 | 0 | 765 | 118 | 90270 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
EDWARD_2_ES2BT3_SUN | Hybrid_Solar_1Axis | 2024 | nonsummer | 1 | 0 | 0 | 1065 | 118 | 125670 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
EDWARD_2_ES2BT3_SUN | Hybrid_Solar_1Axis | 2024 | summer | 1 | 0 | 0 | 765 | 118 | 90270 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
EDWARD_2_ESSSB1_SUN | Hybrid_Solar_1Axis | 2022 | nonsummer | 1 | 0 | 0 | 1060 | 68 | 72080 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
EDWARD_2_ESSSB1_SUN | Hybrid_Solar_1Axis | 2022 | summer | 1 | 0 | 0 | 765 | 68 | 52020 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
EDWARD_2_ESSSB1_SUN | Hybrid_Solar_1Axis | 2023 | nonsummer | 1 | 0 | 0 | 1060 | 68 | 72080 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
EDWARD_2_ESSSB1_SUN | Hybrid_Solar_1Axis | 2023 | summer | 1 | 0 | 0 | 765 | 68 | 52020 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
EDWARD_2_ESSSB1_SUN | Hybrid_Solar_1Axis | 2024 | nonsummer | 1 | 0 | 0 | 1065 | 68 | 72420 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
EDWARD_2_ESSSB1_SUN | Hybrid_Solar_1Axis | 2024 | summer | 1 | 0 | 0 | 765 | 68 | 52020 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
EDWARD_2_ESSSB2_SUN | Hybrid_Solar_1Axis | 2022 | nonsummer | 1 | 0 | 0 | 1060 | 132 | 139920 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
EDWARD_2_ESSSB2_SUN | Hybrid_Solar_1Axis | 2022 | summer | 1 | 0 | 0 | 765 | 132 | 100980 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
EDWARD_2_ESSSB2_SUN | Hybrid_Solar_1Axis | 2023 | nonsummer | 1 | 0 | 0 | 1060 | 132 | 139920 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
EDWARD_2_ESSSB2_SUN | Hybrid_Solar_1Axis | 2023 | summer | 1 | 0 | 0 | 765 | 132 | 100980 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
EDWARD_2_ESSSB2_SUN | Hybrid_Solar_1Axis | 2024 | nonsummer | 1 | 0 | 0 | 1065 | 132 | 140580 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
EDWARD_2_ESSSB2_SUN | Hybrid_Solar_1Axis | 2024 | summer | 1 | 0 | 0 | 765 | 132 | 100980 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
HAMLIN_1_BLDSB1_SUN | Hybrid_Solar_1Axis | 2022 | nonsummer | 1 | 0 | 0 | 1060 | 150 | 159000 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
HAMLIN_1_BLDSB1_SUN | Hybrid_Solar_1Axis | 2022 | summer | 1 | 0 | 0 | 765 | 150 | 114750 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
HAMLIN_1_BLDSB1_SUN | Hybrid_Solar_1Axis | 2023 | nonsummer | 1 | 0 | 0 | 1060 | 150 | 159000 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
HAMLIN_1_BLDSB1_SUN | Hybrid_Solar_1Axis | 2023 | summer | 1 | 0 | 0 | 765 | 150 | 114750 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
HAMLIN_1_BLDSB1_SUN | Hybrid_Solar_1Axis | 2024 | nonsummer | 1 | 0 | 0 | 1065 | 150 | 159750 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
HAMLIN_1_BLDSB1_SUN | Hybrid_Solar_1Axis | 2024 | summer | 1 | 0 | 0 | 765 | 150 | 114750 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
HAMLIN_1_BMSBT2_SUN | Hybrid_Solar_1Axis | 2022 | nonsummer | 1 | 0 | 0 | 1060 | 50 | 53000 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
HAMLIN_1_BMSBT2_SUN | Hybrid_Solar_1Axis | 2022 | summer | 1 | 0 | 0 | 765 | 50 | 38250 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
HAMLIN_1_BMSBT2_SUN | Hybrid_Solar_1Axis | 2023 | nonsummer | 1 | 0 | 0 | 1060 | 50 | 53000 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
HAMLIN_1_BMSBT2_SUN | Hybrid_Solar_1Axis | 2023 | summer | 1 | 0 | 0 | 765 | 50 | 38250 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
HAMLIN_1_BMSBT2_SUN | Hybrid_Solar_1Axis | 2024 | nonsummer | 1 | 0 | 0 | 1065 | 50 | 53250 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
HAMLIN_1_BMSBT2_SUN | Hybrid_Solar_1Axis | 2024 | summer | 1 | 0 | 0 | 765 | 50 | 38250 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
LNCSTR_6_SOLAR2_SUN | Hybrid_Solar_1Axis | 2022 | nonsummer | 1 | 0 | 0 | 1060 | 3 | 3180 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
LNCSTR_6_SOLAR2_SUN | Hybrid_Solar_1Axis | 2022 | summer | 1 | 0 | 0 | 765 | 3 | 2295 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
LNCSTR_6_SOLAR2_SUN | Hybrid_Solar_1Axis | 2023 | nonsummer | 1 | 0 | 0 | 1060 | 3 | 3180 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
LNCSTR_6_SOLAR2_SUN | Hybrid_Solar_1Axis | 2023 | summer | 1 | 0 | 0 | 765 | 3 | 2295 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
LNCSTR_6_SOLAR2_SUN | Hybrid_Solar_1Axis | 2024 | nonsummer | 1 | 0 | 0 | 1065 | 3 | 3195 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
LNCSTR_6_SOLAR2_SUN | Hybrid_Solar_1Axis | 2024 | summer | 1 | 0 | 0 | 765 | 3 | 2295 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
MCFLND_5_MBSBX2_SUN | Hybrid_Solar_1Axis | 2022 | nonsummer | 1 | 0 | 0 | 1060 | 300 | 318000 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
MCFLND_5_MBSBX2_SUN | Hybrid_Solar_1Axis | 2022 | summer | 1 | 0 | 0 | 765 | 300 | 229500 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
MCFLND_5_MBSBX2_SUN | Hybrid_Solar_1Axis | 2023 | nonsummer | 1 | 0 | 0 | 1060 | 300 | 318000 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
MCFLND_5_MBSBX2_SUN | Hybrid_Solar_1Axis | 2023 | summer | 1 | 0 | 0 | 765 | 300 | 229500 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
MCFLND_5_MBSBX2_SUN | Hybrid_Solar_1Axis | 2024 | nonsummer | 1 | 0 | 0 | 1065 | 300 | 319500 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
MCFLND_5_MBSBX2_SUN | Hybrid_Solar_1Axis | 2024 | summer | 1 | 0 | 0 | 765 | 300 | 229500 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
NORORC_2_NOSBX2_SUN | Hybrid_Solar_1Axis | 2022 | nonsummer | 1 | 0 | 0 | 1060 | 150 | 159000 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
NORORC_2_NOSBX2_SUN | Hybrid_Solar_1Axis | 2022 | summer | 1 | 0 | 0 | 765 | 150 | 114750 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
NORORC_2_NOSBX2_SUN | Hybrid_Solar_1Axis | 2023 | nonsummer | 1 | 0 | 0 | 1060 | 150 | 159000 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
NORORC_2_NOSBX2_SUN | Hybrid_Solar_1Axis | 2023 | summer | 1 | 0 | 0 | 765 | 150 | 114750 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
NORORC_2_NOSBX2_SUN | Hybrid_Solar_1Axis | 2024 | nonsummer | 1 | 0 | 0 | 1065 | 150 | 159750 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
NORORC_2_NOSBX2_SUN | Hybrid_Solar_1Axis | 2024 | summer | 1 | 0 | 0 | 765 | 150 | 114750 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
PUTHCR_1_PCNSB1_SUN | Hybrid_Solar_1Axis | 2022 | nonsummer | 1 | 0 | 0 | 1060 | 3 | 3180 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
PUTHCR_1_PCNSB1_SUN | Hybrid_Solar_1Axis | 2022 | summer | 1 | 0 | 0 | 765 | 3 | 2295 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
PUTHCR_1_PCNSB1_SUN | Hybrid_Solar_1Axis | 2023 | nonsummer | 1 | 0 | 0 | 1060 | 3 | 3180 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
PUTHCR_1_PCNSB1_SUN | Hybrid_Solar_1Axis | 2023 | summer | 1 | 0 | 0 | 765 | 3 | 2295 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
PUTHCR_1_PCNSB1_SUN | Hybrid_Solar_1Axis | 2024 | nonsummer | 1 | 0 | 0 | 1065 | 3 | 3195 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
PUTHCR_1_PCNSB1_SUN | Hybrid_Solar_1Axis | 2024 | summer | 1 | 0 | 0 | 765 | 3 | 2295 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
RATSKE_2_RBSSB1_SUN | Hybrid_Solar_1Axis | 2022 | nonsummer | 1 | 0 | 0 | 1060 | 60 | 63600 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
RATSKE_2_RBSSB1_SUN | Hybrid_Solar_1Axis | 2022 | summer | 1 | 0 | 0 | 765 | 60 | 45900 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
RATSKE_2_RBSSB1_SUN | Hybrid_Solar_1Axis | 2023 | nonsummer | 1 | 0 | 0 | 1060 | 60 | 63600 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
RATSKE_2_RBSSB1_SUN | Hybrid_Solar_1Axis | 2023 | summer | 1 | 0 | 0 | 765 | 60 | 45900 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
RATSKE_2_RBSSB1_SUN | Hybrid_Solar_1Axis | 2024 | nonsummer | 1 | 0 | 0 | 1065 | 60 | 63900 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
RATSKE_2_RBSSB1_SUN | Hybrid_Solar_1Axis | 2024 | summer | 1 | 0 | 0 | 765 | 60 | 45900 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
RATSKE_2_RBSSB2_SUN | Hybrid_Solar_1Axis | 2022 | nonsummer | 1 | 0 | 0 | 1060 | 40 | 42400 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
RATSKE_2_RBSSB2_SUN | Hybrid_Solar_1Axis | 2022 | summer | 1 | 0 | 0 | 765 | 40 | 30600 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
RATSKE_2_RBSSB2_SUN | Hybrid_Solar_1Axis | 2023 | nonsummer | 1 | 0 | 0 | 1060 | 40 | 42400 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
RATSKE_2_RBSSB2_SUN | Hybrid_Solar_1Axis | 2023 | summer | 1 | 0 | 0 | 765 | 40 | 30600 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
RATSKE_2_RBSSB2_SUN | Hybrid_Solar_1Axis | 2024 | nonsummer | 1 | 0 | 0 | 1065 | 40 | 42600 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
RATSKE_2_RBSSB2_SUN | Hybrid_Solar_1Axis | 2024 | summer | 1 | 0 | 0 | 765 | 40 | 30600 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SANBRN_2_EESSB2_SUN | Hybrid_Solar_1Axis | 2022 | nonsummer | 1 | 0 | 0 | 1060 | 130 | 137800 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SANBRN_2_EESSB2_SUN | Hybrid_Solar_1Axis | 2022 | summer | 1 | 0 | 0 | 765 | 130 | 99450 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SANBRN_2_EESSB2_SUN | Hybrid_Solar_1Axis | 2023 | nonsummer | 1 | 0 | 0 | 1060 | 130 | 137800 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SANBRN_2_EESSB2_SUN | Hybrid_Solar_1Axis | 2023 | summer | 1 | 0 | 0 | 765 | 130 | 99450 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SANBRN_2_EESSB2_SUN | Hybrid_Solar_1Axis | 2024 | nonsummer | 1 | 0 | 0 | 1065 | 130 | 138450 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SANBRN_2_EESSB2_SUN | Hybrid_Solar_1Axis | 2024 | summer | 1 | 0 | 0 | 765 | 130 | 99450 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SANBRN_2_ES1BT3_SUN | Hybrid_Solar_1Axis | 2022 | nonsummer | 1 | 0 | 0 | 1060 | 40 | 42400 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SANBRN_2_ES1BT3_SUN | Hybrid_Solar_1Axis | 2022 | summer | 1 | 0 | 0 | 765 | 40 | 30600 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SANBRN_2_ES1BT3_SUN | Hybrid_Solar_1Axis | 2023 | nonsummer | 1 | 0 | 0 | 1060 | 40 | 42400 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SANBRN_2_ES1BT3_SUN | Hybrid_Solar_1Axis | 2023 | summer | 1 | 0 | 0 | 765 | 40 | 30600 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SANBRN_2_ES1BT3_SUN | Hybrid_Solar_1Axis | 2024 | nonsummer | 1 | 0 | 0 | 1065 | 40 | 42600 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SANBRN_2_ES1BT3_SUN | Hybrid_Solar_1Axis | 2024 | summer | 1 | 0 | 0 | 765 | 40 | 30600 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SANBRN_2_ES2SB3_SUN | Hybrid_Solar_1Axis | 2022 | nonsummer | 1 | 0 | 0 | 1060 | 33 | 34980 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SANBRN_2_ES2SB3_SUN | Hybrid_Solar_1Axis | 2022 | summer | 1 | 0 | 0 | 765 | 33 | 25245 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SANBRN_2_ES2SB3_SUN | Hybrid_Solar_1Axis | 2023 | nonsummer | 1 | 0 | 0 | 1060 | 33 | 34980 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SANBRN_2_ES2SB3_SUN | Hybrid_Solar_1Axis | 2023 | summer | 1 | 0 | 0 | 765 | 33 | 25245 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SANBRN_2_ES2SB3_SUN | Hybrid_Solar_1Axis | 2024 | nonsummer | 1 | 0 | 0 | 1065 | 33 | 35145 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SANBRN_2_ES2SB3_SUN | Hybrid_Solar_1Axis | 2024 | summer | 1 | 0 | 0 | 765 | 33 | 25245 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SANBRN_2_SS2SB4_SUN | Hybrid_Solar_1Axis | 2022 | nonsummer | 1 | 0 | 0 | 1060 | 36 | 38160 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SANBRN_2_SS2SB4_SUN | Hybrid_Solar_1Axis | 2022 | summer | 1 | 0 | 0 | 765 | 36 | 27540 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SANBRN_2_SS2SB4_SUN | Hybrid_Solar_1Axis | 2023 | nonsummer | 1 | 0 | 0 | 1060 | 36 | 38160 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SANBRN_2_SS2SB4_SUN | Hybrid_Solar_1Axis | 2023 | summer | 1 | 0 | 0 | 765 | 36 | 27540 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SANBRN_2_SS2SB4_SUN | Hybrid_Solar_1Axis | 2024 | nonsummer | 1 | 0 | 0 | 1065 | 36 | 38340 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SANBRN_2_SS2SB4_SUN | Hybrid_Solar_1Axis | 2024 | summer | 1 | 0 | 0 | 765 | 36 | 27540 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SLATE_2_SLASR2_SUN | Hybrid_Solar_1Axis | 2022 | nonsummer | 1 | 0 | 0 | 1060 | 93 | 98580 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SLATE_2_SLASR2_SUN | Hybrid_Solar_1Axis | 2022 | summer | 1 | 0 | 0 | 765 | 93 | 71145 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SLATE_2_SLASR2_SUN | Hybrid_Solar_1Axis | 2023 | nonsummer | 1 | 0 | 0 | 1060 | 93 | 98580 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SLATE_2_SLASR2_SUN | Hybrid_Solar_1Axis | 2023 | summer | 1 | 0 | 0 | 765 | 93 | 71145 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SLATE_2_SLASR2_SUN | Hybrid_Solar_1Axis | 2024 | nonsummer | 1 | 0 | 0 | 1065 | 93 | 99045 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SLATE_2_SLASR2_SUN | Hybrid_Solar_1Axis | 2024 | summer | 1 | 0 | 0 | 765 | 93 | 71145 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SLATE_2_SLASR4_SUN | Hybrid_Solar_1Axis | 2022 | nonsummer | 1 | 0 | 0 | 1060 | 63 | 66780 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SLATE_2_SLASR4_SUN | Hybrid_Solar_1Axis | 2022 | summer | 1 | 0 | 0 | 765 | 63 | 48195 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SLATE_2_SLASR4_SUN | Hybrid_Solar_1Axis | 2023 | nonsummer | 1 | 0 | 0 | 1060 | 63 | 66780 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SLATE_2_SLASR4_SUN | Hybrid_Solar_1Axis | 2023 | summer | 1 | 0 | 0 | 765 | 63 | 48195 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SLATE_2_SLASR4_SUN | Hybrid_Solar_1Axis | 2024 | nonsummer | 1 | 0 | 0 | 1065 | 63 | 67095 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SLATE_2_SLASR4_SUN | Hybrid_Solar_1Axis | 2024 | summer | 1 | 0 | 0 | 765 | 63 | 48195 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SLATE_2_SLASR5_SUN | Hybrid_Solar_1Axis | 2022 | nonsummer | 1 | 0 | 0 | 1060 | 26 | 27560 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SLATE_2_SLASR5_SUN | Hybrid_Solar_1Axis | 2022 | summer | 1 | 0 | 0 | 765 | 26 | 19890 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SLATE_2_SLASR5_SUN | Hybrid_Solar_1Axis | 2023 | nonsummer | 1 | 0 | 0 | 1060 | 26 | 27560 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SLATE_2_SLASR5_SUN | Hybrid_Solar_1Axis | 2023 | summer | 1 | 0 | 0 | 765 | 26 | 19890 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SLATE_2_SLASR5_SUN | Hybrid_Solar_1Axis | 2024 | nonsummer | 1 | 0 | 0 | 1065 | 26 | 27690 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SLATE_2_SLASR5_SUN | Hybrid_Solar_1Axis | 2024 | summer | 1 | 0 | 0 | 765 | 26 | 19890 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SLATE_2_SLASR3_SUN | Hybrid_Solar_Fixed | 2022 | nonsummer | 1 | 0 | 0 | 1060 | 67.5 | 71550 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SLATE_2_SLASR3_SUN | Hybrid_Solar_Fixed | 2022 | summer | 1 | 0 | 0 | 765 | 67.5 | 51637.5 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SLATE_2_SLASR3_SUN | Hybrid_Solar_Fixed | 2023 | nonsummer | 1 | 0 | 0 | 1060 | 67.5 | 71550 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SLATE_2_SLASR3_SUN | Hybrid_Solar_Fixed | 2023 | summer | 1 | 0 | 0 | 765 | 67.5 | 51637.5 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SLATE_2_SLASR3_SUN | Hybrid_Solar_Fixed | 2024 | nonsummer | 1 | 0 | 0 | 1065 | 67.5 | 71887.5 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SLATE_2_SLASR3_SUN | Hybrid_Solar_Fixed | 2024 | summer | 1 | 0 | 0 | 765 | 67.5 | 51637.5 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
ALAMO_6_UNIT | Hydro | 2022 | nonsummer | 31413 | 2696.2 | 0 | 1060 | 17 | 18020 | 0 | Individual | 14.96% | 0% |  |  | 14.96% | 0% | TRUE |  |  | 14.96% | 0%
ALAMO_6_UNIT | Hydro | 2022 | summer | 31413 | 680 | 0 | 765 | 17 | 13005 | 0 | Individual | 5.229% | 0% |  |  | 5.229% | 0% | TRUE |  |  | 5.229% | 0%
ALAMO_6_UNIT | Hydro | 2023 | nonsummer | 31413 | 0 | 0 | 1060 | 17 | 18020 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
ALAMO_6_UNIT | Hydro | 2023 | summer | 31413 | 27.2 | 0 | 765 | 17 | 13005 | 0 | Individual | 0.2092% | 0% |  |  | 0.2092% | 0% | TRUE |  |  | 0.2092% | 0%
ALAMO_6_UNIT | Hydro | 2024 | nonsummer | 31413 | 7992.8333 | 0 | 1065 | 17 | 18105 | 0 | Individual | 44.15% | 0% |  |  | 44.15% | 0% | TRUE |  |  | 44.15% | 0%
ALAMO_6_UNIT | Hydro | 2024 | summer | 31413 | 574.3167 | 0 | 765 | 17 | 13005 | 0 | Individual | 4.416% | 0% |  |  | 4.416% | 0% | TRUE |  |  | 4.416% | 0%
APLHIL_1_SFKHY1 | Hydro | 2022 | nonsummer | 44169 | 1594.6 | 0 | 1060 | 2.68 | 2840.8 | 0 | Individual | 56.13% | 0% |  |  | 56.13% | 0% | TRUE |  |  | 56.13% | 0%
APLHIL_1_SFKHY1 | Hydro | 2022 | summer | 44169 | 281.4 | 0 | 765 | 2.68 | 2050.2 | 0 | Individual | 13.73% | 0% |  |  | 13.73% | 0% | TRUE |  |  | 13.73% | 0%
APLHIL_1_SFKHY1 | Hydro | 2023 | nonsummer | 44169 | 243.88 | 0 | 1060 | 2.68 | 2840.8 | 0 | Individual | 8.585% | 0% |  |  | 8.585% | 0% | TRUE |  |  | 8.585% | 0%
APLHIL_1_SFKHY1 | Hydro | 2023 | summer | 44169 | 139.2707 | 0 | 765 | 2.68 | 2050.2 | 0 | Individual | 6.793% | 0% |  |  | 6.793% | 0% | TRUE |  |  | 6.793% | 0%
APLHIL_1_SFKHY1 | Hydro | 2024 | nonsummer | 44169 | 119.394 | 0 | 1065 | 2.68 | 2854.2 | 0 | Individual | 4.183% | 0% |  |  | 4.183% | 0% | TRUE |  |  | 4.183% | 0%
APLHIL_1_SFKHY1 | Hydro | 2024 | summer | 44169 | 8.04 | 0 | 765 | 2.68 | 2050.2 | 0 | Individual | 0.3922% | 0% |  |  | 0.3922% | 0% | TRUE |  |  | 0.3922% | 0%
BALCHS_7_UNIT 1 | Hydro | 2022 | nonsummer | 9863 | 1570.07 | 0 | 1060 | 31 | 32860 | 0 | Individual | 4.778% | 0% |  |  | 4.778% | 0% | TRUE |  |  | 4.778% | 0%
BALCHS_7_UNIT 1 | Hydro | 2022 | summer | 9863 | 270.9667 | 0 | 765 | 31 | 23715 | 0 | Individual | 1.143% | 0% |  |  | 1.143% | 0% | TRUE |  |  | 1.143% | 0%
BALCHS_7_UNIT 1 | Hydro | 2023 | nonsummer | 9863 | 505.8 | 0 | 1060 | 31 | 32860 | 0 | Individual | 1.539% | 0% |  |  | 1.539% | 0% | TRUE |  |  | 1.539% | 0%
BALCHS_7_UNIT 1 | Hydro | 2023 | summer | 9863 | 584.6667 | 2.2333 | 765 | 31 | 23715 | 0 | Individual | 2.465% | 0.009417% |  |  | 2.465% | 0.009417% | TRUE |  |  | 2.465% | 0.009417%
BALCHS_7_UNIT 1 | Hydro | 2024 | nonsummer | 9863 | 1207.2033 | 0 | 1065 | 31 | 33015 | 0 | Individual | 3.657% | 0% |  |  | 3.657% | 0% | TRUE |  |  | 3.657% | 0%
BALCHS_7_UNIT 1 | Hydro | 2024 | summer | 9863 | 695.6333 | 22.1 | 765 | 31 | 23715 | 0 | Individual | 2.933% | 0.09319% |  |  | 2.933% | 0.09319% | TRUE |  |  | 2.933% | 0.09319%
BALCHS_7_UNIT 2 | Hydro | 2022 | nonsummer | 21186 | 4786.2617 | 0 | 1060 | 52.5 | 55650 | 0 | Individual | 8.601% | 0% |  |  | 8.601% | 0% | TRUE |  |  | 8.601% | 0%
BALCHS_7_UNIT 2 | Hydro | 2022 | summer | 21186 | 272.525 | 0 | 765 | 52.5 | 40162.5 | 0 | Individual | 0.6786% | 0% |  |  | 0.6786% | 0% | TRUE |  |  | 0.6786% | 0%
BALCHS_7_UNIT 2 | Hydro | 2023 | nonsummer | 21186 | 2176.05 | 0 | 1060 | 52.5 | 55650 | 0 | Individual | 3.91% | 0% |  |  | 3.91% | 0% | TRUE |  |  | 3.91% | 0%
BALCHS_7_UNIT 2 | Hydro | 2023 | summer | 21186 | 621.1292 | 0 | 765 | 52.5 | 40162.5 | 0 | Individual | 1.547% | 0% |  |  | 1.547% | 0% | TRUE |  |  | 1.547% | 0%
BALCHS_7_UNIT 2 | Hydro | 2024 | nonsummer | 21186 | 364.7917 | 0 | 1065 | 52.5 | 55912.5 | 0 | Individual | 0.6524% | 0% |  |  | 0.6524% | 0% | TRUE |  |  | 0.6524% | 0%
BALCHS_7_UNIT 2 | Hydro | 2024 | summer | 21186 | 1416.125 | 0 | 765 | 52.5 | 40162.5 | 0 | Individual | 3.526% | 0% |  |  | 3.526% | 0% | TRUE |  |  | 3.526% | 0%
BALCHS_7_UNIT 3 | Hydro | 2022 | nonsummer | 21186 | 4366.0133 | 0 | 1060 | 54.6 | 57876 | 0 | Individual | 7.544% | 0% |  |  | 7.544% | 0% | TRUE |  |  | 7.544% | 0%
BALCHS_7_UNIT 3 | Hydro | 2022 | summer | 21186 | 161.7033 | 0 | 765 | 54.6 | 41769 | 0 | Individual | 0.3871% | 0% |  |  | 0.3871% | 0% | TRUE |  |  | 0.3871% | 0%
BALCHS_7_UNIT 3 | Hydro | 2023 | nonsummer | 21186 | 2600.11 | 0 | 1060 | 54.6 | 57876 | 0 | Individual | 4.493% | 0% |  |  | 4.493% | 0% | TRUE |  |  | 4.493% | 0%
BALCHS_7_UNIT 3 | Hydro | 2023 | summer | 21186 | 719.2233 | 0 | 765 | 54.6 | 41769 | 0 | Individual | 1.722% | 0% |  |  | 1.722% | 0% | TRUE |  |  | 1.722% | 0%
BALCHS_7_UNIT 3 | Hydro | 2024 | nonsummer | 21186 | 478.0767 | 0 | 1065 | 54.6 | 58149 | 0 | Individual | 0.8222% | 0% |  |  | 0.8222% | 0% | TRUE |  |  | 0.8222% | 0%
BALCHS_7_UNIT 3 | Hydro | 2024 | summer | 21186 | 1615.9267 | 0 | 765 | 54.6 | 41769 | 0 | Individual | 3.869% | 0% |  |  | 3.869% | 0% | TRUE |  |  | 3.869% | 0%
BEARDS_7_UNIT 1 | Hydro | 2022 | nonsummer | 20821 | 9.4167 | 0 | 1060 | 11.5 | 12190 | 0 | Individual | 0.07725% | 0% |  |  | 0.07725% | 0% | TRUE |  |  | 0.07725% | 0%
BEARDS_7_UNIT 1 | Hydro | 2022 | summer | 20821 | 59.9917 | 0 | 765 | 11.5 | 8797.5 | 0 | Individual | 0.6819% | 0% |  |  | 0.6819% | 0% | TRUE |  |  | 0.6819% | 0%
BEARDS_7_UNIT 1 | Hydro | 2023 | nonsummer | 20821 | 25.7733 | 0 | 1060 | 11.5 | 12190 | 0 | Individual | 0.2114% | 0% |  |  | 0.2114% | 0% | TRUE |  |  | 0.2114% | 0%
BEARDS_7_UNIT 1 | Hydro | 2023 | summer | 20821 | 40.25 | 0 | 765 | 11.5 | 8797.5 | 0 | Individual | 0.4575% | 0% |  |  | 0.4575% | 0% | TRUE |  |  | 0.4575% | 0%
BEARDS_7_UNIT 1 | Hydro | 2024 | nonsummer | 20821 | 57.5 | 0 | 1065 | 11.5 | 12247.5 | 0 | Individual | 0.4695% | 0% |  |  | 0.4695% | 0% | TRUE |  |  | 0.4695% | 0%
BEARDS_7_UNIT 1 | Hydro | 2024 | summer | 20821 | 0 | 0 | 765 | 11.5 | 8797.5 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
BELDEN_7_UNIT 1 | Hydro | 2022 | nonsummer | 25204 | 33609.44 | 0 | 1060 | 119 | 126140 | 0 | Individual | 26.64% | 0% |  |  | 26.64% | 0% | TRUE |  |  | 26.64% | 0%
BELDEN_7_UNIT 1 | Hydro | 2022 | summer | 25204 | 41046.8353 | 0 | 765 | 119 | 91035 | 0 | Individual | 45.09% | 0% |  |  | 45.09% | 0% | TRUE |  |  | 45.09% | 0%
BELDEN_7_UNIT 1 | Hydro | 2023 | nonsummer | 25204 | 40548.8447 | 0 | 1060 | 119 | 126140 | 0 | Individual | 32.15% | 0% |  |  | 32.15% | 0% | TRUE |  |  | 32.15% | 0%
BELDEN_7_UNIT 1 | Hydro | 2023 | summer | 25204 | 83680.1 | 0 | 765 | 119 | 91035 | 0 | Individual | 91.92% | 0% |  |  | 91.92% | 0% | TRUE |  |  | 91.92% | 0%
BELDEN_7_UNIT 1 | Hydro | 2024 | nonsummer | 25204 | 32158.9833 | 0 | 1065 | 119 | 126735 | 0 | Individual | 25.37% | 0% |  |  | 25.37% | 0% | TRUE |  |  | 25.37% | 0%
BELDEN_7_UNIT 1 | Hydro | 2024 | summer | 25204 | 28846.0162 | 0 | 765 | 119 | 91035 | 0 | Individual | 31.69% | 0% |  |  | 31.69% | 0% | TRUE |  |  | 31.69% | 0%
BIGCRK_2_EXESWD | Hydro | 2022 | nonsummer | 4750 | 240962.7333 | 0 | 1060 | 820 | 869200 | 0 | Individual | 27.72% | 0% |  |  | 27.72% | 0% | TRUE |  |  | 27.72% | 0%
BIGCRK_2_EXESWD | Hydro | 2022 | summer | 4750 | 151964.6333 | 0 | 765 | 820 | 627300 | 0 | Individual | 24.23% | 0% |  |  | 24.23% | 0% | TRUE |  |  | 24.23% | 0%
BIGCRK_2_EXESWD | Hydro | 2023 | nonsummer | 4750 | 242575.945 | 0 | 1060 | 820 | 869200 | 0 | Individual | 27.91% | 0% |  |  | 27.91% | 0% | TRUE |  |  | 27.91% | 0%
BIGCRK_2_EXESWD | Hydro | 2023 | summer | 4750 | 176949.66 | 0 | 765 | 820 | 627300 | 0 | Individual | 28.21% | 0% |  |  | 28.21% | 0% | TRUE |  |  | 28.21% | 0%
BIGCRK_2_EXESWD | Hydro | 2024 | nonsummer | 4750 | 239031.5667 | 0 | 1065 | 820 | 873300 | 0 | Individual | 27.37% | 0% |  |  | 27.37% | 0% | TRUE |  |  | 27.37% | 0%
BIGCRK_2_EXESWD | Hydro | 2024 | summer | 4750 | 94645.3167 | 0 | 765 | 820 | 627300 | 0 | Individual | 15.09% | 0% |  |  | 15.09% | 0% | TRUE |  |  | 15.09% | 0%
BLACK_7_UNIT 1 | Hydro | 2022 | nonsummer | 24108 | 4131.3667 | 0 | 1060 | 85 | 90100 | 0 | Individual | 4.585% | 0% |  |  | 4.585% | 0% | TRUE |  |  | 4.585% | 0%
BLACK_7_UNIT 1 | Hydro | 2022 | summer | 24108 | 617.7067 | 0 | 765 | 85 | 65025 | 0 | Individual | 0.95% | 0% |  |  | 0.95% | 0% | TRUE |  |  | 0.95% | 0%
BLACK_7_UNIT 1 | Hydro | 2023 | nonsummer | 24108 | 7724.3333 | 115 | 1060 | 85 | 90100 | 0 | Individual | 8.573% | 0.1276% |  |  | 8.573% | 0.1276% | TRUE |  |  | 8.573% | 0.1276%
BLACK_7_UNIT 1 | Hydro | 2023 | summer | 24108 | 1364.6 | 0 | 765 | 85 | 65025 | 0 | Individual | 2.099% | 0% |  |  | 2.099% | 0% | TRUE |  |  | 2.099% | 0%
BLACK_7_UNIT 1 | Hydro | 2024 | nonsummer | 24108 | 5455.3833 | 0 | 1065 | 85 | 90525 | 0 | Individual | 6.026% | 0% |  |  | 6.026% | 0% | TRUE |  |  | 6.026% | 0%
BLACK_7_UNIT 1 | Hydro | 2024 | summer | 24108 | 2248.055 | 0 | 765 | 85 | 65025 | 0 | Individual | 3.457% | 0% |  |  | 3.457% | 0% | TRUE |  |  | 3.457% | 0%
BLACK_7_UNIT 2 | Hydro | 2022 | nonsummer | 23743 | 3482.32 | 44.1 | 1060 | 84.1 | 89146 | 0 | Individual | 3.906% | 0.04947% |  |  | 3.906% | 0.04947% | TRUE |  |  | 3.906% | 0.04947%
BLACK_7_UNIT 2 | Hydro | 2022 | summer | 23743 | 1012.0867 | 0 | 765 | 84.1 | 64336.5 | 0 | Individual | 1.573% | 0% |  |  | 1.573% | 0% | TRUE |  |  | 1.573% | 0%
BLACK_7_UNIT 2 | Hydro | 2023 | nonsummer | 23743 | 3394.3167 | 0 | 1060 | 84.1 | 89146 | 0 | Individual | 3.808% | 0% |  |  | 3.808% | 0% | TRUE |  |  | 3.808% | 0%
BLACK_7_UNIT 2 | Hydro | 2023 | summer | 23743 | 981.4017 | 0 | 765 | 84.1 | 64336.5 | 0 | Individual | 1.525% | 0% |  |  | 1.525% | 0% | TRUE |  |  | 1.525% | 0%
BLACK_7_UNIT 2 | Hydro | 2024 | nonsummer | 23743 | 3758.8033 | 0 | 1065 | 84.1 | 89566.5 | 0 | Individual | 4.197% | 0% |  |  | 4.197% | 0% | TRUE |  |  | 4.197% | 0%
BLACK_7_UNIT 2 | Hydro | 2024 | summer | 23743 | 2307.1533 | 0 | 765 | 84.1 | 64336.5 | 0 | Individual | 3.586% | 0% |  |  | 3.586% | 0% | TRUE |  |  | 3.586% | 0%
BLCKBT_2_STONEY | Hydro | 2022 | nonsummer | 32143 | 3927.39 | 0 | 1060 | 6.2 | 6572 | 0 | Individual | 59.76% | 0% |  |  | 59.76% | 0% | TRUE |  |  | 59.76% | 0%
BLCKBT_2_STONEY | Hydro | 2022 | summer | 32143 | 1878.7033 | 0 | 765 | 6.2 | 4743 | 0 | Individual | 39.61% | 0% |  |  | 39.61% | 0% | TRUE |  |  | 39.61% | 0%
BLCKBT_2_STONEY | Hydro | 2023 | nonsummer | 32143 | 906.8533 | 0 | 1060 | 6.2 | 6572 | 0 | Individual | 13.8% | 0% |  |  | 13.8% | 0% | TRUE |  |  | 13.8% | 0%
BLCKBT_2_STONEY | Hydro | 2023 | summer | 32143 | 746.3767 | 0 | 765 | 6.2 | 4743 | 0 | Individual | 15.74% | 0% |  |  | 15.74% | 0% | TRUE |  |  | 15.74% | 0%
BLCKBT_2_STONEY | Hydro | 2024 | nonsummer | 32143 | 1407.9167 | 0 | 1065 | 6.2 | 6603 | 0 | Individual | 21.32% | 0% |  |  | 21.32% | 0% | TRUE |  |  | 21.32% | 0%
BLCKBT_2_STONEY | Hydro | 2024 | summer | 32143 | 3761.3333 | 0 | 765 | 6.2 | 4743 | 0 | Individual | 79.3% | 0% |  |  | 79.3% | 0% | TRUE |  |  | 79.3% | 0%
BUCKCK_7_PL1X2 | Hydro | 2022 | nonsummer | 10228 | 3018.1667 | 0 | 1060 | 57.25 | 60685 | 0 | Individual | 4.973% | 0% |  |  | 4.973% | 0% | TRUE |  |  | 4.973% | 0%
BUCKCK_7_PL1X2 | Hydro | 2022 | summer | 10228 | 847.24 | 47.2452 | 765 | 57.25 | 43796.25 | 0 | Individual | 1.935% | 0.1079% |  |  | 1.935% | 0.1079% | TRUE |  |  | 1.935% | 0.1079%
BUCKCK_7_PL1X2 | Hydro | 2023 | nonsummer | 10228 | 1624.0333 | 0 | 1060 | 57.25 | 60685 | 0 | Individual | 2.676% | 0% |  |  | 2.676% | 0% | TRUE |  |  | 2.676% | 0%
BUCKCK_7_PL1X2 | Hydro | 2023 | summer | 10228 | 2396.1933 | 14.75 | 765 | 57.25 | 43796.25 | 0 | Individual | 5.471% | 0.03368% |  |  | 5.471% | 0.03368% | TRUE |  |  | 5.471% | 0.03368%
BUCKCK_7_PL1X2 | Hydro | 2024 | nonsummer | 10228 | 4190.32 | 0 | 1065 | 57.25 | 60971.25 | 0 | Individual | 6.873% | 0% |  |  | 6.873% | 0% | TRUE |  |  | 6.873% | 0%
BUCKCK_7_PL1X2 | Hydro | 2024 | summer | 10228 | 1500.5667 | 0 | 765 | 57.25 | 43796.25 | 0 | Individual | 3.426% | 0% |  |  | 3.426% | 0% | TRUE |  |  | 3.426% | 0%
BUTTVL_7_UNIT 1 | Hydro | 2022 | nonsummer | 21186 | 131.6667 | 0 | 1060 | 39.5 | 41870 | 0 | Individual | 0.3145% | 0% |  |  | 0.3145% | 0% | TRUE |  |  | 0.3145% | 0%
BUTTVL_7_UNIT 1 | Hydro | 2022 | summer | 21186 | 518.335 | 0 | 765 | 39.5 | 30217.5 | 0 | Individual | 1.715% | 0% |  |  | 1.715% | 0% | TRUE |  |  | 1.715% | 0%
BUTTVL_7_UNIT 1 | Hydro | 2023 | nonsummer | 21186 | 6183.725 | 0 | 1060 | 39.5 | 41870 | 0 | Individual | 14.77% | 0% |  |  | 14.77% | 0% | TRUE |  |  | 14.77% | 0%
BUTTVL_7_UNIT 1 | Hydro | 2023 | summer | 21186 | 0 | 0 | 765 | 39.5 | 30217.5 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
BUTTVL_7_UNIT 1 | Hydro | 2024 | nonsummer | 21186 | 0 | 0 | 1065 | 39.5 | 42067.5 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
BUTTVL_7_UNIT 1 | Hydro | 2024 | summer | 21186 | 858.4667 | 0 | 765 | 39.5 | 30217.5 | 0 | Individual | 2.841% | 0% |  |  | 2.841% | 0% | TRUE |  |  | 2.841% | 0%
CAMPFW_7_FARWST | Hydro | 2022 | nonsummer | 31048 | 1224 | 0 | 1060 | 6.8 | 7208 | 0 | Individual | 16.98% | 0% |  |  | 16.98% | 0% | TRUE |  |  | 16.98% | 0%
CAMPFW_7_FARWST | Hydro | 2022 | summer | 31048 | 108.8 | 0 | 765 | 6.8 | 5202 | 0 | Individual | 2.092% | 0% |  |  | 2.092% | 0% | TRUE |  |  | 2.092% | 0%
CAMPFW_7_FARWST | Hydro | 2023 | nonsummer | 31048 | 2073.5467 | 0 | 1060 | 6.8 | 7208 | 0 | Individual | 28.77% | 0% |  |  | 28.77% | 0% | TRUE |  |  | 28.77% | 0%
CAMPFW_7_FARWST | Hydro | 2023 | summer | 31048 | 1666 | 0 | 765 | 6.8 | 5202 | 0 | Individual | 32.03% | 0% |  |  | 32.03% | 0% | TRUE |  |  | 32.03% | 0%
CAMPFW_7_FARWST | Hydro | 2024 | nonsummer | 31048 | 782 | 0 | 1065 | 6.8 | 7242 | 0 | Individual | 10.8% | 0% |  |  | 10.8% | 0% | TRUE |  |  | 10.8% | 0%
CAMPFW_7_FARWST | Hydro | 2024 | summer | 31048 | 0 | 0 | 765 | 6.8 | 5202 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
CARBOU_7_PL2X3 | Hydro | 2022 | nonsummer | 7672 | 24535.0833 | 0 | 1060 | 49 | 51940 | 0 | Individual | 47.24% | 0% |  |  | 47.24% | 0% | TRUE |  |  | 47.24% | 0%
CARBOU_7_PL2X3 | Hydro | 2022 | summer | 7672 | 16056.5867 | 0 | 765 | 49 | 37485 | 0 | Individual | 42.83% | 0% |  |  | 42.83% | 0% | TRUE |  |  | 42.83% | 0%
CARBOU_7_PL2X3 | Hydro | 2023 | nonsummer | 7672 | 3605.6243 | 0 | 1060 | 49 | 51940 | 0 | Individual | 6.942% | 0% |  |  | 6.942% | 0% | TRUE |  |  | 6.942% | 0%
CARBOU_7_PL2X3 | Hydro | 2023 | summer | 7672 | 7617.1817 | 0 | 765 | 49 | 37485 | 0 | Individual | 20.32% | 0% |  |  | 20.32% | 0% | TRUE |  |  | 20.32% | 0%
CARBOU_7_PL2X3 | Hydro | 2024 | nonsummer | 7672 | 6372.6592 | 0 | 1065 | 49 | 52185 | 0 | Individual | 12.21% | 0% |  |  | 12.21% | 0% | TRUE |  |  | 12.21% | 0%
CARBOU_7_PL2X3 | Hydro | 2024 | summer | 7672 | 9376.4935 | 0 | 765 | 49 | 37485 | 0 | Individual | 25.01% | 0% |  |  | 25.01% | 0% | TRUE |  |  | 25.01% | 0%
CARBOU_7_PL4X5 | Hydro | 2022 | nonsummer | 21186 | 53570.6567 | 0 | 1060 | 120 | 127200 | 0 | Individual | 42.12% | 0% |  |  | 42.12% | 0% | TRUE |  |  | 42.12% | 0%
CARBOU_7_PL4X5 | Hydro | 2022 | summer | 21186 | 19959.718 | 0 | 765 | 120 | 91800 | 0 | Individual | 21.74% | 0% |  |  | 21.74% | 0% | TRUE |  |  | 21.74% | 0%
CARBOU_7_PL4X5 | Hydro | 2023 | nonsummer | 21186 | 15034.9125 | 0 | 1060 | 120 | 127200 | 0 | Individual | 11.82% | 0% |  |  | 11.82% | 0% | TRUE |  |  | 11.82% | 0%
CARBOU_7_PL4X5 | Hydro | 2023 | summer | 21186 | 6606.9 | 0 | 765 | 120 | 91800 | 0 | Individual | 7.197% | 0% |  |  | 7.197% | 0% | TRUE |  |  | 7.197% | 0%
CARBOU_7_PL4X5 | Hydro | 2024 | nonsummer | 21186 | 45527.7633 | 0 | 1065 | 120 | 127800 | 0 | Individual | 35.62% | 0% |  |  | 35.62% | 0% | TRUE |  |  | 35.62% | 0%
CARBOU_7_PL4X5 | Hydro | 2024 | summer | 21186 | 39497.456 | 0 | 765 | 120 | 91800 | 0 | Individual | 43.03% | 0% |  |  | 43.03% | 0% | TRUE |  |  | 43.03% | 0%
CARBOU_7_UNIT 1 | Hydro | 2022 | nonsummer | 7672 | 4225.9667 | 0 | 1060 | 24 | 25440 | 0 | Individual | 16.61% | 0% |  |  | 16.61% | 0% | TRUE |  |  | 16.61% | 0%
CARBOU_7_UNIT 1 | Hydro | 2022 | summer | 7672 | 4200 | 0 | 765 | 24 | 18360 | 0 | Individual | 22.88% | 0% |  |  | 22.88% | 0% | TRUE |  |  | 22.88% | 0%
CARBOU_7_UNIT 1 | Hydro | 2023 | nonsummer | 7672 | 4271.5 | 0 | 1060 | 24 | 25440 | 0 | Individual | 16.79% | 0% |  |  | 16.79% | 0% | TRUE |  |  | 16.79% | 0%
CARBOU_7_UNIT 1 | Hydro | 2023 | summer | 7672 | 12129 | 0 | 765 | 24 | 18360 | 0 | Individual | 66.06% | 0% |  |  | 66.06% | 0% | TRUE |  |  | 66.06% | 0%
CARBOU_7_UNIT 1 | Hydro | 2024 | nonsummer | 7672 | 1717.5333 | 0 | 1065 | 24 | 25560 | 0 | Individual | 6.72% | 0% |  |  | 6.72% | 0% | TRUE |  |  | 6.72% | 0%
CARBOU_7_UNIT 1 | Hydro | 2024 | summer | 7672 | 1744.94 | 0 | 765 | 24 | 18360 | 0 | Individual | 9.504% | 0% |  |  | 9.504% | 0% | TRUE |  |  | 9.504% | 0%
CENTER_2_RHONDO | Hydro | 2022 | nonsummer | 30682 | 1715.05 | 0 | 1060 | 1.91 | 2024.6 | 0 | Individual | 84.71% | 0% |  |  | 84.71% | 0% | TRUE |  |  | 84.71% | 0%
CENTER_2_RHONDO | Hydro | 2022 | summer | 30682 | 1310.65 | 0 | 765 | 1.91 | 1461.15 | 0 | Individual | 89.7% | 0% |  |  | 89.7% | 0% | TRUE |  |  | 89.7% | 0%
CENTER_2_RHONDO | Hydro | 2023 | nonsummer | 30682 | 1922.55 | 0 | 1060 | 1.91 | 2024.6 | 0 | Individual | 94.96% | 0% |  |  | 94.96% | 0% | TRUE |  |  | 94.96% | 0%
CENTER_2_RHONDO | Hydro | 2023 | summer | 30682 | 1336.3583 | 0 | 765 | 1.91 | 1461.15 | 0 | Individual | 91.46% | 0% |  |  | 91.46% | 0% | TRUE |  |  | 91.46% | 0%
CENTER_2_RHONDO | Hydro | 2024 | nonsummer | 30682 | 0 | 0 | 1065 | 1.91 | 2034.15 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
CENTER_2_RHONDO | Hydro | 2024 | summer | 30682 | 0 | 0 | 765 | 1.91 | 1461.15 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
CHICPK_7_UNIT 1 | Hydro | 2022 | nonsummer | 23743 | 21595.0017 | 0 | 1060 | 42 | 44520 | 0 | Individual | 48.51% | 0% |  |  | 48.51% | 0% | TRUE |  |  | 48.51% | 0%
CHICPK_7_UNIT 1 | Hydro | 2022 | summer | 23743 | 8608.3 | 0 | 765 | 42 | 32130 | 0 | Individual | 26.79% | 0% |  |  | 26.79% | 0% | TRUE |  |  | 26.79% | 0%
CHICPK_7_UNIT 1 | Hydro | 2023 | nonsummer | 23743 | 15692.3402 | 0 | 1060 | 42 | 44520 | 0 | Individual | 35.25% | 0% |  |  | 35.25% | 0% | TRUE |  |  | 35.25% | 0%
CHICPK_7_UNIT 1 | Hydro | 2023 | summer | 23743 | 11527 | 0 | 765 | 42 | 32130 | 0 | Individual | 35.88% | 0% |  |  | 35.88% | 0% | TRUE |  |  | 35.88% | 0%
CHICPK_7_UNIT 1 | Hydro | 2024 | nonsummer | 23743 | 25605.9 | 0 | 1065 | 42 | 44730 | 0 | Individual | 57.25% | 0% |  |  | 57.25% | 0% | TRUE |  |  | 57.25% | 0%
CHICPK_7_UNIT 1 | Hydro | 2024 | summer | 23743 | 21753 | 0 | 765 | 42 | 32130 | 0 | Individual | 67.7% | 0% |  |  | 67.7% | 0% | TRUE |  |  | 67.7% | 0%
COLGAT_7_UNIT 1 | Hydro | 2022 | nonsummer | 25204 | 25497.67 | 0 | 1060 | 176.72 | 187323.2 | 0 | Individual | 13.61% | 0% |  |  | 13.61% | 0% | TRUE |  |  | 13.61% | 0%
COLGAT_7_UNIT 1 | Hydro | 2022 | summer | 25204 | 17893.5333 | 0 | 765 | 176.72 | 135190.8 | 0 | Individual | 13.24% | 0% |  |  | 13.24% | 0% | TRUE |  |  | 13.24% | 0%
COLGAT_7_UNIT 1 | Hydro | 2023 | nonsummer | 25204 | 20560.8033 | 0 | 1060 | 176.72 | 187323.2 | 0 | Individual | 10.98% | 0% |  |  | 10.98% | 0% | TRUE |  |  | 10.98% | 0%
COLGAT_7_UNIT 1 | Hydro | 2023 | summer | 25204 | 15146.64 | 0 | 765 | 176.72 | 135190.8 | 0 | Individual | 11.2% | 0% |  |  | 11.2% | 0% | TRUE |  |  | 11.2% | 0%
COLGAT_7_UNIT 1 | Hydro | 2024 | nonsummer | 25204 | 27089.25 | 0 | 1065 | 176.72 | 188206.8 | 0 | Individual | 14.39% | 0% |  |  | 14.39% | 0% | TRUE |  |  | 14.39% | 0%
COLGAT_7_UNIT 1 | Hydro | 2024 | summer | 25204 | 13284.95 | 0 | 765 | 176.72 | 135190.8 | 0 | Individual | 9.827% | 0% |  |  | 9.827% | 0% | TRUE |  |  | 9.827% | 0%
COLGAT_7_UNIT 2 | Hydro | 2022 | nonsummer | 25204 | 23775.5333 | 0 | 1060 | 175.67 | 186210.2 | 0 | Individual | 12.77% | 0% |  |  | 12.77% | 0% | TRUE |  |  | 12.77% | 0%
COLGAT_7_UNIT 2 | Hydro | 2022 | summer | 25204 | 14902.9833 | 0 | 765 | 175.67 | 134387.55 | 0 | Individual | 11.09% | 0% |  |  | 11.09% | 0% | TRUE |  |  | 11.09% | 0%
COLGAT_7_UNIT 2 | Hydro | 2023 | nonsummer | 25204 | 21641.7167 | 0 | 1060 | 175.67 | 186210.2 | 0 | Individual | 11.62% | 0% |  |  | 11.62% | 0% | TRUE |  |  | 11.62% | 0%
COLGAT_7_UNIT 2 | Hydro | 2023 | summer | 25204 | 14509.39 | 0 | 765 | 175.67 | 134387.55 | 0 | Individual | 10.8% | 0% |  |  | 10.8% | 0% | TRUE |  |  | 10.8% | 0%
COLGAT_7_UNIT 2 | Hydro | 2024 | nonsummer | 25204 | 21658.1333 | 0 | 1065 | 175.67 | 187088.55 | 0 | Individual | 11.58% | 0% |  |  | 11.58% | 0% | TRUE |  |  | 11.58% | 0%
COLGAT_7_UNIT 2 | Hydro | 2024 | summer | 25204 | 15630.0833 | 0 | 765 | 175.67 | 134387.55 | 0 | Individual | 11.63% | 0% |  |  | 11.63% | 0% | TRUE |  |  | 11.63% | 0%
COLVIL_7_PL1X2 | Hydro | 2022 | nonsummer | 32873 | 1234.3 | 0 | 1060 | 246.86 | 261671.6 | 0 | Individual | 0.4717% | 0% |  |  | 0.4717% | 0% | TRUE |  |  | 0.4717% | 0%
COLVIL_7_PL1X2 | Hydro | 2022 | summer | 32873 | 854.2857 | 0 | 765 | 246.86 | 188847.9 | 0 | Individual | 0.4524% | 0% |  |  | 0.4524% | 0% | TRUE |  |  | 0.4524% | 0%
COLVIL_7_PL1X2 | Hydro | 2023 | nonsummer | 32873 | 1282.191 | 0 | 1060 | 246.86 | 261671.6 | 0 | Individual | 0.49% | 0% |  |  | 0.49% | 0% | TRUE |  |  | 0.49% | 0%
COLVIL_7_PL1X2 | Hydro | 2023 | summer | 32873 | 833.1737 | 0 | 765 | 246.86 | 188847.9 | 0 | Individual | 0.4412% | 0% |  |  | 0.4412% | 0% | TRUE |  |  | 0.4412% | 0%
COLVIL_7_PL1X2 | Hydro | 2024 | nonsummer | 32873 | 36395.3033 | 0 | 1065 | 246.86 | 262905.9 | 0 | Individual | 13.84% | 0% |  |  | 13.84% | 0% | TRUE |  |  | 13.84% | 0%
COLVIL_7_PL1X2 | Hydro | 2024 | summer | 32873 | 3010.7127 | 0 | 765 | 246.86 | 188847.9 | 0 | Individual | 1.594% | 0% |  |  | 1.594% | 0% | TRUE |  |  | 1.594% | 0%
CONTRL_1_POOLE | Hydro | 2022 | nonsummer | 8767 | 8475.81 | 640.24 | 1060 | 11.07 | 11734.2 | 0 | Individual | 72.23% | 5.456% |  |  | 72.23% | 5.456% | TRUE |  |  | 72.23% | 5.456%
CONTRL_1_POOLE | Hydro | 2022 | summer | 8767 | 3865.9133 | 0 | 765 | 11.07 | 8468.55 | 0 | Individual | 45.65% | 0% |  |  | 45.65% | 0% | TRUE |  |  | 45.65% | 0%
CONTRL_1_POOLE | Hydro | 2023 | nonsummer | 8767 | 8367.735 | 0 | 1060 | 11.07 | 11734.2 | 0 | Individual | 71.31% | 0% |  |  | 71.31% | 0% | TRUE |  |  | 71.31% | 0%
CONTRL_1_POOLE | Hydro | 2023 | summer | 8767 | 781.6533 | 0 | 765 | 11.07 | 8468.55 | 0 | Individual | 9.23% | 0% |  |  | 9.23% | 0% | TRUE |  |  | 9.23% | 0%
CONTRL_1_POOLE | Hydro | 2024 | nonsummer | 8767 | 4975.97 | 0 | 1065 | 11.07 | 11789.55 | 0 | Individual | 42.21% | 0% |  |  | 42.21% | 0% | TRUE |  |  | 42.21% | 0%
CONTRL_1_POOLE | Hydro | 2024 | summer | 8767 | 380.59 | 0 | 765 | 11.07 | 8468.55 | 0 | Individual | 4.494% | 0% |  |  | 4.494% | 0% | TRUE |  |  | 4.494% | 0%
CONTRL_1_RUSHCK | Hydro | 2022 | nonsummer | 5845 | 5816.4 | 1063.9 | 1060 | 12.19 | 12921.4 | 0 | Individual | 45.01% | 8.234% |  |  | 45.01% | 8.234% | TRUE |  |  | 45.01% | 8.234%
CONTRL_1_RUSHCK | Hydro | 2022 | summer | 5845 | 2221.62 | 0 | 765 | 12.19 | 9325.35 | 0 | Individual | 23.82% | 0% |  |  | 23.82% | 0% | TRUE |  |  | 23.82% | 0%
CONTRL_1_RUSHCK | Hydro | 2023 | nonsummer | 5845 | 9331.48 | 0 | 1060 | 12.19 | 12921.4 | 0 | Individual | 72.22% | 0% |  |  | 72.22% | 0% | TRUE |  |  | 72.22% | 0%
CONTRL_1_RUSHCK | Hydro | 2023 | summer | 5845 | 1618.89 | 0 | 765 | 12.19 | 9325.35 | 0 | Individual | 17.36% | 0% |  |  | 17.36% | 0% | TRUE |  |  | 17.36% | 0%
CONTRL_1_RUSHCK | Hydro | 2024 | nonsummer | 5845 | 3379.9 | 0 | 1065 | 12.19 | 12982.35 | 0 | Individual | 26.03% | 0% |  |  | 26.03% | 0% | TRUE |  |  | 26.03% | 0%
CONTRL_1_RUSHCK | Hydro | 2024 | summer | 5845 | 120.9 | 0 | 765 | 12.19 | 9325.35 | 0 | Individual | 1.296% | 0% |  |  | 1.296% | 0% | TRUE |  |  | 1.296% | 0%
COVERD_2_QFUNTS | Hydro | 2022 | nonsummer | 31782 | 0 | 0 | 1060 | 5.5 | 5830 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
COVERD_2_QFUNTS | Hydro | 2022 | summer | 31782 | 62.8833 | 0 | 765 | 5.5 | 4207.5 | 0 | Individual | 1.495% | 0% |  |  | 1.495% | 0% | TRUE |  |  | 1.495% | 0%
COVERD_2_QFUNTS | Hydro | 2023 | nonsummer | 31782 | 0 | 0 | 1060 | 5.5 | 5830 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
COVERD_2_QFUNTS | Hydro | 2023 | summer | 31782 | 93.8667 | 0 | 765 | 5.5 | 4207.5 | 0 | Individual | 2.231% | 0% |  |  | 2.231% | 0% | TRUE |  |  | 2.231% | 0%
COVERD_2_QFUNTS | Hydro | 2024 | nonsummer | 31782 | 22.5 | 0 | 1065 | 5.5 | 5857.5 | 0 | Individual | 0.3841% | 0% |  |  | 0.3841% | 0% | TRUE |  |  | 0.3841% | 0%
COVERD_2_QFUNTS | Hydro | 2024 | summer | 31782 | 29.975 | 0 | 765 | 5.5 | 4207.5 | 0 | Individual | 0.7124% | 0% |  |  | 0.7124% | 0% | TRUE |  |  | 0.7124% | 0%
CRESTA_7_PL1X2 | Hydro | 2022 | nonsummer | 17899 | 20488.2453 | 0 | 1060 | 70.4 | 74624 | 0 | Individual | 27.46% | 0% |  |  | 27.46% | 0% | TRUE |  |  | 27.46% | 0%
CRESTA_7_PL1X2 | Hydro | 2022 | summer | 17899 | 20014.7708 | 0 | 765 | 70.4 | 53856 | 0 | Individual | 37.16% | 0% |  |  | 37.16% | 0% | TRUE |  |  | 37.16% | 0%
CRESTA_7_PL1X2 | Hydro | 2023 | nonsummer | 17899 | 3149.3333 | 0 | 1060 | 70.4 | 74624 | 0 | Individual | 4.22% | 0% |  |  | 4.22% | 0% | TRUE |  |  | 4.22% | 0%
CRESTA_7_PL1X2 | Hydro | 2023 | summer | 17899 | 18113.5217 | 0 | 765 | 70.4 | 53856 | 0 | Individual | 33.63% | 0% |  |  | 33.63% | 0% | TRUE |  |  | 33.63% | 0%
CRESTA_7_PL1X2 | Hydro | 2024 | nonsummer | 17899 | 8037.2983 | 0 | 1065 | 70.4 | 74976 | 0 | Individual | 10.72% | 0% |  |  | 10.72% | 0% | TRUE |  |  | 10.72% | 0%
CRESTA_7_PL1X2 | Hydro | 2024 | summer | 17899 | 28553.8668 | 0 | 765 | 70.4 | 53856 | 0 | Individual | 53.02% | 0% |  |  | 53.02% | 0% | TRUE |  |  | 53.02% | 0%
DONNLS_7_UNIT | Hydro | 2022 | nonsummer | 20821 | 1145 | 0 | 1060 | 72 | 76320 | 0 | Individual | 1.5% | 0% |  |  | 1.5% | 0% | TRUE |  |  | 1.5% | 0%
DONNLS_7_UNIT | Hydro | 2022 | summer | 20821 | 0 | 0 | 765 | 72 | 55080 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
DONNLS_7_UNIT | Hydro | 2023 | nonsummer | 20821 | 2984.2 | 0 | 1060 | 72 | 76320 | 0 | Individual | 3.91% | 0% |  |  | 3.91% | 0% | TRUE |  |  | 3.91% | 0%
DONNLS_7_UNIT | Hydro | 2023 | summer | 20821 | 2442.5 | 0 | 765 | 72 | 55080 | 0 | Individual | 4.434% | 0% |  |  | 4.434% | 0% | TRUE |  |  | 4.434% | 0%
DONNLS_7_UNIT | Hydro | 2024 | nonsummer | 20821 | 2677.0667 | 0 | 1065 | 72 | 76680 | 0 | Individual | 3.491% | 0% |  |  | 3.491% | 0% | TRUE |  |  | 3.491% | 0%
DONNLS_7_UNIT | Hydro | 2024 | summer | 20821 | 1173.95 | 0 | 765 | 72 | 55080 | 0 | Individual | 2.131% | 0% |  |  | 2.131% | 0% | TRUE |  |  | 2.131% | 0%
DRUM_7_PL1X2 | Hydro | 2022 | nonsummer | 4750 | 7713.7167 | 0 | 1060 | 26 | 27560 | 0 | Individual | 27.99% | 0% |  |  | 27.99% | 0% | TRUE |  |  | 27.99% | 0%
DRUM_7_PL1X2 | Hydro | 2022 | summer | 4750 | 6006 | 0 | 765 | 26 | 19890 | 0 | Individual | 30.2% | 0% |  |  | 30.2% | 0% | TRUE |  |  | 30.2% | 0%
DRUM_7_PL1X2 | Hydro | 2023 | nonsummer | 4750 | 2319.6 | 0 | 1060 | 26 | 27560 | 0 | Individual | 8.417% | 0% |  |  | 8.417% | 0% | TRUE |  |  | 8.417% | 0%
DRUM_7_PL1X2 | Hydro | 2023 | summer | 4750 | 2094.6 | 0 | 765 | 26 | 19890 | 0 | Individual | 10.53% | 0% |  |  | 10.53% | 0% | TRUE |  |  | 10.53% | 0%
DRUM_7_PL1X2 | Hydro | 2024 | nonsummer | 4750 | 17507.1 | 0 | 1065 | 26 | 27690 | 0 | Individual | 63.23% | 0% |  |  | 63.23% | 0% | TRUE |  |  | 63.23% | 0%
DRUM_7_PL1X2 | Hydro | 2024 | summer | 4750 | 11729.4167 | 0 | 765 | 26 | 19890 | 0 | Individual | 58.97% | 0% |  |  | 58.97% | 0% | TRUE |  |  | 58.97% | 0%
DRUM_7_PL3X4 | Hydro | 2022 | nonsummer | 8037 | 15613.8333 | 0 | 1060 | 28.9 | 30634 | 0 | Individual | 50.97% | 0% |  |  | 50.97% | 0% | TRUE |  |  | 50.97% | 0%
DRUM_7_PL3X4 | Hydro | 2022 | summer | 8037 | 7851.45 | 0 | 765 | 28.9 | 22108.5 | 0 | Individual | 35.51% | 0% |  |  | 35.51% | 0% | TRUE |  |  | 35.51% | 0%
DRUM_7_PL3X4 | Hydro | 2023 | nonsummer | 8037 | 10106.435 | 0 | 1060 | 28.9 | 30634 | 0 | Individual | 32.99% | 0% |  |  | 32.99% | 0% | TRUE |  |  | 32.99% | 0%
DRUM_7_PL3X4 | Hydro | 2023 | summer | 8037 | 7815.8333 | 0 | 765 | 28.9 | 22108.5 | 0 | Individual | 35.35% | 0% |  |  | 35.35% | 0% | TRUE |  |  | 35.35% | 0%
DRUM_7_PL3X4 | Hydro | 2024 | nonsummer | 8037 | 19351.0333 | 0 | 1065 | 28.9 | 30778.5 | 0 | Individual | 62.87% | 0% |  |  | 62.87% | 0% | TRUE |  |  | 62.87% | 0%
DRUM_7_PL3X4 | Hydro | 2024 | summer | 8037 | 13225.18 | 0 | 765 | 28.9 | 22108.5 | 0 | Individual | 59.82% | 0% |  |  | 59.82% | 0% | TRUE |  |  | 59.82% | 0%
DRUM_7_UNIT 5 | Hydro | 2022 | nonsummer | 23743 | 5717.38 | 0 | 1060 | 50 | 53000 | 0 | Individual | 10.79% | 0% |  |  | 10.79% | 0% | TRUE |  |  | 10.79% | 0%
DRUM_7_UNIT 5 | Hydro | 2022 | summer | 23743 | 1053.3667 | 0 | 765 | 50 | 38250 | 0 | Individual | 2.754% | 0% |  |  | 2.754% | 0% | TRUE |  |  | 2.754% | 0%
DRUM_7_UNIT 5 | Hydro | 2023 | nonsummer | 23743 | 1779 | 0 | 1060 | 50 | 53000 | 0 | Individual | 3.357% | 0% |  |  | 3.357% | 0% | TRUE |  |  | 3.357% | 0%
DRUM_7_UNIT 5 | Hydro | 2023 | summer | 23743 | 2007.5 | 0 | 765 | 50 | 38250 | 0 | Individual | 5.248% | 0% |  |  | 5.248% | 0% | TRUE |  |  | 5.248% | 0%
DRUM_7_UNIT 5 | Hydro | 2024 | nonsummer | 23743 | 23633.8333 | 0 | 1065 | 50 | 53250 | 0 | Individual | 44.38% | 0% |  |  | 44.38% | 0% | TRUE |  |  | 44.38% | 0%
DRUM_7_UNIT 5 | Hydro | 2024 | summer | 23743 | 14271.4 | 0 | 765 | 50 | 38250 | 0 | Individual | 37.31% | 0% |  |  | 37.31% | 0% | TRUE |  |  | 37.31% | 0%
DUTCH1_7_UNIT 1 | Hydro | 2022 | nonsummer | 15707 | 2193.1567 | 0 | 1060 | 22 | 23320 | 0 | Individual | 9.405% | 0% |  |  | 9.405% | 0% | TRUE |  |  | 9.405% | 0%
DUTCH1_7_UNIT 1 | Hydro | 2022 | summer | 15707 | 3410.6333 | 0 | 765 | 22 | 16830 | 0 | Individual | 20.27% | 0% |  |  | 20.27% | 0% | TRUE |  |  | 20.27% | 0%
DUTCH1_7_UNIT 1 | Hydro | 2023 | nonsummer | 15707 | 1864.17 | 0 | 1060 | 22 | 23320 | 0 | Individual | 7.994% | 0% |  |  | 7.994% | 0% | TRUE |  |  | 7.994% | 0%
DUTCH1_7_UNIT 1 | Hydro | 2023 | summer | 15707 | 3427.4667 | 0 | 765 | 22 | 16830 | 0 | Individual | 20.37% | 0% |  |  | 20.37% | 0% | TRUE |  |  | 20.37% | 0%
DUTCH1_7_UNIT 1 | Hydro | 2024 | nonsummer | 15707 | 7225.2333 | 0 | 1065 | 22 | 23430 | 0 | Individual | 30.84% | 0% |  |  | 30.84% | 0% | TRUE |  |  | 30.84% | 0%
DUTCH1_7_UNIT 1 | Hydro | 2024 | summer | 15707 | 7490.2483 | 0 | 765 | 22 | 16830 | 0 | Individual | 44.51% | 0% |  |  | 44.51% | 0% | TRUE |  |  | 44.51% | 0%
DUTCH2_7_UNIT 1 | Hydro | 2022 | nonsummer | 23743 | 13723.1167 | 0 | 1060 | 26 | 27560 | 0 | Individual | 49.79% | 0% |  |  | 49.79% | 0% | TRUE |  |  | 49.79% | 0%
DUTCH2_7_UNIT 1 | Hydro | 2022 | summer | 23743 | 9033.5 | 0 | 765 | 26 | 19890 | 0 | Individual | 45.42% | 0% |  |  | 45.42% | 0% | TRUE |  |  | 45.42% | 0%
DUTCH2_7_UNIT 1 | Hydro | 2023 | nonsummer | 23743 | 10889.9667 | 84.0667 | 1060 | 26 | 27560 | 0 | Individual | 39.51% | 0.305% |  |  | 39.51% | 0.305% | TRUE |  |  | 39.51% | 0.305%
DUTCH2_7_UNIT 1 | Hydro | 2023 | summer | 23743 | 6314.1 | 0 | 765 | 26 | 19890 | 0 | Individual | 31.75% | 0% |  |  | 31.75% | 0% | TRUE |  |  | 31.75% | 0%
DUTCH2_7_UNIT 1 | Hydro | 2024 | nonsummer | 23743 | 18324.9 | 0 | 1065 | 26 | 27690 | 0 | Individual | 66.18% | 0% |  |  | 66.18% | 0% | TRUE |  |  | 66.18% | 0%
DUTCH2_7_UNIT 1 | Hydro | 2024 | summer | 23743 | 11010.5667 | 0 | 765 | 26 | 19890 | 0 | Individual | 55.36% | 0% |  |  | 55.36% | 0% | TRUE |  |  | 55.36% | 0%
DVLCYN_1_UNITS | Hydro | 2022 | nonsummer | 26299 | 6446.3333 | 0 | 1060 | 235 | 249100 | 0 | Individual | 2.588% | 0% |  |  | 2.588% | 0% | TRUE |  |  | 2.588% | 0%
DVLCYN_1_UNITS | Hydro | 2022 | summer | 26299 | 1326 | 0 | 765 | 235 | 179775 | 0 | Individual | 0.7376% | 0% |  |  | 0.7376% | 0% | TRUE |  |  | 0.7376% | 0%
DVLCYN_1_UNITS | Hydro | 2023 | nonsummer | 26299 | 2925.8167 | 0 | 1060 | 235 | 249100 | 0 | Individual | 1.175% | 0% |  |  | 1.175% | 0% | TRUE |  |  | 1.175% | 0%
DVLCYN_1_UNITS | Hydro | 2023 | summer | 26299 | 1866.3333 | 0 | 765 | 235 | 179775 | 0 | Individual | 1.038% | 0% |  |  | 1.038% | 0% | TRUE |  |  | 1.038% | 0%
DVLCYN_1_UNITS | Hydro | 2024 | nonsummer | 26299 | 7890.1333 | 0 | 1065 | 235 | 250275 | 0 | Individual | 3.153% | 0% |  |  | 3.153% | 0% | TRUE |  |  | 3.153% | 0%
DVLCYN_1_UNITS | Hydro | 2024 | summer | 26299 | 5349.5 | 0 | 765 | 235 | 179775 | 0 | Individual | 2.976% | 0% |  |  | 2.976% | 0% | TRUE |  |  | 2.976% | 0%
ELECTR_7_PL1X3 | Hydro | 2022 | nonsummer | 17533 | 9466.71 | 0 | 1060 | 93 | 98580 | 0 | Individual | 9.603% | 0% |  |  | 9.603% | 0% | TRUE |  |  | 9.603% | 0%
ELECTR_7_PL1X3 | Hydro | 2022 | summer | 17533 | 1160.32 | 0 | 765 | 93 | 71145 | 0 | Individual | 1.631% | 0% |  |  | 1.631% | 0% | TRUE |  |  | 1.631% | 0%
ELECTR_7_PL1X3 | Hydro | 2023 | nonsummer | 17533 | 16624.9183 | 0 | 1060 | 93 | 98580 | 0 | Individual | 16.86% | 0% |  |  | 16.86% | 0% | TRUE |  |  | 16.86% | 0%
ELECTR_7_PL1X3 | Hydro | 2023 | summer | 17533 | 1617.3 | 0 | 765 | 93 | 71145 | 0 | Individual | 2.273% | 0% |  |  | 2.273% | 0% | TRUE |  |  | 2.273% | 0%
ELECTR_7_PL1X3 | Hydro | 2024 | nonsummer | 17533 | 6943.7867 | 0 | 1065 | 93 | 99045 | 0 | Individual | 7.011% | 0% |  |  | 7.011% | 0% | TRUE |  |  | 7.011% | 0%
ELECTR_7_PL1X3 | Hydro | 2024 | summer | 17533 | 8665.8667 | 0 | 765 | 93 | 71145 | 0 | Individual | 12.18% | 0% |  |  | 12.18% | 0% | TRUE |  |  | 12.18% | 0%
ELKCRK_6_STONYG | Hydro | 2022 | nonsummer | 31413 | 3091.9 | 0 | 1060 | 4.9 | 5194 | 0 | Individual | 59.53% | 0% |  |  | 59.53% | 0% | TRUE |  |  | 59.53% | 0%
ELKCRK_6_STONYG | Hydro | 2022 | summer | 31413 | 2211.4517 | 0 | 765 | 4.9 | 3748.5 | 0 | Individual | 59% | 0% |  |  | 59% | 0% | TRUE |  |  | 59% | 0%
ELKCRK_6_STONYG | Hydro | 2023 | nonsummer | 31413 | 1419.5367 | 0 | 1060 | 4.9 | 5194 | 0 | Individual | 27.33% | 0% |  |  | 27.33% | 0% | TRUE |  |  | 27.33% | 0%
ELKCRK_6_STONYG | Hydro | 2023 | summer | 31413 | 2376.5 | 0 | 765 | 4.9 | 3748.5 | 0 | Individual | 63.4% | 0% |  |  | 63.4% | 0% | TRUE |  |  | 63.4% | 0%
ELKCRK_6_STONYG | Hydro | 2024 | nonsummer | 31413 | 640.5983 | 0 | 1065 | 4.9 | 5218.5 | 0 | Individual | 12.28% | 0% |  |  | 12.28% | 0% | TRUE |  |  | 12.28% | 0%
ELKCRK_6_STONYG | Hydro | 2024 | summer | 31413 | 3091.9 | 0 | 765 | 4.9 | 3748.5 | 0 | Individual | 82.48% | 0% |  |  | 82.48% | 0% | TRUE |  |  | 82.48% | 0%
EXCHEC_7_UNIT 1 | Hydro | 2022 | nonsummer | 24473 | 29240.95 | 0 | 1060 | 94.5 | 100170 | 0 | Individual | 29.19% | 0% |  |  | 29.19% | 0% | TRUE |  |  | 29.19% | 0%
EXCHEC_7_UNIT 1 | Hydro | 2022 | summer | 24473 | 23197 | 0 | 765 | 94.5 | 72292.5 | 0 | Individual | 32.09% | 0% |  |  | 32.09% | 0% | TRUE |  |  | 32.09% | 0%
EXCHEC_7_UNIT 1 | Hydro | 2023 | nonsummer | 24473 | 11494.3 | 0 | 1060 | 94.5 | 100170 | 0 | Individual | 11.47% | 0% |  |  | 11.47% | 0% | TRUE |  |  | 11.47% | 0%
EXCHEC_7_UNIT 1 | Hydro | 2023 | summer | 24473 | 19912 | 0 | 765 | 94.5 | 72292.5 | 0 | Individual | 27.54% | 0% |  |  | 27.54% | 0% | TRUE |  |  | 27.54% | 0%
EXCHEC_7_UNIT 1 | Hydro | 2024 | nonsummer | 24473 | 0 | 0 | 1065 | 94.5 | 100642.5 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
EXCHEC_7_UNIT 1 | Hydro | 2024 | summer | 24473 | 86.625 | 23.625 | 765 | 94.5 | 72292.5 | 0 | Individual | 0.1198% | 0.03268% |  |  | 0.1198% | 0.03268% | TRUE |  |  | 0.1198% | 0.03268%
FMEADO_7_UNIT | Hydro | 2022 | nonsummer | 24108 | 59.2 | 0 | 1060 | 16 | 16960 | 0 | Individual | 0.3491% | 0% |  |  | 0.3491% | 0% | TRUE |  |  | 0.3491% | 0%
FMEADO_7_UNIT | Hydro | 2022 | summer | 24108 | 0 | 0 | 765 | 16 | 12240 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
FMEADO_7_UNIT | Hydro | 2023 | nonsummer | 24108 | 1206.3 | 0 | 1060 | 16 | 16960 | 0 | Individual | 7.113% | 0% |  |  | 7.113% | 0% | TRUE |  |  | 7.113% | 0%
FMEADO_7_UNIT | Hydro | 2023 | summer | 24108 | 1094.4 | 0 | 765 | 16 | 12240 | 0 | Individual | 8.941% | 0% |  |  | 8.941% | 0% | TRUE |  |  | 8.941% | 0%
FMEADO_7_UNIT | Hydro | 2024 | nonsummer | 24108 | 1732.8 | 0 | 1065 | 16 | 17040 | 0 | Individual | 10.17% | 0% |  |  | 10.17% | 0% | TRUE |  |  | 10.17% | 0%
FMEADO_7_UNIT | Hydro | 2024 | summer | 24108 | 100 | 0 | 765 | 16 | 12240 | 0 | Individual | 0.817% | 0% |  |  | 0.817% | 0% | TRUE |  |  | 0.817% | 0%
FORBST_7_UNIT 1 | Hydro | 2022 | nonsummer | 23012 | 0 | 0 | 1060 | 37.5 | 39750 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
FORBST_7_UNIT 1 | Hydro | 2022 | summer | 23012 | 32.75 | 0 | 765 | 37.5 | 28687.5 | 0 | Individual | 0.1142% | 0% |  |  | 0.1142% | 0% | TRUE |  |  | 0.1142% | 0%
FORBST_7_UNIT 1 | Hydro | 2023 | nonsummer | 23012 | 2716.8667 | 0 | 1060 | 37.5 | 39750 | 0 | Individual | 6.835% | 0% |  |  | 6.835% | 0% | TRUE |  |  | 6.835% | 0%
FORBST_7_UNIT 1 | Hydro | 2023 | summer | 23012 | 100.6667 | 0 | 765 | 37.5 | 28687.5 | 0 | Individual | 0.3509% | 0% |  |  | 0.3509% | 0% | TRUE |  |  | 0.3509% | 0%
FORBST_7_UNIT 1 | Hydro | 2024 | nonsummer | 23012 | 187.5 | 0 | 1065 | 37.5 | 39937.5 | 0 | Individual | 0.4695% | 0% |  |  | 0.4695% | 0% | TRUE |  |  | 0.4695% | 0%
FORBST_7_UNIT 1 | Hydro | 2024 | summer | 23012 | 96.875 | 0 | 765 | 37.5 | 28687.5 | 0 | Individual | 0.3377% | 0% |  |  | 0.3377% | 0% | TRUE |  |  | 0.3377% | 0%
GRIZLY_1_UNIT 1 | Hydro | 2022 | nonsummer | 33970 | 0 | 0 | 1060 | 20 | 21200 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
GRIZLY_1_UNIT 1 | Hydro | 2022 | summer | 33970 | 0 | 0 | 765 | 20 | 15300 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
GRIZLY_1_UNIT 1 | Hydro | 2023 | nonsummer | 33970 | 3 | 0 | 1060 | 20 | 21200 | 0 | Individual | 0.01415% | 0% |  |  | 0.01415% | 0% | TRUE |  |  | 0.01415% | 0%
GRIZLY_1_UNIT 1 | Hydro | 2023 | summer | 33970 | 0 | 0 | 765 | 20 | 15300 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
GRIZLY_1_UNIT 1 | Hydro | 2024 | nonsummer | 33970 | 4510.01 | 0 | 1065 | 20 | 21300 | 0 | Individual | 21.17% | 0% |  |  | 21.17% | 0% | TRUE |  |  | 21.17% | 0%
GRIZLY_1_UNIT 1 | Hydro | 2024 | summer | 33970 | 237.5 | 0 | 765 | 20 | 15300 | 0 | Individual | 1.552% | 0% |  |  | 1.552% | 0% | TRUE |  |  | 1.552% | 0%
HAASPH_7_PL1X2 | Hydro | 2022 | nonsummer | 21186 | 14400 | 0 | 1060 | 144 | 152640 | 0 | Individual | 9.434% | 0% |  |  | 9.434% | 0% | TRUE |  |  | 9.434% | 0%
HAASPH_7_PL1X2 | Hydro | 2022 | summer | 21186 | 459.7 | 0 | 765 | 144 | 110160 | 0 | Individual | 0.4173% | 0% |  |  | 0.4173% | 0% | TRUE |  |  | 0.4173% | 0%
HAASPH_7_PL1X2 | Hydro | 2023 | nonsummer | 21186 | 3545.7167 | 0 | 1060 | 144 | 152640 | 0 | Individual | 2.323% | 0% |  |  | 2.323% | 0% | TRUE |  |  | 2.323% | 0%
HAASPH_7_PL1X2 | Hydro | 2023 | summer | 21186 | 7306.1333 | 0 | 765 | 144 | 110160 | 0 | Individual | 6.632% | 0% |  |  | 6.632% | 0% | TRUE |  |  | 6.632% | 0%
HAASPH_7_PL1X2 | Hydro | 2024 | nonsummer | 21186 | 4054.2333 | 0 | 1065 | 144 | 153360 | 0 | Individual | 2.644% | 0% |  |  | 2.644% | 0% | TRUE |  |  | 2.644% | 0%
HAASPH_7_PL1X2 | Hydro | 2024 | summer | 21186 | 3678.4 | 0 | 765 | 144 | 110160 | 0 | Individual | 3.339% | 0% |  |  | 3.339% | 0% | TRUE |  |  | 3.339% | 0%
HALSEY_6_UNIT | Hydro | 2022 | nonsummer | 5845 | 2355.008 | 0 | 1060 | 13.5 | 14310 | 0 | Individual | 16.46% | 0% |  |  | 16.46% | 0% | TRUE |  |  | 16.46% | 0%
HALSEY_6_UNIT | Hydro | 2022 | summer | 5845 | 0 | 0 | 765 | 13.5 | 10327.5 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
HALSEY_6_UNIT | Hydro | 2023 | nonsummer | 5845 | 0 | 0 | 1060 | 13.5 | 14310 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
HALSEY_6_UNIT | Hydro | 2023 | summer | 5845 | 0 | 0 | 765 | 13.5 | 10327.5 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
HALSEY_6_UNIT | Hydro | 2024 | nonsummer | 5845 | 0 | 0 | 1065 | 13.5 | 14377.5 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
HALSEY_6_UNIT | Hydro | 2024 | summer | 5845 | 1651.325 | 0 | 765 | 13.5 | 10327.5 | 0 | Individual | 15.99% | 0% |  |  | 15.99% | 0% | TRUE |  |  | 15.99% | 0%
HYTTHM_2_UNITS | Hydro | 2022 | nonsummer | 24838 | 83847.7667 | 0 | 1060 | 933.1 | 989086 | 0 | Individual | 8.477% | 0% |  |  | 8.477% | 0% | TRUE |  |  | 8.477% | 0%
HYTTHM_2_UNITS | Hydro | 2022 | summer | 24838 | 124585.4967 | 0 | 765 | 933.1 | 713821.5 | 0 | Individual | 17.45% | 0% |  |  | 17.45% | 0% | TRUE |  |  | 17.45% | 0%
HYTTHM_2_UNITS | Hydro | 2023 | nonsummer | 24838 | 113068.4617 | 0 | 1060 | 933.1 | 989086 | 0 | Individual | 11.43% | 0% |  |  | 11.43% | 0% | TRUE |  |  | 11.43% | 0%
HYTTHM_2_UNITS | Hydro | 2023 | summer | 24838 | 97002.6367 | 0 | 765 | 933.1 | 713821.5 | 0 | Individual | 13.59% | 0% |  |  | 13.59% | 0% | TRUE |  |  | 13.59% | 0%
HYTTHM_2_UNITS | Hydro | 2024 | nonsummer | 24838 | 115852.3467 | 0 | 1065 | 933.1 | 993751.5 | 0 | Individual | 11.66% | 0% |  |  | 11.66% | 0% | TRUE |  |  | 11.66% | 0%
HYTTHM_2_UNITS | Hydro | 2024 | summer | 24838 | 56346.685 | 0 | 765 | 933.1 | 713821.5 | 0 | Individual | 7.894% | 0% |  |  | 7.894% | 0% | TRUE |  |  | 7.894% | 0%
INTKEP_2_UNITS | Hydro | 2022 | nonsummer | 38899 | 47416.5833 | 0 | 1060 | 405 | 429300 | 0 | Individual | 11.05% | 0% |  |  | 11.05% | 0% | TRUE |  |  | 11.05% | 0%
INTKEP_2_UNITS | Hydro | 2022 | summer | 38899 | 64609.2833 | 0 | 765 | 405 | 309825 | 0 | Individual | 20.85% | 0% |  |  | 20.85% | 0% | TRUE |  |  | 20.85% | 0%
INTKEP_2_UNITS | Hydro | 2023 | nonsummer | 38899 | 127791.2667 | 0 | 1060 | 405 | 429300 | 0 | Individual | 29.77% | 0% |  |  | 29.77% | 0% | TRUE |  |  | 29.77% | 0%
INTKEP_2_UNITS | Hydro | 2023 | summer | 38899 | 47146.6 | 0 | 765 | 405 | 309825 | 0 | Individual | 15.22% | 0% |  |  | 15.22% | 0% | TRUE |  |  | 15.22% | 0%
INTKEP_2_UNITS | Hydro | 2024 | nonsummer | 38899 | 142855.9333 | 0 | 1065 | 405 | 431325 | 0 | Individual | 33.12% | 0% |  |  | 33.12% | 0% | TRUE |  |  | 33.12% | 0%
INTKEP_2_UNITS | Hydro | 2024 | summer | 38899 | 31739.25 | 0 | 765 | 405 | 309825 | 0 | Individual | 10.24% | 0% |  |  | 10.24% | 0% | TRUE |  |  | 10.24% | 0%
KELYRG_6_UNIT | Hydro | 2022 | nonsummer | 23012 | 6.125 | 0 | 1060 | 11 | 11660 | 0 | Individual | 0.05253% | 0% |  |  | 0.05253% | 0% | TRUE |  |  | 0.05253% | 0%
KELYRG_6_UNIT | Hydro | 2022 | summer | 23012 | 165 | 0 | 765 | 11 | 8415 | 0 | Individual | 1.961% | 0% |  |  | 1.961% | 0% | TRUE |  |  | 1.961% | 0%
KELYRG_6_UNIT | Hydro | 2023 | nonsummer | 23012 | 1309.22 | 0 | 1060 | 11 | 11660 | 0 | Individual | 11.23% | 0% |  |  | 11.23% | 0% | TRUE |  |  | 11.23% | 0%
KELYRG_6_UNIT | Hydro | 2023 | summer | 23012 | 0 | 0 | 765 | 11 | 8415 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
KELYRG_6_UNIT | Hydro | 2024 | nonsummer | 23012 | 0 | 0 | 1065 | 11 | 11715 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
KELYRG_6_UNIT | Hydro | 2024 | summer | 23012 | 198 | 0 | 765 | 11 | 8415 | 0 | Individual | 2.353% | 0% |  |  | 2.353% | 0% | TRUE |  |  | 2.353% | 0%
KERKH2_7_UNIT 1 | Hydro | 2022 | nonsummer | 30317 | 21542.2807 | 0 | 1060 | 153.9 | 163134 | 0 | Individual | 13.21% | 0% |  |  | 13.21% | 0% | TRUE |  |  | 13.21% | 0%
KERKH2_7_UNIT 1 | Hydro | 2022 | summer | 30317 | 18744.0398 | 575.94 | 765 | 153.9 | 117733.5 | 0 | Individual | 15.92% | 0.4892% |  |  | 15.92% | 0.4892% | TRUE |  |  | 15.92% | 0.4892%
KERKH2_7_UNIT 1 | Hydro | 2023 | nonsummer | 30317 | 44565.0052 | 0 | 1060 | 153.9 | 163134 | 0 | Individual | 27.32% | 0% |  |  | 27.32% | 0% | TRUE |  |  | 27.32% | 0%
KERKH2_7_UNIT 1 | Hydro | 2023 | summer | 30317 | 8530.345 | 0 | 765 | 153.9 | 117733.5 | 0 | Individual | 7.245% | 0% |  |  | 7.245% | 0% | TRUE |  |  | 7.245% | 0%
KERKH2_7_UNIT 1 | Hydro | 2024 | nonsummer | 30317 | 22452.5542 | 554.8555 | 1065 | 153.9 | 163903.5 | 0 | Individual | 13.7% | 0.3385% |  |  | 13.7% | 0.3385% | TRUE |  |  | 13.7% | 0.3385%
KERKH2_7_UNIT 1 | Hydro | 2024 | summer | 30317 | 26682.583 | 1063.2367 | 765 | 153.9 | 117733.5 | 0 | Individual | 22.66% | 0.9031% |  |  | 22.66% | 0.9031% | TRUE |  |  | 22.66% | 0.9031%
KINGRV_7_UNIT 1 | Hydro | 2022 | nonsummer | 22647 | 3314.9583 | 0 | 1060 | 51.2 | 54272 | 0 | Individual | 6.108% | 0% |  |  | 6.108% | 0% | TRUE |  |  | 6.108% | 0%
KINGRV_7_UNIT 1 | Hydro | 2022 | summer | 22647 | 374.6917 | 0 | 765 | 51.2 | 39168 | 0 | Individual | 0.9566% | 0% |  |  | 0.9566% | 0% | TRUE |  |  | 0.9566% | 0%
KINGRV_7_UNIT 1 | Hydro | 2023 | nonsummer | 22647 | 2883.9833 | 0 | 1060 | 51.2 | 54272 | 0 | Individual | 5.314% | 0% |  |  | 5.314% | 0% | TRUE |  |  | 5.314% | 0%
KINGRV_7_UNIT 1 | Hydro | 2023 | summer | 22647 | 1568.9667 | 0 | 765 | 51.2 | 39168 | 0 | Individual | 4.006% | 0% |  |  | 4.006% | 0% | TRUE |  |  | 4.006% | 0%
KINGRV_7_UNIT 1 | Hydro | 2024 | nonsummer | 22647 | 2174.4133 | 17.2667 | 1065 | 51.2 | 54528 | 0 | Individual | 3.988% | 0.03167% |  |  | 3.988% | 0.03167% | TRUE |  |  | 3.988% | 0.03167%
KINGRV_7_UNIT 1 | Hydro | 2024 | summer | 22647 | 3526.87 | 0 | 765 | 51.2 | 39168 | 0 | Individual | 9.004% | 0% |  |  | 9.004% | 0% | TRUE |  |  | 9.004% | 0%
MCSWAN_6_UNITS | Hydro | 2022 | nonsummer | 24473 | 4936.35 | 0 | 1060 | 9 | 9540 | 0 | Individual | 51.74% | 0% |  |  | 51.74% | 0% | TRUE |  |  | 51.74% | 0%
MCSWAN_6_UNITS | Hydro | 2022 | summer | 24473 | 0 | 0 | 765 | 9 | 6885 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
MCSWAN_6_UNITS | Hydro | 2023 | nonsummer | 24473 | 180 | 0 | 1060 | 9 | 9540 | 0 | Individual | 1.887% | 0% |  |  | 1.887% | 0% | TRUE |  |  | 1.887% | 0%
MCSWAN_6_UNITS | Hydro | 2023 | summer | 24473 | 0 | 0 | 765 | 9 | 6885 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
MCSWAN_6_UNITS | Hydro | 2024 | nonsummer | 24473 | 21.6 | 0 | 1065 | 9 | 9585 | 0 | Individual | 0.2254% | 0% |  |  | 0.2254% | 0% | TRUE |  |  | 0.2254% | 0%
MCSWAN_6_UNITS | Hydro | 2024 | summer | 24473 | 4.05 | 0 | 765 | 9 | 6885 | 0 | Individual | 0.05882% | 0% |  |  | 0.05882% | 0% | TRUE |  |  | 0.05882% | 0%
MDFKRL_2_PROJCT | Hydro | 2022 | nonsummer | 24108 | 13911.7667 | 0 | 1060 | 210 | 222600 | 0 | Individual | 6.25% | 0% |  |  | 6.25% | 0% | TRUE |  |  | 6.25% | 0%
MDFKRL_2_PROJCT | Hydro | 2022 | summer | 24108 | 16.3333 | 0 | 765 | 210 | 160650 | 0 | Individual | 0.01017% | 0% |  |  | 0.01017% | 0% | TRUE |  |  | 0.01017% | 0%
MDFKRL_2_PROJCT | Hydro | 2023 | nonsummer | 24108 | 26598.7833 | 0 | 1060 | 210 | 222600 | 0 | Individual | 11.95% | 0% |  |  | 11.95% | 0% | TRUE |  |  | 11.95% | 0%
MDFKRL_2_PROJCT | Hydro | 2023 | summer | 24108 | 765 | 0 | 765 | 210 | 160650 | 0 | Individual | 0.4762% | 0% |  |  | 0.4762% | 0% | TRUE |  |  | 0.4762% | 0%
MDFKRL_2_PROJCT | Hydro | 2024 | nonsummer | 24108 | 8102.3167 | 0 | 1065 | 210 | 223650 | 0 | Individual | 3.623% | 0% |  |  | 3.623% | 0% | TRUE |  |  | 3.623% | 0%
MDFKRL_2_PROJCT | Hydro | 2024 | summer | 24108 | 416.5 | 64.6667 | 765 | 210 | 160650 | 0 | Individual | 0.2593% | 0.04025% |  |  | 0.2593% | 0.04025% | TRUE |  |  | 0.2593% | 0.04025%
MERCFL_6_UNIT | Hydro | 2022 | nonsummer | 10959 | 983.5 | 0 | 1060 | 3.5 | 3710 | 0 | Individual | 26.51% | 0% |  |  | 26.51% | 0% | TRUE |  |  | 26.51% | 0%
MERCFL_6_UNIT | Hydro | 2022 | summer | 10959 | 12.1333 | 0 | 765 | 3.5 | 2677.5 | 0 | Individual | 0.4532% | 0% |  |  | 0.4532% | 0% | TRUE |  |  | 0.4532% | 0%
MERCFL_6_UNIT | Hydro | 2023 | nonsummer | 10959 | 820.0917 | 0 | 1060 | 3.5 | 3710 | 0 | Individual | 22.1% | 0% |  |  | 22.1% | 0% | TRUE |  |  | 22.1% | 0%
MERCFL_6_UNIT | Hydro | 2023 | summer | 10959 | 0 | 0 | 765 | 3.5 | 2677.5 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
MERCFL_6_UNIT | Hydro | 2024 | nonsummer | 10959 | 1050 | 0 | 1065 | 3.5 | 3727.5 | 0 | Individual | 28.17% | 0% |  |  | 28.17% | 0% | TRUE |  |  | 28.17% | 0%
MERCFL_6_UNIT | Hydro | 2024 | summer | 10959 | 0 | 0 | 765 | 3.5 | 2677.5 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
MIRLOM_7_MWDLKM | Hydro | 2022 | nonsummer | 29221 | 72.1667 | 0 | 1060 | 5 | 5300 | 0 | Individual | 1.362% | 0% |  |  | 1.362% | 0% | TRUE |  |  | 1.362% | 0%
MIRLOM_7_MWDLKM | Hydro | 2022 | summer | 29221 | 5 | 0 | 765 | 5 | 3825 | 0 | Individual | 0.1307% | 0% |  |  | 0.1307% | 0% | TRUE |  |  | 0.1307% | 0%
MIRLOM_7_MWDLKM | Hydro | 2023 | nonsummer | 29221 | 2727.8333 | 0 | 1060 | 5 | 5300 | 0 | Individual | 51.47% | 0% |  |  | 51.47% | 0% | TRUE |  |  | 51.47% | 0%
MIRLOM_7_MWDLKM | Hydro | 2023 | summer | 29221 | 1167.0833 | 0 | 765 | 5 | 3825 | 0 | Individual | 30.51% | 0% |  |  | 30.51% | 0% | TRUE |  |  | 30.51% | 0%
MIRLOM_7_MWDLKM | Hydro | 2024 | nonsummer | 29221 | 290.1667 | 0 | 1065 | 5 | 5325 | 0 | Individual | 5.449% | 0% |  |  | 5.449% | 0% | TRUE |  |  | 5.449% | 0%
MIRLOM_7_MWDLKM | Hydro | 2024 | summer | 29221 | 165.25 | 0 | 765 | 5 | 3825 | 0 | Individual | 4.32% | 0% |  |  | 4.32% | 0% | TRUE |  |  | 4.32% | 0%
MOJAVE_1_SIPHON | Hydro | 2022 | nonsummer | 35065 | 188.8567 | 0 | 1060 | 14.36 | 15221.6 | 0 | Individual | 1.241% | 0% |  |  | 1.241% | 0% | TRUE |  |  | 1.241% | 0%
MOJAVE_1_SIPHON | Hydro | 2022 | summer | 35065 | 0 | 0 | 765 | 14.36 | 10985.4 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
MOJAVE_1_SIPHON | Hydro | 2023 | nonsummer | 35065 | 275.2993 | 0 | 1060 | 14.36 | 15221.6 | 0 | Individual | 1.809% | 0% |  |  | 1.809% | 0% | TRUE |  |  | 1.809% | 0%
MOJAVE_1_SIPHON | Hydro | 2023 | summer | 35065 | 2519.7207 | 0 | 765 | 14.36 | 10985.4 | 0 | Individual | 22.94% | 0% |  |  | 22.94% | 0% | TRUE |  |  | 22.94% | 0%
MOJAVE_1_SIPHON | Hydro | 2024 | nonsummer | 35065 | 225.3827 | 0 | 1065 | 14.36 | 15293.4 | 0 | Individual | 1.474% | 0% |  |  | 1.474% | 0% | TRUE |  |  | 1.474% | 0%
MOJAVE_1_SIPHON | Hydro | 2024 | summer | 35065 | 457.6727 | 0 | 765 | 14.36 | 10985.4 | 0 | Individual | 4.166% | 0% |  |  | 4.166% | 0% | TRUE |  |  | 4.166% | 0%
NAROW1_2_UNIT | Hydro | 2022 | nonsummer | 44095 | 4869.41 | 0 | 1060 | 12 | 12720 | 0 | Individual | 38.28% | 0% |  |  | 38.28% | 0% | TRUE |  |  | 38.28% | 0%
NAROW1_2_UNIT | Hydro | 2022 | summer | 44095 | 1289.7167 | 0 | 765 | 12 | 9180 | 0 | Individual | 14.05% | 0% |  |  | 14.05% | 0% | TRUE |  |  | 14.05% | 0%
NAROW1_2_UNIT | Hydro | 2023 | nonsummer | 44095 | 3447.6383 | 0 | 1060 | 12 | 12720 | 0 | Individual | 27.1% | 0% |  |  | 27.1% | 0% | TRUE |  |  | 27.1% | 0%
NAROW1_2_UNIT | Hydro | 2023 | summer | 44095 | 1383.33 | 0 | 765 | 12 | 9180 | 0 | Individual | 15.07% | 0% |  |  | 15.07% | 0% | TRUE |  |  | 15.07% | 0%
NAROW1_2_UNIT | Hydro | 2024 | nonsummer | 44095 | 2872.5167 | 0 | 1065 | 12 | 12780 | 0 | Individual | 22.48% | 0% |  |  | 22.48% | 0% | TRUE |  |  | 22.48% | 0%
NAROW1_2_UNIT | Hydro | 2024 | summer | 44095 | 2162.75 | 0 | 765 | 12 | 9180 | 0 | Individual | 23.56% | 0% |  |  | 23.56% | 0% | TRUE |  |  | 23.56% | 0%
NAROW2_2_UNIT | Hydro | 2022 | nonsummer | 25204 | 53979.815 | 0 | 1060 | 55 | 58300 | 0 | Individual | 92.59% | 0% |  |  | 92.59% | 0% | TRUE |  |  | 92.59% | 0%
NAROW2_2_UNIT | Hydro | 2022 | summer | 25204 | 27342.76 | 0 | 765 | 55 | 42075 | 0 | Individual | 64.99% | 0% |  |  | 64.99% | 0% | TRUE |  |  | 64.99% | 0%
NAROW2_2_UNIT | Hydro | 2023 | nonsummer | 25204 | 22072.36 | 0 | 1060 | 55 | 58300 | 0 | Individual | 37.86% | 0% |  |  | 37.86% | 0% | TRUE |  |  | 37.86% | 0%
NAROW2_2_UNIT | Hydro | 2023 | summer | 25204 | 17913.66 | 0 | 765 | 55 | 42075 | 0 | Individual | 42.58% | 0% |  |  | 42.58% | 0% | TRUE |  |  | 42.58% | 0%
NAROW2_2_UNIT | Hydro | 2024 | nonsummer | 25204 | 29698.1917 | 0 | 1065 | 55 | 58575 | 0 | Individual | 50.7% | 0% |  |  | 50.7% | 0% | TRUE |  |  | 50.7% | 0%
NAROW2_2_UNIT | Hydro | 2024 | summer | 25204 | 22461.4633 | 0 | 765 | 55 | 42075 | 0 | Individual | 53.38% | 0% |  |  | 53.38% | 0% | TRUE |  |  | 53.38% | 0%
OLINDA_2_COYCRK | Hydro | 2022 | nonsummer | 28907 | 3302.15 | 0 | 1060 | 3.13 | 3317.8 | 0 | Individual | 99.53% | 0% |  |  | 99.53% | 0% | TRUE |  |  | 99.53% | 0%
OLINDA_2_COYCRK | Hydro | 2022 | summer | 28907 | 2394.45 | 0 | 765 | 3.13 | 2394.45 | 0 | Individual | 100% | 0% |  |  | 100% | 0% | TRUE |  |  | 100% | 0%
OLINDA_2_COYCRK | Hydro | 2023 | nonsummer | 28907 | 3302.15 | 0 | 1060 | 3.13 | 3317.8 | 0 | Individual | 99.53% | 0% |  |  | 99.53% | 0% | TRUE |  |  | 99.53% | 0%
OLINDA_2_COYCRK | Hydro | 2023 | summer | 28907 | 2394.45 | 0 | 765 | 3.13 | 2394.45 | 0 | Individual | 100% | 0% |  |  | 100% | 0% | TRUE |  |  | 100% | 0%
OLINDA_2_COYCRK | Hydro | 2024 | nonsummer | 28907 | 0 | 0 | 1065 | 3.13 | 3333.45 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
OLINDA_2_COYCRK | Hydro | 2024 | summer | 28907 | 0 | 0 | 765 | 3.13 | 2394.45 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
PADUA_6_MWDSDM | Hydro | 2022 | nonsummer | 29587 | 0 | 0 | 1060 | 9.9 | 10494 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
PADUA_6_MWDSDM | Hydro | 2022 | summer | 29587 | 49.5 | 0 | 765 | 9.9 | 7573.5 | 0 | Individual | 0.6536% | 0% |  |  | 0.6536% | 0% | TRUE |  |  | 0.6536% | 0%
PADUA_6_MWDSDM | Hydro | 2023 | nonsummer | 29587 | 346.5 | 0 | 1060 | 9.9 | 10494 | 0 | Individual | 3.302% | 0% |  |  | 3.302% | 0% | TRUE |  |  | 3.302% | 0%
PADUA_6_MWDSDM | Hydro | 2023 | summer | 29587 | 74 | 0 | 765 | 9.9 | 7573.5 | 0 | Individual | 0.9771% | 0% |  |  | 0.9771% | 0% | TRUE |  |  | 0.9771% | 0%
PADUA_6_MWDSDM | Hydro | 2024 | nonsummer | 29587 | 0 | 0 | 1065 | 9.9 | 10543.5 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
PADUA_6_MWDSDM | Hydro | 2024 | summer | 29587 | 0 | 0 | 765 | 9.9 | 7573.5 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
PADUA_7_SDIMAS | Hydro | 2022 | nonsummer | 31440 | 0 | 0 | 1060 | 1.05 | 1113 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
PADUA_7_SDIMAS | Hydro | 2022 | summer | 31440 | 0 | 0 | 765 | 1.05 | 803.25 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
PADUA_7_SDIMAS | Hydro | 2023 | nonsummer | 31440 | 136.5 | 0 | 1060 | 1.05 | 1113 | 0 | Individual | 12.26% | 0% |  |  | 12.26% | 0% | TRUE |  |  | 12.26% | 0%
PADUA_7_SDIMAS | Hydro | 2023 | summer | 31440 | 244.825 | 0 | 765 | 1.05 | 803.25 | 0 | Individual | 30.48% | 0% |  |  | 30.48% | 0% | TRUE |  |  | 30.48% | 0%
PADUA_7_SDIMAS | Hydro | 2024 | nonsummer | 31440 | 372.75 | 0 | 1065 | 1.05 | 1118.25 | 0 | Individual | 33.33% | 0% |  |  | 33.33% | 0% | TRUE |  |  | 33.33% | 0%
PADUA_7_SDIMAS | Hydro | 2024 | summer | 31440 | 630 | 0 | 765 | 1.05 | 803.25 | 0 | Individual | 78.43% | 0% |  |  | 78.43% | 0% | TRUE |  |  | 78.43% | 0%
PARDEB_6_UNITS | Hydro | 2022 | nonsummer | 10959 | 10478.1 | 0 | 1060 | 30 | 31800 | 0 | Individual | 32.95% | 0% |  |  | 32.95% | 0% | TRUE |  |  | 32.95% | 0%
PARDEB_6_UNITS | Hydro | 2022 | summer | 10959 | 3510.5 | 0 | 765 | 30 | 22950 | 0 | Individual | 15.3% | 0% |  |  | 15.3% | 0% | TRUE |  |  | 15.3% | 0%
PARDEB_6_UNITS | Hydro | 2023 | nonsummer | 10959 | 4501.2667 | 0 | 1060 | 30 | 31800 | 0 | Individual | 14.15% | 0% |  |  | 14.15% | 0% | TRUE |  |  | 14.15% | 0%
PARDEB_6_UNITS | Hydro | 2023 | summer | 10959 | 752.025 | 0 | 765 | 30 | 22950 | 0 | Individual | 3.277% | 0% |  |  | 3.277% | 0% | TRUE |  |  | 3.277% | 0%
PARDEB_6_UNITS | Hydro | 2024 | nonsummer | 10959 | 4021.7667 | 0 | 1065 | 30 | 31950 | 0 | Individual | 12.59% | 0% |  |  | 12.59% | 0% | TRUE |  |  | 12.59% | 0%
PARDEB_6_UNITS | Hydro | 2024 | summer | 10959 | 620.63 | 0 | 765 | 30 | 22950 | 0 | Individual | 2.704% | 0% |  |  | 2.704% | 0% | TRUE |  |  | 2.704% | 0%
PINFLT_7_UNITS | Hydro | 2022 | nonsummer | 30682 | 113820.05 | 26889.3 | 1060 | 198.51 | 210420.6 | 0 | Individual | 54.09% | 12.78% |  |  | 54.09% | 12.78% | TRUE |  |  | 54.09% | 12.78%
PINFLT_7_UNITS | Hydro | 2022 | summer | 30682 | 105221.686 | 9193.4833 | 765 | 198.51 | 151860.15 | 0 | Individual | 69.29% | 6.054% |  |  | 69.29% | 6.054% | TRUE |  |  | 69.29% | 6.054%
PINFLT_7_UNITS | Hydro | 2023 | nonsummer | 30682 | 89570.5783 | 0 | 1060 | 198.51 | 210420.6 | 0 | Individual | 42.57% | 0% |  |  | 42.57% | 0% | TRUE |  |  | 42.57% | 0%
PINFLT_7_UNITS | Hydro | 2023 | summer | 30682 | 25907.25 | 0 | 765 | 198.51 | 151860.15 | 0 | Individual | 17.06% | 0% |  |  | 17.06% | 0% | TRUE |  |  | 17.06% | 0%
PINFLT_7_UNITS | Hydro | 2024 | nonsummer | 30682 | 20064.9585 | 0 | 1065 | 198.51 | 211413.15 | 0 | Individual | 9.491% | 0% |  |  | 9.491% | 0% | TRUE |  |  | 9.491% | 0%
PINFLT_7_UNITS | Hydro | 2024 | summer | 30682 | 54386.525 | 0 | 765 | 198.51 | 151860.15 | 0 | Individual | 35.81% | 0% |  |  | 35.81% | 0% | TRUE |  |  | 35.81% | 0%
PIT1_7_UNIT 1 | Hydro | 2022 | nonsummer | 8037 | 11360 | 0 | 1060 | 32 | 33920 | 0 | Individual | 33.49% | 0% |  |  | 33.49% | 0% | TRUE |  |  | 33.49% | 0%
PIT1_7_UNIT 1 | Hydro | 2022 | summer | 8037 | 1154 | 0 | 765 | 32 | 24480 | 0 | Individual | 4.714% | 0% |  |  | 4.714% | 0% | TRUE |  |  | 4.714% | 0%
PIT1_7_UNIT 1 | Hydro | 2023 | nonsummer | 8037 | 24044.1 | 0 | 1060 | 32 | 33920 | 0 | Individual | 70.88% | 0% |  |  | 70.88% | 0% | TRUE |  |  | 70.88% | 0%
PIT1_7_UNIT 1 | Hydro | 2023 | summer | 8037 | 1043.4667 | 0 | 765 | 32 | 24480 | 0 | Individual | 4.263% | 0% |  |  | 4.263% | 0% | TRUE |  |  | 4.263% | 0%
PIT1_7_UNIT 1 | Hydro | 2024 | nonsummer | 8037 | 512.7 | 0 | 1065 | 32 | 34080 | 0 | Individual | 1.504% | 0% |  |  | 1.504% | 0% | TRUE |  |  | 1.504% | 0%
PIT1_7_UNIT 1 | Hydro | 2024 | summer | 8037 | 94.6 | 0 | 765 | 32 | 24480 | 0 | Individual | 0.3864% | 0% |  |  | 0.3864% | 0% | TRUE |  |  | 0.3864% | 0%
PIT1_7_UNIT 2 | Hydro | 2022 | nonsummer | 8037 | 72 | 0 | 1060 | 32 | 33920 | 0 | Individual | 0.2123% | 0% |  |  | 0.2123% | 0% | TRUE |  |  | 0.2123% | 0%
PIT1_7_UNIT 2 | Hydro | 2022 | summer | 8037 | 137.0333 | 0 | 765 | 32 | 24480 | 0 | Individual | 0.5598% | 0% |  |  | 0.5598% | 0% | TRUE |  |  | 0.5598% | 0%
PIT1_7_UNIT 2 | Hydro | 2023 | nonsummer | 8037 | 9.8333 | 0 | 1060 | 32 | 33920 | 0 | Individual | 0.02899% | 0% |  |  | 0.02899% | 0% | TRUE |  |  | 0.02899% | 0%
PIT1_7_UNIT 2 | Hydro | 2023 | summer | 8037 | 249.55 | 0 | 765 | 32 | 24480 | 0 | Individual | 1.019% | 0% |  |  | 1.019% | 0% | TRUE |  |  | 1.019% | 0%
PIT1_7_UNIT 2 | Hydro | 2024 | nonsummer | 8037 | 460.455 | 0 | 1065 | 32 | 34080 | 0 | Individual | 1.351% | 0% |  |  | 1.351% | 0% | TRUE |  |  | 1.351% | 0%
PIT1_7_UNIT 2 | Hydro | 2024 | summer | 8037 | 7 | 0 | 765 | 32 | 24480 | 0 | Individual | 0.02859% | 0% |  |  | 0.02859% | 0% | TRUE |  |  | 0.02859% | 0%
PIT3_7_PL1X3 | Hydro | 2022 | nonsummer | 9133 | 21298.0067 | 0 | 1060 | 70.6 | 74836 | 0 | Individual | 28.46% | 0% |  |  | 28.46% | 0% | TRUE |  |  | 28.46% | 0%
PIT3_7_PL1X3 | Hydro | 2022 | summer | 9133 | 3524.5467 | 8.51 | 765 | 70.6 | 54009 | 0 | Individual | 6.526% | 0.01576% |  |  | 6.526% | 0.01576% | TRUE |  |  | 6.526% | 0.01576%
PIT3_7_PL1X3 | Hydro | 2023 | nonsummer | 9133 | 247.7833 | 0 | 1060 | 70.6 | 74836 | 0 | Individual | 0.3311% | 0% |  |  | 0.3311% | 0% | TRUE |  |  | 0.3311% | 0%
PIT3_7_PL1X3 | Hydro | 2023 | summer | 9133 | 784.71 | 0 | 765 | 70.6 | 54009 | 0 | Individual | 1.453% | 0% |  |  | 1.453% | 0% | TRUE |  |  | 1.453% | 0%
PIT3_7_PL1X3 | Hydro | 2024 | nonsummer | 9133 | 672.9567 | 0 | 1065 | 70.6 | 75189 | 0 | Individual | 0.895% | 0% |  |  | 0.895% | 0% | TRUE |  |  | 0.895% | 0%
PIT3_7_PL1X3 | Hydro | 2024 | summer | 9133 | 161.03 | 11.9467 | 765 | 70.6 | 54009 | 0 | Individual | 0.2982% | 0.02212% |  |  | 0.2982% | 0.02212% | TRUE |  |  | 0.2982% | 0.02212%
PIT4_7_PL1X2 | Hydro | 2022 | nonsummer | 20090 | 1526.1833 | 0 | 1060 | 95 | 100700 | 0 | Individual | 1.516% | 0% |  |  | 1.516% | 0% | TRUE |  |  | 1.516% | 0%
PIT4_7_PL1X2 | Hydro | 2022 | summer | 20090 | 587.4667 | 4.7 | 765 | 95 | 72675 | 0 | Individual | 0.8083% | 0.006467% |  |  | 0.8083% | 0.006467% | TRUE |  |  | 0.8083% | 0.006467%
PIT4_7_PL1X2 | Hydro | 2023 | nonsummer | 20090 | 674.9167 | 0 | 1060 | 95 | 100700 | 0 | Individual | 0.6702% | 0% |  |  | 0.6702% | 0% | TRUE |  |  | 0.6702% | 0%
PIT4_7_PL1X2 | Hydro | 2023 | summer | 20090 | 908.7333 | 0 | 765 | 95 | 72675 | 0 | Individual | 1.25% | 0% |  |  | 1.25% | 0% | TRUE |  |  | 1.25% | 0%
PIT4_7_PL1X2 | Hydro | 2024 | nonsummer | 20090 | 664.4283 | 0 | 1065 | 95 | 101175 | 0 | Individual | 0.6567% | 0% |  |  | 0.6567% | 0% | TRUE |  |  | 0.6567% | 0%
PIT4_7_PL1X2 | Hydro | 2024 | summer | 20090 | 895.95 | 0 | 765 | 95 | 72675 | 0 | Individual | 1.233% | 0% |  |  | 1.233% | 0% | TRUE |  |  | 1.233% | 0%
PIT5_7_PL1X2 | Hydro | 2022 | nonsummer | 16072 | 753.8833 | 0 | 1060 | 82 | 86920 | 0 | Individual | 0.8673% | 0% |  |  | 0.8673% | 0% | TRUE |  |  | 0.8673% | 0%
PIT5_7_PL1X2 | Hydro | 2022 | summer | 16072 | 558.4 | 0 | 765 | 82 | 62730 | 0 | Individual | 0.8902% | 0% |  |  | 0.8902% | 0% | TRUE |  |  | 0.8902% | 0%
PIT5_7_PL1X2 | Hydro | 2023 | nonsummer | 16072 | 1533.9333 | 0 | 1060 | 82 | 86920 | 0 | Individual | 1.765% | 0% |  |  | 1.765% | 0% | TRUE |  |  | 1.765% | 0%
PIT5_7_PL1X2 | Hydro | 2023 | summer | 16072 | 1490.5167 | 1.3333 | 765 | 82 | 62730 | 0 | Individual | 2.376% | 0.002126% |  |  | 2.376% | 0.002126% | TRUE |  |  | 2.376% | 0.002126%
PIT5_7_PL1X2 | Hydro | 2024 | nonsummer | 16072 | 3037.2 | 0 | 1065 | 82 | 87330 | 0 | Individual | 3.478% | 0% |  |  | 3.478% | 0% | TRUE |  |  | 3.478% | 0%
PIT5_7_PL1X2 | Hydro | 2024 | summer | 16072 | 692.6833 | 0 | 765 | 82 | 62730 | 0 | Individual | 1.104% | 0% |  |  | 1.104% | 0% | TRUE |  |  | 1.104% | 0%
PIT5_7_PL3X4 | Hydro | 2022 | nonsummer | 16072 | 19944.4167 | 0 | 1060 | 82 | 86920 | 0 | Individual | 22.95% | 0% |  |  | 22.95% | 0% | TRUE |  |  | 22.95% | 0%
PIT5_7_PL3X4 | Hydro | 2022 | summer | 16072 | 637.6133 | 0 | 765 | 82 | 62730 | 0 | Individual | 1.016% | 0% |  |  | 1.016% | 0% | TRUE |  |  | 1.016% | 0%
PIT5_7_PL3X4 | Hydro | 2023 | nonsummer | 16072 | 885.7 | 0 | 1060 | 82 | 86920 | 0 | Individual | 1.019% | 0% |  |  | 1.019% | 0% | TRUE |  |  | 1.019% | 0%
PIT5_7_PL3X4 | Hydro | 2023 | summer | 16072 | 1858.9833 | 0 | 765 | 82 | 62730 | 0 | Individual | 2.963% | 0% |  |  | 2.963% | 0% | TRUE |  |  | 2.963% | 0%
PIT5_7_PL3X4 | Hydro | 2024 | nonsummer | 16072 | 656.5 | 0 | 1065 | 82 | 87330 | 0 | Individual | 0.7517% | 0% |  |  | 0.7517% | 0% | TRUE |  |  | 0.7517% | 0%
PIT5_7_PL3X4 | Hydro | 2024 | summer | 16072 | 787.8667 | 0 | 765 | 82 | 62730 | 0 | Individual | 1.256% | 0% |  |  | 1.256% | 0% | TRUE |  |  | 1.256% | 0%
PIT6_7_UNIT 1 | Hydro | 2022 | nonsummer | 23743 | 1481.987 | 0 | 1060 | 39 | 41340 | 0 | Individual | 3.585% | 0% |  |  | 3.585% | 0% | TRUE |  |  | 3.585% | 0%
PIT6_7_UNIT 1 | Hydro | 2022 | summer | 23743 | 832.4205 | 0 | 765 | 39 | 29835 | 0 | Individual | 2.79% | 0% |  |  | 2.79% | 0% | TRUE |  |  | 2.79% | 0%
PIT6_7_UNIT 1 | Hydro | 2023 | nonsummer | 23743 | 1460.2987 | 0 | 1060 | 39 | 41340 | 0 | Individual | 3.532% | 0% |  |  | 3.532% | 0% | TRUE |  |  | 3.532% | 0%
PIT6_7_UNIT 1 | Hydro | 2023 | summer | 23743 | 950.2432 | 0 | 765 | 39 | 29835 | 0 | Individual | 3.185% | 0% |  |  | 3.185% | 0% | TRUE |  |  | 3.185% | 0%
PIT6_7_UNIT 1 | Hydro | 2024 | nonsummer | 23743 | 1824.2993 | 0 | 1065 | 39 | 41535 | 0 | Individual | 4.392% | 0% |  |  | 4.392% | 0% | TRUE |  |  | 4.392% | 0%
PIT6_7_UNIT 1 | Hydro | 2024 | summer | 23743 | 1230.5635 | 0 | 765 | 39 | 29835 | 0 | Individual | 4.125% | 0% |  |  | 4.125% | 0% | TRUE |  |  | 4.125% | 0%
PIT6_7_UNIT 2 | Hydro | 2022 | nonsummer | 23743 | 2600.257 | 0 | 1060 | 40 | 42400 | 0 | Individual | 6.133% | 0% |  |  | 6.133% | 0% | TRUE |  |  | 6.133% | 0%
PIT6_7_UNIT 2 | Hydro | 2022 | summer | 23743 | 1513.8995 | 0 | 765 | 40 | 30600 | 0 | Individual | 4.947% | 0% |  |  | 4.947% | 0% | TRUE |  |  | 4.947% | 0%
PIT6_7_UNIT 2 | Hydro | 2023 | nonsummer | 23743 | 1870.6673 | 0 | 1060 | 40 | 42400 | 0 | Individual | 4.412% | 0% |  |  | 4.412% | 0% | TRUE |  |  | 4.412% | 0%
PIT6_7_UNIT 2 | Hydro | 2023 | summer | 23743 | 1363.5058 | 0 | 765 | 40 | 30600 | 0 | Individual | 4.456% | 0% |  |  | 4.456% | 0% | TRUE |  |  | 4.456% | 0%
PIT6_7_UNIT 2 | Hydro | 2024 | nonsummer | 23743 | 2284.7705 | 0 | 1065 | 40 | 42600 | 0 | Individual | 5.363% | 0% |  |  | 5.363% | 0% | TRUE |  |  | 5.363% | 0%
PIT6_7_UNIT 2 | Hydro | 2024 | summer | 23743 | 1946.8495 | 0 | 765 | 40 | 30600 | 0 | Individual | 6.362% | 0% |  |  | 6.362% | 0% | TRUE |  |  | 6.362% | 0%
PIT7_7_UNIT 1 | Hydro | 2022 | nonsummer | 23743 | 2026.474 | 0 | 1060 | 55.7 | 59042 | 0 | Individual | 3.432% | 0% |  |  | 3.432% | 0% | TRUE |  |  | 3.432% | 0%
PIT7_7_UNIT 1 | Hydro | 2022 | summer | 23743 | 1090.2088 | 0 | 765 | 55.7 | 42610.5 | 0 | Individual | 2.559% | 0% |  |  | 2.559% | 0% | TRUE |  |  | 2.559% | 0%
PIT7_7_UNIT 1 | Hydro | 2023 | nonsummer | 23743 | 1389.316 | 0 | 1060 | 55.7 | 59042 | 0 | Individual | 2.353% | 0% |  |  | 2.353% | 0% | TRUE |  |  | 2.353% | 0%
PIT7_7_UNIT 1 | Hydro | 2023 | summer | 23743 | 1353.7082 | 0 | 765 | 55.7 | 42610.5 | 0 | Individual | 3.177% | 0% |  |  | 3.177% | 0% | TRUE |  |  | 3.177% | 0%
PIT7_7_UNIT 1 | Hydro | 2024 | nonsummer | 23743 | 2334.5232 | 0 | 1065 | 55.7 | 59320.5 | 0 | Individual | 3.935% | 0% |  |  | 3.935% | 0% | TRUE |  |  | 3.935% | 0%
PIT7_7_UNIT 1 | Hydro | 2024 | summer | 23743 | 1484.4225 | 2.3542 | 765 | 55.7 | 42610.5 | 0 | Individual | 3.484% | 0.005525% |  |  | 3.484% | 0.005525% | TRUE |  |  | 3.484% | 0.005525%
PIT7_7_UNIT 2 | Hydro | 2022 | nonsummer | 23743 | 24891.6447 | 0 | 1060 | 54.6 | 57876 | 0 | Individual | 43.01% | 0% |  |  | 43.01% | 0% | TRUE |  |  | 43.01% | 0%
PIT7_7_UNIT 2 | Hydro | 2022 | summer | 23743 | 8639.232 | 0 | 765 | 54.6 | 41769 | 0 | Individual | 20.68% | 0% |  |  | 20.68% | 0% | TRUE |  |  | 20.68% | 0%
PIT7_7_UNIT 2 | Hydro | 2023 | nonsummer | 23743 | 3150.8833 | 0 | 1060 | 54.6 | 57876 | 0 | Individual | 5.444% | 0% |  |  | 5.444% | 0% | TRUE |  |  | 5.444% | 0%
PIT7_7_UNIT 2 | Hydro | 2023 | summer | 23743 | 771.2012 | 0 | 765 | 54.6 | 41769 | 0 | Individual | 1.846% | 0% |  |  | 1.846% | 0% | TRUE |  |  | 1.846% | 0%
PIT7_7_UNIT 2 | Hydro | 2024 | nonsummer | 23743 | 1422.8287 | 0 | 1065 | 54.6 | 58149 | 0 | Individual | 2.447% | 0% |  |  | 2.447% | 0% | TRUE |  |  | 2.447% | 0%
PIT7_7_UNIT 2 | Hydro | 2024 | summer | 23743 | 755.781 | 0 | 765 | 54.6 | 41769 | 0 | Individual | 1.809% | 0% |  |  | 1.809% | 0% | TRUE |  |  | 1.809% | 0%
POEPH_7_UNIT 1 | Hydro | 2022 | nonsummer | 21186 | 24362.354 | 0 | 1060 | 68 | 72080 | 0 | Individual | 33.8% | 0% |  |  | 33.8% | 0% | TRUE |  |  | 33.8% | 0%
POEPH_7_UNIT 1 | Hydro | 2022 | summer | 21186 | 28283.1288 | 0 | 765 | 68 | 52020 | 0 | Individual | 54.37% | 0% |  |  | 54.37% | 0% | TRUE |  |  | 54.37% | 0%
POEPH_7_UNIT 1 | Hydro | 2023 | nonsummer | 21186 | 11518.86 | 0 | 1060 | 68 | 72080 | 0 | Individual | 15.98% | 0% |  |  | 15.98% | 0% | TRUE |  |  | 15.98% | 0%
POEPH_7_UNIT 1 | Hydro | 2023 | summer | 21186 | 27461.0545 | 0 | 765 | 68 | 52020 | 0 | Individual | 52.79% | 0% |  |  | 52.79% | 0% | TRUE |  |  | 52.79% | 0%
POEPH_7_UNIT 1 | Hydro | 2024 | nonsummer | 21186 | 9077.1225 | 0 | 1065 | 68 | 72420 | 0 | Individual | 12.53% | 0% |  |  | 12.53% | 0% | TRUE |  |  | 12.53% | 0%
POEPH_7_UNIT 1 | Hydro | 2024 | summer | 21186 | 23807.0087 | 0 | 765 | 68 | 52020 | 0 | Individual | 45.77% | 0% |  |  | 45.77% | 0% | TRUE |  |  | 45.77% | 0%
POEPH_7_UNIT 2 | Hydro | 2022 | nonsummer | 21186 | 22622.3932 | 0 | 1060 | 68.5 | 72610 | 0 | Individual | 31.16% | 0% |  |  | 31.16% | 0% | TRUE |  |  | 31.16% | 0%
POEPH_7_UNIT 2 | Hydro | 2022 | summer | 21186 | 27466.224 | 0 | 765 | 68.5 | 52402.5 | 0 | Individual | 52.41% | 0% |  |  | 52.41% | 0% | TRUE |  |  | 52.41% | 0%
POEPH_7_UNIT 2 | Hydro | 2023 | nonsummer | 21186 | 15263.9265 | 0 | 1060 | 68.5 | 72610 | 0 | Individual | 21.02% | 0% |  |  | 21.02% | 0% | TRUE |  |  | 21.02% | 0%
POEPH_7_UNIT 2 | Hydro | 2023 | summer | 21186 | 26219.9858 | 0 | 765 | 68.5 | 52402.5 | 0 | Individual | 50.04% | 0% |  |  | 50.04% | 0% | TRUE |  |  | 50.04% | 0%
POEPH_7_UNIT 2 | Hydro | 2024 | nonsummer | 21186 | 5410.1717 | 0 | 1065 | 68.5 | 72952.5 | 0 | Individual | 7.416% | 0% |  |  | 7.416% | 0% | TRUE |  |  | 7.416% | 0%
POEPH_7_UNIT 2 | Hydro | 2024 | summer | 21186 | 20190.16 | 25.6417 | 765 | 68.5 | 52402.5 | 0 | Individual | 38.53% | 0.04893% |  |  | 38.53% | 0.04893% | TRUE |  |  | 38.53% | 0.04893%
RCKCRK_7_UNIT 1 | Hydro | 2022 | nonsummer | 18264 | 21442.2462 | 0 | 1060 | 57 | 60420 | 0 | Individual | 35.49% | 0% |  |  | 35.49% | 0% | TRUE |  |  | 35.49% | 0%
RCKCRK_7_UNIT 1 | Hydro | 2022 | summer | 18264 | 14640.2443 | 0 | 765 | 57 | 43605 | 0 | Individual | 33.57% | 0% |  |  | 33.57% | 0% | TRUE |  |  | 33.57% | 0%
RCKCRK_7_UNIT 1 | Hydro | 2023 | nonsummer | 18264 | 9802.0567 | 0 | 1060 | 57 | 60420 | 0 | Individual | 16.22% | 0% |  |  | 16.22% | 0% | TRUE |  |  | 16.22% | 0%
RCKCRK_7_UNIT 1 | Hydro | 2023 | summer | 18264 | 24860.7993 | 0 | 765 | 57 | 43605 | 0 | Individual | 57.01% | 0% |  |  | 57.01% | 0% | TRUE |  |  | 57.01% | 0%
RCKCRK_7_UNIT 1 | Hydro | 2024 | nonsummer | 18264 | 7884.1058 | 0 | 1065 | 57 | 60705 | 0 | Individual | 12.99% | 0% |  |  | 12.99% | 0% | TRUE |  |  | 12.99% | 0%
RCKCRK_7_UNIT 1 | Hydro | 2024 | summer | 18264 | 17187.3082 | 0 | 765 | 57 | 43605 | 0 | Individual | 39.42% | 0% |  |  | 39.42% | 0% | TRUE |  |  | 39.42% | 0%
RCKCRK_7_UNIT 2 | Hydro | 2022 | nonsummer | 18264 | 29880.6925 | 0 | 1060 | 56.9 | 60314 | 0 | Individual | 49.54% | 0% |  |  | 49.54% | 0% | TRUE |  |  | 49.54% | 0%
RCKCRK_7_UNIT 2 | Hydro | 2022 | summer | 18264 | 22242.685 | 0 | 765 | 56.9 | 43528.5 | 0 | Individual | 51.1% | 0% |  |  | 51.1% | 0% | TRUE |  |  | 51.1% | 0%
RCKCRK_7_UNIT 2 | Hydro | 2023 | nonsummer | 18264 | 8856.7633 | 0 | 1060 | 56.9 | 60314 | 0 | Individual | 14.68% | 0% |  |  | 14.68% | 0% | TRUE |  |  | 14.68% | 0%
RCKCRK_7_UNIT 2 | Hydro | 2023 | summer | 18264 | 2032.8408 | 0 | 765 | 56.9 | 43528.5 | 0 | Individual | 4.67% | 0% |  |  | 4.67% | 0% | TRUE |  |  | 4.67% | 0%
RCKCRK_7_UNIT 2 | Hydro | 2024 | nonsummer | 18264 | 5498.68 | 0 | 1065 | 56.9 | 60598.5 | 0 | Individual | 9.074% | 0% |  |  | 9.074% | 0% | TRUE |  |  | 9.074% | 0%
RCKCRK_7_UNIT 2 | Hydro | 2024 | summer | 18264 | 15545.8182 | 0 | 765 | 56.9 | 43528.5 | 0 | Individual | 35.71% | 0% |  |  | 35.71% | 0% | TRUE |  |  | 35.71% | 0%
RECTOR_2_QF | Hydro | 2022 | nonsummer | 43969 | 11953.55 | 0 | 1060 | 20.09 | 21295.4 | 0 | Individual | 56.13% | 0% |  |  | 56.13% | 0% | TRUE |  |  | 56.13% | 0%
RECTOR_2_QF | Hydro | 2022 | summer | 43969 | 10547.25 | 0 | 765 | 20.09 | 15368.85 | 0 | Individual | 68.63% | 0% |  |  | 68.63% | 0% | TRUE |  |  | 68.63% | 0%
RECTOR_2_QF | Hydro | 2023 | nonsummer | 43969 | 11451.3 | 0 | 1060 | 20.09 | 21295.4 | 0 | Individual | 53.77% | 0% |  |  | 53.77% | 0% | TRUE |  |  | 53.77% | 0%
RECTOR_2_QF | Hydro | 2023 | summer | 43969 | 2929.4568 | 0 | 765 | 20.09 | 15368.85 | 0 | Individual | 19.06% | 0% |  |  | 19.06% | 0% | TRUE |  |  | 19.06% | 0%
RECTOR_2_QF | Hydro | 2024 | nonsummer | 43969 | 17377.85 | 0 | 1065 | 20.09 | 21395.85 | 0 | Individual | 81.22% | 0% |  |  | 81.22% | 0% | TRUE |  |  | 81.22% | 0%
RECTOR_2_QF | Hydro | 2024 | summer | 43969 | 13439.8752 | 0 | 765 | 20.09 | 15368.85 | 0 | Individual | 87.45% | 0% |  |  | 87.45% | 0% | TRUE |  |  | 87.45% | 0%
ROLLIN_6_UNIT | Hydro | 2022 | nonsummer | 29221 | 5982.175 | 0 | 1060 | 13.5 | 14310 | 0 | Individual | 41.8% | 0% |  |  | 41.8% | 0% | TRUE |  |  | 41.8% | 0%
ROLLIN_6_UNIT | Hydro | 2022 | summer | 29221 | 2996.4643 | 0 | 765 | 13.5 | 10327.5 | 0 | Individual | 29.01% | 0% |  |  | 29.01% | 0% | TRUE |  |  | 29.01% | 0%
ROLLIN_6_UNIT | Hydro | 2023 | nonsummer | 29221 | 1137.5 | 0 | 1060 | 13.5 | 14310 | 0 | Individual | 7.949% | 0% |  |  | 7.949% | 0% | TRUE |  |  | 7.949% | 0%
ROLLIN_6_UNIT | Hydro | 2023 | summer | 29221 | 718.4 | 0 | 765 | 13.5 | 10327.5 | 0 | Individual | 6.956% | 0% |  |  | 6.956% | 0% | TRUE |  |  | 6.956% | 0%
ROLLIN_6_UNIT | Hydro | 2024 | nonsummer | 29221 | 5775.1155 | 0 | 1065 | 13.5 | 14377.5 | 0 | Individual | 40.17% | 0% |  |  | 40.17% | 0% | TRUE |  |  | 40.17% | 0%
ROLLIN_6_UNIT | Hydro | 2024 | summer | 29221 | 6782.025 | 0 | 765 | 13.5 | 10327.5 | 0 | Individual | 65.67% | 0% |  |  | 65.67% | 0% | TRUE |  |  | 65.67% | 0%
SALTSP_7_UNITS | Hydro | 2022 | nonsummer | 11324 | 23345.765 | 0 | 1060 | 46 | 48760 | 0 | Individual | 47.88% | 0% |  |  | 47.88% | 0% | TRUE |  |  | 47.88% | 0%
SALTSP_7_UNITS | Hydro | 2022 | summer | 11324 | 53.0667 | 0 | 765 | 46 | 35190 | 0 | Individual | 0.1508% | 0% |  |  | 0.1508% | 0% | TRUE |  |  | 0.1508% | 0%
SALTSP_7_UNITS | Hydro | 2023 | nonsummer | 11324 | 11154.3 | 0 | 1060 | 46 | 48760 | 0 | Individual | 22.88% | 0% |  |  | 22.88% | 0% | TRUE |  |  | 22.88% | 0%
SALTSP_7_UNITS | Hydro | 2023 | summer | 11324 | 13230 | 0 | 765 | 46 | 35190 | 0 | Individual | 37.6% | 0% |  |  | 37.6% | 0% | TRUE |  |  | 37.6% | 0%
SALTSP_7_UNITS | Hydro | 2024 | nonsummer | 11324 | 16821.1 | 0 | 1065 | 46 | 48990 | 0 | Individual | 34.34% | 0% |  |  | 34.34% | 0% | TRUE |  |  | 34.34% | 0%
SALTSP_7_UNITS | Hydro | 2024 | summer | 11324 | 11343.6167 | 0 | 765 | 46 | 35190 | 0 | Individual | 32.24% | 0% |  |  | 32.24% | 0% | TRUE |  |  | 32.24% | 0%
SAUGUS_6_MWDFTH | Hydro | 2022 | nonsummer | 29587 | 0 | 0 | 1060 | 9.1 | 9646 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SAUGUS_6_MWDFTH | Hydro | 2022 | summer | 29587 | 0 | 0 | 765 | 9.1 | 6961.5 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SAUGUS_6_MWDFTH | Hydro | 2023 | nonsummer | 29587 | 637 | 0 | 1060 | 9.1 | 9646 | 0 | Individual | 6.604% | 0% |  |  | 6.604% | 0% | TRUE |  |  | 6.604% | 0%
SAUGUS_6_MWDFTH | Hydro | 2023 | summer | 29587 | 307.7317 | 0 | 765 | 9.1 | 6961.5 | 0 | Individual | 4.42% | 0% |  |  | 4.42% | 0% | TRUE |  |  | 4.42% | 0%
SAUGUS_6_MWDFTH | Hydro | 2024 | nonsummer | 29587 | 3321.5 | 0 | 1065 | 9.1 | 9691.5 | 0 | Individual | 34.27% | 0% |  |  | 34.27% | 0% | TRUE |  |  | 34.27% | 0%
SAUGUS_6_MWDFTH | Hydro | 2024 | summer | 29587 | 0 | 0 | 765 | 9.1 | 6961.5 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SLYCRK_1_UNIT 1 | Hydro | 2022 | nonsummer | 30317 | 368.9833 | 0 | 1060 | 13 | 13780 | 0 | Individual | 2.678% | 0% |  |  | 2.678% | 0% | TRUE |  |  | 2.678% | 0%
SLYCRK_1_UNIT 1 | Hydro | 2022 | summer | 30317 | 900.46 | 0 | 765 | 13 | 9945 | 0 | Individual | 9.054% | 0% |  |  | 9.054% | 0% | TRUE |  |  | 9.054% | 0%
SLYCRK_1_UNIT 1 | Hydro | 2023 | nonsummer | 30317 | 66.7333 | 0 | 1060 | 13 | 13780 | 0 | Individual | 0.4843% | 0% |  |  | 0.4843% | 0% | TRUE |  |  | 0.4843% | 0%
SLYCRK_1_UNIT 1 | Hydro | 2023 | summer | 30317 | 64.35 | 0 | 765 | 13 | 9945 | 0 | Individual | 0.6471% | 0% |  |  | 0.6471% | 0% | TRUE |  |  | 0.6471% | 0%
SLYCRK_1_UNIT 1 | Hydro | 2024 | nonsummer | 30317 | 24.2667 | 0 | 1065 | 13 | 13845 | 0 | Individual | 0.1753% | 0% |  |  | 0.1753% | 0% | TRUE |  |  | 0.1753% | 0%
SLYCRK_1_UNIT 1 | Hydro | 2024 | summer | 30317 | 48.3167 | 0 | 765 | 13 | 9945 | 0 | Individual | 0.4858% | 0% |  |  | 0.4858% | 0% | TRUE |  |  | 0.4858% | 0%
SPAULD_6_UNIT12 | Hydro | 2022 | nonsummer | 10594 | 4128.925 | 0 | 1060 | 11.4 | 12084 | 0 | Individual | 34.17% | 0% |  |  | 34.17% | 0% | TRUE |  |  | 34.17% | 0%
SPAULD_6_UNIT12 | Hydro | 2022 | summer | 10594 | 479.6733 | 0 | 765 | 11.4 | 8721 | 0 | Individual | 5.5% | 0% |  |  | 5.5% | 0% | TRUE |  |  | 5.5% | 0%
SPAULD_6_UNIT12 | Hydro | 2023 | nonsummer | 10594 | 2518.7133 | 0 | 1060 | 11.4 | 12084 | 0 | Individual | 20.84% | 0% |  |  | 20.84% | 0% | TRUE |  |  | 20.84% | 0%
SPAULD_6_UNIT12 | Hydro | 2023 | summer | 10594 | 3348.8533 | 0 | 765 | 11.4 | 8721 | 0 | Individual | 38.4% | 0% |  |  | 38.4% | 0% | TRUE |  |  | 38.4% | 0%
SPAULD_6_UNIT12 | Hydro | 2024 | nonsummer | 10594 | 9351 | 0 | 1065 | 11.4 | 12141 | 0 | Individual | 77.02% | 0% |  |  | 77.02% | 0% | TRUE |  |  | 77.02% | 0%
SPAULD_6_UNIT12 | Hydro | 2024 | summer | 10594 | 5528.7167 | 0 | 765 | 11.4 | 8721 | 0 | Individual | 63.4% | 0% |  |  | 63.4% | 0% | TRUE |  |  | 63.4% | 0%
SPICER_1_UNITS | Hydro | 2022 | nonsummer | 32874 | 5.3 | 0 | 1060 | 6 | 6360 | 0 | Individual | 0.08333% | 0% |  |  | 0.08333% | 0% | TRUE |  |  | 0.08333% | 0%
SPICER_1_UNITS | Hydro | 2022 | summer | 32874 | 0.25 | 0 | 765 | 6 | 4590 | 0 | Individual | 0.005447% | 0% |  |  | 0.005447% | 0% | TRUE |  |  | 0.005447% | 0%
SPICER_1_UNITS | Hydro | 2023 | nonsummer | 32874 | 138.45 | 0 | 1060 | 6 | 6360 | 0 | Individual | 2.177% | 0% |  |  | 2.177% | 0% | TRUE |  |  | 2.177% | 0%
SPICER_1_UNITS | Hydro | 2023 | summer | 32874 | 18 | 0 | 765 | 6 | 4590 | 0 | Individual | 0.3922% | 0% |  |  | 0.3922% | 0% | TRUE |  |  | 0.3922% | 0%
SPICER_1_UNITS | Hydro | 2024 | nonsummer | 32874 | 44 | 0 | 1065 | 6 | 6390 | 0 | Individual | 0.6886% | 0% |  |  | 0.6886% | 0% | TRUE |  |  | 0.6886% | 0%
SPICER_1_UNITS | Hydro | 2024 | summer | 32874 | 57.8 | 0 | 765 | 6 | 4590 | 0 | Individual | 1.259% | 0% |  |  | 1.259% | 0% | TRUE |  |  | 1.259% | 0%
SPRGVL_2_SUCCES | Hydro | 2022 | nonsummer | 45523 | 0 | 0 | 0 | 1.4 | 0 | 1060 | Group |  |  | 17.82% | 0.4078% | 17.82% | 0.4078% | TRUE | 17.82% | 0.4078% | 17.82% | 0.4078%
SPRGVL_2_SUCCES | Hydro | 2022 | summer | 45523 | 0 | 0 | 0 | 1.4 | 0 | 765 | Group |  |  | 17.13% | 0.1946% | 17.13% | 0.1946% | TRUE | 17.13% | 0.1946% | 17.13% | 0.1946%
SPRGVL_2_SUCCES | Hydro | 2023 | nonsummer | 45523 | 0 | 0 | 0 | 1.4 | 0 | 1060 | Group |  |  | 15.5% | 0.002835% | 15.5% | 0.002835% | TRUE | 15.5% | 0.002835% | 15.5% | 0.002835%
SPRGVL_2_SUCCES | Hydro | 2023 | summer | 45523 | 0 | 0 | 0 | 1.4 | 0 | 765 | Group |  |  | 15.09% | 0.001797% | 15.09% | 0.001797% | TRUE | 15.09% | 0.001797% | 15.09% | 0.001797%
SPRGVL_2_SUCCES | Hydro | 2024 | nonsummer | 45523 | 427 | 0 | 305 | 1.4 | 427 | 760 | Blended | 100% | 0% | 15.08% | 0.008108% | 39.4% | 0.005786% | TRUE | 15.08% | 0.008108% | 39.4% | 0.005786%
SPRGVL_2_SUCCES | Hydro | 2024 | summer | 45523 | 364 | 0 | 370 | 1.4 | 518 | 395 | Blended | 70.27% | 0% | 13.63% | 0.02394% | 41.02% | 0.01236% | TRUE | 13.63% | 0.02394% | 41.02% | 0.01236%
STANIS_7_UNIT 1 | Hydro | 2022 | nonsummer | 23012 | 16648.2017 | 0 | 1060 | 91 | 96460 | 0 | Individual | 17.26% | 0% |  |  | 17.26% | 0% | TRUE |  |  | 17.26% | 0%
STANIS_7_UNIT 1 | Hydro | 2022 | summer | 23012 | 3617.81 | 0 | 765 | 91 | 69615 | 0 | Individual | 5.197% | 0% |  |  | 5.197% | 0% | TRUE |  |  | 5.197% | 0%
STANIS_7_UNIT 1 | Hydro | 2023 | nonsummer | 23012 | 1977.8333 | 0 | 1060 | 91 | 96460 | 0 | Individual | 2.05% | 0% |  |  | 2.05% | 0% | TRUE |  |  | 2.05% | 0%
STANIS_7_UNIT 1 | Hydro | 2023 | summer | 23012 | 296.04 | 0 | 765 | 91 | 69615 | 0 | Individual | 0.4253% | 0% |  |  | 0.4253% | 0% | TRUE |  |  | 0.4253% | 0%
STANIS_7_UNIT 1 | Hydro | 2024 | nonsummer | 23012 | 544.804 | 0 | 1065 | 91 | 96915 | 0 | Individual | 0.5621% | 0% |  |  | 0.5621% | 0% | TRUE |  |  | 0.5621% | 0%
STANIS_7_UNIT 1 | Hydro | 2024 | summer | 23012 | 0 | 0 | 765 | 91 | 69615 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
TIGRCK_7_UNITS | Hydro | 2022 | nonsummer | 11324 | 763.1833 | 0 | 1060 | 62 | 65720 | 0 | Individual | 1.161% | 0% |  |  | 1.161% | 0% | TRUE |  |  | 1.161% | 0%
TIGRCK_7_UNITS | Hydro | 2022 | summer | 11324 | 5669.665 | 25 | 765 | 62 | 47430 | 0 | Individual | 11.95% | 0.05271% |  |  | 11.95% | 0.05271% | TRUE |  |  | 11.95% | 0.05271%
TIGRCK_7_UNITS | Hydro | 2023 | nonsummer | 11324 | 15508.575 | 0 | 1060 | 62 | 65720 | 0 | Individual | 23.6% | 0% |  |  | 23.6% | 0% | TRUE |  |  | 23.6% | 0%
TIGRCK_7_UNITS | Hydro | 2023 | summer | 11324 | 2867.0333 | 0 | 765 | 62 | 47430 | 0 | Individual | 6.045% | 0% |  |  | 6.045% | 0% | TRUE |  |  | 6.045% | 0%
TIGRCK_7_UNITS | Hydro | 2024 | nonsummer | 11324 | 1054.2333 | 0 | 1065 | 62 | 66030 | 0 | Individual | 1.597% | 0% |  |  | 1.597% | 0% | TRUE |  |  | 1.597% | 0%
TIGRCK_7_UNITS | Hydro | 2024 | summer | 11324 | 421.1333 | 0 | 765 | 62 | 47430 | 0 | Individual | 0.8879% | 0% |  |  | 0.8879% | 0% | TRUE |  |  | 0.8879% | 0%
TVYVLY_6_KRSHY1 | Hydro | 2022 | nonsummer | 44454 | 546 | 0 | 1060 | 1.3 | 1378 | 0 | Individual | 39.62% | 0% |  |  | 39.62% | 0% | TRUE |  |  | 39.62% | 0%
TVYVLY_6_KRSHY1 | Hydro | 2022 | summer | 44454 | 175.5 | 0 | 765 | 1.3 | 994.5 | 0 | Individual | 17.65% | 0% |  |  | 17.65% | 0% | TRUE |  |  | 17.65% | 0%
TVYVLY_6_KRSHY1 | Hydro | 2023 | nonsummer | 44454 | 981.4 | 0 | 1060 | 1.3 | 1378 | 0 | Individual | 71.22% | 0% |  |  | 71.22% | 0% | TRUE |  |  | 71.22% | 0%
TVYVLY_6_KRSHY1 | Hydro | 2023 | summer | 44454 | 994.5 | 0 | 765 | 1.3 | 994.5 | 0 | Individual | 100% | 0% |  |  | 100% | 0% | TRUE |  |  | 100% | 0%
TVYVLY_6_KRSHY1 | Hydro | 2024 | nonsummer | 44454 | 708.825 | 0 | 1065 | 1.3 | 1384.5 | 0 | Individual | 51.2% | 0% |  |  | 51.2% | 0% | TRUE |  |  | 51.2% | 0%
TVYVLY_6_KRSHY1 | Hydro | 2024 | summer | 44454 | 594.75 | 0 | 765 | 1.3 | 994.5 | 0 | Individual | 59.8% | 0% |  |  | 59.8% | 0% | TRUE |  |  | 59.8% | 0%
UKIAH_7_LAKEMN | Hydro | 2022 | nonsummer | 39265 | 1192.1667 | 0 | 1060 | 3.5 | 3710 | 0 | Individual | 32.13% | 0% |  |  | 32.13% | 0% | TRUE |  |  | 32.13% | 0%
UKIAH_7_LAKEMN | Hydro | 2022 | summer | 39265 | 107.6417 | 0 | 765 | 3.5 | 2677.5 | 0 | Individual | 4.02% | 0% |  |  | 4.02% | 0% | TRUE |  |  | 4.02% | 0%
UKIAH_7_LAKEMN | Hydro | 2023 | nonsummer | 39265 | 464.7917 | 0 | 1060 | 3.5 | 3710 | 0 | Individual | 12.53% | 0% |  |  | 12.53% | 0% | TRUE |  |  | 12.53% | 0%
UKIAH_7_LAKEMN | Hydro | 2023 | summer | 39265 | 0 | 0 | 765 | 3.5 | 2677.5 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
UKIAH_7_LAKEMN | Hydro | 2024 | nonsummer | 39265 | 159.7667 | 0 | 1065 | 3.5 | 3727.5 | 0 | Individual | 4.286% | 0% |  |  | 4.286% | 0% | TRUE |  |  | 4.286% | 0%
UKIAH_7_LAKEMN | Hydro | 2024 | summer | 39265 | 5.8917 | 0 | 765 | 3.5 | 2677.5 | 0 | Individual | 0.22% | 0% |  |  | 0.22% | 0% | TRUE |  |  | 0.22% | 0%
VALLEY_5_PERRIS | Hydro | 2022 | nonsummer | 30317 | 8376.7 | 0 | 1060 | 7.94 | 8416.4 | 0 | Individual | 99.53% | 0% |  |  | 99.53% | 0% | TRUE |  |  | 99.53% | 0%
VALLEY_5_PERRIS | Hydro | 2022 | summer | 30317 | 6074.1 | 0 | 765 | 7.94 | 6074.1 | 0 | Individual | 100% | 0% |  |  | 100% | 0% | TRUE |  |  | 100% | 0%
VALLEY_5_PERRIS | Hydro | 2023 | nonsummer | 30317 | 7379.1407 | 0 | 1060 | 7.94 | 8416.4 | 0 | Individual | 87.68% | 0% |  |  | 87.68% | 0% | TRUE |  |  | 87.68% | 0%
VALLEY_5_PERRIS | Hydro | 2023 | summer | 30317 | 5814.4 | 0 | 765 | 7.94 | 6074.1 | 0 | Individual | 95.72% | 0% |  |  | 95.72% | 0% | TRUE |  |  | 95.72% | 0%
VALLEY_5_PERRIS | Hydro | 2024 | nonsummer | 30317 | 0 | 0 | 1065 | 7.94 | 8456.1 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
VALLEY_5_PERRIS | Hydro | 2024 | summer | 30317 | 0 | 0 | 765 | 7.94 | 6074.1 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
VILLPK_2_VALLYV | Hydro | 2022 | nonsummer | 31048 | 4325.5 | 0 | 1060 | 4.1 | 4346 | 0 | Individual | 99.53% | 0% |  |  | 99.53% | 0% | TRUE |  |  | 99.53% | 0%
VILLPK_2_VALLYV | Hydro | 2022 | summer | 31048 | 2921.5 | 0 | 765 | 4.1 | 3136.5 | 0 | Individual | 93.15% | 0% |  |  | 93.15% | 0% | TRUE |  |  | 93.15% | 0%
VILLPK_2_VALLYV | Hydro | 2023 | nonsummer | 31048 | 4325.5 | 0 | 1060 | 4.1 | 4346 | 0 | Individual | 99.53% | 0% |  |  | 99.53% | 0% | TRUE |  |  | 99.53% | 0%
VILLPK_2_VALLYV | Hydro | 2023 | summer | 31048 | 3136.5 | 0 | 765 | 4.1 | 3136.5 | 0 | Individual | 100% | 0% |  |  | 100% | 0% | TRUE |  |  | 100% | 0%
VILLPK_2_VALLYV | Hydro | 2024 | nonsummer | 31048 | 0 | 0 | 1065 | 4.1 | 4366.5 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
VILLPK_2_VALLYV | Hydro | 2024 | summer | 31048 | 0 | 0 | 765 | 4.1 | 3136.5 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
VILLPK_6_MWDYOR | Hydro | 2022 | nonsummer | 29587 | 25.5 | 0 | 1060 | 5.1 | 5406 | 0 | Individual | 0.4717% | 0% |  |  | 0.4717% | 0% | TRUE |  |  | 0.4717% | 0%
VILLPK_6_MWDYOR | Hydro | 2022 | summer | 29587 | 0 | 0 | 765 | 5.1 | 3901.5 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
VILLPK_6_MWDYOR | Hydro | 2023 | nonsummer | 29587 | 49.3 | 0 | 1060 | 5.1 | 5406 | 0 | Individual | 0.9119% | 0% |  |  | 0.9119% | 0% | TRUE |  |  | 0.9119% | 0%
VILLPK_6_MWDYOR | Hydro | 2023 | summer | 29587 | 0 | 72.76 | 765 | 5.1 | 3901.5 | 0 | Individual | 0% | 1.865% |  |  | 0% | 1.865% | TRUE |  |  | 0% | 1.865%
VILLPK_6_MWDYOR | Hydro | 2024 | nonsummer | 29587 | 0 | 0 | 1065 | 5.1 | 5431.5 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
VILLPK_6_MWDYOR | Hydro | 2024 | summer | 29587 | 0 | 0 | 765 | 5.1 | 3901.5 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
WARNE_2_UNIT | Hydro | 2022 | nonsummer | 29952 | 104.5 | 0 | 1060 | 76 | 80560 | 0 | Individual | 0.1297% | 0% |  |  | 0.1297% | 0% | TRUE |  |  | 0.1297% | 0%
WARNE_2_UNIT | Hydro | 2022 | summer | 29952 | 0 | 0 | 765 | 76 | 58140 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
WARNE_2_UNIT | Hydro | 2023 | nonsummer | 29952 | 253.3333 | 0 | 1060 | 76 | 80560 | 0 | Individual | 0.3145% | 0% |  |  | 0.3145% | 0% | TRUE |  |  | 0.3145% | 0%
WARNE_2_UNIT | Hydro | 2023 | summer | 29952 | 1604.8667 | 0 | 765 | 76 | 58140 | 0 | Individual | 2.76% | 0% |  |  | 2.76% | 0% | TRUE |  |  | 2.76% | 0%
WARNE_2_UNIT | Hydro | 2024 | nonsummer | 29952 | 1686.9 | 0 | 1065 | 76 | 80940 | 0 | Individual | 2.084% | 0% |  |  | 2.084% | 0% | TRUE |  |  | 2.084% | 0%
WARNE_2_UNIT | Hydro | 2024 | summer | 29952 | 659.6333 | 0 | 765 | 76 | 58140 | 0 | Individual | 1.135% | 0% |  |  | 1.135% | 0% | TRUE |  |  | 1.135% | 0%
WDLEAF_7_UNIT 1 | Hydro | 2022 | nonsummer | 23012 | 1332 | 0 | 1060 | 60 | 63600 | 0 | Individual | 2.094% | 0% |  |  | 2.094% | 0% | TRUE |  |  | 2.094% | 0%
WDLEAF_7_UNIT 1 | Hydro | 2022 | summer | 23012 | 115.9167 | 0 | 765 | 60 | 45900 | 0 | Individual | 0.2525% | 0% |  |  | 0.2525% | 0% | TRUE |  |  | 0.2525% | 0%
WDLEAF_7_UNIT 1 | Hydro | 2023 | nonsummer | 23012 | 6817.75 | 0 | 1060 | 60 | 63600 | 0 | Individual | 10.72% | 0% |  |  | 10.72% | 0% | TRUE |  |  | 10.72% | 0%
WDLEAF_7_UNIT 1 | Hydro | 2023 | summer | 23012 | 517 | 0 | 765 | 60 | 45900 | 0 | Individual | 1.126% | 0% |  |  | 1.126% | 0% | TRUE |  |  | 1.126% | 0%
WDLEAF_7_UNIT 1 | Hydro | 2024 | nonsummer | 23012 | 2716.55 | 0 | 1065 | 60 | 63900 | 0 | Individual | 4.251% | 0% |  |  | 4.251% | 0% | TRUE |  |  | 4.251% | 0%
WDLEAF_7_UNIT 1 | Hydro | 2024 | summer | 23012 | 175 | 0 | 765 | 60 | 45900 | 0 | Individual | 0.3813% | 0% |  |  | 0.3813% | 0% | TRUE |  |  | 0.3813% | 0%
WESTPT_2_UNIT | Hydro | 2022 | nonsummer | 17533 | 196.74 | 0 | 1060 | 14 | 14840 | 0 | Individual | 1.326% | 0% |  |  | 1.326% | 0% | TRUE |  |  | 1.326% | 0%
WESTPT_2_UNIT | Hydro | 2022 | summer | 17533 | 37.8333 | 7 | 765 | 14 | 10710 | 0 | Individual | 0.3533% | 0.06536% |  |  | 0.3533% | 0.06536% | TRUE |  |  | 0.3533% | 0.06536%
WESTPT_2_UNIT | Hydro | 2023 | nonsummer | 17533 | 223 | 0 | 1060 | 14 | 14840 | 0 | Individual | 1.503% | 0% |  |  | 1.503% | 0% | TRUE |  |  | 1.503% | 0%
WESTPT_2_UNIT | Hydro | 2023 | summer | 17533 | 155.4833 | 0 | 765 | 14 | 10710 | 0 | Individual | 1.452% | 0% |  |  | 1.452% | 0% | TRUE |  |  | 1.452% | 0%
WESTPT_2_UNIT | Hydro | 2024 | nonsummer | 17533 | 38.3167 | 0 | 1065 | 14 | 14910 | 0 | Individual | 0.257% | 0% |  |  | 0.257% | 0% | TRUE |  |  | 0.257% | 0%
WESTPT_2_UNIT | Hydro | 2024 | summer | 17533 | 0 | 0 | 765 | 14 | 10710 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
WISE_1_UNIT 1 | Hydro | 2022 | nonsummer | 6211 | 4057.3667 | 0 | 1060 | 14.5 | 15370 | 0 | Individual | 26.4% | 0% |  |  | 26.4% | 0% | TRUE |  |  | 26.4% | 0%
WISE_1_UNIT 1 | Hydro | 2022 | summer | 6211 | 1291.4708 | 0 | 765 | 14.5 | 11092.5 | 0 | Individual | 11.64% | 0% |  |  | 11.64% | 0% | TRUE |  |  | 11.64% | 0%
WISE_1_UNIT 1 | Hydro | 2023 | nonsummer | 6211 | 1511.5983 | 0 | 1060 | 14.5 | 15370 | 0 | Individual | 9.835% | 0% |  |  | 9.835% | 0% | TRUE |  |  | 9.835% | 0%
WISE_1_UNIT 1 | Hydro | 2023 | summer | 6211 | 676.88 | 0 | 765 | 14.5 | 11092.5 | 0 | Individual | 6.102% | 0% |  |  | 6.102% | 0% | TRUE |  |  | 6.102% | 0%
WISE_1_UNIT 1 | Hydro | 2024 | nonsummer | 6211 | 5295.9358 | 0 | 1065 | 14.5 | 15442.5 | 0 | Individual | 34.29% | 0% |  |  | 34.29% | 0% | TRUE |  |  | 34.29% | 0%
WISE_1_UNIT 1 | Hydro | 2024 | summer | 6211 | 6586.9033 | 0 | 765 | 14.5 | 11092.5 | 0 | Individual | 59.38% | 0% |  |  | 59.38% | 0% | TRUE |  |  | 59.38% | 0%
WISE_1_UNIT 2 | Hydro | 2022 | nonsummer | 31413 | 3296 | 0 | 1060 | 3.2 | 3392 | 0 | Individual | 97.17% | 0% |  |  | 97.17% | 0% | TRUE |  |  | 97.17% | 0%
WISE_1_UNIT 2 | Hydro | 2022 | summer | 31413 | 2448 | 0 | 765 | 3.2 | 2448 | 0 | Individual | 100% | 0% |  |  | 100% | 0% | TRUE |  |  | 100% | 0%
WISE_1_UNIT 2 | Hydro | 2023 | nonsummer | 31413 | 3371.2 | 0 | 1060 | 3.2 | 3392 | 0 | Individual | 99.39% | 0% |  |  | 99.39% | 0% | TRUE |  |  | 99.39% | 0%
WISE_1_UNIT 2 | Hydro | 2023 | summer | 31413 | 2448 | 0 | 765 | 3.2 | 2448 | 0 | Individual | 100% | 0% |  |  | 100% | 0% | TRUE |  |  | 100% | 0%
WISE_1_UNIT 2 | Hydro | 2024 | nonsummer | 31413 | 2416 | 0 | 1065 | 3.2 | 3408 | 0 | Individual | 70.89% | 0% |  |  | 70.89% | 0% | TRUE |  |  | 70.89% | 0%
WISE_1_UNIT 2 | Hydro | 2024 | summer | 31413 | 2176 | 0 | 765 | 3.2 | 2448 | 0 | Individual | 88.89% | 0% |  |  | 88.89% | 0% | TRUE |  |  | 88.89% | 0%
WISHON_6_UNITS | Hydro | 2022 | nonsummer | 3654 | 9922.0433 | 0 | 1060 | 18.4 | 19504 | 0 | Individual | 50.87% | 0% |  |  | 50.87% | 0% | TRUE |  |  | 50.87% | 0%
WISHON_6_UNITS | Hydro | 2022 | summer | 3654 | 5867.8917 | 0 | 765 | 18.4 | 14076 | 0 | Individual | 41.69% | 0% |  |  | 41.69% | 0% | TRUE |  |  | 41.69% | 0%
WISHON_6_UNITS | Hydro | 2023 | nonsummer | 3654 | 8872.9683 | 0 | 1060 | 18.4 | 19504 | 0 | Individual | 45.49% | 0% |  |  | 45.49% | 0% | TRUE |  |  | 45.49% | 0%
WISHON_6_UNITS | Hydro | 2023 | summer | 3654 | 8105.6067 | 0 | 765 | 18.4 | 14076 | 0 | Individual | 57.58% | 0% |  |  | 57.58% | 0% | TRUE |  |  | 57.58% | 0%
WISHON_6_UNITS | Hydro | 2024 | nonsummer | 3654 | 11999.405 | 0 | 1065 | 18.4 | 19596 | 0 | Individual | 61.23% | 0% |  |  | 61.23% | 0% | TRUE |  |  | 61.23% | 0%
WISHON_6_UNITS | Hydro | 2024 | summer | 3654 | 4112.48 | 0 | 765 | 18.4 | 14076 | 0 | Individual | 29.22% | 0% |  |  | 29.22% | 0% | TRUE |  |  | 29.22% | 0%
DIABLO_7_UNIT 1 | Nuclear | 2022 | nonsummer | 1985-01-01 | 21490 | 0 | 1060 | 1150 | 1219000 | 0 | Individual | 1.763% | 0% |  |  | 1.763% | 0% | TRUE |  |  | 1.763% | 0%
DIABLO_7_UNIT 1 | Nuclear | 2022 | summer | 1985-01-01 | 0 | 0 | 765 | 1150 | 879750 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
DIABLO_7_UNIT 1 | Nuclear | 2023 | nonsummer | 1985-01-01 | 20388.3333 | 0 | 1060 | 1150 | 1219000 | 0 | Individual | 1.673% | 0% |  |  | 1.673% | 0% | TRUE |  |  | 1.673% | 0%
DIABLO_7_UNIT 1 | Nuclear | 2023 | summer | 1985-01-01 | 10965.5 | 0 | 765 | 1150 | 879750 | 0 | Individual | 1.246% | 0% |  |  | 1.246% | 0% | TRUE |  |  | 1.246% | 0%
DIABLO_7_UNIT 1 | Nuclear | 2024 | nonsummer | 1985-01-01 | 0 | 0 | 1065 | 1150 | 1224750 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
DIABLO_7_UNIT 1 | Nuclear | 2024 | summer | 1985-01-01 | 10495.1333 | 0 | 765 | 1150 | 879750 | 0 | Individual | 1.193% | 0% |  |  | 1.193% | 0% | TRUE |  |  | 1.193% | 0%
DIABLO_7_UNIT 2 | Nuclear | 2022 | nonsummer | 1986-01-01 | 25561.6667 | 0 | 1060 | 1150 | 1219000 | 0 | Individual | 2.097% | 0% |  |  | 2.097% | 0% | TRUE |  |  | 2.097% | 0%
DIABLO_7_UNIT 2 | Nuclear | 2022 | summer | 1986-01-01 | 0 | 0 | 765 | 1150 | 879750 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
DIABLO_7_UNIT 2 | Nuclear | 2023 | nonsummer | 1986-01-01 | 17792.8 | 5549.6667 | 1060 | 1150 | 1219000 | 0 | Individual | 1.46% | 0.4553% |  |  | 1.46% | 0.4553% | TRUE |  |  | 1.46% | 0.4553%
DIABLO_7_UNIT 2 | Nuclear | 2023 | summer | 1986-01-01 | 6671 | 0 | 765 | 1150 | 879750 | 0 | Individual | 0.7583% | 0% |  |  | 0.7583% | 0% | TRUE |  |  | 0.7583% | 0%
DIABLO_7_UNIT 2 | Nuclear | 2024 | nonsummer | 1986-01-01 | 13620 | 0 | 1065 | 1150 | 1224750 | 0 | Individual | 1.112% | 0% |  |  | 1.112% | 0% | TRUE |  |  | 1.112% | 0%
DIABLO_7_UNIT 2 | Nuclear | 2024 | summer | 1986-01-01 | 0 | 0 | 765 | 1150 | 879750 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
PVERDE_5_SCEDYN | Nuclear | 2022 | nonsummer | 2009-03-31 | 14865 | 0 | 1060 | 635 | 673100 | 0 | Individual | 2.208% | 0% |  |  | 2.208% | 0% | TRUE |  |  | 2.208% | 0%
PVERDE_5_SCEDYN | Nuclear | 2022 | summer | 2009-03-31 | 0 | 0 | 765 | 635 | 485775 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
PVERDE_5_SCEDYN | Nuclear | 2023 | nonsummer | 2009-03-31 | 27503.1833 | 0 | 1060 | 635 | 673100 | 0 | Individual | 4.086% | 0% |  |  | 4.086% | 0% | TRUE |  |  | 4.086% | 0%
PVERDE_5_SCEDYN | Nuclear | 2023 | summer | 2009-03-31 | 9916.6667 | 150 | 765 | 635 | 485775 | 0 | Individual | 2.041% | 0.03088% |  |  | 2.041% | 0.03088% | TRUE |  |  | 2.041% | 0.03088%
PVERDE_5_SCEDYN | Nuclear | 2024 | nonsummer | 2009-03-31 | 20956.5 | 0 | 1065 | 635 | 676275 | 0 | Individual | 3.099% | 0% |  |  | 3.099% | 0% | TRUE |  |  | 3.099% | 0%
PVERDE_5_SCEDYN | Nuclear | 2024 | summer | 2009-03-31 | 222 | 2071.8667 | 765 | 635 | 485775 | 0 | Individual | 0.0457% | 0.4265% |  |  | 0.0457% | 0.4265% | TRUE |  |  | 0.0457% | 0.4265%
ALMASL_2_AL6BT6 | Paired_BattStorage | 2022 | nonsummer | 44739 | 384 | 0 | 305 | 50 | 15250 | 755 | Blended | 2.518% | 0% | 7.043% | 0% | 5.741% | 0% | TRUE | 7.043% | 0% | 5.741% | 0%
ALMASL_2_AL6BT6 | Paired_BattStorage | 2022 | summer | 44739 | 2653.6 | 0 | 635 | 50 | 31750 | 130 | Blended | 8.358% | 0% | 14.17% | 0% | 9.346% | 0% | TRUE | 14.17% | 0% | 9.346% | 0%
ALMASL_2_AL6BT6 | Paired_BattStorage | 2023 | nonsummer | 44739 | 2507.85 | 0 | 1060 | 50 | 53000 | 0 | Individual | 4.732% | 0% |  |  | 4.732% | 0% | TRUE |  |  | 4.732% | 0%
ALMASL_2_AL6BT6 | Paired_BattStorage | 2023 | summer | 44739 | 11015 | 0 | 765 | 50 | 38250 | 0 | Individual | 28.8% | 0% |  |  | 28.8% | 0% | TRUE |  |  | 28.8% | 0%
ALMASL_2_AL6BT6 | Paired_BattStorage | 2024 | nonsummer | 44739 | 5926.9467 | 0 | 1065 | 50 | 53250 | 0 | Individual | 11.13% | 0% |  |  | 11.13% | 0% | TRUE |  |  | 11.13% | 0%
ALMASL_2_AL6BT6 | Paired_BattStorage | 2024 | summer | 44739 | 4403.8958 | 0 | 765 | 50 | 38250 | 0 | Individual | 11.51% | 0% |  |  | 11.51% | 0% | TRUE |  |  | 11.51% | 0%
BIGSKY_2_AS2BT1 | Paired_BattStorage | 2022 | nonsummer | 44806 | 1880.7833 | 0 | 305 | 127 | 38735 | 755 | Blended | 4.856% | 0% | 7.043% | 0% | 6.413% | 0% | TRUE | 7.043% | 0% | 6.413% | 0%
BIGSKY_2_AS2BT1 | Paired_BattStorage | 2022 | summer | 44806 | 1058.6333 | 0 | 300 | 127 | 38100 | 465 | Blended | 2.779% | 0% | 14.17% | 0% | 9.705% | 0% | TRUE | 14.17% | 0% | 9.705% | 0%
BIGSKY_2_AS2BT1 | Paired_BattStorage | 2023 | nonsummer | 44806 | 5074.35 | 0 | 1060 | 127 | 134620 | 0 | Individual | 3.769% | 0% |  |  | 3.769% | 0% | TRUE |  |  | 3.769% | 0%
BIGSKY_2_AS2BT1 | Paired_BattStorage | 2023 | summer | 44806 | 921.0833 | 0 | 765 | 127 | 97155 | 0 | Individual | 0.9481% | 0% |  |  | 0.9481% | 0% | TRUE |  |  | 0.9481% | 0%
BIGSKY_2_AS2BT1 | Paired_BattStorage | 2024 | nonsummer | 44806 | 208.7 | 0 | 1065 | 127 | 135255 | 0 | Individual | 0.1543% | 0% |  |  | 0.1543% | 0% | TRUE |  |  | 0.1543% | 0%
BIGSKY_2_AS2BT1 | Paired_BattStorage | 2024 | summer | 44806 | 0 | 0 | 765 | 127 | 97155 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
BIGSKY_2_ASLBT2 | Paired_BattStorage | 2022 | nonsummer | 44772 | 1581.25 | 0 | 305 | 100 | 30500 | 755 | Blended | 5.184% | 0% | 7.043% | 0% | 6.508% | 0% | TRUE | 7.043% | 0% | 6.508% | 0%
BIGSKY_2_ASLBT2 | Paired_BattStorage | 2022 | summer | 44772 | 3301.95 | 0 | 470 | 100 | 47000 | 295 | Blended | 7.025% | 0% | 14.17% | 0% | 9.782% | 0% | TRUE | 14.17% | 0% | 9.782% | 0%
BIGSKY_2_ASLBT2 | Paired_BattStorage | 2023 | nonsummer | 44772 | 2047.5 | 0 | 1060 | 100 | 106000 | 0 | Individual | 1.932% | 0% |  |  | 1.932% | 0% | TRUE |  |  | 1.932% | 0%
BIGSKY_2_ASLBT2 | Paired_BattStorage | 2023 | summer | 44772 | 402 | 0 | 765 | 100 | 76500 | 0 | Individual | 0.5255% | 0% |  |  | 0.5255% | 0% | TRUE |  |  | 0.5255% | 0%
BIGSKY_2_ASLBT2 | Paired_BattStorage | 2024 | nonsummer | 44772 | 542.0167 | 0 | 1065 | 100 | 106500 | 0 | Individual | 0.5089% | 0% |  |  | 0.5089% | 0% | TRUE |  |  | 0.5089% | 0%
BIGSKY_2_ASLBT2 | Paired_BattStorage | 2024 | summer | 44772 | 54.5 | 0 | 765 | 100 | 76500 | 0 | Individual | 0.07124% | 0% |  |  | 0.07124% | 0% | TRUE |  |  | 0.07124% | 0%
BLKCRK_2_GMCBT1 | Paired_BattStorage | 2022 | nonsummer | 44377 | 2903.6783 | 0 | 1060 | 230 | 243800 | 0 | Individual | 1.191% | 0% |  |  | 1.191% | 0% | TRUE |  |  | 1.191% | 0%
BLKCRK_2_GMCBT1 | Paired_BattStorage | 2022 | summer | 44377 | 13244.5245 | 0 | 765 | 230 | 175950 | 0 | Individual | 7.527% | 0% |  |  | 7.527% | 0% | TRUE |  |  | 7.527% | 0%
BLKCRK_2_GMCBT1 | Paired_BattStorage | 2023 | nonsummer | 44377 | 22673.5078 | 0 | 1060 | 230 | 243800 | 0 | Individual | 9.3% | 0% |  |  | 9.3% | 0% | TRUE |  |  | 9.3% | 0%
BLKCRK_2_GMCBT1 | Paired_BattStorage | 2023 | summer | 44377 | 38855.5822 | 0 | 765 | 230 | 175950 | 0 | Individual | 22.08% | 0% |  |  | 22.08% | 0% | TRUE |  |  | 22.08% | 0%
BLKCRK_2_GMCBT1 | Paired_BattStorage | 2024 | nonsummer | 44377 | 4184.8863 | 0 | 1065 | 230 | 244950 | 0 | Individual | 1.708% | 0% |  |  | 1.708% | 0% | TRUE |  |  | 1.708% | 0%
BLKCRK_2_GMCBT1 | Paired_BattStorage | 2024 | summer | 44377 | 1735.3128 | 0 | 765 | 230 | 175950 | 0 | Individual | 0.9863% | 0% |  |  | 0.9863% | 0% | TRUE |  |  | 0.9863% | 0%
BLM W_2_COSBT1 | Paired_BattStorage | 2022 | nonsummer | 44620 | 5043.49 | 0 | 770 | 60 | 46200 | 290 | Blended | 10.92% | 0% | 7.043% | 0% | 9.857% | 0% | TRUE | 7.043% | 0% | 9.857% | 0%
BLM W_2_COSBT1 | Paired_BattStorage | 2022 | summer | 44620 | 9248.081 | 0 | 765 | 60 | 45900 | 0 | Individual | 20.15% | 0% |  |  | 20.15% | 0% | TRUE |  |  | 20.15% | 0%
BLM W_2_COSBT1 | Paired_BattStorage | 2023 | nonsummer | 44620 | 5273.9038 | 0 | 1060 | 60 | 63600 | 0 | Individual | 8.292% | 0% |  |  | 8.292% | 0% | TRUE |  |  | 8.292% | 0%
BLM W_2_COSBT1 | Paired_BattStorage | 2023 | summer | 44620 | 7161.547 | 0 | 765 | 60 | 45900 | 0 | Individual | 15.6% | 0% |  |  | 15.6% | 0% | TRUE |  |  | 15.6% | 0%
BLM W_2_COSBT1 | Paired_BattStorage | 2024 | nonsummer | 44620 | 3664.9208 | 0 | 1065 | 60 | 63900 | 0 | Individual | 5.735% | 0% |  |  | 5.735% | 0% | TRUE |  |  | 5.735% | 0%
BLM W_2_COSBT1 | Paired_BattStorage | 2024 | summer | 44620 | 2429.2883 | 0 | 765 | 60 | 45900 | 0 | Individual | 5.293% | 0% |  |  | 5.293% | 0% | TRUE |  |  | 5.293% | 0%
CALFTN_2_CFSBT1 | Paired_BattStorage | 2022 | nonsummer | 44439 | 2100 | 0 | 1060 | 60 | 63600 | 0 | Individual | 3.302% | 0% |  |  | 3.302% | 0% | TRUE |  |  | 3.302% | 0%
CALFTN_2_CFSBT1 | Paired_BattStorage | 2022 | summer | 44439 | 591 | 0 | 765 | 60 | 45900 | 0 | Individual | 1.288% | 0% |  |  | 1.288% | 0% | TRUE |  |  | 1.288% | 0%
CALFTN_2_CFSBT1 | Paired_BattStorage | 2023 | nonsummer | 44439 | 3975.2 | 0 | 1060 | 60 | 63600 | 0 | Individual | 6.25% | 0% |  |  | 6.25% | 0% | TRUE |  |  | 6.25% | 0%
CALFTN_2_CFSBT1 | Paired_BattStorage | 2023 | summer | 44439 | 325 | 0 | 765 | 60 | 45900 | 0 | Individual | 0.7081% | 0% |  |  | 0.7081% | 0% | TRUE |  |  | 0.7081% | 0%
CALFTN_2_CFSBT1 | Paired_BattStorage | 2024 | nonsummer | 44439 | 2040 | 0 | 1065 | 60 | 63900 | 0 | Individual | 3.192% | 0% |  |  | 3.192% | 0% | TRUE |  |  | 3.192% | 0%
CALFTN_2_CFSBT1 | Paired_BattStorage | 2024 | summer | 44439 | 9222 | 0 | 765 | 60 | 45900 | 0 | Individual | 20.09% | 0% |  |  | 20.09% | 0% | TRUE |  |  | 20.09% | 0%
CENTPD_2_BMSX2 | Paired_BattStorage | 2022 | nonsummer | 44916 | 0 | 0 | 55 | 112 | 6160 | 1005 | Blended | 0% | 0% | 7.043% | 0% | 6.677% | 0% | TRUE | 7.043% | 0% | 6.677% | 0%
CENTPD_2_BMSX2 | Paired_BattStorage | 2022 | summer | 44916 | 0 | 0 | 0 | 112 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
CENTPD_2_BMSX2 | Paired_BattStorage | 2023 | nonsummer | 44916 | 14505.8333 | 0 | 1060 | 112 | 118720 | 0 | Individual | 12.22% | 0% |  |  | 12.22% | 0% | TRUE |  |  | 12.22% | 0%
CENTPD_2_BMSX2 | Paired_BattStorage | 2023 | summer | 44916 | 2483.7333 | 0 | 765 | 112 | 85680 | 0 | Individual | 2.899% | 0% |  |  | 2.899% | 0% | TRUE |  |  | 2.899% | 0%
CENTPD_2_BMSX2 | Paired_BattStorage | 2024 | nonsummer | 44916 | 6592.5 | 0 | 1065 | 112 | 119280 | 0 | Individual | 5.527% | 0% |  |  | 5.527% | 0% | TRUE |  |  | 5.527% | 0%
CENTPD_2_BMSX2 | Paired_BattStorage | 2024 | summer | 44916 | 2193 | 0 | 765 | 112 | 85680 | 0 | Individual | 2.56% | 0% |  |  | 2.56% | 0% | TRUE |  |  | 2.56% | 0%
CHESTN_2_CHWBX2 | Paired_BattStorage | 2022 | nonsummer | 45274 | 0 | 0 | 0 | 135 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
CHESTN_2_CHWBX2 | Paired_BattStorage | 2022 | summer | 45274 | 0 | 0 | 0 | 135 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
CHESTN_2_CHWBX2 | Paired_BattStorage | 2023 | nonsummer | 45274 | 985.5 | 0 | 90 | 135 | 12150 | 970 | Blended | 8.111% | 0% | 9.571% | 0% | 9.447% | 0% | TRUE | 9.571% | 0% | 9.447% | 0%
CHESTN_2_CHWBX2 | Paired_BattStorage | 2023 | summer | 45274 | 0 | 0 | 0 | 135 | 0 | 765 | Group |  |  | 14.95% | 0% | 14.95% | 0% | TRUE | 14.95% | 0% | 14.95% | 0%
CHESTN_2_CHWBX2 | Paired_BattStorage | 2024 | nonsummer | 45274 | 1047.6 | 0 | 1065 | 135 | 143775 | 0 | Individual | 0.7286% | 0% |  |  | 0.7286% | 0% | TRUE |  |  | 0.7286% | 0%
CHESTN_2_CHWBX2 | Paired_BattStorage | 2024 | summer | 45274 | 0 | 0 | 765 | 135 | 103275 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
CMBLND_2_DS2BT1 | Paired_BattStorage | 2022 | nonsummer | 45252 | 0 | 0 | 0 | 52 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
CMBLND_2_DS2BT1 | Paired_BattStorage | 2022 | summer | 45252 | 0 | 0 | 0 | 52 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
CMBLND_2_DS2BT1 | Paired_BattStorage | 2023 | nonsummer | 45252 | 1008.85 | 0 | 200 | 52 | 10400 | 860 | Blended | 9.7% | 0% | 9.571% | 0% | 9.595% | 0% | TRUE | 9.571% | 0% | 9.595% | 0%
CMBLND_2_DS2BT1 | Paired_BattStorage | 2023 | summer | 45252 | 0 | 0 | 0 | 52 | 0 | 765 | Group |  |  | 14.95% | 0% | 14.95% | 0% | TRUE | 14.95% | 0% | 14.95% | 0%
CMBLND_2_DS2BT1 | Paired_BattStorage | 2024 | nonsummer | 45252 | 1153.5167 | 0 | 1065 | 52 | 55380 | 0 | Individual | 2.083% | 0% |  |  | 2.083% | 0% | TRUE |  |  | 2.083% | 0%
CMBLND_2_DS2BT1 | Paired_BattStorage | 2024 | summer | 45252 | 1068.3 | 0 | 765 | 52 | 39780 | 0 | Individual | 2.686% | 0% |  |  | 2.686% | 0% | TRUE |  |  | 2.686% | 0%
CMBLND_2_DS2BT2 | Paired_BattStorage | 2022 | nonsummer | 45252 | 0 | 0 | 0 | 33 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
CMBLND_2_DS2BT2 | Paired_BattStorage | 2022 | summer | 45252 | 0 | 0 | 0 | 33 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
CMBLND_2_DS2BT2 | Paired_BattStorage | 2023 | nonsummer | 45252 | 14 | 0 | 200 | 33 | 6600 | 860 | Blended | 0.2121% | 0% | 9.571% | 0% | 7.805% | 0% | TRUE | 9.571% | 0% | 7.805% | 0%
CMBLND_2_DS2BT2 | Paired_BattStorage | 2023 | summer | 45252 | 0 | 0 | 0 | 33 | 0 | 765 | Group |  |  | 14.95% | 0% | 14.95% | 0% | TRUE | 14.95% | 0% | 14.95% | 0%
CMBLND_2_DS2BT2 | Paired_BattStorage | 2024 | nonsummer | 45252 | 54.1333 | 0 | 1065 | 33 | 35145 | 0 | Individual | 0.154% | 0% |  |  | 0.154% | 0% | TRUE |  |  | 0.154% | 0%
CMBLND_2_DS2BT2 | Paired_BattStorage | 2024 | summer | 45252 | 814.2833 | 0 | 765 | 33 | 25245 | 0 | Individual | 3.226% | 0% |  |  | 3.226% | 0% | TRUE |  |  | 3.226% | 0%
CMBLND_2_DS2BT3 | Paired_BattStorage | 2022 | nonsummer | 45261 | 0 | 0 | 0 | 46 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
CMBLND_2_DS2BT3 | Paired_BattStorage | 2022 | summer | 45261 | 0 | 0 | 0 | 46 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
CMBLND_2_DS2BT3 | Paired_BattStorage | 2023 | nonsummer | 45261 | 30 | 0 | 155 | 46 | 7130 | 905 | Blended | 0.4208% | 0% | 9.571% | 0% | 8.233% | 0% | TRUE | 9.571% | 0% | 8.233% | 0%
CMBLND_2_DS2BT3 | Paired_BattStorage | 2023 | summer | 45261 | 0 | 0 | 0 | 46 | 0 | 765 | Group |  |  | 14.95% | 0% | 14.95% | 0% | TRUE | 14.95% | 0% | 14.95% | 0%
CMBLND_2_DS2BT3 | Paired_BattStorage | 2024 | nonsummer | 45261 | 400 | 0 | 1065 | 46 | 48990 | 0 | Individual | 0.8165% | 0% |  |  | 0.8165% | 0% | TRUE |  |  | 0.8165% | 0%
CMBLND_2_DS2BT3 | Paired_BattStorage | 2024 | summer | 45261 | 994.6417 | 0 | 765 | 46 | 35190 | 0 | Individual | 2.826% | 0% |  |  | 2.826% | 0% | TRUE |  |  | 2.826% | 0%
DRACKR_2_DSUBT1 | Paired_BattStorage | 2022 | nonsummer | 44420 | 5330.55 | 0 | 1060 | 63 | 66780 | 0 | Individual | 7.982% | 0% |  |  | 7.982% | 0% | TRUE |  |  | 7.982% | 0%
DRACKR_2_DSUBT1 | Paired_BattStorage | 2022 | summer | 44420 | 12000.8997 | 0 | 765 | 63 | 48195 | 0 | Individual | 24.9% | 0% |  |  | 24.9% | 0% | TRUE |  |  | 24.9% | 0%
DRACKR_2_DSUBT1 | Paired_BattStorage | 2023 | nonsummer | 44420 | 9159.4867 | 0 | 1060 | 63 | 66780 | 0 | Individual | 13.72% | 0% |  |  | 13.72% | 0% | TRUE |  |  | 13.72% | 0%
DRACKR_2_DSUBT1 | Paired_BattStorage | 2023 | summer | 44420 | 10828.5703 | 0 | 765 | 63 | 48195 | 0 | Individual | 22.47% | 0% |  |  | 22.47% | 0% | TRUE |  |  | 22.47% | 0%
DRACKR_2_DSUBT1 | Paired_BattStorage | 2024 | nonsummer | 44420 | 2195.7135 | 0 | 1065 | 63 | 67095 | 0 | Individual | 3.273% | 0% |  |  | 3.273% | 0% | TRUE |  |  | 3.273% | 0%
DRACKR_2_DSUBT1 | Paired_BattStorage | 2024 | summer | 44420 | 670.9033 | 0 | 765 | 63 | 48195 | 0 | Individual | 1.392% | 0% |  |  | 1.392% | 0% | TRUE |  |  | 1.392% | 0%
DRACKR_2_DSUBT2 | Paired_BattStorage | 2022 | nonsummer | 44294 | 5513.5865 | 0 | 1060 | 115 | 121900 | 0 | Individual | 4.523% | 0% |  |  | 4.523% | 0% | TRUE |  |  | 4.523% | 0%
DRACKR_2_DSUBT2 | Paired_BattStorage | 2022 | summer | 44294 | 11410.7718 | 0 | 765 | 115 | 87975 | 0 | Individual | 12.97% | 0% |  |  | 12.97% | 0% | TRUE |  |  | 12.97% | 0%
DRACKR_2_DSUBT2 | Paired_BattStorage | 2023 | nonsummer | 44294 | 16649.868 | 0 | 1060 | 115 | 121900 | 0 | Individual | 13.66% | 0% |  |  | 13.66% | 0% | TRUE |  |  | 13.66% | 0%
DRACKR_2_DSUBT2 | Paired_BattStorage | 2023 | summer | 44294 | 9560.236 | 0 | 765 | 115 | 87975 | 0 | Individual | 10.87% | 0% |  |  | 10.87% | 0% | TRUE |  |  | 10.87% | 0%
DRACKR_2_DSUBT2 | Paired_BattStorage | 2024 | nonsummer | 44294 | 2995.5308 | 0 | 1065 | 115 | 122475 | 0 | Individual | 2.446% | 0% |  |  | 2.446% | 0% | TRUE |  |  | 2.446% | 0%
DRACKR_2_DSUBT2 | Paired_BattStorage | 2024 | summer | 44294 | 607.2957 | 0 | 765 | 115 | 87975 | 0 | Individual | 0.6903% | 0% |  |  | 0.6903% | 0% | TRUE |  |  | 0.6903% | 0%
DRACKR_2_DSUBT3 | Paired_BattStorage | 2022 | nonsummer | 44400 | 3585.5667 | 0 | 1060 | 115 | 121900 | 0 | Individual | 2.941% | 0% |  |  | 2.941% | 0% | TRUE |  |  | 2.941% | 0%
DRACKR_2_DSUBT3 | Paired_BattStorage | 2022 | summer | 44400 | 7309.1208 | 0 | 765 | 115 | 87975 | 0 | Individual | 8.308% | 0% |  |  | 8.308% | 0% | TRUE |  |  | 8.308% | 0%
DRACKR_2_DSUBT3 | Paired_BattStorage | 2023 | nonsummer | 44400 | 9667.939 | 0 | 1060 | 115 | 121900 | 0 | Individual | 7.931% | 0% |  |  | 7.931% | 0% | TRUE |  |  | 7.931% | 0%
DRACKR_2_DSUBT3 | Paired_BattStorage | 2023 | summer | 44400 | 17616.2803 | 0 | 765 | 115 | 87975 | 0 | Individual | 20.02% | 0% |  |  | 20.02% | 0% | TRUE |  |  | 20.02% | 0%
DRACKR_2_DSUBT3 | Paired_BattStorage | 2024 | nonsummer | 44400 | 1693.032 | 0 | 1065 | 115 | 122475 | 0 | Individual | 1.382% | 0% |  |  | 1.382% | 0% | TRUE |  |  | 1.382% | 0%
DRACKR_2_DSUBT3 | Paired_BattStorage | 2024 | summer | 44400 | 499.8403 | 0 | 765 | 115 | 87975 | 0 | Individual | 0.5682% | 0% |  |  | 0.5682% | 0% | TRUE |  |  | 0.5682% | 0%
DRACKR_2_DSUBT4 | Paired_BattStorage | 2022 | nonsummer | 44832 | 6115.5725 | 0 | 305 | 47 | 14335 | 755 | Blended | 42.66% | 0% | 7.043% | 0% | 17.29% | 0% | TRUE | 7.043% | 0% | 17.29% | 0%
DRACKR_2_DSUBT4 | Paired_BattStorage | 2022 | summer | 44832 | 3179.005 | 0 | 170 | 47 | 7990 | 595 | Blended | 39.79% | 0% | 14.17% | 0% | 19.87% | 0% | TRUE | 14.17% | 0% | 19.87% | 0%
DRACKR_2_DSUBT4 | Paired_BattStorage | 2023 | nonsummer | 44832 | 5841.2552 | 0 | 1060 | 47 | 49820 | 0 | Individual | 11.72% | 0% |  |  | 11.72% | 0% | TRUE |  |  | 11.72% | 0%
DRACKR_2_DSUBT4 | Paired_BattStorage | 2023 | summer | 44832 | 11880.7423 | 0 | 765 | 47 | 35955 | 0 | Individual | 33.04% | 0% |  |  | 33.04% | 0% | TRUE |  |  | 33.04% | 0%
DRACKR_2_DSUBT4 | Paired_BattStorage | 2024 | nonsummer | 44832 | 1112.8967 | 0 | 1065 | 47 | 50055 | 0 | Individual | 2.223% | 0% |  |  | 2.223% | 0% | TRUE |  |  | 2.223% | 0%
DRACKR_2_DSUBT4 | Paired_BattStorage | 2024 | summer | 44832 | 425.5932 | 0 | 765 | 47 | 35955 | 0 | Individual | 1.184% | 0% |  |  | 1.184% | 0% | TRUE |  |  | 1.184% | 0%
DSRTHV_2_DH2BT1 | Paired_BattStorage | 2022 | nonsummer | 44357 | 6090.2892 | 0 | 1060 | 35 | 37100 | 0 | Individual | 16.42% | 0% |  |  | 16.42% | 0% | TRUE |  |  | 16.42% | 0%
DSRTHV_2_DH2BT1 | Paired_BattStorage | 2022 | summer | 44357 | 5845.9238 | 0 | 765 | 35 | 26775 | 0 | Individual | 21.83% | 0% |  |  | 21.83% | 0% | TRUE |  |  | 21.83% | 0%
DSRTHV_2_DH2BT1 | Paired_BattStorage | 2023 | nonsummer | 44357 | 18031.3517 | 0 | 1060 | 35 | 37100 | 0 | Individual | 48.6% | 0% |  |  | 48.6% | 0% | TRUE |  |  | 48.6% | 0%
DSRTHV_2_DH2BT1 | Paired_BattStorage | 2023 | summer | 44357 | 20906.1503 | 0 | 765 | 35 | 26775 | 0 | Individual | 78.08% | 0% |  |  | 78.08% | 0% | TRUE |  |  | 78.08% | 0%
DSRTHV_2_DH2BT1 | Paired_BattStorage | 2024 | nonsummer | 44357 | 10877.5125 | 0 | 1065 | 35 | 37275 | 0 | Individual | 29.18% | 0% |  |  | 29.18% | 0% | TRUE |  |  | 29.18% | 0%
DSRTHV_2_DH2BT1 | Paired_BattStorage | 2024 | summer | 44357 | 4658.6133 | 0 | 765 | 35 | 26775 | 0 | Individual | 17.4% | 0% |  |  | 17.4% | 0% | TRUE |  |  | 17.4% | 0%
DSRTSN_2_DS2BX2 | Paired_BattStorage | 2022 | nonsummer | 45391 | 0 | 0 | 0 | 230 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
DSRTSN_2_DS2BX2 | Paired_BattStorage | 2022 | summer | 45391 | 0 | 0 | 0 | 230 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
DSRTSN_2_DS2BX2 | Paired_BattStorage | 2023 | nonsummer | 45391 | 0 | 0 | 0 | 230 | 0 | 1060 | Group |  |  | 9.571% | 0% | 9.571% | 0% | TRUE | 9.571% | 0% | 9.571% | 0%
DSRTSN_2_DS2BX2 | Paired_BattStorage | 2023 | summer | 45391 | 0 | 0 | 0 | 230 | 0 | 765 | Group |  |  | 14.95% | 0% | 14.95% | 0% | TRUE | 14.95% | 0% | 14.95% | 0%
DSRTSN_2_DS2BX2 | Paired_BattStorage | 2024 | nonsummer | 45391 | 4820.8317 | 0 | 570 | 230 | 131100 | 495 | Blended | 3.677% | 0% | 4.358% | 0.003109% | 3.994% | 0.001445% | TRUE | 4.358% | 0.003109% | 3.994% | 0.001445%
DSRTSN_2_DS2BX2 | Paired_BattStorage | 2024 | summer | 45391 | 3832.1213 | 0 | 765 | 230 | 175950 | 0 | Individual | 2.178% | 0% |  |  | 2.178% | 0% | TRUE |  |  | 2.178% | 0%
DSRTSN_2_DS2X2 | Paired_BattStorage | 2022 | nonsummer | 44801 | 282.7667 | 0 | 305 | 230 | 70150 | 755 | Blended | 0.4031% | 0% | 7.043% | 0% | 5.132% | 0% | TRUE | 7.043% | 0% | 5.132% | 0%
DSRTSN_2_DS2X2 | Paired_BattStorage | 2022 | summer | 44801 | 6599.1383 | 0 | 325 | 230 | 74750 | 440 | Blended | 8.828% | 0% | 14.17% | 0% | 11.9% | 0% | TRUE | 14.17% | 0% | 11.9% | 0%
DSRTSN_2_DS2X2 | Paired_BattStorage | 2023 | nonsummer | 44801 | 9551.0008 | 0 | 1060 | 230 | 243800 | 0 | Individual | 3.918% | 0% |  |  | 3.918% | 0% | TRUE |  |  | 3.918% | 0%
DSRTSN_2_DS2X2 | Paired_BattStorage | 2023 | summer | 44801 | 8493.271 | 0 | 765 | 230 | 175950 | 0 | Individual | 4.827% | 0% |  |  | 4.827% | 0% | TRUE |  |  | 4.827% | 0%
DSRTSN_2_DS2X2 | Paired_BattStorage | 2024 | nonsummer | 44801 | 8192.9858 | 0 | 1065 | 230 | 244950 | 0 | Individual | 3.345% | 0% |  |  | 3.345% | 0% | TRUE |  |  | 3.345% | 0%
DSRTSN_2_DS2X2 | Paired_BattStorage | 2024 | summer | 44801 | 1787.9522 | 0 | 765 | 230 | 175950 | 0 | Individual | 1.016% | 0% |  |  | 1.016% | 0% | TRUE |  |  | 1.016% | 0%
FIFTHS_2_FSSBT | Paired_BattStorage | 2022 | nonsummer | 45184 | 0 | 0 | 0 | 137 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
FIFTHS_2_FSSBT | Paired_BattStorage | 2022 | summer | 45184 | 0 | 0 | 0 | 137 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
FIFTHS_2_FSSBT | Paired_BattStorage | 2023 | nonsummer | 45184 | 0 | 0 | 305 | 137 | 41785 | 755 | Blended | 0% | 0% | 9.571% | 0% | 6.817% | 0% | TRUE | 9.571% | 0% | 6.817% | 0%
FIFTHS_2_FSSBT | Paired_BattStorage | 2023 | summer | 45184 | 1379 | 0 | 235 | 137 | 32195 | 530 | Blended | 4.283% | 0% | 14.95% | 0% | 11.68% | 0% | TRUE | 14.95% | 0% | 11.68% | 0%
FIFTHS_2_FSSBT | Paired_BattStorage | 2024 | nonsummer | 45184 | 0 | 0 | 1065 | 137 | 145905 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
FIFTHS_2_FSSBT | Paired_BattStorage | 2024 | summer | 45184 | 0 | 0 | 765 | 137 | 104805 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
FILIPPI_2_QZSBTX | Paired_BattStorage | 2022 | nonsummer | 45643 | 0 | 0 | 0 | 150 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
FILIPPI_2_QZSBTX | Paired_BattStorage | 2022 | summer | 45643 | 0 | 0 | 0 | 150 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
FILIPPI_2_QZSBTX | Paired_BattStorage | 2023 | nonsummer | 45643 | 0 | 0 | 0 | 150 | 0 | 1060 | Group |  |  | 9.571% | 0% | 9.571% | 0% | TRUE | 9.571% | 0% | 9.571% | 0%
FILIPPI_2_QZSBTX | Paired_BattStorage | 2023 | summer | 45643 | 0 | 0 | 0 | 150 | 0 | 765 | Group |  |  | 14.95% | 0% | 14.95% | 0% | TRUE | 14.95% | 0% | 14.95% | 0%
FILIPPI_2_QZSBTX | Paired_BattStorage | 2024 | nonsummer | 45643 | 0 | 0 | 75 | 150 | 11250 | 990 | Blended | 0% | 0% | 4.358% | 0.003109% | 4.051% | 0.00289% | TRUE | 4.358% | 0.003109% | 4.051% | 0.00289%
FILIPPI_2_QZSBTX | Paired_BattStorage | 2024 | summer | 45643 | 0 | 0 | 0 | 150 | 0 | 765 | Group |  |  | 3.923% | 0.0004805% | 3.923% | 0.0004805% | TRUE | 3.923% | 0.0004805% | 3.923% | 0.0004805%
GARLND_2_GARBT1 | Paired_BattStorage | 2022 | nonsummer | 44592 | 9718.45 | 0 | 910 | 88 | 80080 | 150 | Blended | 12.14% | 0% | 7.043% | 0% | 11.42% | 0% | TRUE | 7.043% | 0% | 11.42% | 0%
GARLND_2_GARBT1 | Paired_BattStorage | 2022 | summer | 44592 | 13914.0333 | 0 | 765 | 88 | 67320 | 0 | Individual | 20.67% | 0% |  |  | 20.67% | 0% | TRUE |  |  | 20.67% | 0%
GARLND_2_GARBT1 | Paired_BattStorage | 2023 | nonsummer | 44592 | 17145.8 | 0 | 1060 | 88 | 93280 | 0 | Individual | 18.38% | 0% |  |  | 18.38% | 0% | TRUE |  |  | 18.38% | 0%
GARLND_2_GARBT1 | Paired_BattStorage | 2023 | summer | 44592 | 15583.6833 | 0 | 765 | 88 | 67320 | 0 | Individual | 23.15% | 0% |  |  | 23.15% | 0% | TRUE |  |  | 23.15% | 0%
GARLND_2_GARBT1 | Paired_BattStorage | 2024 | nonsummer | 44592 | 11665.1 | 0 | 1065 | 88 | 93720 | 0 | Individual | 12.45% | 0% |  |  | 12.45% | 0% | TRUE |  |  | 12.45% | 0%
GARLND_2_GARBT1 | Paired_BattStorage | 2024 | summer | 44592 | 13751.4167 | 0 | 765 | 88 | 67320 | 0 | Individual | 20.43% | 0% |  |  | 20.43% | 0% | TRUE |  |  | 20.43% | 0%
GASKW1_2_GW2BT1 | Paired_BattStorage | 2022 | nonsummer | 45051 | 0 | 0 | 0 | 20 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
GASKW1_2_GW2BT1 | Paired_BattStorage | 2022 | summer | 45051 | 0 | 0 | 0 | 20 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
GASKW1_2_GW2BT1 | Paired_BattStorage | 2023 | nonsummer | 45051 | 681.57 | 0 | 440 | 20 | 8800 | 620 | Blended | 7.745% | 0% | 9.571% | 0% | 8.813% | 0% | TRUE | 9.571% | 0% | 8.813% | 0%
GASKW1_2_GW2BT1 | Paired_BattStorage | 2023 | summer | 45051 | 2573.295 | 0 | 765 | 20 | 15300 | 0 | Individual | 16.82% | 0% |  |  | 16.82% | 0% | TRUE |  |  | 16.82% | 0%
GASKW1_2_GW2BT1 | Paired_BattStorage | 2024 | nonsummer | 45051 | 5677.7763 | 0 | 1065 | 20 | 21300 | 0 | Individual | 26.66% | 0% |  |  | 26.66% | 0% | TRUE |  |  | 26.66% | 0%
GASKW1_2_GW2BT1 | Paired_BattStorage | 2024 | summer | 45051 | 5287.0273 | 0 | 765 | 20 | 15300 | 0 | Individual | 34.56% | 0% |  |  | 34.56% | 0% | TRUE |  |  | 34.56% | 0%
HIGHDS_2_H5SBT1 | Paired_BattStorage | 2022 | nonsummer | 44538 | 8147.7022 | 0 | 1060 | 50 | 53000 | 0 | Individual | 15.37% | 0% |  |  | 15.37% | 0% | TRUE |  |  | 15.37% | 0%
HIGHDS_2_H5SBT1 | Paired_BattStorage | 2022 | summer | 44538 | 5951.1972 | 0 | 765 | 50 | 38250 | 0 | Individual | 15.56% | 0% |  |  | 15.56% | 0% | TRUE |  |  | 15.56% | 0%
HIGHDS_2_H5SBT1 | Paired_BattStorage | 2023 | nonsummer | 44538 | 5739.8613 | 0 | 1060 | 50 | 53000 | 0 | Individual | 10.83% | 0% |  |  | 10.83% | 0% | TRUE |  |  | 10.83% | 0%
HIGHDS_2_H5SBT1 | Paired_BattStorage | 2023 | summer | 44538 | 4715.004 | 0 | 765 | 50 | 38250 | 0 | Individual | 12.33% | 0% |  |  | 12.33% | 0% | TRUE |  |  | 12.33% | 0%
HIGHDS_2_H5SBT1 | Paired_BattStorage | 2024 | nonsummer | 44538 | 6371.8578 | 0 | 1065 | 50 | 53250 | 0 | Individual | 11.97% | 0% |  |  | 11.97% | 0% | TRUE |  |  | 11.97% | 0%
HIGHDS_2_H5SBT1 | Paired_BattStorage | 2024 | summer | 44538 | 3079.4895 | 0 | 765 | 50 | 38250 | 0 | Individual | 8.051% | 0% |  |  | 8.051% | 0% | TRUE |  |  | 8.051% | 0%
KRAMER_1_R1BX3 | Paired_BattStorage | 2022 | nonsummer | 45108 | 0 | 0 | 0 | 75 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
KRAMER_1_R1BX3 | Paired_BattStorage | 2022 | summer | 45108 | 0 | 0 | 0 | 75 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
KRAMER_1_R1BX3 | Paired_BattStorage | 2023 | nonsummer | 45108 | 1033.3833 | 0 | 305 | 75 | 22875 | 755 | Blended | 4.518% | 0% | 9.571% | 0% | 8.117% | 0% | TRUE | 9.571% | 0% | 8.117% | 0%
KRAMER_1_R1BX3 | Paired_BattStorage | 2023 | summer | 45108 | 1003.4167 | 0 | 615 | 75 | 46125 | 150 | Blended | 2.175% | 0% | 14.95% | 0% | 4.681% | 0% | TRUE | 14.95% | 0% | 4.681% | 0%
KRAMER_1_R1BX3 | Paired_BattStorage | 2024 | nonsummer | 45108 | 4653.0833 | 0 | 1065 | 75 | 79875 | 0 | Individual | 5.825% | 0% |  |  | 5.825% | 0% | TRUE |  |  | 5.825% | 0%
KRAMER_1_R1BX3 | Paired_BattStorage | 2024 | summer | 45108 | 375 | 0 | 765 | 75 | 57375 | 0 | Individual | 0.6536% | 0% |  |  | 0.6536% | 0% | TRUE |  |  | 0.6536% | 0%
KRAMER_1_R2BX2 | Paired_BattStorage | 2022 | nonsummer | 45168 | 0 | 0 | 0 | 40 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
KRAMER_1_R2BX2 | Paired_BattStorage | 2022 | summer | 45168 | 0 | 0 | 0 | 40 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
KRAMER_1_R2BX2 | Paired_BattStorage | 2023 | nonsummer | 45168 | 57.672 | 0 | 305 | 40 | 12200 | 755 | Blended | 0.4727% | 0% | 9.571% | 0% | 6.953% | 0% | TRUE | 9.571% | 0% | 6.953% | 0%
KRAMER_1_R2BX2 | Paired_BattStorage | 2023 | summer | 45168 | 349.1 | 0 | 315 | 40 | 12600 | 450 | Blended | 2.771% | 0% | 14.95% | 0% | 9.937% | 0% | TRUE | 14.95% | 0% | 9.937% | 0%
KRAMER_1_R2BX2 | Paired_BattStorage | 2024 | nonsummer | 45168 | 659.3927 | 0 | 1065 | 40 | 42600 | 0 | Individual | 1.548% | 0% |  |  | 1.548% | 0% | TRUE |  |  | 1.548% | 0%
KRAMER_1_R2BX2 | Paired_BattStorage | 2024 | summer | 45168 | 481.844 | 0 | 765 | 40 | 30600 | 0 | Individual | 1.575% | 0% |  |  | 1.575% | 0% | TRUE |  |  | 1.575% | 0%
MCFLND_5_MFSBT1 | Paired_BattStorage | 2022 | nonsummer | 45282 | 0 | 0 | 0 | 100 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
MCFLND_5_MFSBT1 | Paired_BattStorage | 2022 | summer | 45282 | 0 | 0 | 0 | 100 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
MCFLND_5_MFSBT1 | Paired_BattStorage | 2023 | nonsummer | 45282 | 133.825 | 0 | 50 | 100 | 5000 | 1010 | Blended | 2.676% | 0% | 9.571% | 0% | 9.246% | 0% | TRUE | 9.571% | 0% | 9.246% | 0%
MCFLND_5_MFSBT1 | Paired_BattStorage | 2023 | summer | 45282 | 0 | 0 | 0 | 100 | 0 | 765 | Group |  |  | 14.95% | 0% | 14.95% | 0% | TRUE | 14.95% | 0% | 14.95% | 0%
MCFLND_5_MFSBT1 | Paired_BattStorage | 2024 | nonsummer | 45282 | 4543.9333 | 0 | 1065 | 100 | 106500 | 0 | Individual | 4.267% | 0% |  |  | 4.267% | 0% | TRUE |  |  | 4.267% | 0%
MCFLND_5_MFSBT1 | Paired_BattStorage | 2024 | summer | 45282 | 10037.1333 | 0 | 765 | 100 | 76500 | 0 | Individual | 13.12% | 0% |  |  | 13.12% | 0% | TRUE |  |  | 13.12% | 0%
MCFLND_5_MSCBT1 | Paired_BattStorage | 2022 | nonsummer | 45756 | 0 | 0 | 0 | 185 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
MCFLND_5_MSCBT1 | Paired_BattStorage | 2022 | summer | 45756 | 0 | 0 | 0 | 185 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
MCFLND_5_MSCBT1 | Paired_BattStorage | 2023 | nonsummer | 45756 | 0 | 0 | 0 | 185 | 0 | 1060 | Group |  |  | 9.571% | 0% | 9.571% | 0% | TRUE | 9.571% | 0% | 9.571% | 0%
MCFLND_5_MSCBT1 | Paired_BattStorage | 2023 | summer | 45756 | 0 | 0 | 0 | 185 | 0 | 765 | Group |  |  | 14.95% | 0% | 14.95% | 0% | TRUE | 14.95% | 0% | 14.95% | 0%
MCFLND_5_MSCBT1 | Paired_BattStorage | 2024 | nonsummer | 45756 | 0 | 0 | 0 | 185 | 0 | 1065 | Group |  |  | 4.358% | 0.003109% | 4.358% | 0.003109% | TRUE | 4.358% | 0.003109% | 4.358% | 0.003109%
MCFLND_5_MSCBT1 | Paired_BattStorage | 2024 | summer | 45756 | 0 | 0 | 0 | 185 | 0 | 765 | Group |  |  | 3.923% | 0.0004805% | 3.923% | 0.0004805% | TRUE | 3.923% | 0.0004805% | 3.923% | 0.0004805%
MSTANG_2_MTGBT1 | Paired_BattStorage | 2022 | nonsummer | 44501 | 1931.5 | 0 | 1060 | 75 | 79500 | 0 | Individual | 2.43% | 0% |  |  | 2.43% | 0% | TRUE |  |  | 2.43% | 0%
MSTANG_2_MTGBT1 | Paired_BattStorage | 2022 | summer | 44501 | 3272.2082 | 0 | 765 | 75 | 57375 | 0 | Individual | 5.703% | 0% |  |  | 5.703% | 0% | TRUE |  |  | 5.703% | 0%
MSTANG_2_MTGBT1 | Paired_BattStorage | 2023 | nonsummer | 44501 | 8619.5092 | 0 | 1060 | 75 | 79500 | 0 | Individual | 10.84% | 0% |  |  | 10.84% | 0% | TRUE |  |  | 10.84% | 0%
MSTANG_2_MTGBT1 | Paired_BattStorage | 2023 | summer | 44501 | 4349.9067 | 0 | 765 | 75 | 57375 | 0 | Individual | 7.582% | 0% |  |  | 7.582% | 0% | TRUE |  |  | 7.582% | 0%
MSTANG_2_MTGBT1 | Paired_BattStorage | 2024 | nonsummer | 44501 | 7998.3552 | 0 | 1065 | 75 | 79875 | 0 | Individual | 10.01% | 0% |  |  | 10.01% | 0% | TRUE |  |  | 10.01% | 0%
MSTANG_2_MTGBT1 | Paired_BattStorage | 2024 | summer | 44501 | 2950.4167 | 0 | 765 | 75 | 57375 | 0 | Individual | 5.142% | 0% |  |  | 5.142% | 0% | TRUE |  |  | 5.142% | 0%
OBERON_5_O1BBX2 | Paired_BattStorage | 2022 | nonsummer | 45233 | 0 | 0 | 0 | 125 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
OBERON_5_O1BBX2 | Paired_BattStorage | 2022 | summer | 45233 | 0 | 0 | 0 | 125 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
OBERON_5_O1BBX2 | Paired_BattStorage | 2023 | nonsummer | 45233 | 0 | 0 | 295 | 125 | 36875 | 765 | Blended | 0% | 0% | 9.571% | 0% | 6.907% | 0% | TRUE | 9.571% | 0% | 6.907% | 0%
OBERON_5_O1BBX2 | Paired_BattStorage | 2023 | summer | 45233 | 0 | 0 | 0 | 125 | 0 | 765 | Group |  |  | 14.95% | 0% | 14.95% | 0% | TRUE | 14.95% | 0% | 14.95% | 0%
OBERON_5_O1BBX2 | Paired_BattStorage | 2024 | nonsummer | 45233 | 3397.9167 | 0 | 1065 | 125 | 133125 | 0 | Individual | 2.552% | 0% |  |  | 2.552% | 0% | TRUE |  |  | 2.552% | 0%
OBERON_5_O1BBX2 | Paired_BattStorage | 2024 | summer | 45233 | 2089.1667 | 0 | 765 | 125 | 95625 | 0 | Individual | 2.185% | 0% |  |  | 2.185% | 0% | TRUE |  |  | 2.185% | 0%
OBERON_5_O2BBX2 | Paired_BattStorage | 2022 | nonsummer | 45233 | 0 | 0 | 0 | 125 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
OBERON_5_O2BBX2 | Paired_BattStorage | 2022 | summer | 45233 | 0 | 0 | 0 | 125 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
OBERON_5_O2BBX2 | Paired_BattStorage | 2023 | nonsummer | 45233 | 0 | 0 | 295 | 125 | 36875 | 765 | Blended | 0% | 0% | 9.571% | 0% | 6.907% | 0% | TRUE | 9.571% | 0% | 6.907% | 0%
OBERON_5_O2BBX2 | Paired_BattStorage | 2023 | summer | 45233 | 0 | 0 | 0 | 125 | 0 | 765 | Group |  |  | 14.95% | 0% | 14.95% | 0% | TRUE | 14.95% | 0% | 14.95% | 0%
OBERON_5_O2BBX2 | Paired_BattStorage | 2024 | nonsummer | 45233 | 955.5 | 0 | 1065 | 125 | 133125 | 0 | Individual | 0.7177% | 0% |  |  | 0.7177% | 0% | TRUE |  |  | 0.7177% | 0%
OBERON_5_O2BBX2 | Paired_BattStorage | 2024 | summer | 45233 | 9767.2 | 0 | 765 | 125 | 95625 | 0 | Individual | 10.21% | 0% |  |  | 10.21% | 0% | TRUE |  |  | 10.21% | 0%
PALSEL_6_PLSBT1 | Paired_BattStorage | 2022 | nonsummer | 45463 | 0 | 0 | 0 | 15 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
PALSEL_6_PLSBT1 | Paired_BattStorage | 2022 | summer | 45463 | 0 | 0 | 0 | 15 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
PALSEL_6_PLSBT1 | Paired_BattStorage | 2023 | nonsummer | 45463 | 0 | 0 | 0 | 15 | 0 | 1060 | Group |  |  | 9.571% | 0% | 9.571% | 0% | TRUE | 9.571% | 0% | 9.571% | 0%
PALSEL_6_PLSBT1 | Paired_BattStorage | 2023 | summer | 45463 | 0 | 0 | 0 | 15 | 0 | 765 | Group |  |  | 14.95% | 0% | 14.95% | 0% | TRUE | 14.95% | 0% | 14.95% | 0%
PALSEL_6_PLSBT1 | Paired_BattStorage | 2024 | nonsummer | 45463 | 96 | 0 | 305 | 15 | 4575 | 760 | Blended | 2.098% | 0% | 4.358% | 0.003109% | 3.711% | 0.002219% | TRUE | 4.358% | 0.003109% | 3.711% | 0.002219%
PALSEL_6_PLSBT1 | Paired_BattStorage | 2024 | summer | 45463 | 297.5167 | 0 | 670 | 15 | 10050 | 95 | Blended | 2.96% | 0% | 3.923% | 0.0004805% | 3.08% | 5.967e-05% | TRUE | 3.923% | 0.0004805% | 3.08% | 5.967e-05%
POLRIS_2_ASEBT1 | Paired_BattStorage | 2022 | nonsummer | 45289 | 0 | 0 | 0 | 28 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
POLRIS_2_ASEBT1 | Paired_BattStorage | 2022 | summer | 45289 | 0 | 0 | 0 | 28 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
POLRIS_2_ASEBT1 | Paired_BattStorage | 2023 | nonsummer | 45289 | 0 | 0 | 15 | 28 | 420 | 1045 | Blended | 0% | 0% | 9.571% | 0% | 9.435% | 0% | TRUE | 9.571% | 0% | 9.435% | 0%
POLRIS_2_ASEBT1 | Paired_BattStorage | 2023 | summer | 45289 | 0 | 0 | 0 | 28 | 0 | 765 | Group |  |  | 14.95% | 0% | 14.95% | 0% | TRUE | 14.95% | 0% | 14.95% | 0%
POLRIS_2_ASEBT1 | Paired_BattStorage | 2024 | nonsummer | 45289 | 1067.9333 | 0 | 1065 | 28 | 29820 | 0 | Individual | 3.581% | 0% |  |  | 3.581% | 0% | TRUE |  |  | 3.581% | 0%
POLRIS_2_ASEBT1 | Paired_BattStorage | 2024 | summer | 45289 | 2846.75 | 0 | 765 | 28 | 21420 | 0 | Individual | 13.29% | 0% |  |  | 13.29% | 0% | TRUE |  |  | 13.29% | 0%
POLRIS_2_ASRBT1 | Paired_BattStorage | 2022 | nonsummer | 45378 | 0 | 0 | 0 | 80 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
POLRIS_2_ASRBT1 | Paired_BattStorage | 2022 | summer | 45378 | 0 | 0 | 0 | 80 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
POLRIS_2_ASRBT1 | Paired_BattStorage | 2023 | nonsummer | 45378 | 0 | 0 | 0 | 80 | 0 | 1060 | Group |  |  | 9.571% | 0% | 9.571% | 0% | TRUE | 9.571% | 0% | 9.571% | 0%
POLRIS_2_ASRBT1 | Paired_BattStorage | 2023 | summer | 45378 | 0 | 0 | 0 | 80 | 0 | 765 | Group |  |  | 14.95% | 0% | 14.95% | 0% | TRUE | 14.95% | 0% | 14.95% | 0%
POLRIS_2_ASRBT1 | Paired_BattStorage | 2024 | nonsummer | 45378 | 9599.6667 | 0 | 635 | 80 | 50800 | 430 | Blended | 18.9% | 0% | 4.358% | 0.003109% | 13.03% | 0.001255% | TRUE | 4.358% | 0.003109% | 13.03% | 0.001255%
POLRIS_2_ASRBT1 | Paired_BattStorage | 2024 | summer | 45378 | 2404.5167 | 0 | 765 | 80 | 61200 | 0 | Individual | 3.929% | 0% |  |  | 3.929% | 0% | TRUE |  |  | 3.929% | 0%
PRIMM_2_SSSBT1 | Paired_BattStorage | 2022 | nonsummer | 45748 | 0 | 0 | 0 | 200 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
PRIMM_2_SSSBT1 | Paired_BattStorage | 2022 | summer | 45748 | 0 | 0 | 0 | 200 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
PRIMM_2_SSSBT1 | Paired_BattStorage | 2023 | nonsummer | 45748 | 0 | 0 | 0 | 200 | 0 | 1060 | Group |  |  | 9.571% | 0% | 9.571% | 0% | TRUE | 9.571% | 0% | 9.571% | 0%
PRIMM_2_SSSBT1 | Paired_BattStorage | 2023 | summer | 45748 | 0 | 0 | 0 | 200 | 0 | 765 | Group |  |  | 14.95% | 0% | 14.95% | 0% | TRUE | 14.95% | 0% | 14.95% | 0%
PRIMM_2_SSSBT1 | Paired_BattStorage | 2024 | nonsummer | 45748 | 0 | 0 | 0 | 200 | 0 | 1065 | Group |  |  | 4.358% | 0.003109% | 4.358% | 0.003109% | TRUE | 4.358% | 0.003109% | 4.358% | 0.003109%
PRIMM_2_SSSBT1 | Paired_BattStorage | 2024 | summer | 45748 | 0 | 0 | 0 | 200 | 0 | 765 | Group |  |  | 3.923% | 0.0004805% | 3.923% | 0.0004805% | TRUE | 3.923% | 0.0004805% | 3.923% | 0.0004805%
PROXSR_2_PS1BT1 | Paired_BattStorage | 2022 | nonsummer | 45390 | 0 | 0 | 0 | 40 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
PROXSR_2_PS1BT1 | Paired_BattStorage | 2022 | summer | 45390 | 0 | 0 | 0 | 40 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
PROXSR_2_PS1BT1 | Paired_BattStorage | 2023 | nonsummer | 45390 | 0 | 0 | 0 | 40 | 0 | 1060 | Group |  |  | 9.571% | 0% | 9.571% | 0% | TRUE | 9.571% | 0% | 9.571% | 0%
PROXSR_2_PS1BT1 | Paired_BattStorage | 2023 | summer | 45390 | 0 | 0 | 0 | 40 | 0 | 765 | Group |  |  | 14.95% | 0% | 14.95% | 0% | TRUE | 14.95% | 0% | 14.95% | 0%
PROXSR_2_PS1BT1 | Paired_BattStorage | 2024 | nonsummer | 45390 | 1727.9787 | 0 | 575 | 40 | 23000 | 490 | Blended | 7.513% | 0% | 4.358% | 0.003109% | 6.062% | 0.001431% | TRUE | 4.358% | 0.003109% | 6.062% | 0.001431%
PROXSR_2_PS1BT1 | Paired_BattStorage | 2024 | summer | 45390 | 683.0698 | 0 | 765 | 40 | 30600 | 0 | Individual | 2.232% | 0% |  |  | 2.232% | 0% | TRUE |  |  | 2.232% | 0%
PROXSR_2_PS1BT2 | Paired_BattStorage | 2022 | nonsummer | 45419 | 0 | 0 | 0 | 32 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
PROXSR_2_PS1BT2 | Paired_BattStorage | 2022 | summer | 45419 | 0 | 0 | 0 | 32 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
PROXSR_2_PS1BT2 | Paired_BattStorage | 2023 | nonsummer | 45419 | 0 | 0 | 0 | 32 | 0 | 1060 | Group |  |  | 9.571% | 0% | 9.571% | 0% | TRUE | 9.571% | 0% | 9.571% | 0%
PROXSR_2_PS1BT2 | Paired_BattStorage | 2023 | summer | 45419 | 0 | 0 | 0 | 32 | 0 | 765 | Group |  |  | 14.95% | 0% | 14.95% | 0% | TRUE | 14.95% | 0% | 14.95% | 0%
PROXSR_2_PS1BT2 | Paired_BattStorage | 2024 | nonsummer | 45419 | 423.3333 | 0 | 430 | 32 | 13760 | 635 | Blended | 3.077% | 0% | 4.358% | 0.003109% | 3.841% | 0.001854% | TRUE | 4.358% | 0.003109% | 3.841% | 0.001854%
PROXSR_2_PS1BT2 | Paired_BattStorage | 2024 | summer | 45419 | 0 | 0 | 765 | 32 | 24480 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
PROXSR_2_PS2BT3 | Paired_BattStorage | 2022 | nonsummer | 45393 | 0 | 0 | 0 | 90 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
PROXSR_2_PS2BT3 | Paired_BattStorage | 2022 | summer | 45393 | 0 | 0 | 0 | 90 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
PROXSR_2_PS2BT3 | Paired_BattStorage | 2023 | nonsummer | 45393 | 0 | 0 | 0 | 90 | 0 | 1060 | Group |  |  | 9.571% | 0% | 9.571% | 0% | TRUE | 9.571% | 0% | 9.571% | 0%
PROXSR_2_PS2BT3 | Paired_BattStorage | 2023 | summer | 45393 | 0 | 0 | 0 | 90 | 0 | 765 | Group |  |  | 14.95% | 0% | 14.95% | 0% | TRUE | 14.95% | 0% | 14.95% | 0%
PROXSR_2_PS2BT3 | Paired_BattStorage | 2024 | nonsummer | 45393 | 6213.513 | 0 | 560 | 90 | 50400 | 505 | Blended | 12.33% | 0% | 4.358% | 0.003109% | 8.549% | 0.001474% | TRUE | 4.358% | 0.003109% | 8.549% | 0.001474%
PROXSR_2_PS2BT3 | Paired_BattStorage | 2024 | summer | 45393 | 2649.511 | 0 | 765 | 90 | 68850 | 0 | Individual | 3.848% | 0% |  |  | 3.848% | 0% | TRUE |  |  | 3.848% | 0%
REXFRD_2_RSFBX2 | Paired_BattStorage | 2022 | nonsummer | 45709 | 0 | 0 | 0 | 240 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
REXFRD_2_RSFBX2 | Paired_BattStorage | 2022 | summer | 45709 | 0 | 0 | 0 | 240 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
REXFRD_2_RSFBX2 | Paired_BattStorage | 2023 | nonsummer | 45709 | 0 | 0 | 0 | 240 | 0 | 1060 | Group |  |  | 9.571% | 0% | 9.571% | 0% | TRUE | 9.571% | 0% | 9.571% | 0%
REXFRD_2_RSFBX2 | Paired_BattStorage | 2023 | summer | 45709 | 0 | 0 | 0 | 240 | 0 | 765 | Group |  |  | 14.95% | 0% | 14.95% | 0% | TRUE | 14.95% | 0% | 14.95% | 0%
REXFRD_2_RSFBX2 | Paired_BattStorage | 2024 | nonsummer | 45709 | 0 | 0 | 0 | 240 | 0 | 1065 | Group |  |  | 4.358% | 0.003109% | 4.358% | 0.003109% | TRUE | 4.358% | 0.003109% | 4.358% | 0.003109%
REXFRD_2_RSFBX2 | Paired_BattStorage | 2024 | summer | 45709 | 0 | 0 | 0 | 240 | 0 | 765 | Group |  |  | 3.923% | 0.0004805% | 3.923% | 0.0004805% | TRUE | 3.923% | 0.0004805% | 3.923% | 0.0004805%
RSMNDS_2_CSRBT1 | Paired_BattStorage | 2022 | nonsummer | 45870 | 0 | 0 | 0 | 15 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
RSMNDS_2_CSRBT1 | Paired_BattStorage | 2022 | summer | 45870 | 0 | 0 | 0 | 15 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
RSMNDS_2_CSRBT1 | Paired_BattStorage | 2023 | nonsummer | 45870 | 0 | 0 | 0 | 15 | 0 | 1060 | Group |  |  | 9.571% | 0% | 9.571% | 0% | TRUE | 9.571% | 0% | 9.571% | 0%
RSMNDS_2_CSRBT1 | Paired_BattStorage | 2023 | summer | 45870 | 0 | 0 | 0 | 15 | 0 | 765 | Group |  |  | 14.95% | 0% | 14.95% | 0% | TRUE | 14.95% | 0% | 14.95% | 0%
RSMNDS_2_CSRBT1 | Paired_BattStorage | 2024 | nonsummer | 45870 | 0 | 0 | 0 | 15 | 0 | 1065 | Group |  |  | 4.358% | 0.003109% | 4.358% | 0.003109% | TRUE | 4.358% | 0.003109% | 4.358% | 0.003109%
RSMNDS_2_CSRBT1 | Paired_BattStorage | 2024 | summer | 45870 | 0 | 0 | 0 | 15 | 0 | 765 | Group |  |  | 3.923% | 0.0004805% | 3.923% | 0.0004805% | TRUE | 3.923% | 0.0004805% | 3.923% | 0.0004805%
RSMNDS_2_CSRBT2 | Paired_BattStorage | 2022 | nonsummer | 45870 | 0 | 0 | 0 | 10 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
RSMNDS_2_CSRBT2 | Paired_BattStorage | 2022 | summer | 45870 | 0 | 0 | 0 | 10 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
RSMNDS_2_CSRBT2 | Paired_BattStorage | 2023 | nonsummer | 45870 | 0 | 0 | 0 | 10 | 0 | 1060 | Group |  |  | 9.571% | 0% | 9.571% | 0% | TRUE | 9.571% | 0% | 9.571% | 0%
RSMNDS_2_CSRBT2 | Paired_BattStorage | 2023 | summer | 45870 | 0 | 0 | 0 | 10 | 0 | 765 | Group |  |  | 14.95% | 0% | 14.95% | 0% | TRUE | 14.95% | 0% | 14.95% | 0%
RSMNDS_2_CSRBT2 | Paired_BattStorage | 2024 | nonsummer | 45870 | 0 | 0 | 0 | 10 | 0 | 1065 | Group |  |  | 4.358% | 0.003109% | 4.358% | 0.003109% | TRUE | 4.358% | 0.003109% | 4.358% | 0.003109%
RSMNDS_2_CSRBT2 | Paired_BattStorage | 2024 | summer | 45870 | 0 | 0 | 0 | 10 | 0 | 765 | Group |  |  | 3.923% | 0.0004805% | 3.923% | 0.0004805% | TRUE | 3.923% | 0.0004805% | 3.923% | 0.0004805%
RTEDDY_2_RWSBT1 | Paired_BattStorage | 2022 | nonsummer | 45414 | 0 | 0 | 0 | 30 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
RTEDDY_2_RWSBT1 | Paired_BattStorage | 2022 | summer | 45414 | 0 | 0 | 0 | 30 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
RTEDDY_2_RWSBT1 | Paired_BattStorage | 2023 | nonsummer | 45414 | 0 | 0 | 0 | 30 | 0 | 1060 | Group |  |  | 9.571% | 0% | 9.571% | 0% | TRUE | 9.571% | 0% | 9.571% | 0%
RTEDDY_2_RWSBT1 | Paired_BattStorage | 2023 | summer | 45414 | 0 | 0 | 0 | 30 | 0 | 765 | Group |  |  | 14.95% | 0% | 14.95% | 0% | TRUE | 14.95% | 0% | 14.95% | 0%
RTEDDY_2_RWSBT1 | Paired_BattStorage | 2024 | nonsummer | 45414 | 169.5 | 0 | 455 | 30 | 13650 | 610 | Blended | 1.242% | 0% | 4.358% | 0.003109% | 3.027% | 0.001781% | TRUE | 4.358% | 0.003109% | 3.027% | 0.001781%
RTEDDY_2_RWSBT1 | Paired_BattStorage | 2024 | summer | 45414 | 496.3833 | 0 | 765 | 30 | 22950 | 0 | Individual | 2.163% | 0% |  |  | 2.163% | 0% | TRUE |  |  | 2.163% | 0%
RTEDDY_2_RWSBT2 | Paired_BattStorage | 2022 | nonsummer | 45414 | 0 | 0 | 0 | 30 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
RTEDDY_2_RWSBT2 | Paired_BattStorage | 2022 | summer | 45414 | 0 | 0 | 0 | 30 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
RTEDDY_2_RWSBT2 | Paired_BattStorage | 2023 | nonsummer | 45414 | 0 | 0 | 0 | 30 | 0 | 1060 | Group |  |  | 9.571% | 0% | 9.571% | 0% | TRUE | 9.571% | 0% | 9.571% | 0%
RTEDDY_2_RWSBT2 | Paired_BattStorage | 2023 | summer | 45414 | 0 | 0 | 0 | 30 | 0 | 765 | Group |  |  | 14.95% | 0% | 14.95% | 0% | TRUE | 14.95% | 0% | 14.95% | 0%
RTEDDY_2_RWSBT2 | Paired_BattStorage | 2024 | nonsummer | 45414 | 783.3667 | 0 | 455 | 30 | 13650 | 610 | Blended | 5.739% | 0% | 4.358% | 0.003109% | 4.948% | 0.001781% | TRUE | 4.358% | 0.003109% | 4.948% | 0.001781%
RTEDDY_2_RWSBT2 | Paired_BattStorage | 2024 | summer | 45414 | 585.7 | 0 | 765 | 30 | 22950 | 0 | Individual | 2.552% | 0% |  |  | 2.552% | 0% | TRUE |  |  | 2.552% | 0%
RTEDDY_2_RWSBT3 | Paired_BattStorage | 2022 | nonsummer | 45421 | 0 | 0 | 0 | 45 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
RTEDDY_2_RWSBT3 | Paired_BattStorage | 2022 | summer | 45421 | 0 | 0 | 0 | 45 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
RTEDDY_2_RWSBT3 | Paired_BattStorage | 2023 | nonsummer | 45421 | 0 | 0 | 0 | 45 | 0 | 1060 | Group |  |  | 9.571% | 0% | 9.571% | 0% | TRUE | 9.571% | 0% | 9.571% | 0%
RTEDDY_2_RWSBT3 | Paired_BattStorage | 2023 | summer | 45421 | 0 | 0 | 0 | 45 | 0 | 765 | Group |  |  | 14.95% | 0% | 14.95% | 0% | TRUE | 14.95% | 0% | 14.95% | 0%
RTEDDY_2_RWSBT3 | Paired_BattStorage | 2024 | nonsummer | 45421 | 126.5 | 0 | 420 | 45 | 18900 | 645 | Blended | 0.6693% | 0% | 4.358% | 0.003109% | 2.903% | 0.001883% | TRUE | 4.358% | 0.003109% | 2.903% | 0.001883%
RTEDDY_2_RWSBT3 | Paired_BattStorage | 2024 | summer | 45421 | 299.5667 | 0 | 765 | 45 | 34425 | 0 | Individual | 0.8702% | 0% |  |  | 0.8702% | 0% | TRUE |  |  | 0.8702% | 0%
RTEDDY_2_RWSBT4 | Paired_BattStorage | 2022 | nonsummer | 45414 | 0 | 0 | 0 | 30 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
RTEDDY_2_RWSBT4 | Paired_BattStorage | 2022 | summer | 45414 | 0 | 0 | 0 | 30 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
RTEDDY_2_RWSBT4 | Paired_BattStorage | 2023 | nonsummer | 45414 | 0 | 0 | 0 | 30 | 0 | 1060 | Group |  |  | 9.571% | 0% | 9.571% | 0% | TRUE | 9.571% | 0% | 9.571% | 0%
RTEDDY_2_RWSBT4 | Paired_BattStorage | 2023 | summer | 45414 | 0 | 0 | 0 | 30 | 0 | 765 | Group |  |  | 14.95% | 0% | 14.95% | 0% | TRUE | 14.95% | 0% | 14.95% | 0%
RTEDDY_2_RWSBT4 | Paired_BattStorage | 2024 | nonsummer | 45414 | 177.2 | 0 | 455 | 30 | 13650 | 610 | Blended | 1.298% | 0% | 4.358% | 0.003109% | 3.051% | 0.001781% | TRUE | 4.358% | 0.003109% | 3.051% | 0.001781%
RTEDDY_2_RWSBT4 | Paired_BattStorage | 2024 | summer | 45414 | 69.95 | 0 | 765 | 30 | 22950 | 0 | Individual | 0.3048% | 0% |  |  | 0.3048% | 0% | TRUE |  |  | 0.3048% | 0%
RTEDDY_2_RWSBT5 | Paired_BattStorage | 2022 | nonsummer | 45415 | 0 | 0 | 0 | 12 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
RTEDDY_2_RWSBT5 | Paired_BattStorage | 2022 | summer | 45415 | 0 | 0 | 0 | 12 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
RTEDDY_2_RWSBT5 | Paired_BattStorage | 2023 | nonsummer | 45415 | 0 | 0 | 0 | 12 | 0 | 1060 | Group |  |  | 9.571% | 0% | 9.571% | 0% | TRUE | 9.571% | 0% | 9.571% | 0%
RTEDDY_2_RWSBT5 | Paired_BattStorage | 2023 | summer | 45415 | 0 | 0 | 0 | 12 | 0 | 765 | Group |  |  | 14.95% | 0% | 14.95% | 0% | TRUE | 14.95% | 0% | 14.95% | 0%
RTEDDY_2_RWSBT5 | Paired_BattStorage | 2024 | nonsummer | 45415 | 36 | 0 | 450 | 12 | 5400 | 615 | Blended | 0.6667% | 0% | 4.358% | 0.003109% | 2.798% | 0.001796% | TRUE | 4.358% | 0.003109% | 2.798% | 0.001796%
RTEDDY_2_RWSBT5 | Paired_BattStorage | 2024 | summer | 45415 | 78.7333 | 0 | 765 | 12 | 9180 | 0 | Individual | 0.8577% | 0% |  |  | 0.8577% | 0% | TRUE |  |  | 0.8577% | 0%
SCARLT_2_SS2BT1 | Paired_BattStorage | 2022 | nonsummer | 45637 | 0 | 0 | 0 | 150 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
SCARLT_2_SS2BT1 | Paired_BattStorage | 2022 | summer | 45637 | 0 | 0 | 0 | 150 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
SCARLT_2_SS2BT1 | Paired_BattStorage | 2023 | nonsummer | 45637 | 0 | 0 | 0 | 150 | 0 | 1060 | Group |  |  | 9.571% | 0% | 9.571% | 0% | TRUE | 9.571% | 0% | 9.571% | 0%
SCARLT_2_SS2BT1 | Paired_BattStorage | 2023 | summer | 45637 | 0 | 0 | 0 | 150 | 0 | 765 | Group |  |  | 14.95% | 0% | 14.95% | 0% | TRUE | 14.95% | 0% | 14.95% | 0%
SCARLT_2_SS2BT1 | Paired_BattStorage | 2024 | nonsummer | 45637 | 12927.5 | 0 | 105 | 150 | 15750 | 960 | Blended | 82.08% | 0% | 4.358% | 0.003109% | 12.02% | 0.002803% | TRUE | 4.358% | 0.003109% | 12.02% | 0.002803%
SCARLT_2_SS2BT1 | Paired_BattStorage | 2024 | summer | 45637 | 0 | 0 | 0 | 150 | 0 | 765 | Group |  |  | 3.923% | 0.0004805% | 3.923% | 0.0004805% | TRUE | 3.923% | 0.0004805% | 3.923% | 0.0004805%
SCARLT_2_SSABT1 | Paired_BattStorage | 2022 | nonsummer | 45415 | 0 | 0 | 0 | 10 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
SCARLT_2_SSABT1 | Paired_BattStorage | 2022 | summer | 45415 | 0 | 0 | 0 | 10 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
SCARLT_2_SSABT1 | Paired_BattStorage | 2023 | nonsummer | 45415 | 0 | 0 | 0 | 10 | 0 | 1060 | Group |  |  | 9.571% | 0% | 9.571% | 0% | TRUE | 9.571% | 0% | 9.571% | 0%
SCARLT_2_SSABT1 | Paired_BattStorage | 2023 | summer | 45415 | 0 | 0 | 0 | 10 | 0 | 765 | Group |  |  | 14.95% | 0% | 14.95% | 0% | TRUE | 14.95% | 0% | 14.95% | 0%
SCARLT_2_SSABT1 | Paired_BattStorage | 2024 | nonsummer | 45415 | 760.8133 | 0 | 450 | 10 | 4500 | 615 | Blended | 16.91% | 0% | 4.358% | 0.003109% | 9.661% | 0.001796% | TRUE | 4.358% | 0.003109% | 9.661% | 0.001796%
SCARLT_2_SSABT1 | Paired_BattStorage | 2024 | summer | 45415 | 1965.6552 | 0 | 765 | 10 | 7650 | 0 | Individual | 25.69% | 0% |  |  | 25.69% | 0% | TRUE |  |  | 25.69% | 0%
SCARLT_2_SSBBT1 | Paired_BattStorage | 2022 | nonsummer | 45415 | 0 | 0 | 0 | 30 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
SCARLT_2_SSBBT1 | Paired_BattStorage | 2022 | summer | 45415 | 0 | 0 | 0 | 30 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
SCARLT_2_SSBBT1 | Paired_BattStorage | 2023 | nonsummer | 45415 | 0 | 0 | 0 | 30 | 0 | 1060 | Group |  |  | 9.571% | 0% | 9.571% | 0% | TRUE | 9.571% | 0% | 9.571% | 0%
SCARLT_2_SSBBT1 | Paired_BattStorage | 2023 | summer | 45415 | 0 | 0 | 0 | 30 | 0 | 765 | Group |  |  | 14.95% | 0% | 14.95% | 0% | TRUE | 14.95% | 0% | 14.95% | 0%
SCARLT_2_SSBBT1 | Paired_BattStorage | 2024 | nonsummer | 45415 | 2600.7333 | 0 | 450 | 30 | 13500 | 615 | Blended | 19.26% | 0% | 4.358% | 0.003109% | 10.66% | 0.001796% | TRUE | 4.358% | 0.003109% | 10.66% | 0.001796%
SCARLT_2_SSBBT1 | Paired_BattStorage | 2024 | summer | 45415 | 6577.0498 | 0 | 765 | 30 | 22950 | 0 | Individual | 28.66% | 0% |  |  | 28.66% | 0% | TRUE |  |  | 28.66% | 0%
SISPRG_2_DS3BT1 | Paired_BattStorage | 2022 | nonsummer | 45245 | 0 | 0 | 0 | 61.5 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
SISPRG_2_DS3BT1 | Paired_BattStorage | 2022 | summer | 45245 | 0 | 0 | 0 | 61.5 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
SISPRG_2_DS3BT1 | Paired_BattStorage | 2023 | nonsummer | 45245 | 352.35 | 0 | 235 | 61.5 | 14452.5 | 825 | Blended | 2.438% | 0% | 9.571% | 0% | 7.989% | 0% | TRUE | 9.571% | 0% | 7.989% | 0%
SISPRG_2_DS3BT1 | Paired_BattStorage | 2023 | summer | 45245 | 0 | 0 | 0 | 61.5 | 0 | 765 | Group |  |  | 14.95% | 0% | 14.95% | 0% | TRUE | 14.95% | 0% | 14.95% | 0%
SISPRG_2_DS3BT1 | Paired_BattStorage | 2024 | nonsummer | 45245 | 1219.5407 | 130 | 1065 | 61.5 | 65497.5 | 0 | Individual | 1.862% | 0.1985% |  |  | 1.862% | 0.1985% | TRUE |  |  | 1.862% | 0.1985%
SISPRG_2_DS3BT1 | Paired_BattStorage | 2024 | summer | 45245 | 1876.0027 | 0 | 765 | 61.5 | 47047.5 | 0 | Individual | 3.987% | 0% |  |  | 3.987% | 0% | TRUE |  |  | 3.987% | 0%
SISPRG_2_DS3BT2 | Paired_BattStorage | 2022 | nonsummer | 45162 | 0 | 0 | 0 | 60 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
SISPRG_2_DS3BT2 | Paired_BattStorage | 2022 | summer | 45162 | 0 | 0 | 0 | 60 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
SISPRG_2_DS3BT2 | Paired_BattStorage | 2023 | nonsummer | 45162 | 199 | 0 | 305 | 60 | 18300 | 755 | Blended | 1.087% | 0% | 9.571% | 0% | 7.13% | 0% | TRUE | 9.571% | 0% | 7.13% | 0%
SISPRG_2_DS3BT2 | Paired_BattStorage | 2023 | summer | 45162 | 372.6667 | 0 | 345 | 60 | 20700 | 420 | Blended | 1.8% | 0% | 14.95% | 0% | 9.021% | 0% | TRUE | 14.95% | 0% | 9.021% | 0%
SISPRG_2_DS3BT2 | Paired_BattStorage | 2024 | nonsummer | 45162 | 497.485 | 0 | 1065 | 60 | 63900 | 0 | Individual | 0.7785% | 0% |  |  | 0.7785% | 0% | TRUE |  |  | 0.7785% | 0%
SISPRG_2_DS3BT2 | Paired_BattStorage | 2024 | summer | 45162 | 2765.7867 | 0 | 765 | 60 | 45900 | 0 | Individual | 6.026% | 0% |  |  | 6.026% | 0% | TRUE |  |  | 6.026% | 0%
SISPRG_2_DS3BT3 | Paired_BattStorage | 2022 | nonsummer | 45174 | 0 | 0 | 0 | 12.5 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
SISPRG_2_DS3BT3 | Paired_BattStorage | 2022 | summer | 45174 | 0 | 0 | 0 | 12.5 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
SISPRG_2_DS3BT3 | Paired_BattStorage | 2023 | nonsummer | 45174 | 705.75 | 0 | 305 | 12.5 | 3812.5 | 755 | Blended | 18.51% | 0% | 9.571% | 0% | 12.14% | 0% | TRUE | 9.571% | 0% | 12.14% | 0%
SISPRG_2_DS3BT3 | Paired_BattStorage | 2023 | summer | 45174 | 391.0917 | 0 | 285 | 12.5 | 3562.5 | 480 | Blended | 10.98% | 0% | 14.95% | 0% | 13.47% | 0% | TRUE | 14.95% | 0% | 13.47% | 0%
SISPRG_2_DS3BT3 | Paired_BattStorage | 2024 | nonsummer | 45174 | 102 | 0 | 1065 | 12.5 | 13312.5 | 0 | Individual | 0.7662% | 0% |  |  | 0.7662% | 0% | TRUE |  |  | 0.7662% | 0%
SISPRG_2_DS3BT3 | Paired_BattStorage | 2024 | summer | 45174 | 705.5167 | 0 | 765 | 12.5 | 9562.5 | 0 | Individual | 7.378% | 0% |  |  | 7.378% | 0% | TRUE |  |  | 7.378% | 0%
SISPRG_2_DS3BT4 | Paired_BattStorage | 2022 | nonsummer | 45162 | 0 | 0 | 0 | 15 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
SISPRG_2_DS3BT4 | Paired_BattStorage | 2022 | summer | 45162 | 0 | 0 | 0 | 15 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
SISPRG_2_DS3BT4 | Paired_BattStorage | 2023 | nonsummer | 45162 | 222.22 | 0 | 305 | 15 | 4575 | 755 | Blended | 4.857% | 0% | 9.571% | 0% | 8.214% | 0% | TRUE | 9.571% | 0% | 8.214% | 0%
SISPRG_2_DS3BT4 | Paired_BattStorage | 2023 | summer | 45162 | 161.0833 | 0 | 345 | 15 | 5175 | 420 | Blended | 3.113% | 0% | 14.95% | 0% | 9.613% | 0% | TRUE | 14.95% | 0% | 9.613% | 0%
SISPRG_2_DS3BT4 | Paired_BattStorage | 2024 | nonsummer | 45162 | 216.3 | 0 | 1065 | 15 | 15975 | 0 | Individual | 1.354% | 0% |  |  | 1.354% | 0% | TRUE |  |  | 1.354% | 0%
SISPRG_2_DS3BT4 | Paired_BattStorage | 2024 | summer | 45162 | 290.5833 | 0 | 765 | 15 | 11475 | 0 | Individual | 2.532% | 0% |  |  | 2.532% | 0% | TRUE |  |  | 2.532% | 0%
SOLBLU_2_WSBBX2 | Paired_BattStorage | 2022 | nonsummer | 45273 | 0 | 0 | 0 | 225 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
SOLBLU_2_WSBBX2 | Paired_BattStorage | 2022 | summer | 45273 | 0 | 0 | 0 | 225 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
SOLBLU_2_WSBBX2 | Paired_BattStorage | 2023 | nonsummer | 45273 | 1877.15 | 0 | 95 | 225 | 21375 | 965 | Blended | 8.782% | 0% | 9.571% | 0% | 9.5% | 0% | TRUE | 9.571% | 0% | 9.5% | 0%
SOLBLU_2_WSBBX2 | Paired_BattStorage | 2023 | summer | 45273 | 0 | 0 | 0 | 225 | 0 | 765 | Group |  |  | 14.95% | 0% | 14.95% | 0% | TRUE | 14.95% | 0% | 14.95% | 0%
SOLBLU_2_WSBBX2 | Paired_BattStorage | 2024 | nonsummer | 45273 | 2196.7633 | 0 | 1065 | 225 | 239625 | 0 | Individual | 0.9168% | 0% |  |  | 0.9168% | 0% | TRUE |  |  | 0.9168% | 0%
SOLBLU_2_WSBBX2 | Paired_BattStorage | 2024 | summer | 45273 | 0 | 0 | 765 | 225 | 172125 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SUNCAT_2_A1ABT1 | Paired_BattStorage | 2022 | nonsummer | 44774 | 5299.0867 | 0 | 305 | 47 | 14335 | 755 | Blended | 36.97% | 0% | 7.043% | 0% | 15.65% | 0% | TRUE | 7.043% | 0% | 15.65% | 0%
SUNCAT_2_A1ABT1 | Paired_BattStorage | 2022 | summer | 44774 | 11448.925 | 0 | 460 | 47 | 21620 | 305 | Blended | 52.96% | 0% | 14.17% | 0% | 37.49% | 0% | TRUE | 14.17% | 0% | 37.49% | 0%
SUNCAT_2_A1ABT1 | Paired_BattStorage | 2023 | nonsummer | 44774 | 10535.999 | 0 | 1060 | 47 | 49820 | 0 | Individual | 21.15% | 0% |  |  | 21.15% | 0% | TRUE |  |  | 21.15% | 0%
SUNCAT_2_A1ABT1 | Paired_BattStorage | 2023 | summer | 44774 | 13270.0433 | 0 | 765 | 47 | 35955 | 0 | Individual | 36.91% | 0% |  |  | 36.91% | 0% | TRUE |  |  | 36.91% | 0%
SUNCAT_2_A1ABT1 | Paired_BattStorage | 2024 | nonsummer | 44774 | 1939.4902 | 0 | 1065 | 47 | 50055 | 0 | Individual | 3.875% | 0% |  |  | 3.875% | 0% | TRUE |  |  | 3.875% | 0%
SUNCAT_2_A1ABT1 | Paired_BattStorage | 2024 | summer | 44774 | 7.5333 | 0 | 765 | 47 | 35955 | 0 | Individual | 0.02095% | 0% |  |  | 0.02095% | 0% | TRUE |  |  | 0.02095% | 0%
SUNCAT_2_A1BBT1 | Paired_BattStorage | 2022 | nonsummer | 44774 | 4565.6217 | 0 | 305 | 63 | 19215 | 755 | Blended | 23.76% | 0% | 7.043% | 0% | 11.85% | 0% | TRUE | 7.043% | 0% | 11.85% | 0%
SUNCAT_2_A1BBT1 | Paired_BattStorage | 2022 | summer | 44774 | 13484.8617 | 0 | 460 | 63 | 28980 | 305 | Blended | 46.53% | 0% | 14.17% | 0% | 33.63% | 0% | TRUE | 14.17% | 0% | 33.63% | 0%
SUNCAT_2_A1BBT1 | Paired_BattStorage | 2023 | nonsummer | 44774 | 15396.8023 | 0 | 1060 | 63 | 66780 | 0 | Individual | 23.06% | 0% |  |  | 23.06% | 0% | TRUE |  |  | 23.06% | 0%
SUNCAT_2_A1BBT1 | Paired_BattStorage | 2023 | summer | 44774 | 20383.7357 | 0 | 765 | 63 | 48195 | 0 | Individual | 42.29% | 0% |  |  | 42.29% | 0% | TRUE |  |  | 42.29% | 0%
SUNCAT_2_A1BBT1 | Paired_BattStorage | 2024 | nonsummer | 44774 | 4003.6898 | 0 | 1065 | 63 | 67095 | 0 | Individual | 5.967% | 0% |  |  | 5.967% | 0% | TRUE |  |  | 5.967% | 0%
SUNCAT_2_A1BBT1 | Paired_BattStorage | 2024 | summer | 44774 | 383.3182 | 0 | 765 | 63 | 48195 | 0 | Individual | 0.7953% | 0% |  |  | 0.7953% | 0% | TRUE |  |  | 0.7953% | 0%
SUNCAT_2_A2ABT2 | Paired_BattStorage | 2022 | nonsummer | 44789 | 7619.565 | 0 | 305 | 132 | 40260 | 755 | Blended | 18.93% | 0% | 7.043% | 0% | 10.46% | 0% | TRUE | 7.043% | 0% | 10.46% | 0%
SUNCAT_2_A2ABT2 | Paired_BattStorage | 2022 | summer | 44789 | 16294.5683 | 0 | 385 | 132 | 50820 | 380 | Blended | 32.06% | 0% | 14.17% | 0% | 23.18% | 0% | TRUE | 14.17% | 0% | 23.18% | 0%
SUNCAT_2_A2ABT2 | Paired_BattStorage | 2023 | nonsummer | 44789 | 18036.3 | 0 | 1060 | 132 | 139920 | 0 | Individual | 12.89% | 0% |  |  | 12.89% | 0% | TRUE |  |  | 12.89% | 0%
SUNCAT_2_A2ABT2 | Paired_BattStorage | 2023 | summer | 44789 | 18822.905 | 0 | 765 | 132 | 100980 | 0 | Individual | 18.64% | 0% |  |  | 18.64% | 0% | TRUE |  |  | 18.64% | 0%
SUNCAT_2_A2ABT2 | Paired_BattStorage | 2024 | nonsummer | 44789 | 5616.3433 | 0 | 1065 | 132 | 140580 | 0 | Individual | 3.995% | 0% |  |  | 3.995% | 0% | TRUE |  |  | 3.995% | 0%
SUNCAT_2_A2ABT2 | Paired_BattStorage | 2024 | summer | 44789 | 1340.4945 | 0 | 765 | 132 | 100980 | 0 | Individual | 1.327% | 0% |  |  | 1.327% | 0% | TRUE |  |  | 1.327% | 0%
TRNQLT_2_RETBT1 | Paired_BattStorage | 2022 | nonsummer | 44636 | 7713.6883 | 0 | 690 | 72 | 49680 | 370 | Blended | 15.53% | 0% | 7.043% | 0% | 12.57% | 0% | TRUE | 7.043% | 0% | 12.57% | 0%
TRNQLT_2_RETBT1 | Paired_BattStorage | 2022 | summer | 44636 | 13317.3167 | 0 | 765 | 72 | 55080 | 0 | Individual | 24.18% | 0% |  |  | 24.18% | 0% | TRUE |  |  | 24.18% | 0%
TRNQLT_2_RETBT1 | Paired_BattStorage | 2023 | nonsummer | 44636 | 14896.5333 | 0 | 1060 | 72 | 76320 | 0 | Individual | 19.52% | 0% |  |  | 19.52% | 0% | TRUE |  |  | 19.52% | 0%
TRNQLT_2_RETBT1 | Paired_BattStorage | 2023 | summer | 44636 | 13747.45 | 0 | 765 | 72 | 55080 | 0 | Individual | 24.96% | 0% |  |  | 24.96% | 0% | TRUE |  |  | 24.96% | 0%
TRNQLT_2_RETBT1 | Paired_BattStorage | 2024 | nonsummer | 44636 | 4853.8333 | 0 | 1065 | 72 | 76680 | 0 | Individual | 6.33% | 0% |  |  | 6.33% | 0% | TRUE |  |  | 6.33% | 0%
TRNQLT_2_RETBT1 | Paired_BattStorage | 2024 | summer | 44636 | 6593.25 | 0 | 765 | 72 | 55080 | 0 | Individual | 11.97% | 0% |  |  | 11.97% | 0% | TRUE |  |  | 11.97% | 0%
VALTNE_2_TSBBT1 | Paired_BattStorage | 2022 | nonsummer | 45840 | 0 | 0 | 0 | 18 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
VALTNE_2_TSBBT1 | Paired_BattStorage | 2022 | summer | 45840 | 0 | 0 | 0 | 18 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
VALTNE_2_TSBBT1 | Paired_BattStorage | 2023 | nonsummer | 45840 | 0 | 0 | 0 | 18 | 0 | 1060 | Group |  |  | 9.571% | 0% | 9.571% | 0% | TRUE | 9.571% | 0% | 9.571% | 0%
VALTNE_2_TSBBT1 | Paired_BattStorage | 2023 | summer | 45840 | 0 | 0 | 0 | 18 | 0 | 765 | Group |  |  | 14.95% | 0% | 14.95% | 0% | TRUE | 14.95% | 0% | 14.95% | 0%
VALTNE_2_TSBBT1 | Paired_BattStorage | 2024 | nonsummer | 45840 | 0 | 0 | 0 | 18 | 0 | 1065 | Group |  |  | 4.358% | 0.003109% | 4.358% | 0.003109% | TRUE | 4.358% | 0.003109% | 4.358% | 0.003109%
VALTNE_2_TSBBT1 | Paired_BattStorage | 2024 | summer | 45840 | 0 | 0 | 0 | 18 | 0 | 765 | Group |  |  | 3.923% | 0.0004805% | 3.923% | 0.0004805% | TRUE | 3.923% | 0.0004805% | 3.923% | 0.0004805%
VALTNE_2_TSBBT2 | Paired_BattStorage | 2022 | nonsummer | 45840 | 0 | 0 | 0 | 22 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
VALTNE_2_TSBBT2 | Paired_BattStorage | 2022 | summer | 45840 | 0 | 0 | 0 | 22 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
VALTNE_2_TSBBT2 | Paired_BattStorage | 2023 | nonsummer | 45840 | 0 | 0 | 0 | 22 | 0 | 1060 | Group |  |  | 9.571% | 0% | 9.571% | 0% | TRUE | 9.571% | 0% | 9.571% | 0%
VALTNE_2_TSBBT2 | Paired_BattStorage | 2023 | summer | 45840 | 0 | 0 | 0 | 22 | 0 | 765 | Group |  |  | 14.95% | 0% | 14.95% | 0% | TRUE | 14.95% | 0% | 14.95% | 0%
VALTNE_2_TSBBT2 | Paired_BattStorage | 2024 | nonsummer | 45840 | 0 | 0 | 0 | 22 | 0 | 1065 | Group |  |  | 4.358% | 0.003109% | 4.358% | 0.003109% | TRUE | 4.358% | 0.003109% | 4.358% | 0.003109%
VALTNE_2_TSBBT2 | Paired_BattStorage | 2024 | summer | 45840 | 0 | 0 | 0 | 22 | 0 | 765 | Group |  |  | 3.923% | 0.0004805% | 3.923% | 0.0004805% | TRUE | 3.923% | 0.0004805% | 3.923% | 0.0004805%
VICPAS_2_SLOBT1 | Paired_BattStorage | 2022 | nonsummer | 45377 | 0 | 0 | 0 | 15 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
VICPAS_2_SLOBT1 | Paired_BattStorage | 2022 | summer | 45377 | 0 | 0 | 0 | 15 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
VICPAS_2_SLOBT1 | Paired_BattStorage | 2023 | nonsummer | 45377 | 0 | 0 | 0 | 15 | 0 | 1060 | Group |  |  | 9.571% | 0% | 9.571% | 0% | TRUE | 9.571% | 0% | 9.571% | 0%
VICPAS_2_SLOBT1 | Paired_BattStorage | 2023 | summer | 45377 | 0 | 0 | 0 | 15 | 0 | 765 | Group |  |  | 14.95% | 0% | 14.95% | 0% | TRUE | 14.95% | 0% | 14.95% | 0%
VICPAS_2_SLOBT1 | Paired_BattStorage | 2024 | nonsummer | 45377 | 132.25 | 0 | 640 | 15 | 9600 | 425 | Blended | 1.378% | 0% | 4.358% | 0.003109% | 2.567% | 0.001241% | TRUE | 4.358% | 0.003109% | 2.567% | 0.001241%
VICPAS_2_SLOBT1 | Paired_BattStorage | 2024 | summer | 45377 | 378.075 | 0 | 765 | 15 | 11475 | 0 | Individual | 3.295% | 0% |  |  | 3.295% | 0% | TRUE |  |  | 3.295% | 0%
VICPAS_2_SOCBT1 | Paired_BattStorage | 2022 | nonsummer | 45377 | 0 | 0 | 0 | 50 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
VICPAS_2_SOCBT1 | Paired_BattStorage | 2022 | summer | 45377 | 0 | 0 | 0 | 50 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
VICPAS_2_SOCBT1 | Paired_BattStorage | 2023 | nonsummer | 45377 | 0 | 0 | 0 | 50 | 0 | 1060 | Group |  |  | 9.571% | 0% | 9.571% | 0% | TRUE | 9.571% | 0% | 9.571% | 0%
VICPAS_2_SOCBT1 | Paired_BattStorage | 2023 | summer | 45377 | 0 | 0 | 0 | 50 | 0 | 765 | Group |  |  | 14.95% | 0% | 14.95% | 0% | TRUE | 14.95% | 0% | 14.95% | 0%
VICPAS_2_SOCBT1 | Paired_BattStorage | 2024 | nonsummer | 45377 | 1134.2167 | 0 | 640 | 50 | 32000 | 425 | Blended | 3.544% | 0% | 4.358% | 0.003109% | 3.869% | 0.001241% | TRUE | 4.358% | 0.003109% | 3.869% | 0.001241%
VICPAS_2_SOCBT1 | Paired_BattStorage | 2024 | summer | 45377 | 2650.9167 | 0 | 765 | 50 | 38250 | 0 | Individual | 6.931% | 0% |  |  | 6.931% | 0% | TRUE |  |  | 6.931% | 0%
VICPAS_2_SOCBT2 | Paired_BattStorage | 2022 | nonsummer | 45377 | 0 | 0 | 0 | 71 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
VICPAS_2_SOCBT2 | Paired_BattStorage | 2022 | summer | 45377 | 0 | 0 | 0 | 71 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
VICPAS_2_SOCBT2 | Paired_BattStorage | 2023 | nonsummer | 45377 | 0 | 0 | 0 | 71 | 0 | 1060 | Group |  |  | 9.571% | 0% | 9.571% | 0% | TRUE | 9.571% | 0% | 9.571% | 0%
VICPAS_2_SOCBT2 | Paired_BattStorage | 2023 | summer | 45377 | 0 | 0 | 0 | 71 | 0 | 765 | Group |  |  | 14.95% | 0% | 14.95% | 0% | TRUE | 14.95% | 0% | 14.95% | 0%
VICPAS_2_SOCBT2 | Paired_BattStorage | 2024 | nonsummer | 45377 | 1929.9333 | 0 | 640 | 71 | 45440 | 425 | Blended | 4.247% | 0% | 4.358% | 0.003109% | 4.292% | 0.001241% | TRUE | 4.358% | 0.003109% | 4.292% | 0.001241%
VICPAS_2_SOCBT2 | Paired_BattStorage | 2024 | summer | 45377 | 2043.75 | 0 | 765 | 71 | 54315 | 0 | Individual | 3.763% | 0% |  |  | 3.763% | 0% | TRUE |  |  | 3.763% | 0%
VICPAS_2_VPSBT1 | Paired_BattStorage | 2022 | nonsummer | 45378 | 0 | 0 | 0 | 50 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
VICPAS_2_VPSBT1 | Paired_BattStorage | 2022 | summer | 45378 | 0 | 0 | 0 | 50 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
VICPAS_2_VPSBT1 | Paired_BattStorage | 2023 | nonsummer | 45378 | 0 | 0 | 0 | 50 | 0 | 1060 | Group |  |  | 9.571% | 0% | 9.571% | 0% | TRUE | 9.571% | 0% | 9.571% | 0%
VICPAS_2_VPSBT1 | Paired_BattStorage | 2023 | summer | 45378 | 0 | 0 | 0 | 50 | 0 | 765 | Group |  |  | 14.95% | 0% | 14.95% | 0% | TRUE | 14.95% | 0% | 14.95% | 0%
VICPAS_2_VPSBT1 | Paired_BattStorage | 2024 | nonsummer | 45378 | 1056.2833 | 0 | 635 | 50 | 31750 | 430 | Blended | 3.327% | 0% | 4.358% | 0.003109% | 3.743% | 0.001255% | TRUE | 4.358% | 0.003109% | 3.743% | 0.001255%
VICPAS_2_VPSBT1 | Paired_BattStorage | 2024 | summer | 45378 | 1838.2333 | 0 | 765 | 50 | 38250 | 0 | Individual | 4.806% | 0% |  |  | 4.806% | 0% | TRUE |  |  | 4.806% | 0%
VLCNTR_6_VCEBT1 | Paired_BattStorage | 2022 | nonsummer | 44529 | 2544.9333 | 0 | 1060 | 54 | 57240 | 0 | Individual | 4.446% | 0% |  |  | 4.446% | 0% | TRUE |  |  | 4.446% | 0%
VLCNTR_6_VCEBT1 | Paired_BattStorage | 2022 | summer | 44529 | 1008.1667 | 0 | 765 | 54 | 41310 | 0 | Individual | 2.44% | 0% |  |  | 2.44% | 0% | TRUE |  |  | 2.44% | 0%
VLCNTR_6_VCEBT1 | Paired_BattStorage | 2023 | nonsummer | 44529 | 4865.8333 | 0 | 1060 | 54 | 57240 | 0 | Individual | 8.501% | 0% |  |  | 8.501% | 0% | TRUE |  |  | 8.501% | 0%
VLCNTR_6_VCEBT1 | Paired_BattStorage | 2023 | summer | 44529 | 9497.7667 | 0 | 765 | 54 | 41310 | 0 | Individual | 22.99% | 0% |  |  | 22.99% | 0% | TRUE |  |  | 22.99% | 0%
VLCNTR_6_VCEBT1 | Paired_BattStorage | 2024 | nonsummer | 44529 | 1189 | 0 | 1065 | 54 | 57510 | 0 | Individual | 2.067% | 0% |  |  | 2.067% | 0% | TRUE |  |  | 2.067% | 0%
VLCNTR_6_VCEBT1 | Paired_BattStorage | 2024 | summer | 44529 | 8.6667 | 16 | 765 | 54 | 41310 | 0 | Individual | 0.02098% | 0.03873% |  |  | 0.02098% | 0.03873% | TRUE |  |  | 0.02098% | 0.03873%
VLCNTR_6_VCEBT2 | Paired_BattStorage | 2022 | nonsummer | 44546 | 7418.25 | 0 | 1060 | 85 | 90100 | 0 | Individual | 8.233% | 0% |  |  | 8.233% | 0% | TRUE |  |  | 8.233% | 0%
VLCNTR_6_VCEBT2 | Paired_BattStorage | 2022 | summer | 44546 | 7015.5833 | 0 | 765 | 85 | 65025 | 0 | Individual | 10.79% | 0% |  |  | 10.79% | 0% | TRUE |  |  | 10.79% | 0%
VLCNTR_6_VCEBT2 | Paired_BattStorage | 2023 | nonsummer | 44546 | 2289.8167 | 0 | 1060 | 85 | 90100 | 0 | Individual | 2.541% | 0% |  |  | 2.541% | 0% | TRUE |  |  | 2.541% | 0%
VLCNTR_6_VCEBT2 | Paired_BattStorage | 2023 | summer | 44546 | 11871.4167 | 0 | 765 | 85 | 65025 | 0 | Individual | 18.26% | 0% |  |  | 18.26% | 0% | TRUE |  |  | 18.26% | 0%
VLCNTR_6_VCEBT2 | Paired_BattStorage | 2024 | nonsummer | 44546 | 1947 | 0 | 1065 | 85 | 90525 | 0 | Individual | 2.151% | 0% |  |  | 2.151% | 0% | TRUE |  |  | 2.151% | 0%
VLCNTR_6_VCEBT2 | Paired_BattStorage | 2024 | summer | 44546 | 0 | 0 | 765 | 85 | 65025 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
WSTWND_2_M89BT2 | Paired_BattStorage | 2022 | nonsummer | 45071 | 0 | 0 | 0 | 70.6 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
WSTWND_2_M89BT2 | Paired_BattStorage | 2022 | summer | 45071 | 0 | 0 | 0 | 70.6 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
WSTWND_2_M89BT2 | Paired_BattStorage | 2023 | nonsummer | 45071 | 862.7167 | 0 | 340 | 70.6 | 24004 | 720 | Blended | 3.594% | 0% | 9.571% | 0% | 7.654% | 0% | TRUE | 9.571% | 0% | 7.654% | 0%
WSTWND_2_M89BT2 | Paired_BattStorage | 2023 | summer | 45071 | 1404.9233 | 0 | 765 | 70.6 | 54009 | 0 | Individual | 2.601% | 0% |  |  | 2.601% | 0% | TRUE |  |  | 2.601% | 0%
WSTWND_2_M89BT2 | Paired_BattStorage | 2024 | nonsummer | 45071 | 8875.8267 | 0 | 1065 | 70.6 | 75189 | 0 | Individual | 11.8% | 0% |  |  | 11.8% | 0% | TRUE |  |  | 11.8% | 0%
WSTWND_2_M89BT2 | Paired_BattStorage | 2024 | summer | 45071 | 6569.6 | 0 | 765 | 70.6 | 54009 | 0 | Individual | 12.16% | 0% |  |  | 12.16% | 0% | TRUE |  |  | 12.16% | 0%
YELPIN_2_YP2BT1 | Paired_BattStorage | 2022 | nonsummer | 45133 | 0 | 0 | 0 | 65 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
YELPIN_2_YP2BT1 | Paired_BattStorage | 2022 | summer | 45133 | 0 | 0 | 0 | 65 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
YELPIN_2_YP2BT1 | Paired_BattStorage | 2023 | nonsummer | 45133 | 2690 | 0 | 305 | 65 | 19825 | 755 | Blended | 13.57% | 0% | 9.571% | 0% | 10.72% | 0% | TRUE | 9.571% | 0% | 10.72% | 0%
YELPIN_2_YP2BT1 | Paired_BattStorage | 2023 | summer | 45133 | 2724.6933 | 0 | 490 | 65 | 31850 | 275 | Blended | 8.555% | 0% | 14.95% | 0% | 10.85% | 0% | TRUE | 14.95% | 0% | 10.85% | 0%
YELPIN_2_YP2BT1 | Paired_BattStorage | 2024 | nonsummer | 45133 | 2481.2013 | 0 | 1065 | 65 | 69225 | 0 | Individual | 3.584% | 0% |  |  | 3.584% | 0% | TRUE |  |  | 3.584% | 0%
YELPIN_2_YP2BT1 | Paired_BattStorage | 2024 | summer | 45133 | 283.452 | 0 | 765 | 65 | 49725 | 0 | Individual | 0.57% | 0% |  |  | 0.57% | 0% | TRUE |  |  | 0.57% | 0%
YELPIN_2_YP2BT2 | Paired_BattStorage | 2022 | nonsummer | 45436 | 0 | 0 | 0 | 28 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
YELPIN_2_YP2BT2 | Paired_BattStorage | 2022 | summer | 45436 | 0 | 0 | 0 | 28 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
YELPIN_2_YP2BT2 | Paired_BattStorage | 2023 | nonsummer | 45436 | 0 | 0 | 0 | 28 | 0 | 1060 | Group |  |  | 9.571% | 0% | 9.571% | 0% | TRUE | 9.571% | 0% | 9.571% | 0%
YELPIN_2_YP2BT2 | Paired_BattStorage | 2023 | summer | 45436 | 0 | 0 | 0 | 28 | 0 | 765 | Group |  |  | 14.95% | 0% | 14.95% | 0% | TRUE | 14.95% | 0% | 14.95% | 0%
YELPIN_2_YP2BT2 | Paired_BattStorage | 2024 | nonsummer | 45436 | 1486.65 | 0 | 345 | 28 | 9660 | 720 | Blended | 15.39% | 0% | 4.358% | 0.003109% | 7.932% | 0.002102% | TRUE | 4.358% | 0.003109% | 7.932% | 0.002102%
YELPIN_2_YP2BT2 | Paired_BattStorage | 2024 | summer | 45436 | 503.5 | 0 | 765 | 28 | 21420 | 0 | Individual | 2.351% | 0% |  |  | 2.351% | 0% | TRUE |  |  | 2.351% | 0%
YELPIN_2_YP2BT3 | Paired_BattStorage | 2022 | nonsummer | 45447 | 0 | 0 | 0 | 32 | 0 | 1060 | Group |  |  | 7.043% | 0% | 7.043% | 0% | TRUE | 7.043% | 0% | 7.043% | 0%
YELPIN_2_YP2BT3 | Paired_BattStorage | 2022 | summer | 45447 | 0 | 0 | 0 | 32 | 0 | 765 | Group |  |  | 14.17% | 0% | 14.17% | 0% | TRUE | 14.17% | 0% | 14.17% | 0%
YELPIN_2_YP2BT3 | Paired_BattStorage | 2023 | nonsummer | 45447 | 0 | 0 | 0 | 32 | 0 | 1060 | Group |  |  | 9.571% | 0% | 9.571% | 0% | TRUE | 9.571% | 0% | 9.571% | 0%
YELPIN_2_YP2BT3 | Paired_BattStorage | 2023 | summer | 45447 | 0 | 0 | 0 | 32 | 0 | 765 | Group |  |  | 14.95% | 0% | 14.95% | 0% | TRUE | 14.95% | 0% | 14.95% | 0%
YELPIN_2_YP2BT3 | Paired_BattStorage | 2024 | nonsummer | 45447 | 1005.3333 | 0 | 305 | 32 | 9760 | 760 | Blended | 10.3% | 0% | 4.358% | 0.003109% | 6.06% | 0.002219% | TRUE | 4.358% | 0.003109% | 6.06% | 0.002219%
YELPIN_2_YP2BT3 | Paired_BattStorage | 2024 | summer | 45447 | 239.5833 | 0 | 750 | 32 | 24000 | 15 | Blended | 0.9983% | 0% | 3.923% | 0.0004805% | 1.056% | 9.421e-06% | TRUE | 3.923% | 0.0004805% | 1.056% | 9.421e-06%
PALSEL_6_PLSSR1 | Paired_Solar_1Axis | 2022 | nonsummer | 45463 | 0 | 0 | 0 | 20 | 0 | 1060 | Group | [6 empty] | TRUE
PALSEL_6_PLSSR1 | Paired_Solar_1Axis | 2022 | summer | 45463 | 0 | 0 | 0 | 20 | 0 | 765 | Group | [6 empty] | TRUE
PALSEL_6_PLSSR1 | Paired_Solar_1Axis | 2023 | nonsummer | 45463 | 0 | 0 | 0 | 20 | 0 | 1060 | Group | [6 empty] | TRUE
PALSEL_6_PLSSR1 | Paired_Solar_1Axis | 2023 | summer | 45463 | 0 | 0 | 0 | 20 | 0 | 765 | Group | [6 empty] | TRUE
PALSEL_6_PLSSR1 | Paired_Solar_1Axis | 2024 | nonsummer | 45463 | 0 | 0 | 305 | 20 | 6100 | 760 | Blended | 0% | 0% | 0% | 0% | 0% | 0% | TRUE | 0% | 0% | 0% | 0%
PALSEL_6_PLSSR1 | Paired_Solar_1Axis | 2024 | summer | 45463 | 334 | 0 | 670 | 20 | 13400 | 95 | Blended | 2.493% | 0% | 2.493% | 0% | 2.493% | 0% | TRUE | 2.493% | 0% | 2.493% | 0%
AGRICO_6_PL3N5 | Peaker | 2022 | nonsummer | 38959 | 533.215 | 0 | 1060 | 22.69 | 24051.4 | 0 | Individual | 2.217% | 0% |  |  | 2.217% | 0% | TRUE |  |  | 2.217% | 0%
AGRICO_6_PL3N5 | Peaker | 2022 | summer | 38959 | 35.1383 | 730.7462 | 765 | 22.69 | 17357.85 | 0 | Individual | 0.2024% | 4.21% |  |  | 0.2024% | 4.21% | TRUE |  |  | 0.2024% | 4.21%
AGRICO_6_PL3N5 | Peaker | 2023 | nonsummer | 38959 | 366.4435 | 37.74 | 1060 | 22.69 | 24051.4 | 0 | Individual | 1.524% | 0.1569% |  |  | 1.524% | 0.1569% | TRUE |  |  | 1.524% | 0.1569%
AGRICO_6_PL3N5 | Peaker | 2023 | summer | 38959 | 124.3895 | 462.65 | 765 | 22.69 | 17357.85 | 0 | Individual | 0.7166% | 2.665% |  |  | 0.7166% | 2.665% | TRUE |  |  | 0.7166% | 2.665%
AGRICO_6_PL3N5 | Peaker | 2024 | nonsummer | 38959 | 89.6255 | 49.5723 | 1065 | 22.69 | 24164.85 | 0 | Individual | 0.3709% | 0.2051% |  |  | 0.3709% | 0.2051% | TRUE |  |  | 0.3709% | 0.2051%
AGRICO_6_PL3N5 | Peaker | 2024 | summer | 38959 | 138.4532 | 1096.0377 | 765 | 22.69 | 17357.85 | 0 | Individual | 0.7976% | 6.314% |  |  | 0.7976% | 6.314% | TRUE |  |  | 0.7976% | 6.314%
ALMEGT_1_UNIT 1 | Peaker | 2022 | nonsummer | 31413 | 11621.7333 | 1056 | 1060 | 25 | 26500 | 0 | Individual | 43.86% | 3.985% |  |  | 43.86% | 3.985% | TRUE |  |  | 43.86% | 3.985%
ALMEGT_1_UNIT 1 | Peaker | 2022 | summer | 31413 | 4400 | 1020 | 765 | 25 | 19125 | 0 | Individual | 23.01% | 5.333% |  |  | 23.01% | 5.333% | TRUE |  |  | 23.01% | 5.333%
ALMEGT_1_UNIT 1 | Peaker | 2023 | nonsummer | 31413 | 148.6 | 1024 | 1060 | 25 | 26500 | 0 | Individual | 0.5608% | 3.864% |  |  | 0.5608% | 3.864% | TRUE |  |  | 0.5608% | 3.864%
ALMEGT_1_UNIT 1 | Peaker | 2023 | summer | 31413 | 5900.7833 | 3790.6167 | 765 | 25 | 19125 | 0 | Individual | 30.85% | 19.82% |  |  | 30.85% | 19.82% | TRUE |  |  | 30.85% | 19.82%
ALMEGT_1_UNIT 1 | Peaker | 2024 | nonsummer | 31413 | 272 | 940 | 1065 | 25 | 26625 | 0 | Individual | 1.022% | 3.531% |  |  | 1.022% | 3.531% | TRUE |  |  | 1.022% | 3.531%
ALMEGT_1_UNIT 1 | Peaker | 2024 | summer | 31413 | 8.4333 | 1235.4 | 765 | 25 | 19125 | 0 | Individual | 0.0441% | 6.46% |  |  | 0.0441% | 6.46% | TRUE |  |  | 0.0441% | 6.46%
ALMEGT_1_UNIT 2 | Peaker | 2022 | nonsummer | 31413 | 3372.75 | 1530 | 1060 | 25 | 26500 | 0 | Individual | 12.73% | 5.774% |  |  | 12.73% | 5.774% | TRUE |  |  | 12.73% | 5.774%
ALMEGT_1_UNIT 2 | Peaker | 2022 | summer | 31413 | 25 | 1235 | 765 | 25 | 19125 | 0 | Individual | 0.1307% | 6.458% |  |  | 0.1307% | 6.458% | TRUE |  |  | 0.1307% | 6.458%
ALMEGT_1_UNIT 2 | Peaker | 2023 | nonsummer | 31413 | 148.6 | 1024 | 1060 | 25 | 26500 | 0 | Individual | 0.5608% | 3.864% |  |  | 0.5608% | 3.864% | TRUE |  |  | 0.5608% | 3.864%
ALMEGT_1_UNIT 2 | Peaker | 2023 | summer | 31413 | 6035.5 | 3694.6167 | 765 | 25 | 19125 | 0 | Individual | 31.56% | 19.32% |  |  | 31.56% | 19.32% | TRUE |  |  | 31.56% | 19.32%
ALMEGT_1_UNIT 2 | Peaker | 2024 | nonsummer | 31413 | 272 | 940 | 1065 | 25 | 26625 | 0 | Individual | 1.022% | 3.531% |  |  | 1.022% | 3.531% | TRUE |  |  | 1.022% | 3.531%
ALMEGT_1_UNIT 2 | Peaker | 2024 | summer | 31413 | 8.4333 | 1191 | 765 | 25 | 19125 | 0 | Individual | 0.0441% | 6.227% |  |  | 0.0441% | 6.227% | TRUE |  |  | 0.0441% | 6.227%
ANAHM_2_CANYN1 | Peaker | 2022 | nonsummer | 40802 | 436.3667 | 0 | 1060 | 49.21 | 52162.6 | 0 | Individual | 0.8366% | 0% |  |  | 0.8366% | 0% | TRUE |  |  | 0.8366% | 0%
ANAHM_2_CANYN1 | Peaker | 2022 | summer | 40802 | 1228.5443 | 0 | 765 | 49.21 | 37645.65 | 0 | Individual | 3.263% | 0% |  |  | 3.263% | 0% | TRUE |  |  | 3.263% | 0%
ANAHM_2_CANYN1 | Peaker | 2023 | nonsummer | 40802 | 24453.2692 | 0 | 1060 | 49.21 | 52162.6 | 0 | Individual | 46.88% | 0% |  |  | 46.88% | 0% | TRUE |  |  | 46.88% | 0%
ANAHM_2_CANYN1 | Peaker | 2023 | summer | 40802 | 30018.1 | 0 | 765 | 49.21 | 37645.65 | 0 | Individual | 79.74% | 0% |  |  | 79.74% | 0% | TRUE |  |  | 79.74% | 0%
ANAHM_2_CANYN1 | Peaker | 2024 | nonsummer | 40802 | 50146.6303 | 0 | 1065 | 49.21 | 52408.65 | 0 | Individual | 95.68% | 0% |  |  | 95.68% | 0% | TRUE |  |  | 95.68% | 0%
ANAHM_2_CANYN1 | Peaker | 2024 | summer | 40802 | 32478.6 | 0 | 765 | 49.21 | 37645.65 | 0 | Individual | 86.27% | 0% |  |  | 86.27% | 0% | TRUE |  |  | 86.27% | 0%
ANAHM_2_CANYN2 | Peaker | 2022 | nonsummer | 40802 | 252.7633 | 0 | 1060 | 48.04 | 50922.4 | 0 | Individual | 0.4964% | 0% |  |  | 0.4964% | 0% | TRUE |  |  | 0.4964% | 0%
ANAHM_2_CANYN2 | Peaker | 2022 | summer | 40802 | 1024.0527 | 0 | 765 | 48.04 | 36750.6 | 0 | Individual | 2.786% | 0% |  |  | 2.786% | 0% | TRUE |  |  | 2.786% | 0%
ANAHM_2_CANYN2 | Peaker | 2023 | nonsummer | 40802 | 144.12 | 0 | 1060 | 48.04 | 50922.4 | 0 | Individual | 0.283% | 0% |  |  | 0.283% | 0% | TRUE |  |  | 0.283% | 0%
ANAHM_2_CANYN2 | Peaker | 2023 | summer | 40802 | 0 | 0 | 765 | 48.04 | 36750.6 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
ANAHM_2_CANYN2 | Peaker | 2024 | nonsummer | 40802 | 0 | 0 | 1065 | 48.04 | 51162.6 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
ANAHM_2_CANYN2 | Peaker | 2024 | summer | 40802 | 53.6447 | 0 | 765 | 48.04 | 36750.6 | 0 | Individual | 0.146% | 0% |  |  | 0.146% | 0% | TRUE |  |  | 0.146% | 0%
ANAHM_2_CANYN3 | Peaker | 2022 | nonsummer | 40754 | 626.15 | 0 | 1060 | 46.49 | 49279.4 | 0 | Individual | 1.271% | 0% |  |  | 1.271% | 0% | TRUE |  |  | 1.271% | 0%
ANAHM_2_CANYN3 | Peaker | 2022 | summer | 40754 | 1383.8523 | 0 | 765 | 46.49 | 35564.85 | 0 | Individual | 3.891% | 0% |  |  | 3.891% | 0% | TRUE |  |  | 3.891% | 0%
ANAHM_2_CANYN3 | Peaker | 2023 | nonsummer | 40754 | 2789.4 | 0 | 1060 | 46.49 | 49279.4 | 0 | Individual | 5.66% | 0% |  |  | 5.66% | 0% | TRUE |  |  | 5.66% | 0%
ANAHM_2_CANYN3 | Peaker | 2023 | summer | 40754 | 0 | 0 | 765 | 46.49 | 35564.85 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
ANAHM_2_CANYN3 | Peaker | 2024 | nonsummer | 40754 | 4339.0667 | 0 | 1065 | 46.49 | 49511.85 | 0 | Individual | 8.764% | 0% |  |  | 8.764% | 0% | TRUE |  |  | 8.764% | 0%
ANAHM_2_CANYN3 | Peaker | 2024 | summer | 40754 | 51.9138 | 0 | 765 | 46.49 | 35564.85 | 0 | Individual | 0.146% | 0% |  |  | 0.146% | 0% | TRUE |  |  | 0.146% | 0%
ANAHM_2_CANYN4 | Peaker | 2022 | nonsummer | 40754 | 298.87 | 0 | 1060 | 49.8 | 52788 | 0 | Individual | 0.5662% | 0% |  |  | 0.5662% | 0% | TRUE |  |  | 0.5662% | 0%
ANAHM_2_CANYN4 | Peaker | 2022 | summer | 40754 | 1183.227 | 0 | 765 | 49.8 | 38097 | 0 | Individual | 3.106% | 0% |  |  | 3.106% | 0% | TRUE |  |  | 3.106% | 0%
ANAHM_2_CANYN4 | Peaker | 2023 | nonsummer | 40754 | 1766.7 | 0 | 1060 | 49.8 | 52788 | 0 | Individual | 3.347% | 0% |  |  | 3.347% | 0% | TRUE |  |  | 3.347% | 0%
ANAHM_2_CANYN4 | Peaker | 2023 | summer | 40754 | 0 | 0 | 765 | 49.8 | 38097 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
ANAHM_2_CANYN4 | Peaker | 2024 | nonsummer | 40754 | 642.42 | 0 | 1065 | 49.8 | 53037 | 0 | Individual | 1.211% | 0% |  |  | 1.211% | 0% | TRUE |  |  | 1.211% | 0%
ANAHM_2_CANYN4 | Peaker | 2024 | summer | 40754 | 196.71 | 0 | 765 | 49.8 | 38097 | 0 | Individual | 0.5163% | 0% |  |  | 0.5163% | 0% | TRUE |  |  | 0.5163% | 0%
BARRE_6_PEAKER | Peaker | 2022 | nonsummer | 39345 | 390.8833 | 1171.65 | 1060 | 49 | 51940 | 0 | Individual | 0.7526% | 2.256% |  |  | 0.7526% | 2.256% | TRUE |  |  | 0.7526% | 2.256%
BARRE_6_PEAKER | Peaker | 2022 | summer | 39345 | 111.626 | 4049.6875 | 765 | 49 | 37485 | 0 | Individual | 0.2978% | 10.8% |  |  | 0.2978% | 10.8% | TRUE |  |  | 0.2978% | 10.8%
BARRE_6_PEAKER | Peaker | 2023 | nonsummer | 39345 | 1549.6667 | 2299.3433 | 1060 | 49 | 51940 | 0 | Individual | 2.984% | 4.427% |  |  | 2.984% | 4.427% | TRUE |  |  | 2.984% | 4.427%
BARRE_6_PEAKER | Peaker | 2023 | summer | 39345 | 764.1315 | 4101.7433 | 765 | 49 | 37485 | 0 | Individual | 2.038% | 10.94% |  |  | 2.038% | 10.94% | TRUE |  |  | 2.038% | 10.94%
BARRE_6_PEAKER | Peaker | 2024 | nonsummer | 39345 | 847.4567 | 1630.7687 | 1065 | 49 | 52185 | 0 | Individual | 1.624% | 3.125% |  |  | 1.624% | 3.125% | TRUE |  |  | 1.624% | 3.125%
BARRE_6_PEAKER | Peaker | 2024 | summer | 39345 | 0 | 4066.61 | 765 | 49 | 37485 | 0 | Individual | 0% | 10.85% |  |  | 0% | 10.85% | TRUE |  |  | 0% | 10.85%
BASICE_2_UNITS | Peaker | 2022 | nonsummer | 32581 | 12272.9333 | 2084.64 | 1060 | 120 | 127200 | 0 | Individual | 9.649% | 1.639% |  |  | 9.649% | 1.639% | TRUE |  |  | 9.649% | 1.639%
BASICE_2_UNITS | Peaker | 2022 | summer | 32581 | 291.5667 | 2491.5167 | 765 | 120 | 91800 | 0 | Individual | 0.3176% | 2.714% |  |  | 0.3176% | 2.714% | TRUE |  |  | 0.3176% | 2.714%
BASICE_2_UNITS | Peaker | 2023 | nonsummer | 32581 | 1946.0333 | 305 | 1060 | 120 | 127200 | 0 | Individual | 1.53% | 0.2398% |  |  | 1.53% | 0.2398% | TRUE |  |  | 1.53% | 0.2398%
BASICE_2_UNITS | Peaker | 2023 | summer | 32581 | 934.0258 | 1815.4602 | 765 | 120 | 91800 | 0 | Individual | 1.017% | 1.978% |  |  | 1.017% | 1.978% | TRUE |  |  | 1.017% | 1.978%
BASICE_2_UNITS | Peaker | 2024 | nonsummer | 32581 | 11046 | 657 | 1065 | 120 | 127800 | 0 | Individual | 8.643% | 0.5141% |  |  | 8.643% | 0.5141% | TRUE |  |  | 8.643% | 0.5141%
BASICE_2_UNITS | Peaker | 2024 | summer | 32581 | 10066.6 | 1567.3667 | 765 | 120 | 91800 | 0 | Individual | 10.97% | 1.707% |  |  | 10.97% | 1.707% | TRUE |  |  | 10.97% | 1.707%
BDGRCK_1_UNITS | Peaker | 2022 | nonsummer | 33329 | 70.42 | 3867.2 | 1060 | 48.08 | 50964.8 | 0 | Individual | 0.1382% | 7.588% |  |  | 0.1382% | 7.588% | TRUE |  |  | 0.1382% | 7.588%
BDGRCK_1_UNITS | Peaker | 2022 | summer | 33329 | 178.2 | 3180.58 | 765 | 48.08 | 36781.2 | 0 | Individual | 0.4845% | 8.647% |  |  | 0.4845% | 8.647% | TRUE |  |  | 0.4845% | 8.647%
BDGRCK_1_UNITS | Peaker | 2023 | nonsummer | 33329 | 319.675 | 3435.32 | 1060 | 48.08 | 50964.8 | 0 | Individual | 0.6272% | 6.741% |  |  | 0.6272% | 6.741% | TRUE |  |  | 0.6272% | 6.741%
BDGRCK_1_UNITS | Peaker | 2023 | summer | 33329 | 3481.6 | 2380.5 | 765 | 48.08 | 36781.2 | 0 | Individual | 9.466% | 6.472% |  |  | 9.466% | 6.472% | TRUE |  |  | 9.466% | 6.472%
BDGRCK_1_UNITS | Peaker | 2024 | nonsummer | 33329 | 932.6667 | 3699.28 | 1065 | 48.08 | 51205.2 | 0 | Individual | 1.821% | 7.224% |  |  | 1.821% | 7.224% | TRUE |  |  | 1.821% | 7.224%
BDGRCK_1_UNITS | Peaker | 2024 | summer | 33329 | 1056.3 | 2804 | 765 | 48.08 | 36781.2 | 0 | Individual | 2.872% | 7.623% |  |  | 2.872% | 7.623% | TRUE |  |  | 2.872% | 7.623%
BEARMT_1_UNIT | Peaker | 2022 | nonsummer | 34792 | 3.8 | 2870.56 | 1060 | 49.21 | 52162.6 | 0 | Individual | 0.007285% | 5.503% |  |  | 0.007285% | 5.503% | TRUE |  |  | 0.007285% | 5.503%
BEARMT_1_UNIT | Peaker | 2022 | summer | 34792 | 0 | 3141.3 | 765 | 49.21 | 37645.65 | 0 | Individual | 0% | 8.344% |  |  | 0% | 8.344% | TRUE |  |  | 0% | 8.344%
BEARMT_1_UNIT | Peaker | 2023 | nonsummer | 34792 | 581.3167 | 3821.77 | 1060 | 49.21 | 52162.6 | 0 | Individual | 1.114% | 7.327% |  |  | 1.114% | 7.327% | TRUE |  |  | 1.114% | 7.327%
BEARMT_1_UNIT | Peaker | 2023 | summer | 34792 | 214.9917 | 3743.65 | 765 | 49.21 | 37645.65 | 0 | Individual | 0.5711% | 9.944% |  |  | 0.5711% | 9.944% | TRUE |  |  | 0.5711% | 9.944%
BEARMT_1_UNIT | Peaker | 2024 | nonsummer | 34792 | 0 | 3701.6783 | 1065 | 49.21 | 52408.65 | 0 | Individual | 0% | 7.063% |  |  | 0% | 7.063% | TRUE |  |  | 0% | 7.063%
BEARMT_1_UNIT | Peaker | 2024 | summer | 34792 | 235.6333 | 3451.31 | 765 | 49.21 | 37645.65 | 0 | Individual | 0.6259% | 9.168% |  |  | 0.6259% | 9.168% | TRUE |  |  | 0.6259% | 9.168%
BOGUE_1_UNITA1 | Peaker | 2022 | nonsummer | 37613 | 1898.4467 | 0 | 1060 | 48.69 | 51611.4 | 0 | Individual | 3.678% | 0% |  |  | 3.678% | 0% | TRUE |  |  | 3.678% | 0%
BOGUE_1_UNITA1 | Peaker | 2022 | summer | 37613 | 534.7843 | 792.527 | 765 | 48.69 | 37247.85 | 0 | Individual | 1.436% | 2.128% |  |  | 1.436% | 2.128% | TRUE |  |  | 1.436% | 2.128%
BOGUE_1_UNITA1 | Peaker | 2023 | nonsummer | 37613 | 0 | 27.133 | 1060 | 48.69 | 51611.4 | 0 | Individual | 0% | 0.05257% |  |  | 0% | 0.05257% | TRUE |  |  | 0% | 0.05257%
BOGUE_1_UNITA1 | Peaker | 2023 | summer | 37613 | 497.5502 | 478.9167 | 765 | 48.69 | 37247.85 | 0 | Individual | 1.336% | 1.286% |  |  | 1.336% | 1.286% | TRUE |  |  | 1.336% | 1.286%
BOGUE_1_UNITA1 | Peaker | 2024 | nonsummer | 37613 | 997.639 | 418.8 | 1065 | 48.69 | 51854.85 | 0 | Individual | 1.924% | 0.8076% |  |  | 1.924% | 0.8076% | TRUE |  |  | 1.924% | 0.8076%
BOGUE_1_UNITA1 | Peaker | 2024 | summer | 37613 | 626.0272 | 1791.3625 | 765 | 48.69 | 37247.85 | 0 | Individual | 1.681% | 4.809% |  |  | 1.681% | 4.809% | TRUE |  |  | 1.681% | 4.809%
BORDER_6_UNITA1 | Peaker | 2022 | nonsummer | 37190 | 5210.5 | 0 | 1060 | 51.25 | 54325 | 0 | Individual | 9.591% | 0% |  |  | 9.591% | 0% | TRUE |  |  | 9.591% | 0%
BORDER_6_UNITA1 | Peaker | 2022 | summer | 37190 | 1085.1698 | 353.5093 | 765 | 51.25 | 39206.25 | 0 | Individual | 2.768% | 0.9017% |  |  | 2.768% | 0.9017% | TRUE |  |  | 2.768% | 0.9017%
BORDER_6_UNITA1 | Peaker | 2023 | nonsummer | 37190 | 1537.3958 | 0 | 1060 | 51.25 | 54325 | 0 | Individual | 2.83% | 0% |  |  | 2.83% | 0% | TRUE |  |  | 2.83% | 0%
BORDER_6_UNITA1 | Peaker | 2023 | summer | 37190 | 1136.8108 | 6.375 | 765 | 51.25 | 39206.25 | 0 | Individual | 2.9% | 0.01626% |  |  | 2.9% | 0.01626% | TRUE |  |  | 2.9% | 0.01626%
BORDER_6_UNITA1 | Peaker | 2024 | nonsummer | 37190 | 3910.375 | 0 | 1065 | 51.25 | 54581.25 | 0 | Individual | 7.164% | 0% |  |  | 7.164% | 0% | TRUE |  |  | 7.164% | 0%
BORDER_6_UNITA1 | Peaker | 2024 | summer | 37190 | 466.685 | 0 | 765 | 51.25 | 39206.25 | 0 | Individual | 1.19% | 0% |  |  | 1.19% | 0% | TRUE |  |  | 1.19% | 0%
CARLS1_2_CARCT1 | Peaker | 2022 | nonsummer | 43423 | 86102.6633 | 184.3 | 1060 | 422 | 447320 | 0 | Individual | 19.25% | 0.0412% |  |  | 19.25% | 0.0412% | TRUE |  |  | 19.25% | 0.0412%
CARLS1_2_CARCT1 | Peaker | 2022 | summer | 43423 | 19325.1842 | 40115.4917 | 765 | 422 | 322830 | 0 | Individual | 5.986% | 12.43% |  |  | 5.986% | 12.43% | TRUE |  |  | 5.986% | 12.43%
CARLS1_2_CARCT1 | Peaker | 2023 | nonsummer | 43423 | 5541.7 | 263.7 | 1060 | 422 | 447320 | 0 | Individual | 1.239% | 0.05895% |  |  | 1.239% | 0.05895% | TRUE |  |  | 1.239% | 0.05895%
CARLS1_2_CARCT1 | Peaker | 2023 | summer | 43423 | 922.9767 | 8993.1 | 765 | 422 | 322830 | 0 | Individual | 0.2859% | 2.786% |  |  | 0.2859% | 2.786% | TRUE |  |  | 0.2859% | 2.786%
CARLS1_2_CARCT1 | Peaker | 2024 | nonsummer | 43423 | 4639.075 | 0 | 1065 | 422 | 449430 | 0 | Individual | 1.032% | 0% |  |  | 1.032% | 0% | TRUE |  |  | 1.032% | 0%
CARLS1_2_CARCT1 | Peaker | 2024 | summer | 43423 | 1941.6733 | 4390.2 | 765 | 422 | 322830 | 0 | Individual | 0.6015% | 1.36% |  |  | 0.6015% | 1.36% | TRUE |  |  | 0.6015% | 1.36%
CARLS2_1_CARCT1 | Peaker | 2022 | nonsummer | 43424 | 1118.9578 | 70.01 | 1060 | 105.5 | 111830 | 0 | Individual | 1.001% | 0.0626% |  |  | 1.001% | 0.0626% | TRUE |  |  | 1.001% | 0.0626%
CARLS2_1_CARCT1 | Peaker | 2022 | summer | 43424 | 447.2042 | 1683.56 | 765 | 105.5 | 80707.5 | 0 | Individual | 0.5541% | 2.086% |  |  | 0.5541% | 2.086% | TRUE |  |  | 0.5541% | 2.086%
CARLS2_1_CARCT1 | Peaker | 2023 | nonsummer | 43424 | 61.5417 | 16.5717 | 1060 | 105.5 | 111830 | 0 | Individual | 0.05503% | 0.01482% |  |  | 0.05503% | 0.01482% | TRUE |  |  | 0.05503% | 0.01482%
CARLS2_1_CARCT1 | Peaker | 2023 | summer | 43424 | 186.7247 | 795.33 | 765 | 105.5 | 80707.5 | 0 | Individual | 0.2314% | 0.9854% |  |  | 0.2314% | 0.9854% | TRUE |  |  | 0.2314% | 0.9854%
CARLS2_1_CARCT1 | Peaker | 2024 | nonsummer | 43424 | 365.2133 | 10.48 | 1065 | 105.5 | 112357.5 | 0 | Individual | 0.325% | 0.009327% |  |  | 0.325% | 0.009327% | TRUE |  |  | 0.325% | 0.009327%
CARLS2_1_CARCT1 | Peaker | 2024 | summer | 43424 | 8778.4317 | 2518.93 | 765 | 105.5 | 80707.5 | 0 | Individual | 10.88% | 3.121% |  |  | 10.88% | 3.121% | TRUE |  |  | 10.88% | 3.121%
CENTER_6_PEAKER | Peaker | 2022 | nonsummer | 39345 | 1236.8 | 27.9 | 1060 | 47.3 | 50138 | 0 | Individual | 2.467% | 0.05565% |  |  | 2.467% | 0.05565% | TRUE |  |  | 2.467% | 0.05565%
CENTER_6_PEAKER | Peaker | 2022 | summer | 39345 | 14.395 | 524.93 | 765 | 47.3 | 36184.5 | 0 | Individual | 0.03978% | 1.451% |  |  | 0.03978% | 1.451% | TRUE |  |  | 0.03978% | 1.451%
CENTER_6_PEAKER | Peaker | 2023 | nonsummer | 39345 | 4636.9767 | 241.72 | 1060 | 47.3 | 50138 | 0 | Individual | 9.248% | 0.4821% |  |  | 9.248% | 0.4821% | TRUE |  |  | 9.248% | 0.4821%
CENTER_6_PEAKER | Peaker | 2023 | summer | 39345 | 575.055 | 366.49 | 765 | 47.3 | 36184.5 | 0 | Individual | 1.589% | 1.013% |  |  | 1.589% | 1.013% | TRUE |  |  | 1.589% | 1.013%
CENTER_6_PEAKER | Peaker | 2024 | nonsummer | 39345 | 1801.3417 | 0.04 | 1065 | 47.3 | 50374.5 | 0 | Individual | 3.576% | 7.941e-05% |  |  | 3.576% | 7.941e-05% | TRUE |  |  | 3.576% | 7.941e-05%
CENTER_6_PEAKER | Peaker | 2024 | summer | 39345 | 351.166 | 617.36 | 765 | 47.3 | 36184.5 | 0 | Individual | 0.9705% | 1.706% |  |  | 0.9705% | 1.706% | TRUE |  |  | 0.9705% | 1.706%
CENTRY_6_PL1X4 | Peaker | 2022 | nonsummer | 37151 | 4252.15 | 0 | 1060 | 41.4 | 43884 | 0 | Individual | 9.69% | 0% |  |  | 9.69% | 0% | TRUE |  |  | 9.69% | 0%
CENTRY_6_PL1X4 | Peaker | 2022 | summer | 37151 | 3145.8333 | 1217 | 765 | 41.4 | 31671 | 0 | Individual | 9.933% | 3.843% |  |  | 9.933% | 3.843% | TRUE |  |  | 9.933% | 3.843%
CENTRY_6_PL1X4 | Peaker | 2023 | nonsummer | 37151 | 3167.65 | 0 | 1060 | 41.4 | 43884 | 0 | Individual | 7.218% | 0% |  |  | 7.218% | 0% | TRUE |  |  | 7.218% | 0%
CENTRY_6_PL1X4 | Peaker | 2023 | summer | 37151 | 1952.95 | 0 | 765 | 41.4 | 31671 | 0 | Individual | 6.166% | 0% |  |  | 6.166% | 0% | TRUE |  |  | 6.166% | 0%
CENTRY_6_PL1X4 | Peaker | 2024 | nonsummer | 37151 | 13294.35 | 0 | 1065 | 41.4 | 44091 | 0 | Individual | 30.15% | 0% |  |  | 30.15% | 0% | TRUE |  |  | 30.15% | 0%
CENTRY_6_PL1X4 | Peaker | 2024 | summer | 37151 | 0 | 0 | 765 | 41.4 | 31671 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
CHALK_1_UNIT | Peaker | 2022 | nonsummer | 32952 | 0 | 3461.1785 | 1060 | 48.67 | 51590.2 | 0 | Individual | 0% | 6.709% |  |  | 0% | 6.709% | TRUE |  |  | 0% | 6.709%
CHALK_1_UNIT | Peaker | 2022 | summer | 32952 | 720.6233 | 2680.76 | 765 | 48.67 | 37232.55 | 0 | Individual | 1.935% | 7.2% |  |  | 1.935% | 7.2% | TRUE |  |  | 1.935% | 7.2%
CHALK_1_UNIT | Peaker | 2023 | nonsummer | 32952 | 0 | 3522.265 | 1060 | 48.67 | 51590.2 | 0 | Individual | 0% | 6.827% |  |  | 0% | 6.827% | TRUE |  |  | 0% | 6.827%
CHALK_1_UNIT | Peaker | 2023 | summer | 32952 | 196.0567 | 3745.35 | 765 | 48.67 | 37232.55 | 0 | Individual | 0.5266% | 10.06% |  |  | 0.5266% | 10.06% | TRUE |  |  | 0.5266% | 10.06%
CHALK_1_UNIT | Peaker | 2024 | nonsummer | 32952 | 0 | 3285.51 | 1065 | 48.67 | 51833.55 | 0 | Individual | 0% | 6.339% |  |  | 0% | 6.339% | TRUE |  |  | 0% | 6.339%
CHALK_1_UNIT | Peaker | 2024 | summer | 32952 | 88 | 3401.99 | 765 | 48.67 | 37232.55 | 0 | Individual | 0.2364% | 9.137% |  |  | 0.2364% | 9.137% | TRUE |  |  | 0.2364% | 9.137%
COCOPP_2_CTG1 | Peaker | 2022 | nonsummer | 41395 | 0 | 3656.98 | 1060 | 204.2 | 216452 | 0 | Individual | 0% | 1.69% |  |  | 0% | 1.69% | TRUE |  |  | 0% | 1.69%
COCOPP_2_CTG1 | Peaker | 2022 | summer | 41395 | 0 | 7895.8273 | 765 | 204.2 | 156213 | 0 | Individual | 0% | 5.055% |  |  | 0% | 5.055% | TRUE |  |  | 0% | 5.055%
COCOPP_2_CTG1 | Peaker | 2023 | nonsummer | 41395 | 5555.8867 | 3336.91 | 1060 | 204.2 | 216452 | 0 | Individual | 2.567% | 1.542% |  |  | 2.567% | 1.542% | TRUE |  |  | 2.567% | 1.542%
COCOPP_2_CTG1 | Peaker | 2023 | summer | 41395 | 0 | 7795.4 | 765 | 204.2 | 156213 | 0 | Individual | 0% | 4.99% |  |  | 0% | 4.99% | TRUE |  |  | 0% | 4.99%
COCOPP_2_CTG1 | Peaker | 2024 | nonsummer | 41395 | 0 | 3300.59 | 1065 | 204.2 | 217473 | 0 | Individual | 0% | 1.518% |  |  | 0% | 1.518% | TRUE |  |  | 0% | 1.518%
COCOPP_2_CTG1 | Peaker | 2024 | summer | 41395 | 0 | 8024.22 | 765 | 204.2 | 156213 | 0 | Individual | 0% | 5.137% |  |  | 0% | 5.137% | TRUE |  |  | 0% | 5.137%
COCOPP_2_CTG2 | Peaker | 2022 | nonsummer | 41395 | 0 | 3049.65 | 1060 | 202.7 | 214862 | 0 | Individual | 0% | 1.419% |  |  | 0% | 1.419% | TRUE |  |  | 0% | 1.419%
COCOPP_2_CTG2 | Peaker | 2022 | summer | 41395 | 962.24 | 7338.6555 | 765 | 202.7 | 155065.5 | 0 | Individual | 0.6205% | 4.733% |  |  | 0.6205% | 4.733% | TRUE |  |  | 0.6205% | 4.733%
COCOPP_2_CTG2 | Peaker | 2023 | nonsummer | 41395 | 11145.29 | 2812.33 | 1060 | 202.7 | 214862 | 0 | Individual | 5.187% | 1.309% |  |  | 5.187% | 1.309% | TRUE |  |  | 5.187% | 1.309%
COCOPP_2_CTG2 | Peaker | 2023 | summer | 41395 | 0 | 7260.76 | 765 | 202.7 | 155065.5 | 0 | Individual | 0% | 4.682% |  |  | 0% | 4.682% | TRUE |  |  | 0% | 4.682%
COCOPP_2_CTG2 | Peaker | 2024 | nonsummer | 41395 | 0 | 2865.9 | 1065 | 202.7 | 215875.5 | 0 | Individual | 0% | 1.328% |  |  | 0% | 1.328% | TRUE |  |  | 0% | 1.328%
COCOPP_2_CTG2 | Peaker | 2024 | summer | 41395 | 182.8933 | 7489.46 | 765 | 202.7 | 155065.5 | 0 | Individual | 0.1179% | 4.83% |  |  | 0.1179% | 4.83% | TRUE |  |  | 0.1179% | 4.83%
COCOPP_2_CTG3 | Peaker | 2022 | nonsummer | 41395 | 1077.9 | 10157.1207 | 1060 | 208.96 | 221497.6 | 0 | Individual | 0.4866% | 4.586% |  |  | 0.4866% | 4.586% | TRUE |  |  | 0.4866% | 4.586%
COCOPP_2_CTG3 | Peaker | 2022 | summer | 41395 | 0 | 12616.235 | 765 | 208.96 | 159854.4 | 0 | Individual | 0% | 7.892% |  |  | 0% | 7.892% | TRUE |  |  | 0% | 7.892%
COCOPP_2_CTG3 | Peaker | 2023 | nonsummer | 41395 | 4645.8773 | 10228.8767 | 1060 | 208.96 | 221497.6 | 0 | Individual | 2.097% | 4.618% |  |  | 2.097% | 4.618% | TRUE |  |  | 2.097% | 4.618%
COCOPP_2_CTG3 | Peaker | 2023 | summer | 41395 | 701.895 | 12517.2 | 765 | 208.96 | 159854.4 | 0 | Individual | 0.4391% | 7.83% |  |  | 0.4391% | 7.83% | TRUE |  |  | 0.4391% | 7.83%
COCOPP_2_CTG3 | Peaker | 2024 | nonsummer | 41395 | 6459.8593 | 7582.6695 | 1065 | 208.96 | 222542.4 | 0 | Individual | 2.903% | 3.407% |  |  | 2.903% | 3.407% | TRUE |  |  | 2.903% | 3.407%
COCOPP_2_CTG3 | Peaker | 2024 | summer | 41395 | 0 | 12373.18 | 765 | 208.96 | 159854.4 | 0 | Individual | 0% | 7.74% |  |  | 0% | 7.74% | TRUE |  |  | 0% | 7.74%
COCOPP_2_CTG4 | Peaker | 2022 | nonsummer | 41395 | 97.845 | 5329.1723 | 1060 | 204.29 | 216547.4 | 0 | Individual | 0.04518% | 2.461% |  |  | 0.04518% | 2.461% | TRUE |  |  | 0.04518% | 2.461%
COCOPP_2_CTG4 | Peaker | 2022 | summer | 41395 | 1915.63 | 7941.73 | 765 | 204.29 | 156281.85 | 0 | Individual | 1.226% | 5.082% |  |  | 1.226% | 5.082% | TRUE |  |  | 1.226% | 5.082%
COCOPP_2_CTG4 | Peaker | 2023 | nonsummer | 41395 | 3714.2415 | 4919.6332 | 1060 | 204.29 | 216547.4 | 0 | Individual | 1.715% | 2.272% |  |  | 1.715% | 2.272% | TRUE |  |  | 1.715% | 2.272%
COCOPP_2_CTG4 | Peaker | 2023 | summer | 41395 | 0 | 7906.81 | 765 | 204.29 | 156281.85 | 0 | Individual | 0% | 5.059% |  |  | 0% | 5.059% | TRUE |  |  | 0% | 5.059%
COCOPP_2_CTG4 | Peaker | 2024 | nonsummer | 41395 | 5288.7945 | 2785.8447 | 1065 | 204.29 | 217568.85 | 0 | Individual | 2.431% | 1.28% |  |  | 2.431% | 1.28% | TRUE |  |  | 2.431% | 1.28%
COCOPP_2_CTG4 | Peaker | 2024 | summer | 41395 | 0 | 7766.89 | 765 | 204.29 | 156281.85 | 0 | Individual | 0% | 4.97% |  |  | 0% | 4.97% | TRUE |  |  | 0% | 4.97%
COLTON_6_AGUAM1 | Peaker | 2022 | nonsummer | 37799 | 0 | 600 | 1060 | 43 | 45580 | 0 | Individual | 0% | 1.316% |  |  | 0% | 1.316% | TRUE |  |  | 0% | 1.316%
COLTON_6_AGUAM1 | Peaker | 2022 | summer | 37799 | 0 | 1227.1603 | 765 | 43 | 32895 | 0 | Individual | 0% | 3.731% |  |  | 0% | 3.731% | TRUE |  |  | 0% | 3.731%
COLTON_6_AGUAM1 | Peaker | 2023 | nonsummer | 37799 | 0 | 0 | 1060 | 43 | 45580 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
COLTON_6_AGUAM1 | Peaker | 2023 | summer | 37799 | 781.1833 | 0 | 765 | 43 | 32895 | 0 | Individual | 2.375% | 0% |  |  | 2.375% | 0% | TRUE |  |  | 2.375% | 0%
COLTON_6_AGUAM1 | Peaker | 2024 | nonsummer | 37799 | 290 | 0 | 1065 | 43 | 45795 | 0 | Individual | 0.6333% | 0% |  |  | 0.6333% | 0% | TRUE |  |  | 0.6333% | 0%
COLTON_6_AGUAM1 | Peaker | 2024 | summer | 37799 | 5188 | 3 | 765 | 43 | 32895 | 0 | Individual | 15.77% | 0.00912% |  |  | 15.77% | 0.00912% | TRUE |  |  | 15.77% | 0.00912%
CSCGNR_1_UNIT 1 | Peaker | 2022 | nonsummer | 31778 | 371.25 | 11.25 | 1060 | 24.75 | 26235 | 0 | Individual | 1.415% | 0.04288% |  |  | 1.415% | 0.04288% | TRUE |  |  | 1.415% | 0.04288%
CSCGNR_1_UNIT 1 | Peaker | 2022 | summer | 31778 | 88.0975 | 0 | 765 | 24.75 | 18933.75 | 0 | Individual | 0.4653% | 0% |  |  | 0.4653% | 0% | TRUE |  |  | 0.4653% | 0%
CSCGNR_1_UNIT 1 | Peaker | 2023 | nonsummer | 31778 | 742.5 | 0 | 1060 | 24.75 | 26235 | 0 | Individual | 2.83% | 0% |  |  | 2.83% | 0% | TRUE |  |  | 2.83% | 0%
CSCGNR_1_UNIT 1 | Peaker | 2023 | summer | 31778 | 990 | 0 | 765 | 24.75 | 18933.75 | 0 | Individual | 5.229% | 0% |  |  | 5.229% | 0% | TRUE |  |  | 5.229% | 0%
CSCGNR_1_UNIT 1 | Peaker | 2024 | nonsummer | 31778 | 3217.5 | 0 | 1065 | 24.75 | 26358.75 | 0 | Individual | 12.21% | 0% |  |  | 12.21% | 0% | TRUE |  |  | 12.21% | 0%
CSCGNR_1_UNIT 1 | Peaker | 2024 | summer | 31778 | 188.5125 | 1640.0825 | 765 | 24.75 | 18933.75 | 0 | Individual | 0.9956% | 8.662% |  |  | 0.9956% | 8.662% | TRUE |  |  | 0.9956% | 8.662%
CSCGNR_1_UNIT 2 | Peaker | 2022 | nonsummer | 31413 | 12221.15 | 0 | 1060 | 24.75 | 26235 | 0 | Individual | 46.58% | 0% |  |  | 46.58% | 0% | TRUE |  |  | 46.58% | 0%
CSCGNR_1_UNIT 2 | Peaker | 2022 | summer | 31413 | 2506.5865 | 0 | 765 | 24.75 | 18933.75 | 0 | Individual | 13.24% | 0% |  |  | 13.24% | 0% | TRUE |  |  | 13.24% | 0%
CSCGNR_1_UNIT 2 | Peaker | 2023 | nonsummer | 31413 | 5425.2543 | 0 | 1060 | 24.75 | 26235 | 0 | Individual | 20.68% | 0% |  |  | 20.68% | 0% | TRUE |  |  | 20.68% | 0%
CSCGNR_1_UNIT 2 | Peaker | 2023 | summer | 31413 | 4290.425 | 0 | 765 | 24.75 | 18933.75 | 0 | Individual | 22.66% | 0% |  |  | 22.66% | 0% | TRUE |  |  | 22.66% | 0%
CSCGNR_1_UNIT 2 | Peaker | 2024 | nonsummer | 31413 | 866.6625 | 0 | 1065 | 24.75 | 26358.75 | 0 | Individual | 3.288% | 0% |  |  | 3.288% | 0% | TRUE |  |  | 3.288% | 0%
CSCGNR_1_UNIT 2 | Peaker | 2024 | summer | 31413 | 0 | 1800.0492 | 765 | 24.75 | 18933.75 | 0 | Individual | 0% | 9.507% |  |  | 0% | 9.507% | TRUE |  |  | 0% | 9.507%
DOUBLC_1_UNITS | Peaker | 2022 | nonsummer | 32581 | 791.41 | 1555.91 | 1060 | 52.23 | 55363.8 | 0 | Individual | 1.429% | 2.81% |  |  | 1.429% | 2.81% | TRUE |  |  | 1.429% | 2.81%
DOUBLC_1_UNITS | Peaker | 2022 | summer | 32581 | 61 | 2112.5 | 765 | 52.23 | 39955.95 | 0 | Individual | 0.1527% | 5.287% |  |  | 0.1527% | 5.287% | TRUE |  |  | 0.1527% | 5.287%
DOUBLC_1_UNITS | Peaker | 2023 | nonsummer | 32581 | 5310.15 | 1931.97 | 1060 | 52.23 | 55363.8 | 0 | Individual | 9.591% | 3.49% |  |  | 9.591% | 3.49% | TRUE |  |  | 9.591% | 3.49%
DOUBLC_1_UNITS | Peaker | 2023 | summer | 32581 | 1028.1117 | 2126.65 | 765 | 52.23 | 39955.95 | 0 | Individual | 2.573% | 5.322% |  |  | 2.573% | 5.322% | TRUE |  |  | 2.573% | 5.322%
DOUBLC_1_UNITS | Peaker | 2024 | nonsummer | 32581 | 13456.8643 | 2406.3205 | 1065 | 52.23 | 55624.95 | 0 | Individual | 24.19% | 4.326% |  |  | 24.19% | 4.326% | TRUE |  |  | 24.19% | 4.326%
DOUBLC_1_UNITS | Peaker | 2024 | summer | 32581 | 389.915 | 2564.2833 | 765 | 52.23 | 39955.95 | 0 | Individual | 0.9759% | 6.418% |  |  | 0.9759% | 6.418% | TRUE |  |  | 0.9759% | 6.418%
DREWS_6_PL1X4 | Peaker | 2022 | nonsummer | 37117 | 11225 | 0 | 1060 | 41.4 | 43884 | 0 | Individual | 25.58% | 0% |  |  | 25.58% | 0% | TRUE |  |  | 25.58% | 0%
DREWS_6_PL1X4 | Peaker | 2022 | summer | 37117 | 7683.5 | 1962 | 765 | 41.4 | 31671 | 0 | Individual | 24.26% | 6.195% |  |  | 24.26% | 6.195% | TRUE |  |  | 24.26% | 6.195%
DREWS_6_PL1X4 | Peaker | 2023 | nonsummer | 37117 | 3508.6725 | 0 | 1060 | 41.4 | 43884 | 0 | Individual | 7.995% | 0% |  |  | 7.995% | 0% | TRUE |  |  | 7.995% | 0%
DREWS_6_PL1X4 | Peaker | 2023 | summer | 37117 | 4307.55 | 0 | 765 | 41.4 | 31671 | 0 | Individual | 13.6% | 0% |  |  | 13.6% | 0% | TRUE |  |  | 13.6% | 0%
DREWS_6_PL1X4 | Peaker | 2024 | nonsummer | 37117 | 4657.5 | 0 | 1065 | 41.4 | 44091 | 0 | Individual | 10.56% | 0% |  |  | 10.56% | 0% | TRUE |  |  | 10.56% | 0%
DREWS_6_PL1X4 | Peaker | 2024 | summer | 37117 | 92.7 | 0 | 765 | 41.4 | 31671 | 0 | Individual | 0.2927% | 0% |  |  | 0.2927% | 0% | TRUE |  |  | 0.2927% | 0%
ELCAJN_6_LM6K | Peaker | 2022 | nonsummer | 40345 | 1210.5167 | 0 | 1060 | 48.1 | 50986 | 0 | Individual | 2.374% | 0% |  |  | 2.374% | 0% | TRUE |  |  | 2.374% | 0%
ELCAJN_6_LM6K | Peaker | 2022 | summer | 40345 | 3123.0233 | 488.3 | 765 | 48.1 | 36796.5 | 0 | Individual | 8.487% | 1.327% |  |  | 8.487% | 1.327% | TRUE |  |  | 8.487% | 1.327%
ELCAJN_6_LM6K | Peaker | 2023 | nonsummer | 40345 | 814.275 | 0 | 1060 | 48.1 | 50986 | 0 | Individual | 1.597% | 0% |  |  | 1.597% | 0% | TRUE |  |  | 1.597% | 0%
ELCAJN_6_LM6K | Peaker | 2023 | summer | 40345 | 13655.74 | 13 | 765 | 48.1 | 36796.5 | 0 | Individual | 37.11% | 0.03533% |  |  | 37.11% | 0.03533% | TRUE |  |  | 37.11% | 0.03533%
ELCAJN_6_LM6K | Peaker | 2024 | nonsummer | 40345 | 1086.2583 | 0 | 1065 | 48.1 | 51226.5 | 0 | Individual | 2.121% | 0% |  |  | 2.121% | 0% | TRUE |  |  | 2.121% | 0%
ELCAJN_6_LM6K | Peaker | 2024 | summer | 40345 | 656.385 | 490.4 | 765 | 48.1 | 36796.5 | 0 | Individual | 1.784% | 1.333% |  |  | 1.784% | 1.333% | TRUE |  |  | 1.784% | 1.333%
ELCAJN_6_UNITA1 | Peaker | 2022 | nonsummer | 37405 | 272.117 | 0 | 1060 | 45.42 | 48145.2 | 0 | Individual | 0.5652% | 0% |  |  | 0.5652% | 0% | TRUE |  |  | 0.5652% | 0%
ELCAJN_6_UNITA1 | Peaker | 2022 | summer | 37405 | 5737.2357 | 0 | 765 | 45.42 | 34746.3 | 0 | Individual | 16.51% | 0% |  |  | 16.51% | 0% | TRUE |  |  | 16.51% | 0%
ELCAJN_6_UNITA1 | Peaker | 2023 | nonsummer | 37405 | 907.19 | 0 | 1060 | 45.42 | 48145.2 | 0 | Individual | 1.884% | 0% |  |  | 1.884% | 0% | TRUE |  |  | 1.884% | 0%
ELCAJN_6_UNITA1 | Peaker | 2023 | summer | 37405 | 2608.6147 | 0 | 765 | 45.42 | 34746.3 | 0 | Individual | 7.508% | 0% |  |  | 7.508% | 0% | TRUE |  |  | 7.508% | 0%
ELCAJN_6_UNITA1 | Peaker | 2024 | nonsummer | 37405 | 1135.5 | 0 | 1065 | 45.42 | 48372.3 | 0 | Individual | 2.347% | 0% |  |  | 2.347% | 0% | TRUE |  |  | 2.347% | 0%
ELCAJN_6_UNITA1 | Peaker | 2024 | summer | 37405 | 2210.9127 | 0 | 765 | 45.42 | 34746.3 | 0 | Individual | 6.363% | 0% |  |  | 6.363% | 0% | TRUE |  |  | 6.363% | 0%
ESCNDO_6_PL1X2 | Peaker | 2022 | nonsummer | 41664 | 4509.241 | 0 | 1060 | 48.71 | 51632.6 | 0 | Individual | 8.733% | 0% |  |  | 8.733% | 0% | TRUE |  |  | 8.733% | 0%
ESCNDO_6_PL1X2 | Peaker | 2022 | summer | 41664 | 1372.9658 | 587.76 | 765 | 48.71 | 37263.15 | 0 | Individual | 3.685% | 1.577% |  |  | 3.685% | 1.577% | TRUE |  |  | 3.685% | 1.577%
ESCNDO_6_PL1X2 | Peaker | 2023 | nonsummer | 41664 | 8332.6732 | 0 | 1060 | 48.71 | 51632.6 | 0 | Individual | 16.14% | 0% |  |  | 16.14% | 0% | TRUE |  |  | 16.14% | 0%
ESCNDO_6_PL1X2 | Peaker | 2023 | summer | 41664 | 168.5228 | 279.87 | 765 | 48.71 | 37263.15 | 0 | Individual | 0.4523% | 0.7511% |  |  | 0.4523% | 0.7511% | TRUE |  |  | 0.4523% | 0.7511%
ESCNDO_6_PL1X2 | Peaker | 2024 | nonsummer | 41664 | 5459.5792 | 0 | 1065 | 48.71 | 51876.15 | 0 | Individual | 10.52% | 0% |  |  | 10.52% | 0% | TRUE |  |  | 10.52% | 0%
ESCNDO_6_PL1X2 | Peaker | 2024 | summer | 41664 | 127.5975 | 324.3 | 765 | 48.71 | 37263.15 | 0 | Individual | 0.3424% | 0.8703% |  |  | 0.3424% | 0.8703% | TRUE |  |  | 0.3424% | 0.8703%
ESCNDO_6_UNITB1 | Peaker | 2022 | nonsummer | 37187 | 8585.6673 | 12.09 | 1060 | 50.96 | 54017.6 | 0 | Individual | 15.89% | 0.02238% |  |  | 15.89% | 0.02238% | TRUE |  |  | 15.89% | 0.02238%
ESCNDO_6_UNITB1 | Peaker | 2022 | summer | 37187 | 3171.6992 | 181.35 | 765 | 50.96 | 38984.4 | 0 | Individual | 8.136% | 0.4652% |  |  | 8.136% | 0.4652% | TRUE |  |  | 8.136% | 0.4652%
ESCNDO_6_UNITB1 | Peaker | 2023 | nonsummer | 37187 | 3348.5113 | 0 | 1060 | 50.96 | 54017.6 | 0 | Individual | 6.199% | 0% |  |  | 6.199% | 0% | TRUE |  |  | 6.199% | 0%
ESCNDO_6_UNITB1 | Peaker | 2023 | summer | 37187 | 3925.9313 | 0 | 765 | 50.96 | 38984.4 | 0 | Individual | 10.07% | 0% |  |  | 10.07% | 0% | TRUE |  |  | 10.07% | 0%
ESCNDO_6_UNITB1 | Peaker | 2024 | nonsummer | 37187 | 823.3833 | 0 | 1065 | 50.96 | 54272.4 | 0 | Individual | 1.517% | 0% |  |  | 1.517% | 0% | TRUE |  |  | 1.517% | 0%
ESCNDO_6_UNITB1 | Peaker | 2024 | summer | 37187 | 1486.6787 | 0 | 765 | 50.96 | 38984.4 | 0 | Individual | 3.814% | 0% |  |  | 3.814% | 0% | TRUE |  |  | 3.814% | 0%
ESCO_6_GLMQF | Peaker | 2022 | nonsummer | 34335 | 4696.97 | 0 | 1060 | 49.9 | 52894 | 0 | Individual | 8.88% | 0% |  |  | 8.88% | 0% | TRUE |  |  | 8.88% | 0%
ESCO_6_GLMQF | Peaker | 2022 | summer | 34335 | 6489.1547 | 0 | 765 | 49.9 | 38173.5 | 0 | Individual | 17% | 0% |  |  | 17% | 0% | TRUE |  |  | 17% | 0%
ESCO_6_GLMQF | Peaker | 2023 | nonsummer | 34335 | 7221.48 | 0.69 | 1060 | 49.9 | 52894 | 0 | Individual | 13.65% | 0.001304% |  |  | 13.65% | 0.001304% | TRUE |  |  | 13.65% | 0.001304%
ESCO_6_GLMQF | Peaker | 2023 | summer | 34335 | 2361.45 | 0 | 765 | 49.9 | 38173.5 | 0 | Individual | 6.186% | 0% |  |  | 6.186% | 0% | TRUE |  |  | 6.186% | 0%
ESCO_6_GLMQF | Peaker | 2024 | nonsummer | 34335 | 998 | 1.31 | 1065 | 49.9 | 53143.5 | 0 | Individual | 1.878% | 0.002465% |  |  | 1.878% | 0.002465% | TRUE |  |  | 1.878% | 0.002465%
ESCO_6_GLMQF | Peaker | 2024 | summer | 34335 | 374.2567 | 1421.64 | 765 | 49.9 | 38173.5 | 0 | Individual | 0.9804% | 3.724% |  |  | 0.9804% | 3.724% | TRUE |  |  | 0.9804% | 3.724%
ETIWND_2_UNIT1 | Peaker | 2022 | nonsummer | 42370 | 0 | 0 | 1060 | 33.6 | 35616 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
ETIWND_2_UNIT1 | Peaker | 2022 | summer | 42370 | 0 | 0 | 765 | 33.6 | 25704 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
ETIWND_2_UNIT1 | Peaker | 2023 | nonsummer | 42370 | 23297.04 | 0 | 1060 | 33.6 | 35616 | 0 | Individual | 65.41% | 0% |  |  | 65.41% | 0% | TRUE |  |  | 65.41% | 0%
ETIWND_2_UNIT1 | Peaker | 2023 | summer | 42370 | 22128.3 | 0 | 765 | 33.6 | 25704 | 0 | Individual | 86.09% | 0% |  |  | 86.09% | 0% | TRUE |  |  | 86.09% | 0%
ETIWND_2_UNIT1 | Peaker | 2024 | nonsummer | 42370 | 3102.96 | 0 | 1065 | 33.6 | 35784 | 0 | Individual | 8.671% | 0% |  |  | 8.671% | 0% | TRUE |  |  | 8.671% | 0%
ETIWND_2_UNIT1 | Peaker | 2024 | summer | 42370 | 0 | 0 | 765 | 33.6 | 25704 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
ETIWND_6_GRPLND | Peaker | 2022 | nonsummer | 39345 | 943.6767 | 290.8167 | 1060 | 45.64 | 48378.4 | 0 | Individual | 1.951% | 0.6011% |  |  | 1.951% | 0.6011% | TRUE |  |  | 1.951% | 0.6011%
ETIWND_6_GRPLND | Peaker | 2022 | summer | 39345 | 222.1588 | 833.92 | 765 | 45.64 | 34914.6 | 0 | Individual | 0.6363% | 2.388% |  |  | 0.6363% | 2.388% | TRUE |  |  | 0.6363% | 2.388%
ETIWND_6_GRPLND | Peaker | 2023 | nonsummer | 39345 | 453.3573 | 627.2833 | 1060 | 45.64 | 48378.4 | 0 | Individual | 0.9371% | 1.297% |  |  | 0.9371% | 1.297% | TRUE |  |  | 0.9371% | 1.297%
ETIWND_6_GRPLND | Peaker | 2023 | summer | 39345 | 2262.873 | 598.14 | 765 | 45.64 | 34914.6 | 0 | Individual | 6.481% | 1.713% |  |  | 6.481% | 1.713% | TRUE |  |  | 6.481% | 1.713%
ETIWND_6_GRPLND | Peaker | 2024 | nonsummer | 39345 | 648.088 | 12.87 | 1065 | 45.64 | 48606.6 | 0 | Individual | 1.333% | 0.02648% |  |  | 1.333% | 0.02648% | TRUE |  |  | 1.333% | 0.02648%
ETIWND_6_GRPLND | Peaker | 2024 | summer | 39345 | 1073.145 | 1085.12 | 765 | 45.64 | 34914.6 | 0 | Individual | 3.074% | 3.108% |  |  | 3.074% | 3.108% | TRUE |  |  | 3.074% | 3.108%
GILRPP_1_PL1X2 | Peaker | 2022 | nonsummer | 37285 | 0 | 8.5 | 1060 | 95.2 | 100912 | 0 | Individual | 0% | 0.008423% |  |  | 0% | 0.008423% | TRUE |  |  | 0% | 0.008423%
GILRPP_1_PL1X2 | Peaker | 2022 | summer | 37285 | 411.6667 | 79.74 | 765 | 95.2 | 72828 | 0 | Individual | 0.5653% | 0.1095% |  |  | 0.5653% | 0.1095% | TRUE |  |  | 0.5653% | 0.1095%
GILRPP_1_PL1X2 | Peaker | 2023 | nonsummer | 37285 | 0 | 0 | 1060 | 95.2 | 100912 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
GILRPP_1_PL1X2 | Peaker | 2023 | summer | 37285 | 56.2083 | 0 | 765 | 95.2 | 72828 | 0 | Individual | 0.07718% | 0% |  |  | 0.07718% | 0% | TRUE |  |  | 0.07718% | 0%
GILRPP_1_PL1X2 | Peaker | 2024 | nonsummer | 37285 | 0 | 24.5867 | 1065 | 95.2 | 101388 | 0 | Individual | 0% | 0.02425% |  |  | 0% | 0.02425% | TRUE |  |  | 0% | 0.02425%
GILRPP_1_PL1X2 | Peaker | 2024 | summer | 37285 | 479.8767 | 33.4 | 765 | 95.2 | 72828 | 0 | Individual | 0.6589% | 0.04586% |  |  | 0.6589% | 0.04586% | TRUE |  |  | 0.6589% | 0.04586%
GILRPP_1_PL3X4 | Peaker | 2022 | nonsummer | 37315 | 870.87 | 0 | 1060 | 46.2 | 48972 | 0 | Individual | 1.778% | 0% |  |  | 1.778% | 0% | TRUE |  |  | 1.778% | 0%
GILRPP_1_PL3X4 | Peaker | 2022 | summer | 37315 | 362.2967 | 6 | 765 | 46.2 | 35343 | 0 | Individual | 1.025% | 0.01698% |  |  | 1.025% | 0.01698% | TRUE |  |  | 1.025% | 0.01698%
GILRPP_1_PL3X4 | Peaker | 2023 | nonsummer | 37315 | 0 | 0 | 1060 | 46.2 | 48972 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
GILRPP_1_PL3X4 | Peaker | 2023 | summer | 37315 | 0 | 0 | 765 | 46.2 | 35343 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
GILRPP_1_PL3X4 | Peaker | 2024 | nonsummer | 37315 | 0 | 0 | 1065 | 46.2 | 49203 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
GILRPP_1_PL3X4 | Peaker | 2024 | summer | 37315 | 0 | 0 | 765 | 46.2 | 35343 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
GLNARM_7_UNIT 1 | Peaker | 2022 | nonsummer | 27760 | 211.5 | 0 | 1060 | 22.13 | 23457.8 | 0 | Individual | 0.9016% | 0% |  |  | 0.9016% | 0% | TRUE |  |  | 0.9016% | 0%
GLNARM_7_UNIT 1 | Peaker | 2022 | summer | 27760 | 300.3 | 0 | 765 | 22.13 | 16929.45 | 0 | Individual | 1.774% | 0% |  |  | 1.774% | 0% | TRUE |  |  | 1.774% | 0%
GLNARM_7_UNIT 1 | Peaker | 2023 | nonsummer | 27760 | 7356.7497 | 0 | 1060 | 22.13 | 23457.8 | 0 | Individual | 31.36% | 0% |  |  | 31.36% | 0% | TRUE |  |  | 31.36% | 0%
GLNARM_7_UNIT 1 | Peaker | 2023 | summer | 27760 | 11.4338 | 0 | 765 | 22.13 | 16929.45 | 0 | Individual | 0.06754% | 0% |  |  | 0.06754% | 0% | TRUE |  |  | 0.06754% | 0%
GLNARM_7_UNIT 1 | Peaker | 2024 | nonsummer | 27760 | 0 | 0 | 1065 | 22.13 | 23568.45 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
GLNARM_7_UNIT 1 | Peaker | 2024 | summer | 27760 | 357.7407 | 0 | 765 | 22.13 | 16929.45 | 0 | Individual | 2.113% | 0% |  |  | 2.113% | 0% | TRUE |  |  | 2.113% | 0%
GLNARM_7_UNIT 2 | Peaker | 2022 | nonsummer | 27760 | 1332.4933 | 0 | 1060 | 22.38 | 23722.8 | 0 | Individual | 5.617% | 0% |  |  | 5.617% | 0% | TRUE |  |  | 5.617% | 0%
GLNARM_7_UNIT 2 | Peaker | 2022 | summer | 27760 | 704.88 | 0 | 765 | 22.38 | 17120.7 | 0 | Individual | 4.117% | 0% |  |  | 4.117% | 0% | TRUE |  |  | 4.117% | 0%
GLNARM_7_UNIT 2 | Peaker | 2023 | nonsummer | 27760 | 895.2 | 0 | 1060 | 22.38 | 23722.8 | 0 | Individual | 3.774% | 0% |  |  | 3.774% | 0% | TRUE |  |  | 3.774% | 0%
GLNARM_7_UNIT 2 | Peaker | 2023 | summer | 27760 | 93.25 | 0 | 765 | 22.38 | 17120.7 | 0 | Individual | 0.5447% | 0% |  |  | 0.5447% | 0% | TRUE |  |  | 0.5447% | 0%
GLNARM_7_UNIT 2 | Peaker | 2024 | nonsummer | 27760 | 562.111 | 0 | 1065 | 22.38 | 23834.7 | 0 | Individual | 2.358% | 0% |  |  | 2.358% | 0% | TRUE |  |  | 2.358% | 0%
GLNARM_7_UNIT 2 | Peaker | 2024 | summer | 27760 | 979.5335 | 0 | 765 | 22.38 | 17120.7 | 0 | Individual | 5.721% | 0% |  |  | 5.721% | 0% | TRUE |  |  | 5.721% | 0%
GLNARM_7_UNIT 3 | Peaker | 2022 | nonsummer | 37994 | 1320.2435 | 0 | 1060 | 44.83 | 47519.8 | 0 | Individual | 2.778% | 0% |  |  | 2.778% | 0% | TRUE |  |  | 2.778% | 0%
GLNARM_7_UNIT 3 | Peaker | 2022 | summer | 37994 | 17.8753 | 0 | 765 | 44.83 | 34294.95 | 0 | Individual | 0.05212% | 0% |  |  | 0.05212% | 0% | TRUE |  |  | 0.05212% | 0%
GLNARM_7_UNIT 3 | Peaker | 2023 | nonsummer | 37994 | 3914.4062 | 0 | 1060 | 44.83 | 47519.8 | 0 | Individual | 8.237% | 0% |  |  | 8.237% | 0% | TRUE |  |  | 8.237% | 0%
GLNARM_7_UNIT 3 | Peaker | 2023 | summer | 37994 | 720.0465 | 0 | 765 | 44.83 | 34294.95 | 0 | Individual | 2.1% | 0% |  |  | 2.1% | 0% | TRUE |  |  | 2.1% | 0%
GLNARM_7_UNIT 3 | Peaker | 2024 | nonsummer | 37994 | 236.708 | 40.6125 | 1065 | 44.83 | 47743.95 | 0 | Individual | 0.4958% | 0.08506% |  |  | 0.4958% | 0.08506% | TRUE |  |  | 0.4958% | 0.08506%
GLNARM_7_UNIT 3 | Peaker | 2024 | summer | 37994 | 325.5165 | 55.7808 | 765 | 44.83 | 34294.95 | 0 | Individual | 0.9492% | 0.1627% |  |  | 0.9492% | 0.1627% | TRUE |  |  | 0.9492% | 0.1627%
GLNARM_7_UNIT 4 | Peaker | 2022 | nonsummer | 37994 | 3494.021 | 0 | 1060 | 42.42 | 44965.2 | 0 | Individual | 7.771% | 0% |  |  | 7.771% | 0% | TRUE |  |  | 7.771% | 0%
GLNARM_7_UNIT 4 | Peaker | 2022 | summer | 37994 | 4058.0993 | 0 | 765 | 42.42 | 32451.3 | 0 | Individual | 12.51% | 0% |  |  | 12.51% | 0% | TRUE |  |  | 12.51% | 0%
GLNARM_7_UNIT 4 | Peaker | 2023 | nonsummer | 37994 | 2544.97 | 0 | 1060 | 42.42 | 44965.2 | 0 | Individual | 5.66% | 0% |  |  | 5.66% | 0% | TRUE |  |  | 5.66% | 0%
GLNARM_7_UNIT 4 | Peaker | 2023 | summer | 37994 | 951.01 | 0 | 765 | 42.42 | 32451.3 | 0 | Individual | 2.931% | 0% |  |  | 2.931% | 0% | TRUE |  |  | 2.931% | 0%
GLNARM_7_UNIT 4 | Peaker | 2024 | nonsummer | 37994 | 149.2363 | 0 | 1065 | 42.42 | 45177.3 | 0 | Individual | 0.3303% | 0% |  |  | 0.3303% | 0% | TRUE |  |  | 0.3303% | 0%
GLNARM_7_UNIT 4 | Peaker | 2024 | summer | 37994 | 340.4127 | 38.9217 | 765 | 42.42 | 32451.3 | 0 | Individual | 1.049% | 0.1199% |  |  | 1.049% | 0.1199% | TRUE |  |  | 1.049% | 0.1199%
GOLETA_6_ELLWOD | Peaker | 2022 | nonsummer | 35914 | 6102.9 | 0 | 1060 | 54 | 57240 | 0 | Individual | 10.66% | 0% |  |  | 10.66% | 0% | TRUE |  |  | 10.66% | 0%
GOLETA_6_ELLWOD | Peaker | 2022 | summer | 35914 | 396.9 | 0 | 765 | 54 | 41310 | 0 | Individual | 0.9608% | 0% |  |  | 0.9608% | 0% | TRUE |  |  | 0.9608% | 0%
GOLETA_6_ELLWOD | Peaker | 2023 | nonsummer | 35914 | 348.3 | 0 | 1060 | 54 | 57240 | 0 | Individual | 0.6085% | 0% |  |  | 0.6085% | 0% | TRUE |  |  | 0.6085% | 0%
GOLETA_6_ELLWOD | Peaker | 2023 | summer | 35914 | 300.6 | 0 | 765 | 54 | 41310 | 0 | Individual | 0.7277% | 0% |  |  | 0.7277% | 0% | TRUE |  |  | 0.7277% | 0%
GOLETA_6_ELLWOD | Peaker | 2024 | nonsummer | 35914 | 6939 | 0 | 1065 | 54 | 57510 | 0 | Individual | 12.07% | 0% |  |  | 12.07% | 0% | TRUE |  |  | 12.07% | 0%
GOLETA_6_ELLWOD | Peaker | 2024 | summer | 35914 | 873 | 0 | 765 | 54 | 41310 | 0 | Individual | 2.113% | 0% |  |  | 2.113% | 0% | TRUE |  |  | 2.113% | 0%
HENRTA_6_ELCTG1 | Peaker | 2022 | nonsummer | 45660 | 0 | 0 | 0 | 50 | 0 | 1060 | Group |  |  | 6.683% | 1.141% | 6.683% | 1.141% | TRUE | 6.683% | 1.141% | 6.683% | 1.141%
HENRTA_6_ELCTG1 | Peaker | 2022 | summer | 45660 | 0 | 0 | 0 | 50 | 0 | 765 | Group |  |  | 3.545% | 3.836% | 3.545% | 3.836% | TRUE | 3.545% | 3.836% | 3.545% | 3.836%
HENRTA_6_ELCTG1 | Peaker | 2023 | nonsummer | 45660 | 0 | 0 | 0 | 50 | 0 | 1060 | Group |  |  | 8.176% | 1.093% | 8.176% | 1.093% | TRUE | 8.176% | 1.093% | 8.176% | 1.093%
HENRTA_6_ELCTG1 | Peaker | 2023 | summer | 45660 | 0 | 0 | 0 | 50 | 0 | 765 | Group |  |  | 4.935% | 3.264% | 4.935% | 3.264% | TRUE | 4.935% | 3.264% | 4.935% | 3.264%
HENRTA_6_ELCTG1 | Peaker | 2024 | nonsummer | 45660 | 2325 | 0 | 0 | 50 | 0 | 1065 | Group |  |  | 6.289% | 1.398% | 6.289% | 1.398% | TRUE | 6.289% | 1.398% | 6.289% | 1.398%
HENRTA_6_ELCTG1 | Peaker | 2024 | summer | 45660 | 0 | 0 | 0 | 50 | 0 | 765 | Group |  |  | 5.607% | 3.804% | 5.607% | 3.804% | TRUE | 5.607% | 3.804% | 5.607% | 3.804%
HENRTA_6_ELCTG2 | Peaker | 2022 | nonsummer | 45660 | 0 | 0 | 0 | 50 | 0 | 1060 | Group |  |  | 6.683% | 1.141% | 6.683% | 1.141% | TRUE | 6.683% | 1.141% | 6.683% | 1.141%
HENRTA_6_ELCTG2 | Peaker | 2022 | summer | 45660 | 0 | 0 | 0 | 50 | 0 | 765 | Group |  |  | 3.545% | 3.836% | 3.545% | 3.836% | TRUE | 3.545% | 3.836% | 3.545% | 3.836%
HENRTA_6_ELCTG2 | Peaker | 2023 | nonsummer | 45660 | 0 | 0 | 0 | 50 | 0 | 1060 | Group |  |  | 8.176% | 1.093% | 8.176% | 1.093% | TRUE | 8.176% | 1.093% | 8.176% | 1.093%
HENRTA_6_ELCTG2 | Peaker | 2023 | summer | 45660 | 0 | 0 | 0 | 50 | 0 | 765 | Group |  |  | 4.935% | 3.264% | 4.935% | 3.264% | TRUE | 4.935% | 3.264% | 4.935% | 3.264%
HENRTA_6_ELCTG2 | Peaker | 2024 | nonsummer | 45660 | 2325 | 0 | 0 | 50 | 0 | 1065 | Group |  |  | 6.289% | 1.398% | 6.289% | 1.398% | TRUE | 6.289% | 1.398% | 6.289% | 1.398%
HENRTA_6_ELCTG2 | Peaker | 2024 | summer | 45660 | 0 | 0 | 0 | 50 | 0 | 765 | Group |  |  | 5.607% | 3.804% | 5.607% | 3.804% | TRUE | 5.607% | 3.804% | 5.607% | 3.804%
HINSON_6_LBECH1 | Peaker | 2022 | nonsummer | 39295 | 315 | 0 | 1060 | 63 | 66780 | 0 | Individual | 0.4717% | 0% |  |  | 0.4717% | 0% | TRUE |  |  | 0.4717% | 0%
HINSON_6_LBECH1 | Peaker | 2022 | summer | 39295 | 63 | 14.5667 | 765 | 63 | 48195 | 0 | Individual | 0.1307% | 0.03022% |  |  | 0.1307% | 0.03022% | TRUE |  |  | 0.1307% | 0.03022%
HINSON_6_LBECH1 | Peaker | 2023 | nonsummer | 39295 | 897.75 | 0 | 1060 | 63 | 66780 | 0 | Individual | 1.344% | 0% |  |  | 1.344% | 0% | TRUE |  |  | 1.344% | 0%
HINSON_6_LBECH1 | Peaker | 2023 | summer | 39295 | 2446.5 | 0 | 765 | 63 | 48195 | 0 | Individual | 5.076% | 0% |  |  | 5.076% | 0% | TRUE |  |  | 5.076% | 0%
HINSON_6_LBECH1 | Peaker | 2024 | nonsummer | 39295 | 0 | 0 | 1065 | 63 | 67095 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
HINSON_6_LBECH1 | Peaker | 2024 | summer | 39295 | 0 | 0 | 765 | 63 | 48195 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
HINSON_6_LBECH2 | Peaker | 2022 | nonsummer | 39295 | 0 | 0 | 1060 | 63 | 66780 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
HINSON_6_LBECH2 | Peaker | 2022 | summer | 39295 | 0 | 9.5 | 765 | 63 | 48195 | 0 | Individual | 0% | 0.01971% |  |  | 0% | 0.01971% | TRUE |  |  | 0% | 0.01971%
HINSON_6_LBECH2 | Peaker | 2023 | nonsummer | 39295 | 267.75 | 0 | 1060 | 63 | 66780 | 0 | Individual | 0.4009% | 0% |  |  | 0.4009% | 0% | TRUE |  |  | 0.4009% | 0%
HINSON_6_LBECH2 | Peaker | 2023 | summer | 39295 | 2457 | 0 | 765 | 63 | 48195 | 0 | Individual | 5.098% | 0% |  |  | 5.098% | 0% | TRUE |  |  | 5.098% | 0%
HINSON_6_LBECH2 | Peaker | 2024 | nonsummer | 39295 | 0 | 0 | 1065 | 63 | 67095 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
HINSON_6_LBECH2 | Peaker | 2024 | summer | 39295 | 0 | 0 | 765 | 63 | 48195 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
HINSON_6_LBECH3 | Peaker | 2022 | nonsummer | 39295 | 0 | 0 | 1060 | 63 | 66780 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
HINSON_6_LBECH3 | Peaker | 2022 | summer | 39295 | 0 | 34.8333 | 765 | 63 | 48195 | 0 | Individual | 0% | 0.07228% |  |  | 0% | 0.07228% | TRUE |  |  | 0% | 0.07228%
HINSON_6_LBECH3 | Peaker | 2023 | nonsummer | 39295 | 157.5 | 0 | 1060 | 63 | 66780 | 0 | Individual | 0.2358% | 0% |  |  | 0.2358% | 0% | TRUE |  |  | 0.2358% | 0%
HINSON_6_LBECH3 | Peaker | 2023 | summer | 39295 | 0 | 0 | 765 | 63 | 48195 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
HINSON_6_LBECH3 | Peaker | 2024 | nonsummer | 39295 | 36235.5 | 0 | 1065 | 63 | 67095 | 0 | Individual | 54.01% | 0% |  |  | 54.01% | 0% | TRUE |  |  | 54.01% | 0%
HINSON_6_LBECH3 | Peaker | 2024 | summer | 39295 | 3883.95 | 0 | 765 | 63 | 48195 | 0 | Individual | 8.059% | 0% |  |  | 8.059% | 0% | TRUE |  |  | 8.059% | 0%
HINSON_6_LBECH4 | Peaker | 2022 | nonsummer | 39295 | 0 | 0 | 1060 | 63 | 66780 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
HINSON_6_LBECH4 | Peaker | 2022 | summer | 39295 | 0 | 4.75 | 765 | 63 | 48195 | 0 | Individual | 0% | 0.009856% |  |  | 0% | 0.009856% | TRUE |  |  | 0% | 0.009856%
HINSON_6_LBECH4 | Peaker | 2023 | nonsummer | 39295 | 488.25 | 0 | 1060 | 63 | 66780 | 0 | Individual | 0.7311% | 0% |  |  | 0.7311% | 0% | TRUE |  |  | 0.7311% | 0%
HINSON_6_LBECH4 | Peaker | 2023 | summer | 39295 | 113.4 | 0 | 765 | 63 | 48195 | 0 | Individual | 0.2353% | 0% |  |  | 0.2353% | 0% | TRUE |  |  | 0.2353% | 0%
HINSON_6_LBECH4 | Peaker | 2024 | nonsummer | 39295 | 0 | 0 | 1065 | 63 | 67095 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
HINSON_6_LBECH4 | Peaker | 2024 | summer | 39295 | 0 | 0 | 765 | 63 | 48195 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
INDIGO_1_UNIT 1 | Peaker | 2022 | nonsummer | 37153 | 608.55 | 224.7 | 1060 | 45.3 | 48018 | 0 | Individual | 1.267% | 0.4679% |  |  | 1.267% | 0.4679% | TRUE |  |  | 1.267% | 0.4679%
INDIGO_1_UNIT 1 | Peaker | 2022 | summer | 37153 | 263.39 | 2593.775 | 765 | 45.3 | 34654.5 | 0 | Individual | 0.76% | 7.485% |  |  | 0.76% | 7.485% | TRUE |  |  | 0.76% | 7.485%
INDIGO_1_UNIT 1 | Peaker | 2023 | nonsummer | 37153 | 6020.395 | 0 | 1060 | 45.3 | 48018 | 0 | Individual | 12.54% | 0% |  |  | 12.54% | 0% | TRUE |  |  | 12.54% | 0%
INDIGO_1_UNIT 1 | Peaker | 2023 | summer | 37153 | 672.8 | 1751.7317 | 765 | 45.3 | 34654.5 | 0 | Individual | 1.941% | 5.055% |  |  | 1.941% | 5.055% | TRUE |  |  | 1.941% | 5.055%
INDIGO_1_UNIT 1 | Peaker | 2024 | nonsummer | 37153 | 226.5 | 128.5 | 1065 | 45.3 | 48244.5 | 0 | Individual | 0.4695% | 0.2664% |  |  | 0.4695% | 0.2664% | TRUE |  |  | 0.4695% | 0.2664%
INDIGO_1_UNIT 1 | Peaker | 2024 | summer | 37153 | 629.7767 | 2401.5 | 765 | 45.3 | 34654.5 | 0 | Individual | 1.817% | 6.93% |  |  | 1.817% | 6.93% | TRUE |  |  | 1.817% | 6.93%
INDIGO_1_UNIT 2 | Peaker | 2022 | nonsummer | 37153 | 501.32 | 544.5 | 1060 | 45.3 | 48018 | 0 | Individual | 1.044% | 1.134% |  |  | 1.044% | 1.134% | TRUE |  |  | 1.044% | 1.134%
INDIGO_1_UNIT 2 | Peaker | 2022 | summer | 37153 | 40.1 | 3454 | 765 | 45.3 | 34654.5 | 0 | Individual | 0.1157% | 9.967% |  |  | 0.1157% | 9.967% | TRUE |  |  | 0.1157% | 9.967%
INDIGO_1_UNIT 2 | Peaker | 2023 | nonsummer | 37153 | 10687.805 | 0 | 1060 | 45.3 | 48018 | 0 | Individual | 22.26% | 0% |  |  | 22.26% | 0% | TRUE |  |  | 22.26% | 0%
INDIGO_1_UNIT 2 | Peaker | 2023 | summer | 37153 | 601.8933 | 2355.955 | 765 | 45.3 | 34654.5 | 0 | Individual | 1.737% | 6.798% |  |  | 1.737% | 6.798% | TRUE |  |  | 1.737% | 6.798%
INDIGO_1_UNIT 2 | Peaker | 2024 | nonsummer | 37153 | 0 | 249.6 | 1065 | 45.3 | 48244.5 | 0 | Individual | 0% | 0.5174% |  |  | 0% | 0.5174% | TRUE |  |  | 0% | 0.5174%
INDIGO_1_UNIT 2 | Peaker | 2024 | summer | 37153 | 45.3 | 3154.4 | 765 | 45.3 | 34654.5 | 0 | Individual | 0.1307% | 9.102% |  |  | 0.1307% | 9.102% | TRUE |  |  | 0.1307% | 9.102%
INDIGO_1_UNIT 3 | Peaker | 2022 | nonsummer | 37153 | 3624 | 622.5 | 1060 | 45.3 | 48018 | 0 | Individual | 7.547% | 1.296% |  |  | 7.547% | 1.296% | TRUE |  |  | 7.547% | 1.296%
INDIGO_1_UNIT 3 | Peaker | 2022 | summer | 37153 | 112.6833 | 3108 | 765 | 45.3 | 34654.5 | 0 | Individual | 0.3252% | 8.969% |  |  | 0.3252% | 8.969% | TRUE |  |  | 0.3252% | 8.969%
INDIGO_1_UNIT 3 | Peaker | 2023 | nonsummer | 37153 | 9432.9733 | 0 | 1060 | 45.3 | 48018 | 0 | Individual | 19.64% | 0% |  |  | 19.64% | 0% | TRUE |  |  | 19.64% | 0%
INDIGO_1_UNIT 3 | Peaker | 2023 | summer | 37153 | 399 | 2684.0583 | 765 | 45.3 | 34654.5 | 0 | Individual | 1.151% | 7.745% |  |  | 1.151% | 7.745% | TRUE |  |  | 1.151% | 7.745%
INDIGO_1_UNIT 3 | Peaker | 2024 | nonsummer | 37153 | 0 | 268.9 | 1065 | 45.3 | 48244.5 | 0 | Individual | 0% | 0.5574% |  |  | 0% | 0.5574% | TRUE |  |  | 0% | 0.5574%
INDIGO_1_UNIT 3 | Peaker | 2024 | summer | 37153 | 304.3583 | 3399.9 | 765 | 45.3 | 34654.5 | 0 | Individual | 0.8783% | 9.811% |  |  | 0.8783% | 9.811% | TRUE |  |  | 0.8783% | 9.811%
KELSO_2_UNITS | Peaker | 2022 | nonsummer | 41183 | 195.3797 | 1317.71 | 1060 | 198.03 | 209911.8 | 0 | Individual | 0.09308% | 0.6277% |  |  | 0.09308% | 0.6277% | TRUE |  |  | 0.09308% | 0.6277%
KELSO_2_UNITS | Peaker | 2022 | summer | 41183 | 192.6483 | 6535.11 | 765 | 198.03 | 151492.95 | 0 | Individual | 0.1272% | 4.314% |  |  | 0.1272% | 4.314% | TRUE |  |  | 0.1272% | 4.314%
KELSO_2_UNITS | Peaker | 2023 | nonsummer | 41183 | 9326.8677 | 3525.2768 | 1060 | 198.03 | 209911.8 | 0 | Individual | 4.443% | 1.679% |  |  | 4.443% | 1.679% | TRUE |  |  | 4.443% | 1.679%
KELSO_2_UNITS | Peaker | 2023 | summer | 41183 | 5369.8422 | 6903.8498 | 765 | 198.03 | 151492.95 | 0 | Individual | 3.545% | 4.557% |  |  | 3.545% | 4.557% | TRUE |  |  | 3.545% | 4.557%
KELSO_2_UNITS | Peaker | 2024 | nonsummer | 41183 | 26286.5558 | 1935.76 | 1065 | 198.03 | 210901.95 | 0 | Individual | 12.46% | 0.9178% |  |  | 12.46% | 0.9178% | TRUE |  |  | 12.46% | 0.9178%
KELSO_2_UNITS | Peaker | 2024 | summer | 41183 | 315.9033 | 7254.81 | 765 | 198.03 | 151492.95 | 0 | Individual | 0.2085% | 4.789% |  |  | 0.2085% | 4.789% | TRUE |  |  | 0.2085% | 4.789%
KERNFT_1_UNITS | Peaker | 2022 | nonsummer | 32515 | 1300.12 | 3134.28 | 1060 | 52.4 | 55544 | 0 | Individual | 2.341% | 5.643% |  |  | 2.341% | 5.643% | TRUE |  |  | 2.341% | 5.643%
KERNFT_1_UNITS | Peaker | 2022 | summer | 32515 | 16555.5233 | 2955.98 | 765 | 52.4 | 40086 | 0 | Individual | 41.3% | 7.374% |  |  | 41.3% | 7.374% | TRUE |  |  | 41.3% | 7.374%
KERNFT_1_UNITS | Peaker | 2023 | nonsummer | 32515 | 1551.2 | 3078.7 | 1060 | 52.4 | 55544 | 0 | Individual | 2.793% | 5.543% |  |  | 2.793% | 5.543% | TRUE |  |  | 2.793% | 5.543%
KERNFT_1_UNITS | Peaker | 2023 | summer | 32515 | 696.16 | 2257.8 | 765 | 52.4 | 40086 | 0 | Individual | 1.737% | 5.632% |  |  | 1.737% | 5.632% | TRUE |  |  | 1.737% | 5.632%
KERNFT_1_UNITS | Peaker | 2024 | nonsummer | 32515 | 1186.3533 | 1905.2367 | 1065 | 52.4 | 55806 | 0 | Individual | 2.126% | 3.414% |  |  | 2.126% | 3.414% | TRUE |  |  | 2.126% | 3.414%
KERNFT_1_UNITS | Peaker | 2024 | summer | 32515 | 1318.6967 | 2931.5 | 765 | 52.4 | 40086 | 0 | Individual | 3.29% | 7.313% |  |  | 3.29% | 7.313% | TRUE |  |  | 3.29% | 7.313%
KINGCO_1_KINGBR | Peaker | 2022 | nonsummer | 33212 | 196.65 | 0 | 1060 | 34.5 | 36570 | 0 | Individual | 0.5377% | 0% |  |  | 0.5377% | 0% | TRUE |  |  | 0.5377% | 0%
KINGCO_1_KINGBR | Peaker | 2022 | summer | 33212 | 0 | 0 | 765 | 34.5 | 26392.5 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
KINGCO_1_KINGBR | Peaker | 2023 | nonsummer | 33212 | 0 | 0 | 1060 | 34.5 | 36570 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
KINGCO_1_KINGBR | Peaker | 2023 | summer | 33212 | 150.075 | 0 | 765 | 34.5 | 26392.5 | 0 | Individual | 0.5686% | 0% |  |  | 0.5686% | 0% | TRUE |  |  | 0.5686% | 0%
KINGCO_1_KINGBR | Peaker | 2024 | nonsummer | 33212 | 135.875 | 0 | 1065 | 34.5 | 36742.5 | 0 | Individual | 0.3698% | 0% |  |  | 0.3698% | 0% | TRUE |  |  | 0.3698% | 0%
KINGCO_1_KINGBR | Peaker | 2024 | summer | 33212 | 1641.385 | 0 | 765 | 34.5 | 26392.5 | 0 | Individual | 6.219% | 0% |  |  | 6.219% | 0% | TRUE |  |  | 6.219% | 0%
KNGCTY_6_UNITA1 | Peaker | 2022 | nonsummer | 37270 | 1843.8357 | 165.1 | 1060 | 44.6 | 47276 | 0 | Individual | 3.9% | 0.3492% |  |  | 3.9% | 0.3492% | TRUE |  |  | 3.9% | 0.3492%
KNGCTY_6_UNITA1 | Peaker | 2022 | summer | 37270 | 0 | 674 | 765 | 44.6 | 34119 | 0 | Individual | 0% | 1.975% |  |  | 0% | 1.975% | TRUE |  |  | 0% | 1.975%
KNGCTY_6_UNITA1 | Peaker | 2023 | nonsummer | 37270 | 1140.81 | 0 | 1060 | 44.6 | 47276 | 0 | Individual | 2.413% | 0% |  |  | 2.413% | 0% | TRUE |  |  | 2.413% | 0%
KNGCTY_6_UNITA1 | Peaker | 2023 | summer | 37270 | 453.21 | 0 | 765 | 44.6 | 34119 | 0 | Individual | 1.328% | 0% |  |  | 1.328% | 0% | TRUE |  |  | 1.328% | 0%
KNGCTY_6_UNITA1 | Peaker | 2024 | nonsummer | 37270 | 237.7033 | 209 | 1065 | 44.6 | 47499 | 0 | Individual | 0.5004% | 0.44% |  |  | 0.5004% | 0.44% | TRUE |  |  | 0.5004% | 0.44%
KNGCTY_6_UNITA1 | Peaker | 2024 | summer | 37270 | 195.55 | 2075 | 765 | 44.6 | 34119 | 0 | Individual | 0.5731% | 6.082% |  |  | 0.5731% | 6.082% | TRUE |  |  | 0.5731% | 6.082%
LARKSP_6_UNIT 1 | Peaker | 2022 | nonsummer | 37147 | 3090.765 | 636 | 1060 | 49 | 51940 | 0 | Individual | 5.951% | 1.224% |  |  | 5.951% | 1.224% | TRUE |  |  | 5.951% | 1.224%
LARKSP_6_UNIT 1 | Peaker | 2022 | summer | 37147 | 134.1667 | 1972.5 | 765 | 49 | 37485 | 0 | Individual | 0.3579% | 5.262% |  |  | 0.3579% | 5.262% | TRUE |  |  | 0.3579% | 5.262%
LARKSP_6_UNIT 1 | Peaker | 2023 | nonsummer | 37147 | 5530.4333 | 210 | 1060 | 49 | 51940 | 0 | Individual | 10.65% | 0.4043% |  |  | 10.65% | 0.4043% | TRUE |  |  | 10.65% | 0.4043%
LARKSP_6_UNIT 1 | Peaker | 2023 | summer | 37147 | 908.5 | 2451.51 | 765 | 49 | 37485 | 0 | Individual | 2.424% | 6.54% |  |  | 2.424% | 6.54% | TRUE |  |  | 2.424% | 6.54%
LARKSP_6_UNIT 1 | Peaker | 2024 | nonsummer | 37147 | 5178.175 | 326 | 1065 | 49 | 52185 | 0 | Individual | 9.923% | 0.6247% |  |  | 9.923% | 0.6247% | TRUE |  |  | 9.923% | 0.6247%
LARKSP_6_UNIT 1 | Peaker | 2024 | summer | 37147 | 106.925 | 2227.5 | 765 | 49 | 37485 | 0 | Individual | 0.2852% | 5.942% |  |  | 0.2852% | 5.942% | TRUE |  |  | 0.2852% | 5.942%
LARKSP_6_UNIT 2 | Peaker | 2022 | nonsummer | 37147 | 3159.6477 | 743.9 | 1060 | 49 | 51940 | 0 | Individual | 6.083% | 1.432% |  |  | 6.083% | 1.432% | TRUE |  |  | 6.083% | 1.432%
LARKSP_6_UNIT 2 | Peaker | 2022 | summer | 37147 | 93 | 1612.1 | 765 | 49 | 37485 | 0 | Individual | 0.2481% | 4.301% |  |  | 0.2481% | 4.301% | TRUE |  |  | 0.2481% | 4.301%
LARKSP_6_UNIT 2 | Peaker | 2023 | nonsummer | 37147 | 7828.6833 | 210 | 1060 | 49 | 51940 | 0 | Individual | 15.07% | 0.4043% |  |  | 15.07% | 0.4043% | TRUE |  |  | 15.07% | 0.4043%
LARKSP_6_UNIT 2 | Peaker | 2023 | summer | 37147 | 760.94 | 1478.9317 | 765 | 49 | 37485 | 0 | Individual | 2.03% | 3.945% |  |  | 2.03% | 3.945% | TRUE |  |  | 2.03% | 3.945%
LARKSP_6_UNIT 2 | Peaker | 2024 | nonsummer | 37147 | 208.6833 | 326 | 1065 | 49 | 52185 | 0 | Individual | 0.3999% | 0.6247% |  |  | 0.3999% | 0.6247% | TRUE |  |  | 0.3999% | 0.6247%
LARKSP_6_UNIT 2 | Peaker | 2024 | summer | 37147 | 504.2167 | 2227.5 | 765 | 49 | 37485 | 0 | Individual | 1.345% | 5.942% |  |  | 1.345% | 5.942% | TRUE |  |  | 1.345% | 5.942%
LIVOAK_1_UNIT 1 | Peaker | 2022 | nonsummer | 33313 | 389.7233 | 5635.4 | 1060 | 49.7 | 52682 | 0 | Individual | 0.7398% | 10.7% |  |  | 0.7398% | 10.7% | TRUE |  |  | 0.7398% | 10.7%
LIVOAK_1_UNIT 1 | Peaker | 2022 | summer | 33313 | 243.6333 | 6574.5667 | 765 | 49.7 | 38020.5 | 0 | Individual | 0.6408% | 17.29% |  |  | 0.6408% | 17.29% | TRUE |  |  | 0.6408% | 17.29%
LIVOAK_1_UNIT 1 | Peaker | 2023 | nonsummer | 33313 | 6055.705 | 4488.9 | 1060 | 49.7 | 52682 | 0 | Individual | 11.49% | 8.521% |  |  | 11.49% | 8.521% | TRUE |  |  | 11.49% | 8.521%
LIVOAK_1_UNIT 1 | Peaker | 2023 | summer | 33313 | 1262.84 | 5157 | 765 | 49.7 | 38020.5 | 0 | Individual | 3.321% | 13.56% |  |  | 3.321% | 13.56% | TRUE |  |  | 3.321% | 13.56%
LIVOAK_1_UNIT 1 | Peaker | 2024 | nonsummer | 33313 | 732.6 | 4017.1 | 1065 | 49.7 | 52930.5 | 0 | Individual | 1.384% | 7.589% |  |  | 1.384% | 7.589% | TRUE |  |  | 1.384% | 7.589%
LIVOAK_1_UNIT 1 | Peaker | 2024 | summer | 33313 | 928.35 | 4459.36 | 765 | 49.7 | 38020.5 | 0 | Individual | 2.442% | 11.73% |  |  | 2.442% | 11.73% | TRUE |  |  | 2.442% | 11.73%
LMBEPK_2_UNITA1 | Peaker | 2022 | nonsummer | 37627 | 1869.7333 | 0 | 1060 | 47.5 | 50350 | 0 | Individual | 3.713% | 0% |  |  | 3.713% | 0% | TRUE |  |  | 3.713% | 0%
LMBEPK_2_UNITA1 | Peaker | 2022 | summer | 37627 | 1264.665 | 28.5 | 765 | 47.5 | 36337.5 | 0 | Individual | 3.48% | 0.07843% |  |  | 3.48% | 0.07843% | TRUE |  |  | 3.48% | 0.07843%
LMBEPK_2_UNITA1 | Peaker | 2023 | nonsummer | 37627 | 1077 | 0 | 1060 | 47.5 | 50350 | 0 | Individual | 2.139% | 0% |  |  | 2.139% | 0% | TRUE |  |  | 2.139% | 0%
LMBEPK_2_UNITA1 | Peaker | 2023 | summer | 37627 | 482.3592 | 0 | 765 | 47.5 | 36337.5 | 0 | Individual | 1.327% | 0% |  |  | 1.327% | 0% | TRUE |  |  | 1.327% | 0%
LMBEPK_2_UNITA1 | Peaker | 2024 | nonsummer | 37627 | 559.7083 | 213.9417 | 1065 | 47.5 | 50587.5 | 0 | Individual | 1.106% | 0.4229% |  |  | 1.106% | 0.4229% | TRUE |  |  | 1.106% | 0.4229%
LMBEPK_2_UNITA1 | Peaker | 2024 | summer | 37627 | 0 | 925.5417 | 765 | 47.5 | 36337.5 | 0 | Individual | 0% | 2.547% |  |  | 0% | 2.547% | TRUE |  |  | 0% | 2.547%
LMBEPK_2_UNITA2 | Peaker | 2022 | nonsummer | 37627 | 519.6333 | 22.78 | 1060 | 47.6 | 50456 | 0 | Individual | 1.03% | 0.04515% |  |  | 1.03% | 0.04515% | TRUE |  |  | 1.03% | 0.04515%
LMBEPK_2_UNITA2 | Peaker | 2022 | summer | 37627 | 400.3405 | 94.4133 | 765 | 47.6 | 36414 | 0 | Individual | 1.099% | 0.2593% |  |  | 1.099% | 0.2593% | TRUE |  |  | 1.099% | 0.2593%
LMBEPK_2_UNITA2 | Peaker | 2023 | nonsummer | 37627 | 1920.66 | 6.11 | 1060 | 47.6 | 50456 | 0 | Individual | 3.807% | 0.01211% |  |  | 3.807% | 0.01211% | TRUE |  |  | 3.807% | 0.01211%
LMBEPK_2_UNITA2 | Peaker | 2023 | summer | 37627 | 4695.5358 | 0 | 765 | 47.6 | 36414 | 0 | Individual | 12.89% | 0% |  |  | 12.89% | 0% | TRUE |  |  | 12.89% | 0%
LMBEPK_2_UNITA2 | Peaker | 2024 | nonsummer | 37627 | 115.8267 | 739.8 | 1065 | 47.6 | 50694 | 0 | Individual | 0.2285% | 1.459% |  |  | 0.2285% | 1.459% | TRUE |  |  | 0.2285% | 1.459%
LMBEPK_2_UNITA2 | Peaker | 2024 | summer | 37627 | 30.6667 | 452.8933 | 765 | 47.6 | 36414 | 0 | Individual | 0.08422% | 1.244% |  |  | 0.08422% | 1.244% | TRUE |  |  | 0.08422% | 1.244%
LMBEPK_2_UNITA3 | Peaker | 2022 | nonsummer | 37627 | 763.1058 | 18.3125 | 1060 | 47.75 | 50615 | 0 | Individual | 1.508% | 0.03618% |  |  | 1.508% | 0.03618% | TRUE |  |  | 1.508% | 0.03618%
LMBEPK_2_UNITA3 | Peaker | 2022 | summer | 37627 | 107.965 | 51 | 765 | 47.75 | 36528.75 | 0 | Individual | 0.2956% | 0.1396% |  |  | 0.2956% | 0.1396% | TRUE |  |  | 0.2956% | 0.1396%
LMBEPK_2_UNITA3 | Peaker | 2023 | nonsummer | 37627 | 218.0583 | 0 | 1060 | 47.75 | 50615 | 0 | Individual | 0.4308% | 0% |  |  | 0.4308% | 0% | TRUE |  |  | 0.4308% | 0%
LMBEPK_2_UNITA3 | Peaker | 2023 | summer | 37627 | 229.9958 | 89.4417 | 765 | 47.75 | 36528.75 | 0 | Individual | 0.6296% | 0.2449% |  |  | 0.6296% | 0.2449% | TRUE |  |  | 0.6296% | 0.2449%
LMBEPK_2_UNITA3 | Peaker | 2024 | nonsummer | 37627 | 576.9792 | 568.25 | 1065 | 47.75 | 50853.75 | 0 | Individual | 1.135% | 1.117% |  |  | 1.135% | 1.117% | TRUE |  |  | 1.135% | 1.117%
LMBEPK_2_UNITA3 | Peaker | 2024 | summer | 37627 | 177.9833 | 996.3 | 765 | 47.75 | 36528.75 | 0 | Individual | 0.4872% | 2.727% |  |  | 0.4872% | 2.727% | TRUE |  |  | 0.4872% | 2.727%
LODI25_2_UNIT 1 | Peaker | 2022 | nonsummer | 31413 | 162.2167 | 2260 | 1060 | 25 | 26500 | 0 | Individual | 0.6121% | 8.528% |  |  | 0.6121% | 8.528% | TRUE |  |  | 0.6121% | 8.528%
LODI25_2_UNIT 1 | Peaker | 2022 | summer | 31413 | 400.1 | 2334.85 | 765 | 25 | 19125 | 0 | Individual | 2.092% | 12.21% |  |  | 2.092% | 12.21% | TRUE |  |  | 2.092% | 12.21%
LODI25_2_UNIT 1 | Peaker | 2023 | nonsummer | 31413 | 3318 | 1519 | 1060 | 25 | 26500 | 0 | Individual | 12.52% | 5.732% |  |  | 12.52% | 5.732% | TRUE |  |  | 12.52% | 5.732%
LODI25_2_UNIT 1 | Peaker | 2023 | summer | 31413 | 0 | 2217 | 765 | 25 | 19125 | 0 | Individual | 0% | 11.59% |  |  | 0% | 11.59% | TRUE |  |  | 0% | 11.59%
LODI25_2_UNIT 1 | Peaker | 2024 | nonsummer | 31413 | 391.3167 | 1715 | 1065 | 25 | 26625 | 0 | Individual | 1.47% | 6.441% |  |  | 1.47% | 6.441% | TRUE |  |  | 1.47% | 6.441%
LODI25_2_UNIT 1 | Peaker | 2024 | summer | 31413 | 515.4333 | 2218 | 765 | 25 | 19125 | 0 | Individual | 2.695% | 11.6% |  |  | 2.695% | 11.6% | TRUE |  |  | 2.695% | 11.6%
MALAGA_1_AUCTG1 | Peaker | 2022 | nonsummer | 45614 | 0 | 0 | 0 | 55.3 | 0 | 1060 | Group |  |  | 6.683% | 1.141% | 6.683% | 1.141% | TRUE | 6.683% | 1.141% | 6.683% | 1.141%
MALAGA_1_AUCTG1 | Peaker | 2022 | summer | 45614 | 0 | 0 | 0 | 55.3 | 0 | 765 | Group |  |  | 3.545% | 3.836% | 3.545% | 3.836% | TRUE | 3.545% | 3.836% | 3.545% | 3.836%
MALAGA_1_AUCTG1 | Peaker | 2023 | nonsummer | 45614 | 0 | 0 | 0 | 55.3 | 0 | 1060 | Group |  |  | 8.176% | 1.093% | 8.176% | 1.093% | TRUE | 8.176% | 1.093% | 8.176% | 1.093%
MALAGA_1_AUCTG1 | Peaker | 2023 | summer | 45614 | 0 | 0 | 0 | 55.3 | 0 | 765 | Group |  |  | 4.935% | 3.264% | 4.935% | 3.264% | TRUE | 4.935% | 3.264% | 4.935% | 3.264%
MALAGA_1_AUCTG1 | Peaker | 2024 | nonsummer | 45614 | 3594.5 | 0 | 220 | 55.3 | 12166 | 845 | Blended | 29.55% | 0% | 6.289% | 1.398% | 11.09% | 1.109% | TRUE | 6.289% | 1.398% | 11.09% | 1.109%
MALAGA_1_AUCTG1 | Peaker | 2024 | summer | 45614 | 0 | 0 | 0 | 55.3 | 0 | 765 | Group |  |  | 5.607% | 3.804% | 5.607% | 3.804% | TRUE | 5.607% | 3.804% | 5.607% | 3.804%
MALAGA_1_AUCTG2 | Peaker | 2022 | nonsummer | 45614 | 0 | 0 | 0 | 55.3 | 0 | 1060 | Group |  |  | 6.683% | 1.141% | 6.683% | 1.141% | TRUE | 6.683% | 1.141% | 6.683% | 1.141%
MALAGA_1_AUCTG2 | Peaker | 2022 | summer | 45614 | 0 | 0 | 0 | 55.3 | 0 | 765 | Group |  |  | 3.545% | 3.836% | 3.545% | 3.836% | TRUE | 3.545% | 3.836% | 3.545% | 3.836%
MALAGA_1_AUCTG2 | Peaker | 2023 | nonsummer | 45614 | 0 | 0 | 0 | 55.3 | 0 | 1060 | Group |  |  | 8.176% | 1.093% | 8.176% | 1.093% | TRUE | 8.176% | 1.093% | 8.176% | 1.093%
MALAGA_1_AUCTG2 | Peaker | 2023 | summer | 45614 | 0 | 0 | 0 | 55.3 | 0 | 765 | Group |  |  | 4.935% | 3.264% | 4.935% | 3.264% | TRUE | 4.935% | 3.264% | 4.935% | 3.264%
MALAGA_1_AUCTG2 | Peaker | 2024 | nonsummer | 45614 | 3594.5 | 0 | 220 | 55.3 | 12166 | 845 | Blended | 29.55% | 0% | 6.289% | 1.398% | 11.09% | 1.109% | TRUE | 6.289% | 1.398% | 11.09% | 1.109%
MALAGA_1_AUCTG2 | Peaker | 2024 | summer | 45614 | 0 | 0 | 0 | 55.3 | 0 | 765 | Group |  |  | 5.607% | 3.804% | 5.607% | 3.804% | TRUE | 5.607% | 3.804% | 5.607% | 3.804%
MIRLOM_6_PEAKER | Peaker | 2022 | nonsummer | 39345 | 0 | 719.04 | 1060 | 47.18 | 50010.8 | 0 | Individual | 0% | 1.438% |  |  | 0% | 1.438% | TRUE |  |  | 0% | 1.438%
MIRLOM_6_PEAKER | Peaker | 2022 | summer | 39345 | 337.4373 | 2836.0533 | 765 | 47.18 | 36092.7 | 0 | Individual | 0.9349% | 7.858% |  |  | 0.9349% | 7.858% | TRUE |  |  | 0.9349% | 7.858%
MIRLOM_6_PEAKER | Peaker | 2023 | nonsummer | 39345 | 637.2333 | 559.08 | 1060 | 47.18 | 50010.8 | 0 | Individual | 1.274% | 1.118% |  |  | 1.274% | 1.118% | TRUE |  |  | 1.274% | 1.118%
MIRLOM_6_PEAKER | Peaker | 2023 | summer | 39345 | 222.585 | 2337.9 | 765 | 47.18 | 36092.7 | 0 | Individual | 0.6167% | 6.477% |  |  | 0.6167% | 6.477% | TRUE |  |  | 0.6167% | 6.477%
MIRLOM_6_PEAKER | Peaker | 2024 | nonsummer | 39345 | 471.8 | 555.22 | 1065 | 47.18 | 50246.7 | 0 | Individual | 0.939% | 1.105% |  |  | 0.939% | 1.105% | TRUE |  |  | 0.939% | 1.105%
MIRLOM_6_PEAKER | Peaker | 2024 | summer | 39345 | 1797.9918 | 2634.69 | 765 | 47.18 | 36092.7 | 0 | Individual | 4.982% | 7.3% |  |  | 4.982% | 7.3% | TRUE |  |  | 4.982% | 7.3%
MKTRCK_1_UNIT 1 | Peaker | 2022 | nonsummer | 33527 | 1053.59 | 2757.59 | 1060 | 47.72 | 50583.2 | 0 | Individual | 2.083% | 5.452% |  |  | 2.083% | 5.452% | TRUE |  |  | 2.083% | 5.452%
MKTRCK_1_UNIT 1 | Peaker | 2022 | summer | 33527 | 7588.565 | 439 | 765 | 47.72 | 36505.8 | 0 | Individual | 20.79% | 1.203% |  |  | 20.79% | 1.203% | TRUE |  |  | 20.79% | 1.203%
MKTRCK_1_UNIT 1 | Peaker | 2023 | nonsummer | 33527 | 2630.55 | 2118.98 | 1060 | 47.72 | 50583.2 | 0 | Individual | 5.2% | 4.189% |  |  | 5.2% | 4.189% | TRUE |  |  | 5.2% | 4.189%
MKTRCK_1_UNIT 1 | Peaker | 2023 | summer | 33527 | 4140.6 | 3294.3 | 765 | 47.72 | 36505.8 | 0 | Individual | 11.34% | 9.024% |  |  | 11.34% | 9.024% | TRUE |  |  | 11.34% | 9.024%
MKTRCK_1_UNIT 1 | Peaker | 2024 | nonsummer | 33527 | 5580.2 | 2452.16 | 1065 | 47.72 | 50821.8 | 0 | Individual | 10.98% | 4.825% |  |  | 10.98% | 4.825% | TRUE |  |  | 10.98% | 4.825%
MKTRCK_1_UNIT 1 | Peaker | 2024 | summer | 33527 | 1888.7033 | 3436.7 | 765 | 47.72 | 36505.8 | 0 | Individual | 5.174% | 9.414% |  |  | 5.174% | 9.414% | TRUE |  |  | 5.174% | 9.414%
MNDALY_6_MCGRTH | Peaker | 2022 | nonsummer | 41214 | 271.026 | 1534.18 | 1060 | 48.56 | 51473.6 | 0 | Individual | 0.5265% | 2.981% |  |  | 0.5265% | 2.981% | TRUE |  |  | 0.5265% | 2.981%
MNDALY_6_MCGRTH | Peaker | 2022 | summer | 41214 | 414.1847 | 5214.4157 | 765 | 48.56 | 37148.4 | 0 | Individual | 1.115% | 14.04% |  |  | 1.115% | 14.04% | TRUE |  |  | 1.115% | 14.04%
MNDALY_6_MCGRTH | Peaker | 2023 | nonsummer | 41214 | 104.0377 | 2402.91 | 1060 | 48.56 | 51473.6 | 0 | Individual | 0.2021% | 4.668% |  |  | 0.2021% | 4.668% | TRUE |  |  | 0.2021% | 4.668%
MNDALY_6_MCGRTH | Peaker | 2023 | summer | 41214 | 418.968 | 4810.92 | 765 | 48.56 | 37148.4 | 0 | Individual | 1.128% | 12.95% |  |  | 1.128% | 12.95% | TRUE |  |  | 1.128% | 12.95%
MNDALY_6_MCGRTH | Peaker | 2024 | nonsummer | 41214 | 199.515 | 3019.44 | 1065 | 48.56 | 51716.4 | 0 | Individual | 0.3858% | 5.838% |  |  | 0.3858% | 5.838% | TRUE |  |  | 0.3858% | 5.838%
MNDALY_6_MCGRTH | Peaker | 2024 | summer | 41214 | 0 | 5232.64 | 765 | 48.56 | 37148.4 | 0 | Individual | 0% | 14.09% |  |  | 0% | 14.09% | TRUE |  |  | 0% | 14.09%
MRGT_6_MEF2 | Peaker | 2022 | nonsummer | 40032 | 387.9333 | 0 | 1060 | 44 | 46640 | 0 | Individual | 0.8318% | 0% |  |  | 0.8318% | 0% | TRUE |  |  | 0.8318% | 0%
MRGT_6_MEF2 | Peaker | 2022 | summer | 40032 | 4.4 | 0 | 765 | 44 | 33660 | 0 | Individual | 0.01307% | 0% |  |  | 0.01307% | 0% | TRUE |  |  | 0.01307% | 0%
MRGT_6_MEF2 | Peaker | 2023 | nonsummer | 40032 | 619.6667 | 0 | 1060 | 44 | 46640 | 0 | Individual | 1.329% | 0% |  |  | 1.329% | 0% | TRUE |  |  | 1.329% | 0%
MRGT_6_MEF2 | Peaker | 2023 | summer | 40032 | 779.5333 | 0 | 765 | 44 | 33660 | 0 | Individual | 2.316% | 0% |  |  | 2.316% | 0% | TRUE |  |  | 2.316% | 0%
MRGT_6_MEF2 | Peaker | 2024 | nonsummer | 40032 | 0 | 0 | 1065 | 44 | 46860 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
MRGT_6_MEF2 | Peaker | 2024 | summer | 40032 | 220 | 0 | 765 | 44 | 33660 | 0 | Individual | 0.6536% | 0% |  |  | 0.6536% | 0% | TRUE |  |  | 0.6536% | 0%
MRGT_6_MMAREF | Peaker | 2022 | nonsummer | 38560 | 408.75 | 0 | 1060 | 45 | 47700 | 0 | Individual | 0.8569% | 0% |  |  | 0.8569% | 0% | TRUE |  |  | 0.8569% | 0%
MRGT_6_MMAREF | Peaker | 2022 | summer | 38560 | 63 | 0 | 765 | 45 | 34425 | 0 | Individual | 0.183% | 0% |  |  | 0.183% | 0% | TRUE |  |  | 0.183% | 0%
MRGT_6_MMAREF | Peaker | 2023 | nonsummer | 38560 | 932.25 | 0 | 1060 | 45 | 47700 | 0 | Individual | 1.954% | 0% |  |  | 1.954% | 0% | TRUE |  |  | 1.954% | 0%
MRGT_6_MMAREF | Peaker | 2023 | summer | 38560 | 0 | 0 | 765 | 45 | 34425 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
MRGT_6_MMAREF | Peaker | 2024 | nonsummer | 38560 | 0 | 0 | 1065 | 45 | 47925 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
MRGT_6_MMAREF | Peaker | 2024 | summer | 38560 | 0 | 0 | 765 | 45 | 34425 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
OAK C_7_UNIT 1 | Peaker | 2022 | nonsummer | 28491 | 27419.6233 | 0 | 1060 | 55 | 58300 | 0 | Individual | 47.03% | 0% |  |  | 47.03% | 0% | TRUE |  |  | 47.03% | 0%
OAK C_7_UNIT 1 | Peaker | 2022 | summer | 28491 | 23871.5083 | 25.2917 | 765 | 55 | 42075 | 0 | Individual | 56.74% | 0.06011% |  |  | 56.74% | 0.06011% | TRUE |  |  | 56.74% | 0.06011%
OAK C_7_UNIT 1 | Peaker | 2023 | nonsummer | 28491 | 31293.65 | 0 | 1060 | 55 | 58300 | 0 | Individual | 53.68% | 0% |  |  | 53.68% | 0% | TRUE |  |  | 53.68% | 0%
OAK C_7_UNIT 1 | Peaker | 2023 | summer | 28491 | 22959.0667 | 0 | 765 | 55 | 42075 | 0 | Individual | 54.57% | 0% |  |  | 54.57% | 0% | TRUE |  |  | 54.57% | 0%
OAK C_7_UNIT 1 | Peaker | 2024 | nonsummer | 28491 | 2843.5583 | 0 | 1065 | 55 | 58575 | 0 | Individual | 4.855% | 0% |  |  | 4.855% | 0% | TRUE |  |  | 4.855% | 0%
OAK C_7_UNIT 1 | Peaker | 2024 | summer | 28491 | 5409.95 | 0 | 765 | 55 | 42075 | 0 | Individual | 12.86% | 0% |  |  | 12.86% | 0% | TRUE |  |  | 12.86% | 0%
OAK C_7_UNIT 3 | Peaker | 2022 | nonsummer | 28491 | 3674.0983 | 0 | 1060 | 55 | 58300 | 0 | Individual | 6.302% | 0% |  |  | 6.302% | 0% | TRUE |  |  | 6.302% | 0%
OAK C_7_UNIT 3 | Peaker | 2022 | summer | 28491 | 3769.7333 | 294.4 | 765 | 55 | 42075 | 0 | Individual | 8.96% | 0.6997% |  |  | 8.96% | 0.6997% | TRUE |  |  | 8.96% | 0.6997%
OAK C_7_UNIT 3 | Peaker | 2023 | nonsummer | 28491 | 7755.15 | 0 | 1060 | 55 | 58300 | 0 | Individual | 13.3% | 0% |  |  | 13.3% | 0% | TRUE |  |  | 13.3% | 0%
OAK C_7_UNIT 3 | Peaker | 2023 | summer | 28491 | 1875 | 0 | 765 | 55 | 42075 | 0 | Individual | 4.456% | 0% |  |  | 4.456% | 0% | TRUE |  |  | 4.456% | 0%
OAK C_7_UNIT 3 | Peaker | 2024 | nonsummer | 28491 | 2327.95 | 0 | 1065 | 55 | 58575 | 0 | Individual | 3.974% | 0% |  |  | 3.974% | 0% | TRUE |  |  | 3.974% | 0%
OAK C_7_UNIT 3 | Peaker | 2024 | summer | 28491 | 2926.7333 | 0 | 765 | 55 | 42075 | 0 | Individual | 6.956% | 0% |  |  | 6.956% | 0% | TRUE |  |  | 6.956% | 0%
OGROVE_6_PL1X2 | Peaker | 2022 | nonsummer | 40345 | 8660 | 0 | 1060 | 96 | 101760 | 0 | Individual | 8.51% | 0% |  |  | 8.51% | 0% | TRUE |  |  | 8.51% | 0%
OGROVE_6_PL1X2 | Peaker | 2022 | summer | 40345 | 0 | 0 | 765 | 96 | 73440 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
OGROVE_6_PL1X2 | Peaker | 2023 | nonsummer | 40345 | 1513.2833 | 0 | 1060 | 96 | 101760 | 0 | Individual | 1.487% | 0% |  |  | 1.487% | 0% | TRUE |  |  | 1.487% | 0%
OGROVE_6_PL1X2 | Peaker | 2023 | summer | 40345 | 572.4833 | 0 | 765 | 96 | 73440 | 0 | Individual | 0.7795% | 0% |  |  | 0.7795% | 0% | TRUE |  |  | 0.7795% | 0%
OGROVE_6_PL1X2 | Peaker | 2024 | nonsummer | 40345 | 331.0733 | 0 | 1065 | 96 | 102240 | 0 | Individual | 0.3238% | 0% |  |  | 0.3238% | 0% | TRUE |  |  | 0.3238% | 0%
OGROVE_6_PL1X2 | Peaker | 2024 | summer | 40345 | 228.15 | 0 | 765 | 96 | 73440 | 0 | Individual | 0.3107% | 0% |  |  | 0.3107% | 0% | TRUE |  |  | 0.3107% | 0%
OMAR_2_UNIT 1 | Peaker | 2022 | nonsummer | 31168 | 6423.75 | 0 | 1060 | 75 | 79500 | 0 | Individual | 8.08% | 0% |  |  | 8.08% | 0% | TRUE |  |  | 8.08% | 0%
OMAR_2_UNIT 1 | Peaker | 2022 | summer | 31168 | 2250 | 0 | 765 | 75 | 57375 | 0 | Individual | 3.922% | 0% |  |  | 3.922% | 0% | TRUE |  |  | 3.922% | 0%
OMAR_2_UNIT 1 | Peaker | 2023 | nonsummer | 31168 | 581.25 | 0 | 1060 | 75 | 79500 | 0 | Individual | 0.7311% | 0% |  |  | 0.7311% | 0% | TRUE |  |  | 0.7311% | 0%
OMAR_2_UNIT 1 | Peaker | 2023 | summer | 31168 | 628.75 | 0 | 765 | 75 | 57375 | 0 | Individual | 1.096% | 0% |  |  | 1.096% | 0% | TRUE |  |  | 1.096% | 0%
OMAR_2_UNIT 1 | Peaker | 2024 | nonsummer | 31168 | 95 | 0 | 1065 | 75 | 79875 | 0 | Individual | 0.1189% | 0% |  |  | 0.1189% | 0% | TRUE |  |  | 0.1189% | 0%
OMAR_2_UNIT 1 | Peaker | 2024 | summer | 31168 | 749 | 0 | 765 | 75 | 57375 | 0 | Individual | 1.305% | 0% |  |  | 1.305% | 0% | TRUE |  |  | 1.305% | 0%
OMAR_2_UNIT 2 | Peaker | 2022 | nonsummer | 31168 | 3137.5 | 0 | 1060 | 75 | 79500 | 0 | Individual | 3.947% | 0% |  |  | 3.947% | 0% | TRUE |  |  | 3.947% | 0%
OMAR_2_UNIT 2 | Peaker | 2022 | summer | 31168 | 185 | 0 | 765 | 75 | 57375 | 0 | Individual | 0.3224% | 0% |  |  | 0.3224% | 0% | TRUE |  |  | 0.3224% | 0%
OMAR_2_UNIT 2 | Peaker | 2023 | nonsummer | 31168 | 8306.25 | 0 | 1060 | 75 | 79500 | 0 | Individual | 10.45% | 0% |  |  | 10.45% | 0% | TRUE |  |  | 10.45% | 0%
OMAR_2_UNIT 2 | Peaker | 2023 | summer | 31168 | 10537.5 | 0 | 765 | 75 | 57375 | 0 | Individual | 18.37% | 0% |  |  | 18.37% | 0% | TRUE |  |  | 18.37% | 0%
OMAR_2_UNIT 2 | Peaker | 2024 | nonsummer | 31168 | 922.5 | 0 | 1065 | 75 | 79875 | 0 | Individual | 1.155% | 0% |  |  | 1.155% | 0% | TRUE |  |  | 1.155% | 0%
OMAR_2_UNIT 2 | Peaker | 2024 | summer | 31168 | 986.25 | 0 | 765 | 75 | 57375 | 0 | Individual | 1.719% | 0% |  |  | 1.719% | 0% | TRUE |  |  | 1.719% | 0%
OMAR_2_UNIT 3 | Peaker | 2022 | nonsummer | 31168 | 6257.5 | 0 | 1060 | 75 | 79500 | 0 | Individual | 7.871% | 0% |  |  | 7.871% | 0% | TRUE |  |  | 7.871% | 0%
OMAR_2_UNIT 3 | Peaker | 2022 | summer | 31168 | 3225 | 0 | 765 | 75 | 57375 | 0 | Individual | 5.621% | 0% |  |  | 5.621% | 0% | TRUE |  |  | 5.621% | 0%
OMAR_2_UNIT 3 | Peaker | 2023 | nonsummer | 31168 | 2192.5 | 0 | 1060 | 75 | 79500 | 0 | Individual | 2.758% | 0% |  |  | 2.758% | 0% | TRUE |  |  | 2.758% | 0%
OMAR_2_UNIT 3 | Peaker | 2023 | summer | 31168 | 147.5 | 0 | 765 | 75 | 57375 | 0 | Individual | 0.2571% | 0% |  |  | 0.2571% | 0% | TRUE |  |  | 0.2571% | 0%
OMAR_2_UNIT 3 | Peaker | 2024 | nonsummer | 31168 | 2625 | 0 | 1065 | 75 | 79875 | 0 | Individual | 3.286% | 0% |  |  | 3.286% | 0% | TRUE |  |  | 3.286% | 0%
OMAR_2_UNIT 3 | Peaker | 2024 | summer | 31168 | 1416.25 | 0 | 765 | 75 | 57375 | 0 | Individual | 2.468% | 0% |  |  | 2.468% | 0% | TRUE |  |  | 2.468% | 0%
OTAY_6_PL1X2 | Peaker | 2022 | nonsummer | 38876 | 243.3555 | 0 | 1060 | 39.57 | 41944.2 | 0 | Individual | 0.5802% | 0% |  |  | 0.5802% | 0% | TRUE |  |  | 0.5802% | 0%
OTAY_6_PL1X2 | Peaker | 2022 | summer | 38876 | 563.8725 | 4.78 | 765 | 39.57 | 30271.05 | 0 | Individual | 1.863% | 0.01579% |  |  | 1.863% | 0.01579% | TRUE |  |  | 1.863% | 0.01579%
OTAY_6_PL1X2 | Peaker | 2023 | nonsummer | 38876 | 772.2745 | 0 | 1060 | 39.57 | 41944.2 | 0 | Individual | 1.841% | 0% |  |  | 1.841% | 0% | TRUE |  |  | 1.841% | 0%
OTAY_6_PL1X2 | Peaker | 2023 | summer | 38876 | 745.8945 | 53.55 | 765 | 39.57 | 30271.05 | 0 | Individual | 2.464% | 0.1769% |  |  | 2.464% | 0.1769% | TRUE |  |  | 2.464% | 0.1769%
OTAY_6_PL1X2 | Peaker | 2024 | nonsummer | 38876 | 791.4 | 0 | 1065 | 39.57 | 42142.05 | 0 | Individual | 1.878% | 0% |  |  | 1.878% | 0% | TRUE |  |  | 1.878% | 0%
OTAY_6_PL1X2 | Peaker | 2024 | summer | 38876 | 66.3638 | 47.55 | 765 | 39.57 | 30271.05 | 0 | Individual | 0.2192% | 0.1571% |  |  | 0.2192% | 0.1571% | TRUE |  |  | 0.2192% | 0.1571%
PIOPIC_2_CTG1 | Peaker | 2022 | nonsummer | 42677 | 8943.866 | 2530.08 | 1060 | 111.3 | 117978 | 0 | Individual | 7.581% | 2.145% |  |  | 7.581% | 2.145% | TRUE |  |  | 7.581% | 2.145%
PIOPIC_2_CTG1 | Peaker | 2022 | summer | 42677 | 90.1087 | 5661.36 | 765 | 111.3 | 85144.5 | 0 | Individual | 0.1058% | 6.649% |  |  | 0.1058% | 6.649% | TRUE |  |  | 0.1058% | 6.649%
PIOPIC_2_CTG1 | Peaker | 2023 | nonsummer | 42677 | 7.755 | 2441.38 | 1060 | 111.3 | 117978 | 0 | Individual | 0.006573% | 2.069% |  |  | 0.006573% | 2.069% | TRUE |  |  | 0.006573% | 2.069%
PIOPIC_2_CTG1 | Peaker | 2023 | summer | 42677 | 108.6633 | 5017.89 | 765 | 111.3 | 85144.5 | 0 | Individual | 0.1276% | 5.893% |  |  | 0.1276% | 5.893% | TRUE |  |  | 0.1276% | 5.893%
PIOPIC_2_CTG1 | Peaker | 2024 | nonsummer | 42677 | 0 | 2638.83 | 1065 | 111.3 | 118534.5 | 0 | Individual | 0% | 2.226% |  |  | 0% | 2.226% | TRUE |  |  | 0% | 2.226%
PIOPIC_2_CTG1 | Peaker | 2024 | summer | 42677 | 94.9063 | 4337.15 | 765 | 111.3 | 85144.5 | 0 | Individual | 0.1115% | 5.094% |  |  | 0.1115% | 5.094% | TRUE |  |  | 0.1115% | 5.094%
PIOPIC_2_CTG2 | Peaker | 2022 | nonsummer | 42677 | 20.042 | 1331.24 | 1060 | 112.7 | 119462 | 0 | Individual | 0.01678% | 1.114% |  |  | 0.01678% | 1.114% | TRUE |  |  | 0.01678% | 1.114%
PIOPIC_2_CTG2 | Peaker | 2022 | summer | 42677 | 203.8297 | 4785.74 | 765 | 112.7 | 86215.5 | 0 | Individual | 0.2364% | 5.551% |  |  | 0.2364% | 5.551% | TRUE |  |  | 0.2364% | 5.551%
PIOPIC_2_CTG2 | Peaker | 2023 | nonsummer | 42677 | 455.0008 | 1263.695 | 1060 | 112.7 | 119462 | 0 | Individual | 0.3809% | 1.058% |  |  | 0.3809% | 1.058% | TRUE |  |  | 0.3809% | 1.058%
PIOPIC_2_CTG2 | Peaker | 2023 | summer | 42677 | 84.0308 | 4058.08 | 765 | 112.7 | 86215.5 | 0 | Individual | 0.09747% | 4.707% |  |  | 0.09747% | 4.707% | TRUE |  |  | 0.09747% | 4.707%
PIOPIC_2_CTG2 | Peaker | 2024 | nonsummer | 42677 | 0 | 1289.32 | 1065 | 112.7 | 120025.5 | 0 | Individual | 0% | 1.074% |  |  | 0% | 1.074% | TRUE |  |  | 0% | 1.074%
PIOPIC_2_CTG2 | Peaker | 2024 | summer | 42677 | 642.8192 | 3690.2 | 765 | 112.7 | 86215.5 | 0 | Individual | 0.7456% | 4.28% |  |  | 0.7456% | 4.28% | TRUE |  |  | 0.7456% | 4.28%
PIOPIC_2_CTG3 | Peaker | 2022 | nonsummer | 42677 | 0 | 1205.04 | 1060 | 112 | 118720 | 0 | Individual | 0% | 1.015% |  |  | 0% | 1.015% | TRUE |  |  | 0% | 1.015%
PIOPIC_2_CTG3 | Peaker | 2022 | summer | 42677 | 728.2695 | 5206.92 | 765 | 112 | 85680 | 0 | Individual | 0.85% | 6.077% |  |  | 0.85% | 6.077% | TRUE |  |  | 0.85% | 6.077%
PIOPIC_2_CTG3 | Peaker | 2023 | nonsummer | 42677 | 19.775 | 1245.3867 | 1060 | 112 | 118720 | 0 | Individual | 0.01666% | 1.049% |  |  | 0.01666% | 1.049% | TRUE |  |  | 0.01666% | 1.049%
PIOPIC_2_CTG3 | Peaker | 2023 | summer | 42677 | 506.4458 | 4514.06 | 765 | 112 | 85680 | 0 | Individual | 0.5911% | 5.269% |  |  | 0.5911% | 5.269% | TRUE |  |  | 0.5911% | 5.269%
PIOPIC_2_CTG3 | Peaker | 2024 | nonsummer | 42677 | 433.43 | 2249.02 | 1065 | 112 | 119280 | 0 | Individual | 0.3634% | 1.885% |  |  | 0.3634% | 1.885% | TRUE |  |  | 0.3634% | 1.885%
PIOPIC_2_CTG3 | Peaker | 2024 | summer | 42677 | 751.0615 | 4914.98 | 765 | 112 | 85680 | 0 | Individual | 0.8766% | 5.736% |  |  | 0.8766% | 5.736% | TRUE |  |  | 0.8766% | 5.736%
PNCHEG_2_PL1X4 | Peaker | 2022 | nonsummer | 39960 | 113830.95 | 195.2033 | 1060 | 417 | 442020 | 0 | Individual | 25.75% | 0.04416% |  |  | 25.75% | 0.04416% | TRUE |  |  | 25.75% | 0.04416%
PNCHEG_2_PL1X4 | Peaker | 2022 | summer | 39960 | 13353.97 | 19265.29 | 765 | 417 | 319005 | 0 | Individual | 4.186% | 6.039% |  |  | 4.186% | 6.039% | TRUE |  |  | 4.186% | 6.039%
PNCHEG_2_PL1X4 | Peaker | 2023 | nonsummer | 39960 | 161377.1083 | 1271.0867 | 1060 | 417 | 442020 | 0 | Individual | 36.51% | 0.2876% |  |  | 36.51% | 0.2876% | TRUE |  |  | 36.51% | 0.2876%
PNCHEG_2_PL1X4 | Peaker | 2023 | summer | 39960 | 53978.6667 | 12770.07 | 765 | 417 | 319005 | 0 | Individual | 16.92% | 4.003% |  |  | 16.92% | 4.003% | TRUE |  |  | 16.92% | 4.003%
PNCHEG_2_PL1X4 | Peaker | 2024 | nonsummer | 39960 | 65876.5667 | 3107.8783 | 1065 | 417 | 444105 | 0 | Individual | 14.83% | 0.6998% |  |  | 14.83% | 0.6998% | TRUE |  |  | 14.83% | 0.6998%
PNCHEG_2_PL1X4 | Peaker | 2024 | summer | 39960 | 16505.0783 | 22385.29 | 765 | 417 | 319005 | 0 | Individual | 5.174% | 7.017% |  |  | 5.174% | 7.017% | TRUE |  |  | 5.174% | 7.017%
PNCHPP_1_PL1X2 | Peaker | 2022 | nonsummer | 39936 | 1554.33 | 2644.27 | 1060 | 119.91 | 127104.6 | 0 | Individual | 1.223% | 2.08% |  |  | 1.223% | 2.08% | TRUE |  |  | 1.223% | 2.08%
PNCHPP_1_PL1X2 | Peaker | 2022 | summer | 39936 | 2677.8 | 10282.1 | 765 | 119.91 | 91731.15 | 0 | Individual | 2.919% | 11.21% |  |  | 2.919% | 11.21% | TRUE |  |  | 2.919% | 11.21%
PNCHPP_1_PL1X2 | Peaker | 2023 | nonsummer | 39936 | 8934.853 | 3712.2935 | 1060 | 119.91 | 127104.6 | 0 | Individual | 7.03% | 2.921% |  |  | 7.03% | 2.921% | TRUE |  |  | 7.03% | 2.921%
PNCHPP_1_PL1X2 | Peaker | 2023 | summer | 39936 | 977.85 | 8696.39 | 765 | 119.91 | 91731.15 | 0 | Individual | 1.066% | 9.48% |  |  | 1.066% | 9.48% | TRUE |  |  | 1.066% | 9.48%
PNCHPP_1_PL1X2 | Peaker | 2024 | nonsummer | 39936 | 3221.4835 | 1663.88 | 1065 | 119.91 | 127704.15 | 0 | Individual | 2.523% | 1.303% |  |  | 2.523% | 1.303% | TRUE |  |  | 2.523% | 1.303%
PNCHPP_1_PL1X2 | Peaker | 2024 | summer | 39936 | 1933.2327 | 19.775 | 765 | 119.91 | 91731.15 | 0 | Individual | 2.107% | 0.02156% |  |  | 2.107% | 0.02156% | TRUE |  |  | 2.107% | 0.02156%
PNOCHE_1_PL1X2 | Peaker | 2022 | nonsummer | 38517 | 687.0875 | 47.8252 | 1060 | 49.97 | 52968.2 | 0 | Individual | 1.297% | 0.09029% |  |  | 1.297% | 0.09029% | TRUE |  |  | 1.297% | 0.09029%
PNOCHE_1_PL1X2 | Peaker | 2022 | summer | 38517 | 394.2403 | 1502.5858 | 765 | 49.97 | 38227.05 | 0 | Individual | 1.031% | 3.931% |  |  | 1.031% | 3.931% | TRUE |  |  | 1.031% | 3.931%
PNOCHE_1_PL1X2 | Peaker | 2023 | nonsummer | 38517 | 4589.446 | 87.54 | 1060 | 49.97 | 52968.2 | 0 | Individual | 8.665% | 0.1653% |  |  | 8.665% | 0.1653% | TRUE |  |  | 8.665% | 0.1653%
PNOCHE_1_PL1X2 | Peaker | 2023 | summer | 38517 | 105.98 | 1454.8332 | 765 | 49.97 | 38227.05 | 0 | Individual | 0.2772% | 3.806% |  |  | 0.2772% | 3.806% | TRUE |  |  | 0.2772% | 3.806%
PNOCHE_1_PL1X2 | Peaker | 2024 | nonsummer | 38517 | 1663.1682 | 107.6137 | 1065 | 49.97 | 53218.05 | 0 | Individual | 3.125% | 0.2022% |  |  | 3.125% | 0.2022% | TRUE |  |  | 3.125% | 0.2022%
PNOCHE_1_PL1X2 | Peaker | 2024 | summer | 38517 | 332.811 | 1744.9912 | 765 | 49.97 | 38227.05 | 0 | Individual | 0.8706% | 4.565% |  |  | 0.8706% | 4.565% | TRUE |  |  | 0.8706% | 4.565%
PNOCHE_1_UNITA1 | Peaker | 2022 | nonsummer | 37252 | 1049.4 | 52.01 | 1060 | 52.3 | 55438 | 0 | Individual | 1.893% | 0.09382% |  |  | 1.893% | 0.09382% | TRUE |  |  | 1.893% | 0.09382%
PNOCHE_1_UNITA1 | Peaker | 2022 | summer | 37252 | 354.9933 | 360 | 765 | 52.3 | 40009.5 | 0 | Individual | 0.8873% | 0.8998% |  |  | 0.8873% | 0.8998% | TRUE |  |  | 0.8873% | 0.8998%
PNOCHE_1_UNITA1 | Peaker | 2023 | nonsummer | 37252 | 9813.6317 | 0 | 1060 | 52.3 | 55438 | 0 | Individual | 17.7% | 0% |  |  | 17.7% | 0% | TRUE |  |  | 17.7% | 0%
PNOCHE_1_UNITA1 | Peaker | 2023 | summer | 37252 | 859.2933 | 28.21 | 765 | 52.3 | 40009.5 | 0 | Individual | 2.148% | 0.07051% |  |  | 2.148% | 0.07051% | TRUE |  |  | 2.148% | 0.07051%
PNOCHE_1_UNITA1 | Peaker | 2024 | nonsummer | 37252 | 5090.04 | 0 | 1065 | 52.3 | 55699.5 | 0 | Individual | 9.138% | 0% |  |  | 9.138% | 0% | TRUE |  |  | 9.138% | 0%
PNOCHE_1_UNITA1 | Peaker | 2024 | summer | 37252 | 1046 | 0 | 765 | 52.3 | 40009.5 | 0 | Individual | 2.614% | 0% |  |  | 2.614% | 0% | TRUE |  |  | 2.614% | 0%
RVRVEW_1_UNITA1 | Peaker | 2022 | nonsummer | 37743 | 6477.52 | 8 | 1060 | 48.7 | 51622 | 0 | Individual | 12.55% | 0.0155% |  |  | 12.55% | 0.0155% | TRUE |  |  | 12.55% | 0.0155%
RVRVEW_1_UNITA1 | Peaker | 2022 | summer | 37743 | 837.7467 | 90.45 | 765 | 48.7 | 37255.5 | 0 | Individual | 2.249% | 0.2428% |  |  | 2.249% | 0.2428% | TRUE |  |  | 2.249% | 0.2428%
RVRVEW_1_UNITA1 | Peaker | 2023 | nonsummer | 37743 | 1378.8083 | 7.215 | 1060 | 48.7 | 51622 | 0 | Individual | 2.671% | 0.01398% |  |  | 2.671% | 0.01398% | TRUE |  |  | 2.671% | 0.01398%
RVRVEW_1_UNITA1 | Peaker | 2023 | summer | 37743 | 2184.1367 | 69.4167 | 765 | 48.7 | 37255.5 | 0 | Individual | 5.863% | 0.1863% |  |  | 5.863% | 0.1863% | TRUE |  |  | 5.863% | 0.1863%
RVRVEW_1_UNITA1 | Peaker | 2024 | nonsummer | 37743 | 505.6683 | 241.21 | 1065 | 48.7 | 51865.5 | 0 | Individual | 0.975% | 0.4651% |  |  | 0.975% | 0.4651% | TRUE |  |  | 0.975% | 0.4651%
RVRVEW_1_UNITA1 | Peaker | 2024 | summer | 37743 | 907.08 | 1524.68 | 765 | 48.7 | 37255.5 | 0 | Individual | 2.435% | 4.092% |  |  | 2.435% | 4.092% | TRUE |  |  | 2.435% | 4.092%
RVSIDE_2_RERCU3 | Peaker | 2022 | nonsummer | 40634 | 0 | 0 | 1060 | 49 | 51940 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
RVSIDE_2_RERCU3 | Peaker | 2022 | summer | 40634 | 0 | 0 | 765 | 49 | 37485 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
RVSIDE_2_RERCU3 | Peaker | 2023 | nonsummer | 40634 | 245 | 0 | 1060 | 49 | 51940 | 0 | Individual | 0.4717% | 0% |  |  | 0.4717% | 0% | TRUE |  |  | 0.4717% | 0%
RVSIDE_2_RERCU3 | Peaker | 2023 | summer | 40634 | 0 | 0 | 765 | 49 | 37485 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
RVSIDE_2_RERCU3 | Peaker | 2024 | nonsummer | 40634 | 216.8333 | 0 | 1065 | 49 | 52185 | 0 | Individual | 0.4155% | 0% |  |  | 0.4155% | 0% | TRUE |  |  | 0.4155% | 0%
RVSIDE_2_RERCU3 | Peaker | 2024 | summer | 40634 | 1741.95 | 0 | 765 | 49 | 37485 | 0 | Individual | 4.647% | 0% |  |  | 4.647% | 0% | TRUE |  |  | 4.647% | 0%
RVSIDE_2_RERCU4 | Peaker | 2022 | nonsummer | 40634 | 0 | 0 | 1060 | 49 | 51940 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
RVSIDE_2_RERCU4 | Peaker | 2022 | summer | 40634 | 0 | 0 | 765 | 49 | 37485 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
RVSIDE_2_RERCU4 | Peaker | 2023 | nonsummer | 40634 | 0 | 0 | 1060 | 49 | 51940 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
RVSIDE_2_RERCU4 | Peaker | 2023 | summer | 40634 | 7 | 0 | 765 | 49 | 37485 | 0 | Individual | 0.01867% | 0% |  |  | 0.01867% | 0% | TRUE |  |  | 0.01867% | 0%
RVSIDE_2_RERCU4 | Peaker | 2024 | nonsummer | 40634 | 93.8 | 0 | 1065 | 49 | 52185 | 0 | Individual | 0.1797% | 0% |  |  | 0.1797% | 0% | TRUE |  |  | 0.1797% | 0%
RVSIDE_2_RERCU4 | Peaker | 2024 | summer | 40634 | 1715 | 0 | 765 | 49 | 37485 | 0 | Individual | 4.575% | 0% |  |  | 4.575% | 0% | TRUE |  |  | 4.575% | 0%
RVSIDE_6_RERCU1 | Peaker | 2022 | nonsummer | 38869 | 11604 | 0 | 1060 | 48.35 | 51251 | 0 | Individual | 22.64% | 0% |  |  | 22.64% | 0% | TRUE |  |  | 22.64% | 0%
RVSIDE_6_RERCU1 | Peaker | 2022 | summer | 38869 | 80.43 | 0 | 765 | 48.35 | 36987.75 | 0 | Individual | 0.2175% | 0% |  |  | 0.2175% | 0% | TRUE |  |  | 0.2175% | 0%
RVSIDE_6_RERCU1 | Peaker | 2023 | nonsummer | 38869 | 1450.5 | 0 | 1060 | 48.35 | 51251 | 0 | Individual | 2.83% | 0% |  |  | 2.83% | 0% | TRUE |  |  | 2.83% | 0%
RVSIDE_6_RERCU1 | Peaker | 2023 | summer | 38869 | 0 | 0 | 765 | 48.35 | 36987.75 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
RVSIDE_6_RERCU1 | Peaker | 2024 | nonsummer | 38869 | 0 | 0 | 1065 | 48.35 | 51492.75 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
RVSIDE_6_RERCU1 | Peaker | 2024 | summer | 38869 | 1738.125 | 0 | 765 | 48.35 | 36987.75 | 0 | Individual | 4.699% | 0% |  |  | 4.699% | 0% | TRUE |  |  | 4.699% | 0%
RVSIDE_6_RERCU2 | Peaker | 2022 | nonsummer | 38869 | 101.85 | 0 | 1060 | 48.5 | 51410 | 0 | Individual | 0.1981% | 0% |  |  | 0.1981% | 0% | TRUE |  |  | 0.1981% | 0%
RVSIDE_6_RERCU2 | Peaker | 2022 | summer | 38869 | 129.3333 | 0 | 765 | 48.5 | 37102.5 | 0 | Individual | 0.3486% | 0% |  |  | 0.3486% | 0% | TRUE |  |  | 0.3486% | 0%
RVSIDE_6_RERCU2 | Peaker | 2023 | nonsummer | 38869 | 0 | 0 | 1060 | 48.5 | 51410 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
RVSIDE_6_RERCU2 | Peaker | 2023 | summer | 38869 | 0 | 0 | 765 | 48.5 | 37102.5 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
RVSIDE_6_RERCU2 | Peaker | 2024 | nonsummer | 38869 | 3880 | 0 | 1065 | 48.5 | 51652.5 | 0 | Individual | 7.512% | 0% |  |  | 7.512% | 0% | TRUE |  |  | 7.512% | 0%
RVSIDE_6_RERCU2 | Peaker | 2024 | summer | 38869 | 1745.75 | 0 | 765 | 48.5 | 37102.5 | 0 | Individual | 4.705% | 0% |  |  | 4.705% | 0% | TRUE |  |  | 4.705% | 0%
RVSIDE_6_SPRING | Peaker | 2022 | nonsummer | 37420 | 4.5 | 0 | 1060 | 36 | 38160 | 0 | Individual | 0.01179% | 0% |  |  | 0.01179% | 0% | TRUE |  |  | 0.01179% | 0%
RVSIDE_6_SPRING | Peaker | 2022 | summer | 37420 | 61.6333 | 0 | 765 | 36 | 27540 | 0 | Individual | 0.2238% | 0% |  |  | 0.2238% | 0% | TRUE |  |  | 0.2238% | 0%
RVSIDE_6_SPRING | Peaker | 2023 | nonsummer | 37420 | 411.6667 | 0 | 1060 | 36 | 38160 | 0 | Individual | 1.079% | 0% |  |  | 1.079% | 0% | TRUE |  |  | 1.079% | 0%
RVSIDE_6_SPRING | Peaker | 2023 | summer | 37420 | 75 | 0 | 765 | 36 | 27540 | 0 | Individual | 0.2723% | 0% |  |  | 0.2723% | 0% | TRUE |  |  | 0.2723% | 0%
RVSIDE_6_SPRING | Peaker | 2024 | nonsummer | 37420 | 66 | 0 | 1065 | 36 | 38340 | 0 | Individual | 0.1721% | 0% |  |  | 0.1721% | 0% | TRUE |  |  | 0.1721% | 0%
RVSIDE_6_SPRING | Peaker | 2024 | summer | 37420 | 1278 | 0 | 765 | 36 | 27540 | 0 | Individual | 4.641% | 0% |  |  | 4.641% | 0% | TRUE |  |  | 4.641% | 0%
SENTNL_2_CTG1 | Peaker | 2022 | nonsummer | 41400 | 5835.862 | 2524.2 | 1060 | 107.68 | 114140.8 | 0 | Individual | 5.113% | 2.211% |  |  | 5.113% | 2.211% | TRUE |  |  | 5.113% | 2.211%
SENTNL_2_CTG1 | Peaker | 2022 | summer | 41400 | 125.032 | 3227.72 | 765 | 107.68 | 82375.2 | 0 | Individual | 0.1518% | 3.918% |  |  | 0.1518% | 3.918% | TRUE |  |  | 0.1518% | 3.918%
SENTNL_2_CTG1 | Peaker | 2023 | nonsummer | 41400 | 12268.8873 | 1096.06 | 1060 | 107.68 | 114140.8 | 0 | Individual | 10.75% | 0.9603% |  |  | 10.75% | 0.9603% | TRUE |  |  | 10.75% | 0.9603%
SENTNL_2_CTG1 | Peaker | 2023 | summer | 41400 | 8943.7 | 2483.6 | 765 | 107.68 | 82375.2 | 0 | Individual | 10.86% | 3.015% |  |  | 10.86% | 3.015% | TRUE |  |  | 10.86% | 3.015%
SENTNL_2_CTG1 | Peaker | 2024 | nonsummer | 41400 | 142.5083 | 6748.7032 | 1065 | 107.68 | 114679.2 | 0 | Individual | 0.1243% | 5.885% |  |  | 0.1243% | 5.885% | TRUE |  |  | 0.1243% | 5.885%
SENTNL_2_CTG1 | Peaker | 2024 | summer | 41400 | 487.8 | 8704 | 765 | 107.68 | 82375.2 | 0 | Individual | 0.5922% | 10.57% |  |  | 0.5922% | 10.57% | TRUE |  |  | 0.5922% | 10.57%
SENTNL_2_CTG2 | Peaker | 2022 | nonsummer | 41400 | 7932.8595 | 3027.61 | 1060 | 104.19 | 110441.4 | 0 | Individual | 7.183% | 2.741% |  |  | 7.183% | 2.741% | TRUE |  |  | 7.183% | 2.741%
SENTNL_2_CTG2 | Peaker | 2022 | summer | 41400 | 220.4207 | 4525.946 | 765 | 104.19 | 79705.35 | 0 | Individual | 0.2765% | 5.678% |  |  | 0.2765% | 5.678% | TRUE |  |  | 0.2765% | 5.678%
SENTNL_2_CTG2 | Peaker | 2023 | nonsummer | 41400 | 2815.3203 | 1858.47 | 1060 | 104.19 | 110441.4 | 0 | Individual | 2.549% | 1.683% |  |  | 2.549% | 1.683% | TRUE |  |  | 2.549% | 1.683%
SENTNL_2_CTG2 | Peaker | 2023 | summer | 41400 | 36.795 | 6362.5433 | 765 | 104.19 | 79705.35 | 0 | Individual | 0.04616% | 7.983% |  |  | 0.04616% | 7.983% | TRUE |  |  | 0.04616% | 7.983%
SENTNL_2_CTG2 | Peaker | 2024 | nonsummer | 41400 | 48.625 | 6750.8553 | 1065 | 104.19 | 110962.35 | 0 | Individual | 0.04382% | 6.084% |  |  | 0.04382% | 6.084% | TRUE |  |  | 0.04382% | 6.084%
SENTNL_2_CTG2 | Peaker | 2024 | summer | 41400 | 1041.9 | 8490 | 765 | 104.19 | 79705.35 | 0 | Individual | 1.307% | 10.65% |  |  | 1.307% | 10.65% | TRUE |  |  | 1.307% | 10.65%
SENTNL_2_CTG3 | Peaker | 2022 | nonsummer | 41400 | 7017.938 | 2478.78 | 1060 | 105.69 | 112031.4 | 0 | Individual | 6.264% | 2.213% |  |  | 6.264% | 2.213% | TRUE |  |  | 6.264% | 2.213%
SENTNL_2_CTG3 | Peaker | 2022 | summer | 41400 | 1665.2463 | 3331.1577 | 765 | 105.69 | 80852.85 | 0 | Individual | 2.06% | 4.12% |  |  | 2.06% | 4.12% | TRUE |  |  | 2.06% | 4.12%
SENTNL_2_CTG3 | Peaker | 2023 | nonsummer | 41400 | 38543.0167 | 1607.98 | 1060 | 105.69 | 112031.4 | 0 | Individual | 34.4% | 1.435% |  |  | 34.4% | 1.435% | TRUE |  |  | 34.4% | 1.435%
SENTNL_2_CTG3 | Peaker | 2023 | summer | 41400 | 717.6608 | 6234.7433 | 765 | 105.69 | 80852.85 | 0 | Individual | 0.8876% | 7.711% |  |  | 0.8876% | 7.711% | TRUE |  |  | 0.8876% | 7.711%
SENTNL_2_CTG3 | Peaker | 2024 | nonsummer | 41400 | 105690 | 0 | 1065 | 105.69 | 112559.85 | 0 | Individual | 93.9% | 0% |  |  | 93.9% | 0% | TRUE |  |  | 93.9% | 0%
SENTNL_2_CTG3 | Peaker | 2024 | summer | 41400 | 80852.85 | 0 | 765 | 105.69 | 80852.85 | 0 | Individual | 100% | 0% |  |  | 100% | 0% | TRUE |  |  | 100% | 0%
SENTNL_2_CTG4 | Peaker | 2022 | nonsummer | 41400 | 9235.3215 | 2441.42 | 1060 | 106.55 | 112943 | 0 | Individual | 8.177% | 2.162% |  |  | 8.177% | 2.162% | TRUE |  |  | 8.177% | 2.162%
SENTNL_2_CTG4 | Peaker | 2022 | summer | 41400 | 229.3307 | 3265.626 | 765 | 106.55 | 81510.75 | 0 | Individual | 0.2814% | 4.006% |  |  | 0.2814% | 4.006% | TRUE |  |  | 0.2814% | 4.006%
SENTNL_2_CTG4 | Peaker | 2023 | nonsummer | 41400 | 6976.205 | 2498.23 | 1060 | 106.55 | 112943 | 0 | Individual | 6.177% | 2.212% |  |  | 6.177% | 2.212% | TRUE |  |  | 6.177% | 2.212%
SENTNL_2_CTG4 | Peaker | 2023 | summer | 41400 | 264.31 | 6071.6633 | 765 | 106.55 | 81510.75 | 0 | Individual | 0.3243% | 7.449% |  |  | 0.3243% | 7.449% | TRUE |  |  | 0.3243% | 7.449%
SENTNL_2_CTG4 | Peaker | 2024 | nonsummer | 41400 | 7086.6133 | 7213.55 | 1065 | 106.55 | 113475.75 | 0 | Individual | 6.245% | 6.357% |  |  | 6.245% | 6.357% | TRUE |  |  | 6.245% | 6.357%
SENTNL_2_CTG4 | Peaker | 2024 | summer | 41400 | 1598.25 | 8521.35 | 765 | 106.55 | 81510.75 | 0 | Individual | 1.961% | 10.45% |  |  | 1.961% | 10.45% | TRUE |  |  | 1.961% | 10.45%
SENTNL_2_CTG5 | Peaker | 2022 | nonsummer | 41400 | 5213.338 | 2541.03 | 1060 | 107.52 | 113971.2 | 0 | Individual | 4.574% | 2.23% |  |  | 4.574% | 2.23% | TRUE |  |  | 4.574% | 2.23%
SENTNL_2_CTG5 | Peaker | 2022 | summer | 41400 | 231.4647 | 3237.81 | 765 | 107.52 | 82252.8 | 0 | Individual | 0.2814% | 3.936% |  |  | 0.2814% | 3.936% | TRUE |  |  | 0.2814% | 3.936%
SENTNL_2_CTG5 | Peaker | 2023 | nonsummer | 41400 | 33476.9557 | 1360.99 | 1060 | 107.52 | 113971.2 | 0 | Individual | 29.37% | 1.194% |  |  | 29.37% | 1.194% | TRUE |  |  | 29.37% | 1.194%
SENTNL_2_CTG5 | Peaker | 2023 | summer | 41400 | 291.1733 | 6097.5467 | 765 | 107.52 | 82252.8 | 0 | Individual | 0.354% | 7.413% |  |  | 0.354% | 7.413% | TRUE |  |  | 0.354% | 7.413%
SENTNL_2_CTG5 | Peaker | 2024 | nonsummer | 41400 | 0 | 6752.77 | 1065 | 107.52 | 114508.8 | 0 | Individual | 0% | 5.897% |  |  | 0% | 5.897% | TRUE |  |  | 0% | 5.897%
SENTNL_2_CTG5 | Peaker | 2024 | summer | 41400 | 2320.75 | 8909.8 | 765 | 107.52 | 82252.8 | 0 | Individual | 2.821% | 10.83% |  |  | 2.821% | 10.83% | TRUE |  |  | 2.821% | 10.83%
SENTNL_2_CTG6 | Peaker | 2022 | nonsummer | 41400 | 10336.2377 | 2408.97 | 1060 | 105 | 111300 | 0 | Individual | 9.287% | 2.164% |  |  | 9.287% | 2.164% | TRUE |  |  | 9.287% | 2.164%
SENTNL_2_CTG6 | Peaker | 2022 | summer | 41400 | 3952.7152 | 3393.8437 | 765 | 105 | 80325 | 0 | Individual | 4.921% | 4.225% |  |  | 4.921% | 4.225% | TRUE |  |  | 4.921% | 4.225%
SENTNL_2_CTG6 | Peaker | 2023 | nonsummer | 41400 | 2910.441 | 1949.5433 | 1060 | 105 | 111300 | 0 | Individual | 2.615% | 1.752% |  |  | 2.615% | 1.752% | TRUE |  |  | 2.615% | 1.752%
SENTNL_2_CTG6 | Peaker | 2023 | summer | 41400 | 46.8067 | 5979.5067 | 765 | 105 | 80325 | 0 | Individual | 0.05827% | 7.444% |  |  | 0.05827% | 7.444% | TRUE |  |  | 0.05827% | 7.444%
SENTNL_2_CTG6 | Peaker | 2024 | nonsummer | 41400 | 11.585 | 6501.61 | 1065 | 105 | 111825 | 0 | Individual | 0.01036% | 5.814% |  |  | 0.01036% | 5.814% | TRUE |  |  | 0.01036% | 5.814%
SENTNL_2_CTG6 | Peaker | 2024 | summer | 41400 | 5076.8567 | 9024.1 | 765 | 105 | 80325 | 0 | Individual | 6.32% | 11.23% |  |  | 6.32% | 11.23% | TRUE |  |  | 6.32% | 11.23%
SENTNL_2_CTG7 | Peaker | 2022 | nonsummer | 41400 | 11301.4803 | 2344.36 | 1060 | 106.73 | 113133.8 | 0 | Individual | 9.989% | 2.072% |  |  | 9.989% | 2.072% | TRUE |  |  | 9.989% | 2.072%
SENTNL_2_CTG7 | Peaker | 2022 | summer | 41400 | 229.7267 | 3247.274 | 765 | 106.73 | 81648.45 | 0 | Individual | 0.2814% | 3.977% |  |  | 0.2814% | 3.977% | TRUE |  |  | 0.2814% | 3.977%
SENTNL_2_CTG7 | Peaker | 2023 | nonsummer | 41400 | 10098.2233 | 2048.75 | 1060 | 106.73 | 113133.8 | 0 | Individual | 8.926% | 1.811% |  |  | 8.926% | 1.811% | TRUE |  |  | 8.926% | 1.811%
SENTNL_2_CTG7 | Peaker | 2023 | summer | 41400 | 23817.1938 | 2439.95 | 765 | 106.73 | 81648.45 | 0 | Individual | 29.17% | 2.988% |  |  | 29.17% | 2.988% | TRUE |  |  | 29.17% | 2.988%
SENTNL_2_CTG7 | Peaker | 2024 | nonsummer | 41400 | 0 | 6533.95 | 1065 | 106.73 | 113667.45 | 0 | Individual | 0% | 5.748% |  |  | 0% | 5.748% | TRUE |  |  | 0% | 5.748%
SENTNL_2_CTG7 | Peaker | 2024 | summer | 41400 | 10106.9933 | 8930.8 | 765 | 106.73 | 81648.45 | 0 | Individual | 12.38% | 10.94% |  |  | 12.38% | 10.94% | TRUE |  |  | 12.38% | 10.94%
SENTNL_2_CTG8 | Peaker | 2022 | nonsummer | 41400 | 9253.9715 | 2449.99 | 1060 | 106.85 | 113261 | 0 | Individual | 8.17% | 2.163% |  |  | 8.17% | 2.163% | TRUE |  |  | 8.17% | 2.163%
SENTNL_2_CTG8 | Peaker | 2022 | summer | 41400 | 229.9907 | 3440.216 | 765 | 106.85 | 81740.25 | 0 | Individual | 0.2814% | 4.209% |  |  | 0.2814% | 4.209% | TRUE |  |  | 0.2814% | 4.209%
SENTNL_2_CTG8 | Peaker | 2023 | nonsummer | 41400 | 7866.7008 | 2642.81 | 1060 | 106.85 | 113261 | 0 | Individual | 6.946% | 2.333% |  |  | 6.946% | 2.333% | TRUE |  |  | 6.946% | 2.333%
SENTNL_2_CTG8 | Peaker | 2023 | summer | 41400 | 0 | 6134.9733 | 765 | 106.85 | 81740.25 | 0 | Individual | 0% | 7.505% |  |  | 0% | 7.505% | TRUE |  |  | 0% | 7.505%
SENTNL_2_CTG8 | Peaker | 2024 | nonsummer | 41400 | 0 | 7029.45 | 1065 | 106.85 | 113795.25 | 0 | Individual | 0% | 6.177% |  |  | 0% | 6.177% | TRUE |  |  | 0% | 6.177%
SENTNL_2_CTG8 | Peaker | 2024 | summer | 41400 | 0 | 8932.35 | 765 | 106.85 | 81740.25 | 0 | Individual | 0% | 10.93% |  |  | 0% | 10.93% | TRUE |  |  | 0% | 10.93%
SIERRA_1_UNITS | Peaker | 2022 | nonsummer | 32563 | 1975.6 | 1722.83 | 1060 | 52.43 | 55575.8 | 0 | Individual | 3.555% | 3.1% |  |  | 3.555% | 3.1% | TRUE |  |  | 3.555% | 3.1%
SIERRA_1_UNITS | Peaker | 2022 | summer | 32563 | 734.18 | 2104.15 | 765 | 52.43 | 40108.95 | 0 | Individual | 1.83% | 5.246% |  |  | 1.83% | 5.246% | TRUE |  |  | 1.83% | 5.246%
SIERRA_1_UNITS | Peaker | 2023 | nonsummer | 32563 | 452 | 2499.7827 | 1060 | 52.43 | 55575.8 | 0 | Individual | 0.8133% | 4.498% |  |  | 0.8133% | 4.498% | TRUE |  |  | 0.8133% | 4.498%
SIERRA_1_UNITS | Peaker | 2023 | summer | 32563 | 744 | 2280.15 | 765 | 52.43 | 40108.95 | 0 | Individual | 1.855% | 5.685% |  |  | 1.855% | 5.685% | TRUE |  |  | 1.855% | 5.685%
SIERRA_1_UNITS | Peaker | 2024 | nonsummer | 32563 | 12.5 | 1888.6267 | 1065 | 52.43 | 55837.95 | 0 | Individual | 0.02239% | 3.382% |  |  | 0.02239% | 3.382% | TRUE |  |  | 0.02239% | 3.382%
SIERRA_1_UNITS | Peaker | 2024 | summer | 32563 | 224.6333 | 2686.9 | 765 | 52.43 | 40108.95 | 0 | Individual | 0.5601% | 6.699% |  |  | 0.5601% | 6.699% | TRUE |  |  | 0.5601% | 6.699%
STANTN_2_STAGT1 | Peaker | 2022 | nonsummer | 43971 | 11.25 | 7.8063 | 1060 | 49.65 | 52629 | 0 | Individual | 0.02138% | 0.01483% |  |  | 0.02138% | 0.01483% | TRUE |  |  | 0.02138% | 0.01483%
STANTN_2_STAGT1 | Peaker | 2022 | summer | 43971 | 317.76 | 25.2085 | 765 | 49.65 | 37982.25 | 0 | Individual | 0.8366% | 0.06637% |  |  | 0.8366% | 0.06637% | TRUE |  |  | 0.8366% | 0.06637%
STANTN_2_STAGT1 | Peaker | 2023 | nonsummer | 43971 | 733.9925 | 0 | 1060 | 49.65 | 52629 | 0 | Individual | 1.395% | 0% |  |  | 1.395% | 0% | TRUE |  |  | 1.395% | 0%
STANTN_2_STAGT1 | Peaker | 2023 | summer | 43971 | 7.0092 | 4.2592 | 765 | 49.65 | 37982.25 | 0 | Individual | 0.01845% | 0.01121% |  |  | 0.01845% | 0.01121% | TRUE |  |  | 0.01845% | 0.01121%
STANTN_2_STAGT1 | Peaker | 2024 | nonsummer | 43971 | 1798.1575 | 0.01 | 1065 | 49.65 | 52877.25 | 0 | Individual | 3.401% | 1.891e-05% |  |  | 3.401% | 1.891e-05% | TRUE |  |  | 3.401% | 1.891e-05%
STANTN_2_STAGT1 | Peaker | 2024 | summer | 43971 | 0 | 39.2388 | 765 | 49.65 | 37982.25 | 0 | Individual | 0% | 0.1033% |  |  | 0% | 0.1033% | TRUE |  |  | 0% | 0.1033%
STANTN_2_STAGT2 | Peaker | 2022 | nonsummer | 43971 | 347.55 | 9.6833 | 1060 | 49.65 | 52629 | 0 | Individual | 0.6604% | 0.0184% |  |  | 0.6604% | 0.0184% | TRUE |  |  | 0.6604% | 0.0184%
STANTN_2_STAGT2 | Peaker | 2022 | summer | 43971 | 281.5293 | 676.9898 | 765 | 49.65 | 37982.25 | 0 | Individual | 0.7412% | 1.782% |  |  | 0.7412% | 1.782% | TRUE |  |  | 0.7412% | 1.782%
STANTN_2_STAGT2 | Peaker | 2023 | nonsummer | 43971 | 820.71 | 13.86 | 1060 | 49.65 | 52629 | 0 | Individual | 1.559% | 0.02634% |  |  | 1.559% | 0.02634% | TRUE |  |  | 1.559% | 0.02634%
STANTN_2_STAGT2 | Peaker | 2023 | summer | 43971 | 104.2022 | 758.5675 | 765 | 49.65 | 37982.25 | 0 | Individual | 0.2743% | 1.997% |  |  | 0.2743% | 1.997% | TRUE |  |  | 0.2743% | 1.997%
STANTN_2_STAGT2 | Peaker | 2024 | nonsummer | 43971 | 246.595 | 2.4235 | 1065 | 49.65 | 52877.25 | 0 | Individual | 0.4664% | 0.004583% |  |  | 0.4664% | 0.004583% | TRUE |  |  | 0.4664% | 0.004583%
STANTN_2_STAGT2 | Peaker | 2024 | summer | 43971 | 102.9807 | 585.9492 | 765 | 49.65 | 37982.25 | 0 | Individual | 0.2711% | 1.543% |  |  | 0.2711% | 1.543% | TRUE |  |  | 0.2711% | 1.543%
STIGCT_2_LODI | Peaker | 2022 | nonsummer | 35065 | 685.922 | 3679 | 1060 | 49.9 | 52894 | 0 | Individual | 1.297% | 6.955% |  |  | 1.297% | 6.955% | TRUE |  |  | 1.297% | 6.955%
STIGCT_2_LODI | Peaker | 2022 | summer | 35065 | 3364.6677 | 3964 | 765 | 49.9 | 38173.5 | 0 | Individual | 8.814% | 10.38% |  |  | 8.814% | 10.38% | TRUE |  |  | 8.814% | 10.38%
STIGCT_2_LODI | Peaker | 2023 | nonsummer | 35065 | 230 | 5390.9 | 1060 | 49.9 | 52894 | 0 | Individual | 0.4348% | 10.19% |  |  | 0.4348% | 10.19% | TRUE |  |  | 0.4348% | 10.19%
STIGCT_2_LODI | Peaker | 2023 | summer | 35065 | 119.75 | 3443.5 | 765 | 49.9 | 38173.5 | 0 | Individual | 0.3137% | 9.021% |  |  | 0.3137% | 9.021% | TRUE |  |  | 0.3137% | 9.021%
STIGCT_2_LODI | Peaker | 2024 | nonsummer | 35065 | 15219.5 | 2718 | 1065 | 49.9 | 53143.5 | 0 | Individual | 28.64% | 5.114% |  |  | 28.64% | 5.114% | TRUE |  |  | 28.64% | 5.114%
STIGCT_2_LODI | Peaker | 2024 | summer | 35065 | 6433.8667 | 2324 | 765 | 49.9 | 38173.5 | 0 | Individual | 16.85% | 6.088% |  |  | 16.85% | 6.088% | TRUE |  |  | 16.85% | 6.088%
SYCAMR_2_UNIT 2 | Peaker | 2022 | nonsummer | 31778 | 4338 | 0 | 1060 | 76 | 80560 | 0 | Individual | 5.385% | 0% |  |  | 5.385% | 0% | TRUE |  |  | 5.385% | 0%
SYCAMR_2_UNIT 2 | Peaker | 2022 | summer | 31778 | 154 | 0 | 765 | 76 | 58140 | 0 | Individual | 0.2649% | 0% |  |  | 0.2649% | 0% | TRUE |  |  | 0.2649% | 0%
SYCAMR_2_UNIT 2 | Peaker | 2023 | nonsummer | 31778 | 25229 | 0 | 1060 | 76 | 80560 | 0 | Individual | 31.32% | 0% |  |  | 31.32% | 0% | TRUE |  |  | 31.32% | 0%
SYCAMR_2_UNIT 2 | Peaker | 2023 | summer | 31778 | 2810.7333 | 0 | 765 | 76 | 58140 | 0 | Individual | 4.834% | 0% |  |  | 4.834% | 0% | TRUE |  |  | 4.834% | 0%
SYCAMR_2_UNIT 2 | Peaker | 2024 | nonsummer | 31778 | 23180 | 0 | 1065 | 76 | 80940 | 0 | Individual | 28.64% | 0% |  |  | 28.64% | 0% | TRUE |  |  | 28.64% | 0%
SYCAMR_2_UNIT 2 | Peaker | 2024 | summer | 31778 | 5408.6667 | 0 | 765 | 76 | 58140 | 0 | Individual | 9.303% | 0% |  |  | 9.303% | 0% | TRUE |  |  | 9.303% | 0%
SYCAMR_2_UNIT 4 | Peaker | 2022 | nonsummer | 31778 | 13466.7667 | 0 | 1060 | 76 | 80560 | 0 | Individual | 16.72% | 0% |  |  | 16.72% | 0% | TRUE |  |  | 16.72% | 0%
SYCAMR_2_UNIT 4 | Peaker | 2022 | summer | 31778 | 1697.8 | 0 | 765 | 76 | 58140 | 0 | Individual | 2.92% | 0% |  |  | 2.92% | 0% | TRUE |  |  | 2.92% | 0%
SYCAMR_2_UNIT 4 | Peaker | 2023 | nonsummer | 31778 | 9781.2333 | 0 | 1060 | 76 | 80560 | 0 | Individual | 12.14% | 0% |  |  | 12.14% | 0% | TRUE |  |  | 12.14% | 0%
SYCAMR_2_UNIT 4 | Peaker | 2023 | summer | 31778 | 0 | 0 | 765 | 76 | 58140 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
SYCAMR_2_UNIT 4 | Peaker | 2024 | nonsummer | 31778 | 10455.0667 | 0 | 1065 | 76 | 80940 | 0 | Individual | 12.92% | 0% |  |  | 12.92% | 0% | TRUE |  |  | 12.92% | 0%
SYCAMR_2_UNIT 4 | Peaker | 2024 | summer | 31778 | 760 | 0 | 765 | 76 | 58140 | 0 | Individual | 1.307% | 0% |  |  | 1.307% | 0% | TRUE |  |  | 1.307% | 0%
VACADX_1_UNITA1 | Peaker | 2022 | nonsummer | 37428 | 2453.593 | 0 | 1060 | 51.91 | 55024.6 | 0 | Individual | 4.459% | 0% |  |  | 4.459% | 0% | TRUE |  |  | 4.459% | 0%
VACADX_1_UNITA1 | Peaker | 2022 | summer | 37428 | 1223.7015 | 316.8 | 765 | 51.91 | 39711.15 | 0 | Individual | 3.082% | 0.7978% |  |  | 3.082% | 0.7978% | TRUE |  |  | 3.082% | 0.7978%
VACADX_1_UNITA1 | Peaker | 2023 | nonsummer | 37428 | 2640.9173 | 0 | 1060 | 51.91 | 55024.6 | 0 | Individual | 4.8% | 0% |  |  | 4.8% | 0% | TRUE |  |  | 4.8% | 0%
VACADX_1_UNITA1 | Peaker | 2023 | summer | 37428 | 2543.2383 | 0 | 765 | 51.91 | 39711.15 | 0 | Individual | 6.404% | 0% |  |  | 6.404% | 0% | TRUE |  |  | 6.404% | 0%
VACADX_1_UNITA1 | Peaker | 2024 | nonsummer | 37428 | 0 | 0 | 1065 | 51.91 | 55284.15 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
VACADX_1_UNITA1 | Peaker | 2024 | summer | 37428 | 7704.4327 | 16.8533 | 765 | 51.91 | 39711.15 | 0 | Individual | 19.4% | 0.04244% |  |  | 19.4% | 0.04244% | TRUE |  |  | 19.4% | 0.04244%
VERNON_6_GONZL1 | Peaker | 2022 | nonsummer | 41438 | 6066.25 | 0 | 1060 | 5.75 | 6095 | 0 | Individual | 99.53% | 0% |  |  | 99.53% | 0% | TRUE |  |  | 99.53% | 0%
VERNON_6_GONZL1 | Peaker | 2022 | summer | 41438 | 4398.75 | 0 | 765 | 5.75 | 4398.75 | 0 | Individual | 100% | 0% |  |  | 100% | 0% | TRUE |  |  | 100% | 0%
VERNON_6_GONZL1 | Peaker | 2023 | nonsummer | 41438 | 511.75 | 0 | 1060 | 5.75 | 6095 | 0 | Individual | 8.396% | 0% |  |  | 8.396% | 0% | TRUE |  |  | 8.396% | 0%
VERNON_6_GONZL1 | Peaker | 2023 | summer | 41438 | 57.5 | 0 | 765 | 5.75 | 4398.75 | 0 | Individual | 1.307% | 0% |  |  | 1.307% | 0% | TRUE |  |  | 1.307% | 0%
VERNON_6_GONZL1 | Peaker | 2024 | nonsummer | 41438 | 40.25 | 0 | 1065 | 5.75 | 6123.75 | 0 | Individual | 0.6573% | 0% |  |  | 0.6573% | 0% | TRUE |  |  | 0.6573% | 0%
VERNON_6_GONZL1 | Peaker | 2024 | summer | 41438 | 14.375 | 0 | 765 | 5.75 | 4398.75 | 0 | Individual | 0.3268% | 0% |  |  | 0.3268% | 0% | TRUE |  |  | 0.3268% | 0%
VERNON_6_GONZL2 | Peaker | 2022 | nonsummer | 41438 | 201.4417 | 0 | 1060 | 5.75 | 6095 | 0 | Individual | 3.305% | 0% |  |  | 3.305% | 0% | TRUE |  |  | 3.305% | 0%
VERNON_6_GONZL2 | Peaker | 2022 | summer | 41438 | 29.9 | 0 | 765 | 5.75 | 4398.75 | 0 | Individual | 0.6797% | 0% |  |  | 0.6797% | 0% | TRUE |  |  | 0.6797% | 0%
VERNON_6_GONZL2 | Peaker | 2023 | nonsummer | 41438 | 460 | 0 | 1060 | 5.75 | 6095 | 0 | Individual | 7.547% | 0% |  |  | 7.547% | 0% | TRUE |  |  | 7.547% | 0%
VERNON_6_GONZL2 | Peaker | 2023 | summer | 41438 | 28.75 | 0 | 765 | 5.75 | 4398.75 | 0 | Individual | 0.6536% | 0% |  |  | 0.6536% | 0% | TRUE |  |  | 0.6536% | 0%
VERNON_6_GONZL2 | Peaker | 2024 | nonsummer | 41438 | 758.9042 | 0 | 1065 | 5.75 | 6123.75 | 0 | Individual | 12.39% | 0% |  |  | 12.39% | 0% | TRUE |  |  | 12.39% | 0%
VERNON_6_GONZL2 | Peaker | 2024 | summer | 41438 | 0 | 0 | 765 | 5.75 | 4398.75 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
VESTAL_2_WELLHD | Peaker | 2022 | nonsummer | 41290 | 4137.2333 | 0 | 1060 | 49 | 51940 | 0 | Individual | 7.965% | 0% |  |  | 7.965% | 0% | TRUE |  |  | 7.965% | 0%
VESTAL_2_WELLHD | Peaker | 2022 | summer | 41290 | 430.85 | 32.245 | 765 | 49 | 37485 | 0 | Individual | 1.149% | 0.08602% |  |  | 1.149% | 0.08602% | TRUE |  |  | 1.149% | 0.08602%
VESTAL_2_WELLHD | Peaker | 2023 | nonsummer | 41290 | 2790.5667 | 0 | 1060 | 49 | 51940 | 0 | Individual | 5.373% | 0% |  |  | 5.373% | 0% | TRUE |  |  | 5.373% | 0%
VESTAL_2_WELLHD | Peaker | 2023 | summer | 41290 | 6525.1667 | 0 | 765 | 49 | 37485 | 0 | Individual | 17.41% | 0% |  |  | 17.41% | 0% | TRUE |  |  | 17.41% | 0%
VESTAL_2_WELLHD | Peaker | 2024 | nonsummer | 41290 | 1008.3167 | 204.6933 | 1065 | 49 | 52185 | 0 | Individual | 1.932% | 0.3922% |  |  | 1.932% | 0.3922% | TRUE |  |  | 1.932% | 0.3922%
VESTAL_2_WELLHD | Peaker | 2024 | summer | 41290 | 2909.346 | 601.5667 | 765 | 49 | 37485 | 0 | Individual | 7.761% | 1.605% |  |  | 7.761% | 1.605% | TRUE |  |  | 7.761% | 1.605%
WALCRK_2_CTG1 | Peaker | 2022 | nonsummer | 41354 | 2022.634 | 0 | 1060 | 100.1 | 106106 | 0 | Individual | 1.906% | 0% |  |  | 1.906% | 0% | TRUE |  |  | 1.906% | 0%
WALCRK_2_CTG1 | Peaker | 2022 | summer | 41354 | 5890.4787 | 0 | 765 | 100.1 | 76576.5 | 0 | Individual | 7.692% | 0% |  |  | 7.692% | 0% | TRUE |  |  | 7.692% | 0%
WALCRK_2_CTG1 | Peaker | 2023 | nonsummer | 41354 | 2534.786 | 0 | 1060 | 100.1 | 106106 | 0 | Individual | 2.389% | 0% |  |  | 2.389% | 0% | TRUE |  |  | 2.389% | 0%
WALCRK_2_CTG1 | Peaker | 2023 | summer | 41354 | 0 | 0 | 765 | 100.1 | 76576.5 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
WALCRK_2_CTG1 | Peaker | 2024 | nonsummer | 41354 | 2028.04 | 0 | 1065 | 100.1 | 106606.5 | 0 | Individual | 1.902% | 0% |  |  | 1.902% | 0% | TRUE |  |  | 1.902% | 0%
WALCRK_2_CTG1 | Peaker | 2024 | summer | 41354 | 9714.705 | 169.4033 | 765 | 100.1 | 76576.5 | 0 | Individual | 12.69% | 0.2212% |  |  | 12.69% | 0.2212% | TRUE |  |  | 12.69% | 0.2212%
WALCRK_2_CTG2 | Peaker | 2022 | nonsummer | 41354 | 31609.4698 | 0 | 1060 | 100.1 | 106106 | 0 | Individual | 29.79% | 0% |  |  | 29.79% | 0% | TRUE |  |  | 29.79% | 0%
WALCRK_2_CTG2 | Peaker | 2022 | summer | 41354 | 20312.336 | 0 | 765 | 100.1 | 76576.5 | 0 | Individual | 26.53% | 0% |  |  | 26.53% | 0% | TRUE |  |  | 26.53% | 0%
WALCRK_2_CTG2 | Peaker | 2023 | nonsummer | 41354 | 52597.5818 | 0 | 1060 | 100.1 | 106106 | 0 | Individual | 49.57% | 0% |  |  | 49.57% | 0% | TRUE |  |  | 49.57% | 0%
WALCRK_2_CTG2 | Peaker | 2023 | summer | 41354 | 1561.4213 | 0 | 765 | 100.1 | 76576.5 | 0 | Individual | 2.039% | 0% |  |  | 2.039% | 0% | TRUE |  |  | 2.039% | 0%
WALCRK_2_CTG2 | Peaker | 2024 | nonsummer | 41354 | 3684.3583 | 0 | 1065 | 100.1 | 106606.5 | 0 | Individual | 3.456% | 0% |  |  | 3.456% | 0% | TRUE |  |  | 3.456% | 0%
WALCRK_2_CTG2 | Peaker | 2024 | summer | 41354 | 380.38 | 35.775 | 765 | 100.1 | 76576.5 | 0 | Individual | 0.4967% | 0.04672% |  |  | 0.4967% | 0.04672% | TRUE |  |  | 0.4967% | 0.04672%
WALCRK_2_CTG3 | Peaker | 2022 | nonsummer | 41354 | 1702.6508 | 0 | 1060 | 100.1 | 106106 | 0 | Individual | 1.605% | 0% |  |  | 1.605% | 0% | TRUE |  |  | 1.605% | 0%
WALCRK_2_CTG3 | Peaker | 2022 | summer | 41354 | 1058.2525 | 18.625 | 765 | 100.1 | 76576.5 | 0 | Individual | 1.382% | 0.02432% |  |  | 1.382% | 0.02432% | TRUE |  |  | 1.382% | 0.02432%
WALCRK_2_CTG3 | Peaker | 2023 | nonsummer | 41354 | 2548.7425 | 0 | 1060 | 100.1 | 106106 | 0 | Individual | 2.402% | 0% |  |  | 2.402% | 0% | TRUE |  |  | 2.402% | 0%
WALCRK_2_CTG3 | Peaker | 2023 | summer | 41354 | 0 | 0 | 765 | 100.1 | 76576.5 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
WALCRK_2_CTG3 | Peaker | 2024 | nonsummer | 41354 | 9734 | 0 | 1065 | 100.1 | 106606.5 | 0 | Individual | 9.131% | 0% |  |  | 9.131% | 0% | TRUE |  |  | 9.131% | 0%
WALCRK_2_CTG3 | Peaker | 2024 | summer | 41354 | 1594.1967 | 125.1683 | 765 | 100.1 | 76576.5 | 0 | Individual | 2.082% | 0.1635% |  |  | 2.082% | 0.1635% | TRUE |  |  | 2.082% | 0.1635%
WALCRK_2_CTG4 | Peaker | 2022 | nonsummer | 41362 | 4137.8967 | 0 | 1060 | 100.1 | 106106 | 0 | Individual | 3.9% | 0% |  |  | 3.9% | 0% | TRUE |  |  | 3.9% | 0%
WALCRK_2_CTG4 | Peaker | 2022 | summer | 41362 | 7888.2067 | 0 | 765 | 100.1 | 76576.5 | 0 | Individual | 10.3% | 0% |  |  | 10.3% | 0% | TRUE |  |  | 10.3% | 0%
WALCRK_2_CTG4 | Peaker | 2023 | nonsummer | 41362 | 1172.665 | 0 | 1060 | 100.1 | 106106 | 0 | Individual | 1.105% | 0% |  |  | 1.105% | 0% | TRUE |  |  | 1.105% | 0%
WALCRK_2_CTG4 | Peaker | 2023 | summer | 41362 | 9352.15 | 0 | 765 | 100.1 | 76576.5 | 0 | Individual | 12.21% | 0% |  |  | 12.21% | 0% | TRUE |  |  | 12.21% | 0%
WALCRK_2_CTG4 | Peaker | 2024 | nonsummer | 41362 | 13129.9 | 0 | 1065 | 100.1 | 106606.5 | 0 | Individual | 12.32% | 0% |  |  | 12.32% | 0% | TRUE |  |  | 12.32% | 0%
WALCRK_2_CTG4 | Peaker | 2024 | summer | 41362 | 64064 | 0 | 765 | 100.1 | 76576.5 | 0 | Individual | 83.66% | 0% |  |  | 83.66% | 0% | TRUE |  |  | 83.66% | 0%
WALCRK_2_CTG5 | Peaker | 2022 | nonsummer | 41394 | 1580.2275 | 0 | 1060 | 100.1 | 106106 | 0 | Individual | 1.489% | 0% |  |  | 1.489% | 0% | TRUE |  |  | 1.489% | 0%
WALCRK_2_CTG5 | Peaker | 2022 | summer | 41394 | 2028.8683 | 0 | 765 | 100.1 | 76576.5 | 0 | Individual | 2.649% | 0% |  |  | 2.649% | 0% | TRUE |  |  | 2.649% | 0%
WALCRK_2_CTG5 | Peaker | 2023 | nonsummer | 41394 | 1532.5383 | 0 | 1060 | 100.1 | 106106 | 0 | Individual | 1.444% | 0% |  |  | 1.444% | 0% | TRUE |  |  | 1.444% | 0%
WALCRK_2_CTG5 | Peaker | 2023 | summer | 41394 | 314.4658 | 0 | 765 | 100.1 | 76576.5 | 0 | Individual | 0.4107% | 0% |  |  | 0.4107% | 0% | TRUE |  |  | 0.4107% | 0%
WALCRK_2_CTG5 | Peaker | 2024 | nonsummer | 41394 | 2002 | 0 | 1065 | 100.1 | 106606.5 | 0 | Individual | 1.878% | 0% |  |  | 1.878% | 0% | TRUE |  |  | 1.878% | 0%
WALCRK_2_CTG5 | Peaker | 2024 | summer | 41394 | 7329.6967 | 156.0317 | 765 | 100.1 | 76576.5 | 0 | Individual | 9.572% | 0.2038% |  |  | 9.572% | 0.2038% | TRUE |  |  | 9.572% | 0.2038%
WOLFSK_1_UNITA1 | Peaker | 2022 | nonsummer | 37702 | 5572.5017 | 0 | 1060 | 48.68 | 51600.8 | 0 | Individual | 10.8% | 0% |  |  | 10.8% | 0% | TRUE |  |  | 10.8% | 0%
WOLFSK_1_UNITA1 | Peaker | 2022 | summer | 37702 | 411.405 | 501.55 | 765 | 48.68 | 37240.2 | 0 | Individual | 1.105% | 1.347% |  |  | 1.105% | 1.347% | TRUE |  |  | 1.105% | 1.347%
WOLFSK_1_UNITA1 | Peaker | 2023 | nonsummer | 37702 | 994.6947 | 0 | 1060 | 48.68 | 51600.8 | 0 | Individual | 1.928% | 0% |  |  | 1.928% | 0% | TRUE |  |  | 1.928% | 0%
WOLFSK_1_UNITA1 | Peaker | 2023 | summer | 37702 | 54.6668 | 366.4453 | 765 | 48.68 | 37240.2 | 0 | Individual | 0.1468% | 0.984% |  |  | 0.1468% | 0.984% | TRUE |  |  | 0.1468% | 0.984%
WOLFSK_1_UNITA1 | Peaker | 2024 | nonsummer | 37702 | 339.9487 | 486.036 | 1065 | 48.68 | 51844.2 | 0 | Individual | 0.6557% | 0.9375% |  |  | 0.6557% | 0.9375% | TRUE |  |  | 0.6557% | 0.9375%
WOLFSK_1_UNITA1 | Peaker | 2024 | summer | 37702 | 0 | 1079.3698 | 765 | 48.68 | 37240.2 | 0 | Individual | 0% | 2.898% |  |  | 0% | 2.898% | TRUE |  |  | 0% | 2.898%
YUBACT_6_UNITA1 | Peaker | 2022 | nonsummer | 37463 | 287.3733 | 13.044 | 1060 | 47.16 | 49989.6 | 0 | Individual | 0.5749% | 0.02609% |  |  | 0.5749% | 0.02609% | TRUE |  |  | 0.5749% | 0.02609%
YUBACT_6_UNITA1 | Peaker | 2022 | summer | 37463 | 179.812 | 747.118 | 765 | 47.16 | 36077.4 | 0 | Individual | 0.4984% | 2.071% |  |  | 0.4984% | 2.071% | TRUE |  |  | 0.4984% | 2.071%
YUBACT_6_UNITA1 | Peaker | 2023 | nonsummer | 37463 | 329.334 | 4.212 | 1060 | 47.16 | 49989.6 | 0 | Individual | 0.6588% | 0.008426% |  |  | 0.6588% | 0.008426% | TRUE |  |  | 0.6588% | 0.008426%
YUBACT_6_UNITA1 | Peaker | 2023 | summer | 37463 | 368.634 | 218.632 | 765 | 47.16 | 36077.4 | 0 | Individual | 1.022% | 0.606% |  |  | 1.022% | 0.606% | TRUE |  |  | 1.022% | 0.606%
YUBACT_6_UNITA1 | Peaker | 2024 | nonsummer | 37463 | 1026.266 | 187 | 1065 | 47.16 | 50225.4 | 0 | Individual | 2.043% | 0.3723% |  |  | 2.043% | 0.3723% | TRUE |  |  | 2.043% | 0.3723%
YUBACT_6_UNITA1 | Peaker | 2024 | summer | 37463 | 271.1647 | 1341.94 | 765 | 47.16 | 36077.4 | 0 | Individual | 0.7516% | 3.72% |  |  | 0.7516% | 3.72% | TRUE |  |  | 0.7516% | 3.72%
BANKPP_2_NSPIN | Pump | 2022 | nonsummer | 39903 | 0 | 0 | 1060 | 270 | 286200 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
BANKPP_2_NSPIN | Pump | 2022 | summer | 39903 | 0 | 0 | 765 | 270 | 206550 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
BANKPP_2_NSPIN | Pump | 2023 | nonsummer | 39903 | 337.5 | 0 | 1060 | 270 | 286200 | 0 | Individual | 0.1179% | 0% |  |  | 0.1179% | 0% | TRUE |  |  | 0.1179% | 0%
BANKPP_2_NSPIN | Pump | 2023 | summer | 39903 | 1548 | 0 | 765 | 270 | 206550 | 0 | Individual | 0.7495% | 0% |  |  | 0.7495% | 0% | TRUE |  |  | 0.7495% | 0%
BANKPP_2_NSPIN | Pump | 2024 | nonsummer | 39903 | 0 | 0 | 1065 | 270 | 287550 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
BANKPP_2_NSPIN | Pump | 2024 | summer | 39903 | 0 | 0 | 765 | 270 | 206550 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
DOSMGO_2_NSPIN | Pump | 2022 | nonsummer | 39903 | 0 | 0 | 1060 | 159 | 168540 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
DOSMGO_2_NSPIN | Pump | 2022 | summer | 39903 | 0 | 0 | 765 | 159 | 121635 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
DOSMGO_2_NSPIN | Pump | 2023 | nonsummer | 39903 | 0 | 0 | 1060 | 159 | 168540 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
DOSMGO_2_NSPIN | Pump | 2023 | summer | 39903 | 0 | 0 | 765 | 159 | 121635 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
DOSMGO_2_NSPIN | Pump | 2024 | nonsummer | 39903 | 0 | 0 | 1065 | 159 | 169335 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
DOSMGO_2_NSPIN | Pump | 2024 | summer | 39903 | 0 | 0 | 765 | 159 | 121635 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
EDMONS_2_NSPIN | Pump | 2022 | nonsummer | 39903 | 46216.22 | 0 | 1060 | 775.8 | 822348 | 0 | Individual | 5.62% | 0% |  |  | 5.62% | 0% | TRUE |  |  | 5.62% | 0%
EDMONS_2_NSPIN | Pump | 2022 | summer | 39903 | 45900 | 0 | 765 | 775.8 | 593487 | 0 | Individual | 7.734% | 0% |  |  | 7.734% | 0% | TRUE |  |  | 7.734% | 0%
EDMONS_2_NSPIN | Pump | 2023 | nonsummer | 39903 | 52011 | 0 | 1060 | 775.8 | 822348 | 0 | Individual | 6.325% | 0% |  |  | 6.325% | 0% | TRUE |  |  | 6.325% | 0%
EDMONS_2_NSPIN | Pump | 2023 | summer | 39903 | 35572.3333 | 0 | 765 | 775.8 | 593487 | 0 | Individual | 5.994% | 0% |  |  | 5.994% | 0% | TRUE |  |  | 5.994% | 0%
EDMONS_2_NSPIN | Pump | 2024 | nonsummer | 39903 | 49278 | 0 | 1065 | 775.8 | 826227 | 0 | Individual | 5.964% | 0% |  |  | 5.964% | 0% | TRUE |  |  | 5.964% | 0%
EDMONS_2_NSPIN | Pump | 2024 | summer | 39903 | 38687 | 0 | 765 | 775.8 | 593487 | 0 | Individual | 6.519% | 0% |  |  | 6.519% | 0% | TRUE |  |  | 6.519% | 0%
OSO_6_NSPIN | Pump | 2022 | nonsummer | 39903 | 0 | 0 | 1060 | 70 | 74200 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
OSO_6_NSPIN | Pump | 2022 | summer | 39903 | 0 | 0 | 765 | 70 | 53550 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
OSO_6_NSPIN | Pump | 2023 | nonsummer | 39903 | 0 | 0 | 1060 | 70 | 74200 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
OSO_6_NSPIN | Pump | 2023 | summer | 39903 | 0 | 0 | 765 | 70 | 53550 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
OSO_6_NSPIN | Pump | 2024 | nonsummer | 39903 | 0 | 0 | 1065 | 70 | 74550 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
OSO_6_NSPIN | Pump | 2024 | summer | 39903 | 0 | 0 | 765 | 70 | 53550 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
PEARBL_2_NSPIN | Pump | 2022 | nonsummer | 39903 | 0 | 0 | 1060 | 118 | 125080 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
PEARBL_2_NSPIN | Pump | 2022 | summer | 39903 | 0 | 0 | 765 | 118 | 90270 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
PEARBL_2_NSPIN | Pump | 2023 | nonsummer | 39903 | 118 | 0 | 1060 | 118 | 125080 | 0 | Individual | 0.09434% | 0% |  |  | 0.09434% | 0% | TRUE |  |  | 0.09434% | 0%
PEARBL_2_NSPIN | Pump | 2023 | summer | 39903 | 0 | 0 | 765 | 118 | 90270 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
PEARBL_2_NSPIN | Pump | 2024 | nonsummer | 39903 | 0 | 0 | 1065 | 118 | 125670 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
PEARBL_2_NSPIN | Pump | 2024 | summer | 39903 | 590 | 0 | 765 | 118 | 90270 | 0 | Individual | 0.6536% | 0% |  |  | 0.6536% | 0% | TRUE |  |  | 0.6536% | 0%
EASTWD_7_UNIT | Pumped Hydro | 2022 | nonsummer | 31778 | 1000 | 0 | 1060 | 200 | 212000 | 0 | Individual | 0.4717% | 0% |  |  | 0.4717% | 0% | TRUE |  |  | 0.4717% | 0%
EASTWD_7_UNIT | Pumped Hydro | 2022 | summer | 31778 | 31400 | 165.6667 | 765 | 200 | 153000 | 0 | Individual | 20.52% | 0.1083% |  |  | 20.52% | 0.1083% | TRUE |  |  | 20.52% | 0.1083%
EASTWD_7_UNIT | Pumped Hydro | 2023 | nonsummer | 31778 | 0 | 0 | 1060 | 200 | 212000 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
EASTWD_7_UNIT | Pumped Hydro | 2023 | summer | 31778 | 65400 | 0 | 765 | 200 | 153000 | 0 | Individual | 42.75% | 0% |  |  | 42.75% | 0% | TRUE |  |  | 42.75% | 0%
EASTWD_7_UNIT | Pumped Hydro | 2024 | nonsummer | 31778 | 8016.6667 | 0 | 1065 | 200 | 213000 | 0 | Individual | 3.764% | 0% |  |  | 3.764% | 0% | TRUE |  |  | 3.764% | 0%
EASTWD_7_UNIT | Pumped Hydro | 2024 | summer | 31778 | 27518.6667 | 0 | 765 | 200 | 153000 | 0 | Individual | 17.99% | 0% |  |  | 17.99% | 0% | TRUE |  |  | 17.99% | 0%
HELMPG_7_UNIT 1 | Pumped Hydro | 2022 | nonsummer | 30682 | 70884.3167 | 0 | 1060 | 407 | 431420 | 0 | Individual | 16.43% | 0% |  |  | 16.43% | 0% | TRUE |  |  | 16.43% | 0%
HELMPG_7_UNIT 1 | Pumped Hydro | 2022 | summer | 30682 | 2272.4167 | 0 | 765 | 407 | 311355 | 0 | Individual | 0.7298% | 0% |  |  | 0.7298% | 0% | TRUE |  |  | 0.7298% | 0%
HELMPG_7_UNIT 1 | Pumped Hydro | 2023 | nonsummer | 30682 | 4884.1 | 0 | 1060 | 407 | 431420 | 0 | Individual | 1.132% | 0% |  |  | 1.132% | 0% | TRUE |  |  | 1.132% | 0%
HELMPG_7_UNIT 1 | Pumped Hydro | 2023 | summer | 30682 | 2665.85 | 0 | 765 | 407 | 311355 | 0 | Individual | 0.8562% | 0% |  |  | 0.8562% | 0% | TRUE |  |  | 0.8562% | 0%
HELMPG_7_UNIT 1 | Pumped Hydro | 2024 | nonsummer | 30682 | 12135.3833 | 0 | 1065 | 407 | 433455 | 0 | Individual | 2.8% | 0% |  |  | 2.8% | 0% | TRUE |  |  | 2.8% | 0%
HELMPG_7_UNIT 1 | Pumped Hydro | 2024 | summer | 30682 | 12589.5 | 0 | 765 | 407 | 311355 | 0 | Individual | 4.043% | 0% |  |  | 4.043% | 0% | TRUE |  |  | 4.043% | 0%
HELMPG_7_UNIT 2 | Pumped Hydro | 2022 | nonsummer | 30682 | 60769.1333 | 0 | 1060 | 407 | 431420 | 0 | Individual | 14.09% | 0% |  |  | 14.09% | 0% | TRUE |  |  | 14.09% | 0%
HELMPG_7_UNIT 2 | Pumped Hydro | 2022 | summer | 30682 | 0 | 0 | 765 | 407 | 311355 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
HELMPG_7_UNIT 2 | Pumped Hydro | 2023 | nonsummer | 30682 | 3588.3833 | 0 | 1060 | 407 | 431420 | 0 | Individual | 0.8318% | 0% |  |  | 0.8318% | 0% | TRUE |  |  | 0.8318% | 0%
HELMPG_7_UNIT 2 | Pumped Hydro | 2023 | summer | 30682 | 8567.35 | 0 | 765 | 407 | 311355 | 0 | Individual | 2.752% | 0% |  |  | 2.752% | 0% | TRUE |  |  | 2.752% | 0%
HELMPG_7_UNIT 2 | Pumped Hydro | 2024 | nonsummer | 30682 | 7665.1667 | 0 | 1065 | 407 | 433455 | 0 | Individual | 1.768% | 0% |  |  | 1.768% | 0% | TRUE |  |  | 1.768% | 0%
HELMPG_7_UNIT 2 | Pumped Hydro | 2024 | summer | 30682 | 7095 | 0 | 765 | 407 | 311355 | 0 | Individual | 2.279% | 0% |  |  | 2.279% | 0% | TRUE |  |  | 2.279% | 0%
HELMPG_7_UNIT 3 | Pumped Hydro | 2022 | nonsummer | 30682 | 81275 | 0 | 1060 | 404 | 428240 | 0 | Individual | 18.98% | 0% |  |  | 18.98% | 0% | TRUE |  |  | 18.98% | 0%
HELMPG_7_UNIT 3 | Pumped Hydro | 2022 | summer | 30682 | 1232.2 | 0 | 765 | 404 | 309060 | 0 | Individual | 0.3987% | 0% |  |  | 0.3987% | 0% | TRUE |  |  | 0.3987% | 0%
HELMPG_7_UNIT 3 | Pumped Hydro | 2023 | nonsummer | 30682 | 6039.8 | 0 | 1060 | 404 | 428240 | 0 | Individual | 1.41% | 0% |  |  | 1.41% | 0% | TRUE |  |  | 1.41% | 0%
HELMPG_7_UNIT 3 | Pumped Hydro | 2023 | summer | 30682 | 11392.8 | 0 | 765 | 404 | 309060 | 0 | Individual | 3.686% | 0% |  |  | 3.686% | 0% | TRUE |  |  | 3.686% | 0%
HELMPG_7_UNIT 3 | Pumped Hydro | 2024 | nonsummer | 30682 | 9628.6667 | 0 | 1065 | 404 | 430260 | 0 | Individual | 2.238% | 0% |  |  | 2.238% | 0% | TRUE |  |  | 2.238% | 0%
HELMPG_7_UNIT 3 | Pumped Hydro | 2024 | summer | 30682 | 4860 | 0 | 765 | 404 | 309060 | 0 | Individual | 1.573% | 0% |  |  | 1.573% | 0% | TRUE |  |  | 1.573% | 0%
CDWR07_2_GEN | Reciprocating Engine | 2022 | nonsummer | 2009-03-31 | 0 | 0 | 1060 | 415.3 | 440218 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
CDWR07_2_GEN | Reciprocating Engine | 2022 | summer | 2009-03-31 | 0 | 0 | 765 | 415.3 | 317704.5 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
CDWR07_2_GEN | Reciprocating Engine | 2023 | nonsummer | 2009-03-31 | 264.225 | 0 | 1060 | 415.3 | 440218 | 0 | Individual | 0.06002% | 0% |  |  | 0.06002% | 0% | TRUE |  |  | 0.06002% | 0%
CDWR07_2_GEN | Reciprocating Engine | 2023 | summer | 2009-03-31 | 0 | 0 | 765 | 415.3 | 317704.5 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
CDWR07_2_GEN | Reciprocating Engine | 2024 | nonsummer | 2009-03-31 | 402.3 | 0 | 1065 | 415.3 | 442294.5 | 0 | Individual | 0.09096% | 0% |  |  | 0.09096% | 0% | TRUE |  |  | 0.09096% | 0%
CDWR07_2_GEN | Reciprocating Engine | 2024 | summer | 2009-03-31 | 2076.5 | 0 | 765 | 415.3 | 317704.5 | 0 | Individual | 0.6536% | 0% |  |  | 0.6536% | 0% | TRUE |  |  | 0.6536% | 0%
CHWCHL_1_UNIT | Reciprocating Engine | 2022 | nonsummer | 2001-06-13 | 1162.5 | 0 | 1060 | 48.6 | 51516 | 0 | Individual | 2.257% | 0% |  |  | 2.257% | 0% | TRUE |  |  | 2.257% | 0%
CHWCHL_1_UNIT | Reciprocating Engine | 2022 | summer | 2001-06-13 | 916.9 | 136.2167 | 765 | 48.6 | 37179 | 0 | Individual | 2.466% | 0.3664% |  |  | 2.466% | 0.3664% | TRUE |  |  | 2.466% | 0.3664%
CHWCHL_1_UNIT | Reciprocating Engine | 2023 | nonsummer | 2001-06-13 | 1079.5 | 0 | 1060 | 48.6 | 51516 | 0 | Individual | 2.095% | 0% |  |  | 2.095% | 0% | TRUE |  |  | 2.095% | 0%
CHWCHL_1_UNIT | Reciprocating Engine | 2023 | summer | 2001-06-13 | 112.5333 | 742.875 | 765 | 48.6 | 37179 | 0 | Individual | 0.3027% | 1.998% |  |  | 0.3027% | 1.998% | TRUE |  |  | 0.3027% | 1.998%
CHWCHL_1_UNIT | Reciprocating Engine | 2024 | nonsummer | 2001-06-13 | 350.84 | 0 | 1065 | 48.6 | 51759 | 0 | Individual | 0.6778% | 0% |  |  | 0.6778% | 0% | TRUE |  |  | 0.6778% | 0%
CHWCHL_1_UNIT | Reciprocating Engine | 2024 | summer | 2001-06-13 | 111.88 | 503.1233 | 765 | 48.6 | 37179 | 0 | Individual | 0.3009% | 1.353% |  |  | 0.3009% | 1.353% | TRUE |  |  | 0.3009% | 1.353%
HUMBPP_1_UNITS3 | Reciprocating Engine | 2022 | nonsummer | 2010-09-29 | 1234.348 | 0 | 1060 | 65.08 | 68984.8 | 0 | Individual | 1.789% | 0% |  |  | 1.789% | 0% | TRUE |  |  | 1.789% | 0%
HUMBPP_1_UNITS3 | Reciprocating Engine | 2022 | summer | 2010-09-29 | 15846.8118 | 0 | 765 | 65.08 | 49786.2 | 0 | Individual | 31.83% | 0% |  |  | 31.83% | 0% | TRUE |  |  | 31.83% | 0%
HUMBPP_1_UNITS3 | Reciprocating Engine | 2023 | nonsummer | 2010-09-29 | 2940.587 | 0 | 1060 | 65.08 | 68984.8 | 0 | Individual | 4.263% | 0% |  |  | 4.263% | 0% | TRUE |  |  | 4.263% | 0%
HUMBPP_1_UNITS3 | Reciprocating Engine | 2023 | summer | 2010-09-29 | 868.1568 | 0 | 765 | 65.08 | 49786.2 | 0 | Individual | 1.744% | 0% |  |  | 1.744% | 0% | TRUE |  |  | 1.744% | 0%
HUMBPP_1_UNITS3 | Reciprocating Engine | 2024 | nonsummer | 2010-09-29 | 1875.1175 | 3644.48 | 1065 | 65.08 | 69310.2 | 0 | Individual | 2.705% | 5.258% |  |  | 2.705% | 5.258% | TRUE |  |  | 2.705% | 5.258%
HUMBPP_1_UNITS3 | Reciprocating Engine | 2024 | summer | 2010-09-29 | 1301.6 | 0 | 765 | 65.08 | 49786.2 | 0 | Individual | 2.614% | 0% |  |  | 2.614% | 0% | TRUE |  |  | 2.614% | 0%
HUMBPP_6_UNITS | Reciprocating Engine | 2022 | nonsummer | 2010-09-29 | 8435.7238 | 0 | 1060 | 97.62 | 103477.2 | 0 | Individual | 8.152% | 0% |  |  | 8.152% | 0% | TRUE |  |  | 8.152% | 0%
HUMBPP_6_UNITS | Reciprocating Engine | 2022 | summer | 2010-09-29 | 19803.1398 | 0 | 765 | 97.62 | 74679.3 | 0 | Individual | 26.52% | 0% |  |  | 26.52% | 0% | TRUE |  |  | 26.52% | 0%
HUMBPP_6_UNITS | Reciprocating Engine | 2023 | nonsummer | 2010-09-29 | 5484.617 | 0 | 1060 | 97.62 | 103477.2 | 0 | Individual | 5.3% | 0% |  |  | 5.3% | 0% | TRUE |  |  | 5.3% | 0%
HUMBPP_6_UNITS | Reciprocating Engine | 2023 | summer | 2010-09-29 | 578.9408 | 0 | 765 | 97.62 | 74679.3 | 0 | Individual | 0.7752% | 0% |  |  | 0.7752% | 0% | TRUE |  |  | 0.7752% | 0%
HUMBPP_6_UNITS | Reciprocating Engine | 2024 | nonsummer | 2010-09-29 | 3570.4515 | 13179.9347 | 1065 | 97.62 | 103965.3 | 0 | Individual | 3.434% | 12.68% |  |  | 3.434% | 12.68% | TRUE |  |  | 3.434% | 12.68%
HUMBPP_6_UNITS | Reciprocating Engine | 2024 | summer | 2010-09-29 | 5210.4675 | 162.7 | 765 | 97.62 | 74679.3 | 0 | Individual | 6.977% | 0.2179% |  |  | 6.977% | 0.2179% | TRUE |  |  | 6.977% | 0.2179%
REDBLF_6_UNIT | Reciprocating Engine | 2022 | nonsummer | 2001-08-11 | 0 | 0 | 1060 | 44 | 46640 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
REDBLF_6_UNIT | Reciprocating Engine | 2022 | summer | 2001-08-11 | 0 | 0 | 765 | 44 | 33660 | 0 | Individual | 0% | 0% |  |  | 0% | 0% | TRUE |  |  | 0% | 0%
REDBLF_6_UNIT | Reciprocating Engine | 2023 | nonsummer | 2001-08-11 | 125 | 0 | 1060 | 44 | 46640 | 0 | Individual | 0.268% | 0% |  |  | 0.268% | 0% | TRUE |  |  | 0.268% | 0%
REDBLF_6_UNIT | Reciprocating Engine | 2023 | summer | 2001-08-11 | 468.2167 | 8.8 | 765 | 44 | 33660 | 0 | Individual | 1.391% | 0.02614% |  |  | 1.391% | 0.02614% | TRUE |  |  | 1.391% | 0.02614%
REDBLF_6_UNIT | Reciprocating Engine | 2024 | nonsummer | 2001-08-11 | 2012.2667 | 0 | 1065 | 44 | 46860 | 0 | Individual | 4.294% | 0% |  |  | 4.294% | 0% | TRUE |  |  | 4.294% | 0%
REDBLF_6_UNIT | Reciprocating Engine | 2024 | summer | 2001-08-11 | 30 | 0 | 765 | 44 | 33660 | 0 | Individual | 0.08913% | 0% |  |  | 0.08913% | 0% | TRUE |  |  | 0.08913% | 0%
CABALO_2_M2WSR2 | Solar_1Axis | 2022 | nonsummer | 44146 | 9499.4592 | 0 | 1060 | 100 | 106000 | 0 | Individual | 8.962% | 0% |  |  | 8.962% | 0% | TRUE |  |  | 8.962% | 0%
CABALO_2_M2WSR2 | Solar_1Axis | 2022 | summer | 44146 | 5601.3573 | 0 | 765 | 100 | 76500 | 0 | Individual | 7.322% | 0% |  |  | 7.322% | 0% | TRUE |  |  | 7.322% | 0%
CABALO_2_M2WSR2 | Solar_1Axis | 2023 | nonsummer | 44146 | 3410.77 | 0 | 1060 | 100 | 106000 | 0 | Individual | 3.218% | 0% |  |  | 3.218% | 0% | TRUE |  |  | 3.218% | 0%
CABALO_2_M2WSR2 | Solar_1Axis | 2023 | summer | 44146 | 2478.9433 | 0 | 765 | 100 | 76500 | 0 | Individual | 3.24% | 0% |  |  | 3.24% | 0% | TRUE |  |  | 3.24% | 0%
CABALO_2_M2WSR2 | Solar_1Axis | 2024 | nonsummer | 44146 | 6944.6867 | 0 | 1065 | 100 | 106500 | 0 | Individual | 6.521% | 0% |  |  | 6.521% | 0% | TRUE |  |  | 6.521% | 0%
CABALO_2_M2WSR2 | Solar_1Axis | 2024 | summer | 44146 | 379.68 | 0 | 765 | 100 | 76500 | 0 | Individual | 0.4963% | 0% |  |  | 0.4963% | 0% | TRUE |  |  | 0.4963% | 0%
ELNIDO_1_ECRSR1 | Solar_Fixed | 2022 | nonsummer | 45713 | 0 | 0 | 0 | 3 | 0 | 1060 | Group | [6 empty] | FALSE
ELNIDO_1_ECRSR1 | Solar_Fixed | 2022 | summer | 45713 | 0 | 0 | 0 | 3 | 0 | 765 | Group | [6 empty] | FALSE
ELNIDO_1_ECRSR1 | Solar_Fixed | 2023 | nonsummer | 45713 | 0 | 0 | 0 | 3 | 0 | 1060 | Group | [6 empty] | FALSE
ELNIDO_1_ECRSR1 | Solar_Fixed | 2023 | summer | 45713 | 0 | 0 | 0 | 3 | 0 | 765 | Group | [6 empty] | FALSE
ELNIDO_1_ECRSR1 | Solar_Fixed | 2024 | nonsummer | 45713 | 0 | 0 | 0 | 3 | 0 | 1065 | Group | [6 empty] | FALSE
ELNIDO_1_ECRSR1 | Solar_Fixed | 2024 | summer | 45713 | 0 | 0 | 0 | 3 | 0 | 765 | Group | [6 empty] | FALSE

## Outage Data
YEAR | SEASON | RESOURCE ID | NATURE OF WORK | OUTAGE MWH DURING DEMAND
2022 | summer | ACACIA_6_SOLAR | PLANT_MAINTENANCE | 39
2022 | summer | ADERA_1_SOLAR1 | PLANT_MAINTENANCE | 7.5
2022 | summer | ADLIN_1_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 7710.89
2022 | summer | ADLIN_1_UNITS | PLANT_TROUBLE | 80.6667
2022 | summer | ADLIN_1_UNITS | TRANSMISSION_INDUCED | 70
2022 | summer | ADMEST_6_SOLAR | PLANT_TROUBLE | 62.0613
2022 | summer | ADOBEE_1_SOLAR | METERING_TELEMETRY | 0
2022 | summer | ADOBEE_1_SOLAR | PLANT_TROUBLE | 0
2022 | summer | ADOBEE_1_SOLAR | TRANSMISSION_INDUCED | 0
2022 | summer | AGRICO_6_PL3N5 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 26.4717
2022 | summer | AGRICO_6_PL3N5 | AMBIENT_DUE_TO_TEMP | 730.7462
2022 | summer | AGRICO_6_PL3N5 | PLANT_TROUBLE | 8.6667
2022 | summer | AGUCAL_5_SOLAR1 | PLANT_TROUBLE | 0
2022 | summer | AKINGS_6_AMESR1 | PLANT_MAINTENANCE | 49.1667
2022 | summer | AKINGS_6_AMESR1 | PLANT_TROUBLE | 132.2583
2022 | summer | ALAMIT_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 7530.1667
2022 | summer | ALAMIT_2_PL1X3 | PLANT_TROUBLE | 5730.0492
2022 | summer | ALAMIT_7_ES1 | METERING_TELEMETRY | 225
2022 | summer | ALAMIT_7_ES1 | PLANT_TROUBLE | 12736.6258
2022 | summer | ALAMIT_7_UNIT 3 | AMBIENT_DUE_TO_TEMP | 1325.1773
2022 | summer | ALAMIT_7_UNIT 3 | AMBIENT_NOT_DUE_TO_TEMP | 111.5
2022 | summer | ALAMIT_7_UNIT 3 | PLANT_TROUBLE | 27989.513
2022 | summer | ALAMIT_7_UNIT 3 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2022 | summer | ALAMIT_7_UNIT 3 | UNIT_SUPPORTING_STARTUP | 775.1613
2022 | summer | ALAMIT_7_UNIT 3 | UNIT_TESTING | 0
2022 | summer | ALAMIT_7_UNIT 4 | AMBIENT_DUE_TO_TEMP | 2323.1078
2022 | summer | ALAMIT_7_UNIT 4 | AMBIENT_NOT_DUE_TO_TEMP | 167.9628
2022 | summer | ALAMIT_7_UNIT 4 | PLANT_TROUBLE | 20103.7317
2022 | summer | ALAMIT_7_UNIT 4 | UNIT_SUPPORTING_STARTUP | 446.9688
2022 | summer | ALAMIT_7_UNIT 4 | UNIT_TESTING | 0
2022 | summer | ALAMIT_7_UNIT 5 | AMBIENT_DUE_TO_TEMP | 1888.75
2022 | summer | ALAMIT_7_UNIT 5 | PLANT_MAINTENANCE | 8216
2022 | summer | ALAMIT_7_UNIT 5 | PLANT_TROUBLE | 21651.5
2022 | summer | ALAMIT_7_UNIT 5 | UNIT_TESTING | 0
2022 | summer | ALAMO_6_UNIT | PLANT_MAINTENANCE | 0
2022 | summer | ALAMO_6_UNIT | PLANT_TROUBLE | 680
2022 | summer | ALHMBR_1_ALHSLR | AMBIENT_DUE_TO_TEMP | 113.3333
2022 | summer | ALHMBR_1_ALHSLR | PLANT_MAINTENANCE | 493.3333
2022 | summer | ALHMBR_1_ALHSLR | PLANT_TROUBLE | 8.3333
2022 | summer | ALHMBR_1_ALHSLR | TRANSMISSION_INDUCED | 1000
2022 | summer | ALMASL_2_AL6BT6 | PLANT_MAINTENANCE | 2302.8
2022 | summer | ALMASL_2_AL6BT6 | PLANT_TROUBLE | 350.8
2022 | summer | ALMASL_2_GS1SR1 | PLANT_MAINTENANCE | 0
2022 | summer | ALMASL_2_GS1SR1 | PLANT_TROUBLE | 0
2022 | summer | ALMASL_2_GS4SR4 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | summer | ALMASL_2_GS4SR4 | PLANT_MAINTENANCE | 0
2022 | summer | ALMASL_2_GS6SR6 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | summer | ALMASL_2_GS6SR6 | PLANT_MAINTENANCE | 0
2022 | summer | ALMASL_2_GS7SR7 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | summer | ALMASL_2_GS7SR7 | PLANT_MAINTENANCE | 0
2022 | summer | ALMEGT_1_UNIT 1 | AMBIENT_DUE_TO_TEMP | 1020
2022 | summer | ALMEGT_1_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 25
2022 | summer | ALMEGT_1_UNIT 1 | PLANT_TROUBLE | 4375
2022 | summer | ALMEGT_1_UNIT 2 | AMBIENT_DUE_TO_TEMP | 1235
2022 | summer | ALMEGT_1_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 25
2022 | summer | ALMEGT_1_UNIT 2 | PLANT_TROUBLE | 0
2022 | summer | ALPSLR_1_NTHSLR | METERING_TELEMETRY | 65.3333
2022 | summer | ALPSLR_1_NTHSLR | PLANT_TROUBLE | 14
2022 | summer | ALPSLR_1_SPSSLR | PLANT_MAINTENANCE | 100
2022 | summer | ALPSLR_1_SPSSLR | PLANT_TROUBLE | 0
2022 | summer | ALT6DN_2_WIND7 | PLANT_MAINTENANCE | 1897.7805
2022 | summer | ALT6DS_2_WIND9 | METERING_TELEMETRY | 660
2022 | summer | ALTA3A_2_CPCE4 | METERING_TELEMETRY | 615
2022 | summer | ALTA3A_2_CPCE4 | PLANT_TROUBLE | 4042.05
2022 | summer | ALTA3A_2_CPCE5 | METERING_TELEMETRY | 833.1
2022 | summer | ALTA3A_2_CPCE5 | PLANT_TROUBLE | 3915.3
2022 | summer | ALTA3A_2_CPCE8 | PLANT_MAINTENANCE | 7930.1
2022 | summer | ALTA3A_2_CPCE8 | PLANT_TROUBLE | 2516.15
2022 | summer | ALTA4A_2_CPCW1 | METERING_TELEMETRY | 690
2022 | summer | ALTA4A_2_CPCW1 | PLANT_TROUBLE | 2313.7
2022 | summer | ALTA4B_2_CPCW2 | METERING_TELEMETRY | 735
2022 | summer | ALTA4B_2_CPCW2 | PLANT_TROUBLE | 3113.4
2022 | summer | ALTA4B_2_CPCW3 | METERING_TELEMETRY | 675
2022 | summer | ALTA4B_2_CPCW3 | PLANT_MAINTENANCE | 1470
2022 | summer | ALTA4B_2_CPCW3 | PLANT_TROUBLE | 3851.25
2022 | summer | ALTA6B_2_WIND11 | METERING_TELEMETRY | 434
2022 | summer | ALTA6B_2_WIND11 | PLANT_MAINTENANCE | 422.75
2022 | summer | ALTA6B_2_WIND11 | PLANT_TROUBLE | 852.9417
2022 | summer | ALTA6E_2_WIND10 | METERING_TELEMETRY | 670.5953
2022 | summer | ALTA6E_2_WIND10 | PLANT_TROUBLE | 3088.4897
2022 | summer | ALTWD_2_COAWD1 | PLANT_MAINTENANCE | 0
2022 | summer | ALTWD_2_COAWD1 | PLANT_TROUBLE | 79.2
2022 | summer | ANAHM_2_CANYN1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 984.2
2022 | summer | ANAHM_2_CANYN1 | PLANT_TROUBLE | 230.3712
2022 | summer | ANAHM_2_CANYN1 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 13.9732
2022 | summer | ANAHM_2_CANYN2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 960.8
2022 | summer | ANAHM_2_CANYN2 | PLANT_TROUBLE | 63.2527
2022 | summer | ANAHM_2_CANYN3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 929.8
2022 | summer | ANAHM_2_CANYN3 | PLANT_TROUBLE | 454.0523
2022 | summer | ANAHM_2_CANYN3 | TRANSMISSION_INDUCED | 46.49
2022 | summer | ANAHM_2_CANYN4 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 996
2022 | summer | ANAHM_2_CANYN4 | PLANT_TROUBLE | 172.6737
2022 | summer | ANAHM_2_CANYN4 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 14.5533
2022 | summer | ANZA_6_SOLAR1 | TRANSMISSION_INDUCED | 697.6667
2022 | summer | APLHIL_1_SFKHY1 | PLANT_TROUBLE | 281.4
2022 | summer | AQUAWS_2_AQWSR1 | PLANT_TROUBLE | 2067.3333
2022 | summer | AQUAWS_2_AQWSR1 | TRANSMISSION_INDUCED | 1497
2022 | summer | ARBWD_6_QF | METERING_TELEMETRY | 0
2022 | summer | ARBWD_6_QF | PLANT_TROUBLE | 0
2022 | summer | ARBWD_6_QF | TRANSMISSION_INDUCED | 6.95
2022 | summer | ARCOGN_2_UNITS | AMBIENT_DUE_TO_TEMP | 180
2022 | summer | ARCOGN_2_UNITS | PLANT_TROUBLE | 17474.1667
2022 | summer | ARKANS_1_ARKSLR | PLANT_MAINTENANCE | 13.3333
2022 | summer | ARKANS_1_ARKSLR | PLANT_TROUBLE | 53.3333
2022 | summer | ARKANS_1_ARKSLR | TRANSMISSION_INDUCED | 1238.3333
2022 | summer | ARLNTN_2_AR1SR1 | METERING_TELEMETRY | 0
2022 | summer | ARLNTN_2_AR1SR1 | PLANT_MAINTENANCE | 0
2022 | summer | ARLNTN_2_AR1SR1 | TRANSMISSION_INDUCED | 0
2022 | summer | ARLNTN_2_AR1SR1 | UNIT_TESTING | 0
2022 | summer | ARLNTN_2_ASUSR1 | PLANT_TROUBLE | 1724.4933
2022 | summer | ARVINN_6_ORION1 | TRANSMISSION_INDUCED | 39
2022 | summer | ARVINN_6_ORION2 | TRANSMISSION_INDUCED | 26
2022 | summer | ASTORA_2_SOLAR1 | TRANSMISSION_INDUCED | 400
2022 | summer | ASTORA_2_SOLAR2 | PLANT_MAINTENANCE | 0
2022 | summer | ASTORA_2_SOLAR2 | PLANT_TROUBLE | 47.4375
2022 | summer | ASTORA_2_SOLAR2 | UNIT_TESTING | 300
2022 | summer | ATHOS_5_AP1X2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 154.1667
2022 | summer | ATHOS_5_AP1X2 | AMBIENT_DUE_TO_TEMP | 560
2022 | summer | ATHOS_5_AP1X2 | PLANT_MAINTENANCE | 5633.1
2022 | summer | ATHOS_5_AP1X2 | PLANT_TROUBLE | 249.5
2022 | summer | ATHOS_5_AP2X2 | AMBIENT_DUE_TO_TEMP | 20.5333
2022 | summer | ATHOS_5_AP2X2 | PLANT_MAINTENANCE | 2200
2022 | summer | ATHOS_5_AP2X2 | PLANT_TROUBLE | 0
2022 | summer | ATWEL2_1_SOLAR1 | PLANT_TROUBLE | 0
2022 | summer | ATWELL_1_SOLAR | METERING_TELEMETRY | 20
2022 | summer | ATWELL_1_SOLAR | PLANT_TROUBLE | 176.6667
2022 | summer | AVENAL_6_AVPARK | PLANT_TROUBLE | 1
2022 | summer | AVENAL_6_AVPARK | TRANSMISSION_INDUCED | 60
2022 | summer | AVENAL_6_AVSLR1 | PLANT_TROUBLE | 39.5
2022 | summer | AVENAL_6_AVSLR2 | PLANT_MAINTENANCE | 0
2022 | summer | AVENAL_6_AVSLR2 | PLANT_TROUBLE | 0
2022 | summer | AVENAL_6_SANDDG | METERING_TELEMETRY | 0
2022 | summer | AVENAL_6_SANDDG | PLANT_TROUBLE | 107.6667
2022 | summer | AVENAL_6_SANDDG | TRANSMISSION_INDUCED | 310.3333
2022 | summer | AVENAL_6_SUNCTY | TRANSMISSION_INDUCED | 200
2022 | summer | AVSOLR_2_SOLAR | PLANT_MAINTENANCE | 61.655
2022 | summer | AVSOLR_2_SOLAR | PLANT_TROUBLE | 277.0167
2022 | summer | BALCHS_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 35.9667
2022 | summer | BALCHS_7_UNIT 1 | PLANT_MAINTENANCE | 184.45
2022 | summer | BALCHS_7_UNIT 1 | PLANT_TROUBLE | 46.1
2022 | summer | BALCHS_7_UNIT 1 | TRANSITIONAL_LIMITATION | 4.45
2022 | summer | BALCHS_7_UNIT 1 | TRANSMISSION_INDUCED | 0
2022 | summer | BALCHS_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 145.7083
2022 | summer | BALCHS_7_UNIT 2 | PLANT_TROUBLE | 121.625
2022 | summer | BALCHS_7_UNIT 2 | TRANSITIONAL_LIMITATION | 5.1917
2022 | summer | BALCHS_7_UNIT 3 | AMBIENT_NOT_DUE_TO_TEMP | 153.3967
2022 | summer | BALCHS_7_UNIT 3 | TRANSITIONAL_LIMITATION | 8.3067
2022 | summer | BANKPP_2_NSPIN | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2022 | summer | BANKPP_2_NSPIN | PLANT_MAINTENANCE | 0
2022 | summer | BANKPP_2_NSPIN | TRANSMISSION_INDUCED | 0
2022 | summer | BARRE_6_PEAKER | AMBIENT_DUE_TO_TEMP | 4049.6875
2022 | summer | BARRE_6_PEAKER | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | summer | BARRE_6_PEAKER | PLANT_TROUBLE | 111.626
2022 | summer | BASICE_2_UNITS | AMBIENT_DUE_TO_TEMP | 2491.5167
2022 | summer | BASICE_2_UNITS | PLANT_TROUBLE | 291.5667
2022 | summer | BASICE_2_UNITS | TRANSMISSION_INDUCED | 0
2022 | summer | BCTSYS_5_PWXDYN | TRANSITIONAL_LIMITATION | 310300
2022 | summer | BDGRCK_1_UNITS | AMBIENT_DUE_TO_TEMP | 3180.58
2022 | summer | BDGRCK_1_UNITS | PLANT_TROUBLE | 178.2
2022 | summer | BEARDS_7_UNIT 1 | PLANT_TROUBLE | 59.9917
2022 | summer | BEARMT_1_UNIT | AMBIENT_DUE_TO_TEMP | 3141.3
2022 | summer | BEARMT_1_UNIT | PLANT_TROUBLE | 0
2022 | summer | BEJNLS_5_BV2SCEDYN | PLANT_TROUBLE | 835
2022 | summer | BEJNLS_5_BV2SCEDYN | TRANSMISSION_INDUCED | 970
2022 | summer | BEKWJS_5_BV1SCEDYN | PLANT_TROUBLE | 650
2022 | summer | BEKWJS_5_BV1SCEDYN | TRANSMISSION_INDUCED | 760
2022 | summer | BELDEN_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 41029.602
2022 | summer | BELDEN_7_UNIT 1 | PLANT_TROUBLE | 17.2333
2022 | summer | BELDEN_7_UNIT 1 | TRANSMISSION_INDUCED | 77.35
2022 | summer | BGSKYN_2_AS2SR1 | METERING_TELEMETRY | 360
2022 | summer | BGSKYN_2_AS2SR1 | PLANT_MAINTENANCE | 2410.5167
2022 | summer | BGSKYN_2_AS2SR1 | PLANT_TROUBLE | 7113.3167
2022 | summer | BGSKYN_2_AS2SR1 | UNIT_TESTING | 156
2022 | summer | BGSKYN_2_ASPSR2 | PLANT_MAINTENANCE | 77
2022 | summer | BGSKYN_2_ASPSR2 | PLANT_TROUBLE | 15582.2
2022 | summer | BGSKYN_2_ASPSR2 | UNIT_TESTING | 192.5
2022 | summer | BGSKYN_2_ASSR3A | PLANT_MAINTENANCE | 15
2022 | summer | BGSKYN_2_ASSR3A | PLANT_TROUBLE | 210
2022 | summer | BGSKYN_2_ASSR3A | UNIT_TESTING | 30
2022 | summer | BGSKYN_2_ASSR3B | PLANT_MAINTENANCE | 5
2022 | summer | BGSKYN_2_ASSR3B | PLANT_TROUBLE | 133.3167
2022 | summer | BGSKYN_2_ASSR3B | UNIT_TESTING | 10
2022 | summer | BGSKYN_2_BS3SR3 | METERING_TELEMETRY | 175
2022 | summer | BGSKYN_2_BS3SR3 | PLANT_MAINTENANCE | 35
2022 | summer | BGSKYN_2_BS3SR3 | PLANT_TROUBLE | 10003.9667
2022 | summer | BIGCRK_2_EXESWD | AMBIENT_NOT_DUE_TO_TEMP | 149680.0167
2022 | summer | BIGCRK_2_EXESWD | PLANT_MAINTENANCE | 1100
2022 | summer | BIGCRK_2_EXESWD | PLANT_TROUBLE | 1184.6167
2022 | summer | BIGCRK_2_EXESWD | TRANSMISSION_INDUCED | 852.5
2022 | summer | BIGSKY_2_AS2BT1 | METERING_TELEMETRY | 0
2022 | summer | BIGSKY_2_AS2BT1 | NEW_GENERATOR_TEST_ENERGY | 1856.95
2022 | summer | BIGSKY_2_AS2BT1 | PLANT_TROUBLE | 1058.6333
2022 | summer | BIGSKY_2_AS2BT1 | UNIT_TESTING | 0
2022 | summer | BIGSKY_2_ASLBT2 | NEW_GENERATOR_TEST_ENERGY | 850
2022 | summer | BIGSKY_2_ASLBT2 | PLANT_MAINTENANCE | 0
2022 | summer | BIGSKY_2_ASLBT2 | PLANT_TROUBLE | 3301.95
2022 | summer | BIGSKY_2_ASLBT2 | TRANSMISSION_INDUCED | 0
2022 | summer | BIGSKY_2_ASLBT2 | UNIT_TESTING | 50
2022 | summer | BIGSKY_2_BSKSR6 | PLANT_MAINTENANCE | 13.6
2022 | summer | BIGSKY_2_BSKSR6 | PLANT_TROUBLE | 17
2022 | summer | BIGSKY_2_BSKSR7 | PLANT_MAINTENANCE | 58.25
2022 | summer | BIGSKY_2_BSKSR7 | PLANT_TROUBLE | 28.3667
2022 | summer | BIGSKY_2_BSKSR8 | PLANT_MAINTENANCE | 14
2022 | summer | BIGSKY_2_BSKSR8 | PLANT_TROUBLE | 104.6917
2022 | summer | BIGSKY_2_SOLAR1 | METERING_TELEMETRY | 60
2022 | summer | BIGSKY_2_SOLAR1 | PLANT_MAINTENANCE | 29.9667
2022 | summer | BIGSKY_2_SOLAR1 | PLANT_TROUBLE | 1048.8333
2022 | summer | BIGSKY_2_SOLAR2 | PLANT_TROUBLE | 673.25
2022 | summer | BIGSKY_2_SOLAR3 | PLANT_TROUBLE | 284.3333
2022 | summer | BIGSKY_2_SOLAR4 | PLANT_TROUBLE | 427.3333
2022 | summer | BIGSKY_2_SOLAR5 | PLANT_TROUBLE | 3.8333
2022 | summer | BIGSKY_2_SOLAR6 | PLANT_MAINTENANCE | 122.25
2022 | summer | BIGSKY_2_SOLAR6 | PLANT_TROUBLE | 4951.5333
2022 | summer | BIGSKY_2_SOLAR7 | PLANT_TROUBLE | 443.3
2022 | summer | BIOMAS_1_UNIT 1 | PLANT_TROUBLE | 1088.8333
2022 | summer | BISHOP_1_ALAMO | AMBIENT_NOT_DUE_TO_TEMP | 6538.95
2022 | summer | BISHOP_1_ALAMO | PLANT_TROUBLE | 9.659
2022 | summer | BISHOP_1_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 5984
2022 | summer | BISHOP_1_UNITS | METERING_TELEMETRY | 0
2022 | summer | BKRFLD_2_SOLAR1 | PLANT_TROUBLE | 504.022
2022 | summer | BLACK_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 573.79
2022 | summer | BLACK_7_UNIT 1 | PLANT_TROUBLE | 43.9167
2022 | summer | BLACK_7_UNIT 1 | TRANSMISSION_INDUCED | 985.5167
2022 | summer | BLACK_7_UNIT 2 | AMBIENT_DUE_TO_TEMP | 0
2022 | summer | BLACK_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 538.65
2022 | summer | BLACK_7_UNIT 2 | PLANT_TROUBLE | 473.4367
2022 | summer | BLACK_7_UNIT 2 | TRANSMISSION_INDUCED | 1320.9583
2022 | summer | BLAST_1_WIND | PLANT_TROUBLE | 125
2022 | summer | BLCKBT_2_STONEY | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1692.7033
2022 | summer | BLCKBT_2_STONEY | AMBIENT_NOT_DUE_TO_TEMP | 155
2022 | summer | BLCKBT_2_STONEY | PLANT_TROUBLE | 31
2022 | summer | BLCKBT_2_STONEY | TRANSMISSION_INDUCED | 0
2022 | summer | BLCKWL_6_SOLAR1 | PLANT_TROUBLE | 0
2022 | summer | BLCKWL_6_SOLAR1 | TRANSMISSION_INDUCED | 382.4
2022 | summer | BLKCRK_2_GMCBT1 | METERING_TELEMETRY | 0
2022 | summer | BLKCRK_2_GMCBT1 | PLANT_MAINTENANCE | 7219.1078
2022 | summer | BLKCRK_2_GMCBT1 | PLANT_TROUBLE | 6025.4167
2022 | summer | BLKCRK_2_GMCBT1 | TRANSMISSION_INDUCED | 0
2022 | summer | BLKCRK_2_GMCBT1 | UNIT_TESTING | 1380
2022 | summer | BLKCRK_2_SOLAR1 | PLANT_MAINTENANCE | 228.6667
2022 | summer | BLKCRK_2_SOLAR1 | TRANSMISSION_INDUCED | 0
2022 | summer | BLKDIA_2_BDEBT1 | PLANT_MAINTENANCE | 0
2022 | summer | BLKDIA_2_BDEBT1 | PLANT_TROUBLE | 44542.65
2022 | summer | BLM W_2_COSBT1 | PLANT_MAINTENANCE | 4493.725
2022 | summer | BLM W_2_COSBT1 | PLANT_TROUBLE | 4754.356
2022 | summer | BLM W_2_COSBT1 | UNIT_TESTING | 90
2022 | summer | BLM_2_UNITS | PLANT_MAINTENANCE | 5250
2022 | summer | BLM_2_UNITS | PLANT_TROUBLE | 100
2022 | summer | BLM_2_UNITS | TRANSMISSION_INDUCED | 83.8333
2022 | summer | BLYTHE_1_SOLAR1 | PLANT_TROUBLE | 407.9667
2022 | summer | BLYTHE_1_SOLAR1 | TRANSMISSION_INDUCED | 17.15
2022 | summer | BLYTHE_1_SOLAR2 | PLANT_TROUBLE | 113.6667
2022 | summer | BNNIEN_7_ALTAPH | AMBIENT_NOT_DUE_TO_TEMP | 115.2
2022 | summer | BNNIEN_7_ALTAPH | PLANT_MAINTENANCE | 0
2022 | summer | BNNIEN_7_ALTAPH | PLANT_TROUBLE | 78.5833
2022 | summer | BNNIEN_7_ALTAPH | TRANSMISSION_INDUCED | 0
2022 | summer | BOGUE_1_UNITA1 | AMBIENT_DUE_TO_TEMP | 792.527
2022 | summer | BOGUE_1_UNITA1 | PLANT_MAINTENANCE | 0
2022 | summer | BOGUE_1_UNITA1 | PLANT_TROUBLE | 534.7843
2022 | summer | BORDER_6_UNITA1 | AMBIENT_DUE_TO_TEMP | 353.5093
2022 | summer | BORDER_6_UNITA1 | PLANT_MAINTENANCE | 508.2292
2022 | summer | BORDER_6_UNITA1 | PLANT_TROUBLE | 576.9407
2022 | summer | BOWMN_6_HYDRO | PLANT_MAINTENANCE | 226.8
2022 | summer | BRDSLD_2_HIWIND | PLANT_MAINTENANCE | 28837.23
2022 | summer | BRDSLD_2_HIWIND | PLANT_TROUBLE | 0
2022 | summer | BRDSLD_2_HIWIND | TRANSMISSION_INDUCED | 0
2022 | summer | BRDSLD_2_MTZUM2 | PLANT_MAINTENANCE | 1947.5
2022 | summer | BRDSLD_2_MTZUM2 | PLANT_TROUBLE | 140.78
2022 | summer | BRDSLD_2_MTZUM2 | TRANSMISSION_INDUCED | 0
2022 | summer | BRDSLD_2_MTZUMA | AMBIENT_DUE_TO_TEMP | 143.5533
2022 | summer | BRDSLD_2_MTZUMA | PLANT_MAINTENANCE | 0
2022 | summer | BRDSLD_2_MTZUMA | TRANSMISSION_INDUCED | 0
2022 | summer | BRDSLD_2_SHILO1 | PLANT_TROUBLE | 609.4
2022 | summer | BRDSLD_2_SHILO1 | TRANSMISSION_INDUCED | 0
2022 | summer | BRDSLD_2_SHILO2 | AMBIENT_DUE_TO_TEMP | 799.2667
2022 | summer | BRDSLD_2_SHILO2 | METERING_TELEMETRY | 33.5
2022 | summer | BRDSLD_2_SHILO2 | PLANT_MAINTENANCE | 5556.8667
2022 | summer | BRDSLD_2_SHILO2 | PLANT_TROUBLE | 585.7
2022 | summer | BRDSLD_2_SHILO2 | TRANSMISSION_INDUCED | 0
2022 | summer | BRDSLD_2_SHILO2 | UNIT_TESTING | 0
2022 | summer | BRDSLD_2_SHLO3A | AMBIENT_DUE_TO_TEMP | 264.5217
2022 | summer | BRDSLD_2_SHLO3A | AMBIENT_NOT_DUE_TO_TEMP | 410
2022 | summer | BRDSLD_2_SHLO3A | PLANT_MAINTENANCE | 1102.7292
2022 | summer | BRDSLD_2_SHLO3A | PLANT_TROUBLE | 0
2022 | summer | BRDSLD_2_SHLO3A | TRANSMISSION_INDUCED | 0
2022 | summer | BRDSLD_2_SHLO3B | AMBIENT_DUE_TO_TEMP | 311.9342
2022 | summer | BRDSLD_2_SHLO3B | PLANT_MAINTENANCE | 1951.1392
2022 | summer | BRDSLD_2_SHLO3B | TRANSMISSION_INDUCED | 0
2022 | summer | BREGGO_6_DEGRSL | TRANSMISSION_INDUCED | 220.5
2022 | summer | BREGGO_6_SOLAR | PLANT_TROUBLE | 1.5
2022 | summer | BREGGO_6_SOLAR | TRANSMISSION_INDUCED | 1035.6667
2022 | summer | BRODIE_2_WIND | PLANT_MAINTENANCE | 1313.85
2022 | summer | BUCKBL_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 370.2225
2022 | summer | BUCKBL_2_PL1X3 | PLANT_TROUBLE | 6285.1408
2022 | summer | BUCKBL_2_PL1X3 | TRANSMISSION_INDUCED | 0
2022 | summer | BUCKCK_2_HYDRO | TRANSMISSION_INDUCED | 8.316
2022 | summer | BUCKCK_7_OAKFLT | PLANT_MAINTENANCE | 71.5
2022 | summer | BUCKCK_7_OAKFLT | TRANSMISSION_INDUCED | 923
2022 | summer | BUCKCK_7_PL1X2 | AMBIENT_DUE_TO_TEMP | 47.2452
2022 | summer | BUCKCK_7_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 494.24
2022 | summer | BUCKCK_7_PL1X2 | PLANT_TROUBLE | 353
2022 | summer | BUCKCK_7_PL1X2 | TRANSMISSION_INDUCED | 330
2022 | summer | BUCKCK_7_PL1X2 | UNIT_TESTING | 0
2022 | summer | BUCKWD_1_QF | PLANT_MAINTENANCE | 1211.45
2022 | summer | BUCKWD_1_QF | PLANT_TROUBLE | 10.5
2022 | summer | BUCKWD_7_WINTCV | PLANT_TROUBLE | 499.29
2022 | summer | BURNYF_2_UNIT 1 | PLANT_MAINTENANCE | 141.94
2022 | summer | BURNYF_2_UNIT 1 | PLANT_TROUBLE | 489.25
2022 | summer | BUTTVL_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 115.4667
2022 | summer | BUTTVL_7_UNIT 1 | PLANT_TROUBLE | 402.8683
2022 | summer | BUTTVL_7_UNIT 1 | TRANSMISSION_INDUCED | 1946.5
2022 | summer | CABALO_2_M2BSR1 | PLANT_TROUBLE | 1831
2022 | summer | CABALO_2_M2WSR2 | PLANT_MAINTENANCE | 194.3333
2022 | summer | CABALO_2_M2WSR2 | PLANT_TROUBLE | 5407.024
2022 | summer | CALFTN_2_CFSBT1 | METERING_TELEMETRY | 0
2022 | summer | CALFTN_2_CFSBT1 | PLANT_TROUBLE | 591
2022 | summer | CALFTS_2_CFSSR1 | AMBIENT_NOT_DUE_TO_TEMP | 189.5667
2022 | summer | CALFTS_2_CFSSR1 | METERING_TELEMETRY | 297.5
2022 | summer | CALFTS_2_CFSSR1 | PLANT_TROUBLE | 1260.4667
2022 | summer | CALGEN_1_UNITS | PLANT_MAINTENANCE | 400
2022 | summer | CALGEN_1_UNITS | PLANT_TROUBLE | 484
2022 | summer | CALGEN_1_UNITS | TRANSMISSION_INDUCED | 0
2022 | summer | CALPIN_1_AGNEW | AMBIENT_DUE_TO_TEMP | 56.194
2022 | summer | CALPIN_1_AGNEW | PLANT_TROUBLE | 1716.3067
2022 | summer | CALPIN_1_AGNEW | TRANSITIONAL_LIMITATION | 57.12
2022 | summer | CALPIN_1_AGNEW | UNIT_TESTING | 7.14
2022 | summer | CALPSS_6_SOLAR1 | TRANSMISSION_INDUCED | 497.5
2022 | summer | CAMCHE_1_PL1X3 | AMBIENT_NOT_DUE_TO_TEMP | 7119.07
2022 | summer | CAMLOT_2_SOLAR1 | PLANT_MAINTENANCE | 0
2022 | summer | CAMLOT_2_SOLAR1 | PLANT_TROUBLE | 1013.85
2022 | summer | CAMLOT_2_SOLAR2 | AMBIENT_NOT_DUE_TO_TEMP | 225
2022 | summer | CAMLOT_2_SOLAR2 | PLANT_TROUBLE | 98.8773
2022 | summer | CAMPFW_7_FARWST | PLANT_TROUBLE | 108.8
2022 | summer | CAMPFW_7_FARWST | TRANSMISSION_INDUCED | 115.6
2022 | summer | CAPWD_1_QF | AMBIENT_DUE_TO_TEMP | 2834.75
2022 | summer | CAPWD_1_QF | PLANT_TROUBLE | 2980.25
2022 | summer | CARBOU_7_PL2X3 | AMBIENT_NOT_DUE_TO_TEMP | 15937.8867
2022 | summer | CARBOU_7_PL2X3 | PLANT_MAINTENANCE | 2.45
2022 | summer | CARBOU_7_PL2X3 | PLANT_TROUBLE | 116.25
2022 | summer | CARBOU_7_PL2X3 | TRANSMISSION_INDUCED | 3325.65
2022 | summer | CARBOU_7_PL4X5 | AMBIENT_NOT_DUE_TO_TEMP | 19959.718
2022 | summer | CARBOU_7_PL4X5 | TRANSMISSION_INDUCED | 1478
2022 | summer | CARBOU_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 3840
2022 | summer | CARBOU_7_UNIT 1 | PLANT_MAINTENANCE | 360
2022 | summer | CARLS1_2_CARCT1 | AMBIENT_DUE_TO_TEMP | 40115.4917
2022 | summer | CARLS1_2_CARCT1 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | summer | CARLS1_2_CARCT1 | PLANT_MAINTENANCE | 0
2022 | summer | CARLS1_2_CARCT1 | PLANT_TROUBLE | 4561.8842
2022 | summer | CARLS1_2_CARCT1 | SHORT_TERM_USE_LIMIT_REACHED | 14763.3
2022 | summer | CARLS2_1_CARCT1 | AMBIENT_DUE_TO_TEMP | 1683.56
2022 | summer | CARLS2_1_CARCT1 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | summer | CARLS2_1_CARCT1 | PLANT_MAINTENANCE | 0
2022 | summer | CARLS2_1_CARCT1 | PLANT_TROUBLE | 447.2042
2022 | summer | CATLNA_2_SOLAR | PLANT_TROUBLE | 20
2022 | summer | CATLNA_2_SOLAR2 | PLANT_MAINTENANCE | 27
2022 | summer | CATLNA_2_SOLAR2 | UNIT_TESTING | 0
2022 | summer | CAVLSR_2_BSOLAR | PLANT_TROUBLE | 73.3333
2022 | summer | CAVLSR_2_RSOLAR | METERING_TELEMETRY | 0
2022 | summer | CAVLSR_2_RSOLAR | PLANT_MAINTENANCE | 489.16
2022 | summer | CAVLSR_2_RSOLAR | PLANT_TROUBLE | 579.9833
2022 | summer | CAYTNO_2_VASCO | PLANT_MAINTENANCE | 11.4817
2022 | summer | CAYTNO_2_VASCO | PLANT_TROUBLE | 416.7592
2022 | summer | CENT40_1_C40SR1 | PLANT_TROUBLE | 0
2022 | summer | CENTER_2_RHONDO | AMBIENT_NOT_DUE_TO_TEMP | 1310.65
2022 | summer | CENTER_6_PEAKER | AMBIENT_DUE_TO_TEMP | 524.93
2022 | summer | CENTER_6_PEAKER | ENVIRONMENTAL_RESTRICTIONS | 11.825
2022 | summer | CENTER_6_PEAKER | PLANT_MAINTENANCE | 0
2022 | summer | CENTER_6_PEAKER | PLANT_TROUBLE | 2.57
2022 | summer | CENTRY_6_PL1X4 | AMBIENT_DUE_TO_TEMP | 1217
2022 | summer | CENTRY_6_PL1X4 | METERING_TELEMETRY | 0
2022 | summer | CENTRY_6_PL1X4 | PLANT_TROUBLE | 3145.8333
2022 | summer | CENTRY_6_PL1X4 | TRANSMISSION_INDUCED | 330
2022 | summer | CENTRY_6_PL1X4 | UNIT_TESTING | 4
2022 | summer | CHALK_1_UNIT | AMBIENT_DUE_TO_TEMP | 2680.76
2022 | summer | CHALK_1_UNIT | PLANT_MAINTENANCE | 243.35
2022 | summer | CHALK_1_UNIT | PLANT_TROUBLE | 477.2733
2022 | summer | CHALK_1_UNIT | TRANSMISSION_INDUCED | 230.505
2022 | summer | CHARMN_2_PGONG1 | PLANT_TROUBLE | 702.0733
2022 | summer | CHEVCY_1_UNIT | PLANT_MAINTENANCE | 0
2022 | summer | CHEVCY_1_UNIT | PLANT_TROUBLE | 0
2022 | summer | CHEVMN_2_UNITS | PLANT_MAINTENANCE | 35026.035
2022 | summer | CHICPK_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 8608.3
2022 | summer | CHICPK_7_UNIT 1 | TRANSMISSION_INDUCED | 0
2022 | summer | CHILLS_1_SYCENG | PLANT_MAINTENANCE | 0
2022 | summer | CHILLS_1_SYCENG | PLANT_TROUBLE | 61.3875
2022 | summer | CHILLS_7_UNITA1 | PLANT_TROUBLE | 80.25
2022 | summer | CHINO_2_APEBT1 | PLANT_MAINTENANCE | 0
2022 | summer | CHINO_2_APEBT1 | PLANT_TROUBLE | 656.4767
2022 | summer | CHINO_2_APEBT1 | UNIT_TESTING | 100
2022 | summer | CHINO_6_CIMGEN | PLANT_TROUBLE | 0
2022 | summer | CHWCHL_1_BIOMAS | PLANT_MAINTENANCE | 97.2
2022 | summer | CHWCHL_1_BIOMAS | PLANT_TROUBLE | 1731.4833
2022 | summer | CHWCHL_1_UNIT | AMBIENT_DUE_TO_TEMP | 136.2167
2022 | summer | CHWCHL_1_UNIT | PLANT_TROUBLE | 916.9
2022 | summer | CHWCHL_1_UNIT | TRANSMISSION_INDUCED | 598.3
2022 | summer | CLINESCO_3_PVDYN | PLANT_TROUBLE | 1282.0747
2022 | summer | CLINESCO_3_PVDYN | TRANSMISSION_INDUCED | 1299.908
2022 | summer | CLINESCO_3_WBDYN | PLANT_TROUBLE | 1920.134
2022 | summer | CLINESCO_3_WBDYN | TRANSMISSION_INDUCED | 1804.2
2022 | summer | CLOVDL_1_SOLAR | PLANT_TROUBLE | 1147.5
2022 | summer | CLOVER_2_UNIT | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 183.15
2022 | summer | CLOVER_2_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 17.622
2022 | summer | COCOPP_2_CTG1 | AMBIENT_DUE_TO_TEMP | 7895.8273
2022 | summer | COCOPP_2_CTG1 | PLANT_TROUBLE | 0
2022 | summer | COCOPP_2_CTG2 | AMBIENT_DUE_TO_TEMP | 7338.6555
2022 | summer | COCOPP_2_CTG2 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 962.24
2022 | summer | COCOPP_2_CTG3 | AMBIENT_DUE_TO_TEMP | 12616.235
2022 | summer | COCOPP_2_CTG3 | PLANT_MAINTENANCE | 0
2022 | summer | COCOPP_2_CTG3 | PLANT_TROUBLE | 0
2022 | summer | COCOPP_2_CTG4 | AMBIENT_DUE_TO_TEMP | 7941.73
2022 | summer | COCOPP_2_CTG4 | PLANT_TROUBLE | 1915.63
2022 | summer | COGNAT_1_UNIT | PLANT_TROUBLE | 886.5
2022 | summer | COLEMN_2_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 3044.1667
2022 | summer | COLEMN_2_UNIT | PLANT_MAINTENANCE | 1310.8333
2022 | summer | COLGAT_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 17154.8667
2022 | summer | COLGAT_7_UNIT 1 | PLANT_TROUBLE | 738.6667
2022 | summer | COLGAT_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 14902.9833
2022 | summer | COLGAT_7_UNIT 2 | TRANSMISSION_INDUCED | 526.5
2022 | summer | COLGNS_2_CNSSR1 | PLANT_MAINTENANCE | 1165.3667
2022 | summer | COLGNS_2_CNSSR1 | PLANT_TROUBLE | 0
2022 | summer | COLGNS_2_CNSSR1 | TRANSMISSION_INDUCED | 374
2022 | summer | COLPIN_6_COLLNS | PLANT_MAINTENANCE | 49.5
2022 | summer | COLPIN_6_COLLNS | TRANSMISSION_INDUCED | 166.43
2022 | summer | COLTON_6_AGUAM1 | AMBIENT_DUE_TO_TEMP | 1227.1603
2022 | summer | COLUSA_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 37562.6932
2022 | summer | COLUSA_2_PL1X3 | METERING_TELEMETRY | 8982.2
2022 | summer | COLUSA_2_PL1X3 | PLANT_TROUBLE | 11760.3283
2022 | summer | COLUSA_2_PL1X3 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2022 | summer | COLVIL_7_PL1X2 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | summer | COLVIL_7_PL1X2 | PLANT_MAINTENANCE | 252
2022 | summer | COLVIL_7_PL1X2 | PLANT_TROUBLE | 602.2857
2022 | summer | CONTRL_1_CASAD1 | METERING_TELEMETRY | 0
2022 | summer | CONTRL_1_CASAD1 | PLANT_TROUBLE | 181.1917
2022 | summer | CONTRL_1_CASAD2 | PLANT_TROUBLE | 189.115
2022 | summer | CONTRL_1_CASAD3 | METERING_TELEMETRY | 34.4
2022 | summer | CONTRL_1_CASAD3 | PLANT_TROUBLE | 40.1867
2022 | summer | CONTRL_1_LUNDY | AMBIENT_NOT_DUE_TO_TEMP | 1284.025
2022 | summer | CONTRL_1_LUNDY | PLANT_TROUBLE | 29.52
2022 | summer | CONTRL_1_LUNDY | TRANSMISSION_INDUCED | 14.975
2022 | summer | CONTRL_1_OXBOW | AMBIENT_DUE_TO_TEMP | 2281.6167
2022 | summer | CONTRL_1_OXBOW | AMBIENT_NOT_DUE_TO_TEMP | 45.2083
2022 | summer | CONTRL_1_OXBOW | METERING_TELEMETRY | 0
2022 | summer | CONTRL_1_OXBOW | PLANT_TROUBLE | 117.8
2022 | summer | CONTRL_1_OXBOW | TRANSMISSION_INDUCED | 3186.2667
2022 | summer | CONTRL_1_OXBOW | UNIT_SUPPORTING_STARTUP | 68.4
2022 | summer | CONTRL_1_POOLE | AMBIENT_NOT_DUE_TO_TEMP | 3865.9133
2022 | summer | CONTRL_1_POOLE | METERING_TELEMETRY | 0
2022 | summer | CONTRL_1_POOLE | TRANSMISSION_INDUCED | 151.48
2022 | summer | CONTRL_1_RUSHCK | AMBIENT_NOT_DUE_TO_TEMP | 2221.62
2022 | summer | CONTRL_1_RUSHCK | TRANSMISSION_INDUCED | 0.1
2022 | summer | COPMT2_2_SOLAR2 | METERING_TELEMETRY | 155
2022 | summer | COPMTN_2_CM10 | TRANSMISSION_INDUCED | 10
2022 | summer | COPMTN_2_SOLAR1 | TRANSMISSION_INDUCED | 48
2022 | summer | CORCAN_1_SOLAR1 | TRANSMISSION_INDUCED | 19.84
2022 | summer | CORONS_6_CLRWTR | PLANT_MAINTENANCE | 49
2022 | summer | CORONS_6_CLRWTR | PLANT_TROUBLE | 96.4127
2022 | summer | CORRAL_6_SJOAQN | PLANT_MAINTENANCE | 308.35
2022 | summer | CORRAL_6_SJOAQN | PLANT_TROUBLE | 40.75
2022 | summer | CORRAL_6_SJOAQN | TRANSMISSION_INDUCED | 970.2833
2022 | summer | COVERD_2_HCKHY1 | ENVIRONMENTAL_RESTRICTIONS | 82.68
2022 | summer | COVERD_2_HCKHY1 | PLANT_TROUBLE | 455.8883
2022 | summer | COVERD_2_HCKHY1 | TRANSMISSION_INDUCED | 89.57
2022 | summer | COVERD_2_MCKHY1 | AMBIENT_NOT_DUE_TO_TEMP | 2046.2
2022 | summer | COVERD_2_QFUNTS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 62.8833
2022 | summer | COVERD_2_QFUNTS | TRANSMISSION_INDUCED | 71.5
2022 | summer | COVERD_2_RCKHY1 | AMBIENT_NOT_DUE_TO_TEMP | 68
2022 | summer | COVERD_2_RCKHY1 | TRANSMISSION_INDUCED | 32
2022 | summer | COWCRK_2_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 507.4
2022 | summer | CPVERD_2_SOLAR | PLANT_MAINTENANCE | 158
2022 | summer | CPVERD_2_SOLAR | PLANT_TROUBLE | 104.25
2022 | summer | CRELMN_6_RAMON1 | PLANT_MAINTENANCE | 6
2022 | summer | CRELMN_6_RAMON1 | PLANT_TROUBLE | 5.1
2022 | summer | CRELMN_6_RAMON2 | PLANT_MAINTENANCE | 15
2022 | summer | CRELMN_6_RAMON2 | PLANT_TROUBLE | 12.8333
2022 | summer | CRELMN_6_RAMSR3 | PLANT_TROUBLE | 3304.8
2022 | summer | CRESTA_7_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 19953.7708
2022 | summer | CRESTA_7_PL1X2 | PLANT_TROUBLE | 61
2022 | summer | CRESTA_7_PL1X2 | TRANSMISSION_INDUCED | 0
2022 | summer | CRIMSN_2_CRMBT1 | METERING_TELEMETRY | 0
2022 | summer | CRIMSN_2_CRMBT1 | NEW_GENERATOR_TEST_ENERGY | 600
2022 | summer | CRIMSN_2_CRMBT1 | PLANT_MAINTENANCE | 0
2022 | summer | CRIMSN_2_CRMBT1 | PLANT_TROUBLE | 2658.184
2022 | summer | CRIMSN_2_CRMBT1 | UNIT_TESTING | 1800
2022 | summer | CRIMSN_2_CRMBT2 | METERING_TELEMETRY | 150
2022 | summer | CRIMSN_2_CRMBT2 | NEW_GENERATOR_TEST_ENERGY | 0
2022 | summer | CRIMSN_2_CRMBT2 | PLANT_MAINTENANCE | 0
2022 | summer | CRIMSN_2_CRMBT2 | PLANT_TROUBLE | 0
2022 | summer | CRNEVL_6_CRNVA | AMBIENT_NOT_DUE_TO_TEMP | 27
2022 | summer | CRNEVL_6_CRNVA | PLANT_TROUBLE | 504
2022 | summer | CRNEVL_6_CRNVA | TRANSMISSION_INDUCED | 0
2022 | summer | CRNEVL_6_SJQN 2 | PLANT_MAINTENANCE | 2416
2022 | summer | CRNEVL_6_SJQN 2 | TRANSMISSION_INDUCED | 0
2022 | summer | CROKET_7_UNIT | AMBIENT_DUE_TO_TEMP | 591.3
2022 | summer | CROKET_7_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 19.7333
2022 | summer | CROKET_7_UNIT | PLANT_TROUBLE | 1052
2022 | summer | CROKET_7_UNIT | TRANSMISSION_INDUCED | 0
2022 | summer | CRSTWD_6_KUMYAY | PLANT_MAINTENANCE | 31.5333
2022 | summer | CRSTWD_6_KUMYAY | PLANT_TROUBLE | 1602.7333
2022 | summer | CRSTWD_6_KUMYAY | TRANSMISSION_INDUCED | 250
2022 | summer | CRWCKS_1_SOLAR1 | METERING_TELEMETRY | 380
2022 | summer | CRWCKS_1_SOLAR1 | PLANT_TROUBLE | 2640
2022 | summer | CRWCKS_1_SOLAR1 | TRANSMISSION_INDUCED | 0
2022 | summer | CSCCOG_1_UNIT 1 | PLANT_MAINTENANCE | 122.5
2022 | summer | CSCCOG_1_UNIT 1 | PLANT_TROUBLE | 2607.5
2022 | summer | CSCGNR_1_UNIT 1 | PLANT_MAINTENANCE | 59.8125
2022 | summer | CSCGNR_1_UNIT 1 | PLANT_TROUBLE | 28.285
2022 | summer | CSCGNR_1_UNIT 2 | PLANT_MAINTENANCE | 410.374
2022 | summer | CSCGNR_1_UNIT 2 | PLANT_TROUBLE | 2096.2125
2022 | summer | CSLR4S_2_SOLAR | METERING_TELEMETRY | 130
2022 | summer | CSLR4S_2_SOLAR | PLANT_TROUBLE | 350
2022 | summer | CSTRVL_7_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 59.15
2022 | summer | CSTRVL_7_PL1X2 | TRANSMISSION_INDUCED | 88
2022 | summer | CSTRVL_7_QFUNTS | TRANSMISSION_INDUCED | 10
2022 | summer | CUYAMS_6_CUYSR1 | PLANT_TROUBLE | 58
2022 | summer | CUYAMS_6_CUYSR1 | TRANSMISSION_INDUCED | 341.3333
2022 | summer | DAIRLD_1_CR1BM1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 253.05
2022 | summer | DAIRLD_1_CR1BM1 | PLANT_TROUBLE | 22.7
2022 | summer | DEADCK_1_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 1473.92
2022 | summer | DEERCR_6_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 440.6667
2022 | summer | DEERCR_6_UNIT 1 | PLANT_TROUBLE | 37.45
2022 | summer | DELSUR_6_CREST | METERING_TELEMETRY | 287.5
2022 | summer | DELSUR_6_CREST | PLANT_TROUBLE | 3996.875
2022 | summer | DELSUR_6_DRYFRB | METERING_TELEMETRY | 5
2022 | summer | DELSUR_6_DRYFRB | PLANT_MAINTENANCE | 3.7333
2022 | summer | DELSUR_6_DRYFRB | PLANT_TROUBLE | 54.6333
2022 | summer | DELSUR_6_SOLAR1 | METERING_TELEMETRY | 80
2022 | summer | DELSUR_6_SOLAR1 | PLANT_MAINTENANCE | 1
2022 | summer | DELSUR_6_SOLAR1 | PLANT_TROUBLE | 912.2917
2022 | summer | DELSUR_6_SOLAR1 | TRANSMISSION_INDUCED | 18
2022 | summer | DELTA_2_PL1X4 | AMBIENT_DUE_TO_TEMP | 36005.1667
2022 | summer | DELTA_2_PL1X4 | PLANT_TROUBLE | 21809.2917
2022 | summer | DELTA_2_PL1X4 | TRANSITIONAL_LIMITATION | 573
2022 | summer | DEVERS_1_SOLAR1 | METERING_TELEMETRY | 120
2022 | summer | DEVERS_1_SOLAR1 | PLANT_TROUBLE | 60
2022 | summer | DEVERS_1_SOLAR2 | METERING_TELEMETRY | 65.7
2022 | summer | DEVERS_1_SOLAR2 | PLANT_TROUBLE | 0
2022 | summer | DEXZEL_1_UNIT | PLANT_MAINTENANCE | 5496.75
2022 | summer | DEXZEL_1_UNIT | PLANT_TROUBLE | 7509.5
2022 | summer | DISCOV_1_CHEVRN | PLANT_MAINTENANCE | 316.3333
2022 | summer | DISCOV_1_CHEVRN | PLANT_TROUBLE | 759.3
2022 | summer | DIXNLD_1_LNDFL | METERING_TELEMETRY | 0
2022 | summer | DIXNLD_1_LNDFL | PLANT_TROUBLE | 8
2022 | summer | DONNLS_7_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | summer | DONNLS_7_UNIT | TRANSMISSION_INDUCED | 1412.5
2022 | summer | DOSMGO_2_NSPIN | TRANSMISSION_INDUCED | 2353.2
2022 | summer | DOUBLC_1_UNITS | AMBIENT_DUE_TO_TEMP | 2112.5
2022 | summer | DOUBLC_1_UNITS | PLANT_MAINTENANCE | 0
2022 | summer | DOUBLC_1_UNITS | PLANT_TROUBLE | 61
2022 | summer | DOUBLC_1_UNITS | RTU_RIG | 0
2022 | summer | DRACKR_2_D4SR4B | PLANT_MAINTENANCE | 0
2022 | summer | DRACKR_2_D4SR4B | PLANT_TROUBLE | 331.2917
2022 | summer | DRACKR_2_D4SR4B | TRANSMISSION_INDUCED | 0
2022 | summer | DRACKR_2_DS3SR3 | METERING_TELEMETRY | 0
2022 | summer | DRACKR_2_DS3SR3 | PLANT_MAINTENANCE | 61.0307
2022 | summer | DRACKR_2_DS3SR3 | PLANT_TROUBLE | 10.2617
2022 | summer | DRACKR_2_DS3SR3 | TRANSMISSION_INDUCED | 0
2022 | summer | DRACKR_2_DS4SR4 | PLANT_MAINTENANCE | 93.75
2022 | summer | DRACKR_2_DS4SR4 | PLANT_TROUBLE | 202.7843
2022 | summer | DRACKR_2_DS4SR4 | TRANSMISSION_INDUCED | 0
2022 | summer | DRACKR_2_DS4SR4 | UNIT_TESTING | 0
2022 | summer | DRACKR_2_DSUBT1 | METERING_TELEMETRY | 0
2022 | summer | DRACKR_2_DSUBT1 | PLANT_MAINTENANCE | 94.5
2022 | summer | DRACKR_2_DSUBT1 | PLANT_TROUBLE | 11906.3997
2022 | summer | DRACKR_2_DSUBT1 | TRANSMISSION_INDUCED | 0
2022 | summer | DRACKR_2_DSUBT2 | PLANT_MAINTENANCE | 9531.978
2022 | summer | DRACKR_2_DSUBT2 | PLANT_TROUBLE | 1878.7938
2022 | summer | DRACKR_2_DSUBT2 | TRANSMISSION_INDUCED | 0
2022 | summer | DRACKR_2_DSUBT2 | UNIT_TESTING | 920
2022 | summer | DRACKR_2_DSUBT3 | METERING_TELEMETRY | 0
2022 | summer | DRACKR_2_DSUBT3 | PLANT_MAINTENANCE | 2635.3542
2022 | summer | DRACKR_2_DSUBT3 | PLANT_TROUBLE | 4673.7667
2022 | summer | DRACKR_2_DSUBT3 | TRANSMISSION_INDUCED | 0
2022 | summer | DRACKR_2_DSUBT3 | UNIT_TESTING | 345
2022 | summer | DRACKR_2_DSUBT4 | NEW_GENERATOR_TEST_ENERGY | 0
2022 | summer | DRACKR_2_DSUBT4 | PLANT_MAINTENANCE | 0
2022 | summer | DRACKR_2_DSUBT4 | PLANT_TROUBLE | 3179.005
2022 | summer | DRACKR_2_DSUBT4 | TRANSMISSION_INDUCED | 0
2022 | summer | DRACKR_2_SOLAR1 | PLANT_MAINTENANCE | 165
2022 | summer | DRACKR_2_SOLAR1 | PLANT_TROUBLE | 676.7333
2022 | summer | DRACKR_2_SOLAR1 | TRANSMISSION_INDUCED | 0
2022 | summer | DRACKR_2_SOLAR2 | PLANT_MAINTENANCE | 0
2022 | summer | DRACKR_2_SOLAR2 | PLANT_TROUBLE | 0
2022 | summer | DRACKR_2_SOLAR2 | TRANSMISSION_INDUCED | 0
2022 | summer | DREWS_6_PL1X4 | AMBIENT_DUE_TO_TEMP | 1962
2022 | summer | DREWS_6_PL1X4 | ENVIRONMENTAL_RESTRICTIONS | 540
2022 | summer | DREWS_6_PL1X4 | PLANT_TROUBLE | 7143.5
2022 | summer | DREWS_6_PL1X4 | TRANSMISSION_INDUCED | 135
2022 | summer | DREWS_6_PL1X4 | UNIT_TESTING | 29.4
2022 | summer | DRUM_7_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 6006
2022 | summer | DRUM_7_PL3X4 | AMBIENT_NOT_DUE_TO_TEMP | 7809.85
2022 | summer | DRUM_7_PL3X4 | PLANT_TROUBLE | 41.6
2022 | summer | DRUM_7_UNIT 5 | AMBIENT_NOT_DUE_TO_TEMP | 1030.1667
2022 | summer | DRUM_7_UNIT 5 | PLANT_TROUBLE | 23.2
2022 | summer | DSABLA_7_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 73
2022 | summer | DSABLA_7_UNIT | PLANT_TROUBLE | 35.7667
2022 | summer | DSFLWR_2_WS2SR1 | PLANT_TROUBLE | 750
2022 | summer | DSFLWR_2_WS2SR1 | TRANSMISSION_INDUCED | 112.5
2022 | summer | DSRTHV_2_DH1SR1 | PLANT_MAINTENANCE | 0
2022 | summer | DSRTHV_2_DH2BT1 | METERING_TELEMETRY | 0
2022 | summer | DSRTHV_2_DH2BT1 | PLANT_MAINTENANCE | 4588.9988
2022 | summer | DSRTHV_2_DH2BT1 | PLANT_TROUBLE | 1256.925
2022 | summer | DSRTHV_2_DH2BT1 | UNIT_TESTING | 0
2022 | summer | DSRTHV_2_DH2SR2 | METERING_TELEMETRY | 540
2022 | summer | DSRTHV_2_DH2SR2 | PLANT_MAINTENANCE | 0
2022 | summer | DSRTHV_2_DH2SR2 | PLANT_TROUBLE | 1222.9167
2022 | summer | DSRTHV_2_DH2SR2 | UNIT_TESTING | 0
2022 | summer | DSRTSL_2_SOLAR1 | PLANT_MAINTENANCE | 24
2022 | summer | DSRTSL_2_SOLAR1 | PLANT_TROUBLE | 2381.16
2022 | summer | DSRTSN_2_DS2X2 | NEW_GENERATOR_TEST_ENERGY | 0
2022 | summer | DSRTSN_2_DS2X2 | PLANT_MAINTENANCE | 2751.6167
2022 | summer | DSRTSN_2_DS2X2 | PLANT_TROUBLE | 3847.5217
2022 | summer | DSRTSN_2_DS2X2 | UNIT_TESTING | 916.1667
2022 | summer | DSRTSN_2_SOLAR1 | PLANT_TROUBLE | 1809.5967
2022 | summer | DSRTSN_2_SOLAR2 | PLANT_TROUBLE | 25
2022 | summer | DSRTSN_2_SOLAR2 | UNIT_TESTING | 0
2022 | summer | DTCHWD_2_BT3WND | METERING_TELEMETRY | 9
2022 | summer | DTCHWD_2_BT4WND | METERING_TELEMETRY | 13.04
2022 | summer | DUANE_1_PL1X3 | AMBIENT_DUE_TO_TEMP | 7215.4667
2022 | summer | DUANE_1_PL1X3 | METERING_TELEMETRY | 39
2022 | summer | DUANE_1_PL1X3 | PLANT_MAINTENANCE | 6711.4
2022 | summer | DUANE_1_PL1X3 | PLANT_TROUBLE | 2788.2733
2022 | summer | DUANE_1_PL1X3 | UNIT_TESTING | 0
2022 | summer | DURNMESA_3_WBDYN | TRANSMISSION_INDUCED | 911.2
2022 | summer | DUTCH1_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 3404.4
2022 | summer | DUTCH1_7_UNIT 1 | METERING_TELEMETRY | 0
2022 | summer | DUTCH1_7_UNIT 1 | PLANT_TROUBLE | 6.2333
2022 | summer | DUTCH1_7_UNIT 1 | TRANSMISSION_INDUCED | 0
2022 | summer | DUTCH2_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 9033.5
2022 | summer | DUTCH2_7_UNIT 1 | PLANT_TROUBLE | 0
2022 | summer | DUTCH2_7_UNIT 1 | TRANSMISSION_INDUCED | 0
2022 | summer | DVLCYN_1_UNITS | AMBIENT_DUE_TO_TEMP | 0
2022 | summer | DVLCYN_1_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 885.25
2022 | summer | DVLCYN_1_UNITS | OTHER_USE_LIMIT_REACHED | 0
2022 | summer | DVLCYN_1_UNITS | PLANT_MAINTENANCE | 34.4167
2022 | summer | DVLCYN_1_UNITS | PLANT_TROUBLE | 0
2022 | summer | DVLCYN_1_UNITS | SHORT_TERM_USE_LIMIT_REACHED | 406.3333
2022 | summer | DVLCYN_1_UNITS | TRANSMISSION_INDUCED | 75
2022 | summer | DVLCYN_1_UNITS | UNIT_TESTING | 0
2022 | summer | DYERSM_6_DSWWD1 | PLANT_MAINTENANCE | 60
2022 | summer | DYERSM_6_DSWWD1 | TRANSMISSION_INDUCED | 191.8933
2022 | summer | EASTWD_7_UNIT | AMBIENT_DUE_TO_TEMP | 165.6667
2022 | summer | EASTWD_7_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 6008
2022 | summer | EASTWD_7_UNIT | PLANT_TROUBLE | 25392
2022 | summer | EASTWD_7_UNIT | TRANSMISSION_INDUCED | 3449.9
2022 | summer | EDMONS_2_NSPIN | PLANT_TROUBLE | 45900
2022 | summer | EDWARD_2_E21SB1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 3391.3333
2022 | summer | EDWARD_2_E21SB1 | NEW_GENERATOR_TEST_ENERGY | 2070
2022 | summer | EDWARD_2_E21SB1 | PLANT_MAINTENANCE | 166
2022 | summer | EDWARD_2_E21SB1 | PLANT_TROUBLE | 127.4
2022 | summer | EDWARD_2_E23SB1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1091.6
2022 | summer | EDWARD_2_E23SB1 | AMBIENT_NOT_DUE_TO_TEMP | 197.5
2022 | summer | EDWARD_2_E23SB1 | PLANT_MAINTENANCE | 102
2022 | summer | EDWARD_2_E23SB1 | PLANT_TROUBLE | 0
2022 | summer | EDWARD_2_ES2BT3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 4257.2833
2022 | summer | EDWARD_2_ES2BT3 | AMBIENT_NOT_DUE_TO_TEMP | 586.3833
2022 | summer | EDWARD_2_ES2BT3 | PLANT_MAINTENANCE | 151
2022 | summer | EDWARD_2_ES2BT3 | PLANT_TROUBLE | 2168.5
2022 | summer | EEKTMN_6_SOLAR1 | PLANT_TROUBLE | 0
2022 | summer | ELCABO_5_ECWSCEDYN | PLANT_MAINTENANCE | 0
2022 | summer | ELCABO_5_ECWSCEDYN | PLANT_TROUBLE | 216
2022 | summer | ELCABO_5_ECWSCEDYN | TRANSMISSION_INDUCED | 29794.6233
2022 | summer | ELCAJN_6_EB1BT1 | PLANT_TROUBLE | 412.125
2022 | summer | ELCAJN_6_LM6K | AMBIENT_DUE_TO_TEMP | 488.3
2022 | summer | ELCAJN_6_LM6K | PLANT_MAINTENANCE | 0
2022 | summer | ELCAJN_6_LM6K | PLANT_TROUBLE | 3123.0233
2022 | summer | ELCAJN_6_LM6K | UNIT_TESTING | 0
2022 | summer | ELCAJN_6_UNITA1 | METERING_TELEMETRY | 908.4
2022 | summer | ELCAJN_6_UNITA1 | PLANT_MAINTENANCE | 2952.3
2022 | summer | ELCAJN_6_UNITA1 | PLANT_TROUBLE | 1876.5357
2022 | summer | ELDORO_7_UNIT 1 | PLANT_TROUBLE | 165
2022 | summer | ELDORO_7_UNIT 2 | PLANT_TROUBLE | 198.9333
2022 | summer | ELECTR_7_PL1X3 | AMBIENT_NOT_DUE_TO_TEMP | 995.3
2022 | summer | ELECTR_7_PL1X3 | PLANT_TROUBLE | 165.02
2022 | summer | ELECTR_7_PL1X3 | TRANSMISSION_INDUCED | 919.35
2022 | summer | ELKCRK_6_STONYG | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 2205
2022 | summer | ELKCRK_6_STONYG | PLANT_TROUBLE | 6.4517
2022 | summer | ELKCRK_6_STONYG | TRANSMISSION_INDUCED | 1.96
2022 | summer | ELKHIL_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 38827.95
2022 | summer | ELKHIL_2_PL1X3 | PLANT_MAINTENANCE | 2760
2022 | summer | ELKHIL_2_PL1X3 | PLANT_TROUBLE | 17475.4167
2022 | summer | ELKHRN_1_EESX3 | PLANT_TROUBLE | 38580.5
2022 | summer | ELNIDP_6_BIOMAS | PLANT_MAINTENANCE | 105
2022 | summer | ELNIDP_6_BIOMAS | PLANT_TROUBLE | 1578.35
2022 | summer | ELNIDP_6_BIOMAS | TRANSMISSION_INDUCED | 52.5
2022 | summer | ELSEGN_2_UN1011 | AMBIENT_DUE_TO_TEMP | 392.7
2022 | summer | ELSEGN_2_UN1011 | OTHER_USE_LIMIT_REACHED | 1371.5
2022 | summer | ELSEGN_2_UN1011 | PLANT_TROUBLE | 25855.6517
2022 | summer | ELSEGN_2_UN2021 | AMBIENT_DUE_TO_TEMP | 3740.954
2022 | summer | ELSEGN_2_UN2021 | OTHER_USE_LIMIT_REACHED | 4076.1
2022 | summer | ELSEGN_2_UN2021 | PLANT_MAINTENANCE | 0
2022 | summer | ELSEGN_2_UN2021 | PLANT_TROUBLE | 32654.334
2022 | summer | ELSEGN_2_UN2021 | TRANSMISSION_INDUCED | 0
2022 | summer | ELSEGN_2_UN2021 | UNIT_TESTING | 0
2022 | summer | ENERSJ_2_WIND | METERING_TELEMETRY | 0
2022 | summer | ENERSJ_2_WIND | PLANT_MAINTENANCE | 377.5
2022 | summer | ENERSJ_2_WIND | TRANSMISSION_INDUCED | 755
2022 | summer | ENERSJ_5_ESJWD2 | PLANT_MAINTENANCE | 363.58
2022 | summer | ENERSJ_5_ESJWD2 | PLANT_TROUBLE | 675.7
2022 | summer | ENERSJ_5_ESJWD2 | TRANSMISSION_INDUCED | 525
2022 | summer | ESCNDO_6_EB1BT1 | PLANT_TROUBLE | 2271.9083
2022 | summer | ESCNDO_6_EB2BT2 | PLANT_TROUBLE | 2671.925
2022 | summer | ESCNDO_6_EB3BT3 | PLANT_TROUBLE | 2898.0333
2022 | summer | ESCNDO_6_PL1X2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1308.16
2022 | summer | ESCNDO_6_PL1X2 | AMBIENT_DUE_TO_TEMP | 587.76
2022 | summer | ESCNDO_6_PL1X2 | PLANT_MAINTENANCE | 0
2022 | summer | ESCNDO_6_PL1X2 | PLANT_TROUBLE | 64.8058
2022 | summer | ESCNDO_6_UNITB1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 796.416
2022 | summer | ESCNDO_6_UNITB1 | AMBIENT_DUE_TO_TEMP | 181.35
2022 | summer | ESCNDO_6_UNITB1 | PLANT_MAINTENANCE | 745.6127
2022 | summer | ESCNDO_6_UNITB1 | PLANT_TROUBLE | 1629.6705
2022 | summer | ESCNDO_6_UNITB1 | TRANSMISSION_INDUCED | 0
2022 | summer | ESCO_6_GLMQF | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1464.95
2022 | summer | ESCO_6_GLMQF | PLANT_TROUBLE | 5024.2047
2022 | summer | ESNHWR_2_WC1BT1 | PLANT_MAINTENANCE | 31.5
2022 | summer | ESNHWR_2_WC1BT1 | PLANT_TROUBLE | 231.65
2022 | summer | ESNHWR_2_WC1BT1 | UNIT_TESTING | 0
2022 | summer | ESQUON_6_LNDFIL | PLANT_MAINTENANCE | 12.81
2022 | summer | ESQUON_6_LNDFIL | PLANT_TROUBLE | 36.68
2022 | summer | ESTWND_2_OPPWD1 | METERING_TELEMETRY | 0
2022 | summer | ESTWND_2_OPPWD1 | PLANT_MAINTENANCE | 0
2022 | summer | ESTWND_2_OPPWD1 | TRANSMISSION_INDUCED | 0
2022 | summer | ETIWND_2_FONTNA | AMBIENT_NOT_DUE_TO_TEMP | 1654.4
2022 | summer | ETIWND_2_FONTNA | PLANT_TROUBLE | 0
2022 | summer | ETIWND_2_RTS010 | PLANT_TROUBLE | 487.5
2022 | summer | ETIWND_2_RTS023 | PLANT_TROUBLE | 812.5
2022 | summer | ETIWND_2_UNIT1 | PLANT_TROUBLE | 0
2022 | summer | ETIWND_2_UNIT1 | TRANSMISSION_INDUCED | 4.5
2022 | summer | ETIWND_6_GRPLND | AMBIENT_DUE_TO_TEMP | 833.92
2022 | summer | ETIWND_6_GRPLND | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | summer | ETIWND_6_GRPLND | PLANT_TROUBLE | 222.1588
2022 | summer | ETIWND_6_GRPLND | TRANSMISSION_INDUCED | 112.877
2022 | summer | EXCHEC_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 23197
2022 | summer | EXCLSG_1_SOLAR | PLANT_MAINTENANCE | 59
2022 | summer | EXCLSG_1_SOLAR | PLANT_TROUBLE | 120
2022 | summer | EXCLSG_1_SOLAR | TRANSMISSION_INDUCED | 240
2022 | summer | FLOWD2_2_FPLWND | PLANT_MAINTENANCE | 1681.002
2022 | summer | FLOWD2_2_FPLWND | TRANSMISSION_INDUCED | 0
2022 | summer | FMEADO_6_HELLHL | TRANSMISSION_INDUCED | 165
2022 | summer | FMEADO_7_UNIT | PLANT_TROUBLE | 0
2022 | summer | FMEADO_7_UNIT | TRANSMISSION_INDUCED | 4400
2022 | summer | FORBST_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 32.75
2022 | summer | FORBST_7_UNIT 1 | PLANT_TROUBLE | 0
2022 | summer | FRESHW_1_SOLAR1 | METERING_TELEMETRY | 1.6667
2022 | summer | FRESHW_1_SOLAR1 | TRANSMISSION_INDUCED | 63.6667
2022 | summer | FRNTBW_6_SOLAR1 | METERING_TELEMETRY | 100
2022 | summer | FRNTBW_6_SOLAR1 | TRANSMISSION_INDUCED | 145
2022 | summer | FROGTN_1_UTICAA | PLANT_MAINTENANCE | 0
2022 | summer | FROGTN_1_UTICAA | PLANT_TROUBLE | 2.2633
2022 | summer | FROGTN_1_UTICAA | TRANSMISSION_INDUCED | 0
2022 | summer | FROGTN_1_UTICAM | PLANT_MAINTENANCE | 0
2022 | summer | FROGTN_1_UTICAM | PLANT_TROUBLE | 0
2022 | summer | FROGTN_1_UTICAM | TRANSMISSION_INDUCED | 12.06
2022 | summer | FTSWRD_6_TRFORK | TRANSMISSION_INDUCED | 30.97
2022 | summer | FTSWRD_7_QFUNTS | TRANSMISSION_INDUCED | 30.4
2022 | summer | GALE_1_SR3SR3 | PLANT_TROUBLE | 357.65
2022 | summer | GANSO_1_WSTBM1 | PLANT_MAINTENANCE | 0
2022 | summer | GARLND_2_GARBT1 | METERING_TELEMETRY | 0
2022 | summer | GARLND_2_GARBT1 | PLANT_MAINTENANCE | 5485.0667
2022 | summer | GARLND_2_GARBT1 | PLANT_TROUBLE | 8428.9667
2022 | summer | GARLND_2_GARBT1 | UNIT_TESTING | 0
2022 | summer | GARLND_2_GASLR | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | summer | GARLND_2_GASLR | METERING_TELEMETRY | 0
2022 | summer | GARLND_2_GASLR | PLANT_MAINTENANCE | 1041
2022 | summer | GARLND_2_GASLR | PLANT_TROUBLE | 17889.65
2022 | summer | GARLND_2_GASLR | UNIT_TESTING | 0
2022 | summer | GARLND_2_GASLRA | PLANT_MAINTENANCE | 110
2022 | summer | GARLND_2_GASLRA | PLANT_TROUBLE | 848.8
2022 | summer | GARLND_2_GASLRA | UNIT_TESTING | 0
2022 | summer | GARNET_1_SOLAR | PLANT_TROUBLE | 4
2022 | summer | GARNET_1_SOLAR2 | METERING_TELEMETRY | 10
2022 | summer | GARNET_1_SOLAR2 | PLANT_MAINTENANCE | 0
2022 | summer | GARNET_1_SOLAR2 | PLANT_TROUBLE | 2035
2022 | summer | GARNET_1_WIND | TRANSMISSION_INDUCED | 97.5
2022 | summer | GARNET_1_WINDS | PLANT_MAINTENANCE | 1764.6
2022 | summer | GARNET_1_WINDS | PLANT_TROUBLE | 0
2022 | summer | GARNET_1_WINDS | TRANSMISSION_INDUCED | 1.65
2022 | summer | GARNET_2_HYDRO | AMBIENT_NOT_DUE_TO_TEMP | 765
2022 | summer | GARNET_2_WIND1 | PLANT_TROUBLE | 145.6
2022 | summer | GARNET_2_WIND1 | TRANSMISSION_INDUCED | 560
2022 | summer | GARNET_2_WIND2 | PLANT_MAINTENANCE | 617.5658
2022 | summer | GARNET_2_WIND2 | PLANT_TROUBLE | 440.5225
2022 | summer | GARNET_2_WIND3 | PLANT_TROUBLE | 14.7
2022 | summer | GARNET_2_WIND3 | TRANSMISSION_INDUCED | 63
2022 | summer | GARNET_2_WIND4 | METERING_TELEMETRY | 98
2022 | summer | GARNET_2_WIND4 | TRANSMISSION_INDUCED | 106.1667
2022 | summer | GARNET_2_WPMWD6 | PLANT_TROUBLE | 3498.7
2022 | summer | GASKW1_2_GW1SR1 | PLANT_MAINTENANCE | 34.4
2022 | summer | GASKW1_2_GW1SR1 | PLANT_TROUBLE | 2030.2733
2022 | summer | GASKW1_2_GW1SR1 | TRANSMISSION_INDUCED | 0
2022 | summer | GASKW1_2_GW1SR1 | UNIT_TESTING | 0
2022 | summer | GATES_2_WSOLAR | PLANT_MAINTENANCE | 0
2022 | summer | GATEWY_2_GESBT1 | PLANT_TROUBLE | 1602.1833
2022 | summer | GATEWY_2_GESBT1 | RTU_RIG | 0
2022 | summer | GATWAY_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 76814.1003
2022 | summer | GATWAY_2_PL1X3 | PLANT_MAINTENANCE | 0
2022 | summer | GATWAY_2_PL1X3 | PLANT_TROUBLE | 14040.145
2022 | summer | GENESI_2_STG | AMBIENT_NOT_DUE_TO_TEMP | 12846.9167
2022 | summer | GEYS11_7_UNIT11 | AMBIENT_NOT_DUE_TO_TEMP | 9578.75
2022 | summer | GEYS11_7_UNIT11 | PLANT_TROUBLE | 165.6667
2022 | summer | GEYS11_7_UNIT11 | TRANSITIONAL_LIMITATION | 0
2022 | summer | GEYS11_7_UNIT11 | TRANSMISSION_INDUCED | 101.0365
2022 | summer | GEYS12_7_UNIT12 | AMBIENT_NOT_DUE_TO_TEMP | 11244
2022 | summer | GEYS12_7_UNIT12 | PLANT_TROUBLE | 11.2
2022 | summer | GEYS13_7_UNIT13 | AMBIENT_NOT_DUE_TO_TEMP | 17864.4
2022 | summer | GEYS13_7_UNIT13 | PLANT_TROUBLE | 200.8
2022 | summer | GEYS14_7_UNIT14 | AMBIENT_NOT_DUE_TO_TEMP | 10372
2022 | summer | GEYS14_7_UNIT14 | PLANT_TROUBLE | 570.15
2022 | summer | GEYS16_7_UNIT16 | AMBIENT_NOT_DUE_TO_TEMP | 11070.2333
2022 | summer | GEYS16_7_UNIT16 | PLANT_MAINTENANCE | 440
2022 | summer | GEYS16_7_UNIT16 | PLANT_TROUBLE | 395.5667
2022 | summer | GEYS17_7_UNIT17 | AMBIENT_NOT_DUE_TO_TEMP | 13647.5167
2022 | summer | GEYS17_7_UNIT17 | PLANT_MAINTENANCE | 0
2022 | summer | GEYS17_7_UNIT17 | PLANT_TROUBLE | 3543.9667
2022 | summer | GEYS17_7_UNIT17 | TRANSITIONAL_LIMITATION | 0
2022 | summer | GEYS18_7_UNIT18 | AMBIENT_NOT_DUE_TO_TEMP | 21961.5
2022 | summer | GEYS20_7_UNIT20 | AMBIENT_NOT_DUE_TO_TEMP | 11178.3833
2022 | summer | GIFENS_6_BUGSL1 | PLANT_TROUBLE | 100
2022 | summer | GIFENS_6_BUGSL1 | UNIT_TESTING | 90
2022 | summer | GIFFEN_6_SOLAR | PLANT_TROUBLE | 0
2022 | summer | GIFFEN_6_SOLAR1 | PLANT_TROUBLE | 2
2022 | summer | GILROY_1_UNIT | AMBIENT_DUE_TO_TEMP | 8737.3667
2022 | summer | GILROY_1_UNIT | ENVIRONMENTAL_RESTRICTIONS | 392.6667
2022 | summer | GILROY_1_UNIT | PLANT_MAINTENANCE | 2400
2022 | summer | GILROY_1_UNIT | PLANT_TROUBLE | 1963.95
2022 | summer | GILROY_1_UNIT | TRANSMISSION_INDUCED | 273.65
2022 | summer | GILRPP_1_PL1X2 | AMBIENT_DUE_TO_TEMP | 79.74
2022 | summer | GILRPP_1_PL1X2 | ENVIRONMENTAL_RESTRICTIONS | 127.4583
2022 | summer | GILRPP_1_PL1X2 | PLANT_TROUBLE | 284.2083
2022 | summer | GILRPP_1_PL1X2 | RTU_RIG | 0
2022 | summer | GILRPP_1_PL1X2 | TRANSMISSION_INDUCED | 236.4133
2022 | summer | GILRPP_1_PL1X2 | UNIT_TESTING | 190
2022 | summer | GILRPP_1_PL3X4 | AMBIENT_DUE_TO_TEMP | 6
2022 | summer | GILRPP_1_PL3X4 | PLANT_TROUBLE | 362.2967
2022 | summer | GILRPP_1_PL3X4 | TRANSMISSION_INDUCED | 114.73
2022 | summer | GLDTWN_6_COLUM3 | METERING_TELEMETRY | 25
2022 | summer | GLDTWN_6_COLUM3 | PLANT_MAINTENANCE | 30
2022 | summer | GLDTWN_6_COLUM3 | PLANT_TROUBLE | 50
2022 | summer | GLDTWN_6_SOLAR | PLANT_MAINTENANCE | 0
2022 | summer | GLDTWN_6_SOLAR | PLANT_TROUBLE | 68.9167
2022 | summer | GLNARM_2_UNIT 5 | ENVIRONMENTAL_RESTRICTIONS | 18.54
2022 | summer | GLNARM_2_UNIT 5 | METERING_TELEMETRY | 0
2022 | summer | GLNARM_2_UNIT 5 | PLANT_MAINTENANCE | 0
2022 | summer | GLNARM_2_UNIT 5 | PLANT_TROUBLE | 918.3332
2022 | summer | GLNARM_2_UNIT 5 | UNIT_TESTING | 0
2022 | summer | GLNARM_7_UNIT 1 | METERING_TELEMETRY | 270
2022 | summer | GLNARM_7_UNIT 1 | PLANT_TROUBLE | 30.3
2022 | summer | GLNARM_7_UNIT 1 | UNIT_TESTING | 0
2022 | summer | GLNARM_7_UNIT 2 | PLANT_MAINTENANCE | 376
2022 | summer | GLNARM_7_UNIT 2 | PLANT_TROUBLE | 328.88
2022 | summer | GLNARM_7_UNIT 2 | UNIT_TESTING | 7.2
2022 | summer | GLNARM_7_UNIT 3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 9.4185
2022 | summer | GLNARM_7_UNIT 3 | METERING_TELEMETRY | 0
2022 | summer | GLNARM_7_UNIT 3 | PLANT_TROUBLE | 8.4568
2022 | summer | GLNARM_7_UNIT 4 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 4.6787
2022 | summer | GLNARM_7_UNIT 4 | METERING_TELEMETRY | 0
2022 | summer | GLNARM_7_UNIT 4 | PLANT_TROUBLE | 4053.4207
2022 | summer | GLNARM_7_UNIT 4 | UNIT_TESTING | 0
2022 | summer | GLOW_6_SOLAR | PLANT_TROUBLE | 32.175
2022 | summer | GOLETA_2_VALBT1 | METERING_TELEMETRY | 0
2022 | summer | GOLETA_2_VALBT1 | PLANT_MAINTENANCE | 10.8333
2022 | summer | GOLETA_2_VALBT1 | PLANT_TROUBLE | 5
2022 | summer | GOLETA_6_ELLWOD | PLANT_TROUBLE | 396.9
2022 | summer | GOLETA_6_TR2BM2 | AMBIENT_DUE_TO_TEMP | 28.65
2022 | summer | GOLETA_6_TR2BM2 | AMBIENT_NOT_DUE_TO_TEMP | 254.2217
2022 | summer | GOLETA_6_TR2BM2 | NEW_GENERATOR_TEST_ENERGY | 0
2022 | summer | GOLETA_6_TR2BM2 | PLANT_MAINTENANCE | 78.586
2022 | summer | GOLETA_6_TR2BM2 | PLANT_TROUBLE | 134.5318
2022 | summer | GONZLS_6_UNIT | PLANT_MAINTENANCE | 7.9283
2022 | summer | GONZLS_6_UNIT | PLANT_TROUBLE | 57.155
2022 | summer | GONZLS_6_UNIT | TRANSMISSION_INDUCED | 4.26
2022 | summer | GOOSLK_1_SOLAR1 | PLANT_TROUBLE | 12
2022 | summer | GOOSLK_1_SOLAR1 | TRANSMISSION_INDUCED | 120
2022 | summer | GRADYW_5_GDYWD1 | PLANT_TROUBLE | 1327.3167
2022 | summer | GRADYW_5_GDYWD1 | TRANSMISSION_INDUCED | 1450
2022 | summer | GRIFFI_2_LSPDYN | PLANT_TROUBLE | 0
2022 | summer | GRIZLY_1_UNIT 1 | TRANSMISSION_INDUCED | 14128.6667
2022 | summer | GRNLF1_1_PL1X2 | AMBIENT_DUE_TO_TEMP | 59.8
2022 | summer | GRNLF1_1_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 98.4833
2022 | summer | GRNLF1_1_PL1X2 | NEW_GENERATOR_TEST_ENERGY | 3035
2022 | summer | GRNLF1_1_PL1X2 | PLANT_MAINTENANCE | 0
2022 | summer | GRNLF1_1_PL1X2 | PLANT_TROUBLE | 3519.5
2022 | summer | GRNLF1_1_PL1X2 | UNIT_TESTING | 120
2022 | summer | GRNLF2_1_UNIT | PLANT_TROUBLE | 26568
2022 | summer | GRNLF2_1_UNIT | UNIT_TESTING | 2.2
2022 | summer | GRNVLY_7_SCLAND | PLANT_MAINTENANCE | 242.495
2022 | summer | GRNVLY_7_SCLAND | PLANT_TROUBLE | 106.6377
2022 | summer | GRNVLY_7_SCLAND | TRANSMISSION_INDUCED | 5.472
2022 | summer | GRSCRK_6_BGCKWW | ENVIRONMENTAL_RESTRICTIONS | 3450
2022 | summer | GUERNS_6_HD3BM3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 6
2022 | summer | GUERNS_6_HD3BM3 | PLANT_MAINTENANCE | 0
2022 | summer | GUERNS_6_HD3BM3 | PLANT_TROUBLE | 1.75
2022 | summer | GUERNS_6_HD3BM3 | TRANSMISSION_INDUCED | 0
2022 | summer | GUERNS_6_SOLAR | METERING_TELEMETRY | 2000
2022 | summer | GUERNS_6_SOLAR | PLANT_TROUBLE | 300
2022 | summer | GUERNS_6_SOLAR | TRANSMISSION_INDUCED | 0
2022 | summer | GUERNS_6_VH2BM1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 4.5
2022 | summer | GUERNS_6_VH2BM1 | PLANT_MAINTENANCE | 0
2022 | summer | GUERNS_6_VH2BM1 | PLANT_TROUBLE | 23.9
2022 | summer | GUERNS_6_VH2BM1 | TRANSMISSION_INDUCED | 0
2022 | summer | GWFPWR_1_UNITS | AMBIENT_DUE_TO_TEMP | 7002.9583
2022 | summer | GWFPWR_1_UNITS | PLANT_TROUBLE | 104.7108
2022 | summer | GYS5X6_7_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 14799.15
2022 | summer | GYS5X6_7_UNITS | PLANT_MAINTENANCE | 1.65
2022 | summer | GYS5X6_7_UNITS | PLANT_TROUBLE | 74.3333
2022 | summer | GYS5X6_7_UNITS | TRANSMISSION_INDUCED | 0
2022 | summer | GYS7X8_7_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 13286.3333
2022 | summer | GYS7X8_7_UNITS | PLANT_TROUBLE | 0
2022 | summer | GYS7X8_7_UNITS | TRANSITIONAL_LIMITATION | 0
2022 | summer | GYS7X8_7_UNITS | TRANSMISSION_INDUCED | 0
2022 | summer | HAASPH_7_PL1X2 | AMBIENT_DUE_TO_TEMP | 0
2022 | summer | HAASPH_7_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 100.8
2022 | summer | HAASPH_7_PL1X2 | PLANT_TROUBLE | 350
2022 | summer | HAASPH_7_PL1X2 | TRANSITIONAL_LIMITATION | 8.9
2022 | summer | HAASPH_7_PL1X2 | TRANSMISSION_INDUCED | 144
2022 | summer | HARBGN_7_UNITS | AMBIENT_DUE_TO_TEMP | 10314.2
2022 | summer | HARBGN_7_UNITS | PLANT_MAINTENANCE | 504.8333
2022 | summer | HARBGN_7_UNITS | PLANT_TROUBLE | 2130.6005
2022 | summer | HARDWK_6_STWBM1 | AMBIENT_DUE_TO_TEMP | 18.6
2022 | summer | HARDWK_6_STWBM1 | PLANT_MAINTENANCE | 0
2022 | summer | HARDWK_6_STWBM1 | PLANT_TROUBLE | 20.1667
2022 | summer | HATCR1_7_UNIT | PLANT_TROUBLE | 30.0333
2022 | summer | HATCR1_7_UNIT | TRANSMISSION_INDUCED | 4.9583
2022 | summer | HATCR2_7_UNIT | PLANT_TROUBLE | 811.6083
2022 | summer | HATCR2_7_UNIT | TRANSMISSION_INDUCED | 3.9667
2022 | summer | HATLOS_6_BWDHY1 | PLANT_TROUBLE | 0
2022 | summer | HATLOS_6_LSCRK | AMBIENT_NOT_DUE_TO_TEMP | 387.2
2022 | summer | HATLOS_6_LSCRK | PLANT_MAINTENANCE | 0
2022 | summer | HATRDG_2_WIND | PLANT_MAINTENANCE | 234.6
2022 | summer | HAYPRS_6_HAYHD1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 4266.3
2022 | summer | HAYPRS_6_HAYHD2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 4935.3
2022 | summer | HELMPG_7_UNIT 1 | PLANT_TROUBLE | 2272.4167
2022 | summer | HELMPG_7_UNIT 1 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2022 | summer | HELMPG_7_UNIT 1 | TRANSMISSION_INDUCED | 3098.7667
2022 | summer | HELMPG_7_UNIT 2 | PLANT_TROUBLE | 0
2022 | summer | HELMPG_7_UNIT 2 | TRANSMISSION_INDUCED | 1395.55
2022 | summer | HELMPG_7_UNIT 3 | PLANT_TROUBLE | 1232.2
2022 | summer | HELMPG_7_UNIT 3 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2022 | summer | HELMPG_7_UNIT 3 | TRANSMISSION_INDUCED | 2257.1
2022 | summer | HENRTA_6_HDEBT1 | PLANT_MAINTENANCE | 2
2022 | summer | HENRTA_6_HDEBT1 | PLANT_TROUBLE | 0
2022 | summer | HENRTA_6_SOLAR1 | PLANT_TROUBLE | 262.35
2022 | summer | HENRTA_6_SOLAR2 | PLANT_MAINTENANCE | 0
2022 | summer | HENRTA_6_UNITA1 | AMBIENT_DUE_TO_TEMP | 3626.177
2022 | summer | HENRTA_6_UNITA1 | PLANT_TROUBLE | 0
2022 | summer | HENRTA_6_UNITA2 | AMBIENT_DUE_TO_TEMP | 3555.0865
2022 | summer | HENRTA_6_UNITA2 | PLANT_MAINTENANCE | 144.2822
2022 | summer | HENRTA_6_UNITA2 | PLANT_TROUBLE | 0
2022 | summer | HENRTS_1_SOLAR | PLANT_MAINTENANCE | 50
2022 | summer | HENRTS_1_SOLAR | PLANT_TROUBLE | 440.8
2022 | summer | HENRTS_1_SOLAR | TRANSMISSION_INDUCED | 483.3333
2022 | summer | HIDSRT_2_UNITS | AMBIENT_DUE_TO_TEMP | 70854.4
2022 | summer | HIDSRT_2_UNITS | PLANT_MAINTENANCE | 3944
2022 | summer | HIDSRT_2_UNITS | PLANT_TROUBLE | 2355.3
2022 | summer | HIDSRT_2_UNITS | TRANSMISSION_INDUCED | 3951
2022 | summer | HIGGNS_1_COMBIE | PLANT_MAINTENANCE | 9.4917
2022 | summer | HIGHDS_2_H5SBT1 | METERING_TELEMETRY | 61
2022 | summer | HIGHDS_2_H5SBT1 | PLANT_MAINTENANCE | 250
2022 | summer | HIGHDS_2_H5SBT1 | PLANT_TROUBLE | 5640.1972
2022 | summer | HIGHDS_2_H5SBT1 | UNIT_TESTING | 35
2022 | summer | HIGHDS_2_H5SSR1 | PLANT_MAINTENANCE | 37.5
2022 | summer | HIGHDS_2_H5SSR1 | PLANT_TROUBLE | 1023.3333
2022 | summer | HIGHDS_2_H5SSR1 | TRANSMISSION_INDUCED | 143.3333
2022 | summer | HIGHDS_2_H5SSR1 | UNIT_TESTING | 30
2022 | summer | HINSON_6_CARBGN | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 750
2022 | summer | HINSON_6_LBECH1 | AMBIENT_DUE_TO_TEMP | 14.5667
2022 | summer | HINSON_6_LBECH1 | PLANT_TROUBLE | 63
2022 | summer | HINSON_6_LBECH2 | AMBIENT_DUE_TO_TEMP | 9.5
2022 | summer | HINSON_6_LBECH3 | AMBIENT_DUE_TO_TEMP | 34.8333
2022 | summer | HINSON_6_LBECH4 | AMBIENT_DUE_TO_TEMP | 4.75
2022 | summer | HINSON_6_LBECH4 | PLANT_TROUBLE | 0
2022 | summer | HINSON_6_SERRGN | PLANT_MAINTENANCE | 2372
2022 | summer | HNTGBH_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 9053.5333
2022 | summer | HNTGBH_2_PL1X3 | PLANT_TROUBLE | 434.3333
2022 | summer | HNTGBH_7_UNIT 2 | AMBIENT_DUE_TO_TEMP | 1023.0347
2022 | summer | HNTGBH_7_UNIT 2 | PLANT_MAINTENANCE | 0
2022 | summer | HNTGBH_7_UNIT 2 | PLANT_TROUBLE | 250.66
2022 | summer | HNTGBH_7_UNIT 2 | TRANSMISSION_INDUCED | 2177.664
2022 | summer | HNTGBH_7_UNIT 2 | UNIT_TESTING | 0
2022 | summer | HOLSTR_1_SOLAR | METERING_TELEMETRY | 3
2022 | summer | HOLSTR_1_SOLAR | PLANT_TROUBLE | 0.625
2022 | summer | HOLSTR_1_SOLAR2 | TRANSMISSION_INDUCED | 9
2022 | summer | HOOVER_2_MWDDYN | AMBIENT_NOT_DUE_TO_TEMP | 83023
2022 | summer | HOOVER_2_MWDDYN | PLANT_MAINTENANCE | 1705
2022 | summer | HOOVER_2_MWDDYN | PLANT_TROUBLE | 223
2022 | summer | HOOVER_2_VEADYN | AMBIENT_NOT_DUE_TO_TEMP | 5298
2022 | summer | HOOVER_2_VEADYN | PLANT_MAINTENANCE | 0
2022 | summer | HOOVER_2_VEADYN | PLANT_TROUBLE | 18
2022 | summer | HUMBPP_1_UNITS3 | AMBIENT_NOT_DUE_TO_TEMP | 40.675
2022 | summer | HUMBPP_1_UNITS3 | PLANT_MAINTENANCE | 1692.08
2022 | summer | HUMBPP_1_UNITS3 | PLANT_TROUBLE | 14114.0568
2022 | summer | HUMBPP_1_UNITS3 | TRANSMISSION_INDUCED | 1692.0043
2022 | summer | HUMBPP_6_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 58.3008
2022 | summer | HUMBPP_6_UNITS | PLANT_MAINTENANCE | 16540.899
2022 | summer | HUMBPP_6_UNITS | PLANT_TROUBLE | 3203.94
2022 | summer | HUMBPP_6_UNITS | TRANSMISSION_INDUCED | 0
2022 | summer | HYTTHM_2_UNITS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 48721.78
2022 | summer | HYTTHM_2_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 1260
2022 | summer | HYTTHM_2_UNITS | ENVIRONMENTAL_RESTRICTIONS | 61677.2333
2022 | summer | HYTTHM_2_UNITS | PLANT_MAINTENANCE | 1810.5
2022 | summer | HYTTHM_2_UNITS | PLANT_TROUBLE | 11115.9833
2022 | summer | INDIGO_1_UNIT 1 | AMBIENT_DUE_TO_TEMP | 2593.775
2022 | summer | INDIGO_1_UNIT 1 | PLANT_MAINTENANCE | 0
2022 | summer | INDIGO_1_UNIT 1 | PLANT_TROUBLE | 263.39
2022 | summer | INDIGO_1_UNIT 1 | TRANSMISSION_INDUCED | 763
2022 | summer | INDIGO_1_UNIT 2 | AMBIENT_DUE_TO_TEMP | 3454
2022 | summer | INDIGO_1_UNIT 2 | PLANT_MAINTENANCE | 0
2022 | summer | INDIGO_1_UNIT 2 | PLANT_TROUBLE | 40.1
2022 | summer | INDIGO_1_UNIT 2 | TRANSMISSION_INDUCED | 744.8333
2022 | summer | INDIGO_1_UNIT 3 | AMBIENT_DUE_TO_TEMP | 3108
2022 | summer | INDIGO_1_UNIT 3 | PLANT_MAINTENANCE | 0
2022 | summer | INDIGO_1_UNIT 3 | PLANT_TROUBLE | 112.6833
2022 | summer | INDIGO_1_UNIT 3 | TRANSMISSION_INDUCED | 810
2022 | summer | INTKEP_2_UNITS | ENVIRONMENTAL_RESTRICTIONS | 61355.2
2022 | summer | INTKEP_2_UNITS | PLANT_MAINTENANCE | 1625
2022 | summer | INTKEP_2_UNITS | PLANT_TROUBLE | 1629.0833
2022 | summer | INTKEP_2_UNITS | TRANSMISSION_INDUCED | 0
2022 | summer | INTMNT_3_ANAHEIM | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 14738
2022 | summer | INTMNT_3_ANAHEIM | PLANT_TROUBLE | 500
2022 | summer | INTMNT_3_ANAHEIM | UNIT_TESTING | 145
2022 | summer | INTMNT_3_PASADENA | PLANT_TROUBLE | 290
2022 | summer | INTMNT_3_PASADENA | UNIT_SUPPORTING_STARTUP | 0
2022 | summer | INTMNT_3_PASADENA | UNIT_TESTING | 46
2022 | summer | INTMNT_3_RIVERSIDE | ENVIRONMENTAL_RESTRICTIONS | 872.7
2022 | summer | INTMNT_3_RIVERSIDE | PLANT_TROUBLE | 290
2022 | summer | INTTRB_6_UNIT | TRANSMISSION_INDUCED | 10.4267
2022 | summer | IVANPA_1_UNIT1 | AMBIENT_DUE_TO_TEMP | 630
2022 | summer | IVANPA_1_UNIT1 | AMBIENT_NOT_DUE_TO_TEMP | 28691.2
2022 | summer | IVANPA_1_UNIT1 | PLANT_TROUBLE | 3910
2022 | summer | IVANPA_1_UNIT1 | UNIT_TESTING | 0
2022 | summer | IVANPA_1_UNIT2 | AMBIENT_DUE_TO_TEMP | 598.5
2022 | summer | IVANPA_1_UNIT2 | PLANT_TROUBLE | 17.7333
2022 | summer | IVANPA_1_UNIT3 | AMBIENT_DUE_TO_TEMP | 665
2022 | summer | IVANPA_1_UNIT3 | AMBIENT_NOT_DUE_TO_TEMP | 30089.0333
2022 | summer | IVANPA_1_UNIT3 | PLANT_TROUBLE | 2660
2022 | summer | IVSLR2_2_SM2SR1 | PLANT_TROUBLE | 345
2022 | summer | IVSLRP_2_SOLAR1 | PLANT_MAINTENANCE | 0
2022 | summer | IVSLRP_2_SOLAR1 | PLANT_TROUBLE | 51427
2022 | summer | IVWEST_2_SOLAR1 | PLANT_TROUBLE | 10
2022 | summer | JACMSR_1_JACSR1 | TRANSMISSION_INDUCED | 106.6667
2022 | summer | JANCRK_6_RCABT1 | PLANT_MAINTENANCE | 3.42
2022 | summer | JANCRK_6_RCABT1 | PLANT_TROUBLE | 2.9242
2022 | summer | JANCRK_6_RCABT1 | TRANSMISSION_INDUCED | 5.25
2022 | summer | JAWBNE_2_NSRWND | AMBIENT_NOT_DUE_TO_TEMP | 330.8133
2022 | summer | JAWBNE_2_NSRWND | METERING_TELEMETRY | 364
2022 | summer | JAWBNE_2_NSRWND | PLANT_MAINTENANCE | 7988.78
2022 | summer | JAWBNE_2_NSRWND | TRANSMISSION_INDUCED | 0
2022 | summer | JAWBNE_2_SRWND | AMBIENT_NOT_DUE_TO_TEMP | 41.25
2022 | summer | JAWBNE_2_SRWND | METERING_TELEMETRY | 75
2022 | summer | JAWBNE_2_SRWND | PLANT_MAINTENANCE | 0
2022 | summer | JAWBNE_2_SRWND | PLANT_TROUBLE | 2560.2
2022 | summer | JAWBNE_2_SRWND | TRANSMISSION_INDUCED | 0
2022 | summer | JAWBNE_2_SRWWD2 | PLANT_MAINTENANCE | 264
2022 | summer | JAWBNE_2_SRWWD2 | PLANT_TROUBLE | 4399.6507
2022 | summer | JAWBNE_2_SRWWD2 | TRANSMISSION_INDUCED | 0
2022 | summer | JAYNE_6_WLSLR | PLANT_MAINTENANCE | 17.7
2022 | summer | JOANEC_2_STABT1 | PLANT_TROUBLE | 567.6667
2022 | summer | JOANEC_2_STABT1 | UNIT_TESTING | 0
2022 | summer | JOANEC_2_STABT2 | PLANT_MAINTENANCE | 70
2022 | summer | JOANEC_2_STABT2 | PLANT_TROUBLE | 52.5
2022 | summer | JOHANN_2_JOSBT1 | METERING_TELEMETRY | 46.5
2022 | summer | JOHANN_2_JOSBT1 | PLANT_MAINTENANCE | 11.95
2022 | summer | JOHANN_2_JOSBT1 | PLANT_TROUBLE | 513.05
2022 | summer | JOHANN_2_JOSBT1 | UNIT_TESTING | 0
2022 | summer | JOHANN_2_JOSBT2 | METERING_TELEMETRY | 46.5
2022 | summer | JOHANN_2_JOSBT2 | PLANT_MAINTENANCE | 3
2022 | summer | JOHANN_2_JOSBT2 | PLANT_TROUBLE | 334
2022 | summer | JOHANN_2_JOSBT2 | UNIT_TESTING | 0
2022 | summer | JOHANN_2_OCEBT2 | PLANT_MAINTENANCE | 0
2022 | summer | JOHANN_2_OCEBT2 | PLANT_TROUBLE | 0
2022 | summer | JOHANN_2_OCEBT2 | TRANSMISSION_INDUCED | 12
2022 | summer | JOHANN_2_OCEBT3 | PLANT_MAINTENANCE | 0
2022 | summer | JOHANN_2_OCEBT3 | PLANT_TROUBLE | 3.1
2022 | summer | JOHANN_2_OCEBT3 | TRANSMISSION_INDUCED | 8
2022 | summer | KANSAS_6_SOLAR | AMBIENT_DUE_TO_TEMP | 10
2022 | summer | KANSAS_6_SOLAR | METERING_TELEMETRY | 93.3333
2022 | summer | KANSAS_6_SOLAR | PLANT_TROUBLE | 68.85
2022 | summer | KANSAS_6_SOLAR | TRANSMISSION_INDUCED | 0
2022 | summer | KEARNY_6_NESBT1 | PLANT_TROUBLE | 313.7
2022 | summer | KEARNY_6_SESBT2 | PLANT_TROUBLE | 562.75
2022 | summer | KEKAWK_6_UNIT | PLANT_TROUBLE | 4207.5
2022 | summer | KELSO_2_UNITS | AMBIENT_DUE_TO_TEMP | 6535.11
2022 | summer | KELSO_2_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | summer | KELSO_2_UNITS | PLANT_TROUBLE | 192.6483
2022 | summer | KELYRG_6_UNIT | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | summer | KELYRG_6_UNIT | PLANT_MAINTENANCE | 165
2022 | summer | KELYRG_6_UNIT | TRANSMISSION_INDUCED | 88
2022 | summer | KERKH2_7_UNIT 1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 614.135
2022 | summer | KERKH2_7_UNIT 1 | AMBIENT_DUE_TO_TEMP | 575.94
2022 | summer | KERKH2_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 17673.7198
2022 | summer | KERKH2_7_UNIT 1 | METERING_TELEMETRY | 28.215
2022 | summer | KERKH2_7_UNIT 1 | PLANT_TROUBLE | 427.97
2022 | summer | KERMAN_6_SOLAR2 | PLANT_TROUBLE | 236.25
2022 | summer | KERNFT_1_UNITS | AMBIENT_DUE_TO_TEMP | 2955.98
2022 | summer | KERNFT_1_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 92
2022 | summer | KERNFT_1_UNITS | PLANT_TROUBLE | 16463.5233
2022 | summer | KERNFT_1_UNITS | RTU_RIG | 0
2022 | summer | KERNRG_1_UNITS | AMBIENT_DUE_TO_TEMP | 0
2022 | summer | KERNRG_1_UNITS | PLANT_MAINTENANCE | 1428.8
2022 | summer | KERNRG_1_UNITS | PLANT_TROUBLE | 524.9733
2022 | summer | KERRGN_1_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 7758.525
2022 | summer | KERRGN_1_UNIT 1 | PLANT_TROUBLE | 198.75
2022 | summer | KERRGN_1_UNIT 1 | TRANSMISSION_INDUCED | 136.1167
2022 | summer | KINGCO_1_KINGBR | TRANSMISSION_INDUCED | 4450.5
2022 | summer | KINGRV_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 227.065
2022 | summer | KINGRV_7_UNIT 1 | PLANT_TROUBLE | 147.6267
2022 | summer | KINGRV_7_UNIT 1 | TRANSMISSION_INDUCED | 0
2022 | summer | KIRKER_7_KELCYN | PLANT_MAINTENANCE | 119.2007
2022 | summer | KIRKER_7_KELCYN | PLANT_TROUBLE | 456.3793
2022 | summer | KIRKER_7_KELCYN | TRANSMISSION_INDUCED | 96.5807
2022 | summer | KNGBRD_2_SOLAR1 | PLANT_MAINTENANCE | 20
2022 | summer | KNGBRD_2_SOLAR2 | METERING_TELEMETRY | 0
2022 | summer | KNGCTY_6_UNITA1 | AMBIENT_DUE_TO_TEMP | 674
2022 | summer | KNGCTY_6_UNITA1 | METERING_TELEMETRY | 0
2022 | summer | KNGCTY_6_UNITA1 | TRANSMISSION_INDUCED | 0
2022 | summer | KNTSTH_6_SOLAR | PLANT_MAINTENANCE | 20
2022 | summer | KNTSTH_6_SOLAR | PLANT_TROUBLE | 684.4
2022 | summer | KYCORA_6_KMSBT1 | PLANT_TROUBLE | 386.975
2022 | summer | LAKHDG_6_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 3000
2022 | summer | LAKHDG_6_UNIT 1 | PLANT_MAINTENANCE | 0
2022 | summer | LAKHDG_6_UNIT 1 | PLANT_TROUBLE | 100
2022 | summer | LAKHDG_6_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 3000
2022 | summer | LAMONT_1_SOLAR1 | PLANT_TROUBLE | 240
2022 | summer | LAMONT_1_SOLAR2 | PLANT_TROUBLE | 0
2022 | summer | LAMONT_1_SOLAR2 | TRANSMISSION_INDUCED | 77
2022 | summer | LAMONT_1_SOLAR3 | PLANT_TROUBLE | 1419.165
2022 | summer | LAMONT_1_SOLAR3 | TRANSMISSION_INDUCED | 45.885
2022 | summer | LAMONT_1_SOLAR4 | PLANT_TROUBLE | 846.4057
2022 | summer | LAMONT_1_SOLAR5 | PLANT_MAINTENANCE | 0
2022 | summer | LAMONT_1_SOLAR5 | PLANT_TROUBLE | 2878.852
2022 | summer | LAPLMA_2_UNIT 1 | AMBIENT_DUE_TO_TEMP | 10360.0833
2022 | summer | LAPLMA_2_UNIT 1 | PLANT_TROUBLE | 8707.1
2022 | summer | LAPLMA_2_UNIT 1 | UNIT_TESTING | 489
2022 | summer | LAPLMA_2_UNIT 2 | AMBIENT_DUE_TO_TEMP | 12613
2022 | summer | LAPLMA_2_UNIT 2 | PLANT_TROUBLE | 5416.2333
2022 | summer | LAPLMA_2_UNIT 2 | UNIT_TESTING | 1052.45
2022 | summer | LAPLMA_2_UNIT 3 | AMBIENT_DUE_TO_TEMP | 9264.4333
2022 | summer | LAPLMA_2_UNIT 3 | PLANT_TROUBLE | 8607.7333
2022 | summer | LAPLMA_2_UNIT 3 | UNIT_TESTING | 669
2022 | summer | LAPLMA_2_UNIT 4 | AMBIENT_DUE_TO_TEMP | 14525.6667
2022 | summer | LAPLMA_2_UNIT 4 | PLANT_TROUBLE | 4429.45
2022 | summer | LAPLMA_2_UNIT 4 | UNIT_TESTING | 1533.8333
2022 | summer | LARKSP_6_UNIT 1 | AMBIENT_DUE_TO_TEMP | 1972.5
2022 | summer | LARKSP_6_UNIT 1 | PLANT_MAINTENANCE | 0
2022 | summer | LARKSP_6_UNIT 1 | PLANT_TROUBLE | 134.1667
2022 | summer | LARKSP_6_UNIT 2 | AMBIENT_DUE_TO_TEMP | 1612.1
2022 | summer | LARKSP_6_UNIT 2 | METERING_TELEMETRY | 0
2022 | summer | LARKSP_6_UNIT 2 | PLANT_MAINTENANCE | 0
2022 | summer | LARKSP_6_UNIT 2 | PLANT_TROUBLE | 93
2022 | summer | LAROA2_2_UNITA1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 3497.3333
2022 | summer | LAROA2_2_UNITA1 | AMBIENT_DUE_TO_TEMP | 10977.5667
2022 | summer | LAROA2_2_UNITA1 | PLANT_MAINTENANCE | 1610
2022 | summer | LAROA2_2_UNITA1 | PLANT_TROUBLE | 8769.05
2022 | summer | LASSEN_6_UNITS | METERING_TELEMETRY | 0
2022 | summer | LASSEN_6_UNITS | PLANT_TROUBLE | 825.5
2022 | summer | LASSEN_6_UNITS | TRANSMISSION_INDUCED | 1522
2022 | summer | LEBECS_2_UNITS | AMBIENT_DUE_TO_TEMP | 14973.7967
2022 | summer | LEBECS_2_UNITS | PLANT_TROUBLE | 86742.7835
2022 | summer | LEBECS_2_UNITS | TRANSMISSION_INDUCED | 3118
2022 | summer | LEBECS_2_UNITS | UNIT_TESTING | 80.98
2022 | summer | LECEF_1_UNITS | AMBIENT_DUE_TO_TEMP | 14424.52
2022 | summer | LECEF_1_UNITS | METERING_TELEMETRY | 3689.4167
2022 | summer | LECEF_1_UNITS | PLANT_MAINTENANCE | 945.68
2022 | summer | LECEF_1_UNITS | PLANT_TROUBLE | 548.7833
2022 | summer | LECEF_1_UNITS | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 4025.4667
2022 | summer | LECONT_2_LESBT1 | METERING_TELEMETRY | 0
2022 | summer | LECONT_2_LESBT1 | NEW_GENERATOR_TEST_ENERGY | 0
2022 | summer | LECONT_2_LESBT1 | PLANT_MAINTENANCE | 9993.0667
2022 | summer | LECONT_2_LESBT1 | PLANT_TROUBLE | 0
2022 | summer | LECONT_2_LESBT1 | UNIT_TESTING | 0
2022 | summer | LEPRFD_1_KANSAS | PLANT_TROUBLE | 306.45
2022 | summer | LGHTHP_6_ICEGEN | AMBIENT_DUE_TO_TEMP | 104
2022 | summer | LGHTHP_6_ICEGEN | PLANT_TROUBLE | 5040.8
2022 | summer | LGHTHP_6_ICEGEN | UNIT_TESTING | 24
2022 | summer | LHILLS_6_SOLAR1 | PLANT_TROUBLE | 23.3333
2022 | summer | LHILLS_6_SOLAR1 | TRANSMISSION_INDUCED | 200
2022 | summer | LITLRK_6_GBCSR1 | PLANT_TROUBLE | 50.25
2022 | summer | LITLRK_6_SOLAR1 | METERING_TELEMETRY | 100
2022 | summer | LITLRK_6_SOLAR1 | PLANT_TROUBLE | 1813.95
2022 | summer | LITLRK_6_SOLAR2 | METERING_TELEMETRY | 20
2022 | summer | LITLRK_6_SOLAR2 | PLANT_TROUBLE | 24.4667
2022 | summer | LITLRK_6_SOLAR2 | TRANSMISSION_INDUCED | 0
2022 | summer | LITLRK_6_SOLAR4 | PLANT_MAINTENANCE | 0
2022 | summer | LIVOAK_1_UNIT 1 | AMBIENT_DUE_TO_TEMP | 6574.5667
2022 | summer | LIVOAK_1_UNIT 1 | PLANT_TROUBLE | 243.6333
2022 | summer | LMBEPK_2_UNITA1 | AMBIENT_DUE_TO_TEMP | 28.5
2022 | summer | LMBEPK_2_UNITA1 | PLANT_TROUBLE | 1264.665
2022 | summer | LMBEPK_2_UNITA1 | TRANSMISSION_INDUCED | 0
2022 | summer | LMBEPK_2_UNITA2 | AMBIENT_DUE_TO_TEMP | 94.4133
2022 | summer | LMBEPK_2_UNITA2 | PLANT_TROUBLE | 400.3405
2022 | summer | LMBEPK_2_UNITA2 | TRANSMISSION_INDUCED | 0
2022 | summer | LMBEPK_2_UNITA3 | AMBIENT_DUE_TO_TEMP | 51
2022 | summer | LMBEPK_2_UNITA3 | PLANT_TROUBLE | 107.965
2022 | summer | LMBEPK_2_UNITA3 | TRANSMISSION_INDUCED | 0
2022 | summer | LMEC_1_PL1X3 | AMBIENT_DUE_TO_TEMP | 19576.6167
2022 | summer | LMEC_1_PL1X3 | PLANT_TROUBLE | 23380.9667
2022 | summer | LNCSTR_6_SOLAR2 | METERING_TELEMETRY | 0
2022 | summer | LODI25_2_UNIT 1 | AMBIENT_DUE_TO_TEMP | 2334.85
2022 | summer | LODI25_2_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 26
2022 | summer | LODI25_2_UNIT 1 | ENVIRONMENTAL_RESTRICTIONS | 106.3333
2022 | summer | LODI25_2_UNIT 1 | PLANT_TROUBLE | 267.7667
2022 | summer | LODIEC_2_PL1X2 | AMBIENT_DUE_TO_TEMP | 30711.1067
2022 | summer | LODIEC_2_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 1125
2022 | summer | LODIEC_2_PL1X2 | PLANT_TROUBLE | 85417.1037
2022 | summer | LODIEC_2_PL1X2 | UNIT_TESTING | 76.48
2022 | summer | LOTUS_6_LSFSR1 | PLANT_MAINTENANCE | 394.25
2022 | summer | LOTUS_6_LSFSR1 | PLANT_TROUBLE | 873.1667
2022 | summer | LOWGAP_7_QFUNTS | ENVIRONMENTAL_RESTRICTIONS | 827.25
2022 | summer | LOWGAP_7_QFUNTS | PLANT_MAINTENANCE | 1
2022 | summer | LOWGAP_7_QFUNTS | PLANT_TROUBLE | 1
2022 | summer | LOWGAP_7_QFUNTS | TRANSMISSION_INDUCED | 0
2022 | summer | LTBEAR_1_LB3SR3 | PLANT_MAINTENANCE | 0
2022 | summer | LTBEAR_1_LB3SR3 | PLANT_TROUBLE | 22.5
2022 | summer | LTBEAR_1_LB4SR4 | PLANT_TROUBLE | 191.8333
2022 | summer | LTBEAR_1_LB4SR5 | PLANT_TROUBLE | 235
2022 | summer | LTBERA_1_LB1SR1 | PLANT_TROUBLE | 129.1667
2022 | summer | MAGNLA_6_ANAHEIM | AMBIENT_DUE_TO_TEMP | 2230
2022 | summer | MAGNLA_6_ANAHEIM | PLANT_MAINTENANCE | 2928
2022 | summer | MAGNLA_6_ANAHEIM | PLANT_TROUBLE | 1120.4667
2022 | summer | MAGNLA_6_ANAHEIM | UNIT_TESTING | 0
2022 | summer | MAGNLA_6_CERRITOS | PLANT_MAINTENANCE | 161
2022 | summer | MAGNLA_6_CERRITOS | PLANT_TROUBLE | 73.6667
2022 | summer | MAGNLA_6_COLTON | PLANT_MAINTENANCE | 294
2022 | summer | MAGNLA_6_COLTON | PLANT_TROUBLE | 73.8333
2022 | summer | MAGNLA_6_PASADENA | PLANT_MAINTENANCE | 476
2022 | summer | MAGNLA_6_PASADENA | PLANT_TROUBLE | 180
2022 | summer | MAGNLA_6_PASADENA | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2022 | summer | MAGUND_1_BKISR1 | PLANT_TROUBLE | 0
2022 | summer | MAGUND_1_BKISR1 | TRANSMISSION_INDUCED | 0
2022 | summer | MAGUND_1_BKSSR2 | PLANT_TROUBLE | 451.9625
2022 | summer | MALAGA_1_PL1X2 | AMBIENT_DUE_TO_TEMP | 135
2022 | summer | MALAGA_1_PL1X2 | PLANT_TROUBLE | 141.6
2022 | summer | MALCHQ_7_UNIT 1 | TRANSMISSION_INDUCED | 6825
2022 | summer | MALIN_5_GCPDDYN | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | summer | MALIN_5_GCPDDYN | PLANT_TROUBLE | 0
2022 | summer | MANTEC_1_ML1SR1 | PLANT_TROUBLE | 1.5167
2022 | summer | MANTEC_1_ML1SR1 | TRANSMISSION_INDUCED | 0
2022 | summer | MANZNA_2_WIND | AMBIENT_DUE_TO_TEMP | 179.7
2022 | summer | MANZNA_2_WIND | ENVIRONMENTAL_RESTRICTIONS | 708.75
2022 | summer | MANZNA_2_WIND | METERING_TELEMETRY | 4.3
2022 | summer | MANZNA_2_WIND | PLANT_MAINTENANCE | 506.15
2022 | summer | MANZNA_2_WIND | PLANT_TROUBLE | 2634.2333
2022 | summer | MARCPW_6_SOLAR1 | PLANT_TROUBLE | 119.6667
2022 | summer | MARCPW_6_SOLAR1 | TRANSMISSION_INDUCED | 30
2022 | summer | MARTIN_1_SUNSET | PLANT_MAINTENANCE | 4.5
2022 | summer | MARTIN_1_SUNSET | TRANSMISSION_INDUCED | 0
2022 | summer | MCARTH_6_FRIVRB | PLANT_MAINTENANCE | 1.225
2022 | summer | MCARTH_6_FRIVRB | PLANT_TROUBLE | 0
2022 | summer | MCCALL_1_QF | AMBIENT_NOT_DUE_TO_TEMP | 7.8
2022 | summer | MDFKRL_2_PROJCT | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | summer | MDFKRL_2_PROJCT | PLANT_TROUBLE | 16.3333
2022 | summer | MDFKRL_2_PROJCT | TRANSMISSION_INDUCED | 23100
2022 | summer | MENBIO_6_RENEW1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | summer | MENBIO_6_RENEW1 | TRANSMISSION_INDUCED | 93.25
2022 | summer | MERCED_1_SOLAR1 | PLANT_TROUBLE | 0
2022 | summer | MERCED_1_SOLAR2 | PLANT_TROUBLE | 0
2022 | summer | MERCFL_6_UNIT | PLANT_TROUBLE | 12.1333
2022 | summer | METEC_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 19706.5267
2022 | summer | METEC_2_PL1X3 | PLANT_TROUBLE | 21114.0357
2022 | summer | MIDWD_2_WIND2 | PLANT_MAINTENANCE | 4.5
2022 | summer | MIDWD_7_CORAMB | TRANSMISSION_INDUCED | 17.875
2022 | summer | MIDWY3_2_MDSSR1 | PLANT_MAINTENANCE | 0
2022 | summer | MIDWY3_2_MDSSR1 | PLANT_TROUBLE | 1142.5167
2022 | summer | MIDWY3_2_MDSSR1 | TRANSMISSION_INDUCED | 703.7
2022 | summer | MIDWYS_2_MIDSL1 | PLANT_MAINTENANCE | 74.85
2022 | summer | MIDWYS_2_MIDSL1 | PLANT_TROUBLE | 0
2022 | summer | MILFRD_7_PASADENA | PLANT_TROUBLE | 1.0917
2022 | summer | MIRLOM_2_CORONA | PLANT_TROUBLE | 28.5
2022 | summer | MIRLOM_2_MLBBTA | METERING_TELEMETRY | 0
2022 | summer | MIRLOM_2_MLBBTA | PLANT_MAINTENANCE | 100
2022 | summer | MIRLOM_2_MLBBTA | PLANT_TROUBLE | 0
2022 | summer | MIRLOM_2_MLBBTB | METERING_TELEMETRY | 71
2022 | summer | MIRLOM_2_MLBBTB | PLANT_MAINTENANCE | 206.4
2022 | summer | MIRLOM_2_MLBBTB | PLANT_TROUBLE | 156.5267
2022 | summer | MIRLOM_2_MLBBTB | TRANSMISSION_INDUCED | 0
2022 | summer | MIRLOM_2_ONTARO | PLANT_TROUBLE | 2196.8647
2022 | summer | MIRLOM_2_TEMESC | PLANT_MAINTENANCE | 14.25
2022 | summer | MIRLOM_6_PEAKER | AMBIENT_DUE_TO_TEMP | 2836.0533
2022 | summer | MIRLOM_6_PEAKER | PLANT_TROUBLE | 337.4373
2022 | summer | MIRLOM_7_MWDLKM | PLANT_TROUBLE | 5
2022 | summer | MKTRCK_1_UNIT 1 | AMBIENT_DUE_TO_TEMP | 439
2022 | summer | MKTRCK_1_UNIT 1 | PLANT_MAINTENANCE | 340
2022 | summer | MKTRCK_1_UNIT 1 | PLANT_TROUBLE | 7248.565
2022 | summer | MNDALY_6_MCGRTH | AMBIENT_DUE_TO_TEMP | 5214.4157
2022 | summer | MNDALY_6_MCGRTH | METERING_TELEMETRY | 149.455
2022 | summer | MNDALY_6_MCGRTH | PLANT_TROUBLE | 264.7297
2022 | summer | MNDALY_6_MCGRTH | TRANSMISSION_INDUCED | 34.1768
2022 | summer | MNDALY_6_MCGRTH | UNIT_TESTING | 0
2022 | summer | MNDOTA_1_SOLAR1 | PLANT_MAINTENANCE | 8.9917
2022 | summer | MNDOTA_1_SOLAR1 | PLANT_TROUBLE | 521.04
2022 | summer | MNDOTA_1_SOLAR2 | PLANT_TROUBLE | 1.25
2022 | summer | MOJAVW_2_SOLAR | PLANT_TROUBLE | 101.25
2022 | summer | MONLTH_6_BATTRY | PLANT_TROUBLE | 2436.95
2022 | summer | MONTPH_7_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 1957.4
2022 | summer | MONTPH_7_UNITS | TRANSMISSION_INDUCED | 27
2022 | summer | MOORPK_2_ACOBT1 | PLANT_MAINTENANCE | 68.2958
2022 | summer | MOORPK_2_ACOBT1 | PLANT_TROUBLE | 50.5267
2022 | summer | MOORPK_2_ACOBT1 | TRANSMISSION_INDUCED | 0
2022 | summer | MOORPK_2_CALABS | PLANT_MAINTENANCE | 169.725
2022 | summer | MOORPK_2_CALABS | PLANT_TROUBLE | 47.427
2022 | summer | MORWD_6_QF | PLANT_TROUBLE | 12.8
2022 | summer | MORWD_6_QF | TRANSMISSION_INDUCED | 48
2022 | summer | MOSSLD_2_PSP1 | AMBIENT_DUE_TO_TEMP | 1671.7667
2022 | summer | MOSSLD_2_PSP1 | ENVIRONMENTAL_RESTRICTIONS | 33.1667
2022 | summer | MOSSLD_2_PSP1 | PLANT_MAINTENANCE | 1980.5
2022 | summer | MOSSLD_2_PSP1 | PLANT_TROUBLE | 10570.6667
2022 | summer | MOSSLD_2_PSP1 | UNIT_TESTING | 1782
2022 | summer | MOSSLD_2_PSP2 | AMBIENT_DUE_TO_TEMP | 1494.6167
2022 | summer | MOSSLD_2_PSP2 | ENVIRONMENTAL_RESTRICTIONS | 255.6667
2022 | summer | MOSSLD_2_PSP2 | PLANT_MAINTENANCE | 2550
2022 | summer | MOSSLD_2_PSP2 | PLANT_TROUBLE | 3123.5833
2022 | summer | MOSSLD_2_PSP2 | UNIT_TESTING | 406.6667
2022 | summer | MRCHNT_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 71801.8667
2022 | summer | MRCHNT_2_PL1X3 | PLANT_TROUBLE | 3265
2022 | summer | MRGT_6_MEF2 | PLANT_TROUBLE | 4.4
2022 | summer | MRGT_6_MMAREF | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | summer | MRGT_6_MMAREF | PLANT_TROUBLE | 63
2022 | summer | MRGT_6_TGEBT1 | PLANT_MAINTENANCE | 0
2022 | summer | MRGT_6_TGEBT1 | PLANT_TROUBLE | 7445.5
2022 | summer | MRLSDS_6_SOLAR1 | METERING_TELEMETRY | 75
2022 | summer | MRLSDS_6_SOLAR1 | PLANT_TROUBLE | 0.99667
2022 | summer | MRLSDS_6_SOLAR1 | TRANSMISSION_INDUCED | 75
2022 | summer | MRLSDS_6_SOLAR1 | UNIT_TESTING | 0
2022 | summer | MSOLAR_2_SOLAR1 | PLANT_MAINTENANCE | 247.5
2022 | summer | MSOLAR_2_SOLAR2 | METERING_TELEMETRY | 9.55
2022 | summer | MSOLAR_2_SOLAR2 | PLANT_MAINTENANCE | 1.66
2022 | summer | MSOLAR_2_SOLAR2 | PLANT_TROUBLE | 461.4575
2022 | summer | MSOLAR_2_SOLAR3 | PLANT_MAINTENANCE | 1604.5
2022 | summer | MSOLAR_2_SOLAR3 | PLANT_TROUBLE | 1621.9
2022 | summer | MSTANG_2_MTGBT1 | METERING_TELEMETRY | 25
2022 | summer | MSTANG_2_MTGBT1 | PLANT_MAINTENANCE | 119.5
2022 | summer | MSTANG_2_MTGBT1 | PLANT_TROUBLE | 3127.7082
2022 | summer | MSTANG_2_MTGBT1 | UNIT_TESTING | 0
2022 | summer | MSTANG_2_SOLAR | PLANT_MAINTENANCE | 480.8193
2022 | summer | MSTANG_2_SOLAR | UNIT_TESTING | 73.3333
2022 | summer | MSTANG_2_SOLAR3 | PLANT_MAINTENANCE | 648.7432
2022 | summer | MSTANG_2_SOLAR3 | PLANT_TROUBLE | 2273.8998
2022 | summer | MSTANG_2_SOLAR3 | UNIT_TESTING | 93.3333
2022 | summer | MSTANG_2_SOLAR4 | PLANT_MAINTENANCE | 398.9193
2022 | summer | MSTANG_2_SOLAR4 | PLANT_TROUBLE | 267
2022 | summer | MSTANG_2_SOLAR4 | UNIT_TESTING | 13.3333
2022 | summer | MTNPOS_1_UNIT | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 396.9427
2022 | summer | MTNPOS_1_UNIT | AMBIENT_DUE_TO_TEMP | 146.056
2022 | summer | MTNPOS_1_UNIT | METERING_TELEMETRY | 233.2
2022 | summer | MTNPOS_1_UNIT | PLANT_MAINTENANCE | 548.3667
2022 | summer | MTNPOS_1_UNIT | PLANT_TROUBLE | 7960.2947
2022 | summer | MTWIND_1_MVPWD1 | NEW_GENERATOR_TEST_ENERGY | 0
2022 | summer | MTWIND_1_MVPWD1 | PLANT_MAINTENANCE | 0
2022 | summer | MTWIND_1_UNIT 3 | AMBIENT_DUE_TO_TEMP | 1026.6563
2022 | summer | MTWIND_1_UNIT 3 | PLANT_TROUBLE | 6.688
2022 | summer | MURRAY_6_UNIT | PLANT_MAINTENANCE | 20.6
2022 | summer | MURRAY_6_UNIT | PLANT_TROUBLE | 0.68667
2022 | summer | NAROW1_2_UNIT | ENVIRONMENTAL_RESTRICTIONS | 1263.7167
2022 | summer | NAROW1_2_UNIT | PLANT_TROUBLE | 26
2022 | summer | NAROW1_2_UNIT | TRANSMISSION_INDUCED | 26
2022 | summer | NAROW2_2_UNIT | ENVIRONMENTAL_RESTRICTIONS | 27319.3
2022 | summer | NAROW2_2_UNIT | PLANT_TROUBLE | 23.46
2022 | summer | NAROW2_2_UNIT | TRANSMISSION_INDUCED | 0
2022 | summer | NAVYII_2_UNITS | TRANSMISSION_INDUCED | 310.5
2022 | summer | NCPA_7_GP1UN1 | TRANSMISSION_INDUCED | 583.425
2022 | summer | NCPA_7_GP1UN2 | TRANSMISSION_INDUCED | 627.4353
2022 | summer | NCPA_7_GP2UN3 | AMBIENT_NOT_DUE_TO_TEMP | 32451.3
2022 | summer | NCPA_7_GP2UN4 | PLANT_TROUBLE | 0
2022 | summer | NEENCH_6_SOLAR | PLANT_MAINTENANCE | 132
2022 | summer | NEENCH_6_SOLAR | PLANT_TROUBLE | 23.1633
2022 | summer | NGILAA_5_SDGDYN | AMBIENT_DUE_TO_TEMP | 3750
2022 | summer | NGILAA_5_SDGDYN | PLANT_TROUBLE | 248.7333
2022 | summer | NHOGAN_6_UNITS | TRANSMISSION_INDUCED | 0
2022 | summer | NWCSTL_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 8340
2022 | summer | NZWIND_2_WDSTR5 | PLANT_MAINTENANCE | 31.55
2022 | summer | NZWIND_2_WDSTR5 | PLANT_TROUBLE | 0
2022 | summer | NZWIND_6_CALWND | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | summer | NZWIND_6_CALWND | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | summer | NZWIND_6_WDSTR | PLANT_TROUBLE | 78.725
2022 | summer | NZWIND_6_WDSTR2 | PLANT_TROUBLE | 65.12
2022 | summer | NZWIND_6_WDSTR3 | PLANT_TROUBLE | 61.76
2022 | summer | NZWIND_6_WDSTR4 | PLANT_TROUBLE | 0
2022 | summer | OAK C_7_UNIT 1 | AMBIENT_DUE_TO_TEMP | 25.2917
2022 | summer | OAK C_7_UNIT 1 | ENVIRONMENTAL_RESTRICTIONS | 2025
2022 | summer | OAK C_7_UNIT 1 | PLANT_MAINTENANCE | 135
2022 | summer | OAK C_7_UNIT 1 | PLANT_TROUBLE | 21711.5083
2022 | summer | OAK C_7_UNIT 3 | AMBIENT_DUE_TO_TEMP | 294.4
2022 | summer | OAK C_7_UNIT 3 | ENVIRONMENTAL_RESTRICTIONS | 34.8333
2022 | summer | OAK C_7_UNIT 3 | PLANT_MAINTENANCE | 54
2022 | summer | OAK C_7_UNIT 3 | PLANT_TROUBLE | 3680.9
2022 | summer | OAK C_7_UNIT 3 | TRANSMISSION_INDUCED | 49.5
2022 | summer | OASIS_6_CREST | PLANT_TROUBLE | 12.875
2022 | summer | OASIS_6_GBDSR4 | PLANT_TROUBLE | 12.9
2022 | summer | OASIS_6_LPPSR1 | PLANT_TROUBLE | 13.35
2022 | summer | OASIS_6_SOLAR2 | METERING_TELEMETRY | 8.925
2022 | summer | OASIS_6_SOLAR2 | PLANT_TROUBLE | 1126.0917
2022 | summer | OCTILO_5_WIND | PLANT_MAINTENANCE | 0
2022 | summer | OCTILO_5_WIND | PLANT_TROUBLE | 54725
2022 | summer | OGROVE_6_PL1X2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2022 | summer | OGROVE_6_PL1X2 | PLANT_TROUBLE | 0
2022 | summer | OILFLD_7_QFUNTS | AMBIENT_NOT_DUE_TO_TEMP | 2882.65
2022 | summer | OILFLD_7_QFUNTS | PLANT_MAINTENANCE | 0
2022 | summer | OLDRIV_6_CESDBM | PLANT_MAINTENANCE | 20
2022 | summer | OLDRIV_6_CESDBM | PLANT_TROUBLE | 3
2022 | summer | OLDRIV_6_LKVBM1 | PLANT_MAINTENANCE | 15
2022 | summer | OLDRIV_6_LKVBM1 | PLANT_TROUBLE | 1.3333
2022 | summer | OLDRV1_6_SOLAR | PLANT_TROUBLE | 0
2022 | summer | OLDRV1_6_SOLAR | TRANSMISSION_INDUCED | 100
2022 | summer | OLINDA_2_COYCRK | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 2394.45
2022 | summer | OLINDA_2_LNDFL2 | AMBIENT_DUE_TO_TEMP | 1089.5
2022 | summer | OLINDA_2_LNDFL2 | PLANT_MAINTENANCE | 201.9
2022 | summer | OLINDA_2_LNDFL2 | PLANT_TROUBLE | 95.3617
2022 | summer | OLIVEP_1_SOLAR | PLANT_MAINTENANCE | 10
2022 | summer | OLIVEP_1_SOLAR | PLANT_TROUBLE | 0
2022 | summer | OLIVEP_1_SOLAR | TRANSMISSION_INDUCED | 0
2022 | summer | OLIVEP_1_SOLAR2 | PLANT_TROUBLE | 0
2022 | summer | OLIVEP_1_SOLAR2 | TRANSMISSION_INDUCED | 0
2022 | summer | OLSEN_2_UNIT | TRANSMISSION_INDUCED | 82.5
2022 | summer | OMAR_2_UNIT 1 | PLANT_TROUBLE | 2250
2022 | summer | OMAR_2_UNIT 1 | UNIT_TESTING | 5.8333
2022 | summer | OMAR_2_UNIT 2 | PLANT_MAINTENANCE | 0
2022 | summer | OMAR_2_UNIT 2 | PLANT_TROUBLE | 185
2022 | summer | OMAR_2_UNIT 2 | UNIT_TESTING | 0
2022 | summer | OMAR_2_UNIT 3 | PLANT_MAINTENANCE | 3225
2022 | summer | OMAR_2_UNIT 3 | UNIT_TESTING | 5.8333
2022 | summer | OMAR_2_UNIT 4 | AMBIENT_DUE_TO_TEMP | 54.4
2022 | summer | OMAR_2_UNIT 4 | PLANT_TROUBLE | 1126.25
2022 | summer | OMAR_2_UNIT 4 | UNIT_TESTING | 9.1667
2022 | summer | ORLND_6_HIGHLI | PLANT_TROUBLE | 382.5
2022 | summer | ORMOND_7_UNIT 1 | AMBIENT_DUE_TO_TEMP | 4238.5167
2022 | summer | ORMOND_7_UNIT 1 | PLANT_MAINTENANCE | 6523.176
2022 | summer | ORMOND_7_UNIT 1 | PLANT_TROUBLE | 60478.4805
2022 | summer | ORMOND_7_UNIT 2 | AMBIENT_DUE_TO_TEMP | 2701.25
2022 | summer | ORMOND_7_UNIT 2 | PLANT_TROUBLE | 30547.6333
2022 | summer | ORMOND_7_UNIT 2 | TRANSMISSION_INDUCED | 3750
2022 | summer | OROLOM_1_SOLAR1 | TRANSMISSION_INDUCED | 0
2022 | summer | OROLOM_1_SOLAR2 | METERING_TELEMETRY | 0
2022 | summer | OROLOM_1_SOLAR2 | TRANSMISSION_INDUCED | 0
2022 | summer | OROVIL_6_UNIT | PLANT_MAINTENANCE | 348.15
2022 | summer | OROVIL_6_UNIT | PLANT_TROUBLE | 3184.05
2022 | summer | OROVIL_6_UNIT | TRANSMISSION_INDUCED | 0
2022 | summer | OTAY_6_ECVBT1 | TRANSMISSION_INDUCED | 369.35
2022 | summer | OTAY_6_ECVBT2 | TRANSMISSION_INDUCED | 2295
2022 | summer | OTAY_6_PL1X2 | AMBIENT_DUE_TO_TEMP | 4.78
2022 | summer | OTAY_6_PL1X2 | PLANT_TROUBLE | 563.8725
2022 | summer | OTAY_6_PL1X2 | UNIT_TESTING | 0
2022 | summer | OTMESA_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 29357.2
2022 | summer | OTMESA_2_PL1X3 | PLANT_MAINTENANCE | 4218.4
2022 | summer | OTMESA_2_PL1X3 | PLANT_TROUBLE | 39206.05
2022 | summer | OTMESA_2_PL1X3 | UNIT_TESTING | 30
2022 | summer | OXBOW_6_DRUM | PLANT_TROUBLE | 40.6
2022 | summer | OXBOW_6_DRUM | TRANSMISSION_INDUCED | 684.4
2022 | summer | OXMTN_6_LNDFIL | PLANT_MAINTENANCE | 74.6177
2022 | summer | OXMTN_6_LNDFIL | PLANT_TROUBLE | 258.9742
2022 | summer | OXMTN_6_LNDFIL | TRANSMISSION_INDUCED | 112.041
2022 | summer | PACLUM_6_UNIT | PLANT_MAINTENANCE | 60.5
2022 | summer | PACLUM_6_UNIT | PLANT_TROUBLE | 5483.4
2022 | summer | PACLUM_6_UNIT | TRANSMISSION_INDUCED | 44
2022 | summer | PADUA_2_ONTARO | AMBIENT_NOT_DUE_TO_TEMP | 582.3
2022 | summer | PADUA_2_ONTARO | PLANT_TROUBLE | 343
2022 | summer | PADUA_2_ONTARO | TRANSMISSION_INDUCED | 2
2022 | summer | PADUA_6_MWDSDM | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 49.5
2022 | summer | PALALT_7_COBUG | PLANT_TROUBLE | 3442.5
2022 | summer | PALOMR_2_PL1X3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1191.05
2022 | summer | PALOMR_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 58.0867
2022 | summer | PALOMR_2_PL1X3 | PLANT_TROUBLE | 3738.9243
2022 | summer | PARDEB_6_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 2980.5
2022 | summer | PARDEB_6_UNITS | PLANT_MAINTENANCE | 350
2022 | summer | PARDEB_6_UNITS | PLANT_TROUBLE | 180
2022 | summer | PARDEB_6_UNITS | TRANSMISSION_INDUCED | 335
2022 | summer | PBLOSM_2_SOLAR | PLANT_TROUBLE | 133
2022 | summer | PBLOSM_2_SOLAR | TRANSMISSION_INDUCED | 217.3917
2022 | summer | PEABDY_2_LNDFIL | PLANT_MAINTENANCE | 0
2022 | summer | PEABDY_2_LNDFIL | PLANT_TROUBLE | 32
2022 | summer | PEABDY_2_LNDFIL | TRANSMISSION_INDUCED | 4.8
2022 | summer | PEABDY_2_LNDFL1 | AMBIENT_DUE_TO_TEMP | 250.6683
2022 | summer | PEABDY_2_LNDFL1 | AMBIENT_NOT_DUE_TO_TEMP | 40.1
2022 | summer | PEABDY_2_LNDFL1 | PLANT_MAINTENANCE | 43.4983
2022 | summer | PEABDY_2_LNDFL1 | PLANT_TROUBLE | 310.2033
2022 | summer | PEARBL_2_NSPIN | TRANSMISSION_INDUCED | 2419
2022 | summer | PEASE_1_TBEBT1 | METERING_TELEMETRY | 75
2022 | summer | PEASE_1_TBEBT1 | PLANT_TROUBLE | 490.7
2022 | summer | PGCC_1_PDRP06 | SHORT_TERM_USE_LIMIT_REACHED | 1.7
2022 | summer | PGCC_1_PDRP07 | SHORT_TERM_USE_LIMIT_REACHED | 0.65
2022 | summer | PGCC_1_PDRP09 | SHORT_TERM_USE_LIMIT_REACHED | 6.05
2022 | summer | PGCC_1_PDRP16 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | PGCC_1_PDRP19 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | PGCC_1_PDRP20 | SHORT_TERM_USE_LIMIT_REACHED | 49.95
2022 | summer | PGCC_1_PDRP37 | OTHER_USE_LIMIT_REACHED | 3.3
2022 | summer | PGEB_2_PDRP106 | OTHER_USE_LIMIT_REACHED | 21.1
2022 | summer | PGEB_2_PDRP12 | SHORT_TERM_USE_LIMIT_REACHED | 3.4
2022 | summer | PGEB_2_PDRP13 | SHORT_TERM_USE_LIMIT_REACHED | 3.9
2022 | summer | PGEB_2_PDRP14 | SHORT_TERM_USE_LIMIT_REACHED | 1.65
2022 | summer | PGEB_2_PDRP15 | SHORT_TERM_USE_LIMIT_REACHED | 60.64
2022 | summer | PGEB_2_PDRP16 | SHORT_TERM_USE_LIMIT_REACHED | 1.8
2022 | summer | PGEB_2_PDRP60 | SHORT_TERM_USE_LIMIT_REACHED | 49.95
2022 | summer | PGEB_2_PDRP62 | SHORT_TERM_USE_LIMIT_REACHED | 49.95
2022 | summer | PGEB_2_PDRP67 | SHORT_TERM_USE_LIMIT_REACHED | 49.95
2022 | summer | PGEB_2_PDRP68 | SHORT_TERM_USE_LIMIT_REACHED | 49.95
2022 | summer | PGEB_2_PDRP69 | SHORT_TERM_USE_LIMIT_REACHED | 49.95
2022 | summer | PGF1_2_PDRP05 | SHORT_TERM_USE_LIMIT_REACHED | 5.85
2022 | summer | PGF1_2_PDRP06 | SHORT_TERM_USE_LIMIT_REACHED | 28.65
2022 | summer | PGF1_2_PDRP102 | OTHER_USE_LIMIT_REACHED | 18.7
2022 | summer | PGF1_2_PDRP12 | SHORT_TERM_USE_LIMIT_REACHED | 30.1
2022 | summer | PGF1_2_PDRP13 | SHORT_TERM_USE_LIMIT_REACHED | 50.96
2022 | summer | PGF1_2_PDRP14 | SHORT_TERM_USE_LIMIT_REACHED | 19.05
2022 | summer | PGF1_2_PDRP15 | SHORT_TERM_USE_LIMIT_REACHED | 0.6
2022 | summer | PGF1_2_PDRP60 | SHORT_TERM_USE_LIMIT_REACHED | 49.95
2022 | summer | PGF1_2_PDRP61 | SHORT_TERM_USE_LIMIT_REACHED | 49.95
2022 | summer | PGF1_2_PDRP63 | SHORT_TERM_USE_LIMIT_REACHED | 49.95
2022 | summer | PGF1_2_PDRP74 | SHORT_TERM_USE_LIMIT_REACHED | 49.95
2022 | summer | PGF1_2_PDRP75 | SHORT_TERM_USE_LIMIT_REACHED | 49.95
2022 | summer | PGFG_1_PDRP07 | SHORT_TERM_USE_LIMIT_REACHED | 0.55
2022 | summer | PGFG_1_PDRP10 | SHORT_TERM_USE_LIMIT_REACHED | 5.36
2022 | summer | PGFG_1_PDRP20 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | PGFG_1_PDRP39 | OTHER_USE_LIMIT_REACHED | 3
2022 | summer | PGHB_6_PDRP03 | SHORT_TERM_USE_LIMIT_REACHED | 4.3
2022 | summer | PGHB_6_PDRP11 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | PGKN_2_PDRP03 | SHORT_TERM_USE_LIMIT_REACHED | 1.5
2022 | summer | PGKN_2_PDRP04 | SHORT_TERM_USE_LIMIT_REACHED | 20.35
2022 | summer | PGKN_2_PDRP05 | SHORT_TERM_USE_LIMIT_REACHED | 5.05
2022 | summer | PGKN_2_PDRP10 | SHORT_TERM_USE_LIMIT_REACHED | 20.16
2022 | summer | PGKN_2_PDRP24 | SHORT_TERM_USE_LIMIT_REACHED | 49.95
2022 | summer | PGKN_2_PDRP45 | OTHER_USE_LIMIT_REACHED | 9.25
2022 | summer | PGNB_2_PDRP06 | SHORT_TERM_USE_LIMIT_REACHED | 0.55
2022 | summer | PGNB_2_PDRP07 | SHORT_TERM_USE_LIMIT_REACHED | 0.55
2022 | summer | PGNB_2_PDRP08 | SHORT_TERM_USE_LIMIT_REACHED | 8.55
2022 | summer | PGNB_2_PDRP10 | SHORT_TERM_USE_LIMIT_REACHED | 3.92
2022 | summer | PGNB_2_PDRP13 | SHORT_TERM_USE_LIMIT_REACHED | 0.55
2022 | summer | PGNB_2_PDRP19 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | PGNB_2_PDRP20 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | PGNB_2_PDRP21 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | PGNB_2_PDRP25 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | PGNB_2_PDRP39 | OTHER_USE_LIMIT_REACHED | 7.15
2022 | summer | PGNC_1_PDRP02 | SHORT_TERM_USE_LIMIT_REACHED | 1.76
2022 | summer | PGNC_1_PDRP09 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | PGNC_1_PDRP17 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | PGNP_2_PDRP03 | SHORT_TERM_USE_LIMIT_REACHED | 0.65
2022 | summer | PGNP_2_PDRP04 | SHORT_TERM_USE_LIMIT_REACHED | 7.15
2022 | summer | PGNP_2_PDRP05 | SHORT_TERM_USE_LIMIT_REACHED | 1.4
2022 | summer | PGNP_2_PDRP06 | SHORT_TERM_USE_LIMIT_REACHED | 8.3
2022 | summer | PGNP_2_PDRP07 | SHORT_TERM_USE_LIMIT_REACHED | 47.84
2022 | summer | PGNP_2_PDRP12 | SHORT_TERM_USE_LIMIT_REACHED | 0.55
2022 | summer | PGNP_2_PDRP30 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | PGNP_2_PDRP31 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | PGNP_2_PDRP34 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | PGNP_2_PDRP40 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | PGNP_2_PDRP41 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | PGNP_2_PDRP42 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | PGNP_2_PDRP51 | OTHER_USE_LIMIT_REACHED | 12.75
2022 | summer | PGP2_2_PDRP09 | SHORT_TERM_USE_LIMIT_REACHED | 0.55
2022 | summer | PGP2_2_PDRP11 | SHORT_TERM_USE_LIMIT_REACHED | 11.12
2022 | summer | PGP2_2_PDRP12 | SHORT_TERM_USE_LIMIT_REACHED | 0.55
2022 | summer | PGP2_2_PDRP35 | SHORT_TERM_USE_LIMIT_REACHED | 49.95
2022 | summer | PGP2_2_PDRP59 | OTHER_USE_LIMIT_REACHED | 5.2
2022 | summer | PGP2_2_PDRP65 | SHORT_TERM_USE_LIMIT_REACHED | 49.95
2022 | summer | PGSB_1_PDRP100 | OTHER_USE_LIMIT_REACHED | 14.7
2022 | summer | PGSB_1_PDRP15 | SHORT_TERM_USE_LIMIT_REACHED | 4.2
2022 | summer | PGSB_1_PDRP18 | SHORT_TERM_USE_LIMIT_REACHED | 4.6
2022 | summer | PGSB_1_PDRP19 | SHORT_TERM_USE_LIMIT_REACHED | 0.85
2022 | summer | PGSB_1_PDRP24 | SHORT_TERM_USE_LIMIT_REACHED | 16.4
2022 | summer | PGSB_1_PDRP60 | SHORT_TERM_USE_LIMIT_REACHED | 49.95
2022 | summer | PGSB_1_PDRP64 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | PGSB_1_PDRP66 | SHORT_TERM_USE_LIMIT_REACHED | 49.95
2022 | summer | PGSB_1_PDRP67 | SHORT_TERM_USE_LIMIT_REACHED | 49.95
2022 | summer | PGSF_2_PDRP13 | SHORT_TERM_USE_LIMIT_REACHED | 0.65
2022 | summer | PGSF_2_PDRP15 | SHORT_TERM_USE_LIMIT_REACHED | 1.55
2022 | summer | PGSF_2_PDRP34 | SHORT_TERM_USE_LIMIT_REACHED | 49.95
2022 | summer | PGSF_2_PDRP35 | SHORT_TERM_USE_LIMIT_REACHED | 49.95
2022 | summer | PGSF_2_PDRP37 | SHORT_TERM_USE_LIMIT_REACHED | 49.95
2022 | summer | PGSF_2_PDRP38 | SHORT_TERM_USE_LIMIT_REACHED | 49.95
2022 | summer | PGSF_2_PDRP46 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | PGSF_2_PDRP55 | OTHER_USE_LIMIT_REACHED | 3.25
2022 | summer | PGSI_1_PDRP04 | SHORT_TERM_USE_LIMIT_REACHED | 0.9
2022 | summer | PGSI_1_PDRP05 | SHORT_TERM_USE_LIMIT_REACHED | 0.6
2022 | summer | PGSI_1_PDRP08 | SHORT_TERM_USE_LIMIT_REACHED | 1.3
2022 | summer | PGSI_1_PDRP13 | SHORT_TERM_USE_LIMIT_REACHED | 53.52
2022 | summer | PGSI_1_PDRP14 | SHORT_TERM_USE_LIMIT_REACHED | 0.7
2022 | summer | PGSI_1_PDRP18 | SHORT_TERM_USE_LIMIT_REACHED | 2.55
2022 | summer | PGSI_1_PDRP48 | SHORT_TERM_USE_LIMIT_REACHED | 49.95
2022 | summer | PGSI_1_PDRP50 | OTHER_USE_LIMIT_REACHED | 9.85
2022 | summer | PGST_2_PDRP02 | SHORT_TERM_USE_LIMIT_REACHED | 0.9
2022 | summer | PGST_2_PDRP04 | SHORT_TERM_USE_LIMIT_REACHED | 3.5
2022 | summer | PGST_2_PDRP05 | SHORT_TERM_USE_LIMIT_REACHED | 25.68
2022 | summer | PGST_2_PDRP06 | SHORT_TERM_USE_LIMIT_REACHED | 10.55
2022 | summer | PGST_2_PDRP24 | OTHER_USE_LIMIT_REACHED | 3.3
2022 | summer | PGST_2_PDRP39 | SHORT_TERM_USE_LIMIT_REACHED | 49.95
2022 | summer | PGZP_2_PDRP01 | SHORT_TERM_USE_LIMIT_REACHED | 9.9
2022 | summer | PGZP_2_PDRP03 | SHORT_TERM_USE_LIMIT_REACHED | 31.1
2022 | summer | PGZP_2_PDRP04 | SHORT_TERM_USE_LIMIT_REACHED | 28.5
2022 | summer | PGZP_2_PDRP05 | SHORT_TERM_USE_LIMIT_REACHED | 10.05
2022 | summer | PGZP_2_PDRP13 | SHORT_TERM_USE_LIMIT_REACHED | 7.2
2022 | summer | PGZP_2_PDRP24 | SHORT_TERM_USE_LIMIT_REACHED | 49.95
2022 | summer | PGZP_2_PDRP34 | SHORT_TERM_USE_LIMIT_REACHED | 49.95
2022 | summer | PGZP_2_PDRP35 | SHORT_TERM_USE_LIMIT_REACHED | 49.95
2022 | summer | PGZP_2_PDRP47 | OTHER_USE_LIMIT_REACHED | 3.3
2022 | summer | PHOENX_1_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | summer | PHOENX_1_UNIT | PLANT_TROUBLE | 15.1333
2022 | summer | PHOENX_1_UNIT | TRANSMISSION_INDUCED | 12.1333
2022 | summer | PINFLT_7_UNITS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 35496.7
2022 | summer | PINFLT_7_UNITS | AMBIENT_DUE_TO_TEMP | 9193.4833
2022 | summer | PINFLT_7_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 41295.45
2022 | summer | PINFLT_7_UNITS | METERING_TELEMETRY | 28429.536
2022 | summer | PIOPIC_2_CTG1 | AMBIENT_DUE_TO_TEMP | 5661.36
2022 | summer | PIOPIC_2_CTG1 | PLANT_MAINTENANCE | 0
2022 | summer | PIOPIC_2_CTG1 | PLANT_TROUBLE | 90.1087
2022 | summer | PIOPIC_2_CTG2 | AMBIENT_DUE_TO_TEMP | 4785.74
2022 | summer | PIOPIC_2_CTG2 | PLANT_MAINTENANCE | 112.7
2022 | summer | PIOPIC_2_CTG2 | PLANT_TROUBLE | 91.1297
2022 | summer | PIOPIC_2_CTG3 | AMBIENT_DUE_TO_TEMP | 5206.92
2022 | summer | PIOPIC_2_CTG3 | PLANT_TROUBLE | 728.2695
2022 | summer | PIT1_6_FRIVRA | PLANT_MAINTENANCE | 1.225
2022 | summer | PIT1_6_FRIVRA | PLANT_TROUBLE | 0
2022 | summer | PIT1_6_FRIVRA | TRANSMISSION_INDUCED | 0
2022 | summer | PIT1_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 34
2022 | summer | PIT1_7_UNIT 1 | PLANT_TROUBLE | 1120
2022 | summer | PIT1_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 137.0333
2022 | summer | PIT1_7_UNIT 2 | TRANSMISSION_INDUCED | 52.5
2022 | summer | PIT3_7_PL1X3 | AMBIENT_DUE_TO_TEMP | 8.51
2022 | summer | PIT3_7_PL1X3 | AMBIENT_NOT_DUE_TO_TEMP | 326.28
2022 | summer | PIT3_7_PL1X3 | PLANT_MAINTENANCE | 3024.0667
2022 | summer | PIT3_7_PL1X3 | PLANT_TROUBLE | 174.2
2022 | summer | PIT4_7_PL1X2 | AMBIENT_DUE_TO_TEMP | 4.7
2022 | summer | PIT4_7_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 587.4667
2022 | summer | PIT4_7_PL1X2 | PLANT_TROUBLE | 0
2022 | summer | PIT4_7_PL1X2 | TRANSMISSION_INDUCED | 346.75
2022 | summer | PIT5_7_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 558.4
2022 | summer | PIT5_7_PL3X4 | AMBIENT_NOT_DUE_TO_TEMP | 434.5467
2022 | summer | PIT5_7_PL3X4 | PLANT_TROUBLE | 203.0667
2022 | summer | PIT6_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 832.4205
2022 | summer | PIT6_7_UNIT 1 | TRANSMISSION_INDUCED | 0
2022 | summer | PIT6_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 1513.8995
2022 | summer | PIT6_7_UNIT 2 | TRANSMISSION_INDUCED | 0
2022 | summer | PIT7_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 1090.2088
2022 | summer | PIT7_7_UNIT 1 | METERING_TELEMETRY | 0
2022 | summer | PIT7_7_UNIT 1 | PLANT_MAINTENANCE | 0
2022 | summer | PIT7_7_UNIT 1 | PLANT_TROUBLE | 0
2022 | summer | PIT7_7_UNIT 1 | TRANSMISSION_INDUCED | 1390.25
2022 | summer | PIT7_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 296.352
2022 | summer | PIT7_7_UNIT 2 | METERING_TELEMETRY | 0
2022 | summer | PIT7_7_UNIT 2 | PLANT_MAINTENANCE | 8341.97
2022 | summer | PIT7_7_UNIT 2 | RTU_RIG | 0.91
2022 | summer | PIUTE_6_GNBSR1 | PLANT_TROUBLE | 24.25
2022 | summer | PLACVL_1_CHILIB | PLANT_MAINTENANCE | 58.38
2022 | summer | PLACVL_1_CHILIB | PLANT_TROUBLE | 46.565
2022 | summer | PLACVL_1_CHILIB | TRANSMISSION_INDUCED | 0
2022 | summer | PLAINV_6_BSOLAR | AMBIENT_NOT_DUE_TO_TEMP | 84
2022 | summer | PLAINV_6_BSOLAR | PLANT_MAINTENANCE | 40
2022 | summer | PLAINV_6_BSOLAR | PLANT_TROUBLE | 934.9167
2022 | summer | PLAINV_6_DSOLAR | PLANT_TROUBLE | 47
2022 | summer | PLAINV_6_NLRSR1 | PLANT_TROUBLE | 1922.85
2022 | summer | PLAINV_6_SOLAR3 | PLANT_MAINTENANCE | 2
2022 | summer | PLAINV_6_SOLAR3 | PLANT_TROUBLE | 1640.6083
2022 | summer | PLAINV_6_SOLARC | PLANT_MAINTENANCE | 0
2022 | summer | PLAINV_6_SOLARC | PLANT_TROUBLE | 157.3333
2022 | summer | PLMSSR_6_HISIER | PLANT_MAINTENANCE | 164.45
2022 | summer | PLMSSR_6_HISIER | PLANT_TROUBLE | 35.4813
2022 | summer | PLMSSR_6_HISIER | TRANSMISSION_INDUCED | 284
2022 | summer | PLSNTG_7_LNCLND | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 6.7093
2022 | summer | PLSNTG_7_LNCLND | PLANT_TROUBLE | 112.4433
2022 | summer | PMDLET_6_SOLAR1 | METERING_TELEMETRY | 175
2022 | summer | PMDLET_6_SOLAR1 | PLANT_TROUBLE | 383.8333
2022 | summer | PMDLET_6_SOLAR1 | TRANSMISSION_INDUCED | 0
2022 | summer | PNCHEG_2_PL1X4 | AMBIENT_DUE_TO_TEMP | 19265.29
2022 | summer | PNCHEG_2_PL1X4 | PLANT_MAINTENANCE | 2949.6533
2022 | summer | PNCHEG_2_PL1X4 | PLANT_TROUBLE | 10404.3167
2022 | summer | PNCHEG_2_PL1X4 | TRANSMISSION_INDUCED | 0
2022 | summer | PNCHPP_1_PL1X2 | AMBIENT_DUE_TO_TEMP | 10282.1
2022 | summer | PNCHPP_1_PL1X2 | METERING_TELEMETRY | 1931
2022 | summer | PNCHPP_1_PL1X2 | PLANT_MAINTENANCE | 0
2022 | summer | PNCHPP_1_PL1X2 | PLANT_TROUBLE | 746.8
2022 | summer | PNCHVS_2_SOLAR | PLANT_MAINTENANCE | 14.9545
2022 | summer | PNCHVS_2_SOLAR | PLANT_TROUBLE | 60
2022 | summer | PNOCHE_1_PL1X2 | AMBIENT_DUE_TO_TEMP | 1502.5858
2022 | summer | PNOCHE_1_PL1X2 | PLANT_TROUBLE | 394.2403
2022 | summer | PNOCHE_1_PL1X2 | TRANSMISSION_INDUCED | 141.5817
2022 | summer | PNOCHE_1_UNITA1 | AMBIENT_DUE_TO_TEMP | 360
2022 | summer | PNOCHE_1_UNITA1 | PLANT_MAINTENANCE | 0
2022 | summer | PNOCHE_1_UNITA1 | PLANT_TROUBLE | 354.9933
2022 | summer | PNOCHE_1_UNITA1 | UNIT_TESTING | 16
2022 | summer | POEPH_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 28283.1288
2022 | summer | POEPH_7_UNIT 1 | PLANT_TROUBLE | 0
2022 | summer | POEPH_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 22653.674
2022 | summer | POEPH_7_UNIT 2 | PLANT_TROUBLE | 4812.55
2022 | summer | POEPH_7_UNIT 2 | TRANSMISSION_INDUCED | 1.5
2022 | summer | POTTER_6_UNITS | PLANT_MAINTENANCE | 7726.5
2022 | summer | PRCTVY_1_MIGBT1 | PLANT_MAINTENANCE | 10
2022 | summer | PRCTVY_1_MIGBT1 | PLANT_TROUBLE | 577.3
2022 | summer | PRIMM_2_SOLAR1 | PLANT_TROUBLE | 164.45
2022 | summer | PUTHCR_1_PCNSB1 | NEW_GENERATOR_TEST_ENERGY | 0
2022 | summer | PUTHCR_1_PCNSB1 | PLANT_MAINTENANCE | 0
2022 | summer | PWEST_1_UNIT | PLANT_TROUBLE | 1606.5
2022 | summer | RAMON_2_SCEDYN | AMBIENT_NOT_DUE_TO_TEMP | 36721.7
2022 | summer | RATSKE_2_NROSR1 | PLANT_MAINTENANCE | 75
2022 | summer | RATSKE_2_NROSR1 | PLANT_TROUBLE | 1100
2022 | summer | RATSKE_2_RBSSB1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 747.9333
2022 | summer | RATSKE_2_RBSSB1 | PLANT_MAINTENANCE | 0
2022 | summer | RATSKE_2_RBSSB1 | UNIT_TESTING | 30
2022 | summer | RATSKE_2_RBSSB2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 482.6667
2022 | summer | RATSKE_2_RBSSB2 | NEW_GENERATOR_TEST_ENERGY | 0
2022 | summer | RATSKE_2_RBSSB2 | PLANT_MAINTENANCE | 0
2022 | summer | RATSKE_2_RBSSB2 | PLANT_TROUBLE | 15
2022 | summer | RATSKE_2_RBSSB2 | UNIT_TESTING | 20
2022 | summer | RCKCRK_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 14640.2443
2022 | summer | RCKCRK_7_UNIT 1 | PLANT_TROUBLE | 0
2022 | summer | RCKCRK_7_UNIT 1 | TRANSMISSION_INDUCED | 139.65
2022 | summer | RCKCRK_7_UNIT 1 | UNIT_TESTING | 0
2022 | summer | RCKCRK_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 22242.685
2022 | summer | RCKCRK_7_UNIT 2 | TRANSMISSION_INDUCED | 139.405
2022 | summer | RECTOR_2_CREST | PLANT_TROUBLE | 4.55
2022 | summer | RECTOR_2_KAWEAH | AMBIENT_NOT_DUE_TO_TEMP | 3408
2022 | summer | RECTOR_2_KAWEAH | PLANT_MAINTENANCE | 15
2022 | summer | RECTOR_2_KAWEAH | TRANSMISSION_INDUCED | 7
2022 | summer | RECTOR_2_KAWH 1 | AMBIENT_NOT_DUE_TO_TEMP | 1121.25
2022 | summer | RECTOR_2_KAWH 1 | PLANT_MAINTENANCE | 0
2022 | summer | RECTOR_2_KAWH 1 | PLANT_TROUBLE | 348.75
2022 | summer | RECTOR_2_QF | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 10245.9
2022 | summer | RECTOR_2_QF | PLANT_TROUBLE | 301.35
2022 | summer | RECTOR_2_TFDBM1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 35.0667
2022 | summer | RECTOR_2_TFDBM1 | PLANT_MAINTENANCE | 1.4
2022 | summer | RECTOR_2_TFDBM1 | PLANT_TROUBLE | 44.2667
2022 | summer | REDBLF_6_UNIT | TRANSMISSION_INDUCED | 0
2022 | summer | REDOND_7_UNIT 5 | AMBIENT_DUE_TO_TEMP | 579.0637
2022 | summer | REDOND_7_UNIT 5 | AMBIENT_NOT_DUE_TO_TEMP | 178.7243
2022 | summer | REDOND_7_UNIT 5 | PLANT_TROUBLE | 11974.6297
2022 | summer | REDOND_7_UNIT 5 | UNIT_SUPPORTING_STARTUP | 295.9175
2022 | summer | REDOND_7_UNIT 5 | UNIT_TESTING | 0
2022 | summer | REDOND_7_UNIT 6 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 871.45
2022 | summer | REDOND_7_UNIT 6 | AMBIENT_DUE_TO_TEMP | 2618.146
2022 | summer | REDOND_7_UNIT 6 | PLANT_TROUBLE | 5580.895
2022 | summer | REDOND_7_UNIT 6 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 522.87
2022 | summer | REDOND_7_UNIT 6 | UNIT_SUPPORTING_STARTUP | 614.1983
2022 | summer | REDOND_7_UNIT 6 | UNIT_TESTING | 0
2022 | summer | REDOND_7_UNIT 8 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 2463.3333
2022 | summer | REDOND_7_UNIT 8 | AMBIENT_DUE_TO_TEMP | 4126.3333
2022 | summer | REDOND_7_UNIT 8 | AMBIENT_NOT_DUE_TO_TEMP | 180
2022 | summer | REDOND_7_UNIT 8 | PLANT_TROUBLE | 7530
2022 | summer | REDOND_7_UNIT 8 | UNIT_TESTING | 0
2022 | summer | RENWD_1_QF | PLANT_MAINTENANCE | 483.2
2022 | summer | RENWD_1_QF | PLANT_TROUBLE | 202.5
2022 | summer | RICHMN_1_CHVSR2 | ENVIRONMENTAL_RESTRICTIONS | 36.125
2022 | summer | RICHMN_1_CHVSR2 | PLANT_TROUBLE | 59.6417
2022 | summer | RICHMN_1_SOLAR | ENVIRONMENTAL_RESTRICTIONS | 8.5
2022 | summer | RICHMN_1_SOLAR | PLANT_TROUBLE | 20
2022 | summer | RICHMN_1_SOLAR | TRANSMISSION_INDUCED | 1.1333
2022 | summer | RICHMN_7_BAYENV | AMBIENT_NOT_DUE_TO_TEMP | 1912.5
2022 | summer | RIOBRV_6_UNIT 1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 5740
2022 | summer | RIOBRV_6_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | summer | RIOBRV_6_UNIT 1 | PLANT_TROUBLE | 36.6333
2022 | summer | ROLLIN_6_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 2967.0777
2022 | summer | ROLLIN_6_UNIT | PLANT_TROUBLE | 29.3867
2022 | summer | ROSMDW_2_WIND1 | METERING_TELEMETRY | 2
2022 | summer | ROSMDW_2_WIND1 | PLANT_MAINTENANCE | 4143.4
2022 | summer | ROSMDW_2_WIND1 | PLANT_TROUBLE | 62.0667
2022 | summer | ROSMND_6_SOLAR | PLANT_TROUBLE | 314.375
2022 | summer | RSMSLR_6_SOLAR2 | METERING_TELEMETRY | 50
2022 | summer | RTEDDY_2_SEBSR4 | PLANT_MAINTENANCE | 140
2022 | summer | RTREE_2_WIND2 | PLANT_MAINTENANCE | 1582.9817
2022 | summer | RTREE_2_WIND2 | PLANT_TROUBLE | 6.6
2022 | summer | RUSCTY_2_UNITS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 59300.4333
2022 | summer | RUSCTY_2_UNITS | AMBIENT_DUE_TO_TEMP | 19152.4435
2022 | summer | RUSCTY_2_UNITS | METERING_TELEMETRY | 60.2
2022 | summer | RUSCTY_2_UNITS | PLANT_MAINTENANCE | 0
2022 | summer | RUSCTY_2_UNITS | PLANT_TROUBLE | 29528.3358
2022 | summer | RUSCTY_2_UNITS | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 369.3833
2022 | summer | RUSCTY_2_UNITS | UNIT_SUPPORTING_STARTUP | 0
2022 | summer | RUSCTY_2_UNITS | UNIT_TESTING | 609.699
2022 | summer | RVRVEW_1_UNITA1 | AMBIENT_DUE_TO_TEMP | 90.45
2022 | summer | RVRVEW_1_UNITA1 | PLANT_TROUBLE | 837.7467
2022 | summer | RVSIDE_2_RERCU3 | PLANT_TROUBLE | 0
2022 | summer | RVSIDE_2_RERCU4 | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | summer | RVSIDE_2_RERCU4 | PLANT_TROUBLE | 0
2022 | summer | RVSIDE_6_RERCU1 | PLANT_MAINTENANCE | 0
2022 | summer | RVSIDE_6_RERCU1 | PLANT_TROUBLE | 80.43
2022 | summer | RVSIDE_6_RERCU2 | PLANT_MAINTENANCE | 0
2022 | summer | RVSIDE_6_RERCU2 | PLANT_TROUBLE | 129.3333
2022 | summer | RVSIDE_6_SPRING | PLANT_TROUBLE | 61.6333
2022 | summer | SALIRV_2_UNIT | PLANT_MAINTENANCE | 0
2022 | summer | SALIRV_2_UNIT | PLANT_TROUBLE | 64.35
2022 | summer | SALTSP_7_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 53.0667
2022 | summer | SALTSP_7_UNITS | TRANSMISSION_INDUCED | 3111.1333
2022 | summer | SANBRN_2_ES1BT3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 786.708
2022 | summer | SANBRN_2_ES1BT3 | AMBIENT_NOT_DUE_TO_TEMP | 163.057
2022 | summer | SANBRN_2_ES1BT3 | PLANT_TROUBLE | 565.6565
2022 | summer | SANBRN_2_ES2SB3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1763.8
2022 | summer | SANBRN_2_ES2SB3 | AMBIENT_NOT_DUE_TO_TEMP | 175.7
2022 | summer | SANBRN_2_ES2SB3 | PLANT_TROUBLE | 450.1
2022 | summer | SANBRN_2_ESABT1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | summer | SANBRN_2_ESABT1 | METERING_TELEMETRY | 0
2022 | summer | SANBRN_2_ESABT1 | PLANT_MAINTENANCE | 0
2022 | summer | SANBRN_2_ESABT1 | PLANT_TROUBLE | 1325.8333
2022 | summer | SANBRN_2_ESABT1 | UNIT_TESTING | 0
2022 | summer | SANBRN_2_ESBBT1 | PLANT_MAINTENANCE | 0
2022 | summer | SANBRN_2_ESBBT1 | PLANT_TROUBLE | 361.3
2022 | summer | SANBRN_2_ESBBT1 | UNIT_TESTING | 600
2022 | summer | SANDLT_2_SUNITS | AMBIENT_NOT_DUE_TO_TEMP | 23170
2022 | summer | SANDLT_2_SUNITS | METERING_TELEMETRY | 687.5
2022 | summer | SANDLT_2_SUNITS | PLANT_MAINTENANCE | 2490
2022 | summer | SANDLT_2_SUNITS | PLANT_TROUBLE | 4051.1667
2022 | summer | SANLOB_1_LNDFIL | AMBIENT_DUE_TO_TEMP | 0
2022 | summer | SANLOB_1_LNDFIL | PLANT_MAINTENANCE | 22.5
2022 | summer | SANLOB_1_LNDFIL | PLANT_TROUBLE | 105.65
2022 | summer | SANLOB_1_LNDFIL | TRANSMISSION_INDUCED | 0
2022 | summer | SANLOB_1_LNDFIL | UNIT_TESTING | 0
2022 | summer | SANTFG_7_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 9266
2022 | summer | SANTFG_7_UNITS | PLANT_TROUBLE | 0
2022 | summer | SANTGO_2_LNDFL1 | AMBIENT_DUE_TO_TEMP | 207.5333
2022 | summer | SANTGO_2_LNDFL1 | PLANT_MAINTENANCE | 39
2022 | summer | SANTGO_2_LNDFL1 | PLANT_TROUBLE | 451.7
2022 | summer | SANTGO_2_MABBT1 | METERING_TELEMETRY | 120
2022 | summer | SANTGO_2_MABBT1 | PLANT_MAINTENANCE | 8.4
2022 | summer | SANTGO_2_MABBT1 | PLANT_TROUBLE | 186.325
2022 | summer | SANWD_1_QF | PLANT_MAINTENANCE | 3661.0118
2022 | summer | SANWD_1_QF | PLANT_TROUBLE | 217
2022 | summer | SAUGUS_7_CHIQCN | TRANSMISSION_INDUCED | 24
2022 | summer | SBERDO_2_PSP3 | AMBIENT_DUE_TO_TEMP | 20419.6535
2022 | summer | SBERDO_2_PSP3 | METERING_TELEMETRY | 940
2022 | summer | SBERDO_2_PSP3 | PLANT_MAINTENANCE | 5446.0865
2022 | summer | SBERDO_2_PSP3 | PLANT_TROUBLE | 4700.6533
2022 | summer | SBERDO_2_PSP3 | UNIT_TESTING | 0
2022 | summer | SBERDO_2_PSP4 | AMBIENT_DUE_TO_TEMP | 23660.19
2022 | summer | SBERDO_2_PSP4 | METERING_TELEMETRY | 929.5
2022 | summer | SBERDO_2_PSP4 | PLANT_TROUBLE | 6016.7622
2022 | summer | SBERDO_2_PSP4 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 375.2
2022 | summer | SBERDO_2_REDLND | PLANT_TROUBLE | 190
2022 | summer | SBERDO_2_SNTANA | AMBIENT_NOT_DUE_TO_TEMP | 1234.9
2022 | summer | SBERDO_2_SNTANA | PLANT_TROUBLE | 4081.85
2022 | summer | SBERDO_6_MILLCK | AMBIENT_NOT_DUE_TO_TEMP | 1583.4067
2022 | summer | SBERDO_6_MILLCK | PLANT_TROUBLE | 122.3
2022 | summer | SBERDO_6_MILLCK | TRANSMISSION_INDUCED | 0.6
2022 | summer | SCEC_1_PDRP107 | SHORT_TERM_USE_LIMIT_REACHED | 49.95
2022 | summer | SCEC_1_PDRP108 | SHORT_TERM_USE_LIMIT_REACHED | 49.95
2022 | summer | SCEC_1_PDRP109 | SHORT_TERM_USE_LIMIT_REACHED | 49.95
2022 | summer | SCEC_1_PDRP110 | SHORT_TERM_USE_LIMIT_REACHED | 49.95
2022 | summer | SCEC_1_PDRP124 | MONTHLY_USE_LIMIT_REACHED | 54.9
2022 | summer | SCEC_1_PDRP134 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | SCEC_1_PDRP138 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | SCEC_1_PDRP16 | MONTHLY_USE_LIMIT_REACHED | 2706.3
2022 | summer | SCEC_1_PDRP160 | SHORT_TERM_USE_LIMIT_REACHED | 49.95
2022 | summer | SCEC_1_PDRP161 | SHORT_TERM_USE_LIMIT_REACHED | 49.95
2022 | summer | SCEC_1_PDRP163 | SHORT_TERM_USE_LIMIT_REACHED | 49.95
2022 | summer | SCEC_1_PDRP17 | MONTHLY_USE_LIMIT_REACHED | 1803.8
2022 | summer | SCEC_1_PDRP171 | PLANT_TROUBLE | 20
2022 | summer | SCEC_1_PDRP173 | MONTHLY_USE_LIMIT_REACHED | 66.9
2022 | summer | SCEC_1_PDRP180 | OTHER_USE_LIMIT_REACHED | 49.5
2022 | summer | SCEC_1_PDRP60 | MONTHLY_USE_LIMIT_REACHED | 19.85
2022 | summer | SCEC_1_RDRR08 | OTHER_USE_LIMIT_REACHED | 335.4217
2022 | summer | SCEHOV_2_HOOVER | AMBIENT_NOT_DUE_TO_TEMP | 92474.8798
2022 | summer | SCEHOV_2_HOOVER | METERING_TELEMETRY | 0
2022 | summer | SCEHOV_2_HOOVER | MONTHLY_USE_LIMIT_REACHED | 287.01
2022 | summer | SCEHOV_2_HOOVER | OTHER_USE_LIMIT_REACHED | 1899.5
2022 | summer | SCEHOV_2_HOOVER | PLANT_TROUBLE | 5715.45
2022 | summer | SCEN_6_PDRP13 | MONTHLY_USE_LIMIT_REACHED | 242.15
2022 | summer | SCEN_6_PDRP28 | MONTHLY_USE_LIMIT_REACHED | 181.5
2022 | summer | SCEN_6_PDRP58 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | SCEN_6_PDRP59 | SHORT_TERM_USE_LIMIT_REACHED | 49.95
2022 | summer | SCEN_6_PDRP62 | SHORT_TERM_USE_LIMIT_REACHED | 49.95
2022 | summer | SCEN_6_PDRP65 | SHORT_TERM_USE_LIMIT_REACHED | 49.95
2022 | summer | SCEN_6_PDRP90 | OTHER_USE_LIMIT_REACHED | 18
2022 | summer | SCEN_6_RDRR02 | OTHER_USE_LIMIT_REACHED | 161.9667
2022 | summer | SCEW_2_PDRP03 | ANNUAL_USE_LIMIT_REACHED | 1675
2022 | summer | SCEW_2_PDRP09 | MONTHLY_USE_LIMIT_REACHED | 25
2022 | summer | SCEW_2_PDRP10 | MONTHLY_USE_LIMIT_REACHED | 37.5
2022 | summer | SCEW_2_PDRP106 | SHORT_TERM_USE_LIMIT_REACHED | 49.95
2022 | summer | SCEW_2_PDRP107 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | SCEW_2_PDRP108 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | SCEW_2_PDRP109 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | SCEW_2_PDRP110 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | SCEW_2_PDRP111 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | SCEW_2_PDRP112 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | SCEW_2_PDRP114 | MONTHLY_USE_LIMIT_REACHED | 161.75
2022 | summer | SCEW_2_PDRP117 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | SCEW_2_PDRP12 | MONTHLY_USE_LIMIT_REACHED | 397.3
2022 | summer | SCEW_2_PDRP123 | SHORT_TERM_USE_LIMIT_REACHED | 49.95
2022 | summer | SCEW_2_PDRP131 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | SCEW_2_PDRP159 | MONTHLY_USE_LIMIT_REACHED | 218.4
2022 | summer | SCEW_2_PDRP160 | MONTHLY_USE_LIMIT_REACHED | 137.4
2022 | summer | SCEW_2_PDRP163 | MONTHLY_USE_LIMIT_REACHED | 245.7
2022 | summer | SCEW_2_PDRP167 | MONTHLY_USE_LIMIT_REACHED | 282.6
2022 | summer | SCEW_2_PDRP170 | OTHER_USE_LIMIT_REACHED | 26
2022 | summer | SCEW_2_PDRP172 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | SCEW_2_PDRP173 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | SCEW_2_PDRP174 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | SCEW_2_PDRP35 | MONTHLY_USE_LIMIT_REACHED | 1006.95
2022 | summer | SCEW_2_PDRP85 | MONTHLY_USE_LIMIT_REACHED | 39.8
2022 | summer | SCEW_2_PDRP89 | MONTHLY_USE_LIMIT_REACHED | 40.35
2022 | summer | SCEW_2_RDRR08 | OTHER_USE_LIMIT_REACHED | 491.55
2022 | summer | SCHD_1_PDRP14 | MONTHLY_USE_LIMIT_REACHED | 139.15
2022 | summer | SCHD_1_PDRP48 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | SCHD_1_PDRP60 | OTHER_USE_LIMIT_REACHED | 6.5
2022 | summer | SCHD_1_PDRP61 | SHORT_TERM_USE_LIMIT_REACHED | 49.95
2022 | summer | SCHD_1_RDRR08 | OTHER_USE_LIMIT_REACHED | 252.3667
2022 | summer | SCHLTE_1_PL1X3 | AMBIENT_DUE_TO_TEMP | 25547.4433
2022 | summer | SCHNDR_1_FIVPTS | METERING_TELEMETRY | 1260
2022 | summer | SCHNDR_1_FIVPTS | PLANT_TROUBLE | 0
2022 | summer | SCHNDR_1_OS2BM2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 5.7333
2022 | summer | SCHNDR_1_OS2BM2 | PLANT_TROUBLE | 4
2022 | summer | SCHNDR_1_WSTSDE | PLANT_TROUBLE | 2590
2022 | summer | SCNW_6_PDRP05 | MONTHLY_USE_LIMIT_REACHED | 236.5
2022 | summer | SCNW_6_PDRP40 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | SCNW_6_PDRP41 | SHORT_TERM_USE_LIMIT_REACHED | 49.95
2022 | summer | SCNW_6_PDRP51 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | SCNW_6_PDRP57 | MONTHLY_USE_LIMIT_REACHED | 168
2022 | summer | SCNW_6_PDRP61 | MONTHLY_USE_LIMIT_REACHED | 513.4
2022 | summer | SCNW_6_PDRP70 | OTHER_USE_LIMIT_REACHED | 25
2022 | summer | SCNW_6_RDRR08 | OTHER_USE_LIMIT_REACHED | 28.25
2022 | summer | SDG1_1_PDRP100 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | SDG1_1_PDRP101 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | SDG1_1_PDRP102 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | SDG1_1_PDRP103 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | SDG1_1_PDRP105 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | SDG1_1_PDRP84 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | SDG1_1_PDRP85 | SHORT_TERM_USE_LIMIT_REACHED | 49.95
2022 | summer | SDG1_1_PDRP88 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | SDG1_1_PDRP91 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | SDG1_1_PDRP97 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | SDG1_1_PDRP98 | SHORT_TERM_USE_LIMIT_REACHED | 4.95
2022 | summer | SEARLS_7_ARGUS | METERING_TELEMETRY | 57
2022 | summer | SEGS_1_SR2SL2 | AMBIENT_NOT_DUE_TO_TEMP | 182.6667
2022 | summer | SEGS_1_SR2SL2 | PLANT_TROUBLE | 78
2022 | summer | SENTNL_2_CTG1 | AMBIENT_DUE_TO_TEMP | 3227.72
2022 | summer | SENTNL_2_CTG1 | PLANT_MAINTENANCE | 0
2022 | summer | SENTNL_2_CTG1 | PLANT_TROUBLE | 125.032
2022 | summer | SENTNL_2_CTG1 | UNIT_TESTING | 126.228
2022 | summer | SENTNL_2_CTG2 | AMBIENT_DUE_TO_TEMP | 4525.946
2022 | summer | SENTNL_2_CTG2 | PLANT_MAINTENANCE | 0
2022 | summer | SENTNL_2_CTG2 | PLANT_TROUBLE | 220.4207
2022 | summer | SENTNL_2_CTG2 | UNIT_TESTING | 153.34
2022 | summer | SENTNL_2_CTG3 | AMBIENT_DUE_TO_TEMP | 3331.1577
2022 | summer | SENTNL_2_CTG3 | AMBIENT_NOT_DUE_TO_TEMP | 16.58
2022 | summer | SENTNL_2_CTG3 | ENVIRONMENTAL_RESTRICTIONS | 1185.91
2022 | summer | SENTNL_2_CTG3 | PLANT_MAINTENANCE | 0
2022 | summer | SENTNL_2_CTG3 | PLANT_TROUBLE | 462.7563
2022 | summer | SENTNL_2_CTG3 | UNIT_TESTING | 188.4615
2022 | summer | SENTNL_2_CTG4 | AMBIENT_DUE_TO_TEMP | 3265.626
2022 | summer | SENTNL_2_CTG4 | PLANT_TROUBLE | 229.3307
2022 | summer | SENTNL_2_CTG4 | UNIT_TESTING | 174.16
2022 | summer | SENTNL_2_CTG5 | AMBIENT_DUE_TO_TEMP | 3237.81
2022 | summer | SENTNL_2_CTG5 | PLANT_MAINTENANCE | 0
2022 | summer | SENTNL_2_CTG5 | PLANT_TROUBLE | 231.4647
2022 | summer | SENTNL_2_CTG5 | UNIT_TESTING | 118.35
2022 | summer | SENTNL_2_CTG6 | AMBIENT_DUE_TO_TEMP | 3393.8437
2022 | summer | SENTNL_2_CTG6 | ENVIRONMENTAL_RESTRICTIONS | 86.377
2022 | summer | SENTNL_2_CTG6 | PLANT_MAINTENANCE | 0
2022 | summer | SENTNL_2_CTG6 | PLANT_TROUBLE | 3866.3382
2022 | summer | SENTNL_2_CTG6 | UNIT_TESTING | 177
2022 | summer | SENTNL_2_CTG7 | AMBIENT_DUE_TO_TEMP | 3247.274
2022 | summer | SENTNL_2_CTG7 | PLANT_TROUBLE | 229.7267
2022 | summer | SENTNL_2_CTG7 | UNIT_TESTING | 121.46
2022 | summer | SENTNL_2_CTG8 | AMBIENT_DUE_TO_TEMP | 3440.216
2022 | summer | SENTNL_2_CTG8 | PLANT_TROUBLE | 229.9907
2022 | summer | SGREGY_6_SANGER | AMBIENT_DUE_TO_TEMP | 33
2022 | summer | SGREGY_6_SANGER | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | summer | SGREGY_6_SANGER | ANNUAL_USE_LIMIT_REACHED | 12316.5
2022 | summer | SGREGY_6_SANGER | PLANT_MAINTENANCE | 648.025
2022 | summer | SGREGY_6_SANGER | UNIT_TESTING | 12.075
2022 | summer | SIERRA_1_UNITS | AMBIENT_DUE_TO_TEMP | 2104.15
2022 | summer | SIERRA_1_UNITS | PLANT_TROUBLE | 720.53
2022 | summer | SIERRA_1_UNITS | RTU_RIG | 13.65
2022 | summer | SIERRA_1_UNITS | UNIT_TESTING | 0
2022 | summer | SIGHEB_6_MIRDYN | PLANT_MAINTENANCE | 680
2022 | summer | SKERN_6_SOLAR1 | PLANT_TROUBLE | 21.3333
2022 | summer | SKERN_6_SOLAR2 | PLANT_TROUBLE | 150
2022 | summer | SLATE_2_SLASR1 | METERING_TELEMETRY | 0
2022 | summer | SLATE_2_SLASR1 | PLANT_MAINTENANCE | 0
2022 | summer | SLATE_2_SLASR1 | PLANT_TROUBLE | 1925.2875
2022 | summer | SLATE_2_SLASR2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 3118.625
2022 | summer | SLATE_2_SLASR2 | AMBIENT_DUE_TO_TEMP | 572.5833
2022 | summer | SLATE_2_SLASR2 | AMBIENT_NOT_DUE_TO_TEMP | 53
2022 | summer | SLATE_2_SLASR2 | METERING_TELEMETRY | 0
2022 | summer | SLATE_2_SLASR2 | PLANT_MAINTENANCE | 0
2022 | summer | SLATE_2_SLASR2 | PLANT_TROUBLE | 333.9092
2022 | summer | SLATE_2_SLASR3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1830.5333
2022 | summer | SLATE_2_SLASR3 | AMBIENT_DUE_TO_TEMP | 576.6667
2022 | summer | SLATE_2_SLASR3 | METERING_TELEMETRY | 0
2022 | summer | SLATE_2_SLASR3 | PLANT_MAINTENANCE | 0
2022 | summer | SLATE_2_SLASR3 | PLANT_TROUBLE | 825.375
2022 | summer | SLATE_2_SLASR4 | AMBIENT_NOT_DUE_TO_TEMP | 5268.1217
2022 | summer | SLATE_2_SLASR4 | METERING_TELEMETRY | 19.02
2022 | summer | SLATE_2_SLASR4 | PLANT_MAINTENANCE | 0
2022 | summer | SLATE_2_SLASR4 | PLANT_TROUBLE | 63
2022 | summer | SLATE_2_SLASR5 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 706.74
2022 | summer | SLATE_2_SLASR5 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 223.6503
2022 | summer | SLATE_2_SLASR5 | AMBIENT_DUE_TO_TEMP | 24.85
2022 | summer | SLATE_2_SLASR5 | AMBIENT_NOT_DUE_TO_TEMP | 499.0625
2022 | summer | SLATE_2_SLASR5 | AMBIENT_NOT_DUE_TO_TEMP | 73
2022 | summer | SLATE_2_SLASR5 | METERING_TELEMETRY | 16.6667
2022 | summer | SLATE_2_SLASR5 | METERING_TELEMETRY | 43.1097
2022 | summer | SLATE_2_SLASR5 | PLANT_MAINTENANCE | 0
2022 | summer | SLATE_2_SLASR5 | PLANT_MAINTENANCE | 0
2022 | summer | SLATE_2_SLASR5 | PLANT_TROUBLE | 685.6508
2022 | summer | SLATE_2_SLASR5 | PLANT_TROUBLE | 0
2022 | summer | SLATE_2_SLASR5 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2022 | summer | SLATE_2_SLASR5 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2022 | summer | SLATE_2_SLASR5 | UNIT_TESTING | 0
2022 | summer | SLRMS3_2_SRMSR1 | PLANT_TROUBLE | 0
2022 | summer | SLST13_2_SOLAR1 | PLANT_MAINTENANCE | 0
2022 | summer | SLST13_2_SOLAR1 | PLANT_TROUBLE | 406.5
2022 | summer | SLSTR1_2_SOLAR1 | PLANT_TROUBLE | 1335
2022 | summer | SLUISP_2_UNITS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 77508.535
2022 | summer | SLUISP_2_UNITS | METERING_TELEMETRY | 36.65
2022 | summer | SLUISP_2_UNITS | PLANT_TROUBLE | 1145.9167
2022 | summer | SLYCRK_1_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 891.46
2022 | summer | SLYCRK_1_UNIT 1 | PLANT_TROUBLE | 9
2022 | summer | SLYCRK_1_UNIT 1 | UNIT_TESTING | 0
2022 | summer | SMPRIP_1_SMPSON | PLANT_MAINTENANCE | 273.9975
2022 | summer | SMPRIP_1_SMPSON | PLANT_TROUBLE | 13372.1525
2022 | summer | SMPRIP_1_SMPSON | TRANSMISSION_INDUCED | 92.1
2022 | summer | SMUDGO_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 7501.64
2022 | summer | SMUDGO_7_UNIT 1 | PLANT_TROUBLE | 9722.08
2022 | summer | SMYRNA_1_DL1SR1 | PLANT_TROUBLE | 50
2022 | summer | SNCLRA_2_HOWLNG | AMBIENT_NOT_DUE_TO_TEMP | 521
2022 | summer | SNCLRA_2_HOWLNG | PLANT_MAINTENANCE | 780.2
2022 | summer | SNCLRA_2_HOWLNG | PLANT_TROUBLE | 4580.6
2022 | summer | SNCLRA_2_SILBT1 | PLANT_MAINTENANCE | 0
2022 | summer | SNCLRA_2_SILBT1 | PLANT_TROUBLE | 0
2022 | summer | SNCLRA_2_UNIT | PLANT_MAINTENANCE | 5637.5
2022 | summer | SNCLRA_2_UNIT1 | PLANT_MAINTENANCE | 121
2022 | summer | SNCLRA_2_VESBT1 | METERING_TELEMETRY | 0
2022 | summer | SNCLRA_2_VESBT1 | PLANT_MAINTENANCE | 100
2022 | summer | SNCLRA_2_VESBT1 | PLANT_TROUBLE | 1013.3333
2022 | summer | SNCLRA_2_VESBT1 | TRANSMISSION_INDUCED | 52
2022 | summer | SNCLRA_2_VESBT1 | UNIT_TESTING | 800
2022 | summer | SNCLRA_6_PROCGN | PLANT_TROUBLE | 1053.8
2022 | summer | SNCLRA_6_PROCGN | TRANSMISSION_INDUCED | 0
2022 | summer | SNORA_2_SNRSLR | PLANT_MAINTENANCE | 300
2022 | summer | SNORA_2_SNRSLR | TRANSMISSION_INDUCED | 1238.3333
2022 | summer | SOUTH_2_UNIT | METERING_TELEMETRY | 140.225
2022 | summer | SOUTH_2_UNIT | PLANT_TROUBLE | 0
2022 | summer | SOUTH_2_UNIT | TRANSMISSION_INDUCED | 0
2022 | summer | SPANSH_6_FBEHY1 | PLANT_TROUBLE | 188.1
2022 | summer | SPAULD_6_UNIT 3 | AMBIENT_NOT_DUE_TO_TEMP | 504.8
2022 | summer | SPAULD_6_UNIT 3 | PLANT_MAINTENANCE | 1443
2022 | summer | SPAULD_6_UNIT 3 | PLANT_TROUBLE | 1.197
2022 | summer | SPAULD_6_UNIT 3 | TRANSMISSION_INDUCED | 42.575
2022 | summer | SPAULD_6_UNIT12 | AMBIENT_NOT_DUE_TO_TEMP | 324.9933
2022 | summer | SPAULD_6_UNIT12 | PLANT_MAINTENANCE | 0
2022 | summer | SPAULD_6_UNIT12 | PLANT_TROUBLE | 154.68
2022 | summer | SPAULD_6_UNIT12 | TRANSMISSION_INDUCED | 0
2022 | summer | SPBURN_2_UNIT 1 | METERING_TELEMETRY | 0
2022 | summer | SPBURN_2_UNIT 1 | PLANT_MAINTENANCE | 110
2022 | summer | SPBURN_2_UNIT 1 | PLANT_TROUBLE | 1496.1667
2022 | summer | SPBURN_2_UNIT 1 | TRANSMISSION_INDUCED | 374
2022 | summer | SPBURN_7_SNOWMT | AMBIENT_NOT_DUE_TO_TEMP | 2294.25
2022 | summer | SPI LI_2_UNIT 1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 22.475
2022 | summer | SPI LI_2_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 219.1267
2022 | summer | SPI LI_2_UNIT 1 | PLANT_MAINTENANCE | 86
2022 | summer | SPI LI_2_UNIT 1 | PLANT_TROUBLE | 434.0133
2022 | summer | SPIAND_1_ANDSN2 | PLANT_TROUBLE | 147.9675
2022 | summer | SPICER_1_UNITS | PLANT_TROUBLE | 0.25
2022 | summer | SPICER_1_UNITS | TRANSMISSION_INDUCED | 254.7
2022 | summer | SPIFBD_1_PL1X2 | PLANT_TROUBLE | 387.625
2022 | summer | SPQUIN_6_SRPCQU | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 90.325
2022 | summer | SPQUIN_6_SRPCQU | PLANT_MAINTENANCE | 389.95
2022 | summer | SPQUIN_6_SRPCQU | PLANT_TROUBLE | 743.5815
2022 | summer | SPQUIN_6_SRPCQU | TRANSMISSION_INDUCED | 1135.6
2022 | summer | SPRGAP_1_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 2135
2022 | summer | SPRGVL_2_TULESC | ENVIRONMENTAL_RESTRICTIONS | 1912.5
2022 | summer | STANIS_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 3162.81
2022 | summer | STANIS_7_UNIT 1 | PLANT_TROUBLE | 455
2022 | summer | STANTN_2_STAGT1 | AMBIENT_DUE_TO_TEMP | 25.2085
2022 | summer | STANTN_2_STAGT1 | PLANT_MAINTENANCE | 0
2022 | summer | STANTN_2_STAGT1 | PLANT_TROUBLE | 317.76
2022 | summer | STANTN_2_STAGT2 | AMBIENT_DUE_TO_TEMP | 676.9898
2022 | summer | STANTN_2_STAGT2 | AMBIENT_NOT_DUE_TO_TEMP | 10.14
2022 | summer | STANTN_2_STAGT2 | PLANT_MAINTENANCE | 0
2022 | summer | STANTN_2_STAGT2 | PLANT_TROUBLE | 271.3893
2022 | summer | STIGCT_2_LODI | AMBIENT_DUE_TO_TEMP | 3964
2022 | summer | STIGCT_2_LODI | AMBIENT_NOT_DUE_TO_TEMP | 29.5
2022 | summer | STIGCT_2_LODI | PLANT_TROUBLE | 3335.1677
2022 | summer | STNRES_1_UNIT | PLANT_MAINTENANCE | 806.0267
2022 | summer | STNRES_1_UNIT | PLANT_TROUBLE | 119
2022 | summer | STOILS_1_UNITS | AMBIENT_DUE_TO_TEMP | 216
2022 | summer | STOILS_1_UNITS | PLANT_MAINTENANCE | 2810
2022 | summer | STOILS_1_UNITS | PLANT_TROUBLE | 15174
2022 | summer | STROUD_6_WWHSR1 | PLANT_TROUBLE | 1140.735
2022 | summer | SUMWHT_6_SWSSR1 | PLANT_TROUBLE | 4344.1267
2022 | summer | SUNCAT_2_A1ABT1 | NEW_GENERATOR_TEST_ENERGY | 0
2022 | summer | SUNCAT_2_A1ABT1 | PLANT_TROUBLE | 11448.925
2022 | summer | SUNCAT_2_A1BBT1 | NEW_GENERATOR_TEST_ENERGY | 0
2022 | summer | SUNCAT_2_A1BBT1 | PLANT_TROUBLE | 13484.8617
2022 | summer | SUNCAT_2_A2ABT2 | NEW_GENERATOR_TEST_ENERGY | 0
2022 | summer | SUNCAT_2_A2ABT2 | PLANT_MAINTENANCE | 3017.8333
2022 | summer | SUNCAT_2_A2ABT2 | PLANT_TROUBLE | 13276.735
2022 | summer | SUNCAT_2_A2ABT2 | UNIT_TESTING | 0
2022 | summer | SUNRIS_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 37537.3
2022 | summer | SUNRIS_2_PL1X3 | PLANT_MAINTENANCE | 1902
2022 | summer | SUNRIS_2_PL1X3 | PLANT_TROUBLE | 104.85
2022 | summer | SUNSET_2_UNITS | AMBIENT_DUE_TO_TEMP | 14263
2022 | summer | SUNSET_2_UNITS | PLANT_MAINTENANCE | 4800
2022 | summer | SUNSET_2_UNITS | PLANT_TROUBLE | 111.9333
2022 | summer | SUNSHN_2_LNDFL | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 18.6667
2022 | summer | SUNSHN_2_LNDFL | AMBIENT_DUE_TO_TEMP | 574.9083
2022 | summer | SUNSHN_2_LNDFL | AMBIENT_NOT_DUE_TO_TEMP | 114.7833
2022 | summer | SUNSHN_2_LNDFL | PLANT_MAINTENANCE | 166.02
2022 | summer | SUNSHN_2_LNDFL | PLANT_TROUBLE | 393.475
2022 | summer | SUNSHN_2_LNDFL | TRANSMISSION_INDUCED | 54
2022 | summer | SUNSLR_1_SSVSR1 | PLANT_MAINTENANCE | 646.2
2022 | summer | SUNSLR_1_SSVSR1 | PLANT_TROUBLE | 2278.6333
2022 | summer | SUNST2_5_SS2SR1 | PLANT_MAINTENANCE | 750
2022 | summer | SUNST2_5_SS2SR1 | PLANT_TROUBLE | 9260.8667
2022 | summer | SUTTER_2_CISO | AMBIENT_DUE_TO_TEMP | 14656.103
2022 | summer | SUTTER_2_CISO | PLANT_MAINTENANCE | 2700
2022 | summer | SUTTER_2_CISO | PLANT_TROUBLE | 7312.4667
2022 | summer | SUTTER_2_CISO | RTU_RIG | 0
2022 | summer | SYCAMR_2_UNIT 1 | PLANT_MAINTENANCE | 14307
2022 | summer | SYCAMR_2_UNIT 1 | PLANT_TROUBLE | 733.8333
2022 | summer | SYCAMR_2_UNIT 2 | PLANT_TROUBLE | 152
2022 | summer | SYCAMR_2_UNIT 2 | RTU_RIG | 2
2022 | summer | SYCAMR_2_UNIT 2 | UNIT_TESTING | 0
2022 | summer | SYCAMR_2_UNIT 3 | PLANT_TROUBLE | 370
2022 | summer | SYCAMR_2_UNIT 3 | UNIT_TESTING | 9.3333
2022 | summer | SYCAMR_2_UNIT 4 | PLANT_MAINTENANCE | 0
2022 | summer | SYCAMR_2_UNIT 4 | PLANT_TROUBLE | 1694.8
2022 | summer | SYCAMR_2_UNIT 4 | RTU_RIG | 3
2022 | summer | SYCAMR_2_UNIT 4 | UNIT_TESTING | 14
2022 | summer | TANHIL_6_SOLART | PLANT_TROUBLE | 152.9
2022 | summer | TANHIL_6_SOLART | TRANSMISSION_INDUCED | 85
2022 | summer | TBLMTN_6_QF | PLANT_MAINTENANCE | 8.5
2022 | summer | TBLMTN_6_QF | PLANT_TROUBLE | 20.2017
2022 | summer | TBLMTN_6_QF | UNIT_TESTING | 0
2022 | summer | TECOLOTE_3_WBDYN | PLANT_MAINTENANCE | 50
2022 | summer | TECOLOTE_3_WBDYN | PLANT_TROUBLE | 3851.664
2022 | summer | TECOLOTE_3_WBDYN | TRANSMISSION_INDUCED | 6342.4
2022 | summer | TEHAPI_2_PW1WD1 | PLANT_MAINTENANCE | 160.8467
2022 | summer | TEHAPI_2_PW1WD1 | TRANSMISSION_INDUCED | 466.985
2022 | summer | TEHAPI_2_PW2WD2 | TRANSMISSION_INDUCED | 141.6
2022 | summer | TEHAPI_2_WIND1 | PLANT_MAINTENANCE | 198.5
2022 | summer | TEHAPI_2_WIND1 | PLANT_TROUBLE | 39.7
2022 | summer | TEHAPI_2_WIND1 | TRANSMISSION_INDUCED | 0
2022 | summer | TEHAPI_2_WIND2 | PLANT_MAINTENANCE | 195.5893
2022 | summer | TEHAPI_2_WIND2 | PLANT_TROUBLE | 49.2917
2022 | summer | TEHAPI_2_WIND2 | TRANSMISSION_INDUCED | 0
2022 | summer | TENGEN_2_PL1X2 | AMBIENT_DUE_TO_TEMP | 150.2067
2022 | summer | TENGEN_2_PL1X2 | PLANT_MAINTENANCE | 7627.95
2022 | summer | TENGEN_2_PL1X2 | PLANT_TROUBLE | 342.51
2022 | summer | TENGEN_2_PL1X2 | TRANSMISSION_INDUCED | 0
2022 | summer | TENGEN_2_PL1X2 | UNIT_TESTING | 736.2
2022 | summer | TERMEX_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 52809.9167
2022 | summer | TERMEX_2_PL1X3 | PLANT_TROUBLE | 16061.5667
2022 | summer | TIDWTR_2_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 2154
2022 | summer | TIDWTR_2_UNITS | PLANT_MAINTENANCE | 1305
2022 | summer | TIDWTR_2_UNITS | PLANT_TROUBLE | 755.81
2022 | summer | TIFFNY_1_DILLON | AMBIENT_DUE_TO_TEMP | 2376.6667
2022 | summer | TIFFNY_1_DILLON | PLANT_TROUBLE | 45
2022 | summer | TIGRCK_7_UNITS | AMBIENT_DUE_TO_TEMP | 25
2022 | summer | TIGRCK_7_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 5183.2717
2022 | summer | TIGRCK_7_UNITS | PLANT_MAINTENANCE | 480
2022 | summer | TIGRCK_7_UNITS | PLANT_TROUBLE | 6.3933
2022 | summer | TIGRCK_7_UNITS | TRANSMISSION_INDUCED | 788.95
2022 | summer | TITANS_2_TTSSR1 | PLANT_TROUBLE | 1103.2
2022 | summer | TITANS_2_TTSSR1 | TRANSMISSION_INDUCED | 1050
2022 | summer | TOADTW_6_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 285
2022 | summer | TOADTW_6_UNIT | TRANSMISSION_INDUCED | 18.025
2022 | summer | TOPAZ_2_SOLAR | PLANT_TROUBLE | 15610
2022 | summer | TORTLA_1_SOLAR | PLANT_TROUBLE | 286.6667
2022 | summer | TOWNSITE_2_MEADDYN | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 628
2022 | summer | TOWNSITE_2_MEADDYN | PLANT_MAINTENANCE | 727.65
2022 | summer | TOWNSITE_2_MEADDYN | PLANT_TROUBLE | 3707.5
2022 | summer | TRNQL8_2_ROJSR1 | PLANT_MAINTENANCE | 75
2022 | summer | TRNQL8_2_ROJSR1 | PLANT_TROUBLE | 100
2022 | summer | TRNQL8_2_VERSR1 | PLANT_MAINTENANCE | 45
2022 | summer | TRNQL8_2_VERSR1 | PLANT_TROUBLE | 16.25
2022 | summer | TRNQLT_2_RETBT1 | METERING_TELEMETRY | 12
2022 | summer | TRNQLT_2_RETBT1 | PLANT_MAINTENANCE | 7136.0333
2022 | summer | TRNQLT_2_RETBT1 | PLANT_TROUBLE | 6169.2833
2022 | summer | TRNQLT_2_RETBT1 | UNIT_TESTING | 0
2022 | summer | TRNQLT_2_SOLAR | METERING_TELEMETRY | 0
2022 | summer | TRNQLT_2_SOLAR | PLANT_MAINTENANCE | 0
2022 | summer | TRNQLT_2_SOLAR | PLANT_TROUBLE | 1931.83
2022 | summer | TRNQLT_2_SOLAR | UNIT_TESTING | 0
2022 | summer | TRNSWD_1_QF | PLANT_MAINTENANCE | 11.25
2022 | summer | TRNSWD_1_QF | PLANT_TROUBLE | 22487.1375
2022 | summer | TULEWD_1_TULWD1 | PLANT_TROUBLE | 0
2022 | summer | TULEWD_1_TULWD1 | TRANSMISSION_INDUCED | 652.5
2022 | summer | TVYVLY_6_KRSHY1 | AMBIENT_NOT_DUE_TO_TEMP | 104
2022 | summer | TVYVLY_6_KRSHY1 | ENVIRONMENTAL_RESTRICTIONS | 39
2022 | summer | TVYVLY_6_KRSHY1 | PLANT_TROUBLE | 32.5
2022 | summer | TWISSL_6_SOLAR1 | PLANT_MAINTENANCE | 20
2022 | summer | TWISSL_6_SOLAR1 | PLANT_TROUBLE | 25.3333
2022 | summer | TXMCKT_6_UNIT | METERING_TELEMETRY | 0
2022 | summer | TXMCKT_6_UNIT | PLANT_MAINTENANCE | 56.79
2022 | summer | TXMCKT_6_UNIT | PLANT_TROUBLE | 41.87
2022 | summer | UKIAH_7_LAKEMN | METERING_TELEMETRY | 107.6417
2022 | summer | UKIAH_7_LAKEMN | PLANT_TROUBLE | 0
2022 | summer | ULTPCH_1_UNIT 1 | METERING_TELEMETRY | 90
2022 | summer | ULTPCH_1_UNIT 1 | PLANT_MAINTENANCE | 89.7
2022 | summer | ULTPCH_1_UNIT 1 | PLANT_TROUBLE | 1476.6
2022 | summer | ULTPCH_1_UNIT 1 | TRANSMISSION_INDUCED | 180
2022 | summer | ULTPFR_1_UNIT 1 | METERING_TELEMETRY | 32.45
2022 | summer | ULTPFR_1_UNIT 1 | PLANT_MAINTENANCE | 174.7758
2022 | summer | ULTPFR_1_UNIT 1 | PLANT_TROUBLE | 6202.9865
2022 | summer | ULTRCK_2_UNIT | PLANT_MAINTENANCE | 0
2022 | summer | ULTRCK_2_UNIT | PLANT_TROUBLE | 1659.7808
2022 | summer | UNCHEM_1_UNIT | PLANT_TROUBLE | 2874.7833
2022 | summer | UNVRSY_1_UNIT 1 | AMBIENT_DUE_TO_TEMP | 12.2
2022 | summer | UNVRSY_1_UNIT 1 | PLANT_MAINTENANCE | 0
2022 | summer | UNVRSY_1_UNIT 1 | PLANT_TROUBLE | 190
2022 | summer | UNVRSY_1_UNIT 1 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2022 | summer | USWND2_1_WIND1 | METERING_TELEMETRY | 26.85
2022 | summer | USWND2_1_WIND1 | PLANT_TROUBLE | 2395.519
2022 | summer | USWND2_1_WIND2 | METERING_TELEMETRY | 26.85
2022 | summer | USWND2_1_WIND2 | PLANT_MAINTENANCE | 2934.3898
2022 | summer | USWND2_1_WIND3 | PLANT_MAINTENANCE | 43.7
2022 | summer | USWND2_1_WIND3 | PLANT_TROUBLE | 5639.2583
2022 | summer | USWND2_1_WIND3 | RTU_RIG | 20.7
2022 | summer | USWND2_1_WIND3 | TRANSMISSION_INDUCED | 0
2022 | summer | USWNDR_2_LABWD1 | PLANT_MAINTENANCE | 841.125
2022 | summer | USWNDR_2_LABWD1 | TRANSMISSION_INDUCED | 0
2022 | summer | USWNDR_2_SMUD | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 3334.729
2022 | summer | USWNDR_2_SMUD | PLANT_MAINTENANCE | 62.7
2022 | summer | USWNDR_2_SMUD | PLANT_TROUBLE | 0
2022 | summer | USWNDR_2_SMUD | TRANSMISSION_INDUCED | 0
2022 | summer | USWNDR_2_SMUD2 | PLANT_MAINTENANCE | 1242.45
2022 | summer | USWNDR_2_SMUD2 | PLANT_TROUBLE | 0
2022 | summer | USWNDR_2_SMUD2 | TRANSMISSION_INDUCED | 0
2022 | summer | USWPFK_6_FRICK | METERING_TELEMETRY | 17.5
2022 | summer | USWPFK_6_FRICK | PLANT_MAINTENANCE | 0
2022 | summer | USWPFK_6_FRICK | PLANT_TROUBLE | 0
2022 | summer | USWPFK_6_FRICK | TRANSMISSION_INDUCED | 47
2022 | summer | USWPJR_2_UNITS | PLANT_MAINTENANCE | 701.5
2022 | summer | VACADX_1_UNITA1 | AMBIENT_DUE_TO_TEMP | 316.8
2022 | summer | VACADX_1_UNITA1 | PLANT_MAINTENANCE | 1206.205
2022 | summer | VACADX_1_UNITA1 | PLANT_TROUBLE | 17.4965
2022 | summer | VACADX_1_UNITA1 | UNIT_TESTING | 0
2022 | summer | VALLEY_5_PERRIS | AMBIENT_NOT_DUE_TO_TEMP | 6074.1
2022 | summer | VALLEY_5_REDMTN | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1771.5
2022 | summer | VALLEY_5_REDMTN | AMBIENT_DUE_TO_TEMP | 29.5
2022 | summer | VALLEY_5_REDMTN | AMBIENT_NOT_DUE_TO_TEMP | 118
2022 | summer | VALLEY_5_REDMTN | PLANT_TROUBLE | 88.5
2022 | summer | VALLEY_5_REDMTN | TRANSMISSION_INDUCED | 29.5
2022 | summer | VALLEY_5_REDMTN | UNIT_TESTING | 0
2022 | summer | VEDDER_1_SEKERN | PLANT_MAINTENANCE | 143.3667
2022 | summer | VEDDER_1_SEKERN | PLANT_TROUBLE | 9539.55
2022 | summer | VENWD_1_WIND3 | PLANT_MAINTENANCE | 298.64
2022 | summer | VENWD_1_WIND3 | PLANT_TROUBLE | 0
2022 | summer | VERNON_6_GONZL1 | PLANT_TROUBLE | 4398.75
2022 | summer | VERNON_6_GONZL2 | ANNUAL_USE_LIMIT_REACHED | 0
2022 | summer | VERNON_6_GONZL2 | OTHER_USE_LIMIT_REACHED | 1.15
2022 | summer | VERNON_6_GONZL2 | SHORT_TERM_USE_LIMIT_REACHED | 28.75
2022 | summer | VERNON_6_MALBRG | AMBIENT_DUE_TO_TEMP | 45
2022 | summer | VERNON_6_MALBRG | PLANT_MAINTENANCE | 0
2022 | summer | VERNON_6_MALBRG | PLANT_TROUBLE | 2758.9167
2022 | summer | VERNON_6_MALBRG | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2022 | summer | VERNON_6_MALBRG | UNIT_SUPPORTING_STARTUP | 847.2
2022 | summer | VESTAL_2_KERN | AMBIENT_NOT_DUE_TO_TEMP | 14091.4583
2022 | summer | VESTAL_2_SOLAR1 | METERING_TELEMETRY | 100
2022 | summer | VESTAL_2_SOLAR1 | PLANT_MAINTENANCE | 60.6667
2022 | summer | VESTAL_2_SOLAR1 | PLANT_TROUBLE | 0
2022 | summer | VESTAL_2_SOLAR2 | METERING_TELEMETRY | 238
2022 | summer | VESTAL_2_SOLAR2 | PLANT_MAINTENANCE | 14
2022 | summer | VESTAL_2_SOLAR2 | PLANT_TROUBLE | 76.7667
2022 | summer | VESTAL_2_TS5SR1 | PLANT_MAINTENANCE | 242.5733
2022 | summer | VESTAL_2_TS5SR1 | PLANT_TROUBLE | 2022.87
2022 | summer | VESTAL_2_TS5SR1 | TRANSMISSION_INDUCED | 0
2022 | summer | VESTAL_2_WELLHD | AMBIENT_DUE_TO_TEMP | 32.245
2022 | summer | VESTAL_2_WELLHD | AMBIENT_NOT_DUE_TO_TEMP | 65.3333
2022 | summer | VESTAL_2_WELLHD | PLANT_MAINTENANCE | 0
2022 | summer | VESTAL_2_WELLHD | PLANT_TROUBLE | 365.5167
2022 | summer | VESTAL_6_QF | AMBIENT_NOT_DUE_TO_TEMP | 8610.665
2022 | summer | VESTAL_6_QF | PLANT_TROUBLE | 43.5
2022 | summer | VICTOR_1_CREST | PLANT_TROUBLE | 212.8167
2022 | summer | VICTOR_1_CREST | TRANSMISSION_INDUCED | 4.85
2022 | summer | VICTOR_1_EXSLRA | PLANT_TROUBLE | 1.9333
2022 | summer | VICTOR_1_EXSLRA | TRANSMISSION_INDUCED | 6.4667
2022 | summer | VICTOR_1_EXSLRB | PLANT_TROUBLE | 0
2022 | summer | VICTOR_1_EXSLRB | TRANSMISSION_INDUCED | 6.4333
2022 | summer | VICTOR_1_LVSLR1 | PLANT_TROUBLE | 100
2022 | summer | VICTOR_1_LVSLR1 | TRANSMISSION_INDUCED | 0
2022 | summer | VICTOR_1_LVSLR2 | PLANT_TROUBLE | 200
2022 | summer | VICTOR_1_LVSLR2 | TRANSMISSION_INDUCED | 0
2022 | summer | VICTOR_1_SOLAR1 | PLANT_TROUBLE | 0
2022 | summer | VICTOR_1_SOLAR2 | PLANT_TROUBLE | 0
2022 | summer | VICTOR_1_SOLAR3 | PLANT_MAINTENANCE | 0
2022 | summer | VICTOR_1_SOLAR3 | PLANT_TROUBLE | 34.3
2022 | summer | VICTOR_1_SOLAR3 | TRANSMISSION_INDUCED | 1.5167
2022 | summer | VICTOR_1_SOLAR4 | PLANT_MAINTENANCE | 0
2022 | summer | VICTOR_1_SOLAR4 | PLANT_TROUBLE | 98
2022 | summer | VICTOR_1_SOLAR4 | TRANSMISSION_INDUCED | 4.3333
2022 | summer | VICTOR_1_VDRYFB | PLANT_TROUBLE | 121.5
2022 | summer | VILLPK_2_VALLYV | AMBIENT_NOT_DUE_TO_TEMP | 2921.5
2022 | summer | VISTRA_5_DALBT1 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | summer | VISTRA_5_DALBT1 | PLANT_MAINTENANCE | 90
2022 | summer | VISTRA_5_DALBT1 | PLANT_TROUBLE | 5333.8
2022 | summer | VISTRA_5_DALBT1 | TRANSMISSION_INDUCED | 0
2022 | summer | VISTRA_5_DALBT2 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | summer | VISTRA_5_DALBT2 | PLANT_MAINTENANCE | 148.3333
2022 | summer | VISTRA_5_DALBT2 | PLANT_TROUBLE | 5891.3
2022 | summer | VISTRA_5_DALBT2 | TRANSMISSION_INDUCED | 0
2022 | summer | VISTRA_5_DALBT3 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | summer | VISTRA_5_DALBT3 | PLANT_MAINTENANCE | 255
2022 | summer | VISTRA_5_DALBT3 | PLANT_TROUBLE | 10791.5667
2022 | summer | VISTRA_5_DALBT3 | TRANSMISSION_INDUCED | 0
2022 | summer | VISTRA_5_DALBT4 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | summer | VISTRA_5_DALBT4 | PLANT_MAINTENANCE | 167.7333
2022 | summer | VISTRA_5_DALBT4 | PLANT_TROUBLE | 9386.5833
2022 | summer | VISTRA_5_DALBT4 | TRANSMISSION_INDUCED | 0
2022 | summer | VLCNTR_6_VCEBT1 | PLANT_MAINTENANCE | 275.7833
2022 | summer | VLCNTR_6_VCEBT1 | PLANT_TROUBLE | 732.3833
2022 | summer | VLCNTR_6_VCEBT2 | AMBIENT_NOT_DUE_TO_TEMP | 2137.4167
2022 | summer | VLCNTR_6_VCEBT2 | PLANT_MAINTENANCE | 225
2022 | summer | VLCNTR_6_VCEBT2 | PLANT_TROUBLE | 4653.1667
2022 | summer | VLCNTR_6_VCSLR1 | PLANT_MAINTENANCE | 7.5
2022 | summer | VLCNTR_6_VCSLR2 | PLANT_MAINTENANCE | 15
2022 | summer | VOLTA_2_UNIT 1 | PLANT_MAINTENANCE | 6961.5
2022 | summer | VOLTA_2_UNIT 2 | TRANSMISSION_INDUCED | 0
2022 | summer | VOLTA_6_BAILCK | AMBIENT_NOT_DUE_TO_TEMP | 464.49
2022 | summer | VOLTA_6_BAILCK | TRANSMISSION_INDUCED | 0.07
2022 | summer | VOLTA_6_DIGHYD | PLANT_TROUBLE | 6.8
2022 | summer | VOLTA_6_DIGHYD | TRANSMISSION_INDUCED | 0.7
2022 | summer | VOLTA_7_PONHY1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 837.5
2022 | summer | VSTAES_6_VESBT1 | PLANT_MAINTENANCE | 0
2022 | summer | VSTAES_6_VESBT1 | PLANT_TROUBLE | 273.7
2022 | summer | WADHAM_6_UNIT | METERING_TELEMETRY | 0
2022 | summer | WADHAM_6_UNIT | PLANT_TROUBLE | 581.4
2022 | summer | WALCRK_2_CTG1 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | summer | WALCRK_2_CTG1 | OTHER_USE_LIMIT_REACHED | 486.6
2022 | summer | WALCRK_2_CTG1 | PLANT_MAINTENANCE | 481.734
2022 | summer | WALCRK_2_CTG1 | PLANT_TROUBLE | 4922.1447
2022 | summer | WALCRK_2_CTG2 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | summer | WALCRK_2_CTG2 | METERING_TELEMETRY | 484.55
2022 | summer | WALCRK_2_CTG2 | OTHER_USE_LIMIT_REACHED | 88.8342
2022 | summer | WALCRK_2_CTG2 | PLANT_MAINTENANCE | 80.7583
2022 | summer | WALCRK_2_CTG2 | PLANT_TROUBLE | 19658.1935
2022 | summer | WALCRK_2_CTG3 | AMBIENT_DUE_TO_TEMP | 18.625
2022 | summer | WALCRK_2_CTG3 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | summer | WALCRK_2_CTG3 | METERING_TELEMETRY | 8.0542
2022 | summer | WALCRK_2_CTG3 | OTHER_USE_LIMIT_REACHED | 386.6
2022 | summer | WALCRK_2_CTG3 | PLANT_MAINTENANCE | 190.0783
2022 | summer | WALCRK_2_CTG3 | PLANT_TROUBLE | 473.52
2022 | summer | WALCRK_2_CTG3 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | summer | WALCRK_2_CTG4 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | summer | WALCRK_2_CTG4 | OTHER_USE_LIMIT_REACHED | 0
2022 | summer | WALCRK_2_CTG4 | PLANT_TROUBLE | 7888.2067
2022 | summer | WALCRK_2_CTG5 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | summer | WALCRK_2_CTG5 | OTHER_USE_LIMIT_REACHED | 0
2022 | summer | WALCRK_2_CTG5 | PLANT_MAINTENANCE | 138.5317
2022 | summer | WALCRK_2_CTG5 | PLANT_TROUBLE | 1890.3367
2022 | summer | WALCRK_2_CTG5 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | summer | WALNUT_6_HILLGEN | PLANT_TROUBLE | 449.6667
2022 | summer | WALNUT_6_HILLGEN | TRANSMISSION_INDUCED | 127.6833
2022 | summer | WALNUT_7_WCOVST | PLANT_TROUBLE | 45.5
2022 | summer | WARNE_2_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | summer | WARNE_2_UNIT | TRANSMISSION_INDUCED | 380
2022 | summer | WAUKNA_1_SOLAR | PLANT_TROUBLE | 26.6667
2022 | summer | WDLEAF_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 20.9167
2022 | summer | WDLEAF_7_UNIT 1 | PLANT_TROUBLE | 95
2022 | summer | WEBER_6_FORWRD | PLANT_MAINTENANCE | 0
2022 | summer | WEBER_6_FORWRD | PLANT_TROUBLE | 222.355
2022 | summer | WESTPT_2_UNIT | AMBIENT_DUE_TO_TEMP | 7
2022 | summer | WESTPT_2_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 4
2022 | summer | WESTPT_2_UNIT | PLANT_TROUBLE | 33.8333
2022 | summer | WESTPT_2_UNIT | TRANSMISSION_INDUCED | 494.4333
2022 | summer | WFRESN_1_SOLAR | PLANT_TROUBLE | 1147.5
2022 | summer | WHEATL_6_LNDFIL | PLANT_MAINTENANCE | 0.775
2022 | summer | WHEATL_6_LNDFIL | PLANT_TROUBLE | 41.4625
2022 | summer | WHITEH_2_MEADDYN1 | PLANT_TROUBLE | 2573.9187
2022 | summer | WHITEH_2_MEADDYN2 | PLANT_TROUBLE | 4292.6367
2022 | summer | WHTWTR_1_WINDA1 | PLANT_MAINTENANCE | 10600.9833
2022 | summer | WHTWTR_1_WINDA1 | TRANSMISSION_INDUCED | 304.1667
2022 | summer | WILLMS_6_ARBBM1 | NEW_GENERATOR_TEST_ENERGY | 1.5
2022 | summer | WILLMS_6_ARBBM1 | PLANT_TROUBLE | 114.3392
2022 | summer | WILLMS_6_ARBBM1 | UNIT_TESTING | 0
2022 | summer | WISE_1_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 1291.4708
2022 | summer | WISE_1_UNIT 1 | PLANT_MAINTENANCE | 0
2022 | summer | WISE_1_UNIT 1 | PLANT_TROUBLE | 0
2022 | summer | WISE_1_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 2448
2022 | summer | WISHON_6_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 624.805
2022 | summer | WISHON_6_UNITS | METERING_TELEMETRY | 270.5867
2022 | summer | WISHON_6_UNITS | PLANT_MAINTENANCE | 4244.5
2022 | summer | WISHON_6_UNITS | PLANT_TROUBLE | 728
2022 | summer | WISHON_6_UNITS | TRANSMISSION_INDUCED | 0
2022 | summer | WISTER_2_WISSR1 | NEW_GENERATOR_TEST_ENERGY | 0
2022 | summer | WISTER_2_WISSR1 | PLANT_TROUBLE | 2457.3167
2022 | summer | WISTER_2_WISSR1 | TRANSMISSION_INDUCED | 840
2022 | summer | WISTRA_2_WRSSR1 | PLANT_MAINTENANCE | 1614.4167
2022 | summer | WISTRA_2_WRSSR1 | PLANT_TROUBLE | 0
2022 | summer | WISTRA_2_WRSSR1 | TRANSMISSION_INDUCED | 500
2022 | summer | WLDWD_1_SOLAR1 | PLANT_TROUBLE | 400
2022 | summer | WLDWD_1_SOLAR2 | TRANSMISSION_INDUCED | 75
2022 | summer | WNDMAS_2_UNIT 1 | PLANT_MAINTENANCE | 224.2833
2022 | summer | WNDMAS_2_UNIT 1 | TRANSMISSION_INDUCED | 1244.5
2022 | summer | WNDSTR_2_WIND | METERING_TELEMETRY | 4
2022 | summer | WNDSTR_2_WIND | PLANT_MAINTENANCE | 0
2022 | summer | WOLFSK_1_UNITA1 | AMBIENT_DUE_TO_TEMP | 501.55
2022 | summer | WOLFSK_1_UNITA1 | PLANT_TROUBLE | 411.405
2022 | summer | WRGTSR_2_WSFSR1 | METERING_TELEMETRY | 0
2022 | summer | WRGTSR_2_WSFSR1 | PLANT_MAINTENANCE | 593.8333
2022 | summer | WRGTSR_2_WSFSR1 | PLANT_TROUBLE | 11752.49
2022 | summer | WSENGY_1_UNIT 1 | PLANT_TROUBLE | 1539.45
2022 | summer | WSTWND_2_M89WD1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 338.2033
2022 | summer | WSTWND_2_M89WD1 | AMBIENT_NOT_DUE_TO_TEMP | 81.4
2022 | summer | WSTWND_2_M89WD1 | PLANT_MAINTENANCE | 0
2022 | summer | WSTWND_2_M89WD1 | PLANT_TROUBLE | 48.4333
2022 | summer | WSTWND_2_M90WD2 | PLANT_MAINTENANCE | 0
2022 | summer | YUBACT_1_SUNSWT | AMBIENT_DUE_TO_TEMP | 1439.8918
2022 | summer | YUBACT_1_SUNSWT | PLANT_MAINTENANCE | 1346.6915
2022 | summer | YUBACT_1_SUNSWT | PLANT_TROUBLE | 7549.6113
2022 | summer | YUBACT_6_UNITA1 | AMBIENT_DUE_TO_TEMP | 747.118
2022 | summer | YUBACT_6_UNITA1 | PLANT_TROUBLE | 179.812
2022 | summer | ZOND_6_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 13081.5
2022 | nonsummer | 7STDRD_1_SOLAR1 | METERING_TELEMETRY | 30
2022 | nonsummer | 7STDRD_1_SOLAR1 | TRANSMISSION_INDUCED | 240
2022 | nonsummer | ACACIA_6_SOLAR | PLANT_MAINTENANCE | 0
2022 | nonsummer | ACACIA_6_SOLAR | PLANT_TROUBLE | 10
2022 | nonsummer | ADERA_1_SOLAR1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | ADERA_1_SOLAR1 | PLANT_TROUBLE | 197.5
2022 | nonsummer | ADERA_1_SOLAR1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | ADLIN_1_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 10011.89
2022 | nonsummer | ADLIN_1_UNITS | PLANT_MAINTENANCE | 224
2022 | nonsummer | ADLIN_1_UNITS | PLANT_TROUBLE | 3050.8338
2022 | nonsummer | ADLIN_1_UNITS | TRANSMISSION_INDUCED | 0
2022 | nonsummer | ADMEST_6_SOLAR | METERING_TELEMETRY | 0
2022 | nonsummer | ADMEST_6_SOLAR | PLANT_TROUBLE | 439.1013
2022 | nonsummer | ADOBEE_1_SOLAR | METERING_TELEMETRY | 0
2022 | nonsummer | ADOBEE_1_SOLAR | PLANT_MAINTENANCE | 0
2022 | nonsummer | ADOBEE_1_SOLAR | PLANT_TROUBLE | 0
2022 | nonsummer | ADOBEE_1_SOLAR | TRANSMISSION_INDUCED | 0
2022 | nonsummer | ADOBEE_1_SOLAR | UNIT_TESTING | 40
2022 | nonsummer | AGCANA_X_HOOVER | RIMS_OUTAGE | 3600
2022 | nonsummer | AGRICO_6_PL3N5 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 226.9
2022 | nonsummer | AGRICO_6_PL3N5 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | AGRICO_6_PL3N5 | AMBIENT_NOT_DUE_TO_TEMP | 113.45
2022 | nonsummer | AGRICO_6_PL3N5 | PLANT_MAINTENANCE | 181.52
2022 | nonsummer | AGRICO_6_PL3N5 | PLANT_TROUBLE | 11.345
2022 | nonsummer | AGRICO_6_PL3N5 | TRANSMISSION_INDUCED | 34.035
2022 | nonsummer | AGUCAL_5_SOLAR1 | PLANT_MAINTENANCE | 2347.5
2022 | nonsummer | AGUCAL_5_SOLAR1 | PLANT_TROUBLE | 0
2022 | nonsummer | AKINGS_6_AMESR1 | PLANT_MAINTENANCE | 677.2333
2022 | nonsummer | AKINGS_6_AMESR1 | PLANT_TROUBLE | 367.8
2022 | nonsummer | AKINGS_6_AMESR1 | TRANSMISSION_INDUCED | 981.95
2022 | nonsummer | ALAMIT_2_PL1X3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1349.4
2022 | nonsummer | ALAMIT_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 36.8
2022 | nonsummer | ALAMIT_2_PL1X3 | PLANT_MAINTENANCE | 39666.685
2022 | nonsummer | ALAMIT_2_PL1X3 | PLANT_TROUBLE | 4329.4172
2022 | nonsummer | ALAMIT_2_PL1X3 | TRANSITIONAL_LIMITATION | 0
2022 | nonsummer | ALAMIT_2_PL1X3 | UNIT_TESTING | 2133.34
2022 | nonsummer | ALAMIT_7_ES1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | ALAMIT_7_ES1 | METERING_TELEMETRY | 0
2022 | nonsummer | ALAMIT_7_ES1 | PLANT_TROUBLE | 18641.0267
2022 | nonsummer | ALAMIT_7_UNIT 3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 653.52
2022 | nonsummer | ALAMIT_7_UNIT 3 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | ALAMIT_7_UNIT 3 | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | ALAMIT_7_UNIT 3 | PLANT_MAINTENANCE | 3440
2022 | nonsummer | ALAMIT_7_UNIT 3 | PLANT_TROUBLE | 32254.6433
2022 | nonsummer | ALAMIT_7_UNIT 3 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2022 | nonsummer | ALAMIT_7_UNIT 3 | TRANSMISSION_INDUCED | 1328
2022 | nonsummer | ALAMIT_7_UNIT 3 | UNIT_SUPPORTING_STARTUP | 271.4113
2022 | nonsummer | ALAMIT_7_UNIT 3 | UNIT_TESTING | 109.995
2022 | nonsummer | ALAMIT_7_UNIT 4 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 668.86
2022 | nonsummer | ALAMIT_7_UNIT 4 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | ALAMIT_7_UNIT 4 | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | ALAMIT_7_UNIT 4 | PLANT_MAINTENANCE | 1672.15
2022 | nonsummer | ALAMIT_7_UNIT 4 | PLANT_TROUBLE | 15466.9807
2022 | nonsummer | ALAMIT_7_UNIT 4 | UNIT_SUPPORTING_STARTUP | 146.8715
2022 | nonsummer | ALAMIT_7_UNIT 4 | UNIT_TESTING | 0
2022 | nonsummer | ALAMIT_7_UNIT 5 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | ALAMIT_7_UNIT 5 | PLANT_MAINTENANCE | 14400
2022 | nonsummer | ALAMIT_7_UNIT 5 | PLANT_TROUBLE | 7200
2022 | nonsummer | ALAMIT_7_UNIT 5 | TRANSMISSION_INDUCED | 2400
2022 | nonsummer | ALAMIT_7_UNIT 5 | UNIT_TESTING | 0
2022 | nonsummer | ALAMO_6_UNIT | PLANT_MAINTENANCE | 2650.8667
2022 | nonsummer | ALAMO_6_UNIT | PLANT_TROUBLE | 45.3333
2022 | nonsummer | ALHMBR_1_ALHSLR | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | ALHMBR_1_ALHSLR | PLANT_MAINTENANCE | 125
2022 | nonsummer | ALHMBR_1_ALHSLR | PLANT_TROUBLE | 125
2022 | nonsummer | ALHMBR_1_ALHSLR | TRANSITIONAL_LIMITATION | 92
2022 | nonsummer | ALHMBR_1_ALHSLR | TRANSMISSION_INDUCED | 0
2022 | nonsummer | ALMASL_2_AL6BT6 | NEW_GENERATOR_TEST_ENERGY | 0
2022 | nonsummer | ALMASL_2_AL6BT6 | PLANT_MAINTENANCE | 250
2022 | nonsummer | ALMASL_2_AL6BT6 | PLANT_TROUBLE | 134
2022 | nonsummer | ALMASL_2_GS1SR1 | PLANT_MAINTENANCE | 437.5
2022 | nonsummer | ALMASL_2_GS1SR1 | PLANT_TROUBLE | 0
2022 | nonsummer | ALMASL_2_GS4SR4 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | ALMASL_2_GS4SR4 | PLANT_MAINTENANCE | 700
2022 | nonsummer | ALMASL_2_GS6SR6 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | ALMASL_2_GS6SR6 | PLANT_MAINTENANCE | 350
2022 | nonsummer | ALMASL_2_GS6SR6 | PLANT_TROUBLE | 200
2022 | nonsummer | ALMASL_2_GS7SR7 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | ALMASL_2_GS7SR7 | PLANT_MAINTENANCE | 396
2022 | nonsummer | ALMEGT_1_UNIT 1 | AMBIENT_DUE_TO_TEMP | 1056
2022 | nonsummer | ALMEGT_1_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | ALMEGT_1_UNIT 1 | PLANT_TROUBLE | 11621.7333
2022 | nonsummer | ALMEGT_1_UNIT 1 | RTU_RIG | 0
2022 | nonsummer | ALMEGT_1_UNIT 2 | AMBIENT_DUE_TO_TEMP | 1530
2022 | nonsummer | ALMEGT_1_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | ALMEGT_1_UNIT 2 | PLANT_MAINTENANCE | 0
2022 | nonsummer | ALMEGT_1_UNIT 2 | PLANT_TROUBLE | 3372.75
2022 | nonsummer | ALMEGT_1_UNIT 2 | RTU_RIG | 0
2022 | nonsummer | ALMEGT_1_UNIT 2 | TRANSMISSION_INDUCED | 1995
2022 | nonsummer | ALMEGT_1_UNIT 2 | UNIT_TESTING | 0
2022 | nonsummer | ALPSLR_1_NTHSLR | METERING_TELEMETRY | 0
2022 | nonsummer | ALPSLR_1_NTHSLR | PLANT_MAINTENANCE | 51.6667
2022 | nonsummer | ALPSLR_1_NTHSLR | PLANT_TROUBLE | 0
2022 | nonsummer | ALPSLR_1_NTHSLR | TRANSMISSION_INDUCED | 100
2022 | nonsummer | ALPSLR_1_SPSSLR | PLANT_MAINTENANCE | 241.6667
2022 | nonsummer | ALPSLR_1_SPSSLR | PLANT_TROUBLE | 125
2022 | nonsummer | ALPSLR_1_SPSSLR | TRANSMISSION_INDUCED | 250
2022 | nonsummer | ALT6DN_2_WIND7 | PLANT_MAINTENANCE | 0
2022 | nonsummer | ALT6DS_2_WIND9 | METERING_TELEMETRY | 0
2022 | nonsummer | ALT6DS_2_WIND9 | TRANSMISSION_INDUCED | 1716
2022 | nonsummer | ALTA3A_2_CPCE4 | METERING_TELEMETRY | 135
2022 | nonsummer | ALTA3A_2_CPCE4 | PLANT_TROUBLE | 4000.1167
2022 | nonsummer | ALTA3A_2_CPCE5 | METERING_TELEMETRY | 6
2022 | nonsummer | ALTA3A_2_CPCE5 | PLANT_TROUBLE | 4267.7767
2022 | nonsummer | ALTA3A_2_CPCE8 | METERING_TELEMETRY | 339
2022 | nonsummer | ALTA3A_2_CPCE8 | PLANT_MAINTENANCE | 6116.15
2022 | nonsummer | ALTA3A_2_CPCE8 | PLANT_TROUBLE | 2728.05
2022 | nonsummer | ALTA4A_2_CPCW1 | METERING_TELEMETRY | 0
2022 | nonsummer | ALTA4A_2_CPCW1 | PLANT_MAINTENANCE | 1032
2022 | nonsummer | ALTA4A_2_CPCW1 | PLANT_TROUBLE | 4969.3
2022 | nonsummer | ALTA4B_2_CPCW2 | METERING_TELEMETRY | 6.35
2022 | nonsummer | ALTA4B_2_CPCW2 | PLANT_TROUBLE | 5794.5
2022 | nonsummer | ALTA4B_2_CPCW3 | METERING_TELEMETRY | 39
2022 | nonsummer | ALTA4B_2_CPCW3 | PLANT_MAINTENANCE | 450
2022 | nonsummer | ALTA4B_2_CPCW3 | PLANT_TROUBLE | 6901.05
2022 | nonsummer | ALTA4B_2_CPCW3 | TRANSMISSION_INDUCED | 300
2022 | nonsummer | ALTA4B_2_CPCW6 | METERING_TELEMETRY | 0
2022 | nonsummer | ALTA4B_2_CPCW6 | PLANT_MAINTENANCE | 1350
2022 | nonsummer | ALTA4B_2_CPCW6 | PLANT_TROUBLE | 952.15
2022 | nonsummer | ALTA4B_2_CPCW6 | RTU_RIG | 21
2022 | nonsummer | ALTA4B_2_CPCW6 | TRANSMISSION_INDUCED | 267.5
2022 | nonsummer | ALTA6B_2_WIND11 | METERING_TELEMETRY | 12.375
2022 | nonsummer | ALTA6B_2_WIND11 | PLANT_MAINTENANCE | 44.075
2022 | nonsummer | ALTA6B_2_WIND11 | PLANT_TROUBLE | 2649.3838
2022 | nonsummer | ALTA6E_2_WIND10 | METERING_TELEMETRY | 0
2022 | nonsummer | ALTA6E_2_WIND10 | PLANT_MAINTENANCE | 914.991
2022 | nonsummer | ALTA6E_2_WIND10 | PLANT_TROUBLE | 8089.9148
2022 | nonsummer | ALTWD_2_AT3WD3 | TRANSMISSION_INDUCED | 20.3547
2022 | nonsummer | ALTWD_2_COAWD1 | PLANT_MAINTENANCE | 319.84
2022 | nonsummer | ALTWD_2_COAWD1 | PLANT_TROUBLE | 846
2022 | nonsummer | ALTWD_2_COAWD1 | TRANSMISSION_INDUCED | 280.345
2022 | nonsummer | ANAHM_2_CANYN1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2022 | nonsummer | ANAHM_2_CANYN1 | PLANT_MAINTENANCE | 49.4
2022 | nonsummer | ANAHM_2_CANYN1 | PLANT_TROUBLE | 386.9667
2022 | nonsummer | ANAHM_2_CANYN1 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2022 | nonsummer | ANAHM_2_CANYN1 | UNIT_TESTING | 0
2022 | nonsummer | ANAHM_2_CANYN2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2022 | nonsummer | ANAHM_2_CANYN2 | PLANT_MAINTENANCE | 49.4
2022 | nonsummer | ANAHM_2_CANYN2 | PLANT_TROUBLE | 203.3633
2022 | nonsummer | ANAHM_2_CANYN2 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | ANAHM_2_CANYN2 | UNIT_TESTING | 9.8
2022 | nonsummer | ANAHM_2_CANYN3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2022 | nonsummer | ANAHM_2_CANYN3 | PLANT_MAINTENANCE | 395.2
2022 | nonsummer | ANAHM_2_CANYN3 | PLANT_TROUBLE | 230.95
2022 | nonsummer | ANAHM_2_CANYN3 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | ANAHM_2_CANYN3 | UNIT_TESTING | 9.8
2022 | nonsummer | ANAHM_2_CANYN4 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2022 | nonsummer | ANAHM_2_CANYN4 | PLANT_MAINTENANCE | 148.2
2022 | nonsummer | ANAHM_2_CANYN4 | PLANT_TROUBLE | 150.67
2022 | nonsummer | ANAHM_2_CANYN4 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2022 | nonsummer | ANAHM_2_CANYN4 | UNIT_TESTING | 0
2022 | nonsummer | ANZA_6_SOLAR1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | ANZA_6_SOLAR1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | APLHIL_1_SFKHY1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | APLHIL_1_SFKHY1 | PLANT_TROUBLE | 1594.6
2022 | nonsummer | APLHIL_1_SFKHY1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | AQUAWS_2_AQWSR1 | PLANT_MAINTENANCE | 494
2022 | nonsummer | AQUAWS_2_AQWSR1 | PLANT_TROUBLE | 5243.95
2022 | nonsummer | AQUAWS_2_AQWSR1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | ARBWD_6_QF | METERING_TELEMETRY | 0
2022 | nonsummer | ARBWD_6_QF | PLANT_TROUBLE | 0
2022 | nonsummer | ARBWD_6_QF | TRANSMISSION_INDUCED | 0
2022 | nonsummer | ARCOGN_2_UNITS | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | ARCOGN_2_UNITS | PLANT_MAINTENANCE | 12650
2022 | nonsummer | ARCOGN_2_UNITS | PLANT_TROUBLE | 25832.5
2022 | nonsummer | ARKANS_1_ARKSLR | PLANT_MAINTENANCE | 0
2022 | nonsummer | ARKANS_1_ARKSLR | PLANT_TROUBLE | 90.8333
2022 | nonsummer | ARKANS_1_ARKSLR | TRANSITIONAL_LIMITATION | 92
2022 | nonsummer | ARKANS_1_ARKSLR | TRANSMISSION_INDUCED | 0
2022 | nonsummer | ARLNTN_2_AR1SR1 | METERING_TELEMETRY | 0
2022 | nonsummer | ARLNTN_2_AR1SR1 | NEW_GENERATOR_TEST_ENERGY | 475
2022 | nonsummer | ARLNTN_2_AR1SR1 | PLANT_MAINTENANCE | 250
2022 | nonsummer | ARLNTN_2_AR1SR1 | PLANT_TROUBLE | 800
2022 | nonsummer | ARLNTN_2_AR1SR1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | ARLNTN_2_AR1SR1 | UNIT_TESTING | 0
2022 | nonsummer | ARLNTN_2_ASUSR1 | PLANT_TROUBLE | 5692
2022 | nonsummer | ARVINN_6_ORION1 | TRANSMISSION_INDUCED | 276
2022 | nonsummer | ARVINN_6_ORION2 | TRANSMISSION_INDUCED | 179.3333
2022 | nonsummer | ASTORA_2_SOLAR1 | PLANT_MAINTENANCE | 296.6667
2022 | nonsummer | ASTORA_2_SOLAR1 | PLANT_TROUBLE | 7
2022 | nonsummer | ASTORA_2_SOLAR1 | TRANSMISSION_INDUCED | 595
2022 | nonsummer | ASTORA_2_SOLAR2 | PLANT_MAINTENANCE | 428.4
2022 | nonsummer | ASTORA_2_SOLAR2 | PLANT_TROUBLE | 93.8875
2022 | nonsummer | ASTORA_2_SOLAR2 | UNIT_TESTING | 148.75
2022 | nonsummer | ATHOS_5_AP1X2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2022 | nonsummer | ATHOS_5_AP1X2 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | ATHOS_5_AP1X2 | METERING_TELEMETRY | 0
2022 | nonsummer | ATHOS_5_AP1X2 | NEW_GENERATOR_TEST_ENERGY | 875
2022 | nonsummer | ATHOS_5_AP1X2 | PLANT_MAINTENANCE | 120.2
2022 | nonsummer | ATHOS_5_AP1X2 | PLANT_TROUBLE | 1425
2022 | nonsummer | ATHOS_5_AP2X2 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | ATHOS_5_AP2X2 | PLANT_MAINTENANCE | 2675.0333
2022 | nonsummer | ATHOS_5_AP2X2 | PLANT_TROUBLE | 814.92
2022 | nonsummer | ATHOS_5_AP2X2 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 2250
2022 | nonsummer | ATWEL2_1_SOLAR1 | PLANT_TROUBLE | 0
2022 | nonsummer | ATWEL2_1_SOLAR1 | RTU_RIG | 100
2022 | nonsummer | ATWEL2_1_SOLAR1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | ATWELL_1_SOLAR | METERING_TELEMETRY | 0
2022 | nonsummer | ATWELL_1_SOLAR | PLANT_TROUBLE | 817.3333
2022 | nonsummer | ATWELL_1_SOLAR | TRANSMISSION_INDUCED | 0
2022 | nonsummer | AVENAL_6_AVPARK | PLANT_TROUBLE | 5
2022 | nonsummer | AVENAL_6_AVPARK | TRANSMISSION_INDUCED | 41.8
2022 | nonsummer | AVENAL_6_AVSLR1 | METERING_TELEMETRY | 118.5
2022 | nonsummer | AVENAL_6_AVSLR1 | PLANT_MAINTENANCE | 39.5
2022 | nonsummer | AVENAL_6_AVSLR1 | PLANT_TROUBLE | 79
2022 | nonsummer | AVENAL_6_AVSLR1 | TRANSMISSION_INDUCED | 341.0167
2022 | nonsummer | AVENAL_6_AVSLR2 | METERING_TELEMETRY | 0
2022 | nonsummer | AVENAL_6_AVSLR2 | PLANT_MAINTENANCE | 39.5
2022 | nonsummer | AVENAL_6_AVSLR2 | PLANT_TROUBLE | 116.3933
2022 | nonsummer | AVENAL_6_AVSLR2 | TRANSMISSION_INDUCED | 459.2533
2022 | nonsummer | AVENAL_6_SANDDG | METERING_TELEMETRY | 0
2022 | nonsummer | AVENAL_6_SANDDG | PLANT_MAINTENANCE | 41.1667
2022 | nonsummer | AVENAL_6_SANDDG | PLANT_TROUBLE | 7.5
2022 | nonsummer | AVENAL_6_SANDDG | TRANSMISSION_INDUCED | 570
2022 | nonsummer | AVENAL_6_SUNCTY | TRANSMISSION_INDUCED | 100
2022 | nonsummer | AVSOLR_2_SOLAR | PLANT_MAINTENANCE | 1135.225
2022 | nonsummer | AVSOLR_2_SOLAR | PLANT_TROUBLE | 0
2022 | nonsummer | BAHIA_2_LKHSR1 | TRANSMISSION_INDUCED | 30
2022 | nonsummer | BALCHS_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 1415.07
2022 | nonsummer | BALCHS_7_UNIT 1 | PLANT_MAINTENANCE | 155
2022 | nonsummer | BALCHS_7_UNIT 1 | PLANT_TROUBLE | 0
2022 | nonsummer | BALCHS_7_UNIT 1 | TRANSITIONAL_LIMITATION | 0
2022 | nonsummer | BALCHS_7_UNIT 1 | TRANSMISSION_INDUCED | 620
2022 | nonsummer | BALCHS_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 4786.2617
2022 | nonsummer | BALCHS_7_UNIT 2 | PLANT_TROUBLE | 0
2022 | nonsummer | BALCHS_7_UNIT 2 | TRANSITIONAL_LIMITATION | 0
2022 | nonsummer | BALCHS_7_UNIT 2 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | BALCHS_7_UNIT 3 | AMBIENT_NOT_DUE_TO_TEMP | 4366.0133
2022 | nonsummer | BALCHS_7_UNIT 3 | TRANSITIONAL_LIMITATION | 0
2022 | nonsummer | BALCHS_7_UNIT 3 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | BANKPP_2_NSPIN | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2022 | nonsummer | BANKPP_2_NSPIN | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | BANKPP_2_NSPIN | METERING_TELEMETRY | 0
2022 | nonsummer | BANKPP_2_NSPIN | PLANT_MAINTENANCE | 0
2022 | nonsummer | BANKPP_2_NSPIN | TRANSMISSION_INDUCED | 0
2022 | nonsummer | BARRE_6_PEAKER | AMBIENT_DUE_TO_TEMP | 1171.65
2022 | nonsummer | BARRE_6_PEAKER | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | BARRE_6_PEAKER | PLANT_MAINTENANCE | 0
2022 | nonsummer | BARRE_6_PEAKER | PLANT_TROUBLE | 390.8833
2022 | nonsummer | BARRE_6_PEAKER | UNIT_TESTING | 58.75
2022 | nonsummer | BASICE_2_UNITS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 4200
2022 | nonsummer | BASICE_2_UNITS | AMBIENT_DUE_TO_TEMP | 2084.64
2022 | nonsummer | BASICE_2_UNITS | PLANT_TROUBLE | 8072.9333
2022 | nonsummer | BASICE_2_UNITS | TRANSMISSION_INDUCED | 0
2022 | nonsummer | BCTSYS_5_PWXDYN | TRANSITIONAL_LIMITATION | 445120
2022 | nonsummer | BDGRCK_1_UNITS | AMBIENT_DUE_TO_TEMP | 3867.2
2022 | nonsummer | BDGRCK_1_UNITS | PLANT_TROUBLE | 70.42
2022 | nonsummer | BDGRCK_1_UNITS | TRANSMISSION_INDUCED | 0
2022 | nonsummer | BDGRCK_1_UNITS | UNIT_TESTING | 27.5627
2022 | nonsummer | BEARDS_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 7.5
2022 | nonsummer | BEARDS_7_UNIT 1 | PLANT_TROUBLE | 1.9167
2022 | nonsummer | BEARDS_7_UNIT 1 | TRANSMISSION_INDUCED | 18.0167
2022 | nonsummer | BEARMT_1_UNIT | AMBIENT_DUE_TO_TEMP | 2870.56
2022 | nonsummer | BEARMT_1_UNIT | PLANT_TROUBLE | 3.8
2022 | nonsummer | BEJNLS_5_BV2SCEDYN | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | BEJNLS_5_BV2SCEDYN | PLANT_TROUBLE | 1366.6167
2022 | nonsummer | BEJNLS_5_BV2SCEDYN | TRANSMISSION_INDUCED | 12788
2022 | nonsummer | BEKWJS_5_BV1SCEDYN | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | BEKWJS_5_BV1SCEDYN | PLANT_TROUBLE | 1072.5
2022 | nonsummer | BEKWJS_5_BV1SCEDYN | TRANSMISSION_INDUCED | 8613.3333
2022 | nonsummer | BELDEN_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 33609.44
2022 | nonsummer | BELDEN_7_UNIT 1 | PLANT_TROUBLE | 0
2022 | nonsummer | BELDEN_7_UNIT 1 | TRANSMISSION_INDUCED | 8388.2167
2022 | nonsummer | BGSKYN_2_AS2SR1 | METERING_TELEMETRY | 0
2022 | nonsummer | BGSKYN_2_AS2SR1 | PLANT_MAINTENANCE | 1603.6
2022 | nonsummer | BGSKYN_2_AS2SR1 | PLANT_TROUBLE | 4924.6667
2022 | nonsummer | BGSKYN_2_AS2SR1 | TRANSMISSION_INDUCED | 210
2022 | nonsummer | BGSKYN_2_AS2SR1 | UNIT_TESTING | 0
2022 | nonsummer | BGSKYN_2_ASPSR2 | PLANT_MAINTENANCE | 706.3333
2022 | nonsummer | BGSKYN_2_ASPSR2 | PLANT_TROUBLE | 8805.3833
2022 | nonsummer | BGSKYN_2_ASPSR2 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | BGSKYN_2_ASPSR2 | UNIT_TESTING | 0
2022 | nonsummer | BGSKYN_2_ASSR1B | NEW_GENERATOR_TEST_ENERGY | 0
2022 | nonsummer | BGSKYN_2_ASSR1B | RTU_RIG | 0
2022 | nonsummer | BGSKYN_2_ASSR1B | TRANSMISSION_INDUCED | 0
2022 | nonsummer | BGSKYN_2_ASSR1B | UNIT_TESTING | 0
2022 | nonsummer | BGSKYN_2_ASSR3A | PLANT_MAINTENANCE | 110.75
2022 | nonsummer | BGSKYN_2_ASSR3A | PLANT_TROUBLE | 50.5
2022 | nonsummer | BGSKYN_2_ASSR3A | TRANSMISSION_INDUCED | 150
2022 | nonsummer | BGSKYN_2_ASSR3A | UNIT_TESTING | 0
2022 | nonsummer | BGSKYN_2_ASSR3B | PLANT_MAINTENANCE | 36.75
2022 | nonsummer | BGSKYN_2_ASSR3B | PLANT_TROUBLE | 572.0833
2022 | nonsummer | BGSKYN_2_ASSR3B | TRANSMISSION_INDUCED | 50
2022 | nonsummer | BGSKYN_2_ASSR3B | UNIT_TESTING | 0
2022 | nonsummer | BGSKYN_2_BS3SR3 | METERING_TELEMETRY | 0
2022 | nonsummer | BGSKYN_2_BS3SR3 | PLANT_MAINTENANCE | 272.6667
2022 | nonsummer | BGSKYN_2_BS3SR3 | PLANT_TROUBLE | 7039.3333
2022 | nonsummer | BIGCRK_2_EXESWD | AMBIENT_NOT_DUE_TO_TEMP | 223044.1
2022 | nonsummer | BIGCRK_2_EXESWD | PLANT_MAINTENANCE | 703.9
2022 | nonsummer | BIGCRK_2_EXESWD | PLANT_TROUBLE | 17214.7333
2022 | nonsummer | BIGCRK_2_EXESWD | TRANSMISSION_INDUCED | 14919.5
2022 | nonsummer | BIGSKY_2_AS2BT1 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | BIGSKY_2_AS2BT1 | ICCP | 0
2022 | nonsummer | BIGSKY_2_AS2BT1 | METERING_TELEMETRY | 0
2022 | nonsummer | BIGSKY_2_AS2BT1 | NEW_GENERATOR_TEST_ENERGY | 0
2022 | nonsummer | BIGSKY_2_AS2BT1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | BIGSKY_2_AS2BT1 | PLANT_TROUBLE | 1880.7833
2022 | nonsummer | BIGSKY_2_AS2BT1 | UNIT_TESTING | 0
2022 | nonsummer | BIGSKY_2_ASLBT2 | NEW_GENERATOR_TEST_ENERGY | 0
2022 | nonsummer | BIGSKY_2_ASLBT2 | PLANT_MAINTENANCE | 0
2022 | nonsummer | BIGSKY_2_ASLBT2 | PLANT_TROUBLE | 1581.25
2022 | nonsummer | BIGSKY_2_ASLBT2 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | BIGSKY_2_ASLBT2 | UNIT_TESTING | 0
2022 | nonsummer | BIGSKY_2_BSKSR6 | PLANT_MAINTENANCE | 128.8
2022 | nonsummer | BIGSKY_2_BSKSR6 | PLANT_TROUBLE | 100
2022 | nonsummer | BIGSKY_2_BSKSR7 | PLANT_MAINTENANCE | 109.1667
2022 | nonsummer | BIGSKY_2_BSKSR7 | PLANT_TROUBLE | 33.025
2022 | nonsummer | BIGSKY_2_BSKSR8 | PLANT_MAINTENANCE | 111.0833
2022 | nonsummer | BIGSKY_2_BSKSR8 | PLANT_TROUBLE | 183.5833
2022 | nonsummer | BIGSKY_2_SOLAR1 | METERING_TELEMETRY | 0
2022 | nonsummer | BIGSKY_2_SOLAR1 | PLANT_MAINTENANCE | 52.5667
2022 | nonsummer | BIGSKY_2_SOLAR1 | PLANT_TROUBLE | 2039.1667
2022 | nonsummer | BIGSKY_2_SOLAR2 | PLANT_TROUBLE | 2341.1667
2022 | nonsummer | BIGSKY_2_SOLAR3 | PLANT_TROUBLE | 214.3583
2022 | nonsummer | BIGSKY_2_SOLAR4 | PLANT_MAINTENANCE | 58
2022 | nonsummer | BIGSKY_2_SOLAR4 | PLANT_TROUBLE | 392.7667
2022 | nonsummer | BIGSKY_2_SOLAR5 | PLANT_TROUBLE | 21.6667
2022 | nonsummer | BIGSKY_2_SOLAR6 | PLANT_MAINTENANCE | 10.6667
2022 | nonsummer | BIGSKY_2_SOLAR6 | PLANT_TROUBLE | 2323.9167
2022 | nonsummer | BIGSKY_2_SOLAR6 | TRANSMISSION_INDUCED | 170
2022 | nonsummer | BIGSKY_2_SOLAR7 | PLANT_MAINTENANCE | 12
2022 | nonsummer | BIGSKY_2_SOLAR7 | PLANT_TROUBLE | 1047.5667
2022 | nonsummer | BIOMAS_1_UNIT 1 | PLANT_TROUBLE | 538.275
2022 | nonsummer | BISHOP_1_ALAMO | AMBIENT_DUE_TO_TEMP | 1748.75
2022 | nonsummer | BISHOP_1_ALAMO | AMBIENT_NOT_DUE_TO_TEMP | 7971.5017
2022 | nonsummer | BISHOP_1_ALAMO | PLANT_MAINTENANCE | 1595.1983
2022 | nonsummer | BISHOP_1_ALAMO | PLANT_TROUBLE | 0
2022 | nonsummer | BISHOP_1_ALAMO | TRANSMISSION_INDUCED | 4.25
2022 | nonsummer | BISHOP_1_UNITS | AMBIENT_DUE_TO_TEMP | 1815
2022 | nonsummer | BISHOP_1_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 9976.0733
2022 | nonsummer | BISHOP_1_UNITS | METERING_TELEMETRY | 0
2022 | nonsummer | BISHOP_1_UNITS | TRANSMISSION_INDUCED | 1.075
2022 | nonsummer | BKRFLD_2_SOLAR1 | METERING_TELEMETRY | 207
2022 | nonsummer | BKRFLD_2_SOLAR1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | BKRFLD_2_SOLAR1 | PLANT_TROUBLE | 857.141
2022 | nonsummer | BLACK_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 3933.0333
2022 | nonsummer | BLACK_7_UNIT 1 | PLANT_TROUBLE | 198.3333
2022 | nonsummer | BLACK_7_UNIT 1 | RTU_RIG | 0
2022 | nonsummer | BLACK_7_UNIT 1 | TRANSMISSION_INDUCED | 148.5
2022 | nonsummer | BLACK_7_UNIT 2 | AMBIENT_DUE_TO_TEMP | 44.1
2022 | nonsummer | BLACK_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 3455.15
2022 | nonsummer | BLACK_7_UNIT 2 | PLANT_TROUBLE | 27.17
2022 | nonsummer | BLACK_7_UNIT 2 | TRANSMISSION_INDUCED | 148.5
2022 | nonsummer | BLAST_1_WIND | METERING_TELEMETRY | 0
2022 | nonsummer | BLAST_1_WIND | PLANT_TROUBLE | 490
2022 | nonsummer | BLAST_1_WIND | TRANSMISSION_INDUCED | 175.2733
2022 | nonsummer | BLCKBT_2_STONEY | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1330.7267
2022 | nonsummer | BLCKBT_2_STONEY | AMBIENT_NOT_DUE_TO_TEMP | 93
2022 | nonsummer | BLCKBT_2_STONEY | ENVIRONMENTAL_RESTRICTIONS | 2503.6633
2022 | nonsummer | BLCKBT_2_STONEY | PLANT_TROUBLE | 0
2022 | nonsummer | BLCKBT_2_STONEY | TRANSMISSION_INDUCED | 248
2022 | nonsummer | BLCKWL_6_SOLAR1 | PLANT_MAINTENANCE | 41.2
2022 | nonsummer | BLCKWL_6_SOLAR1 | PLANT_TROUBLE | 16.4
2022 | nonsummer | BLCKWL_6_SOLAR1 | TRANSMISSION_INDUCED | 114
2022 | nonsummer | BLKCRK_2_GMCBT1 | METERING_TELEMETRY | 0
2022 | nonsummer | BLKCRK_2_GMCBT1 | PLANT_MAINTENANCE | 470.305
2022 | nonsummer | BLKCRK_2_GMCBT1 | PLANT_TROUBLE | 2433.3733
2022 | nonsummer | BLKCRK_2_GMCBT1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | BLKCRK_2_GMCBT1 | UNIT_TESTING | 0
2022 | nonsummer | BLKCRK_2_SOLAR1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | BLKCRK_2_SOLAR1 | PLANT_TROUBLE | 168
2022 | nonsummer | BLKCRK_2_SOLAR1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | BLKDIA_2_BDEBT1 | METERING_TELEMETRY | 246.6667
2022 | nonsummer | BLKDIA_2_BDEBT1 | NEW_GENERATOR_TEST_ENERGY | 25950
2022 | nonsummer | BLKDIA_2_BDEBT1 | PLANT_MAINTENANCE | 223
2022 | nonsummer | BLKDIA_2_BDEBT1 | PLANT_TROUBLE | 1445.9333
2022 | nonsummer | BLKDIA_2_BDEBT1 | TRANSITIONAL_LIMITATION | 6733.1667
2022 | nonsummer | BLM W_2_COSBT1 | METERING_TELEMETRY | 87
2022 | nonsummer | BLM W_2_COSBT1 | NEW_GENERATOR_TEST_ENERGY | 0
2022 | nonsummer | BLM W_2_COSBT1 | PLANT_MAINTENANCE | 1848.6667
2022 | nonsummer | BLM W_2_COSBT1 | PLANT_TROUBLE | 3107.8233
2022 | nonsummer | BLM W_2_COSBT1 | RTU_RIG | 0
2022 | nonsummer | BLM W_2_COSBT1 | UNIT_TESTING | 4976
2022 | nonsummer | BLM_2_UNITS | PLANT_MAINTENANCE | 820
2022 | nonsummer | BLM_2_UNITS | PLANT_TROUBLE | 573.6
2022 | nonsummer | BLM_2_UNITS | TRANSMISSION_INDUCED | 131.8
2022 | nonsummer | BLYTHE_1_SOLAR1 | METERING_TELEMETRY | 210
2022 | nonsummer | BLYTHE_1_SOLAR1 | PLANT_MAINTENANCE | 80
2022 | nonsummer | BLYTHE_1_SOLAR1 | PLANT_TROUBLE | 286.575
2022 | nonsummer | BLYTHE_1_SOLAR1 | TRANSMISSION_INDUCED | 105
2022 | nonsummer | BLYTHE_1_SOLAR2 | PLANT_MAINTENANCE | 54.3333
2022 | nonsummer | BLYTHE_1_SOLAR2 | PLANT_TROUBLE | 115
2022 | nonsummer | BLYTHE_1_SOLAR2 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | BNNIEN_7_ALTAPH | AMBIENT_NOT_DUE_TO_TEMP | 77.9
2022 | nonsummer | BNNIEN_7_ALTAPH | PLANT_MAINTENANCE | 0
2022 | nonsummer | BNNIEN_7_ALTAPH | PLANT_TROUBLE | 0
2022 | nonsummer | BNNIEN_7_ALTAPH | TRANSMISSION_INDUCED | 0
2022 | nonsummer | BOGUE_1_UNITA1 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | BOGUE_1_UNITA1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | BOGUE_1_UNITA1 | PLANT_TROUBLE | 1898.4467
2022 | nonsummer | BORDER_6_UNITA1 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | BORDER_6_UNITA1 | AMBIENT_NOT_DUE_TO_TEMP | 265.3333
2022 | nonsummer | BORDER_6_UNITA1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | BORDER_6_UNITA1 | PLANT_TROUBLE | 4945.1667
2022 | nonsummer | BORDER_6_UNITA1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | BOWMN_6_HYDRO | AMBIENT_NOT_DUE_TO_TEMP | 2070
2022 | nonsummer | BOWMN_6_HYDRO | PLANT_MAINTENANCE | 0
2022 | nonsummer | BOWMN_6_HYDRO | PLANT_TROUBLE | 0
2022 | nonsummer | BOWMN_6_HYDRO | TRANSMISSION_INDUCED | 12.6
2022 | nonsummer | BRDGVL_7_BAKER | PLANT_TROUBLE | 327.8
2022 | nonsummer | BRDSLD_2_HIWIND | PLANT_MAINTENANCE | 19343.7633
2022 | nonsummer | BRDSLD_2_HIWIND | PLANT_TROUBLE | 0
2022 | nonsummer | BRDSLD_2_HIWIND | TRANSMISSION_INDUCED | 0
2022 | nonsummer | BRDSLD_2_MTZUM2 | PLANT_MAINTENANCE | 2916.78
2022 | nonsummer | BRDSLD_2_MTZUM2 | PLANT_TROUBLE | 0
2022 | nonsummer | BRDSLD_2_MTZUM2 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | BRDSLD_2_MTZUMA | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | BRDSLD_2_MTZUMA | PLANT_MAINTENANCE | 2217.66
2022 | nonsummer | BRDSLD_2_MTZUMA | TRANSMISSION_INDUCED | 0
2022 | nonsummer | BRDSLD_2_SHILO1 | PLANT_MAINTENANCE | 74.25
2022 | nonsummer | BRDSLD_2_SHILO1 | PLANT_TROUBLE | 344.05
2022 | nonsummer | BRDSLD_2_SHILO1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | BRDSLD_2_SHILO2 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | BRDSLD_2_SHILO2 | METERING_TELEMETRY | 0
2022 | nonsummer | BRDSLD_2_SHILO2 | PLANT_MAINTENANCE | 13423.7333
2022 | nonsummer | BRDSLD_2_SHILO2 | PLANT_TROUBLE | 42.8333
2022 | nonsummer | BRDSLD_2_SHILO2 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | BRDSLD_2_SHILO2 | UNIT_TESTING | 210
2022 | nonsummer | BRDSLD_2_SHLO3A | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | BRDSLD_2_SHLO3A | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | BRDSLD_2_SHLO3A | METERING_TELEMETRY | 134.2
2022 | nonsummer | BRDSLD_2_SHLO3A | PLANT_MAINTENANCE | 8804.3233
2022 | nonsummer | BRDSLD_2_SHLO3A | PLANT_TROUBLE | 0
2022 | nonsummer | BRDSLD_2_SHLO3A | TRANSMISSION_INDUCED | 0
2022 | nonsummer | BRDSLD_2_SHLO3B | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | BRDSLD_2_SHLO3B | METERING_TELEMETRY | 0
2022 | nonsummer | BRDSLD_2_SHLO3B | PLANT_MAINTENANCE | 2270.4442
2022 | nonsummer | BRDSLD_2_SHLO3B | TRANSMISSION_INDUCED | 0
2022 | nonsummer | BREGGO_6_DEGRSL | PLANT_MAINTENANCE | 0
2022 | nonsummer | BREGGO_6_DEGRSL | PLANT_TROUBLE | 96.09
2022 | nonsummer | BREGGO_6_DEGRSL | TRANSMISSION_INDUCED | 409.5
2022 | nonsummer | BREGGO_6_SOLAR | PLANT_MAINTENANCE | 126.5333
2022 | nonsummer | BREGGO_6_SOLAR | PLANT_TROUBLE | 66
2022 | nonsummer | BREGGO_6_SOLAR | TRANSMISSION_INDUCED | 780
2022 | nonsummer | BREGGO_6_SOLAR | UNIT_TESTING | 0
2022 | nonsummer | BRODIE_2_WIND | PLANT_MAINTENANCE | 1764.15
2022 | nonsummer | BRODIE_2_WIND | PLANT_TROUBLE | 0
2022 | nonsummer | BUCKBL_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | BUCKBL_2_PL1X3 | PLANT_MAINTENANCE | 293.3333
2022 | nonsummer | BUCKBL_2_PL1X3 | PLANT_TROUBLE | 1261.011
2022 | nonsummer | BUCKBL_2_PL1X3 | TRANSMISSION_INDUCED | 5208.9
2022 | nonsummer | BUCKBL_2_PL1X3 | UNIT_TESTING | 1213.1968
2022 | nonsummer | BUCKCK_2_HYDRO | TRANSMISSION_INDUCED | 0
2022 | nonsummer | BUCKCK_7_OAKFLT | AMBIENT_NOT_DUE_TO_TEMP | 13
2022 | nonsummer | BUCKCK_7_OAKFLT | PLANT_MAINTENANCE | 572
2022 | nonsummer | BUCKCK_7_OAKFLT | TRANSMISSION_INDUCED | 786.5
2022 | nonsummer | BUCKCK_7_PL1X2 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | BUCKCK_7_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 350.6667
2022 | nonsummer | BUCKCK_7_PL1X2 | PLANT_MAINTENANCE | 2667.5
2022 | nonsummer | BUCKCK_7_PL1X2 | PLANT_TROUBLE | 0
2022 | nonsummer | BUCKCK_7_PL1X2 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | BUCKCK_7_PL1X2 | UNIT_TESTING | 0
2022 | nonsummer | BUCKWD_1_QF | PLANT_MAINTENANCE | 2958.8083
2022 | nonsummer | BUCKWD_1_QF | PLANT_TROUBLE | 372
2022 | nonsummer | BUCKWD_1_QF | UNIT_TESTING | 0
2022 | nonsummer | BUCKWD_7_WINTCV | PLANT_MAINTENANCE | 0
2022 | nonsummer | BUCKWD_7_WINTCV | PLANT_TROUBLE | 323.29
2022 | nonsummer | BUCKWD_7_WINTCV | TRANSMISSION_INDUCED | 6.6
2022 | nonsummer | BURNYF_2_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 57.0333
2022 | nonsummer | BURNYF_2_UNIT 1 | PLANT_MAINTENANCE | 411.1468
2022 | nonsummer | BURNYF_2_UNIT 1 | PLANT_TROUBLE | 1053.008
2022 | nonsummer | BURNYF_2_UNIT 1 | TRANSMISSION_INDUCED | 203
2022 | nonsummer | BUTTVL_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 108.625
2022 | nonsummer | BUTTVL_7_UNIT 1 | PLANT_TROUBLE | 23.0417
2022 | nonsummer | BUTTVL_7_UNIT 1 | TRANSMISSION_INDUCED | 73.7333
2022 | nonsummer | CABALO_2_M2BSR1 | PLANT_MAINTENANCE | 827.5
2022 | nonsummer | CABALO_2_M2BSR1 | PLANT_TROUBLE | 1996
2022 | nonsummer | CABALO_2_M2WSR2 | PLANT_MAINTENANCE | 2608.2
2022 | nonsummer | CABALO_2_M2WSR2 | PLANT_TROUBLE | 6891.2592
2022 | nonsummer | CABALO_2_M2WSR2 | UNIT_TESTING | 0
2022 | nonsummer | CABZON_1_WINDA1 | PLANT_MAINTENANCE | 239.1667
2022 | nonsummer | CABZON_1_WINDA1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | CALFTN_2_CFSBT1 | METERING_TELEMETRY | 0
2022 | nonsummer | CALFTN_2_CFSBT1 | PLANT_MAINTENANCE | 600
2022 | nonsummer | CALFTN_2_CFSBT1 | PLANT_TROUBLE | 1500
2022 | nonsummer | CALFTN_2_CFSBT1 | RTU_RIG | 0
2022 | nonsummer | CALFTN_2_SOLAR | PLANT_MAINTENANCE | 1163.5
2022 | nonsummer | CALFTS_2_CFSSR1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | CALFTS_2_CFSSR1 | METERING_TELEMETRY | 0
2022 | nonsummer | CALFTS_2_CFSSR1 | PLANT_TROUBLE | 0
2022 | nonsummer | CALGEN_1_UNITS | PLANT_MAINTENANCE | 0
2022 | nonsummer | CALGEN_1_UNITS | PLANT_TROUBLE | 770
2022 | nonsummer | CALGEN_1_UNITS | TRANSMISSION_INDUCED | 60
2022 | nonsummer | CALPIN_1_AGNEW | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1856.4
2022 | nonsummer | CALPIN_1_AGNEW | AMBIENT_DUE_TO_TEMP | 17.94
2022 | nonsummer | CALPIN_1_AGNEW | AMBIENT_NOT_DUE_TO_TEMP | 3426.64
2022 | nonsummer | CALPIN_1_AGNEW | ENVIRONMENTAL_RESTRICTIONS | 134.8067
2022 | nonsummer | CALPIN_1_AGNEW | METERING_TELEMETRY | 0
2022 | nonsummer | CALPIN_1_AGNEW | PLANT_TROUBLE | 1885.276
2022 | nonsummer | CALPIN_1_AGNEW | TRANSITIONAL_LIMITATION | 0
2022 | nonsummer | CALPIN_1_AGNEW | UNIT_TESTING | 16.184
2022 | nonsummer | CALPSS_6_SOLAR1 | PLANT_MAINTENANCE | 69.65
2022 | nonsummer | CALPSS_6_SOLAR1 | PLANT_TROUBLE | 99
2022 | nonsummer | CALPSS_6_SOLAR1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | CAMCHE_1_PL1X3 | AMBIENT_NOT_DUE_TO_TEMP | 9129.6
2022 | nonsummer | CAMCHE_1_PL1X3 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | CAMCHE_1_PL1X3 | PLANT_TROUBLE | 16
2022 | nonsummer | CAMLOT_2_SOLAR1 | PLANT_MAINTENANCE | 135
2022 | nonsummer | CAMLOT_2_SOLAR1 | PLANT_TROUBLE | 937.5
2022 | nonsummer | CAMLOT_2_SOLAR2 | AMBIENT_NOT_DUE_TO_TEMP | 123.75
2022 | nonsummer | CAMLOT_2_SOLAR2 | PLANT_TROUBLE | 0
2022 | nonsummer | CAMLOT_2_SOLAR2 | TRANSMISSION_INDUCED | 225
2022 | nonsummer | CAMPFW_7_FARWST | AMBIENT_NOT_DUE_TO_TEMP | 1190
2022 | nonsummer | CAMPFW_7_FARWST | PLANT_TROUBLE | 34
2022 | nonsummer | CAMPFW_7_FARWST | TRANSMISSION_INDUCED | 17.5667
2022 | nonsummer | CAMPFW_7_FARWST | UNIT_TESTING | 6.8
2022 | nonsummer | CANTUA_1_SOLAR | PLANT_MAINTENANCE | 700
2022 | nonsummer | CANTUA_1_SOLAR | TRANSMISSION_INDUCED | 85.6667
2022 | nonsummer | CAPWD_1_QF | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | CAPWD_1_QF | PLANT_MAINTENANCE | 0
2022 | nonsummer | CAPWD_1_QF | PLANT_TROUBLE | 5962.75
2022 | nonsummer | CARBOU_7_PL2X3 | AMBIENT_NOT_DUE_TO_TEMP | 24503
2022 | nonsummer | CARBOU_7_PL2X3 | PLANT_MAINTENANCE | 0
2022 | nonsummer | CARBOU_7_PL2X3 | PLANT_TROUBLE | 0
2022 | nonsummer | CARBOU_7_PL2X3 | TRANSITIONAL_LIMITATION | 32.0833
2022 | nonsummer | CARBOU_7_PL2X3 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | CARBOU_7_PL4X5 | AMBIENT_NOT_DUE_TO_TEMP | 53470.6567
2022 | nonsummer | CARBOU_7_PL4X5 | PLANT_TROUBLE | 100
2022 | nonsummer | CARBOU_7_PL4X5 | TRANSMISSION_INDUCED | 178
2022 | nonsummer | CARBOU_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 4225.9667
2022 | nonsummer | CARBOU_7_UNIT 1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | CARBOU_7_UNIT 1 | TRANSMISSION_INDUCED | 35.2
2022 | nonsummer | CARLS1_2_CARCT1 | AMBIENT_DUE_TO_TEMP | 184.3
2022 | nonsummer | CARLS1_2_CARCT1 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | CARLS1_2_CARCT1 | PLANT_MAINTENANCE | 1582.5
2022 | nonsummer | CARLS1_2_CARCT1 | PLANT_TROUBLE | 2757.6633
2022 | nonsummer | CARLS1_2_CARCT1 | SHORT_TERM_USE_LIMIT_REACHED | 81762.5
2022 | nonsummer | CARLS1_2_CARCT1 | UNIT_TESTING | 181.5417
2022 | nonsummer | CARLS2_1_CARCT1 | AMBIENT_DUE_TO_TEMP | 70.01
2022 | nonsummer | CARLS2_1_CARCT1 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | CARLS2_1_CARCT1 | PLANT_MAINTENANCE | 124.8417
2022 | nonsummer | CARLS2_1_CARCT1 | PLANT_TROUBLE | 994.1162
2022 | nonsummer | CARLS2_1_CARCT1 | UNIT_TESTING | 0
2022 | nonsummer | CATLNA_2_SOLAR | PLANT_TROUBLE | 7.95
2022 | nonsummer | CATLNA_2_SOLAR2 | PLANT_MAINTENANCE | 0
2022 | nonsummer | CATLNA_2_SOLAR2 | UNIT_TESTING | 0
2022 | nonsummer | CAVLSR_2_BSOLAR | METERING_TELEMETRY | 0
2022 | nonsummer | CAVLSR_2_BSOLAR | PLANT_MAINTENANCE | 0
2022 | nonsummer | CAVLSR_2_BSOLAR | PLANT_TROUBLE | 306.2167
2022 | nonsummer | CAVLSR_2_RSOLAR | METERING_TELEMETRY | 0
2022 | nonsummer | CAVLSR_2_RSOLAR | PLANT_MAINTENANCE | 180
2022 | nonsummer | CAVLSR_2_RSOLAR | PLANT_TROUBLE | 1693.1367
2022 | nonsummer | CAYTNO_2_VASCO | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2022 | nonsummer | CAYTNO_2_VASCO | PLANT_MAINTENANCE | 20.585
2022 | nonsummer | CAYTNO_2_VASCO | PLANT_TROUBLE | 259.6142
2022 | nonsummer | CAYTNO_2_VASCO | TRANSMISSION_INDUCED | 7.74
2022 | nonsummer | CEDRCK_6_UNIT | TRANSMISSION_INDUCED | 40.18
2022 | nonsummer | CEDUCR_2_SOLAR3 | PLANT_MAINTENANCE | 0
2022 | nonsummer | CEDUCR_2_SOLAR4 | PLANT_MAINTENANCE | 0
2022 | nonsummer | CENT40_1_C40SR1 | PLANT_MAINTENANCE | 238.6667
2022 | nonsummer | CENT40_1_C40SR1 | PLANT_TROUBLE | 1871.3333
2022 | nonsummer | CENT40_1_C40SR1 | TRANSMISSION_INDUCED | 1120
2022 | nonsummer | CENTER_2_RHONDO | AMBIENT_NOT_DUE_TO_TEMP | 1715.05
2022 | nonsummer | CENTER_6_PEAKER | AMBIENT_DUE_TO_TEMP | 27.9
2022 | nonsummer | CENTER_6_PEAKER | ENVIRONMENTAL_RESTRICTIONS | 473
2022 | nonsummer | CENTER_6_PEAKER | PLANT_MAINTENANCE | 132.44
2022 | nonsummer | CENTER_6_PEAKER | PLANT_TROUBLE | 631.36
2022 | nonsummer | CENTER_6_PEAKER | UNIT_TESTING | 0
2022 | nonsummer | CENTPD_2_BMSSX2 | NEW_GENERATOR_TEST_ENERGY | 0
2022 | nonsummer | CENTPD_2_BMSX2 | NEW_GENERATOR_TEST_ENERGY | 0
2022 | nonsummer | CENTPD_2_BMSX2 | UNIT_TESTING | 1232
2022 | nonsummer | CENTRY_6_PL1X4 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | CENTRY_6_PL1X4 | METERING_TELEMETRY | 0
2022 | nonsummer | CENTRY_6_PL1X4 | PLANT_MAINTENANCE | 2024.59
2022 | nonsummer | CENTRY_6_PL1X4 | PLANT_TROUBLE | 2227.56
2022 | nonsummer | CENTRY_6_PL1X4 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | CENTRY_6_PL1X4 | UNIT_TESTING | 10.01
2022 | nonsummer | CHALK_1_UNIT | AMBIENT_DUE_TO_TEMP | 3461.1785
2022 | nonsummer | CHALK_1_UNIT | PLANT_MAINTENANCE | 0
2022 | nonsummer | CHALK_1_UNIT | PLANT_TROUBLE | 0
2022 | nonsummer | CHALK_1_UNIT | TRANSMISSION_INDUCED | 0
2022 | nonsummer | CHALK_1_UNIT | UNIT_TESTING | 20.7882
2022 | nonsummer | CHARMN_2_PGONG1 | PLANT_MAINTENANCE | 298.05
2022 | nonsummer | CHARMN_2_PGONG1 | PLANT_TROUBLE | 0
2022 | nonsummer | CHEVCY_1_UNIT | PLANT_MAINTENANCE | 0
2022 | nonsummer | CHEVCY_1_UNIT | PLANT_TROUBLE | 161.19
2022 | nonsummer | CHEVMN_2_UNITS | PLANT_MAINTENANCE | 16554.15
2022 | nonsummer | CHICPK_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 21394.0017
2022 | nonsummer | CHICPK_7_UNIT 1 | PLANT_TROUBLE | 201
2022 | nonsummer | CHICPK_7_UNIT 1 | TRANSMISSION_INDUCED | 294
2022 | nonsummer | CHILLS_1_SYCENG | METERING_TELEMETRY | 0
2022 | nonsummer | CHILLS_1_SYCENG | PLANT_MAINTENANCE | 0
2022 | nonsummer | CHILLS_1_SYCENG | PLANT_TROUBLE | 68.4475
2022 | nonsummer | CHILLS_7_UNITA1 | PLANT_MAINTENANCE | 11.25
2022 | nonsummer | CHILLS_7_UNITA1 | PLANT_TROUBLE | 541.5
2022 | nonsummer | CHINO_2_APEBT1 | METERING_TELEMETRY | 0
2022 | nonsummer | CHINO_2_APEBT1 | PLANT_MAINTENANCE | 460
2022 | nonsummer | CHINO_2_APEBT1 | PLANT_TROUBLE | 520.4233
2022 | nonsummer | CHINO_2_APEBT1 | UNIT_TESTING | 0
2022 | nonsummer | CHINO_6_CIMGEN | PLANT_TROUBLE | 0
2022 | nonsummer | CHINO_6_CIMGEN | TRANSMISSION_INDUCED | 4.3333
2022 | nonsummer | CHWCHL_1_BIOMAS | PLANT_MAINTENANCE | 377.6
2022 | nonsummer | CHWCHL_1_BIOMAS | PLANT_TROUBLE | 3068.6
2022 | nonsummer | CHWCHL_1_UNIT | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | CHWCHL_1_UNIT | PLANT_MAINTENANCE | 217
2022 | nonsummer | CHWCHL_1_UNIT | PLANT_TROUBLE | 945.5
2022 | nonsummer | CHWCHL_1_UNIT | TRANSMISSION_INDUCED | 0
2022 | nonsummer | CLINESCO_3_PVDYN | PLANT_TROUBLE | 131.412
2022 | nonsummer | CLINESCO_3_PVDYN | TRANSMISSION_INDUCED | 10208.52
2022 | nonsummer | CLINESCO_3_WBDYN | PLANT_TROUBLE | 0
2022 | nonsummer | CLINESCO_3_WBDYN | TRANSMISSION_INDUCED | 26529.84
2022 | nonsummer | CLOVDL_1_SOLAR | PLANT_TROUBLE | 1462.5
2022 | nonsummer | CLOVER_2_UNIT | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 12.5235
2022 | nonsummer | CLOVER_2_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | CLOVER_2_UNIT | PLANT_TROUBLE | 6.6
2022 | nonsummer | CLOVER_2_UNIT | TRANSMISSION_INDUCED | 14.355
2022 | nonsummer | CNTNLA_2_SOLAR1 | PLANT_TROUBLE | 0
2022 | nonsummer | CNTNLA_2_SOLAR1 | TRANSMISSION_INDUCED | 2125
2022 | nonsummer | CNTNLA_2_SOLAR2 | TRANSMISSION_INDUCED | 775.2
2022 | nonsummer | COCOPP_2_CTG1 | AMBIENT_DUE_TO_TEMP | 3656.98
2022 | nonsummer | COCOPP_2_CTG1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | COCOPP_2_CTG1 | PLANT_TROUBLE | 0
2022 | nonsummer | COCOPP_2_CTG2 | AMBIENT_DUE_TO_TEMP | 3049.65
2022 | nonsummer | COCOPP_2_CTG2 | PLANT_MAINTENANCE | 0
2022 | nonsummer | COCOPP_2_CTG2 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2022 | nonsummer | COCOPP_2_CTG3 | AMBIENT_DUE_TO_TEMP | 10157.1207
2022 | nonsummer | COCOPP_2_CTG3 | METERING_TELEMETRY | 1077.9
2022 | nonsummer | COCOPP_2_CTG3 | PLANT_MAINTENANCE | 0
2022 | nonsummer | COCOPP_2_CTG3 | PLANT_TROUBLE | 0
2022 | nonsummer | COCOPP_2_CTG3 | UNIT_TESTING | 774.8193
2022 | nonsummer | COCOPP_2_CTG4 | AMBIENT_DUE_TO_TEMP | 5329.1723
2022 | nonsummer | COCOPP_2_CTG4 | METERING_TELEMETRY | 97.845
2022 | nonsummer | COCOPP_2_CTG4 | PLANT_MAINTENANCE | 0
2022 | nonsummer | COCOPP_2_CTG4 | PLANT_TROUBLE | 0
2022 | nonsummer | COCOPP_2_CTG4 | UNIT_TESTING | 782.0953
2022 | nonsummer | COGNAT_1_UNIT | PLANT_MAINTENANCE | 225
2022 | nonsummer | COGNAT_1_UNIT | PLANT_TROUBLE | 2738.4167
2022 | nonsummer | COGNAT_1_UNIT | TRANSMISSION_INDUCED | 225
2022 | nonsummer | COLEMN_2_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 2065.7833
2022 | nonsummer | COLEMN_2_UNIT | PLANT_MAINTENANCE | 0
2022 | nonsummer | COLEMN_2_UNIT | PLANT_TROUBLE | 283.3167
2022 | nonsummer | COLGAT_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 20448.67
2022 | nonsummer | COLGAT_7_UNIT 1 | ENVIRONMENTAL_RESTRICTIONS | 357
2022 | nonsummer | COLGAT_7_UNIT 1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | COLGAT_7_UNIT 1 | PLANT_TROUBLE | 4692
2022 | nonsummer | COLGAT_7_UNIT 1 | TRANSMISSION_INDUCED | 222.1667
2022 | nonsummer | COLGAT_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 22663.5333
2022 | nonsummer | COLGAT_7_UNIT 2 | ENVIRONMENTAL_RESTRICTIONS | 357
2022 | nonsummer | COLGAT_7_UNIT 2 | PLANT_MAINTENANCE | 0
2022 | nonsummer | COLGAT_7_UNIT 2 | PLANT_TROUBLE | 755
2022 | nonsummer | COLGAT_7_UNIT 2 | TRANSMISSION_INDUCED | 570
2022 | nonsummer | COLGNS_2_CNSSR1 | PLANT_MAINTENANCE | 6800.2767
2022 | nonsummer | COLGNS_2_CNSSR1 | PLANT_TROUBLE | 5018.5
2022 | nonsummer | COLGNS_2_CNSSR1 | TRANSITIONAL_LIMITATION | 139.2
2022 | nonsummer | COLGNS_2_CNSSR1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | COLPIN_6_COLLNS | PLANT_MAINTENANCE | 0
2022 | nonsummer | COLPIN_6_COLLNS | PLANT_TROUBLE | 168.3
2022 | nonsummer | COLPIN_6_COLLNS | TRANSMISSION_INDUCED | 0
2022 | nonsummer | COLTON_6_AGUAM1 | AMBIENT_DUE_TO_TEMP | 600
2022 | nonsummer | COLTON_6_AGUAM1 | METERING_TELEMETRY | 0
2022 | nonsummer | COLTON_6_AGUAM1 | UNIT_TESTING | 123
2022 | nonsummer | COLUSA_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 16284.4
2022 | nonsummer | COLUSA_2_PL1X3 | METERING_TELEMETRY | 0
2022 | nonsummer | COLUSA_2_PL1X3 | PLANT_MAINTENANCE | 8493.25
2022 | nonsummer | COLUSA_2_PL1X3 | PLANT_TROUBLE | 16161.7347
2022 | nonsummer | COLUSA_2_PL1X3 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2022 | nonsummer | COLUSA_2_PL1X3 | UNIT_TESTING | 0
2022 | nonsummer | COLVIL_7_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 1234.3
2022 | nonsummer | COLVIL_7_PL1X2 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | COLVIL_7_PL1X2 | PLANT_MAINTENANCE | 0
2022 | nonsummer | COLVIL_7_PL1X2 | PLANT_TROUBLE | 0
2022 | nonsummer | CONTRL_1_CASAD1 | METERING_TELEMETRY | 0
2022 | nonsummer | CONTRL_1_CASAD1 | PLANT_MAINTENANCE | 79.5083
2022 | nonsummer | CONTRL_1_CASAD1 | PLANT_TROUBLE | 384.145
2022 | nonsummer | CONTRL_1_CASAD2 | AMBIENT_DUE_TO_TEMP | 333.4467
2022 | nonsummer | CONTRL_1_CASAD2 | PLANT_MAINTENANCE | 76.8433
2022 | nonsummer | CONTRL_1_CASAD2 | PLANT_TROUBLE | 25.4783
2022 | nonsummer | CONTRL_1_CASAD3 | METERING_TELEMETRY | 0
2022 | nonsummer | CONTRL_1_CASAD3 | PLANT_MAINTENANCE | 87.3
2022 | nonsummer | CONTRL_1_CASAD3 | PLANT_TROUBLE | 528.0117
2022 | nonsummer | CONTRL_1_LUNDY | AMBIENT_DUE_TO_TEMP | 376.5
2022 | nonsummer | CONTRL_1_LUNDY | AMBIENT_NOT_DUE_TO_TEMP | 2222.6
2022 | nonsummer | CONTRL_1_LUNDY | PLANT_TROUBLE | 0
2022 | nonsummer | CONTRL_1_LUNDY | TRANSMISSION_INDUCED | 15.4275
2022 | nonsummer | CONTRL_1_OXBOW | AMBIENT_DUE_TO_TEMP | 282.3292
2022 | nonsummer | CONTRL_1_OXBOW | AMBIENT_NOT_DUE_TO_TEMP | 64.9583
2022 | nonsummer | CONTRL_1_OXBOW | METERING_TELEMETRY | 0
2022 | nonsummer | CONTRL_1_OXBOW | PLANT_TROUBLE | 11840
2022 | nonsummer | CONTRL_1_OXBOW | TRANSMISSION_INDUCED | 0
2022 | nonsummer | CONTRL_1_OXBOW | UNIT_SUPPORTING_STARTUP | 0
2022 | nonsummer | CONTRL_1_POOLE | AMBIENT_DUE_TO_TEMP | 640.24
2022 | nonsummer | CONTRL_1_POOLE | AMBIENT_NOT_DUE_TO_TEMP | 8413.71
2022 | nonsummer | CONTRL_1_POOLE | METERING_TELEMETRY | 0
2022 | nonsummer | CONTRL_1_POOLE | PLANT_MAINTENANCE | 62.1
2022 | nonsummer | CONTRL_1_POOLE | TRANSMISSION_INDUCED | 1.71
2022 | nonsummer | CONTRL_1_RUSHCK | AMBIENT_DUE_TO_TEMP | 1063.9
2022 | nonsummer | CONTRL_1_RUSHCK | AMBIENT_NOT_DUE_TO_TEMP | 5816.4
2022 | nonsummer | CONTRL_1_RUSHCK | TRANSMISSION_INDUCED | 130.53
2022 | nonsummer | COPMT2_2_SOLAR2 | METERING_TELEMETRY | 0
2022 | nonsummer | COPMT2_2_SOLAR2 | PLANT_TROUBLE | 63.4
2022 | nonsummer | COPMT2_2_SOLAR2 | TRANSMISSION_INDUCED | 620
2022 | nonsummer | COPMT4_2_SOLAR4 | PLANT_TROUBLE | 184
2022 | nonsummer | COPMT4_2_SOLAR4 | TRANSMISSION_INDUCED | 668.5333
2022 | nonsummer | COPMTN_2_CM10 | PLANT_TROUBLE | 20.8333
2022 | nonsummer | COPMTN_2_CM10 | TRANSMISSION_INDUCED | 60
2022 | nonsummer | COPMTN_2_SOLAR1 | TRANSMISSION_INDUCED | 288
2022 | nonsummer | CORCAN_1_SOLAR1 | PLANT_TROUBLE | 100
2022 | nonsummer | CORCAN_1_SOLAR1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | CORONS_6_CLRWTR | PLANT_MAINTENANCE | 0
2022 | nonsummer | CORONS_6_CLRWTR | PLANT_TROUBLE | 0
2022 | nonsummer | CORRAL_6_SJOAQN | PLANT_MAINTENANCE | 10.75
2022 | nonsummer | CORRAL_6_SJOAQN | PLANT_TROUBLE | 170.4
2022 | nonsummer | CORRAL_6_SJOAQN | TRANSMISSION_INDUCED | 189.2
2022 | nonsummer | COVERD_2_HCKHY1 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | COVERD_2_HCKHY1 | PLANT_TROUBLE | 16.6508
2022 | nonsummer | COVERD_2_HCKHY1 | TRANSMISSION_INDUCED | 20.67
2022 | nonsummer | COVERD_2_MCKHY1 | AMBIENT_NOT_DUE_TO_TEMP | 2205
2022 | nonsummer | COVERD_2_QFUNTS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2022 | nonsummer | COVERD_2_QFUNTS | TRANSMISSION_INDUCED | 1.8333
2022 | nonsummer | COVERD_2_RCKHY1 | AMBIENT_NOT_DUE_TO_TEMP | 110.5
2022 | nonsummer | COVERD_2_RCKHY1 | ENVIRONMENTAL_RESTRICTIONS | 290
2022 | nonsummer | COVERD_2_RCKHY1 | PLANT_MAINTENANCE | 55.9333
2022 | nonsummer | COVERD_2_RCKHY1 | TRANSMISSION_INDUCED | 9.5
2022 | nonsummer | COWCRK_2_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 226.8
2022 | nonsummer | COWCRK_2_UNIT | PLANT_TROUBLE | 10
2022 | nonsummer | CPVERD_2_SOLAR | PLANT_MAINTENANCE | 596.75
2022 | nonsummer | CPVERD_2_SOLAR | PLANT_TROUBLE | 120
2022 | nonsummer | CRELMN_6_RAMON1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | CRELMN_6_RAMON1 | PLANT_TROUBLE | 0
2022 | nonsummer | CRELMN_6_RAMON2 | PLANT_MAINTENANCE | 0
2022 | nonsummer | CRELMN_6_RAMON2 | PLANT_TROUBLE | 0
2022 | nonsummer | CRELMN_6_RAMSR3 | PLANT_TROUBLE | 4557.6
2022 | nonsummer | CRESTA_7_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 20488.2453
2022 | nonsummer | CRESTA_7_PL1X2 | PLANT_TROUBLE | 0
2022 | nonsummer | CRESTA_7_PL1X2 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | CRIMSN_2_CRMBT1 | AMBIENT_NOT_DUE_TO_TEMP | 36
2022 | nonsummer | CRIMSN_2_CRMBT1 | METERING_TELEMETRY | 0
2022 | nonsummer | CRIMSN_2_CRMBT1 | NEW_GENERATOR_TEST_ENERGY | 0
2022 | nonsummer | CRIMSN_2_CRMBT1 | PLANT_MAINTENANCE | 83.3333
2022 | nonsummer | CRIMSN_2_CRMBT1 | PLANT_TROUBLE | 3871
2022 | nonsummer | CRIMSN_2_CRMBT1 | UNIT_TESTING | 0
2022 | nonsummer | CRIMSN_2_CRMBT2 | METERING_TELEMETRY | 0
2022 | nonsummer | CRIMSN_2_CRMBT2 | NEW_GENERATOR_TEST_ENERGY | 0
2022 | nonsummer | CRIMSN_2_CRMBT2 | PLANT_MAINTENANCE | 0
2022 | nonsummer | CRIMSN_2_CRMBT2 | PLANT_TROUBLE | 0
2022 | nonsummer | CRNEVL_6_CRNVA | AMBIENT_NOT_DUE_TO_TEMP | 107.1
2022 | nonsummer | CRNEVL_6_CRNVA | PLANT_TROUBLE | 614.7
2022 | nonsummer | CRNEVL_6_CRNVA | TRANSMISSION_INDUCED | 8.55
2022 | nonsummer | CRNEVL_6_SJQN 2 | AMBIENT_NOT_DUE_TO_TEMP | 421.7067
2022 | nonsummer | CRNEVL_6_SJQN 2 | PLANT_MAINTENANCE | 2197.12
2022 | nonsummer | CRNEVL_6_SJQN 2 | PLANT_TROUBLE | 10.72
2022 | nonsummer | CRNEVL_6_SJQN 2 | TRANSMISSION_INDUCED | 30.4
2022 | nonsummer | CROKET_7_UNIT | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | CROKET_7_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | CROKET_7_UNIT | PLANT_MAINTENANCE | 6076
2022 | nonsummer | CROKET_7_UNIT | PLANT_TROUBLE | 1844
2022 | nonsummer | CROKET_7_UNIT | TRANSMISSION_INDUCED | 5840
2022 | nonsummer | CRSTWD_6_KUMYAY | METERING_TELEMETRY | 20
2022 | nonsummer | CRSTWD_6_KUMYAY | PLANT_MAINTENANCE | 27.4667
2022 | nonsummer | CRSTWD_6_KUMYAY | PLANT_TROUBLE | 2180
2022 | nonsummer | CRSTWD_6_KUMYAY | TRANSMISSION_INDUCED | 36.6667
2022 | nonsummer | CRWCKS_1_SOLAR1 | METERING_TELEMETRY | 59.6667
2022 | nonsummer | CRWCKS_1_SOLAR1 | PLANT_MAINTENANCE | 59.6667
2022 | nonsummer | CRWCKS_1_SOLAR1 | PLANT_TROUBLE | 43.3333
2022 | nonsummer | CRWCKS_1_SOLAR1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | CSCCOG_1_UNIT 1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | CSCCOG_1_UNIT 1 | PLANT_TROUBLE | 1974.2333
2022 | nonsummer | CSCCOG_1_UNIT 1 | TRANSMISSION_INDUCED | 87.6167
2022 | nonsummer | CSCGNR_1_UNIT 1 | AMBIENT_DUE_TO_TEMP | 11.25
2022 | nonsummer | CSCGNR_1_UNIT 1 | PLANT_MAINTENANCE | 123.75
2022 | nonsummer | CSCGNR_1_UNIT 1 | PLANT_TROUBLE | 247.5
2022 | nonsummer | CSCGNR_1_UNIT 2 | PLANT_MAINTENANCE | 11508.75
2022 | nonsummer | CSCGNR_1_UNIT 2 | PLANT_TROUBLE | 712.4
2022 | nonsummer | CSLR4S_2_SOLAR | METERING_TELEMETRY | 0
2022 | nonsummer | CSLR4S_2_SOLAR | PLANT_MAINTENANCE | 1365
2022 | nonsummer | CSLR4S_2_SOLAR | PLANT_TROUBLE | 661.4333
2022 | nonsummer | CSTOGA_6_LNDFIL | TRANSMISSION_INDUCED | 18.4025
2022 | nonsummer | CSTRVL_7_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 97.5
2022 | nonsummer | CSTRVL_7_PL1X2 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | CSTRVL_7_QFUNTS | TRANSMISSION_INDUCED | 0
2022 | nonsummer | CUMBIA_1_SOLAR | TRANSMISSION_INDUCED | 2412.6833
2022 | nonsummer | CUYAMS_6_CUYSR1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | CUYAMS_6_CUYSR1 | METERING_TELEMETRY | 79.3333
2022 | nonsummer | CUYAMS_6_CUYSR1 | PLANT_TROUBLE | 200
2022 | nonsummer | CUYAMS_6_CUYSR1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | DAIRLD_1_CR1BM1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 105.9167
2022 | nonsummer | DAIRLD_1_CR1BM1 | PLANT_MAINTENANCE | 5.5
2022 | nonsummer | DAIRLD_1_CR1BM1 | PLANT_TROUBLE | 19.4
2022 | nonsummer | DEADCK_1_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 1381.95
2022 | nonsummer | DEERCR_6_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 832.35
2022 | nonsummer | DEERCR_6_UNIT 1 | METERING_TELEMETRY | 105
2022 | nonsummer | DEERCR_6_UNIT 1 | PLANT_MAINTENANCE | 154
2022 | nonsummer | DEERCR_6_UNIT 1 | PLANT_TROUBLE | 105
2022 | nonsummer | DEERCR_6_UNIT 1 | TRANSMISSION_INDUCED | 140
2022 | nonsummer | DELSUR_6_BSOLAR | PLANT_TROUBLE | 9.9
2022 | nonsummer | DELSUR_6_CREST | METERING_TELEMETRY | 7.5
2022 | nonsummer | DELSUR_6_CREST | PLANT_TROUBLE | 432.5
2022 | nonsummer | DELSUR_6_DRYFRB | METERING_TELEMETRY | 0
2022 | nonsummer | DELSUR_6_DRYFRB | PLANT_MAINTENANCE | 0
2022 | nonsummer | DELSUR_6_DRYFRB | PLANT_TROUBLE | 246.45
2022 | nonsummer | DELSUR_6_DRYFRB | TRANSMISSION_INDUCED | 130.5333
2022 | nonsummer | DELSUR_6_SOLAR1 | METERING_TELEMETRY | 142.5
2022 | nonsummer | DELSUR_6_SOLAR1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | DELSUR_6_SOLAR1 | PLANT_TROUBLE | 335.475
2022 | nonsummer | DELSUR_6_SOLAR1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | DELTA_2_PL1X4 | AMBIENT_DUE_TO_TEMP | 1710
2022 | nonsummer | DELTA_2_PL1X4 | AMBIENT_DUE_TO_TEMP | 7270
2022 | nonsummer | DELTA_2_PL1X4 | PLANT_MAINTENANCE | 1578
2022 | nonsummer | DELTA_2_PL1X4 | PLANT_TROUBLE | 434
2022 | nonsummer | DELTA_2_PL1X4 | PLANT_TROUBLE | 48124.2833
2022 | nonsummer | DELTA_2_PL1X4 | TRANSITIONAL_LIMITATION | 593.7
2022 | nonsummer | DELTA_2_PL1X4 | TRANSITIONAL_LIMITATION | 0
2022 | nonsummer | DELTA_2_PL1X4 | TRANSMISSION_INDUCED | 7500
2022 | nonsummer | DEVERS_1_SOLAR | PLANT_TROUBLE | 74
2022 | nonsummer | DEVERS_1_SOLAR1 | METERING_TELEMETRY | 0
2022 | nonsummer | DEVERS_1_SOLAR1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | DEVERS_1_SOLAR1 | PLANT_TROUBLE | 160.2
2022 | nonsummer | DEVERS_1_SOLAR2 | METERING_TELEMETRY | 0
2022 | nonsummer | DEVERS_1_SOLAR2 | PLANT_TROUBLE | 0
2022 | nonsummer | DEVERS_2_DHSPG2 | METERING_TELEMETRY | 7
2022 | nonsummer | DEVERS_2_DHSPG2 | PLANT_TROUBLE | 181.4633
2022 | nonsummer | DEXZEL_1_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 6.2
2022 | nonsummer | DEXZEL_1_UNIT | METERING_TELEMETRY | 0
2022 | nonsummer | DEXZEL_1_UNIT | PLANT_MAINTENANCE | 5647.75
2022 | nonsummer | DEXZEL_1_UNIT | PLANT_TROUBLE | 3453
2022 | nonsummer | DIABLO_7_UNIT 1 | PLANT_TROUBLE | 21490
2022 | nonsummer | DIABLO_7_UNIT 2 | PLANT_MAINTENANCE | 24686.6667
2022 | nonsummer | DIABLO_7_UNIT 2 | PLANT_TROUBLE | 875
2022 | nonsummer | DISCOV_1_CHEVRN | PLANT_MAINTENANCE | 640.52
2022 | nonsummer | DISCOV_1_CHEVRN | PLANT_TROUBLE | 244.9467
2022 | nonsummer | DIXNLD_1_LNDFL | METERING_TELEMETRY | 0
2022 | nonsummer | DIXNLD_1_LNDFL | PLANT_MAINTENANCE | 15.2
2022 | nonsummer | DIXNLD_1_LNDFL | PLANT_TROUBLE | 0
2022 | nonsummer | DMDVLY_1_UNITS | PLANT_MAINTENANCE | 0
2022 | nonsummer | DONNLS_7_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 1145
2022 | nonsummer | DONNLS_7_UNIT | PLANT_TROUBLE | 0
2022 | nonsummer | DONNLS_7_UNIT | TRANSMISSION_INDUCED | 1599.6667
2022 | nonsummer | DOSMGO_2_NSPIN | TRANSMISSION_INDUCED | 0
2022 | nonsummer | DOUBLC_1_UNITS | AMBIENT_DUE_TO_TEMP | 1555.91
2022 | nonsummer | DOUBLC_1_UNITS | PLANT_MAINTENANCE | 0
2022 | nonsummer | DOUBLC_1_UNITS | PLANT_TROUBLE | 791.41
2022 | nonsummer | DOUBLC_1_UNITS | RTU_RIG | 0
2022 | nonsummer | DOUBLC_1_UNITS | UNIT_TESTING | 417.84
2022 | nonsummer | DRACKR_2_D4SR4B | PLANT_MAINTENANCE | 0
2022 | nonsummer | DRACKR_2_D4SR4B | PLANT_TROUBLE | 1178.85
2022 | nonsummer | DRACKR_2_D4SR4B | TRANSMISSION_INDUCED | 0
2022 | nonsummer | DRACKR_2_DS3SR3 | METERING_TELEMETRY | 0
2022 | nonsummer | DRACKR_2_DS3SR3 | PLANT_MAINTENANCE | 203.25
2022 | nonsummer | DRACKR_2_DS3SR3 | PLANT_TROUBLE | 600.124
2022 | nonsummer | DRACKR_2_DS3SR3 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | DRACKR_2_DS4SR4 | PLANT_MAINTENANCE | 0
2022 | nonsummer | DRACKR_2_DS4SR4 | PLANT_TROUBLE | 0
2022 | nonsummer | DRACKR_2_DS4SR4 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | DRACKR_2_DS4SR4 | UNIT_TESTING | 0
2022 | nonsummer | DRACKR_2_DSUBT1 | METERING_TELEMETRY | 0
2022 | nonsummer | DRACKR_2_DSUBT1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | DRACKR_2_DSUBT1 | PLANT_TROUBLE | 5330.55
2022 | nonsummer | DRACKR_2_DSUBT1 | TRANSMISSION_INDUCED | 555.45
2022 | nonsummer | DRACKR_2_DSUBT2 | AMBIENT_NOT_DUE_TO_TEMP | 18.5833
2022 | nonsummer | DRACKR_2_DSUBT2 | METERING_TELEMETRY | 60.3265
2022 | nonsummer | DRACKR_2_DSUBT2 | PLANT_MAINTENANCE | 4271.9833
2022 | nonsummer | DRACKR_2_DSUBT2 | PLANT_TROUBLE | 1162.6933
2022 | nonsummer | DRACKR_2_DSUBT2 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | DRACKR_2_DSUBT2 | UNIT_TESTING | 0
2022 | nonsummer | DRACKR_2_DSUBT3 | METERING_TELEMETRY | 0
2022 | nonsummer | DRACKR_2_DSUBT3 | PLANT_MAINTENANCE | 2560
2022 | nonsummer | DRACKR_2_DSUBT3 | PLANT_TROUBLE | 1025.5667
2022 | nonsummer | DRACKR_2_DSUBT3 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | DRACKR_2_DSUBT3 | UNIT_TESTING | 0
2022 | nonsummer | DRACKR_2_DSUBT4 | NEW_GENERATOR_TEST_ENERGY | 0
2022 | nonsummer | DRACKR_2_DSUBT4 | PLANT_MAINTENANCE | 0
2022 | nonsummer | DRACKR_2_DSUBT4 | PLANT_TROUBLE | 6115.5725
2022 | nonsummer | DRACKR_2_DSUBT4 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | DRACKR_2_SOLAR1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | DRACKR_2_SOLAR1 | PLANT_TROUBLE | 138.2333
2022 | nonsummer | DRACKR_2_SOLAR1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | DRACKR_2_SOLAR2 | PLANT_MAINTENANCE | 121.9333
2022 | nonsummer | DRACKR_2_SOLAR2 | PLANT_TROUBLE | 160
2022 | nonsummer | DRACKR_2_SOLAR2 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | DREWSR_2_BHSSR1 | NEW_GENERATOR_TEST_ENERGY | 0
2022 | nonsummer | DREWSR_2_BHSSR1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | DREWS_6_PL1X4 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | DREWS_6_PL1X4 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | DREWS_6_PL1X4 | PLANT_MAINTENANCE | 7827
2022 | nonsummer | DREWS_6_PL1X4 | PLANT_TROUBLE | 3398
2022 | nonsummer | DREWS_6_PL1X4 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | DREWS_6_PL1X4 | UNIT_TESTING | 0
2022 | nonsummer | DRUM_7_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 7692.05
2022 | nonsummer | DRUM_7_PL1X2 | PLANT_TROUBLE | 21.6667
2022 | nonsummer | DRUM_7_PL1X2 | TRANSMISSION_INDUCED | 151.6667
2022 | nonsummer | DRUM_7_PL3X4 | AMBIENT_NOT_DUE_TO_TEMP | 15450.5
2022 | nonsummer | DRUM_7_PL3X4 | PLANT_TROUBLE | 163.3333
2022 | nonsummer | DRUM_7_PL3X4 | TRANSMISSION_INDUCED | 93.3333
2022 | nonsummer | DRUM_7_UNIT 5 | AMBIENT_NOT_DUE_TO_TEMP | 5717.38
2022 | nonsummer | DRUM_7_UNIT 5 | PLANT_TROUBLE | 0
2022 | nonsummer | DSABLA_7_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 434.8217
2022 | nonsummer | DSABLA_7_UNIT | PLANT_TROUBLE | 0
2022 | nonsummer | DSFLWR_2_WS2SR1 | PLANT_MAINTENANCE | 356.048
2022 | nonsummer | DSFLWR_2_WS2SR1 | PLANT_TROUBLE | 0
2022 | nonsummer | DSFLWR_2_WS2SR1 | TRANSMISSION_INDUCED | 192.325
2022 | nonsummer | DSRTHV_2_DH1SR1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | DSRTHV_2_DH1SR1 | PLANT_TROUBLE | 168.7667
2022 | nonsummer | DSRTHV_2_DH1SR1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | DSRTHV_2_DH2BT1 | METERING_TELEMETRY | 1457.5835
2022 | nonsummer | DSRTHV_2_DH2BT1 | PLANT_MAINTENANCE | 157.83
2022 | nonsummer | DSRTHV_2_DH2BT1 | PLANT_TROUBLE | 4474.8757
2022 | nonsummer | DSRTHV_2_DH2BT1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | DSRTHV_2_DH2BT1 | UNIT_TESTING | 0
2022 | nonsummer | DSRTHV_2_DH2SR2 | METERING_TELEMETRY | 0
2022 | nonsummer | DSRTHV_2_DH2SR2 | PLANT_MAINTENANCE | 0
2022 | nonsummer | DSRTHV_2_DH2SR2 | PLANT_TROUBLE | 149.3333
2022 | nonsummer | DSRTHV_2_DH2SR2 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | DSRTHV_2_DH2SR2 | UNIT_TESTING | 0
2022 | nonsummer | DSRTSL_2_SOLAR1 | PLANT_MAINTENANCE | 8614.27
2022 | nonsummer | DSRTSL_2_SOLAR1 | PLANT_TROUBLE | 3289.55
2022 | nonsummer | DSRTSN_2_DS2X2 | NEW_GENERATOR_TEST_ENERGY | 0
2022 | nonsummer | DSRTSN_2_DS2X2 | PLANT_MAINTENANCE | 0
2022 | nonsummer | DSRTSN_2_DS2X2 | PLANT_TROUBLE | 282.7667
2022 | nonsummer | DSRTSN_2_DS2X2 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | DSRTSN_2_DS2X2 | UNIT_TESTING | 4230
2022 | nonsummer | DSRTSN_2_SOLAR1 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | DSRTSN_2_SOLAR1 | METERING_TELEMETRY | 295
2022 | nonsummer | DSRTSN_2_SOLAR1 | PLANT_MAINTENANCE | 300
2022 | nonsummer | DSRTSN_2_SOLAR1 | PLANT_TROUBLE | 1619.32
2022 | nonsummer | DSRTSN_2_SOLAR1 | RTU_RIG | 489
2022 | nonsummer | DSRTSN_2_SOLAR1 | TRANSMISSION_INDUCED | 1055
2022 | nonsummer | DSRTSN_2_SOLAR2 | PLANT_MAINTENANCE | 281.752
2022 | nonsummer | DSRTSN_2_SOLAR2 | PLANT_TROUBLE | 0
2022 | nonsummer | DSRTSN_2_SOLAR2 | TRANSMISSION_INDUCED | 500
2022 | nonsummer | DSRTSN_2_SOLAR2 | UNIT_TESTING | 0
2022 | nonsummer | DTCHWD_2_BT3WND | METERING_TELEMETRY | 0
2022 | nonsummer | DTCHWD_2_BT3WND | PLANT_MAINTENANCE | 0
2022 | nonsummer | DTCHWD_2_BT4WND | METERING_TELEMETRY | 0
2022 | nonsummer | DTCHWD_2_BT4WND | PLANT_MAINTENANCE | 0
2022 | nonsummer | DUANE_1_PL1X3 | AMBIENT_DUE_TO_TEMP | 2341
2022 | nonsummer | DUANE_1_PL1X3 | AMBIENT_NOT_DUE_TO_TEMP | 2967
2022 | nonsummer | DUANE_1_PL1X3 | METERING_TELEMETRY | 0
2022 | nonsummer | DUANE_1_PL1X3 | PLANT_MAINTENANCE | 17095
2022 | nonsummer | DUANE_1_PL1X3 | PLANT_TROUBLE | 23236.8817
2022 | nonsummer | DUANE_1_PL1X3 | UNIT_TESTING | 0
2022 | nonsummer | DURNMESA_3_WBDYN | PLANT_TROUBLE | 0
2022 | nonsummer | DURNMESA_3_WBDYN | TRANSMISSION_INDUCED | 15214.24
2022 | nonsummer | DUTCH1_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 2183.34
2022 | nonsummer | DUTCH1_7_UNIT 1 | METERING_TELEMETRY | 0
2022 | nonsummer | DUTCH1_7_UNIT 1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | DUTCH1_7_UNIT 1 | PLANT_TROUBLE | 9.8167
2022 | nonsummer | DUTCH1_7_UNIT 1 | TRANSMISSION_INDUCED | 66
2022 | nonsummer | DUTCH2_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 13723.1167
2022 | nonsummer | DUTCH2_7_UNIT 1 | PLANT_TROUBLE | 0
2022 | nonsummer | DUTCH2_7_UNIT 1 | TRANSMISSION_INDUCED | 119.6
2022 | nonsummer | DVLCYN_1_UNITS | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | DVLCYN_1_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 3028.3333
2022 | nonsummer | DVLCYN_1_UNITS | OTHER_USE_LIMIT_REACHED | 131.25
2022 | nonsummer | DVLCYN_1_UNITS | PLANT_MAINTENANCE | 2460.6667
2022 | nonsummer | DVLCYN_1_UNITS | PLANT_TROUBLE | 718.75
2022 | nonsummer | DVLCYN_1_UNITS | SHORT_TERM_USE_LIMIT_REACHED | 107.3333
2022 | nonsummer | DVLCYN_1_UNITS | TRANSMISSION_INDUCED | 0
2022 | nonsummer | DVLCYN_1_UNITS | UNIT_TESTING | 300
2022 | nonsummer | DYERSM_6_DSWWD1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | DYERSM_6_DSWWD1 | PLANT_TROUBLE | 39.1267
2022 | nonsummer | DYERSM_6_DSWWD1 | TRANSITIONAL_LIMITATION | 638
2022 | nonsummer | DYERSM_6_DSWWD1 | TRANSMISSION_INDUCED | 1217.8133
2022 | nonsummer | EASTWD_7_UNIT | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | EASTWD_7_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 1000
2022 | nonsummer | EASTWD_7_UNIT | METERING_TELEMETRY | 0
2022 | nonsummer | EASTWD_7_UNIT | OTHER_USE_LIMIT_REACHED | 0
2022 | nonsummer | EASTWD_7_UNIT | PLANT_MAINTENANCE | 0
2022 | nonsummer | EASTWD_7_UNIT | PLANT_TROUBLE | 0
2022 | nonsummer | EASTWD_7_UNIT | TRANSMISSION_INDUCED | 55500
2022 | nonsummer | EDMONS_2_NSPIN | ENVIRONMENTAL_RESTRICTIONS | 3579
2022 | nonsummer | EDMONS_2_NSPIN | PLANT_MAINTENANCE | 0
2022 | nonsummer | EDMONS_2_NSPIN | PLANT_TROUBLE | 42637.22
2022 | nonsummer | EDMONS_2_NSPIN | TRANSMISSION_INDUCED | 2909.25
2022 | nonsummer | EDWARD_2_E21SB1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 782.9667
2022 | nonsummer | EDWARD_2_E21SB1 | NEW_GENERATOR_TEST_ENERGY | 0
2022 | nonsummer | EDWARD_2_E21SB1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | EDWARD_2_E21SB1 | PLANT_TROUBLE | 1925.6
2022 | nonsummer | EDWARD_2_E21SB1 | UNIT_TESTING | 0
2022 | nonsummer | EDWARD_2_E23SB1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 501.6
2022 | nonsummer | EDWARD_2_E23SB1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | EDWARD_2_E23SB1 | PLANT_MAINTENANCE | 240
2022 | nonsummer | EDWARD_2_E23SB1 | PLANT_TROUBLE | 307
2022 | nonsummer | EDWARD_2_ES2BT3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1152.6333
2022 | nonsummer | EDWARD_2_ES2BT3 | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | EDWARD_2_ES2BT3 | METERING_TELEMETRY | 0
2022 | nonsummer | EDWARD_2_ES2BT3 | NEW_GENERATOR_TEST_ENERGY | 0
2022 | nonsummer | EDWARD_2_ES2BT3 | PLANT_MAINTENANCE | 0
2022 | nonsummer | EDWARD_2_ES2BT3 | PLANT_TROUBLE | 0
2022 | nonsummer | EDWARD_2_ES2BT3 | RIMS_OUTAGE | 0
2022 | nonsummer | EDWARD_2_ES2BT3 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | EDWARD_2_ES2BT3 | UNIT_TESTING | 0
2022 | nonsummer | EEKTMN_6_SOLAR1 | PLANT_MAINTENANCE | 140
2022 | nonsummer | EEKTMN_6_SOLAR1 | PLANT_TROUBLE | 160
2022 | nonsummer | EEKTMN_6_SOLAR1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | ELCABO_5_ECWSCEDYN | AMBIENT_DUE_TO_TEMP | 1877.0667
2022 | nonsummer | ELCABO_5_ECWSCEDYN | PLANT_MAINTENANCE | 0
2022 | nonsummer | ELCABO_5_ECWSCEDYN | PLANT_TROUBLE | 1360
2022 | nonsummer | ELCABO_5_ECWSCEDYN | TRANSITIONAL_LIMITATION | 3714.0667
2022 | nonsummer | ELCABO_5_ECWSCEDYN | TRANSMISSION_INDUCED | 45309.6833
2022 | nonsummer | ELCAJN_6_EB1BT1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | ELCAJN_6_EB1BT1 | PLANT_TROUBLE | 170.625
2022 | nonsummer | ELCAJN_6_LM6K | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | ELCAJN_6_LM6K | PLANT_MAINTENANCE | 8.0167
2022 | nonsummer | ELCAJN_6_LM6K | PLANT_TROUBLE | 1202.5
2022 | nonsummer | ELCAJN_6_LM6K | UNIT_TESTING | 0
2022 | nonsummer | ELCAJN_6_UNITA1 | METERING_TELEMETRY | 0
2022 | nonsummer | ELCAJN_6_UNITA1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | ELCAJN_6_UNITA1 | PLANT_TROUBLE | 272.117
2022 | nonsummer | ELDORO_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 6904
2022 | nonsummer | ELDORO_7_UNIT 1 | PLANT_MAINTENANCE | 660
2022 | nonsummer | ELDORO_7_UNIT 1 | PLANT_TROUBLE | 0
2022 | nonsummer | ELDORO_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 6840
2022 | nonsummer | ELDORO_7_UNIT 2 | PLANT_MAINTENANCE | 660
2022 | nonsummer | ELDORO_7_UNIT 2 | PLANT_TROUBLE | 0
2022 | nonsummer | ELECTR_7_PL1X3 | AMBIENT_NOT_DUE_TO_TEMP | 6373.4767
2022 | nonsummer | ELECTR_7_PL1X3 | PLANT_MAINTENANCE | 1908
2022 | nonsummer | ELECTR_7_PL1X3 | PLANT_TROUBLE | 1185.2333
2022 | nonsummer | ELECTR_7_PL1X3 | RTU_RIG | 0
2022 | nonsummer | ELECTR_7_PL1X3 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | ELKCRK_6_STONYG | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1494.5
2022 | nonsummer | ELKCRK_6_STONYG | AMBIENT_NOT_DUE_TO_TEMP | 972.65
2022 | nonsummer | ELKCRK_6_STONYG | METERING_TELEMETRY | 0
2022 | nonsummer | ELKCRK_6_STONYG | PLANT_TROUBLE | 624.75
2022 | nonsummer | ELKCRK_6_STONYG | TRANSMISSION_INDUCED | 0
2022 | nonsummer | ELKHIL_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 23067.5
2022 | nonsummer | ELKHIL_2_PL1X3 | PLANT_MAINTENANCE | 11897.9667
2022 | nonsummer | ELKHIL_2_PL1X3 | PLANT_TROUBLE | 5226.8667
2022 | nonsummer | ELKHRN_1_EESX3 | PLANT_MAINTENANCE | 225
2022 | nonsummer | ELKHRN_1_EESX3 | PLANT_TROUBLE | 53837.5
2022 | nonsummer | ELNIDP_6_BIOMAS | PLANT_MAINTENANCE | 625.275
2022 | nonsummer | ELNIDP_6_BIOMAS | PLANT_TROUBLE | 2510.575
2022 | nonsummer | ELNIDP_6_BIOMAS | TRANSMISSION_INDUCED | 99.75
2022 | nonsummer | ELSEGN_2_UN1011 | AMBIENT_DUE_TO_TEMP | 1412.4528
2022 | nonsummer | ELSEGN_2_UN1011 | OTHER_USE_LIMIT_REACHED | 3122.4483
2022 | nonsummer | ELSEGN_2_UN1011 | PLANT_MAINTENANCE | 7237.0472
2022 | nonsummer | ELSEGN_2_UN1011 | PLANT_TROUBLE | 734.7617
2022 | nonsummer | ELSEGN_2_UN1011 | UNIT_TESTING | 0
2022 | nonsummer | ELSEGN_2_UN2021 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | ELSEGN_2_UN2021 | ENVIRONMENTAL_RESTRICTIONS | 3265.409
2022 | nonsummer | ELSEGN_2_UN2021 | OTHER_USE_LIMIT_REACHED | 0
2022 | nonsummer | ELSEGN_2_UN2021 | PLANT_MAINTENANCE | 0
2022 | nonsummer | ELSEGN_2_UN2021 | PLANT_TROUBLE | 6413.064
2022 | nonsummer | ELSEGN_2_UN2021 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | ELSEGN_2_UN2021 | UNIT_TESTING | 0
2022 | nonsummer | ENERSJ_2_WIND | METERING_TELEMETRY | 0
2022 | nonsummer | ENERSJ_2_WIND | PLANT_MAINTENANCE | 22.5
2022 | nonsummer | ENERSJ_2_WIND | PLANT_TROUBLE | 1022.2667
2022 | nonsummer | ENERSJ_2_WIND | TRANSMISSION_INDUCED | 0
2022 | nonsummer | ENERSJ_5_ESJWD2 | NEW_GENERATOR_TEST_ENERGY | 0.3
2022 | nonsummer | ENERSJ_5_ESJWD2 | PLANT_MAINTENANCE | 305.9
2022 | nonsummer | ENERSJ_5_ESJWD2 | PLANT_TROUBLE | 2226.2
2022 | nonsummer | ENERSJ_5_ESJWD2 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | ENERSJ_5_ESJWD2 | UNIT_TESTING | 0
2022 | nonsummer | ENWIND_2_WIND1 | TRANSMISSION_INDUCED | 38.2
2022 | nonsummer | ENWIND_2_WIND1 | UNIT_TESTING | 283.5
2022 | nonsummer | ENWIND_2_WIND2 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | ESCNDO_6_EB1BT1 | PLANT_TROUBLE | 1100
2022 | nonsummer | ESCNDO_6_EB2BT2 | PLANT_TROUBLE | 1655
2022 | nonsummer | ESCNDO_6_EB3BT3 | PLANT_TROUBLE | 1677.5
2022 | nonsummer | ESCNDO_6_PL1X2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 4383.9
2022 | nonsummer | ESCNDO_6_PL1X2 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | ESCNDO_6_PL1X2 | PLANT_MAINTENANCE | 90.1135
2022 | nonsummer | ESCNDO_6_PL1X2 | PLANT_TROUBLE | 35.2275
2022 | nonsummer | ESCNDO_6_UNITB1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 2138.6
2022 | nonsummer | ESCNDO_6_UNITB1 | AMBIENT_DUE_TO_TEMP | 12.09
2022 | nonsummer | ESCNDO_6_UNITB1 | PLANT_MAINTENANCE | 1764.6693
2022 | nonsummer | ESCNDO_6_UNITB1 | PLANT_TROUBLE | 4682.398
2022 | nonsummer | ESCNDO_6_UNITB1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | ESCNDO_6_UNITB1 | UNIT_TESTING | 0
2022 | nonsummer | ESCO_6_GLMQF | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 4491
2022 | nonsummer | ESCO_6_GLMQF | PLANT_TROUBLE | 146.9
2022 | nonsummer | ESCO_6_GLMQF | PLANT_TROUBLE | 59.07
2022 | nonsummer | ESCO_6_GLMQF | TRANSMISSION_INDUCED | 0
2022 | nonsummer | ESNHWR_2_WC1BT1 | PLANT_MAINTENANCE | 15
2022 | nonsummer | ESNHWR_2_WC1BT1 | PLANT_TROUBLE | 186.8333
2022 | nonsummer | ESNHWR_2_WC1BT1 | RTU_RIG | 0
2022 | nonsummer | ESNHWR_2_WC1BT1 | UNIT_TESTING | 0
2022 | nonsummer | ESQUON_6_LNDFIL | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 10.5
2022 | nonsummer | ESQUON_6_LNDFIL | PLANT_MAINTENANCE | 0
2022 | nonsummer | ESQUON_6_LNDFIL | PLANT_TROUBLE | 108.255
2022 | nonsummer | ESQUON_6_LNDFIL | TRANSMISSION_INDUCED | 0
2022 | nonsummer | ESTWND_2_OPPWD1 | METERING_TELEMETRY | 0
2022 | nonsummer | ESTWND_2_OPPWD1 | PLANT_MAINTENANCE | 139.0407
2022 | nonsummer | ESTWND_2_OPPWD1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | ESTWND_2_OPPWD1 | UNIT_TESTING | 0
2022 | nonsummer | ETIWND_2_FONTNA | AMBIENT_NOT_DUE_TO_TEMP | 1710.375
2022 | nonsummer | ETIWND_2_FONTNA | PLANT_TROUBLE | 8.1733
2022 | nonsummer | ETIWND_2_FONTNA | TRANSMISSION_INDUCED | 0
2022 | nonsummer | ETIWND_2_RTS010 | PLANT_TROUBLE | 193.8
2022 | nonsummer | ETIWND_2_RTS018 | PLANT_TROUBLE | 352.5
2022 | nonsummer | ETIWND_2_RTS023 | PLANT_TROUBLE | 323.0417
2022 | nonsummer | ETIWND_2_RTS023 | TRANSMISSION_INDUCED | 0.41667
2022 | nonsummer | ETIWND_2_UNIT1 | PLANT_TROUBLE | 0
2022 | nonsummer | ETIWND_2_UNIT1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | ETIWND_6_GRPLND | AMBIENT_DUE_TO_TEMP | 290.8167
2022 | nonsummer | ETIWND_6_GRPLND | ENVIRONMENTAL_RESTRICTIONS | 195.314
2022 | nonsummer | ETIWND_6_GRPLND | PLANT_MAINTENANCE | 0
2022 | nonsummer | ETIWND_6_GRPLND | PLANT_TROUBLE | 748.3627
2022 | nonsummer | ETIWND_6_GRPLND | TRANSMISSION_INDUCED | 0
2022 | nonsummer | ETIWND_6_MWDETI | PLANT_MAINTENANCE | 0
2022 | nonsummer | EXCHEC_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 28246.5333
2022 | nonsummer | EXCHEC_7_UNIT 1 | PLANT_MAINTENANCE | 994.4167
2022 | nonsummer | EXCHEC_7_UNIT 1 | PLANT_TROUBLE | 0
2022 | nonsummer | EXCHEC_7_UNIT 1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | EXCLSG_1_SOLAR | PLANT_MAINTENANCE | 80
2022 | nonsummer | EXCLSG_1_SOLAR | PLANT_TROUBLE | 0
2022 | nonsummer | EXCLSG_1_SOLAR | TRANSMISSION_INDUCED | 0
2022 | nonsummer | FLOWD2_2_FPLWND | METERING_TELEMETRY | 65.8933
2022 | nonsummer | FLOWD2_2_FPLWND | PLANT_MAINTENANCE | 830.5463
2022 | nonsummer | FLOWD2_2_FPLWND | TRANSMISSION_INDUCED | 81
2022 | nonsummer | FLOWD_2_RT2WD2 | PLANT_TROUBLE | 51
2022 | nonsummer | FLOWD_2_RT2WD2 | TRANSMISSION_INDUCED | 75.779
2022 | nonsummer | FLOWD_2_WIND1 | PLANT_MAINTENANCE | 32.3283
2022 | nonsummer | FLOWD_2_WIND1 | TRANSMISSION_INDUCED | 23.8
2022 | nonsummer | FMEADO_6_HELLHL | PLANT_MAINTENANCE | 17.89
2022 | nonsummer | FMEADO_6_HELLHL | PLANT_TROUBLE | 0
2022 | nonsummer | FMEADO_6_HELLHL | TRANSMISSION_INDUCED | 243.77
2022 | nonsummer | FMEADO_7_UNIT | PLANT_TROUBLE | 59.2
2022 | nonsummer | FMEADO_7_UNIT | TRANSMISSION_INDUCED | 4898.7667
2022 | nonsummer | FORBST_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | FORBST_7_UNIT 1 | PLANT_TROUBLE | 0
2022 | nonsummer | FORBST_7_UNIT 1 | TRANSMISSION_INDUCED | 43.75
2022 | nonsummer | FRESHW_1_SOLAR1 | METERING_TELEMETRY | 0
2022 | nonsummer | FRESHW_1_SOLAR1 | PLANT_TROUBLE | 0
2022 | nonsummer | FRESHW_1_SOLAR1 | TRANSMISSION_INDUCED | 100
2022 | nonsummer | FRIANT_6_UNITS | TRANSMISSION_INDUCED | 0
2022 | nonsummer | FRNTBW_6_SOLAR1 | METERING_TELEMETRY | 0
2022 | nonsummer | FRNTBW_6_SOLAR1 | PLANT_TROUBLE | 243
2022 | nonsummer | FRNTBW_6_SOLAR1 | TRANSITIONAL_LIMITATION | 0
2022 | nonsummer | FRNTBW_6_SOLAR1 | TRANSMISSION_INDUCED | 181
2022 | nonsummer | FROGTN_1_UTICAA | PLANT_MAINTENANCE | 0
2022 | nonsummer | FROGTN_1_UTICAA | PLANT_TROUBLE | 0
2022 | nonsummer | FROGTN_1_UTICAA | TRANSMISSION_INDUCED | 1.3067
2022 | nonsummer | FROGTN_1_UTICAM | ENVIRONMENTAL_RESTRICTIONS | 18
2022 | nonsummer | FROGTN_1_UTICAM | PLANT_MAINTENANCE | 0
2022 | nonsummer | FROGTN_1_UTICAM | PLANT_TROUBLE | 24.6
2022 | nonsummer | FROGTN_1_UTICAM | TRANSMISSION_INDUCED | 23.58
2022 | nonsummer | FTSWRD_6_TRFORK | TRANSMISSION_INDUCED | 0
2022 | nonsummer | FTSWRD_7_QFUNTS | TRANSMISSION_INDUCED | 0
2022 | nonsummer | GALE_1_SR3SR3 | METERING_TELEMETRY | 345
2022 | nonsummer | GALE_1_SR3SR3 | PLANT_MAINTENANCE | 41.4
2022 | nonsummer | GALE_1_SR3SR3 | PLANT_TROUBLE | 46.23
2022 | nonsummer | GANSO_1_WSTBM1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 2
2022 | nonsummer | GANSO_1_WSTBM1 | PLANT_MAINTENANCE | 0.11667
2022 | nonsummer | GANSO_1_WSTBM1 | PLANT_TROUBLE | 1.5
2022 | nonsummer | GARLND_2_GARBT1 | AMBIENT_NOT_DUE_TO_TEMP | 1645.75
2022 | nonsummer | GARLND_2_GARBT1 | METERING_TELEMETRY | 41.5
2022 | nonsummer | GARLND_2_GARBT1 | PLANT_MAINTENANCE | 2003
2022 | nonsummer | GARLND_2_GARBT1 | PLANT_TROUBLE | 6028.2
2022 | nonsummer | GARLND_2_GARBT1 | UNIT_TESTING | 73
2022 | nonsummer | GARLND_2_GASLR | AMBIENT_NOT_DUE_TO_TEMP | 360
2022 | nonsummer | GARLND_2_GASLR | METERING_TELEMETRY | 1359.89
2022 | nonsummer | GARLND_2_GASLR | PLANT_MAINTENANCE | 5300.7333
2022 | nonsummer | GARLND_2_GASLR | PLANT_TROUBLE | 11954.1333
2022 | nonsummer | GARLND_2_GASLR | UNIT_TESTING | 25.5
2022 | nonsummer | GARLND_2_GASLRA | PLANT_MAINTENANCE | 320
2022 | nonsummer | GARLND_2_GASLRA | PLANT_TROUBLE | 600
2022 | nonsummer | GARLND_2_GASLRA | UNIT_TESTING | 0
2022 | nonsummer | GARNET_1_SOLAR | PLANT_MAINTENANCE | 28
2022 | nonsummer | GARNET_1_SOLAR | PLANT_TROUBLE | 0
2022 | nonsummer | GARNET_1_SOLAR2 | METERING_TELEMETRY | 0
2022 | nonsummer | GARNET_1_SOLAR2 | PLANT_MAINTENANCE | 0
2022 | nonsummer | GARNET_1_SOLAR2 | PLANT_TROUBLE | 2557.5417
2022 | nonsummer | GARNET_1_SOLAR2 | TRANSMISSION_INDUCED | 4.75
2022 | nonsummer | GARNET_1_UNITS | PLANT_MAINTENANCE | 74.9
2022 | nonsummer | GARNET_1_UNITS | PLANT_TROUBLE | 344.4
2022 | nonsummer | GARNET_1_WIND | PLANT_MAINTENANCE | 6.5
2022 | nonsummer | GARNET_1_WIND | PLANT_TROUBLE | 104
2022 | nonsummer | GARNET_1_WIND | TRANSMISSION_INDUCED | 24.8507
2022 | nonsummer | GARNET_1_WINDS | PLANT_MAINTENANCE | 1916.5167
2022 | nonsummer | GARNET_1_WINDS | PLANT_TROUBLE | 123.1
2022 | nonsummer | GARNET_1_WINDS | TRANSMISSION_INDUCED | 5.5
2022 | nonsummer | GARNET_1_WT3WND | PLANT_MAINTENANCE | 12
2022 | nonsummer | GARNET_1_WT3WND | PLANT_TROUBLE | 302.75
2022 | nonsummer | GARNET_2_COAWD2 | PLANT_TROUBLE | 108
2022 | nonsummer | GARNET_2_COAWD2 | TRANSMISSION_INDUCED | 165.002
2022 | nonsummer | GARNET_2_HYDRO | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 50
2022 | nonsummer | GARNET_2_HYDRO | AMBIENT_NOT_DUE_TO_TEMP | 900
2022 | nonsummer | GARNET_2_HYDRO | ENVIRONMENTAL_RESTRICTIONS | 5
2022 | nonsummer | GARNET_2_HYDRO | TRANSMISSION_INDUCED | 17.15
2022 | nonsummer | GARNET_2_WIND1 | PLANT_TROUBLE | 54.1333
2022 | nonsummer | GARNET_2_WIND1 | TRANSMISSION_INDUCED | 67.2
2022 | nonsummer | GARNET_2_WIND2 | PLANT_MAINTENANCE | 625.2308
2022 | nonsummer | GARNET_2_WIND2 | PLANT_TROUBLE | 734.4017
2022 | nonsummer | GARNET_2_WIND2 | TRANSITIONAL_LIMITATION | 0
2022 | nonsummer | GARNET_2_WIND2 | TRANSMISSION_INDUCED | 79.7
2022 | nonsummer | GARNET_2_WIND3 | PLANT_TROUBLE | 23.1
2022 | nonsummer | GARNET_2_WIND3 | TRANSMISSION_INDUCED | 178.374
2022 | nonsummer | GARNET_2_WIND4 | METERING_TELEMETRY | 0
2022 | nonsummer | GARNET_2_WIND4 | PLANT_TROUBLE | 9.8
2022 | nonsummer | GARNET_2_WIND4 | TRANSMISSION_INDUCED | 70.6567
2022 | nonsummer | GARNET_2_WIND5 | TRANSMISSION_INDUCED | 20.3683
2022 | nonsummer | GARNET_2_WPMWD6 | PLANT_TROUBLE | 4447.5
2022 | nonsummer | GASKW1_2_GW1SR1 | PLANT_MAINTENANCE | 415.98
2022 | nonsummer | GASKW1_2_GW1SR1 | PLANT_TROUBLE | 1767.7333
2022 | nonsummer | GASKW1_2_GW1SR1 | TRANSMISSION_INDUCED | 120
2022 | nonsummer | GASKW1_2_GW1SR1 | UNIT_TESTING | 0
2022 | nonsummer | GATES_2_SOLAR | PLANT_TROUBLE | 3550
2022 | nonsummer | GATES_2_WSOLAR | PLANT_MAINTENANCE | 0
2022 | nonsummer | GATEWY_2_GESBT1 | METERING_TELEMETRY | 0
2022 | nonsummer | GATEWY_2_GESBT1 | PLANT_MAINTENANCE | 2048.525
2022 | nonsummer | GATEWY_2_GESBT1 | PLANT_TROUBLE | 7451.7
2022 | nonsummer | GATEWY_2_GESBT1 | RTU_RIG | 0
2022 | nonsummer | GATWAY_2_PL1X3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2022 | nonsummer | GATWAY_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 34306.92
2022 | nonsummer | GATWAY_2_PL1X3 | PLANT_MAINTENANCE | 54826
2022 | nonsummer | GATWAY_2_PL1X3 | PLANT_TROUBLE | 31522.765
2022 | nonsummer | GATWAY_2_PL1X3 | UNIT_TESTING | 0
2022 | nonsummer | GENESI_2_STG | AMBIENT_NOT_DUE_TO_TEMP | 16472.9167
2022 | nonsummer | GENESI_2_STG | METERING_TELEMETRY | 108.3333
2022 | nonsummer | GEYS11_7_UNIT11 | AMBIENT_NOT_DUE_TO_TEMP | 9865.5567
2022 | nonsummer | GEYS11_7_UNIT11 | PLANT_MAINTENANCE | 0
2022 | nonsummer | GEYS11_7_UNIT11 | PLANT_TROUBLE | 10910.248
2022 | nonsummer | GEYS11_7_UNIT11 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2022 | nonsummer | GEYS11_7_UNIT11 | TRANSITIONAL_LIMITATION | 0
2022 | nonsummer | GEYS11_7_UNIT11 | TRANSMISSION_INDUCED | 97
2022 | nonsummer | GEYS12_7_UNIT12 | AMBIENT_NOT_DUE_TO_TEMP | 13112.1667
2022 | nonsummer | GEYS12_7_UNIT12 | PLANT_TROUBLE | 234.9667
2022 | nonsummer | GEYS13_7_UNIT13 | AMBIENT_NOT_DUE_TO_TEMP | 22803.7333
2022 | nonsummer | GEYS13_7_UNIT13 | PLANT_TROUBLE | 0
2022 | nonsummer | GEYS13_7_UNIT13 | RTU_RIG | 0
2022 | nonsummer | GEYS14_7_UNIT14 | AMBIENT_NOT_DUE_TO_TEMP | 9449.5
2022 | nonsummer | GEYS14_7_UNIT14 | METERING_TELEMETRY | 117.8333
2022 | nonsummer | GEYS14_7_UNIT14 | PLANT_TROUBLE | 164.7833
2022 | nonsummer | GEYS16_7_UNIT16 | AMBIENT_NOT_DUE_TO_TEMP | 16258
2022 | nonsummer | GEYS16_7_UNIT16 | PLANT_MAINTENANCE | 0
2022 | nonsummer | GEYS16_7_UNIT16 | PLANT_TROUBLE | 1064.1
2022 | nonsummer | GEYS17_7_UNIT17 | AMBIENT_NOT_DUE_TO_TEMP | 14529.67
2022 | nonsummer | GEYS17_7_UNIT17 | PLANT_MAINTENANCE | 0
2022 | nonsummer | GEYS17_7_UNIT17 | PLANT_TROUBLE | 943.5833
2022 | nonsummer | GEYS17_7_UNIT17 | TRANSITIONAL_LIMITATION | 0
2022 | nonsummer | GEYS18_7_UNIT18 | AMBIENT_NOT_DUE_TO_TEMP | 27970.3333
2022 | nonsummer | GEYS18_7_UNIT18 | PLANT_TROUBLE | 0
2022 | nonsummer | GEYS20_7_UNIT20 | AMBIENT_NOT_DUE_TO_TEMP | 12997.75
2022 | nonsummer | GEYS20_7_UNIT20 | PLANT_TROUBLE | 0
2022 | nonsummer | GIFENS_6_BUGSL1 | METERING_TELEMETRY | 100
2022 | nonsummer | GIFENS_6_BUGSL1 | PLANT_TROUBLE | 106.6667
2022 | nonsummer | GIFENS_6_BUGSL1 | TRANSMISSION_INDUCED | 100
2022 | nonsummer | GIFENS_6_BUGSL1 | UNIT_TESTING | 0
2022 | nonsummer | GIFFEN_6_SOLAR | PLANT_MAINTENANCE | 452.8333
2022 | nonsummer | GIFFEN_6_SOLAR | PLANT_TROUBLE | 108.5
2022 | nonsummer | GIFFEN_6_SOLAR | TRANSMISSION_INDUCED | 520
2022 | nonsummer | GIFFEN_6_SOLAR1 | METERING_TELEMETRY | 135
2022 | nonsummer | GIFFEN_6_SOLAR1 | PLANT_TROUBLE | 33.225
2022 | nonsummer | GIFFEN_6_SOLAR1 | TRANSMISSION_INDUCED | 418.5
2022 | nonsummer | GILROY_1_UNIT | AMBIENT_DUE_TO_TEMP | 9049
2022 | nonsummer | GILROY_1_UNIT | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | GILROY_1_UNIT | PLANT_MAINTENANCE | 0
2022 | nonsummer | GILROY_1_UNIT | PLANT_TROUBLE | 5311.9167
2022 | nonsummer | GILROY_1_UNIT | TRANSITIONAL_LIMITATION | 0
2022 | nonsummer | GILROY_1_UNIT | TRANSMISSION_INDUCED | 3849
2022 | nonsummer | GILRPP_1_PL1X2 | AMBIENT_DUE_TO_TEMP | 8.5
2022 | nonsummer | GILRPP_1_PL1X2 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | GILRPP_1_PL1X2 | PLANT_TROUBLE | 0
2022 | nonsummer | GILRPP_1_PL1X2 | RTU_RIG | 0
2022 | nonsummer | GILRPP_1_PL1X2 | TRANSMISSION_INDUCED | 1904
2022 | nonsummer | GILRPP_1_PL1X2 | UNIT_TESTING | 0
2022 | nonsummer | GILRPP_1_PL3X4 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | GILRPP_1_PL3X4 | PLANT_MAINTENANCE | 812.35
2022 | nonsummer | GILRPP_1_PL3X4 | PLANT_TROUBLE | 58.52
2022 | nonsummer | GILRPP_1_PL3X4 | TRANSMISSION_INDUCED | 924
2022 | nonsummer | GLDFGR_6_SOLAR1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | GLDTWN_6_COLUM3 | METERING_TELEMETRY | 0
2022 | nonsummer | GLDTWN_6_COLUM3 | PLANT_MAINTENANCE | 95
2022 | nonsummer | GLDTWN_6_COLUM3 | PLANT_TROUBLE | 71.8333
2022 | nonsummer | GLDTWN_6_SOLAR | PLANT_MAINTENANCE | 17.5
2022 | nonsummer | GLDTWN_6_SOLAR | PLANT_TROUBLE | 0
2022 | nonsummer | GLNARM_2_UNIT 5 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 773.2675
2022 | nonsummer | GLNARM_2_UNIT 5 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | GLNARM_2_UNIT 5 | METERING_TELEMETRY | 0
2022 | nonsummer | GLNARM_2_UNIT 5 | PLANT_MAINTENANCE | 409.1188
2022 | nonsummer | GLNARM_2_UNIT 5 | PLANT_TROUBLE | 5290.5708
2022 | nonsummer | GLNARM_2_UNIT 5 | UNIT_TESTING | 0
2022 | nonsummer | GLNARM_7_UNIT 1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 211.5
2022 | nonsummer | GLNARM_7_UNIT 1 | METERING_TELEMETRY | 0
2022 | nonsummer | GLNARM_7_UNIT 1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | GLNARM_7_UNIT 1 | PLANT_TROUBLE | 0
2022 | nonsummer | GLNARM_7_UNIT 1 | UNIT_TESTING | 9.5
2022 | nonsummer | GLNARM_7_UNIT 2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 188
2022 | nonsummer | GLNARM_7_UNIT 2 | PLANT_MAINTENANCE | 94
2022 | nonsummer | GLNARM_7_UNIT 2 | PLANT_TROUBLE | 1050.4933
2022 | nonsummer | GLNARM_7_UNIT 2 | UNIT_TESTING | 0
2022 | nonsummer | GLNARM_7_UNIT 3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 526.7525
2022 | nonsummer | GLNARM_7_UNIT 3 | METERING_TELEMETRY | 0
2022 | nonsummer | GLNARM_7_UNIT 3 | PLANT_MAINTENANCE | 121.041
2022 | nonsummer | GLNARM_7_UNIT 3 | PLANT_TROUBLE | 672.45
2022 | nonsummer | GLNARM_7_UNIT 4 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 498.435
2022 | nonsummer | GLNARM_7_UNIT 4 | METERING_TELEMETRY | 0
2022 | nonsummer | GLNARM_7_UNIT 4 | PLANT_TROUBLE | 2995.586
2022 | nonsummer | GLNARM_7_UNIT 4 | UNIT_TESTING | 41.006
2022 | nonsummer | GLOW_6_SOLAR | PLANT_MAINTENANCE | 70
2022 | nonsummer | GLOW_6_SOLAR | PLANT_TROUBLE | 65
2022 | nonsummer | GOLETA_2_VALBT1 | METERING_TELEMETRY | 0
2022 | nonsummer | GOLETA_2_VALBT1 | PLANT_MAINTENANCE | 89.8333
2022 | nonsummer | GOLETA_2_VALBT1 | PLANT_TROUBLE | 18.3
2022 | nonsummer | GOLETA_2_VALBT1 | TRANSMISSION_INDUCED | 50
2022 | nonsummer | GOLETA_6_ELLWOD | PLANT_MAINTENANCE | 2970
2022 | nonsummer | GOLETA_6_ELLWOD | PLANT_TROUBLE | 3132.9
2022 | nonsummer | GOLETA_6_EXGEN | AMBIENT_NOT_DUE_TO_TEMP | 964
2022 | nonsummer | GOLETA_6_TR2BM2 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | GOLETA_6_TR2BM2 | AMBIENT_NOT_DUE_TO_TEMP | 232.44
2022 | nonsummer | GOLETA_6_TR2BM2 | NEW_GENERATOR_TEST_ENERGY | 0
2022 | nonsummer | GOLETA_6_TR2BM2 | PLANT_MAINTENANCE | 0
2022 | nonsummer | GOLETA_6_TR2BM2 | PLANT_TROUBLE | 0
2022 | nonsummer | GONZLS_6_UNIT | PLANT_MAINTENANCE | 53.3683
2022 | nonsummer | GONZLS_6_UNIT | PLANT_TROUBLE | 119.1853
2022 | nonsummer | GONZLS_6_UNIT | TRANSMISSION_INDUCED | 0
2022 | nonsummer | GOOSLK_1_SOLAR1 | PLANT_TROUBLE | 60
2022 | nonsummer | GOOSLK_1_SOLAR1 | TRANSMISSION_INDUCED | 144
2022 | nonsummer | GRADYW_5_GDYWD1 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | GRADYW_5_GDYWD1 | ENVIRONMENTAL_RESTRICTIONS | 250
2022 | nonsummer | GRADYW_5_GDYWD1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | GRADYW_5_GDYWD1 | PLANT_TROUBLE | 1626.6667
2022 | nonsummer | GRADYW_5_GDYWD1 | TRANSMISSION_INDUCED | 18345.3333
2022 | nonsummer | GRIDLY_6_SOLAR | PLANT_TROUBLE | 18.3333
2022 | nonsummer | GRIFFI_2_LSPDYN | PLANT_TROUBLE | 1428.8333
2022 | nonsummer | GRIZLY_1_UNIT 1 | TRANSMISSION_INDUCED | 21100
2022 | nonsummer | GRNLF1_1_PL1X2 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | GRNLF1_1_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | GRNLF1_1_PL1X2 | ENVIRONMENTAL_RESTRICTIONS | 9750
2022 | nonsummer | GRNLF1_1_PL1X2 | NEW_GENERATOR_TEST_ENERGY | 0
2022 | nonsummer | GRNLF1_1_PL1X2 | PLANT_MAINTENANCE | 0
2022 | nonsummer | GRNLF1_1_PL1X2 | PLANT_TROUBLE | 2100
2022 | nonsummer | GRNLF1_1_PL1X2 | UNIT_TESTING | 0
2022 | nonsummer | GRNLF2_1_UNIT | PLANT_TROUBLE | 15990
2022 | nonsummer | GRNLF2_1_UNIT | UNIT_TESTING | 0
2022 | nonsummer | GRNVLY_7_SCLAND | PLANT_MAINTENANCE | 146.865
2022 | nonsummer | GRNVLY_7_SCLAND | PLANT_TROUBLE | 240.1007
2022 | nonsummer | GRNVLY_7_SCLAND | TRANSMISSION_INDUCED | 0
2022 | nonsummer | GRSCRK_6_BGCKWW | ENVIRONMENTAL_RESTRICTIONS | 1502.5
2022 | nonsummer | GRSCRK_6_BGCKWW | PLANT_MAINTENANCE | 750.8333
2022 | nonsummer | GRSCRK_6_BGCKWW | PLANT_TROUBLE | 29.0833
2022 | nonsummer | GRSCRK_6_BGCKWW | TRANSMISSION_INDUCED | 0
2022 | nonsummer | GUERNS_6_HD3BM3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 72.4625
2022 | nonsummer | GUERNS_6_HD3BM3 | PLANT_MAINTENANCE | 0
2022 | nonsummer | GUERNS_6_HD3BM3 | PLANT_TROUBLE | 38.4167
2022 | nonsummer | GUERNS_6_HD3BM3 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | GUERNS_6_SOLAR | METERING_TELEMETRY | 0
2022 | nonsummer | GUERNS_6_SOLAR | PLANT_TROUBLE | 840
2022 | nonsummer | GUERNS_6_SOLAR | TRANSMISSION_INDUCED | 0
2022 | nonsummer | GUERNS_6_VH2BM1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 59.7958
2022 | nonsummer | GUERNS_6_VH2BM1 | PLANT_MAINTENANCE | 2
2022 | nonsummer | GUERNS_6_VH2BM1 | PLANT_TROUBLE | 37
2022 | nonsummer | GUERNS_6_VH2BM1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | GWFPWR_1_UNITS | AMBIENT_DUE_TO_TEMP | 2643.43
2022 | nonsummer | GWFPWR_1_UNITS | PLANT_TROUBLE | 0
2022 | nonsummer | GYS5X6_7_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 17203.2017
2022 | nonsummer | GYS5X6_7_UNITS | PLANT_MAINTENANCE | 0
2022 | nonsummer | GYS5X6_7_UNITS | PLANT_TROUBLE | 14
2022 | nonsummer | GYS5X6_7_UNITS | TRANSMISSION_INDUCED | 0
2022 | nonsummer | GYS7X8_7_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 14493.3767
2022 | nonsummer | GYS7X8_7_UNITS | PLANT_TROUBLE | 5110.3395
2022 | nonsummer | GYS7X8_7_UNITS | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2022 | nonsummer | GYS7X8_7_UNITS | TRANSITIONAL_LIMITATION | 0
2022 | nonsummer | GYS7X8_7_UNITS | TRANSMISSION_INDUCED | 158
2022 | nonsummer | HAASPH_7_PL1X2 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | HAASPH_7_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 72
2022 | nonsummer | HAASPH_7_PL1X2 | PLANT_TROUBLE | 14328
2022 | nonsummer | HAASPH_7_PL1X2 | TRANSITIONAL_LIMITATION | 0
2022 | nonsummer | HAASPH_7_PL1X2 | TRANSMISSION_INDUCED | 4422
2022 | nonsummer | HALSEY_6_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 1256.95
2022 | nonsummer | HALSEY_6_UNIT | PLANT_TROUBLE | 1098.058
2022 | nonsummer | HARBGN_7_UNITS | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | HARBGN_7_UNITS | PLANT_MAINTENANCE | 1907.675
2022 | nonsummer | HARBGN_7_UNITS | PLANT_TROUBLE | 1090.1
2022 | nonsummer | HARBGN_7_UNITS | UNIT_TESTING | 0
2022 | nonsummer | HARDWK_6_STWBM1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 38.7167
2022 | nonsummer | HARDWK_6_STWBM1 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | HARDWK_6_STWBM1 | METERING_TELEMETRY | 12
2022 | nonsummer | HARDWK_6_STWBM1 | PLANT_MAINTENANCE | 2.7
2022 | nonsummer | HARDWK_6_STWBM1 | PLANT_TROUBLE | 15
2022 | nonsummer | HARDWK_6_STWBM1 | TRANSMISSION_INDUCED | 5
2022 | nonsummer | HATCR1_7_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | HATCR1_7_UNIT | PLANT_TROUBLE | 0.70833
2022 | nonsummer | HATCR1_7_UNIT | TRANSMISSION_INDUCED | 0
2022 | nonsummer | HATCR2_7_UNIT | PLANT_TROUBLE | 2575.5
2022 | nonsummer | HATCR2_7_UNIT | TRANSMISSION_INDUCED | 0
2022 | nonsummer | HATLOS_6_BWDHY1 | PLANT_MAINTENANCE | 1.7
2022 | nonsummer | HATLOS_6_BWDHY1 | PLANT_TROUBLE | 6
2022 | nonsummer | HATLOS_6_BWDHY1 | TRANSMISSION_INDUCED | 4
2022 | nonsummer | HATLOS_6_LSCRK | AMBIENT_NOT_DUE_TO_TEMP | 782.46
2022 | nonsummer | HATLOS_6_LSCRK | PLANT_MAINTENANCE | 1.6433
2022 | nonsummer | HATLOS_6_LSCRK | PLANT_TROUBLE | 5.887
2022 | nonsummer | HATLOS_6_LSCRK | TRANSMISSION_INDUCED | 0.51333
2022 | nonsummer | HATRDG_2_WIND | AMBIENT_DUE_TO_TEMP | 414.1667
2022 | nonsummer | HATRDG_2_WIND | PLANT_MAINTENANCE | 2546.1333
2022 | nonsummer | HAYPRS_6_HAYHD1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 3659.6
2022 | nonsummer | HAYPRS_6_HAYHD1 | AMBIENT_NOT_DUE_TO_TEMP | 491.1
2022 | nonsummer | HAYPRS_6_HAYHD1 | ENVIRONMENTAL_RESTRICTIONS | 319
2022 | nonsummer | HAYPRS_6_HAYHD2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 3051
2022 | nonsummer | HAYPRS_6_HAYHD2 | AMBIENT_NOT_DUE_TO_TEMP | 2780.5
2022 | nonsummer | HELMPG_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 24472.75
2022 | nonsummer | HELMPG_7_UNIT 1 | PLANT_MAINTENANCE | 46411.5667
2022 | nonsummer | HELMPG_7_UNIT 1 | PLANT_TROUBLE | 0
2022 | nonsummer | HELMPG_7_UNIT 1 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2022 | nonsummer | HELMPG_7_UNIT 1 | TRANSMISSION_INDUCED | 399
2022 | nonsummer | HELMPG_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 21041.8
2022 | nonsummer | HELMPG_7_UNIT 2 | PLANT_MAINTENANCE | 39343.3333
2022 | nonsummer | HELMPG_7_UNIT 2 | PLANT_TROUBLE | 384
2022 | nonsummer | HELMPG_7_UNIT 2 | TRANSMISSION_INDUCED | 399
2022 | nonsummer | HELMPG_7_UNIT 3 | AMBIENT_NOT_DUE_TO_TEMP | 26735
2022 | nonsummer | HELMPG_7_UNIT 3 | PLANT_MAINTENANCE | 54540
2022 | nonsummer | HELMPG_7_UNIT 3 | PLANT_TROUBLE | 0
2022 | nonsummer | HELMPG_7_UNIT 3 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2022 | nonsummer | HELMPG_7_UNIT 3 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | HENRTA_6_HDEBT1 | METERING_TELEMETRY | 0
2022 | nonsummer | HENRTA_6_HDEBT1 | PLANT_MAINTENANCE | 128.7333
2022 | nonsummer | HENRTA_6_HDEBT1 | PLANT_TROUBLE | 0
2022 | nonsummer | HENRTA_6_HDEBT1 | RTU_RIG | 0
2022 | nonsummer | HENRTA_6_SOLAR1 | PLANT_TROUBLE | 22.5
2022 | nonsummer | HENRTA_6_SOLAR1 | TRANSMISSION_INDUCED | 30
2022 | nonsummer | HENRTA_6_SOLAR2 | PLANT_MAINTENANCE | 0
2022 | nonsummer | HENRTA_6_SOLAR2 | TRANSMISSION_INDUCED | 10
2022 | nonsummer | HENRTA_6_UNITA1 | AMBIENT_DUE_TO_TEMP | 2360.99
2022 | nonsummer | HENRTA_6_UNITA1 | PLANT_TROUBLE | 106.759
2022 | nonsummer | HENRTA_6_UNITA2 | AMBIENT_DUE_TO_TEMP | 2285.52
2022 | nonsummer | HENRTA_6_UNITA2 | PLANT_MAINTENANCE | 0
2022 | nonsummer | HENRTA_6_UNITA2 | PLANT_TROUBLE | 115.4233
2022 | nonsummer | HENRTS_1_SOLAR | PLANT_MAINTENANCE | 550
2022 | nonsummer | HENRTS_1_SOLAR | PLANT_TROUBLE | 571.5667
2022 | nonsummer | HENRTS_1_SOLAR | TRANSMISSION_INDUCED | 498.1667
2022 | nonsummer | HERDLN_6_BYHSR1 | METERING_TELEMETRY | 0
2022 | nonsummer | HERDLN_6_BYHSR1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | HIDSRT_2_UNITS | AMBIENT_DUE_TO_TEMP | 47457.4167
2022 | nonsummer | HIDSRT_2_UNITS | PLANT_MAINTENANCE | 6189.8333
2022 | nonsummer | HIDSRT_2_UNITS | PLANT_TROUBLE | 6169.2917
2022 | nonsummer | HIDSRT_2_UNITS | TRANSMISSION_INDUCED | 0
2022 | nonsummer | HIDSRT_2_UNITS | UNIT_TESTING | 1060.4925
2022 | nonsummer | HIGGNS_1_COMBIE | PLANT_MAINTENANCE | 0
2022 | nonsummer | HIGGNS_1_COMBIE | PLANT_TROUBLE | 3.3667
2022 | nonsummer | HIGGNS_1_COMBIE | TRANSMISSION_INDUCED | 1.775
2022 | nonsummer | HIGHDS_2_H5SBT1 | METERING_TELEMETRY | 212
2022 | nonsummer | HIGHDS_2_H5SBT1 | PLANT_MAINTENANCE | 1017.8333
2022 | nonsummer | HIGHDS_2_H5SBT1 | PLANT_TROUBLE | 6917.8688
2022 | nonsummer | HIGHDS_2_H5SBT1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | HIGHDS_2_H5SBT1 | UNIT_TESTING | 1300
2022 | nonsummer | HIGHDS_2_H5SSR1 | METERING_TELEMETRY | 200
2022 | nonsummer | HIGHDS_2_H5SSR1 | PLANT_MAINTENANCE | 550
2022 | nonsummer | HIGHDS_2_H5SSR1 | PLANT_TROUBLE | 500
2022 | nonsummer | HIGHDS_2_H5SSR1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | HIGHDS_2_H5SSR1 | UNIT_TESTING | 0
2022 | nonsummer | HINSON_6_CARBGN | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2022 | nonsummer | HINSON_6_CARBGN | PLANT_MAINTENANCE | 226.95
2022 | nonsummer | HINSON_6_CARBGN | PLANT_TROUBLE | 1670
2022 | nonsummer | HINSON_6_LBECH1 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | HINSON_6_LBECH1 | PLANT_TROUBLE | 315
2022 | nonsummer | HINSON_6_LBECH2 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | HINSON_6_LBECH3 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | HINSON_6_LBECH4 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | HINSON_6_LBECH4 | PLANT_MAINTENANCE | 0
2022 | nonsummer | HINSON_6_LBECH4 | PLANT_TROUBLE | 0
2022 | nonsummer | HINSON_6_SERRGN | PLANT_MAINTENANCE | 0
2022 | nonsummer | HINSON_6_SERRGN | PLANT_TROUBLE | 150
2022 | nonsummer | HNTGBH_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 87.1333
2022 | nonsummer | HNTGBH_2_PL1X3 | AMBIENT_NOT_DUE_TO_TEMP | 5.6735
2022 | nonsummer | HNTGBH_2_PL1X3 | PLANT_MAINTENANCE | 1918.7535
2022 | nonsummer | HNTGBH_2_PL1X3 | PLANT_TROUBLE | 56715.5895
2022 | nonsummer | HNTGBH_2_PL1X3 | TRANSMISSION_INDUCED | 13461
2022 | nonsummer | HNTGBH_2_PL1X3 | UNIT_TESTING | 0
2022 | nonsummer | HNTGBH_7_UNIT 2 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | HNTGBH_7_UNIT 2 | PLANT_MAINTENANCE | 328.918
2022 | nonsummer | HNTGBH_7_UNIT 2 | PLANT_TROUBLE | 3527.362
2022 | nonsummer | HNTGBH_7_UNIT 2 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | HNTGBH_7_UNIT 2 | UNIT_TESTING | 454.2
2022 | nonsummer | HOLGAT_1_BORAX | PLANT_MAINTENANCE | 241
2022 | nonsummer | HOLGAT_1_BORAX | PLANT_TROUBLE | 144.6
2022 | nonsummer | HOLSTR_1_SOLAR | METERING_TELEMETRY | 0
2022 | nonsummer | HOLSTR_1_SOLAR | PLANT_TROUBLE | 0
2022 | nonsummer | HOLSTR_1_SOLAR2 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | HOOVER_2_MWDDYN | AMBIENT_NOT_DUE_TO_TEMP | 112769
2022 | nonsummer | HOOVER_2_MWDDYN | PLANT_MAINTENANCE | 540
2022 | nonsummer | HOOVER_2_MWDDYN | PLANT_TROUBLE | 592
2022 | nonsummer | HOOVER_2_MWDDYN | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 6225
2022 | nonsummer | HOOVER_2_MWDDYN | TRANSMISSION_INDUCED | 0
2022 | nonsummer | HOOVER_2_VEADYN | AMBIENT_NOT_DUE_TO_TEMP | 8343
2022 | nonsummer | HOOVER_2_VEADYN | PLANT_MAINTENANCE | 0
2022 | nonsummer | HOOVER_2_VEADYN | PLANT_TROUBLE | 51
2022 | nonsummer | HOOVER_2_VEADYN | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 400
2022 | nonsummer | HOOVER_2_VEADYN | TRANSMISSION_INDUCED | 0
2022 | nonsummer | HUMBPP_1_UNITS3 | AMBIENT_NOT_DUE_TO_TEMP | 583.5507
2022 | nonsummer | HUMBPP_1_UNITS3 | METERING_TELEMETRY | 0
2022 | nonsummer | HUMBPP_1_UNITS3 | PLANT_MAINTENANCE | 244.05
2022 | nonsummer | HUMBPP_1_UNITS3 | PLANT_TROUBLE | 406.7473
2022 | nonsummer | HUMBPP_1_UNITS3 | TRANSMISSION_INDUCED | 1029.7693
2022 | nonsummer | HUMBPP_6_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 5798.0857
2022 | nonsummer | HUMBPP_6_UNITS | PLANT_MAINTENANCE | 650.8
2022 | nonsummer | HUMBPP_6_UNITS | PLANT_TROUBLE | 1986.8382
2022 | nonsummer | HUMBPP_6_UNITS | TRANSMISSION_INDUCED | 1792.954
2022 | nonsummer | HURON_6_SOLAR | PLANT_MAINTENANCE | 800
2022 | nonsummer | HURON_6_SOLAR | TRANSMISSION_INDUCED | 0
2022 | nonsummer | HYTTHM_2_UNITS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 41736.6667
2022 | nonsummer | HYTTHM_2_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 24376.8
2022 | nonsummer | HYTTHM_2_UNITS | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | HYTTHM_2_UNITS | PLANT_MAINTENANCE | 6825.5
2022 | nonsummer | HYTTHM_2_UNITS | PLANT_TROUBLE | 10908.8
2022 | nonsummer | INDIGO_1_UNIT 1 | AMBIENT_DUE_TO_TEMP | 224.7
2022 | nonsummer | INDIGO_1_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 110.25
2022 | nonsummer | INDIGO_1_UNIT 1 | PLANT_MAINTENANCE | 498.3
2022 | nonsummer | INDIGO_1_UNIT 1 | PLANT_TROUBLE | 0
2022 | nonsummer | INDIGO_1_UNIT 1 | TRANSMISSION_INDUCED | 1.855
2022 | nonsummer | INDIGO_1_UNIT 2 | AMBIENT_DUE_TO_TEMP | 544.5
2022 | nonsummer | INDIGO_1_UNIT 2 | PLANT_MAINTENANCE | 453
2022 | nonsummer | INDIGO_1_UNIT 2 | PLANT_TROUBLE | 48.32
2022 | nonsummer | INDIGO_1_UNIT 2 | TRANSMISSION_INDUCED | 21.3
2022 | nonsummer | INDIGO_1_UNIT 3 | AMBIENT_DUE_TO_TEMP | 622.5
2022 | nonsummer | INDIGO_1_UNIT 3 | PLANT_MAINTENANCE | 3624
2022 | nonsummer | INDIGO_1_UNIT 3 | PLANT_TROUBLE | 0
2022 | nonsummer | INDIGO_1_UNIT 3 | TRANSMISSION_INDUCED | 21.05
2022 | nonsummer | INDVLY_1_UNITS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 237.79
2022 | nonsummer | INDVLY_1_UNITS | TRANSMISSION_INDUCED | 1.4548
2022 | nonsummer | INTKEP_2_UNITS | ENVIRONMENTAL_RESTRICTIONS | 43772.3333
2022 | nonsummer | INTKEP_2_UNITS | PLANT_MAINTENANCE | 940
2022 | nonsummer | INTKEP_2_UNITS | PLANT_TROUBLE | 2704.25
2022 | nonsummer | INTKEP_2_UNITS | TRANSMISSION_INDUCED | 2000
2022 | nonsummer | INTKEP_2_UNITS | UNIT_TESTING | 2250
2022 | nonsummer | INTMNT_3_ANAHEIM | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 144178
2022 | nonsummer | INTMNT_3_ANAHEIM | PLANT_MAINTENANCE | 24672
2022 | nonsummer | INTMNT_3_ANAHEIM | PLANT_TROUBLE | 108
2022 | nonsummer | INTMNT_3_ANAHEIM | TRANSITIONAL_LIMITATION | 309
2022 | nonsummer | INTMNT_3_ANAHEIM | TRANSMISSION_INDUCED | 2324
2022 | nonsummer | INTMNT_3_ANAHEIM | UNIT_TESTING | 0
2022 | nonsummer | INTMNT_3_PASADENA | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 28616.88
2022 | nonsummer | INTMNT_3_PASADENA | PLANT_MAINTENANCE | 22004.74
2022 | nonsummer | INTMNT_3_PASADENA | PLANT_TROUBLE | 148.1123
2022 | nonsummer | INTMNT_3_PASADENA | TRANSMISSION_INDUCED | 1033.9977
2022 | nonsummer | INTMNT_3_PASADENA | UNIT_SUPPORTING_STARTUP | 0
2022 | nonsummer | INTMNT_3_PASADENA | UNIT_TESTING | 0
2022 | nonsummer | INTMNT_3_RIVERSIDE | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 22881
2022 | nonsummer | INTMNT_3_RIVERSIDE | ENVIRONMENTAL_RESTRICTIONS | 24279
2022 | nonsummer | INTMNT_3_RIVERSIDE | PLANT_MAINTENANCE | 101
2022 | nonsummer | INTMNT_3_RIVERSIDE | PLANT_TROUBLE | 83.65
2022 | nonsummer | INTMNT_3_RIVERSIDE | TRANSMISSION_INDUCED | 867.95
2022 | nonsummer | INTTRB_6_UNIT | TRANSMISSION_INDUCED | 318.9333
2022 | nonsummer | IVANPA_1_UNIT1 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | IVANPA_1_UNIT1 | AMBIENT_NOT_DUE_TO_TEMP | 17755.2
2022 | nonsummer | IVANPA_1_UNIT1 | PLANT_MAINTENANCE | 3150
2022 | nonsummer | IVANPA_1_UNIT1 | PLANT_TROUBLE | 9099.9167
2022 | nonsummer | IVANPA_1_UNIT1 | UNIT_TESTING | 0
2022 | nonsummer | IVANPA_1_UNIT2 | AMBIENT_DUE_TO_TEMP | 931
2022 | nonsummer | IVANPA_1_UNIT2 | AMBIENT_NOT_DUE_TO_TEMP | 266
2022 | nonsummer | IVANPA_1_UNIT2 | PLANT_TROUBLE | 1330
2022 | nonsummer | IVANPA_1_UNIT2 | RTU_RIG | 2187.85
2022 | nonsummer | IVANPA_1_UNIT3 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | IVANPA_1_UNIT3 | AMBIENT_NOT_DUE_TO_TEMP | 19577.6
2022 | nonsummer | IVANPA_1_UNIT3 | PLANT_TROUBLE | 266
2022 | nonsummer | IVSLR2_2_SM2SR1 | METERING_TELEMETRY | 300
2022 | nonsummer | IVSLR2_2_SM2SR1 | PLANT_TROUBLE | 750
2022 | nonsummer | IVSLRP_2_SOLAR1 | PLANT_MAINTENANCE | 441
2022 | nonsummer | IVSLRP_2_SOLAR1 | PLANT_TROUBLE | 62750
2022 | nonsummer | IVWEST_2_SOLAR1 | PLANT_MAINTENANCE | 571.3333
2022 | nonsummer | IVWEST_2_SOLAR1 | PLANT_TROUBLE | 14
2022 | nonsummer | JACMSR_1_JACSR1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | JANCRK_6_RCABT1 | PLANT_MAINTENANCE | 0.5
2022 | nonsummer | JANCRK_6_RCABT1 | PLANT_TROUBLE | 51.4583
2022 | nonsummer | JANCRK_6_RCABT1 | TRANSMISSION_INDUCED | 20.3292
2022 | nonsummer | JANCRK_6_RCABT1 | UNIT_TESTING | 35
2022 | nonsummer | JAVASR_1_JAVSR1 | NEW_GENERATOR_TEST_ENERGY | 0
2022 | nonsummer | JAVASR_1_JAVSR1 | TRANSMISSION_INDUCED | 105.75
2022 | nonsummer | JAWBNE_2_NSRWND | AMBIENT_NOT_DUE_TO_TEMP | 395
2022 | nonsummer | JAWBNE_2_NSRWND | METERING_TELEMETRY | 70
2022 | nonsummer | JAWBNE_2_NSRWND | PLANT_MAINTENANCE | 13018.8417
2022 | nonsummer | JAWBNE_2_NSRWND | PLANT_TROUBLE | 0
2022 | nonsummer | JAWBNE_2_NSRWND | TRANSMISSION_INDUCED | 0
2022 | nonsummer | JAWBNE_2_SRWND | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | JAWBNE_2_SRWND | METERING_TELEMETRY | 0
2022 | nonsummer | JAWBNE_2_SRWND | PLANT_MAINTENANCE | 0
2022 | nonsummer | JAWBNE_2_SRWND | PLANT_TROUBLE | 9198.2333
2022 | nonsummer | JAWBNE_2_SRWND | TRANSMISSION_INDUCED | 0
2022 | nonsummer | JAWBNE_2_SRWWD2 | AMBIENT_DUE_TO_TEMP | 75.5
2022 | nonsummer | JAWBNE_2_SRWWD2 | PLANT_MAINTENANCE | 0
2022 | nonsummer | JAWBNE_2_SRWWD2 | PLANT_TROUBLE | 4605.878
2022 | nonsummer | JAWBNE_2_SRWWD2 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | JAYNE_6_WLSLR | PLANT_MAINTENANCE | 135
2022 | nonsummer | JAYNE_6_WLSLR | PLANT_TROUBLE | 739
2022 | nonsummer | JOANEC_2_STABT1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | JOANEC_2_STABT1 | PLANT_TROUBLE | 193.1333
2022 | nonsummer | JOANEC_2_STABT1 | TRANSMISSION_INDUCED | 25.3333
2022 | nonsummer | JOANEC_2_STABT1 | UNIT_TESTING | 0
2022 | nonsummer | JOANEC_2_STABT2 | NEW_GENERATOR_TEST_ENERGY | 0
2022 | nonsummer | JOANEC_2_STABT2 | PLANT_MAINTENANCE | 0
2022 | nonsummer | JOANEC_2_STABT2 | PLANT_TROUBLE | 0
2022 | nonsummer | JOHANN_2_JOSBT1 | METERING_TELEMETRY | 0
2022 | nonsummer | JOHANN_2_JOSBT1 | PLANT_MAINTENANCE | 372.6833
2022 | nonsummer | JOHANN_2_JOSBT1 | PLANT_TROUBLE | 167.23
2022 | nonsummer | JOHANN_2_JOSBT1 | RTU_RIG | 0
2022 | nonsummer | JOHANN_2_JOSBT1 | TRANSMISSION_INDUCED | 10
2022 | nonsummer | JOHANN_2_JOSBT1 | UNIT_TESTING | 400
2022 | nonsummer | JOHANN_2_JOSBT2 | METERING_TELEMETRY | 0
2022 | nonsummer | JOHANN_2_JOSBT2 | PLANT_MAINTENANCE | 507.1333
2022 | nonsummer | JOHANN_2_JOSBT2 | PLANT_TROUBLE | 126.6
2022 | nonsummer | JOHANN_2_JOSBT2 | UNIT_TESTING | 650
2022 | nonsummer | JOHANN_2_OCEBT2 | PLANT_MAINTENANCE | 19.2
2022 | nonsummer | JOHANN_2_OCEBT2 | PLANT_TROUBLE | 75
2022 | nonsummer | JOHANN_2_OCEBT2 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | JOHANN_2_OCEBT2 | UNIT_TESTING | 0
2022 | nonsummer | JOHANN_2_OCEBT3 | PLANT_MAINTENANCE | 27.55
2022 | nonsummer | JOHANN_2_OCEBT3 | PLANT_TROUBLE | 50
2022 | nonsummer | JOHANN_2_OCEBT3 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | JOHANN_2_OCEBT3 | UNIT_TESTING | 0
2022 | nonsummer | KANSAS_6_SOLAR | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | KANSAS_6_SOLAR | METERING_TELEMETRY | 100
2022 | nonsummer | KANSAS_6_SOLAR | PLANT_MAINTENANCE | 71.6
2022 | nonsummer | KANSAS_6_SOLAR | PLANT_TROUBLE | 482.825
2022 | nonsummer | KANSAS_6_SOLAR | TRANSMISSION_INDUCED | 0
2022 | nonsummer | KEARNY_6_NESBT1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | KEARNY_6_NESBT1 | PLANT_TROUBLE | 512.6167
2022 | nonsummer | KEARNY_6_SESBT2 | PLANT_MAINTENANCE | 0
2022 | nonsummer | KEARNY_6_SESBT2 | PLANT_TROUBLE | 365
2022 | nonsummer | KEKAWK_6_UNIT | PLANT_TROUBLE | 3602.5
2022 | nonsummer | KEKAWK_6_UNIT | TRANSMISSION_INDUCED | 1732.5
2022 | nonsummer | KELSO_2_UNITS | AMBIENT_DUE_TO_TEMP | 1317.71
2022 | nonsummer | KELSO_2_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | KELSO_2_UNITS | ENVIRONMENTAL_RESTRICTIONS | 81.6747
2022 | nonsummer | KELSO_2_UNITS | PLANT_MAINTENANCE | 0
2022 | nonsummer | KELSO_2_UNITS | PLANT_TROUBLE | 113.705
2022 | nonsummer | KELSO_2_UNITS | UNIT_TESTING | 0
2022 | nonsummer | KELYRG_6_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | KELYRG_6_UNIT | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | KELYRG_6_UNIT | PLANT_MAINTENANCE | 0
2022 | nonsummer | KELYRG_6_UNIT | PLANT_TROUBLE | 6.125
2022 | nonsummer | KELYRG_6_UNIT | TRANSMISSION_INDUCED | 1603.8
2022 | nonsummer | KERKH2_7_UNIT 1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 74.385
2022 | nonsummer | KERKH2_7_UNIT 1 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | KERKH2_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 20836.9057
2022 | nonsummer | KERKH2_7_UNIT 1 | METERING_TELEMETRY | 0
2022 | nonsummer | KERKH2_7_UNIT 1 | PLANT_MAINTENANCE | 271.89
2022 | nonsummer | KERKH2_7_UNIT 1 | PLANT_TROUBLE | 359.1
2022 | nonsummer | KERMAN_6_SOLAR1 | PLANT_MAINTENANCE | 3
2022 | nonsummer | KERMAN_6_SOLAR1 | TRANSMISSION_INDUCED | 1.95
2022 | nonsummer | KERMAN_6_SOLAR2 | PLANT_MAINTENANCE | 3
2022 | nonsummer | KERMAN_6_SOLAR2 | PLANT_TROUBLE | 232.5
2022 | nonsummer | KERMAN_6_SOLAR2 | TRANSMISSION_INDUCED | 1.95
2022 | nonsummer | KERNFT_1_UNITS | AMBIENT_DUE_TO_TEMP | 923.2
2022 | nonsummer | KERNFT_1_UNITS | AMBIENT_DUE_TO_TEMP | 2211.08
2022 | nonsummer | KERNFT_1_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | KERNFT_1_UNITS | PLANT_TROUBLE | 1300.12
2022 | nonsummer | KERNFT_1_UNITS | RTU_RIG | 0
2022 | nonsummer | KERNFT_1_UNITS | UNIT_TESTING | 205.5
2022 | nonsummer | KERNFT_1_UNITS | UNIT_TESTING | 21.12
2022 | nonsummer | KERNRG_1_UNITS | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | KERNRG_1_UNITS | PLANT_MAINTENANCE | 374.4133
2022 | nonsummer | KERNRG_1_UNITS | PLANT_TROUBLE | 278.2133
2022 | nonsummer | KERRGN_1_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 8299.7083
2022 | nonsummer | KERRGN_1_UNIT 1 | METERING_TELEMETRY | 177.6667
2022 | nonsummer | KERRGN_1_UNIT 1 | PLANT_TROUBLE | 0
2022 | nonsummer | KERRGN_1_UNIT 1 | TRANSMISSION_INDUCED | 26
2022 | nonsummer | KINGCO_1_KINGBR | PLANT_MAINTENANCE | 172.5
2022 | nonsummer | KINGCO_1_KINGBR | PLANT_TROUBLE | 24.15
2022 | nonsummer | KINGCO_1_KINGBR | TRANSMISSION_INDUCED | 10522.5
2022 | nonsummer | KINGRV_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 2419.8117
2022 | nonsummer | KINGRV_7_UNIT 1 | PLANT_MAINTENANCE | 768
2022 | nonsummer | KINGRV_7_UNIT 1 | PLANT_TROUBLE | 127.1467
2022 | nonsummer | KINGRV_7_UNIT 1 | TRANSMISSION_INDUCED | 232.1067
2022 | nonsummer | KIRKER_7_KELCYN | PLANT_MAINTENANCE | 0
2022 | nonsummer | KIRKER_7_KELCYN | PLANT_TROUBLE | 752.3045
2022 | nonsummer | KIRKER_7_KELCYN | TRANSMISSION_INDUCED | 11.57
2022 | nonsummer | KNGBRD_2_SOLAR1 | PLANT_MAINTENANCE | 120.6667
2022 | nonsummer | KNGBRD_2_SOLAR1 | PLANT_TROUBLE | 22.2
2022 | nonsummer | KNGBRD_2_SOLAR2 | METERING_TELEMETRY | 0
2022 | nonsummer | KNGBRD_2_SOLAR2 | PLANT_MAINTENANCE | 179
2022 | nonsummer | KNGBRD_2_SOLAR2 | PLANT_TROUBLE | 38.6667
2022 | nonsummer | KNGCTY_6_UNITA1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1784
2022 | nonsummer | KNGCTY_6_UNITA1 | AMBIENT_DUE_TO_TEMP | 165.1
2022 | nonsummer | KNGCTY_6_UNITA1 | METERING_TELEMETRY | 0
2022 | nonsummer | KNGCTY_6_UNITA1 | PLANT_TROUBLE | 59.8357
2022 | nonsummer | KNGCTY_6_UNITA1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | KNTSTH_6_SOLAR | PLANT_MAINTENANCE | 0
2022 | nonsummer | KNTSTH_6_SOLAR | PLANT_TROUBLE | 534.775
2022 | nonsummer | KRAMER_2_SEGS 9 | PLANT_MAINTENANCE | 3360
2022 | nonsummer | KYCORA_6_KMSBT1 | METERING_TELEMETRY | 1.4667
2022 | nonsummer | KYCORA_6_KMSBT1 | PLANT_TROUBLE | 484.9417
2022 | nonsummer | KYCORA_6_KMSBT1 | TRANSMISSION_INDUCED | 3.5
2022 | nonsummer | LAKHDG_6_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 1200
2022 | nonsummer | LAKHDG_6_UNIT 1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | LAKHDG_6_UNIT 1 | PLANT_TROUBLE | 0
2022 | nonsummer | LAKHDG_6_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 1200
2022 | nonsummer | LAKHDG_6_UNIT 2 | PLANT_MAINTENANCE | 0
2022 | nonsummer | LAKHDG_6_UNIT 2 | PLANT_TROUBLE | 0
2022 | nonsummer | LAMONT_1_SOLAR1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | LAMONT_1_SOLAR1 | PLANT_TROUBLE | 0
2022 | nonsummer | LAMONT_1_SOLAR1 | RTU_RIG | 500
2022 | nonsummer | LAMONT_1_SOLAR2 | PLANT_MAINTENANCE | 120
2022 | nonsummer | LAMONT_1_SOLAR2 | PLANT_TROUBLE | 0
2022 | nonsummer | LAMONT_1_SOLAR2 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | LAMONT_1_SOLAR3 | PLANT_MAINTENANCE | 44.97
2022 | nonsummer | LAMONT_1_SOLAR3 | PLANT_TROUBLE | 1310.8525
2022 | nonsummer | LAMONT_1_SOLAR3 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | LAMONT_1_SOLAR4 | PLANT_MAINTENANCE | 79.98
2022 | nonsummer | LAMONT_1_SOLAR4 | PLANT_TROUBLE | 595.5373
2022 | nonsummer | LAMONT_1_SOLAR5 | PLANT_MAINTENANCE | 49.98
2022 | nonsummer | LAMONT_1_SOLAR5 | PLANT_TROUBLE | 1293.9688
2022 | nonsummer | LAPLMA_2_UNIT 1 | AMBIENT_DUE_TO_TEMP | 10809
2022 | nonsummer | LAPLMA_2_UNIT 1 | PLANT_TROUBLE | 3137.4
2022 | nonsummer | LAPLMA_2_UNIT 1 | UNIT_TESTING | 0
2022 | nonsummer | LAPLMA_2_UNIT 2 | AMBIENT_DUE_TO_TEMP | 8326.5
2022 | nonsummer | LAPLMA_2_UNIT 2 | ENVIRONMENTAL_RESTRICTIONS | 10033.8
2022 | nonsummer | LAPLMA_2_UNIT 2 | PLANT_TROUBLE | 3140.643
2022 | nonsummer | LAPLMA_2_UNIT 2 | UNIT_TESTING | 0
2022 | nonsummer | LAPLMA_2_UNIT 3 | AMBIENT_DUE_TO_TEMP | 10834.7667
2022 | nonsummer | LAPLMA_2_UNIT 3 | PLANT_TROUBLE | 6026.3167
2022 | nonsummer | LAPLMA_2_UNIT 3 | UNIT_TESTING | 0
2022 | nonsummer | LAPLMA_2_UNIT 4 | AMBIENT_DUE_TO_TEMP | 16576
2022 | nonsummer | LAPLMA_2_UNIT 4 | ENVIRONMENTAL_RESTRICTIONS | 137
2022 | nonsummer | LAPLMA_2_UNIT 4 | PLANT_TROUBLE | 13953.3167
2022 | nonsummer | LAPLMA_2_UNIT 4 | UNIT_TESTING | 0
2022 | nonsummer | LARKSP_6_UNIT 1 | AMBIENT_DUE_TO_TEMP | 636
2022 | nonsummer | LARKSP_6_UNIT 1 | PLANT_MAINTENANCE | 2968.6
2022 | nonsummer | LARKSP_6_UNIT 1 | PLANT_TROUBLE | 122.165
2022 | nonsummer | LARKSP_6_UNIT 1 | TRANSMISSION_INDUCED | 230.5
2022 | nonsummer | LARKSP_6_UNIT 2 | AMBIENT_DUE_TO_TEMP | 743.9
2022 | nonsummer | LARKSP_6_UNIT 2 | METERING_TELEMETRY | 0
2022 | nonsummer | LARKSP_6_UNIT 2 | PLANT_MAINTENANCE | 3034.1
2022 | nonsummer | LARKSP_6_UNIT 2 | PLANT_TROUBLE | 125.5477
2022 | nonsummer | LARKSP_6_UNIT 2 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | LAROA2_2_UNITA1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2022 | nonsummer | LAROA2_2_UNITA1 | AMBIENT_DUE_TO_TEMP | 1402
2022 | nonsummer | LAROA2_2_UNITA1 | PLANT_MAINTENANCE | 7400.6333
2022 | nonsummer | LAROA2_2_UNITA1 | PLANT_TROUBLE | 1821.5
2022 | nonsummer | LAROA2_2_UNITA1 | UNIT_TESTING | 740
2022 | nonsummer | LASSEN_6_UNITS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 3391.3
2022 | nonsummer | LASSEN_6_UNITS | ENVIRONMENTAL_RESTRICTIONS | 300
2022 | nonsummer | LASSEN_6_UNITS | METERING_TELEMETRY | 0
2022 | nonsummer | LASSEN_6_UNITS | PLANT_MAINTENANCE | 235
2022 | nonsummer | LASSEN_6_UNITS | PLANT_TROUBLE | 229.9267
2022 | nonsummer | LASSEN_6_UNITS | TRANSMISSION_INDUCED | 318
2022 | nonsummer | LEBECS_2_UNITS | AMBIENT_DUE_TO_TEMP | 3396.706
2022 | nonsummer | LEBECS_2_UNITS | PLANT_TROUBLE | 121374.1873
2022 | nonsummer | LEBECS_2_UNITS | TRANSITIONAL_LIMITATION | 808.5667
2022 | nonsummer | LEBECS_2_UNITS | TRANSMISSION_INDUCED | 592.6667
2022 | nonsummer | LEBECS_2_UNITS | UNIT_TESTING | 0
2022 | nonsummer | LECEF_1_UNITS | AMBIENT_DUE_TO_TEMP | 11178.24
2022 | nonsummer | LECEF_1_UNITS | METERING_TELEMETRY | 0
2022 | nonsummer | LECEF_1_UNITS | PLANT_MAINTENANCE | 0
2022 | nonsummer | LECEF_1_UNITS | PLANT_TROUBLE | 5379.48
2022 | nonsummer | LECEF_1_UNITS | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2022 | nonsummer | LECONT_2_LESBT1 | METERING_TELEMETRY | 152.0833
2022 | nonsummer | LECONT_2_LESBT1 | NEW_GENERATOR_TEST_ENERGY | 0
2022 | nonsummer | LECONT_2_LESBT1 | PLANT_MAINTENANCE | 450
2022 | nonsummer | LECONT_2_LESBT1 | PLANT_TROUBLE | 0
2022 | nonsummer | LECONT_2_LESBT1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | LECONT_2_LESBT1 | UNIT_TESTING | 0
2022 | nonsummer | LEPRFD_1_KANSAS | METERING_TELEMETRY | 0
2022 | nonsummer | LEPRFD_1_KANSAS | PLANT_TROUBLE | 875
2022 | nonsummer | LGHTHP_6_ICEGEN | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | LGHTHP_6_ICEGEN | PLANT_TROUBLE | 0
2022 | nonsummer | LGHTHP_6_ICEGEN | TRANSMISSION_INDUCED | 240
2022 | nonsummer | LGHTHP_6_ICEGEN | UNIT_TESTING | 0
2022 | nonsummer | LHILLS_6_SOLAR1 | PLANT_TROUBLE | 206.6667
2022 | nonsummer | LHILLS_6_SOLAR1 | TRANSMISSION_INDUCED | 200
2022 | nonsummer | LITLRK_6_GBCSR1 | PLANT_TROUBLE | 16.25
2022 | nonsummer | LITLRK_6_GBCSR1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | LITLRK_6_SOLAR1 | METERING_TELEMETRY | 0
2022 | nonsummer | LITLRK_6_SOLAR1 | PLANT_MAINTENANCE | 7.875
2022 | nonsummer | LITLRK_6_SOLAR1 | PLANT_TROUBLE | 1995
2022 | nonsummer | LITLRK_6_SOLAR2 | METERING_TELEMETRY | 0
2022 | nonsummer | LITLRK_6_SOLAR2 | PLANT_MAINTENANCE | 0
2022 | nonsummer | LITLRK_6_SOLAR2 | PLANT_TROUBLE | 260
2022 | nonsummer | LITLRK_6_SOLAR2 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | LITLRK_6_SOLAR4 | PLANT_MAINTENANCE | 0
2022 | nonsummer | LIVOAK_1_UNIT 1 | AMBIENT_DUE_TO_TEMP | 5635.4
2022 | nonsummer | LIVOAK_1_UNIT 1 | PLANT_TROUBLE | 389.7233
2022 | nonsummer | LIVOAK_1_UNIT 1 | UNIT_TESTING | 24.3833
2022 | nonsummer | LMBEPK_2_UNITA1 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | LMBEPK_2_UNITA1 | PLANT_MAINTENANCE | 84.3333
2022 | nonsummer | LMBEPK_2_UNITA1 | PLANT_TROUBLE | 1785.4
2022 | nonsummer | LMBEPK_2_UNITA1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | LMBEPK_2_UNITA2 | AMBIENT_DUE_TO_TEMP | 22.78
2022 | nonsummer | LMBEPK_2_UNITA2 | PLANT_MAINTENANCE | 0
2022 | nonsummer | LMBEPK_2_UNITA2 | PLANT_TROUBLE | 519.6333
2022 | nonsummer | LMBEPK_2_UNITA2 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | LMBEPK_2_UNITA3 | AMBIENT_DUE_TO_TEMP | 18.3125
2022 | nonsummer | LMBEPK_2_UNITA3 | PLANT_TROUBLE | 763.1058
2022 | nonsummer | LMBEPK_2_UNITA3 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | LMEC_1_PL1X3 | AMBIENT_DUE_TO_TEMP | 15067.15
2022 | nonsummer | LMEC_1_PL1X3 | PLANT_MAINTENANCE | 2921.1667
2022 | nonsummer | LMEC_1_PL1X3 | PLANT_TROUBLE | 30461.4667
2022 | nonsummer | LNCSTR_6_SOLAR2 | METERING_TELEMETRY | 0
2022 | nonsummer | LOCKFD_1_BEARCK | PLANT_MAINTENANCE | 0
2022 | nonsummer | LOCKFD_1_KSOLAR | PLANT_MAINTENANCE | 0
2022 | nonsummer | LODI25_2_UNIT 1 | AMBIENT_DUE_TO_TEMP | 2260
2022 | nonsummer | LODI25_2_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | LODI25_2_UNIT 1 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | LODI25_2_UNIT 1 | METERING_TELEMETRY | 48.3
2022 | nonsummer | LODI25_2_UNIT 1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | LODI25_2_UNIT 1 | PLANT_TROUBLE | 113.9167
2022 | nonsummer | LODIEC_2_PL1X2 | AMBIENT_DUE_TO_TEMP | 11657.1
2022 | nonsummer | LODIEC_2_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | LODIEC_2_PL1X2 | ENVIRONMENTAL_RESTRICTIONS | 13.75
2022 | nonsummer | LODIEC_2_PL1X2 | PLANT_MAINTENANCE | 0
2022 | nonsummer | LODIEC_2_PL1X2 | PLANT_TROUBLE | 1989.28
2022 | nonsummer | LODIEC_2_PL1X2 | UNIT_TESTING | 0
2022 | nonsummer | LOTUS_6_LSFSR1 | PLANT_MAINTENANCE | 149.1667
2022 | nonsummer | LOTUS_6_LSFSR1 | PLANT_TROUBLE | 304.1667
2022 | nonsummer | LOWGAP_7_QFUNTS | AMBIENT_NOT_DUE_TO_TEMP | 1.01
2022 | nonsummer | LOWGAP_7_QFUNTS | ENVIRONMENTAL_RESTRICTIONS | 387.85
2022 | nonsummer | LOWGAP_7_QFUNTS | METERING_TELEMETRY | 40.5
2022 | nonsummer | LOWGAP_7_QFUNTS | PLANT_MAINTENANCE | 0
2022 | nonsummer | LOWGAP_7_QFUNTS | PLANT_TROUBLE | 4.185
2022 | nonsummer | LOWGAP_7_QFUNTS | TRANSMISSION_INDUCED | 1.35
2022 | nonsummer | LTBEAR_1_LB3SR3 | PLANT_MAINTENANCE | 536
2022 | nonsummer | LTBEAR_1_LB3SR3 | PLANT_TROUBLE | 0
2022 | nonsummer | LTBEAR_1_LB4SR4 | PLANT_MAINTENANCE | 1198.3333
2022 | nonsummer | LTBEAR_1_LB4SR4 | PLANT_TROUBLE | 755.8333
2022 | nonsummer | LTBEAR_1_LB4SR5 | PLANT_MAINTENANCE | 1518.8833
2022 | nonsummer | LTBEAR_1_LB4SR5 | PLANT_TROUBLE | 250
2022 | nonsummer | LTBERA_1_LB1SR1 | PLANT_MAINTENANCE | 340
2022 | nonsummer | LTBERA_1_LB1SR1 | PLANT_TROUBLE | 0
2022 | nonsummer | MAGNLA_6_ANAHEIM | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | MAGNLA_6_ANAHEIM | PLANT_MAINTENANCE | 1464
2022 | nonsummer | MAGNLA_6_ANAHEIM | PLANT_TROUBLE | 1129.7833
2022 | nonsummer | MAGNLA_6_ANAHEIM | TRANSMISSION_INDUCED | 17
2022 | nonsummer | MAGNLA_6_ANAHEIM | UNIT_TESTING | 0
2022 | nonsummer | MAGNLA_6_CERRITOS | PLANT_MAINTENANCE | 588
2022 | nonsummer | MAGNLA_6_CERRITOS | PLANT_TROUBLE | 60
2022 | nonsummer | MAGNLA_6_CERRITOS | UNIT_TESTING | 6
2022 | nonsummer | MAGNLA_6_COLTON | PLANT_MAINTENANCE | 133
2022 | nonsummer | MAGNLA_6_COLTON | PLANT_TROUBLE | 60
2022 | nonsummer | MAGNLA_6_COLTON | UNIT_TESTING | 6
2022 | nonsummer | MAGNLA_6_PASADENA | ICCP | 140
2022 | nonsummer | MAGNLA_6_PASADENA | PLANT_MAINTENANCE | 1070
2022 | nonsummer | MAGNLA_6_PASADENA | PLANT_TROUBLE | 184
2022 | nonsummer | MAGNLA_6_PASADENA | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2022 | nonsummer | MAGNLA_6_PASADENA | TRANSMISSION_INDUCED | 0
2022 | nonsummer | MAGUND_1_BKISR1 | PLANT_TROUBLE | 5
2022 | nonsummer | MAGUND_1_BKISR1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | MAGUND_1_BKSSR2 | PLANT_TROUBLE | 449.275
2022 | nonsummer | MAGUND_1_BKSSR2 | TRANSMISSION_INDUCED | 14.35
2022 | nonsummer | MALAGA_1_PL1X2 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | MALAGA_1_PL1X2 | PLANT_MAINTENANCE | 0
2022 | nonsummer | MALAGA_1_PL1X2 | PLANT_TROUBLE | 148
2022 | nonsummer | MALAGA_1_PL1X2 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | MALCHQ_7_UNIT 1 | TRANSMISSION_INDUCED | 4923.75
2022 | nonsummer | MALIN_5_GCPDDYN | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | MALIN_5_GCPDDYN | PLANT_TROUBLE | 0
2022 | nonsummer | MANTEC_1_ML1SR1 | PLANT_TROUBLE | 0
2022 | nonsummer | MANTEC_1_ML1SR1 | TRANSMISSION_INDUCED | 1.6167
2022 | nonsummer | MANZNA_2_WIND | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | MANZNA_2_WIND | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | MANZNA_2_WIND | METERING_TELEMETRY | 0
2022 | nonsummer | MANZNA_2_WIND | PLANT_MAINTENANCE | 799.75
2022 | nonsummer | MANZNA_2_WIND | PLANT_TROUBLE | 4486.2417
2022 | nonsummer | MARCPW_6_SOLAR1 | PLANT_MAINTENANCE | 60
2022 | nonsummer | MARCPW_6_SOLAR1 | PLANT_TROUBLE | 2142
2022 | nonsummer | MARCPW_6_SOLAR1 | TRANSMISSION_INDUCED | 2274.6667
2022 | nonsummer | MARTIN_1_SUNSET | PLANT_MAINTENANCE | 0
2022 | nonsummer | MARTIN_1_SUNSET | TRANSMISSION_INDUCED | 0
2022 | nonsummer | MCARTH_6_FRIVRB | METERING_TELEMETRY | 7.5
2022 | nonsummer | MCARTH_6_FRIVRB | PLANT_MAINTENANCE | 0
2022 | nonsummer | MCARTH_6_FRIVRB | PLANT_TROUBLE | 7.5
2022 | nonsummer | MCARTH_6_FRIVRB | TRANSMISSION_INDUCED | 1.125
2022 | nonsummer | MCCALL_1_QF | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | MCCALL_1_QF | PLANT_MAINTENANCE | 26
2022 | nonsummer | MCCALL_1_QF | PLANT_TROUBLE | 2.08
2022 | nonsummer | MCSWAN_6_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 200
2022 | nonsummer | MCSWAN_6_UNITS | PLANT_MAINTENANCE | 4736.35
2022 | nonsummer | MDFKRL_2_PROJCT | AMBIENT_NOT_DUE_TO_TEMP | 2731.2667
2022 | nonsummer | MDFKRL_2_PROJCT | PLANT_MAINTENANCE | 3780
2022 | nonsummer | MDFKRL_2_PROJCT | PLANT_TROUBLE | 7400.5
2022 | nonsummer | MDFKRL_2_PROJCT | TRANSMISSION_INDUCED | 58771.2
2022 | nonsummer | MENBIO_6_RENEW1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | MENBIO_6_RENEW1 | METERING_TELEMETRY | 25
2022 | nonsummer | MENBIO_6_RENEW1 | PLANT_MAINTENANCE | 199.2333
2022 | nonsummer | MENBIO_6_RENEW1 | TRANSMISSION_INDUCED | 123.1667
2022 | nonsummer | MERCED_1_SOLAR1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | MERCED_1_SOLAR1 | PLANT_TROUBLE | 0
2022 | nonsummer | MERCED_1_SOLAR2 | PLANT_MAINTENANCE | 0
2022 | nonsummer | MERCED_1_SOLAR2 | PLANT_TROUBLE | 0
2022 | nonsummer | MERCFL_6_UNIT | PLANT_MAINTENANCE | 983.5
2022 | nonsummer | MERCFL_6_UNIT | PLANT_TROUBLE | 0
2022 | nonsummer | METEC_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 6623.0167
2022 | nonsummer | METEC_2_PL1X3 | PLANT_MAINTENANCE | 53509.9
2022 | nonsummer | METEC_2_PL1X3 | PLANT_TROUBLE | 64251.6967
2022 | nonsummer | MIDWD_2_WIND2 | METERING_TELEMETRY | 178.5
2022 | nonsummer | MIDWD_2_WIND2 | PLANT_MAINTENANCE | 0
2022 | nonsummer | MIDWD_2_WIND2 | TRANSMISSION_INDUCED | 6
2022 | nonsummer | MIDWD_7_CORAMB | TRANSMISSION_INDUCED | 0
2022 | nonsummer | MIDWY3_2_MDSSR1 | PLANT_MAINTENANCE | 100
2022 | nonsummer | MIDWY3_2_MDSSR1 | PLANT_TROUBLE | 72.06
2022 | nonsummer | MIDWY3_2_MDSSR1 | TRANSITIONAL_LIMITATION | 70
2022 | nonsummer | MIDWY3_2_MDSSR1 | TRANSMISSION_INDUCED | 63
2022 | nonsummer | MIDWYS_2_MIDSL1 | PLANT_MAINTENANCE | 261.9167
2022 | nonsummer | MIDWYS_2_MIDSL1 | PLANT_TROUBLE | 0
2022 | nonsummer | MILFRD_7_PASADENA | PLANT_TROUBLE | 38.1667
2022 | nonsummer | MILFRD_7_PASADENA | TRANSMISSION_INDUCED | 33
2022 | nonsummer | MIRLOM_2_CORONA | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | MIRLOM_2_CORONA | PLANT_TROUBLE | 14.2025
2022 | nonsummer | MIRLOM_2_CORONA | TRANSMISSION_INDUCED | 0
2022 | nonsummer | MIRLOM_2_MLBBTA | METERING_TELEMETRY | 75.8333
2022 | nonsummer | MIRLOM_2_MLBBTA | PLANT_MAINTENANCE | 0
2022 | nonsummer | MIRLOM_2_MLBBTA | PLANT_TROUBLE | 0
2022 | nonsummer | MIRLOM_2_MLBBTB | METERING_TELEMETRY | 0
2022 | nonsummer | MIRLOM_2_MLBBTB | PLANT_MAINTENANCE | 0
2022 | nonsummer | MIRLOM_2_MLBBTB | PLANT_TROUBLE | 322
2022 | nonsummer | MIRLOM_2_MLBBTB | TRANSMISSION_INDUCED | 0
2022 | nonsummer | MIRLOM_2_ONTARO | PLANT_TROUBLE | 1006.975
2022 | nonsummer | MIRLOM_2_TEMESC | PLANT_MAINTENANCE | 0
2022 | nonsummer | MIRLOM_2_TEMESC | TRANSMISSION_INDUCED | 85.5
2022 | nonsummer | MIRLOM_6_PEAKER | AMBIENT_DUE_TO_TEMP | 719.04
2022 | nonsummer | MIRLOM_6_PEAKER | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | MIRLOM_6_PEAKER | PLANT_MAINTENANCE | 0
2022 | nonsummer | MIRLOM_6_PEAKER | PLANT_TROUBLE | 0
2022 | nonsummer | MIRLOM_6_PEAKER | UNIT_TESTING | 0
2022 | nonsummer | MIRLOM_7_MWDLKM | PLANT_TROUBLE | 72.1667
2022 | nonsummer | MIRLOM_7_MWDLKM | TRANSMISSION_INDUCED | 0
2022 | nonsummer | MKTRCK_1_UNIT 1 | AMBIENT_DUE_TO_TEMP | 2757.59
2022 | nonsummer | MKTRCK_1_UNIT 1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | MKTRCK_1_UNIT 1 | PLANT_TROUBLE | 1053.59
2022 | nonsummer | MKTRCK_1_UNIT 1 | TRANSMISSION_INDUCED | 94.98
2022 | nonsummer | MKTRCK_1_UNIT 1 | UNIT_TESTING | 9.96
2022 | nonsummer | MNDALY_6_MCGRTH | AMBIENT_DUE_TO_TEMP | 1287.56
2022 | nonsummer | MNDALY_6_MCGRTH | AMBIENT_DUE_TO_TEMP | 246.62
2022 | nonsummer | MNDALY_6_MCGRTH | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | MNDALY_6_MCGRTH | METERING_TELEMETRY | 0
2022 | nonsummer | MNDALY_6_MCGRTH | PLANT_TROUBLE | 271.026
2022 | nonsummer | MNDALY_6_MCGRTH | TRANSMISSION_INDUCED | 14.16
2022 | nonsummer | MNDALY_6_MCGRTH | UNIT_TESTING | 0
2022 | nonsummer | MNDOTA_1_SOLAR1 | METERING_TELEMETRY | 0
2022 | nonsummer | MNDOTA_1_SOLAR1 | PLANT_MAINTENANCE | 383
2022 | nonsummer | MNDOTA_1_SOLAR1 | PLANT_TROUBLE | 239.0333
2022 | nonsummer | MNDOTA_1_SOLAR2 | PLANT_TROUBLE | 552.5833
2022 | nonsummer | MOJAVE_1_SIPHON | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 71.8
2022 | nonsummer | MOJAVE_1_SIPHON | PLANT_TROUBLE | 117.0567
2022 | nonsummer | MOJAVW_2_SOLAR | PLANT_MAINTENANCE | 6.3
2022 | nonsummer | MOJAVW_2_SOLAR | PLANT_TROUBLE | 228.6667
2022 | nonsummer | MONLTH_6_BATTRY | PLANT_TROUBLE | 5992.5
2022 | nonsummer | MONTPH_7_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 3351
2022 | nonsummer | MONTPH_7_UNITS | PLANT_MAINTENANCE | 3779
2022 | nonsummer | MONTPH_7_UNITS | TRANSMISSION_INDUCED | 18.6
2022 | nonsummer | MOORPK_2_ACOBT1 | METERING_TELEMETRY | 9.75
2022 | nonsummer | MOORPK_2_ACOBT1 | PLANT_MAINTENANCE | 50.57
2022 | nonsummer | MOORPK_2_ACOBT1 | PLANT_TROUBLE | 121.4692
2022 | nonsummer | MOORPK_2_ACOBT1 | RTU_RIG | 0
2022 | nonsummer | MOORPK_2_ACOBT1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | MOORPK_2_ACOBT1 | UNIT_TESTING | 0
2022 | nonsummer | MOORPK_2_CALABS | PLANT_MAINTENANCE | 155.225
2022 | nonsummer | MOORPK_2_CALABS | PLANT_TROUBLE | 115.126
2022 | nonsummer | MOORPK_2_CALABS | TRANSMISSION_INDUCED | 0
2022 | nonsummer | MORWD_6_QF | PLANT_MAINTENANCE | 24.6
2022 | nonsummer | MORWD_6_QF | PLANT_TROUBLE | 22.5
2022 | nonsummer | MORWD_6_QF | TRANSMISSION_INDUCED | 29.0995
2022 | nonsummer | MOSSLD_2_PSP1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2022 | nonsummer | MOSSLD_2_PSP1 | AMBIENT_DUE_TO_TEMP | 490.25
2022 | nonsummer | MOSSLD_2_PSP1 | ENVIRONMENTAL_RESTRICTIONS | 528.25
2022 | nonsummer | MOSSLD_2_PSP1 | PLANT_MAINTENANCE | 3900
2022 | nonsummer | MOSSLD_2_PSP1 | PLANT_TROUBLE | 16700.3333
2022 | nonsummer | MOSSLD_2_PSP1 | TRANSMISSION_INDUCED | 1752.5
2022 | nonsummer | MOSSLD_2_PSP1 | UNIT_TESTING | 0
2022 | nonsummer | MOSSLD_2_PSP2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2022 | nonsummer | MOSSLD_2_PSP2 | AMBIENT_DUE_TO_TEMP | 178.6833
2022 | nonsummer | MOSSLD_2_PSP2 | ENVIRONMENTAL_RESTRICTIONS | 98.9167
2022 | nonsummer | MOSSLD_2_PSP2 | PLANT_MAINTENANCE | 2550
2022 | nonsummer | MOSSLD_2_PSP2 | PLANT_TROUBLE | 11520
2022 | nonsummer | MOSSLD_2_PSP2 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | MOSSLD_2_PSP2 | UNIT_TESTING | 0
2022 | nonsummer | MRCHNT_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 23965.7137
2022 | nonsummer | MRCHNT_2_PL1X3 | PLANT_TROUBLE | 1667.0833
2022 | nonsummer | MRCHNT_2_PL1X3 | TRANSMISSION_INDUCED | 989.16
2022 | nonsummer | MRGT_6_MEF2 | PLANT_TROUBLE | 387.9333
2022 | nonsummer | MRGT_6_MEF2 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | MRGT_6_MMAREF | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | MRGT_6_MMAREF | PLANT_MAINTENANCE | 120
2022 | nonsummer | MRGT_6_MMAREF | PLANT_TROUBLE | 288.75
2022 | nonsummer | MRGT_6_MMAREF | TRANSMISSION_INDUCED | 0
2022 | nonsummer | MRGT_6_TGEBT1 | AMBIENT_NOT_DUE_TO_TEMP | 74
2022 | nonsummer | MRGT_6_TGEBT1 | METERING_TELEMETRY | 0
2022 | nonsummer | MRGT_6_TGEBT1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | MRGT_6_TGEBT1 | PLANT_TROUBLE | 8626.7083
2022 | nonsummer | MRGT_6_TGEBT1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | MRLSDS_6_SOLAR1 | METERING_TELEMETRY | 0
2022 | nonsummer | MRLSDS_6_SOLAR1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | MRLSDS_6_SOLAR1 | PLANT_TROUBLE | 363.25
2022 | nonsummer | MRLSDS_6_SOLAR1 | TRANSMISSION_INDUCED | 150
2022 | nonsummer | MRLSDS_6_SOLAR1 | UNIT_TESTING | 0
2022 | nonsummer | MSHGTS_6_MMARLF | PLANT_MAINTENANCE | 21.6667
2022 | nonsummer | MSOLAR_2_SOLAR1 | PLANT_MAINTENANCE | 6765
2022 | nonsummer | MSOLAR_2_SOLAR1 | PLANT_TROUBLE | 175
2022 | nonsummer | MSOLAR_2_SOLAR2 | METERING_TELEMETRY | 0
2022 | nonsummer | MSOLAR_2_SOLAR2 | PLANT_MAINTENANCE | 1789.3775
2022 | nonsummer | MSOLAR_2_SOLAR2 | PLANT_TROUBLE | 8.357
2022 | nonsummer | MSOLAR_2_SOLAR2 | TRANSMISSION_INDUCED | 554.455
2022 | nonsummer | MSOLAR_2_SOLAR3 | PLANT_MAINTENANCE | 6688
2022 | nonsummer | MSOLAR_2_SOLAR3 | PLANT_TROUBLE | 8.5
2022 | nonsummer | MSTANG_2_MTGBT1 | METERING_TELEMETRY | 0
2022 | nonsummer | MSTANG_2_MTGBT1 | PLANT_MAINTENANCE | 33.5
2022 | nonsummer | MSTANG_2_MTGBT1 | PLANT_TROUBLE | 1898
2022 | nonsummer | MSTANG_2_MTGBT1 | UNIT_TESTING | 0
2022 | nonsummer | MSTANG_2_SOLAR | METERING_TELEMETRY | 8.16
2022 | nonsummer | MSTANG_2_SOLAR | PLANT_MAINTENANCE | 4280.908
2022 | nonsummer | MSTANG_2_SOLAR | UNIT_TESTING | 0
2022 | nonsummer | MSTANG_2_SOLAR3 | METERING_TELEMETRY | 134.75
2022 | nonsummer | MSTANG_2_SOLAR3 | PLANT_MAINTENANCE | 2518.6
2022 | nonsummer | MSTANG_2_SOLAR3 | PLANT_TROUBLE | 1155
2022 | nonsummer | MSTANG_2_SOLAR3 | UNIT_TESTING | 0
2022 | nonsummer | MSTANG_2_SOLAR4 | METERING_TELEMETRY | 0
2022 | nonsummer | MSTANG_2_SOLAR4 | PLANT_MAINTENANCE | 507.25
2022 | nonsummer | MSTANG_2_SOLAR4 | PLANT_TROUBLE | 0
2022 | nonsummer | MSTANG_2_SOLAR4 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | MSTANG_2_SOLAR4 | UNIT_TESTING | 0
2022 | nonsummer | MTNPOS_1_UNIT | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 3.3267
2022 | nonsummer | MTNPOS_1_UNIT | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | MTNPOS_1_UNIT | METERING_TELEMETRY | 50.0747
2022 | nonsummer | MTNPOS_1_UNIT | PLANT_MAINTENANCE | 3951.65
2022 | nonsummer | MTNPOS_1_UNIT | PLANT_TROUBLE | 12704.8167
2022 | nonsummer | MTNPOS_1_UNIT | UNIT_TESTING | 63.04
2022 | nonsummer | MTWIND_1_MVPWD1 | NEW_GENERATOR_TEST_ENERGY | 0
2022 | nonsummer | MTWIND_1_MVPWD1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | MTWIND_1_MVPWD1 | TRANSMISSION_INDUCED | 23.6
2022 | nonsummer | MTWIND_1_UNIT 3 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | MTWIND_1_UNIT 3 | AMBIENT_NOT_DUE_TO_TEMP | 62.2
2022 | nonsummer | MTWIND_1_UNIT 3 | ENVIRONMENTAL_RESTRICTIONS | 150.8767
2022 | nonsummer | MTWIND_1_UNIT 3 | PLANT_TROUBLE | 782.7987
2022 | nonsummer | MTWIND_1_UNIT 3 | TRANSMISSION_INDUCED | 89.105
2022 | nonsummer | MURRAY_6_UNIT | PLANT_MAINTENANCE | 37.08
2022 | nonsummer | MURRAY_6_UNIT | PLANT_TROUBLE | 20.6
2022 | nonsummer | NAROW1_2_UNIT | ENVIRONMENTAL_RESTRICTIONS | 4345.7267
2022 | nonsummer | NAROW1_2_UNIT | PLANT_MAINTENANCE | 4.2
2022 | nonsummer | NAROW1_2_UNIT | PLANT_TROUBLE | 519.4833
2022 | nonsummer | NAROW1_2_UNIT | TRANSMISSION_INDUCED | 98
2022 | nonsummer | NAROW2_2_UNIT | ENVIRONMENTAL_RESTRICTIONS | 53959.915
2022 | nonsummer | NAROW2_2_UNIT | PLANT_MAINTENANCE | 10
2022 | nonsummer | NAROW2_2_UNIT | PLANT_TROUBLE | 9.9
2022 | nonsummer | NAROW2_2_UNIT | TRANSMISSION_INDUCED | 0
2022 | nonsummer | NAVYII_2_UNITS | PLANT_TROUBLE | 1307
2022 | nonsummer | NAVYII_2_UNITS | TRANSMISSION_INDUCED | 0
2022 | nonsummer | NCPA_7_GP1UN1 | PLANT_MAINTENANCE | 618.72
2022 | nonsummer | NCPA_7_GP1UN1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | NCPA_7_GP1UN2 | PLANT_MAINTENANCE | 306.78
2022 | nonsummer | NCPA_7_GP1UN2 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | NCPA_7_GP2UN3 | AMBIENT_NOT_DUE_TO_TEMP | 44753.1
2022 | nonsummer | NCPA_7_GP2UN4 | PLANT_MAINTENANCE | 0
2022 | nonsummer | NCPA_7_GP2UN4 | PLANT_TROUBLE | 0
2022 | nonsummer | NEENCH_6_SOLAR | PLANT_MAINTENANCE | 64.9
2022 | nonsummer | NEENCH_6_SOLAR | PLANT_TROUBLE | 0
2022 | nonsummer | NGILAA_5_SDGDYN | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 275
2022 | nonsummer | NGILAA_5_SDGDYN | AMBIENT_DUE_TO_TEMP | 2643
2022 | nonsummer | NGILAA_5_SDGDYN | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | NGILAA_5_SDGDYN | PLANT_MAINTENANCE | 0
2022 | nonsummer | NGILAA_5_SDGDYN | PLANT_TROUBLE | 1370
2022 | nonsummer | NGILAA_5_SDGDYN | UNIT_TESTING | 43.8908
2022 | nonsummer | NHOGAN_6_UNITS | PLANT_MAINTENANCE | 370
2022 | nonsummer | NHOGAN_6_UNITS | TRANSMISSION_INDUCED | 20
2022 | nonsummer | NOVATO_6_LNDFL | PLANT_MAINTENANCE | 12
2022 | nonsummer | NOVATO_6_LNDFL | PLANT_TROUBLE | 20
2022 | nonsummer | NOVATO_6_LNDFL | TRANSMISSION_INDUCED | 0
2022 | nonsummer | NWCSTL_7_UNIT 1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 840
2022 | nonsummer | NWCSTL_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 6922.17
2022 | nonsummer | NWCSTL_7_UNIT 1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | NWCSTL_7_UNIT 1 | PLANT_TROUBLE | 135.6
2022 | nonsummer | NWCSTL_7_UNIT 1 | UNIT_TESTING | 1
2022 | nonsummer | NZWIND_2_WDSTR5 | PLANT_MAINTENANCE | 0
2022 | nonsummer | NZWIND_2_WDSTR5 | PLANT_TROUBLE | 94.65
2022 | nonsummer | NZWIND_6_CALWND | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | NZWIND_6_CALWND | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | NZWIND_6_CALWND | PLANT_TROUBLE | 22
2022 | nonsummer | NZWIND_6_CALWND | TRANSMISSION_INDUCED | 26.1
2022 | nonsummer | NZWIND_6_WDSTR | PLANT_MAINTENANCE | 5.025
2022 | nonsummer | NZWIND_6_WDSTR | PLANT_TROUBLE | 18.425
2022 | nonsummer | NZWIND_6_WDSTR2 | PLANT_MAINTENANCE | 6.105
2022 | nonsummer | NZWIND_6_WDSTR2 | PLANT_TROUBLE | 0
2022 | nonsummer | NZWIND_6_WDSTR3 | PLANT_MAINTENANCE | 5.79
2022 | nonsummer | NZWIND_6_WDSTR3 | PLANT_TROUBLE | 27.3417
2022 | nonsummer | NZWIND_6_WDSTR4 | PLANT_MAINTENANCE | 27.08
2022 | nonsummer | NZWIND_6_WDSTR4 | PLANT_TROUBLE | 47.9542
2022 | nonsummer | OAK C_7_UNIT 1 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | OAK C_7_UNIT 1 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | OAK C_7_UNIT 1 | PLANT_MAINTENANCE | 593.1583
2022 | nonsummer | OAK C_7_UNIT 1 | PLANT_TROUBLE | 26826.465
2022 | nonsummer | OAK C_7_UNIT 1 | UNIT_TESTING | 0
2022 | nonsummer | OAK C_7_UNIT 3 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | OAK C_7_UNIT 3 | ENVIRONMENTAL_RESTRICTIONS | 25.5333
2022 | nonsummer | OAK C_7_UNIT 3 | PLANT_MAINTENANCE | 1343.25
2022 | nonsummer | OAK C_7_UNIT 3 | PLANT_TROUBLE | 2305.315
2022 | nonsummer | OAK C_7_UNIT 3 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | OAK C_7_UNIT 3 | UNIT_TESTING | 0
2022 | nonsummer | OAKWD_6_QF | TRANSMISSION_INDUCED | 0
2022 | nonsummer | OASIS_6_CREST | PLANT_TROUBLE | 8.825
2022 | nonsummer | OASIS_6_GBDSR4 | PLANT_TROUBLE | 19.725
2022 | nonsummer | OASIS_6_GBDSR4 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | OASIS_6_LPPSR1 | PLANT_MAINTENANCE | 6.25
2022 | nonsummer | OASIS_6_LPPSR1 | PLANT_TROUBLE | 15
2022 | nonsummer | OASIS_6_SOLAR2 | METERING_TELEMETRY | 0
2022 | nonsummer | OASIS_6_SOLAR2 | PLANT_TROUBLE | 977
2022 | nonsummer | OCTILO_5_WIND | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | OCTILO_5_WIND | PLANT_MAINTENANCE | 0
2022 | nonsummer | OCTILO_5_WIND | PLANT_TROUBLE | 76066.4
2022 | nonsummer | OGROVE_6_PL1X2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 2400
2022 | nonsummer | OGROVE_6_PL1X2 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | OGROVE_6_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | OGROVE_6_PL1X2 | PLANT_MAINTENANCE | 6260
2022 | nonsummer | OGROVE_6_PL1X2 | PLANT_TROUBLE | 0
2022 | nonsummer | OILFLD_7_QFUNTS | AMBIENT_NOT_DUE_TO_TEMP | 3894.5
2022 | nonsummer | OILFLD_7_QFUNTS | PLANT_MAINTENANCE | 0
2022 | nonsummer | OILFLD_7_QFUNTS | PLANT_TROUBLE | 12.75
2022 | nonsummer | OILFLD_7_QFUNTS | TRANSMISSION_INDUCED | 0.8
2022 | nonsummer | OLDRIV_6_CESDBM | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 5.5
2022 | nonsummer | OLDRIV_6_CESDBM | PLANT_MAINTENANCE | 15
2022 | nonsummer | OLDRIV_6_CESDBM | PLANT_TROUBLE | 0
2022 | nonsummer | OLDRIV_6_LKVBM1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 8.5
2022 | nonsummer | OLDRIV_6_LKVBM1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | OLDRIV_6_LKVBM1 | PLANT_TROUBLE | 0
2022 | nonsummer | OLDRV1_6_SOLAR | PLANT_TROUBLE | 440.1667
2022 | nonsummer | OLDRV1_6_SOLAR | TRANSMISSION_INDUCED | 49.6667
2022 | nonsummer | OLINDA_2_COYCRK | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 3302.15
2022 | nonsummer | OLINDA_2_LNDFL2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1534.5
2022 | nonsummer | OLINDA_2_LNDFL2 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | OLINDA_2_LNDFL2 | PLANT_MAINTENANCE | 0
2022 | nonsummer | OLINDA_2_LNDFL2 | PLANT_TROUBLE | 0
2022 | nonsummer | OLINDA_2_LNDFL2 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | OLIVEP_1_SOLAR | PLANT_MAINTENANCE | 40
2022 | nonsummer | OLIVEP_1_SOLAR | PLANT_TROUBLE | 0
2022 | nonsummer | OLIVEP_1_SOLAR | TRANSMISSION_INDUCED | 0
2022 | nonsummer | OLIVEP_1_SOLAR2 | PLANT_TROUBLE | 0
2022 | nonsummer | OLIVEP_1_SOLAR2 | TRANSMISSION_INDUCED | 98.75
2022 | nonsummer | OLSEN_2_UNIT | METERING_TELEMETRY | 0
2022 | nonsummer | OLSEN_2_UNIT | TRANSMISSION_INDUCED | 532.0583
2022 | nonsummer | OMAR_2_UNIT 1 | PLANT_MAINTENANCE | 2625
2022 | nonsummer | OMAR_2_UNIT 1 | PLANT_TROUBLE | 3798.75
2022 | nonsummer | OMAR_2_UNIT 1 | TRANSMISSION_INDUCED | 37.5
2022 | nonsummer | OMAR_2_UNIT 1 | UNIT_TESTING | 0
2022 | nonsummer | OMAR_2_UNIT 2 | PLANT_MAINTENANCE | 2625
2022 | nonsummer | OMAR_2_UNIT 2 | PLANT_TROUBLE | 512.5
2022 | nonsummer | OMAR_2_UNIT 2 | UNIT_TESTING | 0
2022 | nonsummer | OMAR_2_UNIT 3 | PLANT_MAINTENANCE | 5595
2022 | nonsummer | OMAR_2_UNIT 3 | PLANT_TROUBLE | 662.5
2022 | nonsummer | OMAR_2_UNIT 3 | UNIT_TESTING | 0
2022 | nonsummer | OMAR_2_UNIT 4 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | OMAR_2_UNIT 4 | ENVIRONMENTAL_RESTRICTIONS | 1185
2022 | nonsummer | OMAR_2_UNIT 4 | PLANT_MAINTENANCE | 5715
2022 | nonsummer | OMAR_2_UNIT 4 | PLANT_TROUBLE | 6412.5
2022 | nonsummer | OMAR_2_UNIT 4 | TRANSMISSION_INDUCED | 87.5
2022 | nonsummer | OMAR_2_UNIT 4 | UNIT_TESTING | 0
2022 | nonsummer | ONLLPP_6_UNITS | TRANSMISSION_INDUCED | 0
2022 | nonsummer | ORLND_6_HIGHLI | PLANT_TROUBLE | 527.5
2022 | nonsummer | ORMOND_7_UNIT 1 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | ORMOND_7_UNIT 1 | METERING_TELEMETRY | 0
2022 | nonsummer | ORMOND_7_UNIT 1 | PLANT_MAINTENANCE | 9080.5575
2022 | nonsummer | ORMOND_7_UNIT 1 | PLANT_TROUBLE | 19429.37
2022 | nonsummer | ORMOND_7_UNIT 1 | TRANSMISSION_INDUCED | 3706.35
2022 | nonsummer | ORMOND_7_UNIT 2 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | ORMOND_7_UNIT 2 | PLANT_MAINTENANCE | 3750
2022 | nonsummer | ORMOND_7_UNIT 2 | PLANT_TROUBLE | 86250
2022 | nonsummer | ORMOND_7_UNIT 2 | TRANSMISSION_INDUCED | 7500
2022 | nonsummer | OROLOM_1_SOLAR1 | METERING_TELEMETRY | 5.8333
2022 | nonsummer | OROLOM_1_SOLAR1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | OROLOM_1_SOLAR2 | METERING_TELEMETRY | 5.8333
2022 | nonsummer | OROLOM_1_SOLAR2 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | OROVIL_6_UNIT | PLANT_MAINTENANCE | 0
2022 | nonsummer | OROVIL_6_UNIT | PLANT_TROUBLE | 395
2022 | nonsummer | OROVIL_6_UNIT | TRANSMISSION_INDUCED | 5.3083
2022 | nonsummer | OTAY_6_ECVBT1 | TRANSMISSION_INDUCED | 915
2022 | nonsummer | OTAY_6_ECVBT2 | TRANSMISSION_INDUCED | 2078.4
2022 | nonsummer | OTAY_6_PL1X2 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | OTAY_6_PL1X2 | PLANT_MAINTENANCE | 0
2022 | nonsummer | OTAY_6_PL1X2 | PLANT_TROUBLE | 243.3555
2022 | nonsummer | OTAY_6_PL1X2 | UNIT_TESTING | 0
2022 | nonsummer | OTMESA_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 993.2
2022 | nonsummer | OTMESA_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 11346.5833
2022 | nonsummer | OTMESA_2_PL1X3 | PLANT_MAINTENANCE | 0
2022 | nonsummer | OTMESA_2_PL1X3 | PLANT_TROUBLE | 1593
2022 | nonsummer | OTMESA_2_PL1X3 | PLANT_TROUBLE | 19336.6
2022 | nonsummer | OTMESA_2_PL1X3 | UNIT_TESTING | 0
2022 | nonsummer | OXBOW_6_DRUM | PLANT_MAINTENANCE | 145
2022 | nonsummer | OXBOW_6_DRUM | PLANT_TROUBLE | 0
2022 | nonsummer | OXBOW_6_DRUM | TRANSMISSION_INDUCED | 660.7683
2022 | nonsummer | OXMTN_6_LNDFIL | METERING_TELEMETRY | 0
2022 | nonsummer | OXMTN_6_LNDFIL | PLANT_MAINTENANCE | 79.2477
2022 | nonsummer | OXMTN_6_LNDFIL | PLANT_TROUBLE | 149.522
2022 | nonsummer | OXMTN_6_LNDFIL | TRANSMISSION_INDUCED | 385.86
2022 | nonsummer | PACLUM_6_UNIT | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 416
2022 | nonsummer | PACLUM_6_UNIT | PLANT_MAINTENANCE | 19.5
2022 | nonsummer | PACLUM_6_UNIT | PLANT_TROUBLE | 7904.7
2022 | nonsummer | PACLUM_6_UNIT | TRANSMISSION_INDUCED | 382.0667
2022 | nonsummer | PADUA_2_ONTARO | AMBIENT_NOT_DUE_TO_TEMP | 875.76
2022 | nonsummer | PADUA_2_ONTARO | PLANT_TROUBLE | 99.775
2022 | nonsummer | PADUA_2_ONTARO | TRANSMISSION_INDUCED | 46.5
2022 | nonsummer | PADUA_2_SOLAR1 | PLANT_MAINTENANCE | 2.625
2022 | nonsummer | PADUA_6_MWDSDM | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2022 | nonsummer | PAIGES_6_SOLAR | METERING_TELEMETRY | 0
2022 | nonsummer | PAIGES_6_SOLAR | PLANT_MAINTENANCE | 78.6667
2022 | nonsummer | PAIGES_6_SOLAR | PLANT_TROUBLE | 100
2022 | nonsummer | PALALT_7_COBUG | PLANT_TROUBLE | 4747.5
2022 | nonsummer | PALOMR_2_PL1X3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 25688.9
2022 | nonsummer | PALOMR_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | PALOMR_2_PL1X3 | PLANT_MAINTENANCE | 8823.15
2022 | nonsummer | PALOMR_2_PL1X3 | PLANT_TROUBLE | 15843.1583
2022 | nonsummer | PARDEB_6_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 7168.1
2022 | nonsummer | PARDEB_6_UNITS | PLANT_MAINTENANCE | 3260
2022 | nonsummer | PARDEB_6_UNITS | PLANT_TROUBLE | 50
2022 | nonsummer | PARDEB_6_UNITS | TRANSMISSION_INDUCED | 380.175
2022 | nonsummer | PBLOSM_2_SOLAR | PLANT_TROUBLE | 0
2022 | nonsummer | PBLOSM_2_SOLAR | TRANSMISSION_INDUCED | 95
2022 | nonsummer | PEABDY_2_LNDFIL | PLANT_MAINTENANCE | 0
2022 | nonsummer | PEABDY_2_LNDFIL | PLANT_TROUBLE | 16
2022 | nonsummer | PEABDY_2_LNDFIL | TRANSMISSION_INDUCED | 0
2022 | nonsummer | PEABDY_2_LNDFL1 | AMBIENT_DUE_TO_TEMP | 17.2133
2022 | nonsummer | PEABDY_2_LNDFL1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | PEABDY_2_LNDFL1 | PLANT_MAINTENANCE | 58.075
2022 | nonsummer | PEABDY_2_LNDFL1 | PLANT_TROUBLE | 245.8517
2022 | nonsummer | PEABDY_2_LNDFL1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | PEARBL_2_NSPIN | TRANSMISSION_INDUCED | 0
2022 | nonsummer | PEASE_1_TBEBT1 | METERING_TELEMETRY | 0
2022 | nonsummer | PEASE_1_TBEBT1 | PLANT_TROUBLE | 0
2022 | nonsummer | PEORIA_1_SOLAR | PLANT_MAINTENANCE | 0
2022 | nonsummer | PEORIA_1_SOLAR | PLANT_TROUBLE | 4.575
2022 | nonsummer | PGCC_1_PDRP06 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGCC_1_PDRP07 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGCC_1_PDRP09 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGCC_1_PDRP16 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGCC_1_PDRP19 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGCC_1_PDRP20 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGCC_1_PDRP37 | OTHER_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGEB_2_PDRP106 | OTHER_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGEB_2_PDRP12 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGEB_2_PDRP13 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGEB_2_PDRP14 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGEB_2_PDRP15 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGEB_2_PDRP16 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGEB_2_PDRP60 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGEB_2_PDRP62 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGEB_2_PDRP67 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGEB_2_PDRP68 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGEB_2_PDRP69 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGF1_2_PDRP05 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGF1_2_PDRP06 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGF1_2_PDRP102 | OTHER_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGF1_2_PDRP12 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGF1_2_PDRP13 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGF1_2_PDRP14 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGF1_2_PDRP15 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGF1_2_PDRP60 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGF1_2_PDRP61 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGF1_2_PDRP63 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGF1_2_PDRP74 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGF1_2_PDRP75 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGFG_1_PDRP07 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGFG_1_PDRP10 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGFG_1_PDRP20 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGFG_1_PDRP39 | OTHER_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGHB_6_PDRP03 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGHB_6_PDRP11 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGKN_2_PDRP03 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGKN_2_PDRP04 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGKN_2_PDRP05 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGKN_2_PDRP10 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGKN_2_PDRP24 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGKN_2_PDRP45 | OTHER_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGNB_2_PDRP06 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGNB_2_PDRP07 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGNB_2_PDRP08 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGNB_2_PDRP10 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGNB_2_PDRP13 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGNB_2_PDRP19 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGNB_2_PDRP20 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGNB_2_PDRP21 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGNB_2_PDRP25 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGNB_2_PDRP39 | OTHER_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGNC_1_PDRP02 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGNC_1_PDRP09 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGNC_1_PDRP17 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGNP_2_PDRP03 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGNP_2_PDRP04 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGNP_2_PDRP05 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGNP_2_PDRP06 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGNP_2_PDRP07 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGNP_2_PDRP12 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGNP_2_PDRP30 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGNP_2_PDRP31 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGNP_2_PDRP34 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGNP_2_PDRP40 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGNP_2_PDRP41 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGNP_2_PDRP42 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGNP_2_PDRP51 | OTHER_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGP2_2_PDRP09 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGP2_2_PDRP11 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGP2_2_PDRP12 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGP2_2_PDRP35 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGP2_2_PDRP59 | OTHER_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGP2_2_PDRP65 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGSB_1_PDRP100 | OTHER_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGSB_1_PDRP15 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGSB_1_PDRP18 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGSB_1_PDRP19 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGSB_1_PDRP24 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGSB_1_PDRP60 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGSB_1_PDRP64 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGSB_1_PDRP66 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGSB_1_PDRP67 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGSF_2_PDRP13 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGSF_2_PDRP15 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGSF_2_PDRP34 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGSF_2_PDRP35 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGSF_2_PDRP37 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGSF_2_PDRP38 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGSF_2_PDRP46 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGSF_2_PDRP55 | OTHER_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGSI_1_PDRP04 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGSI_1_PDRP05 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGSI_1_PDRP08 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGSI_1_PDRP13 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGSI_1_PDRP14 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGSI_1_PDRP18 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGSI_1_PDRP48 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGSI_1_PDRP50 | OTHER_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGST_2_PDRP02 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGST_2_PDRP04 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGST_2_PDRP05 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGST_2_PDRP06 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGST_2_PDRP24 | OTHER_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGST_2_PDRP39 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGZP_2_PDRP01 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGZP_2_PDRP03 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGZP_2_PDRP04 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGZP_2_PDRP05 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGZP_2_PDRP13 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGZP_2_PDRP24 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGZP_2_PDRP34 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGZP_2_PDRP35 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | PGZP_2_PDRP47 | OTHER_USE_LIMIT_REACHED | 0
2022 | nonsummer | PHOENX_1_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 20
2022 | nonsummer | PHOENX_1_UNIT | PLANT_TROUBLE | 12.6333
2022 | nonsummer | PHOENX_1_UNIT | TRANSMISSION_INDUCED | 38.6667
2022 | nonsummer | PINFLT_7_UNITS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 112827.5
2022 | nonsummer | PINFLT_7_UNITS | AMBIENT_DUE_TO_TEMP | 26889.3
2022 | nonsummer | PINFLT_7_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | PINFLT_7_UNITS | METERING_TELEMETRY | 0
2022 | nonsummer | PINFLT_7_UNITS | PLANT_MAINTENANCE | 992.55
2022 | nonsummer | PIOPIC_2_CTG1 | AMBIENT_DUE_TO_TEMP | 2530.08
2022 | nonsummer | PIOPIC_2_CTG1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | PIOPIC_2_CTG1 | PLANT_TROUBLE | 8943.866
2022 | nonsummer | PIOPIC_2_CTG1 | TRANSMISSION_INDUCED | 111.3
2022 | nonsummer | PIOPIC_2_CTG2 | AMBIENT_DUE_TO_TEMP | 1331.24
2022 | nonsummer | PIOPIC_2_CTG2 | PLANT_MAINTENANCE | 0
2022 | nonsummer | PIOPIC_2_CTG2 | PLANT_TROUBLE | 20.042
2022 | nonsummer | PIOPIC_2_CTG2 | TRANSMISSION_INDUCED | 112.7
2022 | nonsummer | PIOPIC_2_CTG3 | AMBIENT_DUE_TO_TEMP | 1205.04
2022 | nonsummer | PIOPIC_2_CTG3 | PLANT_TROUBLE | 0
2022 | nonsummer | PIOPIC_2_CTG3 | TRANSMISSION_INDUCED | 112
2022 | nonsummer | PIT1_6_FRIVRA | METERING_TELEMETRY | 7.5
2022 | nonsummer | PIT1_6_FRIVRA | PLANT_MAINTENANCE | 5.125
2022 | nonsummer | PIT1_6_FRIVRA | PLANT_TROUBLE | 12
2022 | nonsummer | PIT1_6_FRIVRA | TRANSMISSION_INDUCED | 0
2022 | nonsummer | PIT1_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | PIT1_7_UNIT 1 | PLANT_MAINTENANCE | 2560
2022 | nonsummer | PIT1_7_UNIT 1 | PLANT_TROUBLE | 8800
2022 | nonsummer | PIT1_7_UNIT 1 | TRANSMISSION_INDUCED | 16640
2022 | nonsummer | PIT1_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 72
2022 | nonsummer | PIT1_7_UNIT 2 | PLANT_TROUBLE | 0
2022 | nonsummer | PIT1_7_UNIT 2 | TRANSMISSION_INDUCED | 18810.6667
2022 | nonsummer | PIT3_7_PL1X3 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | PIT3_7_PL1X3 | AMBIENT_NOT_DUE_TO_TEMP | 118.0067
2022 | nonsummer | PIT3_7_PL1X3 | PLANT_MAINTENANCE | 21180
2022 | nonsummer | PIT3_7_PL1X3 | PLANT_TROUBLE | 0
2022 | nonsummer | PIT3_7_PL1X3 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | PIT4_7_PL1X2 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | PIT4_7_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 420.9833
2022 | nonsummer | PIT4_7_PL1X2 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | PIT4_7_PL1X2 | PLANT_TROUBLE | 1105.2
2022 | nonsummer | PIT4_7_PL1X2 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | PIT5_7_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 753.8833
2022 | nonsummer | PIT5_7_PL1X2 | UNIT_TESTING | 0
2022 | nonsummer | PIT5_7_PL3X4 | AMBIENT_NOT_DUE_TO_TEMP | 130.6667
2022 | nonsummer | PIT5_7_PL3X4 | PLANT_MAINTENANCE | 19454.5
2022 | nonsummer | PIT5_7_PL3X4 | PLANT_TROUBLE | 0
2022 | nonsummer | PIT5_7_PL3X4 | UNIT_SUPPORTING_STARTUP | 359.25
2022 | nonsummer | PIT5_7_PL3X4 | UNIT_TESTING | 0
2022 | nonsummer | PIT6_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 1481.987
2022 | nonsummer | PIT6_7_UNIT 1 | TRANSMISSION_INDUCED | 585
2022 | nonsummer | PIT6_7_UNIT 1 | UNIT_TESTING | 43.804
2022 | nonsummer | PIT6_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 2453.225
2022 | nonsummer | PIT6_7_UNIT 2 | PLANT_TROUBLE | 147.032
2022 | nonsummer | PIT6_7_UNIT 2 | TRANSMISSION_INDUCED | 600
2022 | nonsummer | PIT6_7_UNIT 2 | UNIT_TESTING | 43.804
2022 | nonsummer | PIT7_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 2026.474
2022 | nonsummer | PIT7_7_UNIT 1 | METERING_TELEMETRY | 0
2022 | nonsummer | PIT7_7_UNIT 1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | PIT7_7_UNIT 1 | PLANT_TROUBLE | 0
2022 | nonsummer | PIT7_7_UNIT 1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | PIT7_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 214.6647
2022 | nonsummer | PIT7_7_UNIT 2 | METERING_TELEMETRY | 0
2022 | nonsummer | PIT7_7_UNIT 2 | PLANT_MAINTENANCE | 24570
2022 | nonsummer | PIT7_7_UNIT 2 | PLANT_TROUBLE | 106.98
2022 | nonsummer | PIT7_7_UNIT 2 | RTU_RIG | 0
2022 | nonsummer | PIUTE_6_GNBSR1 | PLANT_MAINTENANCE | 7.5
2022 | nonsummer | PIUTE_6_GNBSR1 | PLANT_TROUBLE | 165
2022 | nonsummer | PIUTE_6_GNBSR1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | PLACVL_1_CHILIB | PLANT_MAINTENANCE | 16.68
2022 | nonsummer | PLACVL_1_CHILIB | PLANT_TROUBLE | 0
2022 | nonsummer | PLACVL_1_CHILIB | TRANSMISSION_INDUCED | 58.38
2022 | nonsummer | PLACVL_1_RCKCRE | TRANSMISSION_INDUCED | 16.5833
2022 | nonsummer | PLAINV_6_BSOLAR | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | PLAINV_6_BSOLAR | PLANT_MAINTENANCE | 54
2022 | nonsummer | PLAINV_6_BSOLAR | PLANT_TROUBLE | 1249.7
2022 | nonsummer | PLAINV_6_DSOLAR | PLANT_MAINTENANCE | 0
2022 | nonsummer | PLAINV_6_DSOLAR | PLANT_TROUBLE | 6
2022 | nonsummer | PLAINV_6_NLRSR1 | PLANT_MAINTENANCE | 84.45
2022 | nonsummer | PLAINV_6_NLRSR1 | PLANT_TROUBLE | 1592.2083
2022 | nonsummer | PLAINV_6_SOLAR3 | PLANT_MAINTENANCE | 0
2022 | nonsummer | PLAINV_6_SOLAR3 | PLANT_TROUBLE | 3091.8833
2022 | nonsummer | PLAINV_6_SOLAR3 | UNIT_TESTING | 0
2022 | nonsummer | PLAINV_6_SOLARC | PLANT_MAINTENANCE | 50
2022 | nonsummer | PLAINV_6_SOLARC | PLANT_TROUBLE | 45.9817
2022 | nonsummer | PLMSSR_6_HISIER | PLANT_MAINTENANCE | 301.706
2022 | nonsummer | PLMSSR_6_HISIER | PLANT_TROUBLE | 203.8833
2022 | nonsummer | PLMSSR_6_HISIER | TRANSMISSION_INDUCED | 15.1
2022 | nonsummer | PLSNTG_7_LNCLND | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 48.202
2022 | nonsummer | PLSNTG_7_LNCLND | PLANT_TROUBLE | 0
2022 | nonsummer | PMDLET_6_SOLAR1 | METERING_TELEMETRY | 0
2022 | nonsummer | PMDLET_6_SOLAR1 | PLANT_MAINTENANCE | 7.9
2022 | nonsummer | PMDLET_6_SOLAR1 | PLANT_TROUBLE | 181.2667
2022 | nonsummer | PMDLET_6_SOLAR1 | TRANSMISSION_INDUCED | 71.6667
2022 | nonsummer | PMPJCK_1_RB2SLR | PLANT_MAINTENANCE | 80
2022 | nonsummer | PMPJCK_1_RB2SLR | TRANSMISSION_INDUCED | 40
2022 | nonsummer | PMPJCK_1_SOLAR1 | PLANT_MAINTENANCE | 71.6667
2022 | nonsummer | PMPJCK_1_SOLAR2 | PLANT_TROUBLE | 0
2022 | nonsummer | PNCHEG_2_PL1X4 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 4967.4
2022 | nonsummer | PNCHEG_2_PL1X4 | AMBIENT_DUE_TO_TEMP | 195.2033
2022 | nonsummer | PNCHEG_2_PL1X4 | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | PNCHEG_2_PL1X4 | PLANT_MAINTENANCE | 933.9
2022 | nonsummer | PNCHEG_2_PL1X4 | PLANT_TROUBLE | 2071.15
2022 | nonsummer | PNCHEG_2_PL1X4 | SHORT_TERM_USE_LIMIT_REACHED | 105858.5
2022 | nonsummer | PNCHEG_2_PL1X4 | TRANSMISSION_INDUCED | 758.2
2022 | nonsummer | PNCHPP_1_PL1X2 | AMBIENT_DUE_TO_TEMP | 2644.27
2022 | nonsummer | PNCHPP_1_PL1X2 | METERING_TELEMETRY | 0
2022 | nonsummer | PNCHPP_1_PL1X2 | PLANT_MAINTENANCE | 0
2022 | nonsummer | PNCHPP_1_PL1X2 | PLANT_TROUBLE | 1554.33
2022 | nonsummer | PNCHPP_1_PL1X2 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | PNCHVS_2_SOLAR | PLANT_MAINTENANCE | 0
2022 | nonsummer | PNCHVS_2_SOLAR | PLANT_TROUBLE | 558.2583
2022 | nonsummer | PNOCHE_1_PL1X2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 149.91
2022 | nonsummer | PNOCHE_1_PL1X2 | AMBIENT_DUE_TO_TEMP | 47.8252
2022 | nonsummer | PNOCHE_1_PL1X2 | PLANT_MAINTENANCE | 499.7
2022 | nonsummer | PNOCHE_1_PL1X2 | PLANT_TROUBLE | 37.4775
2022 | nonsummer | PNOCHE_1_PL1X2 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | PNOCHE_1_PL1X2 | UNIT_TESTING | 0
2022 | nonsummer | PNOCHE_1_UNITA1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 260.05
2022 | nonsummer | PNOCHE_1_UNITA1 | AMBIENT_DUE_TO_TEMP | 52.01
2022 | nonsummer | PNOCHE_1_UNITA1 | PLANT_MAINTENANCE | 615.9833
2022 | nonsummer | PNOCHE_1_UNITA1 | PLANT_TROUBLE | 173.3667
2022 | nonsummer | PNOCHE_1_UNITA1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | PNOCHE_1_UNITA1 | UNIT_TESTING | 0
2022 | nonsummer | POEPH_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 19190.954
2022 | nonsummer | POEPH_7_UNIT 1 | PLANT_MAINTENANCE | 4831.4
2022 | nonsummer | POEPH_7_UNIT 1 | PLANT_TROUBLE | 340
2022 | nonsummer | POEPH_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 17778.1765
2022 | nonsummer | POEPH_7_UNIT 2 | PLANT_TROUBLE | 4844.2167
2022 | nonsummer | POEPH_7_UNIT 2 | TRANSMISSION_INDUCED | 342.5
2022 | nonsummer | POTTER_6_UNITS | PLANT_MAINTENANCE | 8999.1
2022 | nonsummer | POTTER_6_UNITS | PLANT_TROUBLE | 1616
2022 | nonsummer | PRCTVY_1_MIGBT1 | PLANT_MAINTENANCE | 64
2022 | nonsummer | PRCTVY_1_MIGBT1 | PLANT_TROUBLE | 68
2022 | nonsummer | PRCTVY_1_MIGBT1 | RTU_RIG | 2
2022 | nonsummer | PRIMM_2_SOLAR1 | PLANT_MAINTENANCE | 935.548
2022 | nonsummer | PRIMM_2_SOLAR1 | PLANT_TROUBLE | 0
2022 | nonsummer | PUTHCR_1_PCNSB1 | NEW_GENERATOR_TEST_ENERGY | 0
2022 | nonsummer | PUTHCR_1_PCNSB1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | PVERDE_5_SCEDYN | PLANT_MAINTENANCE | 14865
2022 | nonsummer | PWEST_1_UNIT | PLANT_TROUBLE | 2121
2022 | nonsummer | RAMON_2_SCEDYN | AMBIENT_NOT_DUE_TO_TEMP | 52630
2022 | nonsummer | RATSKE_2_NROSR1 | PLANT_MAINTENANCE | 1412.5
2022 | nonsummer | RATSKE_2_NROSR1 | PLANT_TROUBLE | 209.5
2022 | nonsummer | RATSKE_2_NROSR1 | TRANSMISSION_INDUCED | 112.5
2022 | nonsummer | RATSKE_2_RBSSB1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1475.1
2022 | nonsummer | RATSKE_2_RBSSB1 | AMBIENT_DUE_TO_TEMP | 60
2022 | nonsummer | RATSKE_2_RBSSB1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | RATSKE_2_RBSSB1 | UNIT_TESTING | 0
2022 | nonsummer | RATSKE_2_RBSSB2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1065.4667
2022 | nonsummer | RATSKE_2_RBSSB2 | AMBIENT_DUE_TO_TEMP | 114.6667
2022 | nonsummer | RATSKE_2_RBSSB2 | NEW_GENERATOR_TEST_ENERGY | 0
2022 | nonsummer | RATSKE_2_RBSSB2 | PLANT_MAINTENANCE | 0
2022 | nonsummer | RATSKE_2_RBSSB2 | PLANT_TROUBLE | 15
2022 | nonsummer | RATSKE_2_RBSSB2 | UNIT_TESTING | 0
2022 | nonsummer | RCKCRK_7_UNIT 1 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | RCKCRK_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 21442.2462
2022 | nonsummer | RCKCRK_7_UNIT 1 | PLANT_TROUBLE | 0
2022 | nonsummer | RCKCRK_7_UNIT 1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | RCKCRK_7_UNIT 1 | UNIT_TESTING | 0
2022 | nonsummer | RCKCRK_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 29723.6025
2022 | nonsummer | RCKCRK_7_UNIT 2 | PLANT_TROUBLE | 157.09
2022 | nonsummer | RCKCRK_7_UNIT 2 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | RECTOR_2_CREST | PLANT_MAINTENANCE | 13.5
2022 | nonsummer | RECTOR_2_CREST | PLANT_TROUBLE | 6.75
2022 | nonsummer | RECTOR_2_CREST | TRANSMISSION_INDUCED | 15.05
2022 | nonsummer | RECTOR_2_KAWEAH | AMBIENT_DUE_TO_TEMP | 1015.25
2022 | nonsummer | RECTOR_2_KAWEAH | AMBIENT_NOT_DUE_TO_TEMP | 5705.3967
2022 | nonsummer | RECTOR_2_KAWEAH | METERING_TELEMETRY | 120
2022 | nonsummer | RECTOR_2_KAWEAH | PLANT_MAINTENANCE | 0
2022 | nonsummer | RECTOR_2_KAWEAH | TRANSMISSION_INDUCED | 0
2022 | nonsummer | RECTOR_2_KAWH 1 | AMBIENT_NOT_DUE_TO_TEMP | 686.25
2022 | nonsummer | RECTOR_2_KAWH 1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | RECTOR_2_KAWH 1 | PLANT_TROUBLE | 1631.25
2022 | nonsummer | RECTOR_2_QF | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 11953.55
2022 | nonsummer | RECTOR_2_QF | PLANT_TROUBLE | 0
2022 | nonsummer | RECTOR_2_TFDBM1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 22.96
2022 | nonsummer | RECTOR_2_TFDBM1 | PLANT_MAINTENANCE | 26.5
2022 | nonsummer | RECTOR_2_TFDBM1 | PLANT_TROUBLE | 34.3733
2022 | nonsummer | REDBLF_6_UNIT | TRANSMISSION_INDUCED | 0
2022 | nonsummer | REDOND_7_UNIT 5 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | REDOND_7_UNIT 5 | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | REDOND_7_UNIT 5 | PLANT_TROUBLE | 17576.02
2022 | nonsummer | REDOND_7_UNIT 5 | UNIT_SUPPORTING_STARTUP | 0
2022 | nonsummer | REDOND_7_UNIT 5 | UNIT_TESTING | 0
2022 | nonsummer | REDOND_7_UNIT 6 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2022 | nonsummer | REDOND_7_UNIT 6 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | REDOND_7_UNIT 6 | PLANT_MAINTENANCE | 9593.05
2022 | nonsummer | REDOND_7_UNIT 6 | PLANT_TROUBLE | 8420.4427
2022 | nonsummer | REDOND_7_UNIT 6 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2022 | nonsummer | REDOND_7_UNIT 6 | UNIT_SUPPORTING_STARTUP | 171.45
2022 | nonsummer | REDOND_7_UNIT 6 | UNIT_TESTING | 0
2022 | nonsummer | REDOND_7_UNIT 8 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2022 | nonsummer | REDOND_7_UNIT 8 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | REDOND_7_UNIT 8 | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | REDOND_7_UNIT 8 | PLANT_MAINTENANCE | 480
2022 | nonsummer | REDOND_7_UNIT 8 | PLANT_TROUBLE | 14446.6533
2022 | nonsummer | REDOND_7_UNIT 8 | UNIT_SUPPORTING_STARTUP | 6080
2022 | nonsummer | REDOND_7_UNIT 8 | UNIT_TESTING | 0
2022 | nonsummer | RENWD_1_QF | PLANT_MAINTENANCE | 647.425
2022 | nonsummer | RENWD_1_QF | PLANT_TROUBLE | 170.9
2022 | nonsummer | RICHMN_1_CHVSR2 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | RICHMN_1_CHVSR2 | PLANT_TROUBLE | 12.6083
2022 | nonsummer | RICHMN_1_SOLAR | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | RICHMN_1_SOLAR | PLANT_TROUBLE | 0
2022 | nonsummer | RICHMN_1_SOLAR | TRANSMISSION_INDUCED | 0
2022 | nonsummer | RICHMN_7_BAYENV | AMBIENT_NOT_DUE_TO_TEMP | 2497
2022 | nonsummer | RICHMN_7_BAYENV | PLANT_TROUBLE | 63.5
2022 | nonsummer | RIOBRV_6_UNIT 1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 5194
2022 | nonsummer | RIOBRV_6_UNIT 1 | AMBIENT_DUE_TO_TEMP | 7508.9
2022 | nonsummer | RIOBRV_6_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | RIOBRV_6_UNIT 1 | PLANT_TROUBLE | 0
2022 | nonsummer | RNDMTN_2_SLSPHY1 | TRANSMISSION_INDUCED | 12.7
2022 | nonsummer | ROLLIN_6_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 5969.125
2022 | nonsummer | ROLLIN_6_UNIT | PLANT_TROUBLE | 13.05
2022 | nonsummer | ROLLIN_6_UNIT | TRANSMISSION_INDUCED | 11.475
2022 | nonsummer | ROSMDW_2_WIND1 | METERING_TELEMETRY | 0
2022 | nonsummer | ROSMDW_2_WIND1 | PLANT_MAINTENANCE | 4748.9
2022 | nonsummer | ROSMDW_2_WIND1 | PLANT_TROUBLE | 68.025
2022 | nonsummer | ROSMND_6_SOLAR | METERING_TELEMETRY | 15
2022 | nonsummer | ROSMND_6_SOLAR | PLANT_TROUBLE | 455.675
2022 | nonsummer | RSMSLR_6_SOLAR1 | PLANT_MAINTENANCE | 50
2022 | nonsummer | RSMSLR_6_SOLAR1 | PLANT_TROUBLE | 171
2022 | nonsummer | RSMSLR_6_SOLAR2 | METERING_TELEMETRY | 0
2022 | nonsummer | RSMSLR_6_SOLAR2 | PLANT_MAINTENANCE | 176.6667
2022 | nonsummer | RSMSLR_6_SOLAR2 | PLANT_TROUBLE | 72
2022 | nonsummer | RSMSLR_6_SOLAR2 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | RTEDDY_2_SEBSR3 | PLANT_MAINTENANCE | 315
2022 | nonsummer | RTEDDY_2_SEBSR3 | UNIT_TESTING | 0
2022 | nonsummer | RTEDDY_2_SEBSR4 | PLANT_MAINTENANCE | 186
2022 | nonsummer | RTEDDY_2_SOLAR2 | PLANT_TROUBLE | 450
2022 | nonsummer | RTREE_2_WIND1 | PLANT_TROUBLE | 29.04
2022 | nonsummer | RTREE_2_WIND2 | PLANT_MAINTENANCE | 1737.8433
2022 | nonsummer | RTREE_2_WIND2 | PLANT_TROUBLE | 0
2022 | nonsummer | RTREE_2_WIND3 | PLANT_TROUBLE | 36.3
2022 | nonsummer | RUSCTY_2_UNITS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2022 | nonsummer | RUSCTY_2_UNITS | AMBIENT_DUE_TO_TEMP | 850.512
2022 | nonsummer | RUSCTY_2_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 103.987
2022 | nonsummer | RUSCTY_2_UNITS | METERING_TELEMETRY | 0
2022 | nonsummer | RUSCTY_2_UNITS | PLANT_MAINTENANCE | 0
2022 | nonsummer | RUSCTY_2_UNITS | PLANT_TROUBLE | 462307.77
2022 | nonsummer | RUSCTY_2_UNITS | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2022 | nonsummer | RUSCTY_2_UNITS | UNIT_SUPPORTING_STARTUP | 0
2022 | nonsummer | RUSCTY_2_UNITS | UNIT_TESTING | 0
2022 | nonsummer | RVRVEW_1_UNITA1 | AMBIENT_DUE_TO_TEMP | 8
2022 | nonsummer | RVRVEW_1_UNITA1 | ENVIRONMENTAL_RESTRICTIONS | 3808
2022 | nonsummer | RVRVEW_1_UNITA1 | PLANT_MAINTENANCE | 1761.2
2022 | nonsummer | RVRVEW_1_UNITA1 | PLANT_TROUBLE | 908.32
2022 | nonsummer | RVSIDE_2_RERCU3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2022 | nonsummer | RVSIDE_2_RERCU3 | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | RVSIDE_2_RERCU3 | PLANT_MAINTENANCE | 0
2022 | nonsummer | RVSIDE_2_RERCU3 | PLANT_TROUBLE | 0
2022 | nonsummer | RVSIDE_2_RERCU4 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2022 | nonsummer | RVSIDE_2_RERCU4 | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | RVSIDE_2_RERCU4 | PLANT_MAINTENANCE | 0
2022 | nonsummer | RVSIDE_2_RERCU4 | PLANT_TROUBLE | 0
2022 | nonsummer | RVSIDE_6_RERCU1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2022 | nonsummer | RVSIDE_6_RERCU1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | RVSIDE_6_RERCU1 | PLANT_TROUBLE | 11604
2022 | nonsummer | RVSIDE_6_RERCU2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2022 | nonsummer | RVSIDE_6_RERCU2 | PLANT_MAINTENANCE | 0
2022 | nonsummer | RVSIDE_6_RERCU2 | PLANT_TROUBLE | 101.85
2022 | nonsummer | RVSIDE_6_SOLAR1 | PLANT_TROUBLE | 687.5
2022 | nonsummer | RVSIDE_6_SPRING | PLANT_TROUBLE | 4.5
2022 | nonsummer | SALIRV_2_UNIT | PLANT_MAINTENANCE | 195
2022 | nonsummer | SALIRV_2_UNIT | PLANT_TROUBLE | 0
2022 | nonsummer | SALTSP_7_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 23235.9
2022 | nonsummer | SALTSP_7_UNITS | PLANT_TROUBLE | 109.865
2022 | nonsummer | SALTSP_7_UNITS | TRANSMISSION_INDUCED | 0
2022 | nonsummer | SAMPSN_6_KELCO1 | PLANT_TROUBLE | 862.5
2022 | nonsummer | SANBRN_2_ES1BT3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 711.9035
2022 | nonsummer | SANBRN_2_ES1BT3 | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | SANBRN_2_ES1BT3 | NEW_GENERATOR_TEST_ENERGY | 0
2022 | nonsummer | SANBRN_2_ES1BT3 | PLANT_MAINTENANCE | 0
2022 | nonsummer | SANBRN_2_ES1BT3 | PLANT_TROUBLE | 0
2022 | nonsummer | SANBRN_2_ES2SB3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 503.3
2022 | nonsummer | SANBRN_2_ES2SB3 | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | SANBRN_2_ES2SB3 | NEW_GENERATOR_TEST_ENERGY | 90
2022 | nonsummer | SANBRN_2_ES2SB3 | PLANT_MAINTENANCE | 0
2022 | nonsummer | SANBRN_2_ES2SB3 | PLANT_TROUBLE | 0
2022 | nonsummer | SANBRN_2_ESABT1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | SANBRN_2_ESABT1 | METERING_TELEMETRY | 0
2022 | nonsummer | SANBRN_2_ESABT1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | SANBRN_2_ESABT1 | PLANT_TROUBLE | 0
2022 | nonsummer | SANBRN_2_ESABT1 | UNIT_TESTING | 336.6667
2022 | nonsummer | SANBRN_2_ESBBT1 | METERING_TELEMETRY | 0
2022 | nonsummer | SANBRN_2_ESBBT1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | SANBRN_2_ESBBT1 | PLANT_TROUBLE | 0
2022 | nonsummer | SANBRN_2_ESBBT1 | UNIT_SUPPORTING_STARTUP | 0
2022 | nonsummer | SANBRN_2_ESBBT1 | UNIT_TESTING | 0
2022 | nonsummer | SANDLT_2_SUNITS | AMBIENT_NOT_DUE_TO_TEMP | 25633.375
2022 | nonsummer | SANDLT_2_SUNITS | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | SANDLT_2_SUNITS | METERING_TELEMETRY | 0
2022 | nonsummer | SANDLT_2_SUNITS | PLANT_MAINTENANCE | 7687.5
2022 | nonsummer | SANDLT_2_SUNITS | PLANT_TROUBLE | 687.5
2022 | nonsummer | SANLOB_1_LNDFIL | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2022 | nonsummer | SANLOB_1_LNDFIL | AMBIENT_DUE_TO_TEMP | 0.16667
2022 | nonsummer | SANLOB_1_LNDFIL | PLANT_MAINTENANCE | 2.925
2022 | nonsummer | SANLOB_1_LNDFIL | PLANT_TROUBLE | 60.25
2022 | nonsummer | SANLOB_1_LNDFIL | TRANSMISSION_INDUCED | 0
2022 | nonsummer | SANLOB_1_LNDFIL | UNIT_TESTING | 0
2022 | nonsummer | SANTFG_7_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 8482
2022 | nonsummer | SANTFG_7_UNITS | PLANT_MAINTENANCE | 0
2022 | nonsummer | SANTFG_7_UNITS | PLANT_TROUBLE | 493.5
2022 | nonsummer | SANTGO_2_LNDFL1 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | SANTGO_2_LNDFL1 | METERING_TELEMETRY | 8
2022 | nonsummer | SANTGO_2_LNDFL1 | PLANT_MAINTENANCE | 104
2022 | nonsummer | SANTGO_2_LNDFL1 | PLANT_TROUBLE | 1371.9733
2022 | nonsummer | SANTGO_2_LNDFL1 | TRANSMISSION_INDUCED | 2
2022 | nonsummer | SANTGO_2_MABBT1 | METERING_TELEMETRY | 0
2022 | nonsummer | SANTGO_2_MABBT1 | PLANT_MAINTENANCE | 340
2022 | nonsummer | SANTGO_2_MABBT1 | PLANT_TROUBLE | 695.3458
2022 | nonsummer | SANTGO_2_MABBT1 | TRANSMISSION_INDUCED | 8
2022 | nonsummer | SANWD_1_QF | PLANT_MAINTENANCE | 9548.999
2022 | nonsummer | SANWD_1_QF | PLANT_TROUBLE | 0
2022 | nonsummer | SANWD_1_QF | TRANSMISSION_INDUCED | 0
2022 | nonsummer | SAUGUS_7_CHIQCN | PLANT_MAINTENANCE | 120
2022 | nonsummer | SAUGUS_7_CHIQCN | TRANSMISSION_INDUCED | 0
2022 | nonsummer | SBERDO_2_PSP3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1665
2022 | nonsummer | SBERDO_2_PSP3 | AMBIENT_DUE_TO_TEMP | 4807.62
2022 | nonsummer | SBERDO_2_PSP3 | METERING_TELEMETRY | 475
2022 | nonsummer | SBERDO_2_PSP3 | PLANT_MAINTENANCE | 41549.4167
2022 | nonsummer | SBERDO_2_PSP3 | PLANT_TROUBLE | 12803.9
2022 | nonsummer | SBERDO_2_PSP3 | UNIT_TESTING | 2572.0833
2022 | nonsummer | SBERDO_2_PSP4 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1663
2022 | nonsummer | SBERDO_2_PSP4 | AMBIENT_DUE_TO_TEMP | 4013.6433
2022 | nonsummer | SBERDO_2_PSP4 | METERING_TELEMETRY | 0
2022 | nonsummer | SBERDO_2_PSP4 | PLANT_MAINTENANCE | 8325
2022 | nonsummer | SBERDO_2_PSP4 | PLANT_TROUBLE | 15585.6143
2022 | nonsummer | SBERDO_2_PSP4 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2022 | nonsummer | SBERDO_2_PSP4 | UNIT_TESTING | 2412.66
2022 | nonsummer | SBERDO_2_REDLND | PLANT_TROUBLE | 0
2022 | nonsummer | SBERDO_2_RTS013 | PLANT_TROUBLE | 822.5
2022 | nonsummer | SBERDO_2_RTS016 | PLANT_TROUBLE | 352.5
2022 | nonsummer | SBERDO_2_SNTANA | AMBIENT_NOT_DUE_TO_TEMP | 2391
2022 | nonsummer | SBERDO_2_SNTANA | PLANT_TROUBLE | 4273.6933
2022 | nonsummer | SBERDO_2_SNTANA | TRANSMISSION_INDUCED | 10
2022 | nonsummer | SBERDO_6_MILLCK | AMBIENT_NOT_DUE_TO_TEMP | 2386
2022 | nonsummer | SBERDO_6_MILLCK | PLANT_MAINTENANCE | 10
2022 | nonsummer | SBERDO_6_MILLCK | PLANT_TROUBLE | 491.15
2022 | nonsummer | SBERDO_6_MILLCK | TRANSMISSION_INDUCED | 0
2022 | nonsummer | SCEC_1_PDRP107 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCEC_1_PDRP108 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCEC_1_PDRP109 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCEC_1_PDRP110 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCEC_1_PDRP124 | ANNUAL_USE_LIMIT_REACHED | 67.71
2022 | nonsummer | SCEC_1_PDRP124 | MONTHLY_USE_LIMIT_REACHED | 45.75
2022 | nonsummer | SCEC_1_PDRP134 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCEC_1_PDRP138 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCEC_1_PDRP16 | MONTHLY_USE_LIMIT_REACHED | 567.45
2022 | nonsummer | SCEC_1_PDRP160 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCEC_1_PDRP161 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCEC_1_PDRP163 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCEC_1_PDRP17 | MONTHLY_USE_LIMIT_REACHED | 1244
2022 | nonsummer | SCEC_1_PDRP171 | PLANT_TROUBLE | 0
2022 | nonsummer | SCEC_1_PDRP173 | MONTHLY_USE_LIMIT_REACHED | 138.26
2022 | nonsummer | SCEC_1_PDRP180 | OTHER_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCEC_1_PDRP60 | MONTHLY_USE_LIMIT_REACHED | 39.7
2022 | nonsummer | SCEC_1_RDRR08 | OTHER_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCEHOV_2_HOOVER | AMBIENT_NOT_DUE_TO_TEMP | 158860.05
2022 | nonsummer | SCEHOV_2_HOOVER | METERING_TELEMETRY | 0
2022 | nonsummer | SCEHOV_2_HOOVER | MONTHLY_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCEHOV_2_HOOVER | OTHER_USE_LIMIT_REACHED | 1348.1133
2022 | nonsummer | SCEHOV_2_HOOVER | PLANT_TROUBLE | 618
2022 | nonsummer | SCEN_6_PDRP13 | MONTHLY_USE_LIMIT_REACHED | 116.9
2022 | nonsummer | SCEN_6_PDRP28 | MONTHLY_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCEN_6_PDRP58 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCEN_6_PDRP59 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCEN_6_PDRP62 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCEN_6_PDRP65 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCEN_6_PDRP90 | OTHER_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCEN_6_RDRR02 | OTHER_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCEW_2_PDRP03 | ANNUAL_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCEW_2_PDRP03 | MONTHLY_USE_LIMIT_REACHED | 200
2022 | nonsummer | SCEW_2_PDRP09 | MONTHLY_USE_LIMIT_REACHED | 262.5
2022 | nonsummer | SCEW_2_PDRP10 | ANNUAL_USE_LIMIT_REACHED | 500
2022 | nonsummer | SCEW_2_PDRP10 | MONTHLY_USE_LIMIT_REACHED | 300
2022 | nonsummer | SCEW_2_PDRP106 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCEW_2_PDRP107 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCEW_2_PDRP108 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCEW_2_PDRP109 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCEW_2_PDRP110 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCEW_2_PDRP111 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCEW_2_PDRP112 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCEW_2_PDRP114 | ANNUAL_USE_LIMIT_REACHED | 420.55
2022 | nonsummer | SCEW_2_PDRP114 | MONTHLY_USE_LIMIT_REACHED | 161.75
2022 | nonsummer | SCEW_2_PDRP117 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCEW_2_PDRP12 | MONTHLY_USE_LIMIT_REACHED | 191.8
2022 | nonsummer | SCEW_2_PDRP123 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCEW_2_PDRP131 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCEW_2_PDRP159 | ANNUAL_USE_LIMIT_REACHED | 1128.4
2022 | nonsummer | SCEW_2_PDRP159 | MONTHLY_USE_LIMIT_REACHED | 596.96
2022 | nonsummer | SCEW_2_PDRP160 | MONTHLY_USE_LIMIT_REACHED | 320.6
2022 | nonsummer | SCEW_2_PDRP163 | MONTHLY_USE_LIMIT_REACHED | 253.89
2022 | nonsummer | SCEW_2_PDRP167 | ANNUAL_USE_LIMIT_REACHED | 621.72
2022 | nonsummer | SCEW_2_PDRP167 | MONTHLY_USE_LIMIT_REACHED | 235.5
2022 | nonsummer | SCEW_2_PDRP167 | OTHER_USE_LIMIT_REACHED | 9.42
2022 | nonsummer | SCEW_2_PDRP170 | OTHER_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCEW_2_PDRP172 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCEW_2_PDRP173 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCEW_2_PDRP174 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCEW_2_PDRP35 | MONTHLY_USE_LIMIT_REACHED | 986.4
2022 | nonsummer | SCEW_2_PDRP85 | MONTHLY_USE_LIMIT_REACHED | 79.6
2022 | nonsummer | SCEW_2_PDRP89 | MONTHLY_USE_LIMIT_REACHED | 80.7
2022 | nonsummer | SCEW_2_RDRR08 | OTHER_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCHD_1_PDRP14 | MONTHLY_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCHD_1_PDRP48 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCHD_1_PDRP60 | OTHER_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCHD_1_PDRP61 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCHD_1_RDRR08 | OTHER_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCHLTE_1_PL1X3 | AMBIENT_DUE_TO_TEMP | 8853.05
2022 | nonsummer | SCHLTE_1_PL1X3 | PLANT_MAINTENANCE | 0
2022 | nonsummer | SCHLTE_1_PL1X3 | PLANT_TROUBLE | 214.0057
2022 | nonsummer | SCHNDR_1_FIVPTS | METERING_TELEMETRY | 150
2022 | nonsummer | SCHNDR_1_FIVPTS | PLANT_MAINTENANCE | 0
2022 | nonsummer | SCHNDR_1_FIVPTS | PLANT_TROUBLE | 225
2022 | nonsummer | SCHNDR_1_OS2BM2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 28
2022 | nonsummer | SCHNDR_1_OS2BM2 | AMBIENT_NOT_DUE_TO_TEMP | 32
2022 | nonsummer | SCHNDR_1_OS2BM2 | METERING_TELEMETRY | 0
2022 | nonsummer | SCHNDR_1_OS2BM2 | PLANT_MAINTENANCE | 5.6
2022 | nonsummer | SCHNDR_1_OS2BM2 | PLANT_TROUBLE | 29.48
2022 | nonsummer | SCHNDR_1_WSTSDE | PLANT_MAINTENANCE | 200
2022 | nonsummer | SCHNDR_1_WSTSDE | PLANT_TROUBLE | 4214.5
2022 | nonsummer | SCNW_6_PDRP05 | MONTHLY_USE_LIMIT_REACHED | 423.5
2022 | nonsummer | SCNW_6_PDRP40 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCNW_6_PDRP41 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCNW_6_PDRP51 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCNW_6_PDRP57 | MONTHLY_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCNW_6_PDRP61 | MONTHLY_USE_LIMIT_REACHED | 664.4
2022 | nonsummer | SCNW_6_PDRP61 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2022 | nonsummer | SCNW_6_PDRP70 | OTHER_USE_LIMIT_REACHED | 0
2022 | nonsummer | SCNW_6_RDRR08 | OTHER_USE_LIMIT_REACHED | 0
2022 | nonsummer | SDG1_1_PDRP100 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | SDG1_1_PDRP101 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | SDG1_1_PDRP102 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | SDG1_1_PDRP103 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | SDG1_1_PDRP105 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | SDG1_1_PDRP84 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | SDG1_1_PDRP85 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | SDG1_1_PDRP88 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | SDG1_1_PDRP91 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | SDG1_1_PDRP97 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | SDG1_1_PDRP98 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | SEARLS_7_ARGUS | METERING_TELEMETRY | 0
2022 | nonsummer | SEARLS_7_ARGUS | PLANT_MAINTENANCE | 285
2022 | nonsummer | SEARLS_7_ARGUS | PLANT_TROUBLE | 285
2022 | nonsummer | SEARLS_7_ARGUS | TRANSMISSION_INDUCED | 2.5333
2022 | nonsummer | SEGS_1_SR2SL2 | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | SEGS_1_SR2SL2 | PLANT_MAINTENANCE | 40
2022 | nonsummer | SEGS_1_SR2SL2 | PLANT_TROUBLE | 0
2022 | nonsummer | SEGS_1_SR2SL2 | TRANSMISSION_INDUCED | 40
2022 | nonsummer | SENTNL_2_CTG1 | AMBIENT_DUE_TO_TEMP | 2524.2
2022 | nonsummer | SENTNL_2_CTG1 | ANNUAL_USE_LIMIT_REACHED | 1566.8
2022 | nonsummer | SENTNL_2_CTG1 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | SENTNL_2_CTG1 | METERING_TELEMETRY | 1372.74
2022 | nonsummer | SENTNL_2_CTG1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | SENTNL_2_CTG1 | PLANT_TROUBLE | 2896.322
2022 | nonsummer | SENTNL_2_CTG1 | UNIT_TESTING | 0
2022 | nonsummer | SENTNL_2_CTG2 | AMBIENT_DUE_TO_TEMP | 3027.61
2022 | nonsummer | SENTNL_2_CTG2 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | SENTNL_2_CTG2 | METERING_TELEMETRY | 1717.6
2022 | nonsummer | SENTNL_2_CTG2 | PLANT_MAINTENANCE | 1452.34
2022 | nonsummer | SENTNL_2_CTG2 | PLANT_TROUBLE | 4762.9195
2022 | nonsummer | SENTNL_2_CTG2 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | SENTNL_2_CTG2 | UNIT_TESTING | 0
2022 | nonsummer | SENTNL_2_CTG3 | AMBIENT_DUE_TO_TEMP | 2478.78
2022 | nonsummer | SENTNL_2_CTG3 | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | SENTNL_2_CTG3 | ENVIRONMENTAL_RESTRICTIONS | 2291.8
2022 | nonsummer | SENTNL_2_CTG3 | METERING_TELEMETRY | 1900
2022 | nonsummer | SENTNL_2_CTG3 | PLANT_MAINTENANCE | 2063.26
2022 | nonsummer | SENTNL_2_CTG3 | PLANT_TROUBLE | 762.878
2022 | nonsummer | SENTNL_2_CTG3 | UNIT_TESTING | 0
2022 | nonsummer | SENTNL_2_CTG4 | AMBIENT_DUE_TO_TEMP | 2441.42
2022 | nonsummer | SENTNL_2_CTG4 | ANNUAL_USE_LIMIT_REACHED | 1598.25
2022 | nonsummer | SENTNL_2_CTG4 | ENVIRONMENTAL_RESTRICTIONS | 40.4428
2022 | nonsummer | SENTNL_2_CTG4 | METERING_TELEMETRY | 3772.71
2022 | nonsummer | SENTNL_2_CTG4 | PLANT_MAINTENANCE | 0
2022 | nonsummer | SENTNL_2_CTG4 | PLANT_TROUBLE | 3823.9187
2022 | nonsummer | SENTNL_2_CTG4 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | SENTNL_2_CTG4 | UNIT_TESTING | 0
2022 | nonsummer | SENTNL_2_CTG5 | AMBIENT_DUE_TO_TEMP | 2541.03
2022 | nonsummer | SENTNL_2_CTG5 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | SENTNL_2_CTG5 | METERING_TELEMETRY | 1855.54
2022 | nonsummer | SENTNL_2_CTG5 | PLANT_MAINTENANCE | 0
2022 | nonsummer | SENTNL_2_CTG5 | PLANT_TROUBLE | 3357.798
2022 | nonsummer | SENTNL_2_CTG5 | UNIT_TESTING | 0
2022 | nonsummer | SENTNL_2_CTG6 | AMBIENT_DUE_TO_TEMP | 2408.97
2022 | nonsummer | SENTNL_2_CTG6 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | SENTNL_2_CTG6 | METERING_TELEMETRY | 1750
2022 | nonsummer | SENTNL_2_CTG6 | PLANT_MAINTENANCE | 4575.93
2022 | nonsummer | SENTNL_2_CTG6 | PLANT_TROUBLE | 4010.3077
2022 | nonsummer | SENTNL_2_CTG6 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | SENTNL_2_CTG6 | UNIT_TESTING | 0
2022 | nonsummer | SENTNL_2_CTG7 | AMBIENT_DUE_TO_TEMP | 2344.36
2022 | nonsummer | SENTNL_2_CTG7 | ANNUAL_USE_LIMIT_REACHED | 980
2022 | nonsummer | SENTNL_2_CTG7 | METERING_TELEMETRY | 1960
2022 | nonsummer | SENTNL_2_CTG7 | PLANT_MAINTENANCE | 0
2022 | nonsummer | SENTNL_2_CTG7 | PLANT_TROUBLE | 8361.4803
2022 | nonsummer | SENTNL_2_CTG7 | UNIT_TESTING | 0
2022 | nonsummer | SENTNL_2_CTG8 | AMBIENT_DUE_TO_TEMP | 2449.99
2022 | nonsummer | SENTNL_2_CTG8 | ANNUAL_USE_LIMIT_REACHED | 4808.25
2022 | nonsummer | SENTNL_2_CTG8 | METERING_TELEMETRY | 89.89
2022 | nonsummer | SENTNL_2_CTG8 | PLANT_MAINTENANCE | 1036.84
2022 | nonsummer | SENTNL_2_CTG8 | PLANT_TROUBLE | 3318.9915
2022 | nonsummer | SENTNL_2_CTG8 | UNIT_TESTING | 0
2022 | nonsummer | SGREGY_6_SANGER | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | SGREGY_6_SANGER | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | SGREGY_6_SANGER | ANNUAL_USE_LIMIT_REACHED | 14731.5
2022 | nonsummer | SGREGY_6_SANGER | PLANT_MAINTENANCE | 3690.925
2022 | nonsummer | SGREGY_6_SANGER | PLANT_TROUBLE | 0
2022 | nonsummer | SGREGY_6_SANGER | UNIT_TESTING | 0
2022 | nonsummer | SIERRA_1_UNITS | AMBIENT_DUE_TO_TEMP | 1722.83
2022 | nonsummer | SIERRA_1_UNITS | PLANT_TROUBLE | 1975.6
2022 | nonsummer | SIERRA_1_UNITS | RTU_RIG | 0
2022 | nonsummer | SIERRA_1_UNITS | UNIT_TESTING | 0
2022 | nonsummer | SIGHEB_6_MIRDYN | PLANT_MAINTENANCE | 1682
2022 | nonsummer | SKERN_6_SOLAR1 | PLANT_MAINTENANCE | 458.3333
2022 | nonsummer | SKERN_6_SOLAR1 | PLANT_TROUBLE | 0
2022 | nonsummer | SKERN_6_SOLAR1 | TRANSMISSION_INDUCED | 200
2022 | nonsummer | SKERN_6_SOLAR2 | PLANT_MAINTENANCE | 208.8333
2022 | nonsummer | SKERN_6_SOLAR2 | PLANT_TROUBLE | 28.3333
2022 | nonsummer | SKERN_6_SOLAR2 | TRANSMISSION_INDUCED | 171
2022 | nonsummer | SLATE_2_SLASR1 | METERING_TELEMETRY | 0
2022 | nonsummer | SLATE_2_SLASR1 | PLANT_MAINTENANCE | 598.14
2022 | nonsummer | SLATE_2_SLASR1 | PLANT_TROUBLE | 564.92
2022 | nonsummer | SLATE_2_SLASR1 | UNIT_TESTING | 0
2022 | nonsummer | SLATE_2_SLASR2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 5048.2833
2022 | nonsummer | SLATE_2_SLASR2 | AMBIENT_DUE_TO_TEMP | 652.19
2022 | nonsummer | SLATE_2_SLASR2 | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | SLATE_2_SLASR2 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | SLATE_2_SLASR2 | METERING_TELEMETRY | 0
2022 | nonsummer | SLATE_2_SLASR2 | PLANT_MAINTENANCE | 1104.65
2022 | nonsummer | SLATE_2_SLASR2 | PLANT_TROUBLE | 1305.0775
2022 | nonsummer | SLATE_2_SLASR2 | UNIT_TESTING | 0
2022 | nonsummer | SLATE_2_SLASR3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 3258.9583
2022 | nonsummer | SLATE_2_SLASR3 | AMBIENT_DUE_TO_TEMP | 852.955
2022 | nonsummer | SLATE_2_SLASR3 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | SLATE_2_SLASR3 | METERING_TELEMETRY | 0
2022 | nonsummer | SLATE_2_SLASR3 | PLANT_MAINTENANCE | 810
2022 | nonsummer | SLATE_2_SLASR3 | PLANT_TROUBLE | 486.715
2022 | nonsummer | SLATE_2_SLASR3 | UNIT_TESTING | 0
2022 | nonsummer | SLATE_2_SLASR4 | AMBIENT_NOT_DUE_TO_TEMP | 12554.0875
2022 | nonsummer | SLATE_2_SLASR4 | METERING_TELEMETRY | 0
2022 | nonsummer | SLATE_2_SLASR4 | NEW_GENERATOR_TEST_ENERGY | 315
2022 | nonsummer | SLATE_2_SLASR4 | PLANT_MAINTENANCE | 644.4042
2022 | nonsummer | SLATE_2_SLASR4 | PLANT_TROUBLE | 517.7572
2022 | nonsummer | SLATE_2_SLASR4 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 324.3092
2022 | nonsummer | SLATE_2_SLASR5 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2022 | nonsummer | SLATE_2_SLASR5 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 2398.7125
2022 | nonsummer | SLATE_2_SLASR5 | AMBIENT_DUE_TO_TEMP | 6.02
2022 | nonsummer | SLATE_2_SLASR5 | AMBIENT_DUE_TO_TEMP | 89.0667
2022 | nonsummer | SLATE_2_SLASR5 | AMBIENT_NOT_DUE_TO_TEMP | 468.965
2022 | nonsummer | SLATE_2_SLASR5 | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | SLATE_2_SLASR5 | METERING_TELEMETRY | 0
2022 | nonsummer | SLATE_2_SLASR5 | METERING_TELEMETRY | 0
2022 | nonsummer | SLATE_2_SLASR5 | NEW_GENERATOR_TEST_ENERGY | 0
2022 | nonsummer | SLATE_2_SLASR5 | PLANT_MAINTENANCE | 52
2022 | nonsummer | SLATE_2_SLASR5 | PLANT_MAINTENANCE | 156
2022 | nonsummer | SLATE_2_SLASR5 | PLANT_TROUBLE | 360.5808
2022 | nonsummer | SLATE_2_SLASR5 | PLANT_TROUBLE | 264.8442
2022 | nonsummer | SLATE_2_SLASR5 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2022 | nonsummer | SLATE_2_SLASR5 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 56
2022 | nonsummer | SLATE_2_SLASR5 | UNIT_TESTING | 0
2022 | nonsummer | SLATE_2_SLASR5 | UNIT_TESTING | 26
2022 | nonsummer | SLRMS3_2_SRMSR1 | PLANT_MAINTENANCE | 1000
2022 | nonsummer | SLRMS3_2_SRMSR1 | PLANT_TROUBLE | 0
2022 | nonsummer | SLRMS3_2_SRMSR1 | TRANSMISSION_INDUCED | 875
2022 | nonsummer | SLST13_2_SOLAR1 | PLANT_MAINTENANCE | 643.8067
2022 | nonsummer | SLST13_2_SOLAR1 | PLANT_TROUBLE | 266.34
2022 | nonsummer | SLSTR1_2_SOLAR1 | PLANT_TROUBLE | 270
2022 | nonsummer | SLUISP_2_UNITS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 93112.2
2022 | nonsummer | SLUISP_2_UNITS | METERING_TELEMETRY | 1378.65
2022 | nonsummer | SLUISP_2_UNITS | PLANT_TROUBLE | 2319.3667
2022 | nonsummer | SLUISP_2_UNITS | TRANSMISSION_INDUCED | 0
2022 | nonsummer | SLYCRK_1_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 13
2022 | nonsummer | SLYCRK_1_UNIT 1 | METERING_TELEMETRY | 0
2022 | nonsummer | SLYCRK_1_UNIT 1 | PLANT_TROUBLE | 355.9833
2022 | nonsummer | SLYCRK_1_UNIT 1 | TRANSMISSION_INDUCED | 294.8833
2022 | nonsummer | SLYCRK_1_UNIT 1 | UNIT_TESTING | 0
2022 | nonsummer | SMPRIP_1_SMPSON | PLANT_MAINTENANCE | 0
2022 | nonsummer | SMPRIP_1_SMPSON | PLANT_TROUBLE | 690.75
2022 | nonsummer | SMPRIP_1_SMPSON | TRANSMISSION_INDUCED | 0
2022 | nonsummer | SMUDGO_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 7595
2022 | nonsummer | SMUDGO_7_UNIT 1 | PLANT_TROUBLE | 35763.7
2022 | nonsummer | SMYRNA_1_DL1SR1 | PLANT_TROUBLE | 27.8167
2022 | nonsummer | SMYRNA_1_DL1SR1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | SNCLRA_2_HOWLNG | AMBIENT_DUE_TO_TEMP | 284.5
2022 | nonsummer | SNCLRA_2_HOWLNG | AMBIENT_NOT_DUE_TO_TEMP | 2661.17
2022 | nonsummer | SNCLRA_2_HOWLNG | PLANT_MAINTENANCE | 1213.95
2022 | nonsummer | SNCLRA_2_HOWLNG | PLANT_TROUBLE | 3853.87
2022 | nonsummer | SNCLRA_2_SILBT1 | PLANT_MAINTENANCE | 5.9333
2022 | nonsummer | SNCLRA_2_SILBT1 | PLANT_TROUBLE | 0
2022 | nonsummer | SNCLRA_2_SILBT1 | UNIT_TESTING | 0
2022 | nonsummer | SNCLRA_2_UNIT | PLANT_MAINTENANCE | 15812.5
2022 | nonsummer | SNCLRA_2_UNIT1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | SNCLRA_2_UNIT1 | TRANSMISSION_INDUCED | 3.6667
2022 | nonsummer | SNCLRA_2_VESBT1 | METERING_TELEMETRY | 266.6667
2022 | nonsummer | SNCLRA_2_VESBT1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | SNCLRA_2_VESBT1 | PLANT_TROUBLE | 2650
2022 | nonsummer | SNCLRA_2_VESBT1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | SNCLRA_2_VESBT1 | UNIT_TESTING | 0
2022 | nonsummer | SNCLRA_6_OXGEN | PLANT_MAINTENANCE | 8728.305
2022 | nonsummer | SNCLRA_6_OXGEN | TRANSMISSION_INDUCED | 95.4
2022 | nonsummer | SNCLRA_6_OXGEN | UNIT_TESTING | 0
2022 | nonsummer | SNCLRA_6_PROCGN | PLANT_MAINTENANCE | 238.7017
2022 | nonsummer | SNCLRA_6_PROCGN | PLANT_TROUBLE | 789.5517
2022 | nonsummer | SNCLRA_6_PROCGN | TRANSMISSION_INDUCED | 0
2022 | nonsummer | SNCLRA_6_QF | PLANT_TROUBLE | 1.925
2022 | nonsummer | SNDBAR_7_UNIT 1 | PLANT_TROUBLE | 16.47
2022 | nonsummer | SNDBAR_7_UNIT 1 | TRANSMISSION_INDUCED | 291.06
2022 | nonsummer | SNMALF_6_UNITS | METERING_TELEMETRY | 25
2022 | nonsummer | SNMALF_6_UNITS | PLANT_TROUBLE | 225
2022 | nonsummer | SNMALF_6_UNITS | TRANSMISSION_INDUCED | 0
2022 | nonsummer | SNORA_2_SNRSLR | PLANT_MAINTENANCE | 0
2022 | nonsummer | SNORA_2_SNRSLR | PLANT_TROUBLE | 83.6
2022 | nonsummer | SNORA_2_SNRSLR | TRANSITIONAL_LIMITATION | 92
2022 | nonsummer | SNORA_2_SNRSLR | TRANSMISSION_INDUCED | 0
2022 | nonsummer | SOUTH_2_UNIT | METERING_TELEMETRY | 0
2022 | nonsummer | SOUTH_2_UNIT | PLANT_TROUBLE | 0
2022 | nonsummer | SOUTH_2_UNIT | TRANSMISSION_INDUCED | 440.2
2022 | nonsummer | SPANSH_6_FBEHY1 | PLANT_TROUBLE | 450.45
2022 | nonsummer | SPANSH_6_FBEHY1 | TRANSMISSION_INDUCED | 56.8095
2022 | nonsummer | SPAULD_6_UNIT 3 | AMBIENT_NOT_DUE_TO_TEMP | 3747.6967
2022 | nonsummer | SPAULD_6_UNIT 3 | PLANT_MAINTENANCE | 0
2022 | nonsummer | SPAULD_6_UNIT 3 | PLANT_TROUBLE | 97.5
2022 | nonsummer | SPAULD_6_UNIT 3 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | SPAULD_6_UNIT12 | AMBIENT_NOT_DUE_TO_TEMP | 4022.925
2022 | nonsummer | SPAULD_6_UNIT12 | PLANT_MAINTENANCE | 0
2022 | nonsummer | SPAULD_6_UNIT12 | PLANT_TROUBLE | 106
2022 | nonsummer | SPAULD_6_UNIT12 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | SPBURN_2_UNIT 1 | METERING_TELEMETRY | 0
2022 | nonsummer | SPBURN_2_UNIT 1 | PLANT_MAINTENANCE | 1870
2022 | nonsummer | SPBURN_2_UNIT 1 | PLANT_TROUBLE | 1103.8333
2022 | nonsummer | SPBURN_2_UNIT 1 | TRANSMISSION_INDUCED | 110
2022 | nonsummer | SPBURN_7_SNOWMT | AMBIENT_NOT_DUE_TO_TEMP | 1027.5
2022 | nonsummer | SPBURN_7_SNOWMT | PLANT_TROUBLE | 2.7
2022 | nonsummer | SPBURN_7_SNOWMT | TRANSMISSION_INDUCED | 0
2022 | nonsummer | SPI LI_2_UNIT 1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2022 | nonsummer | SPI LI_2_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | SPI LI_2_UNIT 1 | PLANT_MAINTENANCE | 172
2022 | nonsummer | SPI LI_2_UNIT 1 | PLANT_TROUBLE | 344
2022 | nonsummer | SPI LI_2_UNIT 1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | SPIAND_1_ANDSN2 | PLANT_MAINTENANCE | 1629
2022 | nonsummer | SPIAND_1_ANDSN2 | PLANT_TROUBLE | 1737.1475
2022 | nonsummer | SPICER_1_UNITS | PLANT_TROUBLE | 5.3
2022 | nonsummer | SPICER_1_UNITS | TRANSMISSION_INDUCED | 185.3
2022 | nonsummer | SPIFBD_1_PL1X2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 150
2022 | nonsummer | SPIFBD_1_PL1X2 | PLANT_MAINTENANCE | 150
2022 | nonsummer | SPIFBD_1_PL1X2 | PLANT_TROUBLE | 691.5
2022 | nonsummer | SPIFBD_1_PL1X2 | TRANSMISSION_INDUCED | 145
2022 | nonsummer | SPOINT_2_MEADDYN | PLANT_TROUBLE | 0
2022 | nonsummer | SPOINT_2_MEADDYN | TRANSITIONAL_LIMITATION | 47125
2022 | nonsummer | SPOINT_2_PARKERDYN | PLANT_MAINTENANCE | 4000
2022 | nonsummer | SPOINT_2_PARKERDYN | TRANSITIONAL_LIMITATION | 29000
2022 | nonsummer | SPQUIN_6_SRPCQU | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2022 | nonsummer | SPQUIN_6_SRPCQU | PLANT_MAINTENANCE | 1544.95
2022 | nonsummer | SPQUIN_6_SRPCQU | PLANT_TROUBLE | 813.1667
2022 | nonsummer | SPQUIN_6_SRPCQU | TRANSMISSION_INDUCED | 78.4
2022 | nonsummer | SPRGAP_1_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | SPRGAP_1_UNIT 1 | PLANT_MAINTENANCE | 5.1333
2022 | nonsummer | SPRGAP_1_UNIT 1 | PLANT_TROUBLE | 4.9
2022 | nonsummer | SPRGAP_1_UNIT 1 | TRANSMISSION_INDUCED | 226.1
2022 | nonsummer | SPRGVL_2_CREST | PLANT_TROUBLE | 0
2022 | nonsummer | SPRGVL_2_TULESC | ENVIRONMENTAL_RESTRICTIONS | 2637.5
2022 | nonsummer | STANIS_7_UNIT 1 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | STANIS_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 16648.2017
2022 | nonsummer | STANIS_7_UNIT 1 | PLANT_TROUBLE | 0
2022 | nonsummer | STANIS_7_UNIT 1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | STANTN_2_STAGT1 | AMBIENT_DUE_TO_TEMP | 7.8063
2022 | nonsummer | STANTN_2_STAGT1 | PLANT_MAINTENANCE | 11.25
2022 | nonsummer | STANTN_2_STAGT1 | PLANT_TROUBLE | 0
2022 | nonsummer | STANTN_2_STAGT1 | UNIT_TESTING | 0
2022 | nonsummer | STANTN_2_STAGT2 | AMBIENT_DUE_TO_TEMP | 9.6833
2022 | nonsummer | STANTN_2_STAGT2 | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | STANTN_2_STAGT2 | PLANT_MAINTENANCE | 297.9
2022 | nonsummer | STANTN_2_STAGT2 | PLANT_TROUBLE | 49.65
2022 | nonsummer | STIGCT_2_LODI | AMBIENT_DUE_TO_TEMP | 3679
2022 | nonsummer | STIGCT_2_LODI | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | STIGCT_2_LODI | PLANT_TROUBLE | 685.922
2022 | nonsummer | STNRES_1_UNIT | PLANT_MAINTENANCE | 3898.1
2022 | nonsummer | STNRES_1_UNIT | PLANT_TROUBLE | 199
2022 | nonsummer | STOILS_1_UNITS | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | STOILS_1_UNITS | PLANT_MAINTENANCE | 0
2022 | nonsummer | STOILS_1_UNITS | PLANT_TROUBLE | 0
2022 | nonsummer | STROUD_6_SOLAR | PLANT_MAINTENANCE | 540
2022 | nonsummer | STROUD_6_SOLAR | PLANT_TROUBLE | 2843.3333
2022 | nonsummer | STROUD_6_SOLAR | TRANSMISSION_INDUCED | 0
2022 | nonsummer | STROUD_6_WWHSR1 | PLANT_TROUBLE | 231.75
2022 | nonsummer | SUMWHT_6_SWSSR1 | PLANT_MAINTENANCE | 41.5917
2022 | nonsummer | SUMWHT_6_SWSSR1 | PLANT_TROUBLE | 2149.9817
2022 | nonsummer | SUNCAT_2_A1ABT1 | NEW_GENERATOR_TEST_ENERGY | 0
2022 | nonsummer | SUNCAT_2_A1ABT1 | PLANT_TROUBLE | 5299.0867
2022 | nonsummer | SUNCAT_2_A1BBT1 | NEW_GENERATOR_TEST_ENERGY | 0
2022 | nonsummer | SUNCAT_2_A1BBT1 | PLANT_TROUBLE | 4565.6217
2022 | nonsummer | SUNCAT_2_A1BBT1 | UNIT_TESTING | 126
2022 | nonsummer | SUNCAT_2_A2ABT2 | NEW_GENERATOR_TEST_ENERGY | 0
2022 | nonsummer | SUNCAT_2_A2ABT2 | PLANT_MAINTENANCE | 0
2022 | nonsummer | SUNCAT_2_A2ABT2 | PLANT_TROUBLE | 7619.565
2022 | nonsummer | SUNCAT_2_A2ABT2 | UNIT_TESTING | 0
2022 | nonsummer | SUNRIS_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 30698.3167
2022 | nonsummer | SUNRIS_2_PL1X3 | METERING_TELEMETRY | 0
2022 | nonsummer | SUNRIS_2_PL1X3 | PLANT_MAINTENANCE | 18710.7
2022 | nonsummer | SUNRIS_2_PL1X3 | PLANT_TROUBLE | 3823.4667
2022 | nonsummer | SUNSET_2_UNITS | AMBIENT_DUE_TO_TEMP | 7730
2022 | nonsummer | SUNSET_2_UNITS | MONTHLY_USE_LIMIT_REACHED | 54808.3333
2022 | nonsummer | SUNSET_2_UNITS | PLANT_MAINTENANCE | 758.3333
2022 | nonsummer | SUNSET_2_UNITS | PLANT_TROUBLE | 264.85
2022 | nonsummer | SUNSHN_2_LNDFL | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2022 | nonsummer | SUNSHN_2_LNDFL | AMBIENT_DUE_TO_TEMP | 7.3467
2022 | nonsummer | SUNSHN_2_LNDFL | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | SUNSHN_2_LNDFL | PLANT_MAINTENANCE | 762.42
2022 | nonsummer | SUNSHN_2_LNDFL | PLANT_TROUBLE | 232.31
2022 | nonsummer | SUNSHN_2_LNDFL | TRANSMISSION_INDUCED | 0
2022 | nonsummer | SUNSLR_1_SSVSR1 | PLANT_MAINTENANCE | 400
2022 | nonsummer | SUNSLR_1_SSVSR1 | PLANT_TROUBLE | 0
2022 | nonsummer | SUNSPT_2_WNASR1 | PLANT_MAINTENANCE | 79.3333
2022 | nonsummer | SUNSPT_2_WNASR1 | PLANT_TROUBLE | 0
2022 | nonsummer | SUNST2_5_SS2SR1 | PLANT_MAINTENANCE | 1545.5
2022 | nonsummer | SUNST2_5_SS2SR1 | PLANT_TROUBLE | 1106.6
2022 | nonsummer | SUNST2_5_SS2SR1 | TRANSMISSION_INDUCED | 300
2022 | nonsummer | SUNSTR_5_SS1SCEDYN | PLANT_MAINTENANCE | 584.7047
2022 | nonsummer | SUTTER_2_CISO | AMBIENT_DUE_TO_TEMP | 2284.0333
2022 | nonsummer | SUTTER_2_CISO | PLANT_MAINTENANCE | 26125
2022 | nonsummer | SUTTER_2_CISO | PLANT_TROUBLE | 11979.5667
2022 | nonsummer | SUTTER_2_CISO | RTU_RIG | 0
2022 | nonsummer | SUTTER_2_CISO | TRANSITIONAL_LIMITATION | 93.99
2022 | nonsummer | SUTTER_2_CISO | TRANSMISSION_INDUCED | 0
2022 | nonsummer | SUTTER_2_CISO | UNIT_TESTING | 0
2022 | nonsummer | SYCAMR_2_UNIT 1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 740
2022 | nonsummer | SYCAMR_2_UNIT 1 | PLANT_MAINTENANCE | 2000
2022 | nonsummer | SYCAMR_2_UNIT 1 | PLANT_TROUBLE | 2905.7333
2022 | nonsummer | SYCAMR_2_UNIT 1 | UNIT_TESTING | 0
2022 | nonsummer | SYCAMR_2_UNIT 2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 760
2022 | nonsummer | SYCAMR_2_UNIT 2 | PLANT_MAINTENANCE | 1480
2022 | nonsummer | SYCAMR_2_UNIT 2 | PLANT_TROUBLE | 2098
2022 | nonsummer | SYCAMR_2_UNIT 2 | RTU_RIG | 0
2022 | nonsummer | SYCAMR_2_UNIT 2 | UNIT_TESTING | 0
2022 | nonsummer | SYCAMR_2_UNIT 3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 740
2022 | nonsummer | SYCAMR_2_UNIT 3 | PLANT_TROUBLE | 3880.7667
2022 | nonsummer | SYCAMR_2_UNIT 3 | UNIT_TESTING | 0
2022 | nonsummer | SYCAMR_2_UNIT 4 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 760
2022 | nonsummer | SYCAMR_2_UNIT 4 | PLANT_MAINTENANCE | 1095
2022 | nonsummer | SYCAMR_2_UNIT 4 | PLANT_TROUBLE | 11611.7667
2022 | nonsummer | SYCAMR_2_UNIT 4 | RTU_RIG | 0
2022 | nonsummer | SYCAMR_2_UNIT 4 | UNIT_TESTING | 0
2022 | nonsummer | TANHIL_6_SOLART | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | TANHIL_6_SOLART | PLANT_MAINTENANCE | 13.0833
2022 | nonsummer | TANHIL_6_SOLART | PLANT_TROUBLE | 499.2833
2022 | nonsummer | TANHIL_6_SOLART | TRANSMISSION_INDUCED | 0
2022 | nonsummer | TBLMTN_6_QF | AMBIENT_NOT_DUE_TO_TEMP | 25.5
2022 | nonsummer | TBLMTN_6_QF | PLANT_MAINTENANCE | 25.5
2022 | nonsummer | TBLMTN_6_QF | PLANT_TROUBLE | 35.275
2022 | nonsummer | TBLMTN_6_QF | TRANSMISSION_INDUCED | 8.5
2022 | nonsummer | TBLMTN_6_QF | UNIT_TESTING | 0
2022 | nonsummer | TECOLOTE_3_WBDYN | PLANT_MAINTENANCE | 840
2022 | nonsummer | TECOLOTE_3_WBDYN | PLANT_TROUBLE | 0
2022 | nonsummer | TECOLOTE_3_WBDYN | TRANSMISSION_INDUCED | 56387.44
2022 | nonsummer | TEHAPI_2_PW1WD1 | PLANT_MAINTENANCE | 79.9415
2022 | nonsummer | TEHAPI_2_PW1WD1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | TEHAPI_2_PW2WD2 | PLANT_MAINTENANCE | 59.16
2022 | nonsummer | TEHAPI_2_PW2WD2 | TRANSMISSION_INDUCED | 67.4137
2022 | nonsummer | TEHAPI_2_WIND1 | METERING_TELEMETRY | 0
2022 | nonsummer | TEHAPI_2_WIND1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | TEHAPI_2_WIND1 | PLANT_TROUBLE | 0
2022 | nonsummer | TEHAPI_2_WIND1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | TEHAPI_2_WIND2 | PLANT_MAINTENANCE | 0
2022 | nonsummer | TEHAPI_2_WIND2 | PLANT_TROUBLE | 0
2022 | nonsummer | TEHAPI_2_WIND2 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | TENGEN_2_PL1X2 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | TENGEN_2_PL1X2 | PLANT_MAINTENANCE | 8029.5
2022 | nonsummer | TENGEN_2_PL1X2 | PLANT_TROUBLE | 0
2022 | nonsummer | TENGEN_2_PL1X2 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | TENGEN_2_PL1X2 | UNIT_TESTING | 704
2022 | nonsummer | TERMEX_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 4340
2022 | nonsummer | TERMEX_2_PL1X3 | PLANT_MAINTENANCE | 18750
2022 | nonsummer | TERMEX_2_PL1X3 | PLANT_TROUBLE | 8507.6667
2022 | nonsummer | TERMEX_2_PL1X3 | UNIT_TESTING | 4593.3333
2022 | nonsummer | TIDWTR_2_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 1062
2022 | nonsummer | TIDWTR_2_UNITS | PLANT_MAINTENANCE | 16248.88
2022 | nonsummer | TIDWTR_2_UNITS | PLANT_TROUBLE | 5908
2022 | nonsummer | TIFFNY_1_DILLON | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | TIFFNY_1_DILLON | METERING_TELEMETRY | 5
2022 | nonsummer | TIFFNY_1_DILLON | PLANT_MAINTENANCE | 474
2022 | nonsummer | TIFFNY_1_DILLON | PLANT_TROUBLE | 915.5833
2022 | nonsummer | TIFFNY_1_DILLON | TRANSMISSION_INDUCED | 130.845
2022 | nonsummer | TIGRCK_7_UNITS | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | TIGRCK_7_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 628.775
2022 | nonsummer | TIGRCK_7_UNITS | PLANT_MAINTENANCE | 0
2022 | nonsummer | TIGRCK_7_UNITS | PLANT_TROUBLE | 134.4083
2022 | nonsummer | TIGRCK_7_UNITS | TRANSMISSION_INDUCED | 93
2022 | nonsummer | TITANS_2_TTSSR1 | PLANT_MAINTENANCE | 682.5
2022 | nonsummer | TITANS_2_TTSSR1 | PLANT_TROUBLE | 0
2022 | nonsummer | TITANS_2_TTSSR1 | TRANSITIONAL_LIMITATION | 132
2022 | nonsummer | TITANS_2_TTSSR1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | TKOPWR_6_HYDRO | PLANT_TROUBLE | 69.9
2022 | nonsummer | TOADTW_6_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 57.375
2022 | nonsummer | TOADTW_6_UNIT | ENVIRONMENTAL_RESTRICTIONS | 15
2022 | nonsummer | TOADTW_6_UNIT | PLANT_TROUBLE | 4.8
2022 | nonsummer | TOADTW_6_UNIT | TRANSMISSION_INDUCED | 19.6
2022 | nonsummer | TOPAZ_2_SOLAR | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | TOPAZ_2_SOLAR | PLANT_MAINTENANCE | 396.4117
2022 | nonsummer | TOPAZ_2_SOLAR | PLANT_TROUBLE | 3710
2022 | nonsummer | TORTLA_1_SOLAR | PLANT_MAINTENANCE | 0
2022 | nonsummer | TORTLA_1_SOLAR | PLANT_TROUBLE | 100
2022 | nonsummer | TOWNSITE_2_MEADDYN | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 261
2022 | nonsummer | TOWNSITE_2_MEADDYN | METERING_TELEMETRY | 240
2022 | nonsummer | TOWNSITE_2_MEADDYN | PLANT_MAINTENANCE | 2237.8
2022 | nonsummer | TOWNSITE_2_MEADDYN | PLANT_TROUBLE | 6220.6
2022 | nonsummer | TOWNSITE_2_MEADDYN | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 315
2022 | nonsummer | TOWNSITE_2_MEADDYN | UNIT_TESTING | 3218.44
2022 | nonsummer | TRNQL8_2_AMASR1 | AMBIENT_NOT_DUE_TO_TEMP | 60
2022 | nonsummer | TRNQL8_2_AMASR1 | PLANT_MAINTENANCE | 188.3333
2022 | nonsummer | TRNQL8_2_AZUSR1 | PLANT_MAINTENANCE | 70
2022 | nonsummer | TRNQL8_2_ROJSR1 | PLANT_MAINTENANCE | 959.375
2022 | nonsummer | TRNQL8_2_ROJSR1 | PLANT_TROUBLE | 4845
2022 | nonsummer | TRNQL8_2_VERSR1 | PLANT_MAINTENANCE | 210
2022 | nonsummer | TRNQL8_2_VERSR1 | PLANT_TROUBLE | 603
2022 | nonsummer | TRNQLT_2_RETBT1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | TRNQLT_2_RETBT1 | METERING_TELEMETRY | 144
2022 | nonsummer | TRNQLT_2_RETBT1 | NEW_GENERATOR_TEST_ENERGY | 0
2022 | nonsummer | TRNQLT_2_RETBT1 | PLANT_MAINTENANCE | 518.4
2022 | nonsummer | TRNQLT_2_RETBT1 | PLANT_TROUBLE | 7051.2883
2022 | nonsummer | TRNQLT_2_RETBT1 | UNIT_TESTING | 0
2022 | nonsummer | TRNQLT_2_SOLAR | METERING_TELEMETRY | 0
2022 | nonsummer | TRNQLT_2_SOLAR | NEW_GENERATOR_TEST_ENERGY | 876
2022 | nonsummer | TRNQLT_2_SOLAR | PLANT_MAINTENANCE | 4674.125
2022 | nonsummer | TRNQLT_2_SOLAR | PLANT_TROUBLE | 2384.75
2022 | nonsummer | TRNQLT_2_SOLAR | UNIT_TESTING | 2096
2022 | nonsummer | TRNSWD_1_QF | AMBIENT_DUE_TO_TEMP | 31.5
2022 | nonsummer | TRNSWD_1_QF | AMBIENT_NOT_DUE_TO_TEMP | 56.2625
2022 | nonsummer | TRNSWD_1_QF | PLANT_MAINTENANCE | 0
2022 | nonsummer | TRNSWD_1_QF | PLANT_TROUBLE | 31889.55
2022 | nonsummer | TRNSWD_1_QF | TRANSMISSION_INDUCED | 0
2022 | nonsummer | TULEWD_1_TULWD1 | AMBIENT_DUE_TO_TEMP | 184.525
2022 | nonsummer | TULEWD_1_TULWD1 | AMBIENT_NOT_DUE_TO_TEMP | 454
2022 | nonsummer | TULEWD_1_TULWD1 | METERING_TELEMETRY | 22.5
2022 | nonsummer | TULEWD_1_TULWD1 | PLANT_TROUBLE | 311.25
2022 | nonsummer | TULEWD_1_TULWD1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | TULEWD_1_TULWD1 | UNIT_TESTING | 0
2022 | nonsummer | TULLCK_7_UNITS | PLANT_TROUBLE | 0
2022 | nonsummer | TULLCK_7_UNITS | TRANSMISSION_INDUCED | 0
2022 | nonsummer | TVYVLY_6_KRSHY1 | AMBIENT_NOT_DUE_TO_TEMP | 422.5
2022 | nonsummer | TVYVLY_6_KRSHY1 | ENVIRONMENTAL_RESTRICTIONS | 123.5
2022 | nonsummer | TVYVLY_6_KRSHY1 | PLANT_TROUBLE | 0
2022 | nonsummer | TWISSL_6_SOLAR1 | METERING_TELEMETRY | 30
2022 | nonsummer | TWISSL_6_SOLAR1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | TWISSL_6_SOLAR1 | PLANT_TROUBLE | 88.5
2022 | nonsummer | TWISSL_6_SOLAR1 | TRANSMISSION_INDUCED | 80
2022 | nonsummer | TX-ELK_6_ECKSR2 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | TX-ELK_6_SOLAR1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | TXMCKT_6_UNIT | METERING_TELEMETRY | 124
2022 | nonsummer | TXMCKT_6_UNIT | PLANT_MAINTENANCE | 597.3233
2022 | nonsummer | TXMCKT_6_UNIT | PLANT_TROUBLE | 104.8333
2022 | nonsummer | TXMCKT_6_UNIT | TRANSMISSION_INDUCED | 11.2
2022 | nonsummer | UKIAH_7_LAKEMN | AMBIENT_NOT_DUE_TO_TEMP | 840
2022 | nonsummer | UKIAH_7_LAKEMN | METERING_TELEMETRY | 0
2022 | nonsummer | UKIAH_7_LAKEMN | PLANT_TROUBLE | 124.6667
2022 | nonsummer | UKIAH_7_LAKEMN | RTU_RIG | 227.5
2022 | nonsummer | UKIAH_7_LAKEMN | TRANSMISSION_INDUCED | 0
2022 | nonsummer | ULTPCH_1_UNIT 1 | METERING_TELEMETRY | 0
2022 | nonsummer | ULTPCH_1_UNIT 1 | PLANT_MAINTENANCE | 360
2022 | nonsummer | ULTPCH_1_UNIT 1 | PLANT_TROUBLE | 393
2022 | nonsummer | ULTPCH_1_UNIT 1 | TRANSMISSION_INDUCED | 270
2022 | nonsummer | ULTPFR_1_UNIT 1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2022 | nonsummer | ULTPFR_1_UNIT 1 | METERING_TELEMETRY | 0
2022 | nonsummer | ULTPFR_1_UNIT 1 | PLANT_MAINTENANCE | 2388.105
2022 | nonsummer | ULTPFR_1_UNIT 1 | PLANT_TROUBLE | 4489.098
2022 | nonsummer | ULTPFR_1_UNIT 1 | TRANSMISSION_INDUCED | 5.5
2022 | nonsummer | ULTRCK_2_UNIT | ENVIRONMENTAL_RESTRICTIONS | 41.5
2022 | nonsummer | ULTRCK_2_UNIT | PLANT_MAINTENANCE | 264.3333
2022 | nonsummer | ULTRCK_2_UNIT | PLANT_TROUBLE | 1462.75
2022 | nonsummer | ULTRCK_2_UNIT | UNIT_TESTING | 0
2022 | nonsummer | UNCHEM_1_UNIT | PLANT_MAINTENANCE | 180
2022 | nonsummer | UNCHEM_1_UNIT | PLANT_TROUBLE | 1250
2022 | nonsummer | UNVRSY_1_UNIT 1 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | UNVRSY_1_UNIT 1 | PLANT_MAINTENANCE | 1710
2022 | nonsummer | UNVRSY_1_UNIT 1 | PLANT_TROUBLE | 1710
2022 | nonsummer | UNVRSY_1_UNIT 1 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2022 | nonsummer | USWND2_1_WIND1 | METERING_TELEMETRY | 10.85
2022 | nonsummer | USWND2_1_WIND1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | USWND2_1_WIND1 | PLANT_TROUBLE | 2454.1345
2022 | nonsummer | USWND2_1_WIND1 | TRANSMISSION_INDUCED | 179
2022 | nonsummer | USWND2_1_WIND2 | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | USWND2_1_WIND2 | METERING_TELEMETRY | 0
2022 | nonsummer | USWND2_1_WIND2 | PLANT_MAINTENANCE | 1200.8812
2022 | nonsummer | USWND2_1_WIND2 | PLANT_TROUBLE | 307.6115
2022 | nonsummer | USWND2_1_WIND2 | TRANSMISSION_INDUCED | 214.8
2022 | nonsummer | USWND2_1_WIND3 | PLANT_MAINTENANCE | 155.35
2022 | nonsummer | USWND2_1_WIND3 | PLANT_TROUBLE | 4283.4257
2022 | nonsummer | USWND2_1_WIND3 | RTU_RIG | 0
2022 | nonsummer | USWND2_1_WIND3 | TRANSMISSION_INDUCED | 218.5
2022 | nonsummer | USWNDR_2_LABWD1 | PLANT_MAINTENANCE | 593.025
2022 | nonsummer | USWNDR_2_LABWD1 | PLANT_TROUBLE | 567.575
2022 | nonsummer | USWNDR_2_LABWD1 | TRANSMISSION_INDUCED | 333
2022 | nonsummer | USWNDR_2_SMUD | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 12751.32
2022 | nonsummer | USWNDR_2_SMUD | PLANT_MAINTENANCE | 0
2022 | nonsummer | USWNDR_2_SMUD | PLANT_TROUBLE | 56.7
2022 | nonsummer | USWNDR_2_SMUD | TRANSMISSION_INDUCED | 0
2022 | nonsummer | USWNDR_2_SMUD2 | PLANT_MAINTENANCE | 8034.4
2022 | nonsummer | USWNDR_2_SMUD2 | PLANT_TROUBLE | 0
2022 | nonsummer | USWNDR_2_SMUD2 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | USWPFK_6_FRICK | METERING_TELEMETRY | 0
2022 | nonsummer | USWPFK_6_FRICK | PLANT_MAINTENANCE | 10
2022 | nonsummer | USWPFK_6_FRICK | PLANT_TROUBLE | 0
2022 | nonsummer | USWPFK_6_FRICK | TRANSMISSION_INDUCED | 127.8333
2022 | nonsummer | USWPJR_2_UNITS | PLANT_MAINTENANCE | 487.5267
2022 | nonsummer | USWPJR_2_UNITS | PLANT_TROUBLE | 5.8267
2022 | nonsummer | USWPJR_2_UNITS | TRANSMISSION_INDUCED | 287.5
2022 | nonsummer | VACADX_1_SOLAR | PLANT_MAINTENANCE | 0
2022 | nonsummer | VACADX_1_UNITA1 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | VACADX_1_UNITA1 | PLANT_MAINTENANCE | 1038.2
2022 | nonsummer | VACADX_1_UNITA1 | PLANT_TROUBLE | 1415.393
2022 | nonsummer | VACADX_1_UNITA1 | TRANSMISSION_INDUCED | 16.0265
2022 | nonsummer | VACADX_1_UNITA1 | UNIT_TESTING | 0
2022 | nonsummer | VALLEY_5_PERRIS | AMBIENT_NOT_DUE_TO_TEMP | 8376.7
2022 | nonsummer | VALLEY_5_REDMTN | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2022 | nonsummer | VALLEY_5_REDMTN | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | VALLEY_5_REDMTN | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | VALLEY_5_REDMTN | ENVIRONMENTAL_RESTRICTIONS | 32.0567
2022 | nonsummer | VALLEY_5_REDMTN | PLANT_TROUBLE | 413
2022 | nonsummer | VALLEY_5_REDMTN | TRANSMISSION_INDUCED | 0
2022 | nonsummer | VALLEY_5_REDMTN | UNIT_TESTING | 0
2022 | nonsummer | VALLEY_5_SOLAR2 | PLANT_TROUBLE | 150
2022 | nonsummer | VALTNE_2_AVASR1 | PLANT_MAINTENANCE | 238.6667
2022 | nonsummer | VALTNE_2_AVASR1 | PLANT_TROUBLE | 0
2022 | nonsummer | VALTNE_2_TBBBT1 | NEW_GENERATOR_TEST_ENERGY | 0
2022 | nonsummer | VALTNE_2_TBBBT1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | VALTNE_2_TBBBT1 | PLANT_TROUBLE | 0
2022 | nonsummer | VALTNE_2_TRSBT1 | NEW_GENERATOR_TEST_ENERGY | 0
2022 | nonsummer | VALTNE_2_TRSBT1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | VALTNE_2_TRSBT1 | PLANT_TROUBLE | 0
2022 | nonsummer | VEDDER_1_SEKERN | PLANT_MAINTENANCE | 110
2022 | nonsummer | VEDDER_1_SEKERN | PLANT_TROUBLE | 13155.85
2022 | nonsummer | VEDDER_1_SEKERN | TRANSMISSION_INDUCED | 0
2022 | nonsummer | VEGA_6_SOLAR1 | PLANT_MAINTENANCE | 80
2022 | nonsummer | VENWD_1_WIND3 | PLANT_MAINTENANCE | 800.235
2022 | nonsummer | VENWD_1_WIND3 | PLANT_TROUBLE | 0
2022 | nonsummer | VENWD_1_WIND3 | TRANSMISSION_INDUCED | 27.0032
2022 | nonsummer | VERNON_6_GONZL1 | PLANT_TROUBLE | 6066.25
2022 | nonsummer | VERNON_6_GONZL2 | ANNUAL_USE_LIMIT_REACHED | 0
2022 | nonsummer | VERNON_6_GONZL2 | METERING_TELEMETRY | 0
2022 | nonsummer | VERNON_6_GONZL2 | OTHER_USE_LIMIT_REACHED | 0
2022 | nonsummer | VERNON_6_GONZL2 | PLANT_MAINTENANCE | 201.25
2022 | nonsummer | VERNON_6_GONZL2 | SHORT_TERM_USE_LIMIT_REACHED | 0.19167
2022 | nonsummer | VERNON_6_GONZL2 | UNIT_TESTING | 0
2022 | nonsummer | VERNON_6_MALBRG | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | VERNON_6_MALBRG | PLANT_MAINTENANCE | 22108.5
2022 | nonsummer | VERNON_6_MALBRG | PLANT_TROUBLE | 638.4
2022 | nonsummer | VERNON_6_MALBRG | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 227.8
2022 | nonsummer | VERNON_6_MALBRG | UNIT_SUPPORTING_STARTUP | 0
2022 | nonsummer | VERNON_6_MALBRG | UNIT_TESTING | 186
2022 | nonsummer | VESTAL_2_KERN | AMBIENT_NOT_DUE_TO_TEMP | 19667
2022 | nonsummer | VESTAL_2_KERN | PLANT_TROUBLE | 4220
2022 | nonsummer | VESTAL_2_SOLAR1 | METERING_TELEMETRY | 600
2022 | nonsummer | VESTAL_2_SOLAR1 | PLANT_MAINTENANCE | 12
2022 | nonsummer | VESTAL_2_SOLAR1 | PLANT_TROUBLE | 298
2022 | nonsummer | VESTAL_2_SOLAR1 | TRANSMISSION_INDUCED | 300
2022 | nonsummer | VESTAL_2_SOLAR2 | METERING_TELEMETRY | 0
2022 | nonsummer | VESTAL_2_SOLAR2 | PLANT_MAINTENANCE | 8.4
2022 | nonsummer | VESTAL_2_SOLAR2 | PLANT_TROUBLE | 1260
2022 | nonsummer | VESTAL_2_SOLAR2 | TRANSMISSION_INDUCED | 210
2022 | nonsummer | VESTAL_2_TS5SR1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | VESTAL_2_TS5SR1 | PLANT_TROUBLE | 333.3
2022 | nonsummer | VESTAL_2_TS5SR1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | VESTAL_2_WELLHD | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | VESTAL_2_WELLHD | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | VESTAL_2_WELLHD | PLANT_MAINTENANCE | 735
2022 | nonsummer | VESTAL_2_WELLHD | PLANT_TROUBLE | 3402.2333
2022 | nonsummer | VESTAL_6_QF | AMBIENT_NOT_DUE_TO_TEMP | 12486.75
2022 | nonsummer | VESTAL_6_QF | PLANT_TROUBLE | 42.5917
2022 | nonsummer | VICTOR_1_CREST | PLANT_TROUBLE | 908.5542
2022 | nonsummer | VICTOR_1_CREST | TRANSMISSION_INDUCED | 0
2022 | nonsummer | VICTOR_1_EXSLRA | PLANT_MAINTENANCE | 6.5
2022 | nonsummer | VICTOR_1_EXSLRA | PLANT_TROUBLE | 10
2022 | nonsummer | VICTOR_1_EXSLRA | TRANSMISSION_INDUCED | 0
2022 | nonsummer | VICTOR_1_EXSLRB | PLANT_MAINTENANCE | 0
2022 | nonsummer | VICTOR_1_EXSLRB | PLANT_TROUBLE | 16.4667
2022 | nonsummer | VICTOR_1_EXSLRB | TRANSMISSION_INDUCED | 0
2022 | nonsummer | VICTOR_1_LVSLR1 | PLANT_MAINTENANCE | 19.8333
2022 | nonsummer | VICTOR_1_LVSLR1 | PLANT_TROUBLE | 0
2022 | nonsummer | VICTOR_1_LVSLR1 | TRANSMISSION_INDUCED | 42.3333
2022 | nonsummer | VICTOR_1_LVSLR2 | PLANT_MAINTENANCE | 200
2022 | nonsummer | VICTOR_1_LVSLR2 | PLANT_TROUBLE | 85
2022 | nonsummer | VICTOR_1_LVSLR2 | TRANSMISSION_INDUCED | 84.6667
2022 | nonsummer | VICTOR_1_SOLAR1 | METERING_TELEMETRY | 630
2022 | nonsummer | VICTOR_1_SOLAR1 | PLANT_MAINTENANCE | 219.625
2022 | nonsummer | VICTOR_1_SOLAR1 | PLANT_TROUBLE | 31.7917
2022 | nonsummer | VICTOR_1_SOLAR2 | PLANT_TROUBLE | 94.3
2022 | nonsummer | VICTOR_1_SOLAR2 | TRANSMISSION_INDUCED | 83.3333
2022 | nonsummer | VICTOR_1_SOLAR3 | PLANT_MAINTENANCE | 35
2022 | nonsummer | VICTOR_1_SOLAR3 | PLANT_TROUBLE | 0
2022 | nonsummer | VICTOR_1_SOLAR3 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | VICTOR_1_SOLAR4 | PLANT_MAINTENANCE | 100
2022 | nonsummer | VICTOR_1_SOLAR4 | PLANT_TROUBLE | 16.6667
2022 | nonsummer | VICTOR_1_SOLAR4 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | VICTOR_1_VDRYFA | PLANT_MAINTENANCE | 12.6167
2022 | nonsummer | VICTOR_1_VDRYFA | PLANT_TROUBLE | 18
2022 | nonsummer | VICTOR_1_VDRYFB | PLANT_MAINTENANCE | 5.1
2022 | nonsummer | VICTOR_1_VDRYFB | PLANT_TROUBLE | 74.3833
2022 | nonsummer | VILLPK_2_VALLYV | AMBIENT_NOT_DUE_TO_TEMP | 4325.5
2022 | nonsummer | VILLPK_6_MWDYOR | PLANT_TROUBLE | 25.5
2022 | nonsummer | VISTRA_5_DALBT1 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | VISTRA_5_DALBT1 | METERING_TELEMETRY | 2000
2022 | nonsummer | VISTRA_5_DALBT1 | PLANT_MAINTENANCE | 48071
2022 | nonsummer | VISTRA_5_DALBT1 | PLANT_TROUBLE | 5851.5167
2022 | nonsummer | VISTRA_5_DALBT1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | VISTRA_5_DALBT2 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | VISTRA_5_DALBT2 | PLANT_MAINTENANCE | 0
2022 | nonsummer | VISTRA_5_DALBT2 | PLANT_TROUBLE | 1825.0333
2022 | nonsummer | VISTRA_5_DALBT2 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | VISTRA_5_DALBT3 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | VISTRA_5_DALBT3 | PLANT_MAINTENANCE | 0
2022 | nonsummer | VISTRA_5_DALBT3 | PLANT_TROUBLE | 2062.6333
2022 | nonsummer | VISTRA_5_DALBT3 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | VISTRA_5_DALBT4 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | VISTRA_5_DALBT4 | METERING_TELEMETRY | 4500
2022 | nonsummer | VISTRA_5_DALBT4 | PLANT_MAINTENANCE | 0
2022 | nonsummer | VISTRA_5_DALBT4 | PLANT_TROUBLE | 48728.6833
2022 | nonsummer | VISTRA_5_DALBT4 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | VLCNTR_6_VCEBT1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | VLCNTR_6_VCEBT1 | PLANT_TROUBLE | 2544.9333
2022 | nonsummer | VLCNTR_6_VCEBT1 | TRANSMISSION_INDUCED | 128.45
2022 | nonsummer | VLCNTR_6_VCEBT2 | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | VLCNTR_6_VCEBT2 | METERING_TELEMETRY | 0
2022 | nonsummer | VLCNTR_6_VCEBT2 | PLANT_MAINTENANCE | 3489.6667
2022 | nonsummer | VLCNTR_6_VCEBT2 | PLANT_TROUBLE | 3928.5833
2022 | nonsummer | VLCNTR_6_VCEBT2 | TRANSMISSION_INDUCED | 238.5
2022 | nonsummer | VLCNTR_6_VCEBT2 | UNIT_TESTING | 0
2022 | nonsummer | VLCNTR_6_VCSLR1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | VLCNTR_6_VCSLR2 | PLANT_MAINTENANCE | 0
2022 | nonsummer | VOLTA_2_UNIT 1 | PLANT_MAINTENANCE | 4140.5
2022 | nonsummer | VOLTA_2_UNIT 1 | PLANT_TROUBLE | 2184
2022 | nonsummer | VOLTA_2_UNIT 2 | PLANT_TROUBLE | 85
2022 | nonsummer | VOLTA_2_UNIT 2 | TRANSMISSION_INDUCED | 6.95
2022 | nonsummer | VOLTA_6_BAILCK | AMBIENT_NOT_DUE_TO_TEMP | 602.85
2022 | nonsummer | VOLTA_6_BAILCK | TRANSMISSION_INDUCED | 3.47
2022 | nonsummer | VOLTA_6_DIGHYD | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | VOLTA_6_DIGHYD | PLANT_TROUBLE | 8.3
2022 | nonsummer | VOLTA_6_DIGHYD | TRANSMISSION_INDUCED | 38.36
2022 | nonsummer | VOLTA_7_PONHY1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 368.75
2022 | nonsummer | VOLTA_7_PONHY1 | AMBIENT_NOT_DUE_TO_TEMP | 426.8958
2022 | nonsummer | VOLTA_7_PONHY1 | PLANT_TROUBLE | 0
2022 | nonsummer | VOYAGR_2_VOAWD5 | METERING_TELEMETRY | 7.2
2022 | nonsummer | VOYAGR_2_VOAWD5 | PLANT_TROUBLE | 69.9
2022 | nonsummer | VOYAGR_2_VOAWD5 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | VOYAGR_2_VOYWD1 | TRANSMISSION_INDUCED | 232.038
2022 | nonsummer | VOYAGR_2_VOYWD2 | METERING_TELEMETRY | 1.75
2022 | nonsummer | VOYAGR_2_VOYWD2 | PLANT_MAINTENANCE | 0
2022 | nonsummer | VOYAGR_2_VOYWD2 | PLANT_TROUBLE | 0
2022 | nonsummer | VOYAGR_2_VOYWD2 | TRANSMISSION_INDUCED | 206.3717
2022 | nonsummer | VOYAGR_2_VOYWD3 | METERING_TELEMETRY | 42
2022 | nonsummer | VOYAGR_2_VOYWD3 | PLANT_TROUBLE | 212.25
2022 | nonsummer | VOYAGR_2_VOYWD3 | TRANSMISSION_INDUCED | 91.5
2022 | nonsummer | VOYAGR_2_VOYWD4 | METERING_TELEMETRY | 12.4
2022 | nonsummer | VOYAGR_2_VOYWD4 | PLANT_TROUBLE | 695.01
2022 | nonsummer | VOYAGR_2_VOYWD4 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | VSTAES_6_VESBT1 | METERING_TELEMETRY | 0
2022 | nonsummer | VSTAES_6_VESBT1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | VSTAES_6_VESBT1 | PLANT_TROUBLE | 887.5
2022 | nonsummer | VSTAES_6_VESBT1 | TRANSMISSION_INDUCED | 40
2022 | nonsummer | WADHAM_6_UNIT | METERING_TELEMETRY | 0
2022 | nonsummer | WADHAM_6_UNIT | PLANT_TROUBLE | 465.6045
2022 | nonsummer | WALCRK_2_CTG1 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | WALCRK_2_CTG1 | OTHER_USE_LIMIT_REACHED | 1172.706
2022 | nonsummer | WALCRK_2_CTG1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | WALCRK_2_CTG1 | PLANT_TROUBLE | 849.928
2022 | nonsummer | WALCRK_2_CTG1 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2022 | nonsummer | WALCRK_2_CTG2 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | WALCRK_2_CTG2 | METERING_TELEMETRY | 0
2022 | nonsummer | WALCRK_2_CTG2 | OTHER_USE_LIMIT_REACHED | 104.9858
2022 | nonsummer | WALCRK_2_CTG2 | PLANT_MAINTENANCE | 0
2022 | nonsummer | WALCRK_2_CTG2 | PLANT_TROUBLE | 31504.484
2022 | nonsummer | WALCRK_2_CTG2 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | WALCRK_2_CTG3 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | WALCRK_2_CTG3 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | WALCRK_2_CTG3 | METERING_TELEMETRY | 0
2022 | nonsummer | WALCRK_2_CTG3 | OTHER_USE_LIMIT_REACHED | 1029.3225
2022 | nonsummer | WALCRK_2_CTG3 | PLANT_MAINTENANCE | 74.0983
2022 | nonsummer | WALCRK_2_CTG3 | PLANT_TROUBLE | 599.23
2022 | nonsummer | WALCRK_2_CTG3 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | WALCRK_2_CTG4 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | WALCRK_2_CTG4 | OTHER_USE_LIMIT_REACHED | 553.84
2022 | nonsummer | WALCRK_2_CTG4 | PLANT_MAINTENANCE | 3381
2022 | nonsummer | WALCRK_2_CTG4 | PLANT_TROUBLE | 203.0567
2022 | nonsummer | WALCRK_2_CTG5 | ENVIRONMENTAL_RESTRICTIONS | 0
2022 | nonsummer | WALCRK_2_CTG5 | OTHER_USE_LIMIT_REACHED | 1021.2683
2022 | nonsummer | WALCRK_2_CTG5 | PLANT_MAINTENANCE | 0
2022 | nonsummer | WALCRK_2_CTG5 | PLANT_TROUBLE | 558.9592
2022 | nonsummer | WALCRK_2_CTG5 | SHORT_TERM_USE_LIMIT_REACHED | 0
2022 | nonsummer | WALNUT_6_HILLGEN | PLANT_TROUBLE | 890.5833
2022 | nonsummer | WALNUT_6_HILLGEN | TRANSMISSION_INDUCED | 0
2022 | nonsummer | WALNUT_7_WCOVST | PLANT_MAINTENANCE | 383.5
2022 | nonsummer | WALNUT_7_WCOVST | PLANT_TROUBLE | 595.2833
2022 | nonsummer | WALNUT_7_WCOVST | TRANSMISSION_INDUCED | 260
2022 | nonsummer | WARNE_2_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | WARNE_2_UNIT | PLANT_TROUBLE | 104.5
2022 | nonsummer | WARNE_2_UNIT | TRANSMISSION_INDUCED | 22.8
2022 | nonsummer | WAUKNA_1_SOLAR | PLANT_MAINTENANCE | 50
2022 | nonsummer | WAUKNA_1_SOLAR | PLANT_TROUBLE | 0
2022 | nonsummer | WAUKNA_1_SOLAR | TRANSMISSION_INDUCED | 0
2022 | nonsummer | WAUKNA_1_SOLAR2 | TRANSMISSION_INDUCED | 98.75
2022 | nonsummer | WDLEAF_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 1187
2022 | nonsummer | WDLEAF_7_UNIT 1 | ENVIRONMENTAL_RESTRICTIONS | 45
2022 | nonsummer | WDLEAF_7_UNIT 1 | PLANT_TROUBLE | 100
2022 | nonsummer | WDLEAF_7_UNIT 1 | TRANSMISSION_INDUCED | 70
2022 | nonsummer | WEBER_6_FORWRD | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0.28
2022 | nonsummer | WEBER_6_FORWRD | PLANT_MAINTENANCE | 16.89
2022 | nonsummer | WEBER_6_FORWRD | PLANT_TROUBLE | 522.41
2022 | nonsummer | WEBER_6_FORWRD | TRANSMISSION_INDUCED | 0
2022 | nonsummer | WESTPT_2_UNIT | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | WESTPT_2_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 150.3067
2022 | nonsummer | WESTPT_2_UNIT | PLANT_TROUBLE | 46.4333
2022 | nonsummer | WESTPT_2_UNIT | TRANSMISSION_INDUCED | 22.1667
2022 | nonsummer | WFRESN_1_SOLAR | PLANT_TROUBLE | 457.5
2022 | nonsummer | WHEATL_6_LNDFIL | PLANT_MAINTENANCE | 71.75
2022 | nonsummer | WHEATL_6_LNDFIL | PLANT_TROUBLE | 51.0483
2022 | nonsummer | WHITEH_2_MEADDYN1 | PLANT_TROUBLE | 2597.292
2022 | nonsummer | WHITEH_2_MEADDYN2 | PLANT_TROUBLE | 8561.233
2022 | nonsummer | WHITNY_6_SOLAR | PLANT_TROUBLE | 10
2022 | nonsummer | WHTWTR_1_WINDA1 | METERING_TELEMETRY | 31.775
2022 | nonsummer | WHTWTR_1_WINDA1 | PLANT_MAINTENANCE | 11507.5
2022 | nonsummer | WHTWTR_1_WINDA1 | TRANSMISSION_INDUCED | 1928.725
2022 | nonsummer | WILLMS_6_ARBBM1 | NEW_GENERATOR_TEST_ENERGY | 0
2022 | nonsummer | WILLMS_6_ARBBM1 | PLANT_MAINTENANCE | 5.939
2022 | nonsummer | WILLMS_6_ARBBM1 | PLANT_TROUBLE | 70.12
2022 | nonsummer | WILLMS_6_ARBBM1 | UNIT_TESTING | 0
2022 | nonsummer | WISE_1_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 4026.78
2022 | nonsummer | WISE_1_UNIT 1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | WISE_1_UNIT 1 | PLANT_TROUBLE | 30.5867
2022 | nonsummer | WISE_1_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 3296
2022 | nonsummer | WISHON_6_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 3616.51
2022 | nonsummer | WISHON_6_UNITS | METERING_TELEMETRY | 0
2022 | nonsummer | WISHON_6_UNITS | PLANT_MAINTENANCE | 4610.3333
2022 | nonsummer | WISHON_6_UNITS | PLANT_TROUBLE | 1695.2
2022 | nonsummer | WISHON_6_UNITS | TRANSMISSION_INDUCED | 1229.55
2022 | nonsummer | WISTER_2_WISSR1 | NEW_GENERATOR_TEST_ENERGY | 0
2022 | nonsummer | WISTER_2_WISSR1 | PLANT_TROUBLE | 3280
2022 | nonsummer | WISTER_2_WISSR1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | WISTRA_2_WRSSR1 | PLANT_MAINTENANCE | 0
2022 | nonsummer | WISTRA_2_WRSSR1 | PLANT_TROUBLE | 280
2022 | nonsummer | WISTRA_2_WRSSR1 | TRANSMISSION_INDUCED | 200
2022 | nonsummer | WLDWD_1_SOLAR1 | PLANT_TROUBLE | 0
2022 | nonsummer | WLDWD_1_SOLAR1 | TRANSMISSION_INDUCED | 100
2022 | nonsummer | WLDWD_1_SOLAR2 | TRANSMISSION_INDUCED | 75
2022 | nonsummer | WNDMAS_2_UNIT 1 | PLANT_MAINTENANCE | 463.1333
2022 | nonsummer | WNDMAS_2_UNIT 1 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | WNDSTR_2_WIND | METERING_TELEMETRY | 324
2022 | nonsummer | WNDSTR_2_WIND | PLANT_MAINTENANCE | 4.3333
2022 | nonsummer | WOLFSK_1_UNITA1 | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | WOLFSK_1_UNITA1 | PLANT_TROUBLE | 5572.5017
2022 | nonsummer | WOODWR_1_HYDRO | METERING_TELEMETRY | 36.5
2022 | nonsummer | WOODWR_1_HYDRO | PLANT_TROUBLE | 31.6333
2022 | nonsummer | WRGTSR_2_WSFSR1 | METERING_TELEMETRY | 0
2022 | nonsummer | WRGTSR_2_WSFSR1 | PLANT_MAINTENANCE | 1531
2022 | nonsummer | WRGTSR_2_WSFSR1 | PLANT_TROUBLE | 6332.0033
2022 | nonsummer | WSENGY_1_UNIT 1 | PLANT_MAINTENANCE | 4315
2022 | nonsummer | WSENGY_1_UNIT 1 | PLANT_TROUBLE | 2918.2098
2022 | nonsummer | WSTWND_2_M89WD1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 566.1525
2022 | nonsummer | WSTWND_2_M89WD1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2022 | nonsummer | WSTWND_2_M89WD1 | PLANT_MAINTENANCE | 1418.825
2022 | nonsummer | WSTWND_2_M89WD1 | PLANT_TROUBLE | 986.3542
2022 | nonsummer | WSTWND_2_M89WD1 | TRANSMISSION_INDUCED | 82.65
2022 | nonsummer | WSTWND_2_M90WD2 | METERING_TELEMETRY | 64.82
2022 | nonsummer | WSTWND_2_M90WD2 | PLANT_MAINTENANCE | 1112.7433
2022 | nonsummer | WSTWND_2_M90WD2 | TRANSMISSION_INDUCED | 0
2022 | nonsummer | YUBACT_1_SUNSWT | AMBIENT_DUE_TO_TEMP | 0
2022 | nonsummer | YUBACT_1_SUNSWT | PLANT_MAINTENANCE | 1848.89
2022 | nonsummer | YUBACT_1_SUNSWT | PLANT_TROUBLE | 249.85
2022 | nonsummer | YUBACT_6_UNITA1 | AMBIENT_DUE_TO_TEMP | 13.044
2022 | nonsummer | YUBACT_6_UNITA1 | ENVIRONMENTAL_RESTRICTIONS | 8.82
2022 | nonsummer | YUBACT_6_UNITA1 | PLANT_TROUBLE | 278.5533
2022 | nonsummer | ZOND_6_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 18040.5
2023 | summer | ACACIA_6_SOLAR | METERING_TELEMETRY | 400
2023 | summer | ACACIA_6_SOLAR | PLANT_TROUBLE | 100
2023 | summer | ADERA_1_SOLAR1 | PLANT_TROUBLE | 557.5
2023 | summer | ADERA_1_SOLAR1 | TRANSMISSION_INDUCED | 0
2023 | summer | ADLIN_1_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 8631.71
2023 | summer | ADLIN_1_UNITS | PLANT_TROUBLE | 288.1622
2023 | summer | ADMEST_6_SOLAR | PLANT_TROUBLE | 2213.0667
2023 | summer | ADMEST_6_SOLAR | TRANSMISSION_INDUCED | 62
2023 | summer | AGRICO_6_PL3N5 | AMBIENT_DUE_TO_TEMP | 462.65
2023 | summer | AGRICO_6_PL3N5 | PLANT_MAINTENANCE | 0
2023 | summer | AGRICO_6_PL3N5 | PLANT_TROUBLE | 124.3895
2023 | summer | AGRICO_6_PL3N5 | UNIT_TESTING | 0
2023 | summer | AGRICO_7_UNIT | AMBIENT_DUE_TO_TEMP | 601.3032
2023 | summer | AGRICO_7_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 9.13
2023 | summer | AGRICO_7_UNIT | PLANT_MAINTENANCE | 0
2023 | summer | AGRICO_7_UNIT | UNIT_TESTING | 50.6
2023 | summer | AGUCAL_5_SOLAR1 | PLANT_TROUBLE | 0.33333
2023 | summer | AKINGS_6_AMESR1 | METERING_TELEMETRY | 0
2023 | summer | AKINGS_6_AMESR1 | PLANT_MAINTENANCE | 99.12
2023 | summer | AKINGS_6_AMESR1 | PLANT_TROUBLE | 1433.6667
2023 | summer | ALAMIT_2_PL1X3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1178
2023 | summer | ALAMIT_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 6557.5
2023 | summer | ALAMIT_2_PL1X3 | PLANT_TROUBLE | 2909.0525
2023 | summer | ALAMIT_2_PL1X3 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2023 | summer | ALAMIT_7_ES1 | METERING_TELEMETRY | 0
2023 | summer | ALAMIT_7_ES1 | PLANT_TROUBLE | 13612.3842
2023 | summer | ALAMIT_7_ES1 | UNIT_TESTING | 1939.7325
2023 | summer | ALAMIT_7_UNIT 3 | AMBIENT_DUE_TO_TEMP | 646
2023 | summer | ALAMIT_7_UNIT 3 | PLANT_TROUBLE | 20350.599
2023 | summer | ALAMIT_7_UNIT 3 | UNIT_SUPPORTING_STARTUP | 1072.8433
2023 | summer | ALAMIT_7_UNIT 3 | UNIT_TESTING | 0
2023 | summer | ALAMIT_7_UNIT 4 | AMBIENT_DUE_TO_TEMP | 886.5548
2023 | summer | ALAMIT_7_UNIT 4 | PLANT_TROUBLE | 19992.4895
2023 | summer | ALAMIT_7_UNIT 4 | UNIT_SUPPORTING_STARTUP | 103.67
2023 | summer | ALAMIT_7_UNIT 4 | UNIT_TESTING | 0
2023 | summer | ALAMIT_7_UNIT 5 | AMBIENT_DUE_TO_TEMP | 1948.3333
2023 | summer | ALAMIT_7_UNIT 5 | PLANT_TROUBLE | 13914.4167
2023 | summer | ALAMIT_7_UNIT 5 | UNIT_TESTING | 1130.9333
2023 | summer | ALAMO_6_UNIT | PLANT_TROUBLE | 27.2
2023 | summer | ALAMO_6_UNIT | TRANSMISSION_INDUCED | 85
2023 | summer | ALHMBR_1_ALHSLR | PLANT_MAINTENANCE | 0
2023 | summer | ALLGNY_6_HYDRO1 | TRANSMISSION_INDUCED | 49.712
2023 | summer | ALMASL_2_AL6BT6 | PLANT_MAINTENANCE | 6075
2023 | summer | ALMASL_2_AL6BT6 | PLANT_TROUBLE | 4940
2023 | summer | ALMASL_2_GS6SR6 | PLANT_MAINTENANCE | 0
2023 | summer | ALMASL_2_GS6SR6 | PLANT_TROUBLE | 786.1833
2023 | summer | ALMEGT_1_UNIT 1 | AMBIENT_DUE_TO_TEMP | 3790.6167
2023 | summer | ALMEGT_1_UNIT 1 | METERING_TELEMETRY | 5567.6
2023 | summer | ALMEGT_1_UNIT 1 | PLANT_MAINTENANCE | 250
2023 | summer | ALMEGT_1_UNIT 1 | PLANT_TROUBLE | 83.1833
2023 | summer | ALMEGT_1_UNIT 2 | AMBIENT_DUE_TO_TEMP | 3694.6167
2023 | summer | ALMEGT_1_UNIT 2 | METERING_TELEMETRY | 5662.9833
2023 | summer | ALMEGT_1_UNIT 2 | PLANT_MAINTENANCE | 250
2023 | summer | ALMEGT_1_UNIT 2 | PLANT_TROUBLE | 122.5167
2023 | summer | ALPSLR_1_NTHSLR | PLANT_MAINTENANCE | 35
2023 | summer | ALPSLR_1_NTHSLR | PLANT_TROUBLE | 7689.8333
2023 | summer | ALPSLR_1_NTHSLR | TRANSMISSION_INDUCED | 8.1667
2023 | summer | ALPSLR_1_NTHSLR | UNIT_TESTING | 2.1667
2023 | summer | ALPSLR_1_SPSSLR | PLANT_MAINTENANCE | 207.35
2023 | summer | ALPSLR_1_SPSSLR | PLANT_TROUBLE | 13116.65
2023 | summer | ALPSLR_1_SPSSLR | TRANSMISSION_INDUCED | 0
2023 | summer | ALT6DN_2_WIND7 | TRANSMISSION_INDUCED | 164.31
2023 | summer | ALT6DS_2_WIND9 | TRANSMISSION_INDUCED | 0
2023 | summer | ALTA3A_2_CPCE4 | METERING_TELEMETRY | 175
2023 | summer | ALTA3A_2_CPCE4 | PLANT_MAINTENANCE | 0
2023 | summer | ALTA3A_2_CPCE4 | PLANT_TROUBLE | 3859.0167
2023 | summer | ALTA3A_2_CPCE5 | METERING_TELEMETRY | 12.15
2023 | summer | ALTA3A_2_CPCE5 | PLANT_TROUBLE | 5387.6833
2023 | summer | ALTA3A_2_CPCE8 | AMBIENT_NOT_DUE_TO_TEMP | 338.1
2023 | summer | ALTA3A_2_CPCE8 | METERING_TELEMETRY | 44.2
2023 | summer | ALTA3A_2_CPCE8 | PLANT_TROUBLE | 8609.5
2023 | summer | ALTA4A_2_CPCW1 | METERING_TELEMETRY | 78.85
2023 | summer | ALTA4A_2_CPCW1 | PLANT_MAINTENANCE | 15
2023 | summer | ALTA4A_2_CPCW1 | PLANT_TROUBLE | 1469.925
2023 | summer | ALTA4B_2_CPCW2 | PLANT_TROUBLE | 3737.1
2023 | summer | ALTA4B_2_CPCW3 | PLANT_TROUBLE | 7223.2
2023 | summer | ALTA4B_2_CPCW6 | PLANT_TROUBLE | 1650
2023 | summer | ALTA6B_2_WIND11 | PLANT_TROUBLE | 1450.5
2023 | summer | ALTA6E_2_WIND10 | METERING_TELEMETRY | 42.75
2023 | summer | ALTA6E_2_WIND10 | PLANT_MAINTENANCE | 0
2023 | summer | ALTA6E_2_WIND10 | PLANT_TROUBLE | 8889.3658
2023 | summer | ALTWD_2_AT3WD3 | PLANT_TROUBLE | 676.3633
2023 | summer | ALTWD_2_AT3WD3 | TRANSMISSION_INDUCED | 18.9467
2023 | summer | ALTWD_2_COAWD1 | PLANT_MAINTENANCE | 385
2023 | summer | ALTWD_2_COAWD1 | PLANT_TROUBLE | 9501.12
2023 | summer | ALTWD_2_COAWD1 | TRANSMISSION_INDUCED | 43.2
2023 | summer | ANAHM_2_CANYN1 | PLANT_TROUBLE | 30018.1
2023 | summer | ANAHM_2_CANYN1 | TRANSMISSION_INDUCED | 0
2023 | summer | ANAHM_2_CANYN2 | UNIT_TESTING | 87.685
2023 | summer | ANAHM_2_CANYN3 | UNIT_TESTING | 37.945
2023 | summer | ANAHM_2_CANYN4 | UNIT_TESTING | 47.875
2023 | summer | ANZA_6_SOLAR1 | PLANT_TROUBLE | 57.2
2023 | summer | ANZA_6_SOLAR1 | TRANSITIONAL_LIMITATION | 7.75
2023 | summer | ANZA_6_SOLAR1 | TRANSMISSION_INDUCED | 330
2023 | summer | APLHIL_1_SFKHY1 | PLANT_TROUBLE | 139.2707
2023 | summer | APLHIL_1_SFKHY1 | TRANSMISSION_INDUCED | 6.5213
2023 | summer | AQUAWS_2_AQWSR1 | PLANT_MAINTENANCE | 0
2023 | summer | AQUAWS_2_AQWSR1 | PLANT_TROUBLE | 171.6
2023 | summer | ARBWD_6_QF | PLANT_MAINTENANCE | 29.75
2023 | summer | ARBWD_6_QF | PLANT_TROUBLE | 0
2023 | summer | ARBWD_6_QF | TRANSMISSION_INDUCED | 0
2023 | summer | ARCOGN_2_UNITS | AMBIENT_DUE_TO_TEMP | 125
2023 | summer | ARCOGN_2_UNITS | PLANT_TROUBLE | 19633.6667
2023 | summer | ARKANS_1_ARKSLR | PLANT_TROUBLE | 0
2023 | summer | ARLNTN_2_AR1SR1 | PLANT_MAINTENANCE | 100
2023 | summer | ARLNTN_2_AR1SR1 | PLANT_TROUBLE | 1702.6
2023 | summer | ARLNTN_2_ASUSR1 | PLANT_TROUBLE | 1375
2023 | summer | ARLVAL_5_SOLAR | TRANSMISSION_INDUCED | 0
2023 | summer | ASTORA_2_SOLAR2 | PLANT_TROUBLE | 144.575
2023 | summer | ATHOS_5_AP1X2 | PLANT_MAINTENANCE | 500
2023 | summer | ATHOS_5_AP1X2 | PLANT_TROUBLE | 2674.75
2023 | summer | ATHOS_5_AP2X2 | METERING_TELEMETRY | 0
2023 | summer | ATHOS_5_AP2X2 | PLANT_MAINTENANCE | 213.7667
2023 | summer | ATHOS_5_AP2X2 | PLANT_TROUBLE | 2050.1167
2023 | summer | ATWEL2_1_SOLAR1 | PLANT_TROUBLE | 41.6667
2023 | summer | ATWEL2_1_SOLAR1 | TRANSMISSION_INDUCED | 0
2023 | summer | ATWELL_1_SOLAR | PLANT_MAINTENANCE | 30.6667
2023 | summer | ATWELL_1_SOLAR | TRANSMISSION_INDUCED | 0
2023 | summer | AVENAL_6_AVPARK | AMBIENT_NOT_DUE_TO_TEMP | 48
2023 | summer | AVENAL_6_AVPARK | METERING_TELEMETRY | 5
2023 | summer | AVENAL_6_AVPARK | PLANT_TROUBLE | 0
2023 | summer | AVENAL_6_AVPARK | TRANSMISSION_INDUCED | 12
2023 | summer | AVENAL_6_AVSLR1 | METERING_TELEMETRY | 39.5
2023 | summer | AVENAL_6_AVSLR1 | PLANT_MAINTENANCE | 12.7717
2023 | summer | AVENAL_6_AVSLR1 | TRANSMISSION_INDUCED | 79
2023 | summer | AVENAL_6_AVSLR2 | METERING_TELEMETRY | 39.5
2023 | summer | AVENAL_6_AVSLR2 | PLANT_TROUBLE | 39.5
2023 | summer | AVENAL_6_AVSLR2 | TRANSMISSION_INDUCED | 79
2023 | summer | AVENAL_6_SANDDG | AMBIENT_NOT_DUE_TO_TEMP | 152
2023 | summer | AVENAL_6_SANDDG | PLANT_TROUBLE | 0
2023 | summer | AVENAL_6_SANDDG | TRANSMISSION_INDUCED | 399
2023 | summer | AVENAL_6_SUNCTY | AMBIENT_NOT_DUE_TO_TEMP | 160
2023 | summer | AVENAL_6_SUNCTY | PLANT_TROUBLE | 0
2023 | summer | AVENAL_6_SUNCTY | TRANSMISSION_INDUCED | 40
2023 | summer | AVSOLR_2_SOLAR | PLANT_MAINTENANCE | 124.2442
2023 | summer | AVSOLR_2_SOLAR | PLANT_TROUBLE | 0
2023 | summer | BALCHS_7_UNIT 1 | AMBIENT_DUE_TO_TEMP | 2.2333
2023 | summer | BALCHS_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 119.6667
2023 | summer | BALCHS_7_UNIT 1 | PLANT_TROUBLE | 465
2023 | summer | BALCHS_7_UNIT 1 | TRANSMISSION_INDUCED | 203.5667
2023 | summer | BALCHS_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 504.7542
2023 | summer | BALCHS_7_UNIT 2 | PLANT_MAINTENANCE | 0
2023 | summer | BALCHS_7_UNIT 2 | PLANT_TROUBLE | 116.375
2023 | summer | BALCHS_7_UNIT 2 | TRANSMISSION_INDUCED | 2.5
2023 | summer | BALCHS_7_UNIT 3 | AMBIENT_NOT_DUE_TO_TEMP | 477.1633
2023 | summer | BALCHS_7_UNIT 3 | PLANT_MAINTENANCE | 0
2023 | summer | BALCHS_7_UNIT 3 | PLANT_TROUBLE | 242.06
2023 | summer | BALCHS_7_UNIT 3 | TRANSMISSION_INDUCED | 0
2023 | summer | BANKPP_2_NSPIN | METERING_TELEMETRY | 1548
2023 | summer | BANKPP_2_NSPIN | TRANSMISSION_INDUCED | 5400
2023 | summer | BARRE_6_PEAKER | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 236.88
2023 | summer | BARRE_6_PEAKER | AMBIENT_DUE_TO_TEMP | 4101.7433
2023 | summer | BARRE_6_PEAKER | ENVIRONMENTAL_RESTRICTIONS | 182.5782
2023 | summer | BARRE_6_PEAKER | OTHER_USE_LIMIT_REACHED | 86.45
2023 | summer | BARRE_6_PEAKER | PLANT_MAINTENANCE | 0
2023 | summer | BARRE_6_PEAKER | PLANT_TROUBLE | 117.0208
2023 | summer | BARRE_6_PEAKER | SHORT_TERM_USE_LIMIT_REACHED | 141.2025
2023 | summer | BASICE_2_UNITS | AMBIENT_DUE_TO_TEMP | 1815.4602
2023 | summer | BASICE_2_UNITS | PLANT_TROUBLE | 934.0258
2023 | summer | BASICE_2_UNITS | TRANSMISSION_INDUCED | 53.3
2023 | summer | BCTSYS_5_PWXDYN | TRANSITIONAL_LIMITATION | 325280
2023 | summer | BDGRCK_1_UNITS | AMBIENT_DUE_TO_TEMP | 2380.5
2023 | summer | BDGRCK_1_UNITS | PLANT_MAINTENANCE | 39.4
2023 | summer | BDGRCK_1_UNITS | PLANT_TROUBLE | 3442.2
2023 | summer | BEARDS_7_UNIT 1 | PLANT_TROUBLE | 40.25
2023 | summer | BEARDS_7_UNIT 1 | TRANSMISSION_INDUCED | 374.35
2023 | summer | BEARMT_1_UNIT | AMBIENT_DUE_TO_TEMP | 3743.65
2023 | summer | BEARMT_1_UNIT | PLANT_TROUBLE | 214.9917
2023 | summer | BEARMT_1_UNIT | TRANSMISSION_INDUCED | 0
2023 | summer | BEJNLS_5_BV2SCEDYN | AMBIENT_DUE_TO_TEMP | 525
2023 | summer | BEJNLS_5_BV2SCEDYN | PLANT_TROUBLE | 891.1333
2023 | summer | BEJNLS_5_BV2SCEDYN | TRANSITIONAL_LIMITATION | 1178
2023 | summer | BEJNLS_5_BV2SCEDYN | TRANSMISSION_INDUCED | 1496
2023 | summer | BEKWJS_5_BV1SCEDYN | AMBIENT_DUE_TO_TEMP | 500
2023 | summer | BEKWJS_5_BV1SCEDYN | PLANT_TROUBLE | 685.3333
2023 | summer | BEKWJS_5_BV1SCEDYN | TRANSITIONAL_LIMITATION | 287.8
2023 | summer | BEKWJS_5_BV1SCEDYN | TRANSMISSION_INDUCED | 682
2023 | summer | BELDEN_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 4012.8
2023 | summer | BELDEN_7_UNIT 1 | PLANT_TROUBLE | 79667.3
2023 | summer | BGSKYN_2_AS2SR1 | PLANT_MAINTENANCE | 8421.3833
2023 | summer | BGSKYN_2_AS2SR1 | PLANT_TROUBLE | 2529
2023 | summer | BGSKYN_2_ASPSR2 | PLANT_MAINTENANCE | 1918.9333
2023 | summer | BGSKYN_2_ASPSR2 | PLANT_TROUBLE | 8085.1667
2023 | summer | BGSKYN_2_ASPSR2 | UNIT_TESTING | 54.0833
2023 | summer | BGSKYN_2_ASSR1B | PLANT_MAINTENANCE | 50.7167
2023 | summer | BGSKYN_2_ASSR1B | PLANT_TROUBLE | 595.15
2023 | summer | BGSKYN_2_ASSR3A | PLANT_MAINTENANCE | 462.3667
2023 | summer | BGSKYN_2_ASSR3A | PLANT_TROUBLE | 530
2023 | summer | BGSKYN_2_ASSR3A | UNIT_TESTING | 13.7667
2023 | summer | BGSKYN_2_ASSR3B | PLANT_MAINTENANCE | 159.3333
2023 | summer | BGSKYN_2_ASSR3B | PLANT_TROUBLE | 0
2023 | summer | BGSKYN_2_ASSR3B | UNIT_TESTING | 4.9167
2023 | summer | BGSKYN_2_BS3SR3 | PLANT_MAINTENANCE | 18
2023 | summer | BGSKYN_2_BS3SR3 | PLANT_TROUBLE | 1141.7083
2023 | summer | BIGCRK_2_EXESWD | AMBIENT_NOT_DUE_TO_TEMP | 153237.86
2023 | summer | BIGCRK_2_EXESWD | ENVIRONMENTAL_RESTRICTIONS | 1650
2023 | summer | BIGCRK_2_EXESWD | PLANT_MAINTENANCE | 21864.8
2023 | summer | BIGCRK_2_EXESWD | PLANT_TROUBLE | 197
2023 | summer | BIGCRK_2_EXESWD | TRANSMISSION_INDUCED | 943.96
2023 | summer | BIGSKY_2_AS2BT1 | METERING_TELEMETRY | 0
2023 | summer | BIGSKY_2_AS2BT1 | PLANT_MAINTENANCE | 0
2023 | summer | BIGSKY_2_AS2BT1 | PLANT_TROUBLE | 921.0833
2023 | summer | BIGSKY_2_ASLBT2 | PLANT_MAINTENANCE | 0
2023 | summer | BIGSKY_2_ASLBT2 | PLANT_TROUBLE | 402
2023 | summer | BIGSKY_2_BSKSR6 | PLANT_TROUBLE | 654.8167
2023 | summer | BIGSKY_2_BSKSR7 | PLANT_TROUBLE | 890
2023 | summer | BIGSKY_2_BSKSR8 | PLANT_TROUBLE | 872.5
2023 | summer | BIGSKY_2_SOLAR1 | PLANT_MAINTENANCE | 20.9
2023 | summer | BIGSKY_2_SOLAR1 | PLANT_TROUBLE | 1957.5
2023 | summer | BIGSKY_2_SOLAR2 | PLANT_TROUBLE | 1077.8
2023 | summer | BIGSKY_2_SOLAR3 | PLANT_TROUBLE | 523.1333
2023 | summer | BIGSKY_2_SOLAR4 | PLANT_TROUBLE | 220
2023 | summer | BIGSKY_2_SOLAR5 | PLANT_TROUBLE | 89.525
2023 | summer | BIGSKY_2_SOLAR6 | PLANT_TROUBLE | 3761.75
2023 | summer | BIGSKY_2_SOLAR7 | PLANT_TROUBLE | 2888.5
2023 | summer | BIOMAS_1_UNIT 1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 469.5
2023 | summer | BIOMAS_1_UNIT 1 | PLANT_TROUBLE | 1019.575
2023 | summer | BISHOP_1_ALAMO | AMBIENT_NOT_DUE_TO_TEMP | 2023.1
2023 | summer | BISHOP_1_ALAMO | METERING_TELEMETRY | 30.9333
2023 | summer | BISHOP_1_ALAMO | PLANT_TROUBLE | 783.55
2023 | summer | BISHOP_1_ALAMO | TRANSMISSION_INDUCED | 156.2333
2023 | summer | BISHOP_1_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 1204.32
2023 | summer | BISHOP_1_UNITS | METERING_TELEMETRY | 68.25
2023 | summer | BISHOP_1_UNITS | PLANT_MAINTENANCE | 7.75
2023 | summer | BISHOP_1_UNITS | PLANT_TROUBLE | 2537.175
2023 | summer | BISHOP_1_UNITS | TRANSMISSION_INDUCED | 129.9167
2023 | summer | BKRFLD_2_SOLAR1 | PLANT_MAINTENANCE | 2.07
2023 | summer | BKRFLD_2_SOLAR1 | PLANT_TROUBLE | 51.175
2023 | summer | BLACK_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 1324
2023 | summer | BLACK_7_UNIT 1 | PLANT_MAINTENANCE | 0
2023 | summer | BLACK_7_UNIT 1 | PLANT_TROUBLE | 40.6
2023 | summer | BLACK_7_UNIT 1 | TRANSMISSION_INDUCED | 252.1667
2023 | summer | BLACK_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 916.0683
2023 | summer | BLACK_7_UNIT 2 | PLANT_TROUBLE | 65.3333
2023 | summer | BLACK_7_UNIT 2 | TRANSMISSION_INDUCED | 249.4967
2023 | summer | BLAST_1_WIND | PLANT_MAINTENANCE | 0
2023 | summer | BLAST_1_WIND | TRANSMISSION_INDUCED | 156
2023 | summer | BLCKBT_2_STONEY | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 378.2
2023 | summer | BLCKBT_2_STONEY | ENVIRONMENTAL_RESTRICTIONS | 341
2023 | summer | BLCKBT_2_STONEY | PLANT_TROUBLE | 27.1767
2023 | summer | BLCKBT_2_STONEY | TRANSMISSION_INDUCED | 0
2023 | summer | BLCKWL_6_SOLAR1 | METERING_TELEMETRY | 13
2023 | summer | BLCKWL_6_SOLAR1 | PLANT_TROUBLE | 371.44
2023 | summer | BLCKWL_6_SOLAR1 | TRANSMISSION_INDUCED | 891
2023 | summer | BLKCRK_2_GMCBT1 | METERING_TELEMETRY | 0
2023 | summer | BLKCRK_2_GMCBT1 | PLANT_TROUBLE | 38855.5822
2023 | summer | BLKCRK_2_GMCBT1 | UNIT_TESTING | 1840
2023 | summer | BLKCRK_2_SOLAR1 | METERING_TELEMETRY | 275
2023 | summer | BLKCRK_2_SOLAR1 | PLANT_MAINTENANCE | 306.8433
2023 | summer | BLKDIA_2_BDEBT1 | PLANT_MAINTENANCE | 2893.75
2023 | summer | BLKDIA_2_BDEBT1 | PLANT_TROUBLE | 1914.3833
2023 | summer | BLKDIA_2_BDEBT1 | TRANSMISSION_INDUCED | 400
2023 | summer | BLKDIA_2_BDEBT1 | UNIT_TESTING | 0
2023 | summer | BLM W_2_COSBT1 | PLANT_MAINTENANCE | 0
2023 | summer | BLM W_2_COSBT1 | PLANT_TROUBLE | 7161.547
2023 | summer | BLM_2_UNITS | PLANT_TROUBLE | 0
2023 | summer | BLYTHE_1_SOLAR1 | METERING_TELEMETRY | 5
2023 | summer | BLYTHE_1_SOLAR1 | PLANT_TROUBLE | 1053.3833
2023 | summer | BLYTHE_1_SOLAR2 | PLANT_TROUBLE | 1113.5333
2023 | summer | BNNIEN_7_ALTAPH | AMBIENT_NOT_DUE_TO_TEMP | 317.6167
2023 | summer | BNNIEN_7_ALTAPH | TRANSMISSION_INDUCED | 4.6667
2023 | summer | BOGUE_1_UNITA1 | AMBIENT_DUE_TO_TEMP | 478.9167
2023 | summer | BOGUE_1_UNITA1 | PLANT_TROUBLE | 497.5502
2023 | summer | BOGUE_1_UNITA1 | UNIT_TESTING | 0
2023 | summer | BORDER_6_UNITA1 | AMBIENT_DUE_TO_TEMP | 6.375
2023 | summer | BORDER_6_UNITA1 | PLANT_MAINTENANCE | 530
2023 | summer | BORDER_6_UNITA1 | PLANT_TROUBLE | 606.8108
2023 | summer | BORDER_6_UNITA1 | TRANSMISSION_INDUCED | 310.0625
2023 | summer | BORDER_6_UNITA1 | UNIT_TESTING | 1.0987
2023 | summer | BOWMN_6_HYDRO | PLANT_TROUBLE | 11.82
2023 | summer | BRDSLD_2_HIWIND | METERING_TELEMETRY | 2349.6
2023 | summer | BRDSLD_2_HIWIND | PLANT_MAINTENANCE | 50751.55
2023 | summer | BRDSLD_2_HIWIND | PLANT_TROUBLE | 1656.65
2023 | summer | BRDSLD_2_MTZUM2 | PLANT_MAINTENANCE | 34.5
2023 | summer | BRDSLD_2_MTZUM2 | PLANT_TROUBLE | 0
2023 | summer | BRDSLD_2_MTZUMA | PLANT_MAINTENANCE | 827.8467
2023 | summer | BRDSLD_2_MTZUMA | PLANT_TROUBLE | 0
2023 | summer | BRDSLD_2_SHILO1 | PLANT_TROUBLE | 1848.4
2023 | summer | BRDSLD_2_SHILO2 | AMBIENT_DUE_TO_TEMP | 649.6
2023 | summer | BRDSLD_2_SHILO2 | PLANT_MAINTENANCE | 2335.0333
2023 | summer | BRDSLD_2_SHILO2 | PLANT_TROUBLE | 277.5
2023 | summer | BRDSLD_2_SHLO3A | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | summer | BRDSLD_2_SHLO3A | PLANT_MAINTENANCE | 2659.96
2023 | summer | BRDSLD_2_SHLO3A | PLANT_TROUBLE | 436.7867
2023 | summer | BRDSLD_2_SHLO3B | PLANT_MAINTENANCE | 550.2208
2023 | summer | BREGGO_6_DEGRSL | PLANT_TROUBLE | 18.9
2023 | summer | BREGGO_6_DEGRSL | TRANSMISSION_INDUCED | 0
2023 | summer | BREGGO_6_SOLAR | PLANT_MAINTENANCE | 1.65
2023 | summer | BREGGO_6_SOLAR | PLANT_TROUBLE | 25.1667
2023 | summer | BREGGO_6_SOLAR | TRANSMISSION_INDUCED | 39
2023 | summer | BRODIE_2_WIND | PLANT_MAINTENANCE | 6175.75
2023 | summer | BRODIE_2_WIND | PLANT_TROUBLE | 0
2023 | summer | BUCKBL_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 0
2023 | summer | BUCKBL_2_PL1X3 | PLANT_TROUBLE | 7336.4642
2023 | summer | BUCKBL_2_PL1X3 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 740.445
2023 | summer | BUCKBL_2_PL1X3 | TRANSMISSION_INDUCED | 1044.8502
2023 | summer | BUCKCK_7_OAKFLT | AMBIENT_NOT_DUE_TO_TEMP | 6.5
2023 | summer | BUCKCK_7_OAKFLT | TRANSMISSION_INDUCED | 988
2023 | summer | BUCKCK_7_PL1X2 | AMBIENT_DUE_TO_TEMP | 14.75
2023 | summer | BUCKCK_7_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 583.9533
2023 | summer | BUCKCK_7_PL1X2 | PLANT_MAINTENANCE | 1448.7
2023 | summer | BUCKCK_7_PL1X2 | PLANT_TROUBLE | 363.54
2023 | summer | BUCKCK_7_PL1X2 | TRANSMISSION_INDUCED | 2640
2023 | summer | BUCKWD_1_QF | PLANT_MAINTENANCE | 488.875
2023 | summer | BUCKWD_1_QF | PLANT_TROUBLE | 766.325
2023 | summer | BURNYF_2_UNIT 1 | PLANT_MAINTENANCE | 12.8333
2023 | summer | BURNYF_2_UNIT 1 | PLANT_TROUBLE | 6763.0917
2023 | summer | BURNYF_2_UNIT 1 | TRANSMISSION_INDUCED | 86.5167
2023 | summer | BUTTVL_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | summer | BUTTVL_7_UNIT 1 | TRANSMISSION_INDUCED | 0
2023 | summer | CABALO_2_M2BSR1 | PLANT_MAINTENANCE | 63.9
2023 | summer | CABALO_2_M2BSR1 | PLANT_TROUBLE | 4863.023
2023 | summer | CABALO_2_M2WSR2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2023 | summer | CABALO_2_M2WSR2 | PLANT_MAINTENANCE | 214.9333
2023 | summer | CABALO_2_M2WSR2 | PLANT_TROUBLE | 2264.01
2023 | summer | CABZON_1_WINDA1 | PLANT_TROUBLE | 233.0167
2023 | summer | CALFTN_2_CFSBT1 | PLANT_MAINTENANCE | 0
2023 | summer | CALFTN_2_CFSBT1 | PLANT_TROUBLE | 325
2023 | summer | CALFTN_2_CFSBT1 | UNIT_TESTING | 0
2023 | summer | CALFTN_2_SOLAR | PLANT_MAINTENANCE | 561.7
2023 | summer | CALFTS_2_CFSSR1 | METERING_TELEMETRY | 82.53
2023 | summer | CALFTS_2_CFSSR1 | PLANT_TROUBLE | 552.1318
2023 | summer | CALGEN_1_UNITS | PLANT_TROUBLE | 2967.2
2023 | summer | CALPIN_1_AGNEW | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 142.8
2023 | summer | CALPIN_1_AGNEW | AMBIENT_DUE_TO_TEMP | 259.2
2023 | summer | CALPIN_1_AGNEW | PLANT_TROUBLE | 1657.224
2023 | summer | CALPIN_1_AGNEW | TRANSITIONAL_LIMITATION | 6.5333
2023 | summer | CAMCHE_1_PL1X3 | AMBIENT_DUE_TO_TEMP | 86.9
2023 | summer | CAMCHE_1_PL1X3 | AMBIENT_NOT_DUE_TO_TEMP | 764.15
2023 | summer | CAMCHE_1_PL1X3 | PLANT_MAINTENANCE | 234.75
2023 | summer | CAMCHE_1_PL1X3 | TRANSMISSION_INDUCED | 0
2023 | summer | CAMLOT_2_SOLAR1 | PLANT_MAINTENANCE | 67.5
2023 | summer | CAMLOT_2_SOLAR2 | PLANT_MAINTENANCE | 90
2023 | summer | CAMLOT_2_SOLAR2 | PLANT_TROUBLE | 0
2023 | summer | CAMPFW_7_FARWST | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 204
2023 | summer | CAMPFW_7_FARWST | AMBIENT_NOT_DUE_TO_TEMP | 1278.4
2023 | summer | CAMPFW_7_FARWST | METERING_TELEMETRY | 183.6
2023 | summer | CAMPFW_7_FARWST | TRANSMISSION_INDUCED | 34
2023 | summer | CAPWD_1_QF | PLANT_TROUBLE | 9368.25
2023 | summer | CARBOU_7_PL2X3 | AMBIENT_NOT_DUE_TO_TEMP | 7617.1817
2023 | summer | CARBOU_7_PL2X3 | TRANSMISSION_INDUCED | 0
2023 | summer | CARBOU_7_PL4X5 | AMBIENT_NOT_DUE_TO_TEMP | 6606.9
2023 | summer | CARBOU_7_PL4X5 | PLANT_TROUBLE | 0
2023 | summer | CARBOU_7_PL4X5 | TRANSMISSION_INDUCED | 0
2023 | summer | CARBOU_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 465
2023 | summer | CARBOU_7_UNIT 1 | PLANT_TROUBLE | 11664
2023 | summer | CARBOU_7_UNIT 1 | TRANSMISSION_INDUCED | 44
2023 | summer | CARLS1_2_CARCT1 | AMBIENT_DUE_TO_TEMP | 8993.1
2023 | summer | CARLS1_2_CARCT1 | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | summer | CARLS1_2_CARCT1 | PLANT_MAINTENANCE | 0
2023 | summer | CARLS1_2_CARCT1 | PLANT_TROUBLE | 922.9767
2023 | summer | CARLS1_2_CARCT1 | TRANSMISSION_INDUCED | 0
2023 | summer | CARLS2_1_CARCT1 | AMBIENT_DUE_TO_TEMP | 795.33
2023 | summer | CARLS2_1_CARCT1 | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | summer | CARLS2_1_CARCT1 | PLANT_MAINTENANCE | 0
2023 | summer | CARLS2_1_CARCT1 | PLANT_TROUBLE | 186.7247
2023 | summer | CATLNA_2_SOLAR | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | summer | CATLNA_2_SOLAR | PLANT_TROUBLE | 54.6
2023 | summer | CAVLSR_2_BSOLAR | PLANT_MAINTENANCE | 30
2023 | summer | CAVLSR_2_BSOLAR | PLANT_TROUBLE | 0
2023 | summer | CAVLSR_2_BSOLAR | TRANSMISSION_INDUCED | 150
2023 | summer | CAVLSR_2_RSOLAR | PLANT_MAINTENANCE | 328.2967
2023 | summer | CAVLSR_2_RSOLAR | PLANT_TROUBLE | 1742.5793
2023 | summer | CAVLSR_2_RSOLAR | TRANSMISSION_INDUCED | 660
2023 | summer | CAYTNO_2_VASCO | PLANT_MAINTENANCE | 6.49
2023 | summer | CAYTNO_2_VASCO | PLANT_TROUBLE | 81.1342
2023 | summer | CAYTNO_2_VASCO | TRANSMISSION_INDUCED | 45.6517
2023 | summer | CEDRCK_6_UNIT | PLANT_TROUBLE | 156.8
2023 | summer | CEDRCK_6_UNIT | TRANSMISSION_INDUCED | 3.2177
2023 | summer | CEDUCR_2_SOLAR1 | TRANSMISSION_INDUCED | 210
2023 | summer | CEDUCR_2_SOLAR2 | PLANT_TROUBLE | 0
2023 | summer | CEDUCR_2_SOLAR2 | TRANSMISSION_INDUCED | 160
2023 | summer | CEDUCR_2_SOLAR3 | TRANSMISSION_INDUCED | 157.5
2023 | summer | CEDUCR_2_SOLAR4 | PLANT_TROUBLE | 150
2023 | summer | CEDUCR_2_SOLAR4 | TRANSMISSION_INDUCED | 110
2023 | summer | CENT40_1_C40SR1 | PLANT_TROUBLE | 906
2023 | summer | CENT40_1_C40SR1 | TRANSITIONAL_LIMITATION | 200
2023 | summer | CENT40_1_C40SR1 | TRANSMISSION_INDUCED | 200
2023 | summer | CENTER_2_RHONDO | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 846.1
2023 | summer | CENTER_2_RHONDO | AMBIENT_NOT_DUE_TO_TEMP | 486.55
2023 | summer | CENTER_2_RHONDO | PLANT_TROUBLE | 3.7083
2023 | summer | CENTER_6_PEAKER | AMBIENT_DUE_TO_TEMP | 366.49
2023 | summer | CENTER_6_PEAKER | PLANT_TROUBLE | 575.055
2023 | summer | CENTPD_2_BMSSX2 | PLANT_MAINTENANCE | 55.6
2023 | summer | CENTPD_2_BMSSX2 | PLANT_TROUBLE | 156
2023 | summer | CENTPD_2_BMSX2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 5
2023 | summer | CENTPD_2_BMSX2 | PLANT_MAINTENANCE | 10
2023 | summer | CENTPD_2_BMSX2 | PLANT_TROUBLE | 2468.7333
2023 | summer | CENTRY_6_PL1X4 | PLANT_MAINTENANCE | 1382
2023 | summer | CENTRY_6_PL1X4 | PLANT_TROUBLE | 570.95
2023 | summer | CENTRY_6_PL1X4 | UNIT_TESTING | 0
2023 | summer | CHALK_1_UNIT | AMBIENT_DUE_TO_TEMP | 3745.35
2023 | summer | CHALK_1_UNIT | PLANT_TROUBLE | 196.0567
2023 | summer | CHARMN_2_PGONG1 | PLANT_MAINTENANCE | 0
2023 | summer | CHARMN_2_PGONG1 | PLANT_TROUBLE | 66.2333
2023 | summer | CHEVCY_1_UNIT | PLANT_TROUBLE | 0
2023 | summer | CHEVMN_2_UNITS | PLANT_MAINTENANCE | 23100.95
2023 | summer | CHICPK_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 11527
2023 | summer | CHICPK_7_UNIT 1 | PLANT_TROUBLE | 0
2023 | summer | CHICPK_7_UNIT 1 | TRANSMISSION_INDUCED | 0
2023 | summer | CHILLS_1_SYCENG | ENVIRONMENTAL_RESTRICTIONS | 8.05
2023 | summer | CHILLS_1_SYCENG | PLANT_TROUBLE | 26.59
2023 | summer | CHILLS_1_SYCENG | TRANSMISSION_INDUCED | 0
2023 | summer | CHILLS_7_UNITA1 | PLANT_TROUBLE | 183.6167
2023 | summer | CHILLS_7_UNITA1 | TRANSMISSION_INDUCED | 5.5875
2023 | summer | CHINO_2_APEBT1 | PLANT_MAINTENANCE | 443.725
2023 | summer | CHINO_2_APEBT1 | PLANT_TROUBLE | 1216.7
2023 | summer | CHINO_2_PESBT1 | PLANT_MAINTENANCE | 0
2023 | summer | CHINO_2_PESBT1 | PLANT_TROUBLE | 1836.3967
2023 | summer | CHINO_2_PESBT1 | UNIT_TESTING | 2400
2023 | summer | CHINO_2_SOLAR | PLANT_TROUBLE | 530
2023 | summer | CHWCHL_1_BIOMAS | PLANT_TROUBLE | 1620
2023 | summer | CHWCHL_1_UNIT | AMBIENT_DUE_TO_TEMP | 742.875
2023 | summer | CHWCHL_1_UNIT | PLANT_TROUBLE | 112.5333
2023 | summer | CLINESCO_3_PVDYN | AMBIENT_DUE_TO_TEMP | 225
2023 | summer | CLINESCO_3_PVDYN | PLANT_TROUBLE | 0
2023 | summer | CLINESCO_3_PVDYN | TRANSITIONAL_LIMITATION | 2033.96
2023 | summer | CLINESCO_3_WBDYN | AMBIENT_DUE_TO_TEMP | 225
2023 | summer | CLINESCO_3_WBDYN | ENVIRONMENTAL_RESTRICTIONS | 302.342
2023 | summer | CLINESCO_3_WBDYN | PLANT_TROUBLE | 256.4
2023 | summer | CLINESCO_3_WBDYN | TRANSITIONAL_LIMITATION | 4209.52
2023 | summer | CLOVER_2_UNIT | PLANT_MAINTENANCE | 5.8575
2023 | summer | CLOVER_2_UNIT | PLANT_TROUBLE | 0
2023 | summer | CLOVER_2_UNIT | TRANSMISSION_INDUCED | 1.98
2023 | summer | CNTNLA_2_SOLAR2 | TRANSMISSION_INDUCED | 0
2023 | summer | COCOPP_2_CTG1 | AMBIENT_DUE_TO_TEMP | 7795.4
2023 | summer | COCOPP_2_CTG2 | AMBIENT_DUE_TO_TEMP | 6818.56
2023 | summer | COCOPP_2_CTG2 | AMBIENT_DUE_TO_TEMP | 442.2
2023 | summer | COCOPP_2_CTG3 | AMBIENT_DUE_TO_TEMP | 12517.2
2023 | summer | COCOPP_2_CTG3 | ENVIRONMENTAL_RESTRICTIONS | 701.895
2023 | summer | COCOPP_2_CTG3 | PLANT_MAINTENANCE | 0
2023 | summer | COCOPP_2_CTG3 | PLANT_TROUBLE | 0
2023 | summer | COCOPP_2_CTG4 | AMBIENT_DUE_TO_TEMP | 7906.81
2023 | summer | COGNAT_1_UNIT | PLANT_MAINTENANCE | 712.5
2023 | summer | COGNAT_1_UNIT | PLANT_TROUBLE | 1453.5
2023 | summer | COLEMN_2_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 55
2023 | summer | COLEMN_2_UNIT | PLANT_MAINTENANCE | 44.85
2023 | summer | COLGAT_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 14736.64
2023 | summer | COLGAT_7_UNIT 1 | ENVIRONMENTAL_RESTRICTIONS | 410
2023 | summer | COLGAT_7_UNIT 1 | PLANT_MAINTENANCE | 0
2023 | summer | COLGAT_7_UNIT 1 | UNIT_TESTING | 0
2023 | summer | COLGAT_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 14099.39
2023 | summer | COLGAT_7_UNIT 2 | ENVIRONMENTAL_RESTRICTIONS | 410
2023 | summer | COLGAT_7_UNIT 2 | PLANT_MAINTENANCE | 0
2023 | summer | COLGAT_7_UNIT 2 | TRANSMISSION_INDUCED | 0
2023 | summer | COLGAT_7_UNIT 2 | UNIT_TESTING | 0
2023 | summer | COLGNS_2_CNSSR1 | PLANT_MAINTENANCE | 574.2
2023 | summer | COLGNS_2_CNSSR1 | PLANT_TROUBLE | 7282.7333
2023 | summer | COLPIN_6_COLLNS | PLANT_MAINTENANCE | 112.97
2023 | summer | COLPIN_6_COLLNS | PLANT_TROUBLE | 396
2023 | summer | COLPIN_6_COLLNS | TRANSMISSION_INDUCED | 45.32
2023 | summer | COLTON_6_AGUAM1 | ENVIRONMENTAL_RESTRICTIONS | 768.8333
2023 | summer | COLTON_6_AGUAM1 | PLANT_TROUBLE | 12.35
2023 | summer | COLUSA_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 30098.695
2023 | summer | COLUSA_2_PL1X3 | PLANT_TROUBLE | 8466.724
2023 | summer | COLVIL_7_PL1X2 | METERING_TELEMETRY | 83.5937
2023 | summer | COLVIL_7_PL1X2 | PLANT_MAINTENANCE | 378
2023 | summer | COLVIL_7_PL1X2 | PLANT_TROUBLE | 371.58
2023 | summer | COLVIL_7_PL1X2 | TRANSMISSION_INDUCED | 179.597
2023 | summer | CONTRL_1_CASAD1 | PLANT_MAINTENANCE | 2.31
2023 | summer | CONTRL_1_CASAD1 | PLANT_TROUBLE | 25.19
2023 | summer | CONTRL_1_CASAD1 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 14.4
2023 | summer | CONTRL_1_CASAD1 | TRANSMISSION_INDUCED | 129.6
2023 | summer | CONTRL_1_CASAD2 | AMBIENT_DUE_TO_TEMP | 1466.7167
2023 | summer | CONTRL_1_CASAD2 | AMBIENT_NOT_DUE_TO_TEMP | 6.5
2023 | summer | CONTRL_1_CASAD2 | PLANT_TROUBLE | 18.375
2023 | summer | CONTRL_1_CASAD2 | TRANSITIONAL_LIMITATION | 19.8
2023 | summer | CONTRL_1_CASAD2 | TRANSMISSION_INDUCED | 114.6
2023 | summer | CONTRL_1_CASAD3 | PLANT_TROUBLE | 50
2023 | summer | CONTRL_1_CASAD3 | TRANSMISSION_INDUCED | 252
2023 | summer | CONTRL_1_LUNDY | AMBIENT_NOT_DUE_TO_TEMP | 566.4
2023 | summer | CONTRL_1_LUNDY | PLANT_TROUBLE | 52.815
2023 | summer | CONTRL_1_LUNDY | TRANSMISSION_INDUCED | 51.1283
2023 | summer | CONTRL_1_OXBOW | AMBIENT_DUE_TO_TEMP | 458.3
2023 | summer | CONTRL_1_OXBOW | AMBIENT_NOT_DUE_TO_TEMP | 101.2
2023 | summer | CONTRL_1_OXBOW | PLANT_MAINTENANCE | 0
2023 | summer | CONTRL_1_OXBOW | PLANT_TROUBLE | 1313.675
2023 | summer | CONTRL_1_OXBOW | TRANSMISSION_INDUCED | 105
2023 | summer | CONTRL_1_OXBOW | UNIT_TESTING | 0
2023 | summer | CONTRL_1_POOLE | AMBIENT_NOT_DUE_TO_TEMP | 781.6533
2023 | summer | CONTRL_1_POOLE | TRANSMISSION_INDUCED | 163.1
2023 | summer | CONTRL_1_QF | TRANSMISSION_INDUCED | 11.9
2023 | summer | CONTRL_1_RUSHCK | AMBIENT_NOT_DUE_TO_TEMP | 1618.89
2023 | summer | CONTRL_1_RUSHCK | TRANSMISSION_INDUCED | 62.245
2023 | summer | COPMT2_2_SOLAR2 | PLANT_TROUBLE | 1010.88
2023 | summer | COPMTN_2_SOLAR1 | AMBIENT_NOT_DUE_TO_TEMP | 190
2023 | summer | COPMTN_2_SOLAR1 | PLANT_TROUBLE | 140
2023 | summer | CORONS_6_CLRWTR | PLANT_TROUBLE | 64.4877
2023 | summer | CORONS_6_CLRWTR | TRANSMISSION_INDUCED | 168
2023 | summer | CORRAL_6_SJOAQN | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 3.5117
2023 | summer | CORRAL_6_SJOAQN | PLANT_MAINTENANCE | 17.325
2023 | summer | CORRAL_6_SJOAQN | PLANT_TROUBLE | 17.175
2023 | summer | CORRAL_6_SJOAQN | TRANSMISSION_INDUCED | 544.4367
2023 | summer | COTTLE_2_FRNKNH | TRANSMISSION_INDUCED | 196.1
2023 | summer | COVERD_2_HCKHY1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 3996.2
2023 | summer | COVERD_2_HCKHY1 | PLANT_TROUBLE | 34.45
2023 | summer | COVERD_2_MCKHY1 | AMBIENT_NOT_DUE_TO_TEMP | 1902
2023 | summer | COVERD_2_QFUNTS | PLANT_TROUBLE | 93.8667
2023 | summer | COVERD_2_RCKHY1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 844.6667
2023 | summer | COWCRK_2_UNIT | PLANT_TROUBLE | 1524
2023 | summer | CPVERD_2_SOLAR | PLANT_TROUBLE | 0
2023 | summer | CPVERD_2_SOLAR | TRANSMISSION_INDUCED | 903.5
2023 | summer | CRELMN_6_AABBT1 | PLANT_TROUBLE | 18.7217
2023 | summer | CRELMN_6_AABBT1 | RTU_RIG | 2.35
2023 | summer | CRESTA_7_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 12077.5297
2023 | summer | CRESTA_7_PL1X2 | PLANT_MAINTENANCE | 5985
2023 | summer | CRESTA_7_PL1X2 | PLANT_TROUBLE | 50.992
2023 | summer | CRIMSN_2_CRMBT1 | METERING_TELEMETRY | 4.1333
2023 | summer | CRIMSN_2_CRMBT1 | PLANT_MAINTENANCE | 0
2023 | summer | CRIMSN_2_CRMBT1 | PLANT_TROUBLE | 5351.6083
2023 | summer | CRIMSN_2_CRMBT1 | UNIT_TESTING | 530
2023 | summer | CRIMSN_2_CRMBT2 | METERING_TELEMETRY | 3.1
2023 | summer | CRIMSN_2_CRMBT2 | PLANT_TROUBLE | 1941.8917
2023 | summer | CRIMSN_2_CRMBT2 | UNIT_TESTING | 300
2023 | summer | CRNEVL_6_CRNVA | AMBIENT_NOT_DUE_TO_TEMP | 27
2023 | summer | CRNEVL_6_CRNVA | PLANT_TROUBLE | 0
2023 | summer | CRNEVL_6_CRNVA | TRANSMISSION_INDUCED | 30.6
2023 | summer | CRNEVL_6_SJQN 2 | AMBIENT_NOT_DUE_TO_TEMP | 1488
2023 | summer | CROKET_7_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 413.6317
2023 | summer | CROKET_7_UNIT | PLANT_MAINTENANCE | 616
2023 | summer | CROKET_7_UNIT | PLANT_TROUBLE | 328
2023 | summer | CRSTWD_6_KUMYAY | PLANT_TROUBLE | 4026.8
2023 | summer | CRSTWD_6_KUMYAY | TRANSMISSION_INDUCED | 108.3833
2023 | summer | CRWCKS_1_SOLAR1 | PLANT_TROUBLE | 2609.5
2023 | summer | CSCCOG_1_UNIT 1 | PLANT_MAINTENANCE | 85.05
2023 | summer | CSCCOG_1_UNIT 1 | PLANT_TROUBLE | 2887.15
2023 | summer | CSCGNR_1_UNIT 1 | PLANT_TROUBLE | 990
2023 | summer | CSCGNR_1_UNIT 2 | METERING_TELEMETRY | 0
2023 | summer | CSCGNR_1_UNIT 2 | PLANT_MAINTENANCE | 123.75
2023 | summer | CSCGNR_1_UNIT 2 | PLANT_TROUBLE | 4166.675
2023 | summer | CSLR4S_2_SOLAR | PLANT_MAINTENANCE | 383.5
2023 | summer | CSLR4S_2_SOLAR | PLANT_TROUBLE | 0
2023 | summer | CUMBIA_1_SOLAR | METERING_TELEMETRY | 75
2023 | summer | CUMBIA_1_SOLAR | PLANT_TROUBLE | 3793.4333
2023 | summer | CUYAMS_6_CUYSR1 | METERING_TELEMETRY | 229.3333
2023 | summer | CUYAMS_6_CUYSR1 | PLANT_TROUBLE | 497.3333
2023 | summer | CUYAMS_6_CUYSR1 | TRANSMISSION_INDUCED | 100
2023 | summer | DAIRLD_1_CR1BM1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 249.5
2023 | summer | DAIRLD_1_CR1BM1 | PLANT_TROUBLE | 3.5
2023 | summer | DEADCK_1_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 1174.7533
2023 | summer | DEERCR_6_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 456.6333
2023 | summer | DEERCR_6_UNIT 1 | PLANT_MAINTENANCE | 153.5333
2023 | summer | DEERCR_6_UNIT 1 | PLANT_TROUBLE | 1066.45
2023 | summer | DEERCR_6_UNIT 1 | TRANSMISSION_INDUCED | 10.5
2023 | summer | DELSUR_6_CREST | PLANT_TROUBLE | 100
2023 | summer | DELSUR_6_CREST | TRANSMISSION_INDUCED | 0
2023 | summer | DELSUR_6_DRYFRB | METERING_TELEMETRY | 24
2023 | summer | DELSUR_6_DRYFRB | PLANT_TROUBLE | 431
2023 | summer | DELSUR_6_DRYFRB | TRANSMISSION_INDUCED | 0
2023 | summer | DELSUR_6_HORSR1 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2023 | summer | DELSUR_6_SOLAR1 | PLANT_TROUBLE | 7.5
2023 | summer | DELSUR_6_SOLAR1 | TRANSMISSION_INDUCED | 0
2023 | summer | DELTA_2_PL1X4 | AMBIENT_DUE_TO_TEMP | 28843.9837
2023 | summer | DELTA_2_PL1X4 | PLANT_MAINTENANCE | 0
2023 | summer | DELTA_2_PL1X4 | PLANT_TROUBLE | 58376.4
2023 | summer | DELTA_2_PL1X4 | TRANSITIONAL_LIMITATION | 5880.8667
2023 | summer | DELTA_2_PL1X4 | UNIT_TESTING | 0
2023 | summer | DEVERS_1_SOLAR | ENVIRONMENTAL_RESTRICTIONS | 92.5
2023 | summer | DEVERS_1_SOLAR1 | PLANT_TROUBLE | 60
2023 | summer | DEVERS_2_DHSPG2 | METERING_TELEMETRY | 7
2023 | summer | DEVERS_2_DHSPG2 | PLANT_TROUBLE | 12.1333
2023 | summer | DEVERS_2_DHSPG2 | TRANSMISSION_INDUCED | 7
2023 | summer | DEXZEL_1_UNIT | PLANT_TROUBLE | 508
2023 | summer | DIABLO_7_UNIT 1 | PLANT_MAINTENANCE | 10965.5
2023 | summer | DIABLO_7_UNIT 2 | PLANT_TROUBLE | 6671
2023 | summer | DISCOV_1_CHEVRN | PLANT_MAINTENANCE | 4554.4333
2023 | summer | DISCOV_1_CHEVRN | PLANT_TROUBLE | 523.65
2023 | summer | DONNLS_7_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 2345
2023 | summer | DONNLS_7_UNIT | METERING_TELEMETRY | 0
2023 | summer | DONNLS_7_UNIT | PLANT_TROUBLE | 97.5
2023 | summer | DONNLS_7_UNIT | TRANSMISSION_INDUCED | 5025.925
2023 | summer | DOUBLC_1_UNITS | AMBIENT_DUE_TO_TEMP | 2126.65
2023 | summer | DOUBLC_1_UNITS | PLANT_TROUBLE | 1028.1117
2023 | summer | DRACKR_2_D4SR4B | PLANT_TROUBLE | 350.535
2023 | summer | DRACKR_2_DS3SR3 | PLANT_MAINTENANCE | 20.064
2023 | summer | DRACKR_2_DS3SR3 | PLANT_TROUBLE | 544.2362
2023 | summer | DRACKR_2_DS3SR3 | UNIT_TESTING | 0
2023 | summer | DRACKR_2_DS4SR4 | PLANT_TROUBLE | 481
2023 | summer | DRACKR_2_DS4SR4 | RTU_RIG | 0
2023 | summer | DRACKR_2_DSUBT1 | PLANT_TROUBLE | 10828.5703
2023 | summer | DRACKR_2_DSUBT2 | METERING_TELEMETRY | 502.1667
2023 | summer | DRACKR_2_DSUBT2 | PLANT_TROUBLE | 9058.0693
2023 | summer | DRACKR_2_DSUBT3 | METERING_TELEMETRY | 426.8
2023 | summer | DRACKR_2_DSUBT3 | PLANT_TROUBLE | 17189.4803
2023 | summer | DRACKR_2_DSUBT3 | UNIT_TESTING | 1859.1667
2023 | summer | DRACKR_2_DSUBT4 | PLANT_TROUBLE | 11880.7423
2023 | summer | DRACKR_2_SOLAR1 | PLANT_TROUBLE | 3164.6167
2023 | summer | DRACKR_2_SOLAR2 | PLANT_TROUBLE | 1054.85
2023 | summer | DRACKR_2_SOLAR2 | UNIT_TESTING | 123
2023 | summer | DREWSR_2_BHSSR1 | PLANT_MAINTENANCE | 150
2023 | summer | DREWSR_2_BHSSR1 | PLANT_TROUBLE | 82.5
2023 | summer | DREWS_6_PL1X4 | METERING_TELEMETRY | 155.8
2023 | summer | DREWS_6_PL1X4 | PLANT_MAINTENANCE | 1135.8333
2023 | summer | DREWS_6_PL1X4 | PLANT_TROUBLE | 3015.9167
2023 | summer | DREWS_6_PL1X4 | TRANSMISSION_INDUCED | 732
2023 | summer | DRUM_7_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 2094.6
2023 | summer | DRUM_7_PL3X4 | AMBIENT_NOT_DUE_TO_TEMP | 6896.8333
2023 | summer | DRUM_7_PL3X4 | PLANT_TROUBLE | 919
2023 | summer | DRUM_7_UNIT 5 | AMBIENT_NOT_DUE_TO_TEMP | 1707.5
2023 | summer | DRUM_7_UNIT 5 | PLANT_MAINTENANCE | 300
2023 | summer | DRUM_7_UNIT 5 | PLANT_TROUBLE | 0
2023 | summer | DSABLA_7_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 1633.2267
2023 | summer | DSABLA_7_UNIT | TRANSMISSION_INDUCED | 1568.1
2023 | summer | DSFLWR_2_W9CSB1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 107.1
2023 | summer | DSFLWR_2_W9CSB1 | METERING_TELEMETRY | 0
2023 | summer | DSFLWR_2_W9CSB1 | PLANT_MAINTENANCE | 858
2023 | summer | DSFLWR_2_W9CSB1 | PLANT_TROUBLE | 1770.5
2023 | summer | DSFLWR_2_W9CSB2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 72
2023 | summer | DSFLWR_2_W9CSB2 | PLANT_MAINTENANCE | 1094
2023 | summer | DSFLWR_2_W9CSB2 | PLANT_TROUBLE | 1676.4833
2023 | summer | DSFLWR_2_WS2SR1 | PLANT_MAINTENANCE | 92.4333
2023 | summer | DSFLWR_2_WS2SR1 | PLANT_TROUBLE | 3795.2
2023 | summer | DSRTHV_2_DH1SR1 | PLANT_MAINTENANCE | 29.8
2023 | summer | DSRTHV_2_DH1SR1 | PLANT_TROUBLE | 390
2023 | summer | DSRTHV_2_DH2BT1 | PLANT_TROUBLE | 20906.1503
2023 | summer | DSRTSL_2_SOLAR1 | METERING_TELEMETRY | 0.703
2023 | summer | DSRTSL_2_SOLAR1 | PLANT_TROUBLE | 11550.4067
2023 | summer | DSRTSN_2_DS2X2 | METERING_TELEMETRY | 39.2
2023 | summer | DSRTSN_2_DS2X2 | PLANT_MAINTENANCE | 0
2023 | summer | DSRTSN_2_DS2X2 | PLANT_TROUBLE | 8454.071
2023 | summer | DSRTSN_2_DS2X2 | UNIT_TESTING | 6440
2023 | summer | DSRTSN_2_SOLAR1 | METERING_TELEMETRY | 1500
2023 | summer | DUANE_1_PL1X3 | AMBIENT_DUE_TO_TEMP | 5967
2023 | summer | DUANE_1_PL1X3 | PLANT_TROUBLE | 6179.05
2023 | summer | DURNMESA_3_WBDYN | AMBIENT_DUE_TO_TEMP | 140
2023 | summer | DURNMESA_3_WBDYN | TRANSITIONAL_LIMITATION | 1737.926
2023 | summer | DUTCH1_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 3371.15
2023 | summer | DUTCH1_7_UNIT 1 | PLANT_MAINTENANCE | 56.3167
2023 | summer | DUTCH1_7_UNIT 1 | TRANSMISSION_INDUCED | 495
2023 | summer | DUTCH2_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 6250
2023 | summer | DUTCH2_7_UNIT 1 | PLANT_TROUBLE | 64.1
2023 | summer | DUTCH2_7_UNIT 1 | TRANSMISSION_INDUCED | 637
2023 | summer | DVLCYN_1_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 234.0833
2023 | summer | DVLCYN_1_UNITS | OTHER_USE_LIMIT_REACHED | 0
2023 | summer | DVLCYN_1_UNITS | PLANT_MAINTENANCE | 1575
2023 | summer | DVLCYN_1_UNITS | PLANT_TROUBLE | 57.25
2023 | summer | DVLCYN_1_UNITS | TRANSMISSION_INDUCED | 343.6667
2023 | summer | DYERSM_6_DSWWD1 | ENVIRONMENTAL_RESTRICTIONS | 1380.6967
2023 | summer | DYERSM_6_DSWWD1 | PLANT_MAINTENANCE | 19.4133
2023 | summer | DYERSM_6_DSWWD1 | PLANT_TROUBLE | 7.35
2023 | summer | DYERSM_6_DSWWD1 | TRANSMISSION_INDUCED | 242.2083
2023 | summer | EASTWD_7_UNIT | PLANT_TROUBLE | 65400
2023 | summer | EASTWD_7_UNIT | TRANSMISSION_INDUCED | 42800
2023 | summer | EDMONS_2_NSPIN | METERING_TELEMETRY | 535.3333
2023 | summer | EDMONS_2_NSPIN | PLANT_TROUBLE | 35037
2023 | summer | EDWARD_2_E21SB1 | METERING_TELEMETRY | 0
2023 | summer | EDWARD_2_E21SB1 | PLANT_TROUBLE | 456.5
2023 | summer | EDWARD_2_E21SB1 | UNIT_TESTING | 0
2023 | summer | EDWARD_2_E23SB1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 34.2667
2023 | summer | EDWARD_2_E23SB1 | PLANT_TROUBLE | 36
2023 | summer | EDWARD_2_E23SB1 | UNIT_TESTING | 48
2023 | summer | EDWARD_2_ES2BT3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 148.4
2023 | summer | EDWARD_2_ES2BT3 | METERING_TELEMETRY | 0
2023 | summer | EDWARD_2_ES2BT3 | PLANT_TROUBLE | 422.8
2023 | summer | EDWARD_2_ES2BT3 | UNIT_TESTING | 0
2023 | summer | EEKTMN_6_SOLAR1 | METERING_TELEMETRY | 278
2023 | summer | EEKTMN_6_SOLAR1 | PLANT_TROUBLE | 3123
2023 | summer | EEKTMN_6_SOLAR1 | TRANSMISSION_INDUCED | 0
2023 | summer | ELCABO_5_ECWSCEDYN | AMBIENT_DUE_TO_TEMP | 1335
2023 | summer | ELCABO_5_ECWSCEDYN | PLANT_MAINTENANCE | 0
2023 | summer | ELCABO_5_ECWSCEDYN | TRANSMISSION_INDUCED | 22146.8167
2023 | summer | ELCAJN_6_EB1BT1 | PLANT_MAINTENANCE | 102
2023 | summer | ELCAJN_6_EB1BT1 | PLANT_TROUBLE | 588
2023 | summer | ELCAJN_6_LM6K | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 13624.9133
2023 | summer | ELCAJN_6_LM6K | AMBIENT_DUE_TO_TEMP | 13
2023 | summer | ELCAJN_6_LM6K | PLANT_MAINTENANCE | 0
2023 | summer | ELCAJN_6_LM6K | PLANT_TROUBLE | 30.8267
2023 | summer | ELCAJN_6_LM6K | TRANSMISSION_INDUCED | 0
2023 | summer | ELCAJN_6_LM6K | UNIT_TESTING | 4.0667
2023 | summer | ELCAJN_6_UNITA1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 2167.6403
2023 | summer | ELCAJN_6_UNITA1 | PLANT_TROUBLE | 440.9743
2023 | summer | ELDORO_7_UNIT 1 | PLANT_TROUBLE | 0
2023 | summer | ELDORO_7_UNIT 2 | PLANT_TROUBLE | 0
2023 | summer | ELECTR_7_PL1X3 | AMBIENT_NOT_DUE_TO_TEMP | 1617.3
2023 | summer | ELKCRK_6_STONYG | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 2376.5
2023 | summer | ELKHIL_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 39864.5
2023 | summer | ELKHIL_2_PL1X3 | PLANT_MAINTENANCE | 1467
2023 | summer | ELKHIL_2_PL1X3 | PLANT_TROUBLE | 1420.3333
2023 | summer | ELKHRN_1_EESX3 | PLANT_MAINTENANCE | 14592.9
2023 | summer | ELKHRN_1_EESX3 | PLANT_TROUBLE | 15.4
2023 | summer | ELNIDP_6_BIOMAS | PLANT_MAINTENANCE | 1575
2023 | summer | ELSEGN_2_UN1011 | AMBIENT_DUE_TO_TEMP | 1332.962
2023 | summer | ELSEGN_2_UN1011 | PLANT_MAINTENANCE | 2176.1927
2023 | summer | ELSEGN_2_UN1011 | PLANT_TROUBLE | 14517.1198
2023 | summer | ELSEGN_2_UN2021 | AMBIENT_DUE_TO_TEMP | 881.341
2023 | summer | ELSEGN_2_UN2021 | PLANT_MAINTENANCE | 4741.863
2023 | summer | ELSEGN_2_UN2021 | PLANT_TROUBLE | 398.552
2023 | summer | ENERSJ_2_WIND | PLANT_TROUBLE | 351.75
2023 | summer | ENERSJ_2_WIND | TRANSMISSION_INDUCED | 234.05
2023 | summer | ENERSJ_5_ESJWD2 | PLANT_TROUBLE | 0
2023 | summer | ENERSJ_5_ESJWD2 | TRANSMISSION_INDUCED | 162.75
2023 | summer | ESCNDO_6_EB1BT1 | PLANT_MAINTENANCE | 0
2023 | summer | ESCNDO_6_EB1BT1 | PLANT_TROUBLE | 764
2023 | summer | ESCNDO_6_EB2BT2 | METERING_TELEMETRY | 45
2023 | summer | ESCNDO_6_EB2BT2 | PLANT_MAINTENANCE | 0
2023 | summer | ESCNDO_6_EB2BT2 | PLANT_TROUBLE | 1427.5
2023 | summer | ESCNDO_6_EB3BT3 | PLANT_MAINTENANCE | 0
2023 | summer | ESCNDO_6_EB3BT3 | PLANT_TROUBLE | 988
2023 | summer | ESCNDO_6_PL1X2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 6.968
2023 | summer | ESCNDO_6_PL1X2 | AMBIENT_DUE_TO_TEMP | 279.87
2023 | summer | ESCNDO_6_PL1X2 | PLANT_MAINTENANCE | 86.0543
2023 | summer | ESCNDO_6_PL1X2 | PLANT_TROUBLE | 75.5005
2023 | summer | ESCNDO_6_PL1X2 | TRANSMISSION_INDUCED | 0
2023 | summer | ESCNDO_6_UNITB1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 460.8
2023 | summer | ESCNDO_6_UNITB1 | PLANT_MAINTENANCE | 1015.2453
2023 | summer | ESCNDO_6_UNITB1 | PLANT_TROUBLE | 2449.886
2023 | summer | ESCO_6_GLMQF | PLANT_TROUBLE | 2361.45
2023 | summer | ESCO_6_GLMQF | TRANSMISSION_INDUCED | 0
2023 | summer | ESNHWR_2_WC1BT1 | PLANT_MAINTENANCE | 62.7
2023 | summer | ESNHWR_2_WC1BT1 | PLANT_TROUBLE | 358.75
2023 | summer | ESQUON_6_LNDFIL | PLANT_MAINTENANCE | 5.11
2023 | summer | ESQUON_6_LNDFIL | PLANT_TROUBLE | 47.46
2023 | summer | ESQUON_6_LNDFIL | TRANSMISSION_INDUCED | 92.4
2023 | summer | ESTWND_2_OPPWD1 | PLANT_TROUBLE | 0
2023 | summer | ETIWND_2_FONTNA | AMBIENT_NOT_DUE_TO_TEMP | 934.825
2023 | summer | ETIWND_2_FONTNA | PLANT_TROUBLE | 237.4
2023 | summer | ETIWND_2_FONTNA | TRANSMISSION_INDUCED | 1
2023 | summer | ETIWND_2_RTS010 | PLANT_TROUBLE | 780
2023 | summer | ETIWND_2_RTS015 | PLANT_TROUBLE | 1590
2023 | summer | ETIWND_2_RTS017 | PLANT_TROUBLE | 1855
2023 | summer | ETIWND_2_RTS018 | PLANT_TROUBLE | 780
2023 | summer | ETIWND_2_RTS023 | PLANT_TROUBLE | 1300
2023 | summer | ETIWND_2_RTS026 | PLANT_TROUBLE | 3180
2023 | summer | ETIWND_2_RTS027 | PLANT_TROUBLE | 1040
2023 | summer | ETIWND_2_UNIT1 | AMBIENT_NOT_DUE_TO_TEMP | 22120
2023 | summer | ETIWND_2_UNIT1 | PLANT_TROUBLE | 8.3
2023 | summer | ETIWND_6_GRPLND | AMBIENT_DUE_TO_TEMP | 598.14
2023 | summer | ETIWND_6_GRPLND | METERING_TELEMETRY | 231.43
2023 | summer | ETIWND_6_GRPLND | OTHER_USE_LIMIT_REACHED | 9.128
2023 | summer | ETIWND_6_GRPLND | PLANT_MAINTENANCE | 456.4
2023 | summer | ETIWND_6_GRPLND | PLANT_TROUBLE | 1565.915
2023 | summer | EXCHEC_7_UNIT 1 | PLANT_MAINTENANCE | 0
2023 | summer | EXCHEC_7_UNIT 1 | PLANT_TROUBLE | 19912
2023 | summer | EXCHEC_7_UNIT 1 | TRANSMISSION_INDUCED | 56
2023 | summer | EXCHEC_7_UNIT 1 | UNIT_TESTING | 472.5
2023 | summer | EXCLSG_1_SOLAR | PLANT_TROUBLE | 2502.75
2023 | summer | FALBRK_6_FESBT1 | METERING_TELEMETRY | 1473
2023 | summer | FALBRK_6_FESBT1 | PLANT_MAINTENANCE | 25
2023 | summer | FALBRK_6_FESBT1 | PLANT_TROUBLE | 4670.6333
2023 | summer | FALBRK_6_FESBT1 | TRANSMISSION_INDUCED | 225.1667
2023 | summer | FIFTHS_2_FSSBT | NEW_GENERATOR_TEST_ENERGY | 0
2023 | summer | FIFTHS_2_FSSBT | PLANT_MAINTENANCE | 1370
2023 | summer | FIFTHS_2_FSSBT | PLANT_TROUBLE | 9
2023 | summer | FIFTHS_2_FSSBT | UNIT_TESTING | 1163.35
2023 | summer | FIFTHS_2_FSSR1 | NEW_GENERATOR_TEST_ENERGY | 9975.2
2023 | summer | FIFTHS_2_FSSR1 | PLANT_MAINTENANCE | 0
2023 | summer | FLOWD2_2_FPLWND | METERING_TELEMETRY | 3.5
2023 | summer | FLOWD2_2_FPLWND | PLANT_MAINTENANCE | 2592.9067
2023 | summer | FLOWD2_2_FPLWND | TRANSMISSION_INDUCED | 254.9167
2023 | summer | FMEADO_6_HELLHL | PLANT_MAINTENANCE | 1.95
2023 | summer | FMEADO_6_HELLHL | PLANT_TROUBLE | 187.25
2023 | summer | FMEADO_6_HELLHL | TRANSMISSION_INDUCED | 3
2023 | summer | FMEADO_7_UNIT | PLANT_TROUBLE | 1072
2023 | summer | FMEADO_7_UNIT | RTU_RIG | 22.4
2023 | summer | FORBST_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 100.6667
2023 | summer | FORKBU_6_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 9084.4967
2023 | summer | FORKBU_6_UNIT | PLANT_TROUBLE | 9.2
2023 | summer | FORKBU_6_UNIT | TRANSMISSION_INDUCED | 20.8
2023 | summer | FRESHW_1_SOLAR1 | PLANT_TROUBLE | 157.3333
2023 | summer | FRESHW_1_SOLAR1 | TRANSMISSION_INDUCED | 160
2023 | summer | FRNTBW_6_SOLAR1 | PLANT_MAINTENANCE | 20
2023 | summer | FRNTBW_6_SOLAR1 | PLANT_TROUBLE | 137.3333
2023 | summer | FRNTBW_6_SOLAR1 | TRANSMISSION_INDUCED | 140
2023 | summer | FROGTN_1_UTICAA | PLANT_MAINTENANCE | 0
2023 | summer | FROGTN_1_UTICAA | PLANT_TROUBLE | 2.6833
2023 | summer | FROGTN_1_UTICAA | TRANSMISSION_INDUCED | 5.0633
2023 | summer | FROGTN_1_UTICAM | PLANT_MAINTENANCE | 18
2023 | summer | FROGTN_1_UTICAM | PLANT_TROUBLE | 10.98
2023 | summer | FROGTN_1_UTICAM | TRANSMISSION_INDUCED | 41.88
2023 | summer | FTSWRD_6_TRFORK | TRANSMISSION_INDUCED | 105.95
2023 | summer | FTSWRD_7_QFUNTS | TRANSMISSION_INDUCED | 104
2023 | summer | GALE_1_SR3SR3 | PLANT_MAINTENANCE | 13.8
2023 | summer | GALE_1_SR3SR3 | PLANT_TROUBLE | 61.87
2023 | summer | GANSO_1_WSTBM1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2023 | summer | GANSO_1_WSTBM1 | PLANT_MAINTENANCE | 0
2023 | summer | GANSO_1_WSTBM1 | PLANT_TROUBLE | 0
2023 | summer | GARLND_2_GARBT1 | METERING_TELEMETRY | 0
2023 | summer | GARLND_2_GARBT1 | PLANT_TROUBLE | 15583.6833
2023 | summer | GARLND_2_GARBT1 | UNIT_TESTING | 2069.1667
2023 | summer | GARLND_2_GASLR | METERING_TELEMETRY | 0
2023 | summer | GARLND_2_GASLR | PLANT_MAINTENANCE | 86.4
2023 | summer | GARLND_2_GASLR | PLANT_TROUBLE | 21589.704
2023 | summer | GARLND_2_GASLR | UNIT_TESTING | 237.6
2023 | summer | GARLND_2_GASLRA | PLANT_TROUBLE | 101.61
2023 | summer | GARLND_2_GASLRA | UNIT_TESTING | 10
2023 | summer | GARNET_1_WIND | PLANT_MAINTENANCE | 75
2023 | summer | GARNET_1_WIND | PLANT_TROUBLE | 1059.6083
2023 | summer | GARNET_1_WIND | TRANSMISSION_INDUCED | 19.2
2023 | summer | GARNET_1_WINDS | PLANT_MAINTENANCE | 1301.2
2023 | summer | GARNET_1_WINDS | PLANT_TROUBLE | 0
2023 | summer | GARNET_1_WT3WND | METERING_TELEMETRY | 0
2023 | summer | GARNET_1_WT3WND | PLANT_TROUBLE | 30
2023 | summer | GARNET_1_WT3WND | TRANSMISSION_INDUCED | 80.38
2023 | summer | GARNET_2_COAWD2 | PLANT_TROUBLE | 1447.38
2023 | summer | GARNET_2_COAWD2 | TRANSMISSION_INDUCED | 116.944
2023 | summer | GARNET_2_HYDRO | AMBIENT_NOT_DUE_TO_TEMP | 310
2023 | summer | GARNET_2_HYDRO | PLANT_TROUBLE | 12.5
2023 | summer | GARNET_2_WIND1 | ENVIRONMENTAL_RESTRICTIONS | 387.1233
2023 | summer | GARNET_2_WIND1 | METERING_TELEMETRY | 0
2023 | summer | GARNET_2_WIND1 | PLANT_MAINTENANCE | 12.6
2023 | summer | GARNET_2_WIND1 | PLANT_TROUBLE | 2846.5617
2023 | summer | GARNET_2_WIND1 | TRANSMISSION_INDUCED | 0
2023 | summer | GARNET_2_WIND2 | PLANT_MAINTENANCE | 2300.7842
2023 | summer | GARNET_2_WIND3 | PLANT_TROUBLE | 3150
2023 | summer | GARNET_2_WIND3 | TRANSMISSION_INDUCED | 12.6
2023 | summer | GARNET_2_WIND4 | METERING_TELEMETRY | 34.9117
2023 | summer | GARNET_2_WIND4 | PLANT_TROUBLE | 518.0933
2023 | summer | GARNET_2_WIND4 | TRANSMISSION_INDUCED | 21.9883
2023 | summer | GARNET_2_WIND5 | METERING_TELEMETRY | 180
2023 | summer | GARNET_2_WIND5 | PLANT_TROUBLE | 246.4
2023 | summer | GARNET_2_WIND5 | TRANSMISSION_INDUCED | 1200
2023 | summer | GASKW1_2_GW1SR1 | METERING_TELEMETRY | 85.8
2023 | summer | GASKW1_2_GW1SR1 | PLANT_MAINTENANCE | 86.24
2023 | summer | GASKW1_2_GW1SR1 | PLANT_TROUBLE | 6027.356
2023 | summer | GASKW1_2_GW2BT1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | summer | GASKW1_2_GW2BT1 | METERING_TELEMETRY | 855
2023 | summer | GASKW1_2_GW2BT1 | PLANT_MAINTENANCE | 1685.4283
2023 | summer | GASKW1_2_GW2BT1 | PLANT_TROUBLE | 32.8667
2023 | summer | GASKW1_2_GW2BT1 | TRANSMISSION_INDUCED | 0
2023 | summer | GASKW1_2_GW2SR1 | PLANT_MAINTENANCE | 0
2023 | summer | GASKW1_2_GW2SR1 | PLANT_TROUBLE | 370.9333
2023 | summer | GASKW1_2_GW2SR2 | METERING_TELEMETRY | 502.6667
2023 | summer | GASKW1_2_GW2SR2 | PLANT_MAINTENANCE | 0
2023 | summer | GASKW1_2_GW2SR2 | PLANT_TROUBLE | 522.5313
2023 | summer | GASKW1_2_GW2SR2 | TRANSMISSION_INDUCED | 140.1667
2023 | summer | GASKW1_2_GW3SR1 | METERING_TELEMETRY | 0
2023 | summer | GASKW1_2_GW3SR1 | PLANT_MAINTENANCE | 70.6667
2023 | summer | GASKW1_2_GW3SR1 | PLANT_TROUBLE | 130
2023 | summer | GASKW1_2_GW4SR1 | METERING_TELEMETRY | 0
2023 | summer | GASKW1_2_GW4SR1 | PLANT_MAINTENANCE | 70.6667
2023 | summer | GASKW1_2_GW4SR1 | PLANT_TROUBLE | 425.97
2023 | summer | GASKW1_2_GW5SR1 | METERING_TELEMETRY | 0
2023 | summer | GASKW1_2_GW5SR1 | PLANT_MAINTENANCE | 70.6667
2023 | summer | GASKW1_2_GW5SR1 | PLANT_TROUBLE | 107.5833
2023 | summer | GATEWY_2_GESBT1 | PLANT_MAINTENANCE | 0
2023 | summer | GATEWY_2_GESBT1 | PLANT_TROUBLE | 6804.1667
2023 | summer | GATWAY_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 66672.115
2023 | summer | GATWAY_2_PL1X3 | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | summer | GATWAY_2_PL1X3 | METERING_TELEMETRY | 48.58
2023 | summer | GATWAY_2_PL1X3 | PLANT_TROUBLE | 8374.5667
2023 | summer | GATWAY_2_PL1X3 | UNIT_TESTING | 0
2023 | summer | GENESI_2_STG | AMBIENT_NOT_DUE_TO_TEMP | 9466.6667
2023 | summer | GENESI_2_STG | PLANT_TROUBLE | 0
2023 | summer | GEYS11_7_UNIT11 | AMBIENT_NOT_DUE_TO_TEMP | 11983.29
2023 | summer | GEYS11_7_UNIT11 | PLANT_TROUBLE | 2876.0798
2023 | summer | GEYS12_7_UNIT12 | AMBIENT_NOT_DUE_TO_TEMP | 12915
2023 | summer | GEYS13_7_UNIT13 | AMBIENT_NOT_DUE_TO_TEMP | 21030
2023 | summer | GEYS13_7_UNIT13 | PLANT_TROUBLE | 194.7333
2023 | summer | GEYS14_7_UNIT14 | AMBIENT_NOT_DUE_TO_TEMP | 12987
2023 | summer | GEYS14_7_UNIT14 | PLANT_TROUBLE | 0
2023 | summer | GEYS16_7_UNIT16 | AMBIENT_NOT_DUE_TO_TEMP | 14112
2023 | summer | GEYS17_7_UNIT17 | AMBIENT_NOT_DUE_TO_TEMP | 14961.8833
2023 | summer | GEYS17_7_UNIT17 | PLANT_TROUBLE | 1590
2023 | summer | GEYS17_7_UNIT17 | TRANSITIONAL_LIMITATION | 114
2023 | summer | GEYS18_7_UNIT18 | AMBIENT_NOT_DUE_TO_TEMP | 25941
2023 | summer | GEYS18_7_UNIT18 | PLANT_TROUBLE | 350
2023 | summer | GEYS18_7_UNIT18 | UNIT_TESTING | 0
2023 | summer | GEYS20_7_UNIT20 | AMBIENT_NOT_DUE_TO_TEMP | 11454
2023 | summer | GEYS20_7_UNIT20 | PLANT_TROUBLE | 47.3
2023 | summer | GIFENS_6_BUGSL1 | PLANT_TROUBLE | 20
2023 | summer | GIFFEN_6_SOLAR | PLANT_TROUBLE | 69.5
2023 | summer | GILROY_1_UNIT | AMBIENT_DUE_TO_TEMP | 7461.7
2023 | summer | GILROY_1_UNIT | PLANT_MAINTENANCE | 0
2023 | summer | GILROY_1_UNIT | TRANSITIONAL_LIMITATION | 49.0885
2023 | summer | GILROY_1_UNIT | TRANSMISSION_INDUCED | 90
2023 | summer | GILRPP_1_PL1X2 | PLANT_TROUBLE | 56.2083
2023 | summer | GILRPP_1_PL1X2 | TRANSMISSION_INDUCED | 71.4
2023 | summer | GILRPP_1_PL3X4 | PLANT_TROUBLE | 0
2023 | summer | GILRPP_1_PL3X4 | TRANSMISSION_INDUCED | 34.65
2023 | summer | GLDFGR_6_SOLAR1 | PLANT_TROUBLE | 100
2023 | summer | GLDFGR_6_SOLAR2 | PLANT_MAINTENANCE | 28.5
2023 | summer | GLDFGR_6_SOLAR2 | PLANT_TROUBLE | 0
2023 | summer | GLDTWN_6_COLUM3 | METERING_TELEMETRY | 0
2023 | summer | GLDTWN_6_COLUM3 | PLANT_TROUBLE | 20
2023 | summer | GLDTWN_6_SOLAR | PLANT_MAINTENANCE | 7.5
2023 | summer | GLNARM_2_UNIT 5 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 16.291
2023 | summer | GLNARM_2_UNIT 5 | AMBIENT_DUE_TO_TEMP | 2.3715
2023 | summer | GLNARM_2_UNIT 5 | PLANT_MAINTENANCE | 197.43
2023 | summer | GLNARM_2_UNIT 5 | PLANT_TROUBLE | 377.5735
2023 | summer | GLNARM_2_UNIT 5 | TRANSMISSION_INDUCED | 137.13
2023 | summer | GLNARM_2_UNIT 5 | UNIT_TESTING | 0
2023 | summer | GLNARM_7_UNIT 1 | PLANT_TROUBLE | 11.4338
2023 | summer | GLNARM_7_UNIT 1 | UNIT_TESTING | 0
2023 | summer | GLNARM_7_UNIT 2 | PLANT_MAINTENANCE | 0
2023 | summer | GLNARM_7_UNIT 2 | PLANT_TROUBLE | 93.25
2023 | summer | GLNARM_7_UNIT 2 | UNIT_TESTING | 0
2023 | summer | GLNARM_7_UNIT 3 | PLANT_TROUBLE | 720.0465
2023 | summer | GLNARM_7_UNIT 3 | UNIT_TESTING | 0
2023 | summer | GLNARM_7_UNIT 4 | PLANT_MAINTENANCE | 81.305
2023 | summer | GLNARM_7_UNIT 4 | PLANT_TROUBLE | 869.705
2023 | summer | GLNARM_7_UNIT 4 | UNIT_TESTING | 0
2023 | summer | GLOW_6_SOLAR | METERING_TELEMETRY | 10
2023 | summer | GLOW_6_SOLAR | PLANT_MAINTENANCE | 20
2023 | summer | GLOW_6_SOLAR | PLANT_TROUBLE | 3.3
2023 | summer | GOLETA_2_VALBT1 | PLANT_MAINTENANCE | 12.2
2023 | summer | GOLETA_2_VALBT1 | PLANT_TROUBLE | 103.2617
2023 | summer | GOLETA_2_VALBT1 | UNIT_TESTING | 50
2023 | summer | GOLETA_6_ELLWOD | PLANT_TROUBLE | 300.6
2023 | summer | GOLETA_6_TR2BM2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 13.5652
2023 | summer | GOLETA_6_TR2BM2 | AMBIENT_NOT_DUE_TO_TEMP | 94.5545
2023 | summer | GOLETA_6_TR2BM2 | PLANT_MAINTENANCE | 30.678
2023 | summer | GOLETA_6_TR2BM2 | PLANT_TROUBLE | 18.3667
2023 | summer | GONZLS_6_UNIT | PLANT_MAINTENANCE | 6.035
2023 | summer | GONZLS_6_UNIT | PLANT_TROUBLE | 41.7717
2023 | summer | GRADYW_5_GDYWD1 | AMBIENT_DUE_TO_TEMP | 700
2023 | summer | GRADYW_5_GDYWD1 | PLANT_TROUBLE | 3222
2023 | summer | GRADYW_5_GDYWD1 | TRANSITIONAL_LIMITATION | 1260.6667
2023 | summer | GRIDLY_6_SOLAR | PLANT_TROUBLE | 0
2023 | summer | GRIZLY_1_UNIT 1 | TRANSMISSION_INDUCED | 15300
2023 | summer | GRNLF1_1_PL1X2 | PLANT_MAINTENANCE | 1620
2023 | summer | GRNLF1_1_PL1X2 | PLANT_TROUBLE | 4162.5
2023 | summer | GRNLF1_1_PL1X2 | UNIT_TESTING | 0
2023 | summer | GRNLF2_1_UNIT | PLANT_TROUBLE | 24501.14
2023 | summer | GRNVLY_7_SCLAND | PLANT_MAINTENANCE | 45.76
2023 | summer | GRNVLY_7_SCLAND | PLANT_TROUBLE | 151.5657
2023 | summer | GRSCRK_6_BGCKWW | AMBIENT_NOT_DUE_TO_TEMP | 3275
2023 | summer | GRSCRK_6_BGCKWW | PLANT_TROUBLE | 0
2023 | summer | GUERNS_6_HD3BM3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 9.925
2023 | summer | GUERNS_6_HD3BM3 | PLANT_MAINTENANCE | 0.56667
2023 | summer | GUERNS_6_HD3BM3 | PLANT_TROUBLE | 12.25
2023 | summer | GUERNS_6_SOLAR | PLANT_TROUBLE | 0
2023 | summer | GUERNS_6_SOLAR | TRANSMISSION_INDUCED | 50
2023 | summer | GUERNS_6_VH2BM1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 6
2023 | summer | GUERNS_6_VH2BM1 | PLANT_MAINTENANCE | 25
2023 | summer | GUERNS_6_VH2BM1 | PLANT_TROUBLE | 56.25
2023 | summer | GWFPWR_1_UNITS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1969.2
2023 | summer | GWFPWR_1_UNITS | AMBIENT_DUE_TO_TEMP | 202.0163
2023 | summer | GWFPWR_1_UNITS | OTHER_USE_LIMIT_REACHED | 5891.19
2023 | summer | GWFPWR_1_UNITS | PLANT_MAINTENANCE | 738.45
2023 | summer | GWFPWR_1_UNITS | UNIT_TESTING | 0
2023 | summer | GYS5X6_7_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 12109.05
2023 | summer | GYS5X6_7_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 5625.9
2023 | summer | GYS5X6_7_UNITS | PLANT_TROUBLE | 0
2023 | summer | GYS5X6_7_UNITS | PLANT_TROUBLE | 4530
2023 | summer | GYS7X8_7_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 13898
2023 | summer | GYS7X8_7_UNITS | PLANT_TROUBLE | 455
2023 | summer | GYS7X8_7_UNITS | TRANSITIONAL_LIMITATION | 36
2023 | summer | GYSRVL_7_WSPRNG | METERING_TELEMETRY | 0
2023 | summer | HAASPH_7_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 4290.9333
2023 | summer | HAASPH_7_PL1X2 | ANNUAL_USE_LIMIT_REACHED | 0
2023 | summer | HAASPH_7_PL1X2 | PLANT_MAINTENANCE | 2191.2
2023 | summer | HAASPH_7_PL1X2 | PLANT_TROUBLE | 824
2023 | summer | HAASPH_7_PL1X2 | TRANSMISSION_INDUCED | 144
2023 | summer | HAASPH_7_PL1X2 | UNIT_SUPPORTING_STARTUP | 0
2023 | summer | HAASPH_7_PL1X2 | UNIT_TESTING | 410
2023 | summer | HARBGN_7_UNITS | AMBIENT_DUE_TO_TEMP | 6140.9
2023 | summer | HARBGN_7_UNITS | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | summer | HARBGN_7_UNITS | PLANT_TROUBLE | 1860.5612
2023 | summer | HARBGN_7_UNITS | TRANSMISSION_INDUCED | 810.3077
2023 | summer | HARBGN_7_UNITS | UNIT_TESTING | 209.7925
2023 | summer | HARDWK_6_STWBM1 | PLANT_MAINTENANCE | 0
2023 | summer | HARDWK_6_STWBM1 | PLANT_TROUBLE | 11.3333
2023 | summer | HATCR1_7_UNIT | PLANT_TROUBLE | 20.5417
2023 | summer | HATCR2_7_UNIT | PLANT_TROUBLE | 3924.1667
2023 | summer | HATLOS_6_LSCRK | AMBIENT_NOT_DUE_TO_TEMP | 654.85
2023 | summer | HATLOS_6_LSCRK | TRANSMISSION_INDUCED | 0
2023 | summer | HAYPRS_6_HAYHD1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 2668
2023 | summer | HAYPRS_6_HAYHD1 | PLANT_TROUBLE | 29
2023 | summer | HAYPRS_6_HAYHD1 | TRANSMISSION_INDUCED | 29
2023 | summer | HAYPRS_6_HAYHD2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 2974.13
2023 | summer | HAYPRS_6_HAYHD2 | PLANT_TROUBLE | 33.5
2023 | summer | HAYPRS_6_HAYHD2 | TRANSMISSION_INDUCED | 33.5
2023 | summer | HELMPG_7_UNIT 1 | PLANT_TROUBLE | 2665.85
2023 | summer | HELMPG_7_UNIT 1 | TRANSMISSION_INDUCED | 3253.2167
2023 | summer | HELMPG_7_UNIT 2 | PLANT_TROUBLE | 8567.35
2023 | summer | HELMPG_7_UNIT 2 | TRANSMISSION_INDUCED | 85.5
2023 | summer | HELMPG_7_UNIT 3 | PLANT_TROUBLE | 11392.8
2023 | summer | HELMPG_7_UNIT 3 | TRANSMISSION_INDUCED | 606
2023 | summer | HENRTA_6_HDEBT1 | PLANT_MAINTENANCE | 0.5
2023 | summer | HENRTA_6_HDEBT1 | PLANT_TROUBLE | 7.1667
2023 | summer | HENRTA_6_HDEBT1 | TRANSMISSION_INDUCED | 0
2023 | summer | HENRTA_6_SOLAR1 | PLANT_TROUBLE | 1132.5
2023 | summer | HENRTA_6_UNITA1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 999.6
2023 | summer | HENRTA_6_UNITA1 | ENVIRONMENTAL_RESTRICTIONS | 37.485
2023 | summer | HENRTA_6_UNITA1 | OTHER_USE_LIMIT_REACHED | 1999.2
2023 | summer | HENRTA_6_UNITA1 | PLANT_MAINTENANCE | 1775.956
2023 | summer | HENRTA_6_UNITA1 | UNIT_TESTING | 89.79
2023 | summer | HENRTA_6_UNITA2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 988.4
2023 | summer | HENRTA_6_UNITA2 | OTHER_USE_LIMIT_REACHED | 1680.28
2023 | summer | HENRTA_6_UNITA2 | PLANT_MAINTENANCE | 1779.12
2023 | summer | HENRTA_6_UNITA2 | PLANT_TROUBLE | 64.246
2023 | summer | HENRTA_6_UNITA2 | UNIT_TESTING | 88.11
2023 | summer | HENRTS_1_SOLAR | PLANT_TROUBLE | 19.8333
2023 | summer | HERDLN_6_BYHSR1 | PLANT_TROUBLE | 210
2023 | summer | HERDLN_6_BYHSR1 | TRANSMISSION_INDUCED | 35
2023 | summer | HIDSRT_2_UNITS | AMBIENT_DUE_TO_TEMP | 2651.4
2023 | summer | HIDSRT_2_UNITS | PLANT_MAINTENANCE | 38250
2023 | summer | HIDSRT_2_UNITS | PLANT_TROUBLE | 9378.5
2023 | summer | HIDSRT_2_UNITS | UNIT_TESTING | 140.5
2023 | summer | HIGGNS_1_COMBIE | PLANT_TROUBLE | 16.25
2023 | summer | HIGGNS_1_COMBIE | TRANSMISSION_INDUCED | 0
2023 | summer | HIGHDS_2_H5SBT1 | METERING_TELEMETRY | 0
2023 | summer | HIGHDS_2_H5SBT1 | PLANT_MAINTENANCE | 0
2023 | summer | HIGHDS_2_H5SBT1 | PLANT_TROUBLE | 4715.004
2023 | summer | HIGHDS_2_H5SSR1 | PLANT_MAINTENANCE | 52.4253
2023 | summer | HINSON_6_LBECH1 | PLANT_TROUBLE | 2446.5
2023 | summer | HINSON_6_LBECH2 | ENVIRONMENTAL_RESTRICTIONS | 157.5
2023 | summer | HINSON_6_LBECH2 | PLANT_TROUBLE | 2299.5
2023 | summer | HINSON_6_LBECH4 | PLANT_TROUBLE | 113.4
2023 | summer | HINSON_6_SERRGN | PLANT_TROUBLE | 6848.1667
2023 | summer | HNTGBH_2_PL1X3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2023 | summer | HNTGBH_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 9526.8517
2023 | summer | HNTGBH_2_PL1X3 | AMBIENT_NOT_DUE_TO_TEMP | 9962
2023 | summer | HNTGBH_2_PL1X3 | METERING_TELEMETRY | 2
2023 | summer | HNTGBH_2_PL1X3 | PLANT_MAINTENANCE | 11914.35
2023 | summer | HNTGBH_2_PL1X3 | PLANT_TROUBLE | 22410.307
2023 | summer | HNTGBH_2_PL1X3 | UNIT_TESTING | 340.41
2023 | summer | HNTGBH_7_UNIT 2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 4536.8
2023 | summer | HNTGBH_7_UNIT 2 | AMBIENT_DUE_TO_TEMP | 149.0407
2023 | summer | HNTGBH_7_UNIT 2 | PLANT_TROUBLE | 6982.486
2023 | summer | HOLGAT_1_BORAX | PLANT_TROUBLE | 0
2023 | summer | HOOVER_2_MWDPT | AMBIENT_NOT_DUE_TO_TEMP | 82627
2023 | summer | HOOVER_2_MWDPT | PLANT_MAINTENANCE | 0
2023 | summer | HOOVER_2_SCEPT | AMBIENT_NOT_DUE_TO_TEMP | 87898.7425
2023 | summer | HOOVER_2_SCEPT | OTHER_USE_LIMIT_REACHED | 743.6667
2023 | summer | HOOVER_2_VEAPT | AMBIENT_NOT_DUE_TO_TEMP | 4160
2023 | summer | HOOVER_2_VEAPT | PLANT_MAINTENANCE | 0
2023 | summer | HUMBPP_1_UNITS3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 22.5068
2023 | summer | HUMBPP_1_UNITS3 | PLANT_TROUBLE | 845.65
2023 | summer | HUMBPP_1_UNITS3 | TRANSMISSION_INDUCED | 195.24
2023 | summer | HUMBPP_6_UNITS | PLANT_MAINTENANCE | 308.8588
2023 | summer | HUMBPP_6_UNITS | PLANT_TROUBLE | 270.082
2023 | summer | HURON_6_SOLAR | TRANSMISSION_INDUCED | 800
2023 | summer | HYTTHM_2_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 676.2333
2023 | summer | HYTTHM_2_UNITS | OTHER_USE_LIMIT_REACHED | 793.135
2023 | summer | HYTTHM_2_UNITS | PLANT_MAINTENANCE | 76647.6617
2023 | summer | HYTTHM_2_UNITS | PLANT_TROUBLE | 18885.6067
2023 | summer | INDIGO_1_UNIT 1 | AMBIENT_DUE_TO_TEMP | 1751.7317
2023 | summer | INDIGO_1_UNIT 1 | METERING_TELEMETRY | 302.325
2023 | summer | INDIGO_1_UNIT 1 | PLANT_MAINTENANCE | 0
2023 | summer | INDIGO_1_UNIT 1 | PLANT_TROUBLE | 370.475
2023 | summer | INDIGO_1_UNIT 1 | TRANSMISSION_INDUCED | 390.6667
2023 | summer | INDIGO_1_UNIT 2 | AMBIENT_DUE_TO_TEMP | 2355.955
2023 | summer | INDIGO_1_UNIT 2 | METERING_TELEMETRY | 201
2023 | summer | INDIGO_1_UNIT 2 | PLANT_MAINTENANCE | 0
2023 | summer | INDIGO_1_UNIT 2 | PLANT_TROUBLE | 400.8933
2023 | summer | INDIGO_1_UNIT 2 | TRANSMISSION_INDUCED | 306.4608
2023 | summer | INDIGO_1_UNIT 3 | AMBIENT_DUE_TO_TEMP | 2684.0583
2023 | summer | INDIGO_1_UNIT 3 | METERING_TELEMETRY | 199.5
2023 | summer | INDIGO_1_UNIT 3 | PLANT_MAINTENANCE | 0
2023 | summer | INDIGO_1_UNIT 3 | PLANT_TROUBLE | 199.5
2023 | summer | INDIGO_1_UNIT 3 | TRANSMISSION_INDUCED | 320.2417
2023 | summer | INDVLY_1_UNITS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 857.85
2023 | summer | INDVLY_1_UNITS | TRANSMISSION_INDUCED | 11.438
2023 | summer | INTKEP_2_UNITS | ENVIRONMENTAL_RESTRICTIONS | 37163
2023 | summer | INTKEP_2_UNITS | PLANT_MAINTENANCE | 8934.5
2023 | summer | INTKEP_2_UNITS | PLANT_TROUBLE | 1049.1
2023 | summer | INTKEP_2_UNITS | UNIT_TESTING | 2020
2023 | summer | INTMNT_3_ANAHEIM | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 17700
2023 | summer | INTMNT_3_ANAHEIM | PLANT_TROUBLE | 1426
2023 | summer | INTMNT_3_ANAHEIM | UNIT_TESTING | 342
2023 | summer | INTMNT_3_PASADENA | PLANT_MAINTENANCE | 185.8333
2023 | summer | INTMNT_3_PASADENA | PLANT_TROUBLE | 842.55
2023 | summer | INTMNT_3_PASADENA | UNIT_TESTING | 0
2023 | summer | INTMNT_3_RIVERSIDE | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 11893.7167
2023 | summer | INTTRB_6_UNIT | TRANSMISSION_INDUCED | 0
2023 | summer | IVANPA_1_UNIT1 | AMBIENT_DUE_TO_TEMP | 504
2023 | summer | IVANPA_1_UNIT1 | AMBIENT_NOT_DUE_TO_TEMP | 19434.2167
2023 | summer | IVANPA_1_UNIT1 | PLANT_TROUBLE | 4471.5833
2023 | summer | IVANPA_1_UNIT2 | AMBIENT_DUE_TO_TEMP | 0
2023 | summer | IVANPA_1_UNIT2 | AMBIENT_NOT_DUE_TO_TEMP | 55.4167
2023 | summer | IVANPA_1_UNIT2 | PLANT_TROUBLE | 6916
2023 | summer | IVANPA_1_UNIT3 | AMBIENT_DUE_TO_TEMP | 532
2023 | summer | IVANPA_1_UNIT3 | AMBIENT_NOT_DUE_TO_TEMP | 20583.5
2023 | summer | IVANPA_1_UNIT3 | PLANT_TROUBLE | 4777.1
2023 | summer | IVSLR2_2_SM2SR1 | ENVIRONMENTAL_RESTRICTIONS | 4075
2023 | summer | IVSLR2_2_SM2SR1 | PLANT_TROUBLE | 3137.9167
2023 | summer | IVSLR2_2_SM2SR1 | TRANSMISSION_INDUCED | 150
2023 | summer | IVSLRP_2_SOLAR1 | PLANT_MAINTENANCE | 32300
2023 | summer | IVSLRP_2_SOLAR1 | PLANT_TROUBLE | 1800
2023 | summer | IVWEST_2_SOLAR1 | PLANT_MAINTENANCE | 100
2023 | summer | JACMSR_1_JACSR1 | TRANSMISSION_INDUCED | 31.3333
2023 | summer | JANCRK_6_RCABT1 | PLANT_MAINTENANCE | 6.2417
2023 | summer | JANCRK_6_RCABT1 | PLANT_TROUBLE | 12.6292
2023 | summer | JAWBNE_2_NSRWND | METERING_TELEMETRY | 991
2023 | summer | JAWBNE_2_NSRWND | PLANT_MAINTENANCE | 9055.1433
2023 | summer | JAWBNE_2_NSRWND | PLANT_TROUBLE | 441.6913
2023 | summer | JAWBNE_2_SRWND | PLANT_MAINTENANCE | 57.1
2023 | summer | JAWBNE_2_SRWND | PLANT_TROUBLE | 3377.7
2023 | summer | JAWBNE_2_SRWWD2 | PLANT_MAINTENANCE | 83.7
2023 | summer | JAWBNE_2_SRWWD2 | PLANT_TROUBLE | 2920.52
2023 | summer | JAYNE_6_WLSLR | METERING_TELEMETRY | 53.1
2023 | summer | JAYNE_6_WLSLR | PLANT_TROUBLE | 90
2023 | summer | JOANEC_2_ST3BT3 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | summer | JOANEC_2_ST3BT3 | PLANT_TROUBLE | 39.0333
2023 | summer | JOANEC_2_STABT1 | PLANT_TROUBLE | 0
2023 | summer | JOANEC_2_STABT2 | PLANT_MAINTENANCE | 19.5
2023 | summer | JOANEC_2_STABT2 | PLANT_TROUBLE | 56.5
2023 | summer | JOHANN_2_JOSBT1 | PLANT_MAINTENANCE | 236.7667
2023 | summer | JOHANN_2_JOSBT1 | PLANT_TROUBLE | 54
2023 | summer | JOHANN_2_JOSBT2 | PLANT_MAINTENANCE | 106.15
2023 | summer | JOHANN_2_JOSBT2 | PLANT_TROUBLE | 209.7667
2023 | summer | JOHANN_2_OCEBT2 | METERING_TELEMETRY | 0
2023 | summer | JOHANN_2_OCEBT2 | PLANT_MAINTENANCE | 1.75
2023 | summer | JOHANN_2_OCEBT2 | PLANT_TROUBLE | 92.6
2023 | summer | JOHANN_2_OCEBT2 | TRANSMISSION_INDUCED | 41.55
2023 | summer | JOHANN_2_OCEBT2 | UNIT_TESTING | 45
2023 | summer | JOHANN_2_OCEBT3 | METERING_TELEMETRY | 0
2023 | summer | JOHANN_2_OCEBT3 | PLANT_MAINTENANCE | 0
2023 | summer | JOHANN_2_OCEBT3 | PLANT_TROUBLE | 2.8833
2023 | summer | JOHANN_2_OCEBT3 | TRANSMISSION_INDUCED | 27.7
2023 | summer | JOHANN_2_OCEBT3 | UNIT_TESTING | 30
2023 | summer | KANSAS_6_SOLAR | METERING_TELEMETRY | 49
2023 | summer | KANSAS_6_SOLAR | PLANT_TROUBLE | 224.6333
2023 | summer | KANSAS_6_SOLAR | TRANSMISSION_INDUCED | 13.3333
2023 | summer | KEARNY_6_NESBT1 | PLANT_TROUBLE | 792.9
2023 | summer | KEARNY_6_SESBT2 | PLANT_TROUBLE | 2.5
2023 | summer | KEKAWK_6_UNIT | PLANT_TROUBLE | 4081
2023 | summer | KELSO_2_UNITS | AMBIENT_DUE_TO_TEMP | 6903.8498
2023 | summer | KELSO_2_UNITS | ENVIRONMENTAL_RESTRICTIONS | 323.11
2023 | summer | KELSO_2_UNITS | PLANT_MAINTENANCE | 950.27
2023 | summer | KELSO_2_UNITS | PLANT_TROUBLE | 4096.4622
2023 | summer | KELSO_2_UNITS | TRANSMISSION_INDUCED | 4868.4
2023 | summer | KELYRG_6_UNIT | PLANT_TROUBLE | 0
2023 | summer | KELYRG_6_UNIT | TRANSMISSION_INDUCED | 42.1667
2023 | summer | KERKH2_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 8077.0433
2023 | summer | KERKH2_7_UNIT 1 | ANNUAL_USE_LIMIT_REACHED | 66.0267
2023 | summer | KERKH2_7_UNIT 1 | PLANT_TROUBLE | 379.4933
2023 | summer | KERKH2_7_UNIT 1 | TRANSITIONAL_LIMITATION | 7.7817
2023 | summer | KERMAN_6_SOLAR1 | PLANT_TROUBLE | 176.25
2023 | summer | KERMAN_6_SOLAR2 | PLANT_TROUBLE | 573.75
2023 | summer | KERNFT_1_UNITS | AMBIENT_DUE_TO_TEMP | 2257.8
2023 | summer | KERNFT_1_UNITS | PLANT_TROUBLE | 696.16
2023 | summer | KERNRG_1_UNITS | PLANT_MAINTENANCE | 1726.2133
2023 | summer | KERNRG_1_UNITS | PLANT_TROUBLE | 1875.0667
2023 | summer | KERNRG_1_UNITS | TRANSMISSION_INDUCED | 0
2023 | summer | KERRGN_1_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 2239
2023 | summer | KERRGN_1_UNIT 1 | PLANT_MAINTENANCE | 2822
2023 | summer | KERRGN_1_UNIT 1 | PLANT_TROUBLE | 449.92
2023 | summer | KERRGN_1_UNIT 1 | TRANSMISSION_INDUCED | 51.9
2023 | summer | KINGCO_1_KINGBR | PLANT_TROUBLE | 150.075
2023 | summer | KINGCO_1_KINGBR | TRANSMISSION_INDUCED | 2932.5
2023 | summer | KINGRV_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 772.22
2023 | summer | KINGRV_7_UNIT 1 | PLANT_TROUBLE | 796.7467
2023 | summer | KINGRV_7_UNIT 1 | TRANSMISSION_INDUCED | 51.2
2023 | summer | KIRKER_7_KELCYN | PLANT_MAINTENANCE | 79.1567
2023 | summer | KIRKER_7_KELCYN | PLANT_TROUBLE | 86.8178
2023 | summer | KIRKER_7_KELCYN | TRANSMISSION_INDUCED | 34.2
2023 | summer | KNGBRD_2_SOLAR1 | METERING_TELEMETRY | 10
2023 | summer | KNGBRD_2_SOLAR1 | PLANT_TROUBLE | 16
2023 | summer | KNGBRD_2_SOLAR2 | PLANT_TROUBLE | 420.5333
2023 | summer | KNGCTY_6_UNITA1 | PLANT_TROUBLE | 453.21
2023 | summer | KNTSTH_6_SOLAR | PLANT_MAINTENANCE | 20
2023 | summer | KNTSTH_6_SOLAR | PLANT_TROUBLE | 1190.5
2023 | summer | KNTSTH_6_WALSR1 | METERING_TELEMETRY | 0
2023 | summer | KNTSTH_6_WALSR1 | PLANT_MAINTENANCE | 0
2023 | summer | KNTSTH_6_WALSR1 | TRANSMISSION_INDUCED | 582.1527
2023 | summer | KRAMER_1_R1BX3 | METERING_TELEMETRY | 100
2023 | summer | KRAMER_1_R1BX3 | NEW_GENERATOR_TEST_ENERGY | 1050
2023 | summer | KRAMER_1_R1BX3 | PLANT_MAINTENANCE | 0
2023 | summer | KRAMER_1_R1BX3 | PLANT_TROUBLE | 903.4167
2023 | summer | KRAMER_1_R1BX3 | TRANSMISSION_INDUCED | 0
2023 | summer | KRAMER_1_R1BX3 | UNIT_TESTING | 875
2023 | summer | KRAMER_1_R1PX3 | METERING_TELEMETRY | 35
2023 | summer | KRAMER_1_R1PX3 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | summer | KRAMER_1_R1PX3 | PLANT_TROUBLE | 12
2023 | summer | KRAMER_1_R1PX3 | TRANSMISSION_INDUCED | 0
2023 | summer | KRAMER_1_R2BX2 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | summer | KRAMER_1_R2BX2 | PLANT_TROUBLE | 349.1
2023 | summer | KRAMER_1_R2BX2 | UNIT_TESTING | 0
2023 | summer | KRAMER_1_R2PX2 | NEW_GENERATOR_TEST_ENERGY | 48
2023 | summer | KRAMER_1_R2PX2 | PLANT_TROUBLE | 0
2023 | summer | KRAMER_2_SEGS 9 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 400
2023 | summer | KRAMER_2_SEGS 9 | AMBIENT_DUE_TO_TEMP | 400
2023 | summer | KRAMER_2_SEGS 9 | PLANT_TROUBLE | 275
2023 | summer | KRNCNY_6_UNIT | PLANT_TROUBLE | 381.2467
2023 | summer | KRNCNY_6_UNIT | TRANSMISSION_INDUCED | 49.1133
2023 | summer | KRNCNY_6_UNIT | UNIT_TESTING | 0
2023 | summer | KYCORA_6_KMSBT1 | PLANT_MAINTENANCE | 2
2023 | summer | KYCORA_6_KMSBT1 | PLANT_TROUBLE | 83.1083
2023 | summer | LAMONT_1_SOLAR1 | PLANT_TROUBLE | 1075
2023 | summer | LAMONT_1_SOLAR1 | UNIT_TESTING | 0
2023 | summer | LAMONT_1_SOLAR2 | PLANT_MAINTENANCE | 9.1
2023 | summer | LAMONT_1_SOLAR2 | PLANT_TROUBLE | 1357.4
2023 | summer | LAMONT_1_SOLAR3 | PLANT_TROUBLE | 609.9942
2023 | summer | LAMONT_1_SOLAR4 | PLANT_TROUBLE | 1333.5283
2023 | summer | LAMONT_1_SOLAR5 | PLANT_TROUBLE | 2488.5617
2023 | summer | LAPLMA_2_UNIT 1 | AMBIENT_DUE_TO_TEMP | 9331
2023 | summer | LAPLMA_2_UNIT 1 | PLANT_TROUBLE | 11961.2167
2023 | summer | LAPLMA_2_UNIT 1 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | summer | LAPLMA_2_UNIT 1 | TRANSMISSION_INDUCED | 1890
2023 | summer | LAPLMA_2_UNIT 1 | UNIT_TESTING | 0
2023 | summer | LAPLMA_2_UNIT 2 | AMBIENT_DUE_TO_TEMP | 5450
2023 | summer | LAPLMA_2_UNIT 2 | PLANT_TROUBLE | 5041.6833
2023 | summer | LAPLMA_2_UNIT 2 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | summer | LAPLMA_2_UNIT 2 | TRANSMISSION_INDUCED | 35874
2023 | summer | LAPLMA_2_UNIT 2 | UNIT_TESTING | 0
2023 | summer | LAPLMA_2_UNIT 3 | AMBIENT_DUE_TO_TEMP | 9742
2023 | summer | LAPLMA_2_UNIT 3 | PLANT_TROUBLE | 1386.2333
2023 | summer | LAPLMA_2_UNIT 3 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | summer | LAPLMA_2_UNIT 3 | TRANSMISSION_INDUCED | 1890
2023 | summer | LAPLMA_2_UNIT 3 | UNIT_TESTING | 109.7
2023 | summer | LAPLMA_2_UNIT 4 | AMBIENT_DUE_TO_TEMP | 7419.1667
2023 | summer | LAPLMA_2_UNIT 4 | PLANT_TROUBLE | 78857.6833
2023 | summer | LAPLMA_2_UNIT 4 | TRANSMISSION_INDUCED | 1865
2023 | summer | LARKSP_6_UNIT 1 | AMBIENT_DUE_TO_TEMP | 2451.51
2023 | summer | LARKSP_6_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | summer | LARKSP_6_UNIT 1 | PLANT_MAINTENANCE | 0
2023 | summer | LARKSP_6_UNIT 1 | PLANT_TROUBLE | 908.5
2023 | summer | LARKSP_6_UNIT 1 | TRANSMISSION_INDUCED | 60.59
2023 | summer | LARKSP_6_UNIT 2 | AMBIENT_DUE_TO_TEMP | 1478.9317
2023 | summer | LARKSP_6_UNIT 2 | PLANT_MAINTENANCE | 0
2023 | summer | LARKSP_6_UNIT 2 | PLANT_TROUBLE | 760.94
2023 | summer | LARKSP_6_UNIT 2 | TRANSMISSION_INDUCED | 188.6983
2023 | summer | LAROA2_2_UNITA1 | AMBIENT_DUE_TO_TEMP | 17001.9167
2023 | summer | LAROA2_2_UNITA1 | PLANT_MAINTENANCE | 1932
2023 | summer | LAROA2_2_UNITA1 | PLANT_TROUBLE | 7552.4167
2023 | summer | LAROA2_2_UNITA1 | UNIT_TESTING | 343.2
2023 | summer | LASSEN_6_UNITS | PLANT_TROUBLE | 1047.5
2023 | summer | LASSEN_6_UNITS | TRANSMISSION_INDUCED | 1650
2023 | summer | LCKHT1_2_LH1SR1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 212.5
2023 | summer | LCKHT1_2_LH1SR1 | METERING_TELEMETRY | 850
2023 | summer | LCKHT1_2_LH1SR1 | NEW_GENERATOR_TEST_ENERGY | 40
2023 | summer | LCKHT1_2_LH1SR1 | PLANT_TROUBLE | 425
2023 | summer | LCKHT1_2_LH1SR1 | UNIT_TESTING | 0
2023 | summer | LCKHT1_2_LH1SR2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 212.5
2023 | summer | LCKHT1_2_LH1SR2 | METERING_TELEMETRY | 750
2023 | summer | LCKHT1_2_LH1SR2 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | summer | LCKHT1_2_LH1SR2 | PLANT_TROUBLE | 1000
2023 | summer | LCKHT1_2_LH1SR2 | UNIT_TESTING | 0
2023 | summer | LEBECS_2_UNITS | AMBIENT_DUE_TO_TEMP | 11818.9978
2023 | summer | LEBECS_2_UNITS | PLANT_MAINTENANCE | 1781.29
2023 | summer | LEBECS_2_UNITS | PLANT_TROUBLE | 36350.71
2023 | summer | LEBECS_2_UNITS | TRANSITIONAL_LIMITATION | 2830.5617
2023 | summer | LECEF_1_UNITS | AMBIENT_DUE_TO_TEMP | 8037.7423
2023 | summer | LECEF_1_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | summer | LECEF_1_UNITS | PLANT_TROUBLE | 56208.9092
2023 | summer | LECEF_1_UNITS | TRANSITIONAL_LIMITATION | 318.3
2023 | summer | LECONT_2_LESBT1 | PLANT_MAINTENANCE | 462.5
2023 | summer | LECONT_2_LESBT1 | PLANT_TROUBLE | 2926.5333
2023 | summer | LECONT_2_LESBT1 | TRANSMISSION_INDUCED | 0
2023 | summer | LECONT_2_LESBT1 | UNIT_TESTING | 0
2023 | summer | LEPRFD_1_KANSAS | PLANT_TROUBLE | 1235.2
2023 | summer | LGHTHP_6_ICEGEN | PLANT_MAINTENANCE | 0
2023 | summer | LGHTHP_6_ICEGEN | PLANT_TROUBLE | 1884
2023 | summer | LGHTHP_6_ICEGEN | TRANSMISSION_INDUCED | 0
2023 | summer | LGHTHP_6_ICEGEN | UNIT_TESTING | 12
2023 | summer | LHILLS_6_SOLAR1 | METERING_TELEMETRY | 49.6667
2023 | summer | LHILLS_6_SOLAR1 | PLANT_TROUBLE | 83.5733
2023 | summer | LHILLS_6_SOLAR1 | TRANSMISSION_INDUCED | 1171
2023 | summer | LITLRK_6_GBCSR1 | PLANT_TROUBLE | 44.575
2023 | summer | LITLRK_6_SOLAR1 | PLANT_TROUBLE | 951.2
2023 | summer | LITLRK_6_SOLAR2 | PLANT_TROUBLE | 0
2023 | summer | LIVOAK_1_UNIT 1 | AMBIENT_DUE_TO_TEMP | 5157
2023 | summer | LIVOAK_1_UNIT 1 | PLANT_TROUBLE | 1262.84
2023 | summer | LMBEPK_2_UNITA1 | PLANT_TROUBLE | 482.3592
2023 | summer | LMBEPK_2_UNITA1 | TRANSMISSION_INDUCED | 0
2023 | summer | LMBEPK_2_UNITA2 | PLANT_TROUBLE | 4695.5358
2023 | summer | LMBEPK_2_UNITA2 | TRANSMISSION_INDUCED | 0
2023 | summer | LMBEPK_2_UNITA3 | AMBIENT_DUE_TO_TEMP | 89.4417
2023 | summer | LMBEPK_2_UNITA3 | PLANT_TROUBLE | 229.9958
2023 | summer | LMBEPK_2_UNITA3 | TRANSMISSION_INDUCED | 0
2023 | summer | LMEC_1_PL1X3 | AMBIENT_DUE_TO_TEMP | 16536.8167
2023 | summer | LMEC_1_PL1X3 | PLANT_MAINTENANCE | 9980.3333
2023 | summer | LMEC_1_PL1X3 | PLANT_TROUBLE | 33675.6167
2023 | summer | LMEC_1_PL1X3 | TRANSITIONAL_LIMITATION | 370
2023 | summer | LMEC_1_PL1X3 | TRANSMISSION_INDUCED | 5654
2023 | summer | LMEC_1_PL1X3 | UNIT_TESTING | 0
2023 | summer | LODI25_2_UNIT 1 | AMBIENT_DUE_TO_TEMP | 2217
2023 | summer | LODI25_2_UNIT 1 | PLANT_MAINTENANCE | 0
2023 | summer | LODI25_2_UNIT 1 | PLANT_TROUBLE | 0
2023 | summer | LODIEC_2_PL1X2 | AMBIENT_DUE_TO_TEMP | 20561.3
2023 | summer | LODIEC_2_PL1X2 | PLANT_MAINTENANCE | 10566.66
2023 | summer | LODIEC_2_PL1X2 | PLANT_TROUBLE | 2475.5347
2023 | summer | LOTUS_6_LSFSR1 | PLANT_TROUBLE | 360
2023 | summer | LOWGAP_1_SUPHR | PLANT_TROUBLE | 524.7
2023 | summer | LOWGAP_7_QFUNTS | TRANSMISSION_INDUCED | 1032.75
2023 | summer | LTBEAR_1_LB3SR3 | PLANT_MAINTENANCE | 0
2023 | summer | LTBEAR_1_LB3SR3 | PLANT_TROUBLE | 0
2023 | summer | LTBEAR_1_LB3SR3 | TRANSMISSION_INDUCED | 2.84
2023 | summer | LTBEAR_1_LB4SR4 | METERING_TELEMETRY | 235
2023 | summer | LTBEAR_1_LB4SR4 | PLANT_MAINTENANCE | 20
2023 | summer | LTBEAR_1_LB4SR4 | TRANSMISSION_INDUCED | 7.12
2023 | summer | LTBEAR_1_LB4SR5 | PLANT_MAINTENANCE | 20.8333
2023 | summer | LTBEAR_1_LB4SR5 | PLANT_TROUBLE | 0
2023 | summer | LTBEAR_1_LB4SR5 | TRANSMISSION_INDUCED | 7.12
2023 | summer | LTBERA_1_LB1SR1 | PLANT_MAINTENANCE | 0
2023 | summer | LTBERA_1_LB1SR1 | TRANSMISSION_INDUCED | 5.68
2023 | summer | MAGNLA_6_ANAHEIM | AMBIENT_DUE_TO_TEMP | 15
2023 | summer | MAGNLA_6_ANAHEIM | PLANT_MAINTENANCE | 2834
2023 | summer | MAGNLA_6_ANAHEIM | UNIT_TESTING | 72
2023 | summer | MAGNLA_6_CERRITOS | PLANT_MAINTENANCE | 286
2023 | summer | MAGNLA_6_CERRITOS | TRANSMISSION_INDUCED | 610
2023 | summer | MAGNLA_6_COLTON | PLANT_MAINTENANCE | 260
2023 | summer | MAGNLA_6_COLTON | TRANSMISSION_INDUCED | 1530
2023 | summer | MAGNLA_6_PASADENA | PLANT_MAINTENANCE | 234
2023 | summer | MAGUND_1_BKSSR2 | PLANT_TROUBLE | 1025
2023 | summer | MALAGA_1_PL1X2 | AMBIENT_DUE_TO_TEMP | 17.5908
2023 | summer | MALAGA_1_PL1X2 | METERING_TELEMETRY | 0
2023 | summer | MALAGA_1_PL1X2 | PLANT_MAINTENANCE | 241.525
2023 | summer | MALCHQ_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 1424.3
2023 | summer | MALCHQ_7_UNIT 1 | METERING_TELEMETRY | 16.25
2023 | summer | MANTEC_1_ML1SR1 | PLANT_TROUBLE | 765
2023 | summer | MANZNA_2_WIND | AMBIENT_DUE_TO_TEMP | 70
2023 | summer | MANZNA_2_WIND | PLANT_MAINTENANCE | 364.5
2023 | summer | MANZNA_2_WIND | PLANT_TROUBLE | 255
2023 | summer | MCARTH_6_FRIVRB | PLANT_TROUBLE | 0
2023 | summer | MCARTH_6_FRIVRB | TRANSMISSION_INDUCED | 0.75
2023 | summer | MCSWAN_6_UNITS | PLANT_TROUBLE | 0
2023 | summer | MDFKRL_2_PROJCT | PLANT_MAINTENANCE | 630
2023 | summer | MDFKRL_2_PROJCT | RTU_RIG | 135
2023 | summer | MENBIO_6_RENEW1 | METERING_TELEMETRY | 257.5
2023 | summer | MENBIO_6_RENEW1 | TRANSMISSION_INDUCED | 25.72
2023 | summer | MERCED_1_SOLAR1 | PLANT_MAINTENANCE | 0
2023 | summer | MERCED_1_SOLAR2 | PLANT_MAINTENANCE | 0
2023 | summer | METEC_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 10874.3553
2023 | summer | METEC_2_PL1X3 | PLANT_MAINTENANCE | 5970.5
2023 | summer | METEC_2_PL1X3 | PLANT_TROUBLE | 69397.149
2023 | summer | METEC_2_PL1X3 | TRANSITIONAL_LIMITATION | 192.7808
2023 | summer | METEC_2_PL1X3 | UNIT_TESTING | 1929
2023 | summer | MIDWD_2_WIND2 | PLANT_MAINTENANCE | 21.75
2023 | summer | MIDWD_7_CORAMB | ENVIRONMENTAL_RESTRICTIONS | 112.5
2023 | summer | MIDWD_7_CORAMB | METERING_TELEMETRY | 11.25
2023 | summer | MIDWD_7_CORAMB | TRANSMISSION_INDUCED | 71.25
2023 | summer | MIDWY3_2_MDSSR1 | PLANT_MAINTENANCE | 14.5
2023 | summer | MIDWY3_2_MDSSR1 | PLANT_TROUBLE | 884.9
2023 | summer | MIRLOM_2_CORONA | PLANT_TROUBLE | 82.365
2023 | summer | MIRLOM_2_MLBBTA | PLANT_TROUBLE | 25.1667
2023 | summer | MIRLOM_2_MLBBTA | RTU_RIG | 24.1667
2023 | summer | MIRLOM_2_MLBBTA | TRANSMISSION_INDUCED | 1066
2023 | summer | MIRLOM_2_MLBBTA | UNIT_TESTING | 0
2023 | summer | MIRLOM_2_MLBBTB | PLANT_MAINTENANCE | 0
2023 | summer | MIRLOM_2_MLBBTB | RTU_RIG | 424.1667
2023 | summer | MIRLOM_2_MLBBTB | TRANSMISSION_INDUCED | 0
2023 | summer | MIRLOM_2_MLBBTB | UNIT_TESTING | 0
2023 | summer | MIRLOM_2_ONTARO | METERING_TELEMETRY | 137.5
2023 | summer | MIRLOM_2_ONTARO | PLANT_TROUBLE | 2722.5
2023 | summer | MIRLOM_2_RTS032 | PLANT_TROUBLE | 795
2023 | summer | MIRLOM_2_RTS033 | PLANT_TROUBLE | 520
2023 | summer | MIRLOM_2_TEMESC | PLANT_TROUBLE | 53.865
2023 | summer | MIRLOM_6_PEAKER | AMBIENT_DUE_TO_TEMP | 2337.9
2023 | summer | MIRLOM_6_PEAKER | PLANT_TROUBLE | 222.585
2023 | summer | MIRLOM_7_MWDLKM | PLANT_TROUBLE | 1167.0833
2023 | summer | MKTRCK_1_UNIT 1 | AMBIENT_DUE_TO_TEMP | 3294.3
2023 | summer | MKTRCK_1_UNIT 1 | PLANT_TROUBLE | 4140.6
2023 | summer | MNDALY_6_MCGRTH | AMBIENT_DUE_TO_TEMP | 4810.92
2023 | summer | MNDALY_6_MCGRTH | AMBIENT_NOT_DUE_TO_TEMP | 169.828
2023 | summer | MNDALY_6_MCGRTH | METERING_TELEMETRY | 0
2023 | summer | MNDALY_6_MCGRTH | PLANT_MAINTENANCE | 211.42
2023 | summer | MNDALY_6_MCGRTH | PLANT_TROUBLE | 37.72
2023 | summer | MNDALY_6_MCGRTH | TRANSMISSION_INDUCED | 0
2023 | summer | MNDOTA_1_SOLAR1 | METERING_TELEMETRY | 59
2023 | summer | MNDOTA_1_SOLAR1 | PLANT_TROUBLE | 0
2023 | summer | MNDOTA_1_SOLAR1 | TRANSMISSION_INDUCED | 8.52
2023 | summer | MNDOTA_1_SOLAR2 | PLANT_TROUBLE | 100.5
2023 | summer | MOJAVE_1_SIPHON | PLANT_MAINTENANCE | 143.6
2023 | summer | MOJAVE_1_SIPHON | PLANT_TROUBLE | 2376.1207
2023 | summer | MOJAVE_1_SIPHON | TRANSMISSION_INDUCED | 8.3767
2023 | summer | MOJAVW_2_SOLAR | PLANT_TROUBLE | 95.0833
2023 | summer | MONTPH_7_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 1051
2023 | summer | MONTPH_7_UNITS | PLANT_TROUBLE | 0
2023 | summer | MOORPK_2_ACOBT1 | METERING_TELEMETRY | 0
2023 | summer | MOORPK_2_ACOBT1 | PLANT_MAINTENANCE | 58.5
2023 | summer | MOORPK_2_ACOBT1 | PLANT_TROUBLE | 7.3017
2023 | summer | MOORPK_2_ACOBT1 | RTU_RIG | 9.75
2023 | summer | MOORPK_2_CALABS | AMBIENT_DUE_TO_TEMP | 4.7233
2023 | summer | MOORPK_2_CALABS | PLANT_MAINTENANCE | 115.368
2023 | summer | MOORPK_2_CALABS | PLANT_TROUBLE | 916.5787
2023 | summer | MORWD_6_QF | PLANT_TROUBLE | 54.5
2023 | summer | MORWD_6_QF | TRANSMISSION_INDUCED | 0
2023 | summer | MOSSLD_2_PSP1 | AMBIENT_DUE_TO_TEMP | 2524.9667
2023 | summer | MOSSLD_2_PSP1 | PLANT_MAINTENANCE | 1300
2023 | summer | MOSSLD_2_PSP1 | PLANT_TROUBLE | 4604.8833
2023 | summer | MOSSLD_2_PSP1 | UNIT_TESTING | 0
2023 | summer | MOSSLD_2_PSP2 | AMBIENT_DUE_TO_TEMP | 1018.8833
2023 | summer | MOSSLD_2_PSP2 | PLANT_TROUBLE | 2525
2023 | summer | MRCHNT_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 47602.6333
2023 | summer | MRCHNT_2_PL1X3 | PLANT_TROUBLE | 18973
2023 | summer | MRGT_6_MEF2 | PLANT_TROUBLE | 779.5333
2023 | summer | MRGT_6_MMAREF | PLANT_TROUBLE | 0
2023 | summer | MRGT_6_TGEBT1 | PLANT_MAINTENANCE | 144
2023 | summer | MRGT_6_TGEBT1 | PLANT_TROUBLE | 3649.5567
2023 | summer | MRGT_6_TGEBT1 | TRANSMISSION_INDUCED | 0
2023 | summer | MRLSDS_6_SOLAR1 | METERING_TELEMETRY | 201.25
2023 | summer | MRLSDS_6_SOLAR1 | PLANT_MAINTENANCE | 1
2023 | summer | MRLSDS_6_SOLAR1 | PLANT_TROUBLE | 345.8
2023 | summer | MSOLAR_2_SOLAR2 | PLANT_MAINTENANCE | 151.215
2023 | summer | MSOLAR_2_SOLAR2 | PLANT_TROUBLE | 27.45
2023 | summer | MSOLAR_2_SOLAR3 | PLANT_MAINTENANCE | 304
2023 | summer | MSOLAR_2_SOLAR3 | PLANT_TROUBLE | 18
2023 | summer | MSTANG_2_MTGBT1 | PLANT_MAINTENANCE | 674.1667
2023 | summer | MSTANG_2_MTGBT1 | PLANT_TROUBLE | 3675.74
2023 | summer | MSTANG_2_SOLAR | PLANT_MAINTENANCE | 300
2023 | summer | MSTANG_2_SOLAR | PLANT_TROUBLE | 16860
2023 | summer | MSTANG_2_SOLAR3 | PLANT_MAINTENANCE | 0
2023 | summer | MSTANG_2_SOLAR3 | PLANT_TROUBLE | 2021.5033
2023 | summer | MSTANG_2_SOLAR4 | PLANT_MAINTENANCE | 70.671
2023 | summer | MSTANG_2_SOLAR4 | PLANT_TROUBLE | 5958.8707
2023 | summer | MTNPOS_1_UNIT | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 43.2
2023 | summer | MTNPOS_1_UNIT | AMBIENT_DUE_TO_TEMP | 61.6887
2023 | summer | MTNPOS_1_UNIT | PLANT_MAINTENANCE | 1421.76
2023 | summer | MTNPOS_1_UNIT | PLANT_TROUBLE | 6884.6507
2023 | summer | MTWIND_1_MVPWD1 | TRANSMISSION_INDUCED | 329.88
2023 | summer | MTWIND_1_UNIT 3 | AMBIENT_DUE_TO_TEMP | 708.1053
2023 | summer | MTWIND_1_UNIT 3 | PLANT_MAINTENANCE | 17.08
2023 | summer | MTWIND_1_UNIT 3 | PLANT_TROUBLE | 443.612
2023 | summer | MTWIND_1_UNIT 3 | RTU_RIG | 94.6
2023 | summer | MTWIND_1_UNIT 3 | TRANSMISSION_INDUCED | 77.28
2023 | summer | MURRAY_6_UNIT | PLANT_MAINTENANCE | 94.76
2023 | summer | MURRAY_6_UNIT | PLANT_TROUBLE | 0
2023 | summer | NAROW1_2_UNIT | ENVIRONMENTAL_RESTRICTIONS | 1383.33
2023 | summer | NAROW1_2_UNIT | PLANT_TROUBLE | 0
2023 | summer | NAROW1_2_UNIT | TRANSMISSION_INDUCED | 20.8
2023 | summer | NAROW2_2_UNIT | ENVIRONMENTAL_RESTRICTIONS | 17913.66
2023 | summer | NAVYII_2_UNITS | PLANT_TROUBLE | 5545
2023 | summer | NCPA_7_GP1UN1 | PLANT_MAINTENANCE | 29720.25
2023 | summer | NCPA_7_GP1UN2 | PLANT_TROUBLE | 3235.14
2023 | summer | NCPA_7_GP2UN3 | AMBIENT_NOT_DUE_TO_TEMP | 32451.3
2023 | summer | NCPA_7_GP2UN4 | PLANT_MAINTENANCE | 13182.5
2023 | summer | NCPA_7_GP2UN4 | PLANT_TROUBLE | 5105.1428
2023 | summer | NEENCH_6_SOLAR | PLANT_MAINTENANCE | 132
2023 | summer | NEENCH_6_SOLAR | PLANT_TROUBLE | 97.15
2023 | summer | NGILAA_5_SDGDYN | AMBIENT_DUE_TO_TEMP | 2020
2023 | summer | NGILAA_5_SDGDYN | ENVIRONMENTAL_RESTRICTIONS | 153
2023 | summer | NHOGAN_6_UNITS | TRANSMISSION_INDUCED | 13.6
2023 | summer | NORCNV_1_NCVBT1 | METERING_TELEMETRY | 166.4
2023 | summer | NORCNV_1_NCVBT1 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | summer | NORCNV_1_NCVBT1 | PLANT_TROUBLE | 2216.2
2023 | summer | NORCNV_1_NCVBT1 | TRANSMISSION_INDUCED | 0
2023 | summer | NWCSTL_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 6295.4533
2023 | summer | NWCSTL_7_UNIT 1 | ENVIRONMENTAL_RESTRICTIONS | 59
2023 | summer | NWCSTL_7_UNIT 1 | PLANT_TROUBLE | 288
2023 | summer | NWCSTL_7_UNIT 1 | TRANSMISSION_INDUCED | 72
2023 | summer | NZWIND_2_WDSTR5 | PLANT_MAINTENANCE | 0
2023 | summer | NZWIND_2_WDSTR5 | TRANSMISSION_INDUCED | 0
2023 | summer | NZWIND_6_CALWND | PLANT_MAINTENANCE | 0
2023 | summer | OAK C_7_UNIT 1 | PLANT_MAINTENANCE | 200
2023 | summer | OAK C_7_UNIT 1 | PLANT_TROUBLE | 22759.0667
2023 | summer | OAK C_7_UNIT 3 | ENVIRONMENTAL_RESTRICTIONS | 30
2023 | summer | OAK C_7_UNIT 3 | PLANT_MAINTENANCE | 540
2023 | summer | OAK C_7_UNIT 3 | PLANT_TROUBLE | 1305
2023 | summer | OAK L_1_GTG1 | TRANSMISSION_INDUCED | 0
2023 | summer | OAKWD_6_QF | METERING_TELEMETRY | 0
2023 | summer | OAKWD_6_QF | PLANT_TROUBLE | 0
2023 | summer | OAKWD_6_QF | TRANSMISSION_INDUCED | 179.1
2023 | summer | OAKWD_6_ZEPHWD | TRANSMISSION_INDUCED | 26.1917
2023 | summer | OASIS_6_CREST | PLANT_TROUBLE | 75
2023 | summer | OASIS_6_GBDSR4 | PLANT_TROUBLE | 0
2023 | summer | OASIS_6_LPPSR1 | PLANT_MAINTENANCE | 157.8167
2023 | summer | OASIS_6_SOLAR1 | PLANT_MAINTENANCE | 165
2023 | summer | OASIS_6_SOLAR1 | PLANT_TROUBLE | 112.5
2023 | summer | OASIS_6_SOLAR2 | METERING_TELEMETRY | 80.3833
2023 | summer | OASIS_6_SOLAR2 | PLANT_TROUBLE | 467.5917
2023 | summer | OASIS_6_VINSR1 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2023 | summer | OCOTLO_6_OCWSB1 | METERING_TELEMETRY | 2125
2023 | summer | OCOTLO_6_OCWSB1 | PLANT_MAINTENANCE | 1589.6667
2023 | summer | OCOTLO_6_OCWSB1 | PLANT_TROUBLE | 1035.8333
2023 | summer | OCOTLO_6_OCWSB1 | UNIT_TESTING | 600
2023 | summer | OCTILO_5_WIND | AMBIENT_DUE_TO_TEMP | 208.6667
2023 | summer | OCTILO_5_WIND | PLANT_MAINTENANCE | 0
2023 | summer | OCTILO_5_WIND | PLANT_TROUBLE | 25488.4
2023 | summer | OGROVE_6_PL1X2 | PLANT_TROUBLE | 572.4833
2023 | summer | OGROVE_6_PL1X2 | TRANSMISSION_INDUCED | 0
2023 | summer | OILFLD_7_QFUNTS | AMBIENT_NOT_DUE_TO_TEMP | 600.95
2023 | summer | OILFLD_7_QFUNTS | PLANT_MAINTENANCE | 0
2023 | summer | OILFLD_7_QFUNTS | PLANT_TROUBLE | 10.912
2023 | summer | OILFLD_7_QFUNTS | TRANSMISSION_INDUCED | 37.7183
2023 | summer | OLDRIV_6_CESDBM | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 2.75
2023 | summer | OLDRIV_6_CESDBM | AMBIENT_NOT_DUE_TO_TEMP | 4.0833
2023 | summer | OLDRIV_6_CESDBM | PLANT_MAINTENANCE | 0
2023 | summer | OLDRIV_6_CESDBM | PLANT_TROUBLE | 0
2023 | summer | OLDRIV_6_LKVBM1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0.75
2023 | summer | OLDRIV_6_LKVBM1 | PLANT_MAINTENANCE | 7.55
2023 | summer | OLDRIV_6_LKVBM1 | PLANT_TROUBLE | 1
2023 | summer | OLINDA_2_COYCRK | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 2394.45
2023 | summer | OLINDA_2_LNDFL2 | PLANT_MAINTENANCE | 252.0583
2023 | summer | OLINDA_2_LNDFL2 | PLANT_TROUBLE | 140.5
2023 | summer | OLIVEP_1_SOLAR | PLANT_MAINTENANCE | 20
2023 | summer | OLIVEP_1_SOLAR | PLANT_TROUBLE | 28.3333
2023 | summer | OLIVEP_1_SOLAR | TRANSMISSION_INDUCED | 16
2023 | summer | OLIVEP_1_SOLAR2 | PLANT_TROUBLE | 111.9167
2023 | summer | OLIVEP_1_SOLAR2 | TRANSMISSION_INDUCED | 15.4708
2023 | summer | OLSEN_2_UNIT | TRANSMISSION_INDUCED | 17.875
2023 | summer | OMAR_2_UNIT 1 | PLANT_TROUBLE | 628.75
2023 | summer | OMAR_2_UNIT 2 | PLANT_MAINTENANCE | 7500
2023 | summer | OMAR_2_UNIT 2 | PLANT_TROUBLE | 3037.5
2023 | summer | OMAR_2_UNIT 3 | PLANT_MAINTENANCE | 0
2023 | summer | OMAR_2_UNIT 3 | PLANT_TROUBLE | 147.5
2023 | summer | OMAR_2_UNIT 4 | PLANT_MAINTENANCE | 0
2023 | summer | OMAR_2_UNIT 4 | PLANT_TROUBLE | 2625
2023 | summer | ONLLPP_6_UNITS | TRANSMISSION_INDUCED | 126
2023 | summer | ORLND_6_HIGHLI | PLANT_TROUBLE | 382.5
2023 | summer | ORMOND_7_UNIT 1 | PLANT_TROUBLE | 115151.0893
2023 | summer | ORMOND_7_UNIT 1 | UNIT_TESTING | 0
2023 | summer | ORMOND_7_UNIT 2 | PLANT_MAINTENANCE | 1129.1712
2023 | summer | ORMOND_7_UNIT 2 | PLANT_TROUBLE | 42491.89
2023 | summer | ORMOND_7_UNIT 2 | TRANSMISSION_INDUCED | 0
2023 | summer | OROLOM_1_SOLAR1 | PLANT_TROUBLE | 0
2023 | summer | OROLOM_1_SOLAR1 | TRANSMISSION_INDUCED | 50
2023 | summer | OROLOM_1_SOLAR2 | PLANT_TROUBLE | 0
2023 | summer | OROLOM_1_SOLAR2 | TRANSMISSION_INDUCED | 50
2023 | summer | OROVIL_6_UNIT | PLANT_TROUBLE | 814.12
2023 | summer | OROVIL_6_UNIT | TRANSMISSION_INDUCED | 52
2023 | summer | OTAY_6_ECVBT1 | TRANSMISSION_INDUCED | 2295
2023 | summer | OTAY_6_PL1X2 | AMBIENT_DUE_TO_TEMP | 53.55
2023 | summer | OTAY_6_PL1X2 | PLANT_MAINTENANCE | 79.14
2023 | summer | OTAY_6_PL1X2 | PLANT_TROUBLE | 666.7545
2023 | summer | OTMESA_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 20972.6947
2023 | summer | OTMESA_2_PL1X3 | PLANT_MAINTENANCE | 14115.6
2023 | summer | OTMESA_2_PL1X3 | PLANT_TROUBLE | 25255.2333
2023 | summer | OTMESA_2_PL1X3 | TRANSITIONAL_LIMITATION | 0
2023 | summer | OTMESA_2_PL1X3 | TRANSMISSION_INDUCED | 261.4
2023 | summer | OXBOW_6_DRUM | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 23.1033
2023 | summer | OXBOW_6_DRUM | TRANSMISSION_INDUCED | 1050.8633
2023 | summer | OXMTN_6_LNDFIL | PLANT_MAINTENANCE | 68.185
2023 | summer | OXMTN_6_LNDFIL | PLANT_TROUBLE | 304.9797
2023 | summer | OXMTN_6_LNDFIL | TRANSMISSION_INDUCED | 53.1
2023 | summer | PACLUM_6_UNIT | PLANT_MAINTENANCE | 240
2023 | summer | PACLUM_6_UNIT | PLANT_TROUBLE | 7891.1333
2023 | summer | PACLUM_6_UNIT | TRANSMISSION_INDUCED | 0.3495
2023 | summer | PADUA_2_ONTARO | AMBIENT_NOT_DUE_TO_TEMP | 192.785
2023 | summer | PADUA_2_ONTARO | PLANT_MAINTENANCE | 40.5
2023 | summer | PADUA_2_ONTARO | PLANT_TROUBLE | 446.1
2023 | summer | PADUA_6_MWDSDM | PLANT_MAINTENANCE | 24.5
2023 | summer | PADUA_6_MWDSDM | PLANT_TROUBLE | 49.5
2023 | summer | PADUA_7_SDIMAS | ENVIRONMENTAL_RESTRICTIONS | 36.75
2023 | summer | PADUA_7_SDIMAS | PLANT_MAINTENANCE | 113.4
2023 | summer | PADUA_7_SDIMAS | PLANT_TROUBLE | 94.675
2023 | summer | PADUA_7_SDIMAS | TRANSMISSION_INDUCED | 0
2023 | summer | PAIGES_6_SOLAR | PLANT_MAINTENANCE | 100
2023 | summer | PAIGES_6_SOLAR | TRANSMISSION_INDUCED | 7.6667
2023 | summer | PALALT_7_COBUG | PLANT_TROUBLE | 2880
2023 | summer | PALOMR_2_PL1X3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 114.8202
2023 | summer | PALOMR_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 259.5362
2023 | summer | PALOMR_2_PL1X3 | AMBIENT_NOT_DUE_TO_TEMP | 239.3
2023 | summer | PALOMR_2_PL1X3 | PLANT_MAINTENANCE | 98819.28
2023 | summer | PALOMR_2_PL1X3 | PLANT_TROUBLE | 9891.3967
2023 | summer | PALOMR_2_PL1X3 | TRANSMISSION_INDUCED | 48233.22
2023 | summer | PALOMR_2_PL1X3 | UNIT_TESTING | 0
2023 | summer | PARDEB_6_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 397.85
2023 | summer | PARDEB_6_UNITS | PLANT_MAINTENANCE | 50
2023 | summer | PARDEB_6_UNITS | PLANT_TROUBLE | 304.175
2023 | summer | PARDEB_6_UNITS | TRANSMISSION_INDUCED | 5.2
2023 | summer | PBLOSM_2_SOLAR | PLANT_TROUBLE | 0
2023 | summer | PEABDY_2_LNDFIL | PLANT_MAINTENANCE | 256
2023 | summer | PEABDY_2_LNDFL1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2023 | summer | PEABDY_2_LNDFL1 | AMBIENT_DUE_TO_TEMP | 196.87
2023 | summer | PEABDY_2_LNDFL1 | AMBIENT_NOT_DUE_TO_TEMP | 8.1817
2023 | summer | PEABDY_2_LNDFL1 | PLANT_MAINTENANCE | 46
2023 | summer | PEABDY_2_LNDFL1 | PLANT_TROUBLE | 144.1817
2023 | summer | PEABDY_2_LNDFL1 | TRANSMISSION_INDUCED | 47.8
2023 | summer | PEASE_1_TBEBT1 | PLANT_MAINTENANCE | 304
2023 | summer | PEASE_1_TBEBT1 | PLANT_TROUBLE | 645.5
2023 | summer | PEASE_1_TBEBT1 | RTU_RIG | 0
2023 | summer | PEASE_1_TBEBT1 | UNIT_TESTING | 30
2023 | summer | PEORIA_1_SOLAR | PLANT_TROUBLE | 360.2917
2023 | summer | PGCC_1_PDRP06 | SHORT_TERM_USE_LIMIT_REACHED | 6.9
2023 | summer | PGCC_1_PDRP07 | SHORT_TERM_USE_LIMIT_REACHED | 18.2
2023 | summer | PGCC_1_PDRP09 | SHORT_TERM_USE_LIMIT_REACHED | 3.75
2023 | summer | PGEB_2_PDRP12 | SHORT_TERM_USE_LIMIT_REACHED | 1.65
2023 | summer | PGEB_2_PDRP13 | SHORT_TERM_USE_LIMIT_REACHED | 4.05
2023 | summer | PGEB_2_PDRP14 | SHORT_TERM_USE_LIMIT_REACHED | 4.7
2023 | summer | PGEB_2_PDRP16 | SHORT_TERM_USE_LIMIT_REACHED | 0.55
2023 | summer | PGEB_2_RDRR01 | SHORT_TERM_USE_LIMIT_REACHED | 302.3
2023 | summer | PGF1_2_PDRP05 | SHORT_TERM_USE_LIMIT_REACHED | 0.9
2023 | summer | PGF1_2_PDRP06 | SHORT_TERM_USE_LIMIT_REACHED | 26.9
2023 | summer | PGF1_2_PDRP12 | SHORT_TERM_USE_LIMIT_REACHED | 8.65
2023 | summer | PGF1_2_PDRP14 | SHORT_TERM_USE_LIMIT_REACHED | 1.05
2023 | summer | PGF1_2_PDRP15 | SHORT_TERM_USE_LIMIT_REACHED | 2.75
2023 | summer | PGF1_2_PDRP22 | SHORT_TERM_USE_LIMIT_REACHED | 0.55
2023 | summer | PGF1_2_PDRP23 | SHORT_TERM_USE_LIMIT_REACHED | 2.95
2023 | summer | PGF1_2_PDRP33 | SHORT_TERM_USE_LIMIT_REACHED | 22.4
2023 | summer | PGFG_1_PDRP07 | SHORT_TERM_USE_LIMIT_REACHED | 0.6
2023 | summer | PGFG_1_PDRP08 | SHORT_TERM_USE_LIMIT_REACHED | 0.55
2023 | summer | PGHB_6_PDRP03 | SHORT_TERM_USE_LIMIT_REACHED | 4.45
2023 | summer | PGKN_2_PDRP01 | SHORT_TERM_USE_LIMIT_REACHED | 0.65
2023 | summer | PGKN_2_PDRP03 | SHORT_TERM_USE_LIMIT_REACHED | 7.2
2023 | summer | PGKN_2_PDRP04 | SHORT_TERM_USE_LIMIT_REACHED | 3.8
2023 | summer | PGNB_2_PDRP06 | SHORT_TERM_USE_LIMIT_REACHED | 0.55
2023 | summer | PGNB_2_PDRP07 | SHORT_TERM_USE_LIMIT_REACHED | 1.3
2023 | summer | PGNB_2_PDRP08 | SHORT_TERM_USE_LIMIT_REACHED | 6.55
2023 | summer | PGNB_2_PDRP44 | SHORT_TERM_USE_LIMIT_REACHED | 1.3
2023 | summer | PGNC_1_PDRP02 | SHORT_TERM_USE_LIMIT_REACHED | 1
2023 | summer | PGNP_2_PDRP03 | SHORT_TERM_USE_LIMIT_REACHED | 1.7
2023 | summer | PGNP_2_PDRP04 | SHORT_TERM_USE_LIMIT_REACHED | 27.5
2023 | summer | PGNP_2_PDRP05 | SHORT_TERM_USE_LIMIT_REACHED | 0.7
2023 | summer | PGNP_2_PDRP06 | SHORT_TERM_USE_LIMIT_REACHED | 2.65
2023 | summer | PGNP_2_PDRP12 | SHORT_TERM_USE_LIMIT_REACHED | 0.55
2023 | summer | PGNP_2_PDRP13 | SHORT_TERM_USE_LIMIT_REACHED | 1.05
2023 | summer | PGNP_2_PDRP58 | SHORT_TERM_USE_LIMIT_REACHED | 14.85
2023 | summer | PGP2_2_PDRP09 | SHORT_TERM_USE_LIMIT_REACHED | 2.1
2023 | summer | PGP2_2_PDRP31 | SHORT_TERM_USE_LIMIT_REACHED | 5.7
2023 | summer | PGSB_1_PDRP106 | SHORT_TERM_USE_LIMIT_REACHED | 14.95
2023 | summer | PGSB_1_PDRP15 | SHORT_TERM_USE_LIMIT_REACHED | 0.55
2023 | summer | PGSB_1_PDRP18 | SHORT_TERM_USE_LIMIT_REACHED | 22.7
2023 | summer | PGSB_1_PDRP19 | SHORT_TERM_USE_LIMIT_REACHED | 3.3
2023 | summer | PGSB_1_PDRP20 | SHORT_TERM_USE_LIMIT_REACHED | 1.1
2023 | summer | PGSF_2_PDRP13 | SHORT_TERM_USE_LIMIT_REACHED | 1.2
2023 | summer | PGSF_2_PDRP14 | SHORT_TERM_USE_LIMIT_REACHED | 0.55
2023 | summer | PGSF_2_PDRP15 | SHORT_TERM_USE_LIMIT_REACHED | 0.9
2023 | summer | PGSI_1_PDRP04 | SHORT_TERM_USE_LIMIT_REACHED | 3.55
2023 | summer | PGSI_1_PDRP05 | SHORT_TERM_USE_LIMIT_REACHED | 0.55
2023 | summer | PGSI_1_PDRP08 | SHORT_TERM_USE_LIMIT_REACHED | 0.55
2023 | summer | PGSI_1_PDRP13 | SHORT_TERM_USE_LIMIT_REACHED | 31.25
2023 | summer | PGSI_1_PDRP18 | SHORT_TERM_USE_LIMIT_REACHED | 7.6
2023 | summer | PGSI_1_PDRP53 | SHORT_TERM_USE_LIMIT_REACHED | 13.55
2023 | summer | PGST_2_PDRP02 | SHORT_TERM_USE_LIMIT_REACHED | 1.95
2023 | summer | PGST_2_PDRP04 | SHORT_TERM_USE_LIMIT_REACHED | 4.5
2023 | summer | PGST_2_PDRP05 | SHORT_TERM_USE_LIMIT_REACHED | 14.7
2023 | summer | PGST_2_PDRP06 | SHORT_TERM_USE_LIMIT_REACHED | 0.55
2023 | summer | PGST_2_PDRP12 | SHORT_TERM_USE_LIMIT_REACHED | 5.55
2023 | summer | PGST_2_PDRP42 | SHORT_TERM_USE_LIMIT_REACHED | 13.5
2023 | summer | PGZP_2_PDRP01 | SHORT_TERM_USE_LIMIT_REACHED | 1.2
2023 | summer | PGZP_2_PDRP03 | SHORT_TERM_USE_LIMIT_REACHED | 38.3
2023 | summer | PGZP_2_PDRP04 | SHORT_TERM_USE_LIMIT_REACHED | 11.85
2023 | summer | PGZP_2_PDRP05 | SHORT_TERM_USE_LIMIT_REACHED | 4
2023 | summer | PHOENX_1_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 14.2667
2023 | summer | PHOENX_1_UNIT | ENVIRONMENTAL_RESTRICTIONS | 8.5
2023 | summer | PHOENX_1_UNIT | PLANT_MAINTENANCE | 280
2023 | summer | PHOENX_1_UNIT | PLANT_TROUBLE | 83
2023 | summer | PHOENX_1_UNIT | TRANSMISSION_INDUCED | 68.7667
2023 | summer | PINFLT_7_UNITS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 5713.15
2023 | summer | PINFLT_7_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 20194.1
2023 | summer | PINFLT_7_UNITS | TRANSMISSION_INDUCED | 6.5
2023 | summer | PIOPIC_2_CTG1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 108.6633
2023 | summer | PIOPIC_2_CTG1 | AMBIENT_DUE_TO_TEMP | 5017.89
2023 | summer | PIOPIC_2_CTG2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 84.0308
2023 | summer | PIOPIC_2_CTG2 | AMBIENT_DUE_TO_TEMP | 4058.08
2023 | summer | PIOPIC_2_CTG2 | PLANT_TROUBLE | 0
2023 | summer | PIOPIC_2_CTG3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 96.4008
2023 | summer | PIOPIC_2_CTG3 | AMBIENT_DUE_TO_TEMP | 4514.06
2023 | summer | PIOPIC_2_CTG3 | PLANT_TROUBLE | 410.045
2023 | summer | PIT1_6_FRIVRA | PLANT_TROUBLE | 30
2023 | summer | PIT1_7_UNIT 1 | AMBIENT_DUE_TO_TEMP | 0
2023 | summer | PIT1_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 13.6
2023 | summer | PIT1_7_UNIT 1 | PLANT_TROUBLE | 1029.8667
2023 | summer | PIT1_7_UNIT 1 | TRANSMISSION_INDUCED | 0
2023 | summer | PIT1_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 249.55
2023 | summer | PIT1_7_UNIT 2 | PLANT_TROUBLE | 0
2023 | summer | PIT1_7_UNIT 2 | TRANSMISSION_INDUCED | 160
2023 | summer | PIT3_7_PL1X3 | AMBIENT_NOT_DUE_TO_TEMP | 332
2023 | summer | PIT3_7_PL1X3 | PLANT_TROUBLE | 452.71
2023 | summer | PIT4_7_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 908.0333
2023 | summer | PIT4_7_PL1X2 | PLANT_TROUBLE | 0.7
2023 | summer | PIT5_7_PL1X2 | AMBIENT_DUE_TO_TEMP | 1.3333
2023 | summer | PIT5_7_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 1489.85
2023 | summer | PIT5_7_PL1X2 | PLANT_TROUBLE | 0.66667
2023 | summer | PIT5_7_PL3X4 | AMBIENT_NOT_DUE_TO_TEMP | 1858.2833
2023 | summer | PIT5_7_PL3X4 | PLANT_TROUBLE | 0.7
2023 | summer | PIT6_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 899.1998
2023 | summer | PIT6_7_UNIT 1 | METERING_TELEMETRY | 0
2023 | summer | PIT6_7_UNIT 1 | PLANT_TROUBLE | 51.0433
2023 | summer | PIT6_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 1363.5058
2023 | summer | PIT6_7_UNIT 2 | METERING_TELEMETRY | 0
2023 | summer | PIT7_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 1337.2282
2023 | summer | PIT7_7_UNIT 1 | METERING_TELEMETRY | 16.48
2023 | summer | PIT7_7_UNIT 1 | PLANT_TROUBLE | 0
2023 | summer | PIT7_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 755.6012
2023 | summer | PIT7_7_UNIT 2 | METERING_TELEMETRY | 15.6
2023 | summer | PIUTE_6_GNBSR1 | PLANT_TROUBLE | 315.375
2023 | summer | PLACVL_1_CHILIB | PLANT_MAINTENANCE | 0
2023 | summer | PLACVL_1_CHILIB | TRANSMISSION_INDUCED | 29.19
2023 | summer | PLAINV_6_BSOLAR | PLANT_TROUBLE | 499.2167
2023 | summer | PLAINV_6_DSOLAR | PLANT_TROUBLE | 7.5
2023 | summer | PLAINV_6_SOLAR3 | PLANT_TROUBLE | 1367.8833
2023 | summer | PLAINV_6_SOLARC | PLANT_MAINTENANCE | 9.8333
2023 | summer | PLAINV_6_SOLARC | PLANT_TROUBLE | 47.1667
2023 | summer | PLMSSR_6_HISIER | PLANT_MAINTENANCE | 3.4883
2023 | summer | PLMSSR_6_HISIER | PLANT_TROUBLE | 102.5303
2023 | summer | PLMSSR_6_HISIER | TRANSMISSION_INDUCED | 0
2023 | summer | PLSNTG_7_LNCLND | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 21.052
2023 | summer | PLSNTG_7_LNCLND | PLANT_TROUBLE | 46.48
2023 | summer | PMDLET_6_SOLAR1 | PLANT_TROUBLE | 74.9333
2023 | summer | PNCHEG_2_PL1X4 | AMBIENT_DUE_TO_TEMP | 12770.07
2023 | summer | PNCHEG_2_PL1X4 | AMBIENT_NOT_DUE_TO_TEMP | 172.0167
2023 | summer | PNCHEG_2_PL1X4 | METERING_TELEMETRY | 152.2
2023 | summer | PNCHEG_2_PL1X4 | PLANT_MAINTENANCE | 90.9
2023 | summer | PNCHEG_2_PL1X4 | PLANT_TROUBLE | 53563.55
2023 | summer | PNCHEG_2_PL1X4 | TRANSMISSION_INDUCED | 46.5267
2023 | summer | PNCHEG_2_PL1X4 | UNIT_TESTING | 0
2023 | summer | PNCHPP_1_PL1X2 | AMBIENT_DUE_TO_TEMP | 8696.39
2023 | summer | PNCHPP_1_PL1X2 | PLANT_MAINTENANCE | 0
2023 | summer | PNCHPP_1_PL1X2 | PLANT_TROUBLE | 977.85
2023 | summer | PNCHPP_1_PL1X2 | TRANSMISSION_INDUCED | 0
2023 | summer | PNCHVS_2_SOLAR | METERING_TELEMETRY | 82.5
2023 | summer | PNCHVS_2_SOLAR | PLANT_TROUBLE | 332.0587
2023 | summer | PNOCHE_1_PL1X2 | AMBIENT_DUE_TO_TEMP | 1454.8332
2023 | summer | PNOCHE_1_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 39.85
2023 | summer | PNOCHE_1_PL1X2 | PLANT_TROUBLE | 66.13
2023 | summer | PNOCHE_1_UNITA1 | AMBIENT_DUE_TO_TEMP | 28.21
2023 | summer | PNOCHE_1_UNITA1 | PLANT_MAINTENANCE | 0
2023 | summer | PNOCHE_1_UNITA1 | PLANT_TROUBLE | 859.2933
2023 | summer | PNOCHE_1_UNITA1 | TRANSMISSION_INDUCED | 0
2023 | summer | POEPH_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 24299.0538
2023 | summer | POEPH_7_UNIT 1 | PLANT_TROUBLE | 3162.0007
2023 | summer | POEPH_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 22178.1898
2023 | summer | POEPH_7_UNIT 2 | PLANT_TROUBLE | 4041.796
2023 | summer | POEPH_7_UNIT 2 | TRANSMISSION_INDUCED | 0
2023 | summer | POTTER_6_UNITS | PLANT_MAINTENANCE | 578
2023 | summer | POTTER_6_UNITS | PLANT_TROUBLE | 937
2023 | summer | PRCTVY_1_MIGBT1 | PLANT_MAINTENANCE | 5
2023 | summer | PRCTVY_1_MIGBT1 | PLANT_TROUBLE | 77.3333
2023 | summer | PRIMM_2_SOLAR1 | PLANT_MAINTENANCE | 88.74
2023 | summer | PRIMM_2_SOLAR1 | PLANT_TROUBLE | 479.9867
2023 | summer | PUTHCR_1_PCNSB1 | METERING_TELEMETRY | 43.75
2023 | summer | PUTHCR_1_PCNSB1 | PLANT_MAINTENANCE | 3
2023 | summer | PUTHCR_1_PCNSB1 | PLANT_TROUBLE | 136.55
2023 | summer | PUTHCR_1_SOLAR1 | PLANT_TROUBLE | 1.2907
2023 | summer | PVERDE_5_SCEDYN | AMBIENT_DUE_TO_TEMP | 150
2023 | summer | PVERDE_5_SCEDYN | PLANT_MAINTENANCE | 820
2023 | summer | PVERDE_5_SCEDYN | PLANT_TROUBLE | 9096.6667
2023 | summer | PWEST_1_UNIT | PLANT_TROUBLE | 1606.5
2023 | summer | RAMON_2_SCEDYN | AMBIENT_NOT_DUE_TO_TEMP | 47524.8333
2023 | summer | RAMON_2_SCEDYN | PLANT_MAINTENANCE | 517.5
2023 | summer | RATSKE_2_NROSR1 | PLANT_MAINTENANCE | 150
2023 | summer | RATSKE_2_NROSR1 | PLANT_TROUBLE | 362.75
2023 | summer | RATSKE_2_NROSR1 | UNIT_TESTING | 0
2023 | summer | RATSKE_2_RBSSB1 | PLANT_MAINTENANCE | 120
2023 | summer | RATSKE_2_RBSSB1 | PLANT_TROUBLE | 0
2023 | summer | RATSKE_2_RBSSB2 | PLANT_MAINTENANCE | 200
2023 | summer | RATSKE_2_RBSSB2 | PLANT_TROUBLE | 0.66667
2023 | summer | RCKCRK_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 24860.7993
2023 | summer | RCKCRK_7_UNIT 1 | PLANT_TROUBLE | 0
2023 | summer | RCKCRK_7_UNIT 1 | TRANSMISSION_INDUCED | 0
2023 | summer | RCKCRK_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 2032.8408
2023 | summer | RCKCRK_7_UNIT 2 | PLANT_TROUBLE | 0
2023 | summer | RDWAY_1_CREST | PLANT_MAINTENANCE | 4
2023 | summer | RDWAY_1_SCKSR1 | PLANT_MAINTENANCE | 141
2023 | summer | RDWAY_1_SCKSR1 | PLANT_TROUBLE | 16.5
2023 | summer | RDWAY_1_SCKSR1 | UNIT_TESTING | 0
2023 | summer | RECTOR_2_IVANPV | PLANT_MAINTENANCE | 52.5
2023 | summer | RECTOR_2_KAWEAH | AMBIENT_NOT_DUE_TO_TEMP | 4255.75
2023 | summer | RECTOR_2_KAWH 1 | AMBIENT_NOT_DUE_TO_TEMP | 1597.5
2023 | summer | RECTOR_2_QF | ENVIRONMENTAL_RESTRICTIONS | 2410.8
2023 | summer | RECTOR_2_QF | PLANT_TROUBLE | 518.6568
2023 | summer | RECTOR_2_TFDBM1 | PLANT_MAINTENANCE | 0
2023 | summer | RECTOR_2_TFDBM1 | PLANT_TROUBLE | 34.0533
2023 | summer | REDBLF_6_UNIT | AMBIENT_DUE_TO_TEMP | 8.8
2023 | summer | REDBLF_6_UNIT | METERING_TELEMETRY | 0
2023 | summer | REDBLF_6_UNIT | PLANT_MAINTENANCE | 311.9167
2023 | summer | REDBLF_6_UNIT | PLANT_TROUBLE | 156.3
2023 | summer | REDBLF_6_UNIT | TRANSMISSION_INDUCED | 24.2
2023 | summer | REDOND_7_UNIT 5 | AMBIENT_DUE_TO_TEMP | 6634.5762
2023 | summer | REDOND_7_UNIT 5 | PLANT_TROUBLE | 5814.8412
2023 | summer | REDOND_7_UNIT 5 | UNIT_SUPPORTING_STARTUP | 0
2023 | summer | REDOND_7_UNIT 5 | UNIT_TESTING | 0
2023 | summer | REDOND_7_UNIT 6 | AMBIENT_DUE_TO_TEMP | 5115.1208
2023 | summer | REDOND_7_UNIT 6 | PLANT_TROUBLE | 4631.519
2023 | summer | REDOND_7_UNIT 6 | UNIT_SUPPORTING_STARTUP | 498.4715
2023 | summer | REDOND_7_UNIT 6 | UNIT_TESTING | 0
2023 | summer | REDOND_7_UNIT 8 | AMBIENT_DUE_TO_TEMP | 2314.6833
2023 | summer | REDOND_7_UNIT 8 | PLANT_TROUBLE | 54541.8
2023 | summer | REDOND_7_UNIT 8 | UNIT_TESTING | 0
2023 | summer | RENWD_1_QF | PLANT_MAINTENANCE | 3063.35
2023 | summer | RICHMN_1_CHVSR2 | PLANT_MAINTENANCE | 8.5
2023 | summer | RICHMN_1_CHVSR2 | PLANT_TROUBLE | 166.55
2023 | summer | RICHMN_1_SOLAR | PLANT_MAINTENANCE | 2
2023 | summer | RICHMN_1_SOLAR | PLANT_TROUBLE | 0
2023 | summer | RICHMN_7_BAYENV | PLANT_TROUBLE | 1912.5
2023 | summer | RIOBRV_6_UNIT 1 | ENVIRONMENTAL_RESTRICTIONS | 70
2023 | summer | RIOBRV_6_UNIT 1 | PLANT_TROUBLE | 717.6167
2023 | summer | RIOBRV_6_UNIT 1 | TRANSMISSION_INDUCED | 14
2023 | summer | RNDMTN_2_SLSPHY1 | TRANSMISSION_INDUCED | 6.6
2023 | summer | ROLLIN_6_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 716.15
2023 | summer | ROLLIN_6_UNIT | PLANT_TROUBLE | 2.25
2023 | summer | ROSMDW_2_WIND1 | PLANT_MAINTENANCE | 3736.4667
2023 | summer | ROSMDW_2_WIND1 | PLANT_TROUBLE | 302.0667
2023 | summer | ROSMND_6_SOLAR | PLANT_TROUBLE | 6.775
2023 | summer | RSMSLR_6_SOLAR1 | PLANT_MAINTENANCE | 119.6667
2023 | summer | RSMSLR_6_SOLAR1 | PLANT_TROUBLE | 20
2023 | summer | RSMSLR_6_SOLAR2 | METERING_TELEMETRY | 0
2023 | summer | RSMSLR_6_SOLAR2 | PLANT_MAINTENANCE | 10
2023 | summer | RTEDDY_2_SC1SR3 | PLANT_MAINTENANCE | 400
2023 | summer | RTEDDY_2_SC1SR3 | PLANT_TROUBLE | 40
2023 | summer | RTEDDY_2_SEBSR3 | PLANT_MAINTENANCE | 616
2023 | summer | RTEDDY_2_SEBSR3 | PLANT_TROUBLE | 56
2023 | summer | RTEDDY_2_SEBSR4 | PLANT_MAINTENANCE | 504
2023 | summer | RTEDDY_2_SEBSR4 | PLANT_TROUBLE | 56
2023 | summer | RTEDDY_2_SOLAR1 | PLANT_TROUBLE | 0
2023 | summer | RTEDDY_2_SPASR4 | PLANT_MAINTENANCE | 260
2023 | summer | RTEDDY_2_SPASR4 | PLANT_TROUBLE | 26
2023 | summer | RTEDDY_2_SRXSR4 | PLANT_MAINTENANCE | 136
2023 | summer | RTEDDY_2_SRXSR4 | PLANT_TROUBLE | 13.6
2023 | summer | RTREE_2_WIND1 | PLANT_MAINTENANCE | 0
2023 | summer | RTREE_2_WIND1 | PLANT_TROUBLE | 0
2023 | summer | RTREE_2_WIND2 | PLANT_MAINTENANCE | 2020.6267
2023 | summer | RTREE_2_WIND2 | PLANT_TROUBLE | 65.395
2023 | summer | RUSCTY_2_UNITS | AMBIENT_DUE_TO_TEMP | 17670.08
2023 | summer | RUSCTY_2_UNITS | PLANT_TROUBLE | 6689.7362
2023 | summer | RUSCTY_2_UNITS | TRANSITIONAL_LIMITATION | 265.1167
2023 | summer | RUSCTY_2_UNITS | UNIT_TESTING | 41.36
2023 | summer | RVRVEW_1_UNITA1 | AMBIENT_DUE_TO_TEMP | 69.4167
2023 | summer | RVRVEW_1_UNITA1 | PLANT_TROUBLE | 2184.1367
2023 | summer | RVSIDE_2_RERCU4 | AMBIENT_NOT_DUE_TO_TEMP | 7
2023 | summer | RVSIDE_2_RERCU4 | PLANT_MAINTENANCE | 0
2023 | summer | RVSIDE_2_RERCU4 | PLANT_TROUBLE | 0
2023 | summer | RVSIDE_6_RERCU1 | PLANT_MAINTENANCE | 0
2023 | summer | RVSIDE_6_RERCU1 | PLANT_TROUBLE | 0
2023 | summer | RVSIDE_6_RERCU2 | PLANT_TROUBLE | 0
2023 | summer | RVSIDE_6_SPRING | PLANT_TROUBLE | 75
2023 | summer | SALIRV_2_UNIT | PLANT_MAINTENANCE | 234
2023 | summer | SALIRV_2_UNIT | PLANT_TROUBLE | 1454.05
2023 | summer | SALTSP_7_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 11580
2023 | summer | SALTSP_7_UNITS | PLANT_MAINTENANCE | 1650
2023 | summer | SALTSP_7_UNITS | PLANT_TROUBLE | 0
2023 | summer | SANBRN_2_ES1BT3 | PLANT_TROUBLE | 0
2023 | summer | SANBRN_2_ES2SB3 | PLANT_TROUBLE | 0
2023 | summer | SANBRN_2_ESABT1 | METERING_TELEMETRY | 0
2023 | summer | SANBRN_2_ESABT1 | PLANT_TROUBLE | 125
2023 | summer | SANBRN_2_ESBBT1 | METERING_TELEMETRY | 50
2023 | summer | SANBRN_2_ESBBT1 | PLANT_MAINTENANCE | 0
2023 | summer | SANBRN_2_ESBBT1 | PLANT_TROUBLE | 125
2023 | summer | SANBRN_2_ESBBT1 | UNIT_TESTING | 0
2023 | summer | SANBRN_2_SS2BT3 | METERING_TELEMETRY | 0
2023 | summer | SANBRN_2_SS2BT3 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | summer | SANBRN_2_SS2BT3 | PLANT_TROUBLE | 2396.7833
2023 | summer | SANBRN_2_SS2BT3 | UNIT_TESTING | 745
2023 | summer | SANBRN_2_SS2SB4 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | summer | SANBRN_2_SS2SB4 | PLANT_MAINTENANCE | 18
2023 | summer | SANBRN_2_SS2SB4 | PLANT_TROUBLE | 36
2023 | summer | SANBRN_2_SS2SB4 | UNIT_TESTING | 0
2023 | summer | SANDLT_2_SUNITS | AMBIENT_DUE_TO_TEMP | 0
2023 | summer | SANDLT_2_SUNITS | AMBIENT_NOT_DUE_TO_TEMP | 15228.5417
2023 | summer | SANDLT_2_SUNITS | PLANT_MAINTENANCE | 0
2023 | summer | SANDLT_2_SUNITS | PLANT_TROUBLE | 0
2023 | summer | SANLOB_1_LNDFIL | AMBIENT_DUE_TO_TEMP | 0.57833
2023 | summer | SANLOB_1_LNDFIL | PLANT_MAINTENANCE | 120.0967
2023 | summer | SANLOB_1_LNDFIL | PLANT_TROUBLE | 95.7233
2023 | summer | SANTFG_7_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 12915
2023 | summer | SANTFG_7_UNITS | PLANT_TROUBLE | 15
2023 | summer | SANTGO_2_LNDFL1 | PLANT_MAINTENANCE | 196
2023 | summer | SANTGO_2_LNDFL1 | PLANT_TROUBLE | 57
2023 | summer | SANTGO_2_LNDFL1 | TRANSMISSION_INDUCED | 0
2023 | summer | SANTGO_2_MABBT1 | PLANT_MAINTENANCE | 830.6483
2023 | summer | SANTGO_2_MABBT1 | PLANT_TROUBLE | 283.9227
2023 | summer | SANWD_1_QF | PLANT_MAINTENANCE | 8772.1352
2023 | summer | SAUGUS_6_MWDFTH | PLANT_TROUBLE | 307.7317
2023 | summer | SAUGUS_7_CHIQCN | PLANT_MAINTENANCE | 47.8667
2023 | summer | SBERDO_2_PSP3 | AMBIENT_DUE_TO_TEMP | 15010.5135
2023 | summer | SBERDO_2_PSP3 | METERING_TELEMETRY | 88.969
2023 | summer | SBERDO_2_PSP3 | PLANT_MAINTENANCE | 8311.81
2023 | summer | SBERDO_2_PSP3 | PLANT_TROUBLE | 3386.7847
2023 | summer | SBERDO_2_PSP3 | UNIT_TESTING | 0
2023 | summer | SBERDO_2_PSP4 | AMBIENT_DUE_TO_TEMP | 18038.41
2023 | summer | SBERDO_2_PSP4 | ENVIRONMENTAL_RESTRICTIONS | 1358.77
2023 | summer | SBERDO_2_PSP4 | METERING_TELEMETRY | 117.75
2023 | summer | SBERDO_2_PSP4 | PLANT_MAINTENANCE | 5854.2267
2023 | summer | SBERDO_2_PSP4 | PLANT_TROUBLE | 7004.5407
2023 | summer | SBERDO_2_PSP4 | UNIT_TESTING | 0
2023 | summer | SBERDO_2_REDLND | PLANT_TROUBLE | 1040
2023 | summer | SBERDO_2_RTS005 | PLANT_TROUBLE | 1300
2023 | summer | SBERDO_2_RTS007 | PLANT_TROUBLE | 1325
2023 | summer | SBERDO_2_RTS011 | PLANT_TROUBLE | 1207.5
2023 | summer | SBERDO_2_RTS013 | PLANT_TROUBLE | 612.5
2023 | summer | SBERDO_2_RTS016 | PLANT_TROUBLE | 780
2023 | summer | SBERDO_2_RTS048 | PLANT_TROUBLE | 875
2023 | summer | SBERDO_2_SNTANA | AMBIENT_NOT_DUE_TO_TEMP | 1360.25
2023 | summer | SBERDO_2_SNTANA | PLANT_TROUBLE | 3837.7583
2023 | summer | SBERDO_6_MILLCK | AMBIENT_NOT_DUE_TO_TEMP | 1415.8
2023 | summer | SBERDO_6_MILLCK | PLANT_TROUBLE | 674.25
2023 | summer | SCEC_1_PDRP124 | MONTHLY_USE_LIMIT_REACHED | 18.3
2023 | summer | SCEC_1_PDRP16 | MONTHLY_USE_LIMIT_REACHED | 1589.4
2023 | summer | SCEC_1_PDRP173 | MONTHLY_USE_LIMIT_REACHED | 22.3
2023 | summer | SCEC_1_RDRR08 | METERING_TELEMETRY | 0
2023 | summer | SCEC_1_RDRR08 | OTHER_USE_LIMIT_REACHED | 74
2023 | summer | SCEC_1_RDRR35 | METERING_TELEMETRY | 46.42
2023 | summer | SCEC_1_RDRR36 | METERING_TELEMETRY | 26.41
2023 | summer | SCEC_1_RDRR37 | METERING_TELEMETRY | 13.71
2023 | summer | SCEC_1_RDRR38 | METERING_TELEMETRY | 55.83
2023 | summer | SCEN_6_RDRR02 | METERING_TELEMETRY | 0
2023 | summer | SCEN_6_RDRR02 | OTHER_USE_LIMIT_REACHED | 37.5
2023 | summer | SCEN_6_RDRR12 | METERING_TELEMETRY | 40.41
2023 | summer | SCEW_2_PDRP03 | MONTHLY_USE_LIMIT_REACHED | 50
2023 | summer | SCEW_2_PDRP09 | MONTHLY_USE_LIMIT_REACHED | 25
2023 | summer | SCEW_2_PDRP10 | PLANT_TROUBLE | 1985.95
2023 | summer | SCEW_2_PDRP114 | MONTHLY_USE_LIMIT_REACHED | 64.7
2023 | summer | SCEW_2_PDRP12 | MONTHLY_USE_LIMIT_REACHED | 529.2
2023 | summer | SCEW_2_PDRP159 | MONTHLY_USE_LIMIT_REACHED | 72.8
2023 | summer | SCEW_2_PDRP160 | MONTHLY_USE_LIMIT_REACHED | 45.8
2023 | summer | SCEW_2_PDRP163 | MONTHLY_USE_LIMIT_REACHED | 81.9
2023 | summer | SCEW_2_PDRP167 | MONTHLY_USE_LIMIT_REACHED | 94.2
2023 | summer | SCEW_2_RDRR08 | METERING_TELEMETRY | 0
2023 | summer | SCEW_2_RDRR08 | OTHER_USE_LIMIT_REACHED | 28.5333
2023 | summer | SCEW_2_RDRR25 | METERING_TELEMETRY | 32.19
2023 | summer | SCEW_2_RDRR26 | METERING_TELEMETRY | 19.54
2023 | summer | SCHD_1_RDRR08 | METERING_TELEMETRY | 0
2023 | summer | SCHD_1_RDRR08 | OTHER_USE_LIMIT_REACHED | 60
2023 | summer | SCHD_1_RDRR11 | METERING_TELEMETRY | 24.08
2023 | summer | SCHLTE_1_PL1X3 | AMBIENT_DUE_TO_TEMP | 2070.8673
2023 | summer | SCHLTE_1_PL1X3 | PLANT_MAINTENANCE | 504.06
2023 | summer | SCHLTE_1_PL1X3 | PLANT_TROUBLE | 1008.12
2023 | summer | SCHNDR_1_WSTSDE | METERING_TELEMETRY | 60
2023 | summer | SCHNDR_1_WSTSDE | PLANT_TROUBLE | 1205
2023 | summer | SCNW_6_PDRP57 | MONTHLY_USE_LIMIT_REACHED | 284.4
2023 | summer | SCNW_6_PDRP61 | MONTHLY_USE_LIMIT_REACHED | 173.7
2023 | summer | SCNW_6_RDRR08 | METERING_TELEMETRY | 0
2023 | summer | SCNW_6_RDRR08 | OTHER_USE_LIMIT_REACHED | 9.5
2023 | summer | SCNW_6_RDRR10 | METERING_TELEMETRY | 16.3
2023 | summer | SEARLS_7_ARGUS | PLANT_MAINTENANCE | 2654
2023 | summer | SEGS_1_SR2SL2 | METERING_TELEMETRY | 100
2023 | summer | SEGS_1_SR2SL2 | PLANT_MAINTENANCE | 40
2023 | summer | SEGS_1_SR2SL2 | TRANSMISSION_INDUCED | 0
2023 | summer | SENTNL_2_CTG1 | AMBIENT_DUE_TO_TEMP | 2483.6
2023 | summer | SENTNL_2_CTG1 | ENVIRONMENTAL_RESTRICTIONS | 8883.9
2023 | summer | SENTNL_2_CTG1 | PLANT_TROUBLE | 59.8
2023 | summer | SENTNL_2_CTG1 | UNIT_TESTING | 225
2023 | summer | SENTNL_2_CTG2 | AMBIENT_DUE_TO_TEMP | 6362.5433
2023 | summer | SENTNL_2_CTG2 | PLANT_MAINTENANCE | 0
2023 | summer | SENTNL_2_CTG2 | PLANT_TROUBLE | 36.795
2023 | summer | SENTNL_2_CTG2 | UNIT_TESTING | 274.21
2023 | summer | SENTNL_2_CTG3 | AMBIENT_DUE_TO_TEMP | 6234.7433
2023 | summer | SENTNL_2_CTG3 | ENVIRONMENTAL_RESTRICTIONS | 22.5723
2023 | summer | SENTNL_2_CTG3 | PLANT_MAINTENANCE | 0
2023 | summer | SENTNL_2_CTG3 | PLANT_TROUBLE | 695.0885
2023 | summer | SENTNL_2_CTG3 | UNIT_TESTING | 139.3927
2023 | summer | SENTNL_2_CTG4 | AMBIENT_DUE_TO_TEMP | 6071.6633
2023 | summer | SENTNL_2_CTG4 | PLANT_MAINTENANCE | 0
2023 | summer | SENTNL_2_CTG4 | PLANT_TROUBLE | 264.31
2023 | summer | SENTNL_2_CTG4 | UNIT_TESTING | 243.0233
2023 | summer | SENTNL_2_CTG5 | AMBIENT_DUE_TO_TEMP | 6097.5467
2023 | summer | SENTNL_2_CTG5 | PLANT_MAINTENANCE | 0
2023 | summer | SENTNL_2_CTG5 | PLANT_TROUBLE | 291.1733
2023 | summer | SENTNL_2_CTG5 | UNIT_TESTING | 183.06
2023 | summer | SENTNL_2_CTG6 | AMBIENT_DUE_TO_TEMP | 5979.5067
2023 | summer | SENTNL_2_CTG6 | PLANT_TROUBLE | 46.8067
2023 | summer | SENTNL_2_CTG6 | UNIT_TESTING | 181.2
2023 | summer | SENTNL_2_CTG7 | AMBIENT_DUE_TO_TEMP | 2439.95
2023 | summer | SENTNL_2_CTG7 | PLANT_MAINTENANCE | 2752.1667
2023 | summer | SENTNL_2_CTG7 | PLANT_TROUBLE | 21065.0272
2023 | summer | SENTNL_2_CTG7 | UNIT_TESTING | 240
2023 | summer | SENTNL_2_CTG8 | AMBIENT_DUE_TO_TEMP | 6134.9733
2023 | summer | SENTNL_2_CTG8 | UNIT_TESTING | 311.55
2023 | summer | SGREGY_6_SANGER | PLANT_MAINTENANCE | 5.635
2023 | summer | SGREGY_6_SANGER | PLANT_TROUBLE | 123.0067
2023 | summer | SHANDN_2_SBBBM1 | NEW_GENERATOR_TEST_ENERGY | 221
2023 | summer | SHUTLE_6_CREST | PLANT_TROUBLE | 387.5
2023 | summer | SIERRA_1_UNITS | AMBIENT_DUE_TO_TEMP | 2280.15
2023 | summer | SIERRA_1_UNITS | PLANT_TROUBLE | 744
2023 | summer | SIGHEB_6_HE2SCEDYN | PLANT_MAINTENANCE | 0
2023 | summer | SIGHEB_6_MIRDYN | ENVIRONMENTAL_RESTRICTIONS | 85
2023 | summer | SIGHEB_6_MIRDYN | PLANT_MAINTENANCE | 93.5
2023 | summer | SIGHEB_6_MIRDYN | PLANT_TROUBLE | 148.75
2023 | summer | SISPRG_2_DS3BT2 | METERING_TELEMETRY | 0
2023 | summer | SISPRG_2_DS3BT2 | PLANT_MAINTENANCE | 0
2023 | summer | SISPRG_2_DS3BT2 | PLANT_TROUBLE | 372.6667
2023 | summer | SISPRG_2_DS3BT2 | UNIT_TESTING | 0
2023 | summer | SISPRG_2_DS3BT3 | METERING_TELEMETRY | 77
2023 | summer | SISPRG_2_DS3BT3 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | summer | SISPRG_2_DS3BT3 | PLANT_TROUBLE | 314.0917
2023 | summer | SISPRG_2_DS3BT3 | RTU_RIG | 0
2023 | summer | SISPRG_2_DS3BT3 | UNIT_TESTING | 12.5
2023 | summer | SISPRG_2_DS3BT4 | METERING_TELEMETRY | 15
2023 | summer | SISPRG_2_DS3BT4 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | summer | SISPRG_2_DS3BT4 | PLANT_MAINTENANCE | 2.3333
2023 | summer | SISPRG_2_DS3BT4 | PLANT_TROUBLE | 143.75
2023 | summer | SISPRG_2_DS3BT4 | UNIT_TESTING | 0
2023 | summer | SISPRG_2_DS3SR1 | METERING_TELEMETRY | 0
2023 | summer | SISPRG_2_DS3SR1 | NEW_GENERATOR_TEST_ENERGY | 1196
2023 | summer | SISPRG_2_DS3SR1 | PLANT_TROUBLE | 0
2023 | summer | SISPRG_2_DS3SR1 | UNIT_TESTING | 0
2023 | summer | SISPRG_2_DS3SR2 | PLANT_MAINTENANCE | 0
2023 | summer | SISPRG_2_DS3SR2 | PLANT_TROUBLE | 900
2023 | summer | SISPRG_2_DS3SR3 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | summer | SISPRG_2_DS3SR3 | PLANT_TROUBLE | 83.3333
2023 | summer | SISPRG_2_DS3SR3 | UNIT_TESTING | 0
2023 | summer | SISPRG_2_DS3SR4 | METERING_TELEMETRY | 23.5167
2023 | summer | SISPRG_2_DS3SR4 | NEW_GENERATOR_TEST_ENERGY | 25
2023 | summer | SISPRG_2_DS3SR4 | PLANT_MAINTENANCE | 68
2023 | summer | SISPRG_2_DS3SR4 | PLANT_TROUBLE | 259.25
2023 | summer | SISPRG_2_DS3SR4 | UNIT_TESTING | 258
2023 | summer | SKERN_6_SOLAR1 | TRANSMISSION_INDUCED | 20
2023 | summer | SKERN_6_SOLAR2 | TRANSMISSION_INDUCED | 10
2023 | summer | SLATE_2_SLASR1 | METERING_TELEMETRY | 75.75
2023 | summer | SLATE_2_SLASR1 | PLANT_MAINTENANCE | 0
2023 | summer | SLATE_2_SLASR1 | PLANT_TROUBLE | 901.6183
2023 | summer | SLATE_2_SLASR2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 257.3
2023 | summer | SLATE_2_SLASR2 | METERING_TELEMETRY | 139.2
2023 | summer | SLATE_2_SLASR2 | PLANT_MAINTENANCE | 139.5
2023 | summer | SLATE_2_SLASR2 | PLANT_TROUBLE | 1746.8
2023 | summer | SLATE_2_SLASR2 | UNIT_TESTING | 0
2023 | summer | SLATE_2_SLASR3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2023 | summer | SLATE_2_SLASR3 | METERING_TELEMETRY | 118.0167
2023 | summer | SLATE_2_SLASR3 | PLANT_MAINTENANCE | 210.185
2023 | summer | SLATE_2_SLASR3 | PLANT_TROUBLE | 2045.775
2023 | summer | SLATE_2_SLASR3 | UNIT_TESTING | 0
2023 | summer | SLATE_2_SLASR4 | METERING_TELEMETRY | 94.5
2023 | summer | SLATE_2_SLASR4 | PLANT_MAINTENANCE | 0
2023 | summer | SLATE_2_SLASR4 | PLANT_TROUBLE | 89.25
2023 | summer | SLATE_2_SLASR5 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1346.3667
2023 | summer | SLATE_2_SLASR5 | METERING_TELEMETRY | 102.7
2023 | summer | SLATE_2_SLASR5 | PLANT_MAINTENANCE | 0
2023 | summer | SLATE_2_SLASR5 | PLANT_TROUBLE | 238.2515
2023 | summer | SLRMS3_2_SRMSR1 | TRANSMISSION_INDUCED | 250
2023 | summer | SLST13_2_SOLAR1 | PLANT_MAINTENANCE | 0
2023 | summer | SLST13_2_SOLAR1 | PLANT_TROUBLE | 1184
2023 | summer | SLST13_2_SOLAR1 | TRANSMISSION_INDUCED | 9146
2023 | summer | SLSTR1_2_SOLAR1 | PLANT_MAINTENANCE | 310
2023 | summer | SLSTR1_2_SOLAR1 | PLANT_TROUBLE | 118.5
2023 | summer | SLSTR2_2_SOLAR2 | PLANT_MAINTENANCE | 276
2023 | summer | SLUISP_2_UNITS | PLANT_MAINTENANCE | 19542.6185
2023 | summer | SLUISP_2_UNITS | PLANT_TROUBLE | 7066.5813
2023 | summer | SLYCRK_1_UNIT 1 | PLANT_TROUBLE | 64.35
2023 | summer | SMPRIP_1_SMPSON | PLANT_MAINTENANCE | 3018.7475
2023 | summer | SMPRIP_1_SMPSON | PLANT_TROUBLE | 303.1625
2023 | summer | SMPRIP_1_SMPSON | TRANSMISSION_INDUCED | 0
2023 | summer | SMRCOS_6_LNDFIL | PLANT_MAINTENANCE | 0
2023 | summer | SMUDGO_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 10154
2023 | summer | SMUDGO_7_UNIT 1 | PLANT_MAINTENANCE | 0
2023 | summer | SMYRNA_1_DL1SR1 | TRANSMISSION_INDUCED | 4
2023 | summer | SNCLRA_2_HOWLNG | AMBIENT_NOT_DUE_TO_TEMP | 56.37
2023 | summer | SNCLRA_2_HOWLNG | PLANT_TROUBLE | 1191.69
2023 | summer | SNCLRA_2_SILBT1 | METERING_TELEMETRY | 0
2023 | summer | SNCLRA_2_SILBT1 | PLANT_MAINTENANCE | 8.8
2023 | summer | SNCLRA_2_SILBT1 | PLANT_TROUBLE | 68
2023 | summer | SNCLRA_2_SILBT1 | UNIT_TESTING | 0
2023 | summer | SNCLRA_2_UNIT | ENVIRONMENTAL_RESTRICTIONS | 2475
2023 | summer | SNCLRA_2_UNIT1 | AMBIENT_NOT_DUE_TO_TEMP | 10710
2023 | summer | SNCLRA_2_UNIT1 | PLANT_MAINTENANCE | 425
2023 | summer | SNCLRA_2_UNIT1 | PLANT_TROUBLE | 104.2083
2023 | summer | SNCLRA_2_VESBT1 | ICCP | 0
2023 | summer | SNCLRA_2_VESBT1 | METERING_TELEMETRY | 500
2023 | summer | SNCLRA_2_VESBT1 | PLANT_MAINTENANCE | 0
2023 | summer | SNCLRA_2_VESBT1 | PLANT_TROUBLE | 4000
2023 | summer | SNCLRA_6_OXGEN | PLANT_TROUBLE | 381.6
2023 | summer | SNDBAR_7_UNIT 1 | PLANT_TROUBLE | 0
2023 | summer | SNDBAR_7_UNIT 1 | TRANSMISSION_INDUCED | 26.92
2023 | summer | SOUTH_2_UNIT | AMBIENT_DUE_TO_TEMP | 35.5
2023 | summer | SOUTH_2_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 48.635
2023 | summer | SOUTH_2_UNIT | TRANSMISSION_INDUCED | 0
2023 | summer | SPAULD_6_UNIT 3 | AMBIENT_NOT_DUE_TO_TEMP | 312.6
2023 | summer | SPAULD_6_UNIT 3 | PLANT_TROUBLE | 0
2023 | summer | SPAULD_6_UNIT12 | AMBIENT_NOT_DUE_TO_TEMP | 825.5
2023 | summer | SPAULD_6_UNIT12 | PLANT_TROUBLE | 2523.3533
2023 | summer | SPAULD_6_UNIT12 | TRANSMISSION_INDUCED | 11.2257
2023 | summer | SPBURN_2_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 26.2
2023 | summer | SPBURN_2_UNIT 1 | PLANT_MAINTENANCE | 660
2023 | summer | SPBURN_2_UNIT 1 | PLANT_TROUBLE | 194.0667
2023 | summer | SPBURN_7_SNOWMT | AMBIENT_NOT_DUE_TO_TEMP | 2088.45
2023 | summer | SPI LI_2_UNIT 1 | PLANT_MAINTENANCE | 86
2023 | summer | SPI LI_2_UNIT 1 | PLANT_TROUBLE | 34.4
2023 | summer | SPI LI_2_UNIT 1 | TRANSMISSION_INDUCED | 0
2023 | summer | SPIAND_1_ANDSN2 | PLANT_TROUBLE | 99.55
2023 | summer | SPICER_1_UNITS | PLANT_TROUBLE | 18
2023 | summer | SPICER_1_UNITS | TRANSMISSION_INDUCED | 456
2023 | summer | SPIFBD_1_PL1X2 | PLANT_MAINTENANCE | 37.5
2023 | summer | SPIFBD_1_PL1X2 | PLANT_TROUBLE | 312.125
2023 | summer | SPIFBD_1_PL1X2 | TRANSMISSION_INDUCED | 11.375
2023 | summer | SPQUIN_6_SRPCQU | PLANT_MAINTENANCE | 644.7333
2023 | summer | SPQUIN_6_SRPCQU | PLANT_TROUBLE | 168.0837
2023 | summer | SPQUIN_6_SRPCQU | TRANSMISSION_INDUCED | 0
2023 | summer | SPRGAP_1_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 1630.82
2023 | summer | SPRGAP_1_UNIT 1 | PLANT_MAINTENANCE | 0
2023 | summer | SPRGAP_1_UNIT 1 | TRANSMISSION_INDUCED | 195.45
2023 | summer | SPRGVL_2_EXETPV | METERING_TELEMETRY | 157.5
2023 | summer | SPRGVL_2_EXETPV | PLANT_TROUBLE | 949.0833
2023 | summer | SPRGVL_2_LINDPV | PLANT_MAINTENANCE | 60
2023 | summer | SPRGVL_2_LINDPV | TRANSMISSION_INDUCED | 60
2023 | summer | SPRGVL_2_PORTPV | METERING_TELEMETRY | 122.5
2023 | summer | SPRGVL_2_PORTPV | PLANT_MAINTENANCE | 52.5
2023 | summer | SPRGVL_2_TULESC | ENVIRONMENTAL_RESTRICTIONS | 1912.5
2023 | summer | SRINTL_6_UNIT | TRANSMISSION_INDUCED | 34.5
2023 | summer | STANIS_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 296.04
2023 | summer | STANTN_2_SBEBX2 | AMBIENT_NOT_DUE_TO_TEMP | 112.2533
2023 | summer | STANTN_2_SBEBX2 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | summer | STANTN_2_SBEBX2 | PLANT_MAINTENANCE | 3867.2883
2023 | summer | STANTN_2_SBEBX2 | PLANT_TROUBLE | 42.4267
2023 | summer | STANTN_2_SBEBX2 | TRANSMISSION_INDUCED | 32.8
2023 | summer | STANTN_2_STAGT1 | AMBIENT_DUE_TO_TEMP | 4.2592
2023 | summer | STANTN_2_STAGT1 | METERING_TELEMETRY | 3.31
2023 | summer | STANTN_2_STAGT1 | PLANT_MAINTENANCE | 0
2023 | summer | STANTN_2_STAGT1 | PLANT_TROUBLE | 3.6992
2023 | summer | STANTN_2_STAGT2 | AMBIENT_DUE_TO_TEMP | 758.5675
2023 | summer | STANTN_2_STAGT2 | AMBIENT_NOT_DUE_TO_TEMP | 17.79
2023 | summer | STANTN_2_STAGT2 | METERING_TELEMETRY | 2.4825
2023 | summer | STANTN_2_STAGT2 | PLANT_MAINTENANCE | 0
2023 | summer | STANTN_2_STAGT2 | PLANT_TROUBLE | 83.9297
2023 | summer | STIGCT_2_LODI | AMBIENT_DUE_TO_TEMP | 3443.5
2023 | summer | STIGCT_2_LODI | PLANT_TROUBLE | 119.75
2023 | summer | STNRES_1_UNIT | PLANT_MAINTENANCE | 497.5
2023 | summer | STOILS_1_UNITS | PLANT_TROUBLE | 1185.6
2023 | summer | STROUD_6_SOLAR | PLANT_MAINTENANCE | 0
2023 | summer | STROUD_6_SOLAR | PLANT_TROUBLE | 935
2023 | summer | STROUD_6_WWHSR1 | PLANT_TROUBLE | 112.5
2023 | summer | SUMWHT_6_SWSSR1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | summer | SUMWHT_6_SWSSR1 | TRANSMISSION_INDUCED | 17.575
2023 | summer | SUNCAT_2_A1ABT1 | PLANT_TROUBLE | 13270.0433
2023 | summer | SUNCAT_2_A1BBT1 | PLANT_TROUBLE | 20383.7357
2023 | summer | SUNCAT_2_A2ABT2 | PLANT_TROUBLE | 18822.905
2023 | summer | SUNCAT_2_A2ABT2 | UNIT_TESTING | 4.4167
2023 | summer | SUNCAT_2_A2BSR2 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | summer | SUNCAT_2_A2BSR2 | PLANT_MAINTENANCE | 2325
2023 | summer | SUNCAT_2_A2BSR2 | UNIT_TESTING | 0
2023 | summer | SUNRIS_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 35269.1933
2023 | summer | SUNRIS_2_PL1X3 | ENVIRONMENTAL_RESTRICTIONS | 469.9887
2023 | summer | SUNRIS_2_PL1X3 | PLANT_MAINTENANCE | 1490.1
2023 | summer | SUNRIS_2_PL1X3 | PLANT_TROUBLE | 12344.8063
2023 | summer | SUNRIS_2_PL1X3 | TRANSITIONAL_LIMITATION | 0
2023 | summer | SUNRIS_2_PL1X3 | TRANSMISSION_INDUCED | 624.28
2023 | summer | SUNSET_2_UNITS | AMBIENT_DUE_TO_TEMP | 14210
2023 | summer | SUNSET_2_UNITS | PLANT_MAINTENANCE | 268
2023 | summer | SUNSET_2_UNITS | PLANT_TROUBLE | 118.5667
2023 | summer | SUNSHN_2_LNDFL | AMBIENT_DUE_TO_TEMP | 66.2167
2023 | summer | SUNSHN_2_LNDFL | AMBIENT_NOT_DUE_TO_TEMP | 52.9117
2023 | summer | SUNSHN_2_LNDFL | METERING_TELEMETRY | 2.85
2023 | summer | SUNSHN_2_LNDFL | PLANT_MAINTENANCE | 835.1083
2023 | summer | SUNSHN_2_LNDFL | PLANT_TROUBLE | 3022.16
2023 | summer | SUNSHN_2_LNDFL | TRANSMISSION_INDUCED | 259.9333
2023 | summer | SUNSLR_1_SSVSR1 | ENVIRONMENTAL_RESTRICTIONS | 104
2023 | summer | SUNSLR_1_SSVSR1 | METERING_TELEMETRY | 234.5
2023 | summer | SUNSLR_1_SSVSR1 | PLANT_MAINTENANCE | 98.9667
2023 | summer | SUNSLR_1_SSVSR1 | PLANT_TROUBLE | 16993.2333
2023 | summer | SUNSPT_2_WNASR1 | METERING_TELEMETRY | 0
2023 | summer | SUNSPT_2_WNASR1 | PLANT_MAINTENANCE | 0
2023 | summer | SUNSPT_2_WNASR1 | PLANT_TROUBLE | 270.75
2023 | summer | SUNST2_5_SS2SR1 | PLANT_MAINTENANCE | 737.5
2023 | summer | SUNSTR_5_SS1SCEDYN | PLANT_TROUBLE | 8290.4
2023 | summer | SUTTER_2_CISO | AMBIENT_DUE_TO_TEMP | 10639.65
2023 | summer | SUTTER_2_CISO | PLANT_MAINTENANCE | 522.3167
2023 | summer | SUTTER_2_CISO | PLANT_TROUBLE | 2115.2333
2023 | summer | SUTTER_2_CISO | TRANSITIONAL_LIMITATION | 43.6667
2023 | summer | SYCAMR_2_UNIT 1 | PLANT_MAINTENANCE | 370
2023 | summer | SYCAMR_2_UNIT 1 | PLANT_TROUBLE | 5744.8667
2023 | summer | SYCAMR_2_UNIT 1 | UNIT_TESTING | 240.5
2023 | summer | SYCAMR_2_UNIT 2 | PLANT_MAINTENANCE | 1900
2023 | summer | SYCAMR_2_UNIT 2 | PLANT_TROUBLE | 910.7333
2023 | summer | SYCAMR_2_UNIT 3 | PLANT_TROUBLE | 622.8333
2023 | summer | SYCAMR_2_UNIT 4 | PLANT_MAINTENANCE | 0
2023 | summer | TANHIL_6_SOLART | PLANT_MAINTENANCE | 0
2023 | summer | TANHIL_6_SOLART | PLANT_TROUBLE | 35.7333
2023 | summer | TBLMTN_6_QF | PLANT_TROUBLE | 476
2023 | summer | TBLMTN_6_QF | TRANSMISSION_INDUCED | 8.5283
2023 | summer | TECOLOTE_3_WBDYN | AMBIENT_DUE_TO_TEMP | 370
2023 | summer | TECOLOTE_3_WBDYN | PLANT_MAINTENANCE | 17.84
2023 | summer | TECOLOTE_3_WBDYN | PLANT_TROUBLE | 1432.4693
2023 | summer | TECOLOTE_3_WBDYN | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 2080.96
2023 | summer | TECOLOTE_3_WBDYN | TRANSITIONAL_LIMITATION | 5637.7573
2023 | summer | TECOLOTE_3_WBDYN | TRANSMISSION_INDUCED | 30097.0667
2023 | summer | TEHAPI_2_PW1WD1 | PLANT_TROUBLE | 575
2023 | summer | TEHAPI_2_PW2WD2 | TRANSMISSION_INDUCED | 1129.44
2023 | summer | TEHAPI_2_WIND1 | TRANSMISSION_INDUCED | 99.25
2023 | summer | TEHAPI_2_WIND2 | PLANT_MAINTENANCE | 76.1063
2023 | summer | TEHAPI_2_WIND2 | PLANT_TROUBLE | 118.3
2023 | summer | TEHAPI_2_WIND2 | TRANSMISSION_INDUCED | 118.3
2023 | summer | TENGEN_2_PL1X2 | PLANT_MAINTENANCE | 3280.7283
2023 | summer | TENGEN_2_PL1X2 | PLANT_TROUBLE | 26.68
2023 | summer | TENGEN_2_PL1X2 | UNIT_TESTING | 75.4
2023 | summer | TERMEX_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 16954.7667
2023 | summer | TERMEX_2_PL1X3 | PLANT_MAINTENANCE | 1797
2023 | summer | TERMEX_2_PL1X3 | PLANT_TROUBLE | 1338.5
2023 | summer | TERMEX_2_PL1X3 | UNIT_TESTING | 587
2023 | summer | TIDWTR_2_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 11.2
2023 | summer | TIDWTR_2_UNITS | PLANT_MAINTENANCE | 5263.8
2023 | summer | TIDWTR_2_UNITS | PLANT_TROUBLE | 14308.9667
2023 | summer | TIFFNY_1_DILLON | AMBIENT_DUE_TO_TEMP | 1677.8
2023 | summer | TIFFNY_1_DILLON | PLANT_TROUBLE | 1321.9667
2023 | summer | TIFFNY_1_DILLON | TRANSMISSION_INDUCED | 108.84
2023 | summer | TIGRCK_7_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 760.425
2023 | summer | TIGRCK_7_UNITS | PLANT_TROUBLE | 2106.6083
2023 | summer | TITANS_2_TTSSR1 | PLANT_MAINTENANCE | 52
2023 | summer | TITANS_2_TTSSR1 | PLANT_TROUBLE | 423.0133
2023 | summer | TITANS_2_TTSSR1 | TRANSMISSION_INDUCED | 4349.5667
2023 | summer | TITANS_2_TTSSR1 | UNIT_TESTING | 0
2023 | summer | TKOPWR_6_HYDRO | TRANSMISSION_INDUCED | 3.5375
2023 | summer | TOADTW_6_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | summer | TOADTW_6_UNIT | PLANT_TROUBLE | 30
2023 | summer | TOADTW_6_UNIT | TRANSMISSION_INDUCED | 132.1
2023 | summer | TOPAZ_2_SOLAR | PLANT_TROUBLE | 52606.7167
2023 | summer | TOPAZ_2_SOLAR | TRANSMISSION_INDUCED | 1350
2023 | summer | TOPAZ_2_SOLAR | UNIT_TESTING | 0
2023 | summer | TORTLA_1_SOLAR | TRANSMISSION_INDUCED | 0
2023 | summer | TOWNSITE_2_MEADDYN | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1903.5
2023 | summer | TOWNSITE_2_MEADDYN | PLANT_MAINTENANCE | 0
2023 | summer | TOWNSITE_2_MEADDYN | PLANT_TROUBLE | 1130
2023 | summer | TOWNSITE_2_MEADDYN | RTU_RIG | 0
2023 | summer | TRNQL8_2_AMASR1 | PLANT_MAINTENANCE | 26.6667
2023 | summer | TRNQL8_2_AZUSR1 | PLANT_TROUBLE | 685.625
2023 | summer | TRNQL8_2_ROJSR1 | PLANT_MAINTENANCE | 295
2023 | summer | TRNQL8_2_ROJSR1 | PLANT_TROUBLE | 599.9167
2023 | summer | TRNQL8_2_VERSR1 | PLANT_MAINTENANCE | 120
2023 | summer | TRNQL8_2_VERSR1 | PLANT_TROUBLE | 15.4
2023 | summer | TRNQLT_2_RETBT1 | PLANT_MAINTENANCE | 214.6
2023 | summer | TRNQLT_2_RETBT1 | PLANT_TROUBLE | 13532.85
2023 | summer | TRNQLT_2_RETBT1 | UNIT_TESTING | 2060.4
2023 | summer | TRNQLT_2_SOLAR | PLANT_MAINTENANCE | 795.9
2023 | summer | TRNQLT_2_SOLAR | PLANT_TROUBLE | 5205.795
2023 | summer | TRNSWD_1_QF | AMBIENT_DUE_TO_TEMP | 2
2023 | summer | TRNSWD_1_QF | PLANT_TROUBLE | 27591.775
2023 | summer | TULARE_2_TFCBM1 | UNIT_TESTING | 0
2023 | summer | TULEWD_1_TULWD1 | PLANT_MAINTENANCE | 140.1
2023 | summer | TULEWD_1_TULWD1 | TRANSMISSION_INDUCED | 269.7
2023 | summer | TULLCK_7_UNITS | PLANT_TROUBLE | 0
2023 | summer | TUPMAN_1_BIOGAS | PLANT_MAINTENANCE | 3
2023 | summer | TUPMAN_1_BIOGAS | PLANT_TROUBLE | 0.6
2023 | summer | TVYVLY_6_KRSHY1 | AMBIENT_NOT_DUE_TO_TEMP | 994.5
2023 | summer | TX-ELK_6_ECKSR2 | TRANSMISSION_INDUCED | 0
2023 | summer | TX-ELK_6_SOLAR1 | TRANSMISSION_INDUCED | 0
2023 | summer | TXMCKT_6_UNIT | AMBIENT_DUE_TO_TEMP | 23.115
2023 | summer | TXMCKT_6_UNIT | METERING_TELEMETRY | 0
2023 | summer | TXMCKT_6_UNIT | PLANT_MAINTENANCE | 50
2023 | summer | TXMCKT_6_UNIT | PLANT_TROUBLE | 2888.3983
2023 | summer | UKIAH_7_LAKEMN | PLANT_TROUBLE | 0
2023 | summer | UKIAH_7_LAKEMN | TRANSMISSION_INDUCED | 0
2023 | summer | ULTPCH_1_UCSBT1 | TRANSMISSION_INDUCED | 16
2023 | summer | ULTPCH_1_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 52.2
2023 | summer | ULTPCH_1_UNIT 1 | METERING_TELEMETRY | 79.5
2023 | summer | ULTPCH_1_UNIT 1 | PLANT_TROUBLE | 259.5
2023 | summer | ULTPCH_1_UNIT 1 | TRANSITIONAL_LIMITATION | 90
2023 | summer | ULTPCH_1_UNIT 1 | TRANSMISSION_INDUCED | 10.8
2023 | summer | ULTPFR_1_UNIT 1 | PLANT_MAINTENANCE | 3834.5267
2023 | summer | ULTPFR_1_UNIT 1 | PLANT_TROUBLE | 1579.5
2023 | summer | ULTRCK_2_UNIT | ENVIRONMENTAL_RESTRICTIONS | 2.8
2023 | summer | ULTRCK_2_UNIT | PLANT_MAINTENANCE | 366
2023 | summer | ULTRCK_2_UNIT | PLANT_TROUBLE | 2635
2023 | summer | ULTRCK_2_UNIT | UNIT_TESTING | 41.95
2023 | summer | UNCHEM_1_UNIT | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 12885
2023 | summer | UNCHEM_1_UNIT | PLANT_TROUBLE | 1650
2023 | summer | UNVRSY_1_UNIT 1 | PLANT_MAINTENANCE | 433.8333
2023 | summer | UNVRSY_1_UNIT 1 | PLANT_TROUBLE | 1776.5
2023 | summer | USWND2_1_WIND1 | PLANT_TROUBLE | 2453.8048
2023 | summer | USWND2_1_WIND1 | TRANSMISSION_INDUCED | 0
2023 | summer | USWND2_1_WIND2 | PLANT_MAINTENANCE | 2344.363
2023 | summer | USWND2_1_WIND2 | PLANT_TROUBLE | 62.75
2023 | summer | USWND2_1_WIND2 | TRANSMISSION_INDUCED | 14.4095
2023 | summer | USWND2_1_WIND3 | PLANT_MAINTENANCE | 0
2023 | summer | USWND2_1_WIND3 | PLANT_TROUBLE | 4935.9117
2023 | summer | USWND2_1_WIND3 | TRANSMISSION_INDUCED | 16.4
2023 | summer | USWND4_2_UNIT2 | TRANSMISSION_INDUCED | 139.3667
2023 | summer | USWNDR_2_LABWD1 | PLANT_MAINTENANCE | 476.2
2023 | summer | USWNDR_2_SMUD2 | PLANT_MAINTENANCE | 6390
2023 | summer | USWPFK_6_FRICK | PLANT_MAINTENANCE | 0.16667
2023 | summer | USWPFK_6_FRICK | PLANT_TROUBLE | 75
2023 | summer | USWPFK_6_FRICK | TRANSMISSION_INDUCED | 87.8333
2023 | summer | USWPJR_2_UNITS | METERING_TELEMETRY | 193.2
2023 | summer | USWPJR_2_UNITS | PLANT_MAINTENANCE | 3794.565
2023 | summer | USWPJR_2_UNITS | PLANT_TROUBLE | 0
2023 | summer | VACADX_1_UNITA1 | PLANT_MAINTENANCE | 0
2023 | summer | VACADX_1_UNITA1 | PLANT_TROUBLE | 2543.2383
2023 | summer | VALLEY_5_PERRIS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 3392.7
2023 | summer | VALLEY_5_PERRIS | AMBIENT_NOT_DUE_TO_TEMP | 2421.7
2023 | summer | VALLEY_5_PERRIS | PLANT_TROUBLE | 0
2023 | summer | VALTNE_2_AVASR1 | PLANT_TROUBLE | 200
2023 | summer | VALTNE_2_TBBBT1 | UNIT_TESTING | 0
2023 | summer | VALTNE_2_TRSBT1 | UNIT_TESTING | 0
2023 | summer | VEDDER_1_SEKERN | PLANT_TROUBLE | 9539.55
2023 | summer | VEGA_6_SOLAR1 | METERING_TELEMETRY | 0
2023 | summer | VEGA_6_SOLAR1 | PLANT_MAINTENANCE | 40
2023 | summer | VEGA_6_SOLAR1 | PLANT_TROUBLE | 0
2023 | summer | VEGA_6_SOLAR1 | TRANSMISSION_INDUCED | 268.6667
2023 | summer | VENWD_1_WIND3 | PLANT_TROUBLE | 41.1777
2023 | summer | VENWD_1_WIND3 | TRANSMISSION_INDUCED | 400.77
2023 | summer | VERNON_6_GONZL1 | PLANT_TROUBLE | 57.5
2023 | summer | VERNON_6_GONZL2 | OTHER_USE_LIMIT_REACHED | 0
2023 | summer | VERNON_6_GONZL2 | PLANT_TROUBLE | 28.75
2023 | summer | VERNON_6_MALBRG | PLANT_TROUBLE | 139
2023 | summer | VESTAL_2_KERN | AMBIENT_NOT_DUE_TO_TEMP | 6241.5
2023 | summer | VESTAL_2_KERN | PLANT_TROUBLE | 1693.2
2023 | summer | VESTAL_2_RTS042 | TRANSMISSION_INDUCED | 0
2023 | summer | VESTAL_2_SOLAR1 | TRANSMISSION_INDUCED | 0
2023 | summer | VESTAL_2_SOLAR2 | TRANSMISSION_INDUCED | 0
2023 | summer | VESTAL_2_TS5SR1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1796.95
2023 | summer | VESTAL_2_TS5SR1 | METERING_TELEMETRY | 0
2023 | summer | VESTAL_2_TS5SR1 | PLANT_TROUBLE | 3834.9315
2023 | summer | VESTAL_2_TS5SR1 | TRANSMISSION_INDUCED | 0
2023 | summer | VESTAL_2_UNIT1 | TRANSMISSION_INDUCED | 0
2023 | summer | VESTAL_2_WELLHD | AMBIENT_NOT_DUE_TO_TEMP | 2743.6833
2023 | summer | VESTAL_2_WELLHD | PLANT_MAINTENANCE | 58.8
2023 | summer | VESTAL_2_WELLHD | PLANT_TROUBLE | 3722.6833
2023 | summer | VESTAL_2_WELLHD | TRANSMISSION_INDUCED | 0
2023 | summer | VESTAL_6_QF | AMBIENT_NOT_DUE_TO_TEMP | 9141.75
2023 | summer | VICTOR_1_CREST | PLANT_TROUBLE | 24.5167
2023 | summer | VICTOR_1_CREST | TRANSMISSION_INDUCED | 0.7
2023 | summer | VICTOR_1_EXSLRA | METERING_TELEMETRY | 45
2023 | summer | VICTOR_1_EXSLRA | PLANT_TROUBLE | 560.1667
2023 | summer | VICTOR_1_EXSLRA | RTU_RIG | 10.5333
2023 | summer | VICTOR_1_EXSLRA | TRANSMISSION_INDUCED | 0
2023 | summer | VICTOR_1_EXSLRB | METERING_TELEMETRY | 0
2023 | summer | VICTOR_1_EXSLRB | PLANT_TROUBLE | 10.3333
2023 | summer | VICTOR_1_EXSLRB | TRANSMISSION_INDUCED | 0.93333
2023 | summer | VICTOR_1_LVSLR1 | PLANT_TROUBLE | 0
2023 | summer | VICTOR_1_LVSLR1 | TRANSMISSION_INDUCED | 0
2023 | summer | VICTOR_1_LVSLR2 | PLANT_TROUBLE | 0
2023 | summer | VICTOR_1_LVSLR2 | TRANSMISSION_INDUCED | 0
2023 | summer | VICTOR_1_SOLAR1 | PLANT_MAINTENANCE | 35
2023 | summer | VICTOR_1_SOLAR1 | PLANT_TROUBLE | 270.9583
2023 | summer | VICTOR_1_SOLAR1 | TRANSMISSION_INDUCED | 0
2023 | summer | VICTOR_1_SOLAR2 | METERING_TELEMETRY | 0
2023 | summer | VICTOR_1_SOLAR2 | PLANT_TROUBLE | 0
2023 | summer | VICTOR_1_SOLAR2 | TRANSMISSION_INDUCED | 0
2023 | summer | VICTOR_1_SOLAR4 | PLANT_MAINTENANCE | 8
2023 | summer | VICTOR_1_SOLAR4 | PLANT_TROUBLE | 0
2023 | summer | VICTOR_1_VDRYFA | METERING_TELEMETRY | 10
2023 | summer | VICTOR_1_VDRYFA | PLANT_TROUBLE | 565
2023 | summer | VICTOR_1_VDRYFB | METERING_TELEMETRY | 90
2023 | summer | VICTOR_1_VDRYFB | PLANT_TROUBLE | 49.8333
2023 | summer | VILLPK_2_VALLYV | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1886
2023 | summer | VILLPK_2_VALLYV | AMBIENT_NOT_DUE_TO_TEMP | 1250.5
2023 | summer | VILLPK_6_MWDYOR | AMBIENT_DUE_TO_TEMP | 72.76
2023 | summer | VISTA_2_RIALTO | METERING_TELEMETRY | 25
2023 | summer | VISTA_2_RIALTO | PLANT_TROUBLE | 505
2023 | summer | VISTA_2_RTS028 | PLANT_TROUBLE | 612.5
2023 | summer | VISTRA_5_DALBT1 | PLANT_MAINTENANCE | 1291.6667
2023 | summer | VISTRA_5_DALBT1 | PLANT_TROUBLE | 12133.3333
2023 | summer | VISTRA_5_DALBT2 | PLANT_MAINTENANCE | 1291.6667
2023 | summer | VISTRA_5_DALBT2 | PLANT_TROUBLE | 10459.1667
2023 | summer | VISTRA_5_DALBT3 | PLANT_MAINTENANCE | 1473.3333
2023 | summer | VISTRA_5_DALBT3 | PLANT_TROUBLE | 12510.3833
2023 | summer | VISTRA_5_DALBT4 | PLANT_MAINTENANCE | 1291.6667
2023 | summer | VISTRA_5_DALBT4 | PLANT_TROUBLE | 350.65
2023 | summer | VISTRA_5_PLABT1 | PLANT_MAINTENANCE | 100
2023 | summer | VISTRA_5_PLABT1 | PLANT_TROUBLE | 247.6133
2023 | summer | VISTRA_5_PLABT2 | METERING_TELEMETRY | 142.2333
2023 | summer | VISTRA_5_PLABT2 | PLANT_MAINTENANCE | 0
2023 | summer | VISTRA_5_PLABT2 | PLANT_TROUBLE | 133.2
2023 | summer | VISTRA_5_PLABT3 | PLANT_MAINTENANCE | 0
2023 | summer | VISTRA_5_PLABT3 | PLANT_TROUBLE | 22
2023 | summer | VISTRA_5_PLABT4 | PLANT_MAINTENANCE | 0
2023 | summer | VISTRA_5_PLABT4 | PLANT_TROUBLE | 285.46
2023 | summer | VISTRA_5_PLABT4 | UNIT_TESTING | 0
2023 | summer | VLCNTR_6_VCEBT1 | PLANT_TROUBLE | 9497.7667
2023 | summer | VLCNTR_6_VCEBT1 | TRANSMISSION_INDUCED | 164
2023 | summer | VLCNTR_6_VCEBT2 | PLANT_TROUBLE | 11871.4167
2023 | summer | VLCNTR_6_VCEBT2 | TRANSMISSION_INDUCED | 56.5
2023 | summer | VLCNTR_6_VCSLR1 | TRANSMISSION_INDUCED | 27.5
2023 | summer | VLCNTR_6_VCSLR2 | PLANT_TROUBLE | 738.1667
2023 | summer | VLCNTR_6_VCSLR2 | TRANSMISSION_INDUCED | 55
2023 | summer | VOLTA_2_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 5.805
2023 | summer | VOLTA_2_UNIT 1 | METERING_TELEMETRY | 2.295
2023 | summer | VOLTA_2_UNIT 1 | PLANT_TROUBLE | 5784.05
2023 | summer | VOLTA_2_UNIT 2 | AMBIENT_DUE_TO_TEMP | 5
2023 | summer | VOLTA_2_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 5
2023 | summer | VOLTA_2_UNIT 2 | TRANSMISSION_INDUCED | 20
2023 | summer | VOLTA_6_BAILCK | AMBIENT_NOT_DUE_TO_TEMP | 256.5
2023 | summer | VOLTA_6_BAILCK | TRANSMISSION_INDUCED | 1.4175
2023 | summer | VOLTA_6_DIGHYD | PLANT_MAINTENANCE | 0
2023 | summer | VOLTA_6_DIGHYD | PLANT_TROUBLE | 0.6
2023 | summer | VOLTA_6_DIGHYD | TRANSMISSION_INDUCED | 3.75
2023 | summer | VOLTA_7_PONHY1 | AMBIENT_NOT_DUE_TO_TEMP | 618.75
2023 | summer | VOLTA_7_PONHY1 | TRANSMISSION_INDUCED | 1.5625
2023 | summer | VOLTA_7_QFUNTS | TRANSMISSION_INDUCED | 0.1875
2023 | summer | VOYAGR_2_VOAWD5 | PLANT_TROUBLE | 0
2023 | summer | VOYAGR_2_VOYWD1 | PLANT_TROUBLE | 644.55
2023 | summer | VOYAGR_2_VOYWD2 | METERING_TELEMETRY | 63.175
2023 | summer | VOYAGR_2_VOYWD2 | PLANT_MAINTENANCE | 631.75
2023 | summer | VOYAGR_2_VOYWD2 | PLANT_TROUBLE | 42.1167
2023 | summer | VOYAGR_2_VOYWD3 | PLANT_TROUBLE | 0
2023 | summer | VOYAGR_2_VOYWD4 | PLANT_TROUBLE | 972
2023 | summer | VSTAES_6_VESBT1 | PLANT_MAINTENANCE | 0
2023 | summer | VSTAES_6_VESBT1 | PLANT_TROUBLE | 320.6583
2023 | summer | VSTAES_6_VESBT1 | TRANSMISSION_INDUCED | 0
2023 | summer | WADHAM_6_UNIT | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1017.45
2023 | summer | WADHAM_6_UNIT | PLANT_TROUBLE | 3316.887
2023 | summer | WALCRK_2_CTG1 | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | summer | WALCRK_2_CTG1 | TRANSMISSION_INDUCED | 389.28
2023 | summer | WALCRK_2_CTG2 | ENVIRONMENTAL_RESTRICTIONS | 43.6095
2023 | summer | WALCRK_2_CTG2 | PLANT_MAINTENANCE | 0
2023 | summer | WALCRK_2_CTG2 | PLANT_TROUBLE | 1517.8118
2023 | summer | WALCRK_2_CTG2 | TRANSMISSION_INDUCED | 311.7272
2023 | summer | WALCRK_2_CTG3 | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | summer | WALCRK_2_CTG3 | PLANT_MAINTENANCE | 0
2023 | summer | WALCRK_2_CTG3 | TRANSMISSION_INDUCED | 310.8908
2023 | summer | WALCRK_2_CTG4 | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | summer | WALCRK_2_CTG4 | PLANT_MAINTENANCE | 8702.05
2023 | summer | WALCRK_2_CTG4 | PLANT_TROUBLE | 650.1
2023 | summer | WALCRK_2_CTG4 | TRANSMISSION_INDUCED | 310.73
2023 | summer | WALCRK_2_CTG5 | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | summer | WALCRK_2_CTG5 | PLANT_TROUBLE | 314.4658
2023 | summer | WALCRK_2_CTG5 | TRANSMISSION_INDUCED | 338.275
2023 | summer | WALNUT_6_HILLGEN | PLANT_TROUBLE | 170.7667
2023 | summer | WALNUT_7_WCOVST | PLANT_TROUBLE | 175.5
2023 | summer | WARNE_2_UNIT | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1057.6667
2023 | summer | WARNE_2_UNIT | PLANT_MAINTENANCE | 380
2023 | summer | WARNE_2_UNIT | PLANT_TROUBLE | 167.2
2023 | summer | WDLEAF_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 350
2023 | summer | WDLEAF_7_UNIT 1 | PLANT_TROUBLE | 167
2023 | summer | WEBER_6_FORWRD | PLANT_TROUBLE | 133
2023 | summer | WESCAN_2_BDSBT1 | METERING_TELEMETRY | 2368
2023 | summer | WESCAN_2_BDSBT1 | PLANT_MAINTENANCE | 95.4667
2023 | summer | WESCAN_2_BDSBT1 | PLANT_TROUBLE | 6623.5667
2023 | summer | WESCAN_2_BDSBT1 | TRANSMISSION_INDUCED | 2534.0633
2023 | summer | WESTPT_2_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 89.9167
2023 | summer | WESTPT_2_UNIT | PLANT_TROUBLE | 65.5667
2023 | summer | WESTPT_2_UNIT | TRANSMISSION_INDUCED | 462
2023 | summer | WFRESN_1_SOLAR | METERING_TELEMETRY | 109
2023 | summer | WFRESN_1_SOLAR | PLANT_TROUBLE | 576
2023 | summer | WHEATL_6_LNDFIL | PLANT_MAINTENANCE | 84.0033
2023 | summer | WHEATL_6_LNDFIL | PLANT_TROUBLE | 0.86333
2023 | summer | WHITEH_2_MEADDYN1 | PLANT_TROUBLE | 3443.5587
2023 | summer | WHITEH_2_MEADDYN2 | PLANT_TROUBLE | 2275
2023 | summer | WHITNY_6_SOLAR | PLANT_TROUBLE | 76.6667
2023 | summer | WHITNY_6_SOLAR | TRANSMISSION_INDUCED | 68.3333
2023 | summer | WHTWTR_1_WINDA1 | PLANT_MAINTENANCE | 2927.5
2023 | summer | WHTWTR_1_WINDA1 | PLANT_TROUBLE | 5204.025
2023 | summer | WILLMS_6_ARBBM1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | summer | WILLMS_6_ARBBM1 | PLANT_MAINTENANCE | 224.95
2023 | summer | WILLMS_6_ARBBM1 | PLANT_TROUBLE | 467.6
2023 | summer | WISE_1_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 588.22
2023 | summer | WISE_1_UNIT 1 | PLANT_TROUBLE | 88.66
2023 | summer | WISE_1_UNIT 1 | TRANSMISSION_INDUCED | 69.05
2023 | summer | WISE_1_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 2448
2023 | summer | WISHON_6_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 2577.7667
2023 | summer | WISHON_6_UNITS | PLANT_MAINTENANCE | 5369.2
2023 | summer | WISHON_6_UNITS | PLANT_TROUBLE | 158.64
2023 | summer | WISTER_2_WISSR1 | PLANT_MAINTENANCE | 0
2023 | summer | WISTER_2_WISSR1 | PLANT_TROUBLE | 8332
2023 | summer | WISTRA_2_WRSSR1 | PLANT_MAINTENANCE | 300
2023 | summer | WISTRA_2_WRSSR1 | PLANT_TROUBLE | 0
2023 | summer | WISTRA_2_WRSSR1 | TRANSMISSION_INDUCED | 183.3333
2023 | summer | WLDWD_1_SOLAR2 | PLANT_TROUBLE | 242.5
2023 | summer | WNDMAS_2_UNIT 1 | PLANT_MAINTENANCE | 291.5167
2023 | summer | WNDMAS_2_UNIT 1 | PLANT_TROUBLE | 39.1833
2023 | summer | WNDSTR_2_WIND | PLANT_TROUBLE | 1551
2023 | summer | WOLFSK_1_UNITA1 | AMBIENT_DUE_TO_TEMP | 366.4453
2023 | summer | WOLFSK_1_UNITA1 | PLANT_TROUBLE | 54.6668
2023 | summer | WOLFSK_1_UNITA1 | TRANSMISSION_INDUCED | 88.4353
2023 | summer | WRGTSR_2_WSFSR1 | PLANT_TROUBLE | 7925.269
2023 | summer | WSENGY_1_UNIT 1 | PLANT_MAINTENANCE | 1408
2023 | summer | WSENGY_1_UNIT 1 | PLANT_TROUBLE | 2984.5333
2023 | summer | WSNR_2_CVPDYN | PLANT_TROUBLE | 21.1667
2023 | summer | WSTWND_2_M89BT2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2023 | summer | WSTWND_2_M89BT2 | METERING_TELEMETRY | 353
2023 | summer | WSTWND_2_M89BT2 | PLANT_MAINTENANCE | 75.0667
2023 | summer | WSTWND_2_M89BT2 | PLANT_TROUBLE | 976.8567
2023 | summer | WSTWND_2_M89BT2 | UNIT_TESTING | 0
2023 | summer | WSTWND_2_M89WD1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 35126.25
2023 | summer | WSTWND_2_M89WD2 | PLANT_TROUBLE | 3052.5
2023 | summer | WSTWND_2_M89WD2 | TRANSMISSION_INDUCED | 0
2023 | summer | WSTWND_2_M90WD2 | PLANT_TROUBLE | 0
2023 | summer | WSTWND_2_M90WD2 | TRANSMISSION_INDUCED | 0
2023 | summer | WSTWND_2_SBSBT1 | PLANT_TROUBLE | 830.6667
2023 | summer | YELPIN_2_YP2BT1 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | summer | YELPIN_2_YP2BT1 | PLANT_TROUBLE | 2724.6933
2023 | summer | YELPIN_2_YP2BT1 | UNIT_TESTING | 325
2023 | summer | YELPIN_2_YP2SR1 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | summer | YELPIN_2_YP2SR1 | PLANT_TROUBLE | 1462.5
2023 | summer | YELPIN_2_YP2SR1 | UNIT_TESTING | 725
2023 | summer | YUBACT_1_SUNSWT | PLANT_MAINTENANCE | 199.88
2023 | summer | YUBACT_1_SUNSWT | PLANT_TROUBLE | 3532.879
2023 | summer | YUBACT_1_SUNSWT | UNIT_TESTING | 0
2023 | summer | YUBACT_6_UNITA1 | AMBIENT_DUE_TO_TEMP | 218.632
2023 | summer | YUBACT_6_UNITA1 | PLANT_TROUBLE | 368.634
2023 | summer | ZOND_6_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 13081.5
2023 | nonsummer | 7STDRD_1_SOLAR1 | METERING_TELEMETRY | 3.6667
2023 | nonsummer | 7STDRD_1_SOLAR1 | PLANT_TROUBLE | 80
2023 | nonsummer | 7STDRD_1_SOLAR1 | TRANSMISSION_INDUCED | 387.3333
2023 | nonsummer | ACACIA_6_SOLAR | METERING_TELEMETRY | 0
2023 | nonsummer | ACACIA_6_SOLAR | PLANT_MAINTENANCE | 137
2023 | nonsummer | ACACIA_6_SOLAR | PLANT_TROUBLE | 0
2023 | nonsummer | ACACIA_6_SOLAR | TRANSMISSION_INDUCED | 0
2023 | nonsummer | ADERA_1_SOLAR1 | METERING_TELEMETRY | 584.6667
2023 | nonsummer | ADERA_1_SOLAR1 | PLANT_TROUBLE | 445.025
2023 | nonsummer | ADERA_1_SOLAR1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | ADLIN_1_UNITS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 2215.79
2023 | nonsummer | ADLIN_1_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 9273.0667
2023 | nonsummer | ADLIN_1_UNITS | PLANT_TROUBLE | 418.0295
2023 | nonsummer | ADMEST_6_SOLAR | PLANT_MAINTENANCE | 161.8833
2023 | nonsummer | ADMEST_6_SOLAR | PLANT_TROUBLE | 2770.8847
2023 | nonsummer | ADMEST_6_SOLAR | TRANSMISSION_INDUCED | 0
2023 | nonsummer | ADOBEE_1_SOLAR | METERING_TELEMETRY | 224
2023 | nonsummer | ADOBEE_1_SOLAR | PLANT_TROUBLE | 20.72
2023 | nonsummer | AGCANA_X_HOOVER | RIMS_OUTAGE | 6200
2023 | nonsummer | AGRICO_6_PL3N5 | AMBIENT_DUE_TO_TEMP | 37.74
2023 | nonsummer | AGRICO_6_PL3N5 | PLANT_MAINTENANCE | 340.35
2023 | nonsummer | AGRICO_6_PL3N5 | PLANT_TROUBLE | 26.0935
2023 | nonsummer | AGRICO_6_PL3N5 | TRANSMISSION_INDUCED | 34.035
2023 | nonsummer | AGRICO_6_PL3N5 | UNIT_TESTING | 0
2023 | nonsummer | AGRICO_7_UNIT | AMBIENT_DUE_TO_TEMP | 39.97
2023 | nonsummer | AGRICO_7_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | AGRICO_7_UNIT | ANNUAL_USE_LIMIT_REACHED | 0
2023 | nonsummer | AGRICO_7_UNIT | PLANT_MAINTENANCE | 0
2023 | nonsummer | AGRICO_7_UNIT | PLANT_TROUBLE | 0
2023 | nonsummer | AGRICO_7_UNIT | TRANSMISSION_INDUCED | 97.8267
2023 | nonsummer | AGRICO_7_UNIT | UNIT_TESTING | 0
2023 | nonsummer | AGUCAL_5_SOLAR1 | METERING_TELEMETRY | 1450
2023 | nonsummer | AGUCAL_5_SOLAR1 | PLANT_MAINTENANCE | 1000.25
2023 | nonsummer | AGUCAL_5_SOLAR1 | PLANT_TROUBLE | 0
2023 | nonsummer | AGUCAL_5_SOLAR1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | AKINGS_6_AMESR1 | METERING_TELEMETRY | 0
2023 | nonsummer | AKINGS_6_AMESR1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | AKINGS_6_AMESR1 | PLANT_TROUBLE | 1479.1583
2023 | nonsummer | ALAMIT_2_PL1X3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2023 | nonsummer | ALAMIT_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 409.5
2023 | nonsummer | ALAMIT_2_PL1X3 | PLANT_MAINTENANCE | 33935.85
2023 | nonsummer | ALAMIT_2_PL1X3 | PLANT_TROUBLE | 6752.8135
2023 | nonsummer | ALAMIT_2_PL1X3 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2023 | nonsummer | ALAMIT_2_PL1X3 | TRANSMISSION_INDUCED | 8771.1
2023 | nonsummer | ALAMIT_2_PL1X3 | UNIT_TESTING | 0
2023 | nonsummer | ALAMIT_7_ES1 | METERING_TELEMETRY | 186.75
2023 | nonsummer | ALAMIT_7_ES1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | ALAMIT_7_ES1 | PLANT_TROUBLE | 19738.5125
2023 | nonsummer | ALAMIT_7_ES1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | ALAMIT_7_ES1 | UNIT_TESTING | 177.2067
2023 | nonsummer | ALAMIT_7_UNIT 3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2023 | nonsummer | ALAMIT_7_UNIT 3 | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | ALAMIT_7_UNIT 3 | PLANT_MAINTENANCE | 1759.058
2023 | nonsummer | ALAMIT_7_UNIT 3 | PLANT_TROUBLE | 31299.01
2023 | nonsummer | ALAMIT_7_UNIT 3 | UNIT_SUPPORTING_STARTUP | 0
2023 | nonsummer | ALAMIT_7_UNIT 3 | UNIT_TESTING | 0
2023 | nonsummer | ALAMIT_7_UNIT 4 | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | ALAMIT_7_UNIT 4 | PLANT_MAINTENANCE | 65213.85
2023 | nonsummer | ALAMIT_7_UNIT 4 | PLANT_TROUBLE | 26533.4768
2023 | nonsummer | ALAMIT_7_UNIT 4 | TRANSMISSION_INDUCED | 1365.5892
2023 | nonsummer | ALAMIT_7_UNIT 4 | UNIT_SUPPORTING_STARTUP | 0
2023 | nonsummer | ALAMIT_7_UNIT 4 | UNIT_TESTING | 0
2023 | nonsummer | ALAMIT_7_UNIT 5 | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | ALAMIT_7_UNIT 5 | PLANT_TROUBLE | 14400
2023 | nonsummer | ALAMIT_7_UNIT 5 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | ALAMIT_7_UNIT 5 | UNIT_TESTING | 0
2023 | nonsummer | ALAMO_6_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | ALAMO_6_UNIT | PLANT_TROUBLE | 0
2023 | nonsummer | ALAMO_6_UNIT | TRANSMISSION_INDUCED | 0
2023 | nonsummer | ALAMO_6_UNIT | UNIT_TESTING | 51
2023 | nonsummer | ALHMBR_1_ALHSLR | PLANT_MAINTENANCE | 0
2023 | nonsummer | ALHMBR_1_ALHSLR | PLANT_TROUBLE | 0
2023 | nonsummer | ALLGNY_6_HYDRO1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | ALMASL_2_AL6BT6 | PLANT_MAINTENANCE | 2065.85
2023 | nonsummer | ALMASL_2_AL6BT6 | PLANT_TROUBLE | 192
2023 | nonsummer | ALMASL_2_AL6BT6 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 250
2023 | nonsummer | ALMASL_2_GS1SR1 | PLANT_MAINTENANCE | 1125
2023 | nonsummer | ALMASL_2_GS1SR1 | PLANT_TROUBLE | 156.25
2023 | nonsummer | ALMASL_2_GS4SR4 | PLANT_TROUBLE | 3.3333
2023 | nonsummer | ALMASL_2_GS6SR6 | PLANT_MAINTENANCE | 425
2023 | nonsummer | ALMASL_2_GS6SR6 | PLANT_TROUBLE | 195
2023 | nonsummer | ALMASL_2_GS7SR7 | PLANT_TROUBLE | 191.4
2023 | nonsummer | ALMEGT_1_UNIT 1 | AMBIENT_DUE_TO_TEMP | 1024
2023 | nonsummer | ALMEGT_1_UNIT 1 | METERING_TELEMETRY | 148.6
2023 | nonsummer | ALMEGT_1_UNIT 1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | ALMEGT_1_UNIT 1 | PLANT_TROUBLE | 0
2023 | nonsummer | ALMEGT_1_UNIT 2 | AMBIENT_DUE_TO_TEMP | 1024
2023 | nonsummer | ALMEGT_1_UNIT 2 | METERING_TELEMETRY | 148.6
2023 | nonsummer | ALMEGT_1_UNIT 2 | PLANT_MAINTENANCE | 0
2023 | nonsummer | ALMEGT_1_UNIT 2 | PLANT_TROUBLE | 0
2023 | nonsummer | ALPSLR_1_NTHSLR | PLANT_MAINTENANCE | 202.8333
2023 | nonsummer | ALPSLR_1_NTHSLR | PLANT_TROUBLE | 6416.6367
2023 | nonsummer | ALPSLR_1_NTHSLR | TRANSMISSION_INDUCED | 152.6667
2023 | nonsummer | ALPSLR_1_NTHSLR | UNIT_TESTING | 0
2023 | nonsummer | ALPSLR_1_SPSSLR | PLANT_MAINTENANCE | 734.8833
2023 | nonsummer | ALPSLR_1_SPSSLR | PLANT_TROUBLE | 10293.24
2023 | nonsummer | ALPSLR_1_SPSSLR | TRANSMISSION_INDUCED | 422.5
2023 | nonsummer | ALT6DN_2_WIND7 | METERING_TELEMETRY | 48
2023 | nonsummer | ALT6DN_2_WIND7 | TRANSMISSION_INDUCED | 72
2023 | nonsummer | ALT6DS_2_WIND9 | TRANSMISSION_INDUCED | 135
2023 | nonsummer | ALTA3A_2_CPCE4 | METERING_TELEMETRY | 0
2023 | nonsummer | ALTA3A_2_CPCE4 | PLANT_MAINTENANCE | 0
2023 | nonsummer | ALTA3A_2_CPCE4 | PLANT_TROUBLE | 4866.5
2023 | nonsummer | ALTA3A_2_CPCE5 | METERING_TELEMETRY | 0
2023 | nonsummer | ALTA3A_2_CPCE5 | PLANT_TROUBLE | 5762.0333
2023 | nonsummer | ALTA3A_2_CPCE8 | AMBIENT_NOT_DUE_TO_TEMP | 393
2023 | nonsummer | ALTA3A_2_CPCE8 | METERING_TELEMETRY | 6
2023 | nonsummer | ALTA3A_2_CPCE8 | PLANT_TROUBLE | 12331.9
2023 | nonsummer | ALTA4A_2_CPCW1 | METERING_TELEMETRY | 67.5
2023 | nonsummer | ALTA4A_2_CPCW1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | ALTA4A_2_CPCW1 | PLANT_TROUBLE | 2641.575
2023 | nonsummer | ALTA4B_2_CPCW2 | METERING_TELEMETRY | 335.4
2023 | nonsummer | ALTA4B_2_CPCW2 | PLANT_MAINTENANCE | 0
2023 | nonsummer | ALTA4B_2_CPCW2 | PLANT_TROUBLE | 6228.75
2023 | nonsummer | ALTA4B_2_CPCW3 | PLANT_TROUBLE | 8255.4
2023 | nonsummer | ALTA4B_2_CPCW6 | PLANT_TROUBLE | 840
2023 | nonsummer | ALTA6B_2_WIND11 | METERING_TELEMETRY | 84
2023 | nonsummer | ALTA6B_2_WIND11 | PLANT_MAINTENANCE | 228.0083
2023 | nonsummer | ALTA6B_2_WIND11 | PLANT_TROUBLE | 1947.216
2023 | nonsummer | ALTA6E_2_WIND10 | METERING_TELEMETRY | 71.25
2023 | nonsummer | ALTA6E_2_WIND10 | PLANT_MAINTENANCE | 0
2023 | nonsummer | ALTA6E_2_WIND10 | PLANT_TROUBLE | 7549.869
2023 | nonsummer | ALTWD_2_AT3WD3 | PLANT_TROUBLE | 0
2023 | nonsummer | ALTWD_2_AT3WD3 | TRANSMISSION_INDUCED | 51
2023 | nonsummer | ALTWD_2_COAWD1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | ALTWD_2_COAWD1 | PLANT_TROUBLE | 12531.9
2023 | nonsummer | ALTWD_2_COAWD1 | TRANSMISSION_INDUCED | 5.88
2023 | nonsummer | ANAHM_2_CANYN1 | PLANT_MAINTENANCE | 98.42
2023 | nonsummer | ANAHM_2_CANYN1 | PLANT_TROUBLE | 24354.8492
2023 | nonsummer | ANAHM_2_CANYN1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | ANAHM_2_CANYN2 | PLANT_MAINTENANCE | 144.12
2023 | nonsummer | ANAHM_2_CANYN2 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | ANAHM_2_CANYN2 | UNIT_TESTING | 0
2023 | nonsummer | ANAHM_2_CANYN3 | PLANT_TROUBLE | 2789.4
2023 | nonsummer | ANAHM_2_CANYN3 | TRANSMISSION_INDUCED | 996.51
2023 | nonsummer | ANAHM_2_CANYN3 | UNIT_TESTING | 0
2023 | nonsummer | ANAHM_2_CANYN4 | PLANT_TROUBLE | 1766.7
2023 | nonsummer | ANAHM_2_CANYN4 | TRANSMISSION_INDUCED | 51.5667
2023 | nonsummer | ANAHM_2_CANYN4 | UNIT_TESTING | 0
2023 | nonsummer | ANZA_6_SOLAR1 | PLANT_TROUBLE | 0
2023 | nonsummer | ANZA_6_SOLAR1 | TRANSITIONAL_LIMITATION | 0
2023 | nonsummer | ANZA_6_SOLAR1 | TRANSMISSION_INDUCED | 6690
2023 | nonsummer | APLHIL_1_SFKHY1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | APLHIL_1_SFKHY1 | PLANT_TROUBLE | 243.88
2023 | nonsummer | APLHIL_1_SFKHY1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | AQUAWS_2_AQWSR1 | METERING_TELEMETRY | 1500
2023 | nonsummer | AQUAWS_2_AQWSR1 | PLANT_MAINTENANCE | 8391.6667
2023 | nonsummer | AQUAWS_2_AQWSR1 | PLANT_TROUBLE | 3090.6667
2023 | nonsummer | ARBWD_6_QF | AMBIENT_DUE_TO_TEMP | 129.125
2023 | nonsummer | ARBWD_6_QF | METERING_TELEMETRY | 218.3125
2023 | nonsummer | ARBWD_6_QF | PLANT_MAINTENANCE | 0
2023 | nonsummer | ARBWD_6_QF | PLANT_TROUBLE | 1259.7525
2023 | nonsummer | ARBWD_6_QF | TRANSMISSION_INDUCED | 0
2023 | nonsummer | ARCOGN_2_UNITS | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | ARCOGN_2_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 2890
2023 | nonsummer | ARCOGN_2_UNITS | METERING_TELEMETRY | 0
2023 | nonsummer | ARCOGN_2_UNITS | PLANT_MAINTENANCE | 17810.25
2023 | nonsummer | ARCOGN_2_UNITS | PLANT_TROUBLE | 17431.25
2023 | nonsummer | ARKANS_1_ARKSLR | METERING_TELEMETRY | 712
2023 | nonsummer | ARKANS_1_ARKSLR | PLANT_MAINTENANCE | 175
2023 | nonsummer | ARKANS_1_ARKSLR | PLANT_TROUBLE | 0
2023 | nonsummer | ARKANS_1_ARKSLR | TRANSMISSION_INDUCED | 150
2023 | nonsummer | ARLNTN_2_AR1SR1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | ARLNTN_2_AR1SR1 | PLANT_TROUBLE | 92
2023 | nonsummer | ARLNTN_2_AR1SR1 | UNIT_TESTING | 0
2023 | nonsummer | ARLNTN_2_ASUSR1 | METERING_TELEMETRY | 18
2023 | nonsummer | ARLNTN_2_ASUSR1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | ARLNTN_2_ASUSR1 | PLANT_TROUBLE | 2231.0233
2023 | nonsummer | ARLVAL_5_SOLAR | TRANSMISSION_INDUCED | 0
2023 | nonsummer | ARVINN_6_ORION1 | PLANT_MAINTENANCE | 96
2023 | nonsummer | ARVINN_6_ORION1 | TRANSMISSION_INDUCED | 1200
2023 | nonsummer | ARVINN_6_ORION2 | TRANSMISSION_INDUCED | 824
2023 | nonsummer | ASTORA_2_SOLAR1 | METERING_TELEMETRY | 295
2023 | nonsummer | ASTORA_2_SOLAR1 | PLANT_MAINTENANCE | 1809.6298
2023 | nonsummer | ASTORA_2_SOLAR1 | PLANT_TROUBLE | 1179.6667
2023 | nonsummer | ASTORA_2_SOLAR1 | TRANSMISSION_INDUCED | 198.3333
2023 | nonsummer | ASTORA_2_SOLAR2 | METERING_TELEMETRY | 181.25
2023 | nonsummer | ASTORA_2_SOLAR2 | PLANT_MAINTENANCE | 955.6
2023 | nonsummer | ASTORA_2_SOLAR2 | PLANT_TROUBLE | 330.75
2023 | nonsummer | ATHOS_5_AP1X2 | PLANT_MAINTENANCE | 3410.3833
2023 | nonsummer | ATHOS_5_AP1X2 | PLANT_TROUBLE | 4983.0133
2023 | nonsummer | ATHOS_5_AP1X2 | TRANSMISSION_INDUCED | 910.0333
2023 | nonsummer | ATHOS_5_AP2X2 | METERING_TELEMETRY | 0
2023 | nonsummer | ATHOS_5_AP2X2 | PLANT_MAINTENANCE | 1653.1
2023 | nonsummer | ATHOS_5_AP2X2 | PLANT_TROUBLE | 393.3333
2023 | nonsummer | ATHOS_5_AP2X2 | TRANSMISSION_INDUCED | 810
2023 | nonsummer | ATWEL2_1_SOLAR1 | PLANT_TROUBLE | 0
2023 | nonsummer | ATWEL2_1_SOLAR1 | TRANSMISSION_INDUCED | 100
2023 | nonsummer | ATWELL_1_SOLAR | AMBIENT_NOT_DUE_TO_TEMP | 100
2023 | nonsummer | ATWELL_1_SOLAR | PLANT_MAINTENANCE | 0
2023 | nonsummer | ATWELL_1_SOLAR | TRANSMISSION_INDUCED | 962.3333
2023 | nonsummer | AVENAL_6_AVPARK | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | AVENAL_6_AVPARK | METERING_TELEMETRY | 0
2023 | nonsummer | AVENAL_6_AVPARK | PLANT_TROUBLE | 0
2023 | nonsummer | AVENAL_6_AVPARK | TRANSMISSION_INDUCED | 0
2023 | nonsummer | AVENAL_6_AVSLR1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | AVENAL_6_AVSLR1 | METERING_TELEMETRY | 0
2023 | nonsummer | AVENAL_6_AVSLR1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | AVENAL_6_AVSLR1 | PLANT_TROUBLE | 0
2023 | nonsummer | AVENAL_6_AVSLR1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | AVENAL_6_AVSLR2 | METERING_TELEMETRY | 0
2023 | nonsummer | AVENAL_6_AVSLR2 | PLANT_TROUBLE | 0
2023 | nonsummer | AVENAL_6_AVSLR2 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | AVENAL_6_SANDDG | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | AVENAL_6_SANDDG | METERING_TELEMETRY | 95
2023 | nonsummer | AVENAL_6_SANDDG | PLANT_TROUBLE | 0
2023 | nonsummer | AVENAL_6_SANDDG | TRANSMISSION_INDUCED | 285
2023 | nonsummer | AVENAL_6_SUNCTY | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | AVENAL_6_SUNCTY | METERING_TELEMETRY | 0
2023 | nonsummer | AVENAL_6_SUNCTY | PLANT_TROUBLE | 0
2023 | nonsummer | AVENAL_6_SUNCTY | TRANSMISSION_INDUCED | 200
2023 | nonsummer | AVSOLR_2_SOLAR | METERING_TELEMETRY | 0
2023 | nonsummer | AVSOLR_2_SOLAR | PLANT_MAINTENANCE | 2755.95
2023 | nonsummer | AVSOLR_2_SOLAR | PLANT_TROUBLE | 207.7
2023 | nonsummer | BALCHS_7_UNIT 1 | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | BALCHS_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 505.8
2023 | nonsummer | BALCHS_7_UNIT 1 | PLANT_TROUBLE | 0
2023 | nonsummer | BALCHS_7_UNIT 1 | TRANSMISSION_INDUCED | 270.7333
2023 | nonsummer | BALCHS_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 2176.05
2023 | nonsummer | BALCHS_7_UNIT 2 | PLANT_MAINTENANCE | 0
2023 | nonsummer | BALCHS_7_UNIT 2 | PLANT_TROUBLE | 0
2023 | nonsummer | BALCHS_7_UNIT 2 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | BALCHS_7_UNIT 3 | AMBIENT_NOT_DUE_TO_TEMP | 1938.54
2023 | nonsummer | BALCHS_7_UNIT 3 | PLANT_MAINTENANCE | 0
2023 | nonsummer | BALCHS_7_UNIT 3 | PLANT_TROUBLE | 661.57
2023 | nonsummer | BALCHS_7_UNIT 3 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | BANKPP_2_NSPIN | METERING_TELEMETRY | 0
2023 | nonsummer | BANKPP_2_NSPIN | PLANT_TROUBLE | 337.5
2023 | nonsummer | BANKPP_2_NSPIN | TRANSMISSION_INDUCED | 0
2023 | nonsummer | BARRE_2_ALASB1 | METERING_TELEMETRY | 0
2023 | nonsummer | BARRE_2_ALASB1 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | BARRE_2_ALASB1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | BARRE_6_PEAKER | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2023 | nonsummer | BARRE_6_PEAKER | AMBIENT_DUE_TO_TEMP | 2299.3433
2023 | nonsummer | BARRE_6_PEAKER | ENVIRONMENTAL_RESTRICTIONS | 215
2023 | nonsummer | BARRE_6_PEAKER | OTHER_USE_LIMIT_REACHED | 0
2023 | nonsummer | BARRE_6_PEAKER | PLANT_MAINTENANCE | 72.42
2023 | nonsummer | BARRE_6_PEAKER | PLANT_TROUBLE | 1166.7767
2023 | nonsummer | BARRE_6_PEAKER | SHORT_TERM_USE_LIMIT_REACHED | 95.47
2023 | nonsummer | BASICE_2_UNITS | AMBIENT_DUE_TO_TEMP | 305
2023 | nonsummer | BASICE_2_UNITS | PLANT_TROUBLE | 1720.0333
2023 | nonsummer | BASICE_2_UNITS | TRANSITIONAL_LIMITATION | 226
2023 | nonsummer | BASICE_2_UNITS | TRANSMISSION_INDUCED | 290
2023 | nonsummer | BCTSYS_5_PWXDYN | TRANSITIONAL_LIMITATION | 447260
2023 | nonsummer | BDGRCK_1_UNITS | AMBIENT_DUE_TO_TEMP | 3435.32
2023 | nonsummer | BDGRCK_1_UNITS | PLANT_MAINTENANCE | 0
2023 | nonsummer | BDGRCK_1_UNITS | PLANT_TROUBLE | 319.675
2023 | nonsummer | BDGRCK_1_UNITS | TRANSMISSION_INDUCED | 0
2023 | nonsummer | BDGRCK_1_UNITS | UNIT_TESTING | 0.64
2023 | nonsummer | BEARDS_7_UNIT 1 | PLANT_TROUBLE | 25.7733
2023 | nonsummer | BEARDS_7_UNIT 1 | TRANSMISSION_INDUCED | 71.875
2023 | nonsummer | BEARMT_1_UNIT | AMBIENT_DUE_TO_TEMP | 3821.77
2023 | nonsummer | BEARMT_1_UNIT | PLANT_TROUBLE | 581.3167
2023 | nonsummer | BEARMT_1_UNIT | TRANSMISSION_INDUCED | 0
2023 | nonsummer | BEARMT_1_UNIT | UNIT_TESTING | 9.68
2023 | nonsummer | BEJNLS_5_BV2SCEDYN | AMBIENT_DUE_TO_TEMP | 1395
2023 | nonsummer | BEJNLS_5_BV2SCEDYN | ENVIRONMENTAL_RESTRICTIONS | 585
2023 | nonsummer | BEJNLS_5_BV2SCEDYN | PLANT_TROUBLE | 3045
2023 | nonsummer | BEJNLS_5_BV2SCEDYN | TRANSITIONAL_LIMITATION | 558
2023 | nonsummer | BEJNLS_5_BV2SCEDYN | TRANSMISSION_INDUCED | 7681.4333
2023 | nonsummer | BEKWJS_5_BV1SCEDYN | AMBIENT_DUE_TO_TEMP | 1075
2023 | nonsummer | BEKWJS_5_BV1SCEDYN | PLANT_TROUBLE | 312
2023 | nonsummer | BEKWJS_5_BV1SCEDYN | TRANSITIONAL_LIMITATION | 405
2023 | nonsummer | BEKWJS_5_BV1SCEDYN | TRANSMISSION_INDUCED | 7989.4667
2023 | nonsummer | BELDEN_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 4253.8447
2023 | nonsummer | BELDEN_7_UNIT 1 | PLANT_TROUBLE | 36295
2023 | nonsummer | BELDEN_7_UNIT 1 | TRANSMISSION_INDUCED | 3.9667
2023 | nonsummer | BGSKYN_2_AS2SR1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | BGSKYN_2_AS2SR1 | PLANT_TROUBLE | 4030.6
2023 | nonsummer | BGSKYN_2_ASPSR2 | ICCP | 305
2023 | nonsummer | BGSKYN_2_ASPSR2 | PLANT_MAINTENANCE | 80.85
2023 | nonsummer | BGSKYN_2_ASPSR2 | PLANT_TROUBLE | 11668.5667
2023 | nonsummer | BGSKYN_2_ASPSR2 | UNIT_TESTING | 0
2023 | nonsummer | BGSKYN_2_ASSR1B | PLANT_MAINTENANCE | 0
2023 | nonsummer | BGSKYN_2_ASSR1B | PLANT_TROUBLE | 26.9167
2023 | nonsummer | BGSKYN_2_ASSR3A | PLANT_MAINTENANCE | 0
2023 | nonsummer | BGSKYN_2_ASSR3A | PLANT_TROUBLE | 272.5
2023 | nonsummer | BGSKYN_2_ASSR3A | UNIT_TESTING | 0
2023 | nonsummer | BGSKYN_2_ASSR3B | PLANT_MAINTENANCE | 0
2023 | nonsummer | BGSKYN_2_ASSR3B | PLANT_TROUBLE | 272.45
2023 | nonsummer | BGSKYN_2_ASSR3B | UNIT_TESTING | 0
2023 | nonsummer | BGSKYN_2_BS3SR3 | PLANT_MAINTENANCE | 0
2023 | nonsummer | BGSKYN_2_BS3SR3 | PLANT_TROUBLE | 13049.8333
2023 | nonsummer | BIGCRK_2_EXESWD | AMBIENT_NOT_DUE_TO_TEMP | 218446.5283
2023 | nonsummer | BIGCRK_2_EXESWD | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | nonsummer | BIGCRK_2_EXESWD | METERING_TELEMETRY | 629.8733
2023 | nonsummer | BIGCRK_2_EXESWD | PLANT_MAINTENANCE | 11835.9933
2023 | nonsummer | BIGCRK_2_EXESWD | PLANT_TROUBLE | 11663.55
2023 | nonsummer | BIGCRK_2_EXESWD | TRANSMISSION_INDUCED | 28011.9333
2023 | nonsummer | BIGSKY_2_AS2BT1 | ICCP | 844.55
2023 | nonsummer | BIGSKY_2_AS2BT1 | METERING_TELEMETRY | 0
2023 | nonsummer | BIGSKY_2_AS2BT1 | PLANT_MAINTENANCE | 251.8833
2023 | nonsummer | BIGSKY_2_AS2BT1 | PLANT_TROUBLE | 3977.9167
2023 | nonsummer | BIGSKY_2_ASLBT2 | PLANT_MAINTENANCE | 0
2023 | nonsummer | BIGSKY_2_ASLBT2 | PLANT_TROUBLE | 2047.5
2023 | nonsummer | BIGSKY_2_BSKSR6 | PLANT_TROUBLE | 585.4417
2023 | nonsummer | BIGSKY_2_BSKSR7 | PLANT_MAINTENANCE | 58.3667
2023 | nonsummer | BIGSKY_2_BSKSR7 | PLANT_TROUBLE | 409.5833
2023 | nonsummer | BIGSKY_2_BSKSR7 | TRANSMISSION_INDUCED | 270
2023 | nonsummer | BIGSKY_2_BSKSR8 | PLANT_MAINTENANCE | 0
2023 | nonsummer | BIGSKY_2_BSKSR8 | PLANT_TROUBLE | 518.6667
2023 | nonsummer | BIGSKY_2_SOLAR1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | BIGSKY_2_SOLAR1 | PLANT_TROUBLE | 3004.55
2023 | nonsummer | BIGSKY_2_SOLAR2 | PLANT_MAINTENANCE | 0
2023 | nonsummer | BIGSKY_2_SOLAR2 | PLANT_TROUBLE | 858.5417
2023 | nonsummer | BIGSKY_2_SOLAR3 | PLANT_TROUBLE | 205.1333
2023 | nonsummer | BIGSKY_2_SOLAR4 | PLANT_MAINTENANCE | 0
2023 | nonsummer | BIGSKY_2_SOLAR4 | PLANT_TROUBLE | 233.2333
2023 | nonsummer | BIGSKY_2_SOLAR5 | PLANT_TROUBLE | 22.5
2023 | nonsummer | BIGSKY_2_SOLAR6 | PLANT_MAINTENANCE | 254.25
2023 | nonsummer | BIGSKY_2_SOLAR6 | PLANT_TROUBLE | 2221.9833
2023 | nonsummer | BIGSKY_2_SOLAR7 | PLANT_MAINTENANCE | 96
2023 | nonsummer | BIGSKY_2_SOLAR7 | PLANT_TROUBLE | 1641.8
2023 | nonsummer | BIOMAS_1_UNIT 1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2023 | nonsummer | BIOMAS_1_UNIT 1 | PLANT_MAINTENANCE | 637.5
2023 | nonsummer | BIOMAS_1_UNIT 1 | PLANT_TROUBLE | 2340.475
2023 | nonsummer | BISHOP_1_ALAMO | AMBIENT_NOT_DUE_TO_TEMP | 8332.18
2023 | nonsummer | BISHOP_1_ALAMO | METERING_TELEMETRY | 0
2023 | nonsummer | BISHOP_1_ALAMO | PLANT_MAINTENANCE | 11.65
2023 | nonsummer | BISHOP_1_ALAMO | PLANT_TROUBLE | 143
2023 | nonsummer | BISHOP_1_ALAMO | TRANSMISSION_INDUCED | 62.0067
2023 | nonsummer | BISHOP_1_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 7122.855
2023 | nonsummer | BISHOP_1_UNITS | METERING_TELEMETRY | 0
2023 | nonsummer | BISHOP_1_UNITS | PLANT_MAINTENANCE | 0
2023 | nonsummer | BISHOP_1_UNITS | PLANT_TROUBLE | 1694.3
2023 | nonsummer | BISHOP_1_UNITS | TRANSMISSION_INDUCED | 42.1583
2023 | nonsummer | BKRFLD_2_SOLAR1 | METERING_TELEMETRY | 1.38
2023 | nonsummer | BKRFLD_2_SOLAR1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | BKRFLD_2_SOLAR1 | PLANT_TROUBLE | 66.286
2023 | nonsummer | BKRFLD_2_SOLAR1 | TRANSMISSION_INDUCED | 55.2
2023 | nonsummer | BLACK_7_UNIT 1 | AMBIENT_DUE_TO_TEMP | 115
2023 | nonsummer | BLACK_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 3887.5
2023 | nonsummer | BLACK_7_UNIT 1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | BLACK_7_UNIT 1 | PLANT_TROUBLE | 3836.8333
2023 | nonsummer | BLACK_7_UNIT 1 | TRANSMISSION_INDUCED | 2905.4083
2023 | nonsummer | BLACK_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 3394.3167
2023 | nonsummer | BLACK_7_UNIT 2 | PLANT_TROUBLE | 0
2023 | nonsummer | BLACK_7_UNIT 2 | TRANSMISSION_INDUCED | 1677.4517
2023 | nonsummer | BLAST_1_WIND | PLANT_MAINTENANCE | 0
2023 | nonsummer | BLAST_1_WIND | PLANT_TROUBLE | 0
2023 | nonsummer | BLAST_1_WIND | TRANSMISSION_INDUCED | 1143.08
2023 | nonsummer | BLCKBT_2_STONEY | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 806
2023 | nonsummer | BLCKBT_2_STONEY | AMBIENT_NOT_DUE_TO_TEMP | 62
2023 | nonsummer | BLCKBT_2_STONEY | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | nonsummer | BLCKBT_2_STONEY | PLANT_TROUBLE | 38.8533
2023 | nonsummer | BLCKBT_2_STONEY | TRANSMISSION_INDUCED | 124
2023 | nonsummer | BLCKWL_6_SOLAR1 | METERING_TELEMETRY | 216
2023 | nonsummer | BLCKWL_6_SOLAR1 | PLANT_TROUBLE | 132
2023 | nonsummer | BLCKWL_6_SOLAR1 | TRANSMISSION_INDUCED | 510
2023 | nonsummer | BLKCRK_2_GMCBT1 | METERING_TELEMETRY | 0
2023 | nonsummer | BLKCRK_2_GMCBT1 | PLANT_MAINTENANCE | 624.5333
2023 | nonsummer | BLKCRK_2_GMCBT1 | PLANT_TROUBLE | 22048.9745
2023 | nonsummer | BLKCRK_2_GMCBT1 | UNIT_TESTING | 645
2023 | nonsummer | BLKCRK_2_SOLAR1 | METERING_TELEMETRY | 0
2023 | nonsummer | BLKCRK_2_SOLAR1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | BLKCRK_2_SOLAR1 | PLANT_TROUBLE | 0
2023 | nonsummer | BLKDIA_2_BDEBT1 | METERING_TELEMETRY | 0
2023 | nonsummer | BLKDIA_2_BDEBT1 | PLANT_MAINTENANCE | 606.7667
2023 | nonsummer | BLKDIA_2_BDEBT1 | PLANT_TROUBLE | 970.35
2023 | nonsummer | BLKDIA_2_BDEBT1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | BLKDIA_2_BDEBT1 | UNIT_TESTING | 0
2023 | nonsummer | BLM W_2_COSBT1 | METERING_TELEMETRY | 0
2023 | nonsummer | BLM W_2_COSBT1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | BLM W_2_COSBT1 | PLANT_TROUBLE | 5273.9038
2023 | nonsummer | BLM W_2_COSBT1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | BLM_2_UNITS | PLANT_TROUBLE | 14126.3333
2023 | nonsummer | BLM_2_UNITS | TRANSMISSION_INDUCED | 360
2023 | nonsummer | BLYTHE_1_SOLAR1 | METERING_TELEMETRY | 0
2023 | nonsummer | BLYTHE_1_SOLAR1 | PLANT_TROUBLE | 515.675
2023 | nonsummer | BLYTHE_1_SOLAR1 | TRANSMISSION_INDUCED | 205
2023 | nonsummer | BLYTHE_1_SOLAR2 | PLANT_TROUBLE | 982.5
2023 | nonsummer | BNNIEN_7_ALTAPH | AMBIENT_DUE_TO_TEMP | 75
2023 | nonsummer | BNNIEN_7_ALTAPH | AMBIENT_NOT_DUE_TO_TEMP | 114.85
2023 | nonsummer | BNNIEN_7_ALTAPH | RTU_RIG | 0
2023 | nonsummer | BNNIEN_7_ALTAPH | TRANSMISSION_INDUCED | 182.2833
2023 | nonsummer | BOGUE_1_UNITA1 | AMBIENT_DUE_TO_TEMP | 27.133
2023 | nonsummer | BOGUE_1_UNITA1 | PLANT_TROUBLE | 0
2023 | nonsummer | BOGUE_1_UNITA1 | UNIT_TESTING | 100.626
2023 | nonsummer | BORDER_6_UNITA1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 256.25
2023 | nonsummer | BORDER_6_UNITA1 | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | BORDER_6_UNITA1 | PLANT_MAINTENANCE | 785.8333
2023 | nonsummer | BORDER_6_UNITA1 | PLANT_TROUBLE | 495.3125
2023 | nonsummer | BORDER_6_UNITA1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | BORDER_6_UNITA1 | UNIT_TESTING | 0
2023 | nonsummer | BOWMN_6_HYDRO | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | BOWMN_6_HYDRO | PLANT_TROUBLE | 19.14
2023 | nonsummer | BOWMN_6_HYDRO | TRANSMISSION_INDUCED | 0
2023 | nonsummer | BRDSLD_2_HIWIND | METERING_TELEMETRY | 0
2023 | nonsummer | BRDSLD_2_HIWIND | PLANT_MAINTENANCE | 54901.93
2023 | nonsummer | BRDSLD_2_HIWIND | PLANT_TROUBLE | 423
2023 | nonsummer | BRDSLD_2_MTZUM2 | METERING_TELEMETRY | 164.9933
2023 | nonsummer | BRDSLD_2_MTZUM2 | PLANT_MAINTENANCE | 4132.525
2023 | nonsummer | BRDSLD_2_MTZUM2 | PLANT_TROUBLE | 0
2023 | nonsummer | BRDSLD_2_MTZUMA | METERING_TELEMETRY | 324.4133
2023 | nonsummer | BRDSLD_2_MTZUMA | PLANT_MAINTENANCE | 1256.1
2023 | nonsummer | BRDSLD_2_MTZUMA | PLANT_TROUBLE | 0
2023 | nonsummer | BRDSLD_2_SHILO1 | PLANT_TROUBLE | 121.7667
2023 | nonsummer | BRDSLD_2_SHILO2 | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | BRDSLD_2_SHILO2 | METERING_TELEMETRY | 0
2023 | nonsummer | BRDSLD_2_SHILO2 | PLANT_MAINTENANCE | 3757.1
2023 | nonsummer | BRDSLD_2_SHILO2 | PLANT_TROUBLE | 0
2023 | nonsummer | BRDSLD_2_SHLO3A | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | BRDSLD_2_SHLO3A | METERING_TELEMETRY | 20.5
2023 | nonsummer | BRDSLD_2_SHLO3A | PLANT_MAINTENANCE | 3507.705
2023 | nonsummer | BRDSLD_2_SHLO3A | PLANT_TROUBLE | 0
2023 | nonsummer | BRDSLD_2_SHLO3B | PLANT_MAINTENANCE | 1296.1383
2023 | nonsummer | BREGGO_6_DEGRSL | PLANT_TROUBLE | 31.5
2023 | nonsummer | BREGGO_6_DEGRSL | TRANSMISSION_INDUCED | 157.5
2023 | nonsummer | BREGGO_6_SOLAR | PLANT_MAINTENANCE | 0
2023 | nonsummer | BREGGO_6_SOLAR | PLANT_TROUBLE | 130.5
2023 | nonsummer | BREGGO_6_SOLAR | TRANSMISSION_INDUCED | 2221
2023 | nonsummer | BRODIE_2_WIND | METERING_TELEMETRY | 309.5
2023 | nonsummer | BRODIE_2_WIND | PLANT_MAINTENANCE | 5411.7833
2023 | nonsummer | BRODIE_2_WIND | PLANT_TROUBLE | 390
2023 | nonsummer | BUCKBL_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | BUCKBL_2_PL1X3 | AMBIENT_NOT_DUE_TO_TEMP | 16913.3415
2023 | nonsummer | BUCKBL_2_PL1X3 | PLANT_TROUBLE | 2011.3175
2023 | nonsummer | BUCKBL_2_PL1X3 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2023 | nonsummer | BUCKBL_2_PL1X3 | TRANSMISSION_INDUCED | 589.52
2023 | nonsummer | BUCKBL_2_PL1X3 | UNIT_TESTING | 2676.3
2023 | nonsummer | BUCKCK_2_HYDRO | TRANSMISSION_INDUCED | 287.1
2023 | nonsummer | BUCKCK_7_OAKFLT | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | BUCKCK_7_OAKFLT | TRANSMISSION_INDUCED | 1371.5
2023 | nonsummer | BUCKCK_7_PL1X2 | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | BUCKCK_7_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 775.2833
2023 | nonsummer | BUCKCK_7_PL1X2 | PLANT_MAINTENANCE | 848.75
2023 | nonsummer | BUCKCK_7_PL1X2 | PLANT_TROUBLE | 0
2023 | nonsummer | BUCKCK_7_PL1X2 | TRANSMISSION_INDUCED | 12786.25
2023 | nonsummer | BUCKWD_1_QF | PLANT_MAINTENANCE | 1119.175
2023 | nonsummer | BUCKWD_1_QF | PLANT_TROUBLE | 0
2023 | nonsummer | BUCKWD_7_WINTCV | AMBIENT_DUE_TO_TEMP | 6.6
2023 | nonsummer | BUCKWD_7_WINTCV | PLANT_TROUBLE | 85.8
2023 | nonsummer | BURNYF_2_UNIT 1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 96.95
2023 | nonsummer | BURNYF_2_UNIT 1 | PLANT_MAINTENANCE | 3.6
2023 | nonsummer | BURNYF_2_UNIT 1 | PLANT_TROUBLE | 4650.2882
2023 | nonsummer | BURNYF_2_UNIT 1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | BUTTVL_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 61.225
2023 | nonsummer | BUTTVL_7_UNIT 1 | PLANT_TROUBLE | 6122.5
2023 | nonsummer | BUTTVL_7_UNIT 1 | TRANSMISSION_INDUCED | 243.5
2023 | nonsummer | CABALO_2_M2BSR1 | METERING_TELEMETRY | 0
2023 | nonsummer | CABALO_2_M2BSR1 | PLANT_MAINTENANCE | 99.1667
2023 | nonsummer | CABALO_2_M2BSR1 | PLANT_TROUBLE | 755.35
2023 | nonsummer | CABALO_2_M2WSR2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2023 | nonsummer | CABALO_2_M2WSR2 | METERING_TELEMETRY | 391
2023 | nonsummer | CABALO_2_M2WSR2 | PLANT_MAINTENANCE | 371.4
2023 | nonsummer | CABALO_2_M2WSR2 | PLANT_TROUBLE | 2648.37
2023 | nonsummer | CABZON_1_WINDA1 | ENVIRONMENTAL_RESTRICTIONS | 78.0167
2023 | nonsummer | CABZON_1_WINDA1 | PLANT_TROUBLE | 143.5
2023 | nonsummer | CABZON_1_WINDA1 | TRANSMISSION_INDUCED | 205
2023 | nonsummer | CALFTN_2_CFSBT1 | METERING_TELEMETRY | 2400
2023 | nonsummer | CALFTN_2_CFSBT1 | PLANT_MAINTENANCE | 315.2
2023 | nonsummer | CALFTN_2_CFSBT1 | PLANT_TROUBLE | 1260
2023 | nonsummer | CALFTN_2_CFSBT1 | UNIT_TESTING | 0
2023 | nonsummer | CALFTN_2_SOLAR | PLANT_MAINTENANCE | 0
2023 | nonsummer | CALFTS_2_CFSSR1 | METERING_TELEMETRY | 0
2023 | nonsummer | CALFTS_2_CFSSR1 | PLANT_TROUBLE | 2056.6333
2023 | nonsummer | CALGEN_1_UNITS | PLANT_TROUBLE | 4450.7333
2023 | nonsummer | CALGEN_1_UNITS | TRANSMISSION_INDUCED | 1820
2023 | nonsummer | CALPIN_1_AGNEW | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 142.8
2023 | nonsummer | CALPIN_1_AGNEW | AMBIENT_DUE_TO_TEMP | 239.848
2023 | nonsummer | CALPIN_1_AGNEW | PLANT_TROUBLE | 2159.416
2023 | nonsummer | CALPIN_1_AGNEW | TRANSITIONAL_LIMITATION | 0
2023 | nonsummer | CALPIN_1_AGNEW | UNIT_TESTING | 34.2
2023 | nonsummer | CALPSS_6_SOLAR1 | PLANT_TROUBLE | 49.5
2023 | nonsummer | CALPSS_6_SOLAR1 | TRANSMISSION_INDUCED | 6547.9
2023 | nonsummer | CAMCHE_1_PL1X3 | AMBIENT_DUE_TO_TEMP | 531.45
2023 | nonsummer | CAMCHE_1_PL1X3 | AMBIENT_NOT_DUE_TO_TEMP | 692.05
2023 | nonsummer | CAMCHE_1_PL1X3 | PLANT_MAINTENANCE | 0
2023 | nonsummer | CAMCHE_1_PL1X3 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | CAMLOT_2_SOLAR1 | PLANT_MAINTENANCE | 268.5
2023 | nonsummer | CAMLOT_2_SOLAR1 | PLANT_TROUBLE | 895
2023 | nonsummer | CAMLOT_2_SOLAR2 | PLANT_MAINTENANCE | 44.75
2023 | nonsummer | CAMLOT_2_SOLAR2 | PLANT_TROUBLE | 0
2023 | nonsummer | CAMLOT_2_SOLAR2 | TRANSMISSION_INDUCED | 225
2023 | nonsummer | CAMPFW_7_FARWST | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1584.4
2023 | nonsummer | CAMPFW_7_FARWST | AMBIENT_NOT_DUE_TO_TEMP | 476
2023 | nonsummer | CAMPFW_7_FARWST | METERING_TELEMETRY | 0
2023 | nonsummer | CAMPFW_7_FARWST | PLANT_TROUBLE | 13.1467
2023 | nonsummer | CAMPFW_7_FARWST | TRANSMISSION_INDUCED | 510
2023 | nonsummer | CAMPFW_7_FARWST | UNIT_TESTING | 0
2023 | nonsummer | CANTUA_1_SOLAR | PLANT_TROUBLE | 11.3333
2023 | nonsummer | CANTUA_1_SOLAR | TRANSMISSION_INDUCED | 50
2023 | nonsummer | CAPWD_1_QF | PLANT_TROUBLE | 17550.25
2023 | nonsummer | CARBOU_7_PL2X3 | AMBIENT_NOT_DUE_TO_TEMP | 3536.81
2023 | nonsummer | CARBOU_7_PL2X3 | PLANT_TROUBLE | 68.8143
2023 | nonsummer | CARBOU_7_PL2X3 | TRANSMISSION_INDUCED | 280.95
2023 | nonsummer | CARBOU_7_PL4X5 | AMBIENT_NOT_DUE_TO_TEMP | 4624.5958
2023 | nonsummer | CARBOU_7_PL4X5 | PLANT_MAINTENANCE | 10339.55
2023 | nonsummer | CARBOU_7_PL4X5 | PLANT_TROUBLE | 70.7667
2023 | nonsummer | CARBOU_7_PL4X5 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | CARBOU_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 140.3
2023 | nonsummer | CARBOU_7_UNIT 1 | METERING_TELEMETRY | 0
2023 | nonsummer | CARBOU_7_UNIT 1 | PLANT_TROUBLE | 4131.2
2023 | nonsummer | CARBOU_7_UNIT 1 | TRANSMISSION_INDUCED | 68.3
2023 | nonsummer | CARLS1_2_CARCT1 | AMBIENT_DUE_TO_TEMP | 263.7
2023 | nonsummer | CARLS1_2_CARCT1 | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | nonsummer | CARLS1_2_CARCT1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | CARLS1_2_CARCT1 | PLANT_TROUBLE | 5541.7
2023 | nonsummer | CARLS1_2_CARCT1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | CARLS2_1_CARCT1 | AMBIENT_DUE_TO_TEMP | 16.5717
2023 | nonsummer | CARLS2_1_CARCT1 | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | nonsummer | CARLS2_1_CARCT1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | CARLS2_1_CARCT1 | PLANT_TROUBLE | 61.5417
2023 | nonsummer | CASCES_6_CESBT1 | NEW_GENERATOR_TEST_ENERGY | 50
2023 | nonsummer | CASCES_6_CESBT1 | PLANT_TROUBLE | 0
2023 | nonsummer | CASCES_6_CESBT1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | CASCES_6_CESBT1 | UNIT_TESTING | 0
2023 | nonsummer | CATLNA_2_SOLAR | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | nonsummer | CATLNA_2_SOLAR | PLANT_TROUBLE | 0
2023 | nonsummer | CATLNA_2_SOLAR2 | PLANT_TROUBLE | 0
2023 | nonsummer | CAVLSR_2_BSOLAR | PLANT_MAINTENANCE | 292
2023 | nonsummer | CAVLSR_2_BSOLAR | PLANT_TROUBLE | 0
2023 | nonsummer | CAVLSR_2_BSOLAR | TRANSMISSION_INDUCED | 0
2023 | nonsummer | CAVLSR_2_RSOLAR | METERING_TELEMETRY | 0
2023 | nonsummer | CAVLSR_2_RSOLAR | PLANT_MAINTENANCE | 1619.2667
2023 | nonsummer | CAVLSR_2_RSOLAR | PLANT_TROUBLE | 153.6167
2023 | nonsummer | CAVLSR_2_RSOLAR | TRANSMISSION_INDUCED | 0
2023 | nonsummer | CAYTNO_2_VASCO | PLANT_MAINTENANCE | 8.9942
2023 | nonsummer | CAYTNO_2_VASCO | PLANT_TROUBLE | 572.0375
2023 | nonsummer | CAYTNO_2_VASCO | TRANSMISSION_INDUCED | 1.72
2023 | nonsummer | CDWR07_2_GEN | PLANT_TROUBLE | 264.225
2023 | nonsummer | CEDRCK_6_UNIT | PLANT_TROUBLE | 0
2023 | nonsummer | CEDRCK_6_UNIT | TRANSMISSION_INDUCED | 4.9
2023 | nonsummer | CEDUCR_2_SOLAR1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | CEDUCR_2_SOLAR2 | PLANT_MAINTENANCE | 55
2023 | nonsummer | CEDUCR_2_SOLAR2 | PLANT_TROUBLE | 0
2023 | nonsummer | CEDUCR_2_SOLAR2 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | CEDUCR_2_SOLAR3 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | CEDUCR_2_SOLAR4 | PLANT_TROUBLE | 0
2023 | nonsummer | CEDUCR_2_SOLAR4 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | CENT40_1_C40SR1 | METERING_TELEMETRY | 40
2023 | nonsummer | CENT40_1_C40SR1 | PLANT_MAINTENANCE | 333.0333
2023 | nonsummer | CENT40_1_C40SR1 | PLANT_TROUBLE | 12110.3117
2023 | nonsummer | CENT40_1_C40SR1 | TRANSITIONAL_LIMITATION | 0
2023 | nonsummer | CENT40_1_C40SR1 | TRANSMISSION_INDUCED | 3135.075
2023 | nonsummer | CENTER_2_RHONDO | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 582.55
2023 | nonsummer | CENTER_2_RHONDO | AMBIENT_NOT_DUE_TO_TEMP | 1340
2023 | nonsummer | CENTER_2_RHONDO | PLANT_TROUBLE | 0
2023 | nonsummer | CENTER_6_PEAKER | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 2744.9767
2023 | nonsummer | CENTER_6_PEAKER | AMBIENT_DUE_TO_TEMP | 241.72
2023 | nonsummer | CENTER_6_PEAKER | AMBIENT_NOT_DUE_TO_TEMP | 1655.5
2023 | nonsummer | CENTER_6_PEAKER | PLANT_MAINTENANCE | 236.5
2023 | nonsummer | CENTER_6_PEAKER | PLANT_TROUBLE | 0
2023 | nonsummer | CENTPD_2_BMSSX2 | METERING_TELEMETRY | 3354
2023 | nonsummer | CENTPD_2_BMSSX2 | PLANT_MAINTENANCE | 4684.1
2023 | nonsummer | CENTPD_2_BMSSX2 | PLANT_TROUBLE | 1405.5
2023 | nonsummer | CENTPD_2_BMSSX2 | TRANSMISSION_INDUCED | 5590
2023 | nonsummer | CENTPD_2_BMSSX2 | UNIT_TESTING | 894.4
2023 | nonsummer | CENTPD_2_BMSX2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2023 | nonsummer | CENTPD_2_BMSX2 | METERING_TELEMETRY | 185
2023 | nonsummer | CENTPD_2_BMSX2 | PLANT_MAINTENANCE | 184
2023 | nonsummer | CENTPD_2_BMSX2 | PLANT_TROUBLE | 14136.8333
2023 | nonsummer | CENTPD_2_BMSX2 | TRANSMISSION_INDUCED | 2800
2023 | nonsummer | CENTPD_2_BMSX2 | UNIT_TESTING | 560
2023 | nonsummer | CENTRY_6_PL1X4 | PLANT_MAINTENANCE | 1128.15
2023 | nonsummer | CENTRY_6_PL1X4 | PLANT_TROUBLE | 2039.5
2023 | nonsummer | CENTRY_6_PL1X4 | UNIT_TESTING | 4.2
2023 | nonsummer | CHALK_1_UNIT | AMBIENT_DUE_TO_TEMP | 3522.265
2023 | nonsummer | CHALK_1_UNIT | PLANT_TROUBLE | 0
2023 | nonsummer | CHALK_1_UNIT | TRANSMISSION_INDUCED | 2125.8
2023 | nonsummer | CHALK_1_UNIT | UNIT_TESTING | 22.68
2023 | nonsummer | CHARMN_2_PGONG1 | PLANT_MAINTENANCE | 1241.2127
2023 | nonsummer | CHARMN_2_PGONG1 | PLANT_TROUBLE | 1788.3
2023 | nonsummer | CHESTN_2_CHWBX2 | PLANT_MAINTENANCE | 0
2023 | nonsummer | CHESTN_2_CHWBX2 | PLANT_TROUBLE | 985.5
2023 | nonsummer | CHESTN_2_CHWBX2 | UNIT_TESTING | 0
2023 | nonsummer | CHESTN_2_CHWSX2 | PLANT_MAINTENANCE | 0
2023 | nonsummer | CHESTN_2_CHWSX2 | PLANT_TROUBLE | 0
2023 | nonsummer | CHESTN_2_CHWSX2 | UNIT_TESTING | 0
2023 | nonsummer | CHEVCD_6_UNIT | TRANSMISSION_INDUCED | 0
2023 | nonsummer | CHEVCO_6_UNIT 1 | PLANT_TROUBLE | 32.5
2023 | nonsummer | CHEVCY_1_UNIT | PLANT_TROUBLE | 0
2023 | nonsummer | CHEVCY_1_UNIT | TRANSMISSION_INDUCED | 169.29
2023 | nonsummer | CHEVMN_2_UNITS | PLANT_MAINTENANCE | 15796.055
2023 | nonsummer | CHICPK_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 15036.3402
2023 | nonsummer | CHICPK_7_UNIT 1 | METERING_TELEMETRY | 32
2023 | nonsummer | CHICPK_7_UNIT 1 | PLANT_TROUBLE | 624
2023 | nonsummer | CHICPK_7_UNIT 1 | TRANSMISSION_INDUCED | 988
2023 | nonsummer | CHILLS_1_SYCENG | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | nonsummer | CHILLS_1_SYCENG | PLANT_MAINTENANCE | 261.5
2023 | nonsummer | CHILLS_1_SYCENG | PLANT_TROUBLE | 166.2675
2023 | nonsummer | CHILLS_1_SYCENG | TRANSMISSION_INDUCED | 0
2023 | nonsummer | CHILLS_7_UNITA1 | PLANT_MAINTENANCE | 215.7375
2023 | nonsummer | CHILLS_7_UNITA1 | PLANT_TROUBLE | 2.625
2023 | nonsummer | CHILLS_7_UNITA1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | CHINO_2_APEBT1 | METERING_TELEMETRY | 0
2023 | nonsummer | CHINO_2_APEBT1 | PLANT_MAINTENANCE | 405.3333
2023 | nonsummer | CHINO_2_APEBT1 | PLANT_TROUBLE | 605.99
2023 | nonsummer | CHINO_2_PESBT1 | PLANT_MAINTENANCE | 80
2023 | nonsummer | CHINO_2_PESBT1 | PLANT_TROUBLE | 2221.25
2023 | nonsummer | CHINO_2_PESBT1 | UNIT_TESTING | 16.3333
2023 | nonsummer | CHINO_2_SOLAR | PLANT_TROUBLE | 305
2023 | nonsummer | CHINO_6_CIMGEN | TRANSMISSION_INDUCED | 0
2023 | nonsummer | CHWCHL_1_BIOMAS | PLANT_MAINTENANCE | 0
2023 | nonsummer | CHWCHL_1_BIOMAS | PLANT_TROUBLE | 4874.76
2023 | nonsummer | CHWCHL_1_UNIT | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | CHWCHL_1_UNIT | PLANT_MAINTENANCE | 72
2023 | nonsummer | CHWCHL_1_UNIT | PLANT_TROUBLE | 1007.5
2023 | nonsummer | CHWCHL_1_UNIT | TRANSMISSION_INDUCED | 2430
2023 | nonsummer | CLINESCO_3_PVDYN | AMBIENT_DUE_TO_TEMP | 799.4
2023 | nonsummer | CLINESCO_3_PVDYN | PLANT_MAINTENANCE | 0
2023 | nonsummer | CLINESCO_3_PVDYN | PLANT_TROUBLE | 0
2023 | nonsummer | CLINESCO_3_PVDYN | TRANSITIONAL_LIMITATION | 485.46
2023 | nonsummer | CLINESCO_3_PVDYN | TRANSMISSION_INDUCED | 17589.8747
2023 | nonsummer | CLINESCO_3_WBDYN | AMBIENT_DUE_TO_TEMP | 1442.8
2023 | nonsummer | CLINESCO_3_WBDYN | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | nonsummer | CLINESCO_3_WBDYN | PLANT_TROUBLE | 0
2023 | nonsummer | CLINESCO_3_WBDYN | TRANSITIONAL_LIMITATION | 1037.52
2023 | nonsummer | CLINESCO_3_WBDYN | TRANSMISSION_INDUCED | 20153.2867
2023 | nonsummer | CLOVDL_1_SOLAR | METERING_TELEMETRY | 225
2023 | nonsummer | CLOVDL_1_SOLAR | PLANT_TROUBLE | 761.5
2023 | nonsummer | CLOVER_2_UNIT | PLANT_MAINTENANCE | 32.67
2023 | nonsummer | CLOVER_2_UNIT | PLANT_TROUBLE | 0.7425
2023 | nonsummer | CLOVER_2_UNIT | TRANSMISSION_INDUCED | 95.4195
2023 | nonsummer | CMBLND_2_DS2BT1 | METERING_TELEMETRY | 0
2023 | nonsummer | CMBLND_2_DS2BT1 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | CMBLND_2_DS2BT1 | PLANT_TROUBLE | 1008.85
2023 | nonsummer | CMBLND_2_DS2BT1 | UNIT_TESTING | 0
2023 | nonsummer | CMBLND_2_DS2BT2 | AMBIENT_NOT_DUE_TO_TEMP | 14
2023 | nonsummer | CMBLND_2_DS2BT2 | UNIT_TESTING | 2145
2023 | nonsummer | CMBLND_2_DS2BT3 | METERING_TELEMETRY | 0
2023 | nonsummer | CMBLND_2_DS2BT3 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | CMBLND_2_DS2BT3 | PLANT_TROUBLE | 30
2023 | nonsummer | CMBLND_2_DS2SR1 | METERING_TELEMETRY | 263
2023 | nonsummer | CMBLND_2_DS2SR1 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | CMBLND_2_DS2SR1 | PLANT_TROUBLE | 0
2023 | nonsummer | CMBLND_2_DS2SR1 | UNIT_TESTING | 2583
2023 | nonsummer | CMBLND_2_DS2SR2 | METERING_TELEMETRY | 0
2023 | nonsummer | CMBLND_2_DS2SR3 | METERING_TELEMETRY | 0
2023 | nonsummer | CMBLND_2_DS2SR3 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | CMBLND_2_DS2SR3 | UNIT_TESTING | 0
2023 | nonsummer | CNTNLA_2_SOLAR2 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | COCOPP_2_CTG1 | AMBIENT_DUE_TO_TEMP | 3336.91
2023 | nonsummer | COCOPP_2_CTG1 | PLANT_MAINTENANCE | 5555.8867
2023 | nonsummer | COCOPP_2_CTG1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | COCOPP_2_CTG2 | AMBIENT_DUE_TO_TEMP | 2135.65
2023 | nonsummer | COCOPP_2_CTG2 | AMBIENT_DUE_TO_TEMP | 676.68
2023 | nonsummer | COCOPP_2_CTG2 | PLANT_MAINTENANCE | 11145.29
2023 | nonsummer | COCOPP_2_CTG2 | PLANT_TROUBLE | 0
2023 | nonsummer | COCOPP_2_CTG2 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | COCOPP_2_CTG3 | AMBIENT_DUE_TO_TEMP | 10228.8767
2023 | nonsummer | COCOPP_2_CTG3 | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | nonsummer | COCOPP_2_CTG3 | PLANT_MAINTENANCE | 4645.8773
2023 | nonsummer | COCOPP_2_CTG3 | PLANT_TROUBLE | 0
2023 | nonsummer | COCOPP_2_CTG4 | AMBIENT_DUE_TO_TEMP | 4919.6332
2023 | nonsummer | COCOPP_2_CTG4 | PLANT_MAINTENANCE | 2778.344
2023 | nonsummer | COCOPP_2_CTG4 | PLANT_TROUBLE | 935.8975
2023 | nonsummer | COCOSB_6_SOLAR | TRANSMISSION_INDUCED | 1.5
2023 | nonsummer | COGNAT_1_UNIT | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1340.85
2023 | nonsummer | COGNAT_1_UNIT | PLANT_MAINTENANCE | 1309
2023 | nonsummer | COGNAT_1_UNIT | PLANT_TROUBLE | 1113.7
2023 | nonsummer | COGNAT_1_UNIT | TRANSMISSION_INDUCED | 450
2023 | nonsummer | COLEMN_2_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 345.6383
2023 | nonsummer | COLEMN_2_UNIT | PLANT_MAINTENANCE | 0
2023 | nonsummer | COLEMN_2_UNIT | PLANT_TROUBLE | 585
2023 | nonsummer | COLEMN_2_UNIT | TRANSMISSION_INDUCED | 0
2023 | nonsummer | COLGAT_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 14325.7033
2023 | nonsummer | COLGAT_7_UNIT 1 | ENVIRONMENTAL_RESTRICTIONS | 4989.1
2023 | nonsummer | COLGAT_7_UNIT 1 | METERING_TELEMETRY | 0
2023 | nonsummer | COLGAT_7_UNIT 1 | PLANT_MAINTENANCE | 1246
2023 | nonsummer | COLGAT_7_UNIT 1 | PLANT_TROUBLE | 0
2023 | nonsummer | COLGAT_7_UNIT 1 | TRANSMISSION_INDUCED | 1620
2023 | nonsummer | COLGAT_7_UNIT 1 | UNIT_TESTING | 0
2023 | nonsummer | COLGAT_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 15066.6167
2023 | nonsummer | COLGAT_7_UNIT 2 | ENVIRONMENTAL_RESTRICTIONS | 4995.1
2023 | nonsummer | COLGAT_7_UNIT 2 | PLANT_MAINTENANCE | 790
2023 | nonsummer | COLGAT_7_UNIT 2 | PLANT_TROUBLE | 790
2023 | nonsummer | COLGAT_7_UNIT 2 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | COLGAT_7_UNIT 2 | UNIT_TESTING | 0
2023 | nonsummer | COLGNS_2_CNSSR1 | PLANT_MAINTENANCE | 1888.5533
2023 | nonsummer | COLGNS_2_CNSSR1 | PLANT_TROUBLE | 7100
2023 | nonsummer | COLGNS_2_CNSSR1 | TRANSMISSION_INDUCED | 1308.8
2023 | nonsummer | COLPIN_6_COLLNS | PLANT_MAINTENANCE | 16.5
2023 | nonsummer | COLPIN_6_COLLNS | PLANT_TROUBLE | 2359.5
2023 | nonsummer | COLPIN_6_COLLNS | TRANSMISSION_INDUCED | 1.43
2023 | nonsummer | COLTON_6_AGUAM1 | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | nonsummer | COLTON_6_AGUAM1 | PLANT_TROUBLE | 0
2023 | nonsummer | COLUSA_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 15947.1455
2023 | nonsummer | COLUSA_2_PL1X3 | PLANT_TROUBLE | 4784.0533
2023 | nonsummer | COLUSA_2_PL1X3 | UNIT_TESTING | 238.8445
2023 | nonsummer | COLVIL_7_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 141.305
2023 | nonsummer | COLVIL_7_PL1X2 | METERING_TELEMETRY | 0
2023 | nonsummer | COLVIL_7_PL1X2 | PLANT_MAINTENANCE | 0
2023 | nonsummer | COLVIL_7_PL1X2 | PLANT_TROUBLE | 1140.886
2023 | nonsummer | COLVIL_7_PL1X2 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | CONTRL_1_CASAD1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | CONTRL_1_CASAD1 | PLANT_TROUBLE | 40.9333
2023 | nonsummer | CONTRL_1_CASAD1 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2023 | nonsummer | CONTRL_1_CASAD1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | CONTRL_1_CASAD2 | AMBIENT_DUE_TO_TEMP | 185.515
2023 | nonsummer | CONTRL_1_CASAD2 | AMBIENT_NOT_DUE_TO_TEMP | 3.9
2023 | nonsummer | CONTRL_1_CASAD2 | METERING_TELEMETRY | 3121.5
2023 | nonsummer | CONTRL_1_CASAD2 | PLANT_MAINTENANCE | 32.5
2023 | nonsummer | CONTRL_1_CASAD2 | PLANT_TROUBLE | 80.5033
2023 | nonsummer | CONTRL_1_CASAD2 | TRANSITIONAL_LIMITATION | 0
2023 | nonsummer | CONTRL_1_CASAD2 | TRANSMISSION_INDUCED | 20.125
2023 | nonsummer | CONTRL_1_CASAD3 | PLANT_TROUBLE | 141.4375
2023 | nonsummer | CONTRL_1_CASAD3 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | CONTRL_1_LUNDY | AMBIENT_NOT_DUE_TO_TEMP | 2213.25
2023 | nonsummer | CONTRL_1_LUNDY | PLANT_TROUBLE | 0
2023 | nonsummer | CONTRL_1_LUNDY | TRANSMISSION_INDUCED | 120.4333
2023 | nonsummer | CONTRL_1_OXBOW | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | CONTRL_1_OXBOW | AMBIENT_NOT_DUE_TO_TEMP | 50
2023 | nonsummer | CONTRL_1_OXBOW | NEW_GENERATOR_TEST_ENERGY | 49
2023 | nonsummer | CONTRL_1_OXBOW | PLANT_MAINTENANCE | 180
2023 | nonsummer | CONTRL_1_OXBOW | PLANT_TROUBLE | 861.8167
2023 | nonsummer | CONTRL_1_OXBOW | TRANSMISSION_INDUCED | 136
2023 | nonsummer | CONTRL_1_OXBOW | UNIT_TESTING | 0
2023 | nonsummer | CONTRL_1_POOLE | AMBIENT_NOT_DUE_TO_TEMP | 8340.565
2023 | nonsummer | CONTRL_1_POOLE | PLANT_TROUBLE | 27
2023 | nonsummer | CONTRL_1_POOLE | RTU_RIG | 0.17
2023 | nonsummer | CONTRL_1_POOLE | TRANSMISSION_INDUCED | 145.9593
2023 | nonsummer | CONTRL_1_QF | TRANSMISSION_INDUCED | 0
2023 | nonsummer | CONTRL_1_RUSHCK | AMBIENT_NOT_DUE_TO_TEMP | 9331.48
2023 | nonsummer | CONTRL_1_RUSHCK | TRANSMISSION_INDUCED | 10.4813
2023 | nonsummer | COPMT2_2_SOLAR2 | PLANT_TROUBLE | 0
2023 | nonsummer | COPMTN_2_SOLAR1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | COPMTN_2_SOLAR1 | PLANT_TROUBLE | 12.8
2023 | nonsummer | CORCAN_1_SOLAR1 | METERING_TELEMETRY | 400
2023 | nonsummer | CORCAN_1_SOLAR1 | PLANT_MAINTENANCE | 40
2023 | nonsummer | CORCAN_1_SOLAR1 | PLANT_TROUBLE | 1171.9067
2023 | nonsummer | CORCAN_1_SOLAR1 | TRANSMISSION_INDUCED | 36
2023 | nonsummer | CORCAN_1_SOLAR2 | PLANT_MAINTENANCE | 0
2023 | nonsummer | CORONS_6_CLRWTR | PLANT_TROUBLE | 0
2023 | nonsummer | CORONS_6_CLRWTR | TRANSMISSION_INDUCED | 0
2023 | nonsummer | CORRAL_6_SJOAQN | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2023 | nonsummer | CORRAL_6_SJOAQN | PLANT_MAINTENANCE | 27.65
2023 | nonsummer | CORRAL_6_SJOAQN | PLANT_TROUBLE | 131.1842
2023 | nonsummer | CORRAL_6_SJOAQN | TRANSMISSION_INDUCED | 134.4467
2023 | nonsummer | COTTLE_2_FRNKNH | TRANSMISSION_INDUCED | 0
2023 | nonsummer | COVERD_2_HCKHY1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 2001.545
2023 | nonsummer | COVERD_2_HCKHY1 | PLANT_TROUBLE | 0
2023 | nonsummer | COVERD_2_HCKHY1 | TRANSMISSION_INDUCED | 13.78
2023 | nonsummer | COVERD_2_MCKHY1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 362
2023 | nonsummer | COVERD_2_MCKHY1 | AMBIENT_NOT_DUE_TO_TEMP | 1332
2023 | nonsummer | COVERD_2_QFUNTS | PLANT_TROUBLE | 0
2023 | nonsummer | COVERD_2_RCKHY1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 320
2023 | nonsummer | COVERD_2_RCKHY1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | COVERD_2_RCKHY1 | PLANT_TROUBLE | 3.8333
2023 | nonsummer | COVERD_2_RCKHY1 | TRANSMISSION_INDUCED | 6.8333
2023 | nonsummer | COWCRK_2_UNIT | PLANT_TROUBLE | 972.2
2023 | nonsummer | COWCRK_2_UNIT | TRANSMISSION_INDUCED | 69.4
2023 | nonsummer | CPVERD_2_SOLAR | PLANT_MAINTENANCE | 1572
2023 | nonsummer | CPVERD_2_SOLAR | PLANT_TROUBLE | 185.1
2023 | nonsummer | CPVERD_2_SOLAR | TRANSMISSION_INDUCED | 168
2023 | nonsummer | CRELMN_6_AABBT1 | PLANT_TROUBLE | 0
2023 | nonsummer | CRELMN_6_AABBT1 | RTU_RIG | 0
2023 | nonsummer | CRELMN_6_RAMON1 | PLANT_TROUBLE | 4
2023 | nonsummer | CRELMN_6_RAMON2 | PLANT_TROUBLE | 10
2023 | nonsummer | CRELMN_6_RAMSR3 | PLANT_TROUBLE | 1468.8
2023 | nonsummer | CRESTA_7_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 3149.3333
2023 | nonsummer | CRESTA_7_PL1X2 | PLANT_MAINTENANCE | 0
2023 | nonsummer | CRESTA_7_PL1X2 | PLANT_TROUBLE | 0
2023 | nonsummer | CRIMSN_2_CRMBT1 | METERING_TELEMETRY | 6340.8167
2023 | nonsummer | CRIMSN_2_CRMBT1 | PLANT_MAINTENANCE | 1538.5833
2023 | nonsummer | CRIMSN_2_CRMBT1 | PLANT_TROUBLE | 23084.1285
2023 | nonsummer | CRIMSN_2_CRMBT1 | UNIT_TESTING | 205
2023 | nonsummer | CRIMSN_2_CRMBT2 | METERING_TELEMETRY | 1335
2023 | nonsummer | CRIMSN_2_CRMBT2 | PLANT_MAINTENANCE | 300
2023 | nonsummer | CRIMSN_2_CRMBT2 | PLANT_TROUBLE | 8095.9553
2023 | nonsummer | CRIMSN_2_CRMBT2 | UNIT_TESTING | 150
2023 | nonsummer | CRNEVL_6_CRNVA | AMBIENT_NOT_DUE_TO_TEMP | 127.935
2023 | nonsummer | CRNEVL_6_CRNVA | PLANT_MAINTENANCE | 0
2023 | nonsummer | CRNEVL_6_CRNVA | PLANT_TROUBLE | 4.5
2023 | nonsummer | CRNEVL_6_CRNVA | TRANSMISSION_INDUCED | 375.72
2023 | nonsummer | CRNEVL_6_SJQN 2 | AMBIENT_NOT_DUE_TO_TEMP | 2726.8267
2023 | nonsummer | CRNEVL_6_SJQN 2 | TRANSMISSION_INDUCED | 278.6133
2023 | nonsummer | CROKET_7_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | CROKET_7_UNIT | PLANT_MAINTENANCE | 0
2023 | nonsummer | CROKET_7_UNIT | PLANT_TROUBLE | 5372
2023 | nonsummer | CROKET_7_UNIT | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2023 | nonsummer | CROKET_7_UNIT | TRANSMISSION_INDUCED | 16112
2023 | nonsummer | CRSTWD_6_KUMYAY | METERING_TELEMETRY | 90
2023 | nonsummer | CRSTWD_6_KUMYAY | PLANT_TROUBLE | 8325.3333
2023 | nonsummer | CRSTWD_6_KUMYAY | TRANSMISSION_INDUCED | 0
2023 | nonsummer | CRWCKS_1_SOLAR1 | METERING_TELEMETRY | 60
2023 | nonsummer | CRWCKS_1_SOLAR1 | PLANT_MAINTENANCE | 80
2023 | nonsummer | CRWCKS_1_SOLAR1 | PLANT_TROUBLE | 535
2023 | nonsummer | CRWCKS_1_SOLAR1 | TRANSMISSION_INDUCED | 219.6667
2023 | nonsummer | CSCCOG_1_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 1785
2023 | nonsummer | CSCCOG_1_UNIT 1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | CSCCOG_1_UNIT 1 | PLANT_TROUBLE | 2859.5
2023 | nonsummer | CSCGNR_1_UNIT 1 | PLANT_MAINTENANCE | 618.75
2023 | nonsummer | CSCGNR_1_UNIT 1 | PLANT_TROUBLE | 123.75
2023 | nonsummer | CSCGNR_1_UNIT 2 | METERING_TELEMETRY | 0
2023 | nonsummer | CSCGNR_1_UNIT 2 | PLANT_MAINTENANCE | 1719.25
2023 | nonsummer | CSCGNR_1_UNIT 2 | PLANT_TROUBLE | 3706.0043
2023 | nonsummer | CSLR4S_2_SOLAR | PLANT_MAINTENANCE | 560
2023 | nonsummer | CSLR4S_2_SOLAR | PLANT_TROUBLE | 0
2023 | nonsummer | CSLR4S_2_SOLAR | TRANSMISSION_INDUCED | 178.4
2023 | nonsummer | CSTRVL_7_PL1X2 | TRANSMISSION_INDUCED | 67.5725
2023 | nonsummer | CSTRVL_7_QFUNTS | TRANSMISSION_INDUCED | 20
2023 | nonsummer | CUMBIA_1_SOLAR | METERING_TELEMETRY | 0
2023 | nonsummer | CUMBIA_1_SOLAR | PLANT_TROUBLE | 806
2023 | nonsummer | CUYAMS_6_CUYSR1 | AMBIENT_NOT_DUE_TO_TEMP | 26.6667
2023 | nonsummer | CUYAMS_6_CUYSR1 | METERING_TELEMETRY | 1252.6667
2023 | nonsummer | CUYAMS_6_CUYSR1 | PLANT_MAINTENANCE | 80
2023 | nonsummer | CUYAMS_6_CUYSR1 | PLANT_TROUBLE | 444.6667
2023 | nonsummer | CUYAMS_6_CUYSR1 | TRANSMISSION_INDUCED | 2347.3333
2023 | nonsummer | DAIRLD_1_CR1BM1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 221.8
2023 | nonsummer | DAIRLD_1_CR1BM1 | PLANT_TROUBLE | 6
2023 | nonsummer | DEADCK_1_UNIT | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 148.8
2023 | nonsummer | DEADCK_1_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 975.25
2023 | nonsummer | DEERCR_6_UNIT 1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1050
2023 | nonsummer | DEERCR_6_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 1467.4
2023 | nonsummer | DEERCR_6_UNIT 1 | PLANT_MAINTENANCE | 35
2023 | nonsummer | DEERCR_6_UNIT 1 | PLANT_TROUBLE | 210
2023 | nonsummer | DEERCR_6_UNIT 1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | DELAMO_2_ALASB2 | METERING_TELEMETRY | 0
2023 | nonsummer | DELAMO_2_ALASB2 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | DELAMO_2_ALASB2 | PLANT_MAINTENANCE | 0
2023 | nonsummer | DELAMO_2_ALASB2 | PLANT_TROUBLE | 200
2023 | nonsummer | DELSUR_6_CREST | PLANT_MAINTENANCE | 9.45
2023 | nonsummer | DELSUR_6_CREST | PLANT_TROUBLE | 261.5333
2023 | nonsummer | DELSUR_6_CREST | TRANSMISSION_INDUCED | 26.7583
2023 | nonsummer | DELSUR_6_DRYFRB | METERING_TELEMETRY | 0
2023 | nonsummer | DELSUR_6_DRYFRB | PLANT_MAINTENANCE | 10
2023 | nonsummer | DELSUR_6_DRYFRB | PLANT_TROUBLE | 419
2023 | nonsummer | DELSUR_6_DRYFRB | TRANSMISSION_INDUCED | 21.25
2023 | nonsummer | DELSUR_6_HORSR1 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2023 | nonsummer | DELSUR_6_SOLAR1 | METERING_TELEMETRY | 30.175
2023 | nonsummer | DELSUR_6_SOLAR1 | PLANT_TROUBLE | 1343.675
2023 | nonsummer | DELSUR_6_SOLAR1 | TRANSMISSION_INDUCED | 26.8667
2023 | nonsummer | DELTA_2_PL1X4 | AMBIENT_DUE_TO_TEMP | 15827.3967
2023 | nonsummer | DELTA_2_PL1X4 | PLANT_MAINTENANCE | 4400
2023 | nonsummer | DELTA_2_PL1X4 | PLANT_TROUBLE | 36289.8602
2023 | nonsummer | DELTA_2_PL1X4 | TRANSITIONAL_LIMITATION | 804.99
2023 | nonsummer | DELTA_2_PL1X4 | UNIT_TESTING | 0
2023 | nonsummer | DEVERS_1_SOLAR | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | nonsummer | DEVERS_1_SOLAR | PLANT_TROUBLE | 0
2023 | nonsummer | DEVERS_1_SOLAR1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | DEVERS_1_SOLAR1 | PLANT_TROUBLE | 0
2023 | nonsummer | DEVERS_1_SOLAR2 | PLANT_TROUBLE | 45
2023 | nonsummer | DEVERS_2_DHSPG2 | METERING_TELEMETRY | 0
2023 | nonsummer | DEVERS_2_DHSPG2 | PLANT_TROUBLE | 14.3967
2023 | nonsummer | DEVERS_2_DHSPG2 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | DEXZEL_1_UNIT | PLANT_MAINTENANCE | 6866.575
2023 | nonsummer | DEXZEL_1_UNIT | PLANT_TROUBLE | 3550.3333
2023 | nonsummer | DEXZEL_1_UNIT | TRANSMISSION_INDUCED | 0
2023 | nonsummer | DIABLO_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 14087
2023 | nonsummer | DIABLO_7_UNIT 1 | METERING_TELEMETRY | 0
2023 | nonsummer | DIABLO_7_UNIT 1 | PLANT_MAINTENANCE | 6301.3333
2023 | nonsummer | DIABLO_7_UNIT 2 | AMBIENT_DUE_TO_TEMP | 5549.6667
2023 | nonsummer | DIABLO_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 10992.8
2023 | nonsummer | DIABLO_7_UNIT 2 | PLANT_TROUBLE | 6800
2023 | nonsummer | DISCOV_1_CHEVRN | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2023 | nonsummer | DISCOV_1_CHEVRN | PLANT_MAINTENANCE | 0
2023 | nonsummer | DISCOV_1_CHEVRN | PLANT_TROUBLE | 3213.5267
2023 | nonsummer | DISCOV_1_CHEVRN | TRANSMISSION_INDUCED | 0
2023 | nonsummer | DONNLS_7_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 2719
2023 | nonsummer | DONNLS_7_UNIT | METERING_TELEMETRY | 0
2023 | nonsummer | DONNLS_7_UNIT | PLANT_TROUBLE | 265.2
2023 | nonsummer | DONNLS_7_UNIT | TRANSMISSION_INDUCED | 417.1833
2023 | nonsummer | DOSMGO_2_NSPIN | TRANSMISSION_INDUCED | 0
2023 | nonsummer | DOUBLC_1_UNITS | AMBIENT_DUE_TO_TEMP | 1931.97
2023 | nonsummer | DOUBLC_1_UNITS | PLANT_MAINTENANCE | 262.3
2023 | nonsummer | DOUBLC_1_UNITS | PLANT_TROUBLE | 5047.85
2023 | nonsummer | DRACKR_2_D4SR4B | PLANT_MAINTENANCE | 50
2023 | nonsummer | DRACKR_2_D4SR4B | PLANT_TROUBLE | 359.7617
2023 | nonsummer | DRACKR_2_DS3SR3 | METERING_TELEMETRY | 0
2023 | nonsummer | DRACKR_2_DS3SR3 | PLANT_MAINTENANCE | 0
2023 | nonsummer | DRACKR_2_DS3SR3 | PLANT_TROUBLE | 363.286
2023 | nonsummer | DRACKR_2_DS3SR3 | UNIT_TESTING | 0
2023 | nonsummer | DRACKR_2_DS4SR4 | METERING_TELEMETRY | 0
2023 | nonsummer | DRACKR_2_DS4SR4 | PLANT_TROUBLE | 399.14
2023 | nonsummer | DRACKR_2_DS4SR4 | RTU_RIG | 0
2023 | nonsummer | DRACKR_2_DSUBT1 | METERING_TELEMETRY | 0
2023 | nonsummer | DRACKR_2_DSUBT1 | PLANT_TROUBLE | 9159.4867
2023 | nonsummer | DRACKR_2_DSUBT2 | METERING_TELEMETRY | 0
2023 | nonsummer | DRACKR_2_DSUBT2 | PLANT_MAINTENANCE | 413.5167
2023 | nonsummer | DRACKR_2_DSUBT2 | PLANT_TROUBLE | 16236.3513
2023 | nonsummer | DRACKR_2_DSUBT2 | UNIT_TESTING | 340
2023 | nonsummer | DRACKR_2_DSUBT3 | METERING_TELEMETRY | 0
2023 | nonsummer | DRACKR_2_DSUBT3 | PLANT_MAINTENANCE | 129.1667
2023 | nonsummer | DRACKR_2_DSUBT3 | PLANT_TROUBLE | 9538.7723
2023 | nonsummer | DRACKR_2_DSUBT3 | UNIT_TESTING | 241.59
2023 | nonsummer | DRACKR_2_DSUBT4 | METERING_TELEMETRY | 0
2023 | nonsummer | DRACKR_2_DSUBT4 | PLANT_TROUBLE | 5841.2552
2023 | nonsummer | DRACKR_2_SOLAR1 | METERING_TELEMETRY | 0
2023 | nonsummer | DRACKR_2_SOLAR1 | PLANT_TROUBLE | 116
2023 | nonsummer | DRACKR_2_SOLAR2 | METERING_TELEMETRY | 0
2023 | nonsummer | DRACKR_2_SOLAR2 | PLANT_MAINTENANCE | 96
2023 | nonsummer | DRACKR_2_SOLAR2 | PLANT_TROUBLE | 456.85
2023 | nonsummer | DRACKR_2_SOLAR2 | UNIT_TESTING | 0
2023 | nonsummer | DREWSR_2_BHSSR1 | METERING_TELEMETRY | 400
2023 | nonsummer | DREWSR_2_BHSSR1 | PLANT_MAINTENANCE | 567.52
2023 | nonsummer | DREWSR_2_BHSSR1 | PLANT_TROUBLE | 963.5183
2023 | nonsummer | DREWSR_2_BHSSR1 | TRANSMISSION_INDUCED | 75
2023 | nonsummer | DREWS_6_PL1X4 | METERING_TELEMETRY | 0
2023 | nonsummer | DREWS_6_PL1X4 | PLANT_MAINTENANCE | 213.75
2023 | nonsummer | DREWS_6_PL1X4 | PLANT_TROUBLE | 3294.9225
2023 | nonsummer | DREWS_6_PL1X4 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | DREWS_6_PL1X4 | UNIT_TESTING | 0
2023 | nonsummer | DRUM_7_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 2317
2023 | nonsummer | DRUM_7_PL1X2 | PLANT_TROUBLE | 2.6
2023 | nonsummer | DRUM_7_PL3X4 | AMBIENT_NOT_DUE_TO_TEMP | 8359.2667
2023 | nonsummer | DRUM_7_PL3X4 | PLANT_MAINTENANCE | 387
2023 | nonsummer | DRUM_7_PL3X4 | PLANT_TROUBLE | 1360.1683
2023 | nonsummer | DRUM_7_UNIT 5 | AMBIENT_NOT_DUE_TO_TEMP | 1779
2023 | nonsummer | DRUM_7_UNIT 5 | PLANT_MAINTENANCE | 0
2023 | nonsummer | DRUM_7_UNIT 5 | PLANT_TROUBLE | 0
2023 | nonsummer | DRUM_7_UNIT 5 | TRANSMISSION_INDUCED | 2400
2023 | nonsummer | DSABLA_7_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 6484.3917
2023 | nonsummer | DSABLA_7_UNIT | PLANT_TROUBLE | 3774
2023 | nonsummer | DSABLA_7_UNIT | TRANSMISSION_INDUCED | 682.9583
2023 | nonsummer | DSFLWR_2_W9CSB1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2023 | nonsummer | DSFLWR_2_W9CSB1 | METERING_TELEMETRY | 0
2023 | nonsummer | DSFLWR_2_W9CSB1 | NEW_GENERATOR_TEST_ENERGY | 1505.5
2023 | nonsummer | DSFLWR_2_W9CSB1 | PLANT_MAINTENANCE | 153
2023 | nonsummer | DSFLWR_2_W9CSB1 | PLANT_TROUBLE | 3502.62
2023 | nonsummer | DSFLWR_2_W9CSB1 | UNIT_TESTING | 2661.4
2023 | nonsummer | DSFLWR_2_W9CSB2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2023 | nonsummer | DSFLWR_2_W9CSB2 | NEW_GENERATOR_TEST_ENERGY | 1062.49
2023 | nonsummer | DSFLWR_2_W9CSB2 | PLANT_MAINTENANCE | 396
2023 | nonsummer | DSFLWR_2_W9CSB2 | PLANT_TROUBLE | 2380.19
2023 | nonsummer | DSFLWR_2_W9CSB2 | UNIT_TESTING | 2095.6
2023 | nonsummer | DSFLWR_2_WS2SR1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | DSFLWR_2_WS2SR1 | PLANT_TROUBLE | 5150.2
2023 | nonsummer | DSRTHV_2_DH1SR1 | METERING_TELEMETRY | 5.75
2023 | nonsummer | DSRTHV_2_DH1SR1 | PLANT_MAINTENANCE | 1.5
2023 | nonsummer | DSRTHV_2_DH1SR1 | PLANT_TROUBLE | 424.1583
2023 | nonsummer | DSRTHV_2_DH2BT1 | PLANT_MAINTENANCE | 105
2023 | nonsummer | DSRTHV_2_DH2BT1 | PLANT_TROUBLE | 17926.3517
2023 | nonsummer | DSRTHV_2_DH2SR2 | PLANT_TROUBLE | 111.4167
2023 | nonsummer | DSRTSL_2_SOLAR1 | METERING_TELEMETRY | 0
2023 | nonsummer | DSRTSL_2_SOLAR1 | PLANT_MAINTENANCE | 3921.3018
2023 | nonsummer | DSRTSL_2_SOLAR1 | PLANT_TROUBLE | 16127.5878
2023 | nonsummer | DSRTSN_2_DS2X2 | METERING_TELEMETRY | 996.6667
2023 | nonsummer | DSRTSN_2_DS2X2 | PLANT_MAINTENANCE | 384
2023 | nonsummer | DSRTSN_2_DS2X2 | PLANT_TROUBLE | 8170.3342
2023 | nonsummer | DSRTSN_2_DS2X2 | UNIT_TESTING | 0
2023 | nonsummer | DSRTSN_2_SOLAR1 | METERING_TELEMETRY | 0
2023 | nonsummer | DSRTSN_2_SOLAR1 | PLANT_MAINTENANCE | 290
2023 | nonsummer | DSRTSN_2_SOLAR1 | PLANT_TROUBLE | 2970.3267
2023 | nonsummer | DTCHWD_2_BT3WND | METERING_TELEMETRY | 0
2023 | nonsummer | DTCHWD_2_BT3WND | PLANT_TROUBLE | 202.5
2023 | nonsummer | DTCHWD_2_BT4WND | METERING_TELEMETRY | 0
2023 | nonsummer | DTCHWD_2_BT4WND | PLANT_TROUBLE | 554.2
2023 | nonsummer | DUANE_1_PL1X3 | AMBIENT_DUE_TO_TEMP | 6962.6667
2023 | nonsummer | DUANE_1_PL1X3 | PLANT_MAINTENANCE | 4097
2023 | nonsummer | DUANE_1_PL1X3 | PLANT_TROUBLE | 5402.5333
2023 | nonsummer | DUANE_1_PL1X3 | UNIT_TESTING | 51.6667
2023 | nonsummer | DURNMESA_3_WBDYN | AMBIENT_DUE_TO_TEMP | 450.8
2023 | nonsummer | DURNMESA_3_WBDYN | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | nonsummer | DURNMESA_3_WBDYN | TRANSITIONAL_LIMITATION | 468.72
2023 | nonsummer | DURNMESA_3_WBDYN | TRANSMISSION_INDUCED | 12178.7453
2023 | nonsummer | DUTCH1_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 1549.17
2023 | nonsummer | DUTCH1_7_UNIT 1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | DUTCH1_7_UNIT 1 | PLANT_TROUBLE | 315
2023 | nonsummer | DUTCH1_7_UNIT 1 | TRANSMISSION_INDUCED | 105
2023 | nonsummer | DUTCH2_7_UNIT 1 | AMBIENT_DUE_TO_TEMP | 84.0667
2023 | nonsummer | DUTCH2_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 10556.5
2023 | nonsummer | DUTCH2_7_UNIT 1 | METERING_TELEMETRY | 6
2023 | nonsummer | DUTCH2_7_UNIT 1 | PLANT_TROUBLE | 327.4667
2023 | nonsummer | DUTCH2_7_UNIT 1 | TRANSMISSION_INDUCED | 130
2023 | nonsummer | DVLCYN_1_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 55.8333
2023 | nonsummer | DVLCYN_1_UNITS | ANNUAL_USE_LIMIT_REACHED | 30.9167
2023 | nonsummer | DVLCYN_1_UNITS | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | nonsummer | DVLCYN_1_UNITS | METERING_TELEMETRY | 0
2023 | nonsummer | DVLCYN_1_UNITS | OTHER_USE_LIMIT_REACHED | 0
2023 | nonsummer | DVLCYN_1_UNITS | PLANT_MAINTENANCE | 2230
2023 | nonsummer | DVLCYN_1_UNITS | PLANT_TROUBLE | 609.0667
2023 | nonsummer | DVLCYN_1_UNITS | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | DVLCYN_1_UNITS | TRANSMISSION_INDUCED | 635.8333
2023 | nonsummer | DYERSM_6_DSWWD1 | ENVIRONMENTAL_RESTRICTIONS | 204.5617
2023 | nonsummer | DYERSM_6_DSWWD1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | DYERSM_6_DSWWD1 | PLANT_TROUBLE | 188.815
2023 | nonsummer | DYERSM_6_DSWWD1 | TRANSMISSION_INDUCED | 1127.4217
2023 | nonsummer | EASTWD_7_UNIT | PLANT_TROUBLE | 0
2023 | nonsummer | EASTWD_7_UNIT | TRANSMISSION_INDUCED | 46600
2023 | nonsummer | EDMONS_2_NSPIN | METERING_TELEMETRY | 0
2023 | nonsummer | EDMONS_2_NSPIN | PLANT_TROUBLE | 52011
2023 | nonsummer | EDWARD_2_E21SB1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1048.5667
2023 | nonsummer | EDWARD_2_E21SB1 | METERING_TELEMETRY | 0
2023 | nonsummer | EDWARD_2_E21SB1 | PLANT_MAINTENANCE | 498
2023 | nonsummer | EDWARD_2_E21SB1 | PLANT_TROUBLE | 3050.9333
2023 | nonsummer | EDWARD_2_E21SB1 | UNIT_TESTING | 0
2023 | nonsummer | EDWARD_2_E23SB1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 308
2023 | nonsummer | EDWARD_2_E23SB1 | PLANT_MAINTENANCE | 72
2023 | nonsummer | EDWARD_2_E23SB1 | PLANT_TROUBLE | 306
2023 | nonsummer | EDWARD_2_E23SB1 | UNIT_TESTING | 0
2023 | nonsummer | EDWARD_2_ES2BT3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1104.8167
2023 | nonsummer | EDWARD_2_ES2BT3 | METERING_TELEMETRY | 0
2023 | nonsummer | EDWARD_2_ES2BT3 | PLANT_MAINTENANCE | 302
2023 | nonsummer | EDWARD_2_ES2BT3 | PLANT_TROUBLE | 2021.1833
2023 | nonsummer | EDWARD_2_ES2BT3 | UNIT_TESTING | 0
2023 | nonsummer | EDWARD_2_ESSSB1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2023 | nonsummer | EDWARD_2_ESSSB1 | METERING_TELEMETRY | 0
2023 | nonsummer | EDWARD_2_ESSSB1 | NEW_GENERATOR_TEST_ENERGY | 8680
2023 | nonsummer | EDWARD_2_ESSSB1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | EDWARD_2_ESSSB1 | PLANT_TROUBLE | 334.4667
2023 | nonsummer | EDWARD_2_ESSSB1 | UNIT_TESTING | 0
2023 | nonsummer | EDWARD_2_ESSSB2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2023 | nonsummer | EDWARD_2_ESSSB2 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | EDWARD_2_ESSSB2 | PLANT_MAINTENANCE | 132
2023 | nonsummer | EDWARD_2_ESSSB2 | PLANT_TROUBLE | 0
2023 | nonsummer | EDWARD_2_ESSSB2 | UNIT_TESTING | 0
2023 | nonsummer | EEKTMN_6_SOLAR1 | METERING_TELEMETRY | 0
2023 | nonsummer | EEKTMN_6_SOLAR1 | PLANT_MAINTENANCE | 60
2023 | nonsummer | EEKTMN_6_SOLAR1 | PLANT_TROUBLE | 270
2023 | nonsummer | EEKTMN_6_SOLAR1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | ELCABO_5_ECWSCEDYN | AMBIENT_DUE_TO_TEMP | 2245
2023 | nonsummer | ELCABO_5_ECWSCEDYN | AMBIENT_NOT_DUE_TO_TEMP | 2633.6833
2023 | nonsummer | ELCABO_5_ECWSCEDYN | METERING_TELEMETRY | 0
2023 | nonsummer | ELCABO_5_ECWSCEDYN | PLANT_MAINTENANCE | 0
2023 | nonsummer | ELCABO_5_ECWSCEDYN | PLANT_TROUBLE | 188.1667
2023 | nonsummer | ELCABO_5_ECWSCEDYN | TRANSITIONAL_LIMITATION | 6452.0333
2023 | nonsummer | ELCABO_5_ECWSCEDYN | TRANSMISSION_INDUCED | 34066.1
2023 | nonsummer | ELCAJN_6_EB1BT1 | PLANT_MAINTENANCE | 142.5
2023 | nonsummer | ELCAJN_6_EB1BT1 | PLANT_MAINTENANCE | 45
2023 | nonsummer | ELCAJN_6_EB1BT1 | PLANT_TROUBLE | 0
2023 | nonsummer | ELCAJN_6_EB1BT1 | PLANT_TROUBLE | 414.625
2023 | nonsummer | ELCAJN_6_EB1BT1 | TRANSMISSION_INDUCED | 225
2023 | nonsummer | ELCAJN_6_LM6K | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 814.275
2023 | nonsummer | ELCAJN_6_LM6K | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | ELCAJN_6_LM6K | PLANT_MAINTENANCE | 0
2023 | nonsummer | ELCAJN_6_LM6K | PLANT_TROUBLE | 0
2023 | nonsummer | ELCAJN_6_LM6K | TRANSMISSION_INDUCED | 0
2023 | nonsummer | ELCAJN_6_LM6K | UNIT_TESTING | 0
2023 | nonsummer | ELCAJN_6_UNITA1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 67.26
2023 | nonsummer | ELCAJN_6_UNITA1 | PLANT_MAINTENANCE | 635.88
2023 | nonsummer | ELCAJN_6_UNITA1 | PLANT_TROUBLE | 204.05
2023 | nonsummer | ELCAJN_6_UNITA1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | ELDORO_7_UNIT 1 | PLANT_MAINTENANCE | 4191
2023 | nonsummer | ELDORO_7_UNIT 1 | PLANT_TROUBLE | 0
2023 | nonsummer | ELDORO_7_UNIT 2 | PLANT_MAINTENANCE | 3960
2023 | nonsummer | ELDORO_7_UNIT 2 | PLANT_TROUBLE | 0
2023 | nonsummer | ELECTR_7_PL1X3 | AMBIENT_NOT_DUE_TO_TEMP | 6465.3567
2023 | nonsummer | ELECTR_7_PL1X3 | PLANT_MAINTENANCE | 8482.1167
2023 | nonsummer | ELECTR_7_PL1X3 | PLANT_TROUBLE | 1677.445
2023 | nonsummer | ELKCRK_6_STONYG | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1328.245
2023 | nonsummer | ELKCRK_6_STONYG | ENVIRONMENTAL_RESTRICTIONS | 90.65
2023 | nonsummer | ELKCRK_6_STONYG | PLANT_TROUBLE | 0.64167
2023 | nonsummer | ELKCRK_6_STONYG | TRANSMISSION_INDUCED | 103.0633
2023 | nonsummer | ELKHIL_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 22282.5
2023 | nonsummer | ELKHIL_2_PL1X3 | PLANT_MAINTENANCE | 6208
2023 | nonsummer | ELKHIL_2_PL1X3 | PLANT_TROUBLE | 14339.4167
2023 | nonsummer | ELKHRN_1_EESX3 | PLANT_MAINTENANCE | 21101.2542
2023 | nonsummer | ELKHRN_1_EESX3 | PLANT_TROUBLE | 15.9
2023 | nonsummer | ELNIDP_6_BIOMAS | METERING_TELEMETRY | 0
2023 | nonsummer | ELNIDP_6_BIOMAS | PLANT_MAINTENANCE | 3935.575
2023 | nonsummer | ELNIDP_6_BIOMAS | PLANT_TROUBLE | 3690.6535
2023 | nonsummer | ELSEGN_2_UN1011 | AMBIENT_DUE_TO_TEMP | 8.15
2023 | nonsummer | ELSEGN_2_UN1011 | PLANT_MAINTENANCE | 0
2023 | nonsummer | ELSEGN_2_UN1011 | PLANT_TROUBLE | 4549.7233
2023 | nonsummer | ELSEGN_2_UN1011 | UNIT_TESTING | 571.4583
2023 | nonsummer | ELSEGN_2_UN2021 | AMBIENT_DUE_TO_TEMP | 1123.1277
2023 | nonsummer | ELSEGN_2_UN2021 | PLANT_MAINTENANCE | 0
2023 | nonsummer | ELSEGN_2_UN2021 | PLANT_TROUBLE | 9404.018
2023 | nonsummer | ELSEGN_2_UN2021 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2023 | nonsummer | ELSEGN_2_UN2021 | TRANSMISSION_INDUCED | 2717.4
2023 | nonsummer | ELSEGN_2_UN2021 | UNIT_TESTING | 508.4923
2023 | nonsummer | ENERSJ_2_WIND | PLANT_TROUBLE | 837.0167
2023 | nonsummer | ENERSJ_2_WIND | TRANSMISSION_INDUCED | 0
2023 | nonsummer | ENERSJ_5_ESJWD2 | PLANT_TROUBLE | 1789.75
2023 | nonsummer | ENERSJ_5_ESJWD2 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | ENWIND_2_WIND1 | TRANSMISSION_INDUCED | 400.85
2023 | nonsummer | ENWIND_2_WIND2 | TRANSMISSION_INDUCED | 2237.04
2023 | nonsummer | ESCNDO_6_EB1BT1 | PLANT_MAINTENANCE | 407.5
2023 | nonsummer | ESCNDO_6_EB1BT1 | PLANT_TROUBLE | 1761.8333
2023 | nonsummer | ESCNDO_6_EB1BT1 | TRANSMISSION_INDUCED | 96
2023 | nonsummer | ESCNDO_6_EB2BT2 | METERING_TELEMETRY | 0
2023 | nonsummer | ESCNDO_6_EB2BT2 | PLANT_MAINTENANCE | 357.5
2023 | nonsummer | ESCNDO_6_EB2BT2 | PLANT_TROUBLE | 1994.4167
2023 | nonsummer | ESCNDO_6_EB2BT2 | TRANSMISSION_INDUCED | 159
2023 | nonsummer | ESCNDO_6_EB3BT3 | PLANT_MAINTENANCE | 400.5
2023 | nonsummer | ESCNDO_6_EB3BT3 | PLANT_TROUBLE | 2307.75
2023 | nonsummer | ESCNDO_6_EB3BT3 | TRANSMISSION_INDUCED | 157.5
2023 | nonsummer | ESCNDO_6_PL1X2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 4854.7633
2023 | nonsummer | ESCNDO_6_PL1X2 | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | ESCNDO_6_PL1X2 | PLANT_MAINTENANCE | 438.39
2023 | nonsummer | ESCNDO_6_PL1X2 | PLANT_TROUBLE | 3039.5198
2023 | nonsummer | ESCNDO_6_PL1X2 | TRANSMISSION_INDUCED | 2898.245
2023 | nonsummer | ESCNDO_6_PL1X2 | UNIT_TESTING | 0
2023 | nonsummer | ESCNDO_6_UNITB1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 2779.5
2023 | nonsummer | ESCNDO_6_UNITB1 | PLANT_MAINTENANCE | 80.0667
2023 | nonsummer | ESCNDO_6_UNITB1 | PLANT_TROUBLE | 488.9447
2023 | nonsummer | ESCNDO_6_UNITB1 | TRANSMISSION_INDUCED | 96.08
2023 | nonsummer | ESCO_6_GLMQF | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 6361.26
2023 | nonsummer | ESCO_6_GLMQF | AMBIENT_DUE_TO_TEMP | 0.69
2023 | nonsummer | ESCO_6_GLMQF | PLANT_MAINTENANCE | 349.3
2023 | nonsummer | ESCO_6_GLMQF | PLANT_TROUBLE | 510.92
2023 | nonsummer | ESCO_6_GLMQF | TRANSMISSION_INDUCED | 0
2023 | nonsummer | ESNHWR_2_WC1BT1 | METERING_TELEMETRY | 15
2023 | nonsummer | ESNHWR_2_WC1BT1 | PLANT_MAINTENANCE | 35
2023 | nonsummer | ESNHWR_2_WC1BT1 | PLANT_TROUBLE | 160
2023 | nonsummer | ESNHWR_2_WC1BT1 | UNIT_TESTING | 62.9833
2023 | nonsummer | ESQUON_6_LNDFIL | PLANT_MAINTENANCE | 67.2
2023 | nonsummer | ESQUON_6_LNDFIL | PLANT_TROUBLE | 38.78
2023 | nonsummer | ESQUON_6_LNDFIL | TRANSMISSION_INDUCED | 86.1
2023 | nonsummer | ESTWND_2_OPPWD1 | PLANT_TROUBLE | 133.3267
2023 | nonsummer | ESTWND_2_OPPWD1 | TRANSMISSION_INDUCED | 1714.2
2023 | nonsummer | ETIWND_2_FONTNA | AMBIENT_NOT_DUE_TO_TEMP | 1327.2883
2023 | nonsummer | ETIWND_2_FONTNA | PLANT_TROUBLE | 286.7833
2023 | nonsummer | ETIWND_2_FONTNA | TRANSMISSION_INDUCED | 0
2023 | nonsummer | ETIWND_2_RTS010 | PLANT_TROUBLE | 1125
2023 | nonsummer | ETIWND_2_RTS015 | PLANT_TROUBLE | 915
2023 | nonsummer | ETIWND_2_RTS017 | PLANT_TROUBLE | 2345
2023 | nonsummer | ETIWND_2_RTS018 | PLANT_TROUBLE | 982.5
2023 | nonsummer | ETIWND_2_RTS023 | PLANT_TROUBLE | 1875
2023 | nonsummer | ETIWND_2_RTS026 | PLANT_TROUBLE | 1230
2023 | nonsummer | ETIWND_2_RTS027 | PLANT_TROUBLE | 410
2023 | nonsummer | ETIWND_2_UNIT1 | AMBIENT_NOT_DUE_TO_TEMP | 23068
2023 | nonsummer | ETIWND_2_UNIT1 | PLANT_MAINTENANCE | 14
2023 | nonsummer | ETIWND_2_UNIT1 | PLANT_TROUBLE | 215.04
2023 | nonsummer | ETIWND_6_GRPLND | AMBIENT_DUE_TO_TEMP | 627.2833
2023 | nonsummer | ETIWND_6_GRPLND | METERING_TELEMETRY | 0
2023 | nonsummer | ETIWND_6_GRPLND | OTHER_USE_LIMIT_REACHED | 0
2023 | nonsummer | ETIWND_6_GRPLND | PLANT_MAINTENANCE | 0
2023 | nonsummer | ETIWND_6_GRPLND | PLANT_TROUBLE | 453.3573
2023 | nonsummer | EXCHEC_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 1770
2023 | nonsummer | EXCHEC_7_UNIT 1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | EXCHEC_7_UNIT 1 | PLANT_TROUBLE | 9724.3
2023 | nonsummer | EXCHEC_7_UNIT 1 | TRANSMISSION_INDUCED | 588.55
2023 | nonsummer | EXCHEC_7_UNIT 1 | UNIT_TESTING | 20.475
2023 | nonsummer | EXCLSG_1_SOLAR | PLANT_TROUBLE | 495
2023 | nonsummer | FALBRK_6_FESBT1 | METERING_TELEMETRY | 0
2023 | nonsummer | FALBRK_6_FESBT1 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | FALBRK_6_FESBT1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | FALBRK_6_FESBT1 | PLANT_TROUBLE | 2686
2023 | nonsummer | FALBRK_6_FESBT1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | FIFTHS_2_FSSBT | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | FIFTHS_2_FSSBT | PLANT_MAINTENANCE | 0
2023 | nonsummer | FIFTHS_2_FSSBT | PLANT_TROUBLE | 0
2023 | nonsummer | FIFTHS_2_FSSBT | UNIT_TESTING | 0
2023 | nonsummer | FIFTHS_2_FSSR1 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | FIFTHS_2_FSSR1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | FIFTHS_2_FSSR1 | UNIT_TESTING | 0
2023 | nonsummer | FLOWD2_2_FPLWND | METERING_TELEMETRY | 122.7833
2023 | nonsummer | FLOWD2_2_FPLWND | PLANT_MAINTENANCE | 1928.8357
2023 | nonsummer | FLOWD2_2_FPLWND | TRANSMISSION_INDUCED | 720
2023 | nonsummer | FMEADO_6_HELLHL | PLANT_MAINTENANCE | 0
2023 | nonsummer | FMEADO_6_HELLHL | PLANT_TROUBLE | 126
2023 | nonsummer | FMEADO_6_HELLHL | TRANSMISSION_INDUCED | 316.71
2023 | nonsummer | FMEADO_7_UNIT | PLANT_TROUBLE | 1206.3
2023 | nonsummer | FMEADO_7_UNIT | RTU_RIG | 0
2023 | nonsummer | FMEADO_7_UNIT | TRANSMISSION_INDUCED | 3606.6667
2023 | nonsummer | FMEADO_7_UNIT | UNIT_TESTING | 0
2023 | nonsummer | FORBST_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 59
2023 | nonsummer | FORBST_7_UNIT 1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | FORBST_7_UNIT 1 | PLANT_TROUBLE | 2657.8667
2023 | nonsummer | FORBST_7_UNIT 1 | TRANSMISSION_INDUCED | 187.5
2023 | nonsummer | FORKBU_6_UNIT | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1654.75
2023 | nonsummer | FORKBU_6_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 2321.75
2023 | nonsummer | FORKBU_6_UNIT | PLANT_TROUBLE | 0
2023 | nonsummer | FORKBU_6_UNIT | TRANSMISSION_INDUCED | 172.9067
2023 | nonsummer | FRESHW_1_SOLAR1 | PLANT_TROUBLE | 0
2023 | nonsummer | FRESHW_1_SOLAR1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | FRIANT_6_UNITS | METERING_TELEMETRY | 875
2023 | nonsummer | FRIANT_6_UNITS | TRANSMISSION_INDUCED | 4500
2023 | nonsummer | FRNTBW_6_SOLAR1 | METERING_TELEMETRY | 20
2023 | nonsummer | FRNTBW_6_SOLAR1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | FRNTBW_6_SOLAR1 | PLANT_TROUBLE | 0
2023 | nonsummer | FRNTBW_6_SOLAR1 | TRANSMISSION_INDUCED | 500
2023 | nonsummer | FROGTN_1_UTICAA | PLANT_MAINTENANCE | 7
2023 | nonsummer | FROGTN_1_UTICAA | PLANT_TROUBLE | 2.03
2023 | nonsummer | FROGTN_1_UTICAA | TRANSMISSION_INDUCED | 4.9233
2023 | nonsummer | FROGTN_1_UTICAM | ENVIRONMENTAL_RESTRICTIONS | 126.54
2023 | nonsummer | FROGTN_1_UTICAM | PLANT_MAINTENANCE | 0
2023 | nonsummer | FROGTN_1_UTICAM | PLANT_TROUBLE | 76.5
2023 | nonsummer | FROGTN_1_UTICAM | TRANSMISSION_INDUCED | 14.64
2023 | nonsummer | FTSWRD_6_TRFORK | TRANSMISSION_INDUCED | 100.571
2023 | nonsummer | FTSWRD_7_QFUNTS | TRANSMISSION_INDUCED | 98.7467
2023 | nonsummer | GALE_1_SR3SR3 | PLANT_MAINTENANCE | 0
2023 | nonsummer | GALE_1_SR3SR3 | PLANT_TROUBLE | 34.27
2023 | nonsummer | GALE_1_SR3SR3 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | GANSO_1_WSTBM1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2023 | nonsummer | GANSO_1_WSTBM1 | PLANT_MAINTENANCE | 3
2023 | nonsummer | GANSO_1_WSTBM1 | PLANT_TROUBLE | 0
2023 | nonsummer | GARLND_2_GARBT1 | METERING_TELEMETRY | 1203
2023 | nonsummer | GARLND_2_GARBT1 | PLANT_MAINTENANCE | 1437.3333
2023 | nonsummer | GARLND_2_GARBT1 | PLANT_TROUBLE | 14505.4667
2023 | nonsummer | GARLND_2_GARBT1 | UNIT_TESTING | 878.5333
2023 | nonsummer | GARLND_2_GASLR | METERING_TELEMETRY | 0
2023 | nonsummer | GARLND_2_GASLR | PLANT_MAINTENANCE | 1555.3333
2023 | nonsummer | GARLND_2_GASLR | PLANT_TROUBLE | 13447.9502
2023 | nonsummer | GARLND_2_GASLR | UNIT_TESTING | 338.4
2023 | nonsummer | GARLND_2_GASLRA | PLANT_MAINTENANCE | 60
2023 | nonsummer | GARLND_2_GASLRA | PLANT_TROUBLE | 110.98
2023 | nonsummer | GARLND_2_GASLRA | UNIT_TESTING | 20
2023 | nonsummer | GARNET_1_SOLAR2 | METERING_TELEMETRY | 15
2023 | nonsummer | GARNET_1_SOLAR2 | PLANT_TROUBLE | 250
2023 | nonsummer | GARNET_1_WIND | PLANT_MAINTENANCE | 15
2023 | nonsummer | GARNET_1_WIND | PLANT_TROUBLE | 0
2023 | nonsummer | GARNET_1_WIND | TRANSMISSION_INDUCED | 209.3283
2023 | nonsummer | GARNET_1_WINDS | PLANT_MAINTENANCE | 1008.275
2023 | nonsummer | GARNET_1_WINDS | PLANT_TROUBLE | 27.725
2023 | nonsummer | GARNET_1_WINDS | TRANSMISSION_INDUCED | 4.5
2023 | nonsummer | GARNET_1_WT3WND | METERING_TELEMETRY | 3.8
2023 | nonsummer | GARNET_1_WT3WND | PLANT_TROUBLE | 0
2023 | nonsummer | GARNET_1_WT3WND | TRANSMISSION_INDUCED | 102.885
2023 | nonsummer | GARNET_2_COAWD2 | PLANT_MAINTENANCE | 37.9
2023 | nonsummer | GARNET_2_COAWD2 | PLANT_TROUBLE | 3957.06
2023 | nonsummer | GARNET_2_COAWD2 | TRANSMISSION_INDUCED | 299.5217
2023 | nonsummer | GARNET_2_HYDRO | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 460
2023 | nonsummer | GARNET_2_HYDRO | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | GARNET_2_HYDRO | PLANT_MAINTENANCE | 95
2023 | nonsummer | GARNET_2_HYDRO | PLANT_TROUBLE | 65
2023 | nonsummer | GARNET_2_WIND1 | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | nonsummer | GARNET_2_WIND1 | METERING_TELEMETRY | 0
2023 | nonsummer | GARNET_2_WIND1 | PLANT_MAINTENANCE | 19
2023 | nonsummer | GARNET_2_WIND1 | PLANT_TROUBLE | 1940.54
2023 | nonsummer | GARNET_2_WIND1 | TRANSMISSION_INDUCED | 166.6208
2023 | nonsummer | GARNET_2_WIND2 | PLANT_MAINTENANCE | 1211.875
2023 | nonsummer | GARNET_2_WIND2 | PLANT_TROUBLE | 453.29
2023 | nonsummer | GARNET_2_WIND2 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | GARNET_2_WIND3 | PLANT_TROUBLE | 0
2023 | nonsummer | GARNET_2_WIND3 | TRANSMISSION_INDUCED | 117.1567
2023 | nonsummer | GARNET_2_WIND4 | METERING_TELEMETRY | 198.52
2023 | nonsummer | GARNET_2_WIND4 | PLANT_TROUBLE | 0
2023 | nonsummer | GARNET_2_WIND4 | TRANSMISSION_INDUCED | 251.3067
2023 | nonsummer | GARNET_2_WIND5 | AMBIENT_NOT_DUE_TO_TEMP | 43.5
2023 | nonsummer | GARNET_2_WIND5 | METERING_TELEMETRY | 0
2023 | nonsummer | GARNET_2_WIND5 | PLANT_TROUBLE | 15
2023 | nonsummer | GARNET_2_WIND5 | TRANSMISSION_INDUCED | 646.75
2023 | nonsummer | GASKW1_2_GW1SR1 | METERING_TELEMETRY | 0
2023 | nonsummer | GASKW1_2_GW1SR1 | PLANT_MAINTENANCE | 329.91
2023 | nonsummer | GASKW1_2_GW1SR1 | PLANT_TROUBLE | 5550.5347
2023 | nonsummer | GASKW1_2_GW2BT1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | GASKW1_2_GW2BT1 | METERING_TELEMETRY | 0
2023 | nonsummer | GASKW1_2_GW2BT1 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | GASKW1_2_GW2BT1 | PLANT_MAINTENANCE | 210.2983
2023 | nonsummer | GASKW1_2_GW2BT1 | PLANT_TROUBLE | 471.2717
2023 | nonsummer | GASKW1_2_GW2BT1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | GASKW1_2_GW2SR1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | GASKW1_2_GW2SR1 | PLANT_TROUBLE | 10
2023 | nonsummer | GASKW1_2_GW2SR2 | METERING_TELEMETRY | 0
2023 | nonsummer | GASKW1_2_GW2SR2 | NEW_GENERATOR_TEST_ENERGY | 522
2023 | nonsummer | GASKW1_2_GW2SR2 | PLANT_MAINTENANCE | 0
2023 | nonsummer | GASKW1_2_GW2SR2 | PLANT_TROUBLE | 0
2023 | nonsummer | GASKW1_2_GW2SR2 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | GASKW1_2_GW2SR2 | UNIT_TESTING | 0
2023 | nonsummer | GASKW1_2_GW3SR1 | METERING_TELEMETRY | 158
2023 | nonsummer | GASKW1_2_GW3SR1 | NEW_GENERATOR_TEST_ENERGY | 240
2023 | nonsummer | GASKW1_2_GW3SR1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | GASKW1_2_GW3SR1 | PLANT_TROUBLE | 8.375
2023 | nonsummer | GASKW1_2_GW3SR1 | UNIT_TESTING | 0
2023 | nonsummer | GASKW1_2_GW4SR1 | METERING_TELEMETRY | 0
2023 | nonsummer | GASKW1_2_GW4SR1 | NEW_GENERATOR_TEST_ENERGY | 240
2023 | nonsummer | GASKW1_2_GW4SR1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | GASKW1_2_GW4SR1 | PLANT_TROUBLE | 0
2023 | nonsummer | GASKW1_2_GW4SR1 | UNIT_TESTING | 0
2023 | nonsummer | GASKW1_2_GW5SR1 | METERING_TELEMETRY | 0
2023 | nonsummer | GASKW1_2_GW5SR1 | NEW_GENERATOR_TEST_ENERGY | 240
2023 | nonsummer | GASKW1_2_GW5SR1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | GASKW1_2_GW5SR1 | PLANT_TROUBLE | 0
2023 | nonsummer | GASKW1_2_GW5SR1 | UNIT_TESTING | 0
2023 | nonsummer | GATES_2_SOLAR | TRANSMISSION_INDUCED | 80
2023 | nonsummer | GATES_2_WSOLAR | TRANSMISSION_INDUCED | 0
2023 | nonsummer | GATEWY_2_GESBT1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | GATEWY_2_GESBT1 | PLANT_TROUBLE | 903.8333
2023 | nonsummer | GATWAY_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 41476.5833
2023 | nonsummer | GATWAY_2_PL1X3 | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | nonsummer | GATWAY_2_PL1X3 | METERING_TELEMETRY | 0
2023 | nonsummer | GATWAY_2_PL1X3 | PLANT_TROUBLE | 2299.4
2023 | nonsummer | GATWAY_2_PL1X3 | UNIT_TESTING | 0
2023 | nonsummer | GENESI_2_STG | AMBIENT_NOT_DUE_TO_TEMP | 15381.25
2023 | nonsummer | GENESI_2_STG | PLANT_TROUBLE | 1375
2023 | nonsummer | GEYS11_7_UNIT11 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 2383
2023 | nonsummer | GEYS11_7_UNIT11 | AMBIENT_NOT_DUE_TO_TEMP | 9252.28
2023 | nonsummer | GEYS11_7_UNIT11 | PLANT_TROUBLE | 1160.778
2023 | nonsummer | GEYS11_7_UNIT11 | TRANSMISSION_INDUCED | 100.1
2023 | nonsummer | GEYS12_7_UNIT12 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 3106
2023 | nonsummer | GEYS12_7_UNIT12 | AMBIENT_NOT_DUE_TO_TEMP | 13647
2023 | nonsummer | GEYS12_7_UNIT12 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | GEYS13_7_UNIT13 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 5094.8
2023 | nonsummer | GEYS13_7_UNIT13 | AMBIENT_NOT_DUE_TO_TEMP | 18888
2023 | nonsummer | GEYS13_7_UNIT13 | PLANT_TROUBLE | 0
2023 | nonsummer | GEYS13_7_UNIT13 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | GEYS14_7_UNIT14 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 2512
2023 | nonsummer | GEYS14_7_UNIT14 | AMBIENT_NOT_DUE_TO_TEMP | 12068
2023 | nonsummer | GEYS14_7_UNIT14 | PLANT_TROUBLE | 163
2023 | nonsummer | GEYS14_7_UNIT14 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 224
2023 | nonsummer | GEYS14_7_UNIT14 | TRANSMISSION_INDUCED | 336
2023 | nonsummer | GEYS16_7_UNIT16 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 2282
2023 | nonsummer | GEYS16_7_UNIT16 | AMBIENT_NOT_DUE_TO_TEMP | 11606
2023 | nonsummer | GEYS16_7_UNIT16 | PLANT_TROUBLE | 797
2023 | nonsummer | GEYS16_7_UNIT16 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | GEYS17_7_UNIT17 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 3470
2023 | nonsummer | GEYS17_7_UNIT17 | AMBIENT_NOT_DUE_TO_TEMP | 13885.5
2023 | nonsummer | GEYS17_7_UNIT17 | PLANT_TROUBLE | 91.4667
2023 | nonsummer | GEYS17_7_UNIT17 | TRANSITIONAL_LIMITATION | 0
2023 | nonsummer | GEYS17_7_UNIT17 | UNIT_TESTING | 0
2023 | nonsummer | GEYS18_7_UNIT18 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 6007
2023 | nonsummer | GEYS18_7_UNIT18 | AMBIENT_NOT_DUE_TO_TEMP | 25821.5
2023 | nonsummer | GEYS18_7_UNIT18 | PLANT_MAINTENANCE | 240
2023 | nonsummer | GEYS18_7_UNIT18 | PLANT_TROUBLE | 0
2023 | nonsummer | GEYS18_7_UNIT18 | TRANSITIONAL_LIMITATION | 96
2023 | nonsummer | GEYS18_7_UNIT18 | UNIT_TESTING | 0
2023 | nonsummer | GEYS20_7_UNIT20 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 3358
2023 | nonsummer | GEYS20_7_UNIT20 | AMBIENT_NOT_DUE_TO_TEMP | 11815.5
2023 | nonsummer | GEYS20_7_UNIT20 | PLANT_TROUBLE | 352.8652
2023 | nonsummer | GEYS20_7_UNIT20 | TRANSITIONAL_LIMITATION | 163.9
2023 | nonsummer | GEYS20_7_UNIT20 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | GIFENS_6_BUGSL1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | GIFENS_6_BUGSL1 | PLANT_TROUBLE | 0
2023 | nonsummer | GIFENS_6_BUGSL1 | TRANSMISSION_INDUCED | 100
2023 | nonsummer | GIFFEN_6_SOLAR | AMBIENT_NOT_DUE_TO_TEMP | 250
2023 | nonsummer | GIFFEN_6_SOLAR | PLANT_TROUBLE | 0
2023 | nonsummer | GIFFEN_6_SOLAR | TRANSMISSION_INDUCED | 66.1667
2023 | nonsummer | GIFFEN_6_SOLAR1 | PLANT_TROUBLE | 34.9167
2023 | nonsummer | GILROY_1_UNIT | AMBIENT_DUE_TO_TEMP | 6084
2023 | nonsummer | GILROY_1_UNIT | PLANT_MAINTENANCE | 1470
2023 | nonsummer | GILROY_1_UNIT | PLANT_TROUBLE | 19695
2023 | nonsummer | GILROY_1_UNIT | TRANSITIONAL_LIMITATION | 0
2023 | nonsummer | GILROY_1_UNIT | TRANSMISSION_INDUCED | 900
2023 | nonsummer | GILRPP_1_PL1X2 | PLANT_MAINTENANCE | 0
2023 | nonsummer | GILRPP_1_PL1X2 | PLANT_TROUBLE | 0
2023 | nonsummer | GILRPP_1_PL1X2 | TRANSMISSION_INDUCED | 2808.4
2023 | nonsummer | GILRPP_1_PL1X2 | UNIT_TESTING | 0
2023 | nonsummer | GILRPP_1_PL3X4 | PLANT_TROUBLE | 0
2023 | nonsummer | GILRPP_1_PL3X4 | TRANSMISSION_INDUCED | 1362.9
2023 | nonsummer | GILRPP_1_PL3X4 | UNIT_TESTING | 76.23
2023 | nonsummer | GLDFGR_6_SOLAR1 | PLANT_MAINTENANCE | 103.3333
2023 | nonsummer | GLDFGR_6_SOLAR1 | PLANT_TROUBLE | 0
2023 | nonsummer | GLDFGR_6_SOLAR2 | METERING_TELEMETRY | 6.08
2023 | nonsummer | GLDFGR_6_SOLAR2 | PLANT_MAINTENANCE | 60.04
2023 | nonsummer | GLDFGR_6_SOLAR2 | PLANT_TROUBLE | 0
2023 | nonsummer | GLDTWN_6_COLUM3 | METERING_TELEMETRY | 0
2023 | nonsummer | GLDTWN_6_COLUM3 | PLANT_MAINTENANCE | 47
2023 | nonsummer | GLDTWN_6_COLUM3 | PLANT_TROUBLE | 28.1667
2023 | nonsummer | GLDTWN_6_SOLAR | METERING_TELEMETRY | 49.5
2023 | nonsummer | GLDTWN_6_SOLAR | PLANT_MAINTENANCE | 30
2023 | nonsummer | GLDTWN_6_SOLAR | PLANT_TROUBLE | 102
2023 | nonsummer | GLNARM_2_UNIT 5 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 20.7323
2023 | nonsummer | GLNARM_2_UNIT 5 | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | GLNARM_2_UNIT 5 | AMBIENT_NOT_DUE_TO_TEMP | 16.337
2023 | nonsummer | GLNARM_2_UNIT 5 | PLANT_MAINTENANCE | 0
2023 | nonsummer | GLNARM_2_UNIT 5 | PLANT_TROUBLE | 11777.0785
2023 | nonsummer | GLNARM_2_UNIT 5 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | GLNARM_2_UNIT 5 | UNIT_TESTING | 0
2023 | nonsummer | GLNARM_7_UNIT 1 | PLANT_TROUBLE | 7356.7497
2023 | nonsummer | GLNARM_7_UNIT 1 | UNIT_TESTING | 23.5887
2023 | nonsummer | GLNARM_7_UNIT 2 | PLANT_MAINTENANCE | 335.7
2023 | nonsummer | GLNARM_7_UNIT 2 | PLANT_TROUBLE | 559.5
2023 | nonsummer | GLNARM_7_UNIT 2 | UNIT_TESTING | 5.38
2023 | nonsummer | GLNARM_7_UNIT 3 | PLANT_MAINTENANCE | 147.1918
2023 | nonsummer | GLNARM_7_UNIT 3 | PLANT_TROUBLE | 3767.2143
2023 | nonsummer | GLNARM_7_UNIT 3 | UNIT_TESTING | 0
2023 | nonsummer | GLNARM_7_UNIT 4 | PLANT_MAINTENANCE | 979.195
2023 | nonsummer | GLNARM_7_UNIT 4 | PLANT_TROUBLE | 1565.775
2023 | nonsummer | GLNARM_7_UNIT 4 | UNIT_TESTING | 13.21
2023 | nonsummer | GLOW_6_SOLAR | METERING_TELEMETRY | 0
2023 | nonsummer | GLOW_6_SOLAR | PLANT_MAINTENANCE | 0
2023 | nonsummer | GLOW_6_SOLAR | PLANT_TROUBLE | 142.9083
2023 | nonsummer | GLOW_6_SOLAR | TRANSMISSION_INDUCED | 1460.8333
2023 | nonsummer | GOLETA_2_VALBT1 | METERING_TELEMETRY | 776.6667
2023 | nonsummer | GOLETA_2_VALBT1 | PLANT_MAINTENANCE | 108.6667
2023 | nonsummer | GOLETA_2_VALBT1 | PLANT_TROUBLE | 85.0383
2023 | nonsummer | GOLETA_2_VALBT1 | UNIT_TESTING | 50
2023 | nonsummer | GOLETA_6_ELLWOD | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2023 | nonsummer | GOLETA_6_ELLWOD | PLANT_MAINTENANCE | 333
2023 | nonsummer | GOLETA_6_ELLWOD | PLANT_TROUBLE | 15.3
2023 | nonsummer | GOLETA_6_ELLWOD | UNIT_TESTING | 0
2023 | nonsummer | GOLETA_6_TR2BM2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 60.85
2023 | nonsummer | GOLETA_6_TR2BM2 | AMBIENT_NOT_DUE_TO_TEMP | 309.52
2023 | nonsummer | GOLETA_6_TR2BM2 | PLANT_MAINTENANCE | 0
2023 | nonsummer | GOLETA_6_TR2BM2 | PLANT_TROUBLE | 0
2023 | nonsummer | GONZLS_6_UNIT | PLANT_MAINTENANCE | 93.6017
2023 | nonsummer | GONZLS_6_UNIT | PLANT_TROUBLE | 267.315
2023 | nonsummer | GOOSLK_1_SOLAR1 | METERING_TELEMETRY | 31.5
2023 | nonsummer | GOOSLK_1_SOLAR1 | PLANT_MAINTENANCE | 60
2023 | nonsummer | GOOSLK_1_SOLAR1 | TRANSMISSION_INDUCED | 840
2023 | nonsummer | GRADYW_5_GDYWD1 | AMBIENT_DUE_TO_TEMP | 1825
2023 | nonsummer | GRADYW_5_GDYWD1 | ENVIRONMENTAL_RESTRICTIONS | 505
2023 | nonsummer | GRADYW_5_GDYWD1 | PLANT_TROUBLE | 1511.25
2023 | nonsummer | GRADYW_5_GDYWD1 | TRANSITIONAL_LIMITATION | 675
2023 | nonsummer | GRADYW_5_GDYWD1 | TRANSMISSION_INDUCED | 12864.6333
2023 | nonsummer | GRIDLY_6_SOLAR | METERING_TELEMETRY | 25
2023 | nonsummer | GRIDLY_6_SOLAR | PLANT_TROUBLE | 0
2023 | nonsummer | GRIDLY_6_SOLAR | TRANSMISSION_INDUCED | 262.5
2023 | nonsummer | GRIFFI_2_LSPDYN | PLANT_TROUBLE | 1013.5333
2023 | nonsummer | GRIZLY_1_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | GRIZLY_1_UNIT 1 | PLANT_TROUBLE | 3
2023 | nonsummer | GRIZLY_1_UNIT 1 | TRANSMISSION_INDUCED | 19670
2023 | nonsummer | GRNLF1_1_PL1X2 | ENVIRONMENTAL_RESTRICTIONS | 36900
2023 | nonsummer | GRNLF1_1_PL1X2 | METERING_TELEMETRY | 3000
2023 | nonsummer | GRNLF1_1_PL1X2 | PLANT_MAINTENANCE | 900
2023 | nonsummer | GRNLF1_1_PL1X2 | PLANT_TROUBLE | 3569.5
2023 | nonsummer | GRNLF1_1_PL1X2 | UNIT_TESTING | 33.5
2023 | nonsummer | GRNLF2_1_UNIT | PLANT_TROUBLE | 51292.81
2023 | nonsummer | GRNVLY_7_SCLAND | PLANT_MAINTENANCE | 106.2907
2023 | nonsummer | GRNVLY_7_SCLAND | PLANT_TROUBLE | 272.331
2023 | nonsummer | GRNVLY_7_SCLAND | TRANSMISSION_INDUCED | 0
2023 | nonsummer | GRSCRK_6_BGCKWW | AMBIENT_NOT_DUE_TO_TEMP | 1215
2023 | nonsummer | GRSCRK_6_BGCKWW | ENVIRONMENTAL_RESTRICTIONS | 22.5
2023 | nonsummer | GRSCRK_6_BGCKWW | PLANT_MAINTENANCE | 0
2023 | nonsummer | GRSCRK_6_BGCKWW | PLANT_TROUBLE | 55.8333
2023 | nonsummer | GRSCRK_6_BGCKWW | TRANSMISSION_INDUCED | 25
2023 | nonsummer | GUERNS_6_HD3BM3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 55.6
2023 | nonsummer | GUERNS_6_HD3BM3 | PLANT_MAINTENANCE | 0
2023 | nonsummer | GUERNS_6_HD3BM3 | PLANT_TROUBLE | 36.5
2023 | nonsummer | GUERNS_6_SOLAR | AMBIENT_NOT_DUE_TO_TEMP | 5300
2023 | nonsummer | GUERNS_6_SOLAR | PLANT_TROUBLE | 64
2023 | nonsummer | GUERNS_6_SOLAR | TRANSMISSION_INDUCED | 50
2023 | nonsummer | GUERNS_6_VH2BM1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 80.1833
2023 | nonsummer | GUERNS_6_VH2BM1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | GUERNS_6_VH2BM1 | PLANT_TROUBLE | 22.3667
2023 | nonsummer | GWFPWR_1_UNITS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2023 | nonsummer | GWFPWR_1_UNITS | AMBIENT_DUE_TO_TEMP | 25.38
2023 | nonsummer | GWFPWR_1_UNITS | OTHER_USE_LIMIT_REACHED | 0
2023 | nonsummer | GWFPWR_1_UNITS | PLANT_MAINTENANCE | 1289.826
2023 | nonsummer | GWFPWR_1_UNITS | UNIT_TESTING | 0
2023 | nonsummer | GYS5X6_7_UNITS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1033.55
2023 | nonsummer | GYS5X6_7_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 15490.5
2023 | nonsummer | GYS5X6_7_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 376
2023 | nonsummer | GYS5X6_7_UNITS | PLANT_MAINTENANCE | 960
2023 | nonsummer | GYS5X6_7_UNITS | PLANT_TROUBLE | 613.3333
2023 | nonsummer | GYS5X6_7_UNITS | PLANT_TROUBLE | 16039.8167
2023 | nonsummer | GYS5X6_7_UNITS | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 174.5333
2023 | nonsummer | GYS5X6_7_UNITS | TRANSMISSION_INDUCED | 96.25
2023 | nonsummer | GYS7X8_7_UNITS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 2995
2023 | nonsummer | GYS7X8_7_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 13219.95
2023 | nonsummer | GYS7X8_7_UNITS | PLANT_TROUBLE | 1071.4
2023 | nonsummer | GYS7X8_7_UNITS | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 179.0667
2023 | nonsummer | GYS7X8_7_UNITS | TRANSITIONAL_LIMITATION | 0
2023 | nonsummer | GYS7X8_7_UNITS | TRANSMISSION_INDUCED | 101.3833
2023 | nonsummer | GYSRVL_7_WSPRNG | METERING_TELEMETRY | 0
2023 | nonsummer | HAASPH_7_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 2549.7167
2023 | nonsummer | HAASPH_7_PL1X2 | ANNUAL_USE_LIMIT_REACHED | 0
2023 | nonsummer | HAASPH_7_PL1X2 | PLANT_MAINTENANCE | 0
2023 | nonsummer | HAASPH_7_PL1X2 | PLANT_TROUBLE | 996
2023 | nonsummer | HAASPH_7_PL1X2 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | HAASPH_7_PL1X2 | UNIT_SUPPORTING_STARTUP | 0
2023 | nonsummer | HAASPH_7_PL1X2 | UNIT_TESTING | 0
2023 | nonsummer | HARBGN_7_UNITS | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | HARBGN_7_UNITS | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | nonsummer | HARBGN_7_UNITS | PLANT_TROUBLE | 436.04
2023 | nonsummer | HARBGN_7_UNITS | TRANSMISSION_INDUCED | 0
2023 | nonsummer | HARBGN_7_UNITS | UNIT_TESTING | 131.97
2023 | nonsummer | HARDWK_6_STWBM1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | HARDWK_6_STWBM1 | PLANT_TROUBLE | 0
2023 | nonsummer | HATCR1_7_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 30
2023 | nonsummer | HATCR1_7_UNIT | PLANT_TROUBLE | 0
2023 | nonsummer | HATCR2_7_UNIT | PLANT_TROUBLE | 6417.925
2023 | nonsummer | HATLOS_6_BWDHY1 | PLANT_TROUBLE | 0
2023 | nonsummer | HATLOS_6_LSCRK | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 137.95
2023 | nonsummer | HATLOS_6_LSCRK | AMBIENT_NOT_DUE_TO_TEMP | 692.95
2023 | nonsummer | HATLOS_6_LSCRK | PLANT_TROUBLE | 0
2023 | nonsummer | HATLOS_6_LSCRK | TRANSMISSION_INDUCED | 0
2023 | nonsummer | HATRDG_2_WIND | PLANT_MAINTENANCE | 3388.4
2023 | nonsummer | HATRDG_2_WIND | PLANT_TROUBLE | 745.5
2023 | nonsummer | HAYPRS_6_HAYHD1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 2186.6
2023 | nonsummer | HAYPRS_6_HAYHD1 | PLANT_TROUBLE | 399.1367
2023 | nonsummer | HAYPRS_6_HAYHD1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | HAYPRS_6_HAYHD2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 2654.9867
2023 | nonsummer | HAYPRS_6_HAYHD2 | PLANT_TROUBLE | 7.4817
2023 | nonsummer | HAYPRS_6_HAYHD2 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | HELMPG_7_UNIT 1 | PLANT_MAINTENANCE | 4070
2023 | nonsummer | HELMPG_7_UNIT 1 | PLANT_TROUBLE | 814.1
2023 | nonsummer | HELMPG_7_UNIT 1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | HELMPG_7_UNIT 2 | PLANT_MAINTENANCE | 0
2023 | nonsummer | HELMPG_7_UNIT 2 | PLANT_TROUBLE | 3588.3833
2023 | nonsummer | HELMPG_7_UNIT 2 | TRANSMISSION_INDUCED | 230.2833
2023 | nonsummer | HELMPG_7_UNIT 3 | PLANT_MAINTENANCE | 40.4
2023 | nonsummer | HELMPG_7_UNIT 3 | PLANT_TROUBLE | 5999.4
2023 | nonsummer | HELMPG_7_UNIT 3 | TRANSMISSION_INDUCED | 60.6
2023 | nonsummer | HENRTA_6_HDEBT1 | METERING_TELEMETRY | 0
2023 | nonsummer | HENRTA_6_HDEBT1 | PLANT_MAINTENANCE | 0.16667
2023 | nonsummer | HENRTA_6_HDEBT1 | PLANT_TROUBLE | 42.6
2023 | nonsummer | HENRTA_6_HDEBT1 | TRANSMISSION_INDUCED | 100
2023 | nonsummer | HENRTA_6_SOLAR1 | PLANT_TROUBLE | 646.475
2023 | nonsummer | HENRTA_6_UNITA1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2023 | nonsummer | HENRTA_6_UNITA1 | ENVIRONMENTAL_RESTRICTIONS | 63.97
2023 | nonsummer | HENRTA_6_UNITA1 | OTHER_USE_LIMIT_REACHED | 0
2023 | nonsummer | HENRTA_6_UNITA1 | PLANT_MAINTENANCE | 127.449
2023 | nonsummer | HENRTA_6_UNITA1 | PLANT_TROUBLE | 599.76
2023 | nonsummer | HENRTA_6_UNITA1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | HENRTA_6_UNITA1 | UNIT_TESTING | 0
2023 | nonsummer | HENRTA_6_UNITA2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2023 | nonsummer | HENRTA_6_UNITA2 | OTHER_USE_LIMIT_REACHED | 0
2023 | nonsummer | HENRTA_6_UNITA2 | PLANT_MAINTENANCE | 126.021
2023 | nonsummer | HENRTA_6_UNITA2 | PLANT_TROUBLE | 74.13
2023 | nonsummer | HENRTA_6_UNITA2 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | HENRTA_6_UNITA2 | UNIT_TESTING | 0
2023 | nonsummer | HENRTS_1_SOLAR | PLANT_MAINTENANCE | 400
2023 | nonsummer | HENRTS_1_SOLAR | PLANT_TROUBLE | 396.5933
2023 | nonsummer | HERDLN_6_BYHSR1 | PLANT_TROUBLE | 0
2023 | nonsummer | HERDLN_6_BYHSR1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | HIDSRT_2_UNITS | AMBIENT_DUE_TO_TEMP | 15160.1667
2023 | nonsummer | HIDSRT_2_UNITS | PLANT_MAINTENANCE | 105180
2023 | nonsummer | HIDSRT_2_UNITS | PLANT_TROUBLE | 26802.5
2023 | nonsummer | HIDSRT_2_UNITS | UNIT_TESTING | 0
2023 | nonsummer | HIGGNS_1_COMBIE | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | HIGGNS_1_COMBIE | PLANT_MAINTENANCE | 0
2023 | nonsummer | HIGGNS_1_COMBIE | PLANT_TROUBLE | 3.6125
2023 | nonsummer | HIGGNS_1_COMBIE | TRANSMISSION_INDUCED | 0.45
2023 | nonsummer | HIGHDS_2_H5SBT1 | METERING_TELEMETRY | 378.5
2023 | nonsummer | HIGHDS_2_H5SBT1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | HIGHDS_2_H5SBT1 | PLANT_TROUBLE | 5361.3613
2023 | nonsummer | HIGHDS_2_H5SBT1 | TRANSMISSION_INDUCED | 500
2023 | nonsummer | HIGHDS_2_H5SBT1 | UNIT_TESTING | 0
2023 | nonsummer | HIGHDS_2_H5SSR1 | METERING_TELEMETRY | 250
2023 | nonsummer | HIGHDS_2_H5SSR1 | PLANT_MAINTENANCE | 470.648
2023 | nonsummer | HINSON_6_LBECH1 | PLANT_MAINTENANCE | 126
2023 | nonsummer | HINSON_6_LBECH1 | PLANT_TROUBLE | 771.75
2023 | nonsummer | HINSON_6_LBECH1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | HINSON_6_LBECH1 | UNIT_TESTING | 0
2023 | nonsummer | HINSON_6_LBECH2 | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | nonsummer | HINSON_6_LBECH2 | PLANT_MAINTENANCE | 126
2023 | nonsummer | HINSON_6_LBECH2 | PLANT_TROUBLE | 141.75
2023 | nonsummer | HINSON_6_LBECH2 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | HINSON_6_LBECH3 | PLANT_MAINTENANCE | 63
2023 | nonsummer | HINSON_6_LBECH3 | PLANT_TROUBLE | 94.5
2023 | nonsummer | HINSON_6_LBECH3 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | HINSON_6_LBECH4 | PLANT_MAINTENANCE | 63
2023 | nonsummer | HINSON_6_LBECH4 | PLANT_TROUBLE | 425.25
2023 | nonsummer | HINSON_6_LBECH4 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | HINSON_6_LBECH4 | UNIT_TESTING | 226.8
2023 | nonsummer | HINSON_6_SERRGN | PLANT_MAINTENANCE | 216
2023 | nonsummer | HINSON_6_SERRGN | PLANT_TROUBLE | 3400
2023 | nonsummer | HNTGBH_2_PL1X3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2023 | nonsummer | HNTGBH_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 69
2023 | nonsummer | HNTGBH_2_PL1X3 | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | HNTGBH_2_PL1X3 | METERING_TELEMETRY | 0
2023 | nonsummer | HNTGBH_2_PL1X3 | PLANT_MAINTENANCE | 15318.45
2023 | nonsummer | HNTGBH_2_PL1X3 | PLANT_TROUBLE | 2536.0545
2023 | nonsummer | HNTGBH_2_PL1X3 | UNIT_TESTING | 0
2023 | nonsummer | HNTGBH_7_UNIT 2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1134.2
2023 | nonsummer | HNTGBH_7_UNIT 2 | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | HNTGBH_7_UNIT 2 | PLANT_TROUBLE | 9382.288
2023 | nonsummer | HNTGBH_7_UNIT 2 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | HNTGBH_7_UNIT 2 | UNIT_TESTING | 479.2
2023 | nonsummer | HOLGAT_1_BORAX | PLANT_TROUBLE | 779.1933
2023 | nonsummer | HOLSTR_1_SOLAR | METERING_TELEMETRY | 0
2023 | nonsummer | HOOVER_2_MWDDYN | AMBIENT_NOT_DUE_TO_TEMP | 38595
2023 | nonsummer | HOOVER_2_MWDPT | AMBIENT_NOT_DUE_TO_TEMP | 75145
2023 | nonsummer | HOOVER_2_MWDPT | AMBIENT_NOT_DUE_TO_TEMP | 48319
2023 | nonsummer | HOOVER_2_MWDPT | PLANT_MAINTENANCE | 0
2023 | nonsummer | HOOVER_2_MWDPT | PLANT_MAINTENANCE | 0
2023 | nonsummer | HOOVER_2_SCEPT | AMBIENT_NOT_DUE_TO_TEMP | 140858
2023 | nonsummer | HOOVER_2_SCEPT | ANNUAL_USE_LIMIT_REACHED | 291
2023 | nonsummer | HOOVER_2_SCEPT | OTHER_USE_LIMIT_REACHED | 3197.6333
2023 | nonsummer | HOOVER_2_SCEPT | RIMS_TESTING | 0
2023 | nonsummer | HOOVER_2_VEADYN | AMBIENT_NOT_DUE_TO_TEMP | 2480
2023 | nonsummer | HOOVER_2_VEAPT | AMBIENT_NOT_DUE_TO_TEMP | 7197
2023 | nonsummer | HOOVER_2_VEAPT | PLANT_MAINTENANCE | 0
2023 | nonsummer | HOOVER_2_VEAPT | RTU_RIG | 0
2023 | nonsummer | HUMBPP_1_UNITS3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 244.05
2023 | nonsummer | HUMBPP_1_UNITS3 | AMBIENT_NOT_DUE_TO_TEMP | 684.616
2023 | nonsummer | HUMBPP_1_UNITS3 | PLANT_MAINTENANCE | 139.601
2023 | nonsummer | HUMBPP_1_UNITS3 | PLANT_TROUBLE | 1872.32
2023 | nonsummer | HUMBPP_1_UNITS3 | TRANSMISSION_INDUCED | 341.67
2023 | nonsummer | HUMBPP_6_UNITS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 953.1508
2023 | nonsummer | HUMBPP_6_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 2436.4325
2023 | nonsummer | HUMBPP_6_UNITS | PLANT_MAINTENANCE | 406.75
2023 | nonsummer | HUMBPP_6_UNITS | PLANT_TROUBLE | 1688.2837
2023 | nonsummer | HUMBPP_6_UNITS | TRANSMISSION_INDUCED | 427.0875
2023 | nonsummer | HURON_6_SOLAR | PLANT_TROUBLE | 23
2023 | nonsummer | HURON_6_SOLAR | TRANSMISSION_INDUCED | 2216
2023 | nonsummer | HYTTHM_2_UNITS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 10666.5483
2023 | nonsummer | HYTTHM_2_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 7287.1583
2023 | nonsummer | HYTTHM_2_UNITS | OTHER_USE_LIMIT_REACHED | 36619.6583
2023 | nonsummer | HYTTHM_2_UNITS | PLANT_MAINTENANCE | 37299.105
2023 | nonsummer | HYTTHM_2_UNITS | PLANT_TROUBLE | 21195.9917
2023 | nonsummer | HYTTHM_2_UNITS | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | INDIGO_1_UNIT 1 | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | INDIGO_1_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 357.895
2023 | nonsummer | INDIGO_1_UNIT 1 | METERING_TELEMETRY | 0
2023 | nonsummer | INDIGO_1_UNIT 1 | PLANT_MAINTENANCE | 5662.5
2023 | nonsummer | INDIGO_1_UNIT 1 | PLANT_TROUBLE | 0
2023 | nonsummer | INDIGO_1_UNIT 1 | TRANSMISSION_INDUCED | 93
2023 | nonsummer | INDIGO_1_UNIT 2 | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | INDIGO_1_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 357.895
2023 | nonsummer | INDIGO_1_UNIT 2 | METERING_TELEMETRY | 0
2023 | nonsummer | INDIGO_1_UNIT 2 | PLANT_MAINTENANCE | 10192.5
2023 | nonsummer | INDIGO_1_UNIT 2 | PLANT_TROUBLE | 137.41
2023 | nonsummer | INDIGO_1_UNIT 2 | TRANSMISSION_INDUCED | 607.2733
2023 | nonsummer | INDIGO_1_UNIT 3 | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | INDIGO_1_UNIT 3 | AMBIENT_NOT_DUE_TO_TEMP | 396.3783
2023 | nonsummer | INDIGO_1_UNIT 3 | METERING_TELEMETRY | 0
2023 | nonsummer | INDIGO_1_UNIT 3 | PLANT_MAINTENANCE | 9036.595
2023 | nonsummer | INDIGO_1_UNIT 3 | PLANT_TROUBLE | 0
2023 | nonsummer | INDIGO_1_UNIT 3 | TRANSMISSION_INDUCED | 134.2733
2023 | nonsummer | INDVLY_1_UNITS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 2257.5
2023 | nonsummer | INDVLY_1_UNITS | TRANSMISSION_INDUCED | 0
2023 | nonsummer | INTKEP_2_UNITS | ENVIRONMENTAL_RESTRICTIONS | 81840.9833
2023 | nonsummer | INTKEP_2_UNITS | PLANT_MAINTENANCE | 39412.4667
2023 | nonsummer | INTKEP_2_UNITS | PLANT_TROUBLE | 6537.8167
2023 | nonsummer | INTKEP_2_UNITS | UNIT_TESTING | 0
2023 | nonsummer | INTMNT_3_ANAHEIM | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 109050
2023 | nonsummer | INTMNT_3_ANAHEIM | PLANT_MAINTENANCE | 4035
2023 | nonsummer | INTMNT_3_ANAHEIM | PLANT_TROUBLE | 0
2023 | nonsummer | INTMNT_3_ANAHEIM | UNIT_TESTING | 318
2023 | nonsummer | INTMNT_3_PASADENA | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2023 | nonsummer | INTMNT_3_PASADENA | PLANT_MAINTENANCE | 0
2023 | nonsummer | INTMNT_3_PASADENA | PLANT_TROUBLE | 0
2023 | nonsummer | INTMNT_3_PASADENA | TRANSMISSION_INDUCED | 5350
2023 | nonsummer | INTMNT_3_PASADENA | UNIT_TESTING | 0
2023 | nonsummer | INTMNT_3_RIVERSIDE | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 72171.68
2023 | nonsummer | INTMNT_3_RIVERSIDE | ENVIRONMENTAL_RESTRICTIONS | 16135
2023 | nonsummer | INTTRB_6_UNIT | TRANSMISSION_INDUCED | 118.9867
2023 | nonsummer | IVANPA_1_UNIT1 | AMBIENT_DUE_TO_TEMP | 252
2023 | nonsummer | IVANPA_1_UNIT1 | AMBIENT_NOT_DUE_TO_TEMP | 22609.2333
2023 | nonsummer | IVANPA_1_UNIT1 | ENVIRONMENTAL_RESTRICTIONS | 252
2023 | nonsummer | IVANPA_1_UNIT1 | PLANT_MAINTENANCE | 1270
2023 | nonsummer | IVANPA_1_UNIT1 | PLANT_TROUBLE | 8643.8833
2023 | nonsummer | IVANPA_1_UNIT2 | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | IVANPA_1_UNIT2 | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | IVANPA_1_UNIT2 | PLANT_MAINTENANCE | 24090
2023 | nonsummer | IVANPA_1_UNIT2 | PLANT_TROUBLE | 26835
2023 | nonsummer | IVANPA_1_UNIT3 | AMBIENT_DUE_TO_TEMP | 266
2023 | nonsummer | IVANPA_1_UNIT3 | AMBIENT_NOT_DUE_TO_TEMP | 12616.6833
2023 | nonsummer | IVANPA_1_UNIT3 | PLANT_MAINTENANCE | 38966.7833
2023 | nonsummer | IVANPA_1_UNIT3 | PLANT_TROUBLE | 2415
2023 | nonsummer | IVSLR2_2_SM2SR1 | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | nonsummer | IVSLR2_2_SM2SR1 | PLANT_MAINTENANCE | 150
2023 | nonsummer | IVSLR2_2_SM2SR1 | PLANT_TROUBLE | 0
2023 | nonsummer | IVSLR2_2_SM2SR1 | TRANSMISSION_INDUCED | 475
2023 | nonsummer | IVSLRP_2_SOLAR1 | METERING_TELEMETRY | 0
2023 | nonsummer | IVSLRP_2_SOLAR1 | PLANT_MAINTENANCE | 18300
2023 | nonsummer | IVSLRP_2_SOLAR1 | PLANT_TROUBLE | 5930
2023 | nonsummer | IVWEST_2_SOLAR1 | PLANT_MAINTENANCE | 1320
2023 | nonsummer | IVWEST_2_SOLAR1 | TRANSMISSION_INDUCED | 398
2023 | nonsummer | JACMSR_1_JACSR1 | METERING_TELEMETRY | 0
2023 | nonsummer | JACMSR_1_JACSR1 | PLANT_MAINTENANCE | 60
2023 | nonsummer | JACMSR_1_JACSR1 | PLANT_TROUBLE | 76
2023 | nonsummer | JACMSR_1_JACSR1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | JANCRK_6_RCABT1 | ENVIRONMENTAL_RESTRICTIONS | 8.75
2023 | nonsummer | JANCRK_6_RCABT1 | METERING_TELEMETRY | 0
2023 | nonsummer | JANCRK_6_RCABT1 | PLANT_MAINTENANCE | 1.75
2023 | nonsummer | JANCRK_6_RCABT1 | PLANT_TROUBLE | 68.2232
2023 | nonsummer | JANCRK_6_RCABT1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | JAVASR_1_JAVSR1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | JAVASR_1_JAVSR1 | PLANT_TROUBLE | 128.525
2023 | nonsummer | JAWBNE_2_NSRWND | AMBIENT_NOT_DUE_TO_TEMP | 258.15
2023 | nonsummer | JAWBNE_2_NSRWND | METERING_TELEMETRY | 379.6267
2023 | nonsummer | JAWBNE_2_NSRWND | PLANT_MAINTENANCE | 18070.4733
2023 | nonsummer | JAWBNE_2_NSRWND | PLANT_TROUBLE | 1489
2023 | nonsummer | JAWBNE_2_SRWND | METERING_TELEMETRY | 258.5667
2023 | nonsummer | JAWBNE_2_SRWND | PLANT_MAINTENANCE | 0
2023 | nonsummer | JAWBNE_2_SRWND | PLANT_TROUBLE | 8714.3333
2023 | nonsummer | JAWBNE_2_SRWWD2 | METERING_TELEMETRY | 0.35
2023 | nonsummer | JAWBNE_2_SRWWD2 | PLANT_MAINTENANCE | 0
2023 | nonsummer | JAWBNE_2_SRWWD2 | PLANT_TROUBLE | 7044.8117
2023 | nonsummer | JAYNE_6_WLSLR | AMBIENT_NOT_DUE_TO_TEMP | 105
2023 | nonsummer | JAYNE_6_WLSLR | METERING_TELEMETRY | 0
2023 | nonsummer | JAYNE_6_WLSLR | PLANT_MAINTENANCE | 62.4
2023 | nonsummer | JAYNE_6_WLSLR | PLANT_TROUBLE | 40
2023 | nonsummer | JOANEC_2_ST3BT3 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | JOANEC_2_ST3BT3 | PLANT_MAINTENANCE | 0
2023 | nonsummer | JOANEC_2_ST3BT3 | PLANT_TROUBLE | 2
2023 | nonsummer | JOANEC_2_STABT1 | PLANT_MAINTENANCE | 120
2023 | nonsummer | JOANEC_2_STABT1 | PLANT_TROUBLE | 110
2023 | nonsummer | JOANEC_2_STABT2 | PLANT_MAINTENANCE | 1.5
2023 | nonsummer | JOANEC_2_STABT2 | PLANT_TROUBLE | 7
2023 | nonsummer | JOHANN_2_JOSBT1 | METERING_TELEMETRY | 51.6667
2023 | nonsummer | JOHANN_2_JOSBT1 | PLANT_MAINTENANCE | 296.5
2023 | nonsummer | JOHANN_2_JOSBT1 | PLANT_TROUBLE | 351.7167
2023 | nonsummer | JOHANN_2_JOSBT1 | TRANSMISSION_INDUCED | 13.5
2023 | nonsummer | JOHANN_2_JOSBT2 | METERING_TELEMETRY | 4.3333
2023 | nonsummer | JOHANN_2_JOSBT2 | PLANT_MAINTENANCE | 102.1
2023 | nonsummer | JOHANN_2_JOSBT2 | PLANT_TROUBLE | 154.2667
2023 | nonsummer | JOHANN_2_JOSBT2 | TRANSMISSION_INDUCED | 13.5
2023 | nonsummer | JOHANN_2_OCEBT2 | METERING_TELEMETRY | 0
2023 | nonsummer | JOHANN_2_OCEBT2 | PLANT_MAINTENANCE | 182.9
2023 | nonsummer | JOHANN_2_OCEBT2 | PLANT_TROUBLE | 144.9333
2023 | nonsummer | JOHANN_2_OCEBT2 | RTU_RIG | 0
2023 | nonsummer | JOHANN_2_OCEBT2 | TRANSMISSION_INDUCED | 33
2023 | nonsummer | JOHANN_2_OCEBT2 | UNIT_TESTING | 59.55
2023 | nonsummer | JOHANN_2_OCEBT3 | METERING_TELEMETRY | 0
2023 | nonsummer | JOHANN_2_OCEBT3 | PLANT_MAINTENANCE | 120
2023 | nonsummer | JOHANN_2_OCEBT3 | PLANT_TROUBLE | 122.25
2023 | nonsummer | JOHANN_2_OCEBT3 | TRANSMISSION_INDUCED | 22
2023 | nonsummer | JOHANN_2_OCEBT3 | UNIT_TESTING | 30
2023 | nonsummer | JOHANN_2_T1BBT1 | PLANT_TROUBLE | 217
2023 | nonsummer | KANSAS_6_SOLAR | METERING_TELEMETRY | 75.3333
2023 | nonsummer | KANSAS_6_SOLAR | PLANT_MAINTENANCE | 110.3333
2023 | nonsummer | KANSAS_6_SOLAR | PLANT_TROUBLE | 436.8667
2023 | nonsummer | KANSAS_6_SOLAR | TRANSMISSION_INDUCED | 61.6667
2023 | nonsummer | KANSAS_6_SOLAR | UNIT_TESTING | 0
2023 | nonsummer | KEARNY_6_NESBT1 | METERING_TELEMETRY | 50
2023 | nonsummer | KEARNY_6_NESBT1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | KEARNY_6_NESBT1 | PLANT_TROUBLE | 50
2023 | nonsummer | KEARNY_6_SESBT2 | METERING_TELEMETRY | 50
2023 | nonsummer | KEARNY_6_SESBT2 | PLANT_MAINTENANCE | 0
2023 | nonsummer | KEARNY_6_SESBT2 | PLANT_TROUBLE | 15
2023 | nonsummer | KEKAWK_6_UNIT | PLANT_TROUBLE | 5802.5
2023 | nonsummer | KELSO_2_UNITS | AMBIENT_DUE_TO_TEMP | 3525.2768
2023 | nonsummer | KELSO_2_UNITS | ENVIRONMENTAL_RESTRICTIONS | 1605.6773
2023 | nonsummer | KELSO_2_UNITS | PLANT_MAINTENANCE | 3658.0822
2023 | nonsummer | KELSO_2_UNITS | PLANT_TROUBLE | 4063.1082
2023 | nonsummer | KELSO_2_UNITS | TRANSMISSION_INDUCED | 479.67
2023 | nonsummer | KELSO_2_UNITS | UNIT_TESTING | 9.26
2023 | nonsummer | KELYRG_6_UNIT | PLANT_TROUBLE | 1309.22
2023 | nonsummer | KELYRG_6_UNIT | TRANSMISSION_INDUCED | 11
2023 | nonsummer | KERKH2_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 32680.3652
2023 | nonsummer | KERKH2_7_UNIT 1 | ANNUAL_USE_LIMIT_REACHED | 0
2023 | nonsummer | KERKH2_7_UNIT 1 | PLANT_TROUBLE | 11884.64
2023 | nonsummer | KERKH2_7_UNIT 1 | TRANSITIONAL_LIMITATION | 0
2023 | nonsummer | KERKH2_7_UNIT 1 | TRANSMISSION_INDUCED | 39
2023 | nonsummer | KERMAN_6_SOLAR1 | PLANT_MAINTENANCE | 3.75
2023 | nonsummer | KERMAN_6_SOLAR1 | PLANT_TROUBLE | 483.75
2023 | nonsummer | KERMAN_6_SOLAR1 | TRANSMISSION_INDUCED | 2.25
2023 | nonsummer | KERMAN_6_SOLAR2 | PLANT_MAINTENANCE | 3.75
2023 | nonsummer | KERMAN_6_SOLAR2 | PLANT_TROUBLE | 810
2023 | nonsummer | KERNFT_1_UNITS | AMBIENT_DUE_TO_TEMP | 3078.7
2023 | nonsummer | KERNFT_1_UNITS | PLANT_MAINTENANCE | 132
2023 | nonsummer | KERNFT_1_UNITS | PLANT_TROUBLE | 1419.2
2023 | nonsummer | KERNFT_1_UNITS | UNIT_TESTING | 0
2023 | nonsummer | KERNRG_1_UNITS | PLANT_MAINTENANCE | 2399.4
2023 | nonsummer | KERNRG_1_UNITS | PLANT_TROUBLE | 390.0533
2023 | nonsummer | KERNRG_1_UNITS | TRANSMISSION_INDUCED | 0
2023 | nonsummer | KERRGN_1_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 4085.8
2023 | nonsummer | KERRGN_1_UNIT 1 | PLANT_MAINTENANCE | 887.5
2023 | nonsummer | KERRGN_1_UNIT 1 | PLANT_TROUBLE | 109.1667
2023 | nonsummer | KERRGN_1_UNIT 1 | TRANSMISSION_INDUCED | 99.3
2023 | nonsummer | KINGCO_1_KINGBR | PLANT_TROUBLE | 0
2023 | nonsummer | KINGCO_1_KINGBR | TRANSMISSION_INDUCED | 4472.925
2023 | nonsummer | KINGRV_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 2044.02
2023 | nonsummer | KINGRV_7_UNIT 1 | METERING_TELEMETRY | 0
2023 | nonsummer | KINGRV_7_UNIT 1 | PLANT_TROUBLE | 839.9633
2023 | nonsummer | KINGRV_7_UNIT 1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | KIRKER_7_KELCYN | PLANT_MAINTENANCE | 76.803
2023 | nonsummer | KIRKER_7_KELCYN | PLANT_TROUBLE | 259.3357
2023 | nonsummer | KIRKER_7_KELCYN | TRANSMISSION_INDUCED | 7.12
2023 | nonsummer | KNGBRD_2_SOLAR1 | METERING_TELEMETRY | 0
2023 | nonsummer | KNGBRD_2_SOLAR1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | KNGBRD_2_SOLAR1 | PLANT_TROUBLE | 192
2023 | nonsummer | KNGBRD_2_SOLAR2 | PLANT_TROUBLE | 85
2023 | nonsummer | KNGCTY_6_UNITA1 | PLANT_MAINTENANCE | 36.96
2023 | nonsummer | KNGCTY_6_UNITA1 | PLANT_TROUBLE | 1103.85
2023 | nonsummer | KNGCTY_6_UNITA1 | TRANSMISSION_INDUCED | 133.8
2023 | nonsummer | KNTSTH_6_SOLAR | PLANT_MAINTENANCE | 31.31
2023 | nonsummer | KNTSTH_6_SOLAR | PLANT_TROUBLE | 1614.7798
2023 | nonsummer | KNTSTH_6_WALSR1 | METERING_TELEMETRY | 0
2023 | nonsummer | KNTSTH_6_WALSR1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | KNTSTH_6_WALSR1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | KRAMER_1_R1BX3 | METERING_TELEMETRY | 0
2023 | nonsummer | KRAMER_1_R1BX3 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | KRAMER_1_R1BX3 | PLANT_MAINTENANCE | 310.05
2023 | nonsummer | KRAMER_1_R1BX3 | PLANT_TROUBLE | 723.3333
2023 | nonsummer | KRAMER_1_R1BX3 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | KRAMER_1_R1BX3 | UNIT_TESTING | 0
2023 | nonsummer | KRAMER_1_R1PX3 | METERING_TELEMETRY | 0
2023 | nonsummer | KRAMER_1_R1PX3 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | KRAMER_1_R1PX3 | PLANT_MAINTENANCE | 0
2023 | nonsummer | KRAMER_1_R1PX3 | PLANT_TROUBLE | 0
2023 | nonsummer | KRAMER_1_R1PX3 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | KRAMER_1_R2BX2 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | KRAMER_1_R2BX2 | PLANT_MAINTENANCE | 57.672
2023 | nonsummer | KRAMER_1_R2BX2 | PLANT_TROUBLE | 0
2023 | nonsummer | KRAMER_1_R2BX2 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | KRAMER_1_R2BX2 | UNIT_TESTING | 0
2023 | nonsummer | KRAMER_1_R2PX2 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | KRAMER_1_R2PX2 | PLANT_TROUBLE | 0
2023 | nonsummer | KRAMER_1_R2PX2 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | KRAMER_2_SEGS 9 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2023 | nonsummer | KRAMER_2_SEGS 9 | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | KRAMER_2_SEGS 9 | PLANT_TROUBLE | 2000
2023 | nonsummer | KRAMER_2_SEGS 9 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | KRNCNY_6_UNIT | PLANT_MAINTENANCE | 52.1167
2023 | nonsummer | KRNCNY_6_UNIT | PLANT_TROUBLE | 657.9067
2023 | nonsummer | KRNCNY_6_UNIT | TRANSMISSION_INDUCED | 53
2023 | nonsummer | KRNCNY_6_UNIT | UNIT_TESTING | 0
2023 | nonsummer | KYCORA_6_KMSBT1 | PLANT_MAINTENANCE | 1
2023 | nonsummer | KYCORA_6_KMSBT1 | PLANT_TROUBLE | 110.5583
2023 | nonsummer | KYCORA_6_KMSBT1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | LAKHDG_6_UNIT 1 | PLANT_MAINTENANCE | 6200
2023 | nonsummer | LAKHDG_6_UNIT 2 | PLANT_MAINTENANCE | 6200
2023 | nonsummer | LAMONT_1_SOLAR1 | PLANT_TROUBLE | 0
2023 | nonsummer | LAMONT_1_SOLAR1 | UNIT_TESTING | 0
2023 | nonsummer | LAMONT_1_SOLAR2 | PLANT_MAINTENANCE | 99.6667
2023 | nonsummer | LAMONT_1_SOLAR2 | PLANT_TROUBLE | 170.91
2023 | nonsummer | LAMONT_1_SOLAR3 | PLANT_TROUBLE | 1897.9887
2023 | nonsummer | LAMONT_1_SOLAR4 | PLANT_MAINTENANCE | 66.65
2023 | nonsummer | LAMONT_1_SOLAR4 | PLANT_TROUBLE | 1350.9953
2023 | nonsummer | LAMONT_1_SOLAR5 | PLANT_TROUBLE | 2464.646
2023 | nonsummer | LAPLMA_2_UNIT 1 | AMBIENT_DUE_TO_TEMP | 6347.8833
2023 | nonsummer | LAPLMA_2_UNIT 1 | PLANT_TROUBLE | 43808.65
2023 | nonsummer | LAPLMA_2_UNIT 1 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | LAPLMA_2_UNIT 1 | TRANSMISSION_INDUCED | 10097
2023 | nonsummer | LAPLMA_2_UNIT 1 | UNIT_TESTING | 6551.575
2023 | nonsummer | LAPLMA_2_UNIT 2 | AMBIENT_DUE_TO_TEMP | 9354
2023 | nonsummer | LAPLMA_2_UNIT 2 | PLANT_MAINTENANCE | 8778
2023 | nonsummer | LAPLMA_2_UNIT 2 | PLANT_TROUBLE | 12755.0667
2023 | nonsummer | LAPLMA_2_UNIT 2 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | LAPLMA_2_UNIT 2 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2023 | nonsummer | LAPLMA_2_UNIT 2 | TRANSMISSION_INDUCED | 1370
2023 | nonsummer | LAPLMA_2_UNIT 2 | UNIT_TESTING | 0
2023 | nonsummer | LAPLMA_2_UNIT 3 | AMBIENT_DUE_TO_TEMP | 9938
2023 | nonsummer | LAPLMA_2_UNIT 3 | PLANT_MAINTENANCE | 1516.75
2023 | nonsummer | LAPLMA_2_UNIT 3 | PLANT_TROUBLE | 15132.5783
2023 | nonsummer | LAPLMA_2_UNIT 3 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | LAPLMA_2_UNIT 3 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2023 | nonsummer | LAPLMA_2_UNIT 3 | TRANSMISSION_INDUCED | 10034
2023 | nonsummer | LAPLMA_2_UNIT 3 | UNIT_TESTING | 0
2023 | nonsummer | LAPLMA_2_UNIT 4 | AMBIENT_DUE_TO_TEMP | 10878
2023 | nonsummer | LAPLMA_2_UNIT 4 | PLANT_TROUBLE | 20600.4488
2023 | nonsummer | LAPLMA_2_UNIT 4 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2023 | nonsummer | LAPLMA_2_UNIT 4 | TRANSMISSION_INDUCED | 1292
2023 | nonsummer | LAPLMA_2_UNIT 4 | UNIT_TESTING | 1354.6
2023 | nonsummer | LARKSP_6_UNIT 1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 735
2023 | nonsummer | LARKSP_6_UNIT 1 | AMBIENT_DUE_TO_TEMP | 210
2023 | nonsummer | LARKSP_6_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | LARKSP_6_UNIT 1 | PLANT_MAINTENANCE | 4252.5
2023 | nonsummer | LARKSP_6_UNIT 1 | PLANT_TROUBLE | 542.9333
2023 | nonsummer | LARKSP_6_UNIT 1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | LARKSP_6_UNIT 2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 735
2023 | nonsummer | LARKSP_6_UNIT 2 | AMBIENT_DUE_TO_TEMP | 210
2023 | nonsummer | LARKSP_6_UNIT 2 | PLANT_MAINTENANCE | 7093.6833
2023 | nonsummer | LARKSP_6_UNIT 2 | PLANT_TROUBLE | 0
2023 | nonsummer | LARKSP_6_UNIT 2 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | LAROA2_2_UNITA1 | AMBIENT_DUE_TO_TEMP | 8971.0833
2023 | nonsummer | LAROA2_2_UNITA1 | PLANT_MAINTENANCE | 3000
2023 | nonsummer | LAROA2_2_UNITA1 | PLANT_TROUBLE | 10755.5
2023 | nonsummer | LAROA2_2_UNITA1 | UNIT_TESTING | 0
2023 | nonsummer | LASSEN_6_UNITS | PLANT_MAINTENANCE | 30
2023 | nonsummer | LASSEN_6_UNITS | PLANT_TROUBLE | 861.5
2023 | nonsummer | LASSEN_6_UNITS | TRANSMISSION_INDUCED | 13
2023 | nonsummer | LCKHT1_2_LH1SR1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2023 | nonsummer | LCKHT1_2_LH1SR1 | METERING_TELEMETRY | 0
2023 | nonsummer | LCKHT1_2_LH1SR1 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | LCKHT1_2_LH1SR1 | PLANT_MAINTENANCE | 1005.8333
2023 | nonsummer | LCKHT1_2_LH1SR1 | PLANT_TROUBLE | 0
2023 | nonsummer | LCKHT1_2_LH1SR1 | UNIT_TESTING | 0
2023 | nonsummer | LCKHT1_2_LH1SR2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2023 | nonsummer | LCKHT1_2_LH1SR2 | METERING_TELEMETRY | 0
2023 | nonsummer | LCKHT1_2_LH1SR2 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | LCKHT1_2_LH1SR2 | PLANT_TROUBLE | 0
2023 | nonsummer | LCKHT1_2_LH1SR2 | UNIT_TESTING | 0
2023 | nonsummer | LEBECS_2_UNITS | AMBIENT_DUE_TO_TEMP | 11222.0032
2023 | nonsummer | LEBECS_2_UNITS | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | nonsummer | LEBECS_2_UNITS | METERING_TELEMETRY | 195.2667
2023 | nonsummer | LEBECS_2_UNITS | PLANT_MAINTENANCE | 31405.38
2023 | nonsummer | LEBECS_2_UNITS | PLANT_TROUBLE | 35285.4485
2023 | nonsummer | LEBECS_2_UNITS | TRANSITIONAL_LIMITATION | 3460.7418
2023 | nonsummer | LEBECS_2_UNITS | TRANSMISSION_INDUCED | 0
2023 | nonsummer | LECEF_1_UNITS | AMBIENT_DUE_TO_TEMP | 9229.4867
2023 | nonsummer | LECEF_1_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | LECEF_1_UNITS | PLANT_MAINTENANCE | 831.2
2023 | nonsummer | LECEF_1_UNITS | PLANT_TROUBLE | 2283.1467
2023 | nonsummer | LECEF_1_UNITS | TRANSITIONAL_LIMITATION | 0
2023 | nonsummer | LECONT_2_LESBT1 | PLANT_MAINTENANCE | 1184.4333
2023 | nonsummer | LECONT_2_LESBT1 | PLANT_TROUBLE | 1802.7833
2023 | nonsummer | LECONT_2_LESBT1 | TRANSMISSION_INDUCED | 437.5
2023 | nonsummer | LECONT_2_LESBT1 | UNIT_TESTING | 0
2023 | nonsummer | LEPRFD_1_KANSAS | PLANT_TROUBLE | 553.1058
2023 | nonsummer | LGHTHP_6_ICEGEN | PLANT_MAINTENANCE | 15019.98
2023 | nonsummer | LGHTHP_6_ICEGEN | PLANT_TROUBLE | 0
2023 | nonsummer | LGHTHP_6_ICEGEN | TRANSMISSION_INDUCED | 0
2023 | nonsummer | LGHTHP_6_ICEGEN | UNIT_TESTING | 0
2023 | nonsummer | LHILLS_6_SOLAR1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | LHILLS_6_SOLAR1 | METERING_TELEMETRY | 0
2023 | nonsummer | LHILLS_6_SOLAR1 | PLANT_TROUBLE | 384
2023 | nonsummer | LHILLS_6_SOLAR1 | TRANSMISSION_INDUCED | 292
2023 | nonsummer | LILIAC_6_SOLAR | PLANT_TROUBLE | 3
2023 | nonsummer | LITLRK_6_GBCSR1 | PLANT_TROUBLE | 37.5
2023 | nonsummer | LITLRK_6_GBCSR1 | TRANSMISSION_INDUCED | 6
2023 | nonsummer | LITLRK_6_SOLAR1 | METERING_TELEMETRY | 25
2023 | nonsummer | LITLRK_6_SOLAR1 | PLANT_TROUBLE | 1342.7833
2023 | nonsummer | LITLRK_6_SOLAR1 | TRANSMISSION_INDUCED | 6
2023 | nonsummer | LITLRK_6_SOLAR2 | METERING_TELEMETRY | 1
2023 | nonsummer | LITLRK_6_SOLAR2 | PLANT_MAINTENANCE | 0
2023 | nonsummer | LITLRK_6_SOLAR2 | PLANT_TROUBLE | 162.2167
2023 | nonsummer | LIVOAK_1_UNIT 1 | AMBIENT_DUE_TO_TEMP | 4488.9
2023 | nonsummer | LIVOAK_1_UNIT 1 | PLANT_MAINTENANCE | 226
2023 | nonsummer | LIVOAK_1_UNIT 1 | PLANT_TROUBLE | 5829.705
2023 | nonsummer | LIVOAK_1_UNIT 1 | UNIT_TESTING | 13.6
2023 | nonsummer | LMBEPK_2_UNITA1 | PLANT_TROUBLE | 1077
2023 | nonsummer | LMBEPK_2_UNITA1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | LMBEPK_2_UNITA1 | UNIT_TESTING | 95
2023 | nonsummer | LMBEPK_2_UNITA2 | AMBIENT_DUE_TO_TEMP | 6.11
2023 | nonsummer | LMBEPK_2_UNITA2 | PLANT_TROUBLE | 1920.66
2023 | nonsummer | LMBEPK_2_UNITA2 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | LMBEPK_2_UNITA2 | UNIT_TESTING | 95.2
2023 | nonsummer | LMBEPK_2_UNITA3 | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | LMBEPK_2_UNITA3 | PLANT_TROUBLE | 218.0583
2023 | nonsummer | LMBEPK_2_UNITA3 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | LMBEPK_2_UNITA3 | UNIT_TESTING | 0
2023 | nonsummer | LMEC_1_PL1X3 | AMBIENT_DUE_TO_TEMP | 14463.59
2023 | nonsummer | LMEC_1_PL1X3 | PLANT_MAINTENANCE | 1525
2023 | nonsummer | LMEC_1_PL1X3 | PLANT_TROUBLE | 75603.5
2023 | nonsummer | LMEC_1_PL1X3 | TRANSITIONAL_LIMITATION | 0
2023 | nonsummer | LMEC_1_PL1X3 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | LMEC_1_PL1X3 | UNIT_TESTING | 0
2023 | nonsummer | LOCKFD_1_KSOLAR | PLANT_MAINTENANCE | 0
2023 | nonsummer | LODI25_2_UNIT 1 | AMBIENT_DUE_TO_TEMP | 1519
2023 | nonsummer | LODI25_2_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | LODI25_2_UNIT 1 | METERING_TELEMETRY | 0
2023 | nonsummer | LODI25_2_UNIT 1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | LODI25_2_UNIT 1 | PLANT_TROUBLE | 3318
2023 | nonsummer | LODIEC_2_PL1X2 | AMBIENT_DUE_TO_TEMP | 16795.9
2023 | nonsummer | LODIEC_2_PL1X2 | PLANT_MAINTENANCE | 0
2023 | nonsummer | LODIEC_2_PL1X2 | PLANT_TROUBLE | 19208
2023 | nonsummer | LODIEC_2_PL1X2 | UNIT_TESTING | 0
2023 | nonsummer | LOTUS_6_LSFSR1 | PLANT_TROUBLE | 298.3333
2023 | nonsummer | LOTUS_6_LSFSR1 | TRANSMISSION_INDUCED | 149.1667
2023 | nonsummer | LOWGAP_1_SUPHR | AMBIENT_NOT_DUE_TO_TEMP | 59.928
2023 | nonsummer | LOWGAP_1_SUPHR | PLANT_TROUBLE | 94.05
2023 | nonsummer | LOWGAP_1_SUPHR | TRANSMISSION_INDUCED | 29.7
2023 | nonsummer | LOWGAP_7_QFUNTS | ENVIRONMENTAL_RESTRICTIONS | 93.1
2023 | nonsummer | LOWGAP_7_QFUNTS | PLANT_TROUBLE | 59.9
2023 | nonsummer | LOWGAP_7_QFUNTS | TRANSMISSION_INDUCED | 556.35
2023 | nonsummer | LTBEAR_1_LB3SR3 | PLANT_MAINTENANCE | 39.3333
2023 | nonsummer | LTBEAR_1_LB3SR3 | PLANT_TROUBLE | 0
2023 | nonsummer | LTBEAR_1_LB3SR3 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | LTBEAR_1_LB4SR4 | METERING_TELEMETRY | 0
2023 | nonsummer | LTBEAR_1_LB4SR4 | PLANT_MAINTENANCE | 124.3917
2023 | nonsummer | LTBEAR_1_LB4SR4 | PLANT_TROUBLE | 62.4833
2023 | nonsummer | LTBEAR_1_LB4SR4 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | LTBEAR_1_LB4SR5 | PLANT_MAINTENANCE | 98.3333
2023 | nonsummer | LTBEAR_1_LB4SR5 | PLANT_TROUBLE | 500
2023 | nonsummer | LTBEAR_1_LB4SR5 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | LTBERA_1_LB1SR1 | PLANT_MAINTENANCE | 78.6667
2023 | nonsummer | LTBERA_1_LB1SR1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | MAGNLA_6_ANAHEIM | AMBIENT_DUE_TO_TEMP | 84
2023 | nonsummer | MAGNLA_6_ANAHEIM | PLANT_MAINTENANCE | 4625
2023 | nonsummer | MAGNLA_6_ANAHEIM | PLANT_TROUBLE | 327
2023 | nonsummer | MAGNLA_6_ANAHEIM | TRANSMISSION_INDUCED | 273
2023 | nonsummer | MAGNLA_6_ANAHEIM | UNIT_TESTING | 51
2023 | nonsummer | MAGNLA_6_CERRITOS | PLANT_MAINTENANCE | 156
2023 | nonsummer | MAGNLA_6_CERRITOS | PLANT_TROUBLE | 20
2023 | nonsummer | MAGNLA_6_CERRITOS | TRANSMISSION_INDUCED | 1510.6
2023 | nonsummer | MAGNLA_6_COLTON | PLANT_MAINTENANCE | 423
2023 | nonsummer | MAGNLA_6_COLTON | PLANT_TROUBLE | 20
2023 | nonsummer | MAGNLA_6_COLTON | TRANSMISSION_INDUCED | 2090
2023 | nonsummer | MAGNLA_6_PASADENA | AMBIENT_NOT_DUE_TO_TEMP | 42
2023 | nonsummer | MAGNLA_6_PASADENA | METERING_TELEMETRY | 1.6
2023 | nonsummer | MAGNLA_6_PASADENA | PLANT_MAINTENANCE | 450
2023 | nonsummer | MAGNLA_6_PASADENA | PLANT_TROUBLE | 57.3
2023 | nonsummer | MAGUND_1_BKISR1 | PLANT_TROUBLE | 0
2023 | nonsummer | MAGUND_1_BKISR1 | TRANSMISSION_INDUCED | 5
2023 | nonsummer | MAGUND_1_BKSSR2 | PLANT_TROUBLE | 780.5417
2023 | nonsummer | MAGUND_1_BKSSR2 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | MALAGA_1_PL1X2 | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | MALAGA_1_PL1X2 | METERING_TELEMETRY | 0
2023 | nonsummer | MALAGA_1_PL1X2 | PLANT_MAINTENANCE | 32.2033
2023 | nonsummer | MALAGA_1_PL1X2 | PLANT_TROUBLE | 578.0498
2023 | nonsummer | MALAGA_1_PL1X2 | TRANSMISSION_INDUCED | 12076.25
2023 | nonsummer | MALCHQ_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 230
2023 | nonsummer | MALCHQ_7_UNIT 1 | METERING_TELEMETRY | 0
2023 | nonsummer | MANTEC_1_ML1SR1 | METERING_TELEMETRY | 45
2023 | nonsummer | MANTEC_1_ML1SR1 | PLANT_TROUBLE | 160
2023 | nonsummer | MANZNA_2_WIND | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | MANZNA_2_WIND | PLANT_MAINTENANCE | 775.7833
2023 | nonsummer | MANZNA_2_WIND | PLANT_TROUBLE | 2780.125
2023 | nonsummer | MARCPW_6_SOLAR1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | MARCPW_6_SOLAR1 | PLANT_TROUBLE | 5269
2023 | nonsummer | MARCPW_6_SOLAR1 | TRANSMISSION_INDUCED | 1201.3333
2023 | nonsummer | MCARTH_6_FRIVRB | PLANT_TROUBLE | 0
2023 | nonsummer | MCARTH_6_FRIVRB | TRANSMISSION_INDUCED | 0
2023 | nonsummer | MCFLND_5_MFSBT1 | PLANT_TROUBLE | 133.825
2023 | nonsummer | MCFLND_5_MFSBT1 | UNIT_TESTING | 0
2023 | nonsummer | MCFLND_5_MFSSR1 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | MCFLND_5_MFSSR1 | PLANT_TROUBLE | 495
2023 | nonsummer | MCFLND_5_MSBBX2 | NEW_GENERATOR_TEST_ENERGY | 9690
2023 | nonsummer | MCFLND_5_MSBSX2 | NEW_GENERATOR_TEST_ENERGY | 41180
2023 | nonsummer | MCSWAN_6_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | MCSWAN_6_UNITS | PLANT_MAINTENANCE | 180
2023 | nonsummer | MCSWAN_6_UNITS | PLANT_TROUBLE | 0
2023 | nonsummer | MDFKRL_2_PROJCT | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 51.6667
2023 | nonsummer | MDFKRL_2_PROJCT | AMBIENT_NOT_DUE_TO_TEMP | 7990.8333
2023 | nonsummer | MDFKRL_2_PROJCT | PLANT_MAINTENANCE | 0
2023 | nonsummer | MDFKRL_2_PROJCT | PLANT_TROUBLE | 18556.2833
2023 | nonsummer | MDFKRL_2_PROJCT | RTU_RIG | 0
2023 | nonsummer | MDFKRL_2_PROJCT | TRANSMISSION_INDUCED | 38937.5
2023 | nonsummer | MDFKRL_2_PROJCT | UNIT_TESTING | 420
2023 | nonsummer | MENBIO_6_RENEW1 | METERING_TELEMETRY | 0
2023 | nonsummer | MENBIO_6_RENEW1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | MENBIO_6_RENEW1 | PLANT_TROUBLE | 75
2023 | nonsummer | MENBIO_6_RENEW1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | MERCED_1_SOLAR1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | MERCED_1_SOLAR2 | PLANT_MAINTENANCE | 0
2023 | nonsummer | MERCFL_6_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 596.15
2023 | nonsummer | MERCFL_6_UNIT | PLANT_MAINTENANCE | 206.4417
2023 | nonsummer | MERCFL_6_UNIT | PLANT_TROUBLE | 17.5
2023 | nonsummer | METEC_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 10239.5817
2023 | nonsummer | METEC_2_PL1X3 | PLANT_MAINTENANCE | 30.5
2023 | nonsummer | METEC_2_PL1X3 | PLANT_TROUBLE | 200776.1748
2023 | nonsummer | METEC_2_PL1X3 | TRANSITIONAL_LIMITATION | 183
2023 | nonsummer | METEC_2_PL1X3 | UNIT_TESTING | 127.635
2023 | nonsummer | MIDWD_2_WIND2 | METERING_TELEMETRY | 143
2023 | nonsummer | MIDWD_2_WIND2 | PLANT_MAINTENANCE | 3.75
2023 | nonsummer | MIDWD_2_WIND2 | PLANT_TROUBLE | 87
2023 | nonsummer | MIDWD_7_CORAMB | AMBIENT_DUE_TO_TEMP | 290
2023 | nonsummer | MIDWD_7_CORAMB | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | nonsummer | MIDWD_7_CORAMB | METERING_TELEMETRY | 0
2023 | nonsummer | MIDWD_7_CORAMB | PLANT_MAINTENANCE | 0
2023 | nonsummer | MIDWD_7_CORAMB | PLANT_TROUBLE | 20
2023 | nonsummer | MIDWD_7_CORAMB | TRANSMISSION_INDUCED | 21.975
2023 | nonsummer | MIDWY3_2_MDSSR1 | PLANT_MAINTENANCE | 4
2023 | nonsummer | MIDWY3_2_MDSSR1 | PLANT_TROUBLE | 329.75
2023 | nonsummer | MIDWY3_2_MDSSR1 | TRANSMISSION_INDUCED | 1422
2023 | nonsummer | MIDWYS_2_MIDSL1 | AMBIENT_NOT_DUE_TO_TEMP | 865
2023 | nonsummer | MIDWYS_2_MIDSL1 | PLANT_MAINTENANCE | 351.2
2023 | nonsummer | MIDWYS_2_MIDSL1 | PLANT_TROUBLE | 293
2023 | nonsummer | MIDWYS_2_MIDSL1 | TRANSMISSION_INDUCED | 15.9
2023 | nonsummer | MIRLOM_2_CORONA | PLANT_TROUBLE | 0
2023 | nonsummer | MIRLOM_2_CREST | PLANT_MAINTENANCE | 0
2023 | nonsummer | MIRLOM_2_MLBBTA | PLANT_MAINTENANCE | 20
2023 | nonsummer | MIRLOM_2_MLBBTA | PLANT_TROUBLE | 27.8333
2023 | nonsummer | MIRLOM_2_MLBBTA | RTU_RIG | 0
2023 | nonsummer | MIRLOM_2_MLBBTA | TRANSMISSION_INDUCED | 0
2023 | nonsummer | MIRLOM_2_MLBBTA | UNIT_TESTING | 0
2023 | nonsummer | MIRLOM_2_MLBBTB | PLANT_MAINTENANCE | 16
2023 | nonsummer | MIRLOM_2_MLBBTB | PLANT_TROUBLE | 267.9667
2023 | nonsummer | MIRLOM_2_MLBBTB | RTU_RIG | 0
2023 | nonsummer | MIRLOM_2_MLBBTB | TRANSMISSION_INDUCED | 0
2023 | nonsummer | MIRLOM_2_MLBBTB | UNIT_TESTING | 0
2023 | nonsummer | MIRLOM_2_ONTARO | METERING_TELEMETRY | 165
2023 | nonsummer | MIRLOM_2_ONTARO | PLANT_TROUBLE | 3960
2023 | nonsummer | MIRLOM_2_RTS032 | PLANT_TROUBLE | 307.5
2023 | nonsummer | MIRLOM_2_RTS033 | PLANT_TROUBLE | 205
2023 | nonsummer | MIRLOM_2_TEMESC | PLANT_TROUBLE | 41.61
2023 | nonsummer | MIRLOM_6_PEAKER | AMBIENT_DUE_TO_TEMP | 559.08
2023 | nonsummer | MIRLOM_6_PEAKER | PLANT_MAINTENANCE | 0
2023 | nonsummer | MIRLOM_6_PEAKER | PLANT_TROUBLE | 416.6633
2023 | nonsummer | MIRLOM_6_PEAKER | SHORT_TERM_USE_LIMIT_REACHED | 220.57
2023 | nonsummer | MIRLOM_7_MWDLKM | PLANT_MAINTENANCE | 25
2023 | nonsummer | MIRLOM_7_MWDLKM | PLANT_TROUBLE | 2702.8333
2023 | nonsummer | MKTRCK_1_UNIT 1 | AMBIENT_DUE_TO_TEMP | 2118.98
2023 | nonsummer | MKTRCK_1_UNIT 1 | PLANT_TROUBLE | 2630.55
2023 | nonsummer | MKTRCK_1_UNIT 1 | UNIT_TESTING | 12.6
2023 | nonsummer | MNDALY_6_MCGRTH | AMBIENT_DUE_TO_TEMP | 2402.91
2023 | nonsummer | MNDALY_6_MCGRTH | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | MNDALY_6_MCGRTH | METERING_TELEMETRY | 0
2023 | nonsummer | MNDALY_6_MCGRTH | PLANT_MAINTENANCE | 0
2023 | nonsummer | MNDALY_6_MCGRTH | PLANT_TROUBLE | 104.0377
2023 | nonsummer | MNDALY_6_MCGRTH | TRANSMISSION_INDUCED | 0
2023 | nonsummer | MNDOTA_1_SOLAR1 | METERING_TELEMETRY | 179
2023 | nonsummer | MNDOTA_1_SOLAR1 | PLANT_MAINTENANCE | 179
2023 | nonsummer | MNDOTA_1_SOLAR1 | PLANT_TROUBLE | 0
2023 | nonsummer | MNDOTA_1_SOLAR1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | MNDOTA_1_SOLAR2 | METERING_TELEMETRY | 100
2023 | nonsummer | MNDOTA_1_SOLAR2 | PLANT_MAINTENANCE | 10
2023 | nonsummer | MNDOTA_1_SOLAR2 | PLANT_TROUBLE | 276.25
2023 | nonsummer | MOJAVE_1_SIPHON | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | nonsummer | MOJAVE_1_SIPHON | PLANT_MAINTENANCE | 0
2023 | nonsummer | MOJAVE_1_SIPHON | PLANT_TROUBLE | 275.2993
2023 | nonsummer | MOJAVE_1_SIPHON | TRANSMISSION_INDUCED | 110.3327
2023 | nonsummer | MOJAVW_2_SOLAR | PLANT_MAINTENANCE | 0
2023 | nonsummer | MOJAVW_2_SOLAR | PLANT_TROUBLE | 101.1667
2023 | nonsummer | MONTPH_7_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 4991.45
2023 | nonsummer | MONTPH_7_UNITS | PLANT_MAINTENANCE | 0
2023 | nonsummer | MONTPH_7_UNITS | PLANT_TROUBLE | 0
2023 | nonsummer | MOORPK_2_ACOBT1 | METERING_TELEMETRY | 5.59
2023 | nonsummer | MOORPK_2_ACOBT1 | PLANT_MAINTENANCE | 29.25
2023 | nonsummer | MOORPK_2_ACOBT1 | PLANT_TROUBLE | 0
2023 | nonsummer | MOORPK_2_ACOBT1 | RTU_RIG | 0
2023 | nonsummer | MOORPK_2_CALABS | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | MOORPK_2_CALABS | PLANT_MAINTENANCE | 4.8
2023 | nonsummer | MOORPK_2_CALABS | PLANT_TROUBLE | 299.5985
2023 | nonsummer | MORWD_6_QF | PLANT_TROUBLE | 0
2023 | nonsummer | MORWD_6_QF | TRANSMISSION_INDUCED | 6.09
2023 | nonsummer | MOSSLD_2_PSP1 | AMBIENT_DUE_TO_TEMP | 324.1333
2023 | nonsummer | MOSSLD_2_PSP1 | ENVIRONMENTAL_RESTRICTIONS | 260
2023 | nonsummer | MOSSLD_2_PSP1 | PLANT_MAINTENANCE | 5100
2023 | nonsummer | MOSSLD_2_PSP1 | PLANT_TROUBLE | 3275.0333
2023 | nonsummer | MOSSLD_2_PSP1 | UNIT_TESTING | 0
2023 | nonsummer | MOSSLD_2_PSP2 | AMBIENT_DUE_TO_TEMP | 504.9333
2023 | nonsummer | MOSSLD_2_PSP2 | ENVIRONMENTAL_RESTRICTIONS | 368.3333
2023 | nonsummer | MOSSLD_2_PSP2 | PLANT_MAINTENANCE | 0
2023 | nonsummer | MOSSLD_2_PSP2 | PLANT_TROUBLE | 9575.1667
2023 | nonsummer | MRCHNT_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 26471.7667
2023 | nonsummer | MRCHNT_2_PL1X3 | PLANT_MAINTENANCE | 0
2023 | nonsummer | MRCHNT_2_PL1X3 | PLANT_TROUBLE | 6714.2167
2023 | nonsummer | MRGT_6_MEF2 | PLANT_TROUBLE | 619.6667
2023 | nonsummer | MRGT_6_MEF2 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | MRGT_6_MMAREF | PLANT_TROUBLE | 932.25
2023 | nonsummer | MRGT_6_MMAREF | TRANSMISSION_INDUCED | 0
2023 | nonsummer | MRGT_6_TGEBT1 | METERING_TELEMETRY | 0
2023 | nonsummer | MRGT_6_TGEBT1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | MRGT_6_TGEBT1 | PLANT_TROUBLE | 3262.9917
2023 | nonsummer | MRGT_6_TGEBT1 | TRANSMISSION_INDUCED | 105
2023 | nonsummer | MRLSDS_6_SOLAR1 | METERING_TELEMETRY | 0
2023 | nonsummer | MRLSDS_6_SOLAR1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | MRLSDS_6_SOLAR1 | PLANT_TROUBLE | 890.1572
2023 | nonsummer | MRLSDS_6_SOLAR1 | TRANSMISSION_INDUCED | 300
2023 | nonsummer | MSOLAR_2_SOLAR1 | PLANT_MAINTENANCE | 1155
2023 | nonsummer | MSOLAR_2_SOLAR1 | PLANT_TROUBLE | 135
2023 | nonsummer | MSOLAR_2_SOLAR2 | METERING_TELEMETRY | 302.43
2023 | nonsummer | MSOLAR_2_SOLAR2 | PLANT_MAINTENANCE | 2318.63
2023 | nonsummer | MSOLAR_2_SOLAR2 | PLANT_TROUBLE | 56.1
2023 | nonsummer | MSOLAR_2_SOLAR3 | PLANT_MAINTENANCE | 2128
2023 | nonsummer | MSOLAR_2_SOLAR3 | PLANT_TROUBLE | 22.2
2023 | nonsummer | MSOLAR_2_SOLAR3 | UNIT_TESTING | 1292
2023 | nonsummer | MSTANG_2_MTGBT1 | PLANT_MAINTENANCE | 1845
2023 | nonsummer | MSTANG_2_MTGBT1 | PLANT_TROUBLE | 6774.5092
2023 | nonsummer | MSTANG_2_SOLAR | PLANT_MAINTENANCE | 11075.28
2023 | nonsummer | MSTANG_2_SOLAR | PLANT_TROUBLE | 9429
2023 | nonsummer | MSTANG_2_SOLAR3 | PLANT_MAINTENANCE | 1323.171
2023 | nonsummer | MSTANG_2_SOLAR3 | PLANT_TROUBLE | 1302.6433
2023 | nonsummer | MSTANG_2_SOLAR4 | PLANT_MAINTENANCE | 1034.6007
2023 | nonsummer | MSTANG_2_SOLAR4 | PLANT_TROUBLE | 2014.1167
2023 | nonsummer | MTNPOS_1_UNIT | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 190.754
2023 | nonsummer | MTNPOS_1_UNIT | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | MTNPOS_1_UNIT | PLANT_MAINTENANCE | 7424.3107
2023 | nonsummer | MTNPOS_1_UNIT | PLANT_TROUBLE | 4787.8893
2023 | nonsummer | MTNPOS_1_UNIT | TRANSMISSION_INDUCED | 20.988
2023 | nonsummer | MTNPOS_1_UNIT | UNIT_TESTING | 2.7733
2023 | nonsummer | MTWIND_1_MVPWD1 | PLANT_TROUBLE | 1247.1433
2023 | nonsummer | MTWIND_1_MVPWD1 | TRANSMISSION_INDUCED | 2013.104
2023 | nonsummer | MTWIND_1_UNIT 3 | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | MTWIND_1_UNIT 3 | AMBIENT_NOT_DUE_TO_TEMP | 17.2573
2023 | nonsummer | MTWIND_1_UNIT 3 | ENVIRONMENTAL_RESTRICTIONS | 11.336
2023 | nonsummer | MTWIND_1_UNIT 3 | PLANT_MAINTENANCE | 0
2023 | nonsummer | MTWIND_1_UNIT 3 | PLANT_TROUBLE | 32.612
2023 | nonsummer | MTWIND_1_UNIT 3 | RTU_RIG | 9.9
2023 | nonsummer | MTWIND_1_UNIT 3 | TRANSMISSION_INDUCED | 769.306
2023 | nonsummer | MURRAY_6_UNIT | PLANT_MAINTENANCE | 57.68
2023 | nonsummer | MURRAY_6_UNIT | PLANT_TROUBLE | 78.1427
2023 | nonsummer | NAROW1_2_UNIT | ENVIRONMENTAL_RESTRICTIONS | 1725.0383
2023 | nonsummer | NAROW1_2_UNIT | PLANT_MAINTENANCE | 15.6
2023 | nonsummer | NAROW1_2_UNIT | PLANT_TROUBLE | 1707
2023 | nonsummer | NAROW1_2_UNIT | TRANSMISSION_INDUCED | 0
2023 | nonsummer | NAROW2_2_UNIT | ENVIRONMENTAL_RESTRICTIONS | 22025.47
2023 | nonsummer | NAROW2_2_UNIT | PLANT_TROUBLE | 46.89
2023 | nonsummer | NAROW2_2_UNIT | TRANSMISSION_INDUCED | 1194.4167
2023 | nonsummer | NAVYII_2_UNITS | PLANT_TROUBLE | 2550
2023 | nonsummer | NAVYII_2_UNITS | TRANSMISSION_INDUCED | 450
2023 | nonsummer | NCPA_7_GP1UN1 | PLANT_MAINTENANCE | 26592.825
2023 | nonsummer | NCPA_7_GP1UN1 | TRANSMISSION_INDUCED | 19.425
2023 | nonsummer | NCPA_7_GP1UN2 | PLANT_MAINTENANCE | 2376.43
2023 | nonsummer | NCPA_7_GP1UN2 | PLANT_TROUBLE | 3780.6907
2023 | nonsummer | NCPA_7_GP1UN2 | TRANSMISSION_INDUCED | 19.97
2023 | nonsummer | NCPA_7_GP2UN3 | AMBIENT_NOT_DUE_TO_TEMP | 44541
2023 | nonsummer | NCPA_7_GP2UN4 | PLANT_MAINTENANCE | 0
2023 | nonsummer | NCPA_7_GP2UN4 | PLANT_TROUBLE | 6809.3915
2023 | nonsummer | NEENCH_6_SOLAR | PLANT_MAINTENANCE | 0
2023 | nonsummer | NEENCH_6_SOLAR | PLANT_TROUBLE | 0
2023 | nonsummer | NGILAA_5_SDGDYN | AMBIENT_DUE_TO_TEMP | 1749.95
2023 | nonsummer | NGILAA_5_SDGDYN | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | nonsummer | NGILAA_5_SDGDYN | PLANT_MAINTENANCE | 2329
2023 | nonsummer | NGILAA_5_SDGDYN | PLANT_TROUBLE | 594
2023 | nonsummer | NGILAA_5_SDGDYN | TRANSMISSION_INDUCED | 290
2023 | nonsummer | NGILAA_5_SDGDYN | UNIT_TESTING | 76.075
2023 | nonsummer | NHOGAN_6_UNITS | TRANSMISSION_INDUCED | 88
2023 | nonsummer | NORCNV_1_NCVBT1 | METERING_TELEMETRY | 0
2023 | nonsummer | NORCNV_1_NCVBT1 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | NORCNV_1_NCVBT1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | NORCNV_1_NCVBT1 | PLANT_TROUBLE | 17.9
2023 | nonsummer | NORCNV_1_NCVBT1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | NOVATO_6_LNDFL | PLANT_TROUBLE | 19.5
2023 | nonsummer | NOVATO_6_LNDFL | TRANSMISSION_INDUCED | 565.5
2023 | nonsummer | NWCSTL_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 4740.0167
2023 | nonsummer | NWCSTL_7_UNIT 1 | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | nonsummer | NWCSTL_7_UNIT 1 | PLANT_TROUBLE | 1196.6
2023 | nonsummer | NWCSTL_7_UNIT 1 | TRANSMISSION_INDUCED | 4.4
2023 | nonsummer | NZWIND_2_WDSTR5 | PLANT_MAINTENANCE | 0
2023 | nonsummer | NZWIND_2_WDSTR5 | PLANT_TROUBLE | 63.1
2023 | nonsummer | NZWIND_2_WDSTR5 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | NZWIND_6_CALWND | PLANT_MAINTENANCE | 0
2023 | nonsummer | NZWIND_6_CALWND | TRANSMISSION_INDUCED | 45
2023 | nonsummer | NZWIND_6_WDSTR | TRANSMISSION_INDUCED | 0
2023 | nonsummer | NZWIND_6_WDSTR2 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | NZWIND_6_WDSTR3 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | NZWIND_6_WDSTR4 | PLANT_MAINTENANCE | 0
2023 | nonsummer | NZWIND_6_WDSTR4 | PLANT_TROUBLE | 34.8655
2023 | nonsummer | OAK C_7_UNIT 1 | PLANT_MAINTENANCE | 1010.25
2023 | nonsummer | OAK C_7_UNIT 1 | PLANT_TROUBLE | 30283.4
2023 | nonsummer | OAK C_7_UNIT 1 | TRANSMISSION_INDUCED | 27
2023 | nonsummer | OAK C_7_UNIT 3 | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | nonsummer | OAK C_7_UNIT 3 | PLANT_MAINTENANCE | 531
2023 | nonsummer | OAK C_7_UNIT 3 | PLANT_TROUBLE | 7224.15
2023 | nonsummer | OAK C_7_UNIT 3 | UNIT_TESTING | 36
2023 | nonsummer | OAK L_1_GTG1 | PLANT_MAINTENANCE | 23
2023 | nonsummer | OAK L_1_GTG1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | OAKWD_6_QF | METERING_TELEMETRY | 0
2023 | nonsummer | OAKWD_6_QF | PLANT_TROUBLE | 559.0567
2023 | nonsummer | OAKWD_6_QF | TRANSMISSION_INDUCED | 0
2023 | nonsummer | OAKWD_6_ZEPHWD | TRANSMISSION_INDUCED | 0
2023 | nonsummer | OASIS_6_AR4SR3 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2023 | nonsummer | OASIS_6_CREST | PLANT_TROUBLE | 90
2023 | nonsummer | OASIS_6_CREST | RTU_RIG | 20
2023 | nonsummer | OASIS_6_GBDSR4 | PLANT_TROUBLE | 6
2023 | nonsummer | OASIS_6_LPPSR1 | METERING_TELEMETRY | 30
2023 | nonsummer | OASIS_6_LPPSR1 | PLANT_MAINTENANCE | 23.5
2023 | nonsummer | OASIS_6_LPPSR1 | PLANT_TROUBLE | 0
2023 | nonsummer | OASIS_6_SOLAR1 | PLANT_MAINTENANCE | 280.5
2023 | nonsummer | OASIS_6_SOLAR1 | PLANT_TROUBLE | 0
2023 | nonsummer | OASIS_6_SOLAR2 | METERING_TELEMETRY | 0
2023 | nonsummer | OASIS_6_SOLAR2 | PLANT_TROUBLE | 1779.3167
2023 | nonsummer | OASIS_6_VINSR1 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2023 | nonsummer | OBERON_5_O1BBX2 | METERING_TELEMETRY | 0
2023 | nonsummer | OBERON_5_O1BBX2 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | OBERON_5_O1BBX2 | PLANT_MAINTENANCE | 0
2023 | nonsummer | OBERON_5_O1BBX2 | PLANT_TROUBLE | 0
2023 | nonsummer | OBERON_5_O1BBX2 | UNIT_TESTING | 0
2023 | nonsummer | OBERON_5_O1SSR3 | METERING_TELEMETRY | 0
2023 | nonsummer | OBERON_5_O1SSR3 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | OBERON_5_O1SSR3 | PLANT_MAINTENANCE | 0
2023 | nonsummer | OBERON_5_O1SSR3 | PLANT_TROUBLE | 0
2023 | nonsummer | OBERON_5_O1SSR3 | UNIT_TESTING | 0
2023 | nonsummer | OBERON_5_O1SSX2 | METERING_TELEMETRY | 0
2023 | nonsummer | OBERON_5_O1SSX2 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | OBERON_5_O1SSX2 | PLANT_MAINTENANCE | 0
2023 | nonsummer | OBERON_5_O1SSX2 | PLANT_TROUBLE | 0
2023 | nonsummer | OBERON_5_O1SSX2 | UNIT_TESTING | 0
2023 | nonsummer | OBERON_5_O2BBX2 | METERING_TELEMETRY | 0
2023 | nonsummer | OBERON_5_O2BBX2 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | OBERON_5_O2BBX2 | PLANT_MAINTENANCE | 0
2023 | nonsummer | OBERON_5_O2BBX2 | PLANT_TROUBLE | 0
2023 | nonsummer | OBERON_5_O2BBX2 | UNIT_TESTING | 0
2023 | nonsummer | OBERON_5_O2SSR4 | METERING_TELEMETRY | 125
2023 | nonsummer | OBERON_5_O2SSR4 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | OBERON_5_O2SSR4 | PLANT_TROUBLE | 0
2023 | nonsummer | OBERON_5_O2SSR4 | UNIT_TESTING | 0
2023 | nonsummer | OBERON_5_O2SSR5 | METERING_TELEMETRY | 125
2023 | nonsummer | OBERON_5_O2SSR5 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | OBERON_5_O2SSR5 | PLANT_MAINTENANCE | 0
2023 | nonsummer | OBERON_5_O2SSR5 | PLANT_TROUBLE | 0
2023 | nonsummer | OBERON_5_O2SSR5 | UNIT_TESTING | 0
2023 | nonsummer | OCOTLO_6_OCWSB1 | METERING_TELEMETRY | 0
2023 | nonsummer | OCOTLO_6_OCWSB1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | OCOTLO_6_OCWSB1 | PLANT_TROUBLE | 556.6667
2023 | nonsummer | OCOTLO_6_OCWSB1 | TRANSITIONAL_LIMITATION | 1020
2023 | nonsummer | OCOTLO_6_OCWSB1 | UNIT_TESTING | 0
2023 | nonsummer | OCTILO_5_WIND | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | OCTILO_5_WIND | AMBIENT_NOT_DUE_TO_TEMP | 5078.8333
2023 | nonsummer | OCTILO_5_WIND | PLANT_MAINTENANCE | 0
2023 | nonsummer | OCTILO_5_WIND | PLANT_TROUBLE | 23575.3667
2023 | nonsummer | OGROVE_6_PL1X2 | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | OGROVE_6_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | OGROVE_6_PL1X2 | PLANT_MAINTENANCE | 1077.1833
2023 | nonsummer | OGROVE_6_PL1X2 | PLANT_TROUBLE | 436.1
2023 | nonsummer | OGROVE_6_PL1X2 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | OILFLD_7_QFUNTS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 553.73
2023 | nonsummer | OILFLD_7_QFUNTS | AMBIENT_NOT_DUE_TO_TEMP | 1421.03
2023 | nonsummer | OILFLD_7_QFUNTS | PLANT_MAINTENANCE | 147.6
2023 | nonsummer | OILFLD_7_QFUNTS | PLANT_TROUBLE | 334.68
2023 | nonsummer | OILFLD_7_QFUNTS | TRANSMISSION_INDUCED | 0.6
2023 | nonsummer | OLDRIV_6_BIOGAS | PLANT_TROUBLE | 0
2023 | nonsummer | OLDRIV_6_CESDBM | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2023 | nonsummer | OLDRIV_6_CESDBM | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | OLDRIV_6_CESDBM | PLANT_MAINTENANCE | 0
2023 | nonsummer | OLDRIV_6_CESDBM | PLANT_TROUBLE | 0
2023 | nonsummer | OLDRIV_6_LKVBM1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 5
2023 | nonsummer | OLDRIV_6_LKVBM1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | OLDRIV_6_LKVBM1 | PLANT_TROUBLE | 3.5
2023 | nonsummer | OLDRV1_6_SOLAR | METERING_TELEMETRY | 0
2023 | nonsummer | OLDRV1_6_SOLAR | PLANT_TROUBLE | 369.6667
2023 | nonsummer | OLINDA_2_COYCRK | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 3302.15
2023 | nonsummer | OLINDA_2_LNDFL2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 2210.5
2023 | nonsummer | OLINDA_2_LNDFL2 | PLANT_MAINTENANCE | 730.5
2023 | nonsummer | OLINDA_2_LNDFL2 | PLANT_TROUBLE | 336.5
2023 | nonsummer | OLINDA_2_LNDFL2 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2023 | nonsummer | OLINDA_2_LNDFL2 | TRANSMISSION_INDUCED | 375
2023 | nonsummer | OLIVEP_1_SOLAR | PLANT_MAINTENANCE | 0
2023 | nonsummer | OLIVEP_1_SOLAR | PLANT_TROUBLE | 38.3333
2023 | nonsummer | OLIVEP_1_SOLAR | TRANSMISSION_INDUCED | 161.6667
2023 | nonsummer | OLIVEP_1_SOLAR | UNIT_TESTING | 0
2023 | nonsummer | OLIVEP_1_SOLAR2 | PLANT_TROUBLE | 37.8542
2023 | nonsummer | OLIVEP_1_SOLAR2 | TRANSMISSION_INDUCED | 159.975
2023 | nonsummer | OLSEN_2_UNIT | PLANT_TROUBLE | 0
2023 | nonsummer | OLSEN_2_UNIT | TRANSMISSION_INDUCED | 272.0667
2023 | nonsummer | OMAR_2_UNIT 1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | OMAR_2_UNIT 1 | PLANT_TROUBLE | 581.25
2023 | nonsummer | OMAR_2_UNIT 2 | PLANT_MAINTENANCE | 5250
2023 | nonsummer | OMAR_2_UNIT 2 | PLANT_TROUBLE | 3056.25
2023 | nonsummer | OMAR_2_UNIT 2 | UNIT_TESTING | 0
2023 | nonsummer | OMAR_2_UNIT 3 | PLANT_MAINTENANCE | 0
2023 | nonsummer | OMAR_2_UNIT 3 | PLANT_TROUBLE | 2192.5
2023 | nonsummer | OMAR_2_UNIT 3 | RTU_RIG | 0
2023 | nonsummer | OMAR_2_UNIT 4 | PLANT_MAINTENANCE | 9769.9167
2023 | nonsummer | OMAR_2_UNIT 4 | PLANT_TROUBLE | 8812.5
2023 | nonsummer | OMAR_2_UNIT 4 | UNIT_TESTING | 0
2023 | nonsummer | ONLLPP_6_UNITS | TRANSMISSION_INDUCED | 0
2023 | nonsummer | ORLND_6_HIGHLI | PLANT_TROUBLE | 527.5
2023 | nonsummer | ORMOND_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 36322.23
2023 | nonsummer | ORMOND_7_UNIT 1 | PLANT_TROUBLE | 25215.5345
2023 | nonsummer | ORMOND_7_UNIT 1 | TRANSMISSION_INDUCED | 1482.54
2023 | nonsummer | ORMOND_7_UNIT 1 | UNIT_TESTING | 1853.175
2023 | nonsummer | ORMOND_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 36750
2023 | nonsummer | ORMOND_7_UNIT 2 | PLANT_MAINTENANCE | 0
2023 | nonsummer | ORMOND_7_UNIT 2 | PLANT_TROUBLE | 9325
2023 | nonsummer | ORMOND_7_UNIT 2 | TRANSMISSION_INDUCED | 1500
2023 | nonsummer | OROLOM_1_SOLAR1 | PLANT_TROUBLE | 0
2023 | nonsummer | OROLOM_1_SOLAR1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | OROLOM_1_SOLAR2 | PLANT_TROUBLE | 100
2023 | nonsummer | OROLOM_1_SOLAR2 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | OROVIL_6_UNIT | PLANT_MAINTENANCE | 7.4
2023 | nonsummer | OROVIL_6_UNIT | PLANT_TROUBLE | 1520.4
2023 | nonsummer | OROVIL_6_UNIT | TRANSMISSION_INDUCED | 7.4
2023 | nonsummer | ORTGA_6_ME1SL1 | METERING_TELEMETRY | 0
2023 | nonsummer | ORTGA_6_ME1SL1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | OTAY_6_ECVBT1 | TRANSMISSION_INDUCED | 2385
2023 | nonsummer | OTAY_6_ECVBT2 | TRANSMISSION_INDUCED | 810
2023 | nonsummer | OTAY_6_PL1X2 | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | OTAY_6_PL1X2 | PLANT_MAINTENANCE | 435.27
2023 | nonsummer | OTAY_6_PL1X2 | PLANT_TROUBLE | 337.0045
2023 | nonsummer | OTMESA_2_PL1X3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 9055.2
2023 | nonsummer | OTMESA_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 12882.5793
2023 | nonsummer | OTMESA_2_PL1X3 | ENVIRONMENTAL_RESTRICTIONS | 1605
2023 | nonsummer | OTMESA_2_PL1X3 | PLANT_MAINTENANCE | 3136.8
2023 | nonsummer | OTMESA_2_PL1X3 | PLANT_TROUBLE | 26226.3833
2023 | nonsummer | OTMESA_2_PL1X3 | TRANSITIONAL_LIMITATION | 0
2023 | nonsummer | OTMESA_2_PL1X3 | TRANSMISSION_INDUCED | 594
2023 | nonsummer | OTMESA_2_PL1X3 | UNIT_TESTING | 501.4
2023 | nonsummer | OXBOW_6_DRUM | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 406
2023 | nonsummer | OXBOW_6_DRUM | PLANT_MAINTENANCE | 9.1833
2023 | nonsummer | OXBOW_6_DRUM | PLANT_TROUBLE | 145
2023 | nonsummer | OXBOW_6_DRUM | TRANSMISSION_INDUCED | 4340.8167
2023 | nonsummer | OXMTN_6_LNDFIL | PLANT_MAINTENANCE | 279.271
2023 | nonsummer | OXMTN_6_LNDFIL | PLANT_TROUBLE | 259.905
2023 | nonsummer | OXMTN_6_LNDFIL | TRANSMISSION_INDUCED | 0
2023 | nonsummer | PACLUM_6_UNIT | PLANT_MAINTENANCE | 199.9
2023 | nonsummer | PACLUM_6_UNIT | PLANT_TROUBLE | 5895.65
2023 | nonsummer | PACLUM_6_UNIT | TRANSMISSION_INDUCED | 110
2023 | nonsummer | PADUA_2_ONTARO | AMBIENT_NOT_DUE_TO_TEMP | 693.2
2023 | nonsummer | PADUA_2_ONTARO | PLANT_MAINTENANCE | 8.1
2023 | nonsummer | PADUA_2_ONTARO | PLANT_TROUBLE | 616.3
2023 | nonsummer | PADUA_2_ONTARO | TRANSMISSION_INDUCED | 40
2023 | nonsummer | PADUA_6_MWDSDM | PLANT_MAINTENANCE | 0
2023 | nonsummer | PADUA_6_MWDSDM | PLANT_TROUBLE | 346.5
2023 | nonsummer | PADUA_7_SDIMAS | ENVIRONMENTAL_RESTRICTIONS | 136.5
2023 | nonsummer | PADUA_7_SDIMAS | PLANT_MAINTENANCE | 0
2023 | nonsummer | PADUA_7_SDIMAS | PLANT_TROUBLE | 0
2023 | nonsummer | PADUA_7_SDIMAS | TRANSMISSION_INDUCED | 0
2023 | nonsummer | PAIGES_6_SOLAR | METERING_TELEMETRY | 300
2023 | nonsummer | PAIGES_6_SOLAR | PLANT_MAINTENANCE | 0
2023 | nonsummer | PAIGES_6_SOLAR | PLANT_TROUBLE | 255.6667
2023 | nonsummer | PAIGES_6_SOLAR | TRANSMISSION_INDUCED | 200
2023 | nonsummer | PALALT_7_COBUG | PLANT_TROUBLE | 4522.5
2023 | nonsummer | PALOMR_2_PL1X3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2023 | nonsummer | PALOMR_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | PALOMR_2_PL1X3 | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | PALOMR_2_PL1X3 | PLANT_MAINTENANCE | 4117.47
2023 | nonsummer | PALOMR_2_PL1X3 | PLANT_TROUBLE | 511.4367
2023 | nonsummer | PALOMR_2_PL1X3 | TRANSMISSION_INDUCED | 88231.5
2023 | nonsummer | PALOMR_2_PL1X3 | UNIT_TESTING | 0
2023 | nonsummer | PARDEB_6_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 1148.1
2023 | nonsummer | PARDEB_6_UNITS | PLANT_MAINTENANCE | 1753.1667
2023 | nonsummer | PARDEB_6_UNITS | PLANT_TROUBLE | 1600
2023 | nonsummer | PARDEB_6_UNITS | TRANSMISSION_INDUCED | 0
2023 | nonsummer | PBLOSM_2_SOLAR | PLANT_TROUBLE | 0
2023 | nonsummer | PEABDY_2_LNDFIL | PLANT_MAINTENANCE | 0
2023 | nonsummer | PEABDY_2_LNDFIL | PLANT_TROUBLE | 44.8533
2023 | nonsummer | PEABDY_2_LNDFIL | TRANSMISSION_INDUCED | 64.8
2023 | nonsummer | PEABDY_2_LNDFL1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 2.4
2023 | nonsummer | PEABDY_2_LNDFL1 | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | PEABDY_2_LNDFL1 | AMBIENT_NOT_DUE_TO_TEMP | 0.61667
2023 | nonsummer | PEABDY_2_LNDFL1 | ENVIRONMENTAL_RESTRICTIONS | 7.4667
2023 | nonsummer | PEABDY_2_LNDFL1 | PLANT_MAINTENANCE | 609.415
2023 | nonsummer | PEABDY_2_LNDFL1 | PLANT_TROUBLE | 594.7783
2023 | nonsummer | PEABDY_2_LNDFL1 | TRANSMISSION_INDUCED | 80
2023 | nonsummer | PEARBL_2_NSPIN | PLANT_MAINTENANCE | 118
2023 | nonsummer | PEASE_1_TBEBT1 | METERING_TELEMETRY | 49.9
2023 | nonsummer | PEASE_1_TBEBT1 | PLANT_MAINTENANCE | 171.85
2023 | nonsummer | PEASE_1_TBEBT1 | PLANT_TROUBLE | 298.75
2023 | nonsummer | PEASE_1_TBEBT1 | RTU_RIG | 112.7
2023 | nonsummer | PEASE_1_TBEBT1 | UNIT_TESTING | 0
2023 | nonsummer | PEORIA_1_SOLAR | PLANT_TROUBLE | 160
2023 | nonsummer | PGCC_1_PDRP06 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGCC_1_PDRP07 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGCC_1_PDRP09 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGEB_2_PDRP12 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGEB_2_PDRP13 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGEB_2_PDRP14 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGEB_2_PDRP16 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGEB_2_RDRR01 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGF1_2_PDRP05 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGF1_2_PDRP06 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGF1_2_PDRP12 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGF1_2_PDRP14 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGF1_2_PDRP15 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGF1_2_PDRP22 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGF1_2_PDRP23 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGF1_2_PDRP33 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGFG_1_PDRP07 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGFG_1_PDRP08 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGHB_6_PDRP03 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGKN_2_PDRP01 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGKN_2_PDRP03 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGKN_2_PDRP04 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGNB_2_PDRP06 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGNB_2_PDRP07 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGNB_2_PDRP08 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGNB_2_PDRP44 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGNC_1_PDRP02 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGNP_2_PDRP03 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGNP_2_PDRP04 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGNP_2_PDRP05 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGNP_2_PDRP06 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGNP_2_PDRP12 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGNP_2_PDRP13 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGNP_2_PDRP58 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGP2_2_PDRP09 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGP2_2_PDRP31 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGSB_1_PDRP106 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGSB_1_PDRP15 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGSB_1_PDRP18 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGSB_1_PDRP19 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGSB_1_PDRP20 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGSF_2_PDRP13 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGSF_2_PDRP14 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGSF_2_PDRP15 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGSI_1_PDRP04 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGSI_1_PDRP05 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGSI_1_PDRP08 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGSI_1_PDRP13 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGSI_1_PDRP18 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGSI_1_PDRP53 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGST_2_PDRP02 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGST_2_PDRP04 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGST_2_PDRP05 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGST_2_PDRP06 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGST_2_PDRP12 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGST_2_PDRP42 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGZP_2_PDRP01 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGZP_2_PDRP03 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGZP_2_PDRP04 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PGZP_2_PDRP05 | SHORT_TERM_USE_LIMIT_REACHED | 0
2023 | nonsummer | PHOENX_1_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 129.355
2023 | nonsummer | PHOENX_1_UNIT | ENVIRONMENTAL_RESTRICTIONS | 120
2023 | nonsummer | PHOENX_1_UNIT | PLANT_MAINTENANCE | 230
2023 | nonsummer | PHOENX_1_UNIT | PLANT_TROUBLE | 4.0333
2023 | nonsummer | PHOENX_1_UNIT | TRANSMISSION_INDUCED | 9.8333
2023 | nonsummer | PINFLT_7_UNITS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 16504.7283
2023 | nonsummer | PINFLT_7_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 877.5
2023 | nonsummer | PINFLT_7_UNITS | PLANT_MAINTENANCE | 72188.35
2023 | nonsummer | PINFLT_7_UNITS | TRANSMISSION_INDUCED | 981.75
2023 | nonsummer | PIOPIC_2_CTG1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2023 | nonsummer | PIOPIC_2_CTG1 | AMBIENT_DUE_TO_TEMP | 2441.38
2023 | nonsummer | PIOPIC_2_CTG1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | PIOPIC_2_CTG1 | PLANT_TROUBLE | 7.755
2023 | nonsummer | PIOPIC_2_CTG1 | UNIT_TESTING | 0
2023 | nonsummer | PIOPIC_2_CTG2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2023 | nonsummer | PIOPIC_2_CTG2 | AMBIENT_DUE_TO_TEMP | 1263.695
2023 | nonsummer | PIOPIC_2_CTG2 | PLANT_TROUBLE | 455.0008
2023 | nonsummer | PIOPIC_2_CTG3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2023 | nonsummer | PIOPIC_2_CTG3 | AMBIENT_DUE_TO_TEMP | 1245.3867
2023 | nonsummer | PIOPIC_2_CTG3 | PLANT_TROUBLE | 19.775
2023 | nonsummer | PIOPIC_2_CTG3 | UNIT_TESTING | 1.8333
2023 | nonsummer | PIT1_6_FRIVRA | PLANT_TROUBLE | 0
2023 | nonsummer | PIT1_6_FRIVRA | TRANSMISSION_INDUCED | 0
2023 | nonsummer | PIT1_7_UNIT 1 | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | PIT1_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 44.1
2023 | nonsummer | PIT1_7_UNIT 1 | PLANT_TROUBLE | 24000
2023 | nonsummer | PIT1_7_UNIT 1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | PIT1_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 9.8333
2023 | nonsummer | PIT1_7_UNIT 2 | PLANT_TROUBLE | 0
2023 | nonsummer | PIT1_7_UNIT 2 | TRANSMISSION_INDUCED | 640
2023 | nonsummer | PIT3_7_PL1X3 | AMBIENT_NOT_DUE_TO_TEMP | 157.8333
2023 | nonsummer | PIT3_7_PL1X3 | PLANT_TROUBLE | 89.95
2023 | nonsummer | PIT4_7_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 674.9167
2023 | nonsummer | PIT4_7_PL1X2 | PLANT_TROUBLE | 0
2023 | nonsummer | PIT4_7_PL1X2 | TRANSMISSION_INDUCED | 967.4167
2023 | nonsummer | PIT5_7_PL1X2 | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | PIT5_7_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 1476.3667
2023 | nonsummer | PIT5_7_PL1X2 | PLANT_MAINTENANCE | 0
2023 | nonsummer | PIT5_7_PL1X2 | PLANT_TROUBLE | 50.5667
2023 | nonsummer | PIT5_7_PL1X2 | TRANSITIONAL_LIMITATION | 7
2023 | nonsummer | PIT5_7_PL1X2 | TRANSMISSION_INDUCED | 207.7333
2023 | nonsummer | PIT5_7_PL3X4 | AMBIENT_NOT_DUE_TO_TEMP | 776.3667
2023 | nonsummer | PIT5_7_PL3X4 | PLANT_MAINTENANCE | 109.3333
2023 | nonsummer | PIT5_7_PL3X4 | PLANT_TROUBLE | 0
2023 | nonsummer | PIT5_7_PL3X4 | TRANSMISSION_INDUCED | 207.7333
2023 | nonsummer | PIT6_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 1423.6833
2023 | nonsummer | PIT6_7_UNIT 1 | METERING_TELEMETRY | 0
2023 | nonsummer | PIT6_7_UNIT 1 | PLANT_TROUBLE | 36.6153
2023 | nonsummer | PIT6_7_UNIT 1 | TRANSMISSION_INDUCED | 314.0667
2023 | nonsummer | PIT6_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 1839.4907
2023 | nonsummer | PIT6_7_UNIT 2 | METERING_TELEMETRY | 0
2023 | nonsummer | PIT6_7_UNIT 2 | PLANT_TROUBLE | 31.1767
2023 | nonsummer | PIT6_7_UNIT 2 | TRANSMISSION_INDUCED | 323.1427
2023 | nonsummer | PIT7_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 1379.412
2023 | nonsummer | PIT7_7_UNIT 1 | METERING_TELEMETRY | 0
2023 | nonsummer | PIT7_7_UNIT 1 | PLANT_TROUBLE | 9.904
2023 | nonsummer | PIT7_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 672.1772
2023 | nonsummer | PIT7_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 310.5257
2023 | nonsummer | PIT7_7_UNIT 2 | METERING_TELEMETRY | 0
2023 | nonsummer | PIT7_7_UNIT 2 | PLANT_MAINTENANCE | 2111.2
2023 | nonsummer | PIT7_7_UNIT 2 | PLANT_TROUBLE | 56.9805
2023 | nonsummer | PIT7_7_UNIT 2 | RTU_RIG | 0
2023 | nonsummer | PIT7_7_UNIT 2 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | PIUTE_6_GNBSR1 | PLANT_TROUBLE | 2.5
2023 | nonsummer | PLACVL_1_CHILIB | PLANT_MAINTENANCE | 0
2023 | nonsummer | PLACVL_1_CHILIB | PLANT_TROUBLE | 41.7
2023 | nonsummer | PLACVL_1_CHILIB | TRANSMISSION_INDUCED | 0
2023 | nonsummer | PLACVL_1_RCKCRE | TRANSMISSION_INDUCED | 5
2023 | nonsummer | PLAINV_6_BSOLAR | PLANT_TROUBLE | 1790.55
2023 | nonsummer | PLAINV_6_DSOLAR | AMBIENT_DUE_TO_TEMP | 10
2023 | nonsummer | PLAINV_6_DSOLAR | PLANT_TROUBLE | 35.65
2023 | nonsummer | PLAINV_6_NLRSR1 | PLANT_TROUBLE | 2342.45
2023 | nonsummer | PLAINV_6_SOLAR3 | PLANT_TROUBLE | 3186.8167
2023 | nonsummer | PLAINV_6_SOLARC | PLANT_MAINTENANCE | 0
2023 | nonsummer | PLAINV_6_SOLARC | PLANT_TROUBLE | 954.2833
2023 | nonsummer | PLMSSR_6_HISIER | PLANT_MAINTENANCE | 89.7
2023 | nonsummer | PLMSSR_6_HISIER | PLANT_TROUBLE | 271.4243
2023 | nonsummer | PLMSSR_6_HISIER | TRANSMISSION_INDUCED | 21.2435
2023 | nonsummer | PLSNTG_7_LNCLND | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2023 | nonsummer | PLSNTG_7_LNCLND | PLANT_TROUBLE | 0
2023 | nonsummer | PLSNTG_7_LNCLND | TRANSMISSION_INDUCED | 49.8
2023 | nonsummer | PMDLET_6_SOLAR1 | PLANT_TROUBLE | 49.6333
2023 | nonsummer | PMDLET_6_SOLAR1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | PMPJCK_1_RB2SLR | PLANT_MAINTENANCE | 100
2023 | nonsummer | PMPJCK_1_SOLAR1 | PLANT_MAINTENANCE | 40
2023 | nonsummer | PMPJCK_1_SOLAR1 | PLANT_TROUBLE | 60
2023 | nonsummer | PNCHEG_2_PL1X4 | AMBIENT_DUE_TO_TEMP | 1271.0867
2023 | nonsummer | PNCHEG_2_PL1X4 | AMBIENT_NOT_DUE_TO_TEMP | 452.475
2023 | nonsummer | PNCHEG_2_PL1X4 | METERING_TELEMETRY | 0
2023 | nonsummer | PNCHEG_2_PL1X4 | PLANT_MAINTENANCE | 2605.5
2023 | nonsummer | PNCHEG_2_PL1X4 | PLANT_TROUBLE | 76340.6833
2023 | nonsummer | PNCHEG_2_PL1X4 | SHORT_TERM_USE_LIMIT_REACHED | 81978.45
2023 | nonsummer | PNCHEG_2_PL1X4 | TRANSMISSION_INDUCED | 973
2023 | nonsummer | PNCHEG_2_PL1X4 | UNIT_TESTING | 0
2023 | nonsummer | PNCHPP_1_PL1X2 | AMBIENT_DUE_TO_TEMP | 3712.2935
2023 | nonsummer | PNCHPP_1_PL1X2 | METERING_TELEMETRY | 0
2023 | nonsummer | PNCHPP_1_PL1X2 | PLANT_MAINTENANCE | 5423.1095
2023 | nonsummer | PNCHPP_1_PL1X2 | PLANT_TROUBLE | 3511.7435
2023 | nonsummer | PNCHPP_1_PL1X2 | TRANSMISSION_INDUCED | 1237.0715
2023 | nonsummer | PNCHPP_1_PL1X2 | UNIT_TESTING | 165.176
2023 | nonsummer | PNCHVS_2_SOLAR | METERING_TELEMETRY | 25
2023 | nonsummer | PNCHVS_2_SOLAR | PLANT_MAINTENANCE | 46.8
2023 | nonsummer | PNCHVS_2_SOLAR | PLANT_TROUBLE | 1420.6667
2023 | nonsummer | PNCHVS_2_SOLAR | TRANSMISSION_INDUCED | 700
2023 | nonsummer | PNOCHE_1_PL1X2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 2.2
2023 | nonsummer | PNOCHE_1_PL1X2 | AMBIENT_DUE_TO_TEMP | 87.54
2023 | nonsummer | PNOCHE_1_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | PNOCHE_1_PL1X2 | PLANT_MAINTENANCE | 4497.3
2023 | nonsummer | PNOCHE_1_PL1X2 | PLANT_TROUBLE | 89.946
2023 | nonsummer | PNOCHE_1_UNITA1 | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | PNOCHE_1_UNITA1 | PLANT_MAINTENANCE | 8274.7317
2023 | nonsummer | PNOCHE_1_UNITA1 | PLANT_TROUBLE | 1538.9
2023 | nonsummer | PNOCHE_1_UNITA1 | TRANSMISSION_INDUCED | 545.6633
2023 | nonsummer | POEPH_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 8561.7267
2023 | nonsummer | POEPH_7_UNIT 1 | PLANT_TROUBLE | 2957.1333
2023 | nonsummer | POEPH_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 10101.2932
2023 | nonsummer | POEPH_7_UNIT 2 | PLANT_TROUBLE | 5162.6333
2023 | nonsummer | POEPH_7_UNIT 2 | TRANSMISSION_INDUCED | 140.8
2023 | nonsummer | POLRIS_2_ASEBT1 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | POLRIS_2_ASEBT1 | PLANT_TROUBLE | 0
2023 | nonsummer | POLRIS_2_ASEBT1 | UNIT_TESTING | 0
2023 | nonsummer | POLRIS_2_ASESR1 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | POLRIS_2_ASESR1 | PLANT_TROUBLE | 52.5
2023 | nonsummer | POLRIS_2_ASESR1 | UNIT_TESTING | 0
2023 | nonsummer | POTTER_6_UNITS | PLANT_MAINTENANCE | 0
2023 | nonsummer | POTTER_6_UNITS | PLANT_TROUBLE | 4595.5
2023 | nonsummer | PRCTVY_1_MIGBT1 | PLANT_MAINTENANCE | 10
2023 | nonsummer | PRCTVY_1_MIGBT1 | PLANT_TROUBLE | 25
2023 | nonsummer | PRCTVY_1_MIGBT1 | UNIT_TESTING | 20
2023 | nonsummer | PRIMM_2_SOLAR1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | PRIMM_2_SOLAR1 | PLANT_TROUBLE | 60
2023 | nonsummer | PUTHCR_1_PCNSB1 | METERING_TELEMETRY | 0
2023 | nonsummer | PUTHCR_1_PCNSB1 | PLANT_MAINTENANCE | 27
2023 | nonsummer | PUTHCR_1_PCNSB1 | PLANT_TROUBLE | 295.05
2023 | nonsummer | PUTHCR_1_SOLAR1 | PLANT_MAINTENANCE | 64.8
2023 | nonsummer | PUTHCR_1_SOLAR1 | PLANT_TROUBLE | 99
2023 | nonsummer | PUTHCR_1_SOLAR1 | TRANSMISSION_INDUCED | 31.68
2023 | nonsummer | PVERDE_5_SCEDYN | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | PVERDE_5_SCEDYN | PLANT_MAINTENANCE | 7781.9167
2023 | nonsummer | PVERDE_5_SCEDYN | PLANT_TROUBLE | 19721.2667
2023 | nonsummer | PWEST_1_UNIT | PLANT_TROUBLE | 2215.5
2023 | nonsummer | RAMON_2_SCEDYN | AMBIENT_NOT_DUE_TO_TEMP | 69688.2333
2023 | nonsummer | RAMON_2_SCEDYN | PLANT_MAINTENANCE | 0
2023 | nonsummer | RATSKE_2_NROSR1 | PLANT_MAINTENANCE | 287
2023 | nonsummer | RATSKE_2_NROSR1 | PLANT_TROUBLE | 154.6667
2023 | nonsummer | RATSKE_2_NROSR1 | UNIT_TESTING | 0
2023 | nonsummer | RATSKE_2_RBSSB1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 130.0833
2023 | nonsummer | RATSKE_2_RBSSB1 | METERING_TELEMETRY | 29
2023 | nonsummer | RATSKE_2_RBSSB1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | RATSKE_2_RBSSB1 | PLANT_TROUBLE | 10.725
2023 | nonsummer | RATSKE_2_RBSSB2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 87.4
2023 | nonsummer | RATSKE_2_RBSSB2 | PLANT_MAINTENANCE | 0
2023 | nonsummer | RATSKE_2_RBSSB2 | PLANT_TROUBLE | 0
2023 | nonsummer | RCKCRK_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 9557.9067
2023 | nonsummer | RCKCRK_7_UNIT 1 | PLANT_TROUBLE | 244.15
2023 | nonsummer | RCKCRK_7_UNIT 1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | RCKCRK_7_UNIT 1 | UNIT_TESTING | 152
2023 | nonsummer | RCKCRK_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 8563.7283
2023 | nonsummer | RCKCRK_7_UNIT 2 | PLANT_MAINTENANCE | 222.8583
2023 | nonsummer | RCKCRK_7_UNIT 2 | PLANT_TROUBLE | 70.1767
2023 | nonsummer | RCKCRK_7_UNIT 2 | TRANSMISSION_INDUCED | 13.75
2023 | nonsummer | RCKCRK_7_UNIT 2 | UNIT_TESTING | 165.9583
2023 | nonsummer | RDWAY_1_CREST | PLANT_MAINTENANCE | 6.325
2023 | nonsummer | RDWAY_1_SCKSR1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | RDWAY_1_SCKSR1 | PLANT_TROUBLE | 0
2023 | nonsummer | RDWAY_1_SCKSR1 | UNIT_TESTING | 0
2023 | nonsummer | RECTOR_2_CREST | PLANT_TROUBLE | 0
2023 | nonsummer | RECTOR_2_IVANPV | PLANT_MAINTENANCE | 0
2023 | nonsummer | RECTOR_2_KAWEAH | AMBIENT_NOT_DUE_TO_TEMP | 6594
2023 | nonsummer | RECTOR_2_KAWH 1 | AMBIENT_NOT_DUE_TO_TEMP | 2373.75
2023 | nonsummer | RECTOR_2_QF | ENVIRONMENTAL_RESTRICTIONS | 4922.05
2023 | nonsummer | RECTOR_2_QF | PLANT_MAINTENANCE | 6027
2023 | nonsummer | RECTOR_2_QF | PLANT_TROUBLE | 502.25
2023 | nonsummer | RECTOR_2_TFDBM1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | RECTOR_2_TFDBM1 | PLANT_TROUBLE | 37.2267
2023 | nonsummer | REDBLF_6_UNIT | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | REDBLF_6_UNIT | METERING_TELEMETRY | 0
2023 | nonsummer | REDBLF_6_UNIT | PLANT_MAINTENANCE | 0
2023 | nonsummer | REDBLF_6_UNIT | PLANT_TROUBLE | 125
2023 | nonsummer | REDBLF_6_UNIT | TRANSMISSION_INDUCED | 51.3333
2023 | nonsummer | REDOND_7_UNIT 5 | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | REDOND_7_UNIT 5 | ENVIRONMENTAL_RESTRICTIONS | 1430.96
2023 | nonsummer | REDOND_7_UNIT 5 | PLANT_TROUBLE | 32199.1005
2023 | nonsummer | REDOND_7_UNIT 5 | UNIT_SUPPORTING_STARTUP | 0
2023 | nonsummer | REDOND_7_UNIT 5 | UNIT_TESTING | 0
2023 | nonsummer | REDOND_7_UNIT 6 | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | REDOND_7_UNIT 6 | ENVIRONMENTAL_RESTRICTIONS | 1394.32
2023 | nonsummer | REDOND_7_UNIT 6 | PLANT_TROUBLE | 3784.7115
2023 | nonsummer | REDOND_7_UNIT 6 | UNIT_SUPPORTING_STARTUP | 221.45
2023 | nonsummer | REDOND_7_UNIT 6 | UNIT_TESTING | 552.6567
2023 | nonsummer | REDOND_7_UNIT 8 | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | REDOND_7_UNIT 8 | ENVIRONMENTAL_RESTRICTIONS | 3840
2023 | nonsummer | REDOND_7_UNIT 8 | PLANT_TROUBLE | 0
2023 | nonsummer | REDOND_7_UNIT 8 | UNIT_TESTING | 699.8333
2023 | nonsummer | REEDLY_6_SOLAR | TRANSMISSION_INDUCED | 0
2023 | nonsummer | RENWD_1_QF | PLANT_MAINTENANCE | 2512.3167
2023 | nonsummer | RENWD_1_QF | PLANT_TROUBLE | 0
2023 | nonsummer | RICHMN_1_CHVSR2 | PLANT_MAINTENANCE | 0
2023 | nonsummer | RICHMN_1_CHVSR2 | PLANT_TROUBLE | 304.5
2023 | nonsummer | RICHMN_1_SOLAR | METERING_TELEMETRY | 12
2023 | nonsummer | RICHMN_1_SOLAR | PLANT_MAINTENANCE | 0
2023 | nonsummer | RICHMN_1_SOLAR | PLANT_TROUBLE | 31.2333
2023 | nonsummer | RICHMN_7_BAYENV | PLANT_TROUBLE | 2637.5
2023 | nonsummer | RIOBRV_6_UNIT 1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 3262.4667
2023 | nonsummer | RIOBRV_6_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 68.8333
2023 | nonsummer | RIOBRV_6_UNIT 1 | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | nonsummer | RIOBRV_6_UNIT 1 | PLANT_TROUBLE | 1190
2023 | nonsummer | RIOBRV_6_UNIT 1 | TRANSMISSION_INDUCED | 73.7333
2023 | nonsummer | RNDMTN_2_SLSPHY1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | ROLLIN_6_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 1102.85
2023 | nonsummer | ROLLIN_6_UNIT | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | nonsummer | ROLLIN_6_UNIT | PLANT_MAINTENANCE | 0
2023 | nonsummer | ROLLIN_6_UNIT | PLANT_TROUBLE | 34.65
2023 | nonsummer | ROLLIN_6_UNIT | TRANSMISSION_INDUCED | 165.045
2023 | nonsummer | ROSMDW_2_WIND1 | PLANT_MAINTENANCE | 4683.8333
2023 | nonsummer | ROSMDW_2_WIND1 | PLANT_TROUBLE | 581.9133
2023 | nonsummer | ROSMDW_2_WIND1 | UNIT_TESTING | 0
2023 | nonsummer | ROSMND_6_SOLAR | METERING_TELEMETRY | 197.5
2023 | nonsummer | ROSMND_6_SOLAR | PLANT_TROUBLE | 802.75
2023 | nonsummer | RSMSLR_6_SOLAR1 | PLANT_MAINTENANCE | 70
2023 | nonsummer | RSMSLR_6_SOLAR1 | PLANT_TROUBLE | 1836.3333
2023 | nonsummer | RSMSLR_6_SOLAR1 | TRANSMISSION_INDUCED | 166.3333
2023 | nonsummer | RSMSLR_6_SOLAR2 | METERING_TELEMETRY | 1100
2023 | nonsummer | RSMSLR_6_SOLAR2 | PLANT_MAINTENANCE | 253.3333
2023 | nonsummer | RSMSLR_6_SOLAR2 | PLANT_TROUBLE | 913.3333
2023 | nonsummer | RTEDDY_2_SC1SR3 | PLANT_MAINTENANCE | 220
2023 | nonsummer | RTEDDY_2_SC1SR3 | PLANT_TROUBLE | 160
2023 | nonsummer | RTEDDY_2_SEBSR3 | PLANT_MAINTENANCE | 980
2023 | nonsummer | RTEDDY_2_SEBSR3 | PLANT_TROUBLE | 224
2023 | nonsummer | RTEDDY_2_SEBSR4 | PLANT_MAINTENANCE | 168
2023 | nonsummer | RTEDDY_2_SEBSR4 | PLANT_TROUBLE | 224
2023 | nonsummer | RTEDDY_2_SOLAR1 | PLANT_MAINTENANCE | 142.9067
2023 | nonsummer | RTEDDY_2_SOLAR1 | PLANT_TROUBLE | 74.7
2023 | nonsummer | RTEDDY_2_SPASR4 | PLANT_MAINTENANCE | 78
2023 | nonsummer | RTEDDY_2_SPASR4 | PLANT_TROUBLE | 104
2023 | nonsummer | RTEDDY_2_SRXSR4 | PLANT_MAINTENANCE | 40.8
2023 | nonsummer | RTEDDY_2_SRXSR4 | PLANT_TROUBLE | 54.4
2023 | nonsummer | RTREE_2_WIND1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | RTREE_2_WIND1 | PLANT_TROUBLE | 0
2023 | nonsummer | RTREE_2_WIND2 | PLANT_MAINTENANCE | 2855.25
2023 | nonsummer | RTREE_2_WIND2 | PLANT_TROUBLE | 1
2023 | nonsummer | RUSCTY_2_UNITS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2023 | nonsummer | RUSCTY_2_UNITS | AMBIENT_DUE_TO_TEMP | 17117.2033
2023 | nonsummer | RUSCTY_2_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 174.4167
2023 | nonsummer | RUSCTY_2_UNITS | PLANT_MAINTENANCE | 13970.4
2023 | nonsummer | RUSCTY_2_UNITS | PLANT_TROUBLE | 50435.6735
2023 | nonsummer | RUSCTY_2_UNITS | TRANSITIONAL_LIMITATION | 0
2023 | nonsummer | RUSCTY_2_UNITS | UNIT_TESTING | 0
2023 | nonsummer | RVRVEW_1_UNITA1 | AMBIENT_DUE_TO_TEMP | 7.215
2023 | nonsummer | RVRVEW_1_UNITA1 | METERING_TELEMETRY | 0
2023 | nonsummer | RVRVEW_1_UNITA1 | PLANT_TROUBLE | 1378.8083
2023 | nonsummer | RVRVEW_1_UNITA1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | RVRVEW_1_UNITA1 | UNIT_TESTING | 0
2023 | nonsummer | RVSIDE_2_RERCU3 | PLANT_TROUBLE | 245
2023 | nonsummer | RVSIDE_2_RERCU4 | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | RVSIDE_2_RERCU4 | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | nonsummer | RVSIDE_2_RERCU4 | PLANT_MAINTENANCE | 0
2023 | nonsummer | RVSIDE_2_RERCU4 | PLANT_TROUBLE | 0
2023 | nonsummer | RVSIDE_6_RERCU1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | RVSIDE_6_RERCU1 | PLANT_TROUBLE | 1450.5
2023 | nonsummer | RVSIDE_6_RERCU2 | PLANT_TROUBLE | 0
2023 | nonsummer | RVSIDE_6_SPRING | PLANT_MAINTENANCE | 225
2023 | nonsummer | RVSIDE_6_SPRING | PLANT_TROUBLE | 186.6667
2023 | nonsummer | RVSIDE_6_SPRING | UNIT_TESTING | 90
2023 | nonsummer | SALIRV_2_UNIT | ENVIRONMENTAL_RESTRICTIONS | 2242.5
2023 | nonsummer | SALIRV_2_UNIT | PLANT_MAINTENANCE | 7410
2023 | nonsummer | SALIRV_2_UNIT | PLANT_TROUBLE | 1218.1
2023 | nonsummer | SALTSP_7_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 9866.5333
2023 | nonsummer | SALTSP_7_UNITS | PLANT_MAINTENANCE | 0
2023 | nonsummer | SALTSP_7_UNITS | PLANT_TROUBLE | 1287.7667
2023 | nonsummer | SAMPSN_6_KELCO1 | PLANT_MAINTENANCE | 1375
2023 | nonsummer | SANBRN_2_EESSB2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2023 | nonsummer | SANBRN_2_EESSB2 | METERING_TELEMETRY | 0
2023 | nonsummer | SANBRN_2_EESSB2 | NEW_GENERATOR_TEST_ENERGY | 500
2023 | nonsummer | SANBRN_2_EESSB2 | PLANT_MAINTENANCE | 0
2023 | nonsummer | SANBRN_2_EESSB2 | PLANT_TROUBLE | 499.3333
2023 | nonsummer | SANBRN_2_EESSB2 | UNIT_TESTING | 679
2023 | nonsummer | SANBRN_2_ES1BT3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 500.0975
2023 | nonsummer | SANBRN_2_ES1BT3 | METERING_TELEMETRY | 403.44
2023 | nonsummer | SANBRN_2_ES1BT3 | PLANT_TROUBLE | 0
2023 | nonsummer | SANBRN_2_ES2SB3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 406
2023 | nonsummer | SANBRN_2_ES2SB3 | METERING_TELEMETRY | 336
2023 | nonsummer | SANBRN_2_ES2SB3 | PLANT_TROUBLE | 25.2
2023 | nonsummer | SANBRN_2_ESABT1 | METERING_TELEMETRY | 500
2023 | nonsummer | SANBRN_2_ESABT1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | SANBRN_2_ESABT1 | PLANT_TROUBLE | 550
2023 | nonsummer | SANBRN_2_ESABT1 | UNIT_TESTING | 375
2023 | nonsummer | SANBRN_2_ESBBT1 | METERING_TELEMETRY | 0
2023 | nonsummer | SANBRN_2_ESBBT1 | PLANT_MAINTENANCE | 350
2023 | nonsummer | SANBRN_2_ESBBT1 | PLANT_TROUBLE | 75
2023 | nonsummer | SANBRN_2_ESBBT1 | UNIT_TESTING | 0
2023 | nonsummer | SANBRN_2_SS2BT3 | METERING_TELEMETRY | 0
2023 | nonsummer | SANBRN_2_SS2BT3 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | SANBRN_2_SS2BT3 | PLANT_MAINTENANCE | 0
2023 | nonsummer | SANBRN_2_SS2BT3 | PLANT_TROUBLE | 348.7
2023 | nonsummer | SANBRN_2_SS2BT3 | UNIT_TESTING | 0
2023 | nonsummer | SANBRN_2_SS2BT4 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | SANBRN_2_SS2BT4 | PLANT_TROUBLE | 0
2023 | nonsummer | SANBRN_2_SS2BT4 | UNIT_TESTING | 0
2023 | nonsummer | SANBRN_2_SS2SB4 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2023 | nonsummer | SANBRN_2_SS2SB4 | METERING_TELEMETRY | 0
2023 | nonsummer | SANBRN_2_SS2SB4 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | SANBRN_2_SS2SB4 | PLANT_MAINTENANCE | 0
2023 | nonsummer | SANBRN_2_SS2SB4 | PLANT_TROUBLE | 144
2023 | nonsummer | SANBRN_2_SS2SB4 | UNIT_TESTING | 0
2023 | nonsummer | SANDLT_2_SUNITS | AMBIENT_DUE_TO_TEMP | 614.1667
2023 | nonsummer | SANDLT_2_SUNITS | AMBIENT_NOT_DUE_TO_TEMP | 30492.9167
2023 | nonsummer | SANDLT_2_SUNITS | PLANT_MAINTENANCE | 0
2023 | nonsummer | SANDLT_2_SUNITS | PLANT_TROUBLE | 0
2023 | nonsummer | SANITR_6_UNITS | PLANT_TROUBLE | 0
2023 | nonsummer | SANLOB_1_LNDFIL | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 7.5
2023 | nonsummer | SANLOB_1_LNDFIL | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | SANLOB_1_LNDFIL | AMBIENT_NOT_DUE_TO_TEMP | 97.5
2023 | nonsummer | SANLOB_1_LNDFIL | PLANT_MAINTENANCE | 10.2
2023 | nonsummer | SANLOB_1_LNDFIL | PLANT_TROUBLE | 139.2233
2023 | nonsummer | SANLOB_1_LNDFIL | TRANSMISSION_INDUCED | 1.7983
2023 | nonsummer | SANTFG_7_UNITS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 3007
2023 | nonsummer | SANTFG_7_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 12720
2023 | nonsummer | SANTFG_7_UNITS | PLANT_TROUBLE | 136.9333
2023 | nonsummer | SANTFG_7_UNITS | TRANSITIONAL_LIMITATION | 153
2023 | nonsummer | SANTFG_7_UNITS | TRANSMISSION_INDUCED | 0
2023 | nonsummer | SANTGO_2_LNDFL1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | SANTGO_2_LNDFL1 | PLANT_TROUBLE | 479.75
2023 | nonsummer | SANTGO_2_LNDFL1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | SANTGO_2_MABBT1 | PLANT_MAINTENANCE | 189.3
2023 | nonsummer | SANTGO_2_MABBT1 | PLANT_TROUBLE | 1055.141
2023 | nonsummer | SANWD_1_QF | PLANT_MAINTENANCE | 9039.6917
2023 | nonsummer | SANWD_1_QF | PLANT_TROUBLE | 129.7
2023 | nonsummer | SANWD_1_QF | TRANSMISSION_INDUCED | 0
2023 | nonsummer | SAUGUS_6_MWDFTH | PLANT_TROUBLE | 637
2023 | nonsummer | SAUGUS_7_CHIQCN | ENVIRONMENTAL_RESTRICTIONS | 640
2023 | nonsummer | SAUGUS_7_CHIQCN | PLANT_MAINTENANCE | 160
2023 | nonsummer | SBERDO_2_PSP3 | AMBIENT_DUE_TO_TEMP | 4097.8503
2023 | nonsummer | SBERDO_2_PSP3 | METERING_TELEMETRY | 865.0328
2023 | nonsummer | SBERDO_2_PSP3 | PLANT_MAINTENANCE | 578.5567
2023 | nonsummer | SBERDO_2_PSP3 | PLANT_TROUBLE | 20383.5463
2023 | nonsummer | SBERDO_2_PSP3 | TRANSITIONAL_LIMITATION | 912.5
2023 | nonsummer | SBERDO_2_PSP3 | UNIT_TESTING | 1182.2972
2023 | nonsummer | SBERDO_2_PSP4 | AMBIENT_DUE_TO_TEMP | 6476.6315
2023 | nonsummer | SBERDO_2_PSP4 | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | nonsummer | SBERDO_2_PSP4 | METERING_TELEMETRY | 15804.5
2023 | nonsummer | SBERDO_2_PSP4 | PLANT_MAINTENANCE | 10961.25
2023 | nonsummer | SBERDO_2_PSP4 | PLANT_TROUBLE | 55651.0612
2023 | nonsummer | SBERDO_2_PSP4 | UNIT_TESTING | 0
2023 | nonsummer | SBERDO_2_REDLND | PLANT_TROUBLE | 610
2023 | nonsummer | SBERDO_2_RTS005 | PLANT_TROUBLE | 512.5
2023 | nonsummer | SBERDO_2_RTS007 | PLANT_TROUBLE | 512.5
2023 | nonsummer | SBERDO_2_RTS011 | PLANT_TROUBLE | 17.5
2023 | nonsummer | SBERDO_2_RTS013 | PLANT_TROUBLE | 2292.5
2023 | nonsummer | SBERDO_2_RTS016 | PLANT_TROUBLE | 982.5
2023 | nonsummer | SBERDO_2_RTS048 | PLANT_TROUBLE | 1025
2023 | nonsummer | SBERDO_2_SNTANA | AMBIENT_NOT_DUE_TO_TEMP | 1883.75
2023 | nonsummer | SBERDO_2_SNTANA | PLANT_TROUBLE | 5448.5
2023 | nonsummer | SBERDO_6_MILLCK | AMBIENT_NOT_DUE_TO_TEMP | 1626.6167
2023 | nonsummer | SBERDO_6_MILLCK | PLANT_TROUBLE | 1092.7
2023 | nonsummer | SBERDO_6_MILLCK | TRANSMISSION_INDUCED | 63
2023 | nonsummer | SCEC_1_PDRP124 | ANNUAL_USE_LIMIT_REACHED | 76.86
2023 | nonsummer | SCEC_1_PDRP124 | MONTHLY_USE_LIMIT_REACHED | 3.66
2023 | nonsummer | SCEC_1_PDRP124 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 9.15
2023 | nonsummer | SCEC_1_PDRP16 | MONTHLY_USE_LIMIT_REACHED | 174.6
2023 | nonsummer | SCEC_1_PDRP17 | MONTHLY_USE_LIMIT_REACHED | 1399.5
2023 | nonsummer | SCEC_1_PDRP173 | MONTHLY_USE_LIMIT_REACHED | 37.91
2023 | nonsummer | SCEC_1_RDRR08 | METERING_TELEMETRY | 0
2023 | nonsummer | SCEC_1_RDRR08 | OTHER_USE_LIMIT_REACHED | 0
2023 | nonsummer | SCEC_1_RDRR35 | METERING_TELEMETRY | 0
2023 | nonsummer | SCEC_1_RDRR36 | METERING_TELEMETRY | 0
2023 | nonsummer | SCEC_1_RDRR37 | METERING_TELEMETRY | 0
2023 | nonsummer | SCEC_1_RDRR38 | METERING_TELEMETRY | 0
2023 | nonsummer | SCEHOV_2_HOOVER | AMBIENT_NOT_DUE_TO_TEMP | 8402.55
2023 | nonsummer | SCEHOV_2_HOOVER | OTHER_USE_LIMIT_REACHED | 0
2023 | nonsummer | SCEHOV_2_HOOVER | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 50226.75
2023 | nonsummer | SCEN_6_RDRR02 | METERING_TELEMETRY | 0
2023 | nonsummer | SCEN_6_RDRR02 | OTHER_USE_LIMIT_REACHED | 0
2023 | nonsummer | SCEN_6_RDRR12 | METERING_TELEMETRY | 0
2023 | nonsummer | SCEW_2_PDRP03 | MONTHLY_USE_LIMIT_REACHED | 85
2023 | nonsummer | SCEW_2_PDRP09 | MONTHLY_USE_LIMIT_REACHED | 45
2023 | nonsummer | SCEW_2_PDRP09 | OTHER_USE_LIMIT_REACHED | 162.5
2023 | nonsummer | SCEW_2_PDRP10 | ANNUAL_USE_LIMIT_REACHED | 12.5
2023 | nonsummer | SCEW_2_PDRP10 | OTHER_USE_LIMIT_REACHED | 375
2023 | nonsummer | SCEW_2_PDRP10 | PLANT_TROUBLE | 1134.75
2023 | nonsummer | SCEW_2_PDRP114 | MONTHLY_USE_LIMIT_REACHED | 109.99
2023 | nonsummer | SCEW_2_PDRP12 | MONTHLY_USE_LIMIT_REACHED | 54.8
2023 | nonsummer | SCEW_2_PDRP159 | ANNUAL_USE_LIMIT_REACHED | 407.68
2023 | nonsummer | SCEW_2_PDRP159 | MONTHLY_USE_LIMIT_REACHED | 14.56
2023 | nonsummer | SCEW_2_PDRP160 | ANNUAL_USE_LIMIT_REACHED | 123.66
2023 | nonsummer | SCEW_2_PDRP160 | MONTHLY_USE_LIMIT_REACHED | 77.86
2023 | nonsummer | SCEW_2_PDRP163 | MONTHLY_USE_LIMIT_REACHED | 139.23
2023 | nonsummer | SCEW_2_PDRP167 | ANNUAL_USE_LIMIT_REACHED | 1196.34
2023 | nonsummer | SCEW_2_PDRP167 | MONTHLY_USE_LIMIT_REACHED | 18.84
2023 | nonsummer | SCEW_2_PDRP167 | PLANT_MAINTENANCE | 47.1
2023 | nonsummer | SCEW_2_PDRP35 | MONTHLY_USE_LIMIT_REACHED | 945.3
2023 | nonsummer | SCEW_2_PDRP85 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 7.96
2023 | nonsummer | SCEW_2_RDRR08 | METERING_TELEMETRY | 0
2023 | nonsummer | SCEW_2_RDRR08 | OTHER_USE_LIMIT_REACHED | 0
2023 | nonsummer | SCEW_2_RDRR25 | METERING_TELEMETRY | 0
2023 | nonsummer | SCEW_2_RDRR26 | METERING_TELEMETRY | 0
2023 | nonsummer | SCHD_1_RDRR08 | METERING_TELEMETRY | 0
2023 | nonsummer | SCHD_1_RDRR08 | OTHER_USE_LIMIT_REACHED | 0
2023 | nonsummer | SCHD_1_RDRR11 | METERING_TELEMETRY | 0
2023 | nonsummer | SCHLTE_1_PL1X3 | AMBIENT_DUE_TO_TEMP | 679.68
2023 | nonsummer | SCHLTE_1_PL1X3 | PLANT_MAINTENANCE | 0
2023 | nonsummer | SCHLTE_1_PL1X3 | PLANT_TROUBLE | 1108.8893
2023 | nonsummer | SCHLTE_1_PL1X3 | TRANSMISSION_INDUCED | 2696.44
2023 | nonsummer | SCHNDR_1_FIVPTS | PLANT_TROUBLE | 225
2023 | nonsummer | SCHNDR_1_FIVPTS | TRANSMISSION_INDUCED | 0
2023 | nonsummer | SCHNDR_1_WSTSDE | METERING_TELEMETRY | 225
2023 | nonsummer | SCHNDR_1_WSTSDE | PLANT_MAINTENANCE | 17.75
2023 | nonsummer | SCHNDR_1_WSTSDE | PLANT_TROUBLE | 224
2023 | nonsummer | SCHNDR_1_WSTSDE | TRANSMISSION_INDUCED | 0
2023 | nonsummer | SCNW_6_PDRP05 | MONTHLY_USE_LIMIT_REACHED | 253
2023 | nonsummer | SCNW_6_PDRP57 | MONTHLY_USE_LIMIT_REACHED | 22.4
2023 | nonsummer | SCNW_6_PDRP61 | MONTHLY_USE_LIMIT_REACHED | 699.45
2023 | nonsummer | SCNW_6_RDRR08 | METERING_TELEMETRY | 0
2023 | nonsummer | SCNW_6_RDRR08 | OTHER_USE_LIMIT_REACHED | 0
2023 | nonsummer | SCNW_6_RDRR10 | METERING_TELEMETRY | 0
2023 | nonsummer | SEARLS_1_TS3SR1 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | SEARLS_1_TS3SR1 | PLANT_TROUBLE | 2.3333
2023 | nonsummer | SEARLS_7_ARGUS | PLANT_MAINTENANCE | 2810
2023 | nonsummer | SEARLS_7_ARGUS | PLANT_TROUBLE | 265
2023 | nonsummer | SEGS_1_SR2SL2 | METERING_TELEMETRY | 0
2023 | nonsummer | SEGS_1_SR2SL2 | PLANT_MAINTENANCE | 39.6667
2023 | nonsummer | SEGS_1_SR2SL2 | TRANSMISSION_INDUCED | 100
2023 | nonsummer | SENTNL_2_CTG1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 180
2023 | nonsummer | SENTNL_2_CTG1 | AMBIENT_DUE_TO_TEMP | 1096.06
2023 | nonsummer | SENTNL_2_CTG1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | SENTNL_2_CTG1 | ENVIRONMENTAL_RESTRICTIONS | 3569.7
2023 | nonsummer | SENTNL_2_CTG1 | PLANT_MAINTENANCE | 6990.2267
2023 | nonsummer | SENTNL_2_CTG1 | PLANT_TROUBLE | 1528.9607
2023 | nonsummer | SENTNL_2_CTG1 | UNIT_TESTING | 167.36
2023 | nonsummer | SENTNL_2_CTG2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 231.3
2023 | nonsummer | SENTNL_2_CTG2 | AMBIENT_DUE_TO_TEMP | 1858.47
2023 | nonsummer | SENTNL_2_CTG2 | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | SENTNL_2_CTG2 | ENVIRONMENTAL_RESTRICTIONS | 111.136
2023 | nonsummer | SENTNL_2_CTG2 | METERING_TELEMETRY | 18.469
2023 | nonsummer | SENTNL_2_CTG2 | PLANT_MAINTENANCE | 1562.85
2023 | nonsummer | SENTNL_2_CTG2 | PLANT_TROUBLE | 891.5653
2023 | nonsummer | SENTNL_2_CTG2 | UNIT_TESTING | 197.7488
2023 | nonsummer | SENTNL_2_CTG3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 246.3
2023 | nonsummer | SENTNL_2_CTG3 | AMBIENT_DUE_TO_TEMP | 1607.98
2023 | nonsummer | SENTNL_2_CTG3 | ENVIRONMENTAL_RESTRICTIONS | 3688.05
2023 | nonsummer | SENTNL_2_CTG3 | METERING_TELEMETRY | 18.45
2023 | nonsummer | SENTNL_2_CTG3 | PLANT_MAINTENANCE | 1585.35
2023 | nonsummer | SENTNL_2_CTG3 | PLANT_TROUBLE | 33004.8667
2023 | nonsummer | SENTNL_2_CTG3 | UNIT_TESTING | 178.45
2023 | nonsummer | SENTNL_2_CTG4 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 254.9
2023 | nonsummer | SENTNL_2_CTG4 | AMBIENT_DUE_TO_TEMP | 2498.23
2023 | nonsummer | SENTNL_2_CTG4 | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | SENTNL_2_CTG4 | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | nonsummer | SENTNL_2_CTG4 | METERING_TELEMETRY | 38.3717
2023 | nonsummer | SENTNL_2_CTG4 | PLANT_MAINTENANCE | 1598.25
2023 | nonsummer | SENTNL_2_CTG4 | PLANT_TROUBLE | 5084.6833
2023 | nonsummer | SENTNL_2_CTG4 | UNIT_TESTING | 33.93
2023 | nonsummer | SENTNL_2_CTG5 | AMBIENT_DUE_TO_TEMP | 1360.99
2023 | nonsummer | SENTNL_2_CTG5 | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | SENTNL_2_CTG5 | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | nonsummer | SENTNL_2_CTG5 | METERING_TELEMETRY | 0
2023 | nonsummer | SENTNL_2_CTG5 | PLANT_MAINTENANCE | 0
2023 | nonsummer | SENTNL_2_CTG5 | PLANT_TROUBLE | 33476.9557
2023 | nonsummer | SENTNL_2_CTG5 | UNIT_TESTING | 0
2023 | nonsummer | SENTNL_2_CTG6 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 239.4
2023 | nonsummer | SENTNL_2_CTG6 | AMBIENT_DUE_TO_TEMP | 1949.5433
2023 | nonsummer | SENTNL_2_CTG6 | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | SENTNL_2_CTG6 | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | nonsummer | SENTNL_2_CTG6 | METERING_TELEMETRY | 25.3
2023 | nonsummer | SENTNL_2_CTG6 | PLANT_MAINTENANCE | 1575
2023 | nonsummer | SENTNL_2_CTG6 | PLANT_TROUBLE | 1070.741
2023 | nonsummer | SENTNL_2_CTG6 | UNIT_TESTING | 141.1667
2023 | nonsummer | SENTNL_2_CTG7 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 180
2023 | nonsummer | SENTNL_2_CTG7 | AMBIENT_DUE_TO_TEMP | 2048.75
2023 | nonsummer | SENTNL_2_CTG7 | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | SENTNL_2_CTG7 | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | nonsummer | SENTNL_2_CTG7 | PLANT_MAINTENANCE | 1533
2023 | nonsummer | SENTNL_2_CTG7 | PLANT_TROUBLE | 8385.2233
2023 | nonsummer | SENTNL_2_CTG7 | UNIT_TESTING | 144
2023 | nonsummer | SENTNL_2_CTG8 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 257.9
2023 | nonsummer | SENTNL_2_CTG8 | AMBIENT_DUE_TO_TEMP | 2642.81
2023 | nonsummer | SENTNL_2_CTG8 | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | SENTNL_2_CTG8 | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | nonsummer | SENTNL_2_CTG8 | PLANT_MAINTENANCE | 6342.75
2023 | nonsummer | SENTNL_2_CTG8 | PLANT_TROUBLE | 1266.0508
2023 | nonsummer | SENTNL_2_CTG8 | UNIT_TESTING | 170.55
2023 | nonsummer | SGREGY_6_SANGER | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1207.5
2023 | nonsummer | SGREGY_6_SANGER | PLANT_MAINTENANCE | 5011.125
2023 | nonsummer | SGREGY_6_SANGER | PLANT_TROUBLE | 1952.125
2023 | nonsummer | SHANDN_2_SBBBM1 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | SHANDN_2_SBBBM1 | PLANT_TROUBLE | 0
2023 | nonsummer | SHANDN_2_SBBBM1 | UNIT_TESTING | 0
2023 | nonsummer | SHUTLE_6_CREST | PLANT_TROUBLE | 425
2023 | nonsummer | SIERRA_1_UNITS | AMBIENT_DUE_TO_TEMP | 2499.7827
2023 | nonsummer | SIERRA_1_UNITS | PLANT_TROUBLE | 452
2023 | nonsummer | SIGHEB_6_HE2SCEDYN | PLANT_MAINTENANCE | 0
2023 | nonsummer | SIGHEB_6_HE2SCEDYN | TRANSMISSION_INDUCED | 44
2023 | nonsummer | SIGHEB_6_MIRDYN | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | nonsummer | SIGHEB_6_MIRDYN | PLANT_MAINTENANCE | 0
2023 | nonsummer | SIGHEB_6_MIRDYN | PLANT_TROUBLE | 0
2023 | nonsummer | SIGHEB_6_MIRDYN | TRANSMISSION_INDUCED | 33
2023 | nonsummer | SISPRG_2_DS3BT1 | METERING_TELEMETRY | 0
2023 | nonsummer | SISPRG_2_DS3BT1 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | SISPRG_2_DS3BT1 | PLANT_TROUBLE | 352.35
2023 | nonsummer | SISPRG_2_DS3BT1 | UNIT_TESTING | 0
2023 | nonsummer | SISPRG_2_DS3BT2 | METERING_TELEMETRY | 0
2023 | nonsummer | SISPRG_2_DS3BT2 | PLANT_MAINTENANCE | 0
2023 | nonsummer | SISPRG_2_DS3BT2 | PLANT_TROUBLE | 199
2023 | nonsummer | SISPRG_2_DS3BT2 | UNIT_TESTING | 0
2023 | nonsummer | SISPRG_2_DS3BT3 | METERING_TELEMETRY | 0
2023 | nonsummer | SISPRG_2_DS3BT3 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | SISPRG_2_DS3BT3 | PLANT_TROUBLE | 705.75
2023 | nonsummer | SISPRG_2_DS3BT3 | RTU_RIG | 0
2023 | nonsummer | SISPRG_2_DS3BT3 | UNIT_TESTING | 0
2023 | nonsummer | SISPRG_2_DS3BT4 | METERING_TELEMETRY | 0
2023 | nonsummer | SISPRG_2_DS3BT4 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | SISPRG_2_DS3BT4 | PLANT_MAINTENANCE | 0
2023 | nonsummer | SISPRG_2_DS3BT4 | PLANT_TROUBLE | 222.22
2023 | nonsummer | SISPRG_2_DS3BT4 | UNIT_TESTING | 0
2023 | nonsummer | SISPRG_2_DS3SR1 | METERING_TELEMETRY | 0
2023 | nonsummer | SISPRG_2_DS3SR1 | NEW_GENERATOR_TEST_ENERGY | 2925
2023 | nonsummer | SISPRG_2_DS3SR1 | PLANT_TROUBLE | 54
2023 | nonsummer | SISPRG_2_DS3SR1 | UNIT_TESTING | 121
2023 | nonsummer | SISPRG_2_DS3SR2 | PLANT_MAINTENANCE | 512
2023 | nonsummer | SISPRG_2_DS3SR2 | PLANT_TROUBLE | 5790
2023 | nonsummer | SISPRG_2_DS3SR3 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | SISPRG_2_DS3SR3 | PLANT_TROUBLE | 0
2023 | nonsummer | SISPRG_2_DS3SR3 | UNIT_TESTING | 0
2023 | nonsummer | SISPRG_2_DS3SR4 | METERING_TELEMETRY | 0
2023 | nonsummer | SISPRG_2_DS3SR4 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | SISPRG_2_DS3SR4 | PLANT_MAINTENANCE | 0
2023 | nonsummer | SISPRG_2_DS3SR4 | PLANT_TROUBLE | 0
2023 | nonsummer | SISPRG_2_DS3SR4 | UNIT_TESTING | 0
2023 | nonsummer | SKERN_6_SOLAR1 | PLANT_MAINTENANCE | 165
2023 | nonsummer | SKERN_6_SOLAR1 | PLANT_TROUBLE | 100
2023 | nonsummer | SKERN_6_SOLAR1 | TRANSMISSION_INDUCED | 1005.6667
2023 | nonsummer | SKERN_6_SOLAR2 | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | SKERN_6_SOLAR2 | PLANT_TROUBLE | 0
2023 | nonsummer | SKERN_6_SOLAR2 | TRANSMISSION_INDUCED | 529.8333
2023 | nonsummer | SLATE_2_SLASR1 | METERING_TELEMETRY | 50.5
2023 | nonsummer | SLATE_2_SLASR1 | PLANT_MAINTENANCE | 207.1617
2023 | nonsummer | SLATE_2_SLASR1 | PLANT_TROUBLE | 1685.9333
2023 | nonsummer | SLATE_2_SLASR2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 372
2023 | nonsummer | SLATE_2_SLASR2 | METERING_TELEMETRY | 0
2023 | nonsummer | SLATE_2_SLASR2 | PLANT_MAINTENANCE | 93
2023 | nonsummer | SLATE_2_SLASR2 | PLANT_TROUBLE | 13334.475
2023 | nonsummer | SLATE_2_SLASR2 | UNIT_TESTING | 196.1083
2023 | nonsummer | SLATE_2_SLASR3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 311.625
2023 | nonsummer | SLATE_2_SLASR3 | METERING_TELEMETRY | 0
2023 | nonsummer | SLATE_2_SLASR3 | PLANT_MAINTENANCE | 67.5
2023 | nonsummer | SLATE_2_SLASR3 | PLANT_TROUBLE | 10511.825
2023 | nonsummer | SLATE_2_SLASR3 | UNIT_TESTING | 150.0767
2023 | nonsummer | SLATE_2_SLASR4 | AMBIENT_NOT_DUE_TO_TEMP | 7454.03
2023 | nonsummer | SLATE_2_SLASR4 | METERING_TELEMETRY | 157.5
2023 | nonsummer | SLATE_2_SLASR4 | PLANT_MAINTENANCE | 0
2023 | nonsummer | SLATE_2_SLASR4 | PLANT_TROUBLE | 292.572
2023 | nonsummer | SLATE_2_SLASR4 | UNIT_TESTING | 52
2023 | nonsummer | SLATE_2_SLASR5 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 3834.275
2023 | nonsummer | SLATE_2_SLASR5 | AMBIENT_NOT_DUE_TO_TEMP | 34.5
2023 | nonsummer | SLATE_2_SLASR5 | METERING_TELEMETRY | 26.8667
2023 | nonsummer | SLATE_2_SLASR5 | PLANT_MAINTENANCE | 0
2023 | nonsummer | SLATE_2_SLASR5 | PLANT_TROUBLE | 545.42
2023 | nonsummer | SLATE_2_SLASR5 | UNIT_TESTING | 26
2023 | nonsummer | SLRMS3_2_SRMSR1 | PLANT_MAINTENANCE | 2250
2023 | nonsummer | SLRMS3_2_SRMSR1 | PLANT_TROUBLE | 485
2023 | nonsummer | SLRMS3_2_SRMSR1 | TRANSMISSION_INDUCED | 513.5
2023 | nonsummer | SLST13_2_SOLAR1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | SLST13_2_SOLAR1 | PLANT_TROUBLE | 0
2023 | nonsummer | SLST13_2_SOLAR1 | TRANSMISSION_INDUCED | 20928.2
2023 | nonsummer | SLSTR1_2_SOLAR1 | PLANT_MAINTENANCE | 2557.5
2023 | nonsummer | SLSTR1_2_SOLAR1 | PLANT_TROUBLE | 890
2023 | nonsummer | SLSTR1_2_SOLAR1 | UNIT_TESTING | 0
2023 | nonsummer | SLSTR2_2_SOLAR2 | PLANT_MAINTENANCE | 0
2023 | nonsummer | SLSTR2_2_SOLAR2 | PLANT_TROUBLE | 370
2023 | nonsummer | SLUISP_2_UNITS | METERING_TELEMETRY | 4608.6
2023 | nonsummer | SLUISP_2_UNITS | PLANT_MAINTENANCE | 15991.15
2023 | nonsummer | SLUISP_2_UNITS | PLANT_TROUBLE | 0
2023 | nonsummer | SLYCRK_1_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 19.0667
2023 | nonsummer | SLYCRK_1_UNIT 1 | PLANT_TROUBLE | 47.6667
2023 | nonsummer | SLYCRK_1_UNIT 1 | TRANSMISSION_INDUCED | 130
2023 | nonsummer | SMPRIP_1_SMPSON | PLANT_MAINTENANCE | 0
2023 | nonsummer | SMPRIP_1_SMPSON | PLANT_TROUBLE | 0
2023 | nonsummer | SMPRIP_1_SMPSON | TRANSMISSION_INDUCED | 0
2023 | nonsummer | SMRCOS_6_LNDFIL | PLANT_MAINTENANCE | 0
2023 | nonsummer | SMUDGO_7_UNIT 1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 2476.1
2023 | nonsummer | SMUDGO_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 13709.5
2023 | nonsummer | SMUDGO_7_UNIT 1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | SMUDGO_7_UNIT 1 | PLANT_TROUBLE | 440.6667
2023 | nonsummer | SMUDGO_7_UNIT 1 | TRANSITIONAL_LIMITATION | 67.6
2023 | nonsummer | SMUDGO_7_UNIT 1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | SMYRNA_1_DL1SR1 | PLANT_TROUBLE | 0
2023 | nonsummer | SMYRNA_1_DL1SR1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | SNCLRA_2_HOWLNG | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | SNCLRA_2_HOWLNG | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | SNCLRA_2_HOWLNG | METERING_TELEMETRY | 266.18
2023 | nonsummer | SNCLRA_2_HOWLNG | PLANT_MAINTENANCE | 193.635
2023 | nonsummer | SNCLRA_2_HOWLNG | PLANT_TROUBLE | 1016.175
2023 | nonsummer | SNCLRA_2_SILBT1 | METERING_TELEMETRY | 0
2023 | nonsummer | SNCLRA_2_SILBT1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | SNCLRA_2_SILBT1 | PLANT_TROUBLE | 11.1833
2023 | nonsummer | SNCLRA_2_SILBT1 | UNIT_TESTING | 11
2023 | nonsummer | SNCLRA_2_UNIT | ENVIRONMENTAL_RESTRICTIONS | 11412.5
2023 | nonsummer | SNCLRA_2_UNIT1 | AMBIENT_NOT_DUE_TO_TEMP | 4727.3333
2023 | nonsummer | SNCLRA_2_UNIT1 | PLANT_MAINTENANCE | 43.3733
2023 | nonsummer | SNCLRA_2_UNIT1 | PLANT_TROUBLE | 960.0267
2023 | nonsummer | SNCLRA_2_VESBT1 | ICCP | 0
2023 | nonsummer | SNCLRA_2_VESBT1 | METERING_TELEMETRY | 500
2023 | nonsummer | SNCLRA_2_VESBT1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | SNCLRA_2_VESBT1 | PLANT_TROUBLE | 3250
2023 | nonsummer | SNCLRA_2_VESBT1 | UNIT_TESTING | 0
2023 | nonsummer | SNCLRA_6_OXGEN | PLANT_MAINTENANCE | 238.5
2023 | nonsummer | SNCLRA_6_OXGEN | PLANT_TROUBLE | 1812.6
2023 | nonsummer | SNCLRA_6_PROCGN | PLANT_TROUBLE | 269.0383
2023 | nonsummer | SNDBAR_7_UNIT 1 | PLANT_TROUBLE | 0
2023 | nonsummer | SNDBAR_7_UNIT 1 | TRANSMISSION_INDUCED | 92.88
2023 | nonsummer | SNMALF_6_UNITS | TRANSMISSION_INDUCED | 0
2023 | nonsummer | SNORA_2_SNRSLR | PLANT_TROUBLE | 0
2023 | nonsummer | SOLBLU_2_WSBBX2 | PLANT_MAINTENANCE | 1445.9
2023 | nonsummer | SOLBLU_2_WSBBX2 | PLANT_TROUBLE | 431.25
2023 | nonsummer | SOLBLU_2_WSBBX2 | UNIT_TESTING | 0
2023 | nonsummer | SOLBLU_2_WSBSX2 | PLANT_TROUBLE | 0
2023 | nonsummer | SOLBLU_2_WSBSX2 | UNIT_TESTING | 0
2023 | nonsummer | SOUTH_2_UNIT | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | SOUTH_2_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 63.5
2023 | nonsummer | SOUTH_2_UNIT | PLANT_TROUBLE | 26.4
2023 | nonsummer | SOUTH_2_UNIT | TRANSMISSION_INDUCED | 191.1083
2023 | nonsummer | SPAULD_6_UNIT 3 | AMBIENT_NOT_DUE_TO_TEMP | 2983.16
2023 | nonsummer | SPAULD_6_UNIT 3 | PLANT_TROUBLE | 0
2023 | nonsummer | SPAULD_6_UNIT 3 | TRANSMISSION_INDUCED | 327.3833
2023 | nonsummer | SPAULD_6_UNIT12 | AMBIENT_NOT_DUE_TO_TEMP | 624.62
2023 | nonsummer | SPAULD_6_UNIT12 | PLANT_TROUBLE | 1894.0933
2023 | nonsummer | SPAULD_6_UNIT12 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | SPBURN_2_UNIT 1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 96.8
2023 | nonsummer | SPBURN_2_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 10.15
2023 | nonsummer | SPBURN_2_UNIT 1 | PLANT_MAINTENANCE | 220
2023 | nonsummer | SPBURN_2_UNIT 1 | PLANT_TROUBLE | 1192.5167
2023 | nonsummer | SPBURN_7_SNOWMT | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 455
2023 | nonsummer | SPBURN_7_SNOWMT | AMBIENT_NOT_DUE_TO_TEMP | 1463.425
2023 | nonsummer | SPBURN_7_SNOWMT | PLANT_MAINTENANCE | 0
2023 | nonsummer | SPI LI_2_UNIT 1 | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | SPI LI_2_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 78
2023 | nonsummer | SPI LI_2_UNIT 1 | PLANT_MAINTENANCE | 258
2023 | nonsummer | SPI LI_2_UNIT 1 | PLANT_TROUBLE | 171.4267
2023 | nonsummer | SPI LI_2_UNIT 1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | SPIAND_1_ANDSN2 | PLANT_TROUBLE | 518.565
2023 | nonsummer | SPIAND_1_ANDSN2 | TRANSMISSION_INDUCED | 474.22
2023 | nonsummer | SPICER_1_UNITS | PLANT_MAINTENANCE | 0
2023 | nonsummer | SPICER_1_UNITS | PLANT_TROUBLE | 73.45
2023 | nonsummer | SPICER_1_UNITS | RTU_RIG | 65
2023 | nonsummer | SPICER_1_UNITS | TRANSMISSION_INDUCED | 138
2023 | nonsummer | SPICER_1_UNITS | UNIT_TESTING | 0
2023 | nonsummer | SPIFBD_1_PL1X2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 266.5
2023 | nonsummer | SPIFBD_1_PL1X2 | PLANT_MAINTENANCE | 37.5
2023 | nonsummer | SPIFBD_1_PL1X2 | PLANT_TROUBLE | 624.75
2023 | nonsummer | SPIFBD_1_PL1X2 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | SPOINT_2_MEADDYN | PLANT_MAINTENANCE | 22750
2023 | nonsummer | SPOINT_2_PARKERDYN | PLANT_MAINTENANCE | 14000
2023 | nonsummer | SPQUIN_6_SRPCQU | AMBIENT_NOT_DUE_TO_TEMP | 48
2023 | nonsummer | SPQUIN_6_SRPCQU | PLANT_MAINTENANCE | 622
2023 | nonsummer | SPQUIN_6_SRPCQU | PLANT_TROUBLE | 2635.5095
2023 | nonsummer | SPQUIN_6_SRPCQU | TRANSMISSION_INDUCED | 628.8
2023 | nonsummer | SPRGAP_1_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 597.65
2023 | nonsummer | SPRGAP_1_UNIT 1 | ENVIRONMENTAL_RESTRICTIONS | 210
2023 | nonsummer | SPRGAP_1_UNIT 1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | SPRGAP_1_UNIT 1 | PLANT_TROUBLE | 20
2023 | nonsummer | SPRGAP_1_UNIT 1 | TRANSMISSION_INDUCED | 16.2167
2023 | nonsummer | SPRGVL_2_EXETPV | METERING_TELEMETRY | 385
2023 | nonsummer | SPRGVL_2_EXETPV | PLANT_TROUBLE | 140
2023 | nonsummer | SPRGVL_2_LINDPV | PLANT_MAINTENANCE | 0
2023 | nonsummer | SPRGVL_2_LINDPV | TRANSMISSION_INDUCED | 0
2023 | nonsummer | SPRGVL_2_PORTPV | METERING_TELEMETRY | 0
2023 | nonsummer | SPRGVL_2_PORTPV | PLANT_MAINTENANCE | 0
2023 | nonsummer | SPRGVL_2_TULESC | ENVIRONMENTAL_RESTRICTIONS | 2637.5
2023 | nonsummer | SRINTL_6_UNIT | TRANSMISSION_INDUCED | 0
2023 | nonsummer | STANIS_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 506.6667
2023 | nonsummer | STANIS_7_UNIT 1 | PLANT_TROUBLE | 1471.1667
2023 | nonsummer | STANIS_7_UNIT 1 | TRANSMISSION_INDUCED | 144.2917
2023 | nonsummer | STANTN_2_SBEBX2 | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | STANTN_2_SBEBX2 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | STANTN_2_SBEBX2 | PLANT_MAINTENANCE | 0
2023 | nonsummer | STANTN_2_SBEBX2 | PLANT_TROUBLE | 0
2023 | nonsummer | STANTN_2_SBEBX2 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | STANTN_2_STAGT1 | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | STANTN_2_STAGT1 | METERING_TELEMETRY | 0
2023 | nonsummer | STANTN_2_STAGT1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | STANTN_2_STAGT1 | PLANT_TROUBLE | 733.9925
2023 | nonsummer | STANTN_2_STAGT2 | AMBIENT_DUE_TO_TEMP | 13.86
2023 | nonsummer | STANTN_2_STAGT2 | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | STANTN_2_STAGT2 | METERING_TELEMETRY | 0
2023 | nonsummer | STANTN_2_STAGT2 | PLANT_MAINTENANCE | 148.78
2023 | nonsummer | STANTN_2_STAGT2 | PLANT_TROUBLE | 671.93
2023 | nonsummer | STIGCT_2_LODI | AMBIENT_DUE_TO_TEMP | 5390.9
2023 | nonsummer | STIGCT_2_LODI | PLANT_MAINTENANCE | 230
2023 | nonsummer | STIGCT_2_LODI | PLANT_TROUBLE | 0
2023 | nonsummer | STNRES_1_UNIT | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 56.7233
2023 | nonsummer | STNRES_1_UNIT | PLANT_MAINTENANCE | 3935.025
2023 | nonsummer | STNRES_1_UNIT | TRANSMISSION_INDUCED | 0
2023 | nonsummer | STOILS_1_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | STOILS_1_UNITS | PLANT_MAINTENANCE | 2810
2023 | nonsummer | STOILS_1_UNITS | PLANT_TROUBLE | 3230
2023 | nonsummer | STRAUS_1_STRWD1 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | STRAUS_1_STRWD1 | PLANT_TROUBLE | 0
2023 | nonsummer | STROUD_6_SOLAR | PLANT_MAINTENANCE | 0
2023 | nonsummer | STROUD_6_SOLAR | PLANT_TROUBLE | 5040
2023 | nonsummer | STROUD_6_WWHSR1 | AMBIENT_NOT_DUE_TO_TEMP | 4.85
2023 | nonsummer | STROUD_6_WWHSR1 | PLANT_TROUBLE | 665.375
2023 | nonsummer | STROUD_6_WWHSR1 | TRANSMISSION_INDUCED | 25.15
2023 | nonsummer | SUMWHT_6_SWSSR1 | AMBIENT_NOT_DUE_TO_TEMP | 59.8167
2023 | nonsummer | SUMWHT_6_SWSSR1 | PLANT_TROUBLE | 579.5
2023 | nonsummer | SUMWHT_6_SWSSR1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | SUNCAT_2_A1ABT1 | PLANT_TROUBLE | 10535.999
2023 | nonsummer | SUNCAT_2_A1ABT1 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2023 | nonsummer | SUNCAT_2_A1ABT1 | UNIT_TESTING | 242.8333
2023 | nonsummer | SUNCAT_2_A1BBT1 | PLANT_TROUBLE | 15289.1357
2023 | nonsummer | SUNCAT_2_A1BBT1 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 107.6667
2023 | nonsummer | SUNCAT_2_A2ABT2 | PLANT_TROUBLE | 18036.3
2023 | nonsummer | SUNCAT_2_A2ABT2 | UNIT_TESTING | 503.8333
2023 | nonsummer | SUNCAT_2_A2BSR2 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | SUNCAT_2_A2BSR2 | PLANT_MAINTENANCE | 0
2023 | nonsummer | SUNCAT_2_A2BSR2 | UNIT_TESTING | 0
2023 | nonsummer | SUNRIS_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 7418.1
2023 | nonsummer | SUNRIS_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 18683.8307
2023 | nonsummer | SUNRIS_2_PL1X3 | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | nonsummer | SUNRIS_2_PL1X3 | PLANT_MAINTENANCE | 2946.1
2023 | nonsummer | SUNRIS_2_PL1X3 | PLANT_MAINTENANCE | 27063.57
2023 | nonsummer | SUNRIS_2_PL1X3 | PLANT_TROUBLE | 0
2023 | nonsummer | SUNRIS_2_PL1X3 | PLANT_TROUBLE | 11022.1493
2023 | nonsummer | SUNRIS_2_PL1X3 | TRANSITIONAL_LIMITATION | 0
2023 | nonsummer | SUNRIS_2_PL1X3 | TRANSMISSION_INDUCED | 1103.1
2023 | nonsummer | SUNRIS_2_PL1X3 | UNIT_SUPPORTING_STARTUP | 0
2023 | nonsummer | SUNRIS_2_PL1X3 | UNIT_TESTING | 0
2023 | nonsummer | SUNRIS_2_PL1X3 | UNIT_TESTING | 669.586
2023 | nonsummer | SUNSET_2_UNITS | AMBIENT_DUE_TO_TEMP | 4179
2023 | nonsummer | SUNSET_2_UNITS | PLANT_MAINTENANCE | 2310
2023 | nonsummer | SUNSET_2_UNITS | PLANT_TROUBLE | 0
2023 | nonsummer | SUNSHN_2_LNDFL | AMBIENT_DUE_TO_TEMP | 11.1333
2023 | nonsummer | SUNSHN_2_LNDFL | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | SUNSHN_2_LNDFL | METERING_TELEMETRY | 47.95
2023 | nonsummer | SUNSHN_2_LNDFL | PLANT_MAINTENANCE | 1481.3342
2023 | nonsummer | SUNSHN_2_LNDFL | PLANT_TROUBLE | 3273.4167
2023 | nonsummer | SUNSHN_2_LNDFL | TRANSMISSION_INDUCED | 0
2023 | nonsummer | SUNSLR_1_SSVSR1 | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | nonsummer | SUNSLR_1_SSVSR1 | METERING_TELEMETRY | 0
2023 | nonsummer | SUNSLR_1_SSVSR1 | PLANT_MAINTENANCE | 162
2023 | nonsummer | SUNSLR_1_SSVSR1 | PLANT_TROUBLE | 3160
2023 | nonsummer | SUNSPT_2_WNASR1 | METERING_TELEMETRY | 0
2023 | nonsummer | SUNSPT_2_WNASR1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | SUNSPT_2_WNASR1 | PLANT_TROUBLE | 83.25
2023 | nonsummer | SUNSPT_2_WNASR1 | TRANSMISSION_INDUCED | 40
2023 | nonsummer | SUNST2_5_SS2SR1 | PLANT_MAINTENANCE | 207.5
2023 | nonsummer | SUNSTR_5_SS1SCEDYN | PLANT_MAINTENANCE | 657.5
2023 | nonsummer | SUNSTR_5_SS1SCEDYN | PLANT_TROUBLE | 2250
2023 | nonsummer | SUTTER_2_CISO | AMBIENT_DUE_TO_TEMP | 2420
2023 | nonsummer | SUTTER_2_CISO | PLANT_MAINTENANCE | 0
2023 | nonsummer | SUTTER_2_CISO | PLANT_TROUBLE | 25230.48
2023 | nonsummer | SUTTER_2_CISO | TRANSITIONAL_LIMITATION | 0
2023 | nonsummer | SUTTER_2_CISO | UNIT_TESTING | 47.475
2023 | nonsummer | SYCAMR_2_UNIT 1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | SYCAMR_2_UNIT 1 | PLANT_TROUBLE | 15919.5
2023 | nonsummer | SYCAMR_2_UNIT 1 | UNIT_TESTING | 0
2023 | nonsummer | SYCAMR_2_UNIT 2 | PLANT_MAINTENANCE | 7980
2023 | nonsummer | SYCAMR_2_UNIT 2 | PLANT_TROUBLE | 17249
2023 | nonsummer | SYCAMR_2_UNIT 3 | PLANT_MAINTENANCE | 2106.5333
2023 | nonsummer | SYCAMR_2_UNIT 3 | PLANT_TROUBLE | 39.4667
2023 | nonsummer | SYCAMR_2_UNIT 4 | PLANT_MAINTENANCE | 1431.4667
2023 | nonsummer | SYCAMR_2_UNIT 4 | PLANT_TROUBLE | 8349.7667
2023 | nonsummer | TANHIL_6_SOLART | AMBIENT_NOT_DUE_TO_TEMP | 31
2023 | nonsummer | TANHIL_6_SOLART | METERING_TELEMETRY | 85
2023 | nonsummer | TANHIL_6_SOLART | PLANT_MAINTENANCE | 143.8833
2023 | nonsummer | TANHIL_6_SOLART | PLANT_TROUBLE | 190.3
2023 | nonsummer | TANHIL_6_SOLART | TRANSMISSION_INDUCED | 289
2023 | nonsummer | TBLMTN_6_QF | AMBIENT_NOT_DUE_TO_TEMP | 119
2023 | nonsummer | TBLMTN_6_QF | PLANT_MAINTENANCE | 0
2023 | nonsummer | TBLMTN_6_QF | PLANT_TROUBLE | 926.5
2023 | nonsummer | TBLMTN_6_QF | TRANSMISSION_INDUCED | 8.5
2023 | nonsummer | TECOLOTE_3_WBDYN | AMBIENT_DUE_TO_TEMP | 930
2023 | nonsummer | TECOLOTE_3_WBDYN | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | nonsummer | TECOLOTE_3_WBDYN | PLANT_MAINTENANCE | 186
2023 | nonsummer | TECOLOTE_3_WBDYN | PLANT_TROUBLE | 293.86
2023 | nonsummer | TECOLOTE_3_WBDYN | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 2392
2023 | nonsummer | TECOLOTE_3_WBDYN | TRANSITIONAL_LIMITATION | 1572.12
2023 | nonsummer | TECOLOTE_3_WBDYN | TRANSMISSION_INDUCED | 60432.2073
2023 | nonsummer | TEHAPI_2_PW1WD1 | PLANT_TROUBLE | 831.4
2023 | nonsummer | TEHAPI_2_PW1WD1 | TRANSMISSION_INDUCED | 1424.7
2023 | nonsummer | TEHAPI_2_PW2WD2 | PLANT_TROUBLE | 117.12
2023 | nonsummer | TEHAPI_2_PW2WD2 | TRANSMISSION_INDUCED | 1537.44
2023 | nonsummer | TEHAPI_2_WIND1 | METERING_TELEMETRY | 149.5367
2023 | nonsummer | TEHAPI_2_WIND1 | PLANT_MAINTENANCE | 9.925
2023 | nonsummer | TEHAPI_2_WIND1 | TRANSMISSION_INDUCED | 724.525
2023 | nonsummer | TEHAPI_2_WIND2 | METERING_TELEMETRY | 178.2387
2023 | nonsummer | TEHAPI_2_WIND2 | PLANT_MAINTENANCE | 0
2023 | nonsummer | TEHAPI_2_WIND2 | PLANT_TROUBLE | 74.9233
2023 | nonsummer | TEHAPI_2_WIND2 | TRANSMISSION_INDUCED | 863.59
2023 | nonsummer | TENGEN_2_PL1X2 | PLANT_MAINTENANCE | 5569
2023 | nonsummer | TENGEN_2_PL1X2 | PLANT_TROUBLE | 377
2023 | nonsummer | TENGEN_2_PL1X2 | TRANSMISSION_INDUCED | 263.9
2023 | nonsummer | TENGEN_2_PL1X2 | UNIT_TESTING | 46.3633
2023 | nonsummer | TERMEX_2_PL1X3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 6250
2023 | nonsummer | TERMEX_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 2346
2023 | nonsummer | TERMEX_2_PL1X3 | PLANT_MAINTENANCE | 9375
2023 | nonsummer | TERMEX_2_PL1X3 | PLANT_TROUBLE | 1218.1667
2023 | nonsummer | TERMEX_2_PL1X3 | UNIT_TESTING | 1505
2023 | nonsummer | TIDWTR_2_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | TIDWTR_2_UNITS | PLANT_MAINTENANCE | 0
2023 | nonsummer | TIDWTR_2_UNITS | PLANT_TROUBLE | 4355
2023 | nonsummer | TIFFNY_1_DILLON | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | TIFFNY_1_DILLON | PLANT_TROUBLE | 270
2023 | nonsummer | TIFFNY_1_DILLON | TRANSMISSION_INDUCED | 1505.2293
2023 | nonsummer | TIGRCK_7_UNITS | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | TIGRCK_7_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 11539.9333
2023 | nonsummer | TIGRCK_7_UNITS | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | nonsummer | TIGRCK_7_UNITS | PLANT_MAINTENANCE | 0
2023 | nonsummer | TIGRCK_7_UNITS | PLANT_TROUBLE | 3968.6417
2023 | nonsummer | TITANS_2_TTSSR1 | PLANT_MAINTENANCE | 210
2023 | nonsummer | TITANS_2_TTSSR1 | PLANT_TROUBLE | 3774.7417
2023 | nonsummer | TITANS_2_TTSSR1 | TRANSMISSION_INDUCED | 861
2023 | nonsummer | TITANS_2_TTSSR1 | UNIT_TESTING | 0
2023 | nonsummer | TKOPWR_6_HYDRO | TRANSMISSION_INDUCED | 87.73
2023 | nonsummer | TOADTW_6_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | TOADTW_6_UNIT | ENVIRONMENTAL_RESTRICTIONS | 142.15
2023 | nonsummer | TOADTW_6_UNIT | PLANT_TROUBLE | 0
2023 | nonsummer | TOADTW_6_UNIT | TRANSMISSION_INDUCED | 55.95
2023 | nonsummer | TOPAZ_2_SOLAR | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | nonsummer | TOPAZ_2_SOLAR | PLANT_MAINTENANCE | 250
2023 | nonsummer | TOPAZ_2_SOLAR | PLANT_TROUBLE | 48545.9
2023 | nonsummer | TOPAZ_2_SOLAR | TRANSMISSION_INDUCED | 0
2023 | nonsummer | TOPAZ_2_SOLAR | UNIT_TESTING | 0
2023 | nonsummer | TORTLA_1_SOLAR | AMBIENT_NOT_DUE_TO_TEMP | 88
2023 | nonsummer | TORTLA_1_SOLAR | PLANT_TROUBLE | 100
2023 | nonsummer | TORTLA_1_SOLAR | TRANSMISSION_INDUCED | 0
2023 | nonsummer | TOWNSITE_2_MEADDYN | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2023 | nonsummer | TOWNSITE_2_MEADDYN | METERING_TELEMETRY | 0
2023 | nonsummer | TOWNSITE_2_MEADDYN | PLANT_MAINTENANCE | 1383.6875
2023 | nonsummer | TOWNSITE_2_MEADDYN | PLANT_TROUBLE | 1373
2023 | nonsummer | TOWNSITE_2_MEADDYN | RTU_RIG | 0
2023 | nonsummer | TRNQL8_2_AMASR1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | TRNQL8_2_AZUSR1 | PLANT_TROUBLE | 0
2023 | nonsummer | TRNQL8_2_ROJSR1 | PLANT_MAINTENANCE | 685
2023 | nonsummer | TRNQL8_2_ROJSR1 | PLANT_TROUBLE | 1456.5
2023 | nonsummer | TRNQL8_2_VERSR1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | TRNQL8_2_VERSR1 | PLANT_TROUBLE | 198
2023 | nonsummer | TRNQLT_2_RETBT1 | METERING_TELEMETRY | 1567.8667
2023 | nonsummer | TRNQLT_2_RETBT1 | PLANT_MAINTENANCE | 1507
2023 | nonsummer | TRNQLT_2_RETBT1 | PLANT_TROUBLE | 11821.6667
2023 | nonsummer | TRNQLT_2_RETBT1 | UNIT_TESTING | 2881.2
2023 | nonsummer | TRNQLT_2_SOLAR | METERING_TELEMETRY | 80.25
2023 | nonsummer | TRNQLT_2_SOLAR | PLANT_MAINTENANCE | 1367.75
2023 | nonsummer | TRNQLT_2_SOLAR | PLANT_TROUBLE | 5009.4207
2023 | nonsummer | TRNQLT_2_SOLAR | UNIT_TESTING | 224.9333
2023 | nonsummer | TRNSWD_1_QF | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | TRNSWD_1_QF | METERING_TELEMETRY | 5320.4928
2023 | nonsummer | TRNSWD_1_QF | PLANT_TROUBLE | 27399.1463
2023 | nonsummer | TRNSWD_1_QF | TRANSMISSION_INDUCED | 30
2023 | nonsummer | TULARE_2_TFCBM1 | PLANT_TROUBLE | 14
2023 | nonsummer | TULARE_2_TFCBM1 | UNIT_TESTING | 0
2023 | nonsummer | TULEWD_1_TULWD1 | AMBIENT_DUE_TO_TEMP | 560.1667
2023 | nonsummer | TULEWD_1_TULWD1 | ENVIRONMENTAL_RESTRICTIONS | 861.75
2023 | nonsummer | TULEWD_1_TULWD1 | METERING_TELEMETRY | 0
2023 | nonsummer | TULEWD_1_TULWD1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | TULEWD_1_TULWD1 | PLANT_TROUBLE | 1308.5
2023 | nonsummer | TULEWD_1_TULWD1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | TULLCK_7_UNITS | PLANT_MAINTENANCE | 228.18
2023 | nonsummer | TULLCK_7_UNITS | PLANT_TROUBLE | 0
2023 | nonsummer | TULLCK_7_UNITS | TRANSMISSION_INDUCED | 0
2023 | nonsummer | TUPMAN_1_BIOGAS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 3
2023 | nonsummer | TUPMAN_1_BIOGAS | PLANT_MAINTENANCE | 0
2023 | nonsummer | TUPMAN_1_BIOGAS | PLANT_TROUBLE | 0
2023 | nonsummer | TVYVLY_6_KRSHY1 | AMBIENT_NOT_DUE_TO_TEMP | 955.4
2023 | nonsummer | TVYVLY_6_KRSHY1 | PLANT_TROUBLE | 26
2023 | nonsummer | TWISSL_6_SOLAR1 | AMBIENT_NOT_DUE_TO_TEMP | 800
2023 | nonsummer | TWISSL_6_SOLAR1 | METERING_TELEMETRY | 800
2023 | nonsummer | TX-ELK_6_ECKSR2 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | TX-ELK_6_SOLAR1 | METERING_TELEMETRY | 0
2023 | nonsummer | TX-ELK_6_SOLAR1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | TXMCKT_6_UNIT | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | TXMCKT_6_UNIT | METERING_TELEMETRY | 0
2023 | nonsummer | TXMCKT_6_UNIT | PLANT_MAINTENANCE | 236.5483
2023 | nonsummer | TXMCKT_6_UNIT | PLANT_TROUBLE | 1719.95
2023 | nonsummer | TXMCKT_6_UNIT | TRANSMISSION_INDUCED | 1008
2023 | nonsummer | UKIAH_7_LAKEMN | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 35
2023 | nonsummer | UKIAH_7_LAKEMN | AMBIENT_NOT_DUE_TO_TEMP | 315
2023 | nonsummer | UKIAH_7_LAKEMN | PLANT_MAINTENANCE | 0
2023 | nonsummer | UKIAH_7_LAKEMN | PLANT_TROUBLE | 114.7917
2023 | nonsummer | UKIAH_7_LAKEMN | TRANSMISSION_INDUCED | 0.058333
2023 | nonsummer | ULTPCH_1_UCSBT1 | TRANSMISSION_INDUCED | 141.6667
2023 | nonsummer | ULTPCH_1_UNIT 1 | AMBIENT_DUE_TO_TEMP | 948
2023 | nonsummer | ULTPCH_1_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 195
2023 | nonsummer | ULTPCH_1_UNIT 1 | METERING_TELEMETRY | 0
2023 | nonsummer | ULTPCH_1_UNIT 1 | PLANT_MAINTENANCE | 18
2023 | nonsummer | ULTPCH_1_UNIT 1 | PLANT_TROUBLE | 1482.9
2023 | nonsummer | ULTPCH_1_UNIT 1 | TRANSITIONAL_LIMITATION | 0
2023 | nonsummer | ULTPCH_1_UNIT 1 | TRANSMISSION_INDUCED | 180
2023 | nonsummer | ULTPFR_1_UNIT 1 | PLANT_MAINTENANCE | 1798.7052
2023 | nonsummer | ULTPFR_1_UNIT 1 | PLANT_TROUBLE | 4567.3698
2023 | nonsummer | ULTRCK_2_UNIT | ENVIRONMENTAL_RESTRICTIONS | 34.5
2023 | nonsummer | ULTRCK_2_UNIT | PLANT_MAINTENANCE | 0
2023 | nonsummer | ULTRCK_2_UNIT | PLANT_TROUBLE | 3948.5383
2023 | nonsummer | ULTRCK_2_UNIT | UNIT_TESTING | 0
2023 | nonsummer | UNCHEM_1_UNIT | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 11006
2023 | nonsummer | UNCHEM_1_UNIT | PLANT_TROUBLE | 7500
2023 | nonsummer | UNVRSY_1_UNIT 1 | PLANT_MAINTENANCE | 570
2023 | nonsummer | UNVRSY_1_UNIT 1 | PLANT_TROUBLE | 6671.5333
2023 | nonsummer | UNVRSY_1_UNIT 1 | TRANSMISSION_INDUCED | 3420
2023 | nonsummer | USWND2_1_WIND1 | PLANT_TROUBLE | 3213.506
2023 | nonsummer | USWND2_1_WIND1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | USWND2_1_WIND2 | PLANT_MAINTENANCE | 2700.408
2023 | nonsummer | USWND2_1_WIND2 | PLANT_TROUBLE | 0
2023 | nonsummer | USWND2_1_WIND2 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | USWND2_1_WIND3 | METERING_TELEMETRY | 1.5333
2023 | nonsummer | USWND2_1_WIND3 | PLANT_MAINTENANCE | 0
2023 | nonsummer | USWND2_1_WIND3 | PLANT_TROUBLE | 3658.335
2023 | nonsummer | USWND2_1_WIND3 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | USWND4_2_UNIT2 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | USWNDR_2_LABWD1 | PLANT_MAINTENANCE | 1585.425
2023 | nonsummer | USWNDR_2_LABWD1 | TRANSMISSION_INDUCED | 4.65
2023 | nonsummer | USWNDR_2_SMUD | PLANT_TROUBLE | 368.31
2023 | nonsummer | USWNDR_2_SMUD2 | PLANT_MAINTENANCE | 766.8
2023 | nonsummer | USWNDR_2_SMUD2 | PLANT_TROUBLE | 324
2023 | nonsummer | USWNDR_2_SMUD2 | TRANSMISSION_INDUCED | 4.26
2023 | nonsummer | USWPFK_6_FRICK | PLANT_MAINTENANCE | 0
2023 | nonsummer | USWPFK_6_FRICK | PLANT_TROUBLE | 0
2023 | nonsummer | USWPFK_6_FRICK | TRANSMISSION_INDUCED | 306
2023 | nonsummer | USWPJR_2_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | USWPJR_2_UNITS | METERING_TELEMETRY | 187.9483
2023 | nonsummer | USWPJR_2_UNITS | PLANT_MAINTENANCE | 5684.8367
2023 | nonsummer | USWPJR_2_UNITS | PLANT_TROUBLE | 0
2023 | nonsummer | USWPJR_2_UNITS | TRANSMISSION_INDUCED | 3726
2023 | nonsummer | VACADX_1_UNITA1 | PLANT_MAINTENANCE | 1674.9627
2023 | nonsummer | VACADX_1_UNITA1 | PLANT_TROUBLE | 965.9547
2023 | nonsummer | VALLEY_5_PERRIS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1424.1407
2023 | nonsummer | VALLEY_5_PERRIS | AMBIENT_NOT_DUE_TO_TEMP | 5955
2023 | nonsummer | VALLEY_5_PERRIS | PLANT_TROUBLE | 0
2023 | nonsummer | VALLEY_5_REDMTN | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 30.7783
2023 | nonsummer | VALLEY_5_REDMTN | PLANT_MAINTENANCE | 5.9
2023 | nonsummer | VALLEY_5_SOLAR2 | PLANT_MAINTENANCE | 80
2023 | nonsummer | VALTNE_2_AVASR1 | METERING_TELEMETRY | 66.6667
2023 | nonsummer | VALTNE_2_AVASR1 | PLANT_MAINTENANCE | 350
2023 | nonsummer | VALTNE_2_AVASR1 | PLANT_TROUBLE | 0
2023 | nonsummer | VALTNE_2_TBBBT1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | VALTNE_2_TBBBT1 | PLANT_TROUBLE | 232
2023 | nonsummer | VALTNE_2_TBBBT1 | UNIT_TESTING | 0
2023 | nonsummer | VALTNE_2_TRSBT1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | VALTNE_2_TRSBT1 | UNIT_TESTING | 0
2023 | nonsummer | VEDDER_1_SEKERN | PLANT_TROUBLE | 13053.5
2023 | nonsummer | VEDDER_1_SEKERN | TRANSMISSION_INDUCED | 0
2023 | nonsummer | VEGA_6_SOLAR1 | METERING_TELEMETRY | 0
2023 | nonsummer | VEGA_6_SOLAR1 | PLANT_MAINTENANCE | 60
2023 | nonsummer | VEGA_6_SOLAR1 | PLANT_TROUBLE | 0
2023 | nonsummer | VEGA_6_SOLAR1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | VENWD_1_WIND3 | PLANT_MAINTENANCE | 145.95
2023 | nonsummer | VENWD_1_WIND3 | PLANT_TROUBLE | 0
2023 | nonsummer | VENWD_1_WIND3 | TRANSMISSION_INDUCED | 445.3
2023 | nonsummer | VERNON_6_GONZL1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | VERNON_6_GONZL1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | VERNON_6_GONZL1 | PLANT_TROUBLE | 511.75
2023 | nonsummer | VERNON_6_GONZL1 | UNIT_TESTING | 0
2023 | nonsummer | VERNON_6_GONZL2 | OTHER_USE_LIMIT_REACHED | 0
2023 | nonsummer | VERNON_6_GONZL2 | PLANT_MAINTENANCE | 460
2023 | nonsummer | VERNON_6_GONZL2 | PLANT_TROUBLE | 0
2023 | nonsummer | VERNON_6_GONZL2 | UNIT_TESTING | 0
2023 | nonsummer | VERNON_6_MALBRG | PLANT_MAINTENANCE | 4170
2023 | nonsummer | VERNON_6_MALBRG | PLANT_TROUBLE | 355
2023 | nonsummer | VESTAL_2_KERN | AMBIENT_NOT_DUE_TO_TEMP | 18967.8367
2023 | nonsummer | VESTAL_2_KERN | PLANT_TROUBLE | 0
2023 | nonsummer | VESTAL_2_RTS042 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | VESTAL_2_SOLAR1 | METERING_TELEMETRY | 0
2023 | nonsummer | VESTAL_2_SOLAR1 | RTU_RIG | 0
2023 | nonsummer | VESTAL_2_SOLAR1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | VESTAL_2_SOLAR2 | PLANT_TROUBLE | 910
2023 | nonsummer | VESTAL_2_SOLAR2 | RTU_RIG | 0
2023 | nonsummer | VESTAL_2_SOLAR2 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | VESTAL_2_TS5SR1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 84.15
2023 | nonsummer | VESTAL_2_TS5SR1 | METERING_TELEMETRY | 0
2023 | nonsummer | VESTAL_2_TS5SR1 | PLANT_MAINTENANCE | 54
2023 | nonsummer | VESTAL_2_TS5SR1 | PLANT_TROUBLE | 4381.8923
2023 | nonsummer | VESTAL_2_TS5SR1 | TRANSMISSION_INDUCED | 276
2023 | nonsummer | VESTAL_2_UNIT1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | VESTAL_2_WELLHD | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | VESTAL_2_WELLHD | AMBIENT_NOT_DUE_TO_TEMP | 9
2023 | nonsummer | VESTAL_2_WELLHD | PLANT_MAINTENANCE | 2716.2333
2023 | nonsummer | VESTAL_2_WELLHD | PLANT_TROUBLE | 65.3333
2023 | nonsummer | VESTAL_2_WELLHD | TRANSMISSION_INDUCED | 0
2023 | nonsummer | VESTAL_2_WELLHD | UNIT_TESTING | 147
2023 | nonsummer | VESTAL_6_QF | AMBIENT_NOT_DUE_TO_TEMP | 11873.5
2023 | nonsummer | VESTAL_6_QF | PLANT_TROUBLE | 341.75
2023 | nonsummer | VICTOR_1_CREST | METERING_TELEMETRY | 0
2023 | nonsummer | VICTOR_1_CREST | PLANT_MAINTENANCE | 90
2023 | nonsummer | VICTOR_1_CREST | PLANT_TROUBLE | 37.875
2023 | nonsummer | VICTOR_1_CREST | TRANSMISSION_INDUCED | 0
2023 | nonsummer | VICTOR_1_EXSLRA | METERING_TELEMETRY | 0
2023 | nonsummer | VICTOR_1_EXSLRA | PLANT_TROUBLE | 57.8
2023 | nonsummer | VICTOR_1_EXSLRA | RTU_RIG | 0
2023 | nonsummer | VICTOR_1_EXSLRA | TRANSMISSION_INDUCED | 0
2023 | nonsummer | VICTOR_1_EXSLRB | METERING_TELEMETRY | 0
2023 | nonsummer | VICTOR_1_EXSLRB | PLANT_TROUBLE | 28.1667
2023 | nonsummer | VICTOR_1_EXSLRB | TRANSMISSION_INDUCED | 0
2023 | nonsummer | VICTOR_1_LVSLR1 | PLANT_MAINTENANCE | 10
2023 | nonsummer | VICTOR_1_LVSLR1 | PLANT_TROUBLE | 0
2023 | nonsummer | VICTOR_1_LVSLR1 | TRANSMISSION_INDUCED | 63.6667
2023 | nonsummer | VICTOR_1_LVSLR2 | PLANT_TROUBLE | 0
2023 | nonsummer | VICTOR_1_LVSLR2 | TRANSMISSION_INDUCED | 127.3333
2023 | nonsummer | VICTOR_1_SOLAR1 | METERING_TELEMETRY | 1032.5
2023 | nonsummer | VICTOR_1_SOLAR1 | PLANT_MAINTENANCE | 87.5
2023 | nonsummer | VICTOR_1_SOLAR1 | PLANT_TROUBLE | 1155.2917
2023 | nonsummer | VICTOR_1_SOLAR1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | VICTOR_1_SOLAR2 | METERING_TELEMETRY | 0
2023 | nonsummer | VICTOR_1_SOLAR2 | PLANT_TROUBLE | 231
2023 | nonsummer | VICTOR_1_SOLAR2 | TRANSMISSION_INDUCED | 100
2023 | nonsummer | VICTOR_1_SOLAR3 | PLANT_MAINTENANCE | 11.55
2023 | nonsummer | VICTOR_1_SOLAR3 | PLANT_TROUBLE | 0
2023 | nonsummer | VICTOR_1_SOLAR4 | PLANT_MAINTENANCE | 18.3333
2023 | nonsummer | VICTOR_1_SOLAR4 | PLANT_TROUBLE | 0
2023 | nonsummer | VICTOR_1_VDRYFA | METERING_TELEMETRY | 0
2023 | nonsummer | VICTOR_1_VDRYFA | PLANT_MAINTENANCE | 9.4167
2023 | nonsummer | VICTOR_1_VDRYFA | PLANT_TROUBLE | 180
2023 | nonsummer | VICTOR_1_VDRYFB | METERING_TELEMETRY | 0
2023 | nonsummer | VICTOR_1_VDRYFB | PLANT_MAINTENANCE | 7.7667
2023 | nonsummer | VICTOR_1_VDRYFB | PLANT_TROUBLE | 43.5
2023 | nonsummer | VICTOR_1_VDRYFB | TRANSMISSION_INDUCED | 0
2023 | nonsummer | VILLPK_2_VALLYV | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1250.5
2023 | nonsummer | VILLPK_2_VALLYV | AMBIENT_NOT_DUE_TO_TEMP | 3075
2023 | nonsummer | VILLPK_6_MWDYOR | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 49.3
2023 | nonsummer | VILLPK_6_MWDYOR | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | VISTA_2_FCELL | PLANT_TROUBLE | 406
2023 | nonsummer | VISTA_2_RIALTO | METERING_TELEMETRY | 10
2023 | nonsummer | VISTA_2_RIALTO | PLANT_TROUBLE | 215
2023 | nonsummer | VISTA_2_RTS028 | PLANT_TROUBLE | 717.5
2023 | nonsummer | VISTRA_5_DALBT1 | PLANT_MAINTENANCE | 1000
2023 | nonsummer | VISTRA_5_DALBT1 | PLANT_TROUBLE | 6890.95
2023 | nonsummer | VISTRA_5_DALBT1 | TRANSMISSION_INDUCED | 585
2023 | nonsummer | VISTRA_5_DALBT1 | UNIT_TESTING | 42.4
2023 | nonsummer | VISTRA_5_DALBT2 | PLANT_MAINTENANCE | 1000
2023 | nonsummer | VISTRA_5_DALBT2 | PLANT_TROUBLE | 9044.5
2023 | nonsummer | VISTRA_5_DALBT2 | TRANSMISSION_INDUCED | 585
2023 | nonsummer | VISTRA_5_DALBT2 | UNIT_TESTING | 5.0333
2023 | nonsummer | VISTRA_5_DALBT3 | PLANT_MAINTENANCE | 1000
2023 | nonsummer | VISTRA_5_DALBT3 | PLANT_TROUBLE | 6744.5667
2023 | nonsummer | VISTRA_5_DALBT3 | TRANSMISSION_INDUCED | 500
2023 | nonsummer | VISTRA_5_DALBT3 | UNIT_TESTING | 0
2023 | nonsummer | VISTRA_5_DALBT4 | PLANT_MAINTENANCE | 1075
2023 | nonsummer | VISTRA_5_DALBT4 | PLANT_TROUBLE | 742.75
2023 | nonsummer | VISTRA_5_DALBT4 | TRANSMISSION_INDUCED | 500
2023 | nonsummer | VISTRA_5_DALBT4 | UNIT_TESTING | 0
2023 | nonsummer | VISTRA_5_PLABT1 | PLANT_MAINTENANCE | 9036
2023 | nonsummer | VISTRA_5_PLABT1 | PLANT_TROUBLE | 1862.67
2023 | nonsummer | VISTRA_5_PLABT1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | VISTRA_5_PLABT1 | UNIT_TESTING | 0
2023 | nonsummer | VISTRA_5_PLABT2 | METERING_TELEMETRY | 0
2023 | nonsummer | VISTRA_5_PLABT2 | PLANT_MAINTENANCE | 0
2023 | nonsummer | VISTRA_5_PLABT2 | PLANT_TROUBLE | 631.3333
2023 | nonsummer | VISTRA_5_PLABT2 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | VISTRA_5_PLABT2 | UNIT_TESTING | 0
2023 | nonsummer | VISTRA_5_PLABT3 | PLANT_MAINTENANCE | 5595
2023 | nonsummer | VISTRA_5_PLABT3 | PLANT_TROUBLE | 18.66
2023 | nonsummer | VISTRA_5_PLABT3 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | VISTRA_5_PLABT3 | UNIT_TESTING | 0
2023 | nonsummer | VISTRA_5_PLABT4 | PLANT_MAINTENANCE | 0
2023 | nonsummer | VISTRA_5_PLABT4 | PLANT_TROUBLE | 118.93
2023 | nonsummer | VISTRA_5_PLABT4 | UNIT_TESTING | 0
2023 | nonsummer | VLCNTR_6_VCEBT1 | METERING_TELEMETRY | 0
2023 | nonsummer | VLCNTR_6_VCEBT1 | PLANT_MAINTENANCE | 62.3333
2023 | nonsummer | VLCNTR_6_VCEBT1 | PLANT_TROUBLE | 4803.5
2023 | nonsummer | VLCNTR_6_VCEBT1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | VLCNTR_6_VCEBT2 | PLANT_MAINTENANCE | 0
2023 | nonsummer | VLCNTR_6_VCEBT2 | PLANT_TROUBLE | 2289.8167
2023 | nonsummer | VLCNTR_6_VCEBT2 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | VLCNTR_6_VCSLR | PLANT_TROUBLE | 2.33
2023 | nonsummer | VLCNTR_6_VCSLR1 | PLANT_MAINTENANCE | 5
2023 | nonsummer | VLCNTR_6_VCSLR1 | PLANT_TROUBLE | 5
2023 | nonsummer | VLCNTR_6_VCSLR1 | TRANSMISSION_INDUCED | 100
2023 | nonsummer | VLCNTR_6_VCSLR2 | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | nonsummer | VLCNTR_6_VCSLR2 | PLANT_MAINTENANCE | 10
2023 | nonsummer | VLCNTR_6_VCSLR2 | PLANT_TROUBLE | 5
2023 | nonsummer | VLCNTR_6_VCSLR2 | TRANSMISSION_INDUCED | 20
2023 | nonsummer | VLYHOM_7_SSJID | TRANSMISSION_INDUCED | 15
2023 | nonsummer | VOLTA_2_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | VOLTA_2_UNIT 1 | METERING_TELEMETRY | 0
2023 | nonsummer | VOLTA_2_UNIT 1 | PLANT_MAINTENANCE | 227.5
2023 | nonsummer | VOLTA_2_UNIT 1 | PLANT_TROUBLE | 6870.5
2023 | nonsummer | VOLTA_2_UNIT 2 | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | VOLTA_2_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | VOLTA_2_UNIT 2 | PLANT_TROUBLE | 16.9833
2023 | nonsummer | VOLTA_2_UNIT 2 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | VOLTA_6_BAILCK | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 88.35
2023 | nonsummer | VOLTA_6_BAILCK | AMBIENT_NOT_DUE_TO_TEMP | 85.5
2023 | nonsummer | VOLTA_6_BAILCK | TRANSMISSION_INDUCED | 0
2023 | nonsummer | VOLTA_6_DIGHYD | AMBIENT_DUE_TO_TEMP | 4.04
2023 | nonsummer | VOLTA_6_DIGHYD | AMBIENT_NOT_DUE_TO_TEMP | 4.6
2023 | nonsummer | VOLTA_6_DIGHYD | PLANT_MAINTENANCE | 0
2023 | nonsummer | VOLTA_6_DIGHYD | PLANT_TROUBLE | 6.95
2023 | nonsummer | VOLTA_6_DIGHYD | TRANSMISSION_INDUCED | 0.59
2023 | nonsummer | VOLTA_7_PONHY1 | AMBIENT_NOT_DUE_TO_TEMP | 565.5417
2023 | nonsummer | VOLTA_7_PONHY1 | PLANT_TROUBLE | 55.25
2023 | nonsummer | VOLTA_7_PONHY1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | VOLTA_7_QFUNTS | PLANT_MAINTENANCE | 0
2023 | nonsummer | VOLTA_7_QFUNTS | TRANSMISSION_INDUCED | 0
2023 | nonsummer | VOYAGR_2_VOAWD5 | PLANT_TROUBLE | 0
2023 | nonsummer | VOYAGR_2_VOYWD1 | PLANT_TROUBLE | 0
2023 | nonsummer | VOYAGR_2_VOYWD2 | METERING_TELEMETRY | 0
2023 | nonsummer | VOYAGR_2_VOYWD2 | PLANT_MAINTENANCE | 0
2023 | nonsummer | VOYAGR_2_VOYWD2 | PLANT_TROUBLE | 0
2023 | nonsummer | VOYAGR_2_VOYWD3 | PLANT_TROUBLE | 0
2023 | nonsummer | VOYAGR_2_VOYWD4 | PLANT_TROUBLE | 0
2023 | nonsummer | VSTAES_6_VESBT1 | PLANT_MAINTENANCE | 801.4667
2023 | nonsummer | VSTAES_6_VESBT1 | PLANT_TROUBLE | 1701.8333
2023 | nonsummer | VSTAES_6_VESBT1 | TRANSMISSION_INDUCED | 24.5333
2023 | nonsummer | VSTAES_6_VESBT1 | UNIT_TESTING | 0
2023 | nonsummer | WADHAM_6_UNIT | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2023 | nonsummer | WADHAM_6_UNIT | METERING_TELEMETRY | 5.3295
2023 | nonsummer | WADHAM_6_UNIT | PLANT_MAINTENANCE | 145.35
2023 | nonsummer | WADHAM_6_UNIT | PLANT_TROUBLE | 6686.1
2023 | nonsummer | WALCRK_2_CTG1 | AMBIENT_NOT_DUE_TO_TEMP | 1.222
2023 | nonsummer | WALCRK_2_CTG1 | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | nonsummer | WALCRK_2_CTG1 | OTHER_USE_LIMIT_REACHED | 1448.446
2023 | nonsummer | WALCRK_2_CTG1 | PLANT_MAINTENANCE | 486.6
2023 | nonsummer | WALCRK_2_CTG1 | PLANT_TROUBLE | 598.518
2023 | nonsummer | WALCRK_2_CTG1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | WALCRK_2_CTG2 | ENVIRONMENTAL_RESTRICTIONS | 199.96
2023 | nonsummer | WALCRK_2_CTG2 | OTHER_USE_LIMIT_REACHED | 119.5223
2023 | nonsummer | WALCRK_2_CTG2 | PLANT_MAINTENANCE | 1878.4388
2023 | nonsummer | WALCRK_2_CTG2 | PLANT_TROUBLE | 50399.6607
2023 | nonsummer | WALCRK_2_CTG2 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | WALCRK_2_CTG2 | UNIT_TESTING | 1279.212
2023 | nonsummer | WALCRK_2_CTG3 | AMBIENT_NOT_DUE_TO_TEMP | 257.2558
2023 | nonsummer | WALCRK_2_CTG3 | ENVIRONMENTAL_RESTRICTIONS | 0
2023 | nonsummer | WALCRK_2_CTG3 | OTHER_USE_LIMIT_REACHED | 855.3525
2023 | nonsummer | WALCRK_2_CTG3 | PLANT_MAINTENANCE | 0
2023 | nonsummer | WALCRK_2_CTG3 | PLANT_TROUBLE | 1436.1342
2023 | nonsummer | WALCRK_2_CTG3 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | WALCRK_2_CTG4 | ENVIRONMENTAL_RESTRICTIONS | 100.405
2023 | nonsummer | WALCRK_2_CTG4 | OTHER_USE_LIMIT_REACHED | 877.45
2023 | nonsummer | WALCRK_2_CTG4 | PLANT_MAINTENANCE | 61.18
2023 | nonsummer | WALCRK_2_CTG4 | PLANT_TROUBLE | 133.63
2023 | nonsummer | WALCRK_2_CTG4 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | WALCRK_2_CTG4 | UNIT_TESTING | 421.82
2023 | nonsummer | WALCRK_2_CTG5 | ANNUAL_USE_LIMIT_REACHED | 0
2023 | nonsummer | WALCRK_2_CTG5 | ENVIRONMENTAL_RESTRICTIONS | 92.4533
2023 | nonsummer | WALCRK_2_CTG5 | OTHER_USE_LIMIT_REACHED | 1295.11
2023 | nonsummer | WALCRK_2_CTG5 | PLANT_MAINTENANCE | 96.65
2023 | nonsummer | WALCRK_2_CTG5 | PLANT_TROUBLE | 48.325
2023 | nonsummer | WALCRK_2_CTG5 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | WALCRK_2_CTG5 | UNIT_TESTING | 0
2023 | nonsummer | WALNUT_6_HILLGEN | PLANT_TROUBLE | 1467.85
2023 | nonsummer | WALNUT_6_HILLGEN | TRANSMISSION_INDUCED | 70.5
2023 | nonsummer | WALNUT_7_WCOVST | PLANT_TROUBLE | 416.8667
2023 | nonsummer | WARNE_2_UNIT | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2023 | nonsummer | WARNE_2_UNIT | PLANT_MAINTENANCE | 0
2023 | nonsummer | WARNE_2_UNIT | PLANT_TROUBLE | 253.3333
2023 | nonsummer | WAUKNA_1_SOLAR | PLANT_MAINTENANCE | 1300
2023 | nonsummer | WDLEAF_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 6074.0833
2023 | nonsummer | WDLEAF_7_UNIT 1 | ENVIRONMENTAL_RESTRICTIONS | 700.6667
2023 | nonsummer | WDLEAF_7_UNIT 1 | PLANT_TROUBLE | 43
2023 | nonsummer | WDLEAF_7_UNIT 1 | TRANSMISSION_INDUCED | 500
2023 | nonsummer | WEBER_6_FORWRD | PLANT_MAINTENANCE | 0
2023 | nonsummer | WEBER_6_FORWRD | PLANT_TROUBLE | 185.3383
2023 | nonsummer | WEBER_6_FORWRD | TRANSMISSION_INDUCED | 0
2023 | nonsummer | WESCAN_2_BDSBT1 | METERING_TELEMETRY | 0
2023 | nonsummer | WESCAN_2_BDSBT1 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | WESCAN_2_BDSBT1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | WESCAN_2_BDSBT1 | PLANT_TROUBLE | 0
2023 | nonsummer | WESCAN_2_BDSBT1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | WESCAN_2_BDSBT1 | UNIT_TESTING | 0
2023 | nonsummer | WESTPT_2_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 153
2023 | nonsummer | WESTPT_2_UNIT | PLANT_MAINTENANCE | 0
2023 | nonsummer | WESTPT_2_UNIT | PLANT_TROUBLE | 70
2023 | nonsummer | WESTPT_2_UNIT | TRANSMISSION_INDUCED | 0
2023 | nonsummer | WFRESN_1_SOLAR | METERING_TELEMETRY | 247.5
2023 | nonsummer | WFRESN_1_SOLAR | PLANT_TROUBLE | 1106.25
2023 | nonsummer | WHEATL_6_LNDFIL | PLANT_MAINTENANCE | 0
2023 | nonsummer | WHEATL_6_LNDFIL | PLANT_TROUBLE | 528.325
2023 | nonsummer | WHEATL_6_LNDFIL | TRANSMISSION_INDUCED | 25.25
2023 | nonsummer | WHITEH_2_MEADDYN1 | PLANT_TROUBLE | 4888.664
2023 | nonsummer | WHITEH_2_MEADDYN2 | PLANT_TROUBLE | 16025.21
2023 | nonsummer | WHITNY_6_SOLAR | PLANT_TROUBLE | 450
2023 | nonsummer | WHITNY_6_SOLAR | TRANSMISSION_INDUCED | 0
2023 | nonsummer | WHTWTR_1_WINDA1 | PLANT_MAINTENANCE | 4875
2023 | nonsummer | WHTWTR_1_WINDA1 | PLANT_TROUBLE | 4117.5
2023 | nonsummer | WILLMS_6_ARBBM1 | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | WILLMS_6_ARBBM1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2023 | nonsummer | WILLMS_6_ARBBM1 | PLANT_MAINTENANCE | 617.9
2023 | nonsummer | WILLMS_6_ARBBM1 | PLANT_TROUBLE | 227.8807
2023 | nonsummer | WILLMS_6_ARBBM1 | TRANSMISSION_INDUCED | 3.45
2023 | nonsummer | WISE_1_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 1511.5983
2023 | nonsummer | WISE_1_UNIT 1 | PLANT_TROUBLE | 0
2023 | nonsummer | WISE_1_UNIT 1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | WISE_1_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 3371.2
2023 | nonsummer | WISHON_6_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 5735.5983
2023 | nonsummer | WISHON_6_UNITS | PLANT_MAINTENANCE | 1679.3233
2023 | nonsummer | WISHON_6_UNITS | PLANT_TROUBLE | 1458.0467
2023 | nonsummer | WISHON_6_UNITS | TRANSMISSION_INDUCED | 1316.005
2023 | nonsummer | WISHON_6_UNITS | UNIT_TESTING | 3.3667
2023 | nonsummer | WISTER_2_WISSR1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | WISTER_2_WISSR1 | PLANT_TROUBLE | 4810
2023 | nonsummer | WISTER_2_WISSR1 | TRANSMISSION_INDUCED | 246
2023 | nonsummer | WISTRA_2_WRSSR1 | PLANT_MAINTENANCE | 300
2023 | nonsummer | WISTRA_2_WRSSR1 | PLANT_TROUBLE | 0
2023 | nonsummer | WISTRA_2_WRSSR1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | WLDWD_1_SOLAR1 | PLANT_TROUBLE | 200
2023 | nonsummer | WLDWD_1_SOLAR2 | PLANT_MAINTENANCE | 60
2023 | nonsummer | WLDWD_1_SOLAR2 | PLANT_TROUBLE | 0
2023 | nonsummer | WNDMAS_2_UNIT 1 | PLANT_MAINTENANCE | 113.65
2023 | nonsummer | WNDMAS_2_UNIT 1 | PLANT_TROUBLE | 723.5833
2023 | nonsummer | WNDMAS_2_UNIT 1 | TRANSMISSION_INDUCED | 760
2023 | nonsummer | WNDSTR_2_WIND | AMBIENT_NOT_DUE_TO_TEMP | 190
2023 | nonsummer | WNDSTR_2_WIND | METERING_TELEMETRY | 15600
2023 | nonsummer | WNDSTR_2_WIND | PLANT_TROUBLE | 520
2023 | nonsummer | WOLFSK_1_UNITA1 | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | WOLFSK_1_UNITA1 | METERING_TELEMETRY | 0
2023 | nonsummer | WOLFSK_1_UNITA1 | PLANT_TROUBLE | 994.6947
2023 | nonsummer | WOLFSK_1_UNITA1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | WRGTSR_2_WSFSR1 | PLANT_TROUBLE | 17813.6
2023 | nonsummer | WRGTSR_2_WSFSR1 | TRANSMISSION_INDUCED | 583.2
2023 | nonsummer | WSENGY_1_UNIT 1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 345.0597
2023 | nonsummer | WSENGY_1_UNIT 1 | AMBIENT_DUE_TO_TEMP | 0
2023 | nonsummer | WSENGY_1_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 25
2023 | nonsummer | WSENGY_1_UNIT 1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | WSENGY_1_UNIT 1 | PLANT_TROUBLE | 3799.6148
2023 | nonsummer | WSNR_2_CVPDYN | PLANT_TROUBLE | 0
2023 | nonsummer | WSTWND_2_M89BT2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2023 | nonsummer | WSTWND_2_M89BT2 | METERING_TELEMETRY | 0
2023 | nonsummer | WSTWND_2_M89BT2 | PLANT_MAINTENANCE | 150.8333
2023 | nonsummer | WSTWND_2_M89BT2 | PLANT_TROUBLE | 711.8833
2023 | nonsummer | WSTWND_2_M89BT2 | TRANSMISSION_INDUCED | 2118
2023 | nonsummer | WSTWND_2_M89BT2 | UNIT_TESTING | 0
2023 | nonsummer | WSTWND_2_M89WD1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 3441.8875
2023 | nonsummer | WSTWND_2_M89WD1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | WSTWND_2_M89WD1 | PLANT_TROUBLE | 0
2023 | nonsummer | WSTWND_2_M89WD2 | PLANT_TROUBLE | 10597.7037
2023 | nonsummer | WSTWND_2_M89WD2 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | WSTWND_2_M90WD2 | PLANT_TROUBLE | 5807.7192
2023 | nonsummer | WSTWND_2_M90WD2 | TRANSMISSION_INDUCED | 1944.6
2023 | nonsummer | WSTWND_2_SBSBT1 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | WSTWND_2_SBSBT1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | WSTWND_2_SBSBT1 | PLANT_TROUBLE | 555.4667
2023 | nonsummer | WSTWND_2_SBSBT1 | TRANSMISSION_INDUCED | 0
2023 | nonsummer | YELPIN_2_YP2BT1 | METERING_TELEMETRY | 0
2023 | nonsummer | YELPIN_2_YP2BT1 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | YELPIN_2_YP2BT1 | PLANT_MAINTENANCE | 0
2023 | nonsummer | YELPIN_2_YP2BT1 | PLANT_TROUBLE | 2690
2023 | nonsummer | YELPIN_2_YP2BT1 | TRANSMISSION_INDUCED | 1100
2023 | nonsummer | YELPIN_2_YP2BT1 | UNIT_TESTING | 0
2023 | nonsummer | YELPIN_2_YP2SR1 | NEW_GENERATOR_TEST_ENERGY | 0
2023 | nonsummer | YELPIN_2_YP2SR1 | PLANT_TROUBLE | 625
2023 | nonsummer | YELPIN_2_YP2SR1 | TRANSMISSION_INDUCED | 1270.3333
2023 | nonsummer | YELPIN_2_YP2SR1 | UNIT_TESTING | 0
2023 | nonsummer | YUBACT_1_SUNSWT | PLANT_MAINTENANCE | 7020.785
2023 | nonsummer | YUBACT_1_SUNSWT | PLANT_TROUBLE | 262.3425
2023 | nonsummer | YUBACT_1_SUNSWT | TRANSMISSION_INDUCED | 177.1993
2023 | nonsummer | YUBACT_1_SUNSWT | UNIT_TESTING | 0
2023 | nonsummer | YUBACT_6_UNITA1 | AMBIENT_DUE_TO_TEMP | 4.212
2023 | nonsummer | YUBACT_6_UNITA1 | PLANT_TROUBLE | 329.334
2023 | nonsummer | YUBACT_6_UNITA1 | TRANSMISSION_INDUCED | 166.648
2023 | nonsummer | ZOND_6_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 18040.5
2024 | summer | 7STDRD_1_SOLAR1 | PLANT_MAINTENANCE | 30.6667
2024 | summer | ACACIA_6_SOLAR | PLANT_MAINTENANCE | 30
2024 | summer | ACACIA_6_SOLAR | PLANT_TROUBLE | 1150
2024 | summer | ADERA_1_SOLAR1 | METERING_TELEMETRY | 0
2024 | summer | ADERA_1_SOLAR1 | PLANT_TROUBLE | 1417.1667
2024 | summer | ADERA_1_SOLAR1 | TRANSMISSION_INDUCED | 0
2024 | summer | ADLIN_1_UNITS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 8503.1505
2024 | summer | ADLIN_1_UNITS | PLANT_MAINTENANCE | 75.8585
2024 | summer | ADLIN_1_UNITS | PLANT_TROUBLE | 142.6445
2024 | summer | ADMEST_6_SOLAR | PLANT_MAINTENANCE | 38
2024 | summer | ADMEST_6_SOLAR | TRANSMISSION_INDUCED | 475
2024 | summer | ADOBEE_1_SOLAR | METERING_TELEMETRY | 20
2024 | summer | ADOBEE_1_SOLAR | PLANT_MAINTENANCE | 89
2024 | summer | ADOBEE_1_SOLAR | PLANT_TROUBLE | 160.2133
2024 | summer | AGRICO_6_PL3N5 | AMBIENT_DUE_TO_TEMP | 1096.0377
2024 | summer | AGRICO_6_PL3N5 | PLANT_TROUBLE | 138.4532
2024 | summer | AGRICO_6_PL3N5 | TRANSMISSION_INDUCED | 0
2024 | summer | AGRICO_7_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 28.11
2024 | summer | AGRICO_7_UNIT | PLANT_MAINTENANCE | 0
2024 | summer | AGRICO_7_UNIT | PLANT_TROUBLE | 767.8875
2024 | summer | AGRICO_7_UNIT | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 206.14
2024 | summer | AGRICO_7_UNIT | TRANSMISSION_INDUCED | 0
2024 | summer | AGUCAL_5_SOLAR1 | METERING_TELEMETRY | 0
2024 | summer | AGUCAL_5_SOLAR1 | PLANT_MAINTENANCE | 465
2024 | summer | AKINGS_6_AMESR1 | METERING_TELEMETRY | 0
2024 | summer | AKINGS_6_AMESR1 | PLANT_MAINTENANCE | 150.6583
2024 | summer | AKINGS_6_AMESR1 | PLANT_TROUBLE | 1667
2024 | summer | ALAMIT_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 4051.1667
2024 | summer | ALAMIT_2_PL1X3 | PLANT_TROUBLE | 1728.15
2024 | summer | ALAMIT_7_ES1 | METERING_TELEMETRY | 427.9
2024 | summer | ALAMIT_7_ES1 | PLANT_MAINTENANCE | 0
2024 | summer | ALAMIT_7_ES1 | PLANT_TROUBLE | 11218.9583
2024 | summer | ALAMIT_7_UNIT 3 | AMBIENT_DUE_TO_TEMP | 176.4
2024 | summer | ALAMIT_7_UNIT 3 | ENVIRONMENTAL_RESTRICTIONS | 240168.6
2024 | summer | ALAMIT_7_UNIT 3 | UNIT_SUPPORTING_STARTUP | 122.9167
2024 | summer | ALAMIT_7_UNIT 3 | UNIT_TESTING | 183.8
2024 | summer | ALAMIT_7_UNIT 4 | AMBIENT_DUE_TO_TEMP | 291.45
2024 | summer | ALAMIT_7_UNIT 4 | ENVIRONMENTAL_RESTRICTIONS | 249150.35
2024 | summer | ALAMIT_7_UNIT 4 | PLANT_TROUBLE | 222.15
2024 | summer | ALAMIT_7_UNIT 5 | AMBIENT_DUE_TO_TEMP | 200
2024 | summer | ALAMIT_7_UNIT 5 | ENVIRONMENTAL_RESTRICTIONS | 358104
2024 | summer | ALAMIT_7_UNIT 5 | PLANT_TROUBLE | 175
2024 | summer | ALAMIT_7_UNIT 5 | UNIT_TESTING | 693.5833
2024 | summer | ALAMO_6_UNIT | ENVIRONMENTAL_RESTRICTIONS | 102
2024 | summer | ALAMO_6_UNIT | PLANT_MAINTENANCE | 431.8
2024 | summer | ALAMO_6_UNIT | PLANT_TROUBLE | 40.5167
2024 | summer | ALAMO_6_UNIT | TRANSMISSION_INDUCED | 214.4833
2024 | summer | ALHMBR_1_ALHSLR | PLANT_MAINTENANCE | 37.5
2024 | summer | ALHMBR_1_ALHSLR | PLANT_TROUBLE | 71.25
2024 | summer | ALLGNY_6_HYDRO1 | TRANSMISSION_INDUCED | 5.3647
2024 | summer | ALMASL_2_AL6BT6 | PLANT_MAINTENANCE | 1342.968
2024 | summer | ALMASL_2_AL6BT6 | PLANT_TROUBLE | 3060.9278
2024 | summer | ALMASL_2_GS6SR6 | PLANT_MAINTENANCE | 0
2024 | summer | ALMASL_2_GS7SR7 | PLANT_MAINTENANCE | 0
2024 | summer | ALMASL_2_GS7SR7 | PLANT_TROUBLE | 138.4
2024 | summer | ALMEGT_1_UNIT 1 | AMBIENT_DUE_TO_TEMP | 1235.4
2024 | summer | ALMEGT_1_UNIT 1 | PLANT_TROUBLE | 8.4333
2024 | summer | ALMEGT_1_UNIT 1 | TRANSMISSION_INDUCED | 190.6
2024 | summer | ALMEGT_1_UNIT 2 | AMBIENT_DUE_TO_TEMP | 1191
2024 | summer | ALMEGT_1_UNIT 2 | PLANT_TROUBLE | 8.4333
2024 | summer | ALMEGT_1_UNIT 2 | TRANSMISSION_INDUCED | 190.6
2024 | summer | ALPSLR_1_NTHSLR | PLANT_MAINTENANCE | 28
2024 | summer | ALPSLR_1_NTHSLR | PLANT_TROUBLE | 547.5
2024 | summer | ALPSLR_1_NTHSLR | TRANSMISSION_INDUCED | 151.5
2024 | summer | ALPSLR_1_SPSSLR | PLANT_MAINTENANCE | 193.3333
2024 | summer | ALPSLR_1_SPSSLR | PLANT_TROUBLE | 3485.2
2024 | summer | ALPSLR_1_SPSSLR | TRANSMISSION_INDUCED | 343.0333
2024 | summer | ALTA3A_2_CPCE4 | PLANT_TROUBLE | 4866.55
2024 | summer | ALTA3A_2_CPCE5 | PLANT_TROUBLE | 8442.8
2024 | summer | ALTA3A_2_CPCE8 | ENVIRONMENTAL_RESTRICTIONS | 43.45
2024 | summer | ALTA3A_2_CPCE8 | METERING_TELEMETRY | 1441.25
2024 | summer | ALTA3A_2_CPCE8 | PLANT_TROUBLE | 11352.6667
2024 | summer | ALTA4A_2_CPCW1 | METERING_TELEMETRY | 15
2024 | summer | ALTA4A_2_CPCW1 | PLANT_TROUBLE | 2764.5083
2024 | summer | ALTA4B_2_CPCW2 | PLANT_TROUBLE | 8455.7175
2024 | summer | ALTA4B_2_CPCW3 | PLANT_TROUBLE | 13539.5667
2024 | summer | ALTA4B_2_CPCW6 | PLANT_TROUBLE | 1203
2024 | summer | ALTA6B_2_WIND11 | PLANT_MAINTENANCE | 0
2024 | summer | ALTA6B_2_WIND11 | PLANT_TROUBLE | 3877.8323
2024 | summer | ALTA6E_2_WIND10 | PLANT_TROUBLE | 7692.9657
2024 | summer | ALTWD_2_COAWD1 | PLANT_MAINTENANCE | 799.2
2024 | summer | ANAHM_2_CANYN1 | PLANT_TROUBLE | 32478.6
2024 | summer | ANAHM_2_CANYN2 | PLANT_TROUBLE | 53.6447
2024 | summer | ANAHM_2_CANYN2 | TRANSMISSION_INDUCED | 0
2024 | summer | ANAHM_2_CANYN3 | PLANT_TROUBLE | 51.9138
2024 | summer | ANAHM_2_CANYN4 | PLANT_TROUBLE | 196.71
2024 | summer | ANZA_6_SOLAR1 | TRANSMISSION_INDUCED | 5
2024 | summer | APLHIL_1_SFKHY1 | PLANT_MAINTENANCE | 5.36
2024 | summer | APLHIL_1_SFKHY1 | PLANT_TROUBLE | 2.68
2024 | summer | APLHIL_1_SFKHY1 | TRANSMISSION_INDUCED | 7.37
2024 | summer | AQUAWS_2_AQWSR1 | METERING_TELEMETRY | 550
2024 | summer | AQUAWS_2_AQWSR1 | PLANT_MAINTENANCE | 0
2024 | summer | ARBWD_6_QF | PLANT_TROUBLE | 120.25
2024 | summer | ARCOGN_2_UNITS | AMBIENT_DUE_TO_TEMP | 34
2024 | summer | ARCOGN_2_UNITS | PLANT_TROUBLE | 36690.25
2024 | summer | ARKANS_1_ARKSLR | PLANT_MAINTENANCE | 5
2024 | summer | ARLNTN_2_AR1SR1 | PLANT_MAINTENANCE | 685.8133
2024 | summer | ARLNTN_2_AR1SR1 | PLANT_TROUBLE | 1708.1667
2024 | summer | ARLNTN_2_ASUSR1 | PLANT_MAINTENANCE | 0
2024 | summer | ARLNTN_2_ASUSR1 | PLANT_TROUBLE | 4031
2024 | summer | ARVINN_6_ORION1 | TRANSMISSION_INDUCED | 203.2
2024 | summer | ARVINN_6_ORION2 | TRANSMISSION_INDUCED | 48
2024 | summer | ASTORA_2_SOLAR1 | PLANT_TROUBLE | 11672
2024 | summer | ASTORA_2_SOLAR2 | PLANT_MAINTENANCE | 224.7667
2024 | summer | ASTORA_2_SOLAR2 | PLANT_TROUBLE | 6011.2167
2024 | summer | ATHOS_5_AP1X2 | PLANT_MAINTENANCE | 137.83
2024 | summer | ATHOS_5_AP1X2 | PLANT_TROUBLE | 0
2024 | summer | ATWEL2_1_SOLAR1 | TRANSMISSION_INDUCED | 40.3333
2024 | summer | ATWELL_1_SOLAR | PLANT_MAINTENANCE | 40
2024 | summer | ATWELL_1_SOLAR | TRANSMISSION_INDUCED | 40.3333
2024 | summer | AVENAL_6_AVPARK | TRANSMISSION_INDUCED | 420
2024 | summer | AVENAL_6_AVSLR2 | PLANT_TROUBLE | 36.735
2024 | summer | AVENAL_6_SANDDG | METERING_TELEMETRY | 285
2024 | summer | AVENAL_6_SANDDG | PLANT_TROUBLE | 3.4167
2024 | summer | AVENAL_6_SANDDG | TRANSMISSION_INDUCED | 3291.4333
2024 | summer | AVENAL_6_SUNCTY | PLANT_TROUBLE | 0
2024 | summer | AVENAL_6_SUNCTY | TRANSMISSION_INDUCED | 1824.3333
2024 | summer | AVSOLR_2_SOLAR | PLANT_MAINTENANCE | 1478.25
2024 | summer | AVSOLR_2_SOLAR | PLANT_TROUBLE | 127.5
2024 | summer | AVSOLR_2_SOLAR | UNIT_TESTING | 0
2024 | summer | BALCHS_7_UNIT 1 | AMBIENT_DUE_TO_TEMP | 22.1
2024 | summer | BALCHS_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 695.6333
2024 | summer | BALCHS_7_UNIT 1 | TRANSMISSION_INDUCED | 522.3333
2024 | summer | BALCHS_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 1416.125
2024 | summer | BALCHS_7_UNIT 2 | TRANSMISSION_INDUCED | 787.5
2024 | summer | BALCHS_7_UNIT 3 | AMBIENT_NOT_DUE_TO_TEMP | 1615.9267
2024 | summer | BALCHS_7_UNIT 3 | TRANSMISSION_INDUCED | 716.17
2024 | summer | BANKPP_2_NSPIN | TRANSMISSION_INDUCED | 5400
2024 | summer | BARRE_2_ALASB1 | PLANT_MAINTENANCE | 0
2024 | summer | BARRE_2_ALASB1 | PLANT_TROUBLE | 85
2024 | summer | BARRE_6_PEAKER | AMBIENT_DUE_TO_TEMP | 4066.61
2024 | summer | BASICE_2_UNITS | AMBIENT_DUE_TO_TEMP | 1567.3667
2024 | summer | BASICE_2_UNITS | PLANT_MAINTENANCE | 1380
2024 | summer | BASICE_2_UNITS | PLANT_TROUBLE | 8686.6
2024 | summer | BCTSYS_5_PWXDYN | TRANSITIONAL_LIMITATION | 323140
2024 | summer | BDGRCK_1_UNITS | AMBIENT_DUE_TO_TEMP | 2804
2024 | summer | BDGRCK_1_UNITS | PLANT_TROUBLE | 1056.3
2024 | summer | BDGRCK_1_UNITS | UNIT_TESTING | 6
2024 | summer | BEARDS_7_UNIT 1 | TRANSMISSION_INDUCED | 244.5667
2024 | summer | BEARMT_1_UNIT | AMBIENT_DUE_TO_TEMP | 3451.31
2024 | summer | BEARMT_1_UNIT | PLANT_TROUBLE | 235.6333
2024 | summer | BEARMT_1_UNIT | UNIT_TESTING | 13.3723
2024 | summer | BEJNLS_5_BV2SCEDYN | PLANT_TROUBLE | 0
2024 | summer | BEJNLS_5_BV2SCEDYN | TRANSITIONAL_LIMITATION | 31.5
2024 | summer | BEJNLS_5_BV2SCEDYN | TRANSMISSION_INDUCED | 408.55
2024 | summer | BEKWJS_5_BV1SCEDYN | PLANT_TROUBLE | 320.6667
2024 | summer | BEKWJS_5_BV1SCEDYN | TRANSITIONAL_LIMITATION | 24
2024 | summer | BEKWJS_5_BV1SCEDYN | TRANSMISSION_INDUCED | 329.9833
2024 | summer | BELDEN_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 28404.61
2024 | summer | BELDEN_7_UNIT 1 | PLANT_TROUBLE | 441.4062
2024 | summer | BELDEN_7_UNIT 1 | TRANSMISSION_INDUCED | 57.5167
2024 | summer | BERCYN_2_BCEBT1 | METERING_TELEMETRY | 0
2024 | summer | BERCYN_2_BCEBT1 | NEW_GENERATOR_TEST_ENERGY | 65
2024 | summer | BERCYN_2_BCEBT1 | PLANT_MAINTENANCE | 325
2024 | summer | BERCYN_2_BCEBT1 | PLANT_TROUBLE | 0
2024 | summer | BERCYN_2_BCEBT1 | UNIT_TESTING | 0
2024 | summer | BGSKYN_2_AS2SR1 | PLANT_MAINTENANCE | 671.4167
2024 | summer | BGSKYN_2_AS2SR1 | PLANT_TROUBLE | 5283.15
2024 | summer | BGSKYN_2_ASPSR2 | PLANT_TROUBLE | 774.4
2024 | summer | BGSKYN_2_ASPSR2 | RTU_RIG | 0
2024 | summer | BGSKYN_2_ASPSR2 | UNIT_TESTING | 0
2024 | summer | BGSKYN_2_ASSR1B | PLANT_TROUBLE | 726.85
2024 | summer | BGSKYN_2_ASSR3A | PLANT_TROUBLE | 114.8917
2024 | summer | BGSKYN_2_ASSR3A | UNIT_TESTING | 0
2024 | summer | BGSKYN_2_ASSR3B | PLANT_TROUBLE | 0
2024 | summer | BGSKYN_2_ASSR3B | UNIT_TESTING | 0
2024 | summer | BGSKYN_2_BS3SR3 | PLANT_TROUBLE | 0
2024 | summer | BIGCRK_2_EXESWD | AMBIENT_NOT_DUE_TO_TEMP | 91227.8167
2024 | summer | BIGCRK_2_EXESWD | PLANT_MAINTENANCE | 2265
2024 | summer | BIGCRK_2_EXESWD | PLANT_TROUBLE | 1152.5
2024 | summer | BIGCRK_2_EXESWD | TRANSMISSION_INDUCED | 0
2024 | summer | BIGSKY_2_AS2BT1 | PLANT_TROUBLE | 0
2024 | summer | BIGSKY_2_AS2BT1 | RTU_RIG | 0
2024 | summer | BIGSKY_2_AS2BT1 | UNIT_TESTING | 131.2333
2024 | summer | BIGSKY_2_ASLBT2 | PLANT_MAINTENANCE | 0
2024 | summer | BIGSKY_2_ASLBT2 | PLANT_TROUBLE | 54.5
2024 | summer | BIGSKY_2_BSKSR6 | PLANT_TROUBLE | 191.5417
2024 | summer | BIGSKY_2_BSKSR7 | PLANT_TROUBLE | 87.5
2024 | summer | BIGSKY_2_BSKSR8 | PLANT_TROUBLE | 672.9583
2024 | summer | BIGSKY_2_SOLAR2 | PLANT_MAINTENANCE | 0
2024 | summer | BIGSKY_2_SOLAR3 | PLANT_TROUBLE | 46.3333
2024 | summer | BIGSKY_2_SOLAR4 | PLANT_MAINTENANCE | 0
2024 | summer | BIGSKY_2_SOLAR4 | PLANT_TROUBLE | 0
2024 | summer | BIGSKY_2_SOLAR5 | PLANT_TROUBLE | 0
2024 | summer | BIGSKY_2_SOLAR6 | PLANT_MAINTENANCE | 220
2024 | summer | BIGSKY_2_SOLAR6 | PLANT_TROUBLE | 1315
2024 | summer | BIGSKY_2_SOLAR6 | UNIT_TESTING | 2
2024 | summer | BIGSKY_2_SOLAR7 | PLANT_TROUBLE | 357.8333
2024 | summer | BIOMAS_1_UNIT 1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 225.09
2024 | summer | BIOMAS_1_UNIT 1 | PLANT_TROUBLE | 517.44
2024 | summer | BISHOP_1_ALAMO | AMBIENT_NOT_DUE_TO_TEMP | 4124.06
2024 | summer | BISHOP_1_ALAMO | PLANT_TROUBLE | 48
2024 | summer | BISHOP_1_ALAMO | TRANSMISSION_INDUCED | 1.5
2024 | summer | BISHOP_1_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 4147.8958
2024 | summer | BISHOP_1_UNITS | PLANT_MAINTENANCE | 400
2024 | summer | BISHOP_1_UNITS | PLANT_TROUBLE | 188.6
2024 | summer | BLACK_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 2248.055
2024 | summer | BLACK_7_UNIT 1 | TRANSMISSION_INDUCED | 490.97
2024 | summer | BLACK_7_UNIT 2 | AMBIENT_DUE_TO_TEMP | 0
2024 | summer | BLACK_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 2288.9317
2024 | summer | BLACK_7_UNIT 2 | PLANT_TROUBLE | 18.2217
2024 | summer | BLACK_7_UNIT 2 | TRANSMISSION_INDUCED | 1970.705
2024 | summer | BLAST_1_WIND | PLANT_MAINTENANCE | 0
2024 | summer | BLCKBT_2_STONEY | PLANT_TROUBLE | 3761.3333
2024 | summer | BLCKBT_2_STONEY | TRANSMISSION_INDUCED | 7.8533
2024 | summer | BLCKWL_6_SOLAR1 | PLANT_TROUBLE | 60
2024 | summer | BLCKWL_6_SOLAR1 | TRANSMISSION_INDUCED | 0
2024 | summer | BLKCRK_2_GMCBT1 | PLANT_TROUBLE | 1735.3128
2024 | summer | BLKCRK_2_GMCBT1 | UNIT_TESTING | 1840
2024 | summer | BLKCRK_2_SOLAR1 | PLANT_MAINTENANCE | 22.1667
2024 | summer | BLKDIA_2_BDEBT1 | PLANT_MAINTENANCE | 1000
2024 | summer | BLKDIA_2_BDEBT1 | PLANT_TROUBLE | 2417.35
2024 | summer | BLKDIA_2_BDEBT1 | UNIT_TESTING | 0
2024 | summer | BLM W_2_COSBT1 | PLANT_MAINTENANCE | 600
2024 | summer | BLM W_2_COSBT1 | PLANT_TROUBLE | 1829.2883
2024 | summer | BLM_2_UNITS | RTU_RIG | 1008.8
2024 | summer | BLVRDE_6_BLVBT1 | PLANT_TROUBLE | 2009.5542
2024 | summer | BLYTHE_1_SOLAR1 | METERING_TELEMETRY | 130
2024 | summer | BLYTHE_1_SOLAR1 | PLANT_MAINTENANCE | 8.75
2024 | summer | BLYTHE_1_SOLAR1 | PLANT_TROUBLE | 690.125
2024 | summer | BLYTHE_1_SOLAR2 | PLANT_MAINTENANCE | 30.4
2024 | summer | BLYTHE_1_SOLAR2 | PLANT_TROUBLE | 793.5
2024 | summer | BNNIEN_7_ALTAPH | AMBIENT_NOT_DUE_TO_TEMP | 414.0675
2024 | summer | BNNIEN_7_ALTAPH | TRANSMISSION_INDUCED | 5.6617
2024 | summer | BOGUE_1_UNITA1 | AMBIENT_DUE_TO_TEMP | 1791.3625
2024 | summer | BOGUE_1_UNITA1 | PLANT_TROUBLE | 626.0272
2024 | summer | BORDER_6_UNITA1 | PLANT_MAINTENANCE | 102.5
2024 | summer | BORDER_6_UNITA1 | PLANT_TROUBLE | 364.185
2024 | summer | BORDER_6_UNITA1 | TRANSMISSION_INDUCED | 0
2024 | summer | BOWMN_6_HYDRO | AMBIENT_NOT_DUE_TO_TEMP | 432
2024 | summer | BOWMN_6_HYDRO | PLANT_TROUBLE | 0
2024 | summer | BOWMN_6_HYDRO | TRANSMISSION_INDUCED | 8.94
2024 | summer | BRDSLD_2_HIWIND | PLANT_MAINTENANCE | 36797.22
2024 | summer | BRDSLD_2_MTZUM2 | METERING_TELEMETRY | 166.6
2024 | summer | BRDSLD_2_MTZUM2 | PLANT_MAINTENANCE | 1898.8033
2024 | summer | BRDSLD_2_MTZUMA | PLANT_MAINTENANCE | 2119.9333
2024 | summer | BRDSLD_2_SHILO1 | PLANT_TROUBLE | 930.2
2024 | summer | BRDSLD_2_SHILO2 | PLANT_MAINTENANCE | 4293.7333
2024 | summer | BRDSLD_2_SHLO3A | PLANT_MAINTENANCE | 2487.665
2024 | summer | BRDSLD_2_SHLO3B | PLANT_MAINTENANCE | 973.9392
2024 | summer | BREGGO_6_DEGRSL | TRANSMISSION_INDUCED | 44.1
2024 | summer | BREGGO_6_DSEBT1 | TRANSMISSION_INDUCED | 36.65
2024 | summer | BREGGO_6_SOLAR | PLANT_TROUBLE | 43.1583
2024 | summer | BREGGO_6_SOLAR | TRANSMISSION_INDUCED | 156
2024 | summer | BRODIE_2_WIND | METERING_TELEMETRY | 234
2024 | summer | BRODIE_2_WIND | PLANT_MAINTENANCE | 7672.5833
2024 | summer | BRODIE_2_WIND | PLANT_TROUBLE | 1155
2024 | summer | BUCKBL_2_PL1X3 | METERING_TELEMETRY | 0
2024 | summer | BUCKBL_2_PL1X3 | PLANT_TROUBLE | 3167.4592
2024 | summer | BUCKCK_7_OAKFLT | AMBIENT_NOT_DUE_TO_TEMP | 6.5
2024 | summer | BUCKCK_7_OAKFLT | TRANSMISSION_INDUCED | 988
2024 | summer | BUCKCK_7_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 510.5667
2024 | summer | BUCKCK_7_PL1X2 | PLANT_TROUBLE | 990
2024 | summer | BUCKCK_7_PL1X2 | RTU_RIG | 0
2024 | summer | BUCKCK_7_PL1X2 | TRANSMISSION_INDUCED | 0
2024 | summer | BUCKCK_7_PL1X2 | UNIT_TESTING | 65.45
2024 | summer | BUCKWD_1_NPALM1 | METERING_TELEMETRY | 12
2024 | summer | BUCKWD_1_QF | PLANT_MAINTENANCE | 285.275
2024 | summer | BURNYF_2_UNIT 1 | PLANT_MAINTENANCE | 856.7833
2024 | summer | BURNYF_2_UNIT 1 | PLANT_TROUBLE | 166.4
2024 | summer | BUTTVL_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 217.25
2024 | summer | BUTTVL_7_UNIT 1 | PLANT_MAINTENANCE | 335.75
2024 | summer | BUTTVL_7_UNIT 1 | PLANT_TROUBLE | 305.4667
2024 | summer | BUTTVL_7_UNIT 1 | TRANSMISSION_INDUCED | 987.5
2024 | summer | CABALO_2_M2BSR1 | PLANT_MAINTENANCE | 46
2024 | summer | CABALO_2_M2BSR1 | PLANT_TROUBLE | 1060
2024 | summer | CABALO_2_M2WSR2 | PLANT_MAINTENANCE | 79.68
2024 | summer | CABALO_2_M2WSR2 | PLANT_TROUBLE | 300
2024 | summer | CALFTN_2_CFSBT1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | summer | CALFTN_2_CFSBT1 | PLANT_MAINTENANCE | 0
2024 | summer | CALFTN_2_CFSBT1 | PLANT_TROUBLE | 9222
2024 | summer | CALFTN_2_SOLAR | PLANT_MAINTENANCE | 0
2024 | summer | CALFTN_2_SOLAR | PLANT_TROUBLE | 6845
2024 | summer | CALFTS_2_CFSSR1 | PLANT_TROUBLE | 1554
2024 | summer | CALGEN_1_UNITS | PLANT_TROUBLE | 325
2024 | summer | CALPIN_1_AGNEW | AMBIENT_DUE_TO_TEMP | 962.8813
2024 | summer | CALPIN_1_AGNEW | PLANT_MAINTENANCE | 86.4267
2024 | summer | CALPIN_1_AGNEW | PLANT_TROUBLE | 240.0833
2024 | summer | CAMCHE_1_PL1X3 | AMBIENT_NOT_DUE_TO_TEMP | 199.8
2024 | summer | CAMCHE_1_PL1X3 | TRANSMISSION_INDUCED | 199.8
2024 | summer | CAMERN_6_BSPSR1 | PLANT_TROUBLE | 1.68
2024 | summer | CANTUA_1_SOLAR | TRANSMISSION_INDUCED | 100
2024 | summer | CAPWD_1_QF | PLANT_TROUBLE | 9218.25
2024 | summer | CARBOU_7_PL2X3 | AMBIENT_NOT_DUE_TO_TEMP | 9290.7435
2024 | summer | CARBOU_7_PL2X3 | PLANT_MAINTENANCE | 85.75
2024 | summer | CARBOU_7_PL2X3 | PLANT_TROUBLE | 0
2024 | summer | CARBOU_7_PL2X3 | TRANSMISSION_INDUCED | 882
2024 | summer | CARBOU_7_PL4X5 | AMBIENT_NOT_DUE_TO_TEMP | 3478.456
2024 | summer | CARBOU_7_PL4X5 | PLANT_MAINTENANCE | 35999
2024 | summer | CARBOU_7_PL4X5 | PLANT_TROUBLE | 20
2024 | summer | CARBOU_7_PL4X5 | TRANSMISSION_INDUCED | 1192.63
2024 | summer | CARBOU_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 1744.94
2024 | summer | CARBOU_7_UNIT 1 | PLANT_TROUBLE | 0
2024 | summer | CARBOU_7_UNIT 1 | TRANSMISSION_INDUCED | 432
2024 | summer | CARLS1_2_CARCT1 | AMBIENT_DUE_TO_TEMP | 4390.2
2024 | summer | CARLS1_2_CARCT1 | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | summer | CARLS1_2_CARCT1 | PLANT_MAINTENANCE | 486.2
2024 | summer | CARLS1_2_CARCT1 | PLANT_TROUBLE | 1455.4733
2024 | summer | CARLS2_1_CARCT1 | AMBIENT_DUE_TO_TEMP | 2518.93
2024 | summer | CARLS2_1_CARCT1 | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | summer | CARLS2_1_CARCT1 | PLANT_MAINTENANCE | 0
2024 | summer | CARLS2_1_CARCT1 | PLANT_TROUBLE | 8778.4317
2024 | summer | CASADB_1_CD4GT1 | AMBIENT_DUE_TO_TEMP | 9709.26
2024 | summer | CASADB_1_CD4GT1 | PLANT_MAINTENANCE | 244.7683
2024 | summer | CASCES_6_CESBT1 | METERING_TELEMETRY | 0
2024 | summer | CASCES_6_CESBT1 | PLANT_MAINTENANCE | 24.1667
2024 | summer | CASCES_6_CESBT1 | PLANT_TROUBLE | 335.9287
2024 | summer | CASCES_6_CESBT1 | TRANSMISSION_INDUCED | 0
2024 | summer | CASCES_6_CESBT1 | UNIT_TESTING | 75
2024 | summer | CASCES_6_CESBT2 | PLANT_TROUBLE | 0
2024 | summer | CATLNA_2_SOLAR | PLANT_MAINTENANCE | 0
2024 | summer | CATLNA_2_SOLAR2 | PLANT_MAINTENANCE | 18
2024 | summer | CAVLSR_2_BSOLAR | PLANT_MAINTENANCE | 0
2024 | summer | CAVLSR_2_BSOLAR | TRANSMISSION_INDUCED | 250.6667
2024 | summer | CAVLSR_2_RSOLAR | PLANT_MAINTENANCE | 0
2024 | summer | CAVLSR_2_RSOLAR | PLANT_TROUBLE | 235.6
2024 | summer | CAVLSR_2_RSOLAR | TRANSMISSION_INDUCED | 106.5333
2024 | summer | CAYTNO_2_VASCO | AMBIENT_DUE_TO_TEMP | 12.5
2024 | summer | CAYTNO_2_VASCO | PLANT_MAINTENANCE | 86
2024 | summer | CAYTNO_2_VASCO | PLANT_TROUBLE | 220.3475
2024 | summer | CAYTNO_2_VASCO | TRANSMISSION_INDUCED | 21.1775
2024 | summer | CDWR07_2_GEN | PLANT_TROUBLE | 2076.5
2024 | summer | CEDRCK_6_UNIT | TRANSMISSION_INDUCED | 0
2024 | summer | CENT40_1_C40SR1 | PLANT_TROUBLE | 3038.775
2024 | summer | CENT40_1_C40SR1 | TRANSMISSION_INDUCED | 1000
2024 | summer | CENTER_2_SOLAR1 | PLANT_MAINTENANCE | 0
2024 | summer | CENTER_6_PEAKER | AMBIENT_DUE_TO_TEMP | 617.36
2024 | summer | CENTER_6_PEAKER | METERING_TELEMETRY | 0.066
2024 | summer | CENTER_6_PEAKER | PLANT_TROUBLE | 303.91
2024 | summer | CENTER_6_PEAKER | RTU_RIG | 47.19
2024 | summer | CENTPD_2_BMSSX2 | METERING_TELEMETRY | 0
2024 | summer | CENTPD_2_BMSSX2 | PLANT_MAINTENANCE | 0
2024 | summer | CENTPD_2_BMSSX2 | PLANT_TROUBLE | 546.46
2024 | summer | CENTPD_2_BMSSX2 | UNIT_TESTING | 0
2024 | summer | CENTPD_2_BMSX2 | METERING_TELEMETRY | 0
2024 | summer | CENTPD_2_BMSX2 | PLANT_MAINTENANCE | 120
2024 | summer | CENTPD_2_BMSX2 | PLANT_TROUBLE | 2073
2024 | summer | CENTRY_6_PL1X4 | UNIT_TESTING | 506.915
2024 | summer | CHALK_1_UNIT | AMBIENT_DUE_TO_TEMP | 3401.99
2024 | summer | CHALK_1_UNIT | PLANT_TROUBLE | 88
2024 | summer | CHALK_1_UNIT | TRANSMISSION_INDUCED | 4.42
2024 | summer | CHALK_1_UNIT | UNIT_TESTING | 75.35
2024 | summer | CHARMN_2_PGONG1 | PLANT_MAINTENANCE | 122.5317
2024 | summer | CHARMN_2_PGONG1 | PLANT_TROUBLE | 41.3958
2024 | summer | CHESTN_2_CHWBX2 | METERING_TELEMETRY | 0
2024 | summer | CHESTN_2_CHWSX2 | METERING_TELEMETRY | 0
2024 | summer | CHESTN_2_CHWSX2 | PLANT_TROUBLE | 3000
2024 | summer | CHEVCY_1_UNIT | PLANT_TROUBLE | 12.15
2024 | summer | CHEVCY_1_UNIT | TRANSMISSION_INDUCED | 14.175
2024 | summer | CHEVMN_2_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 19354.85
2024 | summer | CHEVMN_2_UNITS | PLANT_MAINTENANCE | 6243.5
2024 | summer | CHICPK_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 21753
2024 | summer | CHILLS_1_SYCENG | AMBIENT_DUE_TO_TEMP | 0.1
2024 | summer | CHILLS_1_SYCENG | PLANT_MAINTENANCE | 0
2024 | summer | CHILLS_1_SYCENG | PLANT_TROUBLE | 39.3
2024 | summer | CHILLS_7_UNITA1 | AMBIENT_DUE_TO_TEMP | 264.2833
2024 | summer | CHILLS_7_UNITA1 | PLANT_MAINTENANCE | 7.1
2024 | summer | CHILLS_7_UNITA1 | PLANT_TROUBLE | 14.1333
2024 | summer | CHINO_2_APEBT1 | PLANT_MAINTENANCE | 0
2024 | summer | CHINO_2_APEBT1 | PLANT_TROUBLE | 1695.13
2024 | summer | CHINO_2_PESBT1 | METERING_TELEMETRY | 0
2024 | summer | CHINO_2_PESBT1 | PLANT_TROUBLE | 612.8
2024 | summer | CHINO_2_PESBT1 | UNIT_TESTING | 0
2024 | summer | CHWCHL_1_AVSSR1 | NEW_GENERATOR_TEST_ENERGY | 670.6347
2024 | summer | CHWCHL_1_AVSSR2 | NEW_GENERATOR_TEST_ENERGY | 1311.75
2024 | summer | CHWCHL_1_UNIT | AMBIENT_DUE_TO_TEMP | 503.1233
2024 | summer | CHWCHL_1_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 2.64
2024 | summer | CHWCHL_1_UNIT | PLANT_TROUBLE | 109.24
2024 | summer | CLINESCO_3_PVDYN | PLANT_TROUBLE | 0
2024 | summer | CLINESCO_3_PVDYN | TRANSITIONAL_LIMITATION | 29.955
2024 | summer | CLINESCO_3_PVDYN | TRANSMISSION_INDUCED | 309.741
2024 | summer | CLINESCO_3_WBDYN | PLANT_TROUBLE | 128.214
2024 | summer | CLINESCO_3_WBDYN | TRANSITIONAL_LIMITATION | 78.21
2024 | summer | CLINESCO_3_WBDYN | TRANSMISSION_INDUCED | 559.8827
2024 | summer | CLOVER_2_UNIT | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 10.89
2024 | summer | CLOVER_2_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 2.97
2024 | summer | CLOVER_2_UNIT | ENVIRONMENTAL_RESTRICTIONS | 9.9
2024 | summer | CLOVER_2_UNIT | PLANT_TROUBLE | 6.3525
2024 | summer | CLOVER_2_UNIT | TRANSMISSION_INDUCED | 49.071
2024 | summer | CLRMNT_6_CLEBT1 | PLANT_TROUBLE | 20.5
2024 | summer | CMBLND_2_DS2BT1 | METERING_TELEMETRY | 0
2024 | summer | CMBLND_2_DS2BT1 | PLANT_TROUBLE | 1068.3
2024 | summer | CMBLND_2_DS2BT1 | RTU_RIG | 0
2024 | summer | CMBLND_2_DS2BT1 | UNIT_TESTING | 104
2024 | summer | CMBLND_2_DS2BT2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1.55
2024 | summer | CMBLND_2_DS2BT2 | AMBIENT_NOT_DUE_TO_TEMP | 48.7667
2024 | summer | CMBLND_2_DS2BT2 | METERING_TELEMETRY | 0
2024 | summer | CMBLND_2_DS2BT2 | PLANT_MAINTENANCE | 0
2024 | summer | CMBLND_2_DS2BT2 | PLANT_TROUBLE | 763.9667
2024 | summer | CMBLND_2_DS2BT2 | RTU_RIG | 0
2024 | summer | CMBLND_2_DS2BT2 | UNIT_TESTING | 106
2024 | summer | CMBLND_2_DS2BT3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | summer | CMBLND_2_DS2BT3 | METERING_TELEMETRY | 0
2024 | summer | CMBLND_2_DS2BT3 | PLANT_TROUBLE | 994.6417
2024 | summer | CMBLND_2_DS2BT3 | RTU_RIG | 0
2024 | summer | CMBLND_2_DS2BT3 | UNIT_TESTING | 147
2024 | summer | CMBLND_2_DS2SR1 | METERING_TELEMETRY | 0
2024 | summer | CMBLND_2_DS2SR1 | PLANT_TROUBLE | 140
2024 | summer | CMBLND_2_DS2SR1 | UNIT_TESTING | 13
2024 | summer | CMBLND_2_DS2SR2 | METERING_TELEMETRY | 0
2024 | summer | CMBLND_2_DS2SR2 | PLANT_MAINTENANCE | 0
2024 | summer | CMBLND_2_DS2SR2 | PLANT_TROUBLE | 0
2024 | summer | CMBLND_2_DS2SR2 | RTU_RIG | 0
2024 | summer | CMBLND_2_DS2SR2 | UNIT_TESTING | 143
2024 | summer | CMBLND_2_DS2SR3 | METERING_TELEMETRY | 0
2024 | summer | CMBLND_2_DS2SR3 | UNIT_TESTING | 246.6
2024 | summer | CNTNLA_2_SOLAR1 | TRANSMISSION_INDUCED | 250
2024 | summer | CNTNLA_2_SOLAR2 | TRANSMISSION_INDUCED | 91.2
2024 | summer | COCOPP_2_CTG1 | AMBIENT_DUE_TO_TEMP | 8024.22
2024 | summer | COCOPP_2_CTG1 | PLANT_MAINTENANCE | 0
2024 | summer | COCOPP_2_CTG1 | UNIT_TESTING | 46
2024 | summer | COCOPP_2_CTG2 | AMBIENT_DUE_TO_TEMP | 7489.46
2024 | summer | COCOPP_2_CTG2 | PLANT_MAINTENANCE | 0
2024 | summer | COCOPP_2_CTG2 | PLANT_TROUBLE | 182.8933
2024 | summer | COCOPP_2_CTG2 | UNIT_TESTING | 38.5
2024 | summer | COCOPP_2_CTG3 | AMBIENT_DUE_TO_TEMP | 12373.18
2024 | summer | COCOPP_2_CTG3 | PLANT_MAINTENANCE | 0
2024 | summer | COCOPP_2_CTG3 | PLANT_TROUBLE | 0
2024 | summer | COCOPP_2_CTG3 | UNIT_TESTING | 69.8
2024 | summer | COCOPP_2_CTG4 | AMBIENT_DUE_TO_TEMP | 7766.89
2024 | summer | COCOPP_2_CTG4 | PLANT_MAINTENANCE | 0
2024 | summer | COCOPP_2_CTG4 | UNIT_TESTING | 46.45
2024 | summer | COGNAT_1_UNIT | PLANT_MAINTENANCE | 680
2024 | summer | COGNAT_1_UNIT | PLANT_TROUBLE | 1083.3833
2024 | summer | COGNAT_1_UNIT | UNIT_TESTING | 0
2024 | summer | COLEMN_2_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | summer | COLEMN_2_UNIT | METERING_TELEMETRY | 0
2024 | summer | COLEMN_2_UNIT | PLANT_MAINTENANCE | 63.4833
2024 | summer | COLGAT_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 13284.95
2024 | summer | COLGAT_7_UNIT 1 | PLANT_MAINTENANCE | 0
2024 | summer | COLGAT_7_UNIT 1 | TRANSMISSION_INDUCED | 0
2024 | summer | COLGAT_7_UNIT 1 | UNIT_TESTING | 0
2024 | summer | COLGAT_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 14821.7333
2024 | summer | COLGAT_7_UNIT 2 | PLANT_MAINTENANCE | 395
2024 | summer | COLGAT_7_UNIT 2 | PLANT_TROUBLE | 413.35
2024 | summer | COLGAT_7_UNIT 2 | UNIT_TESTING | 0
2024 | summer | COLGNS_2_CNSSR1 | PLANT_MAINTENANCE | 575.2
2024 | summer | COLGNS_2_CNSSR1 | PLANT_TROUBLE | 14097.4133
2024 | summer | COLGNS_2_CNSSR1 | TRANSMISSION_INDUCED | 192
2024 | summer | COLPIN_6_COLLNS | PLANT_MAINTENANCE | 82.5
2024 | summer | COLPIN_6_COLLNS | TRANSMISSION_INDUCED | 204.6
2024 | summer | COLTON_6_AGUAM1 | AMBIENT_DUE_TO_TEMP | 3
2024 | summer | COLTON_6_AGUAM1 | ENVIRONMENTAL_RESTRICTIONS | 1183
2024 | summer | COLTON_6_AGUAM1 | PLANT_TROUBLE | 4005
2024 | summer | COLTON_6_AGUAM1 | UNIT_TESTING | 2
2024 | summer | COLUSA_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 35695.5075
2024 | summer | COLUSA_2_PL1X3 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | summer | COLUSA_2_PL1X3 | PLANT_TROUBLE | 8109.7417
2024 | summer | COLVIL_7_PL1X2 | PLANT_MAINTENANCE | 0
2024 | summer | COLVIL_7_PL1X2 | PLANT_TROUBLE | 3010.7127
2024 | summer | COLVIL_7_PL1X2 | TRANSMISSION_INDUCED | 1641.619
2024 | summer | CONDOR_2_CDRBT1 | PLANT_MAINTENANCE | 326.6667
2024 | summer | CONDOR_2_CDRBT1 | PLANT_TROUBLE | 1423.3333
2024 | summer | CONDOR_2_CDRBT1 | RTU_RIG | 3816.6667
2024 | summer | CONDOR_2_CDRBT1 | UNIT_TESTING | 2000
2024 | summer | CONTRL_1_CASAD1 | PLANT_MAINTENANCE | 0
2024 | summer | CONTRL_1_CASAD1 | PLANT_TROUBLE | 0
2024 | summer | CONTRL_1_CASAD2 | AMBIENT_DUE_TO_TEMP | 2474.95
2024 | summer | CONTRL_1_CASAD2 | AMBIENT_NOT_DUE_TO_TEMP | 43.8
2024 | summer | CONTRL_1_CASAD2 | METERING_TELEMETRY | 0.4
2024 | summer | CONTRL_1_CASAD2 | PLANT_MAINTENANCE | 0
2024 | summer | CONTRL_1_CASAD2 | PLANT_TROUBLE | 144.1
2024 | summer | CONTRL_1_CASAD2 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 174.4
2024 | summer | CONTRL_1_CASAD3 | PLANT_MAINTENANCE | 0
2024 | summer | CONTRL_1_CASAD3 | PLANT_TROUBLE | 258.3
2024 | summer | CONTRL_1_LUNDY | AMBIENT_NOT_DUE_TO_TEMP | 963.325
2024 | summer | CONTRL_1_LUNDY | PLANT_MAINTENANCE | 15
2024 | summer | CONTRL_1_LUNDY | TRANSMISSION_INDUCED | 37.7
2024 | summer | CONTRL_1_OXBOW | PLANT_MAINTENANCE | 30
2024 | summer | CONTRL_1_OXBOW | PLANT_TROUBLE | 14805.4167
2024 | summer | CONTRL_1_OXBOW | TRANSMISSION_INDUCED | 60
2024 | summer | CONTRL_1_POOLE | AMBIENT_NOT_DUE_TO_TEMP | 279.39
2024 | summer | CONTRL_1_POOLE | PLANT_TROUBLE | 101.2
2024 | summer | CONTRL_1_POOLE | TRANSMISSION_INDUCED | 225.9
2024 | summer | CONTRL_1_QF | TRANSMISSION_INDUCED | 10.2
2024 | summer | CONTRL_1_RUSHCK | AMBIENT_NOT_DUE_TO_TEMP | 120.9
2024 | summer | CONTRL_1_RUSHCK | TRANSMISSION_INDUCED | 0
2024 | summer | COPMT2_2_SOLAR2 | METERING_TELEMETRY | 87.5
2024 | summer | COPMT2_2_SOLAR2 | PLANT_TROUBLE | 30
2024 | summer | COPMT2_2_SOLAR2 | TRANSMISSION_INDUCED | 310
2024 | summer | CORCAN_1_SOLAR1 | PLANT_TROUBLE | 93.3333
2024 | summer | CORCAN_1_SOLAR2 | TRANSMISSION_INDUCED | 55
2024 | summer | CORONS_6_CLRWTR | PLANT_TROUBLE | 711.985
2024 | summer | CORRAL_6_SJOAQN | METERING_TELEMETRY | 55.9
2024 | summer | CORRAL_6_SJOAQN | PLANT_MAINTENANCE | 21.1
2024 | summer | CORRAL_6_SJOAQN | PLANT_TROUBLE | 296.0592
2024 | summer | CORRAL_6_SJOAQN | TRANSMISSION_INDUCED | 236.5
2024 | summer | COVERD_2_HCKHY1 | ENVIRONMENTAL_RESTRICTIONS | 4544.4143
2024 | summer | COVERD_2_MCKHY1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 2011.5
2024 | summer | COVERD_2_QFUNTS | ENVIRONMENTAL_RESTRICTIONS | 29.975
2024 | summer | COVERD_2_QFUNTS | TRANSMISSION_INDUCED | 115.6833
2024 | summer | COVERD_2_RCKHY1 | ENVIRONMENTAL_RESTRICTIONS | 1110.6667
2024 | summer | COVERD_2_RCKHY1 | TRANSMISSION_INDUCED | 1.9667
2024 | summer | COWCRK_2_UNIT | PLANT_TROUBLE | 1468
2024 | summer | CPVERD_2_SOLAR | PLANT_MAINTENANCE | 0
2024 | summer | CPVERD_2_SOLAR | TRANSMISSION_INDUCED | 0
2024 | summer | CRELMN_6_AABBT1 | PLANT_MAINTENANCE | 4.7
2024 | summer | CRELMN_6_AABBT1 | PLANT_TROUBLE | 61.1
2024 | summer | CRELMN_6_AABBT1 | TRANSMISSION_INDUCED | 0
2024 | summer | CRELMN_6_RAMON1 | PLANT_TROUBLE | 12
2024 | summer | CRELMN_6_RAMON2 | PLANT_TROUBLE | 30
2024 | summer | CRELMN_6_RAMSR3 | PLANT_TROUBLE | 151.2
2024 | summer | CRELMN_6_RAMSR3 | TRANSMISSION_INDUCED | 0
2024 | summer | CRESTA_7_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 28553.8668
2024 | summer | CRESTA_7_PL1X2 | PLANT_TROUBLE | 0
2024 | summer | CRESTA_7_PL1X2 | TRANSMISSION_INDUCED | 0
2024 | summer | CRIMSN_2_CRMBT1 | METERING_TELEMETRY | 50
2024 | summer | CRIMSN_2_CRMBT1 | PLANT_MAINTENANCE | 300
2024 | summer | CRIMSN_2_CRMBT1 | PLANT_TROUBLE | 13130.2583
2024 | summer | CRIMSN_2_CRMBT2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 38.8833
2024 | summer | CRIMSN_2_CRMBT2 | METERING_TELEMETRY | 71.2667
2024 | summer | CRIMSN_2_CRMBT2 | PLANT_MAINTENANCE | 94.3333
2024 | summer | CRIMSN_2_CRMBT2 | PLANT_TROUBLE | 4993.1667
2024 | summer | CRNEVL_6_CRNVA | AMBIENT_NOT_DUE_TO_TEMP | 90
2024 | summer | CRNEVL_6_CRNVA | PLANT_MAINTENANCE | 238.5
2024 | summer | CRNEVL_6_SJQN 2 | AMBIENT_NOT_DUE_TO_TEMP | 1488
2024 | summer | CROKET_7_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 130.0833
2024 | summer | CROKET_7_UNIT | PLANT_MAINTENANCE | 0
2024 | summer | CRSTWD_6_KUMYAY | TRANSMISSION_INDUCED | 12.5
2024 | summer | CRWCKS_1_SOLAR1 | METERING_TELEMETRY | 64.4
2024 | summer | CRWCKS_1_SOLAR1 | PLANT_TROUBLE | 150
2024 | summer | CSCCOG_1_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 3605
2024 | summer | CSCGNR_1_UNIT 1 | AMBIENT_DUE_TO_TEMP | 1640.0825
2024 | summer | CSCGNR_1_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | summer | CSCGNR_1_UNIT 1 | PLANT_TROUBLE | 188.5125
2024 | summer | CSCGNR_1_UNIT 2 | AMBIENT_DUE_TO_TEMP | 1800.0492
2024 | summer | CSCGNR_1_UNIT 2 | PLANT_TROUBLE | 0
2024 | summer | CSCGNR_1_UNIT 2 | UNIT_TESTING | 2.65
2024 | summer | CSLR4S_2_SOLAR | PLANT_TROUBLE | 500
2024 | summer | CSLR4S_2_SOLAR | TRANSMISSION_INDUCED | 195
2024 | summer | CSTOGA_6_LNDFIL | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 131.75
2024 | summer | CSTRVL_7_PL1X2 | TRANSMISSION_INDUCED | 22.65
2024 | summer | CSTRVL_7_QFUNTS | TRANSMISSION_INDUCED | 10
2024 | summer | CUMBIA_1_SOLAR | METERING_TELEMETRY | 0
2024 | summer | CUMBIA_1_SOLAR | PLANT_TROUBLE | 360
2024 | summer | CUMBIA_1_SOLAR | TRANSMISSION_INDUCED | 80.2333
2024 | summer | CUYAMA_6_SB3SB1 | METERING_TELEMETRY | 0
2024 | summer | CUYAMA_6_SB3SB1 | PLANT_TROUBLE | 30
2024 | summer | CUYAMS_6_CUYSR1 | METERING_TELEMETRY | 3962
2024 | summer | CUYAMS_6_CUYSR1 | PLANT_TROUBLE | 1748.6667
2024 | summer | CUYAMS_6_CUYSR1 | TRANSMISSION_INDUCED | 1000
2024 | summer | DAIRLD_1_CR1BM1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 225.9667
2024 | summer | DAIRLD_1_CR1BM1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | summer | DAIRLD_1_CR1BM1 | PLANT_MAINTENANCE | 0.13333
2024 | summer | DAIRLD_1_CR1BM1 | PLANT_TROUBLE | 12
2024 | summer | DAVIS_1_SOLAR1 | AMBIENT_NOT_DUE_TO_TEMP | 675
2024 | summer | DAVIS_1_SOLAR2 | AMBIENT_NOT_DUE_TO_TEMP | 565
2024 | summer | DEADCK_1_UNIT | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1286.6917
2024 | summer | DEADCK_1_UNIT | TRANSMISSION_INDUCED | 147.1833
2024 | summer | DEERCR_6_UNIT 1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 2149
2024 | summer | DEERCR_6_UNIT 1 | PLANT_TROUBLE | 264.7167
2024 | summer | DEERCR_6_UNIT 1 | TRANSMISSION_INDUCED | 142.3333
2024 | summer | DELAMO_2_ALASB2 | PLANT_MAINTENANCE | 0
2024 | summer | DELAMO_2_ALASB2 | PLANT_TROUBLE | 50
2024 | summer | DELSUR_6_CREST | METERING_TELEMETRY | 6.85
2024 | summer | DELSUR_6_CREST | PLANT_TROUBLE | 52.15
2024 | summer | DELSUR_6_CREST | TRANSMISSION_INDUCED | 0
2024 | summer | DELSUR_6_DRYFRB | PLANT_TROUBLE | 330
2024 | summer | DELSUR_6_SOLAR1 | TRANSMISSION_INDUCED | 0
2024 | summer | DELSUR_6_SOLAR4 | PLANT_MAINTENANCE | 7.5
2024 | summer | DELSUR_6_SOLAR5 | PLANT_MAINTENANCE | 7.5
2024 | summer | DELTA_2_PL1X4 | AMBIENT_DUE_TO_TEMP | 25896.585
2024 | summer | DELTA_2_PL1X4 | PLANT_TROUBLE | 3303.2333
2024 | summer | DELTA_2_PL1X4 | TRANSITIONAL_LIMITATION | 2086.0843
2024 | summer | DELTA_2_PL1X4 | UNIT_TESTING | 0
2024 | summer | DEVERS_1_SOLAR | PLANT_MAINTENANCE | 0
2024 | summer | DEVERS_1_SOLAR | TRANSMISSION_INDUCED | 37.3083
2024 | summer | DEVERS_1_SOLAR1 | PLANT_MAINTENANCE | 46
2024 | summer | DEVERS_1_SOLAR2 | PLANT_MAINTENANCE | 33.9
2024 | summer | DEVERS_1_SOLAR2 | PLANT_TROUBLE | 45
2024 | summer | DEVERS_2_DHSPG2 | PLANT_TROUBLE | 28
2024 | summer | DEXZEL_1_UNIT | AMBIENT_DUE_TO_TEMP | 30.3
2024 | summer | DEXZEL_1_UNIT | PLANT_TROUBLE | 6719.9032
2024 | summer | DIABLO_7_UNIT 1 | METERING_TELEMETRY | 600
2024 | summer | DIABLO_7_UNIT 1 | PLANT_MAINTENANCE | 6520
2024 | summer | DIABLO_7_UNIT 1 | PLANT_TROUBLE | 3375.1333
2024 | summer | DISCOV_1_CHEVRN | PLANT_MAINTENANCE | 8.1333
2024 | summer | DISCOV_1_CHEVRN | PLANT_TROUBLE | 1070.04
2024 | summer | DIXNLD_1_LNDFL | ENVIRONMENTAL_RESTRICTIONS | 16
2024 | summer | DONNLS_7_UNIT | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1173.95
2024 | summer | DONNLS_7_UNIT | TRANSMISSION_INDUCED | 2797.2
2024 | summer | DOSMGO_2_NSPIN | TRANSMISSION_INDUCED | 156.35
2024 | summer | DOUBLC_1_UNITS | AMBIENT_DUE_TO_TEMP | 2564.2833
2024 | summer | DOUBLC_1_UNITS | PLANT_TROUBLE | 389.915
2024 | summer | DOUBLC_1_UNITS | UNIT_TESTING | 297.84
2024 | summer | DRACKR_2_D4SR4B | PLANT_MAINTENANCE | 0
2024 | summer | DRACKR_2_DS3SR3 | PLANT_MAINTENANCE | 32.8827
2024 | summer | DRACKR_2_DS3SR3 | PLANT_TROUBLE | 556.4787
2024 | summer | DRACKR_2_DS4SR4 | PLANT_MAINTENANCE | 0
2024 | summer | DRACKR_2_DSUBT1 | PLANT_TROUBLE | 670.9033
2024 | summer | DRACKR_2_DSUBT2 | PLANT_TROUBLE | 607.2957
2024 | summer | DRACKR_2_DSUBT2 | UNIT_TESTING | 920
2024 | summer | DRACKR_2_DSUBT3 | PLANT_TROUBLE | 499.8403
2024 | summer | DRACKR_2_DSUBT3 | UNIT_TESTING | 920
2024 | summer | DRACKR_2_DSUBT4 | PLANT_TROUBLE | 425.5932
2024 | summer | DRACKR_2_SOLAR1 | PLANT_TROUBLE | 0
2024 | summer | DRACKR_2_SOLAR2 | PLANT_TROUBLE | 0
2024 | summer | DREWSR_2_BHSSR1 | PLANT_TROUBLE | 0
2024 | summer | DREWS_6_PL1X4 | METERING_TELEMETRY | 92.7
2024 | summer | DREWS_6_PL1X4 | UNIT_TESTING | 698.7217
2024 | summer | DRUM_7_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 11729.4167
2024 | summer | DRUM_7_PL3X4 | AMBIENT_NOT_DUE_TO_TEMP | 13140.9
2024 | summer | DRUM_7_PL3X4 | PLANT_TROUBLE | 84.28
2024 | summer | DRUM_7_UNIT 5 | AMBIENT_NOT_DUE_TO_TEMP | 13371.4
2024 | summer | DRUM_7_UNIT 5 | PLANT_TROUBLE | 900
2024 | summer | DSABLA_7_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 4542.3483
2024 | summer | DSABLA_7_UNIT | PLANT_TROUBLE | 57.0417
2024 | summer | DSFLWR_2_W9CSB1 | METERING_TELEMETRY | 0
2024 | summer | DSFLWR_2_W9CSB1 | PLANT_MAINTENANCE | 0
2024 | summer | DSFLWR_2_W9CSB1 | PLANT_TROUBLE | 459
2024 | summer | DSFLWR_2_W9CSB2 | PLANT_TROUBLE | 4176
2024 | summer | DSFLWR_2_W9CSB2 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 1872
2024 | summer | DSFLWR_2_WS2SR1 | METERING_TELEMETRY | 3797.8
2024 | summer | DSFLWR_2_WS2SR1 | PLANT_MAINTENANCE | 0
2024 | summer | DSFLWR_2_WS2SR1 | PLANT_TROUBLE | 19221.4
2024 | summer | DSRTHV_2_DH1SR1 | PLANT_TROUBLE | 0
2024 | summer | DSRTHV_2_DH2BT1 | METERING_TELEMETRY | 0
2024 | summer | DSRTHV_2_DH2BT1 | PLANT_MAINTENANCE | 700.9433
2024 | summer | DSRTHV_2_DH2BT1 | PLANT_TROUBLE | 3957.67
2024 | summer | DSRTSL_2_SOLAR1 | PLANT_MAINTENANCE | 148.095
2024 | summer | DSRTSL_2_SOLAR1 | PLANT_TROUBLE | 9420.7
2024 | summer | DSRTSL_2_SOLAR1 | TRANSMISSION_INDUCED | 0
2024 | summer | DSRTSN_2_DS2BX2 | METERING_TELEMETRY | 0
2024 | summer | DSRTSN_2_DS2BX2 | PLANT_MAINTENANCE | 0
2024 | summer | DSRTSN_2_DS2BX2 | PLANT_TROUBLE | 3832.1213
2024 | summer | DSRTSN_2_DS2X2 | METERING_TELEMETRY | 295.1667
2024 | summer | DSRTSN_2_DS2X2 | PLANT_TROUBLE | 1492.7855
2024 | summer | DSRTSN_2_DS2X2 | UNIT_TESTING | 3450
2024 | summer | DSRTSN_2_SOLAR1 | METERING_TELEMETRY | 0
2024 | summer | DSRTSN_2_SOLAR1 | PLANT_MAINTENANCE | 150
2024 | summer | DSRTSN_2_SOLAR1 | PLANT_TROUBLE | 1414.25
2024 | summer | DSRTSN_2_SOLAR2 | PLANT_MAINTENANCE | 0
2024 | summer | DSRTSN_2_SOLAR2 | PLANT_TROUBLE | 449.5333
2024 | summer | DTCHWD_2_BT3WND | PLANT_TROUBLE | 642.7
2024 | summer | DTCHWD_2_BT4WND | PLANT_TROUBLE | 2151.6
2024 | summer | DUANE_1_PL1X3 | AMBIENT_NOT_DUE_TO_TEMP | 7439
2024 | summer | DUANE_1_PL1X3 | PLANT_TROUBLE | 742.8145
2024 | summer | DURNMESA_3_WBDYN | PLANT_TROUBLE | 0
2024 | summer | DURNMESA_3_WBDYN | TRANSITIONAL_LIMITATION | 39.81
2024 | summer | DURNMESA_3_WBDYN | TRANSMISSION_INDUCED | 305.622
2024 | summer | DUTCH1_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 7490.2483
2024 | summer | DUTCH1_7_UNIT 1 | PLANT_TROUBLE | 0
2024 | summer | DUTCH1_7_UNIT 1 | TRANSMISSION_INDUCED | 66
2024 | summer | DUTCH2_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 10972.4333
2024 | summer | DUTCH2_7_UNIT 1 | PLANT_TROUBLE | 38.1333
2024 | summer | DUTCH2_7_UNIT 1 | TRANSMISSION_INDUCED | 78
2024 | summer | DVLCYN_1_UNITS | ENVIRONMENTAL_RESTRICTIONS | 61.0833
2024 | summer | DVLCYN_1_UNITS | PLANT_MAINTENANCE | 4740
2024 | summer | DVLCYN_1_UNITS | PLANT_TROUBLE | 38.4167
2024 | summer | DVLCYN_1_UNITS | RTU_RIG | 510
2024 | summer | DVLCYN_1_UNITS | TRANSMISSION_INDUCED | 1075.1667
2024 | summer | DYERSM_6_DSWWD1 | ENVIRONMENTAL_RESTRICTIONS | 96.6633
2024 | summer | DYERSM_6_DSWWD1 | METERING_TELEMETRY | 0
2024 | summer | DYERSM_6_DSWWD1 | PLANT_MAINTENANCE | 57.455
2024 | summer | DYERSM_6_DSWWD1 | PLANT_TROUBLE | 62.5
2024 | summer | DYERSM_6_DSWWD1 | TRANSMISSION_INDUCED | 720.5333
2024 | summer | DYLAN_2_BMTBT1 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | summer | DYLAN_2_BMTBT1 | PLANT_TROUBLE | 85
2024 | summer | DYLAN_2_BMTBT1 | TRANSMISSION_INDUCED | 20
2024 | summer | DYLAN_2_BMTBT1 | UNIT_TESTING | 200
2024 | summer | EASTWD_7_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | summer | EASTWD_7_UNIT | PLANT_MAINTENANCE | 3000
2024 | summer | EASTWD_7_UNIT | PLANT_TROUBLE | 24518.6667
2024 | summer | EASTWD_7_UNIT | TRANSMISSION_INDUCED | 3000
2024 | summer | EASTWD_7_UNIT | UNIT_TESTING | 0
2024 | summer | EDMONS_2_NSPIN | PLANT_TROUBLE | 38687
2024 | summer | EDWARD_2_E21SB1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 55.3333
2024 | summer | EDWARD_2_E21SB1 | PLANT_TROUBLE | 412.2333
2024 | summer | EDWARD_2_E23SB1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | summer | EDWARD_2_E23SB1 | PLANT_MAINTENANCE | 0
2024 | summer | EDWARD_2_E23SB1 | PLANT_TROUBLE | 1790.35
2024 | summer | EDWARD_2_ES2BT3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 10.1667
2024 | summer | EDWARD_2_ES2BT3 | PLANT_TROUBLE | 4388.3167
2024 | summer | EDWARD_2_ESSSB1 | NEW_GENERATOR_TEST_ENERGY | 34752
2024 | summer | EDWARD_2_ESSSB1 | PLANT_TROUBLE | 14548
2024 | summer | EDWARD_2_ESSSB2 | PLANT_MAINTENANCE | 0
2024 | summer | EDWARD_2_ESSSB2 | PLANT_TROUBLE | 12
2024 | summer | EEKTMN_6_SOLAR1 | PLANT_TROUBLE | 5
2024 | summer | ELCABO_5_ECWSCEDYN | AMBIENT_NOT_DUE_TO_TEMP | 39.2
2024 | summer | ELCABO_5_ECWSCEDYN | TRANSITIONAL_LIMITATION | 3068
2024 | summer | ELCABO_5_ECWSCEDYN | TRANSMISSION_INDUCED | 16874.5667
2024 | summer | ELCAJN_6_EB1BT1 | PLANT_MAINTENANCE | 0
2024 | summer | ELCAJN_6_EB1BT1 | PLANT_TROUBLE | 491
2024 | summer | ELCAJN_6_LM6K | AMBIENT_DUE_TO_TEMP | 490.4
2024 | summer | ELCAJN_6_LM6K | PLANT_MAINTENANCE | 0
2024 | summer | ELCAJN_6_LM6K | PLANT_TROUBLE | 656.385
2024 | summer | ELCAJN_6_UNITA1 | PLANT_MAINTENANCE | 0
2024 | summer | ELCAJN_6_UNITA1 | PLANT_TROUBLE | 2210.9127
2024 | summer | ELDORO_7_UNIT 1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 5704.65
2024 | summer | ELDORO_7_UNIT 1 | PLANT_MAINTENANCE | 4
2024 | summer | ELDORO_7_UNIT 2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 5171.5
2024 | summer | ELDORO_7_UNIT 2 | PLANT_MAINTENANCE | 4
2024 | summer | ELECTR_7_PL1X3 | AMBIENT_NOT_DUE_TO_TEMP | 8665.8667
2024 | summer | ELECTR_7_PL1X3 | PLANT_TROUBLE | 0
2024 | summer | ELKCRK_6_STONYG | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1107.4
2024 | summer | ELKCRK_6_STONYG | AMBIENT_NOT_DUE_TO_TEMP | 1984.5
2024 | summer | ELKHIL_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 34652.5833
2024 | summer | ELKHIL_2_PL1X3 | PLANT_MAINTENANCE | 95117
2024 | summer | ELKHIL_2_PL1X3 | PLANT_TROUBLE | 31367.8
2024 | summer | ELKHRN_1_EESX3 | PLANT_MAINTENANCE | 7805.0657
2024 | summer | ELKHRN_1_EESX3 | PLANT_TROUBLE | 1623.7128
2024 | summer | ELLIOT_6_ELIBT1 | METERING_TELEMETRY | 300
2024 | summer | ELLIOT_6_ELIBT1 | PLANT_MAINTENANCE | 1
2024 | summer | ELLIOT_6_ELIBT1 | PLANT_TROUBLE | 0
2024 | summer | ELSEGN_2_UN1011 | AMBIENT_DUE_TO_TEMP | 1893.779
2024 | summer | ELSEGN_2_UN1011 | METERING_TELEMETRY | 292.5973
2024 | summer | ELSEGN_2_UN1011 | PLANT_MAINTENANCE | 9600.85
2024 | summer | ELSEGN_2_UN1011 | PLANT_TROUBLE | 1115.5122
2024 | summer | ELSEGN_2_UN1011 | UNIT_TESTING | 0
2024 | summer | ELSEGN_2_UN2021 | AMBIENT_DUE_TO_TEMP | 149.457
2024 | summer | ELSEGN_2_UN2021 | METERING_TELEMETRY | 0
2024 | summer | ELSEGN_2_UN2021 | PLANT_MAINTENANCE | 7998.214
2024 | summer | ELSEGN_2_UN2021 | PLANT_TROUBLE | 18622.741
2024 | summer | ELSEGN_2_UN2021 | TRANSMISSION_INDUCED | 1358.7
2024 | summer | ENERSJ_2_WIND | PLANT_TROUBLE | 0
2024 | summer | ENERSJ_2_WIND | TRANSMISSION_INDUCED | 0
2024 | summer | ENERSJ_5_ESJWD2 | PLANT_MAINTENANCE | 0
2024 | summer | ENERSJ_5_ESJWD2 | PLANT_TROUBLE | 383.775
2024 | summer | ENERSJ_5_ESJWD2 | TRANSMISSION_INDUCED | 0
2024 | summer | ENWIND_2_WIND1 | PLANT_TROUBLE | 188.4
2024 | summer | ENWIND_2_WIND2 | PLANT_TROUBLE | 65.05
2024 | summer | ESCNDO_6_EB1BT1 | PLANT_MAINTENANCE | 346.5
2024 | summer | ESCNDO_6_EB1BT1 | PLANT_TROUBLE | 2858.5
2024 | summer | ESCNDO_6_EB2BT2 | PLANT_MAINTENANCE | 417.75
2024 | summer | ESCNDO_6_EB2BT2 | PLANT_TROUBLE | 2111.5
2024 | summer | ESCNDO_6_EB3BT3 | METERING_TELEMETRY | 491.5
2024 | summer | ESCNDO_6_EB3BT3 | PLANT_MAINTENANCE | 66
2024 | summer | ESCNDO_6_EB3BT3 | PLANT_TROUBLE | 2305
2024 | summer | ESCNDO_6_PL1X2 | AMBIENT_DUE_TO_TEMP | 324.3
2024 | summer | ESCNDO_6_PL1X2 | PLANT_TROUBLE | 127.5975
2024 | summer | ESCNDO_6_UNITB1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1152
2024 | summer | ESCNDO_6_UNITB1 | PLANT_MAINTENANCE | 0
2024 | summer | ESCNDO_6_UNITB1 | PLANT_TROUBLE | 334.6787
2024 | summer | ESCNDO_6_UNITB1 | TRANSMISSION_INDUCED | 0
2024 | summer | ESCNDO_6_UNITB1 | UNIT_TESTING | 0
2024 | summer | ESCO_6_GLMQF | AMBIENT_DUE_TO_TEMP | 1421.64
2024 | summer | ESCO_6_GLMQF | METERING_TELEMETRY | 249.5
2024 | summer | ESCO_6_GLMQF | PLANT_TROUBLE | 124.7567
2024 | summer | ESNHWR_2_WC1BT1 | METERING_TELEMETRY | 2.7
2024 | summer | ESNHWR_2_WC1BT1 | PLANT_MAINTENANCE | 66
2024 | summer | ESNHWR_2_WC1BT1 | PLANT_TROUBLE | 246.8
2024 | summer | ESNHWR_2_WC1BT1 | RTU_RIG | 13.4
2024 | summer | ESQUON_6_LNDFIL | PLANT_MAINTENANCE | 15.68
2024 | summer | ESQUON_6_LNDFIL | PLANT_TROUBLE | 29.155
2024 | summer | ESQUON_6_LNDFIL | TRANSMISSION_INDUCED | 8.855
2024 | summer | ESTWND_2_OPPWD1 | PLANT_TROUBLE | 0
2024 | summer | ETIWND_2_FONTNA | AMBIENT_NOT_DUE_TO_TEMP | 689.4
2024 | summer | ETIWND_2_FONTNA | TRANSMISSION_INDUCED | 3.2
2024 | summer | ETIWND_2_SEPBT1 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | summer | ETIWND_2_SEPBT1 | PLANT_MAINTENANCE | 0
2024 | summer | ETIWND_2_SEPBT1 | PLANT_TROUBLE | 5964.6667
2024 | summer | ETIWND_2_SEPBT1 | RTU_RIG | 0
2024 | summer | ETIWND_2_SEPBT1 | UNIT_TESTING | 0
2024 | summer | ETIWND_2_UNIT1 | PLANT_TROUBLE | 0
2024 | summer | ETIWND_2_UNIT1 | TRANSMISSION_INDUCED | 168
2024 | summer | ETIWND_6_GRPLND | AMBIENT_DUE_TO_TEMP | 1085.12
2024 | summer | ETIWND_6_GRPLND | AMBIENT_NOT_DUE_TO_TEMP | 9.31
2024 | summer | ETIWND_6_GRPLND | METERING_TELEMETRY | 10.71
2024 | summer | ETIWND_6_GRPLND | PLANT_MAINTENANCE | 34.9915
2024 | summer | ETIWND_6_GRPLND | PLANT_TROUBLE | 1018.1335
2024 | summer | ETIWND_6_GRPLND | TRANSMISSION_INDUCED | 0
2024 | summer | ETIWND_6_INEBT1 | NEW_GENERATOR_TEST_ENERGY | 1750
2024 | summer | ETIWND_6_INEBT1 | UNIT_TESTING | 6020
2024 | summer | EXCHEC_7_UNIT 1 | AMBIENT_DUE_TO_TEMP | 23.625
2024 | summer | EXCHEC_7_UNIT 1 | PLANT_MAINTENANCE | 86.625
2024 | summer | EXCHEC_7_UNIT 1 | PLANT_TROUBLE | 0
2024 | summer | EXCHEC_7_UNIT 1 | TRANSMISSION_INDUCED | 332.5
2024 | summer | EXCHEC_7_UNIT 1 | UNIT_TESTING | 9.45
2024 | summer | EXCLSG_1_SOLAR | PLANT_TROUBLE | 0
2024 | summer | FALBRK_6_FESBT1 | METERING_TELEMETRY | 800
2024 | summer | FALBRK_6_FESBT1 | PLANT_MAINTENANCE | 560
2024 | summer | FALBRK_6_FESBT1 | PLANT_TROUBLE | 98.8333
2024 | summer | FALBRK_6_FESBT1 | TRANSMISSION_INDUCED | 0
2024 | summer | FIFTHS_2_FSSR1 | ENVIRONMENTAL_RESTRICTIONS | 3740
2024 | summer | FILIPPI_2_QZSSRX | NEW_GENERATOR_TEST_ENERGY | 75211.4
2024 | summer | FLOWD2_2_FPLWND | METERING_TELEMETRY | 18.9
2024 | summer | FLOWD2_2_FPLWND | PLANT_MAINTENANCE | 4144.114
2024 | summer | FLOWD2_2_FPLWND | PLANT_TROUBLE | 60.3
2024 | summer | FLOWD2_2_FPLWND | TRANSMISSION_INDUCED | 1922.802
2024 | summer | FLOWD_2_RT2WD2 | PLANT_TROUBLE | 0
2024 | summer | FLOWD_2_WIND1 | PLANT_TROUBLE | 12.8917
2024 | summer | FMEADO_6_HELLHL | PLANT_MAINTENANCE | 0
2024 | summer | FMEADO_6_HELLHL | PLANT_TROUBLE | 22.11
2024 | summer | FMEADO_6_HELLHL | TRANSMISSION_INDUCED | 21.32
2024 | summer | FMEADO_7_UNIT | PLANT_TROUBLE | 100
2024 | summer | FMEADO_7_UNIT | TRANSMISSION_INDUCED | 293.8667
2024 | summer | FORBST_7_UNIT 1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 96.875
2024 | summer | FORBST_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | summer | FORBST_7_UNIT 1 | PLANT_MAINTENANCE | 0
2024 | summer | FORKBU_6_UNIT | PLANT_TROUBLE | 543.84
2024 | summer | FRESHW_1_SOLAR1 | PLANT_TROUBLE | 71.3333
2024 | summer | FRESHW_1_SOLAR1 | TRANSMISSION_INDUCED | 1191.3333
2024 | summer | FRIANT_6_UNITS | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 85
2024 | summer | FRIANT_6_UNITS | TRANSMISSION_INDUCED | 154.1667
2024 | summer | FRNTBW_6_SOLAR1 | PLANT_TROUBLE | 100
2024 | summer | FRNTBW_6_SOLAR1 | TRANSMISSION_INDUCED | 80
2024 | summer | FROGTN_1_UTICAA | PLANT_MAINTENANCE | 7
2024 | summer | FROGTN_1_UTICAA | PLANT_TROUBLE | 14.5367
2024 | summer | FROGTN_1_UTICAA | TRANSMISSION_INDUCED | 12.2733
2024 | summer | FROGTN_1_UTICAM | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | summer | FROGTN_1_UTICAM | PLANT_TROUBLE | 0
2024 | summer | FROGTN_1_UTICAM | TRANSMISSION_INDUCED | 42.66
2024 | summer | FTSWRD_6_TRFORK | TRANSMISSION_INDUCED | 138.55
2024 | summer | FTSWRD_7_QFUNTS | TRANSMISSION_INDUCED | 136
2024 | summer | GALE_1_SR3SR3 | METERING_TELEMETRY | 18.63
2024 | summer | GALE_1_SR3SR3 | PLANT_TROUBLE | 8.97
2024 | summer | GALE_1_SR3SR3 | TRANSMISSION_INDUCED | 60.49
2024 | summer | GANSO_1_WSTBM1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | summer | GANSO_1_WSTBM1 | PLANT_MAINTENANCE | 20
2024 | summer | GANSO_1_WSTBM1 | PLANT_TROUBLE | 7.0833
2024 | summer | GARLND_2_GARBT1 | METERING_TELEMETRY | 348.8333
2024 | summer | GARLND_2_GARBT1 | PLANT_MAINTENANCE | 183.3333
2024 | summer | GARLND_2_GARBT1 | PLANT_TROUBLE | 13219.25
2024 | summer | GARLND_2_GARBT1 | TRANSMISSION_INDUCED | 0
2024 | summer | GARLND_2_GARBT1 | UNIT_TESTING | 253.3667
2024 | summer | GARLND_2_GASLR | METERING_TELEMETRY | 329.755
2024 | summer | GARLND_2_GASLR | PLANT_MAINTENANCE | 1303.589
2024 | summer | GARLND_2_GASLR | PLANT_TROUBLE | 6472.9833
2024 | summer | GARLND_2_GASLR | TRANSMISSION_INDUCED | 0
2024 | summer | GARLND_2_GASLRA | PLANT_MAINTENANCE | 47.3333
2024 | summer | GARLND_2_GASLRA | PLANT_TROUBLE | 109.15
2024 | summer | GARLND_2_GASLRA | TRANSMISSION_INDUCED | 0
2024 | summer | GARLND_2_GASLRA | UNIT_TESTING | 20
2024 | summer | GARNET_1_SOLAR | METERING_TELEMETRY | 20
2024 | summer | GARNET_1_SOLAR | PLANT_MAINTENANCE | 0
2024 | summer | GARNET_1_SOLAR | PLANT_TROUBLE | 240
2024 | summer | GARNET_1_WIND | PLANT_TROUBLE | 1865.5
2024 | summer | GARNET_1_WINDS | PLANT_MAINTENANCE | 550.4
2024 | summer | GARNET_1_WINDS | PLANT_TROUBLE | 0
2024 | summer | GARNET_1_WT3WND | PLANT_TROUBLE | 7.5
2024 | summer | GARNET_2_COAWD2 | PLANT_TROUBLE | 655.2
2024 | summer | GARNET_2_HYDRO | AMBIENT_NOT_DUE_TO_TEMP | 84.3333
2024 | summer | GARNET_2_HYDRO | PLANT_TROUBLE | 14.6667
2024 | summer | GARNET_2_HYDRO | TRANSMISSION_INDUCED | 5
2024 | summer | GARNET_2_WIND1 | TRANSMISSION_INDUCED | 53.2
2024 | summer | GARNET_2_WIND2 | METERING_TELEMETRY | 0
2024 | summer | GARNET_2_WIND2 | PLANT_MAINTENANCE | 1792.9892
2024 | summer | GARNET_2_WIND2 | PLANT_TROUBLE | 15
2024 | summer | GARNET_2_WIND3 | PLANT_MAINTENANCE | 0
2024 | summer | GARNET_2_WIND3 | PLANT_TROUBLE | 0
2024 | summer | GARNET_2_WIND4 | METERING_TELEMETRY | 1303.4
2024 | summer | GARNET_2_WIND4 | PLANT_TROUBLE | 747.74
2024 | summer | GARNET_2_WIND5 | PLANT_TROUBLE | 15
2024 | summer | GASKW1_2_GW1SR1 | METERING_TELEMETRY | 20
2024 | summer | GASKW1_2_GW1SR1 | PLANT_MAINTENANCE | 67
2024 | summer | GASKW1_2_GW1SR1 | PLANT_TROUBLE | 85.8
2024 | summer | GASKW1_2_GW1SR1 | TRANSMISSION_INDUCED | 0
2024 | summer | GASKW1_2_GW2BT1 | METERING_TELEMETRY | 1832
2024 | summer | GASKW1_2_GW2BT1 | PLANT_MAINTENANCE | 3152.1107
2024 | summer | GASKW1_2_GW2BT1 | PLANT_TROUBLE | 302.9167
2024 | summer | GASKW1_2_GW2SR1 | METERING_TELEMETRY | 815.6333
2024 | summer | GASKW1_2_GW2SR1 | PLANT_MAINTENANCE | 32
2024 | summer | GASKW1_2_GW2SR1 | PLANT_TROUBLE | 2531.15
2024 | summer | GASKW1_2_GW2SR1 | RTU_RIG | 19.5
2024 | summer | GASKW1_2_GW2SR2 | METERING_TELEMETRY | 3190
2024 | summer | GASKW1_2_GW2SR2 | PLANT_MAINTENANCE | 266.9833
2024 | summer | GASKW1_2_GW2SR2 | PLANT_TROUBLE | 606.5833
2024 | summer | GASKW1_2_GW3SR1 | METERING_TELEMETRY | 2500
2024 | summer | GASKW1_2_GW3SR1 | PLANT_MAINTENANCE | 58
2024 | summer | GASKW1_2_GW3SR1 | PLANT_TROUBLE | 420.8
2024 | summer | GASKW1_2_GW4SR1 | METERING_TELEMETRY | 2500
2024 | summer | GASKW1_2_GW4SR1 | PLANT_MAINTENANCE | 60
2024 | summer | GASKW1_2_GW4SR1 | PLANT_TROUBLE | 155.6667
2024 | summer | GASKW1_2_GW5SR1 | METERING_TELEMETRY | 2500
2024 | summer | GASKW1_2_GW5SR1 | PLANT_MAINTENANCE | 60
2024 | summer | GASKW1_2_GW5SR1 | PLANT_TROUBLE | 155.6667
2024 | summer | GATEWY_2_GESBT1 | PLANT_MAINTENANCE | 18437.5
2024 | summer | GATEWY_2_GESBT1 | PLANT_TROUBLE | 132715.705
2024 | summer | GATEWY_2_GESBT1 | UNIT_TESTING | 0
2024 | summer | GATWAY_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 70724.5557
2024 | summer | GATWAY_2_PL1X3 | AMBIENT_NOT_DUE_TO_TEMP | 194.3
2024 | summer | GATWAY_2_PL1X3 | PLANT_TROUBLE | 100
2024 | summer | GENESI_2_STG | AMBIENT_NOT_DUE_TO_TEMP | 4193.75
2024 | summer | GENESI_2_STG | PLANT_TROUBLE | 0
2024 | summer | GENESI_2_STG | TRANSMISSION_INDUCED | 500
2024 | summer | GEYS11_7_UNIT11 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 3118.9333
2024 | summer | GEYS11_7_UNIT11 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 11678.87
2024 | summer | GEYS11_7_UNIT11 | PLANT_TROUBLE | 782
2024 | summer | GEYS11_7_UNIT11 | PLANT_TROUBLE | 9108.45
2024 | summer | GEYS11_7_UNIT11 | TRANSMISSION_INDUCED | 844.51
2024 | summer | GEYS12_7_UNIT12 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 12467
2024 | summer | GEYS12_7_UNIT12 | PLANT_TROUBLE | 19.7782
2024 | summer | GEYS13_7_UNIT13 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 20009
2024 | summer | GEYS13_7_UNIT13 | PLANT_MAINTENANCE | 20
2024 | summer | GEYS13_7_UNIT13 | PLANT_TROUBLE | 116.8
2024 | summer | GEYS14_7_UNIT14 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 12104.1
2024 | summer | GEYS14_7_UNIT14 | PLANT_TROUBLE | 6807.1667
2024 | summer | GEYS16_7_UNIT16 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 14207
2024 | summer | GEYS16_7_UNIT16 | PLANT_MAINTENANCE | 20
2024 | summer | GEYS17_7_UNIT17 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 13651.3
2024 | summer | GEYS17_7_UNIT17 | PLANT_MAINTENANCE | 2
2024 | summer | GEYS17_7_UNIT17 | PLANT_TROUBLE | 3895.25
2024 | summer | GEYS18_7_UNIT18 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 23499
2024 | summer | GEYS18_7_UNIT18 | PLANT_TROUBLE | 184.6727
2024 | summer | GEYS20_7_UNIT20 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 12439
2024 | summer | GEYS20_7_UNIT20 | PLANT_TROUBLE | 193.1333
2024 | summer | GIFENS_6_BUGSL1 | METERING_TELEMETRY | 158
2024 | summer | GIFENS_6_BUGSL1 | PLANT_TROUBLE | 200
2024 | summer | GIFFEN_6_SOLAR | TRANSMISSION_INDUCED | 100
2024 | summer | GIFFEN_6_SOLAR1 | PLANT_TROUBLE | 10.7
2024 | summer | GILROY_1_UNIT | AMBIENT_DUE_TO_TEMP | 9233.3
2024 | summer | GILROY_1_UNIT | PLANT_MAINTENANCE | 0
2024 | summer | GILROY_1_UNIT | PLANT_TROUBLE | 958.9
2024 | summer | GILROY_1_UNIT | TRANSMISSION_INDUCED | 157.45
2024 | summer | GILRPP_1_PL1X2 | AMBIENT_DUE_TO_TEMP | 33.4
2024 | summer | GILRPP_1_PL1X2 | PLANT_TROUBLE | 242.3767
2024 | summer | GILRPP_1_PL1X2 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 237.5
2024 | summer | GILRPP_1_PL1X2 | TRANSMISSION_INDUCED | 130.1067
2024 | summer | GILRPP_1_PL3X4 | AMBIENT_DUE_TO_TEMP | 0
2024 | summer | GILRPP_1_PL3X4 | TRANSMISSION_INDUCED | 63.91
2024 | summer | GLDFGR_6_SOLAR1 | PLANT_MAINTENANCE | 0
2024 | summer | GLDFGR_6_SOLAR1 | TRANSMISSION_INDUCED | 50
2024 | summer | GLDFGR_6_SOLAR2 | PLANT_TROUBLE | 30.02
2024 | summer | GLDFGR_6_SOLAR2 | TRANSMISSION_INDUCED | 27.36
2024 | summer | GLDTWN_6_COLUM3 | PLANT_MAINTENANCE | 0
2024 | summer | GLNARM_2_UNIT 5 | PLANT_TROUBLE | 50344.65
2024 | summer | GLNARM_7_UNIT 1 | PLANT_TROUBLE | 357.7407
2024 | summer | GLNARM_7_UNIT 1 | TRANSMISSION_INDUCED | 12.0512
2024 | summer | GLNARM_7_UNIT 1 | UNIT_TESTING | 38.7275
2024 | summer | GLNARM_7_UNIT 2 | PLANT_MAINTENANCE | 0
2024 | summer | GLNARM_7_UNIT 2 | PLANT_TROUBLE | 979.5335
2024 | summer | GLNARM_7_UNIT 2 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2024 | summer | GLNARM_7_UNIT 2 | UNIT_TESTING | 0
2024 | summer | GLNARM_7_UNIT 3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 224.15
2024 | summer | GLNARM_7_UNIT 3 | AMBIENT_DUE_TO_TEMP | 55.7808
2024 | summer | GLNARM_7_UNIT 3 | AMBIENT_NOT_DUE_TO_TEMP | 9.622
2024 | summer | GLNARM_7_UNIT 3 | PLANT_MAINTENANCE | 0
2024 | summer | GLNARM_7_UNIT 3 | PLANT_TROUBLE | 91.7445
2024 | summer | GLNARM_7_UNIT 3 | TRANSMISSION_INDUCED | 63.296
2024 | summer | GLNARM_7_UNIT 3 | UNIT_TESTING | 0
2024 | summer | GLNARM_7_UNIT 4 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 212.1
2024 | summer | GLNARM_7_UNIT 4 | AMBIENT_DUE_TO_TEMP | 38.9217
2024 | summer | GLNARM_7_UNIT 4 | AMBIENT_NOT_DUE_TO_TEMP | 8.2683
2024 | summer | GLNARM_7_UNIT 4 | PLANT_MAINTENANCE | 56.56
2024 | summer | GLNARM_7_UNIT 4 | PLANT_TROUBLE | 63.4843
2024 | summer | GLNARM_7_UNIT 4 | TRANSMISSION_INDUCED | 42.55
2024 | summer | GLNARM_7_UNIT 4 | UNIT_TESTING | 42.42
2024 | summer | GLOW_6_SOLAR | METERING_TELEMETRY | 144
2024 | summer | GLOW_6_SOLAR | PLANT_TROUBLE | 125.5
2024 | summer | GOLETA_2_GE2BT3 | METERING_TELEMETRY | 0
2024 | summer | GOLETA_2_GE2BT3 | PLANT_MAINTENANCE | 2
2024 | summer | GOLETA_2_GE2BT3 | PLANT_TROUBLE | 253
2024 | summer | GOLETA_2_GE2BT3 | UNIT_TESTING | 0
2024 | summer | GOLETA_2_VALBT1 | PLANT_MAINTENANCE | 17.28
2024 | summer | GOLETA_2_VALBT1 | PLANT_TROUBLE | 16.8333
2024 | summer | GOLETA_2_VALBT1 | UNIT_TESTING | 50
2024 | summer | GOLETA_6_ELLWOD | PLANT_MAINTENANCE | 147.6
2024 | summer | GOLETA_6_ELLWOD | PLANT_TROUBLE | 725.4
2024 | summer | GOLETA_6_ELLWOD | TRANSMISSION_INDUCED | 54
2024 | summer | GOLETA_6_TR2BM2 | AMBIENT_NOT_DUE_TO_TEMP | 89.9148
2024 | summer | GOLETA_6_TR2BM2 | PLANT_MAINTENANCE | 29.85
2024 | summer | GOLETA_6_TR2BM2 | PLANT_TROUBLE | 126.6303
2024 | summer | GOLETA_6_TR2BM2 | TRANSMISSION_INDUCED | 59.7
2024 | summer | GONZLS_6_UNIT | PLANT_MAINTENANCE | 6.745
2024 | summer | GONZLS_6_UNIT | PLANT_TROUBLE | 19.5487
2024 | summer | GONZLS_6_UNIT | TRANSMISSION_INDUCED | 42.6
2024 | summer | GOOSLK_1_SOLAR1 | TRANSMISSION_INDUCED | 13
2024 | summer | GRADYW_5_GDYWD1 | PLANT_MAINTENANCE | 0
2024 | summer | GRADYW_5_GDYWD1 | PLANT_TROUBLE | 0
2024 | summer | GRADYW_5_GDYWD1 | TRANSITIONAL_LIMITATION | 37.5
2024 | summer | GRADYW_5_GDYWD1 | TRANSMISSION_INDUCED | 426.2833
2024 | summer | GRIDLY_6_SOLAR | TRANSMISSION_INDUCED | 0
2024 | summer | GRIFFI_2_LSPDYN | PLANT_TROUBLE | 8550
2024 | summer | GRIZLY_1_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 237.5
2024 | summer | GRNLF1_1_PL1X2 | AMBIENT_DUE_TO_TEMP | 31.9167
2024 | summer | GRNLF1_1_PL1X2 | PLANT_TROUBLE | 398.7333
2024 | summer | GRNLF1_1_PL1X2 | UNIT_TESTING | 0
2024 | summer | GRNLF2_1_UNIT | AMBIENT_DUE_TO_TEMP | 8.36
2024 | summer | GRNLF2_1_UNIT | PLANT_TROUBLE | 949.8657
2024 | summer | GRNLF2_1_UNIT | UNIT_TESTING | 0
2024 | summer | GRNVLY_7_SCLAND | PLANT_MAINTENANCE | 34.0333
2024 | summer | GRNVLY_7_SCLAND | PLANT_TROUBLE | 74.2743
2024 | summer | GRNVLY_7_SCLAND | TRANSMISSION_INDUCED | 27.3787
2024 | summer | GRSCRK_6_BGCKWW | AMBIENT_NOT_DUE_TO_TEMP | 3675
2024 | summer | GRZZLY_1_BERKLY | PLANT_MAINTENANCE | 658.75
2024 | summer | GRZZLY_1_BERKLY | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 5533.5
2024 | summer | GUERNS_6_HD3BM3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 9.25
2024 | summer | GUERNS_6_HD3BM3 | PLANT_MAINTENANCE | 3
2024 | summer | GUERNS_6_HD3BM3 | PLANT_TROUBLE | 4.5
2024 | summer | GUERNS_6_SOLAR | PLANT_MAINTENANCE | 18.1667
2024 | summer | GUERNS_6_SOLAR | PLANT_TROUBLE | 507.5
2024 | summer | GUERNS_6_VH2BM1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 13.25
2024 | summer | GUERNS_6_VH2BM1 | PLANT_MAINTENANCE | 3
2024 | summer | GUERNS_6_VH2BM1 | PLANT_TROUBLE | 7.25
2024 | summer | GWFPWR_1_LDCTG1 | NEW_GENERATOR_TEST_ENERGY | 18249
2024 | summer | GWFPWR_1_LDCTG2 | NEW_GENERATOR_TEST_ENERGY | 18249
2024 | summer | GWFPWR_1_UNITS | AMBIENT_DUE_TO_TEMP | 53.432
2024 | summer | GWFPWR_1_UNITS | OTHER_USE_LIMIT_REACHED | 492.3
2024 | summer | GWFPWR_1_UNITS | PLANT_TROUBLE | 198.561
2024 | summer | GYS5X6_7_UNITS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 15613.95
2024 | summer | GYS5X6_7_UNITS | PLANT_MAINTENANCE | 77
2024 | summer | GYS5X6_7_UNITS | PLANT_TROUBLE | 1605.55
2024 | summer | GYS5X6_7_UNITS | TRANSMISSION_INDUCED | 1409.2
2024 | summer | GYS7X8_7_UNITS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 14724.0667
2024 | summer | GYS7X8_7_UNITS | PLANT_TROUBLE | 502.3657
2024 | summer | HAASPH_7_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 3678.4
2024 | summer | HAASPH_7_PL1X2 | PLANT_TROUBLE | 0
2024 | summer | HAASPH_7_PL1X2 | TRANSMISSION_INDUCED | 3640.8
2024 | summer | HALSEY_6_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 426
2024 | summer | HALSEY_6_UNIT | PLANT_MAINTENANCE | 0
2024 | summer | HALSEY_6_UNIT | PLANT_TROUBLE | 1225.325
2024 | summer | HAMLIN_1_BLDSB1 | METERING_TELEMETRY | 0
2024 | summer | HAMLIN_1_BLDSB1 | PLANT_MAINTENANCE | 0
2024 | summer | HAMLIN_1_BLDSB1 | PLANT_TROUBLE | 58769.8667
2024 | summer | HAMLIN_1_BLDSB1 | RTU_RIG | 0
2024 | summer | HAMLIN_1_BLDSB1 | UNIT_TESTING | 0
2024 | summer | HAMLIN_1_BMSBT2 | NEW_GENERATOR_TEST_ENERGY | 19180
2024 | summer | HARBGN_7_UNITS | AMBIENT_DUE_TO_TEMP | 7128.75
2024 | summer | HARBGN_7_UNITS | PLANT_MAINTENANCE | 14284.15
2024 | summer | HARBGN_7_UNITS | PLANT_TROUBLE | 12012.5643
2024 | summer | HARBGN_7_UNITS | RTU_RIG | 0
2024 | summer | HARBGN_7_UNITS | UNIT_TESTING | 20
2024 | summer | HARDWK_6_STWBM1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | summer | HARDWK_6_STWBM1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | summer | HARDWK_6_STWBM1 | PLANT_TROUBLE | 48.1167
2024 | summer | HATCR1_7_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 29.4083
2024 | summer | HATCR2_7_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | summer | HATCR2_7_UNIT | PLANT_MAINTENANCE | 1062.5
2024 | summer | HATCR2_7_UNIT | PLANT_TROUBLE | 728.7333
2024 | summer | HATLOS_6_BWDHY1 | TRANSMISSION_INDUCED | 8
2024 | summer | HATLOS_6_LSCRK | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 685.7
2024 | summer | HATLOS_6_LSCRK | PLANT_MAINTENANCE | 0
2024 | summer | HAYPRS_6_HAYHD1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 3712
2024 | summer | HAYPRS_6_HAYHD1 | PLANT_TROUBLE | 31.1267
2024 | summer | HAYPRS_6_HAYHD1 | TRANSMISSION_INDUCED | 3.5767
2024 | summer | HAYPRS_6_HAYHD2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 4254.5
2024 | summer | HAYPRS_6_HAYHD2 | PLANT_TROUBLE | 390.61
2024 | summer | HELMPG_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 7095
2024 | summer | HELMPG_7_UNIT 1 | PLANT_TROUBLE | 5494.5
2024 | summer | HELMPG_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 7095
2024 | summer | HELMPG_7_UNIT 3 | AMBIENT_NOT_DUE_TO_TEMP | 4860
2024 | summer | HELMPG_7_UNIT 3 | PLANT_TROUBLE | 0
2024 | summer | HENRTA_6_ELCBX2 | METERING_TELEMETRY | 397.6
2024 | summer | HENRTA_6_ELCTG1 | NEW_GENERATOR_TEST_ENERGY | 17427.5
2024 | summer | HENRTA_6_ELCTG2 | NEW_GENERATOR_TEST_ENERGY | 17427.5
2024 | summer | HENRTA_6_HDEBT1 | PLANT_TROUBLE | 4863
2024 | summer | HENRTA_6_HDEBT1 | UNIT_TESTING | 3.5
2024 | summer | HENRTA_6_SOLAR1 | PLANT_MAINTENANCE | 1.5
2024 | summer | HENRTA_6_SOLAR2 | PLANT_TROUBLE | 480
2024 | summer | HENRTA_6_UNITA1 | AMBIENT_DUE_TO_TEMP | 20.94
2024 | summer | HENRTA_6_UNITA1 | ENVIRONMENTAL_RESTRICTIONS | 109.956
2024 | summer | HENRTA_6_UNITA1 | OTHER_USE_LIMIT_REACHED | 424.83
2024 | summer | HENRTA_6_UNITA1 | PLANT_MAINTENANCE | 1911.735
2024 | summer | HENRTA_6_UNITA1 | PLANT_TROUBLE | 27.98
2024 | summer | HENRTA_6_UNITA1 | TRANSMISSION_INDUCED | 50.813
2024 | summer | HENRTA_6_UNITA1 | UNIT_TESTING | 466.5713
2024 | summer | HENRTA_6_UNITA2 | AMBIENT_DUE_TO_TEMP | 19.26
2024 | summer | HENRTA_6_UNITA2 | OTHER_USE_LIMIT_REACHED | 420.07
2024 | summer | HENRTA_6_UNITA2 | PLANT_MAINTENANCE | 1840.895
2024 | summer | HENRTA_6_UNITA2 | PLANT_TROUBLE | 853.3253
2024 | summer | HENRTA_6_UNITA2 | TRANSMISSION_INDUCED | 50.2437
2024 | summer | HENRTS_1_SOLAR | PLANT_MAINTENANCE | 286
2024 | summer | HENRTS_1_SOLAR | PLANT_TROUBLE | 110.2667
2024 | summer | HERDLN_6_BYHSR1 | PLANT_TROUBLE | 20
2024 | summer | HERDLN_6_BYHSR1 | TRANSMISSION_INDUCED | 0
2024 | summer | HIDSRT_2_UNITS | AMBIENT_DUE_TO_TEMP | 453.6167
2024 | summer | HIDSRT_2_UNITS | PLANT_MAINTENANCE | 15866.6667
2024 | summer | HIDSRT_2_UNITS | PLANT_TROUBLE | 5863.8933
2024 | summer | HIGHDS_2_H5SBT1 | PLANT_MAINTENANCE | 250
2024 | summer | HIGHDS_2_H5SBT1 | PLANT_TROUBLE | 2829.4895
2024 | summer | HIGHDS_2_H5SSR1 | PLANT_TROUBLE | 185.3417
2024 | summer | HINSON_6_LBECH3 | PLANT_MAINTENANCE | 3883.95
2024 | summer | HNTGBH_2_PL1X3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 6738
2024 | summer | HNTGBH_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 2216.5567
2024 | summer | HNTGBH_2_PL1X3 | PLANT_TROUBLE | 675.1465
2024 | summer | HNTGBH_7_UNIT 2 | ENVIRONMENTAL_RESTRICTIONS | 164280.6
2024 | summer | HNTGBH_7_UNIT 2 | PLANT_TROUBLE | 5052
2024 | summer | HOLGAT_1_BORAX | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | summer | HOLGAT_1_BORAX | PLANT_MAINTENANCE | 2072.6
2024 | summer | HOLGAT_1_BORAX | PLANT_TROUBLE | 128.5333
2024 | summer | HOLSTR_1_SOLAR | PLANT_MAINTENANCE | 262.5
2024 | summer | HOOVER_2_MWDPT | AMBIENT_NOT_DUE_TO_TEMP | 88440
2024 | summer | HOOVER_2_SCEPT | AMBIENT_NOT_DUE_TO_TEMP | 94274
2024 | summer | HOOVER_2_SCEPT | METERING_TELEMETRY | 0
2024 | summer | HOOVER_2_SCEPT | OTHER_USE_LIMIT_REACHED | 3210.4167
2024 | summer | HOOVER_2_VEAPT | AMBIENT_NOT_DUE_TO_TEMP | 4574
2024 | summer | HOOVER_2_VEAPT | PLANT_MAINTENANCE | 0
2024 | summer | HOOV_2_ANAPT | METERING_TELEMETRY | 0
2024 | summer | HOOV_2_ANAPT | PLANT_TROUBLE | 0
2024 | summer | HOOV_2_ANAPT | RTU_RIG | 0
2024 | summer | HUMBPP_1_UNITS3 | AMBIENT_NOT_DUE_TO_TEMP | 813.5
2024 | summer | HUMBPP_1_UNITS3 | PLANT_MAINTENANCE | 488.1
2024 | summer | HUMBPP_1_UNITS3 | PLANT_TROUBLE | 0
2024 | summer | HUMBPP_6_UNITS | AMBIENT_DUE_TO_TEMP | 162.7
2024 | summer | HUMBPP_6_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 2928.6
2024 | summer | HUMBPP_6_UNITS | PLANT_MAINTENANCE | 1239.2317
2024 | summer | HUMBPP_6_UNITS | PLANT_TROUBLE | 1042.6358
2024 | summer | HUMBPP_6_UNITS | TRANSMISSION_INDUCED | 114.7035
2024 | summer | HUMBPP_6_UNITS | UNIT_TESTING | 0
2024 | summer | HURON_6_SOLAR | PLANT_TROUBLE | 1015
2024 | summer | HYTTHM_2_UNITS | ENVIRONMENTAL_RESTRICTIONS | 1080.47
2024 | summer | HYTTHM_2_UNITS | PLANT_MAINTENANCE | 50552.8783
2024 | summer | HYTTHM_2_UNITS | PLANT_TROUBLE | 4713.3367
2024 | summer | HYTTHM_2_UNITS | TRANSMISSION_INDUCED | 4665.5
2024 | summer | HYTTHM_2_UNITS | UNIT_TESTING | 0
2024 | summer | INDIGO_1_UNIT 1 | AMBIENT_DUE_TO_TEMP | 2401.5
2024 | summer | INDIGO_1_UNIT 1 | ENVIRONMENTAL_RESTRICTIONS | 136.2
2024 | summer | INDIGO_1_UNIT 1 | PLANT_MAINTENANCE | 0
2024 | summer | INDIGO_1_UNIT 1 | PLANT_TROUBLE | 493.5767
2024 | summer | INDIGO_1_UNIT 1 | UNIT_TESTING | 21.9
2024 | summer | INDIGO_1_UNIT 2 | AMBIENT_DUE_TO_TEMP | 3154.4
2024 | summer | INDIGO_1_UNIT 2 | PLANT_MAINTENANCE | 45.3
2024 | summer | INDIGO_1_UNIT 2 | PLANT_TROUBLE | 0
2024 | summer | INDIGO_1_UNIT 3 | AMBIENT_DUE_TO_TEMP | 3399.9
2024 | summer | INDIGO_1_UNIT 3 | PLANT_MAINTENANCE | 76.52
2024 | summer | INDIGO_1_UNIT 3 | PLANT_TROUBLE | 227.8383
2024 | summer | INDIGO_1_UNIT 3 | UNIT_TESTING | 20.1
2024 | summer | INDVLY_1_UNITS | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | summer | INTKEP_2_UNITS | ENVIRONMENTAL_RESTRICTIONS | 27320.6
2024 | summer | INTKEP_2_UNITS | PLANT_MAINTENANCE | 2938.25
2024 | summer | INTKEP_2_UNITS | PLANT_TROUBLE | 1480.4
2024 | summer | INTKEP_2_UNITS | UNIT_TESTING | 160
2024 | summer | INTMNT_3_ANAHEIM | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 12980
2024 | summer | INTMNT_3_ANAHEIM | PLANT_TROUBLE | 1883.8667
2024 | summer | INTMNT_3_ANAHEIM | TRANSITIONAL_LIMITATION | 85.5
2024 | summer | INTMNT_3_ANAHEIM | UNIT_SUPPORTING_STARTUP | 540
2024 | summer | INTMNT_3_ANAHEIM | UNIT_TESTING | 680.75
2024 | summer | INTMNT_3_PASADENA | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | summer | INTMNT_3_PASADENA | PLANT_MAINTENANCE | 943
2024 | summer | INTMNT_3_PASADENA | PLANT_TROUBLE | 45.7333
2024 | summer | INTMNT_3_PASADENA | UNIT_TESTING | 762
2024 | summer | INTMNT_3_RIVERSIDE | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 8448.97
2024 | summer | INTMNT_3_RIVERSIDE | PLANT_MAINTENANCE | 0
2024 | summer | INTMNT_3_RIVERSIDE | PLANT_TROUBLE | 1306
2024 | summer | INTMNT_3_RIVERSIDE | TRANSMISSION_INDUCED | 0
2024 | summer | IVANPA_1_UNIT1 | AMBIENT_NOT_DUE_TO_TEMP | 13122.9
2024 | summer | IVANPA_1_UNIT1 | METERING_TELEMETRY | 0
2024 | summer | IVANPA_1_UNIT1 | PLANT_TROUBLE | 81.9
2024 | summer | IVANPA_1_UNIT1 | TRANSMISSION_INDUCED | 9067.8
2024 | summer | IVANPA_1_UNIT2 | METERING_TELEMETRY | 365
2024 | summer | IVANPA_1_UNIT2 | PLANT_TROUBLE | 3241.8
2024 | summer | IVANPA_1_UNIT2 | TRANSMISSION_INDUCED | 0
2024 | summer | IVANPA_1_UNIT3 | AMBIENT_NOT_DUE_TO_TEMP | 15341.55
2024 | summer | IVANPA_1_UNIT3 | PLANT_TROUBLE | 1393.5167
2024 | summer | IVANPA_1_UNIT3 | TRANSMISSION_INDUCED | 0
2024 | summer | IVSLR2_2_SM2SR1 | TRANSMISSION_INDUCED | 1425
2024 | summer | IVSLRP_2_SOLAR1 | PLANT_MAINTENANCE | 1200
2024 | summer | IVSLRP_2_SOLAR1 | PLANT_TROUBLE | 800
2024 | summer | IVSLRP_2_SOLAR1 | TRANSMISSION_INDUCED | 300
2024 | summer | IVWEST_2_SOLAR1 | PLANT_MAINTENANCE | 0
2024 | summer | JANCRK_6_RCABT1 | METERING_TELEMETRY | 10.5
2024 | summer | JANCRK_6_RCABT1 | PLANT_MAINTENANCE | 7
2024 | summer | JANCRK_6_RCABT1 | PLANT_TROUBLE | 52.1325
2024 | summer | JAVASR_1_JAVSR1 | PLANT_MAINTENANCE | 427.5
2024 | summer | JAVASR_1_JAVSR1 | PLANT_TROUBLE | 22.9
2024 | summer | JAWBNE_2_NSRWND | METERING_TELEMETRY | 80
2024 | summer | JAWBNE_2_NSRWND | PLANT_MAINTENANCE | 9015.78
2024 | summer | JAWBNE_2_NSRWND | PLANT_TROUBLE | 974.4267
2024 | summer | JAWBNE_2_SRWND | PLANT_MAINTENANCE | 96
2024 | summer | JAWBNE_2_SRWND | PLANT_TROUBLE | 1616.2
2024 | summer | JAWBNE_2_SRWWD2 | PLANT_MAINTENANCE | 81.6
2024 | summer | JAWBNE_2_SRWWD2 | PLANT_TROUBLE | 1926.065
2024 | summer | JAYNE_6_WLSLR | PLANT_TROUBLE | 23.7
2024 | summer | JAYNE_6_WLSLR | TRANSMISSION_INDUCED | 444.6
2024 | summer | JOANEC_2_ST3BT3 | PLANT_TROUBLE | 36.6667
2024 | summer | JOANEC_2_ST3BT3 | RTU_RIG | 0
2024 | summer | JOANEC_2_ST3BT3 | UNIT_TESTING | 0
2024 | summer | JOANEC_2_STABT1 | PLANT_TROUBLE | 419.5
2024 | summer | JOANEC_2_STABT1 | UNIT_TESTING | 40
2024 | summer | JOANEC_2_STABT2 | METERING_TELEMETRY | 20
2024 | summer | JOANEC_2_STABT2 | PLANT_MAINTENANCE | 0
2024 | summer | JOANEC_2_STABT2 | PLANT_TROUBLE | 23.6
2024 | summer | JOHANN_2_JOSBT1 | METERING_TELEMETRY | 24.8333
2024 | summer | JOHANN_2_JOSBT1 | PLANT_MAINTENANCE | 5
2024 | summer | JOHANN_2_JOSBT1 | PLANT_TROUBLE | 1581.5833
2024 | summer | JOHANN_2_JOSBT1 | RTU_RIG | 50
2024 | summer | JOHANN_2_JOSBT2 | PLANT_MAINTENANCE | 16
2024 | summer | JOHANN_2_JOSBT2 | PLANT_TROUBLE | 606.6167
2024 | summer | JOHANN_2_JOSBT2 | RTU_RIG | 50
2024 | summer | JOHANN_2_JOSBT2 | TRANSMISSION_INDUCED | 34.3333
2024 | summer | JOHANN_2_OCEBT2 | PLANT_MAINTENANCE | 356
2024 | summer | JOHANN_2_OCEBT2 | PLANT_TROUBLE | 5060.1167
2024 | summer | JOHANN_2_OCEBT3 | PLANT_MAINTENANCE | 0
2024 | summer | JOHANN_2_OCEBT3 | PLANT_TROUBLE | 3242.05
2024 | summer | JOHANN_2_T1BBT1 | PLANT_TROUBLE | 11.2
2024 | summer | JOHANN_2_T1BBT1 | UNIT_TESTING | 16.8
2024 | summer | KANSAS_6_SOLAR | METERING_TELEMETRY | 11.925
2024 | summer | KANSAS_6_SOLAR | PLANT_TROUBLE | 364.725
2024 | summer | KANSAS_6_SOLAR | TRANSMISSION_INDUCED | 300
2024 | summer | KEARNY_6_SESBT2 | PLANT_MAINTENANCE | 0
2024 | summer | KEARNY_6_SESBT2 | PLANT_TROUBLE | 2153.9
2024 | summer | KEKAWK_6_UNIT | PLANT_TROUBLE | 2865.5
2024 | summer | KEKAWK_6_UNIT | TRANSMISSION_INDUCED | 214.5
2024 | summer | KELSO_2_UNITS | AMBIENT_DUE_TO_TEMP | 7254.81
2024 | summer | KELSO_2_UNITS | PLANT_TROUBLE | 315.9033
2024 | summer | KELSO_2_UNITS | UNIT_TESTING | 0
2024 | summer | KELYRG_6_UNIT | PLANT_TROUBLE | 198
2024 | summer | KELYRG_6_UNIT | TRANSMISSION_INDUCED | 0
2024 | summer | KERKH2_7_UNIT 1 | AMBIENT_DUE_TO_TEMP | 1063.2367
2024 | summer | KERKH2_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 15918.1605
2024 | summer | KERKH2_7_UNIT 1 | PLANT_TROUBLE | 10707.0892
2024 | summer | KERKH2_7_UNIT 1 | TRANSITIONAL_LIMITATION | 57.3333
2024 | summer | KERKH2_7_UNIT 1 | TRANSMISSION_INDUCED | 1515.2033
2024 | summer | KERKH2_7_UNIT 1 | UNIT_TESTING | 584.82
2024 | summer | KERMAN_6_SOLAR2 | PLANT_TROUBLE | 573.75
2024 | summer | KERNEY_6_FCSSR1 | NEW_GENERATOR_TEST_ENERGY | 69.8333
2024 | summer | KERNEY_6_FCSSR1 | PLANT_TROUBLE | 91.0217
2024 | summer | KERNFT_1_UNITS | AMBIENT_DUE_TO_TEMP | 2931.5
2024 | summer | KERNFT_1_UNITS | PLANT_TROUBLE | 1278.6967
2024 | summer | KERNFT_1_UNITS | RTU_RIG | 40
2024 | summer | KERNFT_1_UNITS | UNIT_TESTING | 132
2024 | summer | KERNRG_1_UNITS | PLANT_MAINTENANCE | 562.4
2024 | summer | KERNRG_1_UNITS | PLANT_TROUBLE | 15.2
2024 | summer | KERRGN_1_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 1190
2024 | summer | KERRGN_1_UNIT 1 | PLANT_TROUBLE | 0
2024 | summer | KERRGN_1_UNIT 1 | TRANSMISSION_INDUCED | 6.9417
2024 | summer | KINGCO_1_KINGBR | PLANT_TROUBLE | 1641.385
2024 | summer | KINGRV_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 3489.3233
2024 | summer | KINGRV_7_UNIT 1 | PLANT_TROUBLE | 37.5467
2024 | summer | KINGRV_7_UNIT 1 | TRANSMISSION_INDUCED | 296.2
2024 | summer | KIRKER_7_KELCYN | PLANT_MAINTENANCE | 41.54
2024 | summer | KIRKER_7_KELCYN | PLANT_TROUBLE | 160.1713
2024 | summer | KIRKER_7_KELCYN | TRANSMISSION_INDUCED | 17.9373
2024 | summer | KNGBRD_2_SOLAR1 | PLANT_MAINTENANCE | 13
2024 | summer | KNGBRD_2_SOLAR1 | PLANT_TROUBLE | 3696.4167
2024 | summer | KNGBRD_2_SOLAR2 | PLANT_TROUBLE | 272
2024 | summer | KNGCTY_6_UNITA1 | AMBIENT_DUE_TO_TEMP | 2075
2024 | summer | KNGCTY_6_UNITA1 | PLANT_TROUBLE | 195.55
2024 | summer | KNGCTY_6_UNITA1 | TRANSMISSION_INDUCED | 3257
2024 | summer | KNTSTH_6_SOLAR | PLANT_TROUBLE | 57
2024 | summer | KNTSTH_6_WALSR1 | PLANT_MAINTENANCE | 0
2024 | summer | KNTSTH_6_WALSR1 | PLANT_TROUBLE | 180
2024 | summer | KRAMER_1_R1BX3 | METERING_TELEMETRY | 375
2024 | summer | KRAMER_1_R1BX3 | PLANT_TROUBLE | 0
2024 | summer | KRAMER_1_R1BX3 | TRANSMISSION_INDUCED | 0
2024 | summer | KRAMER_1_R1PX3 | PLANT_TROUBLE | 4.4
2024 | summer | KRAMER_1_R1PX3 | TRANSMISSION_INDUCED | 0
2024 | summer | KRAMER_1_R1PX3 | UNIT_TESTING | 0
2024 | summer | KRAMER_1_R2BX2 | PLANT_TROUBLE | 481.844
2024 | summer | KRAMER_1_R2BX2 | UNIT_TESTING | 8
2024 | summer | KRAMER_1_R2PX2 | PLANT_MAINTENANCE | 0
2024 | summer | KRAMER_2_SEGS 9 | AMBIENT_NOT_DUE_TO_TEMP | 400
2024 | summer | KRAMER_2_SEGS 9 | PLANT_TROUBLE | 1166.6667
2024 | summer | KRNCNY_6_UNIT | PLANT_MAINTENANCE | 0
2024 | summer | KRNCNY_6_UNIT | PLANT_TROUBLE | 119.0733
2024 | summer | KYCORA_6_KMSBT1 | PLANT_MAINTENANCE | 0
2024 | summer | KYCORA_6_KMSBT1 | PLANT_TROUBLE | 74.5667
2024 | summer | LAGBEL_2_CBPBT1 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | summer | LAGBEL_2_CBPBT1 | PLANT_MAINTENANCE | 183.3333
2024 | summer | LAGBEL_2_CBPBT1 | PLANT_TROUBLE | 1450
2024 | summer | LAMONT_1_SOLAR1 | PLANT_MAINTENANCE | 60
2024 | summer | LAMONT_1_SOLAR2 | PLANT_MAINTENANCE | 62.34
2024 | summer | LAMONT_1_SOLAR2 | PLANT_TROUBLE | 1536.2633
2024 | summer | LAMONT_1_SOLAR3 | PLANT_TROUBLE | 2104.05
2024 | summer | LAMONT_1_SOLAR4 | METERING_TELEMETRY | 233.1
2024 | summer | LAMONT_1_SOLAR4 | PLANT_TROUBLE | 3512.113
2024 | summer | LAMONT_1_SOLAR5 | PLANT_TROUBLE | 3531.06
2024 | summer | LAPLMA_2_UNIT 1 | AMBIENT_DUE_TO_TEMP | 10951
2024 | summer | LAPLMA_2_UNIT 1 | PLANT_TROUBLE | 6889.2167
2024 | summer | LAPLMA_2_UNIT 1 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2024 | summer | LAPLMA_2_UNIT 1 | UNIT_TESTING | 637.6667
2024 | summer | LAPLMA_2_UNIT 2 | AMBIENT_DUE_TO_TEMP | 9878
2024 | summer | LAPLMA_2_UNIT 2 | PLANT_TROUBLE | 11576.9333
2024 | summer | LAPLMA_2_UNIT 2 | UNIT_TESTING | 649.96
2024 | summer | LAPLMA_2_UNIT 3 | AMBIENT_DUE_TO_TEMP | 11207
2024 | summer | LAPLMA_2_UNIT 3 | PLANT_TROUBLE | 14400.4468
2024 | summer | LAPLMA_2_UNIT 3 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 28
2024 | summer | LAPLMA_2_UNIT 3 | UNIT_TESTING | 1435.6117
2024 | summer | LAPLMA_2_UNIT 4 | AMBIENT_DUE_TO_TEMP | 10452.2667
2024 | summer | LAPLMA_2_UNIT 4 | PLANT_TROUBLE | 26868.5
2024 | summer | LAPLMA_2_UNIT 4 | UNIT_TESTING | 894.717
2024 | summer | LARKSP_6_UNIT 1 | AMBIENT_DUE_TO_TEMP | 2227.5
2024 | summer | LARKSP_6_UNIT 1 | PLANT_MAINTENANCE | 0
2024 | summer | LARKSP_6_UNIT 1 | PLANT_TROUBLE | 106.925
2024 | summer | LARKSP_6_UNIT 2 | AMBIENT_DUE_TO_TEMP | 2227.5
2024 | summer | LARKSP_6_UNIT 2 | ENVIRONMENTAL_RESTRICTIONS | 101.2
2024 | summer | LARKSP_6_UNIT 2 | PLANT_MAINTENANCE | 0
2024 | summer | LARKSP_6_UNIT 2 | PLANT_TROUBLE | 403.0167
2024 | summer | LAROA2_2_UNITA1 | AMBIENT_DUE_TO_TEMP | 16541.5833
2024 | summer | LAROA2_2_UNITA1 | PLANT_TROUBLE | 13894.0533
2024 | summer | LASSEN_6_UNITS | PLANT_TROUBLE | 1305
2024 | summer | LASSEN_6_UNITS | TRANSMISSION_INDUCED | 1548
2024 | summer | LCKHT1_2_LH1BT1 | METERING_TELEMETRY | 22.5
2024 | summer | LCKHT1_2_LH1BT1 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | summer | LCKHT1_2_LH1BT1 | PLANT_MAINTENANCE | 45
2024 | summer | LCKHT1_2_LH1BT1 | PLANT_TROUBLE | 143.5
2024 | summer | LCKHT1_2_LH1BT1 | RTU_RIG | 45
2024 | summer | LCKHT1_2_LH1BT1 | UNIT_TESTING | 0
2024 | summer | LCKHT1_2_LH1SR1 | PLANT_TROUBLE | 4866.1667
2024 | summer | LCKHT1_2_LH1SR2 | PLANT_TROUBLE | 4040.75
2024 | summer | LEBECS_2_UNITS | AMBIENT_DUE_TO_TEMP | 16481.2253
2024 | summer | LEBECS_2_UNITS | PLANT_TROUBLE | 18322.7822
2024 | summer | LEBECS_2_UNITS | TRANSITIONAL_LIMITATION | 6196.6635
2024 | summer | LECEF_1_UNITS | AMBIENT_DUE_TO_TEMP | 14135.6287
2024 | summer | LECEF_1_UNITS | PLANT_MAINTENANCE | 0
2024 | summer | LECEF_1_UNITS | PLANT_TROUBLE | 484.9667
2024 | summer | LECONT_2_LESBT1 | PLANT_MAINTENANCE | 205
2024 | summer | LECONT_2_LESBT1 | PLANT_TROUBLE | 301.2667
2024 | summer | LECONT_2_LESBT1 | RTU_RIG | 0
2024 | summer | LECONT_2_LESBT1 | TRANSMISSION_INDUCED | 250
2024 | summer | LEPRFD_1_KANSAS | PLANT_MAINTENANCE | 1409.5
2024 | summer | LGHTHP_6_ICEGEN | ENVIRONMENTAL_RESTRICTIONS | 720
2024 | summer | LGHTHP_6_ICEGEN | PLANT_TROUBLE | 14330.4
2024 | summer | LGHTHP_6_ICEGEN | TRANSMISSION_INDUCED | 480
2024 | summer | LGHTHP_6_ICEGEN | UNIT_TESTING | 0
2024 | summer | LHILLS_6_SOLAR1 | TRANSMISSION_INDUCED | 100
2024 | summer | LILIAC_6_SOLAR | PLANT_TROUBLE | 480
2024 | summer | LITLRK_6_GBCSR1 | METERING_TELEMETRY | 60
2024 | summer | LITLRK_6_GBCSR1 | PLANT_TROUBLE | 795
2024 | summer | LITLRK_6_SOLAR1 | METERING_TELEMETRY | 427.5
2024 | summer | LITLRK_6_SOLAR1 | PLANT_TROUBLE | 1357.75
2024 | summer | LITLRK_6_SOLAR2 | PLANT_TROUBLE | 56.7333
2024 | summer | LIVOAK_1_UNIT 1 | AMBIENT_DUE_TO_TEMP | 4459.36
2024 | summer | LIVOAK_1_UNIT 1 | PLANT_TROUBLE | 909
2024 | summer | LIVOAK_1_UNIT 1 | RTU_RIG | 19.35
2024 | summer | LIVOAK_1_UNIT 1 | UNIT_TESTING | 20.79
2024 | summer | LMBEPK_2_UNITA1 | AMBIENT_DUE_TO_TEMP | 925.5417
2024 | summer | LMBEPK_2_UNITA1 | PLANT_TROUBLE | 0
2024 | summer | LMBEPK_2_UNITA2 | AMBIENT_DUE_TO_TEMP | 452.8933
2024 | summer | LMBEPK_2_UNITA2 | PLANT_TROUBLE | 30.6667
2024 | summer | LMBEPK_2_UNITA3 | AMBIENT_DUE_TO_TEMP | 996.3
2024 | summer | LMBEPK_2_UNITA3 | PLANT_TROUBLE | 177.9833
2024 | summer | LMBEPK_2_UNITA3 | UNIT_TESTING | 0
2024 | summer | LMEC_1_PL1X3 | AMBIENT_DUE_TO_TEMP | 10910.1333
2024 | summer | LMEC_1_PL1X3 | PLANT_TROUBLE | 16007.5
2024 | summer | LMEC_1_PL1X3 | TRANSMISSION_INDUCED | 32129.8
2024 | summer | LNCSTR_6_SOLAR2 | METERING_TELEMETRY | 0
2024 | summer | LODI25_2_UNIT 1 | AMBIENT_DUE_TO_TEMP | 2218
2024 | summer | LODI25_2_UNIT 1 | PLANT_TROUBLE | 515.4333
2024 | summer | LODI25_6_ERKNG1 | ENVIRONMENTAL_RESTRICTIONS | 3571.65
2024 | summer | LODI25_6_ERKNG1 | TRANSMISSION_INDUCED | 3623.85
2024 | summer | LODIEC_2_PL1X2 | AMBIENT_DUE_TO_TEMP | 21482.8
2024 | summer | LODIEC_2_PL1X2 | PLANT_TROUBLE | 2484.955
2024 | summer | LOTUS_6_LSFSR1 | METERING_TELEMETRY | 0
2024 | summer | LOTUS_6_LSFSR1 | PLANT_MAINTENANCE | 0
2024 | summer | LOTUS_6_LSFSR1 | PLANT_TROUBLE | 702
2024 | summer | LOWGAP_7_QFUNTS | ENVIRONMENTAL_RESTRICTIONS | 689.975
2024 | summer | LOWGAP_7_QFUNTS | PLANT_MAINTENANCE | 0
2024 | summer | LOWGAP_7_QFUNTS | PLANT_TROUBLE | 5.75
2024 | summer | LOWGAP_7_QFUNTS | TRANSMISSION_INDUCED | 0
2024 | summer | LTBEAR_1_LB3SR3 | PLANT_MAINTENANCE | 0
2024 | summer | LTBEAR_1_LB3SR3 | PLANT_TROUBLE | 180
2024 | summer | LTBEAR_1_LB4SR4 | PLANT_MAINTENANCE | 0
2024 | summer | LTBEAR_1_LB4SR4 | PLANT_TROUBLE | 0
2024 | summer | LTBEAR_1_LB4SR5 | PLANT_MAINTENANCE | 0
2024 | summer | LTBERA_1_LB1SR1 | PLANT_MAINTENANCE | 0
2024 | summer | MAGNLA_6_ANAHEIM | AMBIENT_DUE_TO_TEMP | 671
2024 | summer | MAGNLA_6_ANAHEIM | PLANT_MAINTENANCE | 2834
2024 | summer | MAGNLA_6_ANAHEIM | PLANT_TROUBLE | 0
2024 | summer | MAGNLA_6_ANAHEIM | UNIT_TESTING | 20
2024 | summer | MAGNLA_6_CERRITOS | PLANT_MAINTENANCE | 156
2024 | summer | MAGNLA_6_CERRITOS | PLANT_TROUBLE | 156
2024 | summer | MAGNLA_6_COLTON | PLANT_MAINTENANCE | 312
2024 | summer | MAGNLA_6_COLTON | PLANT_TROUBLE | 10
2024 | summer | MAGNLA_6_PASADENA | PLANT_MAINTENANCE | 468
2024 | summer | MAGNLA_6_PASADENA | PLANT_TROUBLE | 25
2024 | summer | MAGNLA_6_PASADENA | UNIT_TESTING | 3.98
2024 | summer | MAGUND_1_BKSSR2 | PLANT_TROUBLE | 523.2167
2024 | summer | MALAGA_1_AUCTG1 | NEW_GENERATOR_TEST_ENERGY | 18249
2024 | summer | MALAGA_1_AUCTG2 | NEW_GENERATOR_TEST_ENERGY | 18249
2024 | summer | MALAGA_1_PL1X2 | ENVIRONMENTAL_RESTRICTIONS | 340.27
2024 | summer | MALAGA_1_PL1X2 | METERING_TELEMETRY | 524.9995
2024 | summer | MALAGA_1_PL1X2 | PLANT_MAINTENANCE | 2898.3
2024 | summer | MALAGA_1_PL1X2 | PLANT_TROUBLE | 60.621
2024 | summer | MALAGA_1_PL1X2 | TRANSMISSION_INDUCED | 3091.52
2024 | summer | MALCHQ_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 12837.5
2024 | summer | MANTEC_1_ML1SR1 | TRANSMISSION_INDUCED | 5
2024 | summer | MANZNA_2_WIND | AMBIENT_DUE_TO_TEMP | 137.6333
2024 | summer | MANZNA_2_WIND | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | summer | MANZNA_2_WIND | PLANT_TROUBLE | 1387.425
2024 | summer | MARCPW_6_SOLAR1 | PLANT_MAINTENANCE | 60
2024 | summer | MARCPW_6_SOLAR1 | TRANSMISSION_INDUCED | 200
2024 | summer | MARVEL_2_MARBT3 | METERING_TELEMETRY | 0
2024 | summer | MARVEL_2_MARBT3 | PLANT_TROUBLE | 1747.85
2024 | summer | MARVEL_2_MARBT3 | UNIT_TESTING | 299.76
2024 | summer | MARVEL_2_MARBX2 | METERING_TELEMETRY | 0
2024 | summer | MARVEL_2_MARBX2 | PLANT_TROUBLE | 6473.4198
2024 | summer | MARVEL_2_MARBX2 | UNIT_TESTING | 1300
2024 | summer | MCARTH_6_FRIVRB | TRANSMISSION_INDUCED | 0
2024 | summer | MCCALL_1_QF | PLANT_MAINTENANCE | 0
2024 | summer | MCFLND_5_MBSBX2 | NEW_GENERATOR_TEST_ENERGY | 1200
2024 | summer | MCFLND_5_MBSBX2 | PLANT_TROUBLE | 16700.75
2024 | summer | MCFLND_5_MBSBX2 | TRANSMISSION_INDUCED | 515
2024 | summer | MCFLND_5_MBSBX2 | UNIT_TESTING | 1643.3333
2024 | summer | MCFLND_5_MFSBT1 | METERING_TELEMETRY | 0
2024 | summer | MCFLND_5_MFSBT1 | PLANT_MAINTENANCE | 475
2024 | summer | MCFLND_5_MFSBT1 | PLANT_TROUBLE | 9517.1333
2024 | summer | MCFLND_5_MFSBT1 | RTU_RIG | 45
2024 | summer | MCFLND_5_MFSBT1 | UNIT_TESTING | 706.6667
2024 | summer | MCFLND_5_MFSSR1 | PLANT_MAINTENANCE | 87
2024 | summer | MCFLND_5_MFSSR1 | PLANT_TROUBLE | 3199.8333
2024 | summer | MCFLND_5_MSBBX2 | NEW_GENERATOR_TEST_ENERGY | 24750
2024 | summer | MCFLND_5_MSBBX2 | PLANT_TROUBLE | 1452.5
2024 | summer | MCFLND_5_MSBBX2 | RTU_RIG | 0
2024 | summer | MCFLND_5_MSBSX2 | NEW_GENERATOR_TEST_ENERGY | 115340
2024 | summer | MCFLND_5_MSBSX2 | PLANT_TROUBLE | 1405
2024 | summer | MCSWAN_6_UNITS | PLANT_TROUBLE | 4.05
2024 | summer | MCSWAN_6_UNITS | TRANSMISSION_INDUCED | 135
2024 | summer | MDFKRL_2_PROJCT | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | summer | MDFKRL_2_PROJCT | AMBIENT_DUE_TO_TEMP | 64.6667
2024 | summer | MDFKRL_2_PROJCT | PLANT_MAINTENANCE | 416.5
2024 | summer | MDFKRL_2_PROJCT | PLANT_TROUBLE | 0
2024 | summer | MDFKRL_2_PROJCT | TRANSMISSION_INDUCED | 1050
2024 | summer | MELRSE_6_MELBT1 | PLANT_TROUBLE | 1550
2024 | summer | MELRSE_6_MELBT2 | PLANT_TROUBLE | 1490
2024 | summer | MENBIO_6_RENEW1 | METERING_TELEMETRY | 125
2024 | summer | MENBIO_6_RENEW1 | TRANSMISSION_INDUCED | 177.5
2024 | summer | METEC_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 14557.05
2024 | summer | METEC_2_PL1X3 | PLANT_MAINTENANCE | 1460.25
2024 | summer | METEC_2_PL1X3 | PLANT_TROUBLE | 18908.9967
2024 | summer | METEC_2_PL1X3 | UNIT_TESTING | 0
2024 | summer | MIDWD_2_WIND2 | PLANT_MAINTENANCE | 0
2024 | summer | MIDWD_2_WIND2 | PLANT_TROUBLE | 125.95
2024 | summer | MIDWD_7_CORAMB | PLANT_MAINTENANCE | 12.75
2024 | summer | MIDWD_7_CORAMB | PLANT_TROUBLE | 640.325
2024 | summer | MIDWY3_2_MDSSR1 | PLANT_MAINTENANCE | 147
2024 | summer | MIDWY3_2_MDSSR1 | PLANT_TROUBLE | 119.8333
2024 | summer | MIDWYS_2_MIDSL1 | PLANT_MAINTENANCE | 0
2024 | summer | MIRLOM_2_CORONA | PLANT_TROUBLE | 23.18
2024 | summer | MIRLOM_2_LNDFL | PLANT_TROUBLE | 0
2024 | summer | MIRLOM_2_MLBBTA | METERING_TELEMETRY | 20
2024 | summer | MIRLOM_2_MLBBTA | PLANT_MAINTENANCE | 0
2024 | summer | MIRLOM_2_MLBBTA | TRANSMISSION_INDUCED | 340
2024 | summer | MIRLOM_2_MLBBTB | PLANT_MAINTENANCE | 49.6667
2024 | summer | MIRLOM_2_TEMESC | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | summer | MIRLOM_2_TEMESC | PLANT_TROUBLE | 43.795
2024 | summer | MIRLOM_2_TEMESC | TRANSMISSION_INDUCED | 10.0225
2024 | summer | MIRLOM_6_PEAKER | AMBIENT_DUE_TO_TEMP | 2634.69
2024 | summer | MIRLOM_6_PEAKER | ENVIRONMENTAL_RESTRICTIONS | 147.455
2024 | summer | MIRLOM_6_PEAKER | PLANT_MAINTENANCE | 0
2024 | summer | MIRLOM_6_PEAKER | PLANT_TROUBLE | 1650.5368
2024 | summer | MIRLOM_6_PEAKER | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2024 | summer | MIRLOM_7_MWDLKM | ENVIRONMENTAL_RESTRICTIONS | 21.5
2024 | summer | MIRLOM_7_MWDLKM | PLANT_MAINTENANCE | 18.75
2024 | summer | MIRLOM_7_MWDLKM | PLANT_TROUBLE | 125
2024 | summer | MKTRCK_1_UNIT 1 | AMBIENT_DUE_TO_TEMP | 3436.7
2024 | summer | MKTRCK_1_UNIT 1 | PLANT_TROUBLE | 1888.7033
2024 | summer | MKTRCK_1_UNIT 1 | TRANSMISSION_INDUCED | 0
2024 | summer | MKTRCK_1_UNIT 1 | UNIT_TESTING | 9.6
2024 | summer | MNDALY_6_MCGRTH | AMBIENT_DUE_TO_TEMP | 5232.64
2024 | summer | MNDALY_6_MCGRTH | PLANT_TROUBLE | 0
2024 | summer | MNDOTA_1_SOLAR1 | METERING_TELEMETRY | 0
2024 | summer | MNDOTA_1_SOLAR1 | PLANT_MAINTENANCE | 447
2024 | summer | MNDOTA_1_SOLAR1 | PLANT_TROUBLE | 3123.7333
2024 | summer | MNDOTA_1_SOLAR2 | PLANT_TROUBLE | 187.3667
2024 | summer | MNDOTA_1_SOLAR2 | TRANSMISSION_INDUCED | 10
2024 | summer | MOJAVE_1_SIPHON | ENVIRONMENTAL_RESTRICTIONS | 86.16
2024 | summer | MOJAVE_1_SIPHON | PLANT_MAINTENANCE | 215.4
2024 | summer | MOJAVE_1_SIPHON | PLANT_TROUBLE | 156.1127
2024 | summer | MOJAVE_1_SIPHON | TRANSMISSION_INDUCED | 182.1327
2024 | summer | MOJAVW_2_SOLAR | PLANT_TROUBLE | 1.7333
2024 | summer | MONTPH_7_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 19.5
2024 | summer | MONTPH_7_UNITS | PLANT_TROUBLE | 4360
2024 | summer | MONTPH_7_UNITS | TRANSMISSION_INDUCED | 13
2024 | summer | MOORPK_2_ACOBT1 | METERING_TELEMETRY | 0
2024 | summer | MOORPK_2_ACOBT1 | PLANT_MAINTENANCE | 2.99
2024 | summer | MOORPK_2_ACOBT1 | PLANT_TROUBLE | 26.7317
2024 | summer | MOORPK_2_ACOBT1 | RTU_RIG | 8.71
2024 | summer | MOORPK_2_ACOBT1 | TRANSMISSION_INDUCED | 1.885
2024 | summer | MOORPK_2_ACOBT1 | UNIT_TESTING | 0
2024 | summer | MOORPK_2_CALABS | PLANT_MAINTENANCE | 3.0477
2024 | summer | MOORPK_2_CALABS | PLANT_TROUBLE | 211.5643
2024 | summer | MOSSLD_2_PSP1 | AMBIENT_DUE_TO_TEMP | 1260.0333
2024 | summer | MOSSLD_2_PSP1 | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | summer | MOSSLD_2_PSP1 | PLANT_MAINTENANCE | 668.5333
2024 | summer | MOSSLD_2_PSP1 | PLANT_TROUBLE | 3949.7667
2024 | summer | MOSSLD_2_PSP1 | TRANSMISSION_INDUCED | 1190
2024 | summer | MOSSLD_2_PSP2 | AMBIENT_DUE_TO_TEMP | 1200.6833
2024 | summer | MOSSLD_2_PSP2 | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | summer | MOSSLD_2_PSP2 | PLANT_MAINTENANCE | 0
2024 | summer | MOSSLD_2_PSP2 | PLANT_TROUBLE | 7493.5667
2024 | summer | MOSSLD_2_PSP2 | TRANSMISSION_INDUCED | 0
2024 | summer | MOSSLD_2_PSP2 | UNIT_TESTING | 0
2024 | summer | MRCHNT_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 53039.9
2024 | summer | MRCHNT_2_PL1X3 | PLANT_MAINTENANCE | 0
2024 | summer | MRCHNT_2_PL1X3 | PLANT_TROUBLE | 5615
2024 | summer | MRCHNT_2_PL1X3 | TRANSMISSION_INDUCED | 29653.8
2024 | summer | MRCHNT_2_PL1X3 | UNIT_TESTING | 0
2024 | summer | MRGT_6_MEF2 | PLANT_MAINTENANCE | 220
2024 | summer | MRGT_6_MMAREF | PLANT_TROUBLE | 0
2024 | summer | MRGT_6_TGEBT1 | PLANT_TROUBLE | 1953.0667
2024 | summer | MRLSDS_6_SOLAR1 | METERING_TELEMETRY | 22.5
2024 | summer | MRLSDS_6_SOLAR1 | PLANT_MAINTENANCE | 4.75
2024 | summer | MRLSDS_6_SOLAR1 | PLANT_TROUBLE | 189
2024 | summer | MRLSDS_6_SOLAR1 | TRANSMISSION_INDUCED | 0
2024 | summer | MSOLAR_2_MS4BT1 | PLANT_MAINTENANCE | 75
2024 | summer | MSOLAR_2_MS4BT1 | PLANT_TROUBLE | 1325
2024 | summer | MSOLAR_2_MS4BT1 | UNIT_TESTING | 0
2024 | summer | MSOLAR_2_MS4SR4 | UNIT_TESTING | 0
2024 | summer | MSOLAR_2_SOLAR1 | PLANT_MAINTENANCE | 4830
2024 | summer | MSOLAR_2_SOLAR1 | PLANT_TROUBLE | 119
2024 | summer | MSOLAR_2_SOLAR2 | PLANT_TROUBLE | 386.457
2024 | summer | MSOLAR_2_SOLAR3 | PLANT_TROUBLE | 21.52
2024 | summer | MSTANG_2_MTGBT1 | PLANT_MAINTENANCE | 2950.4167
2024 | summer | MSTANG_2_SOLAR | PLANT_MAINTENANCE | 14
2024 | summer | MSTANG_2_SOLAR | PLANT_TROUBLE | 1402.2
2024 | summer | MSTANG_2_SOLAR3 | PLANT_MAINTENANCE | 20
2024 | summer | MSTANG_2_SOLAR3 | PLANT_TROUBLE | 261
2024 | summer | MSTANG_2_SOLAR4 | PLANT_MAINTENANCE | 80.27
2024 | summer | MSTANG_2_SOLAR4 | PLANT_TROUBLE | 1403.1133
2024 | summer | MTNPOS_1_UNIT | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | summer | MTNPOS_1_UNIT | METERING_TELEMETRY | 595.68
2024 | summer | MTNPOS_1_UNIT | PLANT_MAINTENANCE | 296.9067
2024 | summer | MTNPOS_1_UNIT | PLANT_TROUBLE | 7420.2547
2024 | summer | MTWIND_1_MVPWD1 | METERING_TELEMETRY | 0
2024 | summer | MTWIND_1_MVPWD1 | RTU_RIG | 233.1
2024 | summer | MTWIND_1_MVPWD1 | TRANSMISSION_INDUCED | 780.155
2024 | summer | MTWIND_1_UNIT 3 | AMBIENT_DUE_TO_TEMP | 2012.1567
2024 | summer | MTWIND_1_UNIT 3 | PLANT_TROUBLE | 26.4427
2024 | summer | MTWIND_1_UNIT 3 | TRANSITIONAL_LIMITATION | 37.74
2024 | summer | MTWIND_1_UNIT 3 | TRANSMISSION_INDUCED | 230.758
2024 | summer | MURRAY_6_UNIT | PLANT_MAINTENANCE | 556.2
2024 | summer | MURRAY_6_UNIT | PLANT_TROUBLE | 0
2024 | summer | NAROW1_2_UNIT | ENVIRONMENTAL_RESTRICTIONS | 1930.25
2024 | summer | NAROW1_2_UNIT | PLANT_TROUBLE | 232.5
2024 | summer | NAROW2_2_UNIT | ENVIRONMENTAL_RESTRICTIONS | 19236.4633
2024 | summer | NAROW2_2_UNIT | PLANT_MAINTENANCE | 3225
2024 | summer | NAROW2_2_UNIT | PLANT_TROUBLE | 0
2024 | summer | NAROW2_2_UNIT | TRANSMISSION_INDUCED | 18.6
2024 | summer | NAVYII_2_UNITS | PLANT_TROUBLE | 450
2024 | summer | NCPA_7_GP1UN2 | PLANT_MAINTENANCE | 1000
2024 | summer | NCPA_7_GP1UN2 | PLANT_TROUBLE | 20500
2024 | summer | NEENCH_6_SOLAR | PLANT_MAINTENANCE | 1.1
2024 | summer | NEENCH_6_SOLAR | PLANT_TROUBLE | 8172
2024 | summer | NOAKS_2_PESBT1 | NEW_GENERATOR_TEST_ENERGY | 54400
2024 | summer | NORCNV_1_NCVBT1 | PLANT_TROUBLE | 396.3248
2024 | summer | NORCNV_1_NCVBT1 | TRANSMISSION_INDUCED | 0
2024 | summer | NORORC_2_NOSBX2 | NEW_GENERATOR_TEST_ENERGY | 25310
2024 | summer | NORORC_2_NOSBX2 | PLANT_MAINTENANCE | 800
2024 | summer | NORORC_2_NOSBX2 | PLANT_TROUBLE | 5590.95
2024 | summer | NOVATO_6_LNDFL | PLANT_MAINTENANCE | 507.9
2024 | summer | NOVATO_6_LNDFL | PLANT_TROUBLE | 963
2024 | summer | NOVATO_6_LNDFL | TRANSMISSION_INDUCED | 27.3
2024 | summer | NWCSTL_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 7080
2024 | summer | NWCSTL_7_UNIT 1 | PLANT_TROUBLE | 0
2024 | summer | NZWIND_2_WDSTR5 | PLANT_TROUBLE | 9.9908
2024 | summer | NZWIND_2_WDSTR5 | TRANSMISSION_INDUCED | 31.55
2024 | summer | NZWIND_6_CALWND | PLANT_TROUBLE | 231.1067
2024 | summer | NZWIND_6_CALWND | TRANSMISSION_INDUCED | 0
2024 | summer | NZWIND_6_WDSTR | PLANT_MAINTENANCE | 16.75
2024 | summer | NZWIND_6_WDSTR | PLANT_TROUBLE | 48.4
2024 | summer | NZWIND_6_WDSTR | TRANSMISSION_INDUCED | 0
2024 | summer | NZWIND_6_WDSTR2 | PLANT_MAINTENANCE | 20.35
2024 | summer | NZWIND_6_WDSTR2 | PLANT_TROUBLE | 85.8
2024 | summer | NZWIND_6_WDSTR2 | TRANSMISSION_INDUCED | 0
2024 | summer | NZWIND_6_WDSTR3 | PLANT_MAINTENANCE | 19.3
2024 | summer | NZWIND_6_WDSTR3 | PLANT_TROUBLE | 126.6263
2024 | summer | NZWIND_6_WDSTR4 | PLANT_TROUBLE | 129.8218
2024 | summer | NZWIND_6_WDSTR4 | TRANSMISSION_INDUCED | 33.85
2024 | summer | OAK C_7_UNIT 1 | PLANT_MAINTENANCE | 163.175
2024 | summer | OAK C_7_UNIT 1 | PLANT_TROUBLE | 5246.775
2024 | summer | OAK C_7_UNIT 3 | PLANT_MAINTENANCE | 237.6
2024 | summer | OAK C_7_UNIT 3 | PLANT_TROUBLE | 2689.1333
2024 | summer | OAK C_7_UNIT 3 | TRANSMISSION_INDUCED | 111.6
2024 | summer | OAK C_7_UNIT 3 | UNIT_TESTING | 0
2024 | summer | OAKWD_6_QF | ENVIRONMENTAL_RESTRICTIONS | 55.74
2024 | summer | OAKWD_6_QF | PLANT_TROUBLE | 39.25
2024 | summer | OAKWD_6_QF | TRANSMISSION_INDUCED | 336.458
2024 | summer | OAKWD_6_ZEPHWD | ENVIRONMENTAL_RESTRICTIONS | 7
2024 | summer | OAKWD_6_ZEPHWD | TRANSMISSION_INDUCED | 47.7167
2024 | summer | OASIS_6_AR8SR3 | PLANT_TROUBLE | 258
2024 | summer | OASIS_6_AR8SR3 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2024 | summer | OASIS_6_CREST | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 35
2024 | summer | OASIS_6_GBDSR4 | PLANT_TROUBLE | 1797
2024 | summer | OASIS_6_GBDSR4 | TRANSMISSION_INDUCED | 10.3
2024 | summer | OASIS_6_LPPSR1 | PLANT_TROUBLE | 90
2024 | summer | OASIS_6_MA4SR1 | PLANT_TROUBLE | 215
2024 | summer | OASIS_6_SOLAR2 | PLANT_TROUBLE | 1202.8
2024 | summer | OASIS_6_VINSR1 | PLANT_MAINTENANCE | 7.5
2024 | summer | OBERON_5_O1BBX2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | summer | OBERON_5_O1BBX2 | METERING_TELEMETRY | 0
2024 | summer | OBERON_5_O1BBX2 | PLANT_MAINTENANCE | 160
2024 | summer | OBERON_5_O1BBX2 | PLANT_TROUBLE | 1929.1667
2024 | summer | OBERON_5_O1SSR3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 320
2024 | summer | OBERON_5_O1SSR3 | METERING_TELEMETRY | 0
2024 | summer | OBERON_5_O1SSR3 | PLANT_MAINTENANCE | 102.9
2024 | summer | OBERON_5_O1SSR3 | PLANT_TROUBLE | 6
2024 | summer | OBERON_5_O1SSR3 | UNIT_TESTING | 0
2024 | summer | OBERON_5_O1SSX2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 520
2024 | summer | OBERON_5_O1SSX2 | METERING_TELEMETRY | 0
2024 | summer | OBERON_5_O1SSX2 | PLANT_MAINTENANCE | 0
2024 | summer | OBERON_5_O1SSX2 | PLANT_TROUBLE | 100
2024 | summer | OBERON_5_O2BBX2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | summer | OBERON_5_O2BBX2 | METERING_TELEMETRY | 616.6667
2024 | summer | OBERON_5_O2BBX2 | PLANT_MAINTENANCE | 0
2024 | summer | OBERON_5_O2BBX2 | PLANT_TROUBLE | 9150.5333
2024 | summer | OBERON_5_O2SSR4 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 420
2024 | summer | OBERON_5_O2SSR4 | METERING_TELEMETRY | 77.0833
2024 | summer | OBERON_5_O2SSR4 | PLANT_MAINTENANCE | 0
2024 | summer | OBERON_5_O2SSR5 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 420
2024 | summer | OBERON_5_O2SSR5 | METERING_TELEMETRY | 77.0833
2024 | summer | OBERON_5_O2SSR5 | PLANT_MAINTENANCE | 0
2024 | summer | OBERON_5_O2SSR5 | PLANT_TROUBLE | 0.46667
2024 | summer | OCOTLO_6_OCWSB1 | METERING_TELEMETRY | 261.2333
2024 | summer | OCOTLO_6_OCWSB1 | PLANT_MAINTENANCE | 0
2024 | summer | OCOTLO_6_OCWSB1 | PLANT_TROUBLE | 468.8067
2024 | summer | OCOTLO_6_OCWSB1 | TRANSMISSION_INDUCED | 2129.25
2024 | summer | OCOTLO_6_OCWSB1 | UNIT_TESTING | 0
2024 | summer | OCTILO_5_WIND | PLANT_TROUBLE | 20830.2333
2024 | summer | OGROVE_6_PL1X2 | PLANT_MAINTENANCE | 98
2024 | summer | OGROVE_6_PL1X2 | PLANT_TROUBLE | 130.15
2024 | summer | OILFLD_7_QFUNTS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 457.2167
2024 | summer | OILFLD_7_QFUNTS | PLANT_MAINTENANCE | 236.25
2024 | summer | OILFLD_7_QFUNTS | PLANT_TROUBLE | 0.9
2024 | summer | OILFLD_7_QFUNTS | TRANSMISSION_INDUCED | 0
2024 | summer | OLDRIV_6_CESDBM | PLANT_MAINTENANCE | 1
2024 | summer | OLDRIV_6_CESDBM | PLANT_TROUBLE | 33
2024 | summer | OLDRIV_6_LKVBM1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 37
2024 | summer | OLDRIV_6_LKVBM1 | PLANT_MAINTENANCE | 1.75
2024 | summer | OLDRIV_6_LKVBM1 | PLANT_TROUBLE | 26.05
2024 | summer | OLDRV1_6_SOLAR | TRANSMISSION_INDUCED | 2980
2024 | summer | OLINDA_2_LNDFL2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 2298
2024 | summer | OLINDA_2_LNDFL2 | PLANT_MAINTENANCE | 158.9
2024 | summer | OLINDA_2_LNDFL2 | PLANT_TROUBLE | 411
2024 | summer | OLIVEP_1_SOLAR | PLANT_MAINTENANCE | 20
2024 | summer | OLIVEP_1_SOLAR | PLANT_TROUBLE | 13.3333
2024 | summer | OLIVEP_1_SOLAR | TRANSMISSION_INDUCED | 230.6667
2024 | summer | OLIVEP_1_SOLAR2 | PLANT_MAINTENANCE | 9.875
2024 | summer | OLIVEP_1_SOLAR2 | TRANSMISSION_INDUCED | 228.1125
2024 | summer | OLSEN_2_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 2318.25
2024 | summer | OLSEN_2_UNIT | TRANSMISSION_INDUCED | 0
2024 | summer | OMAR_2_UNIT 1 | PLANT_MAINTENANCE | 0
2024 | summer | OMAR_2_UNIT 1 | PLANT_TROUBLE | 749
2024 | summer | OMAR_2_UNIT 2 | PLANT_TROUBLE | 986.25
2024 | summer | OMAR_2_UNIT 3 | PLANT_MAINTENANCE | 0
2024 | summer | OMAR_2_UNIT 3 | PLANT_TROUBLE | 1416.25
2024 | summer | OMAR_2_UNIT 4 | PLANT_MAINTENANCE | 3000
2024 | summer | OMAR_2_UNIT 4 | PLANT_TROUBLE | 4365
2024 | summer | OMAR_2_UNIT 4 | UNIT_TESTING | 6.2
2024 | summer | ORLND_6_HIGHLI | PLANT_TROUBLE | 382.5
2024 | summer | ORMOND_7_UNIT 1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 14650.8
2024 | summer | ORMOND_7_UNIT 1 | ENVIRONMENTAL_RESTRICTIONS | 371899.68
2024 | summer | ORMOND_7_UNIT 1 | PLANT_TROUBLE | 10933.7325
2024 | summer | ORMOND_7_UNIT 2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 15412.5
2024 | summer | ORMOND_7_UNIT 2 | ENVIRONMENTAL_RESTRICTIONS | 532245.7372
2024 | summer | ORMOND_7_UNIT 2 | PLANT_TROUBLE | 4753.3882
2024 | summer | OROLOM_1_SOLAR1 | METERING_TELEMETRY | 35
2024 | summer | OROLOM_1_SOLAR2 | METERING_TELEMETRY | 35
2024 | summer | OROVIL_6_UNIT | PLANT_MAINTENANCE | 1162.5
2024 | summer | OROVIL_6_UNIT | PLANT_TROUBLE | 0
2024 | summer | OROVIL_6_UNIT | TRANSMISSION_INDUCED | 75
2024 | summer | OTAY_6_ECVBT1 | NEW_GENERATOR_TEST_ENERGY | 89
2024 | summer | OTAY_6_ECVBT1 | PLANT_TROUBLE | 150
2024 | summer | OTAY_6_ECVBT1 | RTU_RIG | 0
2024 | summer | OTAY_6_ECVBT2 | NEW_GENERATOR_TEST_ENERGY | 68
2024 | summer | OTAY_6_ECVBT2 | PLANT_TROUBLE | 150
2024 | summer | OTAY_6_ECVBT2 | RTU_RIG | 0
2024 | summer | OTAY_6_PL1X2 | AMBIENT_DUE_TO_TEMP | 47.55
2024 | summer | OTAY_6_PL1X2 | PLANT_TROUBLE | 66.3638
2024 | summer | OTMESA_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 26140.2817
2024 | summer | OTMESA_2_PL1X3 | PLANT_TROUBLE | 1958.6698
2024 | summer | OXBOW_6_DRUM | TRANSMISSION_INDUCED | 73.4
2024 | summer | OXMTN_6_LNDFIL | PLANT_MAINTENANCE | 174.195
2024 | summer | OXMTN_6_LNDFIL | PLANT_TROUBLE | 485.068
2024 | summer | OXMTN_6_LNDFIL | TRANSMISSION_INDUCED | 159.123
2024 | summer | PACLUM_6_UNIT | PLANT_TROUBLE | 1756.9833
2024 | summer | PADUA_2_ONTARO | AMBIENT_NOT_DUE_TO_TEMP | 280.875
2024 | summer | PADUA_2_ONTARO | PLANT_TROUBLE | 396.1
2024 | summer | PADUA_2_ONTARO | TRANSMISSION_INDUCED | 235.2
2024 | summer | PADUA_7_SDIMAS | PLANT_MAINTENANCE | 10.5
2024 | summer | PADUA_7_SDIMAS | PLANT_TROUBLE | 619.5
2024 | summer | PAIGES_6_SOLAR | AMBIENT_NOT_DUE_TO_TEMP | 9.6667
2024 | summer | PAIGES_6_SOLAR | METERING_TELEMETRY | 300.6
2024 | summer | PAIGES_6_SOLAR | PLANT_MAINTENANCE | 438.75
2024 | summer | PAIGES_6_SOLAR | PLANT_TROUBLE | 164.1667
2024 | summer | PALA_6_PGCBT1 | METERING_TELEMETRY | 82
2024 | summer | PALA_6_PGCBT1 | PLANT_MAINTENANCE | 0
2024 | summer | PALA_6_PGCBT1 | PLANT_TROUBLE | 1423.3
2024 | summer | PALOMR_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 680.7127
2024 | summer | PALOMR_2_PL1X3 | AMBIENT_NOT_DUE_TO_TEMP | 38.745
2024 | summer | PALOMR_2_PL1X3 | PLANT_TROUBLE | 9871.6425
2024 | summer | PALOMR_2_PL1X3 | TRANSMISSION_INDUCED | 0
2024 | summer | PALSEL_6_PLSBT1 | NEW_GENERATOR_TEST_ENERGY | 75
2024 | summer | PALSEL_6_PLSBT1 | PLANT_TROUBLE | 297.5167
2024 | summer | PALSEL_6_PLSSR1 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | summer | PALSEL_6_PLSSR1 | PLANT_TROUBLE | 334
2024 | summer | PALSEL_6_PLSSR1 | TRANSMISSION_INDUCED | 36
2024 | summer | PANERO_2_MWPWD1 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | summer | PANERO_2_MWPWD1 | PLANT_MAINTENANCE | 207.92
2024 | summer | PANERO_2_MWPWD1 | PLANT_TROUBLE | 48.25
2024 | summer | PANERO_2_MWPWD1 | UNIT_TESTING | 1.88
2024 | summer | PARDEB_6_UNITS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 50.5
2024 | summer | PARDEB_6_UNITS | PLANT_MAINTENANCE | 550
2024 | summer | PARDEB_6_UNITS | PLANT_TROUBLE | 20.13
2024 | summer | PARDEB_6_UNITS | TRANSMISSION_INDUCED | 180.6667
2024 | summer | PARDSE_6_PESBT1 | PLANT_MAINTENANCE | 1.5
2024 | summer | PARDSE_6_PESBT1 | PLANT_TROUBLE | 554.85
2024 | summer | PBLOSM_2_SOLAR | PLANT_MAINTENANCE | 0
2024 | summer | PBLOSM_2_SOLAR | PLANT_TROUBLE | 361
2024 | summer | PBLOSM_2_SOLAR | TRANSMISSION_INDUCED | 283.8917
2024 | summer | PEABDY_2_LNDFIL | PLANT_MAINTENANCE | 20.56
2024 | summer | PEABDY_2_LNDFIL | PLANT_TROUBLE | 11.5733
2024 | summer | PEABDY_2_LNDFIL | TRANSMISSION_INDUCED | 4.8
2024 | summer | PEABDY_2_LNDFL1 | AMBIENT_DUE_TO_TEMP | 231.0133
2024 | summer | PEABDY_2_LNDFL1 | AMBIENT_NOT_DUE_TO_TEMP | 75.1117
2024 | summer | PEABDY_2_LNDFL1 | PLANT_MAINTENANCE | 60.385
2024 | summer | PEABDY_2_LNDFL1 | PLANT_TROUBLE | 659.5417
2024 | summer | PEABDY_2_LNDFL1 | TRANSMISSION_INDUCED | 40
2024 | summer | PEARBL_2_NSPIN | PLANT_TROUBLE | 590
2024 | summer | PEARBL_2_NSPIN | TRANSMISSION_INDUCED | 708
2024 | summer | PEASE_1_TBEBT1 | PLANT_MAINTENANCE | 15
2024 | summer | PEASE_1_TBEBT1 | PLANT_TROUBLE | 269.3
2024 | summer | PEASE_1_TBEBT1 | UNIT_TESTING | 0
2024 | summer | PEORIA_1_SOLAR | PLANT_TROUBLE | 467
2024 | summer | PEORIA_1_SOLAR | TRANSMISSION_INDUCED | 1.1417
2024 | summer | PGCC_1_RDRR01 | PLANT_MAINTENANCE | 0
2024 | summer | PGCC_1_RDRR01 | SHORT_TERM_USE_LIMIT_REACHED | 9.8
2024 | summer | PGEB_2_RDRR01 | PLANT_MAINTENANCE | 0
2024 | summer | PGEB_2_RDRR01 | SHORT_TERM_USE_LIMIT_REACHED | 111
2024 | summer | PGEB_2_RDRR02 | PLANT_MAINTENANCE | 0
2024 | summer | PGEB_2_RDRR02 | SHORT_TERM_USE_LIMIT_REACHED | 85.9
2024 | summer | PGF1_2_RDRR01 | PLANT_MAINTENANCE | 0
2024 | summer | PGF1_2_RDRR01 | SHORT_TERM_USE_LIMIT_REACHED | 129.9
2024 | summer | PGFG_1_RDRR01 | PLANT_MAINTENANCE | 0
2024 | summer | PGFG_1_RDRR01 | SHORT_TERM_USE_LIMIT_REACHED | 8.1
2024 | summer | PGKN_2_RDRR02 | PLANT_MAINTENANCE | 0
2024 | summer | PGKN_2_RDRR02 | SHORT_TERM_USE_LIMIT_REACHED | 272.1
2024 | summer | PGNC_1_RDRR02 | PLANT_MAINTENANCE | 0
2024 | summer | PGNC_1_RDRR02 | SHORT_TERM_USE_LIMIT_REACHED | 16.5
2024 | summer | PGNP_2_PDRP04 | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | summer | PGNP_2_RDRR02 | PLANT_MAINTENANCE | 0
2024 | summer | PGNP_2_RDRR02 | SHORT_TERM_USE_LIMIT_REACHED | 152.95
2024 | summer | PGNP_2_RDRR03 | PLANT_MAINTENANCE | 0
2024 | summer | PGSB_1_RDRR02 | PLANT_MAINTENANCE | 0
2024 | summer | PGSB_1_RDRR02 | SHORT_TERM_USE_LIMIT_REACHED | 62
2024 | summer | PGSI_1_PDRP04 | MONTHLY_USE_LIMIT_REACHED | 6.3
2024 | summer | PGSI_1_RDRR02 | PLANT_MAINTENANCE | 0
2024 | summer | PGSI_1_RDRR02 | SHORT_TERM_USE_LIMIT_REACHED | 67.5
2024 | summer | PGST_2_RDRR01 | PLANT_MAINTENANCE | 0
2024 | summer | PGST_2_RDRR01 | SHORT_TERM_USE_LIMIT_REACHED | 32.1
2024 | summer | PGZP_2_RDRR04 | PLANT_MAINTENANCE | 0
2024 | summer | PGZP_2_RDRR04 | SHORT_TERM_USE_LIMIT_REACHED | 167.7
2024 | summer | PHOENX_1_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 25.5333
2024 | summer | PHOENX_1_UNIT | PLANT_MAINTENANCE | 0
2024 | summer | PHOENX_1_UNIT | PLANT_TROUBLE | 57.7333
2024 | summer | PHOENX_1_UNIT | TRANSMISSION_INDUCED | 12.8667
2024 | summer | PINFLT_7_UNITS | ENVIRONMENTAL_RESTRICTIONS | 27091.4
2024 | summer | PINFLT_7_UNITS | METERING_TELEMETRY | 26997.36
2024 | summer | PINFLT_7_UNITS | PLANT_TROUBLE | 297.765
2024 | summer | PINFLT_7_UNITS | TRANSMISSION_INDUCED | 5955.3
2024 | summer | PIOPIC_2_CTG1 | AMBIENT_DUE_TO_TEMP | 4337.15
2024 | summer | PIOPIC_2_CTG1 | PLANT_TROUBLE | 94.9063
2024 | summer | PIOPIC_2_CTG2 | AMBIENT_DUE_TO_TEMP | 3690.2
2024 | summer | PIOPIC_2_CTG2 | PLANT_TROUBLE | 642.8192
2024 | summer | PIOPIC_2_CTG3 | AMBIENT_DUE_TO_TEMP | 4914.98
2024 | summer | PIOPIC_2_CTG3 | PLANT_TROUBLE | 751.0615
2024 | summer | PIT1_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 43.9
2024 | summer | PIT1_7_UNIT 1 | PLANT_TROUBLE | 50.7
2024 | summer | PIT1_7_UNIT 1 | UNIT_TESTING | 0
2024 | summer | PIT1_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 7
2024 | summer | PIT1_7_UNIT 2 | PLANT_TROUBLE | 0
2024 | summer | PIT3_7_PL1X3 | AMBIENT_DUE_TO_TEMP | 11.9467
2024 | summer | PIT3_7_PL1X3 | AMBIENT_NOT_DUE_TO_TEMP | 128.7
2024 | summer | PIT3_7_PL1X3 | PLANT_TROUBLE | 32.33
2024 | summer | PIT3_7_PL1X3 | TRANSMISSION_INDUCED | 0
2024 | summer | PIT3_7_PL1X3 | UNIT_TESTING | 0
2024 | summer | PIT4_7_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 235.95
2024 | summer | PIT4_7_PL1X2 | PLANT_TROUBLE | 660
2024 | summer | PIT4_7_PL1X2 | TRANSMISSION_INDUCED | 114
2024 | summer | PIT5_7_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 692.6833
2024 | summer | PIT5_7_PL3X4 | AMBIENT_NOT_DUE_TO_TEMP | 577.8667
2024 | summer | PIT5_7_PL3X4 | PLANT_TROUBLE | 210
2024 | summer | PIT6_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 1204.7595
2024 | summer | PIT6_7_UNIT 1 | METERING_TELEMETRY | 16.704
2024 | summer | PIT6_7_UNIT 1 | PLANT_TROUBLE | 9.1
2024 | summer | PIT6_7_UNIT 1 | TRANSMISSION_INDUCED | 581.6177
2024 | summer | PIT6_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 1554.988
2024 | summer | PIT6_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 290.4162
2024 | summer | PIT6_7_UNIT 2 | PLANT_TROUBLE | 101.4453
2024 | summer | PIT6_7_UNIT 2 | TRANSMISSION_INDUCED | 438.2993
2024 | summer | PIT7_7_UNIT 1 | AMBIENT_DUE_TO_TEMP | 2.3542
2024 | summer | PIT7_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 1452.0578
2024 | summer | PIT7_7_UNIT 1 | PLANT_TROUBLE | 32.3647
2024 | summer | PIT7_7_UNIT 1 | RTU_RIG | 0
2024 | summer | PIT7_7_UNIT 1 | TRANSMISSION_INDUCED | 703.9627
2024 | summer | PIT7_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 755.781
2024 | summer | PIT7_7_UNIT 2 | PLANT_TROUBLE | 0
2024 | summer | PIT7_7_UNIT 2 | RTU_RIG | 0
2024 | summer | PIT7_7_UNIT 2 | TRANSMISSION_INDUCED | 751.1562
2024 | summer | PLACVL_1_CHILIB | PLANT_MAINTENANCE | 0
2024 | summer | PLAINV_6_BSOLAR | PLANT_TROUBLE | 5
2024 | summer | PLAINV_6_BSOLAR | TRANSMISSION_INDUCED | 10
2024 | summer | PLAINV_6_DSOLAR | TRANSMISSION_INDUCED | 5
2024 | summer | PLAINV_6_NLRSR1 | PLANT_TROUBLE | 67.1333
2024 | summer | PLAINV_6_NLRSR1 | TRANSMISSION_INDUCED | 10
2024 | summer | PLAINV_6_SOLAR3 | METERING_TELEMETRY | 32.4417
2024 | summer | PLAINV_6_SOLAR3 | PLANT_TROUBLE | 992.5583
2024 | summer | PLAINV_6_SOLAR3 | TRANSMISSION_INDUCED | 10
2024 | summer | PLAINV_6_SOLARC | PLANT_TROUBLE | 8
2024 | summer | PLAINV_6_SOLARC | TRANSMISSION_INDUCED | 10
2024 | summer | PLMSSR_6_HISIER | PLANT_MAINTENANCE | 1.8438
2024 | summer | PLMSSR_6_HISIER | PLANT_TROUBLE | 369.3753
2024 | summer | PLMSSR_6_HISIER | TRANSMISSION_INDUCED | 167.9
2024 | summer | PLSNTG_7_LNCLND | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | summer | PLSNTG_7_LNCLND | PLANT_MAINTENANCE | 24.9
2024 | summer | PLSNTG_7_LNCLND | PLANT_TROUBLE | 85.4
2024 | summer | PMDLET_6_SOLAR1 | PLANT_MAINTENANCE | 23.5
2024 | summer | PMDLET_6_SOLAR1 | PLANT_TROUBLE | 65
2024 | summer | PMPJCK_1_SOLAR1 | TRANSMISSION_INDUCED | 0
2024 | summer | PMPJCK_1_SOLAR2 | PLANT_MAINTENANCE | 69.6667
2024 | summer | PMPJCK_1_SOLAR2 | PLANT_TROUBLE | 10
2024 | summer | PNCHEG_2_PL1X4 | AMBIENT_DUE_TO_TEMP | 22385.29
2024 | summer | PNCHEG_2_PL1X4 | AMBIENT_NOT_DUE_TO_TEMP | 129.1667
2024 | summer | PNCHEG_2_PL1X4 | PLANT_MAINTENANCE | 3345.9167
2024 | summer | PNCHEG_2_PL1X4 | PLANT_TROUBLE | 13029.995
2024 | summer | PNCHEG_2_PL1X4 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2024 | summer | PNCHEG_2_PL1X4 | TRANSMISSION_INDUCED | 0
2024 | summer | PNCHPP_1_PL1X2 | AMBIENT_DUE_TO_TEMP | 19.775
2024 | summer | PNCHPP_1_PL1X2 | PLANT_MAINTENANCE | 951.1275
2024 | summer | PNCHPP_1_PL1X2 | PLANT_TROUBLE | 982.1052
2024 | summer | PNCHVS_2_SOLAR | PLANT_MAINTENANCE | 219.2
2024 | summer | PNCHVS_2_SOLAR | PLANT_TROUBLE | 959.12
2024 | summer | PNOCHE_1_PL1X2 | AMBIENT_DUE_TO_TEMP | 1744.9912
2024 | summer | PNOCHE_1_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 37.95
2024 | summer | PNOCHE_1_PL1X2 | PLANT_TROUBLE | 294.861
2024 | summer | PNOCHE_1_PL1X2 | TRANSMISSION_INDUCED | 159.0812
2024 | summer | PNOCHE_1_UNITA1 | PLANT_MAINTENANCE | 1046
2024 | summer | PNOCHE_1_UNITA1 | UNIT_TESTING | 36.5
2024 | summer | POEPH_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 21369.0087
2024 | summer | POEPH_7_UNIT 1 | PLANT_TROUBLE | 2438
2024 | summer | POEPH_7_UNIT 1 | TRANSMISSION_INDUCED | 0
2024 | summer | POEPH_7_UNIT 2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | summer | POEPH_7_UNIT 2 | AMBIENT_DUE_TO_TEMP | 25.6417
2024 | summer | POEPH_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 17367.1067
2024 | summer | POEPH_7_UNIT 2 | PLANT_TROUBLE | 2823.0533
2024 | summer | POEPH_7_UNIT 2 | TRANSMISSION_INDUCED | 12.7833
2024 | summer | POLRIS_2_ASEBT1 | METERING_TELEMETRY | 560
2024 | summer | POLRIS_2_ASEBT1 | PLANT_TROUBLE | 2286.75
2024 | summer | POLRIS_2_ASESR1 | METERING_TELEMETRY | 840
2024 | summer | POLRIS_2_ASESR1 | PLANT_MAINTENANCE | 112
2024 | summer | POLRIS_2_ASESR1 | PLANT_TROUBLE | 734.2
2024 | summer | POLRIS_2_ASRBT1 | METERING_TELEMETRY | 0
2024 | summer | POLRIS_2_ASRBT1 | PLANT_TROUBLE | 2404.5167
2024 | summer | POLRIS_2_ASRBT1 | RTU_RIG | 0
2024 | summer | POLRIS_2_ASRBT1 | UNIT_TESTING | 218.6667
2024 | summer | POLRIS_2_ASRSR1 | PLANT_MAINTENANCE | 50
2024 | summer | POLRIS_2_ASRSR1 | PLANT_TROUBLE | 892.5
2024 | summer | PRCTVY_1_MIGBT1 | PLANT_MAINTENANCE | 80
2024 | summer | PRCTVY_1_MIGBT1 | PLANT_TROUBLE | 406.55
2024 | summer | PRIMM_2_SOLAR1 | PLANT_TROUBLE | 130.9967
2024 | summer | PRIMM_2_SOLAR1 | TRANSMISSION_INDUCED | 0
2024 | summer | PROXSR_2_PROSR1 | METERING_TELEMETRY | 0
2024 | summer | PROXSR_2_PROSR1 | PLANT_MAINTENANCE | 0
2024 | summer | PROXSR_2_PROSR1 | PLANT_TROUBLE | 441.14
2024 | summer | PROXSR_2_PS1BT1 | METERING_TELEMETRY | 50.6667
2024 | summer | PROXSR_2_PS1BT1 | PLANT_MAINTENANCE | 0
2024 | summer | PROXSR_2_PS1BT1 | PLANT_TROUBLE | 632.4032
2024 | summer | PROXSR_2_PS1BT1 | UNIT_TESTING | 0
2024 | summer | PROXSR_2_PS1BT2 | PLANT_MAINTENANCE | 0
2024 | summer | PROXSR_2_PS1BT2 | PLANT_TROUBLE | 0
2024 | summer | PROXSR_2_PS1BT2 | UNIT_TESTING | 0
2024 | summer | PROXSR_2_PS1SR2 | PLANT_MAINTENANCE | 0
2024 | summer | PROXSR_2_PS1SR2 | PLANT_TROUBLE | 1126.0167
2024 | summer | PROXSR_2_PS2BT3 | METERING_TELEMETRY | 0
2024 | summer | PROXSR_2_PS2BT3 | PLANT_MAINTENANCE | 0
2024 | summer | PROXSR_2_PS2BT3 | PLANT_TROUBLE | 2649.511
2024 | summer | PROXSR_2_PS2BT3 | UNIT_TESTING | 0
2024 | summer | PUTHCR_1_PCNSB1 | METERING_TELEMETRY | 45
2024 | summer | PUTHCR_1_PCNSB1 | PLANT_TROUBLE | 219.35
2024 | summer | PUTHCR_1_SOLAR1 | METERING_TELEMETRY | 39.6
2024 | summer | PVERDE_5_SCEDYN | AMBIENT_DUE_TO_TEMP | 2071.8667
2024 | summer | PVERDE_5_SCEDYN | AMBIENT_NOT_DUE_TO_TEMP | 222
2024 | summer | PWEST_1_UNIT | PLANT_TROUBLE | 1585.5
2024 | summer | RAMON_2_SCEDYN | AMBIENT_NOT_DUE_TO_TEMP | 55459.2333
2024 | summer | RAMON_2_SCEDYN | PLANT_TROUBLE | 850
2024 | summer | RAMON_2_SCEDYN | TRANSMISSION_INDUCED | 0
2024 | summer | RATSKE_2_NROSR1 | PLANT_MAINTENANCE | 0
2024 | summer | RATSKE_2_NROSR1 | PLANT_TROUBLE | 630
2024 | summer | RATSKE_2_RBSSB1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | summer | RATSKE_2_RBSSB1 | PLANT_MAINTENANCE | 100
2024 | summer | RATSKE_2_RBSSB1 | PLANT_TROUBLE | 120
2024 | summer | RATSKE_2_RBSSB1 | UNIT_TESTING | 142.5
2024 | summer | RATSKE_2_RBSSB2 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | summer | RATSKE_2_RBSSB2 | PLANT_MAINTENANCE | 60
2024 | summer | RATSKE_2_RBSSB2 | PLANT_TROUBLE | 0
2024 | summer | RATSKE_2_WAVBT1 | NEW_GENERATOR_TEST_ENERGY | 19530
2024 | summer | RCKCRK_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 17187.3082
2024 | summer | RCKCRK_7_UNIT 1 | PLANT_TROUBLE | 0
2024 | summer | RCKCRK_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 15545.1962
2024 | summer | RCKCRK_7_UNIT 2 | PLANT_TROUBLE | 0.622
2024 | summer | RCKCRK_7_UNIT 2 | TRANSMISSION_INDUCED | 32.7367
2024 | summer | RDWAY_1_SCKSR1 | METERING_TELEMETRY | 0
2024 | summer | RDWAY_1_SCKSR1 | PLANT_MAINTENANCE | 4.75
2024 | summer | RDWAY_1_SCKSR1 | PLANT_TROUBLE | 103.2
2024 | summer | RECTOR_2_KAWEAH | AMBIENT_NOT_DUE_TO_TEMP | 3937.15
2024 | summer | RECTOR_2_KAWEAH | TRANSMISSION_INDUCED | 0.75
2024 | summer | RECTOR_2_KAWH 1 | AMBIENT_NOT_DUE_TO_TEMP | 1721.25
2024 | summer | RECTOR_2_QF | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 708.1725
2024 | summer | RECTOR_2_QF | PLANT_MAINTENANCE | 12556.25
2024 | summer | RECTOR_2_QF | PLANT_TROUBLE | 175.4527
2024 | summer | RECTOR_2_TFDBM1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 4
2024 | summer | RECTOR_2_TFDBM1 | PLANT_MAINTENANCE | 12
2024 | summer | RECTOR_2_TFDBM1 | PLANT_TROUBLE | 23.2
2024 | summer | RECTOR_2_VISSR1 | PLANT_TROUBLE | 0
2024 | summer | REDBLF_6_UNIT | PLANT_TROUBLE | 30
2024 | summer | RENWD_1_QF | PLANT_MAINTENANCE | 552.4917
2024 | summer | RENWD_1_QF | TRANSMISSION_INDUCED | 229.8333
2024 | summer | RENWD_1_QF | UNIT_TESTING | 0
2024 | summer | REXFRD_2_RSFBX2 | NEW_GENERATOR_TEST_ENERGY | 10610
2024 | summer | REXFRD_2_RSFBX2 | PLANT_MAINTENANCE | 0
2024 | summer | REXFRD_2_RSFBX2 | PLANT_TROUBLE | 0
2024 | summer | REXFRD_2_RSFBX2 | TRANSMISSION_INDUCED | 0
2024 | summer | REXFRD_2_RSFSX2 | NEW_GENERATOR_TEST_ENERGY | 83826
2024 | summer | REXFRD_2_RSFSX2 | PLANT_MAINTENANCE | 0
2024 | summer | REXFRD_2_RSFSX2 | PLANT_TROUBLE | 0
2024 | summer | REXFRD_2_RSFSX2 | TRANSMISSION_INDUCED | 0
2024 | summer | RICHMN_1_CHVSR2 | PLANT_TROUBLE | 51.9917
2024 | summer | RICHMN_1_CHVSR2 | TRANSMISSION_INDUCED | 8.3583
2024 | summer | RICHMN_7_BAYENV | PLANT_TROUBLE | 1912.5
2024 | summer | RIOBRV_6_UNIT 1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 577.5
2024 | summer | RIOBRV_6_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 114.35
2024 | summer | RIOBRV_6_UNIT 1 | PLANT_TROUBLE | 268.3333
2024 | summer | ROLLIN_6_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 6782.025
2024 | summer | ROMOLA_5_MPBBT1 | METERING_TELEMETRY | 0
2024 | summer | ROMOLA_5_MPBBT1 | PLANT_MAINTENANCE | 0
2024 | summer | ROMOLA_5_MPBBT1 | PLANT_TROUBLE | 128
2024 | summer | ROMOLA_5_MPBBT1 | UNIT_TESTING | 0
2024 | summer | ROMOLA_5_MPBBT2 | METERING_TELEMETRY | 0
2024 | summer | ROMOLA_5_MPBBT2 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | summer | ROMOLA_5_MPBBT2 | PLANT_TROUBLE | 301.2
2024 | summer | ROMOLA_5_MPBBT3 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | summer | ROMOLA_5_MPBBT3 | PLANT_MAINTENANCE | 59.6
2024 | summer | ROMOLA_5_MPBBT3 | PLANT_TROUBLE | 115.5667
2024 | summer | ROMOLA_5_MPBBT3 | TRANSMISSION_INDUCED | 0
2024 | summer | ROMOLA_5_MPBBT3 | UNIT_TESTING | 0
2024 | summer | ROMOLA_5_MPBBT4 | METERING_TELEMETRY | 0
2024 | summer | ROMOLA_5_MPBBT4 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | summer | ROMOLA_5_MPBBT4 | PLANT_TROUBLE | 1427.7333
2024 | summer | ROMOLA_5_MPBBT4 | TRANSMISSION_INDUCED | 0
2024 | summer | ROSMDW_2_WIND1 | PLANT_MAINTENANCE | 3178.5667
2024 | summer | ROSMDW_2_WIND1 | PLANT_TROUBLE | 652.2667
2024 | summer | ROSMND_6_SOLAR | PLANT_TROUBLE | 21
2024 | summer | RSMSLR_6_SOLAR1 | METERING_TELEMETRY | 0
2024 | summer | RSMSLR_6_SOLAR1 | PLANT_MAINTENANCE | 30
2024 | summer | RSMSLR_6_SOLAR1 | PLANT_TROUBLE | 200
2024 | summer | RSMSLR_6_SOLAR2 | PLANT_MAINTENANCE | 30
2024 | summer | RTEDDY_2_RWSBT1 | METERING_TELEMETRY | 0
2024 | summer | RTEDDY_2_RWSBT1 | PLANT_MAINTENANCE | 15
2024 | summer | RTEDDY_2_RWSBT1 | PLANT_TROUBLE | 481.3833
2024 | summer | RTEDDY_2_RWSBT1 | UNIT_TESTING | 0
2024 | summer | RTEDDY_2_RWSBT2 | METERING_TELEMETRY | 0
2024 | summer | RTEDDY_2_RWSBT2 | PLANT_MAINTENANCE | 158
2024 | summer | RTEDDY_2_RWSBT2 | PLANT_TROUBLE | 427.7
2024 | summer | RTEDDY_2_RWSBT3 | METERING_TELEMETRY | 0
2024 | summer | RTEDDY_2_RWSBT3 | PLANT_MAINTENANCE | 15
2024 | summer | RTEDDY_2_RWSBT3 | PLANT_TROUBLE | 284.5667
2024 | summer | RTEDDY_2_RWSBT4 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | summer | RTEDDY_2_RWSBT4 | METERING_TELEMETRY | 0
2024 | summer | RTEDDY_2_RWSBT4 | PLANT_MAINTENANCE | 15
2024 | summer | RTEDDY_2_RWSBT4 | PLANT_TROUBLE | 54.95
2024 | summer | RTEDDY_2_RWSBT5 | METERING_TELEMETRY | 0
2024 | summer | RTEDDY_2_RWSBT5 | PLANT_MAINTENANCE | 60
2024 | summer | RTEDDY_2_RWSBT5 | PLANT_TROUBLE | 18.7333
2024 | summer | RTEDDY_2_SC1SR3 | METERING_TELEMETRY | 0
2024 | summer | RTEDDY_2_SC1SR3 | PLANT_MAINTENANCE | 0
2024 | summer | RTEDDY_2_SC1SR3 | PLANT_TROUBLE | 60
2024 | summer | RTEDDY_2_SEBSR3 | METERING_TELEMETRY | 280.2167
2024 | summer | RTEDDY_2_SEBSR3 | PLANT_MAINTENANCE | 0
2024 | summer | RTEDDY_2_SEBSR3 | PLANT_TROUBLE | 1209.5667
2024 | summer | RTEDDY_2_SEBSR4 | METERING_TELEMETRY | 280.2167
2024 | summer | RTEDDY_2_SEBSR4 | PLANT_MAINTENANCE | 280
2024 | summer | RTEDDY_2_SEBSR4 | PLANT_TROUBLE | 399.4667
2024 | summer | RTEDDY_2_SOLAR2 | PLANT_MAINTENANCE | 0
2024 | summer | RTEDDY_2_SOLAR2 | PLANT_TROUBLE | 0
2024 | summer | RTEDDY_2_SPASR4 | METERING_TELEMETRY | 0
2024 | summer | RTEDDY_2_SPASR4 | PLANT_TROUBLE | 572.4333
2024 | summer | RTEDDY_2_SRXSR4 | METERING_TELEMETRY | 0
2024 | summer | RTEDDY_2_SRXSR4 | PLANT_MAINTENANCE | 68
2024 | summer | RTEDDY_2_SRXSR4 | PLANT_TROUBLE | 20.4
2024 | summer | RTREE_2_WIND2 | PLANT_MAINTENANCE | 1491.1117
2024 | summer | RUSCTY_2_UNITS | AMBIENT_DUE_TO_TEMP | 19524.5667
2024 | summer | RUSCTY_2_UNITS | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | summer | RUSCTY_2_UNITS | PLANT_TROUBLE | 20889.7457
2024 | summer | RUSCTY_2_UNITS | UNIT_TESTING | 152.518
2024 | summer | RUSSELL_2_SOLANO1 | PLANT_MAINTENANCE | 0
2024 | summer | RUSSELL_2_SOLANO1 | PLANT_TROUBLE | 1958.94
2024 | summer | RVRVEW_1_UNITA1 | AMBIENT_DUE_TO_TEMP | 1524.68
2024 | summer | RVRVEW_1_UNITA1 | PLANT_TROUBLE | 907.08
2024 | summer | RVRVEW_1_UNITA1 | UNIT_TESTING | 6.9307
2024 | summer | RVSIDE_2_RERCU3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | summer | RVSIDE_2_RERCU3 | AMBIENT_NOT_DUE_TO_TEMP | 1715
2024 | summer | RVSIDE_2_RERCU3 | ENVIRONMENTAL_RESTRICTIONS | 26.95
2024 | summer | RVSIDE_2_RERCU3 | PLANT_MAINTENANCE | 0
2024 | summer | RVSIDE_2_RERCU3 | PLANT_TROUBLE | 0
2024 | summer | RVSIDE_2_RERCU4 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | summer | RVSIDE_2_RERCU4 | AMBIENT_NOT_DUE_TO_TEMP | 1715
2024 | summer | RVSIDE_2_RERCU4 | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | summer | RVSIDE_2_RERCU4 | PLANT_MAINTENANCE | 0
2024 | summer | RVSIDE_2_RERCU4 | PLANT_TROUBLE | 0
2024 | summer | RVSIDE_6_RERCU1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | summer | RVSIDE_6_RERCU1 | AMBIENT_NOT_DUE_TO_TEMP | 1692.25
2024 | summer | RVSIDE_6_RERCU1 | PLANT_TROUBLE | 45.875
2024 | summer | RVSIDE_6_RERCU2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | summer | RVSIDE_6_RERCU2 | AMBIENT_NOT_DUE_TO_TEMP | 1697.5
2024 | summer | RVSIDE_6_RERCU2 | ENVIRONMENTAL_RESTRICTIONS | 2
2024 | summer | RVSIDE_6_RERCU2 | PLANT_TROUBLE | 46.25
2024 | summer | RVSIDE_6_SPRING | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | summer | RVSIDE_6_SPRING | AMBIENT_NOT_DUE_TO_TEMP | 1260
2024 | summer | RVSIDE_6_SPRING | PLANT_TROUBLE | 18
2024 | summer | SALIRV_2_UNIT | PLANT_MAINTENANCE | 390
2024 | summer | SALIRV_2_UNIT | PLANT_TROUBLE | 386.75
2024 | summer | SALTSP_7_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 10317.9833
2024 | summer | SALTSP_7_UNITS | PLANT_TROUBLE | 1025.6333
2024 | summer | SAMPSN_6_KELCO1 | PLANT_TROUBLE | 0
2024 | summer | SANBRN_2_EESSB2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | summer | SANBRN_2_EESSB2 | AMBIENT_DUE_TO_TEMP | 0
2024 | summer | SANBRN_2_EESSB2 | PLANT_TROUBLE | 345.8333
2024 | summer | SANBRN_2_ES1BT3 | PLANT_TROUBLE | 106.1017
2024 | summer | SANBRN_2_ES2SB3 | PLANT_TROUBLE | 87.5
2024 | summer | SANBRN_2_ESABT1 | PLANT_TROUBLE | 0
2024 | summer | SANBRN_2_ESBBT1 | PLANT_MAINTENANCE | 0
2024 | summer | SANBRN_2_ESBBT1 | PLANT_TROUBLE | 118.5
2024 | summer | SANBRN_2_SS2BT3 | AMBIENT_DUE_TO_TEMP | 0
2024 | summer | SANBRN_2_SS2BT3 | METERING_TELEMETRY | 0
2024 | summer | SANBRN_2_SS2BT3 | PLANT_TROUBLE | 5742.7833
2024 | summer | SANBRN_2_SS2BT3 | UNIT_TESTING | 0
2024 | summer | SANBRN_2_SS2BT4 | AMBIENT_DUE_TO_TEMP | 0
2024 | summer | SANBRN_2_SS2BT4 | METERING_TELEMETRY | 43.0833
2024 | summer | SANBRN_2_SS2BT4 | PLANT_TROUBLE | 47
2024 | summer | SANBRN_2_SS2BT4 | UNIT_TESTING | 70.5
2024 | summer | SANBRN_2_SS2SB4 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 7.8
2024 | summer | SANBRN_2_SS2SB4 | METERING_TELEMETRY | 0
2024 | summer | SANBRN_2_SS2SB4 | PLANT_MAINTENANCE | 0
2024 | summer | SANBRN_2_SS2SB4 | PLANT_TROUBLE | 140
2024 | summer | SANBRN_2_SS2SB4 | UNIT_TESTING | 0
2024 | summer | SANDLT_2_SUNITS | AMBIENT_NOT_DUE_TO_TEMP | 11893.4167
2024 | summer | SANDLT_2_SUNITS | PLANT_MAINTENANCE | 0
2024 | summer | SANDLT_2_SUNITS | PLANT_TROUBLE | 73.3333
2024 | summer | SANDRN_2_SS1SR1 | NEW_GENERATOR_TEST_ENERGY | 1838.25
2024 | summer | SANDRN_2_SS1SR1 | UNIT_TESTING | 8544.97
2024 | summer | SANDRN_2_SS2SR2 | PLANT_MAINTENANCE | 200
2024 | summer | SANLOB_1_LNDFIL | AMBIENT_NOT_DUE_TO_TEMP | 675.05
2024 | summer | SANLOB_1_LNDFIL | PLANT_MAINTENANCE | 1.2
2024 | summer | SANLOB_1_LNDFIL | PLANT_TROUBLE | 101.25
2024 | summer | SANTFG_7_UNITS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 13576
2024 | summer | SANTFG_7_UNITS | PLANT_TROUBLE | 191.836
2024 | summer | SANTGO_2_LNDFL1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 60.57
2024 | summer | SANTGO_2_LNDFL1 | AMBIENT_DUE_TO_TEMP | 2421.2333
2024 | summer | SANTGO_2_LNDFL1 | METERING_TELEMETRY | 67.4
2024 | summer | SANTGO_2_LNDFL1 | PLANT_TROUBLE | 802.93
2024 | summer | SANTGO_2_LNDFL1 | TRANSMISSION_INDUCED | 0
2024 | summer | SANTGO_2_MABBT1 | PLANT_TROUBLE | 1393
2024 | summer | SANWD_1_QF | PLANT_MAINTENANCE | 2524.0383
2024 | summer | SANWD_1_QF | PLANT_TROUBLE | 4434.2177
2024 | summer | SAUGUS_2_SPESBT1 | METERING_TELEMETRY | 27.5
2024 | summer | SAUGUS_2_SPESBT1 | PLANT_MAINTENANCE | 1837.5
2024 | summer | SAUGUS_2_SPESBT1 | PLANT_TROUBLE | 2070.12
2024 | summer | SAUGUS_2_SPESBT1 | RTU_RIG | 134
2024 | summer | SAUGUS_2_SPESBT1 | UNIT_TESTING | 0
2024 | summer | SAUGUS_7_CHIQCN | PLANT_TROUBLE | 6120
2024 | summer | SBERDO_2_PSP3 | AMBIENT_DUE_TO_TEMP | 4115
2024 | summer | SBERDO_2_PSP3 | AMBIENT_DUE_TO_TEMP | 11581.48
2024 | summer | SBERDO_2_PSP3 | PLANT_TROUBLE | 2583.0192
2024 | summer | SBERDO_2_PSP4 | AMBIENT_DUE_TO_TEMP | 23718.7582
2024 | summer | SBERDO_2_PSP4 | PLANT_MAINTENANCE | 7112.0858
2024 | summer | SBERDO_2_PSP4 | PLANT_TROUBLE | 13927.2127
2024 | summer | SBERDO_2_SNTANA | PLANT_TROUBLE | 5316.75
2024 | summer | SBERDO_6_MILLCK | AMBIENT_NOT_DUE_TO_TEMP | 772.05
2024 | summer | SBERDO_6_MILLCK | PLANT_TROUBLE | 1347
2024 | summer | SBERDO_6_MILLCK | TRANSMISSION_INDUCED | 24
2024 | summer | SCARLT_2_SS2BT1 | PLANT_TROUBLE | 0
2024 | summer | SCARLT_2_SS2BT1 | TRANSMISSION_INDUCED | 150
2024 | summer | SCARLT_2_SS2BT1 | UNIT_TESTING | 10350
2024 | summer | SCARLT_2_SS2SR1 | UNIT_TESTING | 13800
2024 | summer | SCARLT_2_SSABT1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 450
2024 | summer | SCARLT_2_SSABT1 | METERING_TELEMETRY | 211.6667
2024 | summer | SCARLT_2_SSABT1 | PLANT_MAINTENANCE | 208.2867
2024 | summer | SCARLT_2_SSABT1 | PLANT_TROUBLE | 1095.7018
2024 | summer | SCARLT_2_SSABT1 | TRANSMISSION_INDUCED | 10
2024 | summer | SCARLT_2_SSABT1 | UNIT_TESTING | 0
2024 | summer | SCARLT_2_SSASR1 | METERING_TELEMETRY | 838.3333
2024 | summer | SCARLT_2_SSASR1 | PLANT_MAINTENANCE | 4503.2167
2024 | summer | SCARLT_2_SSASR1 | PLANT_TROUBLE | 5832.5
2024 | summer | SCARLT_2_SSASR1 | TRANSMISSION_INDUCED | 100
2024 | summer | SCARLT_2_SSBBT1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1050
2024 | summer | SCARLT_2_SSBBT1 | METERING_TELEMETRY | 450
2024 | summer | SCARLT_2_SSBBT1 | PLANT_MAINTENANCE | 12.9533
2024 | summer | SCARLT_2_SSBBT1 | PLANT_TROUBLE | 5064.0965
2024 | summer | SCARLT_2_SSBBT1 | TRANSMISSION_INDUCED | 30
2024 | summer | SCARLT_2_SSBBT1 | UNIT_TESTING | 0
2024 | summer | SCARLT_2_SSBSR1 | METERING_TELEMETRY | 1169
2024 | summer | SCARLT_2_SSBSR1 | PLANT_MAINTENANCE | 2262.1
2024 | summer | SCARLT_2_SSBSR1 | PLANT_TROUBLE | 5806.505
2024 | summer | SCARLT_2_SSBSR1 | TRANSMISSION_INDUCED | 100
2024 | summer | SCEC_1_PDRP124 | METERING_TELEMETRY | 0
2024 | summer | SCEC_1_PDRP16 | MONTHLY_USE_LIMIT_REACHED | 1015.45
2024 | summer | SCEC_1_PDRP173 | METERING_TELEMETRY | 0
2024 | summer | SCEC_1_PDRP60 | METERING_TELEMETRY | 0
2024 | summer | SCEC_1_RDRR08 | SHORT_TERM_USE_LIMIT_REACHED | 1751.3333
2024 | summer | SCEC_1_RDRR08 | UNIT_TESTING | 296
2024 | summer | SCEC_1_RDRR38 | SHORT_TERM_USE_LIMIT_REACHED | 150.741
2024 | summer | SCEC_1_RDRR39 | SHORT_TERM_USE_LIMIT_REACHED | 129.8703
2024 | summer | SCEN_6_RDRR02 | SHORT_TERM_USE_LIMIT_REACHED | 223.75
2024 | summer | SCEN_6_RDRR02 | UNIT_TESTING | 150
2024 | summer | SCEW_2_PDRP03 | METERING_TELEMETRY | 0
2024 | summer | SCEW_2_PDRP03 | MONTHLY_USE_LIMIT_REACHED | 79.05
2024 | summer | SCEW_2_PDRP09 | METERING_TELEMETRY | 0
2024 | summer | SCEW_2_PDRP10 | METERING_TELEMETRY | 0
2024 | summer | SCEW_2_PDRP10 | OTHER_USE_LIMIT_REACHED | 5.26
2024 | summer | SCEW_2_PDRP114 | METERING_TELEMETRY | 0
2024 | summer | SCEW_2_PDRP12 | MONTHLY_USE_LIMIT_REACHED | 338.1
2024 | summer | SCEW_2_PDRP159 | METERING_TELEMETRY | 0
2024 | summer | SCEW_2_PDRP160 | METERING_TELEMETRY | 0
2024 | summer | SCEW_2_PDRP163 | METERING_TELEMETRY | 0
2024 | summer | SCEW_2_PDRP167 | METERING_TELEMETRY | 0
2024 | summer | SCEW_2_PDRP85 | METERING_TELEMETRY | 0
2024 | summer | SCEW_2_PDRP89 | METERING_TELEMETRY | 0
2024 | summer | SCEW_2_RDRR08 | SHORT_TERM_USE_LIMIT_REACHED | 638.4333
2024 | summer | SCEW_2_RDRR08 | UNIT_TESTING | 428
2024 | summer | SCHD_1_RDRR08 | SHORT_TERM_USE_LIMIT_REACHED | 358
2024 | summer | SCHD_1_RDRR08 | UNIT_TESTING | 240
2024 | summer | SCHLTE_1_PL1X3 | AMBIENT_DUE_TO_TEMP | 3618.532
2024 | summer | SCHLTE_1_PL1X3 | ENVIRONMENTAL_RESTRICTIONS | 435.2947
2024 | summer | SCHLTE_1_PL1X3 | PLANT_TROUBLE | 0
2024 | summer | SCHLTE_1_PL1X3 | UNIT_TESTING | 930.4
2024 | summer | SCHNDR_1_FIVPTS | AMBIENT_NOT_DUE_TO_TEMP | 126
2024 | summer | SCHNDR_1_FIVPTS | METERING_TELEMETRY | 0
2024 | summer | SCHNDR_1_FIVPTS | PLANT_TROUBLE | 1140
2024 | summer | SCHNDR_1_WSTSDE | AMBIENT_NOT_DUE_TO_TEMP | 39.375
2024 | summer | SCHNDR_1_WSTSDE | PLANT_TROUBLE | 2265.55
2024 | summer | SCNW_6_PDRP57 | MONTHLY_USE_LIMIT_REACHED | 181.7
2024 | summer | SCNW_6_PDRP61 | MONTHLY_USE_LIMIT_REACHED | 6.3
2024 | summer | SCNW_6_RDRR08 | SHORT_TERM_USE_LIMIT_REACHED | 56.6833
2024 | summer | SCNW_6_RDRR08 | UNIT_TESTING | 38
2024 | summer | SEGS_1_SR2SL2 | PLANT_TROUBLE | 13
2024 | summer | SEGS_1_SR2SL2 | TRANSMISSION_INDUCED | 0
2024 | summer | SENTNL_2_CTG1 | AMBIENT_DUE_TO_TEMP | 6747.1
2024 | summer | SENTNL_2_CTG1 | AMBIENT_DUE_TO_TEMP | 1956.9
2024 | summer | SENTNL_2_CTG1 | METERING_TELEMETRY | 487.8
2024 | summer | SENTNL_2_CTG1 | PLANT_MAINTENANCE | 0
2024 | summer | SENTNL_2_CTG1 | PLANT_TROUBLE | 0
2024 | summer | SENTNL_2_CTG2 | AMBIENT_DUE_TO_TEMP | 8490
2024 | summer | SENTNL_2_CTG2 | METERING_TELEMETRY | 0
2024 | summer | SENTNL_2_CTG2 | PLANT_MAINTENANCE | 0
2024 | summer | SENTNL_2_CTG2 | PLANT_TROUBLE | 0
2024 | summer | SENTNL_2_CTG2 | RIMS_OUTAGE | 1041.9
2024 | summer | SENTNL_2_CTG3 | PLANT_TROUBLE | 80852.85
2024 | summer | SENTNL_2_CTG4 | AMBIENT_DUE_TO_TEMP | 8521.35
2024 | summer | SENTNL_2_CTG4 | PLANT_MAINTENANCE | 0
2024 | summer | SENTNL_2_CTG4 | PLANT_TROUBLE | 0
2024 | summer | SENTNL_2_CTG4 | RIMS_OUTAGE | 1598.25
2024 | summer | SENTNL_2_CTG5 | AMBIENT_DUE_TO_TEMP | 8909.8
2024 | summer | SENTNL_2_CTG5 | PLANT_MAINTENANCE | 0
2024 | summer | SENTNL_2_CTG5 | PLANT_TROUBLE | 304.65
2024 | summer | SENTNL_2_CTG5 | RIMS_OUTAGE | 2016.1
2024 | summer | SENTNL_2_CTG6 | AMBIENT_DUE_TO_TEMP | 9024.1
2024 | summer | SENTNL_2_CTG6 | PLANT_MAINTENANCE | 0
2024 | summer | SENTNL_2_CTG6 | PLANT_TROUBLE | 351.8567
2024 | summer | SENTNL_2_CTG6 | RIMS_OUTAGE | 4725
2024 | summer | SENTNL_2_CTG7 | AMBIENT_DUE_TO_TEMP | 8930.8
2024 | summer | SENTNL_2_CTG7 | PLANT_MAINTENANCE | 162.56
2024 | summer | SENTNL_2_CTG7 | PLANT_TROUBLE | 3576.7833
2024 | summer | SENTNL_2_CTG7 | RIMS_OUTAGE | 6367.65
2024 | summer | SENTNL_2_CTG8 | AMBIENT_DUE_TO_TEMP | 8932.35
2024 | summer | SENTNL_2_CTG8 | PLANT_MAINTENANCE | 0
2024 | summer | SENTNL_2_CTG8 | PLANT_TROUBLE | 0
2024 | summer | SENTNL_2_CTG8 | RIMS_OUTAGE | 0
2024 | summer | SGREGY_6_SANGER | PLANT_MAINTENANCE | 241.5
2024 | summer | SGREGY_6_SANGER | PLANT_TROUBLE | 48.3
2024 | summer | SHANDN_2_SBBBM1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 78
2024 | summer | SHANDN_2_SBBBM1 | PLANT_TROUBLE | 41.6
2024 | summer | SHELRF_1_UNITS | PLANT_TROUBLE | 1775
2024 | summer | SIERRA_1_UNITS | AMBIENT_DUE_TO_TEMP | 2686.9
2024 | summer | SIERRA_1_UNITS | PLANT_TROUBLE | 224.6333
2024 | summer | SIERRA_1_UNITS | UNIT_TESTING | 112.3275
2024 | summer | SIGHEB_6_HE2SCEDYN | AMBIENT_DUE_TO_TEMP | 1740
2024 | summer | SIGHEB_6_MIRDYN | AMBIENT_DUE_TO_TEMP | 955
2024 | summer | SIGHEB_6_MIRDYN | PLANT_MAINTENANCE | 59.95
2024 | summer | SISPRG_2_DS3BT1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | summer | SISPRG_2_DS3BT1 | METERING_TELEMETRY | 0
2024 | summer | SISPRG_2_DS3BT1 | PLANT_TROUBLE | 1876.0027
2024 | summer | SISPRG_2_DS3BT1 | RTU_RIG | 0
2024 | summer | SISPRG_2_DS3BT1 | UNIT_TESTING | 275.22
2024 | summer | SISPRG_2_DS3BT2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 102.9
2024 | summer | SISPRG_2_DS3BT2 | METERING_TELEMETRY | 39.5
2024 | summer | SISPRG_2_DS3BT2 | PLANT_MAINTENANCE | 0
2024 | summer | SISPRG_2_DS3BT2 | PLANT_TROUBLE | 2623.3867
2024 | summer | SISPRG_2_DS3BT2 | UNIT_TESTING | 0
2024 | summer | SISPRG_2_DS3BT3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 4.25
2024 | summer | SISPRG_2_DS3BT3 | METERING_TELEMETRY | 22.5
2024 | summer | SISPRG_2_DS3BT3 | PLANT_MAINTENANCE | 45
2024 | summer | SISPRG_2_DS3BT3 | PLANT_TROUBLE | 633.7667
2024 | summer | SISPRG_2_DS3BT3 | RTU_RIG | 0
2024 | summer | SISPRG_2_DS3BT3 | UNIT_TESTING | 0
2024 | summer | SISPRG_2_DS3BT4 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | summer | SISPRG_2_DS3BT4 | METERING_TELEMETRY | 0
2024 | summer | SISPRG_2_DS3BT4 | PLANT_MAINTENANCE | 40
2024 | summer | SISPRG_2_DS3BT4 | PLANT_TROUBLE | 250.5833
2024 | summer | SISPRG_2_DS3BT4 | RTU_RIG | 0
2024 | summer | SISPRG_2_DS3BT4 | UNIT_TESTING | 0
2024 | summer | SISPRG_2_DS3SR1 | METERING_TELEMETRY | 0
2024 | summer | SISPRG_2_DS3SR1 | PLANT_MAINTENANCE | 283.5667
2024 | summer | SISPRG_2_DS3SR1 | PLANT_TROUBLE | 440
2024 | summer | SISPRG_2_DS3SR1 | RTU_RIG | 0
2024 | summer | SISPRG_2_DS3SR1 | UNIT_TESTING | 0
2024 | summer | SISPRG_2_DS3SR2 | METERING_TELEMETRY | 0
2024 | summer | SISPRG_2_DS3SR2 | PLANT_MAINTENANCE | 258.5
2024 | summer | SISPRG_2_DS3SR2 | PLANT_TROUBLE | 691.175
2024 | summer | SISPRG_2_DS3SR2 | UNIT_TESTING | 220
2024 | summer | SISPRG_2_DS3SR3 | METERING_TELEMETRY | 0
2024 | summer | SISPRG_2_DS3SR3 | PLANT_MAINTENANCE | 0
2024 | summer | SISPRG_2_DS3SR3 | RTU_RIG | 0
2024 | summer | SISPRG_2_DS3SR3 | UNIT_TESTING | 100
2024 | summer | SISPRG_2_DS3SR4 | METERING_TELEMETRY | 0
2024 | summer | SISPRG_2_DS3SR4 | RTU_RIG | 0
2024 | summer | SISPRG_2_DS3SR4 | UNIT_TESTING | 34
2024 | summer | SKERN_6_SOLAR1 | PLANT_MAINTENANCE | 25
2024 | summer | SKERN_6_SOLAR1 | PLANT_TROUBLE | 296.6667
2024 | summer | SKERN_6_SOLAR1 | TRANSMISSION_INDUCED | 532.6667
2024 | summer | SKERN_6_SOLAR2 | METERING_TELEMETRY | 300
2024 | summer | SKERN_6_SOLAR2 | PLANT_MAINTENANCE | 0
2024 | summer | SKERN_6_SOLAR2 | PLANT_TROUBLE | 272
2024 | summer | SLATE_2_SLASR1 | PLANT_MAINTENANCE | 101
2024 | summer | SLATE_2_SLASR1 | PLANT_TROUBLE | 206.8408
2024 | summer | SLATE_2_SLASR2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | summer | SLATE_2_SLASR2 | PLANT_MAINTENANCE | 7.5
2024 | summer | SLATE_2_SLASR2 | PLANT_TROUBLE | 298.5667
2024 | summer | SLATE_2_SLASR3 | METERING_TELEMETRY | 0
2024 | summer | SLATE_2_SLASR3 | PLANT_MAINTENANCE | 0.23833
2024 | summer | SLATE_2_SLASR3 | PLANT_TROUBLE | 196.0833
2024 | summer | SLATE_2_SLASR4 | METERING_TELEMETRY | 0
2024 | summer | SLATE_2_SLASR4 | PLANT_MAINTENANCE | 0
2024 | summer | SLATE_2_SLASR4 | PLANT_TROUBLE | 18.0167
2024 | summer | SLATE_2_SLASR5 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1363.459
2024 | summer | SLATE_2_SLASR5 | AMBIENT_DUE_TO_TEMP | 0
2024 | summer | SLATE_2_SLASR5 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | summer | SLATE_2_SLASR5 | PLANT_MAINTENANCE | 130
2024 | summer | SLATE_2_SLASR5 | PLANT_TROUBLE | 115.1667
2024 | summer | SLATE_2_SLASR5 | UNIT_TESTING | 0
2024 | summer | SLRMS3_2_SRMSR1 | PLANT_MAINTENANCE | 0
2024 | summer | SLRMS3_2_SRMSR1 | PLANT_TROUBLE | 951.5667
2024 | summer | SLRMS3_2_SRMSR1 | TRANSMISSION_INDUCED | 2375
2024 | summer | SLST13_2_SOLAR1 | PLANT_TROUBLE | 1271
2024 | summer | SLSTR1_2_SOLAR1 | PLANT_TROUBLE | 287
2024 | summer | SLSTR2_2_SOLAR2 | PLANT_MAINTENANCE | 177
2024 | summer | SLUISP_2_UNITS | ENVIRONMENTAL_RESTRICTIONS | 31710.8515
2024 | summer | SLUISP_2_UNITS | PLANT_MAINTENANCE | 99659.3367
2024 | summer | SLUISP_2_UNITS | PLANT_TROUBLE | 259.9167
2024 | summer | SLYCRK_1_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 48.3167
2024 | summer | SLYCRK_1_UNIT 1 | PLANT_MAINTENANCE | 0
2024 | summer | SMPRIP_1_SMPSON | PLANT_TROUBLE | 683.075
2024 | summer | SMPRIP_1_SMPSON | TRANSMISSION_INDUCED | 230.25
2024 | summer | SMUDGO_7_UNIT 1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 10857.7333
2024 | summer | SMUDGO_7_UNIT 1 | PLANT_TROUBLE | 45
2024 | summer | SMYRNA_1_DL1SR1 | TRANSMISSION_INDUCED | 4.75
2024 | summer | SNCLRA_2_HOWLNG | METERING_TELEMETRY | 548.45
2024 | summer | SNCLRA_2_HOWLNG | PLANT_MAINTENANCE | 133.8
2024 | summer | SNCLRA_2_HOWLNG | PLANT_TROUBLE | 1479.9
2024 | summer | SNCLRA_2_SILBT1 | METERING_TELEMETRY | 20.9
2024 | summer | SNCLRA_2_SILBT1 | PLANT_MAINTENANCE | 0
2024 | summer | SNCLRA_2_SILBT1 | PLANT_TROUBLE | 0.58667
2024 | summer | SNCLRA_2_UNIT1 | PLANT_MAINTENANCE | 69.0367
2024 | summer | SNCLRA_2_UNIT1 | PLANT_TROUBLE | 3471
2024 | summer | SNCLRA_2_UNIT1 | TRANSMISSION_INDUCED | 0
2024 | summer | SNCLRA_2_VESBT1 | METERING_TELEMETRY | 2765
2024 | summer | SNCLRA_2_VESBT1 | PLANT_MAINTENANCE | 35
2024 | summer | SNCLRA_2_VESBT1 | PLANT_TROUBLE | 0
2024 | summer | SNCLRA_2_VESBT1 | UNIT_TESTING | 31.6667
2024 | summer | SNCLRA_6_OXGEN | ENVIRONMENTAL_RESTRICTIONS | 2528.1
2024 | summer | SNCLRA_6_OXGEN | PLANT_MAINTENANCE | 477
2024 | summer | SNCLRA_6_OXGEN | PLANT_TROUBLE | 4177.235
2024 | summer | SNCLRA_6_OXGEN | UNIT_TESTING | 0
2024 | summer | SNCLRA_6_PROCGN | PLANT_MAINTENANCE | 83.825
2024 | summer | SNDBAR_7_UNIT 1 | TRANSMISSION_INDUCED | 344.52
2024 | summer | SNORA_2_SNRSLR | PLANT_TROUBLE | 0
2024 | summer | SOLBLU_2_WSBBX2 | METERING_TELEMETRY | 0
2024 | summer | SOLBLU_2_WSBBX2 | UNIT_TESTING | 0
2024 | summer | SOLBLU_2_WSBSX2 | METERING_TELEMETRY | 0
2024 | summer | SOLBLU_2_WSBSX2 | PLANT_MAINTENANCE | 0
2024 | summer | SOLBLU_2_WSBSX2 | PLANT_TROUBLE | 1010
2024 | summer | SOLBLU_2_WSBSX2 | UNIT_TESTING | 0
2024 | summer | SOUTH_2_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 306.01
2024 | summer | SOUTH_2_UNIT | PLANT_TROUBLE | 163.0633
2024 | summer | SOUTH_2_UNIT | TRANSMISSION_INDUCED | 7.6917
2024 | summer | SPAULD_6_UNIT 3 | AMBIENT_NOT_DUE_TO_TEMP | 609.492
2024 | summer | SPAULD_6_UNIT 3 | PLANT_MAINTENANCE | 97.5
2024 | summer | SPAULD_6_UNIT 3 | PLANT_TROUBLE | 759.2
2024 | summer | SPAULD_6_UNIT 3 | TRANSMISSION_INDUCED | 0
2024 | summer | SPAULD_6_UNIT12 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | summer | SPAULD_6_UNIT12 | PLANT_MAINTENANCE | 0
2024 | summer | SPAULD_6_UNIT12 | PLANT_TROUBLE | 5528.7167
2024 | summer | SPAULD_6_UNIT12 | UNIT_TESTING | 16.8167
2024 | summer | SPBURN_2_UNIT 1 | PLANT_MAINTENANCE | 337.7
2024 | summer | SPBURN_2_UNIT 1 | PLANT_TROUBLE | 1185.3667
2024 | summer | SPBURN_2_UNIT 1 | TRANSMISSION_INDUCED | 0
2024 | summer | SPBURN_7_SNOWMT | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 2175
2024 | summer | SPI LI_2_UNIT 1 | PLANT_TROUBLE | 165.7867
2024 | summer | SPI LI_2_UNIT 1 | TRANSMISSION_INDUCED | 0
2024 | summer | SPIAND_1_ANDSN2 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | summer | SPIAND_1_ANDSN2 | PLANT_TROUBLE | 110.8625
2024 | summer | SPIAND_1_ANDSN2 | TRANSMISSION_INDUCED | 0
2024 | summer | SPICER_1_UNITS | PLANT_MAINTENANCE | 49
2024 | summer | SPICER_1_UNITS | PLANT_TROUBLE | 8.8
2024 | summer | SPICER_1_UNITS | TRANSMISSION_INDUCED | 14.6
2024 | summer | SPIFBD_1_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 66.875
2024 | summer | SPIFBD_1_PL1X2 | PLANT_TROUBLE | 241.3583
2024 | summer | SPIFBD_1_PL1X2 | TRANSMISSION_INDUCED | 47.875
2024 | summer | SPQUIN_6_SRPCQU | AMBIENT_DUE_TO_TEMP | 120
2024 | summer | SPQUIN_6_SRPCQU | PLANT_MAINTENANCE | 460
2024 | summer | SPQUIN_6_SRPCQU | PLANT_TROUBLE | 11.0167
2024 | summer | SPQUIN_6_SRPCQU | TRANSMISSION_INDUCED | 432
2024 | summer | SPRGAP_1_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 1220.5167
2024 | summer | SPRGAP_1_UNIT 1 | PLANT_MAINTENANCE | 0
2024 | summer | SPRGAP_1_UNIT 1 | PLANT_TROUBLE | 19.1333
2024 | summer | SPRGAP_1_UNIT 1 | TRANSMISSION_INDUCED | 148.9833
2024 | summer | SPRGVL_2_SUCCES | PLANT_MAINTENANCE | 119
2024 | summer | SPRGVL_2_SUCCES | PLANT_TROUBLE | 28
2024 | summer | SPRGVL_2_SUCCES | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 217
2024 | summer | SPRGVL_2_TULESC | ENVIRONMENTAL_RESTRICTIONS | 1912.5
2024 | summer | STANIS_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | summer | STANIS_7_UNIT 1 | TRANSMISSION_INDUCED | 634.7333
2024 | summer | STANTN_2_SBEBX2 | PLANT_TROUBLE | 105.3333
2024 | summer | STANTN_2_STAGT1 | AMBIENT_DUE_TO_TEMP | 39.2388
2024 | summer | STANTN_2_STAGT2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | summer | STANTN_2_STAGT2 | AMBIENT_DUE_TO_TEMP | 585.9492
2024 | summer | STANTN_2_STAGT2 | PLANT_TROUBLE | 102.9807
2024 | summer | STIGCT_2_LODI | AMBIENT_DUE_TO_TEMP | 2324
2024 | summer | STIGCT_2_LODI | PLANT_TROUBLE | 6433.8667
2024 | summer | STIGCT_2_LODI | UNIT_TESTING | 38.25
2024 | summer | STNRES_1_UNIT | PLANT_MAINTENANCE | 1284.4
2024 | summer | STNRES_1_UNIT | PLANT_TROUBLE | 3485.2517
2024 | summer | STNRES_1_UNIT | RTU_RIG | 0
2024 | summer | STNRES_1_UNIT | TRANSMISSION_INDUCED | 422.875
2024 | summer | STOILS_1_UNITS | PLANT_TROUBLE | 4748.9
2024 | summer | STRAUS_1_STRWD1 | PLANT_MAINTENANCE | 0
2024 | summer | STROUD_6_SOLAR | METERING_TELEMETRY | 400
2024 | summer | STROUD_6_SOLAR | PLANT_TROUBLE | 2815.9833
2024 | summer | STROUD_6_SOLAR | TRANSMISSION_INDUCED | 300
2024 | summer | STROUD_6_WWHSR1 | PLANT_TROUBLE | 150
2024 | summer | STROUD_6_WWHSR1 | TRANSMISSION_INDUCED | 0
2024 | summer | SUMWHT_6_SWSSR1 | PLANT_TROUBLE | 5250.9833
2024 | summer | SUMWHT_6_SWSSR1 | TRANSMISSION_INDUCED | 0
2024 | summer | SUNCAT_2_A1ABT1 | PLANT_TROUBLE | 7.5333
2024 | summer | SUNCAT_2_A1BBT1 | PLANT_TROUBLE | 383.3182
2024 | summer | SUNCAT_2_A2ABT2 | PLANT_TROUBLE | 1340.4945
2024 | summer | SUNCAT_2_A2BSR2 | PLANT_TROUBLE | 28
2024 | summer | SUNCAT_2_A2BSR2 | UNIT_TESTING | 0
2024 | summer | SUNRIS_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 36478.1
2024 | summer | SUNRIS_2_PL1X3 | ENVIRONMENTAL_RESTRICTIONS | 13.1195
2024 | summer | SUNRIS_2_PL1X3 | PLANT_MAINTENANCE | 2980.2
2024 | summer | SUNRIS_2_PL1X3 | PLANT_TROUBLE | 1551.0023
2024 | summer | SUNRIS_2_PL1X3 | UNIT_TESTING | 358.08
2024 | summer | SUNSET_2_UNITS | AMBIENT_DUE_TO_TEMP | 17083
2024 | summer | SUNSET_2_UNITS | PLANT_MAINTENANCE | 335
2024 | summer | SUNSET_2_UNITS | PLANT_TROUBLE | 0
2024 | summer | SUNSHN_2_LNDFL | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | summer | SUNSHN_2_LNDFL | AMBIENT_DUE_TO_TEMP | 286.9
2024 | summer | SUNSHN_2_LNDFL | AMBIENT_NOT_DUE_TO_TEMP | 17.6667
2024 | summer | SUNSHN_2_LNDFL | METERING_TELEMETRY | 65.3
2024 | summer | SUNSHN_2_LNDFL | PLANT_MAINTENANCE | 2790.1667
2024 | summer | SUNSHN_2_LNDFL | PLANT_TROUBLE | 272.91
2024 | summer | SUNSLR_1_SSVSR1 | PLANT_MAINTENANCE | 3.35
2024 | summer | SUNSLR_1_SSVSR1 | PLANT_TROUBLE | 1915
2024 | summer | SUNSPT_2_WNASR1 | PLANT_MAINTENANCE | 0
2024 | summer | SUNSPT_2_WNASR1 | PLANT_TROUBLE | 1645
2024 | summer | SUNST2_5_SS2SR1 | PLANT_MAINTENANCE | 20
2024 | summer | SUNSTR_5_SS1SCEDYN | PLANT_MAINTENANCE | 449.35
2024 | summer | SUNSTR_5_SS1SCEDYN | PLANT_TROUBLE | 3929.1667
2024 | summer | SUTTER_2_CISO | AMBIENT_DUE_TO_TEMP | 8864.0017
2024 | summer | SUTTER_2_CISO | PLANT_TROUBLE | 49420.1817
2024 | summer | SUTTER_2_CISO | TRANSITIONAL_LIMITATION | 384.2848
2024 | summer | SYCAMR_2_UNIT 1 | PLANT_TROUBLE | 690.6667
2024 | summer | SYCAMR_2_UNIT 2 | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | summer | SYCAMR_2_UNIT 2 | PLANT_MAINTENANCE | 0
2024 | summer | SYCAMR_2_UNIT 2 | PLANT_TROUBLE | 5408.6667
2024 | summer | SYCAMR_2_UNIT 2 | UNIT_SUPPORTING_STARTUP | 0
2024 | summer | SYCAMR_2_UNIT 2 | UNIT_TESTING | 0
2024 | summer | SYCAMR_2_UNIT 3 | PLANT_TROUBLE | 387.2667
2024 | summer | SYCAMR_2_UNIT 4 | PLANT_MAINTENANCE | 0
2024 | summer | SYCAMR_2_UNIT 4 | PLANT_TROUBLE | 760
2024 | summer | TAHOE_2_THOBT3 | PLANT_MAINTENANCE | 64.1667
2024 | summer | TANHIL_6_SOLART | PLANT_MAINTENANCE | 62.3333
2024 | summer | TANHIL_6_SOLART | PLANT_TROUBLE | 7.4667
2024 | summer | TBLMTN_6_QF | AMBIENT_NOT_DUE_TO_TEMP | 17
2024 | summer | TBLMTN_6_QF | PLANT_MAINTENANCE | 561
2024 | summer | TBLMTN_6_QF | TRANSMISSION_INDUCED | 17
2024 | summer | TECOLOTE_3_WBDYN | PLANT_TROUBLE | 1104.832
2024 | summer | TECOLOTE_3_WBDYN | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 3239
2024 | summer | TECOLOTE_3_WBDYN | TRANSITIONAL_LIMITATION | 113.76
2024 | summer | TECOLOTE_3_WBDYN | TRANSMISSION_INDUCED | 638.5653
2024 | summer | TEHAPI_2_PW1WD1 | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | summer | TEHAPI_2_PW1WD1 | PLANT_TROUBLE | 11.5
2024 | summer | TEHAPI_2_PW2WD2 | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | summer | TEHAPI_2_PW2WD2 | PLANT_TROUBLE | 2754
2024 | summer | TEHAPI_2_WIND1 | METERING_TELEMETRY | 0
2024 | summer | TEHAPI_2_WIND1 | PLANT_TROUBLE | 99.25
2024 | summer | TEHAPI_2_WIND1 | TRANSMISSION_INDUCED | 23.4892
2024 | summer | TEHAPI_2_WIND2 | METERING_TELEMETRY | 0
2024 | summer | TEHAPI_2_WIND2 | PLANT_TROUBLE | 0
2024 | summer | TEHAPI_2_WIND2 | TRANSMISSION_INDUCED | 27.9977
2024 | summer | TENGEN_2_PL1X2 | ENVIRONMENTAL_RESTRICTIONS | 1754
2024 | summer | TENGEN_2_PL1X2 | METERING_TELEMETRY | 0
2024 | summer | TENGEN_2_PL1X2 | PLANT_MAINTENANCE | 15685
2024 | summer | TENGEN_2_PL1X2 | PLANT_TROUBLE | 1254.1
2024 | summer | TERMEX_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 16710
2024 | summer | TERMEX_2_PL1X3 | PLANT_TROUBLE | 14434.0167
2024 | summer | TIDWTR_2_UNITS | PLANT_MAINTENANCE | 1722
2024 | summer | TIFFNY_1_DILLON | AMBIENT_DUE_TO_TEMP | 4826.2167
2024 | summer | TIFFNY_1_DILLON | METERING_TELEMETRY | 92.8333
2024 | summer | TIFFNY_1_DILLON | PLANT_TROUBLE | 315
2024 | summer | TIFFNY_1_DILLON | TRANSITIONAL_LIMITATION | 76.5
2024 | summer | TIGRCK_7_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 421.1333
2024 | summer | TITANS_2_TTSSR1 | PLANT_MAINTENANCE | 630
2024 | summer | TITANS_2_TTSSR1 | PLANT_TROUBLE | 683.0333
2024 | summer | TKOPWR_6_HYDRO | TRANSMISSION_INDUCED | 0
2024 | summer | TOADTW_6_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 204.525
2024 | summer | TOADTW_6_UNIT | PLANT_MAINTENANCE | 0
2024 | summer | TOADTW_6_UNIT | PLANT_TROUBLE | 0
2024 | summer | TOPAZ_2_SOLAR | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | summer | TOPAZ_2_SOLAR | METERING_TELEMETRY | 100
2024 | summer | TOPAZ_2_SOLAR | PLANT_MAINTENANCE | 550
2024 | summer | TOPAZ_2_SOLAR | PLANT_TROUBLE | 993.1
2024 | summer | TOPAZ_2_SOLAR | TRANSMISSION_INDUCED | 2085.4
2024 | summer | TOPAZ_2_SOLAR | UNIT_TESTING | 10528.5
2024 | summer | TORTLA_1_SOLAR | METERING_TELEMETRY | 0
2024 | summer | TORTLA_1_SOLAR | PLANT_TROUBLE | 20
2024 | summer | TORTLA_1_SOLAR | TRANSMISSION_INDUCED | 100
2024 | summer | TOWNSITE_2_MEADDYN | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 8629.5
2024 | summer | TOWNSITE_2_MEADDYN | METERING_TELEMETRY | 180
2024 | summer | TOWNSITE_2_MEADDYN | PLANT_TROUBLE | 0
2024 | summer | TRNQL8_2_AZUSR1 | PLANT_TROUBLE | 120
2024 | summer | TRNQL8_2_ROJSR1 | PLANT_MAINTENANCE | 100
2024 | summer | TRNQL8_2_ROJSR1 | PLANT_TROUBLE | 1335
2024 | summer | TRNQL8_2_VERSR1 | PLANT_TROUBLE | 467
2024 | summer | TRNQLT_2_RETBT1 | METERING_TELEMETRY | 0
2024 | summer | TRNQLT_2_RETBT1 | PLANT_MAINTENANCE | 40.5
2024 | summer | TRNQLT_2_RETBT1 | PLANT_TROUBLE | 6552.75
2024 | summer | TRNQLT_2_RETBT1 | UNIT_TESTING | 0
2024 | summer | TRNQLT_2_SOLAR | PLANT_MAINTENANCE | 414.19
2024 | summer | TRNQLT_2_SOLAR | PLANT_TROUBLE | 5586.8403
2024 | summer | TRNSWD_1_QF | PLANT_MAINTENANCE | 165
2024 | summer | TRNSWD_1_QF | PLANT_TROUBLE | 22574.55
2024 | summer | TULARE_2_TFCBM1 | PLANT_TROUBLE | 908.5533
2024 | summer | TULARE_2_TFCBM1 | UNIT_TESTING | 196
2024 | summer | TULEWD_1_TULWD1 | PLANT_TROUBLE | 607.5
2024 | summer | TULLCK_7_UNITS | PLANT_TROUBLE | 15.4
2024 | summer | TULLCK_7_UNITS | TRANSMISSION_INDUCED | 0
2024 | summer | TUMBWD_2_WISBT3 | METERING_TELEMETRY | 0
2024 | summer | TUMBWD_2_WISBT3 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | summer | TUMBWD_2_WISBT3 | PLANT_MAINTENANCE | 0
2024 | summer | TUMBWD_2_WISBT3 | PLANT_TROUBLE | 1626.65
2024 | summer | TUMBWD_2_WISBT3 | TRANSMISSION_INDUCED | 300
2024 | summer | TUMBWD_2_WISBT4 | METERING_TELEMETRY | 0
2024 | summer | TUMBWD_2_WISBT4 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | summer | TUMBWD_2_WISBT4 | PLANT_TROUBLE | 151.0617
2024 | summer | TUMBWD_2_WISBT4 | TRANSMISSION_INDUCED | 448.92
2024 | summer | TUPMAN_1_BIOGAS | PLANT_TROUBLE | 74.52
2024 | summer | TVYVLY_6_KRSHY1 | AMBIENT_NOT_DUE_TO_TEMP | 594.75
2024 | summer | TWISSL_6_SOLAR | PLANT_TROUBLE | 150
2024 | summer | TWISSL_6_SOLAR | TRANSMISSION_INDUCED | 7.5
2024 | summer | TWISSL_6_SOLAR1 | TRANSMISSION_INDUCED | 100
2024 | summer | TX-ELK_6_SOLAR1 | PLANT_TROUBLE | 1147.5
2024 | summer | TXMCKT_6_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 25.68
2024 | summer | TXMCKT_6_UNIT | PLANT_MAINTENANCE | 26.9333
2024 | summer | TXMCKT_6_UNIT | PLANT_TROUBLE | 163.04
2024 | summer | UKIAH_7_LAKEMN | PLANT_TROUBLE | 5.8917
2024 | summer | UKIAH_7_LAKEMN | TRANSMISSION_INDUCED | 0
2024 | summer | ULTPCH_1_UCSBT1 | TRANSMISSION_INDUCED | 392.8333
2024 | summer | ULTPCH_1_UNIT 1 | PLANT_MAINTENANCE | 270
2024 | summer | ULTPCH_1_UNIT 1 | PLANT_TROUBLE | 180
2024 | summer | ULTPCH_1_UNIT 1 | TRANSMISSION_INDUCED | 59.4
2024 | summer | ULTPFR_1_UNIT 1 | PLANT_MAINTENANCE | 2351.585
2024 | summer | ULTPFR_1_UNIT 1 | PLANT_TROUBLE | 7457.9
2024 | summer | ULTRCK_2_UNIT | METERING_TELEMETRY | 131.5
2024 | summer | ULTRCK_2_UNIT | PLANT_TROUBLE | 2438.78
2024 | summer | UNVRSY_1_UNIT 1 | TRANSMISSION_INDUCED | 5.7
2024 | summer | USWND2_1_WIND1 | PLANT_TROUBLE | 4770.2617
2024 | summer | USWND2_1_WIND1 | TRANSMISSION_INDUCED | 103.82
2024 | summer | USWND2_1_WIND2 | PLANT_MAINTENANCE | 5405.1138
2024 | summer | USWND2_1_WIND2 | PLANT_TROUBLE | 39.5292
2024 | summer | USWND2_1_WIND2 | TRANSMISSION_INDUCED | 100.24
2024 | summer | USWND2_1_WIND3 | PLANT_TROUBLE | 4285.9633
2024 | summer | USWND2_1_WIND3 | TRANSMISSION_INDUCED | 110.4
2024 | summer | USWND4_2_UNIT2 | TRANSMISSION_INDUCED | 518
2024 | summer | USWNDR_2_LABWD1 | PLANT_TROUBLE | 714.325
2024 | summer | USWNDR_2_LABWD1 | TRANSMISSION_INDUCED | 94.35
2024 | summer | USWPFK_6_FRICK | METERING_TELEMETRY | 0
2024 | summer | USWPFK_6_FRICK | PLANT_TROUBLE | 95
2024 | summer | USWPFK_6_FRICK | TRANSMISSION_INDUCED | 50
2024 | summer | USWPJR_2_UNITS | PLANT_MAINTENANCE | 3182.3917
2024 | summer | USWPJR_2_UNITS | PLANT_TROUBLE | 0
2024 | summer | USWPJR_2_UNITS | TRANSMISSION_INDUCED | 0
2024 | summer | VACADX_1_SOLAR | PLANT_MAINTENANCE | 0
2024 | summer | VACADX_1_UNITA1 | AMBIENT_DUE_TO_TEMP | 16.8533
2024 | summer | VACADX_1_UNITA1 | PLANT_MAINTENANCE | 1331.4915
2024 | summer | VACADX_1_UNITA1 | PLANT_TROUBLE | 6372.9412
2024 | summer | VACADX_1_UNITA1 | UNIT_TESTING | 2.6
2024 | summer | VALLEY_5_REDMTN | PLANT_TROUBLE | 777.1283
2024 | summer | VALLEY_5_SOLAR2 | PLANT_TROUBLE | 100
2024 | summer | VALTNE_2_TBBBT1 | PLANT_MAINTENANCE | 290
2024 | summer | VALTNE_2_TBBBT1 | PLANT_TROUBLE | 932.58
2024 | summer | VALTNE_2_TBBBT1 | UNIT_TESTING | 0
2024 | summer | VALTNE_2_TRSBT1 | PLANT_MAINTENANCE | 30
2024 | summer | VALTNE_2_TRSBT1 | PLANT_TROUBLE | 36
2024 | summer | VALTNE_2_TRSBT1 | UNIT_TESTING | 0
2024 | summer | VEDDER_1_SEKERN | PLANT_TROUBLE | 9539.55
2024 | summer | VEGA_6_SOLAR1 | PLANT_MAINTENANCE | 20
2024 | summer | VEGA_6_SOLAR1 | TRANSMISSION_INDUCED | 1006.6667
2024 | summer | VERNON_6_GONZL1 | ANNUAL_USE_LIMIT_REACHED | 14.375
2024 | summer | VERNON_6_GONZL1 | UNIT_TESTING | 0
2024 | summer | VERNON_6_GONZL2 | UNIT_TESTING | 0
2024 | summer | VERNON_6_MALBRG | PLANT_TROUBLE | 4007.1783
2024 | summer | VESTAL_2_BTNBT1 | PLANT_MAINTENANCE | 2800
2024 | summer | VESTAL_2_KERN | AMBIENT_NOT_DUE_TO_TEMP | 16123
2024 | summer | VESTAL_2_TS5SR1 | PLANT_MAINTENANCE | 27.915
2024 | summer | VESTAL_2_TS5SR1 | PLANT_TROUBLE | 5283.2162
2024 | summer | VESTAL_2_WELLHD | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 343
2024 | summer | VESTAL_2_WELLHD | AMBIENT_DUE_TO_TEMP | 601.5667
2024 | summer | VESTAL_2_WELLHD | AMBIENT_NOT_DUE_TO_TEMP | 3.6
2024 | summer | VESTAL_2_WELLHD | PLANT_MAINTENANCE | 0
2024 | summer | VESTAL_2_WELLHD | PLANT_TROUBLE | 2562.746
2024 | summer | VESTAL_6_QF | AMBIENT_NOT_DUE_TO_TEMP | 179.25
2024 | summer | VESTAL_6_QF | PLANT_TROUBLE | 295.9617
2024 | summer | VESTAL_6_QF | TRANSMISSION_INDUCED | 8.9625
2024 | summer | VICPAS_2_SLOBT1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | summer | VICPAS_2_SLOBT1 | METERING_TELEMETRY | 0
2024 | summer | VICPAS_2_SLOBT1 | PLANT_MAINTENANCE | 0
2024 | summer | VICPAS_2_SLOBT1 | PLANT_TROUBLE | 378.075
2024 | summer | VICPAS_2_SLOBT1 | UNIT_TESTING | 0
2024 | summer | VICPAS_2_SLOSR1 | METERING_TELEMETRY | 0
2024 | summer | VICPAS_2_SLOSR1 | UNIT_TESTING | 0
2024 | summer | VICPAS_2_SOCBT1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 30
2024 | summer | VICPAS_2_SOCBT1 | METERING_TELEMETRY | 0
2024 | summer | VICPAS_2_SOCBT1 | PLANT_MAINTENANCE | 0
2024 | summer | VICPAS_2_SOCBT1 | PLANT_TROUBLE | 2620.9167
2024 | summer | VICPAS_2_SOCBT1 | UNIT_TESTING | 0
2024 | summer | VICPAS_2_SOCBT2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | summer | VICPAS_2_SOCBT2 | METERING_TELEMETRY | 0
2024 | summer | VICPAS_2_SOCBT2 | PLANT_MAINTENANCE | 0
2024 | summer | VICPAS_2_SOCBT2 | PLANT_TROUBLE | 2043.75
2024 | summer | VICPAS_2_SOCBT2 | UNIT_TESTING | 0
2024 | summer | VICPAS_2_SOCSR1 | METERING_TELEMETRY | 0
2024 | summer | VICPAS_2_SOCSR1 | UNIT_TESTING | 0
2024 | summer | VICPAS_2_SOCSR2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | summer | VICPAS_2_SOCSR2 | METERING_TELEMETRY | 0
2024 | summer | VICPAS_2_SOCSR2 | PLANT_MAINTENANCE | 0
2024 | summer | VICPAS_2_SOCSR2 | PLANT_TROUBLE | 23.375
2024 | summer | VICPAS_2_SOCSR3 | METERING_TELEMETRY | 0
2024 | summer | VICPAS_2_SOCSR3 | UNIT_TESTING | 0
2024 | summer | VICPAS_2_VPSBT1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 345
2024 | summer | VICPAS_2_VPSBT1 | AMBIENT_DUE_TO_TEMP | 0
2024 | summer | VICPAS_2_VPSBT1 | METERING_TELEMETRY | 0
2024 | summer | VICPAS_2_VPSBT1 | PLANT_MAINTENANCE | 0
2024 | summer | VICPAS_2_VPSBT1 | PLANT_TROUBLE | 1323.2333
2024 | summer | VICPAS_2_VPSBT1 | RTU_RIG | 170
2024 | summer | VICPAS_2_VPSBT1 | UNIT_TESTING | 0
2024 | summer | VICPAS_2_VPSSR1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | summer | VICPAS_2_VPSSR1 | METERING_TELEMETRY | 0
2024 | summer | VICPAS_2_VPSSR1 | PLANT_MAINTENANCE | 0
2024 | summer | VICPAS_2_VPSSR1 | PLANT_TROUBLE | 8309.5667
2024 | summer | VICTOR_1_CREST | PLANT_TROUBLE | 0
2024 | summer | VICTOR_1_CREST | TRANSMISSION_INDUCED | 0
2024 | summer | VICTOR_1_EXSLRA | PLANT_TROUBLE | 0
2024 | summer | VICTOR_1_EXSLRA | TRANSMISSION_INDUCED | 1.4667
2024 | summer | VICTOR_1_EXSLRB | PLANT_TROUBLE | 0
2024 | summer | VICTOR_1_EXSLRB | TRANSMISSION_INDUCED | 1.4333
2024 | summer | VICTOR_1_LVSLR1 | TRANSMISSION_INDUCED | 71.3333
2024 | summer | VICTOR_1_LVSLR2 | TRANSMISSION_INDUCED | 150
2024 | summer | VICTOR_1_SOLAR1 | PLANT_MAINTENANCE | 0
2024 | summer | VICTOR_1_SOLAR3 | METERING_TELEMETRY | 35
2024 | summer | VICTOR_1_SOLAR3 | PLANT_TROUBLE | 35
2024 | summer | VICTOR_1_SOLAR3 | TRANSMISSION_INDUCED | 2.1
2024 | summer | VICTOR_1_SOLAR4 | METERING_TELEMETRY | 100
2024 | summer | VICTOR_1_SOLAR4 | PLANT_TROUBLE | 0
2024 | summer | VICTOR_1_SOLAR4 | TRANSMISSION_INDUCED | 6
2024 | summer | VIKING_2_VCBBT1 | PLANT_MAINTENANCE | 3750
2024 | summer | VIKING_2_VCBBT1 | TRANSMISSION_INDUCED | 2325
2024 | summer | VIKING_2_VCSSR1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | summer | VIKING_2_VCSSR1 | PLANT_MAINTENANCE | 64.5
2024 | summer | VIKING_2_VCSSR1 | TRANSMISSION_INDUCED | 2015
2024 | summer | VIKING_2_VSHSB1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 412.2333
2024 | summer | VIKING_2_VSHSB1 | AMBIENT_DUE_TO_TEMP | 0
2024 | summer | VIKING_2_VSHSB1 | METERING_TELEMETRY | 0
2024 | summer | VIKING_2_VSHSB1 | PLANT_MAINTENANCE | 3825
2024 | summer | VIKING_2_VSHSB1 | PLANT_TROUBLE | 3620
2024 | summer | VIKING_2_VSHSB1 | TRANSMISSION_INDUCED | 2325
2024 | summer | VIKING_2_VSHSB1 | UNIT_TESTING | 0
2024 | summer | VISTRA_5_DALBT1 | PLANT_TROUBLE | 234.6833
2024 | summer | VISTRA_5_DALBT1 | TRANSMISSION_INDUCED | 0
2024 | summer | VISTRA_5_DALBT2 | PLANT_TROUBLE | 40
2024 | summer | VISTRA_5_DALBT2 | TRANSMISSION_INDUCED | 0
2024 | summer | VISTRA_5_DALBT3 | PLANT_TROUBLE | 80
2024 | summer | VISTRA_5_DALBT3 | TRANSMISSION_INDUCED | 0
2024 | summer | VISTRA_5_DALBT4 | PLANT_MAINTENANCE | 67.4
2024 | summer | VISTRA_5_DALBT4 | PLANT_TROUBLE | 0
2024 | summer | VISTRA_5_DALBT4 | TRANSMISSION_INDUCED | 0
2024 | summer | VISTRA_5_PLABT1 | PLANT_TROUBLE | 0
2024 | summer | VISTRA_5_PLABT2 | PLANT_TROUBLE | 129.0733
2024 | summer | VISTRA_5_PLABT3 | PLANT_TROUBLE | 18.7833
2024 | summer | VISTRA_5_PLABT4 | PLANT_TROUBLE | 0
2024 | summer | VLCNTR_6_VCEBT1 | AMBIENT_DUE_TO_TEMP | 16
2024 | summer | VLCNTR_6_VCEBT1 | PLANT_MAINTENANCE | 0
2024 | summer | VLCNTR_6_VCEBT1 | PLANT_TROUBLE | 8.6667
2024 | summer | VLCNTR_6_VCEBT2 | PLANT_MAINTENANCE | 0
2024 | summer | VLCNTR_6_VCEBT2 | PLANT_TROUBLE | 0
2024 | summer | VLCNTR_6_VCEBT2 | UNIT_TESTING | 0
2024 | summer | VLCNTR_6_VCSLR | PLANT_MAINTENANCE | 195.72
2024 | summer | VLCNTR_6_VCSLR | PLANT_TROUBLE | 4.66
2024 | summer | VLCNTR_6_VCSLR1 | PLANT_TROUBLE | 15
2024 | summer | VLCNTR_6_VCSLR2 | PLANT_TROUBLE | 30
2024 | summer | VOLTA_2_UNIT 1 | PLANT_TROUBLE | 6961.5
2024 | summer | VOLTA_2_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 44.1667
2024 | summer | VOLTA_2_UNIT 2 | TRANSMISSION_INDUCED | 5.15
2024 | summer | VOLTA_6_BAILCK | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 436.05
2024 | summer | VOLTA_6_BAILCK | PLANT_TROUBLE | 21.3
2024 | summer | VOLTA_6_DIGHYD | AMBIENT_NOT_DUE_TO_TEMP | 1.45
2024 | summer | VOLTA_7_PONHY1 | AMBIENT_NOT_DUE_TO_TEMP | 695
2024 | summer | VOLTA_7_PONHY1 | PLANT_TROUBLE | 2.3958
2024 | summer | VOYAGR_2_VOAWD5 | PLANT_TROUBLE | 53.59
2024 | summer | VOYAGR_2_VOYWD1 | PLANT_MAINTENANCE | 386.73
2024 | summer | VOYAGR_2_VOYWD2 | PLANT_TROUBLE | 560.1517
2024 | summer | VOYAGR_2_VOYWD3 | PLANT_TROUBLE | 164.8475
2024 | summer | VOYAGR_2_VOYWD4 | PLANT_TROUBLE | 81.2387
2024 | summer | VSTAES_6_VESBT1 | METERING_TELEMETRY | 0
2024 | summer | VSTAES_6_VESBT1 | PLANT_MAINTENANCE | 10
2024 | summer | VSTAES_6_VESBT1 | PLANT_TROUBLE | 1291.2917
2024 | summer | WADHAM_6_UNIT | PLANT_TROUBLE | 1162.8
2024 | summer | WALCRK_2_CTG1 | AMBIENT_DUE_TO_TEMP | 169.4033
2024 | summer | WALCRK_2_CTG1 | PLANT_MAINTENANCE | 7303.9633
2024 | summer | WALCRK_2_CTG1 | PLANT_TROUBLE | 2410.7417
2024 | summer | WALCRK_2_CTG1 | TRANSMISSION_INDUCED | 0
2024 | summer | WALCRK_2_CTG2 | AMBIENT_DUE_TO_TEMP | 35.775
2024 | summer | WALCRK_2_CTG2 | PLANT_TROUBLE | 380.38
2024 | summer | WALCRK_2_CTG2 | TRANSMISSION_INDUCED | 0
2024 | summer | WALCRK_2_CTG3 | AMBIENT_DUE_TO_TEMP | 125.1683
2024 | summer | WALCRK_2_CTG3 | PLANT_TROUBLE | 1594.1967
2024 | summer | WALCRK_2_CTG3 | TRANSMISSION_INDUCED | 0
2024 | summer | WALCRK_2_CTG4 | AMBIENT_DUE_TO_TEMP | 0
2024 | summer | WALCRK_2_CTG4 | PLANT_TROUBLE | 64064
2024 | summer | WALCRK_2_CTG4 | TRANSMISSION_INDUCED | 0
2024 | summer | WALCRK_2_CTG5 | AMBIENT_DUE_TO_TEMP | 156.0317
2024 | summer | WALCRK_2_CTG5 | PLANT_MAINTENANCE | 0
2024 | summer | WALCRK_2_CTG5 | PLANT_TROUBLE | 7329.6967
2024 | summer | WALCRK_2_CTG5 | TRANSMISSION_INDUCED | 0
2024 | summer | WALNUT_6_HILLGEN | PLANT_TROUBLE | 2436.45
2024 | summer | WALNUT_7_WCOVST | PLANT_TROUBLE | 143.1783
2024 | summer | WARNE_2_UNIT | ENVIRONMENTAL_RESTRICTIONS | 355
2024 | summer | WARNE_2_UNIT | PLANT_TROUBLE | 304.6333
2024 | summer | WDFRDF_2_WFFBT1 | METERING_TELEMETRY | 0
2024 | summer | WDFRDF_2_WFFBT1 | NEW_GENERATOR_TEST_ENERGY | 125
2024 | summer | WDFRDF_2_WFFBT1 | PLANT_MAINTENANCE | 0
2024 | summer | WDFRDF_2_WFFBT1 | PLANT_TROUBLE | 0
2024 | summer | WDLEAF_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | summer | WDLEAF_7_UNIT 1 | PLANT_TROUBLE | 175
2024 | summer | WESCAN_2_BDSBT1 | PLANT_MAINTENANCE | 393
2024 | summer | WESCAN_2_BDSBT1 | TRANSMISSION_INDUCED | 0
2024 | summer | WESCN2_2_BDSBT1 | NEW_GENERATOR_TEST_ENERGY | 3715
2024 | summer | WHEATL_6_LNDFIL | PLANT_TROUBLE | 17.75
2024 | summer | WHITEH_2_MEADDYN1 | PLANT_TROUBLE | 3739.1133
2024 | summer | WHITEH_2_MEADDYN2 | PLANT_TROUBLE | 17597.8613
2024 | summer | WHITEW_5_WWRSR1 | METERING_TELEMETRY | 0
2024 | summer | WHITEW_5_WWRSR1 | NEW_GENERATOR_TEST_ENERGY | 23653.56
2024 | summer | WHITEW_5_WWRSR1 | UNIT_TESTING | 2148
2024 | summer | WHITNY_6_SOLAR | METERING_TELEMETRY | 0
2024 | summer | WHITNY_6_SOLAR | PLANT_MAINTENANCE | 15
2024 | summer | WHTWTR_1_WINDA1 | PLANT_TROUBLE | 13783.5
2024 | summer | WHTWTR_1_WINDA1 | TRANSMISSION_INDUCED | 161.7
2024 | summer | WILLMS_6_ARBBM1 | AMBIENT_DUE_TO_TEMP | 0
2024 | summer | WILLMS_6_ARBBM1 | AMBIENT_NOT_DUE_TO_TEMP | 3.7
2024 | summer | WILLMS_6_ARBBM1 | PLANT_MAINTENANCE | 262.5
2024 | summer | WILLMS_6_ARBBM1 | PLANT_TROUBLE | 84.85
2024 | summer | WISE_1_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 6586.9033
2024 | summer | WISE_1_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 2176
2024 | summer | WISHON_6_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 2112.6
2024 | summer | WISHON_6_UNITS | PLANT_MAINTENANCE | 1071.4
2024 | summer | WISHON_6_UNITS | PLANT_TROUBLE | 928.48
2024 | summer | WISTER_2_WISSR1 | PLANT_TROUBLE | 5525.7333
2024 | summer | WISTER_2_WISSR1 | TRANSMISSION_INDUCED | 40
2024 | summer | WISTRA_2_WRSSR1 | PLANT_MAINTENANCE | 51
2024 | summer | WISTRA_2_WRSSR1 | PLANT_TROUBLE | 388.3333
2024 | summer | WLDWD_1_SOLAR1 | METERING_TELEMETRY | 0
2024 | summer | WLDWD_1_SOLAR1 | PLANT_MAINTENANCE | 0
2024 | summer | WLDWD_1_SOLAR1 | PLANT_TROUBLE | 0
2024 | summer | WLDWD_1_SOLAR1 | TRANSMISSION_INDUCED | 0
2024 | summer | WLDWD_1_SOLAR2 | TRANSMISSION_INDUCED | 0
2024 | summer | WNDMAS_2_UNIT 1 | METERING_TELEMETRY | 50.8333
2024 | summer | WNDMAS_2_UNIT 1 | PLANT_MAINTENANCE | 426.8333
2024 | summer | WNDMAS_2_UNIT 1 | TRANSMISSION_INDUCED | 760
2024 | summer | WNDSTR_2_WIND | PLANT_MAINTENANCE | 415
2024 | summer | WNDSTR_2_WIND | PLANT_TROUBLE | 197.3333
2024 | summer | WOLFSK_1_UNITA1 | AMBIENT_DUE_TO_TEMP | 1079.3698
2024 | summer | WOLFSK_1_UNITA1 | PLANT_TROUBLE | 0
2024 | summer | WRGTSR_2_WSFSR1 | PLANT_MAINTENANCE | 113
2024 | summer | WRGTSR_2_WSFSR1 | PLANT_TROUBLE | 57091.85
2024 | summer | WSENGY_1_UNIT 1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 35
2024 | summer | WSENGY_1_UNIT 1 | PLANT_MAINTENANCE | 1370
2024 | summer | WSENGY_1_UNIT 1 | PLANT_TROUBLE | 8732.642
2024 | summer | WSNR_2_CVPDYN | PLANT_TROUBLE | 0
2024 | summer | WSNR_2_CVPDYN | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 50
2024 | summer | WSTWND_2_M89BT2 | PLANT_TROUBLE | 6569.6
2024 | summer | WSTWND_2_M89WD2 | PLANT_TROUBLE | 14354.9648
2024 | summer | WSTWND_2_M90WD2 | PLANT_TROUBLE | 10159.7492
2024 | summer | WSTWND_2_SBSBT1 | PLANT_MAINTENANCE | 0
2024 | summer | WSTWND_2_SBSBT1 | PLANT_TROUBLE | 0
2024 | summer | WSTWND_2_SBSBT2 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | summer | WSTWND_2_SBSBT2 | PLANT_MAINTENANCE | 0
2024 | summer | WSTWND_2_SBSBT2 | PLANT_TROUBLE | 30
2024 | summer | WSTWND_2_SBSBT2 | UNIT_TESTING | 3
2024 | summer | WSTWND_2_SBSBT3 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | summer | WSTWND_2_SBSBT3 | PLANT_MAINTENANCE | 158.3667
2024 | summer | WSTWND_2_SBSBT3 | PLANT_TROUBLE | 270.5333
2024 | summer | YELPIN_2_YP2BT1 | PLANT_TROUBLE | 283.452
2024 | summer | YELPIN_2_YP2BT2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 243.5
2024 | summer | YELPIN_2_YP2BT2 | PLANT_MAINTENANCE | 0
2024 | summer | YELPIN_2_YP2BT2 | PLANT_TROUBLE | 260
2024 | summer | YELPIN_2_YP2BT2 | UNIT_TESTING | 0
2024 | summer | YELPIN_2_YP2BT3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 29.25
2024 | summer | YELPIN_2_YP2BT3 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | summer | YELPIN_2_YP2BT3 | PLANT_MAINTENANCE | 0
2024 | summer | YELPIN_2_YP2BT3 | PLANT_TROUBLE | 210.3333
2024 | summer | YELPIN_2_YP2BT3 | UNIT_TESTING | 0
2024 | summer | YELPIN_2_YP2SR2 | PLANT_MAINTENANCE | 60
2024 | summer | YELPIN_2_YP2SR2 | PLANT_TROUBLE | 508.21
2024 | summer | YELPIN_2_YP2SR2 | TRANSMISSION_INDUCED | 0
2024 | summer | YELPIN_2_YP2SR2 | UNIT_TESTING | 0
2024 | summer | YELPIN_2_YP2SR3 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | summer | YELPIN_2_YP2SR3 | TRANSMISSION_INDUCED | 0
2024 | summer | YELPIN_2_YP2SR3 | UNIT_TESTING | 0
2024 | summer | YUBACT_1_SUNSWT | PLANT_MAINTENANCE | 1748.95
2024 | summer | YUBACT_1_SUNSWT | PLANT_TROUBLE | 1499.1
2024 | summer | YUBACT_1_SUNSWT | TRANSMISSION_INDUCED | 14.991
2024 | summer | YUBACT_6_UNITA1 | AMBIENT_DUE_TO_TEMP | 1341.94
2024 | summer | YUBACT_6_UNITA1 | PLANT_TROUBLE | 271.1647
2024 | summer | YUBACT_6_UNITA1 | TRANSITIONAL_LIMITATION | 0
2024 | summer | YUBACT_6_UNITA1 | TRANSMISSION_INDUCED | 0
2024 | summer | ZOND_6_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 13081.5
2024 | nonsummer | 7STDRD_1_SOLAR1 | METERING_TELEMETRY | 79.6667
2024 | nonsummer | 7STDRD_1_SOLAR1 | PLANT_MAINTENANCE | 125.3333
2024 | nonsummer | ACACIA_6_SOLAR | PLANT_MAINTENANCE | 60
2024 | nonsummer | ACACIA_6_SOLAR | PLANT_TROUBLE | 0
2024 | nonsummer | ADERA_1_SOLAR1 | METERING_TELEMETRY | 0
2024 | nonsummer | ADERA_1_SOLAR1 | PLANT_TROUBLE | 826.625
2024 | nonsummer | ADERA_1_SOLAR1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | ADLIN_1_UNITS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 9626.88
2024 | nonsummer | ADLIN_1_UNITS | PLANT_MAINTENANCE | 0
2024 | nonsummer | ADLIN_1_UNITS | PLANT_TROUBLE | 777.1123
2024 | nonsummer | ADLIN_1_UNITS | TRANSMISSION_INDUCED | 99
2024 | nonsummer | ADMEST_6_SOLAR | PLANT_MAINTENANCE | 0
2024 | nonsummer | ADMEST_6_SOLAR | PLANT_TROUBLE | 908.2667
2024 | nonsummer | ADMEST_6_SOLAR | TRANSMISSION_INDUCED | 8.55
2024 | nonsummer | ADOBEE_1_SOLAR | METERING_TELEMETRY | 0
2024 | nonsummer | ADOBEE_1_SOLAR | PLANT_MAINTENANCE | 50
2024 | nonsummer | ADOBEE_1_SOLAR | PLANT_TROUBLE | 112
2024 | nonsummer | AGRICO_6_PL3N5 | AMBIENT_DUE_TO_TEMP | 49.5723
2024 | nonsummer | AGRICO_6_PL3N5 | PLANT_MAINTENANCE | 0
2024 | nonsummer | AGRICO_6_PL3N5 | PLANT_TROUBLE | 89.6255
2024 | nonsummer | AGRICO_6_PL3N5 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | AGRICO_7_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | AGRICO_7_UNIT | PLANT_MAINTENANCE | 0
2024 | nonsummer | AGRICO_7_UNIT | PLANT_TROUBLE | 98.9818
2024 | nonsummer | AGRICO_7_UNIT | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2024 | nonsummer | AGRICO_7_UNIT | TRANSMISSION_INDUCED | 0
2024 | nonsummer | AGUCAL_5_SOLAR1 | METERING_TELEMETRY | 0
2024 | nonsummer | AGUCAL_5_SOLAR1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | AGUCAL_5_SOLAR1 | PLANT_TROUBLE | 0
2024 | nonsummer | AGUCAL_5_SOLAR1 | UNIT_TESTING | 0
2024 | nonsummer | AKINGS_6_AMESR1 | METERING_TELEMETRY | 80
2024 | nonsummer | AKINGS_6_AMESR1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | AKINGS_6_AMESR1 | PLANT_TROUBLE | 1308
2024 | nonsummer | AKINGS_6_AMESR1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | ALAMIT_2_AESBT2 | METERING_TELEMETRY | 0
2024 | nonsummer | ALAMIT_2_AESBT2 | PLANT_TROUBLE | 5327.2667
2024 | nonsummer | ALAMIT_2_AESBT2 | UNIT_TESTING | 311.1667
2024 | nonsummer | ALAMIT_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 85.965
2024 | nonsummer | ALAMIT_2_PL1X3 | PLANT_MAINTENANCE | 11848.65
2024 | nonsummer | ALAMIT_2_PL1X3 | PLANT_TROUBLE | 38044.9555
2024 | nonsummer | ALAMIT_2_PL1X3 | TRANSMISSION_INDUCED | 23614.5
2024 | nonsummer | ALAMIT_2_PL1X3 | UNIT_TESTING | 3710.3067
2024 | nonsummer | ALAMIT_7_ES1 | METERING_TELEMETRY | 758.0592
2024 | nonsummer | ALAMIT_7_ES1 | PLANT_MAINTENANCE | 771.8
2024 | nonsummer | ALAMIT_7_ES1 | PLANT_TROUBLE | 21242.2467
2024 | nonsummer | ALAMIT_7_ES1 | UNIT_TESTING | 0
2024 | nonsummer | ALAMIT_7_UNIT 3 | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | ALAMIT_7_UNIT 3 | ENVIRONMENTAL_RESTRICTIONS | 243416.8155
2024 | nonsummer | ALAMIT_7_UNIT 3 | PLANT_MAINTENANCE | 183.8
2024 | nonsummer | ALAMIT_7_UNIT 3 | PLANT_TROUBLE | 333.8
2024 | nonsummer | ALAMIT_7_UNIT 3 | UNIT_SUPPORTING_STARTUP | 0
2024 | nonsummer | ALAMIT_7_UNIT 3 | UNIT_TESTING | 730.8375
2024 | nonsummer | ALAMIT_7_UNIT 4 | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | ALAMIT_7_UNIT 4 | ENVIRONMENTAL_RESTRICTIONS | 232428.85
2024 | nonsummer | ALAMIT_7_UNIT 4 | PLANT_TROUBLE | 0
2024 | nonsummer | ALAMIT_7_UNIT 4 | UNIT_TESTING | 0
2024 | nonsummer | ALAMIT_7_UNIT 5 | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | ALAMIT_7_UNIT 5 | ENVIRONMENTAL_RESTRICTIONS | 436800
2024 | nonsummer | ALAMIT_7_UNIT 5 | PLANT_TROUBLE | 0
2024 | nonsummer | ALAMIT_7_UNIT 5 | UNIT_TESTING | 1190
2024 | nonsummer | ALAMO_6_UNIT | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | nonsummer | ALAMO_6_UNIT | PLANT_MAINTENANCE | 7361
2024 | nonsummer | ALAMO_6_UNIT | PLANT_TROUBLE | 631.8333
2024 | nonsummer | ALAMO_6_UNIT | TRANSMISSION_INDUCED | 0
2024 | nonsummer | ALHMBR_1_ALHSLR | PLANT_MAINTENANCE | 94
2024 | nonsummer | ALHMBR_1_ALHSLR | PLANT_TROUBLE | 74.4667
2024 | nonsummer | ALHMBR_1_ALHSLR | TRANSMISSION_INDUCED | 1175
2024 | nonsummer | ALLGNY_6_HYDRO1 | TRANSMISSION_INDUCED | 2.366
2024 | nonsummer | ALMASL_2_AL6BT6 | PLANT_MAINTENANCE | 3859.5083
2024 | nonsummer | ALMASL_2_AL6BT6 | PLANT_TROUBLE | 2067.4383
2024 | nonsummer | ALMASL_2_AL6BT6 | UNIT_TESTING | 0
2024 | nonsummer | ALMASL_2_GS1SR1 | PLANT_MAINTENANCE | 641.6667
2024 | nonsummer | ALMASL_2_GS4SR4 | PLANT_MAINTENANCE | 595
2024 | nonsummer | ALMASL_2_GS6SR6 | PLANT_MAINTENANCE | 272.4933
2024 | nonsummer | ALMASL_2_GS7SR7 | PLANT_MAINTENANCE | 1140
2024 | nonsummer | ALMASL_2_GS7SR7 | PLANT_TROUBLE | 2273.0167
2024 | nonsummer | ALMEGT_1_UNIT 1 | AMBIENT_DUE_TO_TEMP | 940
2024 | nonsummer | ALMEGT_1_UNIT 1 | METERING_TELEMETRY | 120
2024 | nonsummer | ALMEGT_1_UNIT 1 | PLANT_TROUBLE | 152
2024 | nonsummer | ALMEGT_1_UNIT 1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | ALMEGT_1_UNIT 2 | AMBIENT_DUE_TO_TEMP | 940
2024 | nonsummer | ALMEGT_1_UNIT 2 | METERING_TELEMETRY | 120
2024 | nonsummer | ALMEGT_1_UNIT 2 | PLANT_TROUBLE | 152
2024 | nonsummer | ALMEGT_1_UNIT 2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | ALPSLR_1_NTHSLR | METERING_TELEMETRY | 60
2024 | nonsummer | ALPSLR_1_NTHSLR | PLANT_MAINTENANCE | 38.3333
2024 | nonsummer | ALPSLR_1_NTHSLR | PLANT_TROUBLE | 5071.5
2024 | nonsummer | ALPSLR_1_NTHSLR | TRANSMISSION_INDUCED | 148
2024 | nonsummer | ALPSLR_1_SPSSLR | METERING_TELEMETRY | 150
2024 | nonsummer | ALPSLR_1_SPSSLR | PLANT_MAINTENANCE | 126.5
2024 | nonsummer | ALPSLR_1_SPSSLR | PLANT_TROUBLE | 11715
2024 | nonsummer | ALPSLR_1_SPSSLR | TRANSMISSION_INDUCED | 410.8333
2024 | nonsummer | ALT6DN_2_WIND7 | UNIT_TESTING | 0
2024 | nonsummer | ALT6DS_2_WIND9 | TRANSMISSION_INDUCED | 352
2024 | nonsummer | ALTA3A_2_CPCE4 | PLANT_TROUBLE | 6328.1833
2024 | nonsummer | ALTA3A_2_CPCE5 | PLANT_TROUBLE | 9479.3833
2024 | nonsummer | ALTA3A_2_CPCE8 | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | nonsummer | ALTA3A_2_CPCE8 | METERING_TELEMETRY | 0
2024 | nonsummer | ALTA3A_2_CPCE8 | PLANT_TROUBLE | 21683.3333
2024 | nonsummer | ALTA3A_2_CPCE8 | TRANSMISSION_INDUCED | 402.5
2024 | nonsummer | ALTA4A_2_CPCW1 | METERING_TELEMETRY | 0
2024 | nonsummer | ALTA4A_2_CPCW1 | PLANT_TROUBLE | 3347.1933
2024 | nonsummer | ALTA4B_2_CPCW2 | PLANT_TROUBLE | 8795.2417
2024 | nonsummer | ALTA4B_2_CPCW3 | PLANT_TROUBLE | 9516.5
2024 | nonsummer | ALTA4B_2_CPCW6 | PLANT_MAINTENANCE | 0
2024 | nonsummer | ALTA4B_2_CPCW6 | PLANT_TROUBLE | 915
2024 | nonsummer | ALTA6B_2_WIND11 | PLANT_MAINTENANCE | 0
2024 | nonsummer | ALTA6B_2_WIND11 | PLANT_TROUBLE | 2473.4405
2024 | nonsummer | ALTA6E_2_WIND10 | METERING_TELEMETRY | 0
2024 | nonsummer | ALTA6E_2_WIND10 | PLANT_TROUBLE | 12323.903
2024 | nonsummer | ALTWD_2_AT3WD3 | PLANT_TROUBLE | 0
2024 | nonsummer | ALTWD_2_AT3WD3 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | ALTWD_2_COAWD1 | PLANT_MAINTENANCE | 1657.8
2024 | nonsummer | ALTWD_2_COAWD1 | PLANT_TROUBLE | 216
2024 | nonsummer | ALTWD_2_COAWD1 | TRANSMISSION_INDUCED | 359.4003
2024 | nonsummer | ANAHM_2_CANYN1 | ENVIRONMENTAL_RESTRICTIONS | 2166.8803
2024 | nonsummer | ANAHM_2_CANYN1 | PLANT_TROUBLE | 47979.75
2024 | nonsummer | ANAHM_2_CANYN1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | ANAHM_2_CANYN2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | ANAHM_2_CANYN2 | PLANT_TROUBLE | 0
2024 | nonsummer | ANAHM_2_CANYN2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | ANAHM_2_CANYN3 | PLANT_MAINTENANCE | 108.4767
2024 | nonsummer | ANAHM_2_CANYN3 | PLANT_TROUBLE | 4230.59
2024 | nonsummer | ANAHM_2_CANYN4 | PLANT_MAINTENANCE | 149.4
2024 | nonsummer | ANAHM_2_CANYN4 | PLANT_TROUBLE | 493.02
2024 | nonsummer | ANZA_6_SOLAR1 | PLANT_MAINTENANCE | 60
2024 | nonsummer | ANZA_6_SOLAR1 | PLANT_TROUBLE | 82.8333
2024 | nonsummer | ANZA_6_SOLAR1 | TRANSMISSION_INDUCED | 1434.5
2024 | nonsummer | APLHIL_1_SFKHY1 | PLANT_MAINTENANCE | 58.96
2024 | nonsummer | APLHIL_1_SFKHY1 | PLANT_TROUBLE | 60.434
2024 | nonsummer | APLHIL_1_SFKHY1 | TRANSMISSION_INDUCED | 3.8413
2024 | nonsummer | AQUAWS_2_AQWSR1 | METERING_TELEMETRY | 45370
2024 | nonsummer | AQUAWS_2_AQWSR1 | PLANT_MAINTENANCE | 72.8
2024 | nonsummer | AQUAWS_2_AQWSR1 | PLANT_TROUBLE | 1186.6667
2024 | nonsummer | AQUAWS_2_AQWSR1 | UNIT_TESTING | 0
2024 | nonsummer | ARBWD_6_QF | PLANT_MAINTENANCE | 3.475
2024 | nonsummer | ARBWD_6_QF | PLANT_TROUBLE | 405.2717
2024 | nonsummer | ARBWD_6_QF | TRANSMISSION_INDUCED | 61.71
2024 | nonsummer | ARCOGN_2_UNITS | AMBIENT_DUE_TO_TEMP | 56
2024 | nonsummer | ARCOGN_2_UNITS | METERING_TELEMETRY | 94.7333
2024 | nonsummer | ARCOGN_2_UNITS | PLANT_MAINTENANCE | 1417.5
2024 | nonsummer | ARCOGN_2_UNITS | PLANT_TROUBLE | 15685.3333
2024 | nonsummer | ARCOGN_2_UNITS | TRANSMISSION_INDUCED | 325
2024 | nonsummer | ARKANS_1_ARKSLR | PLANT_MAINTENANCE | 225
2024 | nonsummer | ARKANS_1_ARKSLR | PLANT_TROUBLE | 74.7667
2024 | nonsummer | ARKANS_1_ARKSLR | TRANSMISSION_INDUCED | 2100
2024 | nonsummer | ARLNTN_2_AR1SR1 | PLANT_MAINTENANCE | 2.1333
2024 | nonsummer | ARLNTN_2_AR1SR1 | PLANT_TROUBLE | 100
2024 | nonsummer | ARLNTN_2_ASUSR1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | ARLNTN_2_ASUSR1 | PLANT_TROUBLE | 0
2024 | nonsummer | ARLNTN_2_ASUSR1 | UNIT_TESTING | 0
2024 | nonsummer | ARVINN_6_ORION1 | TRANSMISSION_INDUCED | 188
2024 | nonsummer | ARVINN_6_ORION2 | TRANSMISSION_INDUCED | 85.4667
2024 | nonsummer | ASTORA_2_SOLAR1 | METERING_TELEMETRY | 0
2024 | nonsummer | ASTORA_2_SOLAR1 | PLANT_TROUBLE | 11215.72
2024 | nonsummer | ASTORA_2_SOLAR1 | UNIT_TESTING | 80
2024 | nonsummer | ASTORA_2_SOLAR2 | PLANT_MAINTENANCE | 1685.9167
2024 | nonsummer | ASTORA_2_SOLAR2 | PLANT_TROUBLE | 165.3
2024 | nonsummer | ATHOS_5_AP1X2 | PLANT_MAINTENANCE | 245.8333
2024 | nonsummer | ATHOS_5_AP1X2 | PLANT_TROUBLE | 1250
2024 | nonsummer | ATHOS_5_AP2X2 | PLANT_MAINTENANCE | 196.6667
2024 | nonsummer | ATWEL2_1_SOLAR1 | TRANSMISSION_INDUCED | 100
2024 | nonsummer | ATWELL_1_SOLAR | PLANT_MAINTENANCE | 0
2024 | nonsummer | ATWELL_1_SOLAR | TRANSMISSION_INDUCED | 100
2024 | nonsummer | AVENAL_6_AVPARK | PLANT_TROUBLE | 538.2
2024 | nonsummer | AVENAL_6_AVPARK | TRANSMISSION_INDUCED | 144
2024 | nonsummer | AVENAL_6_AVSLR1 | PLANT_TROUBLE | 0
2024 | nonsummer | AVENAL_6_AVSLR1 | TRANSMISSION_INDUCED | 63.2
2024 | nonsummer | AVENAL_6_AVSLR2 | PLANT_MAINTENANCE | 7.9
2024 | nonsummer | AVENAL_6_AVSLR2 | PLANT_TROUBLE | 0
2024 | nonsummer | AVENAL_6_AVSLR2 | TRANSMISSION_INDUCED | 63.2
2024 | nonsummer | AVENAL_6_SANDDG | METERING_TELEMETRY | 0
2024 | nonsummer | AVENAL_6_SANDDG | PLANT_TROUBLE | 274.8667
2024 | nonsummer | AVENAL_6_SANDDG | TRANSMISSION_INDUCED | 1409.1667
2024 | nonsummer | AVENAL_6_SUNCTY | PLANT_TROUBLE | 0
2024 | nonsummer | AVENAL_6_SUNCTY | TRANSMISSION_INDUCED | 80
2024 | nonsummer | AVSOLR_2_SOLAR | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | nonsummer | AVSOLR_2_SOLAR | METERING_TELEMETRY | 0
2024 | nonsummer | AVSOLR_2_SOLAR | PLANT_MAINTENANCE | 387.0942
2024 | nonsummer | AVSOLR_2_SOLAR | PLANT_TROUBLE | 597.9
2024 | nonsummer | AVSOLR_2_SOLAR | UNIT_TESTING | 0
2024 | nonsummer | BALCHS_7_UNIT 1 | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | BALCHS_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 152.6033
2024 | nonsummer | BALCHS_7_UNIT 1 | PLANT_TROUBLE | 1054.6
2024 | nonsummer | BALCHS_7_UNIT 1 | TRANSMISSION_INDUCED | 19.6333
2024 | nonsummer | BALCHS_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 223.0417
2024 | nonsummer | BALCHS_7_UNIT 2 | PLANT_TROUBLE | 141.75
2024 | nonsummer | BALCHS_7_UNIT 2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | BALCHS_7_UNIT 3 | AMBIENT_NOT_DUE_TO_TEMP | 478.0767
2024 | nonsummer | BALCHS_7_UNIT 3 | TRANSMISSION_INDUCED | 91
2024 | nonsummer | BANKPP_2_NSPIN | TRANSMISSION_INDUCED | 0
2024 | nonsummer | BARRE_2_ALASB1 | METERING_TELEMETRY | 0
2024 | nonsummer | BARRE_2_ALASB1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | BARRE_2_ALASB1 | PLANT_TROUBLE | 151.6667
2024 | nonsummer | BARRE_2_ALASB1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | BARRE_6_PEAKER | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 112.4567
2024 | nonsummer | BARRE_6_PEAKER | AMBIENT_DUE_TO_TEMP | 394.3387
2024 | nonsummer | BARRE_6_PEAKER | AMBIENT_DUE_TO_TEMP | 1236.43
2024 | nonsummer | BARRE_6_PEAKER | PLANT_MAINTENANCE | 735
2024 | nonsummer | BARRE_6_PEAKER | PLANT_TROUBLE | 0
2024 | nonsummer | BARRE_6_PEAKER | PLANT_TROUBLE | 0
2024 | nonsummer | BARRE_6_PEAKER | TRANSMISSION_INDUCED | 0
2024 | nonsummer | BARRE_6_PEAKER | UNIT_TESTING | 0
2024 | nonsummer | BASICE_2_UNITS | AMBIENT_DUE_TO_TEMP | 657
2024 | nonsummer | BASICE_2_UNITS | PLANT_MAINTENANCE | 9600
2024 | nonsummer | BASICE_2_UNITS | PLANT_TROUBLE | 1446
2024 | nonsummer | BASICE_2_UNITS | TRANSMISSION_INDUCED | 0
2024 | nonsummer | BCTSYS_5_PWXDYN | TRANSITIONAL_LIMITATION | 442980
2024 | nonsummer | BDGRCK_1_UNITS | AMBIENT_DUE_TO_TEMP | 3699.28
2024 | nonsummer | BDGRCK_1_UNITS | PLANT_TROUBLE | 932.6667
2024 | nonsummer | BDGRCK_1_UNITS | UNIT_TESTING | 508.6667
2024 | nonsummer | BEARDS_7_UNIT 1 | PLANT_MAINTENANCE | 57.5
2024 | nonsummer | BEARDS_7_UNIT 1 | PLANT_TROUBLE | 0
2024 | nonsummer | BEARDS_7_UNIT 1 | TRANSMISSION_INDUCED | 2.1083
2024 | nonsummer | BEARMT_1_UNIT | AMBIENT_DUE_TO_TEMP | 3701.6783
2024 | nonsummer | BEARMT_1_UNIT | PLANT_TROUBLE | 0
2024 | nonsummer | BEARMT_1_UNIT | TRANSMISSION_INDUCED | 235.6083
2024 | nonsummer | BEARMT_1_UNIT | UNIT_TESTING | 544.7668
2024 | nonsummer | BEJNLS_5_BV2SCEDYN | AMBIENT_DUE_TO_TEMP | 1894
2024 | nonsummer | BEJNLS_5_BV2SCEDYN | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | nonsummer | BEJNLS_5_BV2SCEDYN | PLANT_MAINTENANCE | 0
2024 | nonsummer | BEJNLS_5_BV2SCEDYN | PLANT_TROUBLE | 698.6167
2024 | nonsummer | BEJNLS_5_BV2SCEDYN | TRANSITIONAL_LIMITATION | 0
2024 | nonsummer | BEJNLS_5_BV2SCEDYN | TRANSMISSION_INDUCED | 10960.1333
2024 | nonsummer | BEKWJS_5_BV1SCEDYN | AMBIENT_DUE_TO_TEMP | 925
2024 | nonsummer | BEKWJS_5_BV1SCEDYN | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | nonsummer | BEKWJS_5_BV1SCEDYN | PLANT_TROUBLE | 633.4167
2024 | nonsummer | BEKWJS_5_BV1SCEDYN | TRANSITIONAL_LIMITATION | 0
2024 | nonsummer | BEKWJS_5_BV1SCEDYN | TRANSMISSION_INDUCED | 8045.4
2024 | nonsummer | BELDEN_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 847.3167
2024 | nonsummer | BELDEN_7_UNIT 1 | PLANT_TROUBLE | 31311.6667
2024 | nonsummer | BELDEN_7_UNIT 1 | TRANSMISSION_INDUCED | 585.7
2024 | nonsummer | BERCYN_2_BCEBT1 | METERING_TELEMETRY | 65
2024 | nonsummer | BERCYN_2_BCEBT1 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | nonsummer | BERCYN_2_BCEBT1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | BERCYN_2_BCEBT1 | PLANT_TROUBLE | 65
2024 | nonsummer | BERCYN_2_BCEBT1 | UNIT_TESTING | 0
2024 | nonsummer | BGSKYN_2_AS2SR1 | PLANT_MAINTENANCE | 316
2024 | nonsummer | BGSKYN_2_AS2SR1 | PLANT_TROUBLE | 7120.4
2024 | nonsummer | BGSKYN_2_ASPSR2 | PLANT_MAINTENANCE | 119
2024 | nonsummer | BGSKYN_2_ASPSR2 | PLANT_TROUBLE | 1140.9333
2024 | nonsummer | BGSKYN_2_ASPSR2 | RTU_RIG | 0
2024 | nonsummer | BGSKYN_2_ASPSR2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | BGSKYN_2_ASPSR2 | UNIT_TESTING | 0
2024 | nonsummer | BGSKYN_2_ASSR1B | PLANT_MAINTENANCE | 42.5
2024 | nonsummer | BGSKYN_2_ASSR1B | PLANT_TROUBLE | 248.4
2024 | nonsummer | BGSKYN_2_ASSR3A | PLANT_MAINTENANCE | 163.75
2024 | nonsummer | BGSKYN_2_ASSR3A | PLANT_TROUBLE | 956.5917
2024 | nonsummer | BGSKYN_2_ASSR3A | TRANSMISSION_INDUCED | 0
2024 | nonsummer | BGSKYN_2_ASSR3A | UNIT_TESTING | 0
2024 | nonsummer | BGSKYN_2_ASSR3B | PLANT_MAINTENANCE | 54.5833
2024 | nonsummer | BGSKYN_2_ASSR3B | PLANT_TROUBLE | 17.5
2024 | nonsummer | BGSKYN_2_ASSR3B | UNIT_TESTING | 0
2024 | nonsummer | BGSKYN_2_BS3SR3 | PLANT_TROUBLE | 188.3333
2024 | nonsummer | BIGCRK_2_EXESWD | AMBIENT_NOT_DUE_TO_TEMP | 223419.6417
2024 | nonsummer | BIGCRK_2_EXESWD | PLANT_MAINTENANCE | 2282
2024 | nonsummer | BIGCRK_2_EXESWD | PLANT_TROUBLE | 13329.925
2024 | nonsummer | BIGCRK_2_EXESWD | TRANSMISSION_INDUCED | 52225.25
2024 | nonsummer | BIGSKY_2_AS2BT1 | PLANT_TROUBLE | 208.7
2024 | nonsummer | BIGSKY_2_AS2BT1 | RTU_RIG | 0
2024 | nonsummer | BIGSKY_2_AS2BT1 | UNIT_TESTING | 0
2024 | nonsummer | BIGSKY_2_ASLBT2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | BIGSKY_2_ASLBT2 | PLANT_TROUBLE | 542.0167
2024 | nonsummer | BIGSKY_2_ASLBT2 | UNIT_TESTING | 500
2024 | nonsummer | BIGSKY_2_BSKSR6 | PLANT_TROUBLE | 2475.7333
2024 | nonsummer | BIGSKY_2_BSKSR7 | PLANT_MAINTENANCE | 49.5833
2024 | nonsummer | BIGSKY_2_BSKSR7 | PLANT_TROUBLE | 2793.4
2024 | nonsummer | BIGSKY_2_BSKSR8 | PLANT_TROUBLE | 2122.5
2024 | nonsummer | BIGSKY_2_SOLAR1 | PLANT_MAINTENANCE | 39.6667
2024 | nonsummer | BIGSKY_2_SOLAR1 | PLANT_TROUBLE | 267.5
2024 | nonsummer | BIGSKY_2_SOLAR2 | PLANT_MAINTENANCE | 29.3333
2024 | nonsummer | BIGSKY_2_SOLAR2 | PLANT_TROUBLE | 425
2024 | nonsummer | BIGSKY_2_SOLAR3 | PLANT_TROUBLE | 40
2024 | nonsummer | BIGSKY_2_SOLAR4 | PLANT_MAINTENANCE | 0
2024 | nonsummer | BIGSKY_2_SOLAR4 | PLANT_TROUBLE | 152.5
2024 | nonsummer | BIGSKY_2_SOLAR5 | PLANT_TROUBLE | 80.6
2024 | nonsummer | BIGSKY_2_SOLAR6 | PLANT_MAINTENANCE | 199.2833
2024 | nonsummer | BIGSKY_2_SOLAR6 | PLANT_TROUBLE | 3013.9667
2024 | nonsummer | BIGSKY_2_SOLAR6 | UNIT_TESTING | 0
2024 | nonsummer | BIGSKY_2_SOLAR7 | PLANT_MAINTENANCE | 91.2333
2024 | nonsummer | BIGSKY_2_SOLAR7 | PLANT_TROUBLE | 742.0667
2024 | nonsummer | BIOMAS_1_UNIT 1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | BIOMAS_1_UNIT 1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | BIOMAS_1_UNIT 1 | PLANT_TROUBLE | 1608
2024 | nonsummer | BIOMAS_1_UNIT 1 | TRANSMISSION_INDUCED | 133.45
2024 | nonsummer | BISHOP_1_ALAMO | AMBIENT_NOT_DUE_TO_TEMP | 9048.615
2024 | nonsummer | BISHOP_1_ALAMO | PLANT_MAINTENANCE | 184.7
2024 | nonsummer | BISHOP_1_ALAMO | PLANT_TROUBLE | 0
2024 | nonsummer | BISHOP_1_ALAMO | TRANSMISSION_INDUCED | 8.5
2024 | nonsummer | BISHOP_1_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 8687.87
2024 | nonsummer | BISHOP_1_UNITS | PLANT_MAINTENANCE | 0
2024 | nonsummer | BISHOP_1_UNITS | PLANT_TROUBLE | 750.475
2024 | nonsummer | BISHOP_1_UNITS | TRANSMISSION_INDUCED | 26
2024 | nonsummer | BLACK_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 3713.8
2024 | nonsummer | BLACK_7_UNIT 1 | PLANT_MAINTENANCE | 1341.5833
2024 | nonsummer | BLACK_7_UNIT 1 | PLANT_TROUBLE | 400
2024 | nonsummer | BLACK_7_UNIT 1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | BLACK_7_UNIT 2 | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | BLACK_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 3125.0633
2024 | nonsummer | BLACK_7_UNIT 2 | METERING_TELEMETRY | 98.1167
2024 | nonsummer | BLACK_7_UNIT 2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | BLACK_7_UNIT 2 | PLANT_TROUBLE | 535.6233
2024 | nonsummer | BLACK_7_UNIT 2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | BLAST_1_WIND | PLANT_MAINTENANCE | 0
2024 | nonsummer | BLAST_1_WIND | PLANT_TROUBLE | 0
2024 | nonsummer | BLAST_1_WIND | TRANSMISSION_INDUCED | 72.4655
2024 | nonsummer | BLCKBT_2_STONEY | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 62
2024 | nonsummer | BLCKBT_2_STONEY | METERING_TELEMETRY | 31
2024 | nonsummer | BLCKBT_2_STONEY | PLANT_MAINTENANCE | 155
2024 | nonsummer | BLCKBT_2_STONEY | PLANT_TROUBLE | 1159.9167
2024 | nonsummer | BLCKBT_2_STONEY | TRANSMISSION_INDUCED | 6.2
2024 | nonsummer | BLCKWL_6_SOLAR1 | METERING_TELEMETRY | 96
2024 | nonsummer | BLCKWL_6_SOLAR1 | PLANT_TROUBLE | 466.2
2024 | nonsummer | BLCKWL_6_SOLAR1 | TRANSMISSION_INDUCED | 925.8
2024 | nonsummer | BLKCRK_2_GMCBT1 | METERING_TELEMETRY | 345
2024 | nonsummer | BLKCRK_2_GMCBT1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | BLKCRK_2_GMCBT1 | PLANT_TROUBLE | 3839.8863
2024 | nonsummer | BLKCRK_2_GMCBT1 | UNIT_TESTING | 0
2024 | nonsummer | BLKCRK_2_SOLAR1 | PLANT_MAINTENANCE | 56.62
2024 | nonsummer | BLKCRK_2_SOLAR1 | PLANT_TROUBLE | 37.0733
2024 | nonsummer | BLKDIA_2_BDEBT1 | METERING_TELEMETRY | 0
2024 | nonsummer | BLKDIA_2_BDEBT1 | PLANT_MAINTENANCE | 637.05
2024 | nonsummer | BLKDIA_2_BDEBT1 | PLANT_TROUBLE | 1679.6167
2024 | nonsummer | BLKDIA_2_BDEBT1 | UNIT_TESTING | 0
2024 | nonsummer | BLM W_2_COSBT1 | METERING_TELEMETRY | 0
2024 | nonsummer | BLM W_2_COSBT1 | PLANT_MAINTENANCE | 35
2024 | nonsummer | BLM W_2_COSBT1 | PLANT_TROUBLE | 3629.9208
2024 | nonsummer | BLM W_2_COSBT1 | TRANSMISSION_INDUCED | 99.5
2024 | nonsummer | BLM W_2_COSBT1 | UNIT_TESTING | 0
2024 | nonsummer | BLM_2_UNITS | PLANT_TROUBLE | 3195.485
2024 | nonsummer | BLM_2_UNITS | RTU_RIG | 0
2024 | nonsummer | BLM_2_UNITS | TRANSMISSION_INDUCED | 360
2024 | nonsummer | BLVRDE_6_BLVBT1 | PLANT_TROUBLE | 132
2024 | nonsummer | BLVRDE_6_BLVBT1 | TRANSMISSION_INDUCED | 200
2024 | nonsummer | BLYTHE_1_SOLAR1 | METERING_TELEMETRY | 8.3333
2024 | nonsummer | BLYTHE_1_SOLAR1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | BLYTHE_1_SOLAR1 | PLANT_TROUBLE | 899
2024 | nonsummer | BLYTHE_1_SOLAR1 | TRANSMISSION_INDUCED | 84
2024 | nonsummer | BLYTHE_1_SOLAR2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | BLYTHE_1_SOLAR2 | PLANT_TROUBLE | 655
2024 | nonsummer | BLYTHE_1_SOLAR2 | TRANSMISSION_INDUCED | 431.0333
2024 | nonsummer | BNNIEN_7_ALTAPH | AMBIENT_NOT_DUE_TO_TEMP | 736.03
2024 | nonsummer | BNNIEN_7_ALTAPH | PLANT_TROUBLE | 0
2024 | nonsummer | BNNIEN_7_ALTAPH | TRANSMISSION_INDUCED | 180.5333
2024 | nonsummer | BOGUE_1_UNITA1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | BOGUE_1_UNITA1 | AMBIENT_DUE_TO_TEMP | 418.8
2024 | nonsummer | BOGUE_1_UNITA1 | PLANT_TROUBLE | 997.639
2024 | nonsummer | BORDER_6_UNITA1 | METERING_TELEMETRY | 364.7292
2024 | nonsummer | BORDER_6_UNITA1 | PLANT_MAINTENANCE | 3254.375
2024 | nonsummer | BORDER_6_UNITA1 | PLANT_TROUBLE | 291.2708
2024 | nonsummer | BORDER_6_UNITA1 | TRANSMISSION_INDUCED | 51.25
2024 | nonsummer | BOWMN_6_HYDRO | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | BOWMN_6_HYDRO | PLANT_MAINTENANCE | 0
2024 | nonsummer | BOWMN_6_HYDRO | PLANT_TROUBLE | 0
2024 | nonsummer | BOWMN_6_HYDRO | TRANSMISSION_INDUCED | 73.92
2024 | nonsummer | BRDSLD_2_HIWIND | PLANT_MAINTENANCE | 58118.94
2024 | nonsummer | BRDSLD_2_HIWIND | PLANT_TROUBLE | 747
2024 | nonsummer | BRDSLD_2_MTZUM2 | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | BRDSLD_2_MTZUM2 | METERING_TELEMETRY | 0
2024 | nonsummer | BRDSLD_2_MTZUM2 | PLANT_MAINTENANCE | 4870.4217
2024 | nonsummer | BRDSLD_2_MTZUMA | PLANT_MAINTENANCE | 1745.8567
2024 | nonsummer | BRDSLD_2_SHILO1 | PLANT_MAINTENANCE | 1127.025
2024 | nonsummer | BRDSLD_2_SHILO1 | PLANT_TROUBLE | 313
2024 | nonsummer | BRDSLD_2_SHILO2 | PLANT_MAINTENANCE | 4314.8
2024 | nonsummer | BRDSLD_2_SHILO2 | PLANT_TROUBLE | 0
2024 | nonsummer | BRDSLD_2_SHLO3A | PLANT_MAINTENANCE | 2377.5058
2024 | nonsummer | BRDSLD_2_SHLO3B | PLANT_MAINTENANCE | 671.5067
2024 | nonsummer | BREGGO_6_DEGRSL | PLANT_MAINTENANCE | 0
2024 | nonsummer | BREGGO_6_DEGRSL | PLANT_TROUBLE | 31.5
2024 | nonsummer | BREGGO_6_DEGRSL | TRANSMISSION_INDUCED | 311.01
2024 | nonsummer | BREGGO_6_DSEBT1 | TRANSMISSION_INDUCED | 178.7298
2024 | nonsummer | BREGGO_6_SOLAR | PLANT_TROUBLE | 0
2024 | nonsummer | BREGGO_6_SOLAR | TRANSMISSION_INDUCED | 1063.4
2024 | nonsummer | BRODIE_2_WIND | METERING_TELEMETRY | 1020
2024 | nonsummer | BRODIE_2_WIND | PLANT_MAINTENANCE | 8285.4
2024 | nonsummer | BRODIE_2_WIND | PLANT_TROUBLE | 0
2024 | nonsummer | BUCKBL_2_PL1X3 | METERING_TELEMETRY | 0
2024 | nonsummer | BUCKBL_2_PL1X3 | PLANT_MAINTENANCE | 46894.85
2024 | nonsummer | BUCKBL_2_PL1X3 | PLANT_TROUBLE | 17458.0477
2024 | nonsummer | BUCKBL_2_PL1X3 | TRANSMISSION_INDUCED | 17481.5
2024 | nonsummer | BUCKBL_2_PL1X3 | UNIT_TESTING | 2673.8
2024 | nonsummer | BUCKCK_2_HYDRO | TRANSMISSION_INDUCED | 79.2
2024 | nonsummer | BUCKCK_7_OAKFLT | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | BUCKCK_7_OAKFLT | TRANSMISSION_INDUCED | 1378
2024 | nonsummer | BUCKCK_7_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 2036.52
2024 | nonsummer | BUCKCK_7_PL1X2 | METERING_TELEMETRY | 0
2024 | nonsummer | BUCKCK_7_PL1X2 | PLANT_TROUBLE | 2153.8
2024 | nonsummer | BUCKCK_7_PL1X2 | RTU_RIG | 0
2024 | nonsummer | BUCKCK_7_PL1X2 | TRANSITIONAL_LIMITATION | 0
2024 | nonsummer | BUCKCK_7_PL1X2 | TRANSMISSION_INDUCED | 792
2024 | nonsummer | BUCKCK_7_PL1X2 | UNIT_TESTING | 0.135
2024 | nonsummer | BUCKWD_1_NPALM1 | METERING_TELEMETRY | 0
2024 | nonsummer | BUCKWD_1_QF | PLANT_MAINTENANCE | 475.575
2024 | nonsummer | BUCKWD_1_QF | PLANT_TROUBLE | 75
2024 | nonsummer | BUCKWD_7_WINTCV | PLANT_TROUBLE | 13.2
2024 | nonsummer | BURNYF_2_UNIT 1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 438.45
2024 | nonsummer | BURNYF_2_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 25
2024 | nonsummer | BURNYF_2_UNIT 1 | PLANT_MAINTENANCE | 736.209
2024 | nonsummer | BURNYF_2_UNIT 1 | PLANT_TROUBLE | 3394.3828
2024 | nonsummer | BURNYF_2_UNIT 1 | TRANSMISSION_INDUCED | 1943
2024 | nonsummer | BUTTVL_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | BUTTVL_7_UNIT 1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | BUTTVL_7_UNIT 1 | PLANT_TROUBLE | 0
2024 | nonsummer | BUTTVL_7_UNIT 1 | TRANSMISSION_INDUCED | 40.1583
2024 | nonsummer | CABALO_2_M2BSR1 | METERING_TELEMETRY | 900
2024 | nonsummer | CABALO_2_M2BSR1 | PLANT_MAINTENANCE | 200
2024 | nonsummer | CABALO_2_M2BSR1 | PLANT_TROUBLE | 2066.1333
2024 | nonsummer | CABALO_2_M2BSR1 | TRANSMISSION_INDUCED | 250
2024 | nonsummer | CABALO_2_M2WSR2 | PLANT_MAINTENANCE | 1381
2024 | nonsummer | CABALO_2_M2WSR2 | PLANT_TROUBLE | 5563.6867
2024 | nonsummer | CABALO_2_M2WSR2 | TRANSMISSION_INDUCED | 288.3333
2024 | nonsummer | CABLRO_2_CBSBT1 | NEW_GENERATOR_TEST_ENERGY | 13958
2024 | nonsummer | CABZON_1_WINDA1 | PLANT_TROUBLE | 198.85
2024 | nonsummer | CALFTN_2_CFSBT1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | CALFTN_2_CFSBT1 | METERING_TELEMETRY | 180
2024 | nonsummer | CALFTN_2_CFSBT1 | PLANT_MAINTENANCE | 1620
2024 | nonsummer | CALFTN_2_CFSBT1 | PLANT_TROUBLE | 240
2024 | nonsummer | CALFTN_2_CFSBT1 | UNIT_TESTING | 575.6667
2024 | nonsummer | CALFTN_2_SOLAR | PLANT_MAINTENANCE | 0
2024 | nonsummer | CALFTN_2_SOLAR | PLANT_TROUBLE | 0
2024 | nonsummer | CALFTS_2_CFSSR1 | PLANT_TROUBLE | 0
2024 | nonsummer | CALGEN_1_UNITS | PLANT_MAINTENANCE | 400
2024 | nonsummer | CALGEN_1_UNITS | PLANT_TROUBLE | 6082.05
2024 | nonsummer | CALGEN_1_UNITS | TRANSMISSION_INDUCED | 1603.25
2024 | nonsummer | CALPIN_1_AGNEW | AMBIENT_DUE_TO_TEMP | 238.44
2024 | nonsummer | CALPIN_1_AGNEW | PLANT_MAINTENANCE | 3855.6
2024 | nonsummer | CALPIN_1_AGNEW | PLANT_TROUBLE | 693.3333
2024 | nonsummer | CALPIN_1_AGNEW | TRANSITIONAL_LIMITATION | 0
2024 | nonsummer | CALPIN_1_AGNEW | UNIT_TESTING | 0
2024 | nonsummer | CALPSS_6_SOLAR1 | PLANT_TROUBLE | 53.2
2024 | nonsummer | CALPSS_6_SOLAR1 | TRANSMISSION_INDUCED | 1063
2024 | nonsummer | CAMCHE_1_PL1X3 | AMBIENT_NOT_DUE_TO_TEMP | 799.2
2024 | nonsummer | CAMCHE_1_PL1X3 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | CAMDEN_6_RDDBM1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | CAMERN_6_BSPBT1 | TRANSMISSION_INDUCED | 4.6
2024 | nonsummer | CAMERN_6_BSPSR1 | PLANT_TROUBLE | 56.28
2024 | nonsummer | CAMERN_6_BSPSR1 | TRANSMISSION_INDUCED | 8.4
2024 | nonsummer | CAMLOT_2_SOLAR1 | PLANT_MAINTENANCE | 157.5
2024 | nonsummer | CAMPFW_7_FARWST | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 782
2024 | nonsummer | CANTUA_1_SOLAR | METERING_TELEMETRY | 100
2024 | nonsummer | CANTUA_1_SOLAR | PLANT_MAINTENANCE | 100
2024 | nonsummer | CANTUA_1_SOLAR | TRANSMISSION_INDUCED | 124.8333
2024 | nonsummer | CAPWD_1_QF | PLANT_TROUBLE | 12773
2024 | nonsummer | CAPWD_1_QF | RTU_RIG | 0
2024 | nonsummer | CARBOU_7_PL2X3 | AMBIENT_NOT_DUE_TO_TEMP | 6372.6592
2024 | nonsummer | CARBOU_7_PL2X3 | PLANT_MAINTENANCE | 0
2024 | nonsummer | CARBOU_7_PL2X3 | PLANT_TROUBLE | 0
2024 | nonsummer | CARBOU_7_PL2X3 | TRANSMISSION_INDUCED | 49.5833
2024 | nonsummer | CARBOU_7_PL4X5 | AMBIENT_NOT_DUE_TO_TEMP | 877.28
2024 | nonsummer | CARBOU_7_PL4X5 | PLANT_MAINTENANCE | 44650.4833
2024 | nonsummer | CARBOU_7_PL4X5 | PLANT_TROUBLE | 0
2024 | nonsummer | CARBOU_7_PL4X5 | TRANSMISSION_INDUCED | 119.4333
2024 | nonsummer | CARBOU_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 1533.1333
2024 | nonsummer | CARBOU_7_UNIT 1 | PLANT_TROUBLE | 184.4
2024 | nonsummer | CARBOU_7_UNIT 1 | TRANSMISSION_INDUCED | 59.2
2024 | nonsummer | CARLS1_2_CARCT1 | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | CARLS1_2_CARCT1 | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | nonsummer | CARLS1_2_CARCT1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | CARLS1_2_CARCT1 | PLANT_TROUBLE | 4639.075
2024 | nonsummer | CARLS1_2_CARCT1 | TRANSITIONAL_LIMITATION | 0
2024 | nonsummer | CARLS1_2_CARCT1 | UNIT_TESTING | 103
2024 | nonsummer | CARLS2_1_CARCT1 | AMBIENT_DUE_TO_TEMP | 10.48
2024 | nonsummer | CARLS2_1_CARCT1 | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | nonsummer | CARLS2_1_CARCT1 | PLANT_MAINTENANCE | 201.6883
2024 | nonsummer | CARLS2_1_CARCT1 | PLANT_TROUBLE | 163.525
2024 | nonsummer | CASADB_1_CD4GT1 | AMBIENT_DUE_TO_TEMP | 1121.74
2024 | nonsummer | CASADB_1_CD4GT1 | AMBIENT_NOT_DUE_TO_TEMP | 59.7
2024 | nonsummer | CASADB_1_CD4GT1 | PLANT_MAINTENANCE | 236.6133
2024 | nonsummer | CASADB_1_CD4GT1 | PLANT_TROUBLE | 62.81
2024 | nonsummer | CASADB_1_CD4GT1 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 374.16
2024 | nonsummer | CASADB_1_CD4GT1 | TRANSMISSION_INDUCED | 251.5733
2024 | nonsummer | CASCES_6_CESBT1 | METERING_TELEMETRY | 500
2024 | nonsummer | CASCES_6_CESBT1 | PLANT_MAINTENANCE | 478.6
2024 | nonsummer | CASCES_6_CESBT1 | PLANT_TROUBLE | 125.875
2024 | nonsummer | CASCES_6_CESBT1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | CASCES_6_CESBT1 | UNIT_TESTING | 0
2024 | nonsummer | CASCES_6_CESBT2 | NEW_GENERATOR_TEST_ENERGY | 573
2024 | nonsummer | CASCES_6_CESBT2 | PLANT_MAINTENANCE | 120
2024 | nonsummer | CASCES_6_CESBT2 | PLANT_TROUBLE | 0
2024 | nonsummer | CATLNA_2_SOLAR | PLANT_MAINTENANCE | 0
2024 | nonsummer | CATLNA_2_SOLAR | PLANT_TROUBLE | 9.4
2024 | nonsummer | CATLNA_2_SOLAR | TRANSMISSION_INDUCED | 0
2024 | nonsummer | CATLNA_2_SOLAR2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | CATLNA_2_SOLAR2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | CAVLSR_2_BSOLAR | PLANT_MAINTENANCE | 490.6667
2024 | nonsummer | CAVLSR_2_BSOLAR | PLANT_TROUBLE | 20
2024 | nonsummer | CAVLSR_2_BSOLAR | TRANSMISSION_INDUCED | 80
2024 | nonsummer | CAVLSR_2_RSOLAR | PLANT_MAINTENANCE | 2737
2024 | nonsummer | CAVLSR_2_RSOLAR | PLANT_TROUBLE | 136.0267
2024 | nonsummer | CAVLSR_2_RSOLAR | TRANSMISSION_INDUCED | 420
2024 | nonsummer | CAYTNO_2_VASCO | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | CAYTNO_2_VASCO | PLANT_MAINTENANCE | 29.885
2024 | nonsummer | CAYTNO_2_VASCO | PLANT_TROUBLE | 38.3775
2024 | nonsummer | CAYTNO_2_VASCO | TRANSMISSION_INDUCED | 0
2024 | nonsummer | CDWR07_2_GEN | PLANT_TROUBLE | 402.3
2024 | nonsummer | CEDRCK_6_UNIT | TRANSMISSION_INDUCED | 7.7747
2024 | nonsummer | CEDUCR_2_SOLAR1 | PLANT_TROUBLE | 300
2024 | nonsummer | CEDUCR_2_SOLAR4 | PLANT_MAINTENANCE | 0
2024 | nonsummer | CEDUCR_2_SOLAR4 | PLANT_TROUBLE | 318.8333
2024 | nonsummer | CENT40_1_C40SR1 | PLANT_TROUBLE | 6233.65
2024 | nonsummer | CENT40_1_C40SR1 | TRANSMISSION_INDUCED | 5729.3333
2024 | nonsummer | CENTER_2_RHONDO | TRANSMISSION_INDUCED | 9.55
2024 | nonsummer | CENTER_2_SOLAR1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | CENTER_2_SOLAR1 | TRANSMISSION_INDUCED | 36
2024 | nonsummer | CENTER_6_PEAKER | AMBIENT_DUE_TO_TEMP | 0.04
2024 | nonsummer | CENTER_6_PEAKER | METERING_TELEMETRY | 0
2024 | nonsummer | CENTER_6_PEAKER | PLANT_MAINTENANCE | 236.5
2024 | nonsummer | CENTER_6_PEAKER | PLANT_TROUBLE | 1564.8417
2024 | nonsummer | CENTER_6_PEAKER | RTU_RIG | 0
2024 | nonsummer | CENTER_6_PEAKER | TRANSMISSION_INDUCED | 4193.145
2024 | nonsummer | CENTPD_2_BMSSX2 | METERING_TELEMETRY | 11733
2024 | nonsummer | CENTPD_2_BMSSX2 | PLANT_MAINTENANCE | 1341.8
2024 | nonsummer | CENTPD_2_BMSSX2 | PLANT_TROUBLE | 536
2024 | nonsummer | CENTPD_2_BMSSX2 | UNIT_TESTING | 0
2024 | nonsummer | CENTPD_2_BMSX2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 669.3333
2024 | nonsummer | CENTPD_2_BMSX2 | METERING_TELEMETRY | 2323.6333
2024 | nonsummer | CENTPD_2_BMSX2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | CENTPD_2_BMSX2 | PLANT_TROUBLE | 3599.5333
2024 | nonsummer | CENTPD_2_BMSX2 | UNIT_TESTING | 0
2024 | nonsummer | CENTRY_6_PL1X4 | PLANT_MAINTENANCE | 5537.25
2024 | nonsummer | CENTRY_6_PL1X4 | PLANT_TROUBLE | 7757.1
2024 | nonsummer | CENTRY_6_PL1X4 | TRANSMISSION_INDUCED | 57
2024 | nonsummer | CENTRY_6_PL1X4 | UNIT_TESTING | 0
2024 | nonsummer | CHALK_1_UNIT | AMBIENT_DUE_TO_TEMP | 3285.51
2024 | nonsummer | CHALK_1_UNIT | PLANT_TROUBLE | 0
2024 | nonsummer | CHALK_1_UNIT | TRANSMISSION_INDUCED | 20.295
2024 | nonsummer | CHALK_1_UNIT | UNIT_TESTING | 55.2825
2024 | nonsummer | CHARMN_2_PGONG1 | PLANT_MAINTENANCE | 99.35
2024 | nonsummer | CHARMN_2_PGONG1 | PLANT_TROUBLE | 512.9772
2024 | nonsummer | CHESTN_2_CHWBX2 | METERING_TELEMETRY | 0
2024 | nonsummer | CHESTN_2_CHWBX2 | PLANT_MAINTENANCE | 372.6
2024 | nonsummer | CHESTN_2_CHWBX2 | PLANT_TROUBLE | 675
2024 | nonsummer | CHESTN_2_CHWBX2 | RTU_RIG | 0
2024 | nonsummer | CHESTN_2_CHWBX2 | UNIT_TESTING | 0
2024 | nonsummer | CHESTN_2_CHWSX2 | METERING_TELEMETRY | 0
2024 | nonsummer | CHESTN_2_CHWSX2 | PLANT_MAINTENANCE | 269.4
2024 | nonsummer | CHESTN_2_CHWSX2 | PLANT_TROUBLE | 2643.3333
2024 | nonsummer | CHESTN_2_CHWSX2 | UNIT_TESTING | 677.5
2024 | nonsummer | CHEVCO_6_UNIT 1 | TRANSMISSION_INDUCED | 165
2024 | nonsummer | CHEVCO_6_UNIT 2 | TRANSMISSION_INDUCED | 42.5
2024 | nonsummer | CHEVCY_1_UNIT | PLANT_TROUBLE | 0
2024 | nonsummer | CHEVCY_1_UNIT | TRANSMISSION_INDUCED | 174.555
2024 | nonsummer | CHEVMN_2_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | CHEVMN_2_UNITS | PLANT_MAINTENANCE | 15726.15
2024 | nonsummer | CHEVMN_2_UNITS | PLANT_TROUBLE | 19344.85
2024 | nonsummer | CHEVMN_2_UNITS | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 7311.55
2024 | nonsummer | CHICPK_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 25602.7333
2024 | nonsummer | CHICPK_7_UNIT 1 | PLANT_TROUBLE | 3.1667
2024 | nonsummer | CHICPK_7_UNIT 1 | TRANSMISSION_INDUCED | 6.5
2024 | nonsummer | CHILLS_1_SYCENG | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | CHILLS_1_SYCENG | PLANT_MAINTENANCE | 2.55
2024 | nonsummer | CHILLS_1_SYCENG | PLANT_TROUBLE | 24.4167
2024 | nonsummer | CHILLS_7_UNITA1 | AMBIENT_DUE_TO_TEMP | 147.33
2024 | nonsummer | CHILLS_7_UNITA1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | CHILLS_7_UNITA1 | PLANT_TROUBLE | 386.0792
2024 | nonsummer | CHINO_2_APEBT1 | METERING_TELEMETRY | 250.3333
2024 | nonsummer | CHINO_2_APEBT1 | PLANT_MAINTENANCE | 631.3167
2024 | nonsummer | CHINO_2_APEBT1 | PLANT_TROUBLE | 1327.03
2024 | nonsummer | CHINO_2_APEBT1 | UNIT_TESTING | 31.6667
2024 | nonsummer | CHINO_2_PESBT1 | METERING_TELEMETRY | 1047.3333
2024 | nonsummer | CHINO_2_PESBT1 | PLANT_MAINTENANCE | 86.0933
2024 | nonsummer | CHINO_2_PESBT1 | PLANT_TROUBLE | 717.2533
2024 | nonsummer | CHINO_2_PESBT1 | TRANSMISSION_INDUCED | 511
2024 | nonsummer | CHINO_2_PESBT1 | UNIT_TESTING | 201.3333
2024 | nonsummer | CHWCHL_1_AVSSR1 | NEW_GENERATOR_TEST_ENERGY | 146.048
2024 | nonsummer | CHWCHL_1_AVSSR2 | NEW_GENERATOR_TEST_ENERGY | 285.25
2024 | nonsummer | CHWCHL_1_UNIT | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | CHWCHL_1_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | CHWCHL_1_UNIT | PLANT_TROUBLE | 350.84
2024 | nonsummer | CHWCHL_1_UNIT | TRANSMISSION_INDUCED | 486
2024 | nonsummer | CHWCHL_1_UNIT | UNIT_TESTING | 0
2024 | nonsummer | CLINESCO_3_PVDYN | AMBIENT_DUE_TO_TEMP | 399.7
2024 | nonsummer | CLINESCO_3_PVDYN | PLANT_TROUBLE | 284.1
2024 | nonsummer | CLINESCO_3_PVDYN | TRANSITIONAL_LIMITATION | 0.649
2024 | nonsummer | CLINESCO_3_PVDYN | TRANSMISSION_INDUCED | 3096.8053
2024 | nonsummer | CLINESCO_3_WBDYN | AMBIENT_DUE_TO_TEMP | 721.4
2024 | nonsummer | CLINESCO_3_WBDYN | METERING_TELEMETRY | 0
2024 | nonsummer | CLINESCO_3_WBDYN | PLANT_TROUBLE | 0
2024 | nonsummer | CLINESCO_3_WBDYN | TRANSITIONAL_LIMITATION | 0.97133
2024 | nonsummer | CLINESCO_3_WBDYN | TRANSMISSION_INDUCED | 8148.2267
2024 | nonsummer | CLOVER_2_UNIT | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | CLOVER_2_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | CLOVER_2_UNIT | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | nonsummer | CLOVER_2_UNIT | PLANT_TROUBLE | 24.9975
2024 | nonsummer | CLOVER_2_UNIT | TRANSMISSION_INDUCED | 50.3745
2024 | nonsummer | CLRMNT_6_CLEBT1 | METERING_TELEMETRY | 675
2024 | nonsummer | CLRMNT_6_CLEBT1 | PLANT_TROUBLE | 99.4
2024 | nonsummer | CMBLND_2_DS2BT1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 84.9333
2024 | nonsummer | CMBLND_2_DS2BT1 | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | nonsummer | CMBLND_2_DS2BT1 | METERING_TELEMETRY | 11.2667
2024 | nonsummer | CMBLND_2_DS2BT1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | CMBLND_2_DS2BT1 | PLANT_TROUBLE | 1057.3167
2024 | nonsummer | CMBLND_2_DS2BT1 | RTU_RIG | 0
2024 | nonsummer | CMBLND_2_DS2BT1 | UNIT_TESTING | 0
2024 | nonsummer | CMBLND_2_DS2BT2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | CMBLND_2_DS2BT2 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | CMBLND_2_DS2BT2 | METERING_TELEMETRY | 0
2024 | nonsummer | CMBLND_2_DS2BT2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | CMBLND_2_DS2BT2 | PLANT_TROUBLE | 54.1333
2024 | nonsummer | CMBLND_2_DS2BT2 | RTU_RIG | 0
2024 | nonsummer | CMBLND_2_DS2BT2 | UNIT_TESTING | 0
2024 | nonsummer | CMBLND_2_DS2BT3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | CMBLND_2_DS2BT3 | METERING_TELEMETRY | 0
2024 | nonsummer | CMBLND_2_DS2BT3 | PLANT_MAINTENANCE | 400
2024 | nonsummer | CMBLND_2_DS2BT3 | PLANT_TROUBLE | 0
2024 | nonsummer | CMBLND_2_DS2BT3 | RTU_RIG | 0
2024 | nonsummer | CMBLND_2_DS2BT3 | UNIT_TESTING | 0
2024 | nonsummer | CMBLND_2_DS2SR1 | METERING_TELEMETRY | 0
2024 | nonsummer | CMBLND_2_DS2SR1 | PLANT_TROUBLE | 90
2024 | nonsummer | CMBLND_2_DS2SR1 | RTU_RIG | 0
2024 | nonsummer | CMBLND_2_DS2SR1 | UNIT_TESTING | 0
2024 | nonsummer | CMBLND_2_DS2SR2 | METERING_TELEMETRY | 0
2024 | nonsummer | CMBLND_2_DS2SR2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | CMBLND_2_DS2SR2 | PLANT_TROUBLE | 0
2024 | nonsummer | CMBLND_2_DS2SR2 | RTU_RIG | 0
2024 | nonsummer | CMBLND_2_DS2SR2 | UNIT_TESTING | 0
2024 | nonsummer | CMBLND_2_DS2SR3 | METERING_TELEMETRY | 0
2024 | nonsummer | CMBLND_2_DS2SR3 | PLANT_MAINTENANCE | 0
2024 | nonsummer | CMBLND_2_DS2SR3 | RTU_RIG | 0
2024 | nonsummer | CMBLND_2_DS2SR3 | UNIT_TESTING | 0
2024 | nonsummer | CNTNLA_2_SOLAR1 | TRANSMISSION_INDUCED | 41.6667
2024 | nonsummer | CNTNLA_2_SOLAR2 | TRANSMISSION_INDUCED | 15.2
2024 | nonsummer | COCOPP_2_CTG1 | AMBIENT_DUE_TO_TEMP | 3300.59
2024 | nonsummer | COCOPP_2_CTG1 | METERING_TELEMETRY | 0
2024 | nonsummer | COCOPP_2_CTG1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | COCOPP_2_CTG1 | UNIT_TESTING | 0
2024 | nonsummer | COCOPP_2_CTG2 | AMBIENT_DUE_TO_TEMP | 2865.9
2024 | nonsummer | COCOPP_2_CTG2 | METERING_TELEMETRY | 0
2024 | nonsummer | COCOPP_2_CTG2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | COCOPP_2_CTG2 | PLANT_TROUBLE | 0
2024 | nonsummer | COCOPP_2_CTG2 | UNIT_TESTING | 0
2024 | nonsummer | COCOPP_2_CTG3 | AMBIENT_DUE_TO_TEMP | 7582.6695
2024 | nonsummer | COCOPP_2_CTG3 | METERING_TELEMETRY | 48.7573
2024 | nonsummer | COCOPP_2_CTG3 | PLANT_MAINTENANCE | 6411.102
2024 | nonsummer | COCOPP_2_CTG3 | PLANT_TROUBLE | 0
2024 | nonsummer | COCOPP_2_CTG3 | TRANSMISSION_INDUCED | 2692.1013
2024 | nonsummer | COCOPP_2_CTG3 | UNIT_TESTING | 3040.368
2024 | nonsummer | COCOPP_2_CTG4 | AMBIENT_DUE_TO_TEMP | 2785.8447
2024 | nonsummer | COCOPP_2_CTG4 | METERING_TELEMETRY | 3.4048
2024 | nonsummer | COCOPP_2_CTG4 | PLANT_MAINTENANCE | 5285.3897
2024 | nonsummer | COCOPP_2_CTG4 | PLANT_TROUBLE | 0
2024 | nonsummer | COCOPP_2_CTG4 | TRANSMISSION_INDUCED | 2642.1507
2024 | nonsummer | COCOPP_2_CTG4 | UNIT_TESTING | 2962.205
2024 | nonsummer | COGNAT_1_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | COGNAT_1_UNIT | PLANT_MAINTENANCE | 1619.1
2024 | nonsummer | COGNAT_1_UNIT | PLANT_TROUBLE | 2990.6833
2024 | nonsummer | COGNAT_1_UNIT | TRANSMISSION_INDUCED | 144.75
2024 | nonsummer | COGNAT_1_UNIT | UNIT_TESTING | 0
2024 | nonsummer | COLEMN_2_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 478.8317
2024 | nonsummer | COLEMN_2_UNIT | METERING_TELEMETRY | 0
2024 | nonsummer | COLEMN_2_UNIT | PLANT_MAINTENANCE | 0
2024 | nonsummer | COLEMN_2_UNIT | PLANT_TROUBLE | 12.8
2024 | nonsummer | COLGAT_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 26294.75
2024 | nonsummer | COLGAT_7_UNIT 1 | ENVIRONMENTAL_RESTRICTIONS | 794.5
2024 | nonsummer | COLGAT_7_UNIT 1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | COLGAT_7_UNIT 1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | COLGAT_7_UNIT 1 | UNIT_TESTING | 0
2024 | nonsummer | COLGAT_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 21658.1333
2024 | nonsummer | COLGAT_7_UNIT 2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | COLGAT_7_UNIT 2 | PLANT_TROUBLE | 0
2024 | nonsummer | COLGAT_7_UNIT 2 | UNIT_TESTING | 0
2024 | nonsummer | COLGNS_2_CNSSR1 | PLANT_MAINTENANCE | 846.4
2024 | nonsummer | COLGNS_2_CNSSR1 | PLANT_TROUBLE | 15481.69
2024 | nonsummer | COLGNS_2_CNSSR1 | TRANSMISSION_INDUCED | 670
2024 | nonsummer | COLPIN_6_COLLNS | PLANT_MAINTENANCE | 0
2024 | nonsummer | COLPIN_6_COLLNS | PLANT_TROUBLE | 1402.5
2024 | nonsummer | COLPIN_6_COLLNS | TRANSMISSION_INDUCED | 4.07
2024 | nonsummer | COLTON_6_AGUAM1 | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | COLTON_6_AGUAM1 | ENVIRONMENTAL_RESTRICTIONS | 290
2024 | nonsummer | COLTON_6_AGUAM1 | METERING_TELEMETRY | 0
2024 | nonsummer | COLTON_6_AGUAM1 | PLANT_TROUBLE | 0
2024 | nonsummer | COLTON_6_AGUAM1 | UNIT_TESTING | 0
2024 | nonsummer | COLUSA_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 18724.0133
2024 | nonsummer | COLUSA_2_PL1X3 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | COLUSA_2_PL1X3 | PLANT_TROUBLE | 35637.6617
2024 | nonsummer | COLVIL_7_PL1X2 | METERING_TELEMETRY | 0
2024 | nonsummer | COLVIL_7_PL1X2 | PLANT_MAINTENANCE | 10877.4
2024 | nonsummer | COLVIL_7_PL1X2 | PLANT_TROUBLE | 25517.9033
2024 | nonsummer | COLVIL_7_PL1X2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | CONDOR_2_CDRBT1 | METERING_TELEMETRY | 390
2024 | nonsummer | CONDOR_2_CDRBT1 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | nonsummer | CONDOR_2_CDRBT1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | CONDOR_2_CDRBT1 | PLANT_TROUBLE | 2000
2024 | nonsummer | CONDOR_2_CDRBT1 | RTU_RIG | 0
2024 | nonsummer | CONDOR_2_CDRBT1 | TRANSMISSION_INDUCED | 4500
2024 | nonsummer | CONDOR_2_CDRBT1 | UNIT_TESTING | 6000
2024 | nonsummer | CONTRL_1_CASAD1 | PLANT_MAINTENANCE | 15.95
2024 | nonsummer | CONTRL_1_CASAD1 | PLANT_TROUBLE | 83.76
2024 | nonsummer | CONTRL_1_CASAD1 | TRANSMISSION_INDUCED | 22.5958
2024 | nonsummer | CONTRL_1_CASAD2 | AMBIENT_DUE_TO_TEMP | 567.4
2024 | nonsummer | CONTRL_1_CASAD2 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | CONTRL_1_CASAD2 | METERING_TELEMETRY | 0.7
2024 | nonsummer | CONTRL_1_CASAD2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | CONTRL_1_CASAD2 | PLANT_TROUBLE | 116.8833
2024 | nonsummer | CONTRL_1_CASAD2 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 91.8
2024 | nonsummer | CONTRL_1_CASAD2 | TRANSMISSION_INDUCED | 76.3967
2024 | nonsummer | CONTRL_1_CASAD3 | AMBIENT_NOT_DUE_TO_TEMP | 30
2024 | nonsummer | CONTRL_1_CASAD3 | PLANT_MAINTENANCE | 39
2024 | nonsummer | CONTRL_1_CASAD3 | PLANT_TROUBLE | 0
2024 | nonsummer | CONTRL_1_CASAD3 | TRANSMISSION_INDUCED | 56.485
2024 | nonsummer | CONTRL_1_LUNDY | AMBIENT_NOT_DUE_TO_TEMP | 2505.2125
2024 | nonsummer | CONTRL_1_LUNDY | PLANT_MAINTENANCE | 0
2024 | nonsummer | CONTRL_1_LUNDY | PLANT_TROUBLE | 58.3
2024 | nonsummer | CONTRL_1_LUNDY | TRANSMISSION_INDUCED | 7.1667
2024 | nonsummer | CONTRL_1_OXBOW | AMBIENT_DUE_TO_TEMP | 44.3667
2024 | nonsummer | CONTRL_1_OXBOW | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | CONTRL_1_OXBOW | ENVIRONMENTAL_RESTRICTIONS | 7
2024 | nonsummer | CONTRL_1_OXBOW | PLANT_MAINTENANCE | 2908.5
2024 | nonsummer | CONTRL_1_OXBOW | PLANT_TROUBLE | 6278.5333
2024 | nonsummer | CONTRL_1_OXBOW | TRANSMISSION_INDUCED | 892.335
2024 | nonsummer | CONTRL_1_POOLE | AMBIENT_NOT_DUE_TO_TEMP | 4975.97
2024 | nonsummer | CONTRL_1_POOLE | PLANT_TROUBLE | 0
2024 | nonsummer | CONTRL_1_POOLE | TRANSMISSION_INDUCED | 229.1813
2024 | nonsummer | CONTRL_1_QF | TRANSMISSION_INDUCED | 5.35
2024 | nonsummer | CONTRL_1_RUSHCK | AMBIENT_NOT_DUE_TO_TEMP | 2693.45
2024 | nonsummer | CONTRL_1_RUSHCK | METERING_TELEMETRY | 16
2024 | nonsummer | CONTRL_1_RUSHCK | PLANT_MAINTENANCE | 670.45
2024 | nonsummer | CONTRL_1_RUSHCK | TRANSMISSION_INDUCED | 178.4138
2024 | nonsummer | COPMT2_2_SOLAR2 | METERING_TELEMETRY | 0
2024 | nonsummer | COPMT2_2_SOLAR2 | PLANT_TROUBLE | 282.5
2024 | nonsummer | COPMT2_2_SOLAR2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | COPMTN_2_CM10 | TRANSMISSION_INDUCED | 30
2024 | nonsummer | COPMTN_2_SOLAR1 | PLANT_TROUBLE | 200
2024 | nonsummer | COPMTN_2_SOLAR1 | TRANSMISSION_INDUCED | 144
2024 | nonsummer | CORCAN_1_SOLAR1 | PLANT_MAINTENANCE | 60
2024 | nonsummer | CORCAN_1_SOLAR1 | PLANT_TROUBLE | 0
2024 | nonsummer | CORCAN_1_SOLAR2 | PLANT_MAINTENANCE | 11
2024 | nonsummer | CORCAN_1_SOLAR2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | CORONS_6_CLRWTR | PLANT_MAINTENANCE | 0
2024 | nonsummer | CORONS_6_CLRWTR | PLANT_TROUBLE | 0
2024 | nonsummer | CORRAL_6_SJOAQN | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | CORRAL_6_SJOAQN | METERING_TELEMETRY | 0
2024 | nonsummer | CORRAL_6_SJOAQN | PLANT_MAINTENANCE | 79.865
2024 | nonsummer | CORRAL_6_SJOAQN | PLANT_TROUBLE | 96.94
2024 | nonsummer | CORRAL_6_SJOAQN | TRANSMISSION_INDUCED | 115.15
2024 | nonsummer | COTTLE_2_FRNKNH | TRANSMISSION_INDUCED | 0
2024 | nonsummer | COVERD_2_HCKHY1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 571.1
2024 | nonsummer | COVERD_2_HCKHY1 | ENVIRONMENTAL_RESTRICTIONS | 689
2024 | nonsummer | COVERD_2_HCKHY1 | PLANT_TROUBLE | 216.7313
2024 | nonsummer | COVERD_2_HCKHY1 | TRANSMISSION_INDUCED | 68.9
2024 | nonsummer | COVERD_2_MCKHY1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1133.1
2024 | nonsummer | COVERD_2_QFUNTS | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | nonsummer | COVERD_2_QFUNTS | PLANT_TROUBLE | 22.5
2024 | nonsummer | COVERD_2_QFUNTS | TRANSMISSION_INDUCED | 55
2024 | nonsummer | COVERD_2_RCKHY1 | ENVIRONMENTAL_RESTRICTIONS | 212.9
2024 | nonsummer | COVERD_2_RCKHY1 | PLANT_TROUBLE | 2
2024 | nonsummer | COVERD_2_RCKHY1 | TRANSMISSION_INDUCED | 20
2024 | nonsummer | COWCRK_2_UNIT | PLANT_TROUBLE | 2000
2024 | nonsummer | CPVERD_2_SOLAR | METERING_TELEMETRY | 6255
2024 | nonsummer | CPVERD_2_SOLAR | PLANT_MAINTENANCE | 2085
2024 | nonsummer | CPVERD_2_SOLAR | PLANT_TROUBLE | 854
2024 | nonsummer | CPVERD_2_SOLAR | TRANSMISSION_INDUCED | 17375
2024 | nonsummer | CRELMN_6_AABBT1 | PLANT_MAINTENANCE | 8.3817
2024 | nonsummer | CRELMN_6_AABBT1 | PLANT_TROUBLE | 7.05
2024 | nonsummer | CRELMN_6_AABBT1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | CRELMN_6_RAMON1 | PLANT_MAINTENANCE | 11.9333
2024 | nonsummer | CRELMN_6_RAMON1 | PLANT_TROUBLE | 16
2024 | nonsummer | CRELMN_6_RAMON2 | PLANT_MAINTENANCE | 29.8333
2024 | nonsummer | CRELMN_6_RAMON2 | PLANT_TROUBLE | 40
2024 | nonsummer | CRELMN_6_RAMSR3 | PLANT_TROUBLE | 0
2024 | nonsummer | CRELMN_6_RAMSR3 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | CRESTA_7_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 4954.2733
2024 | nonsummer | CRESTA_7_PL1X2 | PLANT_MAINTENANCE | 216.075
2024 | nonsummer | CRESTA_7_PL1X2 | PLANT_TROUBLE | 2866.95
2024 | nonsummer | CRESTA_7_PL1X2 | TRANSITIONAL_LIMITATION | 0
2024 | nonsummer | CRESTA_7_PL1X2 | TRANSMISSION_INDUCED | 287.4667
2024 | nonsummer | CRIMSN_2_CRMBT1 | METERING_TELEMETRY | 1094
2024 | nonsummer | CRIMSN_2_CRMBT1 | PLANT_MAINTENANCE | 7.85
2024 | nonsummer | CRIMSN_2_CRMBT1 | PLANT_TROUBLE | 7084.7333
2024 | nonsummer | CRIMSN_2_CRMBT1 | TRANSMISSION_INDUCED | 5000
2024 | nonsummer | CRIMSN_2_CRMBT1 | UNIT_TESTING | 917.6667
2024 | nonsummer | CRIMSN_2_CRMBT2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 112.8333
2024 | nonsummer | CRIMSN_2_CRMBT2 | METERING_TELEMETRY | 0
2024 | nonsummer | CRIMSN_2_CRMBT2 | PLANT_MAINTENANCE | 295.25
2024 | nonsummer | CRIMSN_2_CRMBT2 | PLANT_TROUBLE | 3829.3917
2024 | nonsummer | CRIMSN_2_CRMBT2 | TRANSMISSION_INDUCED | 3562.5
2024 | nonsummer | CRIMSN_2_CRMBT2 | UNIT_TESTING | 750
2024 | nonsummer | CRNEVL_6_CRNVA | AMBIENT_NOT_DUE_TO_TEMP | 30.6
2024 | nonsummer | CRNEVL_6_CRNVA | PLANT_MAINTENANCE | 274.5
2024 | nonsummer | CRNEVL_6_CRNVA | PLANT_TROUBLE | 0
2024 | nonsummer | CRNEVL_6_CRNVA | TRANSMISSION_INDUCED | 545.4
2024 | nonsummer | CRNEVL_6_SJQN 2 | AMBIENT_NOT_DUE_TO_TEMP | 3392
2024 | nonsummer | CROKET_7_UNIT | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | CROKET_7_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 130
2024 | nonsummer | CROKET_7_UNIT | PLANT_MAINTENANCE | 2378
2024 | nonsummer | CROKET_7_UNIT | UNIT_TESTING | 0
2024 | nonsummer | CRSTWD_6_KUMYAY | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | CRSTWD_6_KUMYAY | AMBIENT_NOT_DUE_TO_TEMP | 190
2024 | nonsummer | CRSTWD_6_KUMYAY | METERING_TELEMETRY | 145.8333
2024 | nonsummer | CRSTWD_6_KUMYAY | PLANT_TROUBLE | 1359
2024 | nonsummer | CRSTWD_6_KUMYAY | TRANSMISSION_INDUCED | 500
2024 | nonsummer | CRWCKS_1_SOLAR1 | METERING_TELEMETRY | 0
2024 | nonsummer | CRWCKS_1_SOLAR1 | PLANT_TROUBLE | 335
2024 | nonsummer | CRWCKS_1_SOLAR1 | TRANSMISSION_INDUCED | 1440
2024 | nonsummer | CSCCOG_1_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 5285
2024 | nonsummer | CSCGNR_1_UNIT 1 | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | CSCGNR_1_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | CSCGNR_1_UNIT 1 | PLANT_MAINTENANCE | 371.25
2024 | nonsummer | CSCGNR_1_UNIT 1 | PLANT_TROUBLE | 2846.25
2024 | nonsummer | CSCGNR_1_UNIT 1 | UNIT_TESTING | 0
2024 | nonsummer | CSCGNR_1_UNIT 2 | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | CSCGNR_1_UNIT 2 | PLANT_MAINTENANCE | 866.6625
2024 | nonsummer | CSCGNR_1_UNIT 2 | PLANT_TROUBLE | 0
2024 | nonsummer | CSCGNR_1_UNIT 2 | UNIT_TESTING | 0
2024 | nonsummer | CSLR4S_2_SOLAR | PLANT_TROUBLE | 82
2024 | nonsummer | CSLR4S_2_SOLAR | TRANSMISSION_INDUCED | 585
2024 | nonsummer | CSTOGA_6_LNDFIL | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2024 | nonsummer | CSTRVL_7_PL1X2 | PLANT_TROUBLE | 249.15
2024 | nonsummer | CSTRVL_7_PL1X2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | CSTRVL_7_QFUNTS | TRANSMISSION_INDUCED | 0
2024 | nonsummer | CUMBIA_1_SOLAR | METERING_TELEMETRY | 14.8833
2024 | nonsummer | CUMBIA_1_SOLAR | PLANT_TROUBLE | 1471.0167
2024 | nonsummer | CUMBIA_1_SOLAR | TRANSMISSION_INDUCED | 44.65
2024 | nonsummer | CUYAMA_6_SB3SB1 | METERING_TELEMETRY | 0
2024 | nonsummer | CUYAMA_6_SB3SB1 | PLANT_TROUBLE | 0
2024 | nonsummer | CUYAMS_6_CUYSR1 | AMBIENT_NOT_DUE_TO_TEMP | 36.6667
2024 | nonsummer | CUYAMS_6_CUYSR1 | METERING_TELEMETRY | 225.3333
2024 | nonsummer | CUYAMS_6_CUYSR1 | PLANT_TROUBLE | 200
2024 | nonsummer | CUYAMS_6_CUYSR1 | TRANSMISSION_INDUCED | 336
2024 | nonsummer | DAIRLD_1_CR1BM1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 270.0833
2024 | nonsummer | DAIRLD_1_CR1BM1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | DAIRLD_1_CR1BM1 | PLANT_MAINTENANCE | 20
2024 | nonsummer | DAIRLD_1_CR1BM1 | PLANT_TROUBLE | 3
2024 | nonsummer | DAVIS_1_SOLAR1 | AMBIENT_NOT_DUE_TO_TEMP | 285
2024 | nonsummer | DAVIS_1_SOLAR1 | METERING_TELEMETRY | 20
2024 | nonsummer | DAVIS_1_SOLAR2 | AMBIENT_NOT_DUE_TO_TEMP | 270
2024 | nonsummer | DAVIS_1_SOLAR2 | METERING_TELEMETRY | 35
2024 | nonsummer | DEADCK_1_UNIT | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1322.6
2024 | nonsummer | DEADCK_1_UNIT | TRANSMISSION_INDUCED | 50.6333
2024 | nonsummer | DEERCR_6_UNIT 1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 2590
2024 | nonsummer | DEERCR_6_UNIT 1 | PLANT_TROUBLE | 73.6167
2024 | nonsummer | DEERCR_6_UNIT 1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | DELAMO_2_ALASB2 | METERING_TELEMETRY | 0
2024 | nonsummer | DELAMO_2_ALASB2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | DELAMO_2_ALASB2 | PLANT_TROUBLE | 400
2024 | nonsummer | DELSUR_6_CREST | METERING_TELEMETRY | 0
2024 | nonsummer | DELSUR_6_CREST | PLANT_TROUBLE | 28.3917
2024 | nonsummer | DELSUR_6_CREST | TRANSMISSION_INDUCED | 0
2024 | nonsummer | DELSUR_6_DRYFRB | PLANT_TROUBLE | 445
2024 | nonsummer | DELSUR_6_SOLAR1 | METERING_TELEMETRY | 136.5
2024 | nonsummer | DELSUR_6_SOLAR1 | PLANT_TROUBLE | 95.7667
2024 | nonsummer | DELSUR_6_SOLAR1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | DELSUR_6_SOLAR4 | PLANT_MAINTENANCE | 0
2024 | nonsummer | DELSUR_6_SOLAR5 | PLANT_MAINTENANCE | 0
2024 | nonsummer | DELTA_2_PL1X4 | AMBIENT_DUE_TO_TEMP | 14258.4
2024 | nonsummer | DELTA_2_PL1X4 | METERING_TELEMETRY | 429.1333
2024 | nonsummer | DELTA_2_PL1X4 | PLANT_MAINTENANCE | 5727.4
2024 | nonsummer | DELTA_2_PL1X4 | PLANT_TROUBLE | 128949.1167
2024 | nonsummer | DELTA_2_PL1X4 | TRANSITIONAL_LIMITATION | 2368.6033
2024 | nonsummer | DELTA_2_PL1X4 | UNIT_TESTING | 329.6
2024 | nonsummer | DEVERS_1_SOLAR | PLANT_MAINTENANCE | 0
2024 | nonsummer | DEVERS_1_SOLAR | TRANSMISSION_INDUCED | 0
2024 | nonsummer | DEVERS_1_SOLAR1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | DEVERS_1_SOLAR1 | PLANT_TROUBLE | 120
2024 | nonsummer | DEVERS_1_SOLAR2 | PLANT_MAINTENANCE | 18
2024 | nonsummer | DEVERS_1_SOLAR2 | PLANT_TROUBLE | 0
2024 | nonsummer | DEVERS_2_DHSPG2 | METERING_TELEMETRY | 21
2024 | nonsummer | DEVERS_2_DHSPG2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | DEVERS_2_DHSPG2 | PLANT_TROUBLE | 42
2024 | nonsummer | DEXZEL_1_UNIT | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 619.35
2024 | nonsummer | DEXZEL_1_UNIT | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | DEXZEL_1_UNIT | PLANT_MAINTENANCE | 3060.05
2024 | nonsummer | DEXZEL_1_UNIT | PLANT_TROUBLE | 997.1872
2024 | nonsummer | DIABLO_7_UNIT 1 | METERING_TELEMETRY | 0
2024 | nonsummer | DIABLO_7_UNIT 1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | DIABLO_7_UNIT 1 | PLANT_TROUBLE | 0
2024 | nonsummer | DIABLO_7_UNIT 2 | PLANT_TROUBLE | 13620
2024 | nonsummer | DISCOV_1_CHEVRN | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | DISCOV_1_CHEVRN | PLANT_MAINTENANCE | 948.8
2024 | nonsummer | DISCOV_1_CHEVRN | PLANT_TROUBLE | 286.6133
2024 | nonsummer | DISCOV_1_CHEVRN | TRANSMISSION_INDUCED | 0
2024 | nonsummer | DIXNLD_1_LNDFL | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | nonsummer | DIXNLD_1_LNDFL | PLANT_MAINTENANCE | 4.8
2024 | nonsummer | DMDVLY_1_UNITS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 1560
2024 | nonsummer | DONNLS_7_UNIT | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 2560
2024 | nonsummer | DONNLS_7_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 112.5
2024 | nonsummer | DONNLS_7_UNIT | PLANT_TROUBLE | 4.5667
2024 | nonsummer | DONNLS_7_UNIT | TRANSMISSION_INDUCED | 10.8333
2024 | nonsummer | DOSMGO_2_NSPIN | TRANSMISSION_INDUCED | 0
2024 | nonsummer | DOSPAL_1_DPSSR1 | TRANSMISSION_INDUCED | 13.5
2024 | nonsummer | DOUBLC_1_UNITS | AMBIENT_DUE_TO_TEMP | 2406.3205
2024 | nonsummer | DOUBLC_1_UNITS | PLANT_TROUBLE | 13456.8643
2024 | nonsummer | DOUBLC_1_UNITS | UNIT_TESTING | 388.5152
2024 | nonsummer | DRACKR_2_D4SR4B | PLANT_MAINTENANCE | 70
2024 | nonsummer | DRACKR_2_D4SR4B | PLANT_TROUBLE | 72.5
2024 | nonsummer | DRACKR_2_DS3SR3 | PLANT_MAINTENANCE | 0
2024 | nonsummer | DRACKR_2_DS3SR3 | PLANT_TROUBLE | 477.505
2024 | nonsummer | DRACKR_2_DS4SR4 | PLANT_MAINTENANCE | 0
2024 | nonsummer | DRACKR_2_DS4SR4 | PLANT_TROUBLE | 8.74
2024 | nonsummer | DRACKR_2_DSUBT1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | DRACKR_2_DSUBT1 | PLANT_TROUBLE | 1836.9635
2024 | nonsummer | DRACKR_2_DSUBT1 | RTU_RIG | 0
2024 | nonsummer | DRACKR_2_DSUBT1 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 358.75
2024 | nonsummer | DRACKR_2_DSUBT2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | DRACKR_2_DSUBT2 | PLANT_TROUBLE | 2995.5308
2024 | nonsummer | DRACKR_2_DSUBT2 | RTU_RIG | 0
2024 | nonsummer | DRACKR_2_DSUBT2 | UNIT_TESTING | 0
2024 | nonsummer | DRACKR_2_DSUBT3 | PLANT_TROUBLE | 1693.032
2024 | nonsummer | DRACKR_2_DSUBT3 | RTU_RIG | 0
2024 | nonsummer | DRACKR_2_DSUBT3 | UNIT_TESTING | 0
2024 | nonsummer | DRACKR_2_DSUBT4 | PLANT_MAINTENANCE | 0
2024 | nonsummer | DRACKR_2_DSUBT4 | PLANT_TROUBLE | 1112.8967
2024 | nonsummer | DRACKR_2_DSUBT4 | RTU_RIG | 0
2024 | nonsummer | DRACKR_2_SOLAR1 | PLANT_TROUBLE | 98
2024 | nonsummer | DRACKR_2_SOLAR2 | PLANT_TROUBLE | 30
2024 | nonsummer | DRACKR_2_SOLAR2 | UNIT_TESTING | 0
2024 | nonsummer | DREWSR_2_BHSSR1 | PLANT_MAINTENANCE | 1782.8747
2024 | nonsummer | DREWSR_2_BHSSR1 | PLANT_TROUBLE | 871.1
2024 | nonsummer | DREWS_6_PL1X4 | METERING_TELEMETRY | 0
2024 | nonsummer | DREWS_6_PL1X4 | PLANT_MAINTENANCE | 3363.75
2024 | nonsummer | DREWS_6_PL1X4 | PLANT_TROUBLE | 1293.75
2024 | nonsummer | DREWS_6_PL1X4 | UNIT_TESTING | 0
2024 | nonsummer | DRUM_7_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 17507.1
2024 | nonsummer | DRUM_7_PL3X4 | AMBIENT_NOT_DUE_TO_TEMP | 19351.0333
2024 | nonsummer | DRUM_7_PL3X4 | PLANT_TROUBLE | 0
2024 | nonsummer | DRUM_7_UNIT 5 | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | DRUM_7_UNIT 5 | AMBIENT_NOT_DUE_TO_TEMP | 23229.8333
2024 | nonsummer | DRUM_7_UNIT 5 | PLANT_TROUBLE | 404
2024 | nonsummer | DSABLA_7_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 10666.2867
2024 | nonsummer | DSABLA_7_UNIT | PLANT_TROUBLE | 0
2024 | nonsummer | DSFLWR_2_W9CSB1 | METERING_TELEMETRY | 0
2024 | nonsummer | DSFLWR_2_W9CSB1 | NEW_GENERATOR_TEST_ENERGY | 371.85
2024 | nonsummer | DSFLWR_2_W9CSB1 | PLANT_MAINTENANCE | 424
2024 | nonsummer | DSFLWR_2_W9CSB1 | PLANT_TROUBLE | 35374
2024 | nonsummer | DSFLWR_2_W9CSB1 | TRANSMISSION_INDUCED | 705.5
2024 | nonsummer | DSFLWR_2_W9CSB2 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | nonsummer | DSFLWR_2_W9CSB2 | PLANT_MAINTENANCE | 772
2024 | nonsummer | DSFLWR_2_W9CSB2 | PLANT_TROUBLE | 24753
2024 | nonsummer | DSFLWR_2_W9CSB2 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2024 | nonsummer | DSFLWR_2_W9CSB2 | TRANSMISSION_INDUCED | 496.8
2024 | nonsummer | DSFLWR_2_WS2SR1 | METERING_TELEMETRY | 110
2024 | nonsummer | DSFLWR_2_WS2SR1 | PLANT_MAINTENANCE | 1814.1667
2024 | nonsummer | DSFLWR_2_WS2SR1 | PLANT_TROUBLE | 7201.3333
2024 | nonsummer | DSFLWR_2_WS2SR1 | TRANSMISSION_INDUCED | 350
2024 | nonsummer | DSFLWR_2_WS2SR1 | UNIT_SUPPORTING_STARTUP | 1323.5
2024 | nonsummer | DSRTHV_2_DH1SR1 | PLANT_TROUBLE | 0
2024 | nonsummer | DSRTHV_2_DH2BT1 | METERING_TELEMETRY | 0
2024 | nonsummer | DSRTHV_2_DH2BT1 | PLANT_MAINTENANCE | 1259.9972
2024 | nonsummer | DSRTHV_2_DH2BT1 | PLANT_TROUBLE | 9617.5153
2024 | nonsummer | DSRTHV_2_DH2SR2 | PLANT_TROUBLE | 1432
2024 | nonsummer | DSRTSL_2_SOLAR1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | DSRTSL_2_SOLAR1 | PLANT_TROUBLE | 6576.85
2024 | nonsummer | DSRTSL_2_SOLAR1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | DSRTSN_2_DS2BX2 | METERING_TELEMETRY | 0
2024 | nonsummer | DSRTSN_2_DS2BX2 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | nonsummer | DSRTSN_2_DS2BX2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | DSRTSN_2_DS2BX2 | PLANT_TROUBLE | 4820.8317
2024 | nonsummer | DSRTSN_2_DS2BX2 | UNIT_TESTING | 0
2024 | nonsummer | DSRTSN_2_DS2X2 | METERING_TELEMETRY | 0
2024 | nonsummer | DSRTSN_2_DS2X2 | PLANT_MAINTENANCE | 225
2024 | nonsummer | DSRTSN_2_DS2X2 | PLANT_TROUBLE | 7967.9858
2024 | nonsummer | DSRTSN_2_DS2X2 | RTU_RIG | 0
2024 | nonsummer | DSRTSN_2_DS2X2 | TRANSMISSION_INDUCED | 141.8333
2024 | nonsummer | DSRTSN_2_DS2X2 | UNIT_TESTING | 0
2024 | nonsummer | DSRTSN_2_SOLAR1 | METERING_TELEMETRY | 0
2024 | nonsummer | DSRTSN_2_SOLAR1 | PLANT_MAINTENANCE | 1706.7733
2024 | nonsummer | DSRTSN_2_SOLAR1 | PLANT_TROUBLE | 52.5
2024 | nonsummer | DSRTSN_2_SOLAR1 | TRANSMISSION_INDUCED | 190
2024 | nonsummer | DSRTSN_2_SOLAR2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | DSRTSN_2_SOLAR2 | PLANT_TROUBLE | 220.248
2024 | nonsummer | DSRTSN_2_SOLAR2 | TRANSMISSION_INDUCED | 158.3333
2024 | nonsummer | DTCHWD_2_BT3WND | PLANT_TROUBLE | 819.875
2024 | nonsummer | DTCHWD_2_BT3WND | TRANSMISSION_INDUCED | 6.75
2024 | nonsummer | DTCHWD_2_BT4WND | PLANT_TROUBLE | 4922.6
2024 | nonsummer | DUANE_1_PL1X3 | AMBIENT_NOT_DUE_TO_TEMP | 3938
2024 | nonsummer | DUANE_1_PL1X3 | PLANT_MAINTENANCE | 2956
2024 | nonsummer | DUANE_1_PL1X3 | PLANT_TROUBLE | 16006.29
2024 | nonsummer | DUANE_1_PL1X3 | UNIT_TESTING | 2651
2024 | nonsummer | DURNMESA_3_WBDYN | AMBIENT_DUE_TO_TEMP | 550.8
2024 | nonsummer | DURNMESA_3_WBDYN | PLANT_TROUBLE | 0
2024 | nonsummer | DURNMESA_3_WBDYN | TRANSITIONAL_LIMITATION | 0
2024 | nonsummer | DURNMESA_3_WBDYN | TRANSMISSION_INDUCED | 4955.674
2024 | nonsummer | DUTCH1_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 7213.1333
2024 | nonsummer | DUTCH1_7_UNIT 1 | PLANT_MAINTENANCE | 12.1
2024 | nonsummer | DUTCH1_7_UNIT 1 | PLANT_TROUBLE | 0
2024 | nonsummer | DUTCH1_7_UNIT 1 | TRANSMISSION_INDUCED | 220
2024 | nonsummer | DUTCH2_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 18317.6
2024 | nonsummer | DUTCH2_7_UNIT 1 | PLANT_TROUBLE | 7.3
2024 | nonsummer | DUTCH2_7_UNIT 1 | TRANSMISSION_INDUCED | 260
2024 | nonsummer | DVLCYN_1_UNITS | ENVIRONMENTAL_RESTRICTIONS | 1411.2167
2024 | nonsummer | DVLCYN_1_UNITS | PLANT_MAINTENANCE | 2318.1667
2024 | nonsummer | DVLCYN_1_UNITS | PLANT_TROUBLE | 4160.75
2024 | nonsummer | DVLCYN_1_UNITS | RTU_RIG | 0
2024 | nonsummer | DVLCYN_1_UNITS | TRANSMISSION_INDUCED | 250
2024 | nonsummer | DVLCYN_1_UNITS | UNIT_TESTING | 151.25
2024 | nonsummer | DYERSM_6_DSWWD1 | ENVIRONMENTAL_RESTRICTIONS | 216.465
2024 | nonsummer | DYERSM_6_DSWWD1 | METERING_TELEMETRY | 18.6667
2024 | nonsummer | DYERSM_6_DSWWD1 | PLANT_MAINTENANCE | 1011.2333
2024 | nonsummer | DYERSM_6_DSWWD1 | PLANT_TROUBLE | 731.49
2024 | nonsummer | DYERSM_6_DSWWD1 | TRANSMISSION_INDUCED | 1598.1383
2024 | nonsummer | DYLAN_2_BMTBT1 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | nonsummer | DYLAN_2_BMTBT1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | DYLAN_2_BMTBT1 | PLANT_TROUBLE | 150
2024 | nonsummer | DYLAN_2_BMTBT1 | TRANSMISSION_INDUCED | 202.2167
2024 | nonsummer | DYLAN_2_BMTBT1 | UNIT_TESTING | 237.5
2024 | nonsummer | EASTWD_7_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | EASTWD_7_UNIT | PLANT_MAINTENANCE | 2000
2024 | nonsummer | EASTWD_7_UNIT | PLANT_TROUBLE | 6016.6667
2024 | nonsummer | EASTWD_7_UNIT | TRANSMISSION_INDUCED | 3133.3333
2024 | nonsummer | EASTWD_7_UNIT | UNIT_TESTING | 0
2024 | nonsummer | EDMONS_2_NSPIN | ENVIRONMENTAL_RESTRICTIONS | 730
2024 | nonsummer | EDMONS_2_NSPIN | PLANT_TROUBLE | 48548
2024 | nonsummer | EDMONS_2_NSPIN | TRANSMISSION_INDUCED | 0
2024 | nonsummer | EDWARD_2_E21SB1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 157.1333
2024 | nonsummer | EDWARD_2_E21SB1 | PLANT_TROUBLE | 19.3667
2024 | nonsummer | EDWARD_2_E23SB1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | EDWARD_2_E23SB1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | EDWARD_2_E23SB1 | PLANT_TROUBLE | 574.4
2024 | nonsummer | EDWARD_2_ES2BT3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 283.2
2024 | nonsummer | EDWARD_2_ES2BT3 | PLANT_TROUBLE | 12271.7333
2024 | nonsummer | EDWARD_2_ESSSB1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 67.99
2024 | nonsummer | EDWARD_2_ESSSB1 | NEW_GENERATOR_TEST_ENERGY | 36099.25
2024 | nonsummer | EDWARD_2_ESSSB1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | EDWARD_2_ESSSB1 | PLANT_TROUBLE | 9423.0467
2024 | nonsummer | EDWARD_2_ESSSB2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | EDWARD_2_ESSSB2 | PLANT_MAINTENANCE | 3601
2024 | nonsummer | EDWARD_2_ESSSB2 | PLANT_TROUBLE | 1800.5833
2024 | nonsummer | EDWARD_2_ESSSB2 | UNIT_TESTING | 725
2024 | nonsummer | EEKTMN_6_SOLAR1 | PLANT_TROUBLE | 685
2024 | nonsummer | ELCABO_5_ECWSCEDYN | AMBIENT_DUE_TO_TEMP | 1513.2333
2024 | nonsummer | ELCABO_5_ECWSCEDYN | AMBIENT_NOT_DUE_TO_TEMP | 845
2024 | nonsummer | ELCABO_5_ECWSCEDYN | ENVIRONMENTAL_RESTRICTIONS | 355.0833
2024 | nonsummer | ELCABO_5_ECWSCEDYN | TRANSITIONAL_LIMITATION | 4515
2024 | nonsummer | ELCABO_5_ECWSCEDYN | TRANSMISSION_INDUCED | 23955.8667
2024 | nonsummer | ELCAJN_6_EB1BT1 | PLANT_MAINTENANCE | 169.5
2024 | nonsummer | ELCAJN_6_EB1BT1 | PLANT_TROUBLE | 401.65
2024 | nonsummer | ELCAJN_6_LM6K | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | ELCAJN_6_LM6K | PLANT_MAINTENANCE | 0
2024 | nonsummer | ELCAJN_6_LM6K | PLANT_TROUBLE | 1086.2583
2024 | nonsummer | ELCAJN_6_UNITA1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | ELCAJN_6_UNITA1 | PLANT_TROUBLE | 1135.5
2024 | nonsummer | ELDORO_7_UNIT 1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 3355
2024 | nonsummer | ELDORO_7_UNIT 1 | PLANT_MAINTENANCE | 38.4
2024 | nonsummer | ELDORO_7_UNIT 1 | PLANT_TROUBLE | 45
2024 | nonsummer | ELDORO_7_UNIT 2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 2475
2024 | nonsummer | ELDORO_7_UNIT 2 | PLANT_MAINTENANCE | 36.95
2024 | nonsummer | ELDORO_7_UNIT 2 | PLANT_TROUBLE | 45
2024 | nonsummer | ELECTR_7_PL1X3 | AMBIENT_NOT_DUE_TO_TEMP | 4938.7867
2024 | nonsummer | ELECTR_7_PL1X3 | METERING_TELEMETRY | 0
2024 | nonsummer | ELECTR_7_PL1X3 | PLANT_MAINTENANCE | 2005
2024 | nonsummer | ELECTR_7_PL1X3 | PLANT_TROUBLE | 0
2024 | nonsummer | ELKCRK_6_STONYG | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 628.0983
2024 | nonsummer | ELKCRK_6_STONYG | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | ELKCRK_6_STONYG | PLANT_TROUBLE | 12.5
2024 | nonsummer | ELKCRK_6_STONYG | TRANSMISSION_INDUCED | 279.3
2024 | nonsummer | ELKHIL_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 18392.7417
2024 | nonsummer | ELKHIL_2_PL1X3 | PLANT_MAINTENANCE | 48537.6983
2024 | nonsummer | ELKHIL_2_PL1X3 | PLANT_TROUBLE | 46194.7833
2024 | nonsummer | ELKHIL_2_PL1X3 | UNIT_TESTING | 0
2024 | nonsummer | ELKHRN_1_EESX3 | METERING_TELEMETRY | 0
2024 | nonsummer | ELKHRN_1_EESX3 | PLANT_MAINTENANCE | 14471.3828
2024 | nonsummer | ELKHRN_1_EESX3 | PLANT_TROUBLE | 817.5942
2024 | nonsummer | ELKHRN_1_EESX3 | UNIT_TESTING | 173.375
2024 | nonsummer | ELLIOT_6_ELIBT1 | METERING_TELEMETRY | 47
2024 | nonsummer | ELLIOT_6_ELIBT1 | PLANT_MAINTENANCE | 155.4
2024 | nonsummer | ELLIOT_6_ELIBT1 | PLANT_TROUBLE | 153.1667
2024 | nonsummer | ELNIDO_1_ECRSR1 | NEW_GENERATOR_TEST_ENERGY | 446.4
2024 | nonsummer | ELSEGN_2_UN1011 | AMBIENT_DUE_TO_TEMP | 3504.1237
2024 | nonsummer | ELSEGN_2_UN1011 | METERING_TELEMETRY | 0
2024 | nonsummer | ELSEGN_2_UN1011 | PLANT_MAINTENANCE | 2445.843
2024 | nonsummer | ELSEGN_2_UN1011 | PLANT_TROUBLE | 9604.62
2024 | nonsummer | ELSEGN_2_UN1011 | TRANSMISSION_INDUCED | 27.431
2024 | nonsummer | ELSEGN_2_UN1011 | UNIT_TESTING | 0
2024 | nonsummer | ELSEGN_2_UN2021 | AMBIENT_DUE_TO_TEMP | 1050.728
2024 | nonsummer | ELSEGN_2_UN2021 | METERING_TELEMETRY | 0
2024 | nonsummer | ELSEGN_2_UN2021 | PLANT_MAINTENANCE | 245.219
2024 | nonsummer | ELSEGN_2_UN2021 | PLANT_TROUBLE | 6856.911
2024 | nonsummer | ELSEGN_2_UN2021 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | ELSEGN_2_UN2021 | UNIT_TESTING | 1326.997
2024 | nonsummer | ENERSJ_2_WIND | PLANT_MAINTENANCE | 0
2024 | nonsummer | ENERSJ_2_WIND | PLANT_TROUBLE | 577.5
2024 | nonsummer | ENERSJ_2_WIND | TRANSMISSION_INDUCED | 0
2024 | nonsummer | ENERSJ_5_ESJWD2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | ENERSJ_5_ESJWD2 | PLANT_TROUBLE | 293.69
2024 | nonsummer | ENERSJ_5_ESJWD2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | ENWIND_2_WIND1 | PLANT_MAINTENANCE | 138.6747
2024 | nonsummer | ENWIND_2_WIND1 | PLANT_TROUBLE | 30.615
2024 | nonsummer | ENWIND_2_WIND2 | PLANT_MAINTENANCE | 764.8
2024 | nonsummer | ENWIND_2_WIND2 | PLANT_TROUBLE | 302.7333
2024 | nonsummer | ESCNDO_6_EB1BT1 | METERING_TELEMETRY | 690.5
2024 | nonsummer | ESCNDO_6_EB1BT1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | ESCNDO_6_EB1BT1 | PLANT_TROUBLE | 3655
2024 | nonsummer | ESCNDO_6_EB2BT2 | METERING_TELEMETRY | 681
2024 | nonsummer | ESCNDO_6_EB2BT2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | ESCNDO_6_EB2BT2 | PLANT_TROUBLE | 3556.9667
2024 | nonsummer | ESCNDO_6_EB3BT3 | METERING_TELEMETRY | 587.5
2024 | nonsummer | ESCNDO_6_EB3BT3 | PLANT_MAINTENANCE | 0
2024 | nonsummer | ESCNDO_6_EB3BT3 | PLANT_TROUBLE | 4238
2024 | nonsummer | ESCNDO_6_PL1X2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 974.2
2024 | nonsummer | ESCNDO_6_PL1X2 | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | ESCNDO_6_PL1X2 | PLANT_MAINTENANCE | 2293.4292
2024 | nonsummer | ESCNDO_6_PL1X2 | PLANT_TROUBLE | 2191.95
2024 | nonsummer | ESCNDO_6_PL1X2 | TRANSMISSION_INDUCED | 12.1775
2024 | nonsummer | ESCNDO_6_PL1X2 | UNIT_TESTING | 0
2024 | nonsummer | ESCNDO_6_UNITB1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 811.3
2024 | nonsummer | ESCNDO_6_UNITB1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | ESCNDO_6_UNITB1 | PLANT_TROUBLE | 12.0833
2024 | nonsummer | ESCNDO_6_UNITB1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | ESCNDO_6_UNITB1 | UNIT_TESTING | 0
2024 | nonsummer | ESCO_6_GLMQF | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 998
2024 | nonsummer | ESCO_6_GLMQF | AMBIENT_DUE_TO_TEMP | 1.31
2024 | nonsummer | ESCO_6_GLMQF | METERING_TELEMETRY | 0
2024 | nonsummer | ESCO_6_GLMQF | PLANT_TROUBLE | 0
2024 | nonsummer | ESNHWR_2_WC1BT1 | METERING_TELEMETRY | 0
2024 | nonsummer | ESNHWR_2_WC1BT1 | PLANT_MAINTENANCE | 49
2024 | nonsummer | ESNHWR_2_WC1BT1 | PLANT_TROUBLE | 0
2024 | nonsummer | ESNHWR_2_WC1BT1 | RTU_RIG | 4.25
2024 | nonsummer | ESNHWR_2_WC1BT1 | UNIT_TESTING | 52.1
2024 | nonsummer | ESQUON_6_LNDFIL | PLANT_MAINTENANCE | 5.32
2024 | nonsummer | ESQUON_6_LNDFIL | PLANT_TROUBLE | 100.485
2024 | nonsummer | ESQUON_6_LNDFIL | TRANSMISSION_INDUCED | 0
2024 | nonsummer | ESTWND_2_OPPWD1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | ESTWND_2_OPPWD1 | PLANT_TROUBLE | 212.3703
2024 | nonsummer | ESTWND_2_OPPWD1 | TRANSMISSION_INDUCED | 28.57
2024 | nonsummer | ETIWND_2_FONTNA | AMBIENT_NOT_DUE_TO_TEMP | 616
2024 | nonsummer | ETIWND_2_FONTNA | PLANT_TROUBLE | 706.18
2024 | nonsummer | ETIWND_2_FONTNA | TRANSMISSION_INDUCED | 4.25
2024 | nonsummer | ETIWND_2_SEPBT1 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | nonsummer | ETIWND_2_SEPBT1 | PLANT_MAINTENANCE | 4445
2024 | nonsummer | ETIWND_2_SEPBT1 | PLANT_TROUBLE | 11924.9167
2024 | nonsummer | ETIWND_2_SEPBT1 | RTU_RIG | 0
2024 | nonsummer | ETIWND_2_SEPBT1 | UNIT_TESTING | 0
2024 | nonsummer | ETIWND_2_UNIT1 | PLANT_MAINTENANCE | 2648.8
2024 | nonsummer | ETIWND_2_UNIT1 | PLANT_TROUBLE | 454.16
2024 | nonsummer | ETIWND_2_UNIT1 | TRANSMISSION_INDUCED | 131.1742
2024 | nonsummer | ETIWND_6_GRPLND | AMBIENT_DUE_TO_TEMP | 12.87
2024 | nonsummer | ETIWND_6_GRPLND | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | ETIWND_6_GRPLND | METERING_TELEMETRY | 0
2024 | nonsummer | ETIWND_6_GRPLND | PLANT_MAINTENANCE | 0
2024 | nonsummer | ETIWND_6_GRPLND | PLANT_TROUBLE | 648.088
2024 | nonsummer | ETIWND_6_GRPLND | TRANSMISSION_INDUCED | 0
2024 | nonsummer | ETIWND_6_INEBT1 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | nonsummer | ETIWND_6_INEBT1 | PLANT_MAINTENANCE | 7509.6667
2024 | nonsummer | ETIWND_6_INEBT1 | PLANT_TROUBLE | 270.5
2024 | nonsummer | ETIWND_6_INEBT1 | UNIT_TESTING | 4620
2024 | nonsummer | EXCHEC_7_UNIT 1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | EXCHEC_7_UNIT 1 | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | EXCHEC_7_UNIT 1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | EXCHEC_7_UNIT 1 | PLANT_TROUBLE | 0
2024 | nonsummer | EXCHEC_7_UNIT 1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | EXCHEC_7_UNIT 1 | UNIT_TESTING | 0
2024 | nonsummer | EXCLSG_1_SOLAR | PLANT_TROUBLE | 70
2024 | nonsummer | FALBRK_6_FESBT1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | FALBRK_6_FESBT1 | METERING_TELEMETRY | 600
2024 | nonsummer | FALBRK_6_FESBT1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | FALBRK_6_FESBT1 | PLANT_TROUBLE | 1060
2024 | nonsummer | FALBRK_6_FESBT1 | TRANSMISSION_INDUCED | 20
2024 | nonsummer | FIFTHS_2_FSSBT | PLANT_MAINTENANCE | 0
2024 | nonsummer | FIFTHS_2_FSSBT | PLANT_TROUBLE | 0
2024 | nonsummer | FIFTHS_2_FSSBT | UNIT_TESTING | 0
2024 | nonsummer | FIFTHS_2_FSSR1 | ENVIRONMENTAL_RESTRICTIONS | 5005
2024 | nonsummer | FIFTHS_2_FSSR1 | PLANT_MAINTENANCE | 67.5
2024 | nonsummer | FIFTHS_2_FSSR1 | PLANT_TROUBLE | 0
2024 | nonsummer | FIFTHS_2_FSSR1 | UNIT_TESTING | 0
2024 | nonsummer | FILIPPI_2_QZSSRX | NEW_GENERATOR_TEST_ENERGY | 15826.8
2024 | nonsummer | FILIPPI_2_QZSSRX | PLANT_TROUBLE | 1683.5
2024 | nonsummer | FILIPPI_2_QZSSRX | UNIT_TESTING | 0
2024 | nonsummer | FLOWD2_2_FPLWND | METERING_TELEMETRY | 0
2024 | nonsummer | FLOWD2_2_FPLWND | PLANT_MAINTENANCE | 4270.315
2024 | nonsummer | FLOWD2_2_FPLWND | PLANT_TROUBLE | 0
2024 | nonsummer | FLOWD2_2_FPLWND | TRANSMISSION_INDUCED | 643.266
2024 | nonsummer | FLOWD_2_RT2WD2 | PLANT_MAINTENANCE | 178.4915
2024 | nonsummer | FLOWD_2_RT2WD2 | PLANT_TROUBLE | 118.535
2024 | nonsummer | FLOWD_2_WIND1 | PLANT_TROUBLE | 0
2024 | nonsummer | FLOWD_2_WIND1 | TRANSMISSION_INDUCED | 17.85
2024 | nonsummer | FMEADO_6_HELLHL | PLANT_MAINTENANCE | 0
2024 | nonsummer | FMEADO_6_HELLHL | PLANT_TROUBLE | 0
2024 | nonsummer | FMEADO_6_HELLHL | TRANSMISSION_INDUCED | 0.12
2024 | nonsummer | FMEADO_7_UNIT | PLANT_MAINTENANCE | 864
2024 | nonsummer | FMEADO_7_UNIT | PLANT_TROUBLE | 868.8
2024 | nonsummer | FMEADO_7_UNIT | TRANSMISSION_INDUCED | 0
2024 | nonsummer | FORBST_7_UNIT 1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | FORBST_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | FORBST_7_UNIT 1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | FORBST_7_UNIT 1 | PLANT_TROUBLE | 187.5
2024 | nonsummer | FORBST_7_UNIT 1 | TRANSMISSION_INDUCED | 23.125
2024 | nonsummer | FORKBU_6_UNIT | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 712.15
2024 | nonsummer | FORKBU_6_UNIT | PLANT_TROUBLE | 53.625
2024 | nonsummer | FORKBU_6_UNIT | TRANSMISSION_INDUCED | 57.6
2024 | nonsummer | FRESHW_1_SOLAR1 | PLANT_TROUBLE | 0
2024 | nonsummer | FRESHW_1_SOLAR1 | TRANSMISSION_INDUCED | 569
2024 | nonsummer | FRIANT_6_UNITS | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2024 | nonsummer | FRIANT_6_UNITS | TRANSMISSION_INDUCED | 0
2024 | nonsummer | FRNTBW_6_SOLAR1 | METERING_TELEMETRY | 76
2024 | nonsummer | FRNTBW_6_SOLAR1 | PLANT_TROUBLE | 200
2024 | nonsummer | FRNTBW_6_SOLAR1 | TRANSMISSION_INDUCED | 635.3333
2024 | nonsummer | FROGTN_1_UTICAA | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | FROGTN_1_UTICAA | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | nonsummer | FROGTN_1_UTICAA | PLANT_MAINTENANCE | 3.15
2024 | nonsummer | FROGTN_1_UTICAA | PLANT_TROUBLE | 3.5467
2024 | nonsummer | FROGTN_1_UTICAA | TRANSMISSION_INDUCED | 0
2024 | nonsummer | FROGTN_1_UTICAM | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | FROGTN_1_UTICAM | PLANT_TROUBLE | 7.44
2024 | nonsummer | FROGTN_1_UTICAM | TRANSMISSION_INDUCED | 11.04
2024 | nonsummer | FTSWRD_6_TRFORK | TRANSMISSION_INDUCED | 65.2
2024 | nonsummer | FTSWRD_7_QFUNTS | TRANSMISSION_INDUCED | 64
2024 | nonsummer | GALE_1_SR3SR3 | METERING_TELEMETRY | 0
2024 | nonsummer | GALE_1_SR3SR3 | PLANT_TROUBLE | 75.9
2024 | nonsummer | GALE_1_SR3SR3 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | GANSO_1_WSTBM1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | GANSO_1_WSTBM1 | PLANT_MAINTENANCE | 5.2333
2024 | nonsummer | GANSO_1_WSTBM1 | PLANT_TROUBLE | 3.1
2024 | nonsummer | GARLND_2_GARBT1 | AMBIENT_NOT_DUE_TO_TEMP | 31.2
2024 | nonsummer | GARLND_2_GARBT1 | METERING_TELEMETRY | 515
2024 | nonsummer | GARLND_2_GARBT1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | GARLND_2_GARBT1 | PLANT_TROUBLE | 11118.9
2024 | nonsummer | GARLND_2_GARBT1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | GARLND_2_GARBT1 | UNIT_TESTING | 309.4667
2024 | nonsummer | GARLND_2_GASLR | METERING_TELEMETRY | 0
2024 | nonsummer | GARLND_2_GASLR | PLANT_MAINTENANCE | 539.76
2024 | nonsummer | GARLND_2_GASLR | PLANT_TROUBLE | 15850.7288
2024 | nonsummer | GARLND_2_GASLR | TRANSMISSION_INDUCED | 0
2024 | nonsummer | GARLND_2_GASLRA | PLANT_MAINTENANCE | 0
2024 | nonsummer | GARLND_2_GASLRA | PLANT_TROUBLE | 262.15
2024 | nonsummer | GARLND_2_GASLRA | TRANSMISSION_INDUCED | 0
2024 | nonsummer | GARLND_2_GASLRA | UNIT_TESTING | 0
2024 | nonsummer | GARNET_1_SOLAR | METERING_TELEMETRY | 0
2024 | nonsummer | GARNET_1_SOLAR | PLANT_MAINTENANCE | 0
2024 | nonsummer | GARNET_1_SOLAR | PLANT_TROUBLE | 100
2024 | nonsummer | GARNET_1_SOLAR2 | PLANT_MAINTENANCE | 8
2024 | nonsummer | GARNET_1_SOLAR2 | PLANT_TROUBLE | 20
2024 | nonsummer | GARNET_1_WIND | PLANT_MAINTENANCE | 5.7
2024 | nonsummer | GARNET_1_WIND | PLANT_TROUBLE | 0
2024 | nonsummer | GARNET_1_WIND | TRANSMISSION_INDUCED | 13.8167
2024 | nonsummer | GARNET_1_WINDS | PLANT_MAINTENANCE | 673.3
2024 | nonsummer | GARNET_1_WINDS | PLANT_TROUBLE | 112.5
2024 | nonsummer | GARNET_1_WINDS | TRANSMISSION_INDUCED | 24
2024 | nonsummer | GARNET_1_WT3WND | PLANT_MAINTENANCE | 0
2024 | nonsummer | GARNET_1_WT3WND | PLANT_TROUBLE | 30
2024 | nonsummer | GARNET_1_WT3WND | TRANSMISSION_INDUCED | 33.7053
2024 | nonsummer | GARNET_2_COAWD2 | PLANT_MAINTENANCE | 4.3
2024 | nonsummer | GARNET_2_COAWD2 | PLANT_TROUBLE | 1458.06
2024 | nonsummer | GARNET_2_HYDRO | AMBIENT_NOT_DUE_TO_TEMP | 150
2024 | nonsummer | GARNET_2_HYDRO | PLANT_MAINTENANCE | 10
2024 | nonsummer | GARNET_2_HYDRO | PLANT_TROUBLE | 65
2024 | nonsummer | GARNET_2_HYDRO | TRANSMISSION_INDUCED | 0
2024 | nonsummer | GARNET_2_WIND1 | PLANT_TROUBLE | 9.9
2024 | nonsummer | GARNET_2_WIND1 | TRANSMISSION_INDUCED | 6.9583
2024 | nonsummer | GARNET_2_WIND2 | METERING_TELEMETRY | 0
2024 | nonsummer | GARNET_2_WIND2 | PLANT_MAINTENANCE | 2051.6908
2024 | nonsummer | GARNET_2_WIND2 | PLANT_TROUBLE | 715.6425
2024 | nonsummer | GARNET_2_WIND3 | PLANT_MAINTENANCE | 0.63
2024 | nonsummer | GARNET_2_WIND3 | PLANT_TROUBLE | 0
2024 | nonsummer | GARNET_2_WIND4 | METERING_TELEMETRY | 294
2024 | nonsummer | GARNET_2_WIND4 | PLANT_MAINTENANCE | 8.7
2024 | nonsummer | GARNET_2_WIND4 | PLANT_TROUBLE | 107.8
2024 | nonsummer | GARNET_2_WIND4 | TRANSMISSION_INDUCED | 20.7512
2024 | nonsummer | GARNET_2_WIND5 | PLANT_TROUBLE | 0
2024 | nonsummer | GASKW1_2_GW1SR1 | METERING_TELEMETRY | 0
2024 | nonsummer | GASKW1_2_GW1SR1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | GASKW1_2_GW1SR1 | PLANT_TROUBLE | 4758.809
2024 | nonsummer | GASKW1_2_GW1SR1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | GASKW1_2_GW2BT1 | METERING_TELEMETRY | 6.9
2024 | nonsummer | GASKW1_2_GW2BT1 | PLANT_MAINTENANCE | 3030.6263
2024 | nonsummer | GASKW1_2_GW2BT1 | PLANT_TROUBLE | 2640.25
2024 | nonsummer | GASKW1_2_GW2SR1 | METERING_TELEMETRY | 130
2024 | nonsummer | GASKW1_2_GW2SR1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | GASKW1_2_GW2SR1 | PLANT_TROUBLE | 2119.3733
2024 | nonsummer | GASKW1_2_GW2SR1 | RTU_RIG | 0
2024 | nonsummer | GASKW1_2_GW2SR2 | METERING_TELEMETRY | 34
2024 | nonsummer | GASKW1_2_GW2SR2 | PLANT_MAINTENANCE | 254.2897
2024 | nonsummer | GASKW1_2_GW2SR2 | PLANT_TROUBLE | 3625
2024 | nonsummer | GASKW1_2_GW3SR1 | METERING_TELEMETRY | 100
2024 | nonsummer | GASKW1_2_GW3SR1 | PLANT_MAINTENANCE | 20
2024 | nonsummer | GASKW1_2_GW3SR1 | PLANT_TROUBLE | 68.35
2024 | nonsummer | GASKW1_2_GW4SR1 | METERING_TELEMETRY | 119.6667
2024 | nonsummer | GASKW1_2_GW4SR1 | PLANT_MAINTENANCE | 20
2024 | nonsummer | GASKW1_2_GW4SR1 | PLANT_TROUBLE | 0
2024 | nonsummer | GASKW1_2_GW5SR1 | METERING_TELEMETRY | 119.6667
2024 | nonsummer | GASKW1_2_GW5SR1 | PLANT_MAINTENANCE | 20
2024 | nonsummer | GASKW1_2_GW5SR1 | PLANT_TROUBLE | 0
2024 | nonsummer | GATES_2_SOLAR | TRANSMISSION_INDUCED | 59.6667
2024 | nonsummer | GATES_2_WSOLAR | METERING_TELEMETRY | 0
2024 | nonsummer | GATEWY_2_GESBT1 | METERING_TELEMETRY | 500
2024 | nonsummer | GATEWY_2_GESBT1 | PLANT_MAINTENANCE | 22268.4
2024 | nonsummer | GATEWY_2_GESBT1 | PLANT_TROUBLE | 52249.45
2024 | nonsummer | GATEWY_2_GESBT1 | TRANSMISSION_INDUCED | 825
2024 | nonsummer | GATEWY_2_GESBT1 | UNIT_TESTING | 1693.3333
2024 | nonsummer | GATWAY_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 45240.0083
2024 | nonsummer | GATWAY_2_PL1X3 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | GATWAY_2_PL1X3 | PLANT_MAINTENANCE | 958.25
2024 | nonsummer | GATWAY_2_PL1X3 | PLANT_TROUBLE | 1480.8167
2024 | nonsummer | GATWAY_2_PL1X3 | UNIT_TESTING | 0
2024 | nonsummer | GENESI_2_STG | AMBIENT_NOT_DUE_TO_TEMP | 13854.1667
2024 | nonsummer | GENESI_2_STG | PLANT_MAINTENANCE | 0
2024 | nonsummer | GENESI_2_STG | PLANT_TROUBLE | 3718.75
2024 | nonsummer | GENESI_2_STG | TRANSMISSION_INDUCED | 0
2024 | nonsummer | GEYS11_7_UNIT11 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 9063.0467
2024 | nonsummer | GEYS11_7_UNIT11 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 4345.07
2024 | nonsummer | GEYS11_7_UNIT11 | PLANT_TROUBLE | 4720.7
2024 | nonsummer | GEYS11_7_UNIT11 | PLANT_TROUBLE | 1697.7967
2024 | nonsummer | GEYS11_7_UNIT11 | TRANSMISSION_INDUCED | 7.2333
2024 | nonsummer | GEYS11_7_UNIT11 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | GEYS12_7_UNIT12 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 14907.5
2024 | nonsummer | GEYS12_7_UNIT12 | PLANT_TROUBLE | 84
2024 | nonsummer | GEYS13_7_UNIT13 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 25177.8
2024 | nonsummer | GEYS13_7_UNIT13 | PLANT_MAINTENANCE | 967.6667
2024 | nonsummer | GEYS13_7_UNIT13 | PLANT_TROUBLE | 3829.95
2024 | nonsummer | GEYS13_7_UNIT13 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | GEYS14_7_UNIT14 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 13354
2024 | nonsummer | GEYS14_7_UNIT14 | PLANT_MAINTENANCE | 1229
2024 | nonsummer | GEYS14_7_UNIT14 | PLANT_TROUBLE | 618.8167
2024 | nonsummer | GEYS16_7_UNIT16 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 15770.7
2024 | nonsummer | GEYS16_7_UNIT16 | PLANT_MAINTENANCE | 956
2024 | nonsummer | GEYS16_7_UNIT16 | PLANT_TROUBLE | 6.4667
2024 | nonsummer | GEYS17_7_UNIT17 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 11823
2024 | nonsummer | GEYS17_7_UNIT17 | PLANT_MAINTENANCE | 0
2024 | nonsummer | GEYS17_7_UNIT17 | PLANT_TROUBLE | 2523.1167
2024 | nonsummer | GEYS18_7_UNIT18 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 33097.7
2024 | nonsummer | GEYS18_7_UNIT18 | PLANT_TROUBLE | 274.7
2024 | nonsummer | GEYS18_7_UNIT18 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | GEYS20_7_UNIT20 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 16375
2024 | nonsummer | GEYS20_7_UNIT20 | PLANT_TROUBLE | 397.5333
2024 | nonsummer | GEYS20_7_UNIT20 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | GIFENS_6_BUGSL1 | METERING_TELEMETRY | 20
2024 | nonsummer | GIFENS_6_BUGSL1 | PLANT_TROUBLE | 40
2024 | nonsummer | GIFENS_6_BUGSL1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | GIFFEN_6_SOLAR | PLANT_TROUBLE | 130
2024 | nonsummer | GIFFEN_6_SOLAR | TRANSMISSION_INDUCED | 0.5
2024 | nonsummer | GIFFEN_6_SOLAR1 | PLANT_TROUBLE | 0.05
2024 | nonsummer | GIFFEN_6_SOLAR1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | GILROY_1_UNIT | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 3600
2024 | nonsummer | GILROY_1_UNIT | AMBIENT_DUE_TO_TEMP | 6094
2024 | nonsummer | GILROY_1_UNIT | PLANT_MAINTENANCE | 600
2024 | nonsummer | GILROY_1_UNIT | PLANT_TROUBLE | 26418
2024 | nonsummer | GILROY_1_UNIT | TRANSMISSION_INDUCED | 0
2024 | nonsummer | GILROY_1_UNIT | UNIT_TESTING | 0
2024 | nonsummer | GILRPP_1_PL1X2 | AMBIENT_DUE_TO_TEMP | 24.5867
2024 | nonsummer | GILRPP_1_PL1X2 | PLANT_TROUBLE | 0
2024 | nonsummer | GILRPP_1_PL1X2 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2024 | nonsummer | GILRPP_1_PL1X2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | GILRPP_1_PL3X4 | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | GILRPP_1_PL3X4 | PLANT_TROUBLE | 0
2024 | nonsummer | GILRPP_1_PL3X4 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | GLDFGR_6_SOLAR1 | PLANT_MAINTENANCE | 160
2024 | nonsummer | GLDFGR_6_SOLAR1 | TRANSMISSION_INDUCED | 34.6667
2024 | nonsummer | GLDFGR_6_SOLAR2 | METERING_TELEMETRY | 37.24
2024 | nonsummer | GLDFGR_6_SOLAR2 | PLANT_MAINTENANCE | 57
2024 | nonsummer | GLDFGR_6_SOLAR2 | PLANT_TROUBLE | 0
2024 | nonsummer | GLDFGR_6_SOLAR2 | TRANSMISSION_INDUCED | 19.38
2024 | nonsummer | GLDTWN_6_COLUM3 | PLANT_MAINTENANCE | 0
2024 | nonsummer | GLDTWN_6_COLUM3 | PLANT_TROUBLE | 0
2024 | nonsummer | GLDTWN_6_SOLAR | PLANT_TROUBLE | 0
2024 | nonsummer | GLNARM_2_UNIT 5 | PLANT_TROUBLE | 65151.9
2024 | nonsummer | GLNARM_7_UNIT 1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | GLNARM_7_UNIT 1 | PLANT_TROUBLE | 0
2024 | nonsummer | GLNARM_7_UNIT 1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | GLNARM_7_UNIT 1 | UNIT_TESTING | 0
2024 | nonsummer | GLNARM_7_UNIT 2 | PLANT_MAINTENANCE | 223.8
2024 | nonsummer | GLNARM_7_UNIT 2 | PLANT_TROUBLE | 338.311
2024 | nonsummer | GLNARM_7_UNIT 2 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2024 | nonsummer | GLNARM_7_UNIT 2 | UNIT_TESTING | 17.531
2024 | nonsummer | GLNARM_7_UNIT 3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | GLNARM_7_UNIT 3 | AMBIENT_DUE_TO_TEMP | 40.6125
2024 | nonsummer | GLNARM_7_UNIT 3 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | GLNARM_7_UNIT 3 | PLANT_MAINTENANCE | 224.15
2024 | nonsummer | GLNARM_7_UNIT 3 | PLANT_TROUBLE | 12.558
2024 | nonsummer | GLNARM_7_UNIT 3 | TRANSMISSION_INDUCED | 19.15
2024 | nonsummer | GLNARM_7_UNIT 3 | UNIT_TESTING | 0
2024 | nonsummer | GLNARM_7_UNIT 4 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | GLNARM_7_UNIT 4 | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | GLNARM_7_UNIT 4 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | GLNARM_7_UNIT 4 | PLANT_MAINTENANCE | 96.152
2024 | nonsummer | GLNARM_7_UNIT 4 | PLANT_TROUBLE | 53.0843
2024 | nonsummer | GLNARM_7_UNIT 4 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | GLNARM_7_UNIT 4 | UNIT_TESTING | 50.595
2024 | nonsummer | GLOW_6_SOLAR | METERING_TELEMETRY | 6.6667
2024 | nonsummer | GLOW_6_SOLAR | PLANT_MAINTENANCE | 200
2024 | nonsummer | GLOW_6_SOLAR | PLANT_TROUBLE | 170.5167
2024 | nonsummer | GOLETA_2_GE2BT3 | METERING_TELEMETRY | 0
2024 | nonsummer | GOLETA_2_GE2BT3 | PLANT_MAINTENANCE | 1022
2024 | nonsummer | GOLETA_2_GE2BT3 | PLANT_TROUBLE | 0
2024 | nonsummer | GOLETA_2_GE2BT3 | UNIT_TESTING | 240
2024 | nonsummer | GOLETA_2_VALBT1 | METERING_TELEMETRY | 50
2024 | nonsummer | GOLETA_2_VALBT1 | PLANT_MAINTENANCE | 26.2917
2024 | nonsummer | GOLETA_2_VALBT1 | PLANT_TROUBLE | 72.875
2024 | nonsummer | GOLETA_2_VALBT1 | TRANSMISSION_INDUCED | 23.1667
2024 | nonsummer | GOLETA_2_VALBT1 | UNIT_TESTING | 56.6667
2024 | nonsummer | GOLETA_6_ELLWOD | PLANT_MAINTENANCE | 6696
2024 | nonsummer | GOLETA_6_ELLWOD | PLANT_TROUBLE | 243
2024 | nonsummer | GOLETA_6_ELLWOD | TRANSMISSION_INDUCED | 0
2024 | nonsummer | GOLETA_6_ELLWOD | UNIT_TESTING | 54
2024 | nonsummer | GOLETA_6_TR2BM2 | AMBIENT_NOT_DUE_TO_TEMP | 339.5293
2024 | nonsummer | GOLETA_6_TR2BM2 | PLANT_MAINTENANCE | 156.215
2024 | nonsummer | GOLETA_6_TR2BM2 | PLANT_TROUBLE | 47.2957
2024 | nonsummer | GOLETA_6_TR2BM2 | TRANSMISSION_INDUCED | 9.95
2024 | nonsummer | GONZLS_6_UNIT | PLANT_MAINTENANCE | 0.284
2024 | nonsummer | GONZLS_6_UNIT | PLANT_TROUBLE | 508.005
2024 | nonsummer | GONZLS_6_UNIT | TRANSMISSION_INDUCED | 17.2293
2024 | nonsummer | GOOSLK_1_SOLAR1 | PLANT_MAINTENANCE | 228
2024 | nonsummer | GOOSLK_1_SOLAR1 | PLANT_TROUBLE | 60
2024 | nonsummer | GOOSLK_1_SOLAR1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | GRADYW_5_GDYWD1 | AMBIENT_DUE_TO_TEMP | 500
2024 | nonsummer | GRADYW_5_GDYWD1 | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | nonsummer | GRADYW_5_GDYWD1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | GRADYW_5_GDYWD1 | PLANT_TROUBLE | 841.6667
2024 | nonsummer | GRADYW_5_GDYWD1 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 5
2024 | nonsummer | GRADYW_5_GDYWD1 | TRANSITIONAL_LIMITATION | 0
2024 | nonsummer | GRADYW_5_GDYWD1 | TRANSMISSION_INDUCED | 11906.4167
2024 | nonsummer | GRIDLY_6_SOLAR | TRANSMISSION_INDUCED | 0
2024 | nonsummer | GRIFFI_2_LSPDYN | PLANT_TROUBLE | 1533.2
2024 | nonsummer | GRIZLY_1_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 2483.35
2024 | nonsummer | GRIZLY_1_UNIT 1 | PLANT_TROUBLE | 2026.66
2024 | nonsummer | GRIZLY_1_UNIT 1 | TRANSMISSION_INDUCED | 2260
2024 | nonsummer | GRNLF1_1_PL1X2 | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | GRNLF1_1_PL1X2 | PLANT_MAINTENANCE | 984
2024 | nonsummer | GRNLF1_1_PL1X2 | PLANT_TROUBLE | 7267.3233
2024 | nonsummer | GRNLF1_1_PL1X2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | GRNLF1_1_PL1X2 | UNIT_TESTING | 0
2024 | nonsummer | GRNLF2_1_UNIT | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | GRNLF2_1_UNIT | PLANT_TROUBLE | 11611.2
2024 | nonsummer | GRNLF2_1_UNIT | RTU_RIG | 738
2024 | nonsummer | GRNLF2_1_UNIT | UNIT_TESTING | 73.8
2024 | nonsummer | GRNVLY_7_SCLAND | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 4.56
2024 | nonsummer | GRNVLY_7_SCLAND | PLANT_MAINTENANCE | 187.2567
2024 | nonsummer | GRNVLY_7_SCLAND | PLANT_TROUBLE | 494.577
2024 | nonsummer | GRNVLY_7_SCLAND | TRANSMISSION_INDUCED | 2.3307
2024 | nonsummer | GRSCRK_6_BGCKWW | AMBIENT_NOT_DUE_TO_TEMP | 535
2024 | nonsummer | GRSCRK_6_BGCKWW | ENVIRONMENTAL_RESTRICTIONS | 50
2024 | nonsummer | GRSCRK_6_BGCKWW | PLANT_MAINTENANCE | 1.3333
2024 | nonsummer | GRSCRK_6_BGCKWW | PLANT_TROUBLE | 28.75
2024 | nonsummer | GRSCRK_6_BGCKWW | TRANSMISSION_INDUCED | 34.1667
2024 | nonsummer | GRZZLY_1_BERKLY | PLANT_MAINTENANCE | 5219.0567
2024 | nonsummer | GRZZLY_1_BERKLY | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2024 | nonsummer | GUERNS_6_HD3BM3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 76.5
2024 | nonsummer | GUERNS_6_HD3BM3 | PLANT_MAINTENANCE | 0
2024 | nonsummer | GUERNS_6_HD3BM3 | PLANT_TROUBLE | 22.3333
2024 | nonsummer | GUERNS_6_SOLAR | PLANT_MAINTENANCE | 0
2024 | nonsummer | GUERNS_6_SOLAR | PLANT_TROUBLE | 8800
2024 | nonsummer | GUERNS_6_SOLAR | TRANSMISSION_INDUCED | 0
2024 | nonsummer | GUERNS_6_VH2BM1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 43.5
2024 | nonsummer | GUERNS_6_VH2BM1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | GUERNS_6_VH2BM1 | PLANT_TROUBLE | 43.3333
2024 | nonsummer | GWFPWR_1_LDCTG1 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | nonsummer | GWFPWR_1_LDCTG2 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | nonsummer | GWFPWR_1_UNITS | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | GWFPWR_1_UNITS | METERING_TELEMETRY | 98.46
2024 | nonsummer | GWFPWR_1_UNITS | OTHER_USE_LIMIT_REACHED | 0
2024 | nonsummer | GWFPWR_1_UNITS | PLANT_MAINTENANCE | 2991.543
2024 | nonsummer | GWFPWR_1_UNITS | PLANT_TROUBLE | 0
2024 | nonsummer | GWFPWR_1_UNITS | TRANSMISSION_INDUCED | 223.176
2024 | nonsummer | GWFPWR_1_UNITS | UNIT_TESTING | 0
2024 | nonsummer | GYS5X6_7_UNITS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 7814.5
2024 | nonsummer | GYS5X6_7_UNITS | PLANT_MAINTENANCE | 0
2024 | nonsummer | GYS5X6_7_UNITS | PLANT_TROUBLE | 25
2024 | nonsummer | GYS5X6_7_UNITS | PLANT_TROUBLE | 41377.2833
2024 | nonsummer | GYS5X6_7_UNITS | TRANSMISSION_INDUCED | 770
2024 | nonsummer | GYS7X8_7_UNITS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 13556.5
2024 | nonsummer | GYS7X8_7_UNITS | PLANT_MAINTENANCE | 1876.98
2024 | nonsummer | GYS7X8_7_UNITS | PLANT_TROUBLE | 9992.4667
2024 | nonsummer | GYS7X8_7_UNITS | TRANSMISSION_INDUCED | 615
2024 | nonsummer | HAASPH_7_PL1X2 | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | HAASPH_7_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 3694.2333
2024 | nonsummer | HAASPH_7_PL1X2 | PLANT_TROUBLE | 360
2024 | nonsummer | HAASPH_7_PL1X2 | TRANSMISSION_INDUCED | 955.2
2024 | nonsummer | HALSEY_6_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | HALSEY_6_UNIT | PLANT_MAINTENANCE | 0
2024 | nonsummer | HALSEY_6_UNIT | PLANT_TROUBLE | 0
2024 | nonsummer | HAMLIN_1_BLDSB1 | METERING_TELEMETRY | 0
2024 | nonsummer | HAMLIN_1_BLDSB1 | NEW_GENERATOR_TEST_ENERGY | 750
2024 | nonsummer | HAMLIN_1_BLDSB1 | PLANT_MAINTENANCE | 260
2024 | nonsummer | HAMLIN_1_BLDSB1 | PLANT_TROUBLE | 34793.6833
2024 | nonsummer | HAMLIN_1_BLDSB1 | RTU_RIG | 0
2024 | nonsummer | HAMLIN_1_BLDSB1 | UNIT_TESTING | 0
2024 | nonsummer | HAMLIN_1_BMSBT2 | METERING_TELEMETRY | 0
2024 | nonsummer | HAMLIN_1_BMSBT2 | NEW_GENERATOR_TEST_ENERGY | 10030
2024 | nonsummer | HAMLIN_1_BMSBT2 | PLANT_TROUBLE | 2388.8333
2024 | nonsummer | HARBGN_7_UNITS | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | HARBGN_7_UNITS | PLANT_MAINTENANCE | 14967.073
2024 | nonsummer | HARBGN_7_UNITS | PLANT_TROUBLE | 11392.12
2024 | nonsummer | HARBGN_7_UNITS | RTU_RIG | 0
2024 | nonsummer | HARBGN_7_UNITS | UNIT_TESTING | 0
2024 | nonsummer | HARDWK_6_STWBM1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 5
2024 | nonsummer | HARDWK_6_STWBM1 | AMBIENT_NOT_DUE_TO_TEMP | 5
2024 | nonsummer | HARDWK_6_STWBM1 | PLANT_MAINTENANCE | 19.75
2024 | nonsummer | HARDWK_6_STWBM1 | PLANT_TROUBLE | 17.05
2024 | nonsummer | HARDWK_6_STWBM1 | UNIT_TESTING | 0.85
2024 | nonsummer | HATCR1_7_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 31.9
2024 | nonsummer | HATCR1_7_UNIT | PLANT_TROUBLE | 0
2024 | nonsummer | HATCR2_7_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 32.5
2024 | nonsummer | HATCR2_7_UNIT | PLANT_MAINTENANCE | 2125
2024 | nonsummer | HATCR2_7_UNIT | PLANT_TROUBLE | 375.5583
2024 | nonsummer | HATCR2_7_UNIT | TRANSMISSION_INDUCED | 127.5
2024 | nonsummer | HATLOS_6_BWDHY1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | HATLOS_6_LSCRK | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 881.05
2024 | nonsummer | HATLOS_6_LSCRK | PLANT_MAINTENANCE | 0
2024 | nonsummer | HATRDG_2_WIND | AMBIENT_DUE_TO_TEMP | 755.25
2024 | nonsummer | HATRDG_2_WIND | AMBIENT_NOT_DUE_TO_TEMP | 156.8667
2024 | nonsummer | HATRDG_2_WIND | ENVIRONMENTAL_RESTRICTIONS | 18.7
2024 | nonsummer | HATRDG_2_WIND | PLANT_MAINTENANCE | 4037.5333
2024 | nonsummer | HATRDG_2_WIND | PLANT_TROUBLE | 693.7333
2024 | nonsummer | HAYPRS_6_HAYHD1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 3065.9767
2024 | nonsummer | HAYPRS_6_HAYHD1 | PLANT_TROUBLE | 635.1
2024 | nonsummer | HAYPRS_6_HAYHD1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | HAYPRS_6_HAYHD2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 4623
2024 | nonsummer | HAYPRS_6_HAYHD2 | PLANT_TROUBLE | 0
2024 | nonsummer | HELMPG_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | HELMPG_7_UNIT 1 | PLANT_MAINTENANCE | 8472.3833
2024 | nonsummer | HELMPG_7_UNIT 1 | PLANT_TROUBLE | 3663
2024 | nonsummer | HELMPG_7_UNIT 1 | TRANSMISSION_INDUCED | 1424.5
2024 | nonsummer | HELMPG_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | HELMPG_7_UNIT 2 | PLANT_MAINTENANCE | 7665.1667
2024 | nonsummer | HELMPG_7_UNIT 2 | TRANSMISSION_INDUCED | 199.5
2024 | nonsummer | HELMPG_7_UNIT 3 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | HELMPG_7_UNIT 3 | PLANT_MAINTENANCE | 7608.6667
2024 | nonsummer | HELMPG_7_UNIT 3 | PLANT_TROUBLE | 2020
2024 | nonsummer | HELMPG_7_UNIT 3 | TRANSMISSION_INDUCED | 189
2024 | nonsummer | HENRTA_6_ACDSR3 | TRANSMISSION_INDUCED | 3
2024 | nonsummer | HENRTA_6_ELCBX2 | METERING_TELEMETRY | 0
2024 | nonsummer | HENRTA_6_ELCTG1 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | nonsummer | HENRTA_6_ELCTG1 | PLANT_MAINTENANCE | 325
2024 | nonsummer | HENRTA_6_ELCTG1 | RIMS_OUTAGE | 2000
2024 | nonsummer | HENRTA_6_ELCTG2 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | nonsummer | HENRTA_6_ELCTG2 | PLANT_MAINTENANCE | 325
2024 | nonsummer | HENRTA_6_ELCTG2 | PLANT_TROUBLE | 0
2024 | nonsummer | HENRTA_6_ELCTG2 | RIMS_OUTAGE | 2000
2024 | nonsummer | HENRTA_6_HDEBT1 | METERING_TELEMETRY | 0
2024 | nonsummer | HENRTA_6_HDEBT1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | HENRTA_6_HDEBT1 | PLANT_TROUBLE | 3097.9667
2024 | nonsummer | HENRTA_6_HDEBT1 | UNIT_TESTING | 0
2024 | nonsummer | HENRTA_6_SOLAR1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | HENRTA_6_SOLAR1 | PLANT_TROUBLE | 7.5
2024 | nonsummer | HENRTA_6_SOLAR1 | TRANSMISSION_INDUCED | 1.5
2024 | nonsummer | HENRTA_6_SOLAR2 | PLANT_TROUBLE | 940
2024 | nonsummer | HENRTA_6_SOLAR2 | TRANSMISSION_INDUCED | 2
2024 | nonsummer | HENRTA_6_UNITA1 | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | HENRTA_6_UNITA1 | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | nonsummer | HENRTA_6_UNITA1 | METERING_TELEMETRY | 0
2024 | nonsummer | HENRTA_6_UNITA1 | OTHER_USE_LIMIT_REACHED | 0
2024 | nonsummer | HENRTA_6_UNITA1 | PLANT_MAINTENANCE | 724.71
2024 | nonsummer | HENRTA_6_UNITA1 | PLANT_TROUBLE | 0
2024 | nonsummer | HENRTA_6_UNITA1 | RIMS_OUTAGE | 6997.2
2024 | nonsummer | HENRTA_6_UNITA1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | HENRTA_6_UNITA1 | UNIT_TESTING | 80.94
2024 | nonsummer | HENRTA_6_UNITA2 | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | HENRTA_6_UNITA2 | OTHER_USE_LIMIT_REACHED | 0
2024 | nonsummer | HENRTA_6_UNITA2 | PLANT_MAINTENANCE | 667.17
2024 | nonsummer | HENRTA_6_UNITA2 | PLANT_TROUBLE | 0
2024 | nonsummer | HENRTA_6_UNITA2 | RIMS_OUTAGE | 6918.8
2024 | nonsummer | HENRTA_6_UNITA2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | HENRTA_6_UNITA2 | UNIT_TESTING | 0
2024 | nonsummer | HENRTS_1_SOLAR | PLANT_MAINTENANCE | 1196.6667
2024 | nonsummer | HENRTS_1_SOLAR | PLANT_TROUBLE | 751.5667
2024 | nonsummer | HENRTS_1_SOLAR | TRANSMISSION_INDUCED | 381.6667
2024 | nonsummer | HERDLN_6_BYHSR1 | METERING_TELEMETRY | 0
2024 | nonsummer | HERDLN_6_BYHSR1 | PLANT_TROUBLE | 77.6667
2024 | nonsummer | HERDLN_6_BYHSR1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | HIDSRT_2_UNITS | AMBIENT_DUE_TO_TEMP | 1303.6
2024 | nonsummer | HIDSRT_2_UNITS | PLANT_MAINTENANCE | 21250
2024 | nonsummer | HIDSRT_2_UNITS | PLANT_TROUBLE | 31406.1167
2024 | nonsummer | HIGGNS_1_COMBIE | PLANT_TROUBLE | 6
2024 | nonsummer | HIGHDS_2_H5SBT1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | HIGHDS_2_H5SBT1 | PLANT_TROUBLE | 6371.8578
2024 | nonsummer | HIGHDS_2_H5SSR1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | HIGHDS_2_H5SSR1 | PLANT_MAINTENANCE | 169.2
2024 | nonsummer | HIGHDS_2_H5SSR1 | PLANT_TROUBLE | 263
2024 | nonsummer | HINSON_6_LBECH1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | HINSON_6_LBECH1 | UNIT_TESTING | 0
2024 | nonsummer | HINSON_6_LBECH2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | HINSON_6_LBECH2 | UNIT_TESTING | 0
2024 | nonsummer | HINSON_6_LBECH3 | PLANT_MAINTENANCE | 28980
2024 | nonsummer | HINSON_6_LBECH3 | PLANT_TROUBLE | 7255.5
2024 | nonsummer | HINSON_6_LBECH4 | PLANT_MAINTENANCE | 0
2024 | nonsummer | HINSON_6_LBECH4 | UNIT_TESTING | 0
2024 | nonsummer | HNTGBH_2_PL1X3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | HNTGBH_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 210.6633
2024 | nonsummer | HNTGBH_2_PL1X3 | PLANT_MAINTENANCE | 190.55
2024 | nonsummer | HNTGBH_2_PL1X3 | PLANT_TROUBLE | 1628.2945
2024 | nonsummer | HNTGBH_2_PL1X3 | UNIT_TESTING | 540.095
2024 | nonsummer | HNTGBH_7_UNIT 2 | ENVIRONMENTAL_RESTRICTIONS | 157328.6815
2024 | nonsummer | HNTGBH_7_UNIT 2 | PLANT_TROUBLE | 0
2024 | nonsummer | HNTGBH_7_UNIT 2 | UNIT_TESTING | 7.1322
2024 | nonsummer | HOLGAT_1_BORAX | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | nonsummer | HOLGAT_1_BORAX | METERING_TELEMETRY | 0
2024 | nonsummer | HOLGAT_1_BORAX | PLANT_MAINTENANCE | 2169
2024 | nonsummer | HOLGAT_1_BORAX | PLANT_TROUBLE | 384.7967
2024 | nonsummer | HOLSTR_1_SOLAR | PLANT_MAINTENANCE | 0
2024 | nonsummer | HOLSTR_1_SOLAR2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | HOOVER_2_MWDPT | AMBIENT_NOT_DUE_TO_TEMP | 130416
2024 | nonsummer | HOOVER_2_MWDPT | METERING_TELEMETRY | 0
2024 | nonsummer | HOOVER_2_MWDPT | PLANT_MAINTENANCE | 0
2024 | nonsummer | HOOVER_2_MWDPT | RTU_RIG | 0
2024 | nonsummer | HOOVER_2_SCEPT | AMBIENT_NOT_DUE_TO_TEMP | 145367.8333
2024 | nonsummer | HOOVER_2_SCEPT | METERING_TELEMETRY | 1
2024 | nonsummer | HOOVER_2_SCEPT | OTHER_USE_LIMIT_REACHED | 9131.1667
2024 | nonsummer | HOOVER_2_VEAPT | AMBIENT_NOT_DUE_TO_TEMP | 7410
2024 | nonsummer | HOOVER_2_VEAPT | PLANT_MAINTENANCE | 0
2024 | nonsummer | HOOV_2_ANAPT | METERING_TELEMETRY | 0
2024 | nonsummer | HOOV_2_ANAPT | PLANT_TROUBLE | 0
2024 | nonsummer | HOOV_2_ANAPT | RTU_RIG | 0
2024 | nonsummer | HOOV_2_ANAPT | UNIT_TESTING | 0
2024 | nonsummer | HUMBPP_1_UNITS3 | AMBIENT_DUE_TO_TEMP | 3644.48
2024 | nonsummer | HUMBPP_1_UNITS3 | AMBIENT_NOT_DUE_TO_TEMP | 406.75
2024 | nonsummer | HUMBPP_1_UNITS3 | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | nonsummer | HUMBPP_1_UNITS3 | PLANT_MAINTENANCE | 894.85
2024 | nonsummer | HUMBPP_1_UNITS3 | PLANT_TROUBLE | 573.5175
2024 | nonsummer | HUMBPP_1_UNITS3 | TRANSMISSION_INDUCED | 619.3447
2024 | nonsummer | HUMBPP_6_UNITS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 325.4
2024 | nonsummer | HUMBPP_6_UNITS | AMBIENT_DUE_TO_TEMP | 13179.9347
2024 | nonsummer | HUMBPP_6_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 1952.4
2024 | nonsummer | HUMBPP_6_UNITS | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | nonsummer | HUMBPP_6_UNITS | PLANT_MAINTENANCE | 965.8957
2024 | nonsummer | HUMBPP_6_UNITS | PLANT_TROUBLE | 326.7558
2024 | nonsummer | HUMBPP_6_UNITS | TRANSMISSION_INDUCED | 537.9947
2024 | nonsummer | HUMBPP_6_UNITS | UNIT_TESTING | 0
2024 | nonsummer | HURON_6_SOLAR | PLANT_TROUBLE | 4023
2024 | nonsummer | HURON_6_SOLAR | TRANSMISSION_INDUCED | 480
2024 | nonsummer | HYTTHM_2_UNITS | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | nonsummer | HYTTHM_2_UNITS | PLANT_MAINTENANCE | 108297.7567
2024 | nonsummer | HYTTHM_2_UNITS | PLANT_TROUBLE | 7554.59
2024 | nonsummer | HYTTHM_2_UNITS | TRANSMISSION_INDUCED | 0
2024 | nonsummer | HYTTHM_2_UNITS | UNIT_TESTING | 5962.9017
2024 | nonsummer | INDIGO_1_UNIT 1 | AMBIENT_DUE_TO_TEMP | 128.5
2024 | nonsummer | INDIGO_1_UNIT 1 | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | nonsummer | INDIGO_1_UNIT 1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | INDIGO_1_UNIT 1 | PLANT_TROUBLE | 226.5
2024 | nonsummer | INDIGO_1_UNIT 1 | TRANSMISSION_INDUCED | 207.5
2024 | nonsummer | INDIGO_1_UNIT 1 | UNIT_TESTING | 0
2024 | nonsummer | INDIGO_1_UNIT 2 | AMBIENT_DUE_TO_TEMP | 249.6
2024 | nonsummer | INDIGO_1_UNIT 2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | INDIGO_1_UNIT 2 | PLANT_TROUBLE | 0
2024 | nonsummer | INDIGO_1_UNIT 2 | TRANSMISSION_INDUCED | 207.5
2024 | nonsummer | INDIGO_1_UNIT 3 | AMBIENT_DUE_TO_TEMP | 268.9
2024 | nonsummer | INDIGO_1_UNIT 3 | PLANT_MAINTENANCE | 0
2024 | nonsummer | INDIGO_1_UNIT 3 | PLANT_TROUBLE | 0
2024 | nonsummer | INDIGO_1_UNIT 3 | TRANSMISSION_INDUCED | 615.2
2024 | nonsummer | INDIGO_1_UNIT 3 | UNIT_TESTING | 0
2024 | nonsummer | INDVLY_1_UNITS | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | nonsummer | INTKEP_2_UNITS | ENVIRONMENTAL_RESTRICTIONS | 35374.0833
2024 | nonsummer | INTKEP_2_UNITS | PLANT_MAINTENANCE | 101902.7833
2024 | nonsummer | INTKEP_2_UNITS | PLANT_TROUBLE | 5579.0667
2024 | nonsummer | INTKEP_2_UNITS | UNIT_TESTING | 122
2024 | nonsummer | INTMNT_3_ANAHEIM | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 78748
2024 | nonsummer | INTMNT_3_ANAHEIM | PLANT_MAINTENANCE | 4244
2024 | nonsummer | INTMNT_3_ANAHEIM | PLANT_TROUBLE | 1708.3333
2024 | nonsummer | INTMNT_3_ANAHEIM | TRANSITIONAL_LIMITATION | 0
2024 | nonsummer | INTMNT_3_ANAHEIM | TRANSMISSION_INDUCED | 11700
2024 | nonsummer | INTMNT_3_ANAHEIM | UNIT_SUPPORTING_STARTUP | 0
2024 | nonsummer | INTMNT_3_ANAHEIM | UNIT_TESTING | 577
2024 | nonsummer | INTMNT_3_PASADENA | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | INTMNT_3_PASADENA | PLANT_MAINTENANCE | 0
2024 | nonsummer | INTMNT_3_PASADENA | PLANT_TROUBLE | 655
2024 | nonsummer | INTMNT_3_PASADENA | TRANSMISSION_INDUCED | 5350
2024 | nonsummer | INTMNT_3_PASADENA | UNIT_TESTING | 287.97
2024 | nonsummer | INTMNT_3_RIVERSIDE | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 23026.88
2024 | nonsummer | INTMNT_3_RIVERSIDE | PLANT_MAINTENANCE | 4760
2024 | nonsummer | INTMNT_3_RIVERSIDE | PLANT_TROUBLE | 795
2024 | nonsummer | INTMNT_3_RIVERSIDE | TRANSMISSION_INDUCED | 0
2024 | nonsummer | INTTRB_6_UNIT | TRANSMISSION_INDUCED | 608.7333
2024 | nonsummer | INYOKN_1_IKSSR1 | NEW_GENERATOR_TEST_ENERGY | 3582
2024 | nonsummer | INYOKN_1_IKSSR1 | UNIT_TESTING | 39.8
2024 | nonsummer | INYOKN_1_IKSSR2 | NEW_GENERATOR_TEST_ENERGY | 2142
2024 | nonsummer | INYOKN_1_IKSSR2 | UNIT_TESTING | 23.8
2024 | nonsummer | IVANPA_1_UNIT1 | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | IVANPA_1_UNIT1 | AMBIENT_NOT_DUE_TO_TEMP | 19836.6
2024 | nonsummer | IVANPA_1_UNIT1 | METERING_TELEMETRY | 130.2
2024 | nonsummer | IVANPA_1_UNIT1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | IVANPA_1_UNIT1 | PLANT_TROUBLE | 252
2024 | nonsummer | IVANPA_1_UNIT1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | IVANPA_1_UNIT2 | AMBIENT_NOT_DUE_TO_TEMP | 1267
2024 | nonsummer | IVANPA_1_UNIT2 | METERING_TELEMETRY | 0
2024 | nonsummer | IVANPA_1_UNIT2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | IVANPA_1_UNIT2 | PLANT_TROUBLE | 2247
2024 | nonsummer | IVANPA_1_UNIT2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | IVANPA_1_UNIT3 | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | IVANPA_1_UNIT3 | AMBIENT_NOT_DUE_TO_TEMP | 25449.55
2024 | nonsummer | IVANPA_1_UNIT3 | METERING_TELEMETRY | 135.2167
2024 | nonsummer | IVANPA_1_UNIT3 | PLANT_MAINTENANCE | 0
2024 | nonsummer | IVANPA_1_UNIT3 | PLANT_TROUBLE | 665
2024 | nonsummer | IVANPA_1_UNIT3 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | IVSLR2_2_SM2SR1 | PLANT_MAINTENANCE | 38.5
2024 | nonsummer | IVSLR2_2_SM2SR1 | PLANT_TROUBLE | 4557.5
2024 | nonsummer | IVSLR2_2_SM2SR1 | TRANSMISSION_INDUCED | 525
2024 | nonsummer | IVSLRP_2_SOLAR1 | PLANT_MAINTENANCE | 25840
2024 | nonsummer | IVSLRP_2_SOLAR1 | PLANT_TROUBLE | 0
2024 | nonsummer | IVSLRP_2_SOLAR1 | TRANSMISSION_INDUCED | 400
2024 | nonsummer | IVWEST_2_SOLAR1 | PLANT_MAINTENANCE | 54
2024 | nonsummer | IVWEST_2_SOLAR1 | PLANT_TROUBLE | 20
2024 | nonsummer | JACMSR_1_JACSR1 | PLANT_MAINTENANCE | 59.6667
2024 | nonsummer | JANCRK_6_RCABT1 | METERING_TELEMETRY | 0
2024 | nonsummer | JANCRK_6_RCABT1 | PLANT_MAINTENANCE | 4.025
2024 | nonsummer | JANCRK_6_RCABT1 | PLANT_TROUBLE | 86.8875
2024 | nonsummer | JANCRK_6_RCABT1 | TRANSITIONAL_LIMITATION | 0
2024 | nonsummer | JANCRK_6_RCABT1 | TRANSMISSION_INDUCED | 35
2024 | nonsummer | JAVASR_1_JAVSR1 | PLANT_MAINTENANCE | 7.65
2024 | nonsummer | JAVASR_1_JAVSR1 | PLANT_TROUBLE | 0
2024 | nonsummer | JAVASR_1_JAVSR1 | TRANSMISSION_INDUCED | 119.025
2024 | nonsummer | JAWBNE_2_NSRWND | METERING_TELEMETRY | 0
2024 | nonsummer | JAWBNE_2_NSRWND | PLANT_MAINTENANCE | 11499.6083
2024 | nonsummer | JAWBNE_2_NSRWND | PLANT_TROUBLE | 4305.2267
2024 | nonsummer | JAWBNE_2_SRWND | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 64
2024 | nonsummer | JAWBNE_2_SRWND | METERING_TELEMETRY | 159
2024 | nonsummer | JAWBNE_2_SRWND | PLANT_MAINTENANCE | 0
2024 | nonsummer | JAWBNE_2_SRWND | PLANT_TROUBLE | 4654.2
2024 | nonsummer | JAWBNE_2_SRWWD2 | METERING_TELEMETRY | 0
2024 | nonsummer | JAWBNE_2_SRWWD2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | JAWBNE_2_SRWWD2 | PLANT_TROUBLE | 3707.175
2024 | nonsummer | JAYNE_6_WLSLR | AMBIENT_DUE_TO_TEMP | 70
2024 | nonsummer | JAYNE_6_WLSLR | PLANT_TROUBLE | 45
2024 | nonsummer | JAYNE_6_WLSLR | TRANSMISSION_INDUCED | 72
2024 | nonsummer | JOANEC_2_ST3BT3 | PLANT_TROUBLE | 99.3333
2024 | nonsummer | JOANEC_2_ST3BT3 | RTU_RIG | 0
2024 | nonsummer | JOANEC_2_ST3BT3 | UNIT_TESTING | 0
2024 | nonsummer | JOANEC_2_STABT1 | PLANT_MAINTENANCE | 420
2024 | nonsummer | JOANEC_2_STABT1 | PLANT_TROUBLE | 578.3333
2024 | nonsummer | JOANEC_2_STABT1 | UNIT_TESTING | 0
2024 | nonsummer | JOANEC_2_STABT2 | METERING_TELEMETRY | 0
2024 | nonsummer | JOANEC_2_STABT2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | JOANEC_2_STABT2 | PLANT_TROUBLE | 2.3333
2024 | nonsummer | JOHANN_2_JOSBT1 | METERING_TELEMETRY | 0
2024 | nonsummer | JOHANN_2_JOSBT1 | PLANT_MAINTENANCE | 880.8
2024 | nonsummer | JOHANN_2_JOSBT1 | PLANT_TROUBLE | 1296.05
2024 | nonsummer | JOHANN_2_JOSBT1 | RTU_RIG | 0
2024 | nonsummer | JOHANN_2_JOSBT1 | TRANSMISSION_INDUCED | 59.6667
2024 | nonsummer | JOHANN_2_JOSBT1 | UNIT_TESTING | 0
2024 | nonsummer | JOHANN_2_JOSBT2 | PLANT_MAINTENANCE | 127.8333
2024 | nonsummer | JOHANN_2_JOSBT2 | PLANT_TROUBLE | 391.9667
2024 | nonsummer | JOHANN_2_JOSBT2 | RTU_RIG | 0
2024 | nonsummer | JOHANN_2_JOSBT2 | TRANSMISSION_INDUCED | 52.1667
2024 | nonsummer | JOHANN_2_JOSBT2 | UNIT_TESTING | 10
2024 | nonsummer | JOHANN_2_OCEBT2 | PLANT_MAINTENANCE | 55.6333
2024 | nonsummer | JOHANN_2_OCEBT2 | PLANT_TROUBLE | 2807.6833
2024 | nonsummer | JOHANN_2_OCEBT2 | TRANSMISSION_INDUCED | 21.6
2024 | nonsummer | JOHANN_2_OCEBT2 | UNIT_TESTING | 0
2024 | nonsummer | JOHANN_2_OCEBT3 | METERING_TELEMETRY | 0
2024 | nonsummer | JOHANN_2_OCEBT3 | PLANT_MAINTENANCE | 27.5
2024 | nonsummer | JOHANN_2_OCEBT3 | PLANT_TROUBLE | 1865.3
2024 | nonsummer | JOHANN_2_OCEBT3 | TRANSMISSION_INDUCED | 11.3
2024 | nonsummer | JOHANN_2_OCEBT3 | UNIT_TESTING | 22
2024 | nonsummer | JOHANN_2_T1BBT1 | PLANT_TROUBLE | 0
2024 | nonsummer | JOHANN_2_T1BBT1 | UNIT_TESTING | 180.6
2024 | nonsummer | KANSAS_6_SOLAR | AMBIENT_NOT_DUE_TO_TEMP | 10
2024 | nonsummer | KANSAS_6_SOLAR | METERING_TELEMETRY | 0
2024 | nonsummer | KANSAS_6_SOLAR | PLANT_TROUBLE | 2550.5
2024 | nonsummer | KANSAS_6_SOLAR | TRANSMISSION_INDUCED | 600
2024 | nonsummer | KEARNY_6_NESBT1 | METERING_TELEMETRY | 0
2024 | nonsummer | KEARNY_6_NESBT1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | KEARNY_6_NESBT1 | PLANT_TROUBLE | 191.3333
2024 | nonsummer | KEARNY_6_SESBT2 | PLANT_MAINTENANCE | 50
2024 | nonsummer | KEARNY_6_SESBT2 | PLANT_TROUBLE | 736.6667
2024 | nonsummer | KEARNY_6_SESBT2 | UNIT_TESTING | 400
2024 | nonsummer | KEKAWK_6_UNIT | PLANT_TROUBLE | 5830
2024 | nonsummer | KEKAWK_6_UNIT | TRANSMISSION_INDUCED | 0
2024 | nonsummer | KELSO_2_UNITS | AMBIENT_DUE_TO_TEMP | 1935.76
2024 | nonsummer | KELSO_2_UNITS | PLANT_MAINTENANCE | 26221.8
2024 | nonsummer | KELSO_2_UNITS | PLANT_TROUBLE | 64.7558
2024 | nonsummer | KELSO_2_UNITS | UNIT_TESTING | 0
2024 | nonsummer | KELYRG_6_UNIT | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | KELYRG_6_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | KELYRG_6_UNIT | PLANT_TROUBLE | 0
2024 | nonsummer | KELYRG_6_UNIT | TRANSMISSION_INDUCED | 0
2024 | nonsummer | KERKH2_7_UNIT 1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | KERKH2_7_UNIT 1 | AMBIENT_DUE_TO_TEMP | 554.8555
2024 | nonsummer | KERKH2_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 21375.2542
2024 | nonsummer | KERKH2_7_UNIT 1 | PLANT_MAINTENANCE | 769.5
2024 | nonsummer | KERKH2_7_UNIT 1 | PLANT_TROUBLE | 307.8
2024 | nonsummer | KERKH2_7_UNIT 1 | TRANSITIONAL_LIMITATION | 0
2024 | nonsummer | KERKH2_7_UNIT 1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | KERKH2_7_UNIT 1 | UNIT_TESTING | 0
2024 | nonsummer | KERMAN_6_SOLAR2 | PLANT_TROUBLE | 798.75
2024 | nonsummer | KERNEY_6_FCSSR1 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | nonsummer | KERNEY_6_FCSSR1 | PLANT_TROUBLE | 410.9167
2024 | nonsummer | KERNFT_1_UNITS | AMBIENT_DUE_TO_TEMP | 1905.2367
2024 | nonsummer | KERNFT_1_UNITS | PLANT_TROUBLE | 1186.3533
2024 | nonsummer | KERNFT_1_UNITS | RTU_RIG | 0
2024 | nonsummer | KERNFT_1_UNITS | UNIT_TESTING | 713.0267
2024 | nonsummer | KERNRG_1_UNITS | PLANT_MAINTENANCE | 259.4133
2024 | nonsummer | KERNRG_1_UNITS | PLANT_TROUBLE | 630.4133
2024 | nonsummer | KERRGN_1_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 2914.5
2024 | nonsummer | KERRGN_1_UNIT 1 | PLANT_MAINTENANCE | 152
2024 | nonsummer | KERRGN_1_UNIT 1 | PLANT_TROUBLE | 0
2024 | nonsummer | KERRGN_1_UNIT 1 | TRANSMISSION_INDUCED | 24.5333
2024 | nonsummer | KINGCO_1_KINGBR | PLANT_TROUBLE | 135.875
2024 | nonsummer | KINGCO_1_KINGBR | TRANSMISSION_INDUCED | 862.5
2024 | nonsummer | KINGRV_7_UNIT 1 | AMBIENT_DUE_TO_TEMP | 17.2667
2024 | nonsummer | KINGRV_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 2156.7033
2024 | nonsummer | KINGRV_7_UNIT 1 | PLANT_TROUBLE | 17.71
2024 | nonsummer | KINGRV_7_UNIT 1 | TRANSMISSION_INDUCED | 56.32
2024 | nonsummer | KIRKER_7_KELCYN | PLANT_MAINTENANCE | 101.32
2024 | nonsummer | KIRKER_7_KELCYN | PLANT_TROUBLE | 686.9278
2024 | nonsummer | KIRKER_7_KELCYN | TRANSMISSION_INDUCED | 0
2024 | nonsummer | KNGBRD_2_SOLAR1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 30
2024 | nonsummer | KNGBRD_2_SOLAR1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | KNGBRD_2_SOLAR1 | PLANT_TROUBLE | 905
2024 | nonsummer | KNGBRD_2_SOLAR2 | PLANT_TROUBLE | 1055
2024 | nonsummer | KNGCTY_6_UNITA1 | AMBIENT_DUE_TO_TEMP | 209
2024 | nonsummer | KNGCTY_6_UNITA1 | PLANT_TROUBLE | 237.7033
2024 | nonsummer | KNGCTY_6_UNITA1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | KNTSTH_6_SOLAR | PLANT_MAINTENANCE | 57.6667
2024 | nonsummer | KNTSTH_6_SOLAR | PLANT_TROUBLE | 160.2995
2024 | nonsummer | KNTSTH_6_SOLAR | TRANSMISSION_INDUCED | 100
2024 | nonsummer | KNTSTH_6_WALSR1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | KNTSTH_6_WALSR1 | PLANT_TROUBLE | 198.8
2024 | nonsummer | KNTSTH_6_WALSR1 | TRANSMISSION_INDUCED | 59.64
2024 | nonsummer | KNTSTH_6_WALSR1 | UNIT_TESTING | 0
2024 | nonsummer | KRAMER_1_R1BX3 | METERING_TELEMETRY | 675
2024 | nonsummer | KRAMER_1_R1BX3 | PLANT_MAINTENANCE | 40
2024 | nonsummer | KRAMER_1_R1BX3 | PLANT_TROUBLE | 3938.0833
2024 | nonsummer | KRAMER_1_R1BX3 | TRANSMISSION_INDUCED | 5078.75
2024 | nonsummer | KRAMER_1_R1BX3 | UNIT_TESTING | 375
2024 | nonsummer | KRAMER_1_R1PX3 | METERING_TELEMETRY | 360
2024 | nonsummer | KRAMER_1_R1PX3 | PLANT_TROUBLE | 389
2024 | nonsummer | KRAMER_1_R1PX3 | TRANSMISSION_INDUCED | 6094.5
2024 | nonsummer | KRAMER_1_R1PX3 | UNIT_TESTING | 0
2024 | nonsummer | KRAMER_1_R2BX2 | METERING_TELEMETRY | 52.6667
2024 | nonsummer | KRAMER_1_R2BX2 | PLANT_MAINTENANCE | 38
2024 | nonsummer | KRAMER_1_R2BX2 | PLANT_TROUBLE | 568.726
2024 | nonsummer | KRAMER_1_R2BX2 | UNIT_TESTING | 40
2024 | nonsummer | KRAMER_1_R2PX2 | METERING_TELEMETRY | 0
2024 | nonsummer | KRAMER_1_R2PX2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | KRAMER_1_R2PX2 | PLANT_TROUBLE | 144
2024 | nonsummer | KRAMER_2_SEGS 9 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | KRAMER_2_SEGS 9 | PLANT_TROUBLE | 12655.6667
2024 | nonsummer | KRAMER_2_SEGS 9 | TRANSMISSION_INDUCED | 33.3333
2024 | nonsummer | KRNCNY_6_UNIT | PLANT_MAINTENANCE | 0
2024 | nonsummer | KRNCNY_6_UNIT | PLANT_TROUBLE | 495.55
2024 | nonsummer | KRNCNY_6_UNIT | TRANSMISSION_INDUCED | 0
2024 | nonsummer | KYCORA_6_KMSBT1 | PLANT_MAINTENANCE | 18.4167
2024 | nonsummer | KYCORA_6_KMSBT1 | PLANT_TROUBLE | 0
2024 | nonsummer | KYCORA_6_KMSBT1 | TRANSMISSION_INDUCED | 15
2024 | nonsummer | LACIEN_2_VENICE | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 2189
2024 | nonsummer | LAGBEL_2_CBPBT1 | METERING_TELEMETRY | 0
2024 | nonsummer | LAGBEL_2_CBPBT1 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | nonsummer | LAGBEL_2_CBPBT1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | LAGBEL_2_CBPBT1 | PLANT_TROUBLE | 1211.6333
2024 | nonsummer | LAMONT_1_SOLAR1 | PLANT_MAINTENANCE | 360
2024 | nonsummer | LAMONT_1_SOLAR1 | PLANT_TROUBLE | 720
2024 | nonsummer | LAMONT_1_SOLAR1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | LAMONT_1_SOLAR2 | PLANT_MAINTENANCE | 131.4667
2024 | nonsummer | LAMONT_1_SOLAR2 | PLANT_TROUBLE | 1905.6967
2024 | nonsummer | LAMONT_1_SOLAR2 | TRANSMISSION_INDUCED | 74.6533
2024 | nonsummer | LAMONT_1_SOLAR3 | PLANT_MAINTENANCE | 51.2
2024 | nonsummer | LAMONT_1_SOLAR3 | PLANT_TROUBLE | 3259.5832
2024 | nonsummer | LAMONT_1_SOLAR3 | TRANSMISSION_INDUCED | 6
2024 | nonsummer | LAMONT_1_SOLAR4 | METERING_TELEMETRY | 0
2024 | nonsummer | LAMONT_1_SOLAR4 | PLANT_MAINTENANCE | 79.98
2024 | nonsummer | LAMONT_1_SOLAR4 | PLANT_TROUBLE | 4518.6167
2024 | nonsummer | LAMONT_1_SOLAR4 | TRANSMISSION_INDUCED | 22.2167
2024 | nonsummer | LAMONT_1_SOLAR5 | PLANT_TROUBLE | 5105.31
2024 | nonsummer | LAMONT_1_SOLAR5 | TRANSMISSION_INDUCED | 5
2024 | nonsummer | LAPLMA_2_UNIT 1 | AMBIENT_DUE_TO_TEMP | 10170.5
2024 | nonsummer | LAPLMA_2_UNIT 1 | PLANT_MAINTENANCE | 13304
2024 | nonsummer | LAPLMA_2_UNIT 1 | PLANT_TROUBLE | 7701.6333
2024 | nonsummer | LAPLMA_2_UNIT 1 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2024 | nonsummer | LAPLMA_2_UNIT 1 | UNIT_TESTING | 224.65
2024 | nonsummer | LAPLMA_2_UNIT 2 | AMBIENT_DUE_TO_TEMP | 5249.5
2024 | nonsummer | LAPLMA_2_UNIT 2 | AMBIENT_DUE_TO_TEMP | 5729
2024 | nonsummer | LAPLMA_2_UNIT 2 | PLANT_MAINTENANCE | 9310
2024 | nonsummer | LAPLMA_2_UNIT 2 | PLANT_TROUBLE | 492.5833
2024 | nonsummer | LAPLMA_2_UNIT 2 | PLANT_TROUBLE | 11392.1333
2024 | nonsummer | LAPLMA_2_UNIT 2 | UNIT_TESTING | 201.5
2024 | nonsummer | LAPLMA_2_UNIT 2 | UNIT_TESTING | 0
2024 | nonsummer | LAPLMA_2_UNIT 3 | AMBIENT_DUE_TO_TEMP | 14566
2024 | nonsummer | LAPLMA_2_UNIT 3 | PLANT_MAINTENANCE | 9310
2024 | nonsummer | LAPLMA_2_UNIT 3 | PLANT_TROUBLE | 8279.1833
2024 | nonsummer | LAPLMA_2_UNIT 3 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2024 | nonsummer | LAPLMA_2_UNIT 3 | TRANSMISSION_INDUCED | 429
2024 | nonsummer | LAPLMA_2_UNIT 3 | UNIT_TESTING | 337
2024 | nonsummer | LAPLMA_2_UNIT 4 | AMBIENT_DUE_TO_TEMP | 13768
2024 | nonsummer | LAPLMA_2_UNIT 4 | PLANT_MAINTENANCE | 10680
2024 | nonsummer | LAPLMA_2_UNIT 4 | PLANT_TROUBLE | 7017.8833
2024 | nonsummer | LAPLMA_2_UNIT 4 | UNIT_TESTING | 356.5
2024 | nonsummer | LARKSP_6_UNIT 1 | AMBIENT_DUE_TO_TEMP | 326
2024 | nonsummer | LARKSP_6_UNIT 1 | PLANT_MAINTENANCE | 4312
2024 | nonsummer | LARKSP_6_UNIT 1 | PLANT_TROUBLE | 866.175
2024 | nonsummer | LARKSP_6_UNIT 1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | LARKSP_6_UNIT 2 | AMBIENT_DUE_TO_TEMP | 326
2024 | nonsummer | LARKSP_6_UNIT 2 | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | nonsummer | LARKSP_6_UNIT 2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | LARKSP_6_UNIT 2 | PLANT_TROUBLE | 208.6833
2024 | nonsummer | LARKSP_6_UNIT 2 | UNIT_TESTING | 0
2024 | nonsummer | LAROA2_2_UNITA1 | AMBIENT_DUE_TO_TEMP | 8673
2024 | nonsummer | LAROA2_2_UNITA1 | PLANT_MAINTENANCE | 8050
2024 | nonsummer | LAROA2_2_UNITA1 | PLANT_TROUBLE | 14582.4333
2024 | nonsummer | LASSEN_6_UNITS | PLANT_TROUBLE | 1197.1667
2024 | nonsummer | LASSEN_6_UNITS | TRANSMISSION_INDUCED | 0
2024 | nonsummer | LCKHT1_2_LH1BT1 | METERING_TELEMETRY | 0
2024 | nonsummer | LCKHT1_2_LH1BT1 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | nonsummer | LCKHT1_2_LH1BT1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | LCKHT1_2_LH1BT1 | PLANT_TROUBLE | 0
2024 | nonsummer | LCKHT1_2_LH1BT1 | RTU_RIG | 0
2024 | nonsummer | LCKHT1_2_LH1BT1 | TRANSMISSION_INDUCED | 134.25
2024 | nonsummer | LCKHT1_2_LH1BT1 | UNIT_TESTING | 0
2024 | nonsummer | LCKHT1_2_LH1SR1 | PLANT_TROUBLE | 1434.75
2024 | nonsummer | LCKHT1_2_LH1SR1 | TRANSMISSION_INDUCED | 400.9167
2024 | nonsummer | LCKHT1_2_LH1SR2 | PLANT_TROUBLE | 193.75
2024 | nonsummer | LCKHT1_2_LH1SR2 | TRANSMISSION_INDUCED | 728.75
2024 | nonsummer | LEBECS_2_UNITS | AMBIENT_DUE_TO_TEMP | 4378.3217
2024 | nonsummer | LEBECS_2_UNITS | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | nonsummer | LEBECS_2_UNITS | PLANT_TROUBLE | 46584.6933
2024 | nonsummer | LEBECS_2_UNITS | TRANSITIONAL_LIMITATION | 8165.363
2024 | nonsummer | LEBECS_2_UNITS | TRANSMISSION_INDUCED | 0
2024 | nonsummer | LECEF_1_UNITS | AMBIENT_DUE_TO_TEMP | 13210.432
2024 | nonsummer | LECEF_1_UNITS | PLANT_MAINTENANCE | 1253.6653
2024 | nonsummer | LECEF_1_UNITS | PLANT_TROUBLE | 467.3767
2024 | nonsummer | LECEF_1_UNITS | TRANSITIONAL_LIMITATION | 384.8933
2024 | nonsummer | LECEF_1_UNITS | UNIT_TESTING | 292.8833
2024 | nonsummer | LECONT_2_LESBT1 | PLANT_MAINTENANCE | 153.4667
2024 | nonsummer | LECONT_2_LESBT1 | PLANT_TROUBLE | 2137.8333
2024 | nonsummer | LECONT_2_LESBT1 | RTU_RIG | 0
2024 | nonsummer | LECONT_2_LESBT1 | TRANSMISSION_INDUCED | 1143.75
2024 | nonsummer | LEPRFD_1_KANSAS | PLANT_MAINTENANCE | 750.5
2024 | nonsummer | LGHTHP_6_ICEGEN | ENVIRONMENTAL_RESTRICTIONS | 4320
2024 | nonsummer | LGHTHP_6_ICEGEN | PLANT_TROUBLE | 1844
2024 | nonsummer | LGHTHP_6_ICEGEN | TRANSMISSION_INDUCED | 0
2024 | nonsummer | LGHTHP_6_ICEGEN | UNIT_TESTING | 0
2024 | nonsummer | LHILLS_6_SOLAR1 | METERING_TELEMETRY | 60
2024 | nonsummer | LHILLS_6_SOLAR1 | PLANT_TROUBLE | 144.6667
2024 | nonsummer | LHILLS_6_SOLAR1 | TRANSMISSION_INDUCED | 1207.3333
2024 | nonsummer | LILIAC_6_SOLAR | PLANT_TROUBLE | 225
2024 | nonsummer | LITLRK_6_GBCSR1 | METERING_TELEMETRY | 90
2024 | nonsummer | LITLRK_6_GBCSR1 | PLANT_TROUBLE | 60
2024 | nonsummer | LITLRK_6_SOLAR1 | METERING_TELEMETRY | 65
2024 | nonsummer | LITLRK_6_SOLAR1 | PLANT_TROUBLE | 2044
2024 | nonsummer | LITLRK_6_SOLAR1 | RTU_RIG | 96
2024 | nonsummer | LITLRK_6_SOLAR2 | PLANT_TROUBLE | 251.3667
2024 | nonsummer | LIVOAK_1_UNIT 1 | AMBIENT_DUE_TO_TEMP | 4017.1
2024 | nonsummer | LIVOAK_1_UNIT 1 | PLANT_TROUBLE | 732.6
2024 | nonsummer | LIVOAK_1_UNIT 1 | RTU_RIG | 0
2024 | nonsummer | LIVOAK_1_UNIT 1 | TRANSMISSION_INDUCED | 47.7833
2024 | nonsummer | LIVOAK_1_UNIT 1 | UNIT_TESTING | 663.5833
2024 | nonsummer | LMBEPK_2_UNITA1 | AMBIENT_DUE_TO_TEMP | 213.9417
2024 | nonsummer | LMBEPK_2_UNITA1 | PLANT_MAINTENANCE | 559.7083
2024 | nonsummer | LMBEPK_2_UNITA1 | PLANT_TROUBLE | 0
2024 | nonsummer | LMBEPK_2_UNITA1 | TRANSMISSION_INDUCED | 398.6667
2024 | nonsummer | LMBEPK_2_UNITA1 | UNIT_TESTING | 12.325
2024 | nonsummer | LMBEPK_2_UNITA2 | AMBIENT_DUE_TO_TEMP | 739.8
2024 | nonsummer | LMBEPK_2_UNITA2 | PLANT_TROUBLE | 115.8267
2024 | nonsummer | LMBEPK_2_UNITA2 | TRANSMISSION_INDUCED | 413.3267
2024 | nonsummer | LMBEPK_2_UNITA2 | UNIT_TESTING | 0
2024 | nonsummer | LMBEPK_2_UNITA3 | AMBIENT_DUE_TO_TEMP | 75.75
2024 | nonsummer | LMBEPK_2_UNITA3 | AMBIENT_DUE_TO_TEMP | 492.5
2024 | nonsummer | LMBEPK_2_UNITA3 | PLANT_MAINTENANCE | 334.25
2024 | nonsummer | LMBEPK_2_UNITA3 | PLANT_TROUBLE | 143.25
2024 | nonsummer | LMBEPK_2_UNITA3 | PLANT_TROUBLE | 99.4792
2024 | nonsummer | LMBEPK_2_UNITA3 | TRANSMISSION_INDUCED | 400.2
2024 | nonsummer | LMBEPK_2_UNITA3 | UNIT_TESTING | 0
2024 | nonsummer | LMEC_1_PL1X3 | AMBIENT_DUE_TO_TEMP | 9080.3047
2024 | nonsummer | LMEC_1_PL1X3 | PLANT_MAINTENANCE | 77.25
2024 | nonsummer | LMEC_1_PL1X3 | PLANT_TROUBLE | 40684.96
2024 | nonsummer | LMEC_1_PL1X3 | TRANSITIONAL_LIMITATION | 0
2024 | nonsummer | LMEC_1_PL1X3 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | LMEC_1_PL1X3 | UNIT_TESTING | 194.2187
2024 | nonsummer | LNCSTR_6_SOLAR2 | METERING_TELEMETRY | 0
2024 | nonsummer | LOCKFD_1_BEARCK | TRANSMISSION_INDUCED | 3.75
2024 | nonsummer | LOCKFD_1_KSOLAR | TRANSMISSION_INDUCED | 2.5
2024 | nonsummer | LODI25_2_UNIT 1 | AMBIENT_DUE_TO_TEMP | 1715
2024 | nonsummer | LODI25_2_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 230
2024 | nonsummer | LODI25_2_UNIT 1 | OTHER_USE_LIMIT_REACHED | 119
2024 | nonsummer | LODI25_2_UNIT 1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | LODI25_2_UNIT 1 | PLANT_TROUBLE | 42.3167
2024 | nonsummer | LODI25_6_ERKNG1 | ENVIRONMENTAL_RESTRICTIONS | 12162.0805
2024 | nonsummer | LODI25_6_ERKNG1 | TRANSMISSION_INDUCED | 2420
2024 | nonsummer | LODIEC_2_PL1X2 | AMBIENT_DUE_TO_TEMP | 15874.7
2024 | nonsummer | LODIEC_2_PL1X2 | PLANT_TROUBLE | 14374.164
2024 | nonsummer | LODIEC_2_PL1X2 | UNIT_TESTING | 1213.58
2024 | nonsummer | LOTUS_6_LSFSR1 | METERING_TELEMETRY | 0
2024 | nonsummer | LOTUS_6_LSFSR1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | LOTUS_6_LSFSR1 | PLANT_TROUBLE | 0
2024 | nonsummer | LOTUS_6_LSFSR1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | LOWGAP_1_SUPHR | TRANSMISSION_INDUCED | 29.7
2024 | nonsummer | LOWGAP_7_QFUNTS | ENVIRONMENTAL_RESTRICTIONS | 232.65
2024 | nonsummer | LOWGAP_7_QFUNTS | PLANT_MAINTENANCE | 0
2024 | nonsummer | LOWGAP_7_QFUNTS | PLANT_TROUBLE | 116.65
2024 | nonsummer | LOWGAP_7_QFUNTS | TRANSMISSION_INDUCED | 19.5
2024 | nonsummer | LTBEAR_1_LB3SR3 | PLANT_MAINTENANCE | 60
2024 | nonsummer | LTBEAR_1_LB3SR3 | PLANT_TROUBLE | 100
2024 | nonsummer | LTBEAR_1_LB4SR4 | PLANT_MAINTENANCE | 175
2024 | nonsummer | LTBEAR_1_LB4SR4 | PLANT_TROUBLE | 1295.8333
2024 | nonsummer | LTBEAR_1_LB4SR5 | PLANT_MAINTENANCE | 150
2024 | nonsummer | LTBEAR_1_LB4SR5 | PLANT_TROUBLE | 250
2024 | nonsummer | LTBERA_1_LB1SR1 | PLANT_MAINTENANCE | 399.3333
2024 | nonsummer | LTBERA_1_LB1SR1 | PLANT_TROUBLE | 600
2024 | nonsummer | LVNGST_1_WTASR1 | PLANT_MAINTENANCE | 40
2024 | nonsummer | MAGNLA_6_ANAHEIM | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | MAGNLA_6_ANAHEIM | PLANT_MAINTENANCE | 7848
2024 | nonsummer | MAGNLA_6_ANAHEIM | PLANT_TROUBLE | 0
2024 | nonsummer | MAGNLA_6_ANAHEIM | UNIT_TESTING | 364
2024 | nonsummer | MAGNLA_6_CERRITOS | PLANT_MAINTENANCE | 864
2024 | nonsummer | MAGNLA_6_CERRITOS | PLANT_TROUBLE | 0
2024 | nonsummer | MAGNLA_6_COLTON | PLANT_MAINTENANCE | 840
2024 | nonsummer | MAGNLA_6_COLTON | PLANT_TROUBLE | 0
2024 | nonsummer | MAGNLA_6_PASADENA | PLANT_MAINTENANCE | 774
2024 | nonsummer | MAGNLA_6_PASADENA | PLANT_TROUBLE | 0
2024 | nonsummer | MAGNLA_6_PASADENA | UNIT_TESTING | 35.97
2024 | nonsummer | MAGUND_1_BKSSR2 | PLANT_TROUBLE | 1770.8167
2024 | nonsummer | MALAGA_1_ACDBX2 | NEW_GENERATOR_TEST_ENERGY | 291
2024 | nonsummer | MALAGA_1_AUCTG1 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | nonsummer | MALAGA_1_AUCTG1 | RIMS_OUTAGE | 3594.5
2024 | nonsummer | MALAGA_1_AUCTG2 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | nonsummer | MALAGA_1_AUCTG2 | RIMS_OUTAGE | 3594.5
2024 | nonsummer | MALAGA_1_PL1X2 | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | nonsummer | MALAGA_1_PL1X2 | METERING_TELEMETRY | 0
2024 | nonsummer | MALAGA_1_PL1X2 | PLANT_MAINTENANCE | 2628.0157
2024 | nonsummer | MALAGA_1_PL1X2 | PLANT_TROUBLE | 0
2024 | nonsummer | MALAGA_1_PL1X2 | RIMS_OUTAGE | 14974.55
2024 | nonsummer | MALAGA_1_PL1X2 | TRANSMISSION_INDUCED | 4228.2977
2024 | nonsummer | MALAGA_1_PL1X2 | UNIT_TESTING | 218.9827
2024 | nonsummer | MALCHQ_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 3161.5083
2024 | nonsummer | MALCHQ_7_UNIT 1 | PLANT_TROUBLE | 54.98
2024 | nonsummer | MANTEC_1_ML1SR1 | METERING_TELEMETRY | 0
2024 | nonsummer | MANTEC_1_ML1SR1 | TRANSMISSION_INDUCED | 105
2024 | nonsummer | MANZNA_2_WIND | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | MANZNA_2_WIND | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | nonsummer | MANZNA_2_WIND | PLANT_TROUBLE | 2863.575
2024 | nonsummer | MARCPW_6_SOLAR1 | METERING_TELEMETRY | 1500
2024 | nonsummer | MARCPW_6_SOLAR1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | MARCPW_6_SOLAR1 | TRANSMISSION_INDUCED | 3098.6667
2024 | nonsummer | MARVEL_2_MARBT3 | METERING_TELEMETRY | 0
2024 | nonsummer | MARVEL_2_MARBT3 | PLANT_MAINTENANCE | 0
2024 | nonsummer | MARVEL_2_MARBT3 | PLANT_TROUBLE | 962.7858
2024 | nonsummer | MARVEL_2_MARBT3 | RTU_RIG | 0
2024 | nonsummer | MARVEL_2_MARBT3 | UNIT_TESTING | 14.322
2024 | nonsummer | MARVEL_2_MARBX2 | METERING_TELEMETRY | 0
2024 | nonsummer | MARVEL_2_MARBX2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | MARVEL_2_MARBX2 | PLANT_TROUBLE | 2103.0787
2024 | nonsummer | MARVEL_2_MARBX2 | RTU_RIG | 0
2024 | nonsummer | MARVEL_2_MARBX2 | UNIT_TESTING | 260
2024 | nonsummer | MCARTH_6_FRIVRB | TRANSMISSION_INDUCED | 0
2024 | nonsummer | MCCALL_1_QF | PLANT_MAINTENANCE | 0
2024 | nonsummer | MCFLND_5_MBSBX2 | METERING_TELEMETRY | 0
2024 | nonsummer | MCFLND_5_MBSBX2 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | nonsummer | MCFLND_5_MBSBX2 | PLANT_MAINTENANCE | 1625
2024 | nonsummer | MCFLND_5_MBSBX2 | PLANT_TROUBLE | 30564.7333
2024 | nonsummer | MCFLND_5_MBSBX2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | MCFLND_5_MBSBX2 | UNIT_TESTING | 0
2024 | nonsummer | MCFLND_5_MFSBT1 | METERING_TELEMETRY | 321.2333
2024 | nonsummer | MCFLND_5_MFSBT1 | METERING_TELEMETRY | 0
2024 | nonsummer | MCFLND_5_MFSBT1 | PLANT_MAINTENANCE | 1429.1667
2024 | nonsummer | MCFLND_5_MFSBT1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | MCFLND_5_MFSBT1 | PLANT_TROUBLE | 2528.5333
2024 | nonsummer | MCFLND_5_MFSBT1 | PLANT_TROUBLE | 265
2024 | nonsummer | MCFLND_5_MFSBT1 | RTU_RIG | 0
2024 | nonsummer | MCFLND_5_MFSBT1 | UNIT_TESTING | 1.6667
2024 | nonsummer | MCFLND_5_MFSBT1 | UNIT_TESTING | 0
2024 | nonsummer | MCFLND_5_MFSSR1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | MCFLND_5_MFSSR1 | PLANT_TROUBLE | 1442
2024 | nonsummer | MCFLND_5_MFSSR1 | UNIT_TESTING | 0
2024 | nonsummer | MCFLND_5_MSBBX2 | NEW_GENERATOR_TEST_ENERGY | 113250
2024 | nonsummer | MCFLND_5_MSBBX2 | PLANT_TROUBLE | 0
2024 | nonsummer | MCFLND_5_MSBBX2 | RTU_RIG | 0
2024 | nonsummer | MCFLND_5_MSBSX2 | NEW_GENERATOR_TEST_ENERGY | 222190
2024 | nonsummer | MCFLND_5_MSBSX2 | PLANT_TROUBLE | 0
2024 | nonsummer | MCSWAN_6_UNITS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | MCSWAN_6_UNITS | PLANT_MAINTENANCE | 3.6
2024 | nonsummer | MCSWAN_6_UNITS | PLANT_TROUBLE | 18
2024 | nonsummer | MCSWAN_6_UNITS | TRANSMISSION_INDUCED | 180
2024 | nonsummer | MDFKRL_2_PROJCT | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 7282.4167
2024 | nonsummer | MDFKRL_2_PROJCT | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | MDFKRL_2_PROJCT | AMBIENT_NOT_DUE_TO_TEMP | 797.5
2024 | nonsummer | MDFKRL_2_PROJCT | PLANT_MAINTENANCE | 0
2024 | nonsummer | MDFKRL_2_PROJCT | PLANT_TROUBLE | 22.4
2024 | nonsummer | MDFKRL_2_PROJCT | TRANSMISSION_INDUCED | 0
2024 | nonsummer | MDFKRL_2_PROJCT | UNIT_TESTING | 173.3333
2024 | nonsummer | MELRSE_6_MELBT1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | MELRSE_6_MELBT1 | PLANT_TROUBLE | 20
2024 | nonsummer | MELRSE_6_MELBT2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | MELRSE_6_MELBT2 | PLANT_TROUBLE | 350
2024 | nonsummer | MENBIO_6_RENEW1 | METERING_TELEMETRY | 0
2024 | nonsummer | MENBIO_6_RENEW1 | TRANSMISSION_INDUCED | 543.4167
2024 | nonsummer | MERCFL_6_UNIT | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | MERCFL_6_UNIT | PLANT_MAINTENANCE | 35
2024 | nonsummer | MERCFL_6_UNIT | PLANT_TROUBLE | 1015
2024 | nonsummer | METEC_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 11264.3167
2024 | nonsummer | METEC_2_PL1X3 | PLANT_MAINTENANCE | 0
2024 | nonsummer | METEC_2_PL1X3 | PLANT_TROUBLE | 13478.2333
2024 | nonsummer | METEC_2_PL1X3 | TRANSITIONAL_LIMITATION | 214
2024 | nonsummer | METEC_2_PL1X3 | UNIT_TESTING | 0
2024 | nonsummer | MIDWD_2_WIND2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | MIDWD_2_WIND2 | PLANT_TROUBLE | 129.375
2024 | nonsummer | MIDWD_2_WIND2 | TRANSMISSION_INDUCED | 4.5
2024 | nonsummer | MIDWD_7_CORAMB | PLANT_MAINTENANCE | 95.925
2024 | nonsummer | MIDWD_7_CORAMB | PLANT_TROUBLE | 407.4
2024 | nonsummer | MIDWY3_2_MDSSR1 | PLANT_MAINTENANCE | 195.2667
2024 | nonsummer | MIDWY3_2_MDSSR1 | PLANT_TROUBLE | 539.8
2024 | nonsummer | MIDWY3_2_MDSSR1 | TRANSMISSION_INDUCED | 286
2024 | nonsummer | MIDWY3_2_MDSSR1 | UNIT_TESTING | 0
2024 | nonsummer | MIDWYS_2_MIDSL1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | MIDWYS_2_MIDSL1 | PLANT_MAINTENANCE | 311.2683
2024 | nonsummer | MIDWYS_2_MIDSL1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | MIDWYS_2_MIDSL1 | UNIT_TESTING | 0
2024 | nonsummer | MILFRD_7_PASADENA | TRANSMISSION_INDUCED | 267.5
2024 | nonsummer | MIRLOM_2_CORONA | PLANT_MAINTENANCE | 14.25
2024 | nonsummer | MIRLOM_2_CORONA | PLANT_TROUBLE | 586.1025
2024 | nonsummer | MIRLOM_2_LNDFL | METERING_TELEMETRY | 15
2024 | nonsummer | MIRLOM_2_LNDFL | PLANT_TROUBLE | 0
2024 | nonsummer | MIRLOM_2_MLBBTA | METERING_TELEMETRY | 0
2024 | nonsummer | MIRLOM_2_MLBBTA | PLANT_MAINTENANCE | 0
2024 | nonsummer | MIRLOM_2_MLBBTA | TRANSMISSION_INDUCED | 30
2024 | nonsummer | MIRLOM_2_MLBBTB | PLANT_MAINTENANCE | 0
2024 | nonsummer | MIRLOM_2_MLBBTB | PLANT_TROUBLE | 50
2024 | nonsummer | MIRLOM_2_TEMESC | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | nonsummer | MIRLOM_2_TEMESC | PLANT_MAINTENANCE | 14.25
2024 | nonsummer | MIRLOM_2_TEMESC | PLANT_TROUBLE | 26.695
2024 | nonsummer | MIRLOM_2_TEMESC | TRANSMISSION_INDUCED | 0
2024 | nonsummer | MIRLOM_6_PEAKER | AMBIENT_DUE_TO_TEMP | 555.22
2024 | nonsummer | MIRLOM_6_PEAKER | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | nonsummer | MIRLOM_6_PEAKER | PLANT_MAINTENANCE | 471.8
2024 | nonsummer | MIRLOM_6_PEAKER | PLANT_TROUBLE | 0
2024 | nonsummer | MIRLOM_6_PEAKER | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2024 | nonsummer | MIRLOM_7_MWDLKM | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | nonsummer | MIRLOM_7_MWDLKM | PLANT_MAINTENANCE | 41.0833
2024 | nonsummer | MIRLOM_7_MWDLKM | PLANT_TROUBLE | 249.0833
2024 | nonsummer | MKTRCK_1_UNIT 1 | AMBIENT_DUE_TO_TEMP | 2452.16
2024 | nonsummer | MKTRCK_1_UNIT 1 | PLANT_TROUBLE | 5580.2
2024 | nonsummer | MKTRCK_1_UNIT 1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | MKTRCK_1_UNIT 1 | UNIT_TESTING | 279.5
2024 | nonsummer | MNDALY_6_MCGRTH | AMBIENT_DUE_TO_TEMP | 969.64
2024 | nonsummer | MNDALY_6_MCGRTH | AMBIENT_DUE_TO_TEMP | 2049.8
2024 | nonsummer | MNDALY_6_MCGRTH | ENVIRONMENTAL_RESTRICTIONS | 142.515
2024 | nonsummer | MNDALY_6_MCGRTH | METERING_TELEMETRY | 31.95
2024 | nonsummer | MNDALY_6_MCGRTH | METERING_TELEMETRY | 25.05
2024 | nonsummer | MNDALY_6_MCGRTH | PLANT_TROUBLE | 0
2024 | nonsummer | MNDALY_6_MCGRTH | PLANT_TROUBLE | 0
2024 | nonsummer | MNDALY_6_MCGRTH | UNIT_TESTING | 0
2024 | nonsummer | MNDOTA_1_SOLAR1 | METERING_TELEMETRY | 59
2024 | nonsummer | MNDOTA_1_SOLAR1 | PLANT_MAINTENANCE | 119
2024 | nonsummer | MNDOTA_1_SOLAR1 | PLANT_TROUBLE | 5088
2024 | nonsummer | MNDOTA_1_SOLAR2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | MNDOTA_1_SOLAR2 | PLANT_TROUBLE | 649
2024 | nonsummer | MNDOTA_1_SOLAR2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | MOJAVE_1_SIPHON | ENVIRONMENTAL_RESTRICTIONS | 145.036
2024 | nonsummer | MOJAVE_1_SIPHON | PLANT_MAINTENANCE | 80.3467
2024 | nonsummer | MOJAVE_1_SIPHON | PLANT_TROUBLE | 0
2024 | nonsummer | MOJAVE_1_SIPHON | TRANSMISSION_INDUCED | 42.8407
2024 | nonsummer | MOJAVW_2_SOLAR | PLANT_MAINTENANCE | 53.7
2024 | nonsummer | MOJAVW_2_SOLAR | PLANT_TROUBLE | 777.5833
2024 | nonsummer | MONTPH_7_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 1155.5
2024 | nonsummer | MONTPH_7_UNITS | PLANT_MAINTENANCE | 635
2024 | nonsummer | MONTPH_7_UNITS | PLANT_TROUBLE | 2231.5
2024 | nonsummer | MONTPH_7_UNITS | TRANSMISSION_INDUCED | 0
2024 | nonsummer | MOORPK_2_ACOBT1 | METERING_TELEMETRY | 29.25
2024 | nonsummer | MOORPK_2_ACOBT1 | PLANT_MAINTENANCE | 79.95
2024 | nonsummer | MOORPK_2_ACOBT1 | PLANT_TROUBLE | 18.525
2024 | nonsummer | MOORPK_2_ACOBT1 | RTU_RIG | 2.7625
2024 | nonsummer | MOORPK_2_ACOBT1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | MOORPK_2_ACOBT1 | UNIT_TESTING | 14.365
2024 | nonsummer | MOORPK_2_CALABS | PLANT_MAINTENANCE | 87.356
2024 | nonsummer | MOORPK_2_CALABS | PLANT_TROUBLE | 35.42
2024 | nonsummer | MOORPK_2_CALABS | UNIT_TESTING | 0
2024 | nonsummer | MORWD_6_QF | METERING_TELEMETRY | 0
2024 | nonsummer | MORWD_6_QF | PLANT_TROUBLE | 119.6033
2024 | nonsummer | MOSSLD_2_PSP1 | AMBIENT_DUE_TO_TEMP | 395.7167
2024 | nonsummer | MOSSLD_2_PSP1 | ENVIRONMENTAL_RESTRICTIONS | 616.85
2024 | nonsummer | MOSSLD_2_PSP1 | PLANT_MAINTENANCE | 2645.3333
2024 | nonsummer | MOSSLD_2_PSP1 | PLANT_TROUBLE | 11000.6667
2024 | nonsummer | MOSSLD_2_PSP1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | MOSSLD_2_PSP1 | UNIT_TESTING | 112.7333
2024 | nonsummer | MOSSLD_2_PSP2 | AMBIENT_DUE_TO_TEMP | 321.0167
2024 | nonsummer | MOSSLD_2_PSP2 | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | nonsummer | MOSSLD_2_PSP2 | PLANT_MAINTENANCE | 19475
2024 | nonsummer | MOSSLD_2_PSP2 | PLANT_TROUBLE | 42082.5167
2024 | nonsummer | MOSSLD_2_PSP2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | MOSSLD_2_PSP2 | UNIT_TESTING | 0
2024 | nonsummer | MRCHNT_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 10260.4667
2024 | nonsummer | MRCHNT_2_PL1X3 | PLANT_MAINTENANCE | 5992.5
2024 | nonsummer | MRCHNT_2_PL1X3 | PLANT_TROUBLE | 39327.65
2024 | nonsummer | MRCHNT_2_PL1X3 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | MRCHNT_2_PL1X3 | UNIT_TESTING | 0
2024 | nonsummer | MRGT_6_MEF2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | MRGT_6_MEF2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | MRGT_6_MMAREF | PLANT_TROUBLE | 0
2024 | nonsummer | MRGT_6_MMAREF | TRANSMISSION_INDUCED | 0
2024 | nonsummer | MRGT_6_TGEBT1 | PLANT_MAINTENANCE | 49.5
2024 | nonsummer | MRGT_6_TGEBT1 | PLANT_TROUBLE | 443.5
2024 | nonsummer | MRGT_6_TGEBT1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | MRLSDS_6_SOLAR1 | METERING_TELEMETRY | 52.5
2024 | nonsummer | MRLSDS_6_SOLAR1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | MRLSDS_6_SOLAR1 | PLANT_TROUBLE | 19.5
2024 | nonsummer | MRLSDS_6_SOLAR1 | TRANSMISSION_INDUCED | 540
2024 | nonsummer | MSHGTS_6_MMARLF | PLANT_MAINTENANCE | 0
2024 | nonsummer | MSOLAR_2_MS4BT1 | PLANT_MAINTENANCE | 106
2024 | nonsummer | MSOLAR_2_MS4BT1 | PLANT_TROUBLE | 2183.7
2024 | nonsummer | MSOLAR_2_MS4BT1 | UNIT_TESTING | 10
2024 | nonsummer | MSOLAR_2_MS4SR4 | NEW_GENERATOR_TEST_ENERGY | 250
2024 | nonsummer | MSOLAR_2_MS4SR4 | PLANT_MAINTENANCE | 525
2024 | nonsummer | MSOLAR_2_MS4SR4 | UNIT_TESTING | 0
2024 | nonsummer | MSOLAR_2_SOLAR1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | MSOLAR_2_SOLAR1 | PLANT_TROUBLE | 43
2024 | nonsummer | MSOLAR_2_SOLAR2 | PLANT_TROUBLE | 686.25
2024 | nonsummer | MSOLAR_2_SOLAR3 | PLANT_TROUBLE | 62.9
2024 | nonsummer | MSTANG_2_MTGBT1 | METERING_TELEMETRY | 235
2024 | nonsummer | MSTANG_2_MTGBT1 | PLANT_MAINTENANCE | 2972.3417
2024 | nonsummer | MSTANG_2_MTGBT1 | PLANT_TROUBLE | 4791.0135
2024 | nonsummer | MSTANG_2_MTGBT1 | UNIT_TESTING | 686.2333
2024 | nonsummer | MSTANG_2_SOLAR | PLANT_MAINTENANCE | 236.9333
2024 | nonsummer | MSTANG_2_SOLAR | PLANT_TROUBLE | 10881.03
2024 | nonsummer | MSTANG_2_SOLAR3 | PLANT_MAINTENANCE | 79.3333
2024 | nonsummer | MSTANG_2_SOLAR3 | PLANT_TROUBLE | 896.9
2024 | nonsummer | MSTANG_2_SOLAR4 | METERING_TELEMETRY | 0
2024 | nonsummer | MSTANG_2_SOLAR4 | PLANT_MAINTENANCE | 106.5333
2024 | nonsummer | MSTANG_2_SOLAR4 | PLANT_TROUBLE | 5085.8
2024 | nonsummer | MTNPOS_1_UNIT | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | MTNPOS_1_UNIT | METERING_TELEMETRY | 108.2
2024 | nonsummer | MTNPOS_1_UNIT | PLANT_MAINTENANCE | 13059.2
2024 | nonsummer | MTNPOS_1_UNIT | PLANT_TROUBLE | 17128.2217
2024 | nonsummer | MTWIND_1_MVPWD1 | METERING_TELEMETRY | 0
2024 | nonsummer | MTWIND_1_MVPWD1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | MTWIND_1_MVPWD1 | PLANT_TROUBLE | 133.2
2024 | nonsummer | MTWIND_1_MVPWD1 | RTU_RIG | 0
2024 | nonsummer | MTWIND_1_MVPWD1 | TRANSITIONAL_LIMITATION | 57.6
2024 | nonsummer | MTWIND_1_MVPWD1 | TRANSMISSION_INDUCED | 467.91
2024 | nonsummer | MTWIND_1_UNIT 3 | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | MTWIND_1_UNIT 3 | PLANT_TROUBLE | 0
2024 | nonsummer | MTWIND_1_UNIT 3 | TRANSITIONAL_LIMITATION | 0
2024 | nonsummer | MTWIND_1_UNIT 3 | TRANSMISSION_INDUCED | 77.6068
2024 | nonsummer | MURRAY_6_UNIT | PLANT_MAINTENANCE | 94.76
2024 | nonsummer | MURRAY_6_UNIT | PLANT_TROUBLE | 39.8267
2024 | nonsummer | NAROW1_2_UNIT | ENVIRONMENTAL_RESTRICTIONS | 2872.5167
2024 | nonsummer | NAROW1_2_UNIT | PLANT_TROUBLE | 0
2024 | nonsummer | NAROW1_2_UNIT | TRANSMISSION_INDUCED | 144
2024 | nonsummer | NAROW2_2_UNIT | ENVIRONMENTAL_RESTRICTIONS | 29698.1917
2024 | nonsummer | NAROW2_2_UNIT | PLANT_MAINTENANCE | 0
2024 | nonsummer | NAROW2_2_UNIT | PLANT_TROUBLE | 0
2024 | nonsummer | NAROW2_2_UNIT | TRANSMISSION_INDUCED | 0
2024 | nonsummer | NAROW2_2_UNIT | UNIT_TESTING | 0
2024 | nonsummer | NAVYII_2_UNITS | PLANT_TROUBLE | 8667.485
2024 | nonsummer | NAVYII_2_UNITS | TRANSMISSION_INDUCED | 450
2024 | nonsummer | NCPA_7_GP1UN1 | PLANT_MAINTENANCE | 17288.25
2024 | nonsummer | NCPA_7_GP1UN1 | PLANT_TROUBLE | 570.4475
2024 | nonsummer | NCPA_7_GP1UN2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | NCPA_7_GP1UN2 | PLANT_TROUBLE | 15000
2024 | nonsummer | NCPA_7_GP2UN4 | PLANT_MAINTENANCE | 85.46
2024 | nonsummer | NCPA_7_GP2UN4 | PLANT_TROUBLE | 0
2024 | nonsummer | NCPA_7_GP2UN4 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | NEENCH_6_SOLAR | PLANT_MAINTENANCE | 7.56
2024 | nonsummer | NEENCH_6_SOLAR | PLANT_TROUBLE | 3159
2024 | nonsummer | NGILAA_5_SDGDYN | AMBIENT_DUE_TO_TEMP | 325
2024 | nonsummer | NGILAA_5_SDGDYN | PLANT_MAINTENANCE | 55
2024 | nonsummer | NGILAA_5_SDGDYN | UNIT_TESTING | 13.8752
2024 | nonsummer | NHOGAN_6_UNITS | PLANT_MAINTENANCE | 360
2024 | nonsummer | NOAKS_2_PESBT1 | METERING_TELEMETRY | 0
2024 | nonsummer | NOAKS_2_PESBT1 | NEW_GENERATOR_TEST_ENERGY | 4760
2024 | nonsummer | NOAKS_2_PESBT1 | PLANT_TROUBLE | 20
2024 | nonsummer | NOAKS_2_PESBT1 | UNIT_TESTING | 400
2024 | nonsummer | NORCNV_1_NCVBT1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | NORCNV_1_NCVBT1 | PLANT_TROUBLE | 7131.9917
2024 | nonsummer | NORCNV_1_NCVBT1 | RTU_RIG | 0
2024 | nonsummer | NORCNV_1_NCVBT1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | NORORC_2_NOSBX2 | NEW_GENERATOR_TEST_ENERGY | 6100
2024 | nonsummer | NORORC_2_NOSBX2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | NORORC_2_NOSBX2 | PLANT_TROUBLE | 0
2024 | nonsummer | NOVATO_6_LNDFL | PLANT_MAINTENANCE | 0
2024 | nonsummer | NOVATO_6_LNDFL | PLANT_TROUBLE | 0
2024 | nonsummer | NOVATO_6_LNDFL | TRANSMISSION_INDUCED | 1310.4
2024 | nonsummer | NWCSTL_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 8407.462
2024 | nonsummer | NWCSTL_7_UNIT 1 | PLANT_TROUBLE | 0
2024 | nonsummer | NZWIND_2_WDSTR5 | PLANT_MAINTENANCE | 13.0407
2024 | nonsummer | NZWIND_2_WDSTR5 | PLANT_TROUBLE | 0
2024 | nonsummer | NZWIND_2_WDSTR5 | TRANSMISSION_INDUCED | 312.1
2024 | nonsummer | NZWIND_6_CALWND | PLANT_TROUBLE | 0
2024 | nonsummer | NZWIND_6_CALWND | TRANSMISSION_INDUCED | 45.4
2024 | nonsummer | NZWIND_6_WDSTR | PLANT_MAINTENANCE | 5.04
2024 | nonsummer | NZWIND_6_WDSTR | PLANT_TROUBLE | 0
2024 | nonsummer | NZWIND_6_WDSTR | TRANSMISSION_INDUCED | 209.95
2024 | nonsummer | NZWIND_6_WDSTR2 | PLANT_MAINTENANCE | 6.006
2024 | nonsummer | NZWIND_6_WDSTR2 | PLANT_TROUBLE | 0
2024 | nonsummer | NZWIND_6_WDSTR2 | TRANSMISSION_INDUCED | 259.35
2024 | nonsummer | NZWIND_6_WDSTR3 | PLANT_MAINTENANCE | 6.4
2024 | nonsummer | NZWIND_6_WDSTR3 | PLANT_TROUBLE | 23.16
2024 | nonsummer | NZWIND_6_WDSTR3 | TRANSMISSION_INDUCED | 302.1
2024 | nonsummer | NZWIND_6_WDSTR4 | PLANT_MAINTENANCE | 6.304
2024 | nonsummer | NZWIND_6_WDSTR4 | PLANT_TROUBLE | 1.97
2024 | nonsummer | NZWIND_6_WDSTR4 | TRANSMISSION_INDUCED | 275.5
2024 | nonsummer | OAK C_7_UNIT 1 | PLANT_MAINTENANCE | 607.9
2024 | nonsummer | OAK C_7_UNIT 1 | PLANT_TROUBLE | 2235.6583
2024 | nonsummer | OAK C_7_UNIT 1 | TRANSMISSION_INDUCED | 97.1917
2024 | nonsummer | OAK C_7_UNIT 1 | UNIT_TESTING | 0
2024 | nonsummer | OAK C_7_UNIT 3 | PLANT_MAINTENANCE | 270
2024 | nonsummer | OAK C_7_UNIT 3 | PLANT_TROUBLE | 2057.95
2024 | nonsummer | OAK C_7_UNIT 3 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | OAK C_7_UNIT 3 | UNIT_TESTING | 0
2024 | nonsummer | OAKWD_6_QF | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | nonsummer | OAKWD_6_QF | PLANT_TROUBLE | 294.2505
2024 | nonsummer | OAKWD_6_QF | TRANSMISSION_INDUCED | 0
2024 | nonsummer | OAKWD_6_ZEPHWD | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | nonsummer | OAKWD_6_ZEPHWD | PLANT_TROUBLE | 1.1083
2024 | nonsummer | OAKWD_6_ZEPHWD | TRANSMISSION_INDUCED | 0
2024 | nonsummer | OASIS_6_AR4SR1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | OASIS_6_AR4SR2 | PLANT_MAINTENANCE | 5
2024 | nonsummer | OASIS_6_AR8SR3 | PLANT_TROUBLE | 183
2024 | nonsummer | OASIS_6_AR8SR3 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2024 | nonsummer | OASIS_6_CREST | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2024 | nonsummer | OASIS_6_GBDSR4 | PLANT_TROUBLE | 403.675
2024 | nonsummer | OASIS_6_GBDSR4 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | OASIS_6_LPPSR1 | PLANT_TROUBLE | 127.5
2024 | nonsummer | OASIS_6_MA4SR1 | PLANT_TROUBLE | 52.5
2024 | nonsummer | OASIS_6_MA4SR1 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 7.5
2024 | nonsummer | OASIS_6_SOLAR2 | PLANT_TROUBLE | 2469.0667
2024 | nonsummer | OASIS_6_VINSR1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | OBERON_5_O1BBX2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | OBERON_5_O1BBX2 | METERING_TELEMETRY | 125
2024 | nonsummer | OBERON_5_O1BBX2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | OBERON_5_O1BBX2 | PLANT_TROUBLE | 3272.9167
2024 | nonsummer | OBERON_5_O1SSR3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | OBERON_5_O1SSR3 | METERING_TELEMETRY | 100
2024 | nonsummer | OBERON_5_O1SSR3 | PLANT_MAINTENANCE | 1357.1667
2024 | nonsummer | OBERON_5_O1SSR3 | PLANT_TROUBLE | 1704.3333
2024 | nonsummer | OBERON_5_O1SSR3 | UNIT_TESTING | 0
2024 | nonsummer | OBERON_5_O1SSX2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | OBERON_5_O1SSX2 | METERING_TELEMETRY | 150
2024 | nonsummer | OBERON_5_O1SSX2 | PLANT_MAINTENANCE | 367.5
2024 | nonsummer | OBERON_5_O1SSX2 | PLANT_TROUBLE | 38.28
2024 | nonsummer | OBERON_5_O2BBX2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | OBERON_5_O2BBX2 | METERING_TELEMETRY | 125
2024 | nonsummer | OBERON_5_O2BBX2 | PLANT_MAINTENANCE | 149
2024 | nonsummer | OBERON_5_O2BBX2 | PLANT_TROUBLE | 681.5
2024 | nonsummer | OBERON_5_O2SSR4 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | OBERON_5_O2SSR4 | METERING_TELEMETRY | 125
2024 | nonsummer | OBERON_5_O2SSR4 | PLANT_MAINTENANCE | 331
2024 | nonsummer | OBERON_5_O2SSR4 | PLANT_TROUBLE | 562.5
2024 | nonsummer | OBERON_5_O2SSR5 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | OBERON_5_O2SSR5 | METERING_TELEMETRY | 125
2024 | nonsummer | OBERON_5_O2SSR5 | PLANT_MAINTENANCE | 400.05
2024 | nonsummer | OBERON_5_O2SSR5 | PLANT_TROUBLE | 562.5
2024 | nonsummer | OCOTLO_6_OCWSB1 | METERING_TELEMETRY | 199.35
2024 | nonsummer | OCOTLO_6_OCWSB1 | PLANT_MAINTENANCE | 156.2
2024 | nonsummer | OCOTLO_6_OCWSB1 | PLANT_TROUBLE | 736.475
2024 | nonsummer | OCOTLO_6_OCWSB1 | TRANSITIONAL_LIMITATION | 152.1
2024 | nonsummer | OCOTLO_6_OCWSB1 | TRANSMISSION_INDUCED | 5253.16
2024 | nonsummer | OCOTLO_6_OCWSB1 | UNIT_TESTING | 61.6667
2024 | nonsummer | OCTILO_5_WIND | PLANT_MAINTENANCE | 579.7937
2024 | nonsummer | OCTILO_5_WIND | PLANT_TROUBLE | 40195.9167
2024 | nonsummer | OGROVE_6_PL1X2 | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | OGROVE_6_PL1X2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | OGROVE_6_PL1X2 | PLANT_TROUBLE | 331.0733
2024 | nonsummer | OILFLD_7_QFUNTS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 2235.4
2024 | nonsummer | OILFLD_7_QFUNTS | PLANT_MAINTENANCE | 262.5
2024 | nonsummer | OILFLD_7_QFUNTS | PLANT_TROUBLE | 17.032
2024 | nonsummer | OILFLD_7_QFUNTS | TRANSMISSION_INDUCED | 0.452
2024 | nonsummer | OLDRIV_6_CESDBM | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | OLDRIV_6_CESDBM | AMBIENT_DUE_TO_TEMP | 4.4167
2024 | nonsummer | OLDRIV_6_CESDBM | PLANT_MAINTENANCE | 0
2024 | nonsummer | OLDRIV_6_CESDBM | PLANT_TROUBLE | 3.1
2024 | nonsummer | OLDRIV_6_CESDBM | TRANSMISSION_INDUCED | 4
2024 | nonsummer | OLDRIV_6_LKVBM1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 9.25
2024 | nonsummer | OLDRIV_6_LKVBM1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | OLDRIV_6_LKVBM1 | PLANT_TROUBLE | 0
2024 | nonsummer | OLDRIV_6_LKVBM1 | TRANSMISSION_INDUCED | 3
2024 | nonsummer | OLDRV1_6_SOLAR | PLANT_TROUBLE | 0
2024 | nonsummer | OLDRV1_6_SOLAR | TRANSMISSION_INDUCED | 3071
2024 | nonsummer | OLINDA_2_LNDFL2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 3040.8
2024 | nonsummer | OLINDA_2_LNDFL2 | PLANT_MAINTENANCE | 858.7
2024 | nonsummer | OLINDA_2_LNDFL2 | PLANT_TROUBLE | 102.6833
2024 | nonsummer | OLIVEP_1_SOLAR | METERING_TELEMETRY | 60
2024 | nonsummer | OLIVEP_1_SOLAR | PLANT_MAINTENANCE | 0
2024 | nonsummer | OLIVEP_1_SOLAR | PLANT_TROUBLE | 0
2024 | nonsummer | OLIVEP_1_SOLAR | TRANSMISSION_INDUCED | 75.3333
2024 | nonsummer | OLIVEP_1_SOLAR2 | METERING_TELEMETRY | 59.25
2024 | nonsummer | OLIVEP_1_SOLAR2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | OLIVEP_1_SOLAR2 | TRANSMISSION_INDUCED | 74.7208
2024 | nonsummer | OLSEN_2_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 721.1417
2024 | nonsummer | OLSEN_2_UNIT | PLANT_MAINTENANCE | 451
2024 | nonsummer | OLSEN_2_UNIT | PLANT_TROUBLE | 137.5917
2024 | nonsummer | OLSEN_2_UNIT | TRANSMISSION_INDUCED | 214.5
2024 | nonsummer | OMAR_2_UNIT 1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | OMAR_2_UNIT 1 | PLANT_TROUBLE | 95
2024 | nonsummer | OMAR_2_UNIT 2 | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | nonsummer | OMAR_2_UNIT 2 | PLANT_MAINTENANCE | 375
2024 | nonsummer | OMAR_2_UNIT 2 | PLANT_TROUBLE | 547.5
2024 | nonsummer | OMAR_2_UNIT 3 | PLANT_MAINTENANCE | 2625
2024 | nonsummer | OMAR_2_UNIT 3 | PLANT_TROUBLE | 0
2024 | nonsummer | OMAR_2_UNIT 4 | PLANT_MAINTENANCE | 4875
2024 | nonsummer | OMAR_2_UNIT 4 | PLANT_TROUBLE | 11297.5
2024 | nonsummer | OMAR_2_UNIT 4 | UNIT_TESTING | 0.5
2024 | nonsummer | ORLND_6_HIGHLI | PLANT_TROUBLE | 530
2024 | nonsummer | ORMOND_7_UNIT 1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | ORMOND_7_UNIT 1 | ENVIRONMENTAL_RESTRICTIONS | 266857.2
2024 | nonsummer | ORMOND_7_UNIT 1 | PLANT_TROUBLE | 0
2024 | nonsummer | ORMOND_7_UNIT 2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | ORMOND_7_UNIT 2 | ENVIRONMENTAL_RESTRICTIONS | 270000
2024 | nonsummer | ORMOND_7_UNIT 2 | PLANT_TROUBLE | 26250
2024 | nonsummer | ORMOND_7_UNIT 2 | UNIT_TESTING | 0
2024 | nonsummer | OROLOM_1_SOLAR1 | METERING_TELEMETRY | 0
2024 | nonsummer | OROLOM_1_SOLAR1 | PLANT_TROUBLE | 0
2024 | nonsummer | OROLOM_1_SOLAR1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | OROLOM_1_SOLAR2 | METERING_TELEMETRY | 0
2024 | nonsummer | OROLOM_1_SOLAR2 | PLANT_TROUBLE | 0
2024 | nonsummer | OROLOM_1_SOLAR2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | OROVIL_6_UNIT | PLANT_MAINTENANCE | 345
2024 | nonsummer | OROVIL_6_UNIT | PLANT_TROUBLE | 37.5
2024 | nonsummer | OROVIL_6_UNIT | TRANSMISSION_INDUCED | 0
2024 | nonsummer | OTAY_6_ECVBT1 | METERING_TELEMETRY | 0
2024 | nonsummer | OTAY_6_ECVBT1 | NEW_GENERATOR_TEST_ENERGY | 209
2024 | nonsummer | OTAY_6_ECVBT1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | OTAY_6_ECVBT1 | PLANT_TROUBLE | 0
2024 | nonsummer | OTAY_6_ECVBT1 | RTU_RIG | 0
2024 | nonsummer | OTAY_6_ECVBT2 | METERING_TELEMETRY | 0
2024 | nonsummer | OTAY_6_ECVBT2 | NEW_GENERATOR_TEST_ENERGY | 216.4
2024 | nonsummer | OTAY_6_ECVBT2 | PLANT_TROUBLE | 0
2024 | nonsummer | OTAY_6_ECVBT2 | RTU_RIG | 0
2024 | nonsummer | OTAY_6_ECVBT2 | UNIT_TESTING | 0
2024 | nonsummer | OTAY_6_PL1X2 | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | OTAY_6_PL1X2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | OTAY_6_PL1X2 | PLANT_TROUBLE | 791.4
2024 | nonsummer | OTMESA_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 10254.1433
2024 | nonsummer | OTMESA_2_PL1X3 | PLANT_MAINTENANCE | 3099.4
2024 | nonsummer | OTMESA_2_PL1X3 | PLANT_TROUBLE | 107545.882
2024 | nonsummer | OTMESA_2_PL1X3 | TRANSITIONAL_LIMITATION | 1460
2024 | nonsummer | OTMESA_2_PL1X3 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | OXBOW_6_DRUM | METERING_TELEMETRY | 0
2024 | nonsummer | OXBOW_6_DRUM | PLANT_TROUBLE | 5.8
2024 | nonsummer | OXBOW_6_DRUM | TRANSMISSION_INDUCED | 44.37
2024 | nonsummer | OXBOW_6_DRUM | UNIT_TESTING | 0
2024 | nonsummer | OXMTN_6_LNDFIL | PLANT_MAINTENANCE | 476.239
2024 | nonsummer | OXMTN_6_LNDFIL | PLANT_TROUBLE | 276.7257
2024 | nonsummer | OXMTN_6_LNDFIL | TRANSMISSION_INDUCED | 598.61
2024 | nonsummer | PACLUM_6_UNIT | METERING_TELEMETRY | 302
2024 | nonsummer | PACLUM_6_UNIT | PLANT_TROUBLE | 2046.7733
2024 | nonsummer | PACLUM_6_UNIT | TRANSMISSION_INDUCED | 2340.88
2024 | nonsummer | PACLUM_6_UNIT | UNIT_TESTING | 237.6
2024 | nonsummer | PADUA_2_ONTARO | AMBIENT_NOT_DUE_TO_TEMP | 236.2
2024 | nonsummer | PADUA_2_ONTARO | PLANT_TROUBLE | 888
2024 | nonsummer | PADUA_2_ONTARO | TRANSMISSION_INDUCED | 0
2024 | nonsummer | PADUA_7_SDIMAS | ENVIRONMENTAL_RESTRICTIONS | 372.75
2024 | nonsummer | PADUA_7_SDIMAS | PLANT_MAINTENANCE | 0
2024 | nonsummer | PADUA_7_SDIMAS | PLANT_TROUBLE | 0
2024 | nonsummer | PAIGES_6_SOLAR | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | PAIGES_6_SOLAR | METERING_TELEMETRY | 0
2024 | nonsummer | PAIGES_6_SOLAR | PLANT_MAINTENANCE | 50
2024 | nonsummer | PAIGES_6_SOLAR | PLANT_TROUBLE | 125.85
2024 | nonsummer | PALALT_7_COBUG | PLANT_TROUBLE | 652.5
2024 | nonsummer | PALA_6_PGCBT1 | METERING_TELEMETRY | 300
2024 | nonsummer | PALA_6_PGCBT1 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | nonsummer | PALA_6_PGCBT1 | PLANT_MAINTENANCE | 1.8
2024 | nonsummer | PALA_6_PGCBT1 | PLANT_TROUBLE | 457
2024 | nonsummer | PALA_6_PGCBT1 | TRANSMISSION_INDUCED | 121.3333
2024 | nonsummer | PALOMR_2_PL1X3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 11872.2
2024 | nonsummer | PALOMR_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | PALOMR_2_PL1X3 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | PALOMR_2_PL1X3 | PLANT_TROUBLE | 15581.3535
2024 | nonsummer | PALOMR_2_PL1X3 | TRANSMISSION_INDUCED | 9931.9642
2024 | nonsummer | PALOMR_2_PL1X3 | UNIT_TESTING | 0
2024 | nonsummer | PALSEL_6_PLSBT1 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | nonsummer | PALSEL_6_PLSBT1 | PLANT_TROUBLE | 96
2024 | nonsummer | PALSEL_6_PLSSR1 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | nonsummer | PALSEL_6_PLSSR1 | PLANT_TROUBLE | 0
2024 | nonsummer | PALSEL_6_PLSSR1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | PANERO_2_MWPWD1 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | nonsummer | PANERO_2_MWPWD1 | PLANT_MAINTENANCE | 43.18
2024 | nonsummer | PANERO_2_MWPWD1 | PLANT_TROUBLE | 1659.71
2024 | nonsummer | PANERO_2_MWPWD1 | UNIT_TESTING | 0
2024 | nonsummer | PARDEB_6_UNITS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 150
2024 | nonsummer | PARDEB_6_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 912.1
2024 | nonsummer | PARDEB_6_UNITS | PLANT_MAINTENANCE | 2958
2024 | nonsummer | PARDEB_6_UNITS | PLANT_TROUBLE | 1.6667
2024 | nonsummer | PARDEB_6_UNITS | TRANSMISSION_INDUCED | 1650
2024 | nonsummer | PARDSE_6_PESBT1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | PARDSE_6_PESBT1 | PLANT_TROUBLE | 40.8583
2024 | nonsummer | PBLOSM_2_SOLAR | METERING_TELEMETRY | 190
2024 | nonsummer | PBLOSM_2_SOLAR | PLANT_MAINTENANCE | 0
2024 | nonsummer | PBLOSM_2_SOLAR | PLANT_TROUBLE | 7.4417
2024 | nonsummer | PBLOSM_2_SOLAR | TRANSMISSION_INDUCED | 190
2024 | nonsummer | PEABDY_2_LNDFIL | PLANT_MAINTENANCE | 0
2024 | nonsummer | PEABDY_2_LNDFIL | PLANT_TROUBLE | 70.64
2024 | nonsummer | PEABDY_2_LNDFIL | TRANSMISSION_INDUCED | 0
2024 | nonsummer | PEABDY_2_LNDFL1 | AMBIENT_DUE_TO_TEMP | 32.335
2024 | nonsummer | PEABDY_2_LNDFL1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | PEABDY_2_LNDFL1 | PLANT_MAINTENANCE | 202.59
2024 | nonsummer | PEABDY_2_LNDFL1 | PLANT_TROUBLE | 259.3233
2024 | nonsummer | PEABDY_2_LNDFL1 | TRANSMISSION_INDUCED | 109.2
2024 | nonsummer | PEARBL_2_NSPIN | PLANT_TROUBLE | 0
2024 | nonsummer | PEARBL_2_NSPIN | TRANSMISSION_INDUCED | 2383.6
2024 | nonsummer | PEASE_1_TBEBT1 | METERING_TELEMETRY | 0
2024 | nonsummer | PEASE_1_TBEBT1 | PLANT_MAINTENANCE | 48
2024 | nonsummer | PEASE_1_TBEBT1 | PLANT_TROUBLE | 100.3
2024 | nonsummer | PEASE_1_TBEBT1 | RTU_RIG | 0
2024 | nonsummer | PEASE_1_TBEBT1 | UNIT_TESTING | 42
2024 | nonsummer | PEORIA_1_SOLAR | PLANT_TROUBLE | 686.5
2024 | nonsummer | PEORIA_1_SOLAR | TRANSMISSION_INDUCED | 0
2024 | nonsummer | PGCC_1_RDRR01 | PLANT_MAINTENANCE | 0
2024 | nonsummer | PGCC_1_RDRR01 | SHORT_TERM_USE_LIMIT_REACHED | 0
2024 | nonsummer | PGEB_2_RDRR01 | PLANT_MAINTENANCE | 0
2024 | nonsummer | PGEB_2_RDRR01 | SHORT_TERM_USE_LIMIT_REACHED | 0
2024 | nonsummer | PGEB_2_RDRR02 | PLANT_MAINTENANCE | 0
2024 | nonsummer | PGEB_2_RDRR02 | SHORT_TERM_USE_LIMIT_REACHED | 0
2024 | nonsummer | PGF1_2_RDRR01 | PLANT_MAINTENANCE | 0
2024 | nonsummer | PGF1_2_RDRR01 | SHORT_TERM_USE_LIMIT_REACHED | 0
2024 | nonsummer | PGFG_1_RDRR01 | PLANT_MAINTENANCE | 0
2024 | nonsummer | PGFG_1_RDRR01 | SHORT_TERM_USE_LIMIT_REACHED | 0
2024 | nonsummer | PGKN_2_RDRR02 | PLANT_MAINTENANCE | 0
2024 | nonsummer | PGKN_2_RDRR02 | SHORT_TERM_USE_LIMIT_REACHED | 0
2024 | nonsummer | PGNC_1_RDRR02 | PLANT_MAINTENANCE | 0
2024 | nonsummer | PGNC_1_RDRR02 | SHORT_TERM_USE_LIMIT_REACHED | 0
2024 | nonsummer | PGNP_2_PDRP04 | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | nonsummer | PGNP_2_RDRR02 | PLANT_MAINTENANCE | 0
2024 | nonsummer | PGNP_2_RDRR02 | SHORT_TERM_USE_LIMIT_REACHED | 0
2024 | nonsummer | PGNP_2_RDRR03 | PLANT_MAINTENANCE | 0
2024 | nonsummer | PGSB_1_RDRR02 | PLANT_MAINTENANCE | 0
2024 | nonsummer | PGSB_1_RDRR02 | SHORT_TERM_USE_LIMIT_REACHED | 0
2024 | nonsummer | PGSI_1_PDRP04 | MONTHLY_USE_LIMIT_REACHED | 0
2024 | nonsummer | PGSI_1_RDRR02 | PLANT_MAINTENANCE | 0
2024 | nonsummer | PGSI_1_RDRR02 | SHORT_TERM_USE_LIMIT_REACHED | 0
2024 | nonsummer | PGST_2_RDRR01 | PLANT_MAINTENANCE | 0
2024 | nonsummer | PGST_2_RDRR01 | SHORT_TERM_USE_LIMIT_REACHED | 0
2024 | nonsummer | PGZP_2_RDRR04 | PLANT_MAINTENANCE | 0
2024 | nonsummer | PGZP_2_RDRR04 | SHORT_TERM_USE_LIMIT_REACHED | 0
2024 | nonsummer | PHOENX_1_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 22.2977
2024 | nonsummer | PHOENX_1_UNIT | PLANT_MAINTENANCE | 0
2024 | nonsummer | PHOENX_1_UNIT | PLANT_TROUBLE | 293.7
2024 | nonsummer | PHOENX_1_UNIT | RTU_RIG | 71.305
2024 | nonsummer | PHOENX_1_UNIT | TRANSMISSION_INDUCED | 0
2024 | nonsummer | PINFLT_7_UNITS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 15899.557
2024 | nonsummer | PINFLT_7_UNITS | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | nonsummer | PINFLT_7_UNITS | METERING_TELEMETRY | 0
2024 | nonsummer | PINFLT_7_UNITS | PLANT_MAINTENANCE | 4165.4015
2024 | nonsummer | PINFLT_7_UNITS | PLANT_TROUBLE | 0
2024 | nonsummer | PINFLT_7_UNITS | TRANSMISSION_INDUCED | 0
2024 | nonsummer | PIOPIC_2_CTG1 | AMBIENT_DUE_TO_TEMP | 2638.83
2024 | nonsummer | PIOPIC_2_CTG1 | PLANT_TROUBLE | 0
2024 | nonsummer | PIOPIC_2_CTG1 | TRANSMISSION_INDUCED | 653.61
2024 | nonsummer | PIOPIC_2_CTG2 | AMBIENT_DUE_TO_TEMP | 1289.32
2024 | nonsummer | PIOPIC_2_CTG2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | PIOPIC_2_CTG2 | PLANT_TROUBLE | 0
2024 | nonsummer | PIOPIC_2_CTG2 | TRANSMISSION_INDUCED | 664.89
2024 | nonsummer | PIOPIC_2_CTG3 | AMBIENT_DUE_TO_TEMP | 2249.02
2024 | nonsummer | PIOPIC_2_CTG3 | PLANT_TROUBLE | 433.43
2024 | nonsummer | PIOPIC_2_CTG3 | TRANSMISSION_INDUCED | 336
2024 | nonsummer | PIT1_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 512.7
2024 | nonsummer | PIT1_7_UNIT 1 | PLANT_TROUBLE | 0
2024 | nonsummer | PIT1_7_UNIT 1 | UNIT_TESTING | 0
2024 | nonsummer | PIT1_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 460.455
2024 | nonsummer | PIT1_7_UNIT 2 | PLANT_TROUBLE | 0
2024 | nonsummer | PIT3_7_PL1X3 | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | PIT3_7_PL1X3 | AMBIENT_NOT_DUE_TO_TEMP | 539.9567
2024 | nonsummer | PIT3_7_PL1X3 | PLANT_MAINTENANCE | 133
2024 | nonsummer | PIT3_7_PL1X3 | PLANT_TROUBLE | 0
2024 | nonsummer | PIT3_7_PL1X3 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | PIT3_7_PL1X3 | UNIT_TESTING | 0
2024 | nonsummer | PIT4_7_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 471.2617
2024 | nonsummer | PIT4_7_PL1X2 | PLANT_TROUBLE | 193.1667
2024 | nonsummer | PIT4_7_PL1X2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | PIT4_7_PL1X2 | UNIT_TESTING | 0
2024 | nonsummer | PIT5_7_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 2951.7833
2024 | nonsummer | PIT5_7_PL1X2 | PLANT_MAINTENANCE | 85.4167
2024 | nonsummer | PIT5_7_PL1X2 | PLANT_TROUBLE | 0
2024 | nonsummer | PIT5_7_PL3X4 | AMBIENT_NOT_DUE_TO_TEMP | 531.45
2024 | nonsummer | PIT5_7_PL3X4 | PLANT_MAINTENANCE | 125.05
2024 | nonsummer | PIT5_7_PL3X4 | PLANT_TROUBLE | 0
2024 | nonsummer | PIT5_7_QFUNTS | TRANSMISSION_INDUCED | 7.5717
2024 | nonsummer | PIT6_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 1780.1368
2024 | nonsummer | PIT6_7_UNIT 1 | METERING_TELEMETRY | 0
2024 | nonsummer | PIT6_7_UNIT 1 | PLANT_TROUBLE | 44.1625
2024 | nonsummer | PIT6_7_UNIT 1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | PIT6_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 1361.599
2024 | nonsummer | PIT6_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 923.1715
2024 | nonsummer | PIT6_7_UNIT 2 | METERING_TELEMETRY | 0
2024 | nonsummer | PIT6_7_UNIT 2 | PLANT_TROUBLE | 0
2024 | nonsummer | PIT6_7_UNIT 2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | PIT7_7_UNIT 1 | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | PIT7_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 2333.6232
2024 | nonsummer | PIT7_7_UNIT 1 | PLANT_TROUBLE | 0.9
2024 | nonsummer | PIT7_7_UNIT 1 | RTU_RIG | 0
2024 | nonsummer | PIT7_7_UNIT 1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | PIT7_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 1422.4287
2024 | nonsummer | PIT7_7_UNIT 2 | METERING_TELEMETRY | 0.4
2024 | nonsummer | PIT7_7_UNIT 2 | PLANT_TROUBLE | 0
2024 | nonsummer | PIT7_7_UNIT 2 | RTU_RIG | 0
2024 | nonsummer | PIT7_7_UNIT 2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | PIUTE_6_GNBSR1 | PLANT_MAINTENANCE | 7.1
2024 | nonsummer | PLACVL_1_CHILIB | PLANT_MAINTENANCE | 0
2024 | nonsummer | PLACVL_1_CHILIB | PLANT_TROUBLE | 0
2024 | nonsummer | PLACVL_1_CHILIB | TRANSMISSION_INDUCED | 0
2024 | nonsummer | PLAINV_6_BSOLAR | PLANT_TROUBLE | 912.3583
2024 | nonsummer | PLAINV_6_BSOLAR | TRANSMISSION_INDUCED | 0
2024 | nonsummer | PLAINV_6_DSOLAR | PLANT_TROUBLE | 60
2024 | nonsummer | PLAINV_6_DSOLAR | TRANSMISSION_INDUCED | 0
2024 | nonsummer | PLAINV_6_NLRSR1 | PLANT_TROUBLE | 212.8333
2024 | nonsummer | PLAINV_6_NLRSR1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | PLAINV_6_SOLAR3 | METERING_TELEMETRY | 0
2024 | nonsummer | PLAINV_6_SOLAR3 | PLANT_TROUBLE | 1360
2024 | nonsummer | PLAINV_6_SOLAR3 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | PLAINV_6_SOLARC | PLANT_TROUBLE | 5.775
2024 | nonsummer | PLAINV_6_SOLARC | TRANSMISSION_INDUCED | 0
2024 | nonsummer | PLMSSR_6_HISIER | PLANT_MAINTENANCE | 15.0238
2024 | nonsummer | PLMSSR_6_HISIER | PLANT_TROUBLE | 358.5165
2024 | nonsummer | PLMSSR_6_HISIER | TRANSMISSION_INDUCED | 43.3
2024 | nonsummer | PLSNTG_7_LNCLND | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 99.628
2024 | nonsummer | PLSNTG_7_LNCLND | PLANT_MAINTENANCE | 0
2024 | nonsummer | PLSNTG_7_LNCLND | PLANT_TROUBLE | 253.756
2024 | nonsummer | PMDLET_6_SOLAR1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | PMDLET_6_SOLAR1 | PLANT_TROUBLE | 182.95
2024 | nonsummer | PMDLET_6_SOLAR1 | TRANSMISSION_INDUCED | 50
2024 | nonsummer | PMPJCK_1_RB2SLR | PLANT_MAINTENANCE | 80
2024 | nonsummer | PMPJCK_1_RB2SLR | TRANSMISSION_INDUCED | 0
2024 | nonsummer | PMPJCK_1_SOLAR1 | PLANT_MAINTENANCE | 80
2024 | nonsummer | PMPJCK_1_SOLAR1 | TRANSMISSION_INDUCED | 60
2024 | nonsummer | PMPJCK_1_SOLAR2 | PLANT_MAINTENANCE | 80
2024 | nonsummer | PMPJCK_1_SOLAR2 | PLANT_TROUBLE | 0
2024 | nonsummer | PMPJCK_1_SOLAR2 | TRANSMISSION_INDUCED | 40
2024 | nonsummer | PNCHEG_2_PL1X4 | AMBIENT_DUE_TO_TEMP | 3107.8783
2024 | nonsummer | PNCHEG_2_PL1X4 | AMBIENT_NOT_DUE_TO_TEMP | 766.95
2024 | nonsummer | PNCHEG_2_PL1X4 | PLANT_MAINTENANCE | 23886
2024 | nonsummer | PNCHEG_2_PL1X4 | PLANT_TROUBLE | 8898.0167
2024 | nonsummer | PNCHEG_2_PL1X4 | SHORT_TERM_USE_LIMIT_REACHED | 32325.6
2024 | nonsummer | PNCHEG_2_PL1X4 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2024 | nonsummer | PNCHEG_2_PL1X4 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | PNCHPP_1_PL1X2 | AMBIENT_DUE_TO_TEMP | 1663.88
2024 | nonsummer | PNCHPP_1_PL1X2 | METERING_TELEMETRY | 399.7
2024 | nonsummer | PNCHPP_1_PL1X2 | PLANT_MAINTENANCE | 1798.65
2024 | nonsummer | PNCHPP_1_PL1X2 | PLANT_TROUBLE | 1023.1335
2024 | nonsummer | PNCHPP_1_PL1X2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | PNCHVS_2_SOLAR | PLANT_MAINTENANCE | 140
2024 | nonsummer | PNCHVS_2_SOLAR | PLANT_TROUBLE | 99.6
2024 | nonsummer | PNOCHE_1_PL1X2 | AMBIENT_DUE_TO_TEMP | 107.6137
2024 | nonsummer | PNOCHE_1_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | PNOCHE_1_PL1X2 | PLANT_MAINTENANCE | 249.85
2024 | nonsummer | PNOCHE_1_PL1X2 | PLANT_TROUBLE | 1413.3182
2024 | nonsummer | PNOCHE_1_PL1X2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | PNOCHE_1_UNITA1 | PLANT_MAINTENANCE | 4330.44
2024 | nonsummer | PNOCHE_1_UNITA1 | PLANT_TROUBLE | 759.6
2024 | nonsummer | PNOCHE_1_UNITA1 | UNIT_TESTING | 0
2024 | nonsummer | POEPH_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 5285.6058
2024 | nonsummer | POEPH_7_UNIT 1 | PLANT_TROUBLE | 3791.5167
2024 | nonsummer | POEPH_7_UNIT 1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | POEPH_7_UNIT 2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | POEPH_7_UNIT 2 | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | POEPH_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 1799.6717
2024 | nonsummer | POEPH_7_UNIT 2 | PLANT_TROUBLE | 3610.5
2024 | nonsummer | POEPH_7_UNIT 2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | POLRIS_2_ASEBT1 | METERING_TELEMETRY | 0
2024 | nonsummer | POLRIS_2_ASEBT1 | PLANT_MAINTENANCE | 69.0667
2024 | nonsummer | POLRIS_2_ASEBT1 | PLANT_TROUBLE | 998.8667
2024 | nonsummer | POLRIS_2_ASEBT1 | TRANSMISSION_INDUCED | 56
2024 | nonsummer | POLRIS_2_ASEBT1 | UNIT_TESTING | 0
2024 | nonsummer | POLRIS_2_ASESR1 | METERING_TELEMETRY | 0
2024 | nonsummer | POLRIS_2_ASESR1 | PLANT_MAINTENANCE | 56
2024 | nonsummer | POLRIS_2_ASESR1 | PLANT_TROUBLE | 657.7667
2024 | nonsummer | POLRIS_2_ASESR1 | TRANSMISSION_INDUCED | 112
2024 | nonsummer | POLRIS_2_ASRBT1 | METERING_TELEMETRY | 0
2024 | nonsummer | POLRIS_2_ASRBT1 | PLANT_MAINTENANCE | 80
2024 | nonsummer | POLRIS_2_ASRBT1 | PLANT_TROUBLE | 9519.6667
2024 | nonsummer | POLRIS_2_ASRBT1 | RTU_RIG | 0
2024 | nonsummer | POLRIS_2_ASRBT1 | TRANSMISSION_INDUCED | 240
2024 | nonsummer | POLRIS_2_ASRBT1 | UNIT_TESTING | 0
2024 | nonsummer | POLRIS_2_ASRSR1 | METERING_TELEMETRY | 0
2024 | nonsummer | POLRIS_2_ASRSR1 | NEW_GENERATOR_TEST_ENERGY | 2500
2024 | nonsummer | POLRIS_2_ASRSR1 | PLANT_MAINTENANCE | 125
2024 | nonsummer | POLRIS_2_ASRSR1 | PLANT_TROUBLE | 690
2024 | nonsummer | POLRIS_2_ASRSR1 | TRANSMISSION_INDUCED | 354
2024 | nonsummer | POTTER_7_VECINO | TRANSMISSION_INDUCED | 0
2024 | nonsummer | PRCTVY_1_MIGBT1 | METERING_TELEMETRY | 12.3
2024 | nonsummer | PRCTVY_1_MIGBT1 | PLANT_MAINTENANCE | 15
2024 | nonsummer | PRCTVY_1_MIGBT1 | PLANT_TROUBLE | 886.4
2024 | nonsummer | PRCTVY_1_MIGBT1 | UNIT_TESTING | 30
2024 | nonsummer | PRIMM_2_SOLAR1 | METERING_TELEMETRY | 250
2024 | nonsummer | PRIMM_2_SOLAR1 | PLANT_MAINTENANCE | 1312.5433
2024 | nonsummer | PRIMM_2_SOLAR1 | PLANT_TROUBLE | 656.5933
2024 | nonsummer | PRIMM_2_SOLAR1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | PROXSR_2_PROSR1 | METERING_TELEMETRY | 0
2024 | nonsummer | PROXSR_2_PROSR1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | PROXSR_2_PROSR1 | PLANT_TROUBLE | 0
2024 | nonsummer | PROXSR_2_PROSR1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | PROXSR_2_PS1BT1 | AMBIENT_NOT_DUE_TO_TEMP | 43.3333
2024 | nonsummer | PROXSR_2_PS1BT1 | METERING_TELEMETRY | 0
2024 | nonsummer | PROXSR_2_PS1BT1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | PROXSR_2_PS1BT1 | PLANT_TROUBLE | 1684.6453
2024 | nonsummer | PROXSR_2_PS1BT1 | TRANSMISSION_INDUCED | 840
2024 | nonsummer | PROXSR_2_PS1BT1 | UNIT_TESTING | 0
2024 | nonsummer | PROXSR_2_PS1BT2 | NEW_GENERATOR_TEST_ENERGY | 166.9333
2024 | nonsummer | PROXSR_2_PS1BT2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | PROXSR_2_PS1BT2 | PLANT_TROUBLE | 423.3333
2024 | nonsummer | PROXSR_2_PS1BT2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | PROXSR_2_PS1BT2 | UNIT_TESTING | 0
2024 | nonsummer | PROXSR_2_PS1SR2 | NEW_GENERATOR_TEST_ENERGY | 209.22
2024 | nonsummer | PROXSR_2_PS1SR2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | PROXSR_2_PS1SR2 | PLANT_TROUBLE | 28.051
2024 | nonsummer | PROXSR_2_PS1SR2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | PROXSR_2_PS2BT3 | METERING_TELEMETRY | 0
2024 | nonsummer | PROXSR_2_PS2BT3 | PLANT_MAINTENANCE | 0
2024 | nonsummer | PROXSR_2_PS2BT3 | PLANT_TROUBLE | 6213.513
2024 | nonsummer | PROXSR_2_PS2BT3 | TRANSMISSION_INDUCED | 1890
2024 | nonsummer | PROXSR_2_PS2BT3 | UNIT_TESTING | 138
2024 | nonsummer | PUTHCR_1_PCNSB1 | METERING_TELEMETRY | 0
2024 | nonsummer | PUTHCR_1_PCNSB1 | PLANT_TROUBLE | 933.3
2024 | nonsummer | PUTHCR_1_SOLAR1 | METERING_TELEMETRY | 0
2024 | nonsummer | PVERDE_5_SCEDYN | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | PVERDE_5_SCEDYN | AMBIENT_NOT_DUE_TO_TEMP | 62.5
2024 | nonsummer | PVERDE_5_SCEDYN | PLANT_MAINTENANCE | 18719
2024 | nonsummer | PVERDE_5_SCEDYN | PLANT_TROUBLE | 2175
2024 | nonsummer | PWEST_1_UNIT | PLANT_TROUBLE | 1871.505
2024 | nonsummer | RAMON_2_SCEDYN | AMBIENT_NOT_DUE_TO_TEMP | 95461.7
2024 | nonsummer | RAMON_2_SCEDYN | PLANT_MAINTENANCE | 385
2024 | nonsummer | RAMON_2_SCEDYN | PLANT_TROUBLE | 576.6667
2024 | nonsummer | RAMON_2_SCEDYN | TRANSMISSION_INDUCED | 0
2024 | nonsummer | RATSKE_2_NROSR1 | PLANT_MAINTENANCE | 370
2024 | nonsummer | RATSKE_2_NROSR1 | PLANT_TROUBLE | 400
2024 | nonsummer | RATSKE_2_NROSR1 | TRANSMISSION_INDUCED | 825
2024 | nonsummer | RATSKE_2_RBSSB1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | RATSKE_2_RBSSB1 | PLANT_MAINTENANCE | 960
2024 | nonsummer | RATSKE_2_RBSSB1 | PLANT_TROUBLE | 0
2024 | nonsummer | RATSKE_2_RBSSB1 | TRANSMISSION_INDUCED | 323
2024 | nonsummer | RATSKE_2_RBSSB1 | UNIT_TESTING | 0
2024 | nonsummer | RATSKE_2_RBSSB2 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | RATSKE_2_RBSSB2 | PLANT_MAINTENANCE | 480
2024 | nonsummer | RATSKE_2_RBSSB2 | PLANT_TROUBLE | 0
2024 | nonsummer | RATSKE_2_RBSSB2 | TRANSMISSION_INDUCED | 215.3333
2024 | nonsummer | RATSKE_2_WAVBT1 | NEW_GENERATOR_TEST_ENERGY | 8820
2024 | nonsummer | RCKCRK_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 7872.6725
2024 | nonsummer | RCKCRK_7_UNIT 1 | PLANT_TROUBLE | 11.4333
2024 | nonsummer | RCKCRK_7_UNIT 1 | TRANSITIONAL_LIMITATION | 0
2024 | nonsummer | RCKCRK_7_UNIT 1 | TRANSMISSION_INDUCED | 57
2024 | nonsummer | RCKCRK_7_UNIT 1 | UNIT_TESTING | 0
2024 | nonsummer | RCKCRK_7_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 5450.315
2024 | nonsummer | RCKCRK_7_UNIT 2 | PLANT_TROUBLE | 48.365
2024 | nonsummer | RCKCRK_7_UNIT 2 | TRANSITIONAL_LIMITATION | 0
2024 | nonsummer | RCKCRK_7_UNIT 2 | TRANSMISSION_INDUCED | 20.8633
2024 | nonsummer | RDWAY_1_CREST | PLANT_TROUBLE | 4.25
2024 | nonsummer | RDWAY_1_SCKSR1 | METERING_TELEMETRY | 0
2024 | nonsummer | RDWAY_1_SCKSR1 | PLANT_MAINTENANCE | 30
2024 | nonsummer | RDWAY_1_SCKSR1 | PLANT_TROUBLE | 0
2024 | nonsummer | RECTOR_2_KAWEAH | AMBIENT_NOT_DUE_TO_TEMP | 6687
2024 | nonsummer | RECTOR_2_KAWEAH | TRANSMISSION_INDUCED | 30
2024 | nonsummer | RECTOR_2_KAWH 1 | AMBIENT_NOT_DUE_TO_TEMP | 2385
2024 | nonsummer | RECTOR_2_QF | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 7734.65
2024 | nonsummer | RECTOR_2_QF | ENVIRONMENTAL_RESTRICTIONS | 3515.75
2024 | nonsummer | RECTOR_2_QF | PLANT_MAINTENANCE | 6127.45
2024 | nonsummer | RECTOR_2_QF | PLANT_TROUBLE | 0
2024 | nonsummer | RECTOR_2_TFDBM1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 4
2024 | nonsummer | RECTOR_2_TFDBM1 | PLANT_MAINTENANCE | 13.36
2024 | nonsummer | RECTOR_2_TFDBM1 | PLANT_TROUBLE | 51.72
2024 | nonsummer | RECTOR_2_VISSR1 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | nonsummer | RECTOR_2_VISSR1 | PLANT_TROUBLE | 0
2024 | nonsummer | REDBLF_6_UNIT | PLANT_TROUBLE | 2012.2667
2024 | nonsummer | REDBLF_6_UNIT | UNIT_TESTING | 0
2024 | nonsummer | RENWD_1_QF | PLANT_MAINTENANCE | 652.2917
2024 | nonsummer | RENWD_1_QF | PLANT_TROUBLE | 100
2024 | nonsummer | RENWD_1_QF | TRANSMISSION_INDUCED | 0
2024 | nonsummer | RENWD_1_QF | UNIT_TESTING | 0
2024 | nonsummer | REXFRD_2_RSFBX2 | NEW_GENERATOR_TEST_ENERGY | 1200
2024 | nonsummer | REXFRD_2_RSFBX2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | REXFRD_2_RSFBX2 | PLANT_TROUBLE | 0
2024 | nonsummer | REXFRD_2_RSFBX2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | REXFRD_2_RSFSX2 | NEW_GENERATOR_TEST_ENERGY | 75021
2024 | nonsummer | REXFRD_2_RSFSX2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | REXFRD_2_RSFSX2 | PLANT_TROUBLE | 0
2024 | nonsummer | REXFRD_2_RSFSX2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | RICHMN_1_CHVSR2 | PLANT_TROUBLE | 40.6583
2024 | nonsummer | RICHMN_1_CHVSR2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | RICHMN_1_SOLAR | PLANT_MAINTENANCE | 3.6333
2024 | nonsummer | RICHMN_1_SOLAR | PLANT_TROUBLE | 27.1
2024 | nonsummer | RICHMN_7_BAYENV | PLANT_TROUBLE | 2650
2024 | nonsummer | RIOBRV_6_UNIT 1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 6650
2024 | nonsummer | RIOBRV_6_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | RIOBRV_6_UNIT 1 | PLANT_TROUBLE | 560
2024 | nonsummer | RIOBRV_6_UNIT 1 | TRANSMISSION_INDUCED | 28
2024 | nonsummer | RNDMTN_2_SLSPHY1 | METERING_TELEMETRY | 3
2024 | nonsummer | RNDSBG_1_HZASR1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | ROLLIN_6_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 5771.885
2024 | nonsummer | ROLLIN_6_UNIT | PLANT_TROUBLE | 3.2305
2024 | nonsummer | ROLLIN_6_UNIT | TRANSMISSION_INDUCED | 0
2024 | nonsummer | ROLLIN_6_UNIT | UNIT_TESTING | 0
2024 | nonsummer | ROMOLA_5_MPBBT1 | METERING_TELEMETRY | 0
2024 | nonsummer | ROMOLA_5_MPBBT1 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | nonsummer | ROMOLA_5_MPBBT1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | ROMOLA_5_MPBBT1 | PLANT_TROUBLE | 74.1667
2024 | nonsummer | ROMOLA_5_MPBBT1 | UNIT_TESTING | 0
2024 | nonsummer | ROMOLA_5_MPBBT2 | METERING_TELEMETRY | 0
2024 | nonsummer | ROMOLA_5_MPBBT2 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | nonsummer | ROMOLA_5_MPBBT2 | PLANT_TROUBLE | 0
2024 | nonsummer | ROMOLA_5_MPBBT3 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | nonsummer | ROMOLA_5_MPBBT3 | PLANT_MAINTENANCE | 19.1667
2024 | nonsummer | ROMOLA_5_MPBBT3 | PLANT_TROUBLE | 130.0833
2024 | nonsummer | ROMOLA_5_MPBBT3 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | ROMOLA_5_MPBBT3 | UNIT_TESTING | 0
2024 | nonsummer | ROMOLA_5_MPBBT4 | METERING_TELEMETRY | 0
2024 | nonsummer | ROMOLA_5_MPBBT4 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | nonsummer | ROMOLA_5_MPBBT4 | PLANT_TROUBLE | 337.75
2024 | nonsummer | ROMOLA_5_MPBBT4 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | ROSMDW_2_WIND1 | METERING_TELEMETRY | 0
2024 | nonsummer | ROSMDW_2_WIND1 | PLANT_MAINTENANCE | 3350.8
2024 | nonsummer | ROSMDW_2_WIND1 | PLANT_TROUBLE | 354.2333
2024 | nonsummer | ROSMDW_2_WIND1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | ROSMND_6_SOLAR | PLANT_TROUBLE | 7.5
2024 | nonsummer | ROSMND_6_SOLAR | TRANSMISSION_INDUCED | 0
2024 | nonsummer | RSMSLR_6_SOLAR1 | METERING_TELEMETRY | 0
2024 | nonsummer | RSMSLR_6_SOLAR1 | PLANT_MAINTENANCE | 51.6667
2024 | nonsummer | RSMSLR_6_SOLAR1 | PLANT_TROUBLE | 126
2024 | nonsummer | RSMSLR_6_SOLAR2 | PLANT_MAINTENANCE | 26
2024 | nonsummer | RSMSLR_6_SOLAR2 | PLANT_TROUBLE | 60
2024 | nonsummer | RTEDDY_2_RWSBT1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | RTEDDY_2_RWSBT1 | METERING_TELEMETRY | 7.5
2024 | nonsummer | RTEDDY_2_RWSBT1 | NEW_GENERATOR_TEST_ENERGY | 30
2024 | nonsummer | RTEDDY_2_RWSBT1 | PLANT_MAINTENANCE | 32
2024 | nonsummer | RTEDDY_2_RWSBT1 | PLANT_TROUBLE | 130
2024 | nonsummer | RTEDDY_2_RWSBT1 | UNIT_TESTING | 30
2024 | nonsummer | RTEDDY_2_RWSBT2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | RTEDDY_2_RWSBT2 | METERING_TELEMETRY | 7.5
2024 | nonsummer | RTEDDY_2_RWSBT2 | NEW_GENERATOR_TEST_ENERGY | 30
2024 | nonsummer | RTEDDY_2_RWSBT2 | PLANT_MAINTENANCE | 39
2024 | nonsummer | RTEDDY_2_RWSBT2 | PLANT_TROUBLE | 736.8667
2024 | nonsummer | RTEDDY_2_RWSBT2 | UNIT_TESTING | 30
2024 | nonsummer | RTEDDY_2_RWSBT3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | RTEDDY_2_RWSBT3 | METERING_TELEMETRY | 0
2024 | nonsummer | RTEDDY_2_RWSBT3 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | nonsummer | RTEDDY_2_RWSBT3 | PLANT_MAINTENANCE | 45
2024 | nonsummer | RTEDDY_2_RWSBT3 | PLANT_TROUBLE | 81.5
2024 | nonsummer | RTEDDY_2_RWSBT3 | UNIT_TESTING | 45
2024 | nonsummer | RTEDDY_2_RWSBT4 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 73.5
2024 | nonsummer | RTEDDY_2_RWSBT4 | METERING_TELEMETRY | 7.5
2024 | nonsummer | RTEDDY_2_RWSBT4 | NEW_GENERATOR_TEST_ENERGY | 30
2024 | nonsummer | RTEDDY_2_RWSBT4 | PLANT_MAINTENANCE | 30
2024 | nonsummer | RTEDDY_2_RWSBT4 | PLANT_TROUBLE | 66.2
2024 | nonsummer | RTEDDY_2_RWSBT4 | UNIT_TESTING | 30
2024 | nonsummer | RTEDDY_2_RWSBT5 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | RTEDDY_2_RWSBT5 | METERING_TELEMETRY | 3
2024 | nonsummer | RTEDDY_2_RWSBT5 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | nonsummer | RTEDDY_2_RWSBT5 | PLANT_MAINTENANCE | 32
2024 | nonsummer | RTEDDY_2_RWSBT5 | PLANT_TROUBLE | 1
2024 | nonsummer | RTEDDY_2_RWSBT5 | UNIT_TESTING | 12
2024 | nonsummer | RTEDDY_2_SC1SR3 | METERING_TELEMETRY | 120
2024 | nonsummer | RTEDDY_2_SC1SR3 | PLANT_MAINTENANCE | 240
2024 | nonsummer | RTEDDY_2_SC1SR3 | PLANT_TROUBLE | 0
2024 | nonsummer | RTEDDY_2_SEBSR3 | METERING_TELEMETRY | 168
2024 | nonsummer | RTEDDY_2_SEBSR3 | PLANT_MAINTENANCE | 339.7333
2024 | nonsummer | RTEDDY_2_SEBSR3 | PLANT_TROUBLE | 1324
2024 | nonsummer | RTEDDY_2_SEBSR3 | UNIT_TESTING | 0
2024 | nonsummer | RTEDDY_2_SEBSR4 | METERING_TELEMETRY | 168
2024 | nonsummer | RTEDDY_2_SEBSR4 | PLANT_MAINTENANCE | 1120
2024 | nonsummer | RTEDDY_2_SEBSR4 | PLANT_TROUBLE | 1027.6
2024 | nonsummer | RTEDDY_2_SOLAR1 | PLANT_MAINTENANCE | 162
2024 | nonsummer | RTEDDY_2_SOLAR1 | PLANT_TROUBLE | 207.9
2024 | nonsummer | RTEDDY_2_SOLAR1 | UNIT_TESTING | 0
2024 | nonsummer | RTEDDY_2_SOLAR2 | PLANT_MAINTENANCE | 324
2024 | nonsummer | RTEDDY_2_SOLAR2 | PLANT_TROUBLE | 0
2024 | nonsummer | RTEDDY_2_SPASR4 | METERING_TELEMETRY | 78
2024 | nonsummer | RTEDDY_2_SPASR4 | PLANT_MAINTENANCE | 607.9667
2024 | nonsummer | RTEDDY_2_SPASR4 | PLANT_TROUBLE | 221
2024 | nonsummer | RTEDDY_2_SRXSR4 | METERING_TELEMETRY | 40.8
2024 | nonsummer | RTEDDY_2_SRXSR4 | PLANT_MAINTENANCE | 189.9467
2024 | nonsummer | RTEDDY_2_SRXSR4 | PLANT_TROUBLE | 0
2024 | nonsummer | RTEDDY_2_SRXSR4 | UNIT_TESTING | 0
2024 | nonsummer | RTREE_2_WIND1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | RTREE_2_WIND2 | AMBIENT_NOT_DUE_TO_TEMP | 10.725
2024 | nonsummer | RTREE_2_WIND2 | PLANT_MAINTENANCE | 2406.855
2024 | nonsummer | RTREE_2_WIND2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | RTREE_2_WIND3 | PLANT_MAINTENANCE | 245.15
2024 | nonsummer | RTREE_2_WIND3 | PLANT_TROUBLE | 318.1667
2024 | nonsummer | RTREE_2_WIND3 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | RUSCTY_2_UNITS | AMBIENT_DUE_TO_TEMP | 17191.2517
2024 | nonsummer | RUSCTY_2_UNITS | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | nonsummer | RUSCTY_2_UNITS | PLANT_MAINTENANCE | 1607.2483
2024 | nonsummer | RUSCTY_2_UNITS | PLANT_TROUBLE | 320.1
2024 | nonsummer | RUSCTY_2_UNITS | TRANSITIONAL_LIMITATION | 982.5667
2024 | nonsummer | RUSCTY_2_UNITS | UNIT_TESTING | 292
2024 | nonsummer | RUSSELL_2_SOLANO1 | PLANT_MAINTENANCE | 3379.1703
2024 | nonsummer | RUSSELL_2_SOLANO1 | PLANT_TROUBLE | 4672.04
2024 | nonsummer | RVRVEW_1_UNITA1 | AMBIENT_DUE_TO_TEMP | 241.21
2024 | nonsummer | RVRVEW_1_UNITA1 | PLANT_MAINTENANCE | 97.4
2024 | nonsummer | RVRVEW_1_UNITA1 | PLANT_TROUBLE | 408.2683
2024 | nonsummer | RVRVEW_1_UNITA1 | UNIT_TESTING | 0
2024 | nonsummer | RVSIDE_2_RERCU3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | RVSIDE_2_RERCU3 | AMBIENT_NOT_DUE_TO_TEMP | 89.8333
2024 | nonsummer | RVSIDE_2_RERCU3 | ENVIRONMENTAL_RESTRICTIONS | 29
2024 | nonsummer | RVSIDE_2_RERCU3 | PLANT_MAINTENANCE | 0
2024 | nonsummer | RVSIDE_2_RERCU3 | PLANT_TROUBLE | 98
2024 | nonsummer | RVSIDE_2_RERCU4 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | RVSIDE_2_RERCU4 | AMBIENT_NOT_DUE_TO_TEMP | 89.8333
2024 | nonsummer | RVSIDE_2_RERCU4 | ENVIRONMENTAL_RESTRICTIONS | 3.9667
2024 | nonsummer | RVSIDE_2_RERCU4 | PLANT_MAINTENANCE | 0
2024 | nonsummer | RVSIDE_2_RERCU4 | PLANT_TROUBLE | 0
2024 | nonsummer | RVSIDE_6_RERCU1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | RVSIDE_6_RERCU1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | RVSIDE_6_RERCU1 | PLANT_TROUBLE | 0
2024 | nonsummer | RVSIDE_6_RERCU2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | RVSIDE_6_RERCU2 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | RVSIDE_6_RERCU2 | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | nonsummer | RVSIDE_6_RERCU2 | PLANT_TROUBLE | 3880
2024 | nonsummer | RVSIDE_6_SPRING | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | RVSIDE_6_SPRING | AMBIENT_NOT_DUE_TO_TEMP | 66
2024 | nonsummer | RVSIDE_6_SPRING | PLANT_TROUBLE | 0
2024 | nonsummer | SALIRV_2_UNIT | PLANT_MAINTENANCE | 3510
2024 | nonsummer | SALIRV_2_UNIT | PLANT_TROUBLE | 2838.55
2024 | nonsummer | SALTSP_7_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 16775.85
2024 | nonsummer | SALTSP_7_UNITS | PLANT_TROUBLE | 45.25
2024 | nonsummer | SALTSP_7_UNITS | TRANSMISSION_INDUCED | 445.2333
2024 | nonsummer | SAMPSN_6_KELCO1 | PLANT_MAINTENANCE | 1125
2024 | nonsummer | SAMPSN_6_KELCO1 | PLANT_TROUBLE | 1019.5833
2024 | nonsummer | SANBRN_2_EESSB2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | SANBRN_2_EESSB2 | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | SANBRN_2_EESSB2 | PLANT_MAINTENANCE | 123.5
2024 | nonsummer | SANBRN_2_EESSB2 | PLANT_TROUBLE | 749.5167
2024 | nonsummer | SANBRN_2_EESSB2 | UNIT_TESTING | 255.5
2024 | nonsummer | SANBRN_2_ES1BT3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 72.569
2024 | nonsummer | SANBRN_2_ES1BT3 | PLANT_MAINTENANCE | 41.72
2024 | nonsummer | SANBRN_2_ES1BT3 | PLANT_TROUBLE | 252.15
2024 | nonsummer | SANBRN_2_ES2SB3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 56
2024 | nonsummer | SANBRN_2_ES2SB3 | PLANT_MAINTENANCE | 0
2024 | nonsummer | SANBRN_2_ES2SB3 | PLANT_TROUBLE | 0
2024 | nonsummer | SANBRN_2_ESABT1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | SANBRN_2_ESABT1 | PLANT_TROUBLE | 26.6667
2024 | nonsummer | SANBRN_2_ESBBT1 | METERING_TELEMETRY | 0
2024 | nonsummer | SANBRN_2_ESBBT1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | SANBRN_2_ESBBT1 | PLANT_TROUBLE | 1765.3333
2024 | nonsummer | SANBRN_2_SS2BT3 | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | SANBRN_2_SS2BT3 | METERING_TELEMETRY | 0
2024 | nonsummer | SANBRN_2_SS2BT3 | PLANT_MAINTENANCE | 0
2024 | nonsummer | SANBRN_2_SS2BT3 | PLANT_TROUBLE | 2900.3833
2024 | nonsummer | SANBRN_2_SS2BT3 | UNIT_TESTING | 242
2024 | nonsummer | SANBRN_2_SS2BT4 | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | SANBRN_2_SS2BT4 | METERING_TELEMETRY | 0
2024 | nonsummer | SANBRN_2_SS2BT4 | PLANT_MAINTENANCE | 0
2024 | nonsummer | SANBRN_2_SS2BT4 | PLANT_TROUBLE | 0
2024 | nonsummer | SANBRN_2_SS2BT4 | UNIT_TESTING | 0
2024 | nonsummer | SANBRN_2_SS2SB4 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | SANBRN_2_SS2SB4 | METERING_TELEMETRY | 0
2024 | nonsummer | SANBRN_2_SS2SB4 | PLANT_MAINTENANCE | 30
2024 | nonsummer | SANBRN_2_SS2SB4 | PLANT_TROUBLE | 333
2024 | nonsummer | SANBRN_2_SS2SB4 | UNIT_TESTING | 180
2024 | nonsummer | SANDLT_2_SUNITS | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | SANDLT_2_SUNITS | AMBIENT_NOT_DUE_TO_TEMP | 28655
2024 | nonsummer | SANDLT_2_SUNITS | METERING_TELEMETRY | 0
2024 | nonsummer | SANDLT_2_SUNITS | PLANT_MAINTENANCE | 755
2024 | nonsummer | SANDLT_2_SUNITS | PLANT_TROUBLE | 1706.0583
2024 | nonsummer | SANDLT_2_SUNITS | UNIT_TESTING | 0
2024 | nonsummer | SANDRN_2_SS1SR1 | METERING_TELEMETRY | 0
2024 | nonsummer | SANDRN_2_SS1SR1 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | nonsummer | SANDRN_2_SS1SR1 | PLANT_TROUBLE | 375
2024 | nonsummer | SANDRN_2_SS1SR1 | TRANSMISSION_INDUCED | 500
2024 | nonsummer | SANDRN_2_SS1SR1 | UNIT_TESTING | 9214
2024 | nonsummer | SANDRN_2_SS2SR2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 2134.5
2024 | nonsummer | SANDRN_2_SS2SR2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | SANDRN_2_SS2SR2 | PLANT_TROUBLE | 0
2024 | nonsummer | SANDRN_2_SS2SR2 | UNIT_TESTING | 0
2024 | nonsummer | SANLOB_1_LNDFIL | AMBIENT_NOT_DUE_TO_TEMP | 2167.5
2024 | nonsummer | SANLOB_1_LNDFIL | PLANT_MAINTENANCE | 1.5
2024 | nonsummer | SANLOB_1_LNDFIL | PLANT_TROUBLE | 2.0533
2024 | nonsummer | SANTFG_7_UNITS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 17299.3333
2024 | nonsummer | SANTFG_7_UNITS | PLANT_TROUBLE | 1655.0167
2024 | nonsummer | SANTFG_7_UNITS | TRANSITIONAL_LIMITATION | 0
2024 | nonsummer | SANTFG_7_UNITS | TRANSMISSION_INDUCED | 0
2024 | nonsummer | SANTGO_2_LNDFL1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 19.5
2024 | nonsummer | SANTGO_2_LNDFL1 | AMBIENT_DUE_TO_TEMP | 104.9017
2024 | nonsummer | SANTGO_2_LNDFL1 | METERING_TELEMETRY | 0
2024 | nonsummer | SANTGO_2_LNDFL1 | PLANT_MAINTENANCE | 477.69
2024 | nonsummer | SANTGO_2_LNDFL1 | PLANT_TROUBLE | 548.1492
2024 | nonsummer | SANTGO_2_LNDFL1 | TRANSMISSION_INDUCED | 163.7
2024 | nonsummer | SANTGO_2_LNDFL1 | UNIT_TESTING | 3.3
2024 | nonsummer | SANTGO_2_MABBT1 | PLANT_TROUBLE | 2008
2024 | nonsummer | SANTGO_2_MABBT1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | SANWD_1_QF | PLANT_MAINTENANCE | 8502.9967
2024 | nonsummer | SANWD_1_QF | PLANT_TROUBLE | 2745.73
2024 | nonsummer | SANWD_1_QF | TRANSMISSION_INDUCED | 98.6833
2024 | nonsummer | SAUGUS_2_SPESBT1 | METERING_TELEMETRY | 0
2024 | nonsummer | SAUGUS_2_SPESBT1 | PLANT_MAINTENANCE | 2800
2024 | nonsummer | SAUGUS_2_SPESBT1 | PLANT_TROUBLE | 1113
2024 | nonsummer | SAUGUS_2_SPESBT1 | RTU_RIG | 0
2024 | nonsummer | SAUGUS_2_SPESBT1 | UNIT_TESTING | 5317
2024 | nonsummer | SAUGUS_6_MWDFTH | PLANT_TROUBLE | 3321.5
2024 | nonsummer | SAUGUS_7_CHIQCN | PLANT_TROUBLE | 5800
2024 | nonsummer | SBERDO_2_PSP3 | AMBIENT_DUE_TO_TEMP | 666.1
2024 | nonsummer | SBERDO_2_PSP3 | AMBIENT_DUE_TO_TEMP | 90.33
2024 | nonsummer | SBERDO_2_PSP3 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | SBERDO_2_PSP3 | ENVIRONMENTAL_RESTRICTIONS | 1037.5
2024 | nonsummer | SBERDO_2_PSP3 | METERING_TELEMETRY | 0
2024 | nonsummer | SBERDO_2_PSP3 | PLANT_MAINTENANCE | 3050
2024 | nonsummer | SBERDO_2_PSP3 | PLANT_MAINTENANCE | 11175
2024 | nonsummer | SBERDO_2_PSP3 | PLANT_TROUBLE | 4279.1667
2024 | nonsummer | SBERDO_2_PSP3 | PLANT_TROUBLE | 157.25
2024 | nonsummer | SBERDO_2_PSP3 | UNIT_TESTING | 222.99
2024 | nonsummer | SBERDO_2_PSP4 | AMBIENT_DUE_TO_TEMP | 4058.7543
2024 | nonsummer | SBERDO_2_PSP4 | METERING_TELEMETRY | 4
2024 | nonsummer | SBERDO_2_PSP4 | PLANT_MAINTENANCE | 7129.84
2024 | nonsummer | SBERDO_2_PSP4 | PLANT_TROUBLE | 33122.578
2024 | nonsummer | SBERDO_2_PSP4 | UNIT_TESTING | 4368.6
2024 | nonsummer | SBERDO_2_SNTANA | AMBIENT_NOT_DUE_TO_TEMP | 1492
2024 | nonsummer | SBERDO_2_SNTANA | PLANT_TROUBLE | 4832.5
2024 | nonsummer | SBERDO_6_MILLCK | AMBIENT_NOT_DUE_TO_TEMP | 560.625
2024 | nonsummer | SBERDO_6_MILLCK | PLANT_TROUBLE | 1705.8
2024 | nonsummer | SBERDO_6_MILLCK | TRANSMISSION_INDUCED | 0
2024 | nonsummer | SCARLT_2_SS2BT1 | PLANT_MAINTENANCE | 210
2024 | nonsummer | SCARLT_2_SS2BT1 | PLANT_TROUBLE | 12717.5
2024 | nonsummer | SCARLT_2_SS2BT1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | SCARLT_2_SS2BT1 | UNIT_TESTING | 0
2024 | nonsummer | SCARLT_2_SS2SR1 | PLANT_MAINTENANCE | 776.6667
2024 | nonsummer | SCARLT_2_SS2SR1 | PLANT_TROUBLE | 260
2024 | nonsummer | SCARLT_2_SS2SR1 | UNIT_TESTING | 0
2024 | nonsummer | SCARLT_2_SSABT1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 50
2024 | nonsummer | SCARLT_2_SSABT1 | METERING_TELEMETRY | 0
2024 | nonsummer | SCARLT_2_SSABT1 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | nonsummer | SCARLT_2_SSABT1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | SCARLT_2_SSABT1 | PLANT_TROUBLE | 710.8133
2024 | nonsummer | SCARLT_2_SSABT1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | SCARLT_2_SSABT1 | UNIT_TESTING | 130
2024 | nonsummer | SCARLT_2_SSASR1 | METERING_TELEMETRY | 0
2024 | nonsummer | SCARLT_2_SSASR1 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | nonsummer | SCARLT_2_SSASR1 | PLANT_MAINTENANCE | 1496.4833
2024 | nonsummer | SCARLT_2_SSASR1 | PLANT_TROUBLE | 606.2333
2024 | nonsummer | SCARLT_2_SSASR1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | SCARLT_2_SSASR1 | UNIT_TESTING | 626.6667
2024 | nonsummer | SCARLT_2_SSBBT1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | SCARLT_2_SSBBT1 | METERING_TELEMETRY | 0
2024 | nonsummer | SCARLT_2_SSBBT1 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | nonsummer | SCARLT_2_SSBBT1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | SCARLT_2_SSBBT1 | PLANT_TROUBLE | 2600.7333
2024 | nonsummer | SCARLT_2_SSBBT1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | SCARLT_2_SSBBT1 | UNIT_TESTING | 450
2024 | nonsummer | SCARLT_2_SSBSR1 | METERING_TELEMETRY | 0
2024 | nonsummer | SCARLT_2_SSBSR1 | NEW_GENERATOR_TEST_ENERGY | 500
2024 | nonsummer | SCARLT_2_SSBSR1 | PLANT_MAINTENANCE | 1107.7193
2024 | nonsummer | SCARLT_2_SSBSR1 | PLANT_TROUBLE | 1088.5
2024 | nonsummer | SCARLT_2_SSBSR1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | SCARLT_2_SSBSR1 | UNIT_TESTING | 626.6667
2024 | nonsummer | SCEC_1_PDRP124 | METERING_TELEMETRY | 0
2024 | nonsummer | SCEC_1_PDRP124 | MONTHLY_USE_LIMIT_REACHED | 42.6
2024 | nonsummer | SCEC_1_PDRP124 | PLANT_MAINTENANCE | 31.95
2024 | nonsummer | SCEC_1_PDRP16 | MONTHLY_USE_LIMIT_REACHED | 0
2024 | nonsummer | SCEC_1_PDRP173 | METERING_TELEMETRY | 0
2024 | nonsummer | SCEC_1_PDRP173 | MONTHLY_USE_LIMIT_REACHED | 49.2
2024 | nonsummer | SCEC_1_PDRP173 | PLANT_MAINTENANCE | 36.9
2024 | nonsummer | SCEC_1_PDRP60 | METERING_TELEMETRY | 0
2024 | nonsummer | SCEC_1_RDRR08 | SHORT_TERM_USE_LIMIT_REACHED | 0
2024 | nonsummer | SCEC_1_RDRR08 | UNIT_TESTING | 0
2024 | nonsummer | SCEC_1_RDRR38 | SHORT_TERM_USE_LIMIT_REACHED | 0
2024 | nonsummer | SCEC_1_RDRR39 | SHORT_TERM_USE_LIMIT_REACHED | 0
2024 | nonsummer | SCEN_6_RDRR02 | SHORT_TERM_USE_LIMIT_REACHED | 0
2024 | nonsummer | SCEN_6_RDRR02 | UNIT_TESTING | 0
2024 | nonsummer | SCEW_2_PDRP03 | METERING_TELEMETRY | 0
2024 | nonsummer | SCEW_2_PDRP03 | MONTHLY_USE_LIMIT_REACHED | 10.54
2024 | nonsummer | SCEW_2_PDRP03 | PLANT_MAINTENANCE | 79.05
2024 | nonsummer | SCEW_2_PDRP09 | METERING_TELEMETRY | 0
2024 | nonsummer | SCEW_2_PDRP09 | MONTHLY_USE_LIMIT_REACHED | 28.93
2024 | nonsummer | SCEW_2_PDRP09 | PLANT_MAINTENANCE | 39.45
2024 | nonsummer | SCEW_2_PDRP10 | METERING_TELEMETRY | 13.15
2024 | nonsummer | SCEW_2_PDRP10 | MONTHLY_USE_LIMIT_REACHED | 39.45
2024 | nonsummer | SCEW_2_PDRP10 | OTHER_USE_LIMIT_REACHED | 0
2024 | nonsummer | SCEW_2_PDRP10 | PLANT_MAINTENANCE | 39.45
2024 | nonsummer | SCEW_2_PDRP114 | METERING_TELEMETRY | 0
2024 | nonsummer | SCEW_2_PDRP114 | MONTHLY_USE_LIMIT_REACHED | 145
2024 | nonsummer | SCEW_2_PDRP114 | PLANT_MAINTENANCE | 87
2024 | nonsummer | SCEW_2_PDRP12 | MONTHLY_USE_LIMIT_REACHED | 0
2024 | nonsummer | SCEW_2_PDRP159 | METERING_TELEMETRY | 0
2024 | nonsummer | SCEW_2_PDRP159 | MONTHLY_USE_LIMIT_REACHED | 203.5
2024 | nonsummer | SCEW_2_PDRP159 | PLANT_MAINTENANCE | 203.5
2024 | nonsummer | SCEW_2_PDRP160 | METERING_TELEMETRY | 0
2024 | nonsummer | SCEW_2_PDRP160 | MONTHLY_USE_LIMIT_REACHED | 105.2
2024 | nonsummer | SCEW_2_PDRP160 | PLANT_MAINTENANCE | 131.5
2024 | nonsummer | SCEW_2_PDRP163 | METERING_TELEMETRY | 0
2024 | nonsummer | SCEW_2_PDRP163 | MONTHLY_USE_LIMIT_REACHED | 161.6
2024 | nonsummer | SCEW_2_PDRP163 | PLANT_MAINTENANCE | 121.2
2024 | nonsummer | SCEW_2_PDRP167 | METERING_TELEMETRY | 0
2024 | nonsummer | SCEW_2_PDRP167 | MONTHLY_USE_LIMIT_REACHED | 259
2024 | nonsummer | SCEW_2_PDRP167 | PLANT_MAINTENANCE | 155.4
2024 | nonsummer | SCEW_2_PDRP85 | METERING_TELEMETRY | 0
2024 | nonsummer | SCEW_2_PDRP89 | METERING_TELEMETRY | 0
2024 | nonsummer | SCEW_2_RDRR08 | SHORT_TERM_USE_LIMIT_REACHED | 0
2024 | nonsummer | SCEW_2_RDRR08 | UNIT_TESTING | 0
2024 | nonsummer | SCHD_1_RDRR08 | SHORT_TERM_USE_LIMIT_REACHED | 0
2024 | nonsummer | SCHD_1_RDRR08 | UNIT_TESTING | 0
2024 | nonsummer | SCHLTE_1_PL1X3 | AMBIENT_DUE_TO_TEMP | 982.7707
2024 | nonsummer | SCHLTE_1_PL1X3 | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | nonsummer | SCHLTE_1_PL1X3 | PLANT_MAINTENANCE | 929.7107
2024 | nonsummer | SCHLTE_1_PL1X3 | PLANT_TROUBLE | 4137.594
2024 | nonsummer | SCHLTE_1_PL1X3 | UNIT_TESTING | 0
2024 | nonsummer | SCHNDR_1_FIVPTS | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | SCHNDR_1_FIVPTS | METERING_TELEMETRY | 0
2024 | nonsummer | SCHNDR_1_FIVPTS | PLANT_TROUBLE | 21.625
2024 | nonsummer | SCHNDR_1_FIVPTS | UNIT_TESTING | 0
2024 | nonsummer | SCHNDR_1_WSTSDE | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | SCHNDR_1_WSTSDE | PLANT_TROUBLE | 6111.625
2024 | nonsummer | SCNW_6_PDRP57 | MONTHLY_USE_LIMIT_REACHED | 0
2024 | nonsummer | SCNW_6_PDRP61 | MONTHLY_USE_LIMIT_REACHED | 43.05
2024 | nonsummer | SCNW_6_RDRR08 | SHORT_TERM_USE_LIMIT_REACHED | 0
2024 | nonsummer | SCNW_6_RDRR08 | UNIT_TESTING | 0
2024 | nonsummer | SEARLS_1_TS3SR1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | SEGS_1_SR2SL2 | METERING_TELEMETRY | 30
2024 | nonsummer | SEGS_1_SR2SL2 | PLANT_TROUBLE | 0
2024 | nonsummer | SEGS_1_SR2SL2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | SEGS_1_SR2SL2 | UNIT_TESTING | 5
2024 | nonsummer | SENTNL_2_CTG1 | AMBIENT_DUE_TO_TEMP | 5595.9832
2024 | nonsummer | SENTNL_2_CTG1 | AMBIENT_DUE_TO_TEMP | 1152.72
2024 | nonsummer | SENTNL_2_CTG1 | METERING_TELEMETRY | 0
2024 | nonsummer | SENTNL_2_CTG1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | SENTNL_2_CTG1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | SENTNL_2_CTG1 | PLANT_TROUBLE | 142.5083
2024 | nonsummer | SENTNL_2_CTG1 | PLANT_TROUBLE | 0
2024 | nonsummer | SENTNL_2_CTG1 | UNIT_TESTING | 0
2024 | nonsummer | SENTNL_2_CTG2 | AMBIENT_DUE_TO_TEMP | 6750.8553
2024 | nonsummer | SENTNL_2_CTG2 | METERING_TELEMETRY | 0
2024 | nonsummer | SENTNL_2_CTG2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | SENTNL_2_CTG2 | PLANT_TROUBLE | 48.625
2024 | nonsummer | SENTNL_2_CTG2 | RIMS_OUTAGE | 0
2024 | nonsummer | SENTNL_2_CTG2 | UNIT_TESTING | 50.571
2024 | nonsummer | SENTNL_2_CTG3 | PLANT_TROUBLE | 105690
2024 | nonsummer | SENTNL_2_CTG4 | AMBIENT_DUE_TO_TEMP | 1381.05
2024 | nonsummer | SENTNL_2_CTG4 | AMBIENT_DUE_TO_TEMP | 5832.5
2024 | nonsummer | SENTNL_2_CTG4 | PLANT_MAINTENANCE | 4997.195
2024 | nonsummer | SENTNL_2_CTG4 | PLANT_TROUBLE | 2089.4183
2024 | nonsummer | SENTNL_2_CTG4 | RIMS_OUTAGE | 0
2024 | nonsummer | SENTNL_2_CTG5 | AMBIENT_DUE_TO_TEMP | 6752.77
2024 | nonsummer | SENTNL_2_CTG5 | PLANT_MAINTENANCE | 0
2024 | nonsummer | SENTNL_2_CTG5 | PLANT_TROUBLE | 0
2024 | nonsummer | SENTNL_2_CTG5 | RIMS_OUTAGE | 0
2024 | nonsummer | SENTNL_2_CTG5 | UNIT_TESTING | 0
2024 | nonsummer | SENTNL_2_CTG6 | AMBIENT_DUE_TO_TEMP | 6501.61
2024 | nonsummer | SENTNL_2_CTG6 | PLANT_MAINTENANCE | 0
2024 | nonsummer | SENTNL_2_CTG6 | PLANT_TROUBLE | 11.585
2024 | nonsummer | SENTNL_2_CTG6 | RIMS_OUTAGE | 0
2024 | nonsummer | SENTNL_2_CTG7 | AMBIENT_DUE_TO_TEMP | 6533.95
2024 | nonsummer | SENTNL_2_CTG7 | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | nonsummer | SENTNL_2_CTG7 | PLANT_MAINTENANCE | 0
2024 | nonsummer | SENTNL_2_CTG7 | PLANT_TROUBLE | 0
2024 | nonsummer | SENTNL_2_CTG7 | RIMS_OUTAGE | 0
2024 | nonsummer | SENTNL_2_CTG8 | AMBIENT_DUE_TO_TEMP | 7029.45
2024 | nonsummer | SENTNL_2_CTG8 | PLANT_MAINTENANCE | 0
2024 | nonsummer | SENTNL_2_CTG8 | PLANT_TROUBLE | 0
2024 | nonsummer | SENTNL_2_CTG8 | RIMS_OUTAGE | 0
2024 | nonsummer | SGREGY_6_SANGER | PLANT_MAINTENANCE | 241.5
2024 | nonsummer | SGREGY_6_SANGER | PLANT_TROUBLE | 77.76
2024 | nonsummer | SGREGY_6_SANGER | TRANSMISSION_INDUCED | 0
2024 | nonsummer | SHAFTR_1_HWYSR1 | NEW_GENERATOR_TEST_ENERGY | 326.25
2024 | nonsummer | SHANDN_2_SBBBM1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 549.9
2024 | nonsummer | SHANDN_2_SBBBM1 | PLANT_TROUBLE | 0
2024 | nonsummer | SHELRF_1_UNITS | PLANT_TROUBLE | 0
2024 | nonsummer | SHUTLE_6_CREST | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 60
2024 | nonsummer | SIERRA_1_UNITS | AMBIENT_DUE_TO_TEMP | 1888.6267
2024 | nonsummer | SIERRA_1_UNITS | PLANT_TROUBLE | 12.5
2024 | nonsummer | SIERRA_1_UNITS | UNIT_TESTING | 804.5233
2024 | nonsummer | SIGHEB_6_HE2SCEDYN | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | SIGHEB_6_MIRDYN | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | SIGHEB_6_MIRDYN | PLANT_MAINTENANCE | 740
2024 | nonsummer | SIGHEB_6_MIRDYN | PLANT_TROUBLE | 121
2024 | nonsummer | SISPRG_2_DS3BT1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | SISPRG_2_DS3BT1 | AMBIENT_DUE_TO_TEMP | 130
2024 | nonsummer | SISPRG_2_DS3BT1 | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | nonsummer | SISPRG_2_DS3BT1 | METERING_TELEMETRY | 0
2024 | nonsummer | SISPRG_2_DS3BT1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | SISPRG_2_DS3BT1 | PLANT_TROUBLE | 1219.5407
2024 | nonsummer | SISPRG_2_DS3BT1 | RTU_RIG | 0
2024 | nonsummer | SISPRG_2_DS3BT1 | UNIT_TESTING | 0
2024 | nonsummer | SISPRG_2_DS3BT2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | SISPRG_2_DS3BT2 | METERING_TELEMETRY | 300
2024 | nonsummer | SISPRG_2_DS3BT2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | SISPRG_2_DS3BT2 | PLANT_TROUBLE | 197.485
2024 | nonsummer | SISPRG_2_DS3BT2 | UNIT_TESTING | 0
2024 | nonsummer | SISPRG_2_DS3BT3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 35
2024 | nonsummer | SISPRG_2_DS3BT3 | METERING_TELEMETRY | 0
2024 | nonsummer | SISPRG_2_DS3BT3 | PLANT_MAINTENANCE | 0
2024 | nonsummer | SISPRG_2_DS3BT3 | PLANT_TROUBLE | 67
2024 | nonsummer | SISPRG_2_DS3BT3 | RTU_RIG | 0
2024 | nonsummer | SISPRG_2_DS3BT3 | UNIT_TESTING | 0
2024 | nonsummer | SISPRG_2_DS3BT4 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | SISPRG_2_DS3BT4 | METERING_TELEMETRY | 99
2024 | nonsummer | SISPRG_2_DS3BT4 | PLANT_MAINTENANCE | 0
2024 | nonsummer | SISPRG_2_DS3BT4 | PLANT_TROUBLE | 117.3
2024 | nonsummer | SISPRG_2_DS3BT4 | RTU_RIG | 0
2024 | nonsummer | SISPRG_2_DS3BT4 | UNIT_TESTING | 0
2024 | nonsummer | SISPRG_2_DS3SR1 | AMBIENT_DUE_TO_TEMP | 340
2024 | nonsummer | SISPRG_2_DS3SR1 | METERING_TELEMETRY | 0
2024 | nonsummer | SISPRG_2_DS3SR1 | PLANT_MAINTENANCE | 20
2024 | nonsummer | SISPRG_2_DS3SR1 | PLANT_TROUBLE | 0
2024 | nonsummer | SISPRG_2_DS3SR1 | RTU_RIG | 0
2024 | nonsummer | SISPRG_2_DS3SR1 | UNIT_TESTING | 0
2024 | nonsummer | SISPRG_2_DS3SR2 | METERING_TELEMETRY | 0
2024 | nonsummer | SISPRG_2_DS3SR2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | SISPRG_2_DS3SR2 | PLANT_TROUBLE | 0
2024 | nonsummer | SISPRG_2_DS3SR2 | UNIT_TESTING | 0
2024 | nonsummer | SISPRG_2_DS3SR3 | METERING_TELEMETRY | 0
2024 | nonsummer | SISPRG_2_DS3SR3 | PLANT_MAINTENANCE | 0
2024 | nonsummer | SISPRG_2_DS3SR3 | PLANT_TROUBLE | 0
2024 | nonsummer | SISPRG_2_DS3SR3 | RTU_RIG | 0
2024 | nonsummer | SISPRG_2_DS3SR3 | UNIT_TESTING | 0
2024 | nonsummer | SISPRG_2_DS3SR4 | METERING_TELEMETRY | 0
2024 | nonsummer | SISPRG_2_DS3SR4 | PLANT_TROUBLE | 40
2024 | nonsummer | SISPRG_2_DS3SR4 | RTU_RIG | 0
2024 | nonsummer | SISPRG_2_DS3SR4 | UNIT_TESTING | 1
2024 | nonsummer | SKERN_6_SOLAR1 | METERING_TELEMETRY | 100
2024 | nonsummer | SKERN_6_SOLAR1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | SKERN_6_SOLAR1 | PLANT_TROUBLE | 0
2024 | nonsummer | SKERN_6_SOLAR1 | TRANSMISSION_INDUCED | 5100
2024 | nonsummer | SKERN_6_SOLAR2 | METERING_TELEMETRY | 0
2024 | nonsummer | SKERN_6_SOLAR2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | SKERN_6_SOLAR2 | PLANT_TROUBLE | 200
2024 | nonsummer | SKERN_6_SOLAR2 | TRANSMISSION_INDUCED | 2500
2024 | nonsummer | SLATE_2_SLASR1 | METERING_TELEMETRY | 79.9583
2024 | nonsummer | SLATE_2_SLASR1 | PLANT_MAINTENANCE | 319.8333
2024 | nonsummer | SLATE_2_SLASR1 | PLANT_TROUBLE | 1544.5425
2024 | nonsummer | SLATE_2_SLASR1 | TRANSMISSION_INDUCED | 101
2024 | nonsummer | SLATE_2_SLASR2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 13.09
2024 | nonsummer | SLATE_2_SLASR2 | PLANT_MAINTENANCE | 4623.6
2024 | nonsummer | SLATE_2_SLASR2 | PLANT_TROUBLE | 23361.85
2024 | nonsummer | SLATE_2_SLASR2 | TRANSMISSION_INDUCED | 81.6
2024 | nonsummer | SLATE_2_SLASR2 | UNIT_TESTING | 126.5833
2024 | nonsummer | SLATE_2_SLASR3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 26.125
2024 | nonsummer | SLATE_2_SLASR3 | METERING_TELEMETRY | 0
2024 | nonsummer | SLATE_2_SLASR3 | PLANT_MAINTENANCE | 0
2024 | nonsummer | SLATE_2_SLASR3 | PLANT_TROUBLE | 22565.7
2024 | nonsummer | SLATE_2_SLASR3 | TRANSMISSION_INDUCED | 53.4
2024 | nonsummer | SLATE_2_SLASR3 | UNIT_TESTING | 124.865
2024 | nonsummer | SLATE_2_SLASR4 | METERING_TELEMETRY | 0
2024 | nonsummer | SLATE_2_SLASR4 | PLANT_MAINTENANCE | 0
2024 | nonsummer | SLATE_2_SLASR4 | PLANT_TROUBLE | 1402.6067
2024 | nonsummer | SLATE_2_SLASR4 | TRANSMISSION_INDUCED | 1435.35
2024 | nonsummer | SLATE_2_SLASR4 | UNIT_TESTING | 338.1
2024 | nonsummer | SLATE_2_SLASR5 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 2352.7917
2024 | nonsummer | SLATE_2_SLASR5 | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | SLATE_2_SLASR5 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | SLATE_2_SLASR5 | METERING_TELEMETRY | 37.4
2024 | nonsummer | SLATE_2_SLASR5 | PLANT_MAINTENANCE | 0
2024 | nonsummer | SLATE_2_SLASR5 | PLANT_TROUBLE | 680.4283
2024 | nonsummer | SLATE_2_SLASR5 | TRANSMISSION_INDUCED | 171.1667
2024 | nonsummer | SLATE_2_SLASR5 | UNIT_TESTING | 310.2333
2024 | nonsummer | SLRMS3_2_SRMSR1 | METERING_TELEMETRY | 2500
2024 | nonsummer | SLRMS3_2_SRMSR1 | PLANT_MAINTENANCE | 648
2024 | nonsummer | SLRMS3_2_SRMSR1 | PLANT_TROUBLE | 0
2024 | nonsummer | SLRMS3_2_SRMSR1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | SLST13_2_SOLAR1 | METERING_TELEMETRY | 322.8
2024 | nonsummer | SLST13_2_SOLAR1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | SLST13_2_SOLAR1 | PLANT_TROUBLE | 10473.43
2024 | nonsummer | SLSTR1_2_SOLAR1 | PLANT_MAINTENANCE | 815.5
2024 | nonsummer | SLSTR1_2_SOLAR1 | PLANT_TROUBLE | 4533.3
2024 | nonsummer | SLSTR2_2_SOLAR2 | PLANT_MAINTENANCE | 2350.5
2024 | nonsummer | SLSTR2_2_SOLAR2 | PLANT_TROUBLE | 3818.375
2024 | nonsummer | SLSTR2_2_SOLAR2 | TRANSMISSION_INDUCED | 1650
2024 | nonsummer | SLUISP_2_UNITS | ENVIRONMENTAL_RESTRICTIONS | 35
2024 | nonsummer | SLUISP_2_UNITS | PLANT_MAINTENANCE | 181632.2667
2024 | nonsummer | SLUISP_2_UNITS | PLANT_TROUBLE | 2044.2667
2024 | nonsummer | SLYCRK_1_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | SLYCRK_1_UNIT 1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | SLYCRK_1_UNIT 1 | PLANT_TROUBLE | 24.2667
2024 | nonsummer | SLYCRK_1_UNIT 1 | TRANSMISSION_INDUCED | 8.2333
2024 | nonsummer | SMPRIP_1_SMPSON | PLANT_TROUBLE | 45.1793
2024 | nonsummer | SMPRIP_1_SMPSON | TRANSMISSION_INDUCED | 65.2375
2024 | nonsummer | SMUDGO_7_UNIT 1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 14284
2024 | nonsummer | SMUDGO_7_UNIT 1 | PLANT_TROUBLE | 18.6667
2024 | nonsummer | SMUDGO_7_UNIT 1 | TRANSITIONAL_LIMITATION | 0
2024 | nonsummer | SMUDGO_7_UNIT 1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | SMYRNA_1_DL1SR1 | PLANT_TROUBLE | 165
2024 | nonsummer | SMYRNA_1_DL1SR1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | SNCLRA_2_HOWLNG | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | SNCLRA_2_HOWLNG | METERING_TELEMETRY | 844.92
2024 | nonsummer | SNCLRA_2_HOWLNG | PLANT_MAINTENANCE | 172.85
2024 | nonsummer | SNCLRA_2_HOWLNG | PLANT_TROUBLE | 1517.035
2024 | nonsummer | SNCLRA_2_SILBT1 | METERING_TELEMETRY | 330
2024 | nonsummer | SNCLRA_2_SILBT1 | PLANT_MAINTENANCE | 231
2024 | nonsummer | SNCLRA_2_SILBT1 | PLANT_TROUBLE | 334.9667
2024 | nonsummer | SNCLRA_2_UNIT1 | PLANT_MAINTENANCE | 898.8667
2024 | nonsummer | SNCLRA_2_UNIT1 | PLANT_TROUBLE | 5817.2733
2024 | nonsummer | SNCLRA_2_UNIT1 | TRANSMISSION_INDUCED | 305.8
2024 | nonsummer | SNCLRA_2_VESBT1 | METERING_TELEMETRY | 0
2024 | nonsummer | SNCLRA_2_VESBT1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | SNCLRA_2_VESBT1 | PLANT_TROUBLE | 0
2024 | nonsummer | SNCLRA_2_VESBT1 | UNIT_TESTING | 0
2024 | nonsummer | SNCLRA_6_OXGEN | ENVIRONMENTAL_RESTRICTIONS | 238.5
2024 | nonsummer | SNCLRA_6_OXGEN | PLANT_MAINTENANCE | 0
2024 | nonsummer | SNCLRA_6_OXGEN | PLANT_TROUBLE | 5261.09
2024 | nonsummer | SNCLRA_6_OXGEN | UNIT_TESTING | 0
2024 | nonsummer | SNCLRA_6_PROCGN | PLANT_MAINTENANCE | 97.325
2024 | nonsummer | SNCLRA_6_PROCGN | PLANT_TROUBLE | 1230.0583
2024 | nonsummer | SNDBAR_7_UNIT 1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | SNDBAR_7_UNIT 1 | PLANT_TROUBLE | 32.4
2024 | nonsummer | SNDBAR_7_UNIT 1 | TRANSMISSION_INDUCED | 3.24
2024 | nonsummer | SNMALF_6_UNITS | TRANSMISSION_INDUCED | 97.0833
2024 | nonsummer | SNORA_2_SNRSLR | PLANT_MAINTENANCE | 100
2024 | nonsummer | SNORA_2_SNRSLR | PLANT_TROUBLE | 170
2024 | nonsummer | SNORA_2_SNRSLR | TRANSMISSION_INDUCED | 2325
2024 | nonsummer | SOLBLU_2_WSBBX2 | METERING_TELEMETRY | 0
2024 | nonsummer | SOLBLU_2_WSBBX2 | PLANT_MAINTENANCE | 1071.7633
2024 | nonsummer | SOLBLU_2_WSBBX2 | PLANT_TROUBLE | 1125
2024 | nonsummer | SOLBLU_2_WSBBX2 | UNIT_TESTING | 0
2024 | nonsummer | SOLBLU_2_WSBSX2 | METERING_TELEMETRY | 0
2024 | nonsummer | SOLBLU_2_WSBSX2 | PLANT_MAINTENANCE | 1313.3333
2024 | nonsummer | SOLBLU_2_WSBSX2 | PLANT_TROUBLE | 2283.9667
2024 | nonsummer | SOLBLU_2_WSBSX2 | UNIT_TESTING | 129.1667
2024 | nonsummer | SOUTH_2_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 117.9733
2024 | nonsummer | SOUTH_2_UNIT | PLANT_TROUBLE | 4.1417
2024 | nonsummer | SOUTH_2_UNIT | TRANSMISSION_INDUCED | 0
2024 | nonsummer | SPAULD_6_UNIT 3 | AMBIENT_NOT_DUE_TO_TEMP | 728.7
2024 | nonsummer | SPAULD_6_UNIT 3 | PLANT_MAINTENANCE | 0
2024 | nonsummer | SPAULD_6_UNIT 3 | PLANT_TROUBLE | 1145.1917
2024 | nonsummer | SPAULD_6_UNIT 3 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | SPAULD_6_UNIT12 | AMBIENT_NOT_DUE_TO_TEMP | 1513.5
2024 | nonsummer | SPAULD_6_UNIT12 | PLANT_MAINTENANCE | 0
2024 | nonsummer | SPAULD_6_UNIT12 | PLANT_TROUBLE | 7837.5
2024 | nonsummer | SPAULD_6_UNIT12 | UNIT_TESTING | 0
2024 | nonsummer | SPBURN_2_UNIT 1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 11
2024 | nonsummer | SPBURN_2_UNIT 1 | AMBIENT_DUE_TO_TEMP | 65.75
2024 | nonsummer | SPBURN_2_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 6.25
2024 | nonsummer | SPBURN_2_UNIT 1 | PLANT_MAINTENANCE | 1183.9667
2024 | nonsummer | SPBURN_2_UNIT 1 | PLANT_TROUBLE | 1582.75
2024 | nonsummer | SPBURN_2_UNIT 1 | TRANSMISSION_INDUCED | 74.0667
2024 | nonsummer | SPBURN_7_SNOWMT | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 291.4
2024 | nonsummer | SPBURN_7_SNOWMT | ENVIRONMENTAL_RESTRICTIONS | 270
2024 | nonsummer | SPBURN_7_SNOWMT | PLANT_TROUBLE | 90
2024 | nonsummer | SPBURN_7_SNOWMT | TRANSMISSION_INDUCED | 9.65
2024 | nonsummer | SPI LI_2_UNIT 1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 190.5
2024 | nonsummer | SPI LI_2_UNIT 1 | AMBIENT_DUE_TO_TEMP | 89.7267
2024 | nonsummer | SPI LI_2_UNIT 1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | SPI LI_2_UNIT 1 | PLANT_TROUBLE | 159.96
2024 | nonsummer | SPI LI_2_UNIT 1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | SPIAND_1_ANDSN2 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | SPIAND_1_ANDSN2 | PLANT_MAINTENANCE | 8579.4
2024 | nonsummer | SPIAND_1_ANDSN2 | PLANT_TROUBLE | 333.7157
2024 | nonsummer | SPIAND_1_ANDSN2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | SPICER_1_UNITS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 30
2024 | nonsummer | SPICER_1_UNITS | METERING_TELEMETRY | 0
2024 | nonsummer | SPICER_1_UNITS | PLANT_MAINTENANCE | 0
2024 | nonsummer | SPICER_1_UNITS | PLANT_TROUBLE | 14
2024 | nonsummer | SPICER_1_UNITS | TRANSMISSION_INDUCED | 188
2024 | nonsummer | SPIFBD_1_PL1X2 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | SPIFBD_1_PL1X2 | PLANT_MAINTENANCE | 112.5
2024 | nonsummer | SPIFBD_1_PL1X2 | PLANT_TROUBLE | 337.5
2024 | nonsummer | SPIFBD_1_PL1X2 | TRANSMISSION_INDUCED | 30.5
2024 | nonsummer | SPQUIN_6_SRPCQU | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | SPQUIN_6_SRPCQU | PLANT_MAINTENANCE | 372
2024 | nonsummer | SPQUIN_6_SRPCQU | PLANT_TROUBLE | 372.8
2024 | nonsummer | SPQUIN_6_SRPCQU | TRANSMISSION_INDUCED | 37.6
2024 | nonsummer | SPRGAP_1_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 1784.2
2024 | nonsummer | SPRGAP_1_UNIT 1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | SPRGAP_1_UNIT 1 | PLANT_TROUBLE | 0
2024 | nonsummer | SPRGAP_1_UNIT 1 | TRANSMISSION_INDUCED | 56.7
2024 | nonsummer | SPRGVL_2_SUCCES | METERING_TELEMETRY | 0
2024 | nonsummer | SPRGVL_2_SUCCES | PLANT_MAINTENANCE | 0
2024 | nonsummer | SPRGVL_2_SUCCES | PLANT_TROUBLE | 0
2024 | nonsummer | SPRGVL_2_SUCCES | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 427
2024 | nonsummer | SPRGVL_2_TULESC | ENVIRONMENTAL_RESTRICTIONS | 2650
2024 | nonsummer | SRINTL_6_UNIT | TRANSMISSION_INDUCED | 23.115
2024 | nonsummer | STANIS_7_UNIT 1 | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | STANIS_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 481.204
2024 | nonsummer | STANIS_7_UNIT 1 | PLANT_TROUBLE | 63.6
2024 | nonsummer | STANIS_7_UNIT 1 | TRANSMISSION_INDUCED | 364
2024 | nonsummer | STANTN_2_SBEBX2 | PLANT_MAINTENANCE | 274.0533
2024 | nonsummer | STANTN_2_SBEBX2 | PLANT_TROUBLE | 379.8042
2024 | nonsummer | STANTN_2_SBEBX2 | UNIT_TESTING | 9.7
2024 | nonsummer | STANTN_2_STAGT1 | AMBIENT_DUE_TO_TEMP | 0.01
2024 | nonsummer | STANTN_2_STAGT1 | PLANT_MAINTENANCE | 45.5125
2024 | nonsummer | STANTN_2_STAGT1 | PLANT_TROUBLE | 1752.645
2024 | nonsummer | STANTN_2_STAGT2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | STANTN_2_STAGT2 | AMBIENT_DUE_TO_TEMP | 2.4235
2024 | nonsummer | STANTN_2_STAGT2 | PLANT_MAINTENANCE | 197.7725
2024 | nonsummer | STANTN_2_STAGT2 | PLANT_TROUBLE | 48.8225
2024 | nonsummer | STIGCT_2_LODI | AMBIENT_DUE_TO_TEMP | 2718
2024 | nonsummer | STIGCT_2_LODI | PLANT_TROUBLE | 15219.5
2024 | nonsummer | STIGCT_2_LODI | UNIT_TESTING | 0
2024 | nonsummer | STNRES_1_UNIT | PLANT_MAINTENANCE | 0
2024 | nonsummer | STNRES_1_UNIT | PLANT_TROUBLE | 4149.5
2024 | nonsummer | STNRES_1_UNIT | RTU_RIG | 0
2024 | nonsummer | STNRES_1_UNIT | TRANSMISSION_INDUCED | 0
2024 | nonsummer | STOILS_1_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 93.6
2024 | nonsummer | STOILS_1_UNITS | PLANT_MAINTENANCE | 3653
2024 | nonsummer | STOILS_1_UNITS | PLANT_TROUBLE | 1084.625
2024 | nonsummer | STOREY_2_MDRCH2 | TRANSMISSION_INDUCED | 2.0627
2024 | nonsummer | STRAUS_1_STRWD1 | PLANT_MAINTENANCE | 1178
2024 | nonsummer | STRAUS_1_STRWD1 | PLANT_TROUBLE | 2012.0125
2024 | nonsummer | STRAUS_1_STRWD1 | TRANSMISSION_INDUCED | 63.25
2024 | nonsummer | STROUD_6_SOLAR | METERING_TELEMETRY | 0
2024 | nonsummer | STROUD_6_SOLAR | PLANT_MAINTENANCE | 357.5
2024 | nonsummer | STROUD_6_SOLAR | PLANT_TROUBLE | 4675
2024 | nonsummer | STROUD_6_SOLAR | TRANSMISSION_INDUCED | 6100
2024 | nonsummer | STROUD_6_WWHSR1 | METERING_TELEMETRY | 60
2024 | nonsummer | STROUD_6_WWHSR1 | PLANT_TROUBLE | 307.5
2024 | nonsummer | STROUD_6_WWHSR1 | TRANSMISSION_INDUCED | 157.5
2024 | nonsummer | SUMWHT_6_SWSSR1 | METERING_TELEMETRY | 0
2024 | nonsummer | SUMWHT_6_SWSSR1 | PLANT_TROUBLE | 4567.1833
2024 | nonsummer | SUMWHT_6_SWSSR1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | SUNCAT_2_A1ABT1 | ICCP | 0
2024 | nonsummer | SUNCAT_2_A1ABT1 | PLANT_MAINTENANCE | 235
2024 | nonsummer | SUNCAT_2_A1ABT1 | PLANT_TROUBLE | 1472.0902
2024 | nonsummer | SUNCAT_2_A1ABT1 | RTU_RIG | 0
2024 | nonsummer | SUNCAT_2_A1ABT1 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 232.4
2024 | nonsummer | SUNCAT_2_A1ABT1 | UNIT_TESTING | 94
2024 | nonsummer | SUNCAT_2_A1BBT1 | ICCP | 0
2024 | nonsummer | SUNCAT_2_A1BBT1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | SUNCAT_2_A1BBT1 | PLANT_TROUBLE | 3519.6732
2024 | nonsummer | SUNCAT_2_A1BBT1 | RTU_RIG | 0
2024 | nonsummer | SUNCAT_2_A1BBT1 | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 484.0167
2024 | nonsummer | SUNCAT_2_A1BBT1 | UNIT_TESTING | 0
2024 | nonsummer | SUNCAT_2_A2ABT2 | METERING_TELEMETRY | 462
2024 | nonsummer | SUNCAT_2_A2ABT2 | PLANT_MAINTENANCE | 247.4875
2024 | nonsummer | SUNCAT_2_A2ABT2 | PLANT_TROUBLE | 4906.8558
2024 | nonsummer | SUNCAT_2_A2ABT2 | RTU_RIG | 0
2024 | nonsummer | SUNCAT_2_A2BSR2 | PLANT_TROUBLE | 307.88
2024 | nonsummer | SUNCAT_2_A2BSR2 | UNIT_TESTING | 0
2024 | nonsummer | SUNRIS_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 23163.73
2024 | nonsummer | SUNRIS_2_PL1X3 | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | nonsummer | SUNRIS_2_PL1X3 | METERING_TELEMETRY | 0
2024 | nonsummer | SUNRIS_2_PL1X3 | PLANT_MAINTENANCE | 56812.8667
2024 | nonsummer | SUNRIS_2_PL1X3 | PLANT_TROUBLE | 5159.2815
2024 | nonsummer | SUNRIS_2_PL1X3 | TRANSMISSION_INDUCED | 11
2024 | nonsummer | SUNRIS_2_PL1X3 | UNIT_TESTING | 1272.37
2024 | nonsummer | SUNSET_2_UNITS | AMBIENT_DUE_TO_TEMP | 5741.5
2024 | nonsummer | SUNSET_2_UNITS | PLANT_MAINTENANCE | 1557.75
2024 | nonsummer | SUNSET_2_UNITS | PLANT_TROUBLE | 2286.15
2024 | nonsummer | SUNSHN_2_LNDFL | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | SUNSHN_2_LNDFL | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | SUNSHN_2_LNDFL | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | SUNSHN_2_LNDFL | METERING_TELEMETRY | 0
2024 | nonsummer | SUNSHN_2_LNDFL | PLANT_MAINTENANCE | 2680.3667
2024 | nonsummer | SUNSHN_2_LNDFL | PLANT_TROUBLE | 904.6817
2024 | nonsummer | SUNSHN_2_LNDFL | TRANSMISSION_INDUCED | 46.3833
2024 | nonsummer | SUNSLR_1_SSVSR1 | METERING_TELEMETRY | 75
2024 | nonsummer | SUNSLR_1_SSVSR1 | PLANT_MAINTENANCE | 55.025
2024 | nonsummer | SUNSLR_1_SSVSR1 | PLANT_TROUBLE | 0
2024 | nonsummer | SUNSLR_1_SSVSR1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | SUNSPT_2_WNASR1 | METERING_TELEMETRY | 0
2024 | nonsummer | SUNSPT_2_WNASR1 | PLANT_MAINTENANCE | 93.6667
2024 | nonsummer | SUNSPT_2_WNASR1 | PLANT_TROUBLE | 551.9333
2024 | nonsummer | SUNSPT_2_WNASR1 | TRANSMISSION_INDUCED | 54
2024 | nonsummer | SUNST2_5_SS2SR1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | SUNST2_5_SS2SR1 | PLANT_TROUBLE | 2452.5
2024 | nonsummer | SUNSTR_5_SS1SCEDYN | METERING_TELEMETRY | 375
2024 | nonsummer | SUNSTR_5_SS1SCEDYN | PLANT_MAINTENANCE | 1590.95
2024 | nonsummer | SUNSTR_5_SS1SCEDYN | PLANT_TROUBLE | 783.2667
2024 | nonsummer | SUTTER_2_CISO | AMBIENT_DUE_TO_TEMP | 1810.3717
2024 | nonsummer | SUTTER_2_CISO | PLANT_MAINTENANCE | 1135.3333
2024 | nonsummer | SUTTER_2_CISO | PLANT_TROUBLE | 15019.1
2024 | nonsummer | SUTTER_2_CISO | TRANSITIONAL_LIMITATION | 0
2024 | nonsummer | SUTTER_2_CISO | TRANSMISSION_INDUCED | 292.5
2024 | nonsummer | SUTTER_2_CISO | UNIT_TESTING | 157.8283
2024 | nonsummer | SYCAMR_2_UNIT 1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 90.0333
2024 | nonsummer | SYCAMR_2_UNIT 1 | PLANT_MAINTENANCE | 17361.6333
2024 | nonsummer | SYCAMR_2_UNIT 1 | PLANT_TROUBLE | 3718.5
2024 | nonsummer | SYCAMR_2_UNIT 2 | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | nonsummer | SYCAMR_2_UNIT 2 | PLANT_MAINTENANCE | 23180
2024 | nonsummer | SYCAMR_2_UNIT 2 | PLANT_TROUBLE | 0
2024 | nonsummer | SYCAMR_2_UNIT 2 | UNIT_SUPPORTING_STARTUP | 0
2024 | nonsummer | SYCAMR_2_UNIT 2 | UNIT_TESTING | 0
2024 | nonsummer | SYCAMR_2_UNIT 3 | PLANT_MAINTENANCE | 10754.6667
2024 | nonsummer | SYCAMR_2_UNIT 3 | PLANT_TROUBLE | 518
2024 | nonsummer | SYCAMR_2_UNIT 3 | UNIT_TESTING | 0
2024 | nonsummer | SYCAMR_2_UNIT 4 | PLANT_MAINTENANCE | 8740
2024 | nonsummer | SYCAMR_2_UNIT 4 | PLANT_TROUBLE | 1715.0667
2024 | nonsummer | TAHOE_2_THOBT1 | NEW_GENERATOR_TEST_ENERGY | 6360
2024 | nonsummer | TAHOE_2_THOBT2 | NEW_GENERATOR_TEST_ENERGY | 11316
2024 | nonsummer | TAHOE_2_THOBT3 | NEW_GENERATOR_TEST_ENERGY | 14060
2024 | nonsummer | TAHOE_2_THOBT3 | PLANT_MAINTENANCE | 0
2024 | nonsummer | TANHIL_6_SOLART | PLANT_MAINTENANCE | 0
2024 | nonsummer | TANHIL_6_SOLART | PLANT_TROUBLE | 428.9333
2024 | nonsummer | TANHIL_6_SOLART | TRANSMISSION_INDUCED | 0
2024 | nonsummer | TBLMTN_6_QF | AMBIENT_NOT_DUE_TO_TEMP | 170
2024 | nonsummer | TBLMTN_6_QF | PLANT_MAINTENANCE | 85
2024 | nonsummer | TBLMTN_6_QF | PLANT_TROUBLE | 297.5
2024 | nonsummer | TBLMTN_6_QF | TRANSMISSION_INDUCED | 8.5
2024 | nonsummer | TECOLOTE_3_WBDYN | AMBIENT_DUE_TO_TEMP | 2166.8
2024 | nonsummer | TECOLOTE_3_WBDYN | METERING_TELEMETRY | 0
2024 | nonsummer | TECOLOTE_3_WBDYN | PLANT_TROUBLE | 692.784
2024 | nonsummer | TECOLOTE_3_WBDYN | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 6795.8267
2024 | nonsummer | TECOLOTE_3_WBDYN | TRANSITIONAL_LIMITATION | 310
2024 | nonsummer | TECOLOTE_3_WBDYN | TRANSMISSION_INDUCED | 12291.4913
2024 | nonsummer | TEHAPI_2_PW1WD1 | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | nonsummer | TEHAPI_2_PW1WD1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | TEHAPI_2_PW1WD1 | PLANT_TROUBLE | 1684.196
2024 | nonsummer | TEHAPI_2_PW1WD1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | TEHAPI_2_PW2WD2 | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | nonsummer | TEHAPI_2_PW2WD2 | PLANT_MAINTENANCE | 54
2024 | nonsummer | TEHAPI_2_PW2WD2 | PLANT_TROUBLE | 3206.64
2024 | nonsummer | TEHAPI_2_PW2WD2 | TRANSMISSION_INDUCED | 1028.7
2024 | nonsummer | TEHAPI_2_WIND1 | METERING_TELEMETRY | 0
2024 | nonsummer | TEHAPI_2_WIND1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | TEHAPI_2_WIND1 | PLANT_TROUBLE | 209.0867
2024 | nonsummer | TEHAPI_2_WIND1 | TRANSMISSION_INDUCED | 664.975
2024 | nonsummer | TEHAPI_2_WIND2 | METERING_TELEMETRY | 0
2024 | nonsummer | TEHAPI_2_WIND2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | TEHAPI_2_WIND2 | PLANT_TROUBLE | 270.907
2024 | nonsummer | TEHAPI_2_WIND2 | TRANSMISSION_INDUCED | 792.61
2024 | nonsummer | TENGEN_2_PL1X2 | ENVIRONMENTAL_RESTRICTIONS | 2402
2024 | nonsummer | TENGEN_2_PL1X2 | METERING_TELEMETRY | 0
2024 | nonsummer | TENGEN_2_PL1X2 | PLANT_MAINTENANCE | 15794.5
2024 | nonsummer | TENGEN_2_PL1X2 | PLANT_TROUBLE | 63.315
2024 | nonsummer | TENGEN_2_PL1X2 | UNIT_TESTING | 921.5
2024 | nonsummer | TERMEX_2_PL1X3 | AMBIENT_DUE_TO_TEMP | 2184
2024 | nonsummer | TERMEX_2_PL1X3 | PLANT_MAINTENANCE | 13125
2024 | nonsummer | TERMEX_2_PL1X3 | PLANT_TROUBLE | 2648.9833
2024 | nonsummer | TERMEX_2_PL1X3 | TRANSITIONAL_LIMITATION | 1573
2024 | nonsummer | TIDWTR_2_UNITS | METERING_TELEMETRY | 0
2024 | nonsummer | TIDWTR_2_UNITS | PLANT_MAINTENANCE | 3843
2024 | nonsummer | TIDWTR_2_UNITS | PLANT_TROUBLE | 5380.2
2024 | nonsummer | TIFFNY_1_DILLON | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | TIFFNY_1_DILLON | METERING_TELEMETRY | 0
2024 | nonsummer | TIFFNY_1_DILLON | PLANT_TROUBLE | 435
2024 | nonsummer | TIFFNY_1_DILLON | TRANSITIONAL_LIMITATION | 90
2024 | nonsummer | TIFFNY_1_DILLON | TRANSMISSION_INDUCED | 66.9133
2024 | nonsummer | TIGRCK_7_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 551.0833
2024 | nonsummer | TIGRCK_7_UNITS | PLANT_TROUBLE | 503.15
2024 | nonsummer | TIGRCK_7_UNITS | TRANSMISSION_INDUCED | 620
2024 | nonsummer | TITANS_2_TTSSR1 | METERING_TELEMETRY | 0
2024 | nonsummer | TITANS_2_TTSSR1 | PLANT_MAINTENANCE | 70
2024 | nonsummer | TITANS_2_TTSSR1 | PLANT_TROUBLE | 45
2024 | nonsummer | TITANS_2_TTSSR1 | TRANSMISSION_INDUCED | 3990
2024 | nonsummer | TKOPWR_6_HYDRO | TRANSMISSION_INDUCED | 0
2024 | nonsummer | TOADTW_6_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 251.37
2024 | nonsummer | TOADTW_6_UNIT | PLANT_MAINTENANCE | 90
2024 | nonsummer | TOADTW_6_UNIT | PLANT_TROUBLE | 120
2024 | nonsummer | TOADTW_6_UNIT | TRANSMISSION_INDUCED | 0.55
2024 | nonsummer | TOPAZ_2_SOLAR | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | TOPAZ_2_SOLAR | METERING_TELEMETRY | 0
2024 | nonsummer | TOPAZ_2_SOLAR | PLANT_MAINTENANCE | 2508.0167
2024 | nonsummer | TOPAZ_2_SOLAR | PLANT_TROUBLE | 22558.9167
2024 | nonsummer | TOPAZ_2_SOLAR | TRANSMISSION_INDUCED | 0
2024 | nonsummer | TOPAZ_2_SOLAR | UNIT_TESTING | 0
2024 | nonsummer | TORTLA_1_SOLAR | METERING_TELEMETRY | 0
2024 | nonsummer | TORTLA_1_SOLAR | PLANT_TROUBLE | 73
2024 | nonsummer | TORTLA_1_SOLAR | TRANSMISSION_INDUCED | 107.6667
2024 | nonsummer | TOWNSITE_2_MEADDYN | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | TOWNSITE_2_MEADDYN | METERING_TELEMETRY | 270
2024 | nonsummer | TOWNSITE_2_MEADDYN | PLANT_MAINTENANCE | 508.5
2024 | nonsummer | TOWNSITE_2_MEADDYN | PLANT_TROUBLE | 0
2024 | nonsummer | TOWNSITE_2_MEADDYN | UNIT_TESTING | 996
2024 | nonsummer | TRNQL8_2_AMASR1 | ENVIRONMENTAL_RESTRICTIONS | 60
2024 | nonsummer | TRNQL8_2_AMASR1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | TRNQL8_2_AMASR1 | PLANT_TROUBLE | 0
2024 | nonsummer | TRNQL8_2_AMASR1 | TRANSMISSION_INDUCED | 60
2024 | nonsummer | TRNQL8_2_AMASR1 | UNIT_TESTING | 60
2024 | nonsummer | TRNQL8_2_AZUSR1 | PLANT_MAINTENANCE | 100
2024 | nonsummer | TRNQL8_2_AZUSR1 | PLANT_TROUBLE | 0
2024 | nonsummer | TRNQL8_2_ROJSR1 | PLANT_MAINTENANCE | 285
2024 | nonsummer | TRNQL8_2_ROJSR1 | PLANT_TROUBLE | 519.1667
2024 | nonsummer | TRNQL8_2_ROJSR1 | UNIT_TESTING | 900
2024 | nonsummer | TRNQL8_2_VERSR1 | PLANT_TROUBLE | 88
2024 | nonsummer | TRNQL8_2_VERSR1 | UNIT_TESTING | 540
2024 | nonsummer | TRNQLT_2_RETBT1 | METERING_TELEMETRY | 66.8
2024 | nonsummer | TRNQLT_2_RETBT1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | TRNQLT_2_RETBT1 | PLANT_TROUBLE | 4787.0333
2024 | nonsummer | TRNQLT_2_RETBT1 | UNIT_TESTING | 720
2024 | nonsummer | TRNQLT_2_SOLAR | PLANT_MAINTENANCE | 0
2024 | nonsummer | TRNQLT_2_SOLAR | PLANT_TROUBLE | 4466.3938
2024 | nonsummer | TRNSWD_1_QF | PLANT_MAINTENANCE | 0
2024 | nonsummer | TRNSWD_1_QF | PLANT_TROUBLE | 32491.455
2024 | nonsummer | TRNSWD_1_QF | TRANSMISSION_INDUCED | 5
2024 | nonsummer | TULARE_2_TFCBM1 | PLANT_MAINTENANCE | 14
2024 | nonsummer | TULARE_2_TFCBM1 | PLANT_TROUBLE | 429.7067
2024 | nonsummer | TULARE_2_TFCBM1 | UNIT_TESTING | 14
2024 | nonsummer | TULEWD_1_TULWD1 | ENVIRONMENTAL_RESTRICTIONS | 115.5
2024 | nonsummer | TULEWD_1_TULWD1 | PLANT_TROUBLE | 881.125
2024 | nonsummer | TULEWD_1_TULWD1 | RTU_RIG | 652.5
2024 | nonsummer | TULLCK_7_UNITS | PLANT_TROUBLE | 0
2024 | nonsummer | TULLCK_7_UNITS | TRANSMISSION_INDUCED | 230.7067
2024 | nonsummer | TUMBWD_2_WISBT3 | METERING_TELEMETRY | 0
2024 | nonsummer | TUMBWD_2_WISBT3 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | nonsummer | TUMBWD_2_WISBT3 | PLANT_MAINTENANCE | 0
2024 | nonsummer | TUMBWD_2_WISBT3 | PLANT_TROUBLE | 0
2024 | nonsummer | TUMBWD_2_WISBT3 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | TUMBWD_2_WISBT3 | UNIT_TESTING | 0
2024 | nonsummer | TUMBWD_2_WISBT4 | METERING_TELEMETRY | 0
2024 | nonsummer | TUMBWD_2_WISBT4 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | nonsummer | TUMBWD_2_WISBT4 | PLANT_TROUBLE | 0
2024 | nonsummer | TUMBWD_2_WISBT4 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | TUPMAN_1_BIOGAS | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 2.29
2024 | nonsummer | TUPMAN_1_BIOGAS | PLANT_TROUBLE | 22.18
2024 | nonsummer | TVYVLY_6_KRSHY1 | AMBIENT_NOT_DUE_TO_TEMP | 708.825
2024 | nonsummer | TWISSL_6_SOLAR | PLANT_TROUBLE | 7.5
2024 | nonsummer | TWISSL_6_SOLAR | TRANSMISSION_INDUCED | 0
2024 | nonsummer | TWISSL_6_SOLAR1 | TRANSMISSION_INDUCED | 20
2024 | nonsummer | TX-ELK_6_ECKSR2 | PLANT_TROUBLE | 135
2024 | nonsummer | TX-ELK_6_SOLAR1 | METERING_TELEMETRY | 45
2024 | nonsummer | TX-ELK_6_SOLAR1 | PLANT_TROUBLE | 1207.5
2024 | nonsummer | TXMCKT_6_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | TXMCKT_6_UNIT | METERING_TELEMETRY | 0
2024 | nonsummer | TXMCKT_6_UNIT | PLANT_MAINTENANCE | 1387.72
2024 | nonsummer | TXMCKT_6_UNIT | PLANT_TROUBLE | 476.2167
2024 | nonsummer | TXMCKT_6_UNIT | TRANSMISSION_INDUCED | 497.0933
2024 | nonsummer | UKIAH_7_LAKEMN | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 140
2024 | nonsummer | UKIAH_7_LAKEMN | PLANT_MAINTENANCE | 0
2024 | nonsummer | UKIAH_7_LAKEMN | PLANT_TROUBLE | 19.7667
2024 | nonsummer | UKIAH_7_LAKEMN | TRANSMISSION_INDUCED | 0
2024 | nonsummer | ULTPCH_1_UCSBT1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | ULTPCH_1_UNIT 1 | PLANT_MAINTENANCE | 270
2024 | nonsummer | ULTPCH_1_UNIT 1 | PLANT_TROUBLE | 1353
2024 | nonsummer | ULTPCH_1_UNIT 1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | ULTPFR_1_UNIT 1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | ULTPFR_1_UNIT 1 | PLANT_TROUBLE | 11109.3
2024 | nonsummer | ULTRCK_2_UNIT | METERING_TELEMETRY | 9.5
2024 | nonsummer | ULTRCK_2_UNIT | PLANT_MAINTENANCE | 367.22
2024 | nonsummer | ULTRCK_2_UNIT | PLANT_TROUBLE | 2901.0133
2024 | nonsummer | UNVRSY_1_UNIT 1 | METERING_TELEMETRY | 380
2024 | nonsummer | UNVRSY_1_UNIT 1 | PLANT_MAINTENANCE | 190
2024 | nonsummer | UNVRSY_1_UNIT 1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | USWND2_1_WIND1 | PLANT_TROUBLE | 3853.8212
2024 | nonsummer | USWND2_1_WIND1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | USWND2_1_WIND2 | PLANT_MAINTENANCE | 4568.7363
2024 | nonsummer | USWND2_1_WIND2 | PLANT_TROUBLE | 0
2024 | nonsummer | USWND2_1_WIND2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | USWND2_1_WIND3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 20.445
2024 | nonsummer | USWND2_1_WIND3 | PLANT_MAINTENANCE | 0
2024 | nonsummer | USWND2_1_WIND3 | PLANT_TROUBLE | 4305.1517
2024 | nonsummer | USWND2_1_WIND3 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | USWND4_2_UNIT2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | USWNDR_2_LABWD1 | PLANT_MAINTENANCE | 104.825
2024 | nonsummer | USWNDR_2_LABWD1 | PLANT_TROUBLE | 903.95
2024 | nonsummer | USWNDR_2_LABWD1 | TRANSMISSION_INDUCED | 40.5
2024 | nonsummer | USWNDR_2_SMUD | PLANT_TROUBLE | 2530.08
2024 | nonsummer | USWNDR_2_SMUD2 | PLANT_MAINTENANCE | 278.8
2024 | nonsummer | USWPFK_6_FRICK | METERING_TELEMETRY | 0
2024 | nonsummer | USWPFK_6_FRICK | PLANT_TROUBLE | 2044.75
2024 | nonsummer | USWPFK_6_FRICK | TRANSMISSION_INDUCED | 131.125
2024 | nonsummer | USWPJR_2_UNITS | METERING_TELEMETRY | 49.5267
2024 | nonsummer | USWPJR_2_UNITS | PLANT_MAINTENANCE | 3924.7533
2024 | nonsummer | USWPJR_2_UNITS | PLANT_TROUBLE | 0
2024 | nonsummer | USWPJR_2_UNITS | TRANSMISSION_INDUCED | 356.5
2024 | nonsummer | VACADX_1_SOLAR | METERING_TELEMETRY | 12.5
2024 | nonsummer | VACADX_1_SOLAR | PLANT_MAINTENANCE | 0
2024 | nonsummer | VACADX_1_SOLAR | PLANT_TROUBLE | 350.5
2024 | nonsummer | VACADX_1_UNITA1 | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | VACADX_1_UNITA1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | VACADX_1_UNITA1 | PLANT_TROUBLE | 0
2024 | nonsummer | VACADX_1_UNITA1 | UNIT_TESTING | 0
2024 | nonsummer | VALLEY_5_REDMTN | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 147.5
2024 | nonsummer | VALLEY_5_REDMTN | PLANT_TROUBLE | 0
2024 | nonsummer | VALLEY_5_SOLAR2 | PLANT_TROUBLE | 0
2024 | nonsummer | VALTNE_2_AVASR1 | PLANT_TROUBLE | 0
2024 | nonsummer | VALTNE_2_AVASR1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | VALTNE_2_TBBBT1 | METERING_TELEMETRY | 0
2024 | nonsummer | VALTNE_2_TBBBT1 | PLANT_MAINTENANCE | 116.1333
2024 | nonsummer | VALTNE_2_TBBBT1 | PLANT_TROUBLE | 0
2024 | nonsummer | VALTNE_2_TBBBT1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | VALTNE_2_TBBBT1 | UNIT_TESTING | 0
2024 | nonsummer | VALTNE_2_TRSBT1 | METERING_TELEMETRY | 0
2024 | nonsummer | VALTNE_2_TRSBT1 | PLANT_MAINTENANCE | 103.3333
2024 | nonsummer | VALTNE_2_TRSBT1 | PLANT_TROUBLE | 0
2024 | nonsummer | VALTNE_2_TRSBT1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | VALTNE_2_TRSBT1 | UNIT_TESTING | 0
2024 | nonsummer | VALTNE_2_TSASR1 | NEW_GENERATOR_TEST_ENERGY | 11600
2024 | nonsummer | VALTNE_2_TSASR2 | NEW_GENERATOR_TEST_ENERGY | 14000
2024 | nonsummer | VALTNE_2_TSBBT1 | NEW_GENERATOR_TEST_ENERGY | 3600
2024 | nonsummer | VALTNE_2_TSBBT2 | NEW_GENERATOR_TEST_ENERGY | 4400
2024 | nonsummer | VEDDER_1_SEKERN | PLANT_TROUBLE | 13218.2
2024 | nonsummer | VEGA_6_SOLAR1 | PLANT_MAINTENANCE | 43.3333
2024 | nonsummer | VEGA_6_SOLAR1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | VENWD_1_WIND3 | METERING_TELEMETRY | 0
2024 | nonsummer | VENWD_1_WIND3 | PLANT_MAINTENANCE | 12.13
2024 | nonsummer | VERNON_6_GONZL1 | ANNUAL_USE_LIMIT_REACHED | 0
2024 | nonsummer | VERNON_6_GONZL1 | PLANT_MAINTENANCE | 11.5
2024 | nonsummer | VERNON_6_GONZL1 | PLANT_TROUBLE | 0
2024 | nonsummer | VERNON_6_GONZL1 | SHORT_TERM_USE_LIMIT_REACHED | 28.75
2024 | nonsummer | VERNON_6_GONZL1 | UNIT_TESTING | 0
2024 | nonsummer | VERNON_6_GONZL2 | PLANT_MAINTENANCE | 11.5
2024 | nonsummer | VERNON_6_GONZL2 | PLANT_TROUBLE | 747.4042
2024 | nonsummer | VERNON_6_GONZL2 | UNIT_TESTING | 0
2024 | nonsummer | VERNON_6_MALBRG | PLANT_TROUBLE | 6676.7833
2024 | nonsummer | VERNON_6_MALBRG | UNIT_SUPPORTING_STARTUP | 113.85
2024 | nonsummer | VESTAL_2_BTNBT1 | METERING_TELEMETRY | 13.6
2024 | nonsummer | VESTAL_2_BTNBT1 | PLANT_MAINTENANCE | 4637.8333
2024 | nonsummer | VESTAL_2_BTNBT1 | UNIT_TESTING | 394
2024 | nonsummer | VESTAL_2_KERN | AMBIENT_NOT_DUE_TO_TEMP | 16225.7
2024 | nonsummer | VESTAL_2_KERN | PLANT_TROUBLE | 70.15
2024 | nonsummer | VESTAL_2_KERN | TRANSMISSION_INDUCED | 13.5417
2024 | nonsummer | VESTAL_2_SOLAR1 | PLANT_TROUBLE | 130
2024 | nonsummer | VESTAL_2_SOLAR2 | PLANT_TROUBLE | 610.4
2024 | nonsummer | VESTAL_2_TS5SR1 | METERING_TELEMETRY | 0
2024 | nonsummer | VESTAL_2_TS5SR1 | PLANT_MAINTENANCE | 167.49
2024 | nonsummer | VESTAL_2_TS5SR1 | PLANT_TROUBLE | 4567.336
2024 | nonsummer | VESTAL_2_TS5SR1 | TRANSMISSION_INDUCED | 121.8955
2024 | nonsummer | VESTAL_2_WELLHD | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | VESTAL_2_WELLHD | AMBIENT_DUE_TO_TEMP | 204.6933
2024 | nonsummer | VESTAL_2_WELLHD | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | VESTAL_2_WELLHD | METERING_TELEMETRY | 0
2024 | nonsummer | VESTAL_2_WELLHD | PLANT_MAINTENANCE | 735
2024 | nonsummer | VESTAL_2_WELLHD | PLANT_TROUBLE | 273.3167
2024 | nonsummer | VESTAL_6_QF | AMBIENT_NOT_DUE_TO_TEMP | 9722.9142
2024 | nonsummer | VESTAL_6_QF | PLANT_TROUBLE | 75.3517
2024 | nonsummer | VESTAL_6_QF | TRANSMISSION_INDUCED | 0
2024 | nonsummer | VICPAS_2_SLOBT1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | VICPAS_2_SLOBT1 | METERING_TELEMETRY | 47.5
2024 | nonsummer | VICPAS_2_SLOBT1 | NEW_GENERATOR_TEST_ENERGY | 375
2024 | nonsummer | VICPAS_2_SLOBT1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | VICPAS_2_SLOBT1 | PLANT_TROUBLE | 84.75
2024 | nonsummer | VICPAS_2_SLOBT1 | RTU_RIG | 0
2024 | nonsummer | VICPAS_2_SLOBT1 | TRANSMISSION_INDUCED | 52.5
2024 | nonsummer | VICPAS_2_SLOBT1 | UNIT_TESTING | 0
2024 | nonsummer | VICPAS_2_SLOSR1 | METERING_TELEMETRY | 0
2024 | nonsummer | VICPAS_2_SLOSR1 | NEW_GENERATOR_TEST_ENERGY | 148.5
2024 | nonsummer | VICPAS_2_SLOSR1 | PLANT_TROUBLE | 203.775
2024 | nonsummer | VICPAS_2_SLOSR1 | RTU_RIG | 0
2024 | nonsummer | VICPAS_2_SLOSR1 | TRANSMISSION_INDUCED | 173.25
2024 | nonsummer | VICPAS_2_SLOSR1 | UNIT_TESTING | 605.45
2024 | nonsummer | VICPAS_2_SOCBT1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | VICPAS_2_SOCBT1 | METERING_TELEMETRY | 215.5
2024 | nonsummer | VICPAS_2_SOCBT1 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | nonsummer | VICPAS_2_SOCBT1 | PLANT_MAINTENANCE | 500
2024 | nonsummer | VICPAS_2_SOCBT1 | PLANT_TROUBLE | 418.7167
2024 | nonsummer | VICPAS_2_SOCBT1 | RTU_RIG | 0
2024 | nonsummer | VICPAS_2_SOCBT1 | TRANSMISSION_INDUCED | 175
2024 | nonsummer | VICPAS_2_SOCBT1 | UNIT_TESTING | 0
2024 | nonsummer | VICPAS_2_SOCBT2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 14.2
2024 | nonsummer | VICPAS_2_SOCBT2 | METERING_TELEMETRY | 0
2024 | nonsummer | VICPAS_2_SOCBT2 | NEW_GENERATOR_TEST_ENERGY | 2414
2024 | nonsummer | VICPAS_2_SOCBT2 | PLANT_MAINTENANCE | 994
2024 | nonsummer | VICPAS_2_SOCBT2 | PLANT_TROUBLE | 692.1667
2024 | nonsummer | VICPAS_2_SOCBT2 | RTU_RIG | 229.5667
2024 | nonsummer | VICPAS_2_SOCBT2 | TRANSITIONAL_LIMITATION | 0
2024 | nonsummer | VICPAS_2_SOCBT2 | TRANSMISSION_INDUCED | 248.5
2024 | nonsummer | VICPAS_2_SOCBT2 | UNIT_TESTING | 0
2024 | nonsummer | VICPAS_2_SOCSR1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 50
2024 | nonsummer | VICPAS_2_SOCSR1 | METERING_TELEMETRY | 0
2024 | nonsummer | VICPAS_2_SOCSR1 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | nonsummer | VICPAS_2_SOCSR1 | PLANT_MAINTENANCE | 1000
2024 | nonsummer | VICPAS_2_SOCSR1 | PLANT_TROUBLE | 100
2024 | nonsummer | VICPAS_2_SOCSR1 | RTU_RIG | 0
2024 | nonsummer | VICPAS_2_SOCSR1 | TRANSMISSION_INDUCED | 350
2024 | nonsummer | VICPAS_2_SOCSR1 | UNIT_TESTING | 90
2024 | nonsummer | VICPAS_2_SOCSR2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | VICPAS_2_SOCSR2 | METERING_TELEMETRY | 0
2024 | nonsummer | VICPAS_2_SOCSR2 | NEW_GENERATOR_TEST_ENERGY | 240.84
2024 | nonsummer | VICPAS_2_SOCSR2 | PLANT_MAINTENANCE | 1028.5
2024 | nonsummer | VICPAS_2_SOCSR2 | PLANT_TROUBLE | 3151.37
2024 | nonsummer | VICPAS_2_SOCSR2 | RTU_RIG | 0
2024 | nonsummer | VICPAS_2_SOCSR2 | UNIT_TESTING | 84.15
2024 | nonsummer | VICPAS_2_SOCSR3 | METERING_TELEMETRY | 0
2024 | nonsummer | VICPAS_2_SOCSR3 | NEW_GENERATOR_TEST_ENERGY | 60
2024 | nonsummer | VICPAS_2_SOCSR3 | PLANT_TROUBLE | 62.3333
2024 | nonsummer | VICPAS_2_SOCSR3 | RTU_RIG | 0
2024 | nonsummer | VICPAS_2_SOCSR3 | TRANSMISSION_INDUCED | 70
2024 | nonsummer | VICPAS_2_SOCSR3 | UNIT_TESTING | 190
2024 | nonsummer | VICPAS_2_VPSBT1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 100
2024 | nonsummer | VICPAS_2_VPSBT1 | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | VICPAS_2_VPSBT1 | METERING_TELEMETRY | 0
2024 | nonsummer | VICPAS_2_VPSBT1 | PLANT_MAINTENANCE | 150
2024 | nonsummer | VICPAS_2_VPSBT1 | PLANT_TROUBLE | 806.2833
2024 | nonsummer | VICPAS_2_VPSBT1 | RTU_RIG | 0
2024 | nonsummer | VICPAS_2_VPSBT1 | TRANSMISSION_INDUCED | 25
2024 | nonsummer | VICPAS_2_VPSBT1 | UNIT_TESTING | 0
2024 | nonsummer | VICPAS_2_VPSSR1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | VICPAS_2_VPSSR1 | METERING_TELEMETRY | 0
2024 | nonsummer | VICPAS_2_VPSSR1 | PLANT_MAINTENANCE | 600
2024 | nonsummer | VICPAS_2_VPSSR1 | PLANT_TROUBLE | 0
2024 | nonsummer | VICPAS_2_VPSSR1 | TRANSMISSION_INDUCED | 100
2024 | nonsummer | VICPAS_2_VPSSR1 | UNIT_TESTING | 200
2024 | nonsummer | VICTOR_1_CREST | PLANT_MAINTENANCE | 1170.15
2024 | nonsummer | VICTOR_1_CREST | PLANT_TROUBLE | 2058.025
2024 | nonsummer | VICTOR_1_CREST | TRANSMISSION_INDUCED | 25
2024 | nonsummer | VICTOR_1_EXSLRA | PLANT_TROUBLE | 57.1
2024 | nonsummer | VICTOR_1_EXSLRA | TRANSMISSION_INDUCED | 0
2024 | nonsummer | VICTOR_1_EXSLRB | PLANT_MAINTENANCE | 6.9333
2024 | nonsummer | VICTOR_1_EXSLRB | PLANT_TROUBLE | 21.6333
2024 | nonsummer | VICTOR_1_EXSLRB | TRANSMISSION_INDUCED | 0
2024 | nonsummer | VICTOR_1_LVSLR1 | METERING_TELEMETRY | 8
2024 | nonsummer | VICTOR_1_LVSLR1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | VICTOR_1_LVSLR1 | TRANSMISSION_INDUCED | 50
2024 | nonsummer | VICTOR_1_LVSLR2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | VICTOR_1_LVSLR2 | PLANT_TROUBLE | 70
2024 | nonsummer | VICTOR_1_LVSLR2 | TRANSMISSION_INDUCED | 100
2024 | nonsummer | VICTOR_1_SOLAR1 | METERING_TELEMETRY | 1592.5
2024 | nonsummer | VICTOR_1_SOLAR1 | PLANT_MAINTENANCE | 70
2024 | nonsummer | VICTOR_1_SOLAR1 | PLANT_TROUBLE | 175
2024 | nonsummer | VICTOR_1_SOLAR1 | TRANSMISSION_INDUCED | 271.5417
2024 | nonsummer | VICTOR_1_SOLAR2 | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | VICTOR_1_SOLAR2 | METERING_TELEMETRY | 40
2024 | nonsummer | VICTOR_1_SOLAR2 | PLANT_MAINTENANCE | 80
2024 | nonsummer | VICTOR_1_SOLAR2 | PLANT_TROUBLE | 0
2024 | nonsummer | VICTOR_1_SOLAR3 | METERING_TELEMETRY | 266
2024 | nonsummer | VICTOR_1_SOLAR3 | PLANT_TROUBLE | 545.8833
2024 | nonsummer | VICTOR_1_SOLAR3 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | VICTOR_1_SOLAR4 | METERING_TELEMETRY | 0
2024 | nonsummer | VICTOR_1_SOLAR4 | PLANT_TROUBLE | 7.3333
2024 | nonsummer | VICTOR_1_SOLAR4 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | VICTOR_1_VDRYFA | PLANT_TROUBLE | 10.6667
2024 | nonsummer | VICTOR_1_VDRYFB | PLANT_MAINTENANCE | 19.5833
2024 | nonsummer | VICTOR_1_VDRYFB | PLANT_TROUBLE | 147.2667
2024 | nonsummer | VICTOR_1_VDRYFB | TRANSMISSION_INDUCED | 60.6667
2024 | nonsummer | VIKING_2_VCBBT1 | METERING_TELEMETRY | 150
2024 | nonsummer | VIKING_2_VCBBT1 | PLANT_MAINTENANCE | 6000
2024 | nonsummer | VIKING_2_VCBBT1 | PLANT_TROUBLE | 0
2024 | nonsummer | VIKING_2_VCBBT1 | TRANSMISSION_INDUCED | 912.5
2024 | nonsummer | VIKING_2_VCSSR1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | VIKING_2_VCSSR1 | METERING_TELEMETRY | 130
2024 | nonsummer | VIKING_2_VCSSR1 | PLANT_MAINTENANCE | 5330
2024 | nonsummer | VIKING_2_VCSSR1 | PLANT_TROUBLE | 0
2024 | nonsummer | VIKING_2_VCSSR1 | TRANSMISSION_INDUCED | 790.8333
2024 | nonsummer | VIKING_2_VSHSB1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | VIKING_2_VSHSB1 | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | VIKING_2_VSHSB1 | METERING_TELEMETRY | 0
2024 | nonsummer | VIKING_2_VSHSB1 | PLANT_MAINTENANCE | 6000
2024 | nonsummer | VIKING_2_VSHSB1 | PLANT_TROUBLE | 0
2024 | nonsummer | VIKING_2_VSHSB1 | TRANSMISSION_INDUCED | 6000
2024 | nonsummer | VIKING_2_VSHSB1 | UNIT_TESTING | 0
2024 | nonsummer | VISTRA_5_DALBT1 | PLANT_MAINTENANCE | 100
2024 | nonsummer | VISTRA_5_DALBT1 | PLANT_TROUBLE | 2884.9667
2024 | nonsummer | VISTRA_5_DALBT1 | TRANSMISSION_INDUCED | 18.3333
2024 | nonsummer | VISTRA_5_DALBT2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | VISTRA_5_DALBT2 | PLANT_TROUBLE | 2011.95
2024 | nonsummer | VISTRA_5_DALBT2 | TRANSMISSION_INDUCED | 18.3333
2024 | nonsummer | VISTRA_5_DALBT2 | UNIT_TESTING | 500
2024 | nonsummer | VISTRA_5_DALBT3 | PLANT_MAINTENANCE | 0
2024 | nonsummer | VISTRA_5_DALBT3 | PLANT_TROUBLE | 1730.4833
2024 | nonsummer | VISTRA_5_DALBT3 | TRANSMISSION_INDUCED | 18.3333
2024 | nonsummer | VISTRA_5_DALBT3 | UNIT_TESTING | 595.0833
2024 | nonsummer | VISTRA_5_DALBT4 | PLANT_MAINTENANCE | 37.5
2024 | nonsummer | VISTRA_5_DALBT4 | PLANT_TROUBLE | 401.6667
2024 | nonsummer | VISTRA_5_DALBT4 | TRANSMISSION_INDUCED | 18.3333
2024 | nonsummer | VISTRA_5_DALBT4 | UNIT_TESTING | 500
2024 | nonsummer | VISTRA_5_PLABT1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | VISTRA_5_PLABT1 | PLANT_TROUBLE | 6034.47
2024 | nonsummer | VISTRA_5_PLABT1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | VISTRA_5_PLABT1 | UNIT_TESTING | 0
2024 | nonsummer | VISTRA_5_PLABT2 | METERING_TELEMETRY | 0
2024 | nonsummer | VISTRA_5_PLABT2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | VISTRA_5_PLABT2 | PLANT_TROUBLE | 2967.05
2024 | nonsummer | VISTRA_5_PLABT2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | VISTRA_5_PLABT2 | UNIT_TESTING | 0
2024 | nonsummer | VISTRA_5_PLABT3 | PLANT_MAINTENANCE | 0
2024 | nonsummer | VISTRA_5_PLABT3 | PLANT_TROUBLE | 1045.1667
2024 | nonsummer | VISTRA_5_PLABT3 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | VISTRA_5_PLABT3 | UNIT_TESTING | 0
2024 | nonsummer | VISTRA_5_PLABT4 | PLANT_MAINTENANCE | 0
2024 | nonsummer | VISTRA_5_PLABT4 | PLANT_TROUBLE | 1384.8367
2024 | nonsummer | VISTRA_5_PLABT4 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | VISTRA_5_PLABT4 | UNIT_TESTING | 0
2024 | nonsummer | VLCNTR_6_VCEBT1 | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | VLCNTR_6_VCEBT1 | METERING_TELEMETRY | 0
2024 | nonsummer | VLCNTR_6_VCEBT1 | PLANT_MAINTENANCE | 486
2024 | nonsummer | VLCNTR_6_VCEBT1 | PLANT_TROUBLE | 703
2024 | nonsummer | VLCNTR_6_VCEBT1 | TRANSMISSION_INDUCED | 54
2024 | nonsummer | VLCNTR_6_VCEBT2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | VLCNTR_6_VCEBT2 | METERING_TELEMETRY | 0
2024 | nonsummer | VLCNTR_6_VCEBT2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | VLCNTR_6_VCEBT2 | PLANT_TROUBLE | 1947
2024 | nonsummer | VLCNTR_6_VCEBT2 | UNIT_TESTING | 120
2024 | nonsummer | VLCNTR_6_VCSLR | PLANT_MAINTENANCE | 0
2024 | nonsummer | VLCNTR_6_VCSLR | PLANT_TROUBLE | 58.25
2024 | nonsummer | VLCNTR_6_VCSLR1 | PLANT_MAINTENANCE | 14.9167
2024 | nonsummer | VLCNTR_6_VCSLR1 | PLANT_TROUBLE | 20
2024 | nonsummer | VLCNTR_6_VCSLR2 | PLANT_MAINTENANCE | 29.8333
2024 | nonsummer | VLCNTR_6_VCSLR2 | PLANT_TROUBLE | 40
2024 | nonsummer | VOLTA_2_UNIT 1 | PLANT_TROUBLE | 8281
2024 | nonsummer | VOLTA_2_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | VOLTA_2_UNIT 2 | PLANT_TROUBLE | 30
2024 | nonsummer | VOLTA_2_UNIT 2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | VOLTA_6_BAILCK | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 604.2
2024 | nonsummer | VOLTA_6_BAILCK | PLANT_TROUBLE | 10.08
2024 | nonsummer | VOLTA_6_BAILCK | TRANSMISSION_INDUCED | 0
2024 | nonsummer | VOLTA_6_DIGHYD | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | VOLTA_6_DIGHYD | PLANT_TROUBLE | 4.58
2024 | nonsummer | VOLTA_6_DIGHYD | TRANSMISSION_INDUCED | 0
2024 | nonsummer | VOLTA_7_PONHY1 | AMBIENT_NOT_DUE_TO_TEMP | 370.375
2024 | nonsummer | VOLTA_7_PONHY1 | PLANT_TROUBLE | 6.25
2024 | nonsummer | VOLTA_7_PONHY1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | VOLTA_7_QFUNTS | TRANSMISSION_INDUCED | 0
2024 | nonsummer | VOYAGR_2_VOAWD5 | PLANT_TROUBLE | 0
2024 | nonsummer | VOYAGR_2_VOYWD1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | VOYAGR_2_VOYWD2 | METERING_TELEMETRY | 707.56
2024 | nonsummer | VOYAGR_2_VOYWD2 | PLANT_TROUBLE | 0
2024 | nonsummer | VOYAGR_2_VOYWD3 | PLANT_TROUBLE | 0
2024 | nonsummer | VOYAGR_2_VOYWD4 | PLANT_TROUBLE | 0
2024 | nonsummer | VSTAES_6_VESBT1 | METERING_TELEMETRY | 0
2024 | nonsummer | VSTAES_6_VESBT1 | PLANT_MAINTENANCE | 12.5
2024 | nonsummer | VSTAES_6_VESBT1 | PLANT_TROUBLE | 4453.9582
2024 | nonsummer | WADHAM_6_UNIT | METERING_TELEMETRY | 0
2024 | nonsummer | WADHAM_6_UNIT | PLANT_MAINTENANCE | 7558.2
2024 | nonsummer | WADHAM_6_UNIT | PLANT_TROUBLE | 80.3
2024 | nonsummer | WALCRK_2_CTG1 | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | WALCRK_2_CTG1 | PLANT_MAINTENANCE | 2002
2024 | nonsummer | WALCRK_2_CTG1 | PLANT_TROUBLE | 26.04
2024 | nonsummer | WALCRK_2_CTG1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | WALCRK_2_CTG1 | UNIT_TESTING | 0
2024 | nonsummer | WALCRK_2_CTG2 | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | WALCRK_2_CTG2 | PLANT_MAINTENANCE | 3503.5
2024 | nonsummer | WALCRK_2_CTG2 | PLANT_TROUBLE | 180.8583
2024 | nonsummer | WALCRK_2_CTG2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | WALCRK_2_CTG3 | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | WALCRK_2_CTG3 | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | nonsummer | WALCRK_2_CTG3 | PLANT_MAINTENANCE | 2968.5
2024 | nonsummer | WALCRK_2_CTG3 | PLANT_TROUBLE | 6765.5
2024 | nonsummer | WALCRK_2_CTG3 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | WALCRK_2_CTG4 | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | WALCRK_2_CTG4 | PLANT_MAINTENANCE | 0
2024 | nonsummer | WALCRK_2_CTG4 | PLANT_TROUBLE | 13129.9
2024 | nonsummer | WALCRK_2_CTG4 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | WALCRK_2_CTG4 | UNIT_TESTING | 0
2024 | nonsummer | WALCRK_2_CTG5 | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | WALCRK_2_CTG5 | PLANT_MAINTENANCE | 2002
2024 | nonsummer | WALCRK_2_CTG5 | PLANT_TROUBLE | 0
2024 | nonsummer | WALCRK_2_CTG5 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | WALCRK_2_CTG5 | UNIT_TESTING | 0
2024 | nonsummer | WALNUT_6_HILLGEN | PLANT_TROUBLE | 424.2567
2024 | nonsummer | WALNUT_7_WCOVST | PLANT_MAINTENANCE | 357.5
2024 | nonsummer | WALNUT_7_WCOVST | PLANT_TROUBLE | 2156.0083
2024 | nonsummer | WARNE_2_UNIT | ENVIRONMENTAL_RESTRICTIONS | 0
2024 | nonsummer | WARNE_2_UNIT | PLANT_MAINTENANCE | 1013.5833
2024 | nonsummer | WARNE_2_UNIT | PLANT_TROUBLE | 673.3167
2024 | nonsummer | WAUKNA_1_SOLAR | PLANT_MAINTENANCE | 5
2024 | nonsummer | WAUKNA_1_SOLAR | PLANT_TROUBLE | 8
2024 | nonsummer | WDFRDF_2_WFFBT1 | METERING_TELEMETRY | 125
2024 | nonsummer | WDFRDF_2_WFFBT1 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | nonsummer | WDFRDF_2_WFFBT1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | WDFRDF_2_WFFBT1 | PLANT_TROUBLE | 67.5
2024 | nonsummer | WDLEAF_7_UNIT 1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 2716.55
2024 | nonsummer | WDLEAF_7_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | WDLEAF_7_UNIT 1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | WDLEAF_7_UNIT 1 | PLANT_TROUBLE | 0
2024 | nonsummer | WDLEAF_7_UNIT 1 | TRANSMISSION_INDUCED | 36
2024 | nonsummer | WEBER_6_FORWRD | TRANSMISSION_INDUCED | 8.12
2024 | nonsummer | WEEDPC_6_KNSSR1 | NEW_GENERATOR_TEST_ENERGY | 331.8
2024 | nonsummer | WEEDPC_6_KNSSR1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | WESCAN_2_BDSBT1 | METERING_TELEMETRY | 0
2024 | nonsummer | WESCAN_2_BDSBT1 | PLANT_MAINTENANCE | 589.5
2024 | nonsummer | WESCAN_2_BDSBT1 | PLANT_TROUBLE | 1480.3
2024 | nonsummer | WESCAN_2_BDSBT1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | WESCN2_2_BDSBT1 | NEW_GENERATOR_TEST_ENERGY | 9495
2024 | nonsummer | WESTPT_2_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 24.55
2024 | nonsummer | WESTPT_2_UNIT | PLANT_MAINTENANCE | 0
2024 | nonsummer | WESTPT_2_UNIT | PLANT_TROUBLE | 13.7667
2024 | nonsummer | WESTPT_2_UNIT | UNIT_TESTING | 0
2024 | nonsummer | WFRESN_1_SOLAR | PLANT_TROUBLE | 445.75
2024 | nonsummer | WHEATL_6_LNDFIL | PLANT_TROUBLE | 11.3008
2024 | nonsummer | WHITEH_2_MEADDYN1 | PLANT_TROUBLE | 3586.5827
2024 | nonsummer | WHITEH_2_MEADDYN2 | PLANT_TROUBLE | 14685.609
2024 | nonsummer | WHITEW_5_WWRSR1 | METERING_TELEMETRY | 0
2024 | nonsummer | WHITEW_5_WWRSR1 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | nonsummer | WHITEW_5_WWRSR1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | WHITEW_5_WWRSR1 | UNIT_TESTING | 0
2024 | nonsummer | WHITNY_6_SOLAR | METERING_TELEMETRY | 0
2024 | nonsummer | WHITNY_6_SOLAR | PLANT_MAINTENANCE | 0
2024 | nonsummer | WHTWTR_1_WINDA1 | PLANT_MAINTENANCE | 101.6
2024 | nonsummer | WHTWTR_1_WINDA1 | PLANT_TROUBLE | 13706.5
2024 | nonsummer | WHTWTR_1_WINDA1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | WILLMS_6_ARBBM1 | AMBIENT_DUE_TO_TEMP | 0
2024 | nonsummer | WILLMS_6_ARBBM1 | AMBIENT_NOT_DUE_TO_TEMP | 0
2024 | nonsummer | WILLMS_6_ARBBM1 | PLANT_MAINTENANCE | 107
2024 | nonsummer | WILLMS_6_ARBBM1 | PLANT_TROUBLE | 46.45
2024 | nonsummer | WILLMS_6_ARBBM1 | TRANSMISSION_INDUCED | 8.5
2024 | nonsummer | WISE_1_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 5110.7858
2024 | nonsummer | WISE_1_UNIT 1 | PLANT_TROUBLE | 185.15
2024 | nonsummer | WISE_1_UNIT 2 | AMBIENT_NOT_DUE_TO_TEMP | 2416
2024 | nonsummer | WISHON_6_UNITS | AMBIENT_NOT_DUE_TO_TEMP | 9006.3383
2024 | nonsummer | WISHON_6_UNITS | PLANT_MAINTENANCE | 2745
2024 | nonsummer | WISHON_6_UNITS | PLANT_TROUBLE | 248.0667
2024 | nonsummer | WISHON_6_UNITS | TRANSMISSION_INDUCED | 184
2024 | nonsummer | WISTER_2_WISSR1 | PLANT_TROUBLE | 6058
2024 | nonsummer | WISTER_2_WISSR1 | TRANSMISSION_INDUCED | 150
2024 | nonsummer | WISTRA_2_WRSSR1 | PLANT_MAINTENANCE | 165
2024 | nonsummer | WISTRA_2_WRSSR1 | PLANT_TROUBLE | 692.4
2024 | nonsummer | WISTRA_2_WRSSR1 | TRANSMISSION_INDUCED | 200
2024 | nonsummer | WLDWD_1_SOLAR1 | METERING_TELEMETRY | 0
2024 | nonsummer | WLDWD_1_SOLAR1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | WLDWD_1_SOLAR1 | PLANT_TROUBLE | 0
2024 | nonsummer | WLDWD_1_SOLAR1 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | WLDWD_1_SOLAR2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | WNDMAS_2_UNIT 1 | METERING_TELEMETRY | 5
2024 | nonsummer | WNDMAS_2_UNIT 1 | PLANT_MAINTENANCE | 202.2833
2024 | nonsummer | WNDMAS_2_UNIT 1 | TRANSMISSION_INDUCED | 1299.6
2024 | nonsummer | WNDSTR_2_WIND | PLANT_MAINTENANCE | 0
2024 | nonsummer | WNDSTR_2_WIND | PLANT_TROUBLE | 310
2024 | nonsummer | WNDSTR_2_WIND | TRANSMISSION_INDUCED | 60
2024 | nonsummer | WOLFSK_1_UNITA1 | AMBIENT_DUE_TO_TEMP | 486.036
2024 | nonsummer | WOLFSK_1_UNITA1 | PLANT_MAINTENANCE | 339.9487
2024 | nonsummer | WOLFSK_1_UNITA1 | PLANT_TROUBLE | 0
2024 | nonsummer | WRGTSR_2_WSFSR1 | METERING_TELEMETRY | 522.45
2024 | nonsummer | WRGTSR_2_WSFSR1 | PLANT_MAINTENANCE | 402.75
2024 | nonsummer | WRGTSR_2_WSFSR1 | PLANT_TROUBLE | 36572.5
2024 | nonsummer | WSENGY_1_UNIT 1 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 915.0005
2024 | nonsummer | WSENGY_1_UNIT 1 | AMBIENT_NOT_DUE_TO_TEMP | 61.3
2024 | nonsummer | WSENGY_1_UNIT 1 | PLANT_MAINTENANCE | 2804.0808
2024 | nonsummer | WSENGY_1_UNIT 1 | PLANT_TROUBLE | 2614.7215
2024 | nonsummer | WSNR_2_CVPDYN | PLANT_TROUBLE | 0
2024 | nonsummer | WSNR_2_CVPDYN | TECHNICAL_LIMITATIONS_NOT_IN_MARKET_MODEL | 0
2024 | nonsummer | WSTWND_2_M89BT2 | PLANT_MAINTENANCE | 35.3
2024 | nonsummer | WSTWND_2_M89BT2 | PLANT_TROUBLE | 8840.5267
2024 | nonsummer | WSTWND_2_M89BT2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | WSTWND_2_M89WD2 | PLANT_MAINTENANCE | 32.76
2024 | nonsummer | WSTWND_2_M89WD2 | PLANT_TROUBLE | 25609.806
2024 | nonsummer | WSTWND_2_M89WD2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | WSTWND_2_M90WD2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | WSTWND_2_M90WD2 | PLANT_TROUBLE | 21055.5213
2024 | nonsummer | WSTWND_2_M90WD2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | WSTWND_2_SBSBT1 | METERING_TELEMETRY | 24
2024 | nonsummer | WSTWND_2_SBSBT1 | PLANT_MAINTENANCE | 0
2024 | nonsummer | WSTWND_2_SBSBT1 | PLANT_TROUBLE | 6.7167
2024 | nonsummer | WSTWND_2_SBSBT1 | TRANSMISSION_INDUCED | 264
2024 | nonsummer | WSTWND_2_SBSBT2 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | nonsummer | WSTWND_2_SBSBT2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | WSTWND_2_SBSBT2 | PLANT_TROUBLE | 24
2024 | nonsummer | WSTWND_2_SBSBT2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | WSTWND_2_SBSBT2 | UNIT_TESTING | 0
2024 | nonsummer | WSTWND_2_SBSBT3 | METERING_TELEMETRY | 0
2024 | nonsummer | WSTWND_2_SBSBT3 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | nonsummer | WSTWND_2_SBSBT3 | PLANT_MAINTENANCE | 0
2024 | nonsummer | WSTWND_2_SBSBT3 | PLANT_TROUBLE | 0
2024 | nonsummer | WSTWND_2_SBSBT3 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | WSTWND_2_SBSBT3 | UNIT_TESTING | 0
2024 | nonsummer | YELPIN_2_YP2BT1 | PLANT_TROUBLE | 1362.118
2024 | nonsummer | YELPIN_2_YP2BT1 | RTU_RIG | 1119.0833
2024 | nonsummer | YELPIN_2_YP2BT2 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | YELPIN_2_YP2BT2 | METERING_TELEMETRY | 318
2024 | nonsummer | YELPIN_2_YP2BT2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | YELPIN_2_YP2BT2 | PLANT_TROUBLE | 1168.65
2024 | nonsummer | YELPIN_2_YP2BT2 | UNIT_TESTING | 0
2024 | nonsummer | YELPIN_2_YP2BT3 | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 0
2024 | nonsummer | YELPIN_2_YP2BT3 | METERING_TELEMETRY | 285.3333
2024 | nonsummer | YELPIN_2_YP2BT3 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | nonsummer | YELPIN_2_YP2BT3 | PLANT_MAINTENANCE | 0
2024 | nonsummer | YELPIN_2_YP2BT3 | PLANT_TROUBLE | 720
2024 | nonsummer | YELPIN_2_YP2BT3 | UNIT_TESTING | 0
2024 | nonsummer | YELPIN_2_YP2SR1 | PLANT_MAINTENANCE | 1201.5
2024 | nonsummer | YELPIN_2_YP2SR1 | PLANT_TROUBLE | 0
2024 | nonsummer | YELPIN_2_YP2SR1 | UNIT_TESTING | 0
2024 | nonsummer | YELPIN_2_YP2SR2 | PLANT_MAINTENANCE | 0
2024 | nonsummer | YELPIN_2_YP2SR2 | PLANT_TROUBLE | 0
2024 | nonsummer | YELPIN_2_YP2SR2 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | YELPIN_2_YP2SR2 | UNIT_TESTING | 0
2024 | nonsummer | YELPIN_2_YP2SR3 | NEW_GENERATOR_TEST_ENERGY | 0
2024 | nonsummer | YELPIN_2_YP2SR3 | TRANSMISSION_INDUCED | 0
2024 | nonsummer | YELPIN_2_YP2SR3 | UNIT_TESTING | 0
2024 | nonsummer | YUBACT_1_SUNSWT | AMBIENT_DUE_TO_FUEL_INSUFFICIENCY | 149.91
2024 | nonsummer | YUBACT_1_SUNSWT | PLANT_MAINTENANCE | 2248.65
2024 | nonsummer | YUBACT_1_SUNSWT | PLANT_TROUBLE | 313.9782
2024 | nonsummer | YUBACT_1_SUNSWT | TRANSMISSION_INDUCED | 195.7158
2024 | nonsummer | YUBACT_6_UNITA1 | AMBIENT_DUE_TO_TEMP | 187
2024 | nonsummer | YUBACT_6_UNITA1 | PLANT_TROUBLE | 1026.266
2024 | nonsummer | YUBACT_6_UNITA1 | TRANSITIONAL_LIMITATION | 0
2024 | nonsummer | YUBACT_6_UNITA1 | TRANSMISSION_INDUCED | 152.484
2024 | nonsummer | ZOND_6_UNIT | AMBIENT_NOT_DUE_TO_TEMP | 18126

## Demand Hours
START DATETIME | END DATETIME | SEASON | DEMAND HOUR | UCAP SEASON
2022-01-01 | 2022-01-01 01:00 | Winter | FALSE | nonsummer
2022-01-01 01:00 | 2022-01-01 02:00 | Winter | FALSE | nonsummer
2022-01-01 02:00 | 2022-01-01 03:00 | Winter | FALSE | nonsummer
2022-01-01 03:00 | 2022-01-01 04:00 | Winter | FALSE | nonsummer
2022-01-01 04:00 | 2022-01-01 05:00 | Winter | FALSE | nonsummer
2022-01-01 05:00 | 2022-01-01 06:00 | Winter | FALSE | nonsummer
2022-01-01 06:00 | 2022-01-01 07:00 | Winter | FALSE | nonsummer
2022-01-01 07:00 | 2022-01-01 08:00 | Winter | FALSE | nonsummer
2022-01-01 08:00 | 2022-01-01 09:00 | Winter | FALSE | nonsummer
2022-01-01 09:00 | 2022-01-01 10:00 | Winter | FALSE | nonsummer
2022-01-01 10:00 | 2022-01-01 11:00 | Winter | FALSE | nonsummer
2022-01-01 11:00 | 2022-01-01 12:00 | Winter | FALSE | nonsummer
2022-01-01 12:00 | 2022-01-01 13:00 | Winter | FALSE | nonsummer
2022-01-01 13:00 | 2022-01-01 14:00 | Winter | FALSE | nonsummer
2022-01-01 14:00 | 2022-01-01 15:00 | Winter | FALSE | nonsummer
2022-01-01 15:00 | 2022-01-01 16:00 | Winter | FALSE | nonsummer
2022-01-01 16:00 | 2022-01-01 17:00 | Winter | TRUE | nonsummer
2022-01-01 17:00 | 2022-01-01 18:00 | Winter | TRUE | nonsummer
2022-01-01 18:00 | 2022-01-01 19:00 | Winter | TRUE | nonsummer
2022-01-01 19:00 | 2022-01-01 20:00 | Winter | TRUE | nonsummer
2022-01-01 20:00 | 2022-01-01 21:00 | Winter | TRUE | nonsummer
2022-01-01 21:00 | 2022-01-01 22:00 | Winter | FALSE | nonsummer
2022-01-01 22:00 | 2022-01-01 23:00 | Winter | FALSE | nonsummer
2022-01-01 23:00 | 2022-01-02 | Winter | FALSE | nonsummer
2022-01-02 | 2022-01-02 01:00 | Winter | FALSE | nonsummer
2022-01-02 01:00 | 2022-01-02 02:00 | Winter | FALSE | nonsummer
2022-01-02 02:00 | 2022-01-02 03:00 | Winter | FALSE | nonsummer
2022-01-02 03:00 | 2022-01-02 04:00 | Winter | FALSE | nonsummer
2022-01-02 04:00 | 2022-01-02 05:00 | Winter | FALSE | nonsummer
2022-01-02 05:00 | 2022-01-02 06:00 | Winter | FALSE | nonsummer
2022-01-02 06:00 | 2022-01-02 07:00 | Winter | FALSE | nonsummer
2022-01-02 07:00 | 2022-01-02 08:00 | Winter | FALSE | nonsummer
2022-01-02 08:00 | 2022-01-02 09:00 | Winter | FALSE | nonsummer
2022-01-02 09:00 | 2022-01-02 10:00 | Winter | FALSE | nonsummer
2022-01-02 10:00 | 2022-01-02 11:00 | Winter | FALSE | nonsummer
2022-01-02 11:00 | 2022-01-02 12:00 | Winter | FALSE | nonsummer
2022-01-02 12:00 | 2022-01-02 13:00 | Winter | FALSE | nonsummer
2022-01-02 13:00 | 2022-01-02 14:00 | Winter | FALSE | nonsummer
2022-01-02 14:00 | 2022-01-02 15:00 | Winter | FALSE | nonsummer
2022-01-02 15:00 | 2022-01-02 16:00 | Winter | FALSE | nonsummer
2022-01-02 16:00 | 2022-01-02 17:00 | Winter | TRUE | nonsummer
2022-01-02 17:00 | 2022-01-02 18:00 | Winter | TRUE | nonsummer
2022-01-02 18:00 | 2022-01-02 19:00 | Winter | TRUE | nonsummer
2022-01-02 19:00 | 2022-01-02 20:00 | Winter | TRUE | nonsummer
2022-01-02 20:00 | 2022-01-02 21:00 | Winter | TRUE | nonsummer
2022-01-02 21:00 | 2022-01-02 22:00 | Winter | FALSE | nonsummer
2022-01-02 22:00 | 2022-01-02 23:00 | Winter | FALSE | nonsummer
2022-01-02 23:00 | 2022-01-03 | Winter | FALSE | nonsummer
2022-01-03 | 2022-01-03 01:00 | Winter | FALSE | nonsummer
2022-01-03 01:00 | 2022-01-03 02:00 | Winter | FALSE | nonsummer
2022-01-03 02:00 | 2022-01-03 03:00 | Winter | FALSE | nonsummer
2022-01-03 03:00 | 2022-01-03 04:00 | Winter | FALSE | nonsummer
2022-01-03 04:00 | 2022-01-03 05:00 | Winter | FALSE | nonsummer
2022-01-03 05:00 | 2022-01-03 06:00 | Winter | FALSE | nonsummer
2022-01-03 06:00 | 2022-01-03 07:00 | Winter | FALSE | nonsummer
2022-01-03 07:00 | 2022-01-03 08:00 | Winter | FALSE | nonsummer
2022-01-03 08:00 | 2022-01-03 09:00 | Winter | FALSE | nonsummer
2022-01-03 09:00 | 2022-01-03 10:00 | Winter | FALSE | nonsummer
2022-01-03 10:00 | 2022-01-03 11:00 | Winter | FALSE | nonsummer
2022-01-03 11:00 | 2022-01-03 12:00 | Winter | FALSE | nonsummer
2022-01-03 12:00 | 2022-01-03 13:00 | Winter | FALSE | nonsummer
2022-01-03 13:00 | 2022-01-03 14:00 | Winter | FALSE | nonsummer
2022-01-03 14:00 | 2022-01-03 15:00 | Winter | FALSE | nonsummer
2022-01-03 15:00 | 2022-01-03 16:00 | Winter | FALSE | nonsummer
2022-01-03 16:00 | 2022-01-03 17:00 | Winter | TRUE | nonsummer
2022-01-03 17:00 | 2022-01-03 18:00 | Winter | TRUE | nonsummer
2022-01-03 18:00 | 2022-01-03 19:00 | Winter | TRUE | nonsummer
2022-01-03 19:00 | 2022-01-03 20:00 | Winter | TRUE | nonsummer
2022-01-03 20:00 | 2022-01-03 21:00 | Winter | TRUE | nonsummer
2022-01-03 21:00 | 2022-01-03 22:00 | Winter | FALSE | nonsummer
2022-01-03 22:00 | 2022-01-03 23:00 | Winter | FALSE | nonsummer
2022-01-03 23:00 | 2022-01-04 | Winter | FALSE | nonsummer
2022-01-04 | 2022-01-04 01:00 | Winter | FALSE | nonsummer
2022-01-04 01:00 | 2022-01-04 02:00 | Winter | FALSE | nonsummer
2022-01-04 02:00 | 2022-01-04 03:00 | Winter | FALSE | nonsummer
2022-01-04 03:00 | 2022-01-04 04:00 | Winter | FALSE | nonsummer
2022-01-04 04:00 | 2022-01-04 05:00 | Winter | FALSE | nonsummer
2022-01-04 05:00 | 2022-01-04 06:00 | Winter | FALSE | nonsummer
2022-01-04 06:00 | 2022-01-04 07:00 | Winter | FALSE | nonsummer
2022-01-04 07:00 | 2022-01-04 08:00 | Winter | FALSE | nonsummer
2022-01-04 08:00 | 2022-01-04 09:00 | Winter | FALSE | nonsummer
2022-01-04 09:00 | 2022-01-04 10:00 | Winter | FALSE | nonsummer
2022-01-04 10:00 | 2022-01-04 11:00 | Winter | FALSE | nonsummer
2022-01-04 11:00 | 2022-01-04 12:00 | Winter | FALSE | nonsummer
2022-01-04 12:00 | 2022-01-04 13:00 | Winter | FALSE | nonsummer
2022-01-04 13:00 | 2022-01-04 14:00 | Winter | FALSE | nonsummer
2022-01-04 14:00 | 2022-01-04 15:00 | Winter | FALSE | nonsummer
2022-01-04 15:00 | 2022-01-04 16:00 | Winter | FALSE | nonsummer
2022-01-04 16:00 | 2022-01-04 17:00 | Winter | TRUE | nonsummer
2022-01-04 17:00 | 2022-01-04 18:00 | Winter | TRUE | nonsummer
2022-01-04 18:00 | 2022-01-04 19:00 | Winter | TRUE | nonsummer
2022-01-04 19:00 | 2022-01-04 20:00 | Winter | TRUE | nonsummer
2022-01-04 20:00 | 2022-01-04 21:00 | Winter | TRUE | nonsummer
2022-01-04 21:00 | 2022-01-04 22:00 | Winter | FALSE | nonsummer
2022-01-04 22:00 | 2022-01-04 23:00 | Winter | FALSE | nonsummer
2022-01-04 23:00 | 2022-01-05 | Winter | FALSE | nonsummer
2022-01-05 | 2022-01-05 01:00 | Winter | FALSE | nonsummer
2022-01-05 01:00 | 2022-01-05 02:00 | Winter | FALSE | nonsummer
2022-01-05 02:00 | 2022-01-05 03:00 | Winter | FALSE | nonsummer
2022-01-05 03:00 | 2022-01-05 04:00 | Winter | FALSE | nonsummer
2022-01-05 04:00 | 2022-01-05 05:00 | Winter | FALSE | nonsummer
2022-01-05 05:00 | 2022-01-05 06:00 | Winter | FALSE | nonsummer
2022-01-05 06:00 | 2022-01-05 07:00 | Winter | FALSE | nonsummer
2022-01-05 07:00 | 2022-01-05 08:00 | Winter | FALSE | nonsummer
2022-01-05 08:00 | 2022-01-05 09:00 | Winter | FALSE | nonsummer
2022-01-05 09:00 | 2022-01-05 10:00 | Winter | FALSE | nonsummer
2022-01-05 10:00 | 2022-01-05 11:00 | Winter | FALSE | nonsummer
2022-01-05 11:00 | 2022-01-05 12:00 | Winter | FALSE | nonsummer
2022-01-05 12:00 | 2022-01-05 13:00 | Winter | FALSE | nonsummer
2022-01-05 13:00 | 2022-01-05 14:00 | Winter | FALSE | nonsummer
2022-01-05 14:00 | 2022-01-05 15:00 | Winter | FALSE | nonsummer
2022-01-05 15:00 | 2022-01-05 16:00 | Winter | FALSE | nonsummer
2022-01-05 16:00 | 2022-01-05 17:00 | Winter | TRUE | nonsummer
2022-01-05 17:00 | 2022-01-05 18:00 | Winter | TRUE | nonsummer
2022-01-05 18:00 | 2022-01-05 19:00 | Winter | TRUE | nonsummer
2022-01-05 19:00 | 2022-01-05 20:00 | Winter | TRUE | nonsummer
2022-01-05 20:00 | 2022-01-05 21:00 | Winter | TRUE | nonsummer
2022-01-05 21:00 | 2022-01-05 22:00 | Winter | FALSE | nonsummer
2022-01-05 22:00 | 2022-01-05 23:00 | Winter | FALSE | nonsummer
2022-01-05 23:00 | 2022-01-06 | Winter | FALSE | nonsummer
2022-01-06 | 2022-01-06 01:00 | Winter | FALSE | nonsummer
2022-01-06 01:00 | 2022-01-06 02:00 | Winter | FALSE | nonsummer
2022-01-06 02:00 | 2022-01-06 03:00 | Winter | FALSE | nonsummer
2022-01-06 03:00 | 2022-01-06 04:00 | Winter | FALSE | nonsummer
2022-01-06 04:00 | 2022-01-06 05:00 | Winter | FALSE | nonsummer
2022-01-06 05:00 | 2022-01-06 06:00 | Winter | FALSE | nonsummer
2022-01-06 06:00 | 2022-01-06 07:00 | Winter | FALSE | nonsummer
2022-01-06 07:00 | 2022-01-06 08:00 | Winter | FALSE | nonsummer
2022-01-06 08:00 | 2022-01-06 09:00 | Winter | FALSE | nonsummer
2022-01-06 09:00 | 2022-01-06 10:00 | Winter | FALSE | nonsummer
2022-01-06 10:00 | 2022-01-06 11:00 | Winter | FALSE | nonsummer
2022-01-06 11:00 | 2022-01-06 12:00 | Winter | FALSE | nonsummer
2022-01-06 12:00 | 2022-01-06 13:00 | Winter | FALSE | nonsummer
2022-01-06 13:00 | 2022-01-06 14:00 | Winter | FALSE | nonsummer
2022-01-06 14:00 | 2022-01-06 15:00 | Winter | FALSE | nonsummer
2022-01-06 15:00 | 2022-01-06 16:00 | Winter | FALSE | nonsummer
2022-01-06 16:00 | 2022-01-06 17:00 | Winter | TRUE | nonsummer
2022-01-06 17:00 | 2022-01-06 18:00 | Winter | TRUE | nonsummer
2022-01-06 18:00 | 2022-01-06 19:00 | Winter | TRUE | nonsummer
2022-01-06 19:00 | 2022-01-06 20:00 | Winter | TRUE | nonsummer
2022-01-06 20:00 | 2022-01-06 21:00 | Winter | TRUE | nonsummer
2022-01-06 21:00 | 2022-01-06 22:00 | Winter | FALSE | nonsummer
2022-01-06 22:00 | 2022-01-06 23:00 | Winter | FALSE | nonsummer
2022-01-06 23:00 | 2022-01-07 | Winter | FALSE | nonsummer
2022-01-07 | 2022-01-07 01:00 | Winter | FALSE | nonsummer
2022-01-07 01:00 | 2022-01-07 02:00 | Winter | FALSE | nonsummer
2022-01-07 02:00 | 2022-01-07 03:00 | Winter | FALSE | nonsummer
2022-01-07 03:00 | 2022-01-07 04:00 | Winter | FALSE | nonsummer
2022-01-07 04:00 | 2022-01-07 05:00 | Winter | FALSE | nonsummer
2022-01-07 05:00 | 2022-01-07 06:00 | Winter | FALSE | nonsummer
2022-01-07 06:00 | 2022-01-07 07:00 | Winter | FALSE | nonsummer
2022-01-07 07:00 | 2022-01-07 08:00 | Winter | FALSE | nonsummer
2022-01-07 08:00 | 2022-01-07 09:00 | Winter | FALSE | nonsummer
2022-01-07 09:00 | 2022-01-07 10:00 | Winter | FALSE | nonsummer
2022-01-07 10:00 | 2022-01-07 11:00 | Winter | FALSE | nonsummer
2022-01-07 11:00 | 2022-01-07 12:00 | Winter | FALSE | nonsummer
2022-01-07 12:00 | 2022-01-07 13:00 | Winter | FALSE | nonsummer
2022-01-07 13:00 | 2022-01-07 14:00 | Winter | FALSE | nonsummer
2022-01-07 14:00 | 2022-01-07 15:00 | Winter | FALSE | nonsummer
2022-01-07 15:00 | 2022-01-07 16:00 | Winter | FALSE | nonsummer
2022-01-07 16:00 | 2022-01-07 17:00 | Winter | TRUE | nonsummer
2022-01-07 17:00 | 2022-01-07 18:00 | Winter | TRUE | nonsummer
2022-01-07 18:00 | 2022-01-07 19:00 | Winter | TRUE | nonsummer
2022-01-07 19:00 | 2022-01-07 20:00 | Winter | TRUE | nonsummer
2022-01-07 20:00 | 2022-01-07 21:00 | Winter | TRUE | nonsummer
2022-01-07 21:00 | 2022-01-07 22:00 | Winter | FALSE | nonsummer
2022-01-07 22:00 | 2022-01-07 23:00 | Winter | FALSE | nonsummer
2022-01-07 23:00 | 2022-01-08 | Winter | FALSE | nonsummer
2022-01-08 | 2022-01-08 01:00 | Winter | FALSE | nonsummer
2022-01-08 01:00 | 2022-01-08 02:00 | Winter | FALSE | nonsummer
2022-01-08 02:00 | 2022-01-08 03:00 | Winter | FALSE | nonsummer
2022-01-08 03:00 | 2022-01-08 04:00 | Winter | FALSE | nonsummer
2022-01-08 04:00 | 2022-01-08 05:00 | Winter | FALSE | nonsummer
2022-01-08 05:00 | 2022-01-08 06:00 | Winter | FALSE | nonsummer
2022-01-08 06:00 | 2022-01-08 07:00 | Winter | FALSE | nonsummer
2022-01-08 07:00 | 2022-01-08 08:00 | Winter | FALSE | nonsummer
2022-01-08 08:00 | 2022-01-08 09:00 | Winter | FALSE | nonsummer
2022-01-08 09:00 | 2022-01-08 10:00 | Winter | FALSE | nonsummer
2022-01-08 10:00 | 2022-01-08 11:00 | Winter | FALSE | nonsummer
2022-01-08 11:00 | 2022-01-08 12:00 | Winter | FALSE | nonsummer
2022-01-08 12:00 | 2022-01-08 13:00 | Winter | FALSE | nonsummer
2022-01-08 13:00 | 2022-01-08 14:00 | Winter | FALSE | nonsummer
2022-01-08 14:00 | 2022-01-08 15:00 | Winter | FALSE | nonsummer
2022-01-08 15:00 | 2022-01-08 16:00 | Winter | FALSE | nonsummer
2022-01-08 16:00 | 2022-01-08 17:00 | Winter | TRUE | nonsummer
2022-01-08 17:00 | 2022-01-08 18:00 | Winter | TRUE | nonsummer
2022-01-08 18:00 | 2022-01-08 19:00 | Winter | TRUE | nonsummer
2022-01-08 19:00 | 2022-01-08 20:00 | Winter | TRUE | nonsummer
2022-01-08 20:00 | 2022-01-08 21:00 | Winter | TRUE | nonsummer
2022-01-08 21:00 | 2022-01-08 22:00 | Winter | FALSE | nonsummer
2022-01-08 22:00 | 2022-01-08 23:00 | Winter | FALSE | nonsummer
2022-01-08 23:00 | 2022-01-09 | Winter | FALSE | nonsummer
2022-01-09 | 2022-01-09 01:00 | Winter | FALSE | nonsummer
2022-01-09 01:00 | 2022-01-09 02:00 | Winter | FALSE | nonsummer
2022-01-09 02:00 | 2022-01-09 03:00 | Winter | FALSE | nonsummer
2022-01-09 03:00 | 2022-01-09 04:00 | Winter | FALSE | nonsummer
2022-01-09 04:00 | 2022-01-09 05:00 | Winter | FALSE | nonsummer
2022-01-09 05:00 | 2022-01-09 06:00 | Winter | FALSE | nonsummer
2022-01-09 06:00 | 2022-01-09 07:00 | Winter | FALSE | nonsummer
2022-01-09 07:00 | 2022-01-09 08:00 | Winter | FALSE | nonsummer
2022-01-09 08:00 | 2022-01-09 09:00 | Winter | FALSE | nonsummer
2022-01-09 09:00 | 2022-01-09 10:00 | Winter | FALSE | nonsummer
2022-01-09 10:00 | 2022-01-09 11:00 | Winter | FALSE | nonsummer
2022-01-09 11:00 | 2022-01-09 12:00 | Winter | FALSE | nonsummer
2022-01-09 12:00 | 2022-01-09 13:00 | Winter | FALSE | nonsummer
2022-01-09 13:00 | 2022-01-09 14:00 | Winter | FALSE | nonsummer
2022-01-09 14:00 | 2022-01-09 15:00 | Winter | FALSE | nonsummer
2022-01-09 15:00 | 2022-01-09 16:00 | Winter | FALSE | nonsummer
2022-01-09 16:00 | 2022-01-09 17:00 | Winter | TRUE | nonsummer
2022-01-09 17:00 | 2022-01-09 18:00 | Winter | TRUE | nonsummer
2022-01-09 18:00 | 2022-01-09 19:00 | Winter | TRUE | nonsummer
2022-01-09 19:00 | 2022-01-09 20:00 | Winter | TRUE | nonsummer
2022-01-09 20:00 | 2022-01-09 21:00 | Winter | TRUE | nonsummer
2022-01-09 21:00 | 2022-01-09 22:00 | Winter | FALSE | nonsummer
2022-01-09 22:00 | 2022-01-09 23:00 | Winter | FALSE | nonsummer
2022-01-09 23:00 | 2022-01-10 | Winter | FALSE | nonsummer
2022-01-10 | 2022-01-10 01:00 | Winter | FALSE | nonsummer
2022-01-10 01:00 | 2022-01-10 02:00 | Winter | FALSE | nonsummer
2022-01-10 02:00 | 2022-01-10 03:00 | Winter | FALSE | nonsummer
2022-01-10 03:00 | 2022-01-10 04:00 | Winter | FALSE | nonsummer
2022-01-10 04:00 | 2022-01-10 05:00 | Winter | FALSE | nonsummer
2022-01-10 05:00 | 2022-01-10 06:00 | Winter | FALSE | nonsummer
2022-01-10 06:00 | 2022-01-10 07:00 | Winter | FALSE | nonsummer
2022-01-10 07:00 | 2022-01-10 08:00 | Winter | FALSE | nonsummer
2022-01-10 08:00 | 2022-01-10 09:00 | Winter | FALSE | nonsummer
2022-01-10 09:00 | 2022-01-10 10:00 | Winter | FALSE | nonsummer
2022-01-10 10:00 | 2022-01-10 11:00 | Winter | FALSE | nonsummer
2022-01-10 11:00 | 2022-01-10 12:00 | Winter | FALSE | nonsummer
2022-01-10 12:00 | 2022-01-10 13:00 | Winter | FALSE | nonsummer
2022-01-10 13:00 | 2022-01-10 14:00 | Winter | FALSE | nonsummer
2022-01-10 14:00 | 2022-01-10 15:00 | Winter | FALSE | nonsummer
2022-01-10 15:00 | 2022-01-10 16:00 | Winter | FALSE | nonsummer
2022-01-10 16:00 | 2022-01-10 17:00 | Winter | TRUE | nonsummer
2022-01-10 17:00 | 2022-01-10 18:00 | Winter | TRUE | nonsummer
2022-01-10 18:00 | 2022-01-10 19:00 | Winter | TRUE | nonsummer
2022-01-10 19:00 | 2022-01-10 20:00 | Winter | TRUE | nonsummer
2022-01-10 20:00 | 2022-01-10 21:00 | Winter | TRUE | nonsummer
2022-01-10 21:00 | 2022-01-10 22:00 | Winter | FALSE | nonsummer
2022-01-10 22:00 | 2022-01-10 23:00 | Winter | FALSE | nonsummer
2022-01-10 23:00 | 2022-01-11 | Winter | FALSE | nonsummer
2022-01-11 | 2022-01-11 01:00 | Winter | FALSE | nonsummer
2022-01-11 01:00 | 2022-01-11 02:00 | Winter | FALSE | nonsummer
2022-01-11 02:00 | 2022-01-11 03:00 | Winter | FALSE | nonsummer
2022-01-11 03:00 | 2022-01-11 04:00 | Winter | FALSE | nonsummer
2022-01-11 04:00 | 2022-01-11 05:00 | Winter | FALSE | nonsummer
2022-01-11 05:00 | 2022-01-11 06:00 | Winter | FALSE | nonsummer
2022-01-11 06:00 | 2022-01-11 07:00 | Winter | FALSE | nonsummer
2022-01-11 07:00 | 2022-01-11 08:00 | Winter | FALSE | nonsummer
2022-01-11 08:00 | 2022-01-11 09:00 | Winter | FALSE | nonsummer
2022-01-11 09:00 | 2022-01-11 10:00 | Winter | FALSE | nonsummer
2022-01-11 10:00 | 2022-01-11 11:00 | Winter | FALSE | nonsummer
2022-01-11 11:00 | 2022-01-11 12:00 | Winter | FALSE | nonsummer
2022-01-11 12:00 | 2022-01-11 13:00 | Winter | FALSE | nonsummer
2022-01-11 13:00 | 2022-01-11 14:00 | Winter | FALSE | nonsummer
2022-01-11 14:00 | 2022-01-11 15:00 | Winter | FALSE | nonsummer
2022-01-11 15:00 | 2022-01-11 16:00 | Winter | FALSE | nonsummer
2022-01-11 16:00 | 2022-01-11 17:00 | Winter | TRUE | nonsummer
2022-01-11 17:00 | 2022-01-11 18:00 | Winter | TRUE | nonsummer
2022-01-11 18:00 | 2022-01-11 19:00 | Winter | TRUE | nonsummer
2022-01-11 19:00 | 2022-01-11 20:00 | Winter | TRUE | nonsummer
2022-01-11 20:00 | 2022-01-11 21:00 | Winter | TRUE | nonsummer
2022-01-11 21:00 | 2022-01-11 22:00 | Winter | FALSE | nonsummer
2022-01-11 22:00 | 2022-01-11 23:00 | Winter | FALSE | nonsummer
2022-01-11 23:00 | 2022-01-12 | Winter | FALSE | nonsummer
2022-01-12 | 2022-01-12 01:00 | Winter | FALSE | nonsummer
2022-01-12 01:00 | 2022-01-12 02:00 | Winter | FALSE | nonsummer
2022-01-12 02:00 | 2022-01-12 03:00 | Winter | FALSE | nonsummer
2022-01-12 03:00 | 2022-01-12 04:00 | Winter | FALSE | nonsummer
2022-01-12 04:00 | 2022-01-12 05:00 | Winter | FALSE | nonsummer
2022-01-12 05:00 | 2022-01-12 06:00 | Winter | FALSE | nonsummer
2022-01-12 06:00 | 2022-01-12 07:00 | Winter | FALSE | nonsummer
2022-01-12 07:00 | 2022-01-12 08:00 | Winter | FALSE | nonsummer
2022-01-12 08:00 | 2022-01-12 09:00 | Winter | FALSE | nonsummer
2022-01-12 09:00 | 2022-01-12 10:00 | Winter | FALSE | nonsummer
2022-01-12 10:00 | 2022-01-12 11:00 | Winter | FALSE | nonsummer
2022-01-12 11:00 | 2022-01-12 12:00 | Winter | FALSE | nonsummer
2022-01-12 12:00 | 2022-01-12 13:00 | Winter | FALSE | nonsummer
2022-01-12 13:00 | 2022-01-12 14:00 | Winter | FALSE | nonsummer
2022-01-12 14:00 | 2022-01-12 15:00 | Winter | FALSE | nonsummer
2022-01-12 15:00 | 2022-01-12 16:00 | Winter | FALSE | nonsummer
2022-01-12 16:00 | 2022-01-12 17:00 | Winter | TRUE | nonsummer
2022-01-12 17:00 | 2022-01-12 18:00 | Winter | TRUE | nonsummer
2022-01-12 18:00 | 2022-01-12 19:00 | Winter | TRUE | nonsummer
2022-01-12 19:00 | 2022-01-12 20:00 | Winter | TRUE | nonsummer
2022-01-12 20:00 | 2022-01-12 21:00 | Winter | TRUE | nonsummer
2022-01-12 21:00 | 2022-01-12 22:00 | Winter | FALSE | nonsummer
2022-01-12 22:00 | 2022-01-12 23:00 | Winter | FALSE | nonsummer
2022-01-12 23:00 | 2022-01-13 | Winter | FALSE | nonsummer
2022-01-13 | 2022-01-13 01:00 | Winter | FALSE | nonsummer
2022-01-13 01:00 | 2022-01-13 02:00 | Winter | FALSE | nonsummer
2022-01-13 02:00 | 2022-01-13 03:00 | Winter | FALSE | nonsummer
2022-01-13 03:00 | 2022-01-13 04:00 | Winter | FALSE | nonsummer
2022-01-13 04:00 | 2022-01-13 05:00 | Winter | FALSE | nonsummer
2022-01-13 05:00 | 2022-01-13 06:00 | Winter | FALSE | nonsummer
2022-01-13 06:00 | 2022-01-13 07:00 | Winter | FALSE | nonsummer
2022-01-13 07:00 | 2022-01-13 08:00 | Winter | FALSE | nonsummer
2022-01-13 08:00 | 2022-01-13 09:00 | Winter | FALSE | nonsummer
2022-01-13 09:00 | 2022-01-13 10:00 | Winter | FALSE | nonsummer
2022-01-13 10:00 | 2022-01-13 11:00 | Winter | FALSE | nonsummer
2022-01-13 11:00 | 2022-01-13 12:00 | Winter | FALSE | nonsummer
2022-01-13 12:00 | 2022-01-13 13:00 | Winter | FALSE | nonsummer
2022-01-13 13:00 | 2022-01-13 14:00 | Winter | FALSE | nonsummer
2022-01-13 14:00 | 2022-01-13 15:00 | Winter | FALSE | nonsummer
2022-01-13 15:00 | 2022-01-13 16:00 | Winter | FALSE | nonsummer
2022-01-13 16:00 | 2022-01-13 17:00 | Winter | TRUE | nonsummer
2022-01-13 17:00 | 2022-01-13 18:00 | Winter | TRUE | nonsummer
2022-01-13 18:00 | 2022-01-13 19:00 | Winter | TRUE | nonsummer
2022-01-13 19:00 | 2022-01-13 20:00 | Winter | TRUE | nonsummer
2022-01-13 20:00 | 2022-01-13 21:00 | Winter | TRUE | nonsummer
2022-01-13 21:00 | 2022-01-13 22:00 | Winter | FALSE | nonsummer
2022-01-13 22:00 | 2022-01-13 23:00 | Winter | FALSE | nonsummer
2022-01-13 23:00 | 2022-01-14 | Winter | FALSE | nonsummer
2022-01-14 | 2022-01-14 01:00 | Winter | FALSE | nonsummer
2022-01-14 01:00 | 2022-01-14 02:00 | Winter | FALSE | nonsummer
2022-01-14 02:00 | 2022-01-14 03:00 | Winter | FALSE | nonsummer
2022-01-14 03:00 | 2022-01-14 04:00 | Winter | FALSE | nonsummer
2022-01-14 04:00 | 2022-01-14 05:00 | Winter | FALSE | nonsummer
2022-01-14 05:00 | 2022-01-14 06:00 | Winter | FALSE | nonsummer
2022-01-14 06:00 | 2022-01-14 07:00 | Winter | FALSE | nonsummer
2022-01-14 07:00 | 2022-01-14 08:00 | Winter | FALSE | nonsummer
2022-01-14 08:00 | 2022-01-14 09:00 | Winter | FALSE | nonsummer
2022-01-14 09:00 | 2022-01-14 10:00 | Winter | FALSE | nonsummer
2022-01-14 10:00 | 2022-01-14 11:00 | Winter | FALSE | nonsummer
2022-01-14 11:00 | 2022-01-14 12:00 | Winter | FALSE | nonsummer
2022-01-14 12:00 | 2022-01-14 13:00 | Winter | FALSE | nonsummer
2022-01-14 13:00 | 2022-01-14 14:00 | Winter | FALSE | nonsummer
2022-01-14 14:00 | 2022-01-14 15:00 | Winter | FALSE | nonsummer
2022-01-14 15:00 | 2022-01-14 16:00 | Winter | FALSE | nonsummer
2022-01-14 16:00 | 2022-01-14 17:00 | Winter | TRUE | nonsummer
2022-01-14 17:00 | 2022-01-14 18:00 | Winter | TRUE | nonsummer
2022-01-14 18:00 | 2022-01-14 19:00 | Winter | TRUE | nonsummer
2022-01-14 19:00 | 2022-01-14 20:00 | Winter | TRUE | nonsummer
2022-01-14 20:00 | 2022-01-14 21:00 | Winter | TRUE | nonsummer
2022-01-14 21:00 | 2022-01-14 22:00 | Winter | FALSE | nonsummer
2022-01-14 22:00 | 2022-01-14 23:00 | Winter | FALSE | nonsummer
2022-01-14 23:00 | 2022-01-15 | Winter | FALSE | nonsummer
2022-01-15 | 2022-01-15 01:00 | Winter | FALSE | nonsummer
2022-01-15 01:00 | 2022-01-15 02:00 | Winter | FALSE | nonsummer
2022-01-15 02:00 | 2022-01-15 03:00 | Winter | FALSE | nonsummer
2022-01-15 03:00 | 2022-01-15 04:00 | Winter | FALSE | nonsummer
2022-01-15 04:00 | 2022-01-15 05:00 | Winter | FALSE | nonsummer
2022-01-15 05:00 | 2022-01-15 06:00 | Winter | FALSE | nonsummer
2022-01-15 06:00 | 2022-01-15 07:00 | Winter | FALSE | nonsummer
2022-01-15 07:00 | 2022-01-15 08:00 | Winter | FALSE | nonsummer
2022-01-15 08:00 | 2022-01-15 09:00 | Winter | FALSE | nonsummer
2022-01-15 09:00 | 2022-01-15 10:00 | Winter | FALSE | nonsummer
2022-01-15 10:00 | 2022-01-15 11:00 | Winter | FALSE | nonsummer
2022-01-15 11:00 | 2022-01-15 12:00 | Winter | FALSE | nonsummer
2022-01-15 12:00 | 2022-01-15 13:00 | Winter | FALSE | nonsummer
2022-01-15 13:00 | 2022-01-15 14:00 | Winter | FALSE | nonsummer
2022-01-15 14:00 | 2022-01-15 15:00 | Winter | FALSE | nonsummer
2022-01-15 15:00 | 2022-01-15 16:00 | Winter | FALSE | nonsummer
2022-01-15 16:00 | 2022-01-15 17:00 | Winter | TRUE | nonsummer
2022-01-15 17:00 | 2022-01-15 18:00 | Winter | TRUE | nonsummer
2022-01-15 18:00 | 2022-01-15 19:00 | Winter | TRUE | nonsummer
2022-01-15 19:00 | 2022-01-15 20:00 | Winter | TRUE | nonsummer
2022-01-15 20:00 | 2022-01-15 21:00 | Winter | TRUE | nonsummer
2022-01-15 21:00 | 2022-01-15 22:00 | Winter | FALSE | nonsummer
2022-01-15 22:00 | 2022-01-15 23:00 | Winter | FALSE | nonsummer
2022-01-15 23:00 | 2022-01-16 | Winter | FALSE | nonsummer
2022-01-16 | 2022-01-16 01:00 | Winter | FALSE | nonsummer
2022-01-16 01:00 | 2022-01-16 02:00 | Winter | FALSE | nonsummer
2022-01-16 02:00 | 2022-01-16 03:00 | Winter | FALSE | nonsummer
2022-01-16 03:00 | 2022-01-16 04:00 | Winter | FALSE | nonsummer
2022-01-16 04:00 | 2022-01-16 05:00 | Winter | FALSE | nonsummer
2022-01-16 05:00 | 2022-01-16 06:00 | Winter | FALSE | nonsummer
2022-01-16 06:00 | 2022-01-16 07:00 | Winter | FALSE | nonsummer
2022-01-16 07:00 | 2022-01-16 08:00 | Winter | FALSE | nonsummer
2022-01-16 08:00 | 2022-01-16 09:00 | Winter | FALSE | nonsummer
2022-01-16 09:00 | 2022-01-16 10:00 | Winter | FALSE | nonsummer
2022-01-16 10:00 | 2022-01-16 11:00 | Winter | FALSE | nonsummer
2022-01-16 11:00 | 2022-01-16 12:00 | Winter | FALSE | nonsummer
2022-01-16 12:00 | 2022-01-16 13:00 | Winter | FALSE | nonsummer
2022-01-16 13:00 | 2022-01-16 14:00 | Winter | FALSE | nonsummer
2022-01-16 14:00 | 2022-01-16 15:00 | Winter | FALSE | nonsummer
2022-01-16 15:00 | 2022-01-16 16:00 | Winter | FALSE | nonsummer
2022-01-16 16:00 | 2022-01-16 17:00 | Winter | TRUE | nonsummer
2022-01-16 17:00 | 2022-01-16 18:00 | Winter | TRUE | nonsummer
2022-01-16 18:00 | 2022-01-16 19:00 | Winter | TRUE | nonsummer
2022-01-16 19:00 | 2022-01-16 20:00 | Winter | TRUE | nonsummer
2022-01-16 20:00 | 2022-01-16 21:00 | Winter | TRUE | nonsummer
2022-01-16 21:00 | 2022-01-16 22:00 | Winter | FALSE | nonsummer
2022-01-16 22:00 | 2022-01-16 23:00 | Winter | FALSE | nonsummer
2022-01-16 23:00 | 2022-01-17 | Winter | FALSE | nonsummer
2022-01-17 | 2022-01-17 01:00 | Winter | FALSE | nonsummer
2022-01-17 01:00 | 2022-01-17 02:00 | Winter | FALSE | nonsummer
2022-01-17 02:00 | 2022-01-17 03:00 | Winter | FALSE | nonsummer
2022-01-17 03:00 | 2022-01-17 04:00 | Winter | FALSE | nonsummer
2022-01-17 04:00 | 2022-01-17 05:00 | Winter | FALSE | nonsummer
2022-01-17 05:00 | 2022-01-17 06:00 | Winter | FALSE | nonsummer
2022-01-17 06:00 | 2022-01-17 07:00 | Winter | FALSE | nonsummer
2022-01-17 07:00 | 2022-01-17 08:00 | Winter | FALSE | nonsummer
2022-01-17 08:00 | 2022-01-17 09:00 | Winter | FALSE | nonsummer
2022-01-17 09:00 | 2022-01-17 10:00 | Winter | FALSE | nonsummer
2022-01-17 10:00 | 2022-01-17 11:00 | Winter | FALSE | nonsummer
2022-01-17 11:00 | 2022-01-17 12:00 | Winter | FALSE | nonsummer
2022-01-17 12:00 | 2022-01-17 13:00 | Winter | FALSE | nonsummer
2022-01-17 13:00 | 2022-01-17 14:00 | Winter | FALSE | nonsummer
2022-01-17 14:00 | 2022-01-17 15:00 | Winter | FALSE | nonsummer
2022-01-17 15:00 | 2022-01-17 16:00 | Winter | FALSE | nonsummer
2022-01-17 16:00 | 2022-01-17 17:00 | Winter | TRUE | nonsummer
2022-01-17 17:00 | 2022-01-17 18:00 | Winter | TRUE | nonsummer
2022-01-17 18:00 | 2022-01-17 19:00 | Winter | TRUE | nonsummer
2022-01-17 19:00 | 2022-01-17 20:00 | Winter | TRUE | nonsummer
2022-01-17 20:00 | 2022-01-17 21:00 | Winter | TRUE | nonsummer
2022-01-17 21:00 | 2022-01-17 22:00 | Winter | FALSE | nonsummer
2022-01-17 22:00 | 2022-01-17 23:00 | Winter | FALSE | nonsummer
2022-01-17 23:00 | 2022-01-18 | Winter | FALSE | nonsummer
2022-01-18 | 2022-01-18 01:00 | Winter | FALSE | nonsummer
2022-01-18 01:00 | 2022-01-18 02:00 | Winter | FALSE | nonsummer
2022-01-18 02:00 | 2022-01-18 03:00 | Winter | FALSE | nonsummer
2022-01-18 03:00 | 2022-01-18 04:00 | Winter | FALSE | nonsummer
2022-01-18 04:00 | 2022-01-18 05:00 | Winter | FALSE | nonsummer
2022-01-18 05:00 | 2022-01-18 06:00 | Winter | FALSE | nonsummer
2022-01-18 06:00 | 2022-01-18 07:00 | Winter | FALSE | nonsummer
2022-01-18 07:00 | 2022-01-18 08:00 | Winter | FALSE | nonsummer
2022-01-18 08:00 | 2022-01-18 09:00 | Winter | FALSE | nonsummer
2022-01-18 09:00 | 2022-01-18 10:00 | Winter | FALSE | nonsummer
2022-01-18 10:00 | 2022-01-18 11:00 | Winter | FALSE | nonsummer
2022-01-18 11:00 | 2022-01-18 12:00 | Winter | FALSE | nonsummer
2022-01-18 12:00 | 2022-01-18 13:00 | Winter | FALSE | nonsummer
2022-01-18 13:00 | 2022-01-18 14:00 | Winter | FALSE | nonsummer
2022-01-18 14:00 | 2022-01-18 15:00 | Winter | FALSE | nonsummer
2022-01-18 15:00 | 2022-01-18 16:00 | Winter | FALSE | nonsummer
2022-01-18 16:00 | 2022-01-18 17:00 | Winter | TRUE | nonsummer
2022-01-18 17:00 | 2022-01-18 18:00 | Winter | TRUE | nonsummer
2022-01-18 18:00 | 2022-01-18 19:00 | Winter | TRUE | nonsummer
2022-01-18 19:00 | 2022-01-18 20:00 | Winter | TRUE | nonsummer
2022-01-18 20:00 | 2022-01-18 21:00 | Winter | TRUE | nonsummer
2022-01-18 21:00 | 2022-01-18 22:00 | Winter | FALSE | nonsummer
2022-01-18 22:00 | 2022-01-18 23:00 | Winter | FALSE | nonsummer
2022-01-18 23:00 | 2022-01-19 | Winter | FALSE | nonsummer
2022-01-19 | 2022-01-19 01:00 | Winter | FALSE | nonsummer
2022-01-19 01:00 | 2022-01-19 02:00 | Winter | FALSE | nonsummer
2022-01-19 02:00 | 2022-01-19 03:00 | Winter | FALSE | nonsummer
2022-01-19 03:00 | 2022-01-19 04:00 | Winter | FALSE | nonsummer
2022-01-19 04:00 | 2022-01-19 05:00 | Winter | FALSE | nonsummer
2022-01-19 05:00 | 2022-01-19 06:00 | Winter | FALSE | nonsummer
2022-01-19 06:00 | 2022-01-19 07:00 | Winter | FALSE | nonsummer
2022-01-19 07:00 | 2022-01-19 08:00 | Winter | FALSE | nonsummer
2022-01-19 08:00 | 2022-01-19 09:00 | Winter | FALSE | nonsummer
2022-01-19 09:00 | 2022-01-19 10:00 | Winter | FALSE | nonsummer
2022-01-19 10:00 | 2022-01-19 11:00 | Winter | FALSE | nonsummer
2022-01-19 11:00 | 2022-01-19 12:00 | Winter | FALSE | nonsummer
2022-01-19 12:00 | 2022-01-19 13:00 | Winter | FALSE | nonsummer
2022-01-19 13:00 | 2022-01-19 14:00 | Winter | FALSE | nonsummer
2022-01-19 14:00 | 2022-01-19 15:00 | Winter | FALSE | nonsummer
2022-01-19 15:00 | 2022-01-19 16:00 | Winter | FALSE | nonsummer
2022-01-19 16:00 | 2022-01-19 17:00 | Winter | TRUE | nonsummer
2022-01-19 17:00 | 2022-01-19 18:00 | Winter | TRUE | nonsummer
2022-01-19 18:00 | 2022-01-19 19:00 | Winter | TRUE | nonsummer
2022-01-19 19:00 | 2022-01-19 20:00 | Winter | TRUE | nonsummer
2022-01-19 20:00 | 2022-01-19 21:00 | Winter | TRUE | nonsummer
2022-01-19 21:00 | 2022-01-19 22:00 | Winter | FALSE | nonsummer
2022-01-19 22:00 | 2022-01-19 23:00 | Winter | FALSE | nonsummer
2022-01-19 23:00 | 2022-01-20 | Winter | FALSE | nonsummer
2022-01-20 | 2022-01-20 01:00 | Winter | FALSE | nonsummer
2022-01-20 01:00 | 2022-01-20 02:00 | Winter | FALSE | nonsummer
2022-01-20 02:00 | 2022-01-20 03:00 | Winter | FALSE | nonsummer
2022-01-20 03:00 | 2022-01-20 04:00 | Winter | FALSE | nonsummer
2022-01-20 04:00 | 2022-01-20 05:00 | Winter | FALSE | nonsummer
2022-01-20 05:00 | 2022-01-20 06:00 | Winter | FALSE | nonsummer
2022-01-20 06:00 | 2022-01-20 07:00 | Winter | FALSE | nonsummer
2022-01-20 07:00 | 2022-01-20 08:00 | Winter | FALSE | nonsummer
2022-01-20 08:00 | 2022-01-20 09:00 | Winter | FALSE | nonsummer
2022-01-20 09:00 | 2022-01-20 10:00 | Winter | FALSE | nonsummer
2022-01-20 10:00 | 2022-01-20 11:00 | Winter | FALSE | nonsummer
2022-01-20 11:00 | 2022-01-20 12:00 | Winter | FALSE | nonsummer
2022-01-20 12:00 | 2022-01-20 13:00 | Winter | FALSE | nonsummer
2022-01-20 13:00 | 2022-01-20 14:00 | Winter | FALSE | nonsummer
2022-01-20 14:00 | 2022-01-20 15:00 | Winter | FALSE | nonsummer
2022-01-20 15:00 | 2022-01-20 16:00 | Winter | FALSE | nonsummer
2022-01-20 16:00 | 2022-01-20 17:00 | Winter | TRUE | nonsummer
2022-01-20 17:00 | 2022-01-20 18:00 | Winter | TRUE | nonsummer
2022-01-20 18:00 | 2022-01-20 19:00 | Winter | TRUE | nonsummer
2022-01-20 19:00 | 2022-01-20 20:00 | Winter | TRUE | nonsummer
2022-01-20 20:00 | 2022-01-20 21:00 | Winter | TRUE | nonsummer
2022-01-20 21:00 | 2022-01-20 22:00 | Winter | FALSE | nonsummer
2022-01-20 22:00 | 2022-01-20 23:00 | Winter | FALSE | nonsummer
2022-01-20 23:00 | 2022-01-21 | Winter | FALSE | nonsummer
2022-01-21 | 2022-01-21 01:00 | Winter | FALSE | nonsummer
2022-01-21 01:00 | 2022-01-21 02:00 | Winter | FALSE | nonsummer
2022-01-21 02:00 | 2022-01-21 03:00 | Winter | FALSE | nonsummer
2022-01-21 03:00 | 2022-01-21 04:00 | Winter | FALSE | nonsummer
2022-01-21 04:00 | 2022-01-21 05:00 | Winter | FALSE | nonsummer
2022-01-21 05:00 | 2022-01-21 06:00 | Winter | FALSE | nonsummer
2022-01-21 06:00 | 2022-01-21 07:00 | Winter | FALSE | nonsummer
2022-01-21 07:00 | 2022-01-21 08:00 | Winter | FALSE | nonsummer
2022-01-21 08:00 | 2022-01-21 09:00 | Winter | FALSE | nonsummer
2022-01-21 09:00 | 2022-01-21 10:00 | Winter | FALSE | nonsummer
2022-01-21 10:00 | 2022-01-21 11:00 | Winter | FALSE | nonsummer
2022-01-21 11:00 | 2022-01-21 12:00 | Winter | FALSE | nonsummer
2022-01-21 12:00 | 2022-01-21 13:00 | Winter | FALSE | nonsummer
2022-01-21 13:00 | 2022-01-21 14:00 | Winter | FALSE | nonsummer
2022-01-21 14:00 | 2022-01-21 15:00 | Winter | FALSE | nonsummer
2022-01-21 15:00 | 2022-01-21 16:00 | Winter | FALSE | nonsummer
2022-01-21 16:00 | 2022-01-21 17:00 | Winter | TRUE | nonsummer
2022-01-21 17:00 | 2022-01-21 18:00 | Winter | TRUE | nonsummer
2022-01-21 18:00 | 2022-01-21 19:00 | Winter | TRUE | nonsummer
2022-01-21 19:00 | 2022-01-21 20:00 | Winter | TRUE | nonsummer
2022-01-21 20:00 | 2022-01-21 21:00 | Winter | TRUE | nonsummer
2022-01-21 21:00 | 2022-01-21 22:00 | Winter | FALSE | nonsummer
2022-01-21 22:00 | 2022-01-21 23:00 | Winter | FALSE | nonsummer
2022-01-21 23:00 | 2022-01-22 | Winter | FALSE | nonsummer
2022-01-22 | 2022-01-22 01:00 | Winter | FALSE | nonsummer
2022-01-22 01:00 | 2022-01-22 02:00 | Winter | FALSE | nonsummer
2022-01-22 02:00 | 2022-01-22 03:00 | Winter | FALSE | nonsummer
2022-01-22 03:00 | 2022-01-22 04:00 | Winter | FALSE | nonsummer
2022-01-22 04:00 | 2022-01-22 05:00 | Winter | FALSE | nonsummer
2022-01-22 05:00 | 2022-01-22 06:00 | Winter | FALSE | nonsummer
2022-01-22 06:00 | 2022-01-22 07:00 | Winter | FALSE | nonsummer
2022-01-22 07:00 | 2022-01-22 08:00 | Winter | FALSE | nonsummer
2022-01-22 08:00 | 2022-01-22 09:00 | Winter | FALSE | nonsummer
2022-01-22 09:00 | 2022-01-22 10:00 | Winter | FALSE | nonsummer
2022-01-22 10:00 | 2022-01-22 11:00 | Winter | FALSE | nonsummer
2022-01-22 11:00 | 2022-01-22 12:00 | Winter | FALSE | nonsummer
2022-01-22 12:00 | 2022-01-22 13:00 | Winter | FALSE | nonsummer
2022-01-22 13:00 | 2022-01-22 14:00 | Winter | FALSE | nonsummer
2022-01-22 14:00 | 2022-01-22 15:00 | Winter | FALSE | nonsummer
2022-01-22 15:00 | 2022-01-22 16:00 | Winter | FALSE | nonsummer
2022-01-22 16:00 | 2022-01-22 17:00 | Winter | TRUE | nonsummer
2022-01-22 17:00 | 2022-01-22 18:00 | Winter | TRUE | nonsummer
2022-01-22 18:00 | 2022-01-22 19:00 | Winter | TRUE | nonsummer
2022-01-22 19:00 | 2022-01-22 20:00 | Winter | TRUE | nonsummer
2022-01-22 20:00 | 2022-01-22 21:00 | Winter | TRUE | nonsummer
2022-01-22 21:00 | 2022-01-22 22:00 | Winter | FALSE | nonsummer
2022-01-22 22:00 | 2022-01-22 23:00 | Winter | FALSE | nonsummer
2022-01-22 23:00 | 2022-01-23 | Winter | FALSE | nonsummer
2022-01-23 | 2022-01-23 01:00 | Winter | FALSE | nonsummer
2022-01-23 01:00 | 2022-01-23 02:00 | Winter | FALSE | nonsummer
2022-01-23 02:00 | 2022-01-23 03:00 | Winter | FALSE | nonsummer
2022-01-23 03:00 | 2022-01-23 04:00 | Winter | FALSE | nonsummer
2022-01-23 04:00 | 2022-01-23 05:00 | Winter | FALSE | nonsummer
2022-01-23 05:00 | 2022-01-23 06:00 | Winter | FALSE | nonsummer
2022-01-23 06:00 | 2022-01-23 07:00 | Winter | FALSE | nonsummer
2022-01-23 07:00 | 2022-01-23 08:00 | Winter | FALSE | nonsummer
2022-01-23 08:00 | 2022-01-23 09:00 | Winter | FALSE | nonsummer
2022-01-23 09:00 | 2022-01-23 10:00 | Winter | FALSE | nonsummer
2022-01-23 10:00 | 2022-01-23 11:00 | Winter | FALSE | nonsummer
2022-01-23 11:00 | 2022-01-23 12:00 | Winter | FALSE | nonsummer
2022-01-23 12:00 | 2022-01-23 13:00 | Winter | FALSE | nonsummer
2022-01-23 13:00 | 2022-01-23 14:00 | Winter | FALSE | nonsummer
2022-01-23 14:00 | 2022-01-23 15:00 | Winter | FALSE | nonsummer
2022-01-23 15:00 | 2022-01-23 16:00 | Winter | FALSE | nonsummer
2022-01-23 16:00 | 2022-01-23 17:00 | Winter | TRUE | nonsummer
2022-01-23 17:00 | 2022-01-23 18:00 | Winter | TRUE | nonsummer
2022-01-23 18:00 | 2022-01-23 19:00 | Winter | TRUE | nonsummer
2022-01-23 19:00 | 2022-01-23 20:00 | Winter | TRUE | nonsummer
2022-01-23 20:00 | 2022-01-23 21:00 | Winter | TRUE | nonsummer
2022-01-23 21:00 | 2022-01-23 22:00 | Winter | FALSE | nonsummer
2022-01-23 22:00 | 2022-01-23 23:00 | Winter | FALSE | nonsummer
2022-01-23 23:00 | 2022-01-24 | Winter | FALSE | nonsummer
2022-01-24 | 2022-01-24 01:00 | Winter | FALSE | nonsummer
2022-01-24 01:00 | 2022-01-24 02:00 | Winter | FALSE | nonsummer
2022-01-24 02:00 | 2022-01-24 03:00 | Winter | FALSE | nonsummer
2022-01-24 03:00 | 2022-01-24 04:00 | Winter | FALSE | nonsummer
2022-01-24 04:00 | 2022-01-24 05:00 | Winter | FALSE | nonsummer
2022-01-24 05:00 | 2022-01-24 06:00 | Winter | FALSE | nonsummer
2022-01-24 06:00 | 2022-01-24 07:00 | Winter | FALSE | nonsummer
2022-01-24 07:00 | 2022-01-24 08:00 | Winter | FALSE | nonsummer
2022-01-24 08:00 | 2022-01-24 09:00 | Winter | FALSE | nonsummer
2022-01-24 09:00 | 2022-01-24 10:00 | Winter | FALSE | nonsummer
2022-01-24 10:00 | 2022-01-24 11:00 | Winter | FALSE | nonsummer
2022-01-24 11:00 | 2022-01-24 12:00 | Winter | FALSE | nonsummer
2022-01-24 12:00 | 2022-01-24 13:00 | Winter | FALSE | nonsummer
2022-01-24 13:00 | 2022-01-24 14:00 | Winter | FALSE | nonsummer
2022-01-24 14:00 | 2022-01-24 15:00 | Winter | FALSE | nonsummer
2022-01-24 15:00 | 2022-01-24 16:00 | Winter | FALSE | nonsummer
2022-01-24 16:00 | 2022-01-24 17:00 | Winter | TRUE | nonsummer
2022-01-24 17:00 | 2022-01-24 18:00 | Winter | TRUE | nonsummer
2022-01-24 18:00 | 2022-01-24 19:00 | Winter | TRUE | nonsummer
2022-01-24 19:00 | 2022-01-24 20:00 | Winter | TRUE | nonsummer
2022-01-24 20:00 | 2022-01-24 21:00 | Winter | TRUE | nonsummer
2022-01-24 21:00 | 2022-01-24 22:00 | Winter | FALSE | nonsummer
2022-01-24 22:00 | 2022-01-24 23:00 | Winter | FALSE | nonsummer
2022-01-24 23:00 | 2022-01-25 | Winter | FALSE | nonsummer
2022-01-25 | 2022-01-25 01:00 | Winter | FALSE | nonsummer
2022-01-25 01:00 | 2022-01-25 02:00 | Winter | FALSE | nonsummer
2022-01-25 02:00 | 2022-01-25 03:00 | Winter | FALSE | nonsummer
2022-01-25 03:00 | 2022-01-25 04:00 | Winter | FALSE | nonsummer
2022-01-25 04:00 | 2022-01-25 05:00 | Winter | FALSE | nonsummer
2022-01-25 05:00 | 2022-01-25 06:00 | Winter | FALSE | nonsummer
2022-01-25 06:00 | 2022-01-25 07:00 | Winter | FALSE | nonsummer
2022-01-25 07:00 | 2022-01-25 08:00 | Winter | FALSE | nonsummer
2022-01-25 08:00 | 2022-01-25 09:00 | Winter | FALSE | nonsummer
2022-01-25 09:00 | 2022-01-25 10:00 | Winter | FALSE | nonsummer
2022-01-25 10:00 | 2022-01-25 11:00 | Winter | FALSE | nonsummer
2022-01-25 11:00 | 2022-01-25 12:00 | Winter | FALSE | nonsummer
2022-01-25 12:00 | 2022-01-25 13:00 | Winter | FALSE | nonsummer
2022-01-25 13:00 | 2022-01-25 14:00 | Winter | FALSE | nonsummer
2022-01-25 14:00 | 2022-01-25 15:00 | Winter | FALSE | nonsummer
2022-01-25 15:00 | 2022-01-25 16:00 | Winter | FALSE | nonsummer
2022-01-25 16:00 | 2022-01-25 17:00 | Winter | TRUE | nonsummer
2022-01-25 17:00 | 2022-01-25 18:00 | Winter | TRUE | nonsummer
2022-01-25 18:00 | 2022-01-25 19:00 | Winter | TRUE | nonsummer
2022-01-25 19:00 | 2022-01-25 20:00 | Winter | TRUE | nonsummer
2022-01-25 20:00 | 2022-01-25 21:00 | Winter | TRUE | nonsummer
2022-01-25 21:00 | 2022-01-25 22:00 | Winter | FALSE | nonsummer
2022-01-25 22:00 | 2022-01-25 23:00 | Winter | FALSE | nonsummer
2022-01-25 23:00 | 2022-01-26 | Winter | FALSE | nonsummer
2022-01-26 | 2022-01-26 01:00 | Winter | FALSE | nonsummer
2022-01-26 01:00 | 2022-01-26 02:00 | Winter | FALSE | nonsummer
2022-01-26 02:00 | 2022-01-26 03:00 | Winter | FALSE | nonsummer
2022-01-26 03:00 | 2022-01-26 04:00 | Winter | FALSE | nonsummer
2022-01-26 04:00 | 2022-01-26 05:00 | Winter | FALSE | nonsummer
2022-01-26 05:00 | 2022-01-26 06:00 | Winter | FALSE | nonsummer
2022-01-26 06:00 | 2022-01-26 07:00 | Winter | FALSE | nonsummer
2022-01-26 07:00 | 2022-01-26 08:00 | Winter | FALSE | nonsummer
2022-01-26 08:00 | 2022-01-26 09:00 | Winter | FALSE | nonsummer
2022-01-26 09:00 | 2022-01-26 10:00 | Winter | FALSE | nonsummer
2022-01-26 10:00 | 2022-01-26 11:00 | Winter | FALSE | nonsummer
2022-01-26 11:00 | 2022-01-26 12:00 | Winter | FALSE | nonsummer
2022-01-26 12:00 | 2022-01-26 13:00 | Winter | FALSE | nonsummer
2022-01-26 13:00 | 2022-01-26 14:00 | Winter | FALSE | nonsummer
2022-01-26 14:00 | 2022-01-26 15:00 | Winter | FALSE | nonsummer
2022-01-26 15:00 | 2022-01-26 16:00 | Winter | FALSE | nonsummer
2022-01-26 16:00 | 2022-01-26 17:00 | Winter | TRUE | nonsummer
2022-01-26 17:00 | 2022-01-26 18:00 | Winter | TRUE | nonsummer
2022-01-26 18:00 | 2022-01-26 19:00 | Winter | TRUE | nonsummer
2022-01-26 19:00 | 2022-01-26 20:00 | Winter | TRUE | nonsummer
2022-01-26 20:00 | 2022-01-26 21:00 | Winter | TRUE | nonsummer
2022-01-26 21:00 | 2022-01-26 22:00 | Winter | FALSE | nonsummer
2022-01-26 22:00 | 2022-01-26 23:00 | Winter | FALSE | nonsummer
2022-01-26 23:00 | 2022-01-27 | Winter | FALSE | nonsummer
2022-01-27 | 2022-01-27 01:00 | Winter | FALSE | nonsummer
2022-01-27 01:00 | 2022-01-27 02:00 | Winter | FALSE | nonsummer
2022-01-27 02:00 | 2022-01-27 03:00 | Winter | FALSE | nonsummer
2022-01-27 03:00 | 2022-01-27 04:00 | Winter | FALSE | nonsummer
2022-01-27 04:00 | 2022-01-27 05:00 | Winter | FALSE | nonsummer
2022-01-27 05:00 | 2022-01-27 06:00 | Winter | FALSE | nonsummer
2022-01-27 06:00 | 2022-01-27 07:00 | Winter | FALSE | nonsummer
2022-01-27 07:00 | 2022-01-27 08:00 | Winter | FALSE | nonsummer
2022-01-27 08:00 | 2022-01-27 09:00 | Winter | FALSE | nonsummer
2022-01-27 09:00 | 2022-01-27 10:00 | Winter | FALSE | nonsummer
2022-01-27 10:00 | 2022-01-27 11:00 | Winter | FALSE | nonsummer
2022-01-27 11:00 | 2022-01-27 12:00 | Winter | FALSE | nonsummer
2022-01-27 12:00 | 2022-01-27 13:00 | Winter | FALSE | nonsummer
2022-01-27 13:00 | 2022-01-27 14:00 | Winter | FALSE | nonsummer
2022-01-27 14:00 | 2022-01-27 15:00 | Winter | FALSE | nonsummer
2022-01-27 15:00 | 2022-01-27 16:00 | Winter | FALSE | nonsummer
2022-01-27 16:00 | 2022-01-27 17:00 | Winter | TRUE | nonsummer
2022-01-27 17:00 | 2022-01-27 18:00 | Winter | TRUE | nonsummer
2022-01-27 18:00 | 2022-01-27 19:00 | Winter | TRUE | nonsummer
2022-01-27 19:00 | 2022-01-27 20:00 | Winter | TRUE | nonsummer
2022-01-27 20:00 | 2022-01-27 21:00 | Winter | TRUE | nonsummer
2022-01-27 21:00 | 2022-01-27 22:00 | Winter | FALSE | nonsummer
2022-01-27 22:00 | 2022-01-27 23:00 | Winter | FALSE | nonsummer
2022-01-27 23:00 | 2022-01-28 | Winter | FALSE | nonsummer
2022-01-28 | 2022-01-28 01:00 | Winter | FALSE | nonsummer
2022-01-28 01:00 | 2022-01-28 02:00 | Winter | FALSE | nonsummer
2022-01-28 02:00 | 2022-01-28 03:00 | Winter | FALSE | nonsummer
2022-01-28 03:00 | 2022-01-28 04:00 | Winter | FALSE | nonsummer
2022-01-28 04:00 | 2022-01-28 05:00 | Winter | FALSE | nonsummer
2022-01-28 05:00 | 2022-01-28 06:00 | Winter | FALSE | nonsummer
2022-01-28 06:00 | 2022-01-28 07:00 | Winter | FALSE | nonsummer
2022-01-28 07:00 | 2022-01-28 08:00 | Winter | FALSE | nonsummer
2022-01-28 08:00 | 2022-01-28 09:00 | Winter | FALSE | nonsummer
2022-01-28 09:00 | 2022-01-28 10:00 | Winter | FALSE | nonsummer
2022-01-28 10:00 | 2022-01-28 11:00 | Winter | FALSE | nonsummer
2022-01-28 11:00 | 2022-01-28 12:00 | Winter | FALSE | nonsummer
2022-01-28 12:00 | 2022-01-28 13:00 | Winter | FALSE | nonsummer
2022-01-28 13:00 | 2022-01-28 14:00 | Winter | FALSE | nonsummer
2022-01-28 14:00 | 2022-01-28 15:00 | Winter | FALSE | nonsummer
2022-01-28 15:00 | 2022-01-28 16:00 | Winter | FALSE | nonsummer
2022-01-28 16:00 | 2022-01-28 17:00 | Winter | TRUE | nonsummer
2022-01-28 17:00 | 2022-01-28 18:00 | Winter | TRUE | nonsummer
2022-01-28 18:00 | 2022-01-28 19:00 | Winter | TRUE | nonsummer
2022-01-28 19:00 | 2022-01-28 20:00 | Winter | TRUE | nonsummer
2022-01-28 20:00 | 2022-01-28 21:00 | Winter | TRUE | nonsummer
2022-01-28 21:00 | 2022-01-28 22:00 | Winter | FALSE | nonsummer
2022-01-28 22:00 | 2022-01-28 23:00 | Winter | FALSE | nonsummer
2022-01-28 23:00 | 2022-01-29 | Winter | FALSE | nonsummer
2022-01-29 | 2022-01-29 01:00 | Winter | FALSE | nonsummer
2022-01-29 01:00 | 2022-01-29 02:00 | Winter | FALSE | nonsummer
2022-01-29 02:00 | 2022-01-29 03:00 | Winter | FALSE | nonsummer
2022-01-29 03:00 | 2022-01-29 04:00 | Winter | FALSE | nonsummer
2022-01-29 04:00 | 2022-01-29 05:00 | Winter | FALSE | nonsummer
2022-01-29 05:00 | 2022-01-29 06:00 | Winter | FALSE | nonsummer
2022-01-29 06:00 | 2022-01-29 07:00 | Winter | FALSE | nonsummer
2022-01-29 07:00 | 2022-01-29 08:00 | Winter | FALSE | nonsummer
2022-01-29 08:00 | 2022-01-29 09:00 | Winter | FALSE | nonsummer
2022-01-29 09:00 | 2022-01-29 10:00 | Winter | FALSE | nonsummer
2022-01-29 10:00 | 2022-01-29 11:00 | Winter | FALSE | nonsummer
2022-01-29 11:00 | 2022-01-29 12:00 | Winter | FALSE | nonsummer
2022-01-29 12:00 | 2022-01-29 13:00 | Winter | FALSE | nonsummer
2022-01-29 13:00 | 2022-01-29 14:00 | Winter | FALSE | nonsummer
2022-01-29 14:00 | 2022-01-29 15:00 | Winter | FALSE | nonsummer
2022-01-29 15:00 | 2022-01-29 16:00 | Winter | FALSE | nonsummer
2022-01-29 16:00 | 2022-01-29 17:00 | Winter | TRUE | nonsummer
2022-01-29 17:00 | 2022-01-29 18:00 | Winter | TRUE | nonsummer
2022-01-29 18:00 | 2022-01-29 19:00 | Winter | TRUE | nonsummer
2022-01-29 19:00 | 2022-01-29 20:00 | Winter | TRUE | nonsummer
2022-01-29 20:00 | 2022-01-29 21:00 | Winter | TRUE | nonsummer
2022-01-29 21:00 | 2022-01-29 22:00 | Winter | FALSE | nonsummer
2022-01-29 22:00 | 2022-01-29 23:00 | Winter | FALSE | nonsummer
2022-01-29 23:00 | 2022-01-30 | Winter | FALSE | nonsummer
2022-01-30 | 2022-01-30 01:00 | Winter | FALSE | nonsummer
2022-01-30 01:00 | 2022-01-30 02:00 | Winter | FALSE | nonsummer
2022-01-30 02:00 | 2022-01-30 03:00 | Winter | FALSE | nonsummer
2022-01-30 03:00 | 2022-01-30 04:00 | Winter | FALSE | nonsummer
2022-01-30 04:00 | 2022-01-30 05:00 | Winter | FALSE | nonsummer
2022-01-30 05:00 | 2022-01-30 06:00 | Winter | FALSE | nonsummer
2022-01-30 06:00 | 2022-01-30 07:00 | Winter | FALSE | nonsummer
2022-01-30 07:00 | 2022-01-30 08:00 | Winter | FALSE | nonsummer
2022-01-30 08:00 | 2022-01-30 09:00 | Winter | FALSE | nonsummer
2022-01-30 09:00 | 2022-01-30 10:00 | Winter | FALSE | nonsummer
2022-01-30 10:00 | 2022-01-30 11:00 | Winter | FALSE | nonsummer
2022-01-30 11:00 | 2022-01-30 12:00 | Winter | FALSE | nonsummer
2022-01-30 12:00 | 2022-01-30 13:00 | Winter | FALSE | nonsummer
2022-01-30 13:00 | 2022-01-30 14:00 | Winter | FALSE | nonsummer
2022-01-30 14:00 | 2022-01-30 15:00 | Winter | FALSE | nonsummer
2022-01-30 15:00 | 2022-01-30 16:00 | Winter | FALSE | nonsummer
2022-01-30 16:00 | 2022-01-30 17:00 | Winter | TRUE | nonsummer
2022-01-30 17:00 | 2022-01-30 18:00 | Winter | TRUE | nonsummer
2022-01-30 18:00 | 2022-01-30 19:00 | Winter | TRUE | nonsummer
2022-01-30 19:00 | 2022-01-30 20:00 | Winter | TRUE | nonsummer
2022-01-30 20:00 | 2022-01-30 21:00 | Winter | TRUE | nonsummer
2022-01-30 21:00 | 2022-01-30 22:00 | Winter | FALSE | nonsummer
2022-01-30 22:00 | 2022-01-30 23:00 | Winter | FALSE | nonsummer
2022-01-30 23:00 | 2022-01-31 | Winter | FALSE | nonsummer
2022-01-31 | 2022-01-31 01:00 | Winter | FALSE | nonsummer
2022-01-31 01:00 | 2022-01-31 02:00 | Winter | FALSE | nonsummer
2022-01-31 02:00 | 2022-01-31 03:00 | Winter | FALSE | nonsummer
2022-01-31 03:00 | 2022-01-31 04:00 | Winter | FALSE | nonsummer
2022-01-31 04:00 | 2022-01-31 05:00 | Winter | FALSE | nonsummer
2022-01-31 05:00 | 2022-01-31 06:00 | Winter | FALSE | nonsummer
2022-01-31 06:00 | 2022-01-31 07:00 | Winter | FALSE | nonsummer
2022-01-31 07:00 | 2022-01-31 08:00 | Winter | FALSE | nonsummer
2022-01-31 08:00 | 2022-01-31 09:00 | Winter | FALSE | nonsummer
2022-01-31 09:00 | 2022-01-31 10:00 | Winter | FALSE | nonsummer
2022-01-31 10:00 | 2022-01-31 11:00 | Winter | FALSE | nonsummer
2022-01-31 11:00 | 2022-01-31 12:00 | Winter | FALSE | nonsummer
2022-01-31 12:00 | 2022-01-31 13:00 | Winter | FALSE | nonsummer
2022-01-31 13:00 | 2022-01-31 14:00 | Winter | FALSE | nonsummer
2022-01-31 14:00 | 2022-01-31 15:00 | Winter | FALSE | nonsummer
2022-01-31 15:00 | 2022-01-31 16:00 | Winter | FALSE | nonsummer
2022-01-31 16:00 | 2022-01-31 17:00 | Winter | TRUE | nonsummer
2022-01-31 17:00 | 2022-01-31 18:00 | Winter | TRUE | nonsummer
2022-01-31 18:00 | 2022-01-31 19:00 | Winter | TRUE | nonsummer
2022-01-31 19:00 | 2022-01-31 20:00 | Winter | TRUE | nonsummer
2022-01-31 20:00 | 2022-01-31 21:00 | Winter | TRUE | nonsummer
2022-01-31 21:00 | 2022-01-31 22:00 | Winter | FALSE | nonsummer
2022-01-31 22:00 | 2022-01-31 23:00 | Winter | FALSE | nonsummer
2022-01-31 23:00 | 2022-02-01 | Winter | FALSE | nonsummer
2022-02-01 | 2022-02-01 01:00 | Winter | FALSE | nonsummer
2022-02-01 01:00 | 2022-02-01 02:00 | Winter | FALSE | nonsummer
2022-02-01 02:00 | 2022-02-01 03:00 | Winter | FALSE | nonsummer
2022-02-01 03:00 | 2022-02-01 04:00 | Winter | FALSE | nonsummer
2022-02-01 04:00 | 2022-02-01 05:00 | Winter | FALSE | nonsummer
2022-02-01 05:00 | 2022-02-01 06:00 | Winter | FALSE | nonsummer
2022-02-01 06:00 | 2022-02-01 07:00 | Winter | FALSE | nonsummer
2022-02-01 07:00 | 2022-02-01 08:00 | Winter | FALSE | nonsummer
2022-02-01 08:00 | 2022-02-01 09:00 | Winter | FALSE | nonsummer
2022-02-01 09:00 | 2022-02-01 10:00 | Winter | FALSE | nonsummer
2022-02-01 10:00 | 2022-02-01 11:00 | Winter | FALSE | nonsummer
2022-02-01 11:00 | 2022-02-01 12:00 | Winter | FALSE | nonsummer
2022-02-01 12:00 | 2022-02-01 13:00 | Winter | FALSE | nonsummer
2022-02-01 13:00 | 2022-02-01 14:00 | Winter | FALSE | nonsummer
2022-02-01 14:00 | 2022-02-01 15:00 | Winter | FALSE | nonsummer
2022-02-01 15:00 | 2022-02-01 16:00 | Winter | FALSE | nonsummer
2022-02-01 16:00 | 2022-02-01 17:00 | Winter | TRUE | nonsummer
2022-02-01 17:00 | 2022-02-01 18:00 | Winter | TRUE | nonsummer
2022-02-01 18:00 | 2022-02-01 19:00 | Winter | TRUE | nonsummer
2022-02-01 19:00 | 2022-02-01 20:00 | Winter | TRUE | nonsummer
2022-02-01 20:00 | 2022-02-01 21:00 | Winter | TRUE | nonsummer
2022-02-01 21:00 | 2022-02-01 22:00 | Winter | FALSE | nonsummer
2022-02-01 22:00 | 2022-02-01 23:00 | Winter | FALSE | nonsummer
2022-02-01 23:00 | 2022-02-02 | Winter | FALSE | nonsummer
2022-02-02 | 2022-02-02 01:00 | Winter | FALSE | nonsummer
2022-02-02 01:00 | 2022-02-02 02:00 | Winter | FALSE | nonsummer
2022-02-02 02:00 | 2022-02-02 03:00 | Winter | FALSE | nonsummer
2022-02-02 03:00 | 2022-02-02 04:00 | Winter | FALSE | nonsummer
2022-02-02 04:00 | 2022-02-02 05:00 | Winter | FALSE | nonsummer
2022-02-02 05:00 | 2022-02-02 06:00 | Winter | FALSE | nonsummer
2022-02-02 06:00 | 2022-02-02 07:00 | Winter | FALSE | nonsummer
2022-02-02 07:00 | 2022-02-02 08:00 | Winter | FALSE | nonsummer
2022-02-02 08:00 | 2022-02-02 09:00 | Winter | FALSE | nonsummer
2022-02-02 09:00 | 2022-02-02 10:00 | Winter | FALSE | nonsummer
2022-02-02 10:00 | 2022-02-02 11:00 | Winter | FALSE | nonsummer
2022-02-02 11:00 | 2022-02-02 12:00 | Winter | FALSE | nonsummer
2022-02-02 12:00 | 2022-02-02 13:00 | Winter | FALSE | nonsummer
2022-02-02 13:00 | 2022-02-02 14:00 | Winter | FALSE | nonsummer
2022-02-02 14:00 | 2022-02-02 15:00 | Winter | FALSE | nonsummer
2022-02-02 15:00 | 2022-02-02 16:00 | Winter | FALSE | nonsummer
2022-02-02 16:00 | 2022-02-02 17:00 | Winter | TRUE | nonsummer
2022-02-02 17:00 | 2022-02-02 18:00 | Winter | TRUE | nonsummer
2022-02-02 18:00 | 2022-02-02 19:00 | Winter | TRUE | nonsummer
2022-02-02 19:00 | 2022-02-02 20:00 | Winter | TRUE | nonsummer
2022-02-02 20:00 | 2022-02-02 21:00 | Winter | TRUE | nonsummer
2022-02-02 21:00 | 2022-02-02 22:00 | Winter | FALSE | nonsummer
2022-02-02 22:00 | 2022-02-02 23:00 | Winter | FALSE | nonsummer
2022-02-02 23:00 | 2022-02-03 | Winter | FALSE | nonsummer
2022-02-03 | 2022-02-03 01:00 | Winter | FALSE | nonsummer
2022-02-03 01:00 | 2022-02-03 02:00 | Winter | FALSE | nonsummer
2022-02-03 02:00 | 2022-02-03 03:00 | Winter | FALSE | nonsummer
2022-02-03 03:00 | 2022-02-03 04:00 | Winter | FALSE | nonsummer
2022-02-03 04:00 | 2022-02-03 05:00 | Winter | FALSE | nonsummer
2022-02-03 05:00 | 2022-02-03 06:00 | Winter | FALSE | nonsummer
2022-02-03 06:00 | 2022-02-03 07:00 | Winter | FALSE | nonsummer
2022-02-03 07:00 | 2022-02-03 08:00 | Winter | FALSE | nonsummer
2022-02-03 08:00 | 2022-02-03 09:00 | Winter | FALSE | nonsummer
2022-02-03 09:00 | 2022-02-03 10:00 | Winter | FALSE | nonsummer
2022-02-03 10:00 | 2022-02-03 11:00 | Winter | FALSE | nonsummer
2022-02-03 11:00 | 2022-02-03 12:00 | Winter | FALSE | nonsummer
2022-02-03 12:00 | 2022-02-03 13:00 | Winter | FALSE | nonsummer
2022-02-03 13:00 | 2022-02-03 14:00 | Winter | FALSE | nonsummer
2022-02-03 14:00 | 2022-02-03 15:00 | Winter | FALSE | nonsummer
2022-02-03 15:00 | 2022-02-03 16:00 | Winter | FALSE | nonsummer
2022-02-03 16:00 | 2022-02-03 17:00 | Winter | TRUE | nonsummer
2022-02-03 17:00 | 2022-02-03 18:00 | Winter | TRUE | nonsummer
2022-02-03 18:00 | 2022-02-03 19:00 | Winter | TRUE | nonsummer
2022-02-03 19:00 | 2022-02-03 20:00 | Winter | TRUE | nonsummer
2022-02-03 20:00 | 2022-02-03 21:00 | Winter | TRUE | nonsummer
2022-02-03 21:00 | 2022-02-03 22:00 | Winter | FALSE | nonsummer
2022-02-03 22:00 | 2022-02-03 23:00 | Winter | FALSE | nonsummer
2022-02-03 23:00 | 2022-02-04 | Winter | FALSE | nonsummer
2022-02-04 | 2022-02-04 01:00 | Winter | FALSE | nonsummer
2022-02-04 01:00 | 2022-02-04 02:00 | Winter | FALSE | nonsummer
2022-02-04 02:00 | 2022-02-04 03:00 | Winter | FALSE | nonsummer
2022-02-04 03:00 | 2022-02-04 04:00 | Winter | FALSE | nonsummer
2022-02-04 04:00 | 2022-02-04 05:00 | Winter | FALSE | nonsummer
2022-02-04 05:00 | 2022-02-04 06:00 | Winter | FALSE | nonsummer
2022-02-04 06:00 | 2022-02-04 07:00 | Winter | FALSE | nonsummer
2022-02-04 07:00 | 2022-02-04 08:00 | Winter | FALSE | nonsummer
2022-02-04 08:00 | 2022-02-04 09:00 | Winter | FALSE | nonsummer
2022-02-04 09:00 | 2022-02-04 10:00 | Winter | FALSE | nonsummer
2022-02-04 10:00 | 2022-02-04 11:00 | Winter | FALSE | nonsummer
2022-02-04 11:00 | 2022-02-04 12:00 | Winter | FALSE | nonsummer
2022-02-04 12:00 | 2022-02-04 13:00 | Winter | FALSE | nonsummer
2022-02-04 13:00 | 2022-02-04 14:00 | Winter | FALSE | nonsummer
2022-02-04 14:00 | 2022-02-04 15:00 | Winter | FALSE | nonsummer
2022-02-04 15:00 | 2022-02-04 16:00 | Winter | FALSE | nonsummer
2022-02-04 16:00 | 2022-02-04 17:00 | Winter | TRUE | nonsummer
2022-02-04 17:00 | 2022-02-04 18:00 | Winter | TRUE | nonsummer
2022-02-04 18:00 | 2022-02-04 19:00 | Winter | TRUE | nonsummer
2022-02-04 19:00 | 2022-02-04 20:00 | Winter | TRUE | nonsummer
2022-02-04 20:00 | 2022-02-04 21:00 | Winter | TRUE | nonsummer
2022-02-04 21:00 | 2022-02-04 22:00 | Winter | FALSE | nonsummer
2022-02-04 22:00 | 2022-02-04 23:00 | Winter | FALSE | nonsummer
2022-02-04 23:00 | 2022-02-05 | Winter | FALSE | nonsummer
2022-02-05 | 2022-02-05 01:00 | Winter | FALSE | nonsummer
2022-02-05 01:00 | 2022-02-05 02:00 | Winter | FALSE | nonsummer
2022-02-05 02:00 | 2022-02-05 03:00 | Winter | FALSE | nonsummer
2022-02-05 03:00 | 2022-02-05 04:00 | Winter | FALSE | nonsummer
2022-02-05 04:00 | 2022-02-05 05:00 | Winter | FALSE | nonsummer
2022-02-05 05:00 | 2022-02-05 06:00 | Winter | FALSE | nonsummer
2022-02-05 06:00 | 2022-02-05 07:00 | Winter | FALSE | nonsummer
2022-02-05 07:00 | 2022-02-05 08:00 | Winter | FALSE | nonsummer
2022-02-05 08:00 | 2022-02-05 09:00 | Winter | FALSE | nonsummer
2022-02-05 09:00 | 2022-02-05 10:00 | Winter | FALSE | nonsummer
2022-02-05 10:00 | 2022-02-05 11:00 | Winter | FALSE | nonsummer
2022-02-05 11:00 | 2022-02-05 12:00 | Winter | FALSE | nonsummer
2022-02-05 12:00 | 2022-02-05 13:00 | Winter | FALSE | nonsummer
2022-02-05 13:00 | 2022-02-05 14:00 | Winter | FALSE | nonsummer
2022-02-05 14:00 | 2022-02-05 15:00 | Winter | FALSE | nonsummer
2022-02-05 15:00 | 2022-02-05 16:00 | Winter | FALSE | nonsummer
2022-02-05 16:00 | 2022-02-05 17:00 | Winter | TRUE | nonsummer
2022-02-05 17:00 | 2022-02-05 18:00 | Winter | TRUE | nonsummer
2022-02-05 18:00 | 2022-02-05 19:00 | Winter | TRUE | nonsummer
2022-02-05 19:00 | 2022-02-05 20:00 | Winter | TRUE | nonsummer
2022-02-05 20:00 | 2022-02-05 21:00 | Winter | TRUE | nonsummer
2022-02-05 21:00 | 2022-02-05 22:00 | Winter | FALSE | nonsummer
2022-02-05 22:00 | 2022-02-05 23:00 | Winter | FALSE | nonsummer
2022-02-05 23:00 | 2022-02-06 | Winter | FALSE | nonsummer
2022-02-06 | 2022-02-06 01:00 | Winter | FALSE | nonsummer
2022-02-06 01:00 | 2022-02-06 02:00 | Winter | FALSE | nonsummer
2022-02-06 02:00 | 2022-02-06 03:00 | Winter | FALSE | nonsummer
2022-02-06 03:00 | 2022-02-06 04:00 | Winter | FALSE | nonsummer
2022-02-06 04:00 | 2022-02-06 05:00 | Winter | FALSE | nonsummer
2022-02-06 05:00 | 2022-02-06 06:00 | Winter | FALSE | nonsummer
2022-02-06 06:00 | 2022-02-06 07:00 | Winter | FALSE | nonsummer
2022-02-06 07:00 | 2022-02-06 08:00 | Winter | FALSE | nonsummer
2022-02-06 08:00 | 2022-02-06 09:00 | Winter | FALSE | nonsummer
2022-02-06 09:00 | 2022-02-06 10:00 | Winter | FALSE | nonsummer
2022-02-06 10:00 | 2022-02-06 11:00 | Winter | FALSE | nonsummer
2022-02-06 11:00 | 2022-02-06 12:00 | Winter | FALSE | nonsummer
2022-02-06 12:00 | 2022-02-06 13:00 | Winter | FALSE | nonsummer
2022-02-06 13:00 | 2022-02-06 14:00 | Winter | FALSE | nonsummer
2022-02-06 14:00 | 2022-02-06 15:00 | Winter | FALSE | nonsummer
2022-02-06 15:00 | 2022-02-06 16:00 | Winter | FALSE | nonsummer
2022-02-06 16:00 | 2022-02-06 17:00 | Winter | TRUE | nonsummer
2022-02-06 17:00 | 2022-02-06 18:00 | Winter | TRUE | nonsummer
2022-02-06 18:00 | 2022-02-06 19:00 | Winter | TRUE | nonsummer
2022-02-06 19:00 | 2022-02-06 20:00 | Winter | TRUE | nonsummer
2022-02-06 20:00 | 2022-02-06 21:00 | Winter | TRUE | nonsummer
2022-02-06 21:00 | 2022-02-06 22:00 | Winter | FALSE | nonsummer
2022-02-06 22:00 | 2022-02-06 23:00 | Winter | FALSE | nonsummer
2022-02-06 23:00 | 2022-02-07 | Winter | FALSE | nonsummer
2022-02-07 | 2022-02-07 01:00 | Winter | FALSE | nonsummer
2022-02-07 01:00 | 2022-02-07 02:00 | Winter | FALSE | nonsummer
2022-02-07 02:00 | 2022-02-07 03:00 | Winter | FALSE | nonsummer
2022-02-07 03:00 | 2022-02-07 04:00 | Winter | FALSE | nonsummer
2022-02-07 04:00 | 2022-02-07 05:00 | Winter | FALSE | nonsummer
2022-02-07 05:00 | 2022-02-07 06:00 | Winter | FALSE | nonsummer
2022-02-07 06:00 | 2022-02-07 07:00 | Winter | FALSE | nonsummer
2022-02-07 07:00 | 2022-02-07 08:00 | Winter | FALSE | nonsummer
2022-02-07 08:00 | 2022-02-07 09:00 | Winter | FALSE | nonsummer
2022-02-07 09:00 | 2022-02-07 10:00 | Winter | FALSE | nonsummer
2022-02-07 10:00 | 2022-02-07 11:00 | Winter | FALSE | nonsummer
2022-02-07 11:00 | 2022-02-07 12:00 | Winter | FALSE | nonsummer
2022-02-07 12:00 | 2022-02-07 13:00 | Winter | FALSE | nonsummer
2022-02-07 13:00 | 2022-02-07 14:00 | Winter | FALSE | nonsummer
2022-02-07 14:00 | 2022-02-07 15:00 | Winter | FALSE | nonsummer
2022-02-07 15:00 | 2022-02-07 16:00 | Winter | FALSE | nonsummer
2022-02-07 16:00 | 2022-02-07 17:00 | Winter | TRUE | nonsummer
2022-02-07 17:00 | 2022-02-07 18:00 | Winter | TRUE | nonsummer
2022-02-07 18:00 | 2022-02-07 19:00 | Winter | TRUE | nonsummer
2022-02-07 19:00 | 2022-02-07 20:00 | Winter | TRUE | nonsummer
2022-02-07 20:00 | 2022-02-07 21:00 | Winter | TRUE | nonsummer
2022-02-07 21:00 | 2022-02-07 22:00 | Winter | FALSE | nonsummer
2022-02-07 22:00 | 2022-02-07 23:00 | Winter | FALSE | nonsummer
2022-02-07 23:00 | 2022-02-08 | Winter | FALSE | nonsummer
2022-02-08 | 2022-02-08 01:00 | Winter | FALSE | nonsummer
2022-02-08 01:00 | 2022-02-08 02:00 | Winter | FALSE | nonsummer
2022-02-08 02:00 | 2022-02-08 03:00 | Winter | FALSE | nonsummer
2022-02-08 03:00 | 2022-02-08 04:00 | Winter | FALSE | nonsummer
2022-02-08 04:00 | 2022-02-08 05:00 | Winter | FALSE | nonsummer
2022-02-08 05:00 | 2022-02-08 06:00 | Winter | FALSE | nonsummer
2022-02-08 06:00 | 2022-02-08 07:00 | Winter | FALSE | nonsummer
2022-02-08 07:00 | 2022-02-08 08:00 | Winter | FALSE | nonsummer
2022-02-08 08:00 | 2022-02-08 09:00 | Winter | FALSE | nonsummer
2022-02-08 09:00 | 2022-02-08 10:00 | Winter | FALSE | nonsummer
2022-02-08 10:00 | 2022-02-08 11:00 | Winter | FALSE | nonsummer
2022-02-08 11:00 | 2022-02-08 12:00 | Winter | FALSE | nonsummer
2022-02-08 12:00 | 2022-02-08 13:00 | Winter | FALSE | nonsummer
2022-02-08 13:00 | 2022-02-08 14:00 | Winter | FALSE | nonsummer
2022-02-08 14:00 | 2022-02-08 15:00 | Winter | FALSE | nonsummer
2022-02-08 15:00 | 2022-02-08 16:00 | Winter | FALSE | nonsummer
2022-02-08 16:00 | 2022-02-08 17:00 | Winter | TRUE | nonsummer
2022-02-08 17:00 | 2022-02-08 18:00 | Winter | TRUE | nonsummer
2022-02-08 18:00 | 2022-02-08 19:00 | Winter | TRUE | nonsummer
2022-02-08 19:00 | 2022-02-08 20:00 | Winter | TRUE | nonsummer
2022-02-08 20:00 | 2022-02-08 21:00 | Winter | TRUE | nonsummer
2022-02-08 21:00 | 2022-02-08 22:00 | Winter | FALSE | nonsummer
2022-02-08 22:00 | 2022-02-08 23:00 | Winter | FALSE | nonsummer
2022-02-08 23:00 | 2022-02-09 | Winter | FALSE | nonsummer
2022-02-09 | 2022-02-09 01:00 | Winter | FALSE | nonsummer
2022-02-09 01:00 | 2022-02-09 02:00 | Winter | FALSE | nonsummer
2022-02-09 02:00 | 2022-02-09 03:00 | Winter | FALSE | nonsummer
2022-02-09 03:00 | 2022-02-09 04:00 | Winter | FALSE | nonsummer
2022-02-09 04:00 | 2022-02-09 05:00 | Winter | FALSE | nonsummer
2022-02-09 05:00 | 2022-02-09 06:00 | Winter | FALSE | nonsummer
2022-02-09 06:00 | 2022-02-09 07:00 | Winter | FALSE | nonsummer
2022-02-09 07:00 | 2022-02-09 08:00 | Winter | FALSE | nonsummer
2022-02-09 08:00 | 2022-02-09 09:00 | Winter | FALSE | nonsummer
2022-02-09 09:00 | 2022-02-09 10:00 | Winter | FALSE | nonsummer
2022-02-09 10:00 | 2022-02-09 11:00 | Winter | FALSE | nonsummer
2022-02-09 11:00 | 2022-02-09 12:00 | Winter | FALSE | nonsummer
2022-02-09 12:00 | 2022-02-09 13:00 | Winter | FALSE | nonsummer
2022-02-09 13:00 | 2022-02-09 14:00 | Winter | FALSE | nonsummer
2022-02-09 14:00 | 2022-02-09 15:00 | Winter | FALSE | nonsummer
2022-02-09 15:00 | 2022-02-09 16:00 | Winter | FALSE | nonsummer
2022-02-09 16:00 | 2022-02-09 17:00 | Winter | TRUE | nonsummer
2022-02-09 17:00 | 2022-02-09 18:00 | Winter | TRUE | nonsummer
2022-02-09 18:00 | 2022-02-09 19:00 | Winter | TRUE | nonsummer
2022-02-09 19:00 | 2022-02-09 20:00 | Winter | TRUE | nonsummer
2022-02-09 20:00 | 2022-02-09 21:00 | Winter | TRUE | nonsummer
2022-02-09 21:00 | 2022-02-09 22:00 | Winter | FALSE | nonsummer
2022-02-09 22:00 | 2022-02-09 23:00 | Winter | FALSE | nonsummer
2022-02-09 23:00 | 2022-02-10 | Winter | FALSE | nonsummer
2022-02-10 | 2022-02-10 01:00 | Winter | FALSE | nonsummer
2022-02-10 01:00 | 2022-02-10 02:00 | Winter | FALSE | nonsummer
2022-02-10 02:00 | 2022-02-10 03:00 | Winter | FALSE | nonsummer
2022-02-10 03:00 | 2022-02-10 04:00 | Winter | FALSE | nonsummer
2022-02-10 04:00 | 2022-02-10 05:00 | Winter | FALSE | nonsummer
2022-02-10 05:00 | 2022-02-10 06:00 | Winter | FALSE | nonsummer
2022-02-10 06:00 | 2022-02-10 07:00 | Winter | FALSE | nonsummer
2022-02-10 07:00 | 2022-02-10 08:00 | Winter | FALSE | nonsummer
2022-02-10 08:00 | 2022-02-10 09:00 | Winter | FALSE | nonsummer
2022-02-10 09:00 | 2022-02-10 10:00 | Winter | FALSE | nonsummer
2022-02-10 10:00 | 2022-02-10 11:00 | Winter | FALSE | nonsummer
2022-02-10 11:00 | 2022-02-10 12:00 | Winter | FALSE | nonsummer
2022-02-10 12:00 | 2022-02-10 13:00 | Winter | FALSE | nonsummer
2022-02-10 13:00 | 2022-02-10 14:00 | Winter | FALSE | nonsummer
2022-02-10 14:00 | 2022-02-10 15:00 | Winter | FALSE | nonsummer
2022-02-10 15:00 | 2022-02-10 16:00 | Winter | FALSE | nonsummer
2022-02-10 16:00 | 2022-02-10 17:00 | Winter | TRUE | nonsummer
2022-02-10 17:00 | 2022-02-10 18:00 | Winter | TRUE | nonsummer
2022-02-10 18:00 | 2022-02-10 19:00 | Winter | TRUE | nonsummer
2022-02-10 19:00 | 2022-02-10 20:00 | Winter | TRUE | nonsummer
2022-02-10 20:00 | 2022-02-10 21:00 | Winter | TRUE | nonsummer
2022-02-10 21:00 | 2022-02-10 22:00 | Winter | FALSE | nonsummer
2022-02-10 22:00 | 2022-02-10 23:00 | Winter | FALSE | nonsummer
2022-02-10 23:00 | 2022-02-11 | Winter | FALSE | nonsummer
2022-02-11 | 2022-02-11 01:00 | Winter | FALSE | nonsummer
2022-02-11 01:00 | 2022-02-11 02:00 | Winter | FALSE | nonsummer
2022-02-11 02:00 | 2022-02-11 03:00 | Winter | FALSE | nonsummer
2022-02-11 03:00 | 2022-02-11 04:00 | Winter | FALSE | nonsummer
2022-02-11 04:00 | 2022-02-11 05:00 | Winter | FALSE | nonsummer
2022-02-11 05:00 | 2022-02-11 06:00 | Winter | FALSE | nonsummer
2022-02-11 06:00 | 2022-02-11 07:00 | Winter | FALSE | nonsummer
2022-02-11 07:00 | 2022-02-11 08:00 | Winter | FALSE | nonsummer
2022-02-11 08:00 | 2022-02-11 09:00 | Winter | FALSE | nonsummer
2022-02-11 09:00 | 2022-02-11 10:00 | Winter | FALSE | nonsummer
2022-02-11 10:00 | 2022-02-11 11:00 | Winter | FALSE | nonsummer
2022-02-11 11:00 | 2022-02-11 12:00 | Winter | FALSE | nonsummer
2022-02-11 12:00 | 2022-02-11 13:00 | Winter | FALSE | nonsummer
2022-02-11 13:00 | 2022-02-11 14:00 | Winter | FALSE | nonsummer
2022-02-11 14:00 | 2022-02-11 15:00 | Winter | FALSE | nonsummer
2022-02-11 15:00 | 2022-02-11 16:00 | Winter | FALSE | nonsummer
2022-02-11 16:00 | 2022-02-11 17:00 | Winter | TRUE | nonsummer
2022-02-11 17:00 | 2022-02-11 18:00 | Winter | TRUE | nonsummer
2022-02-11 18:00 | 2022-02-11 19:00 | Winter | TRUE | nonsummer
2022-02-11 19:00 | 2022-02-11 20:00 | Winter | TRUE | nonsummer
2022-02-11 20:00 | 2022-02-11 21:00 | Winter | TRUE | nonsummer
2022-02-11 21:00 | 2022-02-11 22:00 | Winter | FALSE | nonsummer
2022-02-11 22:00 | 2022-02-11 23:00 | Winter | FALSE | nonsummer
2022-02-11 23:00 | 2022-02-12 | Winter | FALSE | nonsummer
2022-02-12 | 2022-02-12 01:00 | Winter | FALSE | nonsummer
2022-02-12 01:00 | 2022-02-12 02:00 | Winter | FALSE | nonsummer
2022-02-12 02:00 | 2022-02-12 03:00 | Winter | FALSE | nonsummer
2022-02-12 03:00 | 2022-02-12 04:00 | Winter | FALSE | nonsummer
2022-02-12 04:00 | 2022-02-12 05:00 | Winter | FALSE | nonsummer
2022-02-12 05:00 | 2022-02-12 06:00 | Winter | FALSE | nonsummer
2022-02-12 06:00 | 2022-02-12 07:00 | Winter | FALSE | nonsummer
2022-02-12 07:00 | 2022-02-12 08:00 | Winter | FALSE | nonsummer
2022-02-12 08:00 | 2022-02-12 09:00 | Winter | FALSE | nonsummer
2022-02-12 09:00 | 2022-02-12 10:00 | Winter | FALSE | nonsummer
2022-02-12 10:00 | 2022-02-12 11:00 | Winter | FALSE | nonsummer
2022-02-12 11:00 | 2022-02-12 12:00 | Winter | FALSE | nonsummer
2022-02-12 12:00 | 2022-02-12 13:00 | Winter | FALSE | nonsummer
2022-02-12 13:00 | 2022-02-12 14:00 | Winter | FALSE | nonsummer
2022-02-12 14:00 | 2022-02-12 15:00 | Winter | FALSE | nonsummer
2022-02-12 15:00 | 2022-02-12 16:00 | Winter | FALSE | nonsummer
2022-02-12 16:00 | 2022-02-12 17:00 | Winter | TRUE | nonsummer
2022-02-12 17:00 | 2022-02-12 18:00 | Winter | TRUE | nonsummer
2022-02-12 18:00 | 2022-02-12 19:00 | Winter | TRUE | nonsummer
2022-02-12 19:00 | 2022-02-12 20:00 | Winter | TRUE | nonsummer
2022-02-12 20:00 | 2022-02-12 21:00 | Winter | TRUE | nonsummer
2022-02-12 21:00 | 2022-02-12 22:00 | Winter | FALSE | nonsummer
2022-02-12 22:00 | 2022-02-12 23:00 | Winter | FALSE | nonsummer
2022-02-12 23:00 | 2022-02-13 | Winter | FALSE | nonsummer
2022-02-13 | 2022-02-13 01:00 | Winter | FALSE | nonsummer
2022-02-13 01:00 | 2022-02-13 02:00 | Winter | FALSE | nonsummer
2022-02-13 02:00 | 2022-02-13 03:00 | Winter | FALSE | nonsummer
2022-02-13 03:00 | 2022-02-13 04:00 | Winter | FALSE | nonsummer
2022-02-13 04:00 | 2022-02-13 05:00 | Winter | FALSE | nonsummer
2022-02-13 05:00 | 2022-02-13 06:00 | Winter | FALSE | nonsummer
2022-02-13 06:00 | 2022-02-13 07:00 | Winter | FALSE | nonsummer
2022-02-13 07:00 | 2022-02-13 08:00 | Winter | FALSE | nonsummer
2022-02-13 08:00 | 2022-02-13 09:00 | Winter | FALSE | nonsummer
2022-02-13 09:00 | 2022-02-13 10:00 | Winter | FALSE | nonsummer
2022-02-13 10:00 | 2022-02-13 11:00 | Winter | FALSE | nonsummer
2022-02-13 11:00 | 2022-02-13 12:00 | Winter | FALSE | nonsummer
2022-02-13 12:00 | 2022-02-13 13:00 | Winter | FALSE | nonsummer
2022-02-13 13:00 | 2022-02-13 14:00 | Winter | FALSE | nonsummer
2022-02-13 14:00 | 2022-02-13 15:00 | Winter | FALSE | nonsummer
2022-02-13 15:00 | 2022-02-13 16:00 | Winter | FALSE | nonsummer
2022-02-13 16:00 | 2022-02-13 17:00 | Winter | TRUE | nonsummer
2022-02-13 17:00 | 2022-02-13 18:00 | Winter | TRUE | nonsummer
2022-02-13 18:00 | 2022-02-13 19:00 | Winter | TRUE | nonsummer
2022-02-13 19:00 | 2022-02-13 20:00 | Winter | TRUE | nonsummer
2022-02-13 20:00 | 2022-02-13 21:00 | Winter | TRUE | nonsummer
2022-02-13 21:00 | 2022-02-13 22:00 | Winter | FALSE | nonsummer
2022-02-13 22:00 | 2022-02-13 23:00 | Winter | FALSE | nonsummer
2022-02-13 23:00 | 2022-02-14 | Winter | FALSE | nonsummer
2022-02-14 | 2022-02-14 01:00 | Winter | FALSE | nonsummer
2022-02-14 01:00 | 2022-02-14 02:00 | Winter | FALSE | nonsummer
2022-02-14 02:00 | 2022-02-14 03:00 | Winter | FALSE | nonsummer
2022-02-14 03:00 | 2022-02-14 04:00 | Winter | FALSE | nonsummer
2022-02-14 04:00 | 2022-02-14 05:00 | Winter | FALSE | nonsummer
2022-02-14 05:00 | 2022-02-14 06:00 | Winter | FALSE | nonsummer
2022-02-14 06:00 | 2022-02-14 07:00 | Winter | FALSE | nonsummer
2022-02-14 07:00 | 2022-02-14 08:00 | Winter | FALSE | nonsummer
2022-02-14 08:00 | 2022-02-14 09:00 | Winter | FALSE | nonsummer
2022-02-14 09:00 | 2022-02-14 10:00 | Winter | FALSE | nonsummer
2022-02-14 10:00 | 2022-02-14 11:00 | Winter | FALSE | nonsummer
2022-02-14 11:00 | 2022-02-14 12:00 | Winter | FALSE | nonsummer
2022-02-14 12:00 | 2022-02-14 13:00 | Winter | FALSE | nonsummer
2022-02-14 13:00 | 2022-02-14 14:00 | Winter | FALSE | nonsummer
2022-02-14 14:00 | 2022-02-14 15:00 | Winter | FALSE | nonsummer
2022-02-14 15:00 | 2022-02-14 16:00 | Winter | FALSE | nonsummer
2022-02-14 16:00 | 2022-02-14 17:00 | Winter | TRUE | nonsummer
2022-02-14 17:00 | 2022-02-14 18:00 | Winter | TRUE | nonsummer
2022-02-14 18:00 | 2022-02-14 19:00 | Winter | TRUE | nonsummer
2022-02-14 19:00 | 2022-02-14 20:00 | Winter | TRUE | nonsummer
2022-02-14 20:00 | 2022-02-14 21:00 | Winter | TRUE | nonsummer
2022-02-14 21:00 | 2022-02-14 22:00 | Winter | FALSE | nonsummer
2022-02-14 22:00 | 2022-02-14 23:00 | Winter | FALSE | nonsummer
2022-02-14 23:00 | 2022-02-15 | Winter | FALSE | nonsummer
2022-02-15 | 2022-02-15 01:00 | Winter | FALSE | nonsummer
2022-02-15 01:00 | 2022-02-15 02:00 | Winter | FALSE | nonsummer
2022-02-15 02:00 | 2022-02-15 03:00 | Winter | FALSE | nonsummer
2022-02-15 03:00 | 2022-02-15 04:00 | Winter | FALSE | nonsummer
2022-02-15 04:00 | 2022-02-15 05:00 | Winter | FALSE | nonsummer
2022-02-15 05:00 | 2022-02-15 06:00 | Winter | FALSE | nonsummer
2022-02-15 06:00 | 2022-02-15 07:00 | Winter | FALSE | nonsummer
2022-02-15 07:00 | 2022-02-15 08:00 | Winter | FALSE | nonsummer
2022-02-15 08:00 | 2022-02-15 09:00 | Winter | FALSE | nonsummer
2022-02-15 09:00 | 2022-02-15 10:00 | Winter | FALSE | nonsummer
2022-02-15 10:00 | 2022-02-15 11:00 | Winter | FALSE | nonsummer
2022-02-15 11:00 | 2022-02-15 12:00 | Winter | FALSE | nonsummer
2022-02-15 12:00 | 2022-02-15 13:00 | Winter | FALSE | nonsummer
2022-02-15 13:00 | 2022-02-15 14:00 | Winter | FALSE | nonsummer
2022-02-15 14:00 | 2022-02-15 15:00 | Winter | FALSE | nonsummer
2022-02-15 15:00 | 2022-02-15 16:00 | Winter | FALSE | nonsummer
2022-02-15 16:00 | 2022-02-15 17:00 | Winter | TRUE | nonsummer
2022-02-15 17:00 | 2022-02-15 18:00 | Winter | TRUE | nonsummer
2022-02-15 18:00 | 2022-02-15 19:00 | Winter | TRUE | nonsummer
2022-02-15 19:00 | 2022-02-15 20:00 | Winter | TRUE | nonsummer
2022-02-15 20:00 | 2022-02-15 21:00 | Winter | TRUE | nonsummer
2022-02-15 21:00 | 2022-02-15 22:00 | Winter | FALSE | nonsummer
2022-02-15 22:00 | 2022-02-15 23:00 | Winter | FALSE | nonsummer
2022-02-15 23:00 | 2022-02-16 | Winter | FALSE | nonsummer
2022-02-16 | 2022-02-16 01:00 | Winter | FALSE | nonsummer
2022-02-16 01:00 | 2022-02-16 02:00 | Winter | FALSE | nonsummer
2022-02-16 02:00 | 2022-02-16 03:00 | Winter | FALSE | nonsummer
2022-02-16 03:00 | 2022-02-16 04:00 | Winter | FALSE | nonsummer
2022-02-16 04:00 | 2022-02-16 05:00 | Winter | FALSE | nonsummer
2022-02-16 05:00 | 2022-02-16 06:00 | Winter | FALSE | nonsummer
2022-02-16 06:00 | 2022-02-16 07:00 | Winter | FALSE | nonsummer
2022-02-16 07:00 | 2022-02-16 08:00 | Winter | FALSE | nonsummer
2022-02-16 08:00 | 2022-02-16 09:00 | Winter | FALSE | nonsummer
2022-02-16 09:00 | 2022-02-16 10:00 | Winter | FALSE | nonsummer
2022-02-16 10:00 | 2022-02-16 11:00 | Winter | FALSE | nonsummer
2022-02-16 11:00 | 2022-02-16 12:00 | Winter | FALSE | nonsummer
2022-02-16 12:00 | 2022-02-16 13:00 | Winter | FALSE | nonsummer
2022-02-16 13:00 | 2022-02-16 14:00 | Winter | FALSE | nonsummer
2022-02-16 14:00 | 2022-02-16 15:00 | Winter | FALSE | nonsummer
2022-02-16 15:00 | 2022-02-16 16:00 | Winter | FALSE | nonsummer
2022-02-16 16:00 | 2022-02-16 17:00 | Winter | TRUE | nonsummer
2022-02-16 17:00 | 2022-02-16 18:00 | Winter | TRUE | nonsummer
2022-02-16 18:00 | 2022-02-16 19:00 | Winter | TRUE | nonsummer
2022-02-16 19:00 | 2022-02-16 20:00 | Winter | TRUE | nonsummer
2022-02-16 20:00 | 2022-02-16 21:00 | Winter | TRUE | nonsummer
2022-02-16 21:00 | 2022-02-16 22:00 | Winter | FALSE | nonsummer
2022-02-16 22:00 | 2022-02-16 23:00 | Winter | FALSE | nonsummer
2022-02-16 23:00 | 2022-02-17 | Winter | FALSE | nonsummer
2022-02-17 | 2022-02-17 01:00 | Winter | FALSE | nonsummer
2022-02-17 01:00 | 2022-02-17 02:00 | Winter | FALSE | nonsummer
2022-02-17 02:00 | 2022-02-17 03:00 | Winter | FALSE | nonsummer
2022-02-17 03:00 | 2022-02-17 04:00 | Winter | FALSE | nonsummer
2022-02-17 04:00 | 2022-02-17 05:00 | Winter | FALSE | nonsummer
2022-02-17 05:00 | 2022-02-17 06:00 | Winter | FALSE | nonsummer
2022-02-17 06:00 | 2022-02-17 07:00 | Winter | FALSE | nonsummer
2022-02-17 07:00 | 2022-02-17 08:00 | Winter | FALSE | nonsummer
2022-02-17 08:00 | 2022-02-17 09:00 | Winter | FALSE | nonsummer
2022-02-17 09:00 | 2022-02-17 10:00 | Winter | FALSE | nonsummer
2022-02-17 10:00 | 2022-02-17 11:00 | Winter | FALSE | nonsummer
2022-02-17 11:00 | 2022-02-17 12:00 | Winter | FALSE | nonsummer
2022-02-17 12:00 | 2022-02-17 13:00 | Winter | FALSE | nonsummer
2022-02-17 13:00 | 2022-02-17 14:00 | Winter | FALSE | nonsummer
2022-02-17 14:00 | 2022-02-17 15:00 | Winter | FALSE | nonsummer
2022-02-17 15:00 | 2022-02-17 16:00 | Winter | FALSE | nonsummer
2022-02-17 16:00 | 2022-02-17 17:00 | Winter | TRUE | nonsummer
2022-02-17 17:00 | 2022-02-17 18:00 | Winter | TRUE | nonsummer
2022-02-17 18:00 | 2022-02-17 19:00 | Winter | TRUE | nonsummer
2022-02-17 19:00 | 2022-02-17 20:00 | Winter | TRUE | nonsummer
2022-02-17 20:00 | 2022-02-17 21:00 | Winter | TRUE | nonsummer
2022-02-17 21:00 | 2022-02-17 22:00 | Winter | FALSE | nonsummer
2022-02-17 22:00 | 2022-02-17 23:00 | Winter | FALSE | nonsummer
2022-02-17 23:00 | 2022-02-18 | Winter | FALSE | nonsummer
2022-02-18 | 2022-02-18 01:00 | Winter | FALSE | nonsummer
2022-02-18 01:00 | 2022-02-18 02:00 | Winter | FALSE | nonsummer
2022-02-18 02:00 | 2022-02-18 03:00 | Winter | FALSE | nonsummer
2022-02-18 03:00 | 2022-02-18 04:00 | Winter | FALSE | nonsummer
2022-02-18 04:00 | 2022-02-18 05:00 | Winter | FALSE | nonsummer
2022-02-18 05:00 | 2022-02-18 06:00 | Winter | FALSE | nonsummer
2022-02-18 06:00 | 2022-02-18 07:00 | Winter | FALSE | nonsummer
2022-02-18 07:00 | 2022-02-18 08:00 | Winter | FALSE | nonsummer
2022-02-18 08:00 | 2022-02-18 09:00 | Winter | FALSE | nonsummer
2022-02-18 09:00 | 2022-02-18 10:00 | Winter | FALSE | nonsummer
2022-02-18 10:00 | 2022-02-18 11:00 | Winter | FALSE | nonsummer
2022-02-18 11:00 | 2022-02-18 12:00 | Winter | FALSE | nonsummer
2022-02-18 12:00 | 2022-02-18 13:00 | Winter | FALSE | nonsummer
2022-02-18 13:00 | 2022-02-18 14:00 | Winter | FALSE | nonsummer
2022-02-18 14:00 | 2022-02-18 15:00 | Winter | FALSE | nonsummer
2022-02-18 15:00 | 2022-02-18 16:00 | Winter | FALSE | nonsummer
2022-02-18 16:00 | 2022-02-18 17:00 | Winter | TRUE | nonsummer
2022-02-18 17:00 | 2022-02-18 18:00 | Winter | TRUE | nonsummer
2022-02-18 18:00 | 2022-02-18 19:00 | Winter | TRUE | nonsummer
2022-02-18 19:00 | 2022-02-18 20:00 | Winter | TRUE | nonsummer
2022-02-18 20:00 | 2022-02-18 21:00 | Winter | TRUE | nonsummer
2022-02-18 21:00 | 2022-02-18 22:00 | Winter | FALSE | nonsummer
2022-02-18 22:00 | 2022-02-18 23:00 | Winter | FALSE | nonsummer
2022-02-18 23:00 | 2022-02-19 | Winter | FALSE | nonsummer
2022-02-19 | 2022-02-19 01:00 | Winter | FALSE | nonsummer
2022-02-19 01:00 | 2022-02-19 02:00 | Winter | FALSE | nonsummer
2022-02-19 02:00 | 2022-02-19 03:00 | Winter | FALSE | nonsummer
2022-02-19 03:00 | 2022-02-19 04:00 | Winter | FALSE | nonsummer
2022-02-19 04:00 | 2022-02-19 05:00 | Winter | FALSE | nonsummer
2022-02-19 05:00 | 2022-02-19 06:00 | Winter | FALSE | nonsummer
2022-02-19 06:00 | 2022-02-19 07:00 | Winter | FALSE | nonsummer
2022-02-19 07:00 | 2022-02-19 08:00 | Winter | FALSE | nonsummer
2022-02-19 08:00 | 2022-02-19 09:00 | Winter | FALSE | nonsummer
2022-02-19 09:00 | 2022-02-19 10:00 | Winter | FALSE | nonsummer
2022-02-19 10:00 | 2022-02-19 11:00 | Winter | FALSE | nonsummer
2022-02-19 11:00 | 2022-02-19 12:00 | Winter | FALSE | nonsummer
2022-02-19 12:00 | 2022-02-19 13:00 | Winter | FALSE | nonsummer
2022-02-19 13:00 | 2022-02-19 14:00 | Winter | FALSE | nonsummer
2022-02-19 14:00 | 2022-02-19 15:00 | Winter | FALSE | nonsummer
2022-02-19 15:00 | 2022-02-19 16:00 | Winter | FALSE | nonsummer
2022-02-19 16:00 | 2022-02-19 17:00 | Winter | TRUE | nonsummer
2022-02-19 17:00 | 2022-02-19 18:00 | Winter | TRUE | nonsummer
2022-02-19 18:00 | 2022-02-19 19:00 | Winter | TRUE | nonsummer
2022-02-19 19:00 | 2022-02-19 20:00 | Winter | TRUE | nonsummer
2022-02-19 20:00 | 2022-02-19 21:00 | Winter | TRUE | nonsummer
2022-02-19 21:00 | 2022-02-19 22:00 | Winter | FALSE | nonsummer
2022-02-19 22:00 | 2022-02-19 23:00 | Winter | FALSE | nonsummer
2022-02-19 23:00 | 2022-02-20 | Winter | FALSE | nonsummer
2022-02-20 | 2022-02-20 01:00 | Winter | FALSE | nonsummer
2022-02-20 01:00 | 2022-02-20 02:00 | Winter | FALSE | nonsummer
2022-02-20 02:00 | 2022-02-20 03:00 | Winter | FALSE | nonsummer
2022-02-20 03:00 | 2022-02-20 04:00 | Winter | FALSE | nonsummer
2022-02-20 04:00 | 2022-02-20 05:00 | Winter | FALSE | nonsummer
2022-02-20 05:00 | 2022-02-20 06:00 | Winter | FALSE | nonsummer
2022-02-20 06:00 | 2022-02-20 07:00 | Winter | FALSE | nonsummer
2022-02-20 07:00 | 2022-02-20 08:00 | Winter | FALSE | nonsummer
2022-02-20 08:00 | 2022-02-20 09:00 | Winter | FALSE | nonsummer
2022-02-20 09:00 | 2022-02-20 10:00 | Winter | FALSE | nonsummer
2022-02-20 10:00 | 2022-02-20 11:00 | Winter | FALSE | nonsummer
2022-02-20 11:00 | 2022-02-20 12:00 | Winter | FALSE | nonsummer
2022-02-20 12:00 | 2022-02-20 13:00 | Winter | FALSE | nonsummer
2022-02-20 13:00 | 2022-02-20 14:00 | Winter | FALSE | nonsummer
2022-02-20 14:00 | 2022-02-20 15:00 | Winter | FALSE | nonsummer
2022-02-20 15:00 | 2022-02-20 16:00 | Winter | FALSE | nonsummer
2022-02-20 16:00 | 2022-02-20 17:00 | Winter | TRUE | nonsummer
2022-02-20 17:00 | 2022-02-20 18:00 | Winter | TRUE | nonsummer
2022-02-20 18:00 | 2022-02-20 19:00 | Winter | TRUE | nonsummer
2022-02-20 19:00 | 2022-02-20 20:00 | Winter | TRUE | nonsummer
2022-02-20 20:00 | 2022-02-20 21:00 | Winter | TRUE | nonsummer
2022-02-20 21:00 | 2022-02-20 22:00 | Winter | FALSE | nonsummer
2022-02-20 22:00 | 2022-02-20 23:00 | Winter | FALSE | nonsummer
2022-02-20 23:00 | 2022-02-21 | Winter | FALSE | nonsummer
2022-02-21 | 2022-02-21 01:00 | Winter | FALSE | nonsummer
2022-02-21 01:00 | 2022-02-21 02:00 | Winter | FALSE | nonsummer
2022-02-21 02:00 | 2022-02-21 03:00 | Winter | FALSE | nonsummer
2022-02-21 03:00 | 2022-02-21 04:00 | Winter | FALSE | nonsummer
2022-02-21 04:00 | 2022-02-21 05:00 | Winter | FALSE | nonsummer
2022-02-21 05:00 | 2022-02-21 06:00 | Winter | FALSE | nonsummer
2022-02-21 06:00 | 2022-02-21 07:00 | Winter | FALSE | nonsummer
2022-02-21 07:00 | 2022-02-21 08:00 | Winter | FALSE | nonsummer
2022-02-21 08:00 | 2022-02-21 09:00 | Winter | FALSE | nonsummer
2022-02-21 09:00 | 2022-02-21 10:00 | Winter | FALSE | nonsummer
2022-02-21 10:00 | 2022-02-21 11:00 | Winter | FALSE | nonsummer
2022-02-21 11:00 | 2022-02-21 12:00 | Winter | FALSE | nonsummer
2022-02-21 12:00 | 2022-02-21 13:00 | Winter | FALSE | nonsummer
2022-02-21 13:00 | 2022-02-21 14:00 | Winter | FALSE | nonsummer
2022-02-21 14:00 | 2022-02-21 15:00 | Winter | FALSE | nonsummer
2022-02-21 15:00 | 2022-02-21 16:00 | Winter | FALSE | nonsummer
2022-02-21 16:00 | 2022-02-21 17:00 | Winter | TRUE | nonsummer
2022-02-21 17:00 | 2022-02-21 18:00 | Winter | TRUE | nonsummer
2022-02-21 18:00 | 2022-02-21 19:00 | Winter | TRUE | nonsummer
2022-02-21 19:00 | 2022-02-21 20:00 | Winter | TRUE | nonsummer
2022-02-21 20:00 | 2022-02-21 21:00 | Winter | TRUE | nonsummer
2022-02-21 21:00 | 2022-02-21 22:00 | Winter | FALSE | nonsummer
2022-02-21 22:00 | 2022-02-21 23:00 | Winter | FALSE | nonsummer
2022-02-21 23:00 | 2022-02-22 | Winter | FALSE | nonsummer
2022-02-22 | 2022-02-22 01:00 | Winter | FALSE | nonsummer
2022-02-22 01:00 | 2022-02-22 02:00 | Winter | FALSE | nonsummer
2022-02-22 02:00 | 2022-02-22 03:00 | Winter | FALSE | nonsummer
2022-02-22 03:00 | 2022-02-22 04:00 | Winter | FALSE | nonsummer
2022-02-22 04:00 | 2022-02-22 05:00 | Winter | FALSE | nonsummer
2022-02-22 05:00 | 2022-02-22 06:00 | Winter | FALSE | nonsummer
2022-02-22 06:00 | 2022-02-22 07:00 | Winter | FALSE | nonsummer
2022-02-22 07:00 | 2022-02-22 08:00 | Winter | FALSE | nonsummer
2022-02-22 08:00 | 2022-02-22 09:00 | Winter | FALSE | nonsummer
2022-02-22 09:00 | 2022-02-22 10:00 | Winter | FALSE | nonsummer
2022-02-22 10:00 | 2022-02-22 11:00 | Winter | FALSE | nonsummer
2022-02-22 11:00 | 2022-02-22 12:00 | Winter | FALSE | nonsummer
2022-02-22 12:00 | 2022-02-22 13:00 | Winter | FALSE | nonsummer
2022-02-22 13:00 | 2022-02-22 14:00 | Winter | FALSE | nonsummer
2022-02-22 14:00 | 2022-02-22 15:00 | Winter | FALSE | nonsummer
2022-02-22 15:00 | 2022-02-22 16:00 | Winter | FALSE | nonsummer
2022-02-22 16:00 | 2022-02-22 17:00 | Winter | TRUE | nonsummer
2022-02-22 17:00 | 2022-02-22 18:00 | Winter | TRUE | nonsummer
2022-02-22 18:00 | 2022-02-22 19:00 | Winter | TRUE | nonsummer
2022-02-22 19:00 | 2022-02-22 20:00 | Winter | TRUE | nonsummer
2022-02-22 20:00 | 2022-02-22 21:00 | Winter | TRUE | nonsummer
2022-02-22 21:00 | 2022-02-22 22:00 | Winter | FALSE | nonsummer
2022-02-22 22:00 | 2022-02-22 23:00 | Winter | FALSE | nonsummer
2022-02-22 23:00 | 2022-02-23 | Winter | FALSE | nonsummer
2022-02-23 | 2022-02-23 01:00 | Winter | FALSE | nonsummer
2022-02-23 01:00 | 2022-02-23 02:00 | Winter | FALSE | nonsummer
2022-02-23 02:00 | 2022-02-23 03:00 | Winter | FALSE | nonsummer
2022-02-23 03:00 | 2022-02-23 04:00 | Winter | FALSE | nonsummer
2022-02-23 04:00 | 2022-02-23 05:00 | Winter | FALSE | nonsummer
2022-02-23 05:00 | 2022-02-23 06:00 | Winter | FALSE | nonsummer
2022-02-23 06:00 | 2022-02-23 07:00 | Winter | FALSE | nonsummer
2022-02-23 07:00 | 2022-02-23 08:00 | Winter | FALSE | nonsummer
2022-02-23 08:00 | 2022-02-23 09:00 | Winter | FALSE | nonsummer
2022-02-23 09:00 | 2022-02-23 10:00 | Winter | FALSE | nonsummer
2022-02-23 10:00 | 2022-02-23 11:00 | Winter | FALSE | nonsummer
2022-02-23 11:00 | 2022-02-23 12:00 | Winter | FALSE | nonsummer
2022-02-23 12:00 | 2022-02-23 13:00 | Winter | FALSE | nonsummer
2022-02-23 13:00 | 2022-02-23 14:00 | Winter | FALSE | nonsummer
2022-02-23 14:00 | 2022-02-23 15:00 | Winter | FALSE | nonsummer
2022-02-23 15:00 | 2022-02-23 16:00 | Winter | FALSE | nonsummer
2022-02-23 16:00 | 2022-02-23 17:00 | Winter | TRUE | nonsummer
2022-02-23 17:00 | 2022-02-23 18:00 | Winter | TRUE | nonsummer
2022-02-23 18:00 | 2022-02-23 19:00 | Winter | TRUE | nonsummer
2022-02-23 19:00 | 2022-02-23 20:00 | Winter | TRUE | nonsummer
2022-02-23 20:00 | 2022-02-23 21:00 | Winter | TRUE | nonsummer
2022-02-23 21:00 | 2022-02-23 22:00 | Winter | FALSE | nonsummer
2022-02-23 22:00 | 2022-02-23 23:00 | Winter | FALSE | nonsummer
2022-02-23 23:00 | 2022-02-24 | Winter | FALSE | nonsummer
2022-02-24 | 2022-02-24 01:00 | Winter | FALSE | nonsummer
2022-02-24 01:00 | 2022-02-24 02:00 | Winter | FALSE | nonsummer
2022-02-24 02:00 | 2022-02-24 03:00 | Winter | FALSE | nonsummer
2022-02-24 03:00 | 2022-02-24 04:00 | Winter | FALSE | nonsummer
2022-02-24 04:00 | 2022-02-24 05:00 | Winter | FALSE | nonsummer
2022-02-24 05:00 | 2022-02-24 06:00 | Winter | FALSE | nonsummer
2022-02-24 06:00 | 2022-02-24 07:00 | Winter | FALSE | nonsummer
2022-02-24 07:00 | 2022-02-24 08:00 | Winter | FALSE | nonsummer
2022-02-24 08:00 | 2022-02-24 09:00 | Winter | FALSE | nonsummer
2022-02-24 09:00 | 2022-02-24 10:00 | Winter | FALSE | nonsummer
2022-02-24 10:00 | 2022-02-24 11:00 | Winter | FALSE | nonsummer
2022-02-24 11:00 | 2022-02-24 12:00 | Winter | FALSE | nonsummer
2022-02-24 12:00 | 2022-02-24 13:00 | Winter | FALSE | nonsummer
2022-02-24 13:00 | 2022-02-24 14:00 | Winter | FALSE | nonsummer
2022-02-24 14:00 | 2022-02-24 15:00 | Winter | FALSE | nonsummer
2022-02-24 15:00 | 2022-02-24 16:00 | Winter | FALSE | nonsummer
2022-02-24 16:00 | 2022-02-24 17:00 | Winter | TRUE | nonsummer
2022-02-24 17:00 | 2022-02-24 18:00 | Winter | TRUE | nonsummer
2022-02-24 18:00 | 2022-02-24 19:00 | Winter | TRUE | nonsummer
2022-02-24 19:00 | 2022-02-24 20:00 | Winter | TRUE | nonsummer
2022-02-24 20:00 | 2022-02-24 21:00 | Winter | TRUE | nonsummer
2022-02-24 21:00 | 2022-02-24 22:00 | Winter | FALSE | nonsummer
2022-02-24 22:00 | 2022-02-24 23:00 | Winter | FALSE | nonsummer
2022-02-24 23:00 | 2022-02-25 | Winter | FALSE | nonsummer
2022-02-25 | 2022-02-25 01:00 | Winter | FALSE | nonsummer
2022-02-25 01:00 | 2022-02-25 02:00 | Winter | FALSE | nonsummer
2022-02-25 02:00 | 2022-02-25 03:00 | Winter | FALSE | nonsummer
2022-02-25 03:00 | 2022-02-25 04:00 | Winter | FALSE | nonsummer
2022-02-25 04:00 | 2022-02-25 05:00 | Winter | FALSE | nonsummer
2022-02-25 05:00 | 2022-02-25 06:00 | Winter | FALSE | nonsummer
2022-02-25 06:00 | 2022-02-25 07:00 | Winter | FALSE | nonsummer
2022-02-25 07:00 | 2022-02-25 08:00 | Winter | FALSE | nonsummer
2022-02-25 08:00 | 2022-02-25 09:00 | Winter | FALSE | nonsummer
2022-02-25 09:00 | 2022-02-25 10:00 | Winter | FALSE | nonsummer
2022-02-25 10:00 | 2022-02-25 11:00 | Winter | FALSE | nonsummer
2022-02-25 11:00 | 2022-02-25 12:00 | Winter | FALSE | nonsummer
2022-02-25 12:00 | 2022-02-25 13:00 | Winter | FALSE | nonsummer
2022-02-25 13:00 | 2022-02-25 14:00 | Winter | FALSE | nonsummer
2022-02-25 14:00 | 2022-02-25 15:00 | Winter | FALSE | nonsummer
2022-02-25 15:00 | 2022-02-25 16:00 | Winter | FALSE | nonsummer
2022-02-25 16:00 | 2022-02-25 17:00 | Winter | TRUE | nonsummer
2022-02-25 17:00 | 2022-02-25 18:00 | Winter | TRUE | nonsummer
2022-02-25 18:00 | 2022-02-25 19:00 | Winter | TRUE | nonsummer
2022-02-25 19:00 | 2022-02-25 20:00 | Winter | TRUE | nonsummer
2022-02-25 20:00 | 2022-02-25 21:00 | Winter | TRUE | nonsummer
2022-02-25 21:00 | 2022-02-25 22:00 | Winter | FALSE | nonsummer
2022-02-25 22:00 | 2022-02-25 23:00 | Winter | FALSE | nonsummer
2022-02-25 23:00 | 2022-02-26 | Winter | FALSE | nonsummer
2022-02-26 | 2022-02-26 01:00 | Winter | FALSE | nonsummer
2022-02-26 01:00 | 2022-02-26 02:00 | Winter | FALSE | nonsummer
2022-02-26 02:00 | 2022-02-26 03:00 | Winter | FALSE | nonsummer
2022-02-26 03:00 | 2022-02-26 04:00 | Winter | FALSE | nonsummer
2022-02-26 04:00 | 2022-02-26 05:00 | Winter | FALSE | nonsummer
2022-02-26 05:00 | 2022-02-26 06:00 | Winter | FALSE | nonsummer
2022-02-26 06:00 | 2022-02-26 07:00 | Winter | FALSE | nonsummer
2022-02-26 07:00 | 2022-02-26 08:00 | Winter | FALSE | nonsummer
2022-02-26 08:00 | 2022-02-26 09:00 | Winter | FALSE | nonsummer
2022-02-26 09:00 | 2022-02-26 10:00 | Winter | FALSE | nonsummer
2022-02-26 10:00 | 2022-02-26 11:00 | Winter | FALSE | nonsummer
2022-02-26 11:00 | 2022-02-26 12:00 | Winter | FALSE | nonsummer
2022-02-26 12:00 | 2022-02-26 13:00 | Winter | FALSE | nonsummer
2022-02-26 13:00 | 2022-02-26 14:00 | Winter | FALSE | nonsummer
2022-02-26 14:00 | 2022-02-26 15:00 | Winter | FALSE | nonsummer
2022-02-26 15:00 | 2022-02-26 16:00 | Winter | FALSE | nonsummer
2022-02-26 16:00 | 2022-02-26 17:00 | Winter | TRUE | nonsummer
2022-02-26 17:00 | 2022-02-26 18:00 | Winter | TRUE | nonsummer
2022-02-26 18:00 | 2022-02-26 19:00 | Winter | TRUE | nonsummer
2022-02-26 19:00 | 2022-02-26 20:00 | Winter | TRUE | nonsummer
2022-02-26 20:00 | 2022-02-26 21:00 | Winter | TRUE | nonsummer
2022-02-26 21:00 | 2022-02-26 22:00 | Winter | FALSE | nonsummer
2022-02-26 22:00 | 2022-02-26 23:00 | Winter | FALSE | nonsummer
2022-02-26 23:00 | 2022-02-27 | Winter | FALSE | nonsummer
2022-02-27 | 2022-02-27 01:00 | Winter | FALSE | nonsummer
2022-02-27 01:00 | 2022-02-27 02:00 | Winter | FALSE | nonsummer
2022-02-27 02:00 | 2022-02-27 03:00 | Winter | FALSE | nonsummer
2022-02-27 03:00 | 2022-02-27 04:00 | Winter | FALSE | nonsummer
2022-02-27 04:00 | 2022-02-27 05:00 | Winter | FALSE | nonsummer
2022-02-27 05:00 | 2022-02-27 06:00 | Winter | FALSE | nonsummer
2022-02-27 06:00 | 2022-02-27 07:00 | Winter | FALSE | nonsummer
2022-02-27 07:00 | 2022-02-27 08:00 | Winter | FALSE | nonsummer
2022-02-27 08:00 | 2022-02-27 09:00 | Winter | FALSE | nonsummer
2022-02-27 09:00 | 2022-02-27 10:00 | Winter | FALSE | nonsummer
2022-02-27 10:00 | 2022-02-27 11:00 | Winter | FALSE | nonsummer
2022-02-27 11:00 | 2022-02-27 12:00 | Winter | FALSE | nonsummer
2022-02-27 12:00 | 2022-02-27 13:00 | Winter | FALSE | nonsummer
2022-02-27 13:00 | 2022-02-27 14:00 | Winter | FALSE | nonsummer
2022-02-27 14:00 | 2022-02-27 15:00 | Winter | FALSE | nonsummer
2022-02-27 15:00 | 2022-02-27 16:00 | Winter | FALSE | nonsummer
2022-02-27 16:00 | 2022-02-27 17:00 | Winter | TRUE | nonsummer
2022-02-27 17:00 | 2022-02-27 18:00 | Winter | TRUE | nonsummer
2022-02-27 18:00 | 2022-02-27 19:00 | Winter | TRUE | nonsummer
2022-02-27 19:00 | 2022-02-27 20:00 | Winter | TRUE | nonsummer
2022-02-27 20:00 | 2022-02-27 21:00 | Winter | TRUE | nonsummer
2022-02-27 21:00 | 2022-02-27 22:00 | Winter | FALSE | nonsummer
2022-02-27 22:00 | 2022-02-27 23:00 | Winter | FALSE | nonsummer
2022-02-27 23:00 | 2022-02-28 | Winter | FALSE | nonsummer
2022-02-28 | 2022-02-28 01:00 | Winter | FALSE | nonsummer
2022-02-28 01:00 | 2022-02-28 02:00 | Winter | FALSE | nonsummer
2022-02-28 02:00 | 2022-02-28 03:00 | Winter | FALSE | nonsummer
2022-02-28 03:00 | 2022-02-28 04:00 | Winter | FALSE | nonsummer
2022-02-28 04:00 | 2022-02-28 05:00 | Winter | FALSE | nonsummer
2022-02-28 05:00 | 2022-02-28 06:00 | Winter | FALSE | nonsummer
2022-02-28 06:00 | 2022-02-28 07:00 | Winter | FALSE | nonsummer
2022-02-28 07:00 | 2022-02-28 08:00 | Winter | FALSE | nonsummer
2022-02-28 08:00 | 2022-02-28 09:00 | Winter | FALSE | nonsummer
2022-02-28 09:00 | 2022-02-28 10:00 | Winter | FALSE | nonsummer
2022-02-28 10:00 | 2022-02-28 11:00 | Winter | FALSE | nonsummer
2022-02-28 11:00 | 2022-02-28 12:00 | Winter | FALSE | nonsummer
2022-02-28 12:00 | 2022-02-28 13:00 | Winter | FALSE | nonsummer
2022-02-28 13:00 | 2022-02-28 14:00 | Winter | FALSE | nonsummer
2022-02-28 14:00 | 2022-02-28 15:00 | Winter | FALSE | nonsummer
2022-02-28 15:00 | 2022-02-28 16:00 | Winter | FALSE | nonsummer
2022-02-28 16:00 | 2022-02-28 17:00 | Winter | TRUE | nonsummer
2022-02-28 17:00 | 2022-02-28 18:00 | Winter | TRUE | nonsummer
2022-02-28 18:00 | 2022-02-28 19:00 | Winter | TRUE | nonsummer
2022-02-28 19:00 | 2022-02-28 20:00 | Winter | TRUE | nonsummer
2022-02-28 20:00 | 2022-02-28 21:00 | Winter | TRUE | nonsummer
2022-02-28 21:00 | 2022-02-28 22:00 | Winter | FALSE | nonsummer
2022-02-28 22:00 | 2022-02-28 23:00 | Winter | FALSE | nonsummer
2022-02-28 23:00 | 2022-03-01 | Winter | FALSE | nonsummer
2022-03-01 | 2022-03-01 01:00 | Spring | FALSE | nonsummer
2022-03-01 01:00 | 2022-03-01 02:00 | Spring | FALSE | nonsummer
2022-03-01 02:00 | 2022-03-01 03:00 | Spring | FALSE | nonsummer
2022-03-01 03:00 | 2022-03-01 04:00 | Spring | FALSE | nonsummer
2022-03-01 04:00 | 2022-03-01 05:00 | Spring | FALSE | nonsummer
2022-03-01 05:00 | 2022-03-01 06:00 | Spring | FALSE | nonsummer
2022-03-01 06:00 | 2022-03-01 07:00 | Spring | FALSE | nonsummer
2022-03-01 07:00 | 2022-03-01 08:00 | Spring | FALSE | nonsummer
2022-03-01 08:00 | 2022-03-01 09:00 | Spring | FALSE | nonsummer
2022-03-01 09:00 | 2022-03-01 10:00 | Spring | FALSE | nonsummer
2022-03-01 10:00 | 2022-03-01 11:00 | Spring | FALSE | nonsummer
2022-03-01 11:00 | 2022-03-01 12:00 | Spring | FALSE | nonsummer
2022-03-01 12:00 | 2022-03-01 13:00 | Spring | FALSE | nonsummer
2022-03-01 13:00 | 2022-03-01 14:00 | Spring | FALSE | nonsummer
2022-03-01 14:00 | 2022-03-01 15:00 | Spring | FALSE | nonsummer
2022-03-01 15:00 | 2022-03-01 16:00 | Spring | FALSE | nonsummer
2022-03-01 16:00 | 2022-03-01 17:00 | Spring | FALSE | nonsummer
2022-03-01 17:00 | 2022-03-01 18:00 | Spring | TRUE | nonsummer
2022-03-01 18:00 | 2022-03-01 19:00 | Spring | TRUE | nonsummer
2022-03-01 19:00 | 2022-03-01 20:00 | Spring | TRUE | nonsummer
2022-03-01 20:00 | 2022-03-01 21:00 | Spring | TRUE | nonsummer
2022-03-01 21:00 | 2022-03-01 22:00 | Spring | TRUE | nonsummer
2022-03-01 22:00 | 2022-03-01 23:00 | Spring | FALSE | nonsummer
2022-03-01 23:00 | 2022-03-02 | Spring | FALSE | nonsummer
2022-03-02 | 2022-03-02 01:00 | Spring | FALSE | nonsummer
2022-03-02 01:00 | 2022-03-02 02:00 | Spring | FALSE | nonsummer
2022-03-02 02:00 | 2022-03-02 03:00 | Spring | FALSE | nonsummer
2022-03-02 03:00 | 2022-03-02 04:00 | Spring | FALSE | nonsummer
2022-03-02 04:00 | 2022-03-02 05:00 | Spring | FALSE | nonsummer
2022-03-02 05:00 | 2022-03-02 06:00 | Spring | FALSE | nonsummer
2022-03-02 06:00 | 2022-03-02 07:00 | Spring | FALSE | nonsummer
2022-03-02 07:00 | 2022-03-02 08:00 | Spring | FALSE | nonsummer
2022-03-02 08:00 | 2022-03-02 09:00 | Spring | FALSE | nonsummer
2022-03-02 09:00 | 2022-03-02 10:00 | Spring | FALSE | nonsummer
2022-03-02 10:00 | 2022-03-02 11:00 | Spring | FALSE | nonsummer
2022-03-02 11:00 | 2022-03-02 12:00 | Spring | FALSE | nonsummer
2022-03-02 12:00 | 2022-03-02 13:00 | Spring | FALSE | nonsummer
2022-03-02 13:00 | 2022-03-02 14:00 | Spring | FALSE | nonsummer
2022-03-02 14:00 | 2022-03-02 15:00 | Spring | FALSE | nonsummer
2022-03-02 15:00 | 2022-03-02 16:00 | Spring | FALSE | nonsummer
2022-03-02 16:00 | 2022-03-02 17:00 | Spring | FALSE | nonsummer
2022-03-02 17:00 | 2022-03-02 18:00 | Spring | TRUE | nonsummer
2022-03-02 18:00 | 2022-03-02 19:00 | Spring | TRUE | nonsummer
2022-03-02 19:00 | 2022-03-02 20:00 | Spring | TRUE | nonsummer
2022-03-02 20:00 | 2022-03-02 21:00 | Spring | TRUE | nonsummer
2022-03-02 21:00 | 2022-03-02 22:00 | Spring | TRUE | nonsummer
2022-03-02 22:00 | 2022-03-02 23:00 | Spring | FALSE | nonsummer
2022-03-02 23:00 | 2022-03-03 | Spring | FALSE | nonsummer
2022-03-03 | 2022-03-03 01:00 | Spring | FALSE | nonsummer
2022-03-03 01:00 | 2022-03-03 02:00 | Spring | FALSE | nonsummer
2022-03-03 02:00 | 2022-03-03 03:00 | Spring | FALSE | nonsummer
2022-03-03 03:00 | 2022-03-03 04:00 | Spring | FALSE | nonsummer
2022-03-03 04:00 | 2022-03-03 05:00 | Spring | FALSE | nonsummer
2022-03-03 05:00 | 2022-03-03 06:00 | Spring | FALSE | nonsummer
2022-03-03 06:00 | 2022-03-03 07:00 | Spring | FALSE | nonsummer
2022-03-03 07:00 | 2022-03-03 08:00 | Spring | FALSE | nonsummer
2022-03-03 08:00 | 2022-03-03 09:00 | Spring | FALSE | nonsummer
2022-03-03 09:00 | 2022-03-03 10:00 | Spring | FALSE | nonsummer
2022-03-03 10:00 | 2022-03-03 11:00 | Spring | FALSE | nonsummer
2022-03-03 11:00 | 2022-03-03 12:00 | Spring | FALSE | nonsummer
2022-03-03 12:00 | 2022-03-03 13:00 | Spring | FALSE | nonsummer
2022-03-03 13:00 | 2022-03-03 14:00 | Spring | FALSE | nonsummer
2022-03-03 14:00 | 2022-03-03 15:00 | Spring | FALSE | nonsummer
2022-03-03 15:00 | 2022-03-03 16:00 | Spring | FALSE | nonsummer
2022-03-03 16:00 | 2022-03-03 17:00 | Spring | FALSE | nonsummer
2022-03-03 17:00 | 2022-03-03 18:00 | Spring | TRUE | nonsummer
2022-03-03 18:00 | 2022-03-03 19:00 | Spring | TRUE | nonsummer
2022-03-03 19:00 | 2022-03-03 20:00 | Spring | TRUE | nonsummer
2022-03-03 20:00 | 2022-03-03 21:00 | Spring | TRUE | nonsummer
2022-03-03 21:00 | 2022-03-03 22:00 | Spring | TRUE | nonsummer
2022-03-03 22:00 | 2022-03-03 23:00 | Spring | FALSE | nonsummer
2022-03-03 23:00 | 2022-03-04 | Spring | FALSE | nonsummer
2022-03-04 | 2022-03-04 01:00 | Spring | FALSE | nonsummer
2022-03-04 01:00 | 2022-03-04 02:00 | Spring | FALSE | nonsummer
2022-03-04 02:00 | 2022-03-04 03:00 | Spring | FALSE | nonsummer
2022-03-04 03:00 | 2022-03-04 04:00 | Spring | FALSE | nonsummer
2022-03-04 04:00 | 2022-03-04 05:00 | Spring | FALSE | nonsummer
2022-03-04 05:00 | 2022-03-04 06:00 | Spring | FALSE | nonsummer
2022-03-04 06:00 | 2022-03-04 07:00 | Spring | FALSE | nonsummer
2022-03-04 07:00 | 2022-03-04 08:00 | Spring | FALSE | nonsummer
2022-03-04 08:00 | 2022-03-04 09:00 | Spring | FALSE | nonsummer
2022-03-04 09:00 | 2022-03-04 10:00 | Spring | FALSE | nonsummer
2022-03-04 10:00 | 2022-03-04 11:00 | Spring | FALSE | nonsummer
2022-03-04 11:00 | 2022-03-04 12:00 | Spring | FALSE | nonsummer
2022-03-04 12:00 | 2022-03-04 13:00 | Spring | FALSE | nonsummer
2022-03-04 13:00 | 2022-03-04 14:00 | Spring | FALSE | nonsummer
2022-03-04 14:00 | 2022-03-04 15:00 | Spring | FALSE | nonsummer
2022-03-04 15:00 | 2022-03-04 16:00 | Spring | FALSE | nonsummer
2022-03-04 16:00 | 2022-03-04 17:00 | Spring | FALSE | nonsummer
2022-03-04 17:00 | 2022-03-04 18:00 | Spring | TRUE | nonsummer
2022-03-04 18:00 | 2022-03-04 19:00 | Spring | TRUE | nonsummer
2022-03-04 19:00 | 2022-03-04 20:00 | Spring | TRUE | nonsummer
2022-03-04 20:00 | 2022-03-04 21:00 | Spring | TRUE | nonsummer
2022-03-04 21:00 | 2022-03-04 22:00 | Spring | TRUE | nonsummer
2022-03-04 22:00 | 2022-03-04 23:00 | Spring | FALSE | nonsummer
2022-03-04 23:00 | 2022-03-05 | Spring | FALSE | nonsummer
2022-03-05 | 2022-03-05 01:00 | Spring | FALSE | nonsummer
2022-03-05 01:00 | 2022-03-05 02:00 | Spring | FALSE | nonsummer
2022-03-05 02:00 | 2022-03-05 03:00 | Spring | FALSE | nonsummer
2022-03-05 03:00 | 2022-03-05 04:00 | Spring | FALSE | nonsummer
2022-03-05 04:00 | 2022-03-05 05:00 | Spring | FALSE | nonsummer
2022-03-05 05:00 | 2022-03-05 06:00 | Spring | FALSE | nonsummer
2022-03-05 06:00 | 2022-03-05 07:00 | Spring | FALSE | nonsummer
2022-03-05 07:00 | 2022-03-05 08:00 | Spring | FALSE | nonsummer
2022-03-05 08:00 | 2022-03-05 09:00 | Spring | FALSE | nonsummer
2022-03-05 09:00 | 2022-03-05 10:00 | Spring | FALSE | nonsummer
2022-03-05 10:00 | 2022-03-05 11:00 | Spring | FALSE | nonsummer
2022-03-05 11:00 | 2022-03-05 12:00 | Spring | FALSE | nonsummer
2022-03-05 12:00 | 2022-03-05 13:00 | Spring | FALSE | nonsummer
2022-03-05 13:00 | 2022-03-05 14:00 | Spring | FALSE | nonsummer
2022-03-05 14:00 | 2022-03-05 15:00 | Spring | FALSE | nonsummer
2022-03-05 15:00 | 2022-03-05 16:00 | Spring | FALSE | nonsummer
2022-03-05 16:00 | 2022-03-05 17:00 | Spring | FALSE | nonsummer
2022-03-05 17:00 | 2022-03-05 18:00 | Spring | TRUE | nonsummer
2022-03-05 18:00 | 2022-03-05 19:00 | Spring | TRUE | nonsummer
2022-03-05 19:00 | 2022-03-05 20:00 | Spring | TRUE | nonsummer
2022-03-05 20:00 | 2022-03-05 21:00 | Spring | TRUE | nonsummer
2022-03-05 21:00 | 2022-03-05 22:00 | Spring | TRUE | nonsummer
2022-03-05 22:00 | 2022-03-05 23:00 | Spring | FALSE | nonsummer
2022-03-05 23:00 | 2022-03-06 | Spring | FALSE | nonsummer
2022-03-06 | 2022-03-06 01:00 | Spring | FALSE | nonsummer
2022-03-06 01:00 | 2022-03-06 02:00 | Spring | FALSE | nonsummer
2022-03-06 02:00 | 2022-03-06 03:00 | Spring | FALSE | nonsummer
2022-03-06 03:00 | 2022-03-06 04:00 | Spring | FALSE | nonsummer
2022-03-06 04:00 | 2022-03-06 05:00 | Spring | FALSE | nonsummer
2022-03-06 05:00 | 2022-03-06 06:00 | Spring | FALSE | nonsummer
2022-03-06 06:00 | 2022-03-06 07:00 | Spring | FALSE | nonsummer
2022-03-06 07:00 | 2022-03-06 08:00 | Spring | FALSE | nonsummer
2022-03-06 08:00 | 2022-03-06 09:00 | Spring | FALSE | nonsummer
2022-03-06 09:00 | 2022-03-06 10:00 | Spring | FALSE | nonsummer
2022-03-06 10:00 | 2022-03-06 11:00 | Spring | FALSE | nonsummer
2022-03-06 11:00 | 2022-03-06 12:00 | Spring | FALSE | nonsummer
2022-03-06 12:00 | 2022-03-06 13:00 | Spring | FALSE | nonsummer
2022-03-06 13:00 | 2022-03-06 14:00 | Spring | FALSE | nonsummer
2022-03-06 14:00 | 2022-03-06 15:00 | Spring | FALSE | nonsummer
2022-03-06 15:00 | 2022-03-06 16:00 | Spring | FALSE | nonsummer
2022-03-06 16:00 | 2022-03-06 17:00 | Spring | FALSE | nonsummer
2022-03-06 17:00 | 2022-03-06 18:00 | Spring | TRUE | nonsummer
2022-03-06 18:00 | 2022-03-06 19:00 | Spring | TRUE | nonsummer
2022-03-06 19:00 | 2022-03-06 20:00 | Spring | TRUE | nonsummer
2022-03-06 20:00 | 2022-03-06 21:00 | Spring | TRUE | nonsummer
2022-03-06 21:00 | 2022-03-06 22:00 | Spring | TRUE | nonsummer
2022-03-06 22:00 | 2022-03-06 23:00 | Spring | FALSE | nonsummer
2022-03-06 23:00 | 2022-03-07 | Spring | FALSE | nonsummer
2022-03-07 | 2022-03-07 01:00 | Spring | FALSE | nonsummer
2022-03-07 01:00 | 2022-03-07 02:00 | Spring | FALSE | nonsummer
2022-03-07 02:00 | 2022-03-07 03:00 | Spring | FALSE | nonsummer
2022-03-07 03:00 | 2022-03-07 04:00 | Spring | FALSE | nonsummer
2022-03-07 04:00 | 2022-03-07 05:00 | Spring | FALSE | nonsummer
2022-03-07 05:00 | 2022-03-07 06:00 | Spring | FALSE | nonsummer
2022-03-07 06:00 | 2022-03-07 07:00 | Spring | FALSE | nonsummer
2022-03-07 07:00 | 2022-03-07 08:00 | Spring | FALSE | nonsummer
2022-03-07 08:00 | 2022-03-07 09:00 | Spring | FALSE | nonsummer
2022-03-07 09:00 | 2022-03-07 10:00 | Spring | FALSE | nonsummer
2022-03-07 10:00 | 2022-03-07 11:00 | Spring | FALSE | nonsummer
2022-03-07 11:00 | 2022-03-07 12:00 | Spring | FALSE | nonsummer
2022-03-07 12:00 | 2022-03-07 13:00 | Spring | FALSE | nonsummer
2022-03-07 13:00 | 2022-03-07 14:00 | Spring | FALSE | nonsummer
2022-03-07 14:00 | 2022-03-07 15:00 | Spring | FALSE | nonsummer
2022-03-07 15:00 | 2022-03-07 16:00 | Spring | FALSE | nonsummer
2022-03-07 16:00 | 2022-03-07 17:00 | Spring | FALSE | nonsummer
2022-03-07 17:00 | 2022-03-07 18:00 | Spring | TRUE | nonsummer
2022-03-07 18:00 | 2022-03-07 19:00 | Spring | TRUE | nonsummer
2022-03-07 19:00 | 2022-03-07 20:00 | Spring | TRUE | nonsummer
2022-03-07 20:00 | 2022-03-07 21:00 | Spring | TRUE | nonsummer
2022-03-07 21:00 | 2022-03-07 22:00 | Spring | TRUE | nonsummer
2022-03-07 22:00 | 2022-03-07 23:00 | Spring | FALSE | nonsummer
2022-03-07 23:00 | 2022-03-08 | Spring | FALSE | nonsummer
2022-03-08 | 2022-03-08 01:00 | Spring | FALSE | nonsummer
2022-03-08 01:00 | 2022-03-08 02:00 | Spring | FALSE | nonsummer
2022-03-08 02:00 | 2022-03-08 03:00 | Spring | FALSE | nonsummer
2022-03-08 03:00 | 2022-03-08 04:00 | Spring | FALSE | nonsummer
2022-03-08 04:00 | 2022-03-08 05:00 | Spring | FALSE | nonsummer
2022-03-08 05:00 | 2022-03-08 06:00 | Spring | FALSE | nonsummer
2022-03-08 06:00 | 2022-03-08 07:00 | Spring | FALSE | nonsummer
2022-03-08 07:00 | 2022-03-08 08:00 | Spring | FALSE | nonsummer
2022-03-08 08:00 | 2022-03-08 09:00 | Spring | FALSE | nonsummer
2022-03-08 09:00 | 2022-03-08 10:00 | Spring | FALSE | nonsummer
2022-03-08 10:00 | 2022-03-08 11:00 | Spring | FALSE | nonsummer
2022-03-08 11:00 | 2022-03-08 12:00 | Spring | FALSE | nonsummer
2022-03-08 12:00 | 2022-03-08 13:00 | Spring | FALSE | nonsummer
2022-03-08 13:00 | 2022-03-08 14:00 | Spring | FALSE | nonsummer
2022-03-08 14:00 | 2022-03-08 15:00 | Spring | FALSE | nonsummer
2022-03-08 15:00 | 2022-03-08 16:00 | Spring | FALSE | nonsummer
2022-03-08 16:00 | 2022-03-08 17:00 | Spring | FALSE | nonsummer
2022-03-08 17:00 | 2022-03-08 18:00 | Spring | TRUE | nonsummer
2022-03-08 18:00 | 2022-03-08 19:00 | Spring | TRUE | nonsummer
2022-03-08 19:00 | 2022-03-08 20:00 | Spring | TRUE | nonsummer
2022-03-08 20:00 | 2022-03-08 21:00 | Spring | TRUE | nonsummer
2022-03-08 21:00 | 2022-03-08 22:00 | Spring | TRUE | nonsummer
2022-03-08 22:00 | 2022-03-08 23:00 | Spring | FALSE | nonsummer
2022-03-08 23:00 | 2022-03-09 | Spring | FALSE | nonsummer
2022-03-09 | 2022-03-09 01:00 | Spring | FALSE | nonsummer
2022-03-09 01:00 | 2022-03-09 02:00 | Spring | FALSE | nonsummer
2022-03-09 02:00 | 2022-03-09 03:00 | Spring | FALSE | nonsummer
2022-03-09 03:00 | 2022-03-09 04:00 | Spring | FALSE | nonsummer
2022-03-09 04:00 | 2022-03-09 05:00 | Spring | FALSE | nonsummer
2022-03-09 05:00 | 2022-03-09 06:00 | Spring | FALSE | nonsummer
2022-03-09 06:00 | 2022-03-09 07:00 | Spring | FALSE | nonsummer
2022-03-09 07:00 | 2022-03-09 08:00 | Spring | FALSE | nonsummer
2022-03-09 08:00 | 2022-03-09 09:00 | Spring | FALSE | nonsummer
2022-03-09 09:00 | 2022-03-09 10:00 | Spring | FALSE | nonsummer
2022-03-09 10:00 | 2022-03-09 11:00 | Spring | FALSE | nonsummer
2022-03-09 11:00 | 2022-03-09 12:00 | Spring | FALSE | nonsummer
2022-03-09 12:00 | 2022-03-09 13:00 | Spring | FALSE | nonsummer
2022-03-09 13:00 | 2022-03-09 14:00 | Spring | FALSE | nonsummer
2022-03-09 14:00 | 2022-03-09 15:00 | Spring | FALSE | nonsummer
2022-03-09 15:00 | 2022-03-09 16:00 | Spring | FALSE | nonsummer
2022-03-09 16:00 | 2022-03-09 17:00 | Spring | FALSE | nonsummer
2022-03-09 17:00 | 2022-03-09 18:00 | Spring | TRUE | nonsummer
2022-03-09 18:00 | 2022-03-09 19:00 | Spring | TRUE | nonsummer
2022-03-09 19:00 | 2022-03-09 20:00 | Spring | TRUE | nonsummer
2022-03-09 20:00 | 2022-03-09 21:00 | Spring | TRUE | nonsummer
2022-03-09 21:00 | 2022-03-09 22:00 | Spring | TRUE | nonsummer
2022-03-09 22:00 | 2022-03-09 23:00 | Spring | FALSE | nonsummer
2022-03-09 23:00 | 2022-03-10 | Spring | FALSE | nonsummer
2022-03-10 | 2022-03-10 01:00 | Spring | FALSE | nonsummer
2022-03-10 01:00 | 2022-03-10 02:00 | Spring | FALSE | nonsummer
2022-03-10 02:00 | 2022-03-10 03:00 | Spring | FALSE | nonsummer
2022-03-10 03:00 | 2022-03-10 04:00 | Spring | FALSE | nonsummer
2022-03-10 04:00 | 2022-03-10 05:00 | Spring | FALSE | nonsummer
2022-03-10 05:00 | 2022-03-10 06:00 | Spring | FALSE | nonsummer
2022-03-10 06:00 | 2022-03-10 07:00 | Spring | FALSE | nonsummer
2022-03-10 07:00 | 2022-03-10 08:00 | Spring | FALSE | nonsummer
2022-03-10 08:00 | 2022-03-10 09:00 | Spring | FALSE | nonsummer
2022-03-10 09:00 | 2022-03-10 10:00 | Spring | FALSE | nonsummer
2022-03-10 10:00 | 2022-03-10 11:00 | Spring | FALSE | nonsummer
2022-03-10 11:00 | 2022-03-10 12:00 | Spring | FALSE | nonsummer
2022-03-10 12:00 | 2022-03-10 13:00 | Spring | FALSE | nonsummer
2022-03-10 13:00 | 2022-03-10 14:00 | Spring | FALSE | nonsummer
2022-03-10 14:00 | 2022-03-10 15:00 | Spring | FALSE | nonsummer
2022-03-10 15:00 | 2022-03-10 16:00 | Spring | FALSE | nonsummer
2022-03-10 16:00 | 2022-03-10 17:00 | Spring | FALSE | nonsummer
2022-03-10 17:00 | 2022-03-10 18:00 | Spring | TRUE | nonsummer
2022-03-10 18:00 | 2022-03-10 19:00 | Spring | TRUE | nonsummer
2022-03-10 19:00 | 2022-03-10 20:00 | Spring | TRUE | nonsummer
2022-03-10 20:00 | 2022-03-10 21:00 | Spring | TRUE | nonsummer
2022-03-10 21:00 | 2022-03-10 22:00 | Spring | TRUE | nonsummer
2022-03-10 22:00 | 2022-03-10 23:00 | Spring | FALSE | nonsummer
2022-03-10 23:00 | 2022-03-11 | Spring | FALSE | nonsummer
2022-03-11 | 2022-03-11 01:00 | Spring | FALSE | nonsummer
2022-03-11 01:00 | 2022-03-11 02:00 | Spring | FALSE | nonsummer
2022-03-11 02:00 | 2022-03-11 03:00 | Spring | FALSE | nonsummer
2022-03-11 03:00 | 2022-03-11 04:00 | Spring | FALSE | nonsummer
2022-03-11 04:00 | 2022-03-11 05:00 | Spring | FALSE | nonsummer
2022-03-11 05:00 | 2022-03-11 06:00 | Spring | FALSE | nonsummer
2022-03-11 06:00 | 2022-03-11 07:00 | Spring | FALSE | nonsummer
2022-03-11 07:00 | 2022-03-11 08:00 | Spring | FALSE | nonsummer
2022-03-11 08:00 | 2022-03-11 09:00 | Spring | FALSE | nonsummer
2022-03-11 09:00 | 2022-03-11 10:00 | Spring | FALSE | nonsummer
2022-03-11 10:00 | 2022-03-11 11:00 | Spring | FALSE | nonsummer
2022-03-11 11:00 | 2022-03-11 12:00 | Spring | FALSE | nonsummer
2022-03-11 12:00 | 2022-03-11 13:00 | Spring | FALSE | nonsummer
2022-03-11 13:00 | 2022-03-11 14:00 | Spring | FALSE | nonsummer
2022-03-11 14:00 | 2022-03-11 15:00 | Spring | FALSE | nonsummer
2022-03-11 15:00 | 2022-03-11 16:00 | Spring | FALSE | nonsummer
2022-03-11 16:00 | 2022-03-11 17:00 | Spring | FALSE | nonsummer
2022-03-11 17:00 | 2022-03-11 18:00 | Spring | TRUE | nonsummer
2022-03-11 18:00 | 2022-03-11 19:00 | Spring | TRUE | nonsummer
2022-03-11 19:00 | 2022-03-11 20:00 | Spring | TRUE | nonsummer
2022-03-11 20:00 | 2022-03-11 21:00 | Spring | TRUE | nonsummer
2022-03-11 21:00 | 2022-03-11 22:00 | Spring | TRUE | nonsummer
2022-03-11 22:00 | 2022-03-11 23:00 | Spring | FALSE | nonsummer
2022-03-11 23:00 | 2022-03-12 | Spring | FALSE | nonsummer
2022-03-12 | 2022-03-12 01:00 | Spring | FALSE | nonsummer
2022-03-12 01:00 | 2022-03-12 02:00 | Spring | FALSE | nonsummer
2022-03-12 02:00 | 2022-03-12 03:00 | Spring | FALSE | nonsummer
2022-03-12 03:00 | 2022-03-12 04:00 | Spring | FALSE | nonsummer
2022-03-12 04:00 | 2022-03-12 05:00 | Spring | FALSE | nonsummer
2022-03-12 05:00 | 2022-03-12 06:00 | Spring | FALSE | nonsummer
2022-03-12 06:00 | 2022-03-12 07:00 | Spring | FALSE | nonsummer
2022-03-12 07:00 | 2022-03-12 08:00 | Spring | FALSE | nonsummer
2022-03-12 08:00 | 2022-03-12 09:00 | Spring | FALSE | nonsummer
2022-03-12 09:00 | 2022-03-12 10:00 | Spring | FALSE | nonsummer
2022-03-12 10:00 | 2022-03-12 11:00 | Spring | FALSE | nonsummer
2022-03-12 11:00 | 2022-03-12 12:00 | Spring | FALSE | nonsummer
2022-03-12 12:00 | 2022-03-12 13:00 | Spring | FALSE | nonsummer
2022-03-12 13:00 | 2022-03-12 14:00 | Spring | FALSE | nonsummer
2022-03-12 14:00 | 2022-03-12 15:00 | Spring | FALSE | nonsummer
2022-03-12 15:00 | 2022-03-12 16:00 | Spring | FALSE | nonsummer
2022-03-12 16:00 | 2022-03-12 17:00 | Spring | FALSE | nonsummer
2022-03-12 17:00 | 2022-03-12 18:00 | Spring | TRUE | nonsummer
2022-03-12 18:00 | 2022-03-12 19:00 | Spring | TRUE | nonsummer
2022-03-12 19:00 | 2022-03-12 20:00 | Spring | TRUE | nonsummer
2022-03-12 20:00 | 2022-03-12 21:00 | Spring | TRUE | nonsummer
2022-03-12 21:00 | 2022-03-12 22:00 | Spring | TRUE | nonsummer
2022-03-12 22:00 | 2022-03-12 23:00 | Spring | FALSE | nonsummer
2022-03-12 23:00 | 2022-03-13 | Spring | FALSE | nonsummer
2022-03-13 | 2022-03-13 01:00 | Spring | FALSE | nonsummer
2022-03-13 01:00 | 2022-03-13 02:00 | Spring | FALSE | nonsummer
2022-03-13 02:00 | 2022-03-13 03:00 | Spring | FALSE | nonsummer
2022-03-13 03:00 | 2022-03-13 04:00 | Spring | FALSE | nonsummer
2022-03-13 04:00 | 2022-03-13 05:00 | Spring | FALSE | nonsummer
2022-03-13 05:00 | 2022-03-13 06:00 | Spring | FALSE | nonsummer
2022-03-13 06:00 | 2022-03-13 07:00 | Spring | FALSE | nonsummer
2022-03-13 07:00 | 2022-03-13 08:00 | Spring | FALSE | nonsummer
2022-03-13 08:00 | 2022-03-13 09:00 | Spring | FALSE | nonsummer
2022-03-13 09:00 | 2022-03-13 10:00 | Spring | FALSE | nonsummer
2022-03-13 10:00 | 2022-03-13 11:00 | Spring | FALSE | nonsummer
2022-03-13 11:00 | 2022-03-13 12:00 | Spring | FALSE | nonsummer
2022-03-13 12:00 | 2022-03-13 13:00 | Spring | FALSE | nonsummer
2022-03-13 13:00 | 2022-03-13 14:00 | Spring | FALSE | nonsummer
2022-03-13 14:00 | 2022-03-13 15:00 | Spring | FALSE | nonsummer
2022-03-13 15:00 | 2022-03-13 16:00 | Spring | FALSE | nonsummer
2022-03-13 16:00 | 2022-03-13 17:00 | Spring | FALSE | nonsummer
2022-03-13 17:00 | 2022-03-13 18:00 | Spring | TRUE | nonsummer
2022-03-13 18:00 | 2022-03-13 19:00 | Spring | TRUE | nonsummer
2022-03-13 19:00 | 2022-03-13 20:00 | Spring | TRUE | nonsummer
2022-03-13 20:00 | 2022-03-13 21:00 | Spring | TRUE | nonsummer
2022-03-13 21:00 | 2022-03-13 22:00 | Spring | TRUE | nonsummer
2022-03-13 22:00 | 2022-03-13 23:00 | Spring | FALSE | nonsummer
2022-03-13 23:00 | 2022-03-14 | Spring | FALSE | nonsummer
2022-03-14 | 2022-03-14 01:00 | Spring | FALSE | nonsummer
2022-03-14 01:00 | 2022-03-14 02:00 | Spring | FALSE | nonsummer
2022-03-14 02:00 | 2022-03-14 03:00 | Spring | FALSE | nonsummer
2022-03-14 03:00 | 2022-03-14 04:00 | Spring | FALSE | nonsummer
2022-03-14 04:00 | 2022-03-14 05:00 | Spring | FALSE | nonsummer
2022-03-14 05:00 | 2022-03-14 06:00 | Spring | FALSE | nonsummer
2022-03-14 06:00 | 2022-03-14 07:00 | Spring | FALSE | nonsummer
2022-03-14 07:00 | 2022-03-14 08:00 | Spring | FALSE | nonsummer
2022-03-14 08:00 | 2022-03-14 09:00 | Spring | FALSE | nonsummer
2022-03-14 09:00 | 2022-03-14 10:00 | Spring | FALSE | nonsummer
2022-03-14 10:00 | 2022-03-14 11:00 | Spring | FALSE | nonsummer
2022-03-14 11:00 | 2022-03-14 12:00 | Spring | FALSE | nonsummer
2022-03-14 12:00 | 2022-03-14 13:00 | Spring | FALSE | nonsummer
2022-03-14 13:00 | 2022-03-14 14:00 | Spring | FALSE | nonsummer
2022-03-14 14:00 | 2022-03-14 15:00 | Spring | FALSE | nonsummer
2022-03-14 15:00 | 2022-03-14 16:00 | Spring | FALSE | nonsummer
2022-03-14 16:00 | 2022-03-14 17:00 | Spring | FALSE | nonsummer
2022-03-14 17:00 | 2022-03-14 18:00 | Spring | TRUE | nonsummer
2022-03-14 18:00 | 2022-03-14 19:00 | Spring | TRUE | nonsummer
2022-03-14 19:00 | 2022-03-14 20:00 | Spring | TRUE | nonsummer
2022-03-14 20:00 | 2022-03-14 21:00 | Spring | TRUE | nonsummer
2022-03-14 21:00 | 2022-03-14 22:00 | Spring | TRUE | nonsummer
2022-03-14 22:00 | 2022-03-14 23:00 | Spring | FALSE | nonsummer
2022-03-14 23:00 | 2022-03-15 | Spring | FALSE | nonsummer
2022-03-15 | 2022-03-15 01:00 | Spring | FALSE | nonsummer
2022-03-15 01:00 | 2022-03-15 02:00 | Spring | FALSE | nonsummer
2022-03-15 02:00 | 2022-03-15 03:00 | Spring | FALSE | nonsummer
2022-03-15 03:00 | 2022-03-15 04:00 | Spring | FALSE | nonsummer
2022-03-15 04:00 | 2022-03-15 05:00 | Spring | FALSE | nonsummer
2022-03-15 05:00 | 2022-03-15 06:00 | Spring | FALSE | nonsummer
2022-03-15 06:00 | 2022-03-15 07:00 | Spring | FALSE | nonsummer
2022-03-15 07:00 | 2022-03-15 08:00 | Spring | FALSE | nonsummer
2022-03-15 08:00 | 2022-03-15 09:00 | Spring | FALSE | nonsummer
2022-03-15 09:00 | 2022-03-15 10:00 | Spring | FALSE | nonsummer
2022-03-15 10:00 | 2022-03-15 11:00 | Spring | FALSE | nonsummer
2022-03-15 11:00 | 2022-03-15 12:00 | Spring | FALSE | nonsummer
2022-03-15 12:00 | 2022-03-15 13:00 | Spring | FALSE | nonsummer
2022-03-15 13:00 | 2022-03-15 14:00 | Spring | FALSE | nonsummer
2022-03-15 14:00 | 2022-03-15 15:00 | Spring | FALSE | nonsummer
2022-03-15 15:00 | 2022-03-15 16:00 | Spring | FALSE | nonsummer
2022-03-15 16:00 | 2022-03-15 17:00 | Spring | FALSE | nonsummer
2022-03-15 17:00 | 2022-03-15 18:00 | Spring | TRUE | nonsummer
2022-03-15 18:00 | 2022-03-15 19:00 | Spring | TRUE | nonsummer
2022-03-15 19:00 | 2022-03-15 20:00 | Spring | TRUE | nonsummer
2022-03-15 20:00 | 2022-03-15 21:00 | Spring | TRUE | nonsummer
2022-03-15 21:00 | 2022-03-15 22:00 | Spring | TRUE | nonsummer
2022-03-15 22:00 | 2022-03-15 23:00 | Spring | FALSE | nonsummer
2022-03-15 23:00 | 2022-03-16 | Spring | FALSE | nonsummer
2022-03-16 | 2022-03-16 01:00 | Spring | FALSE | nonsummer
2022-03-16 01:00 | 2022-03-16 02:00 | Spring | FALSE | nonsummer
2022-03-16 02:00 | 2022-03-16 03:00 | Spring | FALSE | nonsummer
2022-03-16 03:00 | 2022-03-16 04:00 | Spring | FALSE | nonsummer
2022-03-16 04:00 | 2022-03-16 05:00 | Spring | FALSE | nonsummer
2022-03-16 05:00 | 2022-03-16 06:00 | Spring | FALSE | nonsummer
2022-03-16 06:00 | 2022-03-16 07:00 | Spring | FALSE | nonsummer
2022-03-16 07:00 | 2022-03-16 08:00 | Spring | FALSE | nonsummer
2022-03-16 08:00 | 2022-03-16 09:00 | Spring | FALSE | nonsummer
2022-03-16 09:00 | 2022-03-16 10:00 | Spring | FALSE | nonsummer
2022-03-16 10:00 | 2022-03-16 11:00 | Spring | FALSE | nonsummer
2022-03-16 11:00 | 2022-03-16 12:00 | Spring | FALSE | nonsummer
2022-03-16 12:00 | 2022-03-16 13:00 | Spring | FALSE | nonsummer
2022-03-16 13:00 | 2022-03-16 14:00 | Spring | FALSE | nonsummer
2022-03-16 14:00 | 2022-03-16 15:00 | Spring | FALSE | nonsummer
2022-03-16 15:00 | 2022-03-16 16:00 | Spring | FALSE | nonsummer
2022-03-16 16:00 | 2022-03-16 17:00 | Spring | FALSE | nonsummer
2022-03-16 17:00 | 2022-03-16 18:00 | Spring | TRUE | nonsummer
2022-03-16 18:00 | 2022-03-16 19:00 | Spring | TRUE | nonsummer
2022-03-16 19:00 | 2022-03-16 20:00 | Spring | TRUE | nonsummer
2022-03-16 20:00 | 2022-03-16 21:00 | Spring | TRUE | nonsummer
2022-03-16 21:00 | 2022-03-16 22:00 | Spring | TRUE | nonsummer
2022-03-16 22:00 | 2022-03-16 23:00 | Spring | FALSE | nonsummer
2022-03-16 23:00 | 2022-03-17 | Spring | FALSE | nonsummer
2022-03-17 | 2022-03-17 01:00 | Spring | FALSE | nonsummer
2022-03-17 01:00 | 2022-03-17 02:00 | Spring | FALSE | nonsummer
2022-03-17 02:00 | 2022-03-17 03:00 | Spring | FALSE | nonsummer
2022-03-17 03:00 | 2022-03-17 04:00 | Spring | FALSE | nonsummer
2022-03-17 04:00 | 2022-03-17 05:00 | Spring | FALSE | nonsummer
2022-03-17 05:00 | 2022-03-17 06:00 | Spring | FALSE | nonsummer
2022-03-17 06:00 | 2022-03-17 07:00 | Spring | FALSE | nonsummer
2022-03-17 07:00 | 2022-03-17 08:00 | Spring | FALSE | nonsummer
2022-03-17 08:00 | 2022-03-17 09:00 | Spring | FALSE | nonsummer
2022-03-17 09:00 | 2022-03-17 10:00 | Spring | FALSE | nonsummer
2022-03-17 10:00 | 2022-03-17 11:00 | Spring | FALSE | nonsummer
2022-03-17 11:00 | 2022-03-17 12:00 | Spring | FALSE | nonsummer
2022-03-17 12:00 | 2022-03-17 13:00 | Spring | FALSE | nonsummer
2022-03-17 13:00 | 2022-03-17 14:00 | Spring | FALSE | nonsummer
2022-03-17 14:00 | 2022-03-17 15:00 | Spring | FALSE | nonsummer
2022-03-17 15:00 | 2022-03-17 16:00 | Spring | FALSE | nonsummer
2022-03-17 16:00 | 2022-03-17 17:00 | Spring | FALSE | nonsummer
2022-03-17 17:00 | 2022-03-17 18:00 | Spring | TRUE | nonsummer
2022-03-17 18:00 | 2022-03-17 19:00 | Spring | TRUE | nonsummer
2022-03-17 19:00 | 2022-03-17 20:00 | Spring | TRUE | nonsummer
2022-03-17 20:00 | 2022-03-17 21:00 | Spring | TRUE | nonsummer
2022-03-17 21:00 | 2022-03-17 22:00 | Spring | TRUE | nonsummer
2022-03-17 22:00 | 2022-03-17 23:00 | Spring | FALSE | nonsummer
2022-03-17 23:00 | 2022-03-18 | Spring | FALSE | nonsummer
2022-03-18 | 2022-03-18 01:00 | Spring | FALSE | nonsummer
2022-03-18 01:00 | 2022-03-18 02:00 | Spring | FALSE | nonsummer
2022-03-18 02:00 | 2022-03-18 03:00 | Spring | FALSE | nonsummer
2022-03-18 03:00 | 2022-03-18 04:00 | Spring | FALSE | nonsummer
2022-03-18 04:00 | 2022-03-18 05:00 | Spring | FALSE | nonsummer
2022-03-18 05:00 | 2022-03-18 06:00 | Spring | FALSE | nonsummer
2022-03-18 06:00 | 2022-03-18 07:00 | Spring | FALSE | nonsummer
2022-03-18 07:00 | 2022-03-18 08:00 | Spring | FALSE | nonsummer
2022-03-18 08:00 | 2022-03-18 09:00 | Spring | FALSE | nonsummer
2022-03-18 09:00 | 2022-03-18 10:00 | Spring | FALSE | nonsummer
2022-03-18 10:00 | 2022-03-18 11:00 | Spring | FALSE | nonsummer
2022-03-18 11:00 | 2022-03-18 12:00 | Spring | FALSE | nonsummer
2022-03-18 12:00 | 2022-03-18 13:00 | Spring | FALSE | nonsummer
2022-03-18 13:00 | 2022-03-18 14:00 | Spring | FALSE | nonsummer
2022-03-18 14:00 | 2022-03-18 15:00 | Spring | FALSE | nonsummer
2022-03-18 15:00 | 2022-03-18 16:00 | Spring | FALSE | nonsummer
2022-03-18 16:00 | 2022-03-18 17:00 | Spring | FALSE | nonsummer
2022-03-18 17:00 | 2022-03-18 18:00 | Spring | TRUE | nonsummer
2022-03-18 18:00 | 2022-03-18 19:00 | Spring | TRUE | nonsummer
2022-03-18 19:00 | 2022-03-18 20:00 | Spring | TRUE | nonsummer
2022-03-18 20:00 | 2022-03-18 21:00 | Spring | TRUE | nonsummer
2022-03-18 21:00 | 2022-03-18 22:00 | Spring | TRUE | nonsummer
2022-03-18 22:00 | 2022-03-18 23:00 | Spring | FALSE | nonsummer
2022-03-18 23:00 | 2022-03-19 | Spring | FALSE | nonsummer
2022-03-19 | 2022-03-19 01:00 | Spring | FALSE | nonsummer
2022-03-19 01:00 | 2022-03-19 02:00 | Spring | FALSE | nonsummer
2022-03-19 02:00 | 2022-03-19 03:00 | Spring | FALSE | nonsummer
2022-03-19 03:00 | 2022-03-19 04:00 | Spring | FALSE | nonsummer
2022-03-19 04:00 | 2022-03-19 05:00 | Spring | FALSE | nonsummer
2022-03-19 05:00 | 2022-03-19 06:00 | Spring | FALSE | nonsummer
2022-03-19 06:00 | 2022-03-19 07:00 | Spring | FALSE | nonsummer
2022-03-19 07:00 | 2022-03-19 08:00 | Spring | FALSE | nonsummer
2022-03-19 08:00 | 2022-03-19 09:00 | Spring | FALSE | nonsummer
2022-03-19 09:00 | 2022-03-19 10:00 | Spring | FALSE | nonsummer
2022-03-19 10:00 | 2022-03-19 11:00 | Spring | FALSE | nonsummer
2022-03-19 11:00 | 2022-03-19 12:00 | Spring | FALSE | nonsummer
2022-03-19 12:00 | 2022-03-19 13:00 | Spring | FALSE | nonsummer
2022-03-19 13:00 | 2022-03-19 14:00 | Spring | FALSE | nonsummer
2022-03-19 14:00 | 2022-03-19 15:00 | Spring | FALSE | nonsummer
2022-03-19 15:00 | 2022-03-19 16:00 | Spring | FALSE | nonsummer
2022-03-19 16:00 | 2022-03-19 17:00 | Spring | FALSE | nonsummer
2022-03-19 17:00 | 2022-03-19 18:00 | Spring | TRUE | nonsummer
2022-03-19 18:00 | 2022-03-19 19:00 | Spring | TRUE | nonsummer
2022-03-19 19:00 | 2022-03-19 20:00 | Spring | TRUE | nonsummer
2022-03-19 20:00 | 2022-03-19 21:00 | Spring | TRUE | nonsummer
2022-03-19 21:00 | 2022-03-19 22:00 | Spring | TRUE | nonsummer
2022-03-19 22:00 | 2022-03-19 23:00 | Spring | FALSE | nonsummer
2022-03-19 23:00 | 2022-03-20 | Spring | FALSE | nonsummer
2022-03-20 | 2022-03-20 01:00 | Spring | FALSE | nonsummer
2022-03-20 01:00 | 2022-03-20 02:00 | Spring | FALSE | nonsummer
2022-03-20 02:00 | 2022-03-20 03:00 | Spring | FALSE | nonsummer
2022-03-20 03:00 | 2022-03-20 04:00 | Spring | FALSE | nonsummer
2022-03-20 04:00 | 2022-03-20 05:00 | Spring | FALSE | nonsummer
2022-03-20 05:00 | 2022-03-20 06:00 | Spring | FALSE | nonsummer
2022-03-20 06:00 | 2022-03-20 07:00 | Spring | FALSE | nonsummer
2022-03-20 07:00 | 2022-03-20 08:00 | Spring | FALSE | nonsummer
2022-03-20 08:00 | 2022-03-20 09:00 | Spring | FALSE | nonsummer
2022-03-20 09:00 | 2022-03-20 10:00 | Spring | FALSE | nonsummer
2022-03-20 10:00 | 2022-03-20 11:00 | Spring | FALSE | nonsummer
2022-03-20 11:00 | 2022-03-20 12:00 | Spring | FALSE | nonsummer
2022-03-20 12:00 | 2022-03-20 13:00 | Spring | FALSE | nonsummer
2022-03-20 13:00 | 2022-03-20 14:00 | Spring | FALSE | nonsummer
2022-03-20 14:00 | 2022-03-20 15:00 | Spring | FALSE | nonsummer
2022-03-20 15:00 | 2022-03-20 16:00 | Spring | FALSE | nonsummer
2022-03-20 16:00 | 2022-03-20 17:00 | Spring | FALSE | nonsummer
2022-03-20 17:00 | 2022-03-20 18:00 | Spring | TRUE | nonsummer
2022-03-20 18:00 | 2022-03-20 19:00 | Spring | TRUE | nonsummer
2022-03-20 19:00 | 2022-03-20 20:00 | Spring | TRUE | nonsummer
2022-03-20 20:00 | 2022-03-20 21:00 | Spring | TRUE | nonsummer
2022-03-20 21:00 | 2022-03-20 22:00 | Spring | TRUE | nonsummer
2022-03-20 22:00 | 2022-03-20 23:00 | Spring | FALSE | nonsummer
2022-03-20 23:00 | 2022-03-21 | Spring | FALSE | nonsummer
2022-03-21 | 2022-03-21 01:00 | Spring | FALSE | nonsummer
2022-03-21 01:00 | 2022-03-21 02:00 | Spring | FALSE | nonsummer
2022-03-21 02:00 | 2022-03-21 03:00 | Spring | FALSE | nonsummer
2022-03-21 03:00 | 2022-03-21 04:00 | Spring | FALSE | nonsummer
2022-03-21 04:00 | 2022-03-21 05:00 | Spring | FALSE | nonsummer
2022-03-21 05:00 | 2022-03-21 06:00 | Spring | FALSE | nonsummer
2022-03-21 06:00 | 2022-03-21 07:00 | Spring | FALSE | nonsummer
2022-03-21 07:00 | 2022-03-21 08:00 | Spring | FALSE | nonsummer
2022-03-21 08:00 | 2022-03-21 09:00 | Spring | FALSE | nonsummer
2022-03-21 09:00 | 2022-03-21 10:00 | Spring | FALSE | nonsummer
2022-03-21 10:00 | 2022-03-21 11:00 | Spring | FALSE | nonsummer
2022-03-21 11:00 | 2022-03-21 12:00 | Spring | FALSE | nonsummer
2022-03-21 12:00 | 2022-03-21 13:00 | Spring | FALSE | nonsummer
2022-03-21 13:00 | 2022-03-21 14:00 | Spring | FALSE | nonsummer
2022-03-21 14:00 | 2022-03-21 15:00 | Spring | FALSE | nonsummer
2022-03-21 15:00 | 2022-03-21 16:00 | Spring | FALSE | nonsummer
2022-03-21 16:00 | 2022-03-21 17:00 | Spring | FALSE | nonsummer
2022-03-21 17:00 | 2022-03-21 18:00 | Spring | TRUE | nonsummer
2022-03-21 18:00 | 2022-03-21 19:00 | Spring | TRUE | nonsummer
2022-03-21 19:00 | 2022-03-21 20:00 | Spring | TRUE | nonsummer
2022-03-21 20:00 | 2022-03-21 21:00 | Spring | TRUE | nonsummer
2022-03-21 21:00 | 2022-03-21 22:00 | Spring | TRUE | nonsummer
2022-03-21 22:00 | 2022-03-21 23:00 | Spring | FALSE | nonsummer
2022-03-21 23:00 | 2022-03-22 | Spring | FALSE | nonsummer
2022-03-22 | 2022-03-22 01:00 | Spring | FALSE | nonsummer
2022-03-22 01:00 | 2022-03-22 02:00 | Spring | FALSE | nonsummer
2022-03-22 02:00 | 2022-03-22 03:00 | Spring | FALSE | nonsummer
2022-03-22 03:00 | 2022-03-22 04:00 | Spring | FALSE | nonsummer
2022-03-22 04:00 | 2022-03-22 05:00 | Spring | FALSE | nonsummer
2022-03-22 05:00 | 2022-03-22 06:00 | Spring | FALSE | nonsummer
2022-03-22 06:00 | 2022-03-22 07:00 | Spring | FALSE | nonsummer
2022-03-22 07:00 | 2022-03-22 08:00 | Spring | FALSE | nonsummer
2022-03-22 08:00 | 2022-03-22 09:00 | Spring | FALSE | nonsummer
2022-03-22 09:00 | 2022-03-22 10:00 | Spring | FALSE | nonsummer
2022-03-22 10:00 | 2022-03-22 11:00 | Spring | FALSE | nonsummer
2022-03-22 11:00 | 2022-03-22 12:00 | Spring | FALSE | nonsummer
2022-03-22 12:00 | 2022-03-22 13:00 | Spring | FALSE | nonsummer
2022-03-22 13:00 | 2022-03-22 14:00 | Spring | FALSE | nonsummer
2022-03-22 14:00 | 2022-03-22 15:00 | Spring | FALSE | nonsummer
2022-03-22 15:00 | 2022-03-22 16:00 | Spring | FALSE | nonsummer
2022-03-22 16:00 | 2022-03-22 17:00 | Spring | FALSE | nonsummer
2022-03-22 17:00 | 2022-03-22 18:00 | Spring | TRUE | nonsummer
2022-03-22 18:00 | 2022-03-22 19:00 | Spring | TRUE | nonsummer
2022-03-22 19:00 | 2022-03-22 20:00 | Spring | TRUE | nonsummer
2022-03-22 20:00 | 2022-03-22 21:00 | Spring | TRUE | nonsummer
2022-03-22 21:00 | 2022-03-22 22:00 | Spring | TRUE | nonsummer
2022-03-22 22:00 | 2022-03-22 23:00 | Spring | FALSE | nonsummer
2022-03-22 23:00 | 2022-03-23 | Spring | FALSE | nonsummer
2022-03-23 | 2022-03-23 01:00 | Spring | FALSE | nonsummer
2022-03-23 01:00 | 2022-03-23 02:00 | Spring | FALSE | nonsummer
2022-03-23 02:00 | 2022-03-23 03:00 | Spring | FALSE | nonsummer
2022-03-23 03:00 | 2022-03-23 04:00 | Spring | FALSE | nonsummer
2022-03-23 04:00 | 2022-03-23 05:00 | Spring | FALSE | nonsummer
2022-03-23 05:00 | 2022-03-23 06:00 | Spring | FALSE | nonsummer
2022-03-23 06:00 | 2022-03-23 07:00 | Spring | FALSE | nonsummer
2022-03-23 07:00 | 2022-03-23 08:00 | Spring | FALSE | nonsummer
2022-03-23 08:00 | 2022-03-23 09:00 | Spring | FALSE | nonsummer
2022-03-23 09:00 | 2022-03-23 10:00 | Spring | FALSE | nonsummer
2022-03-23 10:00 | 2022-03-23 11:00 | Spring | FALSE | nonsummer
2022-03-23 11:00 | 2022-03-23 12:00 | Spring | FALSE | nonsummer
2022-03-23 12:00 | 2022-03-23 13:00 | Spring | FALSE | nonsummer
2022-03-23 13:00 | 2022-03-23 14:00 | Spring | FALSE | nonsummer
2022-03-23 14:00 | 2022-03-23 15:00 | Spring | FALSE | nonsummer
2022-03-23 15:00 | 2022-03-23 16:00 | Spring | FALSE | nonsummer
2022-03-23 16:00 | 2022-03-23 17:00 | Spring | FALSE | nonsummer
2022-03-23 17:00 | 2022-03-23 18:00 | Spring | TRUE | nonsummer
2022-03-23 18:00 | 2022-03-23 19:00 | Spring | TRUE | nonsummer
2022-03-23 19:00 | 2022-03-23 20:00 | Spring | TRUE | nonsummer
2022-03-23 20:00 | 2022-03-23 21:00 | Spring | TRUE | nonsummer
2022-03-23 21:00 | 2022-03-23 22:00 | Spring | TRUE | nonsummer
2022-03-23 22:00 | 2022-03-23 23:00 | Spring | FALSE | nonsummer
2022-03-23 23:00 | 2022-03-24 | Spring | FALSE | nonsummer
2022-03-24 | 2022-03-24 01:00 | Spring | FALSE | nonsummer
2022-03-24 01:00 | 2022-03-24 02:00 | Spring | FALSE | nonsummer
2022-03-24 02:00 | 2022-03-24 03:00 | Spring | FALSE | nonsummer
2022-03-24 03:00 | 2022-03-24 04:00 | Spring | FALSE | nonsummer
2022-03-24 04:00 | 2022-03-24 05:00 | Spring | FALSE | nonsummer
2022-03-24 05:00 | 2022-03-24 06:00 | Spring | FALSE | nonsummer
2022-03-24 06:00 | 2022-03-24 07:00 | Spring | FALSE | nonsummer
2022-03-24 07:00 | 2022-03-24 08:00 | Spring | FALSE | nonsummer
2022-03-24 08:00 | 2022-03-24 09:00 | Spring | FALSE | nonsummer
2022-03-24 09:00 | 2022-03-24 10:00 | Spring | FALSE | nonsummer
2022-03-24 10:00 | 2022-03-24 11:00 | Spring | FALSE | nonsummer
2022-03-24 11:00 | 2022-03-24 12:00 | Spring | FALSE | nonsummer
2022-03-24 12:00 | 2022-03-24 13:00 | Spring | FALSE | nonsummer
2022-03-24 13:00 | 2022-03-24 14:00 | Spring | FALSE | nonsummer
2022-03-24 14:00 | 2022-03-24 15:00 | Spring | FALSE | nonsummer
2022-03-24 15:00 | 2022-03-24 16:00 | Spring | FALSE | nonsummer
2022-03-24 16:00 | 2022-03-24 17:00 | Spring | FALSE | nonsummer
2022-03-24 17:00 | 2022-03-24 18:00 | Spring | TRUE | nonsummer
2022-03-24 18:00 | 2022-03-24 19:00 | Spring | TRUE | nonsummer
2022-03-24 19:00 | 2022-03-24 20:00 | Spring | TRUE | nonsummer
2022-03-24 20:00 | 2022-03-24 21:00 | Spring | TRUE | nonsummer
2022-03-24 21:00 | 2022-03-24 22:00 | Spring | TRUE | nonsummer
2022-03-24 22:00 | 2022-03-24 23:00 | Spring | FALSE | nonsummer
2022-03-24 23:00 | 2022-03-25 | Spring | FALSE | nonsummer
2022-03-25 | 2022-03-25 01:00 | Spring | FALSE | nonsummer
2022-03-25 01:00 | 2022-03-25 02:00 | Spring | FALSE | nonsummer
2022-03-25 02:00 | 2022-03-25 03:00 | Spring | FALSE | nonsummer
2022-03-25 03:00 | 2022-03-25 04:00 | Spring | FALSE | nonsummer
2022-03-25 04:00 | 2022-03-25 05:00 | Spring | FALSE | nonsummer
2022-03-25 05:00 | 2022-03-25 06:00 | Spring | FALSE | nonsummer
2022-03-25 06:00 | 2022-03-25 07:00 | Spring | FALSE | nonsummer
2022-03-25 07:00 | 2022-03-25 08:00 | Spring | FALSE | nonsummer
2022-03-25 08:00 | 2022-03-25 09:00 | Spring | FALSE | nonsummer
2022-03-25 09:00 | 2022-03-25 10:00 | Spring | FALSE | nonsummer
2022-03-25 10:00 | 2022-03-25 11:00 | Spring | FALSE | nonsummer
2022-03-25 11:00 | 2022-03-25 12:00 | Spring | FALSE | nonsummer
2022-03-25 12:00 | 2022-03-25 13:00 | Spring | FALSE | nonsummer
2022-03-25 13:00 | 2022-03-25 14:00 | Spring | FALSE | nonsummer
2022-03-25 14:00 | 2022-03-25 15:00 | Spring | FALSE | nonsummer
2022-03-25 15:00 | 2022-03-25 16:00 | Spring | FALSE | nonsummer
2022-03-25 16:00 | 2022-03-25 17:00 | Spring | FALSE | nonsummer
2022-03-25 17:00 | 2022-03-25 18:00 | Spring | TRUE | nonsummer
2022-03-25 18:00 | 2022-03-25 19:00 | Spring | TRUE | nonsummer
2022-03-25 19:00 | 2022-03-25 20:00 | Spring | TRUE | nonsummer
2022-03-25 20:00 | 2022-03-25 21:00 | Spring | TRUE | nonsummer
2022-03-25 21:00 | 2022-03-25 22:00 | Spring | TRUE | nonsummer
2022-03-25 22:00 | 2022-03-25 23:00 | Spring | FALSE | nonsummer
2022-03-25 23:00 | 2022-03-26 | Spring | FALSE | nonsummer
2022-03-26 | 2022-03-26 01:00 | Spring | FALSE | nonsummer
2022-03-26 01:00 | 2022-03-26 02:00 | Spring | FALSE | nonsummer
2022-03-26 02:00 | 2022-03-26 03:00 | Spring | FALSE | nonsummer
2022-03-26 03:00 | 2022-03-26 04:00 | Spring | FALSE | nonsummer
2022-03-26 04:00 | 2022-03-26 05:00 | Spring | FALSE | nonsummer
2022-03-26 05:00 | 2022-03-26 06:00 | Spring | FALSE | nonsummer
2022-03-26 06:00 | 2022-03-26 07:00 | Spring | FALSE | nonsummer
2022-03-26 07:00 | 2022-03-26 08:00 | Spring | FALSE | nonsummer
2022-03-26 08:00 | 2022-03-26 09:00 | Spring | FALSE | nonsummer
2022-03-26 09:00 | 2022-03-26 10:00 | Spring | FALSE | nonsummer
2022-03-26 10:00 | 2022-03-26 11:00 | Spring | FALSE | nonsummer
2022-03-26 11:00 | 2022-03-26 12:00 | Spring | FALSE | nonsummer
2022-03-26 12:00 | 2022-03-26 13:00 | Spring | FALSE | nonsummer
2022-03-26 13:00 | 2022-03-26 14:00 | Spring | FALSE | nonsummer
2022-03-26 14:00 | 2022-03-26 15:00 | Spring | FALSE | nonsummer
2022-03-26 15:00 | 2022-03-26 16:00 | Spring | FALSE | nonsummer
2022-03-26 16:00 | 2022-03-26 17:00 | Spring | FALSE | nonsummer
2022-03-26 17:00 | 2022-03-26 18:00 | Spring | TRUE | nonsummer
2022-03-26 18:00 | 2022-03-26 19:00 | Spring | TRUE | nonsummer
2022-03-26 19:00 | 2022-03-26 20:00 | Spring | TRUE | nonsummer
2022-03-26 20:00 | 2022-03-26 21:00 | Spring | TRUE | nonsummer
2022-03-26 21:00 | 2022-03-26 22:00 | Spring | TRUE | nonsummer
2022-03-26 22:00 | 2022-03-26 23:00 | Spring | FALSE | nonsummer
2022-03-26 23:00 | 2022-03-27 | Spring | FALSE | nonsummer
2022-03-27 | 2022-03-27 01:00 | Spring | FALSE | nonsummer
2022-03-27 01:00 | 2022-03-27 02:00 | Spring | FALSE | nonsummer
2022-03-27 02:00 | 2022-03-27 03:00 | Spring | FALSE | nonsummer
2022-03-27 03:00 | 2022-03-27 04:00 | Spring | FALSE | nonsummer
2022-03-27 04:00 | 2022-03-27 05:00 | Spring | FALSE | nonsummer
2022-03-27 05:00 | 2022-03-27 06:00 | Spring | FALSE | nonsummer
2022-03-27 06:00 | 2022-03-27 07:00 | Spring | FALSE | nonsummer
2022-03-27 07:00 | 2022-03-27 08:00 | Spring | FALSE | nonsummer
2022-03-27 08:00 | 2022-03-27 09:00 | Spring | FALSE | nonsummer
2022-03-27 09:00 | 2022-03-27 10:00 | Spring | FALSE | nonsummer
2022-03-27 10:00 | 2022-03-27 11:00 | Spring | FALSE | nonsummer
2022-03-27 11:00 | 2022-03-27 12:00 | Spring | FALSE | nonsummer
2022-03-27 12:00 | 2022-03-27 13:00 | Spring | FALSE | nonsummer
2022-03-27 13:00 | 2022-03-27 14:00 | Spring | FALSE | nonsummer
2022-03-27 14:00 | 2022-03-27 15:00 | Spring | FALSE | nonsummer
2022-03-27 15:00 | 2022-03-27 16:00 | Spring | FALSE | nonsummer
2022-03-27 16:00 | 2022-03-27 17:00 | Spring | FALSE | nonsummer
2022-03-27 17:00 | 2022-03-27 18:00 | Spring | TRUE | nonsummer
2022-03-27 18:00 | 2022-03-27 19:00 | Spring | TRUE | nonsummer
2022-03-27 19:00 | 2022-03-27 20:00 | Spring | TRUE | nonsummer
2022-03-27 20:00 | 2022-03-27 21:00 | Spring | TRUE | nonsummer
2022-03-27 21:00 | 2022-03-27 22:00 | Spring | TRUE | nonsummer
2022-03-27 22:00 | 2022-03-27 23:00 | Spring | FALSE | nonsummer
2022-03-27 23:00 | 2022-03-28 | Spring | FALSE | nonsummer
2022-03-28 | 2022-03-28 01:00 | Spring | FALSE | nonsummer
2022-03-28 01:00 | 2022-03-28 02:00 | Spring | FALSE | nonsummer
2022-03-28 02:00 | 2022-03-28 03:00 | Spring | FALSE | nonsummer
2022-03-28 03:00 | 2022-03-28 04:00 | Spring | FALSE | nonsummer
2022-03-28 04:00 | 2022-03-28 05:00 | Spring | FALSE | nonsummer
2022-03-28 05:00 | 2022-03-28 06:00 | Spring | FALSE | nonsummer
2022-03-28 06:00 | 2022-03-28 07:00 | Spring | FALSE | nonsummer
2022-03-28 07:00 | 2022-03-28 08:00 | Spring | FALSE | nonsummer
2022-03-28 08:00 | 2022-03-28 09:00 | Spring | FALSE | nonsummer
2022-03-28 09:00 | 2022-03-28 10:00 | Spring | FALSE | nonsummer
2022-03-28 10:00 | 2022-03-28 11:00 | Spring | FALSE | nonsummer
2022-03-28 11:00 | 2022-03-28 12:00 | Spring | FALSE | nonsummer
2022-03-28 12:00 | 2022-03-28 13:00 | Spring | FALSE | nonsummer
2022-03-28 13:00 | 2022-03-28 14:00 | Spring | FALSE | nonsummer
2022-03-28 14:00 | 2022-03-28 15:00 | Spring | FALSE | nonsummer
2022-03-28 15:00 | 2022-03-28 16:00 | Spring | FALSE | nonsummer
2022-03-28 16:00 | 2022-03-28 17:00 | Spring | FALSE | nonsummer
2022-03-28 17:00 | 2022-03-28 18:00 | Spring | TRUE | nonsummer
2022-03-28 18:00 | 2022-03-28 19:00 | Spring | TRUE | nonsummer
2022-03-28 19:00 | 2022-03-28 20:00 | Spring | TRUE | nonsummer
2022-03-28 20:00 | 2022-03-28 21:00 | Spring | TRUE | nonsummer
2022-03-28 21:00 | 2022-03-28 22:00 | Spring | TRUE | nonsummer
2022-03-28 22:00 | 2022-03-28 23:00 | Spring | FALSE | nonsummer
2022-03-28 23:00 | 2022-03-29 | Spring | FALSE | nonsummer
2022-03-29 | 2022-03-29 01:00 | Spring | FALSE | nonsummer
2022-03-29 01:00 | 2022-03-29 02:00 | Spring | FALSE | nonsummer
2022-03-29 02:00 | 2022-03-29 03:00 | Spring | FALSE | nonsummer
2022-03-29 03:00 | 2022-03-29 04:00 | Spring | FALSE | nonsummer
2022-03-29 04:00 | 2022-03-29 05:00 | Spring | FALSE | nonsummer
2022-03-29 05:00 | 2022-03-29 06:00 | Spring | FALSE | nonsummer
2022-03-29 06:00 | 2022-03-29 07:00 | Spring | FALSE | nonsummer
2022-03-29 07:00 | 2022-03-29 08:00 | Spring | FALSE | nonsummer
2022-03-29 08:00 | 2022-03-29 09:00 | Spring | FALSE | nonsummer
2022-03-29 09:00 | 2022-03-29 10:00 | Spring | FALSE | nonsummer
2022-03-29 10:00 | 2022-03-29 11:00 | Spring | FALSE | nonsummer
2022-03-29 11:00 | 2022-03-29 12:00 | Spring | FALSE | nonsummer
2022-03-29 12:00 | 2022-03-29 13:00 | Spring | FALSE | nonsummer
2022-03-29 13:00 | 2022-03-29 14:00 | Spring | FALSE | nonsummer
2022-03-29 14:00 | 2022-03-29 15:00 | Spring | FALSE | nonsummer
2022-03-29 15:00 | 2022-03-29 16:00 | Spring | FALSE | nonsummer
2022-03-29 16:00 | 2022-03-29 17:00 | Spring | FALSE | nonsummer
2022-03-29 17:00 | 2022-03-29 18:00 | Spring | TRUE | nonsummer
2022-03-29 18:00 | 2022-03-29 19:00 | Spring | TRUE | nonsummer
2022-03-29 19:00 | 2022-03-29 20:00 | Spring | TRUE | nonsummer
2022-03-29 20:00 | 2022-03-29 21:00 | Spring | TRUE | nonsummer
2022-03-29 21:00 | 2022-03-29 22:00 | Spring | TRUE | nonsummer
2022-03-29 22:00 | 2022-03-29 23:00 | Spring | FALSE | nonsummer
2022-03-29 23:00 | 2022-03-30 | Spring | FALSE | nonsummer
2022-03-30 | 2022-03-30 01:00 | Spring | FALSE | nonsummer
2022-03-30 01:00 | 2022-03-30 02:00 | Spring | FALSE | nonsummer
2022-03-30 02:00 | 2022-03-30 03:00 | Spring | FALSE | nonsummer
2022-03-30 03:00 | 2022-03-30 04:00 | Spring | FALSE | nonsummer
2022-03-30 04:00 | 2022-03-30 05:00 | Spring | FALSE | nonsummer
2022-03-30 05:00 | 2022-03-30 06:00 | Spring | FALSE | nonsummer
2022-03-30 06:00 | 2022-03-30 07:00 | Spring | FALSE | nonsummer
2022-03-30 07:00 | 2022-03-30 08:00 | Spring | FALSE | nonsummer
2022-03-30 08:00 | 2022-03-30 09:00 | Spring | FALSE | nonsummer
2022-03-30 09:00 | 2022-03-30 10:00 | Spring | FALSE | nonsummer
2022-03-30 10:00 | 2022-03-30 11:00 | Spring | FALSE | nonsummer
2022-03-30 11:00 | 2022-03-30 12:00 | Spring | FALSE | nonsummer
2022-03-30 12:00 | 2022-03-30 13:00 | Spring | FALSE | nonsummer
2022-03-30 13:00 | 2022-03-30 14:00 | Spring | FALSE | nonsummer
2022-03-30 14:00 | 2022-03-30 15:00 | Spring | FALSE | nonsummer
2022-03-30 15:00 | 2022-03-30 16:00 | Spring | FALSE | nonsummer
2022-03-30 16:00 | 2022-03-30 17:00 | Spring | FALSE | nonsummer
2022-03-30 17:00 | 2022-03-30 18:00 | Spring | TRUE | nonsummer
2022-03-30 18:00 | 2022-03-30 19:00 | Spring | TRUE | nonsummer
2022-03-30 19:00 | 2022-03-30 20:00 | Spring | TRUE | nonsummer
2022-03-30 20:00 | 2022-03-30 21:00 | Spring | TRUE | nonsummer
2022-03-30 21:00 | 2022-03-30 22:00 | Spring | TRUE | nonsummer
2022-03-30 22:00 | 2022-03-30 23:00 | Spring | FALSE | nonsummer
2022-03-30 23:00 | 2022-03-31 | Spring | FALSE | nonsummer
2022-03-31 | 2022-03-31 01:00 | Spring | FALSE | nonsummer
2022-03-31 01:00 | 2022-03-31 02:00 | Spring | FALSE | nonsummer
2022-03-31 02:00 | 2022-03-31 03:00 | Spring | FALSE | nonsummer
2022-03-31 03:00 | 2022-03-31 04:00 | Spring | FALSE | nonsummer
2022-03-31 04:00 | 2022-03-31 05:00 | Spring | FALSE | nonsummer
2022-03-31 05:00 | 2022-03-31 06:00 | Spring | FALSE | nonsummer
2022-03-31 06:00 | 2022-03-31 07:00 | Spring | FALSE | nonsummer
2022-03-31 07:00 | 2022-03-31 08:00 | Spring | FALSE | nonsummer
2022-03-31 08:00 | 2022-03-31 09:00 | Spring | FALSE | nonsummer
2022-03-31 09:00 | 2022-03-31 10:00 | Spring | FALSE | nonsummer
2022-03-31 10:00 | 2022-03-31 11:00 | Spring | FALSE | nonsummer
2022-03-31 11:00 | 2022-03-31 12:00 | Spring | FALSE | nonsummer
2022-03-31 12:00 | 2022-03-31 13:00 | Spring | FALSE | nonsummer
2022-03-31 13:00 | 2022-03-31 14:00 | Spring | FALSE | nonsummer
2022-03-31 14:00 | 2022-03-31 15:00 | Spring | FALSE | nonsummer
2022-03-31 15:00 | 2022-03-31 16:00 | Spring | FALSE | nonsummer
2022-03-31 16:00 | 2022-03-31 17:00 | Spring | FALSE | nonsummer
2022-03-31 17:00 | 2022-03-31 18:00 | Spring | TRUE | nonsummer
2022-03-31 18:00 | 2022-03-31 19:00 | Spring | TRUE | nonsummer
2022-03-31 19:00 | 2022-03-31 20:00 | Spring | TRUE | nonsummer
2022-03-31 20:00 | 2022-03-31 21:00 | Spring | TRUE | nonsummer
2022-03-31 21:00 | 2022-03-31 22:00 | Spring | TRUE | nonsummer
2022-03-31 22:00 | 2022-03-31 23:00 | Spring | FALSE | nonsummer
2022-03-31 23:00 | 2022-04-01 | Spring | FALSE | nonsummer
2022-04-01 | 2022-04-01 01:00 | Spring | FALSE | nonsummer
2022-04-01 01:00 | 2022-04-01 02:00 | Spring | FALSE | nonsummer
2022-04-01 02:00 | 2022-04-01 03:00 | Spring | FALSE | nonsummer
2022-04-01 03:00 | 2022-04-01 04:00 | Spring | FALSE | nonsummer
2022-04-01 04:00 | 2022-04-01 05:00 | Spring | FALSE | nonsummer
2022-04-01 05:00 | 2022-04-01 06:00 | Spring | FALSE | nonsummer
2022-04-01 06:00 | 2022-04-01 07:00 | Spring | FALSE | nonsummer
2022-04-01 07:00 | 2022-04-01 08:00 | Spring | FALSE | nonsummer
2022-04-01 08:00 | 2022-04-01 09:00 | Spring | FALSE | nonsummer
2022-04-01 09:00 | 2022-04-01 10:00 | Spring | FALSE | nonsummer
2022-04-01 10:00 | 2022-04-01 11:00 | Spring | FALSE | nonsummer
2022-04-01 11:00 | 2022-04-01 12:00 | Spring | FALSE | nonsummer
2022-04-01 12:00 | 2022-04-01 13:00 | Spring | FALSE | nonsummer
2022-04-01 13:00 | 2022-04-01 14:00 | Spring | FALSE | nonsummer
2022-04-01 14:00 | 2022-04-01 15:00 | Spring | FALSE | nonsummer
2022-04-01 15:00 | 2022-04-01 16:00 | Spring | FALSE | nonsummer
2022-04-01 16:00 | 2022-04-01 17:00 | Spring | FALSE | nonsummer
2022-04-01 17:00 | 2022-04-01 18:00 | Spring | TRUE | nonsummer
2022-04-01 18:00 | 2022-04-01 19:00 | Spring | TRUE | nonsummer
2022-04-01 19:00 | 2022-04-01 20:00 | Spring | TRUE | nonsummer
2022-04-01 20:00 | 2022-04-01 21:00 | Spring | TRUE | nonsummer
2022-04-01 21:00 | 2022-04-01 22:00 | Spring | TRUE | nonsummer
2022-04-01 22:00 | 2022-04-01 23:00 | Spring | FALSE | nonsummer
2022-04-01 23:00 | 2022-04-02 | Spring | FALSE | nonsummer
2022-04-02 | 2022-04-02 01:00 | Spring | FALSE | nonsummer
2022-04-02 01:00 | 2022-04-02 02:00 | Spring | FALSE | nonsummer
2022-04-02 02:00 | 2022-04-02 03:00 | Spring | FALSE | nonsummer
2022-04-02 03:00 | 2022-04-02 04:00 | Spring | FALSE | nonsummer
2022-04-02 04:00 | 2022-04-02 05:00 | Spring | FALSE | nonsummer
2022-04-02 05:00 | 2022-04-02 06:00 | Spring | FALSE | nonsummer
2022-04-02 06:00 | 2022-04-02 07:00 | Spring | FALSE | nonsummer
2022-04-02 07:00 | 2022-04-02 08:00 | Spring | FALSE | nonsummer
2022-04-02 08:00 | 2022-04-02 09:00 | Spring | FALSE | nonsummer
2022-04-02 09:00 | 2022-04-02 10:00 | Spring | FALSE | nonsummer
2022-04-02 10:00 | 2022-04-02 11:00 | Spring | FALSE | nonsummer
2022-04-02 11:00 | 2022-04-02 12:00 | Spring | FALSE | nonsummer
2022-04-02 12:00 | 2022-04-02 13:00 | Spring | FALSE | nonsummer
2022-04-02 13:00 | 2022-04-02 14:00 | Spring | FALSE | nonsummer
2022-04-02 14:00 | 2022-04-02 15:00 | Spring | FALSE | nonsummer
2022-04-02 15:00 | 2022-04-02 16:00 | Spring | FALSE | nonsummer
2022-04-02 16:00 | 2022-04-02 17:00 | Spring | FALSE | nonsummer
2022-04-02 17:00 | 2022-04-02 18:00 | Spring | TRUE | nonsummer
2022-04-02 18:00 | 2022-04-02 19:00 | Spring | TRUE | nonsummer
2022-04-02 19:00 | 2022-04-02 20:00 | Spring | TRUE | nonsummer
2022-04-02 20:00 | 2022-04-02 21:00 | Spring | TRUE | nonsummer
2022-04-02 21:00 | 2022-04-02 22:00 | Spring | TRUE | nonsummer
2022-04-02 22:00 | 2022-04-02 23:00 | Spring | FALSE | nonsummer
2022-04-02 23:00 | 2022-04-03 | Spring | FALSE | nonsummer
2022-04-03 | 2022-04-03 01:00 | Spring | FALSE | nonsummer
2022-04-03 01:00 | 2022-04-03 02:00 | Spring | FALSE | nonsummer
2022-04-03 02:00 | 2022-04-03 03:00 | Spring | FALSE | nonsummer
2022-04-03 03:00 | 2022-04-03 04:00 | Spring | FALSE | nonsummer
2022-04-03 04:00 | 2022-04-03 05:00 | Spring | FALSE | nonsummer
2022-04-03 05:00 | 2022-04-03 06:00 | Spring | FALSE | nonsummer
2022-04-03 06:00 | 2022-04-03 07:00 | Spring | FALSE | nonsummer
2022-04-03 07:00 | 2022-04-03 08:00 | Spring | FALSE | nonsummer
2022-04-03 08:00 | 2022-04-03 09:00 | Spring | FALSE | nonsummer
2022-04-03 09:00 | 2022-04-03 10:00 | Spring | FALSE | nonsummer
2022-04-03 10:00 | 2022-04-03 11:00 | Spring | FALSE | nonsummer
2022-04-03 11:00 | 2022-04-03 12:00 | Spring | FALSE | nonsummer
2022-04-03 12:00 | 2022-04-03 13:00 | Spring | FALSE | nonsummer
2022-04-03 13:00 | 2022-04-03 14:00 | Spring | FALSE | nonsummer
2022-04-03 14:00 | 2022-04-03 15:00 | Spring | FALSE | nonsummer
2022-04-03 15:00 | 2022-04-03 16:00 | Spring | FALSE | nonsummer
2022-04-03 16:00 | 2022-04-03 17:00 | Spring | FALSE | nonsummer
2022-04-03 17:00 | 2022-04-03 18:00 | Spring | TRUE | nonsummer
2022-04-03 18:00 | 2022-04-03 19:00 | Spring | TRUE | nonsummer
2022-04-03 19:00 | 2022-04-03 20:00 | Spring | TRUE | nonsummer
2022-04-03 20:00 | 2022-04-03 21:00 | Spring | TRUE | nonsummer
2022-04-03 21:00 | 2022-04-03 22:00 | Spring | TRUE | nonsummer
2022-04-03 22:00 | 2022-04-03 23:00 | Spring | FALSE | nonsummer
2022-04-03 23:00 | 2022-04-04 | Spring | FALSE | nonsummer
2022-04-04 | 2022-04-04 01:00 | Spring | FALSE | nonsummer
2022-04-04 01:00 | 2022-04-04 02:00 | Spring | FALSE | nonsummer
2022-04-04 02:00 | 2022-04-04 03:00 | Spring | FALSE | nonsummer
2022-04-04 03:00 | 2022-04-04 04:00 | Spring | FALSE | nonsummer
2022-04-04 04:00 | 2022-04-04 05:00 | Spring | FALSE | nonsummer
2022-04-04 05:00 | 2022-04-04 06:00 | Spring | FALSE | nonsummer
2022-04-04 06:00 | 2022-04-04 07:00 | Spring | FALSE | nonsummer
2022-04-04 07:00 | 2022-04-04 08:00 | Spring | FALSE | nonsummer
2022-04-04 08:00 | 2022-04-04 09:00 | Spring | FALSE | nonsummer
2022-04-04 09:00 | 2022-04-04 10:00 | Spring | FALSE | nonsummer
2022-04-04 10:00 | 2022-04-04 11:00 | Spring | FALSE | nonsummer
2022-04-04 11:00 | 2022-04-04 12:00 | Spring | FALSE | nonsummer
2022-04-04 12:00 | 2022-04-04 13:00 | Spring | FALSE | nonsummer
2022-04-04 13:00 | 2022-04-04 14:00 | Spring | FALSE | nonsummer
2022-04-04 14:00 | 2022-04-04 15:00 | Spring | FALSE | nonsummer
2022-04-04 15:00 | 2022-04-04 16:00 | Spring | FALSE | nonsummer
2022-04-04 16:00 | 2022-04-04 17:00 | Spring | FALSE | nonsummer
2022-04-04 17:00 | 2022-04-04 18:00 | Spring | TRUE | nonsummer
2022-04-04 18:00 | 2022-04-04 19:00 | Spring | TRUE | nonsummer
2022-04-04 19:00 | 2022-04-04 20:00 | Spring | TRUE | nonsummer
2022-04-04 20:00 | 2022-04-04 21:00 | Spring | TRUE | nonsummer
2022-04-04 21:00 | 2022-04-04 22:00 | Spring | TRUE | nonsummer
2022-04-04 22:00 | 2022-04-04 23:00 | Spring | FALSE | nonsummer
2022-04-04 23:00 | 2022-04-05 | Spring | FALSE | nonsummer
2022-04-05 | 2022-04-05 01:00 | Spring | FALSE | nonsummer
2022-04-05 01:00 | 2022-04-05 02:00 | Spring | FALSE | nonsummer
2022-04-05 02:00 | 2022-04-05 03:00 | Spring | FALSE | nonsummer
2022-04-05 03:00 | 2022-04-05 04:00 | Spring | FALSE | nonsummer
2022-04-05 04:00 | 2022-04-05 05:00 | Spring | FALSE | nonsummer
2022-04-05 05:00 | 2022-04-05 06:00 | Spring | FALSE | nonsummer
2022-04-05 06:00 | 2022-04-05 07:00 | Spring | FALSE | nonsummer
2022-04-05 07:00 | 2022-04-05 08:00 | Spring | FALSE | nonsummer
2022-04-05 08:00 | 2022-04-05 09:00 | Spring | FALSE | nonsummer
2022-04-05 09:00 | 2022-04-05 10:00 | Spring | FALSE | nonsummer
2022-04-05 10:00 | 2022-04-05 11:00 | Spring | FALSE | nonsummer
2022-04-05 11:00 | 2022-04-05 12:00 | Spring | FALSE | nonsummer
2022-04-05 12:00 | 2022-04-05 13:00 | Spring | FALSE | nonsummer
2022-04-05 13:00 | 2022-04-05 14:00 | Spring | FALSE | nonsummer
2022-04-05 14:00 | 2022-04-05 15:00 | Spring | FALSE | nonsummer
2022-04-05 15:00 | 2022-04-05 16:00 | Spring | FALSE | nonsummer
2022-04-05 16:00 | 2022-04-05 17:00 | Spring | FALSE | nonsummer
2022-04-05 17:00 | 2022-04-05 18:00 | Spring | TRUE | nonsummer
2022-04-05 18:00 | 2022-04-05 19:00 | Spring | TRUE | nonsummer
2022-04-05 19:00 | 2022-04-05 20:00 | Spring | TRUE | nonsummer
2022-04-05 20:00 | 2022-04-05 21:00 | Spring | TRUE | nonsummer
2022-04-05 21:00 | 2022-04-05 22:00 | Spring | TRUE | nonsummer
2022-04-05 22:00 | 2022-04-05 23:00 | Spring | FALSE | nonsummer
2022-04-05 23:00 | 2022-04-06 | Spring | FALSE | nonsummer
2022-04-06 | 2022-04-06 01:00 | Spring | FALSE | nonsummer
2022-04-06 01:00 | 2022-04-06 02:00 | Spring | FALSE | nonsummer
2022-04-06 02:00 | 2022-04-06 03:00 | Spring | FALSE | nonsummer
2022-04-06 03:00 | 2022-04-06 04:00 | Spring | FALSE | nonsummer
2022-04-06 04:00 | 2022-04-06 05:00 | Spring | FALSE | nonsummer
2022-04-06 05:00 | 2022-04-06 06:00 | Spring | FALSE | nonsummer
2022-04-06 06:00 | 2022-04-06 07:00 | Spring | FALSE | nonsummer
2022-04-06 07:00 | 2022-04-06 08:00 | Spring | FALSE | nonsummer
2022-04-06 08:00 | 2022-04-06 09:00 | Spring | FALSE | nonsummer
2022-04-06 09:00 | 2022-04-06 10:00 | Spring | FALSE | nonsummer
2022-04-06 10:00 | 2022-04-06 11:00 | Spring | FALSE | nonsummer
2022-04-06 11:00 | 2022-04-06 12:00 | Spring | FALSE | nonsummer
2022-04-06 12:00 | 2022-04-06 13:00 | Spring | FALSE | nonsummer
2022-04-06 13:00 | 2022-04-06 14:00 | Spring | FALSE | nonsummer
2022-04-06 14:00 | 2022-04-06 15:00 | Spring | FALSE | nonsummer
2022-04-06 15:00 | 2022-04-06 16:00 | Spring | FALSE | nonsummer
2022-04-06 16:00 | 2022-04-06 17:00 | Spring | FALSE | nonsummer
2022-04-06 17:00 | 2022-04-06 18:00 | Spring | TRUE | nonsummer
2022-04-06 18:00 | 2022-04-06 19:00 | Spring | TRUE | nonsummer
2022-04-06 19:00 | 2022-04-06 20:00 | Spring | TRUE | nonsummer
2022-04-06 20:00 | 2022-04-06 21:00 | Spring | TRUE | nonsummer
2022-04-06 21:00 | 2022-04-06 22:00 | Spring | TRUE | nonsummer
2022-04-06 22:00 | 2022-04-06 23:00 | Spring | FALSE | nonsummer
2022-04-06 23:00 | 2022-04-07 | Spring | FALSE | nonsummer
2022-04-07 | 2022-04-07 01:00 | Spring | FALSE | nonsummer
2022-04-07 01:00 | 2022-04-07 02:00 | Spring | FALSE | nonsummer
2022-04-07 02:00 | 2022-04-07 03:00 | Spring | FALSE | nonsummer
2022-04-07 03:00 | 2022-04-07 04:00 | Spring | FALSE | nonsummer
2022-04-07 04:00 | 2022-04-07 05:00 | Spring | FALSE | nonsummer
2022-04-07 05:00 | 2022-04-07 06:00 | Spring | FALSE | nonsummer
2022-04-07 06:00 | 2022-04-07 07:00 | Spring | FALSE | nonsummer
2022-04-07 07:00 | 2022-04-07 08:00 | Spring | FALSE | nonsummer
2022-04-07 08:00 | 2022-04-07 09:00 | Spring | FALSE | nonsummer
2022-04-07 09:00 | 2022-04-07 10:00 | Spring | FALSE | nonsummer
2022-04-07 10:00 | 2022-04-07 11:00 | Spring | FALSE | nonsummer
2022-04-07 11:00 | 2022-04-07 12:00 | Spring | FALSE | nonsummer
2022-04-07 12:00 | 2022-04-07 13:00 | Spring | FALSE | nonsummer
2022-04-07 13:00 | 2022-04-07 14:00 | Spring | FALSE | nonsummer
2022-04-07 14:00 | 2022-04-07 15:00 | Spring | FALSE | nonsummer
2022-04-07 15:00 | 2022-04-07 16:00 | Spring | FALSE | nonsummer
2022-04-07 16:00 | 2022-04-07 17:00 | Spring | FALSE | nonsummer
2022-04-07 17:00 | 2022-04-07 18:00 | Spring | TRUE | nonsummer
2022-04-07 18:00 | 2022-04-07 19:00 | Spring | TRUE | nonsummer
2022-04-07 19:00 | 2022-04-07 20:00 | Spring | TRUE | nonsummer
2022-04-07 20:00 | 2022-04-07 21:00 | Spring | TRUE | nonsummer
2022-04-07 21:00 | 2022-04-07 22:00 | Spring | TRUE | nonsummer
2022-04-07 22:00 | 2022-04-07 23:00 | Spring | FALSE | nonsummer
2022-04-07 23:00 | 2022-04-08 | Spring | FALSE | nonsummer
2022-04-08 | 2022-04-08 01:00 | Spring | FALSE | nonsummer
2022-04-08 01:00 | 2022-04-08 02:00 | Spring | FALSE | nonsummer
2022-04-08 02:00 | 2022-04-08 03:00 | Spring | FALSE | nonsummer
2022-04-08 03:00 | 2022-04-08 04:00 | Spring | FALSE | nonsummer
2022-04-08 04:00 | 2022-04-08 05:00 | Spring | FALSE | nonsummer
2022-04-08 05:00 | 2022-04-08 06:00 | Spring | FALSE | nonsummer
2022-04-08 06:00 | 2022-04-08 07:00 | Spring | FALSE | nonsummer
2022-04-08 07:00 | 2022-04-08 08:00 | Spring | FALSE | nonsummer
2022-04-08 08:00 | 2022-04-08 09:00 | Spring | FALSE | nonsummer
2022-04-08 09:00 | 2022-04-08 10:00 | Spring | FALSE | nonsummer
2022-04-08 10:00 | 2022-04-08 11:00 | Spring | FALSE | nonsummer
2022-04-08 11:00 | 2022-04-08 12:00 | Spring | FALSE | nonsummer
2022-04-08 12:00 | 2022-04-08 13:00 | Spring | FALSE | nonsummer
2022-04-08 13:00 | 2022-04-08 14:00 | Spring | FALSE | nonsummer
2022-04-08 14:00 | 2022-04-08 15:00 | Spring | FALSE | nonsummer
2022-04-08 15:00 | 2022-04-08 16:00 | Spring | FALSE | nonsummer
2022-04-08 16:00 | 2022-04-08 17:00 | Spring | FALSE | nonsummer
2022-04-08 17:00 | 2022-04-08 18:00 | Spring | TRUE | nonsummer
2022-04-08 18:00 | 2022-04-08 19:00 | Spring | TRUE | nonsummer
2022-04-08 19:00 | 2022-04-08 20:00 | Spring | TRUE | nonsummer
2022-04-08 20:00 | 2022-04-08 21:00 | Spring | TRUE | nonsummer
2022-04-08 21:00 | 2022-04-08 22:00 | Spring | TRUE | nonsummer
2022-04-08 22:00 | 2022-04-08 23:00 | Spring | FALSE | nonsummer
2022-04-08 23:00 | 2022-04-09 | Spring | FALSE | nonsummer
2022-04-09 | 2022-04-09 01:00 | Spring | FALSE | nonsummer
2022-04-09 01:00 | 2022-04-09 02:00 | Spring | FALSE | nonsummer
2022-04-09 02:00 | 2022-04-09 03:00 | Spring | FALSE | nonsummer
2022-04-09 03:00 | 2022-04-09 04:00 | Spring | FALSE | nonsummer
2022-04-09 04:00 | 2022-04-09 05:00 | Spring | FALSE | nonsummer
2022-04-09 05:00 | 2022-04-09 06:00 | Spring | FALSE | nonsummer
2022-04-09 06:00 | 2022-04-09 07:00 | Spring | FALSE | nonsummer
2022-04-09 07:00 | 2022-04-09 08:00 | Spring | FALSE | nonsummer
2022-04-09 08:00 | 2022-04-09 09:00 | Spring | FALSE | nonsummer
2022-04-09 09:00 | 2022-04-09 10:00 | Spring | FALSE | nonsummer
2022-04-09 10:00 | 2022-04-09 11:00 | Spring | FALSE | nonsummer
2022-04-09 11:00 | 2022-04-09 12:00 | Spring | FALSE | nonsummer
2022-04-09 12:00 | 2022-04-09 13:00 | Spring | FALSE | nonsummer
2022-04-09 13:00 | 2022-04-09 14:00 | Spring | FALSE | nonsummer
2022-04-09 14:00 | 2022-04-09 15:00 | Spring | FALSE | nonsummer
2022-04-09 15:00 | 2022-04-09 16:00 | Spring | FALSE | nonsummer
2022-04-09 16:00 | 2022-04-09 17:00 | Spring | FALSE | nonsummer
2022-04-09 17:00 | 2022-04-09 18:00 | Spring | TRUE | nonsummer
2022-04-09 18:00 | 2022-04-09 19:00 | Spring | TRUE | nonsummer
2022-04-09 19:00 | 2022-04-09 20:00 | Spring | TRUE | nonsummer
2022-04-09 20:00 | 2022-04-09 21:00 | Spring | TRUE | nonsummer
2022-04-09 21:00 | 2022-04-09 22:00 | Spring | TRUE | nonsummer
2022-04-09 22:00 | 2022-04-09 23:00 | Spring | FALSE | nonsummer
2022-04-09 23:00 | 2022-04-10 | Spring | FALSE | nonsummer
2022-04-10 | 2022-04-10 01:00 | Spring | FALSE | nonsummer
2022-04-10 01:00 | 2022-04-10 02:00 | Spring | FALSE | nonsummer
2022-04-10 02:00 | 2022-04-10 03:00 | Spring | FALSE | nonsummer
2022-04-10 03:00 | 2022-04-10 04:00 | Spring | FALSE | nonsummer
2022-04-10 04:00 | 2022-04-10 05:00 | Spring | FALSE | nonsummer
2022-04-10 05:00 | 2022-04-10 06:00 | Spring | FALSE | nonsummer
2022-04-10 06:00 | 2022-04-10 07:00 | Spring | FALSE | nonsummer
2022-04-10 07:00 | 2022-04-10 08:00 | Spring | FALSE | nonsummer
2022-04-10 08:00 | 2022-04-10 09:00 | Spring | FALSE | nonsummer
2022-04-10 09:00 | 2022-04-10 10:00 | Spring | FALSE | nonsummer
2022-04-10 10:00 | 2022-04-10 11:00 | Spring | FALSE | nonsummer
2022-04-10 11:00 | 2022-04-10 12:00 | Spring | FALSE | nonsummer
2022-04-10 12:00 | 2022-04-10 13:00 | Spring | FALSE | nonsummer
2022-04-10 13:00 | 2022-04-10 14:00 | Spring | FALSE | nonsummer
2022-04-10 14:00 | 2022-04-10 15:00 | Spring | FALSE | nonsummer
2022-04-10 15:00 | 2022-04-10 16:00 | Spring | FALSE | nonsummer
2022-04-10 16:00 | 2022-04-10 17:00 | Spring | FALSE | nonsummer
2022-04-10 17:00 | 2022-04-10 18:00 | Spring | TRUE | nonsummer
2022-04-10 18:00 | 2022-04-10 19:00 | Spring | TRUE | nonsummer
2022-04-10 19:00 | 2022-04-10 20:00 | Spring | TRUE | nonsummer
2022-04-10 20:00 | 2022-04-10 21:00 | Spring | TRUE | nonsummer
2022-04-10 21:00 | 2022-04-10 22:00 | Spring | TRUE | nonsummer
2022-04-10 22:00 | 2022-04-10 23:00 | Spring | FALSE | nonsummer
2022-04-10 23:00 | 2022-04-11 | Spring | FALSE | nonsummer
2022-04-11 | 2022-04-11 01:00 | Spring | FALSE | nonsummer
2022-04-11 01:00 | 2022-04-11 02:00 | Spring | FALSE | nonsummer
2022-04-11 02:00 | 2022-04-11 03:00 | Spring | FALSE | nonsummer
2022-04-11 03:00 | 2022-04-11 04:00 | Spring | FALSE | nonsummer
2022-04-11 04:00 | 2022-04-11 05:00 | Spring | FALSE | nonsummer
2022-04-11 05:00 | 2022-04-11 06:00 | Spring | FALSE | nonsummer
2022-04-11 06:00 | 2022-04-11 07:00 | Spring | FALSE | nonsummer
2022-04-11 07:00 | 2022-04-11 08:00 | Spring | FALSE | nonsummer
2022-04-11 08:00 | 2022-04-11 09:00 | Spring | FALSE | nonsummer
2022-04-11 09:00 | 2022-04-11 10:00 | Spring | FALSE | nonsummer
2022-04-11 10:00 | 2022-04-11 11:00 | Spring | FALSE | nonsummer
2022-04-11 11:00 | 2022-04-11 12:00 | Spring | FALSE | nonsummer
2022-04-11 12:00 | 2022-04-11 13:00 | Spring | FALSE | nonsummer
2022-04-11 13:00 | 2022-04-11 14:00 | Spring | FALSE | nonsummer
2022-04-11 14:00 | 2022-04-11 15:00 | Spring | FALSE | nonsummer
2022-04-11 15:00 | 2022-04-11 16:00 | Spring | FALSE | nonsummer
2022-04-11 16:00 | 2022-04-11 17:00 | Spring | FALSE | nonsummer
2022-04-11 17:00 | 2022-04-11 18:00 | Spring | TRUE | nonsummer
2022-04-11 18:00 | 2022-04-11 19:00 | Spring | TRUE | nonsummer
2022-04-11 19:00 | 2022-04-11 20:00 | Spring | TRUE | nonsummer
2022-04-11 20:00 | 2022-04-11 21:00 | Spring | TRUE | nonsummer
2022-04-11 21:00 | 2022-04-11 22:00 | Spring | TRUE | nonsummer
2022-04-11 22:00 | 2022-04-11 23:00 | Spring | FALSE | nonsummer
2022-04-11 23:00 | 2022-04-12 | Spring | FALSE | nonsummer
2022-04-12 | 2022-04-12 01:00 | Spring | FALSE | nonsummer
2022-04-12 01:00 | 2022-04-12 02:00 | Spring | FALSE | nonsummer
2022-04-12 02:00 | 2022-04-12 03:00 | Spring | FALSE | nonsummer
2022-04-12 03:00 | 2022-04-12 04:00 | Spring | FALSE | nonsummer
2022-04-12 04:00 | 2022-04-12 05:00 | Spring | FALSE | nonsummer
2022-04-12 05:00 | 2022-04-12 06:00 | Spring | FALSE | nonsummer
2022-04-12 06:00 | 2022-04-12 07:00 | Spring | FALSE | nonsummer
2022-04-12 07:00 | 2022-04-12 08:00 | Spring | FALSE | nonsummer
2022-04-12 08:00 | 2022-04-12 09:00 | Spring | FALSE | nonsummer
2022-04-12 09:00 | 2022-04-12 10:00 | Spring | FALSE | nonsummer
2022-04-12 10:00 | 2022-04-12 11:00 | Spring | FALSE | nonsummer
2022-04-12 11:00 | 2022-04-12 12:00 | Spring | FALSE | nonsummer
2022-04-12 12:00 | 2022-04-12 13:00 | Spring | FALSE | nonsummer
2022-04-12 13:00 | 2022-04-12 14:00 | Spring | FALSE | nonsummer
2022-04-12 14:00 | 2022-04-12 15:00 | Spring | FALSE | nonsummer
2022-04-12 15:00 | 2022-04-12 16:00 | Spring | FALSE | nonsummer
2022-04-12 16:00 | 2022-04-12 17:00 | Spring | FALSE | nonsummer
2022-04-12 17:00 | 2022-04-12 18:00 | Spring | TRUE | nonsummer
2022-04-12 18:00 | 2022-04-12 19:00 | Spring | TRUE | nonsummer
2022-04-12 19:00 | 2022-04-12 20:00 | Spring | TRUE | nonsummer
2022-04-12 20:00 | 2022-04-12 21:00 | Spring | TRUE | nonsummer
2022-04-12 21:00 | 2022-04-12 22:00 | Spring | TRUE | nonsummer
2022-04-12 22:00 | 2022-04-12 23:00 | Spring | FALSE | nonsummer
2022-04-12 23:00 | 2022-04-13 | Spring | FALSE | nonsummer
2022-04-13 | 2022-04-13 01:00 | Spring | FALSE | nonsummer
2022-04-13 01:00 | 2022-04-13 02:00 | Spring | FALSE | nonsummer
2022-04-13 02:00 | 2022-04-13 03:00 | Spring | FALSE | nonsummer
2022-04-13 03:00 | 2022-04-13 04:00 | Spring | FALSE | nonsummer
2022-04-13 04:00 | 2022-04-13 05:00 | Spring | FALSE | nonsummer
2022-04-13 05:00 | 2022-04-13 06:00 | Spring | FALSE | nonsummer
2022-04-13 06:00 | 2022-04-13 07:00 | Spring | FALSE | nonsummer
2022-04-13 07:00 | 2022-04-13 08:00 | Spring | FALSE | nonsummer
2022-04-13 08:00 | 2022-04-13 09:00 | Spring | FALSE | nonsummer
2022-04-13 09:00 | 2022-04-13 10:00 | Spring | FALSE | nonsummer
2022-04-13 10:00 | 2022-04-13 11:00 | Spring | FALSE | nonsummer
2022-04-13 11:00 | 2022-04-13 12:00 | Spring | FALSE | nonsummer
2022-04-13 12:00 | 2022-04-13 13:00 | Spring | FALSE | nonsummer
2022-04-13 13:00 | 2022-04-13 14:00 | Spring | FALSE | nonsummer
2022-04-13 14:00 | 2022-04-13 15:00 | Spring | FALSE | nonsummer
2022-04-13 15:00 | 2022-04-13 16:00 | Spring | FALSE | nonsummer
2022-04-13 16:00 | 2022-04-13 17:00 | Spring | FALSE | nonsummer
2022-04-13 17:00 | 2022-04-13 18:00 | Spring | TRUE | nonsummer
2022-04-13 18:00 | 2022-04-13 19:00 | Spring | TRUE | nonsummer
2022-04-13 19:00 | 2022-04-13 20:00 | Spring | TRUE | nonsummer
2022-04-13 20:00 | 2022-04-13 21:00 | Spring | TRUE | nonsummer
2022-04-13 21:00 | 2022-04-13 22:00 | Spring | TRUE | nonsummer
2022-04-13 22:00 | 2022-04-13 23:00 | Spring | FALSE | nonsummer
2022-04-13 23:00 | 2022-04-14 | Spring | FALSE | nonsummer
2022-04-14 | 2022-04-14 01:00 | Spring | FALSE | nonsummer
2022-04-14 01:00 | 2022-04-14 02:00 | Spring | FALSE | nonsummer
2022-04-14 02:00 | 2022-04-14 03:00 | Spring | FALSE | nonsummer
2022-04-14 03:00 | 2022-04-14 04:00 | Spring | FALSE | nonsummer
2022-04-14 04:00 | 2022-04-14 05:00 | Spring | FALSE | nonsummer
2022-04-14 05:00 | 2022-04-14 06:00 | Spring | FALSE | nonsummer
2022-04-14 06:00 | 2022-04-14 07:00 | Spring | FALSE | nonsummer
2022-04-14 07:00 | 2022-04-14 08:00 | Spring | FALSE | nonsummer
2022-04-14 08:00 | 2022-04-14 09:00 | Spring | FALSE | nonsummer
2022-04-14 09:00 | 2022-04-14 10:00 | Spring | FALSE | nonsummer
2022-04-14 10:00 | 2022-04-14 11:00 | Spring | FALSE | nonsummer
2022-04-14 11:00 | 2022-04-14 12:00 | Spring | FALSE | nonsummer
2022-04-14 12:00 | 2022-04-14 13:00 | Spring | FALSE | nonsummer
2022-04-14 13:00 | 2022-04-14 14:00 | Spring | FALSE | nonsummer
2022-04-14 14:00 | 2022-04-14 15:00 | Spring | FALSE | nonsummer
2022-04-14 15:00 | 2022-04-14 16:00 | Spring | FALSE | nonsummer
2022-04-14 16:00 | 2022-04-14 17:00 | Spring | FALSE | nonsummer
2022-04-14 17:00 | 2022-04-14 18:00 | Spring | TRUE | nonsummer
2022-04-14 18:00 | 2022-04-14 19:00 | Spring | TRUE | nonsummer
2022-04-14 19:00 | 2022-04-14 20:00 | Spring | TRUE | nonsummer
2022-04-14 20:00 | 2022-04-14 21:00 | Spring | TRUE | nonsummer
2022-04-14 21:00 | 2022-04-14 22:00 | Spring | TRUE | nonsummer
2022-04-14 22:00 | 2022-04-14 23:00 | Spring | FALSE | nonsummer
2022-04-14 23:00 | 2022-04-15 | Spring | FALSE | nonsummer
2022-04-15 | 2022-04-15 01:00 | Spring | FALSE | nonsummer
2022-04-15 01:00 | 2022-04-15 02:00 | Spring | FALSE | nonsummer
2022-04-15 02:00 | 2022-04-15 03:00 | Spring | FALSE | nonsummer
2022-04-15 03:00 | 2022-04-15 04:00 | Spring | FALSE | nonsummer
2022-04-15 04:00 | 2022-04-15 05:00 | Spring | FALSE | nonsummer
2022-04-15 05:00 | 2022-04-15 06:00 | Spring | FALSE | nonsummer
2022-04-15 06:00 | 2022-04-15 07:00 | Spring | FALSE | nonsummer
2022-04-15 07:00 | 2022-04-15 08:00 | Spring | FALSE | nonsummer
2022-04-15 08:00 | 2022-04-15 09:00 | Spring | FALSE | nonsummer
2022-04-15 09:00 | 2022-04-15 10:00 | Spring | FALSE | nonsummer
2022-04-15 10:00 | 2022-04-15 11:00 | Spring | FALSE | nonsummer
2022-04-15 11:00 | 2022-04-15 12:00 | Spring | FALSE | nonsummer
2022-04-15 12:00 | 2022-04-15 13:00 | Spring | FALSE | nonsummer
2022-04-15 13:00 | 2022-04-15 14:00 | Spring | FALSE | nonsummer
2022-04-15 14:00 | 2022-04-15 15:00 | Spring | FALSE | nonsummer
2022-04-15 15:00 | 2022-04-15 16:00 | Spring | FALSE | nonsummer
2022-04-15 16:00 | 2022-04-15 17:00 | Spring | FALSE | nonsummer
2022-04-15 17:00 | 2022-04-15 18:00 | Spring | TRUE | nonsummer
2022-04-15 18:00 | 2022-04-15 19:00 | Spring | TRUE | nonsummer
2022-04-15 19:00 | 2022-04-15 20:00 | Spring | TRUE | nonsummer
2022-04-15 20:00 | 2022-04-15 21:00 | Spring | TRUE | nonsummer
2022-04-15 21:00 | 2022-04-15 22:00 | Spring | TRUE | nonsummer
2022-04-15 22:00 | 2022-04-15 23:00 | Spring | FALSE | nonsummer
2022-04-15 23:00 | 2022-04-16 | Spring | FALSE | nonsummer
2022-04-16 | 2022-04-16 01:00 | Spring | FALSE | nonsummer
2022-04-16 01:00 | 2022-04-16 02:00 | Spring | FALSE | nonsummer
2022-04-16 02:00 | 2022-04-16 03:00 | Spring | FALSE | nonsummer
2022-04-16 03:00 | 2022-04-16 04:00 | Spring | FALSE | nonsummer
2022-04-16 04:00 | 2022-04-16 05:00 | Spring | FALSE | nonsummer
2022-04-16 05:00 | 2022-04-16 06:00 | Spring | FALSE | nonsummer
2022-04-16 06:00 | 2022-04-16 07:00 | Spring | FALSE | nonsummer
2022-04-16 07:00 | 2022-04-16 08:00 | Spring | FALSE | nonsummer
2022-04-16 08:00 | 2022-04-16 09:00 | Spring | FALSE | nonsummer
2022-04-16 09:00 | 2022-04-16 10:00 | Spring | FALSE | nonsummer
2022-04-16 10:00 | 2022-04-16 11:00 | Spring | FALSE | nonsummer
2022-04-16 11:00 | 2022-04-16 12:00 | Spring | FALSE | nonsummer
2022-04-16 12:00 | 2022-04-16 13:00 | Spring | FALSE | nonsummer
2022-04-16 13:00 | 2022-04-16 14:00 | Spring | FALSE | nonsummer
2022-04-16 14:00 | 2022-04-16 15:00 | Spring | FALSE | nonsummer
2022-04-16 15:00 | 2022-04-16 16:00 | Spring | FALSE | nonsummer
2022-04-16 16:00 | 2022-04-16 17:00 | Spring | FALSE | nonsummer
2022-04-16 17:00 | 2022-04-16 18:00 | Spring | TRUE | nonsummer
2022-04-16 18:00 | 2022-04-16 19:00 | Spring | TRUE | nonsummer
2022-04-16 19:00 | 2022-04-16 20:00 | Spring | TRUE | nonsummer
2022-04-16 20:00 | 2022-04-16 21:00 | Spring | TRUE | nonsummer
2022-04-16 21:00 | 2022-04-16 22:00 | Spring | TRUE | nonsummer
2022-04-16 22:00 | 2022-04-16 23:00 | Spring | FALSE | nonsummer
2022-04-16 23:00 | 2022-04-17 | Spring | FALSE | nonsummer
2022-04-17 | 2022-04-17 01:00 | Spring | FALSE | nonsummer
2022-04-17 01:00 | 2022-04-17 02:00 | Spring | FALSE | nonsummer
2022-04-17 02:00 | 2022-04-17 03:00 | Spring | FALSE | nonsummer
2022-04-17 03:00 | 2022-04-17 04:00 | Spring | FALSE | nonsummer
2022-04-17 04:00 | 2022-04-17 05:00 | Spring | FALSE | nonsummer
2022-04-17 05:00 | 2022-04-17 06:00 | Spring | FALSE | nonsummer
2022-04-17 06:00 | 2022-04-17 07:00 | Spring | FALSE | nonsummer
2022-04-17 07:00 | 2022-04-17 08:00 | Spring | FALSE | nonsummer
2022-04-17 08:00 | 2022-04-17 09:00 | Spring | FALSE | nonsummer
2022-04-17 09:00 | 2022-04-17 10:00 | Spring | FALSE | nonsummer
2022-04-17 10:00 | 2022-04-17 11:00 | Spring | FALSE | nonsummer
2022-04-17 11:00 | 2022-04-17 12:00 | Spring | FALSE | nonsummer
2022-04-17 12:00 | 2022-04-17 13:00 | Spring | FALSE | nonsummer
2022-04-17 13:00 | 2022-04-17 14:00 | Spring | FALSE | nonsummer
2022-04-17 14:00 | 2022-04-17 15:00 | Spring | FALSE | nonsummer
2022-04-17 15:00 | 2022-04-17 16:00 | Spring | FALSE | nonsummer
2022-04-17 16:00 | 2022-04-17 17:00 | Spring | FALSE | nonsummer
2022-04-17 17:00 | 2022-04-17 18:00 | Spring | TRUE | nonsummer
2022-04-17 18:00 | 2022-04-17 19:00 | Spring | TRUE | nonsummer
2022-04-17 19:00 | 2022-04-17 20:00 | Spring | TRUE | nonsummer
2022-04-17 20:00 | 2022-04-17 21:00 | Spring | TRUE | nonsummer
2022-04-17 21:00 | 2022-04-17 22:00 | Spring | TRUE | nonsummer
2022-04-17 22:00 | 2022-04-17 23:00 | Spring | FALSE | nonsummer
2022-04-17 23:00 | 2022-04-18 | Spring | FALSE | nonsummer
2022-04-18 | 2022-04-18 01:00 | Spring | FALSE | nonsummer
2022-04-18 01:00 | 2022-04-18 02:00 | Spring | FALSE | nonsummer
2022-04-18 02:00 | 2022-04-18 03:00 | Spring | FALSE | nonsummer
2022-04-18 03:00 | 2022-04-18 04:00 | Spring | FALSE | nonsummer
2022-04-18 04:00 | 2022-04-18 05:00 | Spring | FALSE | nonsummer
2022-04-18 05:00 | 2022-04-18 06:00 | Spring | FALSE | nonsummer
2022-04-18 06:00 | 2022-04-18 07:00 | Spring | FALSE | nonsummer
2022-04-18 07:00 | 2022-04-18 08:00 | Spring | FALSE | nonsummer
2022-04-18 08:00 | 2022-04-18 09:00 | Spring | FALSE | nonsummer
2022-04-18 09:00 | 2022-04-18 10:00 | Spring | FALSE | nonsummer
2022-04-18 10:00 | 2022-04-18 11:00 | Spring | FALSE | nonsummer
2022-04-18 11:00 | 2022-04-18 12:00 | Spring | FALSE | nonsummer
2022-04-18 12:00 | 2022-04-18 13:00 | Spring | FALSE | nonsummer
2022-04-18 13:00 | 2022-04-18 14:00 | Spring | FALSE | nonsummer
2022-04-18 14:00 | 2022-04-18 15:00 | Spring | FALSE | nonsummer
2022-04-18 15:00 | 2022-04-18 16:00 | Spring | FALSE | nonsummer
2022-04-18 16:00 | 2022-04-18 17:00 | Spring | FALSE | nonsummer
2022-04-18 17:00 | 2022-04-18 18:00 | Spring | TRUE | nonsummer
2022-04-18 18:00 | 2022-04-18 19:00 | Spring | TRUE | nonsummer
2022-04-18 19:00 | 2022-04-18 20:00 | Spring | TRUE | nonsummer
2022-04-18 20:00 | 2022-04-18 21:00 | Spring | TRUE | nonsummer
2022-04-18 21:00 | 2022-04-18 22:00 | Spring | TRUE | nonsummer
2022-04-18 22:00 | 2022-04-18 23:00 | Spring | FALSE | nonsummer
2022-04-18 23:00 | 2022-04-19 | Spring | FALSE | nonsummer
2022-04-19 | 2022-04-19 01:00 | Spring | FALSE | nonsummer
2022-04-19 01:00 | 2022-04-19 02:00 | Spring | FALSE | nonsummer
2022-04-19 02:00 | 2022-04-19 03:00 | Spring | FALSE | nonsummer
2022-04-19 03:00 | 2022-04-19 04:00 | Spring | FALSE | nonsummer
2022-04-19 04:00 | 2022-04-19 05:00 | Spring | FALSE | nonsummer
2022-04-19 05:00 | 2022-04-19 06:00 | Spring | FALSE | nonsummer
2022-04-19 06:00 | 2022-04-19 07:00 | Spring | FALSE | nonsummer
2022-04-19 07:00 | 2022-04-19 08:00 | Spring | FALSE | nonsummer
2022-04-19 08:00 | 2022-04-19 09:00 | Spring | FALSE | nonsummer
2022-04-19 09:00 | 2022-04-19 10:00 | Spring | FALSE | nonsummer
2022-04-19 10:00 | 2022-04-19 11:00 | Spring | FALSE | nonsummer
2022-04-19 11:00 | 2022-04-19 12:00 | Spring | FALSE | nonsummer
2022-04-19 12:00 | 2022-04-19 13:00 | Spring | FALSE | nonsummer
2022-04-19 13:00 | 2022-04-19 14:00 | Spring | FALSE | nonsummer
2022-04-19 14:00 | 2022-04-19 15:00 | Spring | FALSE | nonsummer
2022-04-19 15:00 | 2022-04-19 16:00 | Spring | FALSE | nonsummer
2022-04-19 16:00 | 2022-04-19 17:00 | Spring | FALSE | nonsummer
2022-04-19 17:00 | 2022-04-19 18:00 | Spring | TRUE | nonsummer
2022-04-19 18:00 | 2022-04-19 19:00 | Spring | TRUE | nonsummer
2022-04-19 19:00 | 2022-04-19 20:00 | Spring | TRUE | nonsummer
2022-04-19 20:00 | 2022-04-19 21:00 | Spring | TRUE | nonsummer
2022-04-19 21:00 | 2022-04-19 22:00 | Spring | TRUE | nonsummer
2022-04-19 22:00 | 2022-04-19 23:00 | Spring | FALSE | nonsummer
2022-04-19 23:00 | 2022-04-20 | Spring | FALSE | nonsummer
2022-04-20 | 2022-04-20 01:00 | Spring | FALSE | nonsummer
2022-04-20 01:00 | 2022-04-20 02:00 | Spring | FALSE | nonsummer
2022-04-20 02:00 | 2022-04-20 03:00 | Spring | FALSE | nonsummer
2022-04-20 03:00 | 2022-04-20 04:00 | Spring | FALSE | nonsummer
2022-04-20 04:00 | 2022-04-20 05:00 | Spring | FALSE | nonsummer
2022-04-20 05:00 | 2022-04-20 06:00 | Spring | FALSE | nonsummer
2022-04-20 06:00 | 2022-04-20 07:00 | Spring | FALSE | nonsummer
2022-04-20 07:00 | 2022-04-20 08:00 | Spring | FALSE | nonsummer
2022-04-20 08:00 | 2022-04-20 09:00 | Spring | FALSE | nonsummer
2022-04-20 09:00 | 2022-04-20 10:00 | Spring | FALSE | nonsummer
2022-04-20 10:00 | 2022-04-20 11:00 | Spring | FALSE | nonsummer
2022-04-20 11:00 | 2022-04-20 12:00 | Spring | FALSE | nonsummer
2022-04-20 12:00 | 2022-04-20 13:00 | Spring | FALSE | nonsummer
2022-04-20 13:00 | 2022-04-20 14:00 | Spring | FALSE | nonsummer
2022-04-20 14:00 | 2022-04-20 15:00 | Spring | FALSE | nonsummer
2022-04-20 15:00 | 2022-04-20 16:00 | Spring | FALSE | nonsummer
2022-04-20 16:00 | 2022-04-20 17:00 | Spring | FALSE | nonsummer
2022-04-20 17:00 | 2022-04-20 18:00 | Spring | TRUE | nonsummer
2022-04-20 18:00 | 2022-04-20 19:00 | Spring | TRUE | nonsummer
2022-04-20 19:00 | 2022-04-20 20:00 | Spring | TRUE | nonsummer
2022-04-20 20:00 | 2022-04-20 21:00 | Spring | TRUE | nonsummer
2022-04-20 21:00 | 2022-04-20 22:00 | Spring | TRUE | nonsummer
2022-04-20 22:00 | 2022-04-20 23:00 | Spring | FALSE | nonsummer
2022-04-20 23:00 | 2022-04-21 | Spring | FALSE | nonsummer
2022-04-21 | 2022-04-21 01:00 | Spring | FALSE | nonsummer
2022-04-21 01:00 | 2022-04-21 02:00 | Spring | FALSE | nonsummer
2022-04-21 02:00 | 2022-04-21 03:00 | Spring | FALSE | nonsummer
2022-04-21 03:00 | 2022-04-21 04:00 | Spring | FALSE | nonsummer
2022-04-21 04:00 | 2022-04-21 05:00 | Spring | FALSE | nonsummer
2022-04-21 05:00 | 2022-04-21 06:00 | Spring | FALSE | nonsummer
2022-04-21 06:00 | 2022-04-21 07:00 | Spring | FALSE | nonsummer
2022-04-21 07:00 | 2022-04-21 08:00 | Spring | FALSE | nonsummer
2022-04-21 08:00 | 2022-04-21 09:00 | Spring | FALSE | nonsummer
2022-04-21 09:00 | 2022-04-21 10:00 | Spring | FALSE | nonsummer
2022-04-21 10:00 | 2022-04-21 11:00 | Spring | FALSE | nonsummer
2022-04-21 11:00 | 2022-04-21 12:00 | Spring | FALSE | nonsummer
2022-04-21 12:00 | 2022-04-21 13:00 | Spring | FALSE | nonsummer
2022-04-21 13:00 | 2022-04-21 14:00 | Spring | FALSE | nonsummer
2022-04-21 14:00 | 2022-04-21 15:00 | Spring | FALSE | nonsummer
2022-04-21 15:00 | 2022-04-21 16:00 | Spring | FALSE | nonsummer
2022-04-21 16:00 | 2022-04-21 17:00 | Spring | FALSE | nonsummer
2022-04-21 17:00 | 2022-04-21 18:00 | Spring | TRUE | nonsummer
2022-04-21 18:00 | 2022-04-21 19:00 | Spring | TRUE | nonsummer
2022-04-21 19:00 | 2022-04-21 20:00 | Spring | TRUE | nonsummer
2022-04-21 20:00 | 2022-04-21 21:00 | Spring | TRUE | nonsummer
2022-04-21 21:00 | 2022-04-21 22:00 | Spring | TRUE | nonsummer
2022-04-21 22:00 | 2022-04-21 23:00 | Spring | FALSE | nonsummer
2022-04-21 23:00 | 2022-04-22 | Spring | FALSE | nonsummer
2022-04-22 | 2022-04-22 01:00 | Spring | FALSE | nonsummer
2022-04-22 01:00 | 2022-04-22 02:00 | Spring | FALSE | nonsummer
2022-04-22 02:00 | 2022-04-22 03:00 | Spring | FALSE | nonsummer
2022-04-22 03:00 | 2022-04-22 04:00 | Spring | FALSE | nonsummer
2022-04-22 04:00 | 2022-04-22 05:00 | Spring | FALSE | nonsummer
2022-04-22 05:00 | 2022-04-22 06:00 | Spring | FALSE | nonsummer
2022-04-22 06:00 | 2022-04-22 07:00 | Spring | FALSE | nonsummer
2022-04-22 07:00 | 2022-04-22 08:00 | Spring | FALSE | nonsummer
2022-04-22 08:00 | 2022-04-22 09:00 | Spring | FALSE | nonsummer
2022-04-22 09:00 | 2022-04-22 10:00 | Spring | FALSE | nonsummer
2022-04-22 10:00 | 2022-04-22 11:00 | Spring | FALSE | nonsummer
2022-04-22 11:00 | 2022-04-22 12:00 | Spring | FALSE | nonsummer
2022-04-22 12:00 | 2022-04-22 13:00 | Spring | FALSE | nonsummer
2022-04-22 13:00 | 2022-04-22 14:00 | Spring | FALSE | nonsummer
2022-04-22 14:00 | 2022-04-22 15:00 | Spring | FALSE | nonsummer
2022-04-22 15:00 | 2022-04-22 16:00 | Spring | FALSE | nonsummer
2022-04-22 16:00 | 2022-04-22 17:00 | Spring | FALSE | nonsummer
2022-04-22 17:00 | 2022-04-22 18:00 | Spring | TRUE | nonsummer
2022-04-22 18:00 | 2022-04-22 19:00 | Spring | TRUE | nonsummer
2022-04-22 19:00 | 2022-04-22 20:00 | Spring | TRUE | nonsummer
2022-04-22 20:00 | 2022-04-22 21:00 | Spring | TRUE | nonsummer
2022-04-22 21:00 | 2022-04-22 22:00 | Spring | TRUE | nonsummer
2022-04-22 22:00 | 2022-04-22 23:00 | Spring | FALSE | nonsummer
2022-04-22 23:00 | 2022-04-23 | Spring | FALSE | nonsummer
2022-04-23 | 2022-04-23 01:00 | Spring | FALSE | nonsummer
2022-04-23 01:00 | 2022-04-23 02:00 | Spring | FALSE | nonsummer
2022-04-23 02:00 | 2022-04-23 03:00 | Spring | FALSE | nonsummer
2022-04-23 03:00 | 2022-04-23 04:00 | Spring | FALSE | nonsummer
2022-04-23 04:00 | 2022-04-23 05:00 | Spring | FALSE | nonsummer
2022-04-23 05:00 | 2022-04-23 06:00 | Spring | FALSE | nonsummer
2022-04-23 06:00 | 2022-04-23 07:00 | Spring | FALSE | nonsummer
2022-04-23 07:00 | 2022-04-23 08:00 | Spring | FALSE | nonsummer
2022-04-23 08:00 | 2022-04-23 09:00 | Spring | FALSE | nonsummer
2022-04-23 09:00 | 2022-04-23 10:00 | Spring | FALSE | nonsummer
2022-04-23 10:00 | 2022-04-23 11:00 | Spring | FALSE | nonsummer
2022-04-23 11:00 | 2022-04-23 12:00 | Spring | FALSE | nonsummer
2022-04-23 12:00 | 2022-04-23 13:00 | Spring | FALSE | nonsummer
2022-04-23 13:00 | 2022-04-23 14:00 | Spring | FALSE | nonsummer
2022-04-23 14:00 | 2022-04-23 15:00 | Spring | FALSE | nonsummer
2022-04-23 15:00 | 2022-04-23 16:00 | Spring | FALSE | nonsummer
2022-04-23 16:00 | 2022-04-23 17:00 | Spring | FALSE | nonsummer
2022-04-23 17:00 | 2022-04-23 18:00 | Spring | TRUE | nonsummer
2022-04-23 18:00 | 2022-04-23 19:00 | Spring | TRUE | nonsummer
2022-04-23 19:00 | 2022-04-23 20:00 | Spring | TRUE | nonsummer
2022-04-23 20:00 | 2022-04-23 21:00 | Spring | TRUE | nonsummer
2022-04-23 21:00 | 2022-04-23 22:00 | Spring | TRUE | nonsummer
2022-04-23 22:00 | 2022-04-23 23:00 | Spring | FALSE | nonsummer
2022-04-23 23:00 | 2022-04-24 | Spring | FALSE | nonsummer
2022-04-24 | 2022-04-24 01:00 | Spring | FALSE | nonsummer
2022-04-24 01:00 | 2022-04-24 02:00 | Spring | FALSE | nonsummer
2022-04-24 02:00 | 2022-04-24 03:00 | Spring | FALSE | nonsummer
2022-04-24 03:00 | 2022-04-24 04:00 | Spring | FALSE | nonsummer
2022-04-24 04:00 | 2022-04-24 05:00 | Spring | FALSE | nonsummer
2022-04-24 05:00 | 2022-04-24 06:00 | Spring | FALSE | nonsummer
2022-04-24 06:00 | 2022-04-24 07:00 | Spring | FALSE | nonsummer
2022-04-24 07:00 | 2022-04-24 08:00 | Spring | FALSE | nonsummer
2022-04-24 08:00 | 2022-04-24 09:00 | Spring | FALSE | nonsummer
2022-04-24 09:00 | 2022-04-24 10:00 | Spring | FALSE | nonsummer
2022-04-24 10:00 | 2022-04-24 11:00 | Spring | FALSE | nonsummer
2022-04-24 11:00 | 2022-04-24 12:00 | Spring | FALSE | nonsummer
2022-04-24 12:00 | 2022-04-24 13:00 | Spring | FALSE | nonsummer
2022-04-24 13:00 | 2022-04-24 14:00 | Spring | FALSE | nonsummer
2022-04-24 14:00 | 2022-04-24 15:00 | Spring | FALSE | nonsummer
2022-04-24 15:00 | 2022-04-24 16:00 | Spring | FALSE | nonsummer
2022-04-24 16:00 | 2022-04-24 17:00 | Spring | FALSE | nonsummer
2022-04-24 17:00 | 2022-04-24 18:00 | Spring | TRUE | nonsummer
2022-04-24 18:00 | 2022-04-24 19:00 | Spring | TRUE | nonsummer
2022-04-24 19:00 | 2022-04-24 20:00 | Spring | TRUE | nonsummer
2022-04-24 20:00 | 2022-04-24 21:00 | Spring | TRUE | nonsummer
2022-04-24 21:00 | 2022-04-24 22:00 | Spring | TRUE | nonsummer
2022-04-24 22:00 | 2022-04-24 23:00 | Spring | FALSE | nonsummer
2022-04-24 23:00 | 2022-04-25 | Spring | FALSE | nonsummer
2022-04-25 | 2022-04-25 01:00 | Spring | FALSE | nonsummer
2022-04-25 01:00 | 2022-04-25 02:00 | Spring | FALSE | nonsummer
2022-04-25 02:00 | 2022-04-25 03:00 | Spring | FALSE | nonsummer
2022-04-25 03:00 | 2022-04-25 04:00 | Spring | FALSE | nonsummer
2022-04-25 04:00 | 2022-04-25 05:00 | Spring | FALSE | nonsummer
2022-04-25 05:00 | 2022-04-25 06:00 | Spring | FALSE | nonsummer
2022-04-25 06:00 | 2022-04-25 07:00 | Spring | FALSE | nonsummer
2022-04-25 07:00 | 2022-04-25 08:00 | Spring | FALSE | nonsummer
2022-04-25 08:00 | 2022-04-25 09:00 | Spring | FALSE | nonsummer
2022-04-25 09:00 | 2022-04-25 10:00 | Spring | FALSE | nonsummer
2022-04-25 10:00 | 2022-04-25 11:00 | Spring | FALSE | nonsummer
2022-04-25 11:00 | 2022-04-25 12:00 | Spring | FALSE | nonsummer
2022-04-25 12:00 | 2022-04-25 13:00 | Spring | FALSE | nonsummer
2022-04-25 13:00 | 2022-04-25 14:00 | Spring | FALSE | nonsummer
2022-04-25 14:00 | 2022-04-25 15:00 | Spring | FALSE | nonsummer
2022-04-25 15:00 | 2022-04-25 16:00 | Spring | FALSE | nonsummer
2022-04-25 16:00 | 2022-04-25 17:00 | Spring | FALSE | nonsummer
2022-04-25 17:00 | 2022-04-25 18:00 | Spring | TRUE | nonsummer
2022-04-25 18:00 | 2022-04-25 19:00 | Spring | TRUE | nonsummer
2022-04-25 19:00 | 2022-04-25 20:00 | Spring | TRUE | nonsummer
2022-04-25 20:00 | 2022-04-25 21:00 | Spring | TRUE | nonsummer
2022-04-25 21:00 | 2022-04-25 22:00 | Spring | TRUE | nonsummer
2022-04-25 22:00 | 2022-04-25 23:00 | Spring | FALSE | nonsummer
2022-04-25 23:00 | 2022-04-26 | Spring | FALSE | nonsummer
2022-04-26 | 2022-04-26 01:00 | Spring | FALSE | nonsummer
2022-04-26 01:00 | 2022-04-26 02:00 | Spring | FALSE | nonsummer
2022-04-26 02:00 | 2022-04-26 03:00 | Spring | FALSE | nonsummer
2022-04-26 03:00 | 2022-04-26 04:00 | Spring | FALSE | nonsummer
2022-04-26 04:00 | 2022-04-26 05:00 | Spring | FALSE | nonsummer
2022-04-26 05:00 | 2022-04-26 06:00 | Spring | FALSE | nonsummer
2022-04-26 06:00 | 2022-04-26 07:00 | Spring | FALSE | nonsummer
2022-04-26 07:00 | 2022-04-26 08:00 | Spring | FALSE | nonsummer
2022-04-26 08:00 | 2022-04-26 09:00 | Spring | FALSE | nonsummer
2022-04-26 09:00 | 2022-04-26 10:00 | Spring | FALSE | nonsummer
2022-04-26 10:00 | 2022-04-26 11:00 | Spring | FALSE | nonsummer
2022-04-26 11:00 | 2022-04-26 12:00 | Spring | FALSE | nonsummer
2022-04-26 12:00 | 2022-04-26 13:00 | Spring | FALSE | nonsummer
2022-04-26 13:00 | 2022-04-26 14:00 | Spring | FALSE | nonsummer
2022-04-26 14:00 | 2022-04-26 15:00 | Spring | FALSE | nonsummer
2022-04-26 15:00 | 2022-04-26 16:00 | Spring | FALSE | nonsummer
2022-04-26 16:00 | 2022-04-26 17:00 | Spring | FALSE | nonsummer
2022-04-26 17:00 | 2022-04-26 18:00 | Spring | TRUE | nonsummer
2022-04-26 18:00 | 2022-04-26 19:00 | Spring | TRUE | nonsummer
2022-04-26 19:00 | 2022-04-26 20:00 | Spring | TRUE | nonsummer
2022-04-26 20:00 | 2022-04-26 21:00 | Spring | TRUE | nonsummer
2022-04-26 21:00 | 2022-04-26 22:00 | Spring | TRUE | nonsummer
2022-04-26 22:00 | 2022-04-26 23:00 | Spring | FALSE | nonsummer
2022-04-26 23:00 | 2022-04-27 | Spring | FALSE | nonsummer
2022-04-27 | 2022-04-27 01:00 | Spring | FALSE | nonsummer
2022-04-27 01:00 | 2022-04-27 02:00 | Spring | FALSE | nonsummer
2022-04-27 02:00 | 2022-04-27 03:00 | Spring | FALSE | nonsummer
2022-04-27 03:00 | 2022-04-27 04:00 | Spring | FALSE | nonsummer
2022-04-27 04:00 | 2022-04-27 05:00 | Spring | FALSE | nonsummer
2022-04-27 05:00 | 2022-04-27 06:00 | Spring | FALSE | nonsummer
2022-04-27 06:00 | 2022-04-27 07:00 | Spring | FALSE | nonsummer
2022-04-27 07:00 | 2022-04-27 08:00 | Spring | FALSE | nonsummer
2022-04-27 08:00 | 2022-04-27 09:00 | Spring | FALSE | nonsummer
2022-04-27 09:00 | 2022-04-27 10:00 | Spring | FALSE | nonsummer
2022-04-27 10:00 | 2022-04-27 11:00 | Spring | FALSE | nonsummer
2022-04-27 11:00 | 2022-04-27 12:00 | Spring | FALSE | nonsummer
2022-04-27 12:00 | 2022-04-27 13:00 | Spring | FALSE | nonsummer
2022-04-27 13:00 | 2022-04-27 14:00 | Spring | FALSE | nonsummer
2022-04-27 14:00 | 2022-04-27 15:00 | Spring | FALSE | nonsummer
2022-04-27 15:00 | 2022-04-27 16:00 | Spring | FALSE | nonsummer
2022-04-27 16:00 | 2022-04-27 17:00 | Spring | FALSE | nonsummer
2022-04-27 17:00 | 2022-04-27 18:00 | Spring | TRUE | nonsummer
2022-04-27 18:00 | 2022-04-27 19:00 | Spring | TRUE | nonsummer
2022-04-27 19:00 | 2022-04-27 20:00 | Spring | TRUE | nonsummer
2022-04-27 20:00 | 2022-04-27 21:00 | Spring | TRUE | nonsummer
2022-04-27 21:00 | 2022-04-27 22:00 | Spring | TRUE | nonsummer
2022-04-27 22:00 | 2022-04-27 23:00 | Spring | FALSE | nonsummer
2022-04-27 23:00 | 2022-04-28 | Spring | FALSE | nonsummer
2022-04-28 | 2022-04-28 01:00 | Spring | FALSE | nonsummer
2022-04-28 01:00 | 2022-04-28 02:00 | Spring | FALSE | nonsummer
2022-04-28 02:00 | 2022-04-28 03:00 | Spring | FALSE | nonsummer
2022-04-28 03:00 | 2022-04-28 04:00 | Spring | FALSE | nonsummer
2022-04-28 04:00 | 2022-04-28 05:00 | Spring | FALSE | nonsummer
2022-04-28 05:00 | 2022-04-28 06:00 | Spring | FALSE | nonsummer
2022-04-28 06:00 | 2022-04-28 07:00 | Spring | FALSE | nonsummer
2022-04-28 07:00 | 2022-04-28 08:00 | Spring | FALSE | nonsummer
2022-04-28 08:00 | 2022-04-28 09:00 | Spring | FALSE | nonsummer
2022-04-28 09:00 | 2022-04-28 10:00 | Spring | FALSE | nonsummer
2022-04-28 10:00 | 2022-04-28 11:00 | Spring | FALSE | nonsummer
2022-04-28 11:00 | 2022-04-28 12:00 | Spring | FALSE | nonsummer
2022-04-28 12:00 | 2022-04-28 13:00 | Spring | FALSE | nonsummer
2022-04-28 13:00 | 2022-04-28 14:00 | Spring | FALSE | nonsummer
2022-04-28 14:00 | 2022-04-28 15:00 | Spring | FALSE | nonsummer
2022-04-28 15:00 | 2022-04-28 16:00 | Spring | FALSE | nonsummer
2022-04-28 16:00 | 2022-04-28 17:00 | Spring | FALSE | nonsummer
2022-04-28 17:00 | 2022-04-28 18:00 | Spring | TRUE | nonsummer
2022-04-28 18:00 | 2022-04-28 19:00 | Spring | TRUE | nonsummer
2022-04-28 19:00 | 2022-04-28 20:00 | Spring | TRUE | nonsummer
2022-04-28 20:00 | 2022-04-28 21:00 | Spring | TRUE | nonsummer
2022-04-28 21:00 | 2022-04-28 22:00 | Spring | TRUE | nonsummer
2022-04-28 22:00 | 2022-04-28 23:00 | Spring | FALSE | nonsummer
2022-04-28 23:00 | 2022-04-29 | Spring | FALSE | nonsummer
2022-04-29 | 2022-04-29 01:00 | Spring | FALSE | nonsummer
2022-04-29 01:00 | 2022-04-29 02:00 | Spring | FALSE | nonsummer
2022-04-29 02:00 | 2022-04-29 03:00 | Spring | FALSE | nonsummer
2022-04-29 03:00 | 2022-04-29 04:00 | Spring | FALSE | nonsummer
2022-04-29 04:00 | 2022-04-29 05:00 | Spring | FALSE | nonsummer
2022-04-29 05:00 | 2022-04-29 06:00 | Spring | FALSE | nonsummer
2022-04-29 06:00 | 2022-04-29 07:00 | Spring | FALSE | nonsummer
2022-04-29 07:00 | 2022-04-29 08:00 | Spring | FALSE | nonsummer
2022-04-29 08:00 | 2022-04-29 09:00 | Spring | FALSE | nonsummer
2022-04-29 09:00 | 2022-04-29 10:00 | Spring | FALSE | nonsummer
2022-04-29 10:00 | 2022-04-29 11:00 | Spring | FALSE | nonsummer
2022-04-29 11:00 | 2022-04-29 12:00 | Spring | FALSE | nonsummer
2022-04-29 12:00 | 2022-04-29 13:00 | Spring | FALSE | nonsummer
2022-04-29 13:00 | 2022-04-29 14:00 | Spring | FALSE | nonsummer
2022-04-29 14:00 | 2022-04-29 15:00 | Spring | FALSE | nonsummer
2022-04-29 15:00 | 2022-04-29 16:00 | Spring | FALSE | nonsummer
2022-04-29 16:00 | 2022-04-29 17:00 | Spring | FALSE | nonsummer
2022-04-29 17:00 | 2022-04-29 18:00 | Spring | TRUE | nonsummer
2022-04-29 18:00 | 2022-04-29 19:00 | Spring | TRUE | nonsummer
2022-04-29 19:00 | 2022-04-29 20:00 | Spring | TRUE | nonsummer
2022-04-29 20:00 | 2022-04-29 21:00 | Spring | TRUE | nonsummer
2022-04-29 21:00 | 2022-04-29 22:00 | Spring | TRUE | nonsummer
2022-04-29 22:00 | 2022-04-29 23:00 | Spring | FALSE | nonsummer
2022-04-29 23:00 | 2022-04-30 | Spring | FALSE | nonsummer
2022-04-30 | 2022-04-30 01:00 | Spring | FALSE | nonsummer
2022-04-30 01:00 | 2022-04-30 02:00 | Spring | FALSE | nonsummer
2022-04-30 02:00 | 2022-04-30 03:00 | Spring | FALSE | nonsummer
2022-04-30 03:00 | 2022-04-30 04:00 | Spring | FALSE | nonsummer
2022-04-30 04:00 | 2022-04-30 05:00 | Spring | FALSE | nonsummer
2022-04-30 05:00 | 2022-04-30 06:00 | Spring | FALSE | nonsummer
2022-04-30 06:00 | 2022-04-30 07:00 | Spring | FALSE | nonsummer
2022-04-30 07:00 | 2022-04-30 08:00 | Spring | FALSE | nonsummer
2022-04-30 08:00 | 2022-04-30 09:00 | Spring | FALSE | nonsummer
2022-04-30 09:00 | 2022-04-30 10:00 | Spring | FALSE | nonsummer
2022-04-30 10:00 | 2022-04-30 11:00 | Spring | FALSE | nonsummer
2022-04-30 11:00 | 2022-04-30 12:00 | Spring | FALSE | nonsummer
2022-04-30 12:00 | 2022-04-30 13:00 | Spring | FALSE | nonsummer
2022-04-30 13:00 | 2022-04-30 14:00 | Spring | FALSE | nonsummer
2022-04-30 14:00 | 2022-04-30 15:00 | Spring | FALSE | nonsummer
2022-04-30 15:00 | 2022-04-30 16:00 | Spring | FALSE | nonsummer
2022-04-30 16:00 | 2022-04-30 17:00 | Spring | FALSE | nonsummer
2022-04-30 17:00 | 2022-04-30 18:00 | Spring | TRUE | nonsummer
2022-04-30 18:00 | 2022-04-30 19:00 | Spring | TRUE | nonsummer
2022-04-30 19:00 | 2022-04-30 20:00 | Spring | TRUE | nonsummer
2022-04-30 20:00 | 2022-04-30 21:00 | Spring | TRUE | nonsummer
2022-04-30 21:00 | 2022-04-30 22:00 | Spring | TRUE | nonsummer
2022-04-30 22:00 | 2022-04-30 23:00 | Spring | FALSE | nonsummer
2022-04-30 23:00 | 2022-05-01 | Spring | FALSE | nonsummer
2022-05-01 | 2022-05-01 01:00 | Spring | FALSE | nonsummer
2022-05-01 01:00 | 2022-05-01 02:00 | Spring | FALSE | nonsummer
2022-05-01 02:00 | 2022-05-01 03:00 | Spring | FALSE | nonsummer
2022-05-01 03:00 | 2022-05-01 04:00 | Spring | FALSE | nonsummer
2022-05-01 04:00 | 2022-05-01 05:00 | Spring | FALSE | nonsummer
2022-05-01 05:00 | 2022-05-01 06:00 | Spring | FALSE | nonsummer
2022-05-01 06:00 | 2022-05-01 07:00 | Spring | FALSE | nonsummer
2022-05-01 07:00 | 2022-05-01 08:00 | Spring | FALSE | nonsummer
2022-05-01 08:00 | 2022-05-01 09:00 | Spring | FALSE | nonsummer
2022-05-01 09:00 | 2022-05-01 10:00 | Spring | FALSE | nonsummer
2022-05-01 10:00 | 2022-05-01 11:00 | Spring | FALSE | nonsummer
2022-05-01 11:00 | 2022-05-01 12:00 | Spring | FALSE | nonsummer
2022-05-01 12:00 | 2022-05-01 13:00 | Spring | FALSE | nonsummer
2022-05-01 13:00 | 2022-05-01 14:00 | Spring | FALSE | nonsummer
2022-05-01 14:00 | 2022-05-01 15:00 | Spring | FALSE | nonsummer
2022-05-01 15:00 | 2022-05-01 16:00 | Spring | FALSE | nonsummer
2022-05-01 16:00 | 2022-05-01 17:00 | Spring | FALSE | nonsummer
2022-05-01 17:00 | 2022-05-01 18:00 | Spring | TRUE | nonsummer
2022-05-01 18:00 | 2022-05-01 19:00 | Spring | TRUE | nonsummer
2022-05-01 19:00 | 2022-05-01 20:00 | Spring | TRUE | nonsummer
2022-05-01 20:00 | 2022-05-01 21:00 | Spring | TRUE | nonsummer
2022-05-01 21:00 | 2022-05-01 22:00 | Spring | TRUE | nonsummer
2022-05-01 22:00 | 2022-05-01 23:00 | Spring | FALSE | nonsummer
2022-05-01 23:00 | 2022-05-02 | Spring | FALSE | nonsummer
2022-05-02 | 2022-05-02 01:00 | Spring | FALSE | nonsummer
2022-05-02 01:00 | 2022-05-02 02:00 | Spring | FALSE | nonsummer
2022-05-02 02:00 | 2022-05-02 03:00 | Spring | FALSE | nonsummer
2022-05-02 03:00 | 2022-05-02 04:00 | Spring | FALSE | nonsummer
2022-05-02 04:00 | 2022-05-02 05:00 | Spring | FALSE | nonsummer
2022-05-02 05:00 | 2022-05-02 06:00 | Spring | FALSE | nonsummer
2022-05-02 06:00 | 2022-05-02 07:00 | Spring | FALSE | nonsummer
2022-05-02 07:00 | 2022-05-02 08:00 | Spring | FALSE | nonsummer
2022-05-02 08:00 | 2022-05-02 09:00 | Spring | FALSE | nonsummer
2022-05-02 09:00 | 2022-05-02 10:00 | Spring | FALSE | nonsummer
2022-05-02 10:00 | 2022-05-02 11:00 | Spring | FALSE | nonsummer
2022-05-02 11:00 | 2022-05-02 12:00 | Spring | FALSE | nonsummer
2022-05-02 12:00 | 2022-05-02 13:00 | Spring | FALSE | nonsummer
2022-05-02 13:00 | 2022-05-02 14:00 | Spring | FALSE | nonsummer
2022-05-02 14:00 | 2022-05-02 15:00 | Spring | FALSE | nonsummer
2022-05-02 15:00 | 2022-05-02 16:00 | Spring | FALSE | nonsummer
2022-05-02 16:00 | 2022-05-02 17:00 | Spring | FALSE | nonsummer
2022-05-02 17:00 | 2022-05-02 18:00 | Spring | TRUE | nonsummer
2022-05-02 18:00 | 2022-05-02 19:00 | Spring | TRUE | nonsummer
2022-05-02 19:00 | 2022-05-02 20:00 | Spring | TRUE | nonsummer
2022-05-02 20:00 | 2022-05-02 21:00 | Spring | TRUE | nonsummer
2022-05-02 21:00 | 2022-05-02 22:00 | Spring | TRUE | nonsummer
2022-05-02 22:00 | 2022-05-02 23:00 | Spring | FALSE | nonsummer
2022-05-02 23:00 | 2022-05-03 | Spring | FALSE | nonsummer
2022-05-03 | 2022-05-03 01:00 | Spring | FALSE | nonsummer
2022-05-03 01:00 | 2022-05-03 02:00 | Spring | FALSE | nonsummer
2022-05-03 02:00 | 2022-05-03 03:00 | Spring | FALSE | nonsummer
2022-05-03 03:00 | 2022-05-03 04:00 | Spring | FALSE | nonsummer
2022-05-03 04:00 | 2022-05-03 05:00 | Spring | FALSE | nonsummer
2022-05-03 05:00 | 2022-05-03 06:00 | Spring | FALSE | nonsummer
2022-05-03 06:00 | 2022-05-03 07:00 | Spring | FALSE | nonsummer
2022-05-03 07:00 | 2022-05-03 08:00 | Spring | FALSE | nonsummer
2022-05-03 08:00 | 2022-05-03 09:00 | Spring | FALSE | nonsummer
2022-05-03 09:00 | 2022-05-03 10:00 | Spring | FALSE | nonsummer
2022-05-03 10:00 | 2022-05-03 11:00 | Spring | FALSE | nonsummer
2022-05-03 11:00 | 2022-05-03 12:00 | Spring | FALSE | nonsummer
2022-05-03 12:00 | 2022-05-03 13:00 | Spring | FALSE | nonsummer
2022-05-03 13:00 | 2022-05-03 14:00 | Spring | FALSE | nonsummer
2022-05-03 14:00 | 2022-05-03 15:00 | Spring | FALSE | nonsummer
2022-05-03 15:00 | 2022-05-03 16:00 | Spring | FALSE | nonsummer
2022-05-03 16:00 | 2022-05-03 17:00 | Spring | FALSE | nonsummer
2022-05-03 17:00 | 2022-05-03 18:00 | Spring | TRUE | nonsummer
2022-05-03 18:00 | 2022-05-03 19:00 | Spring | TRUE | nonsummer
2022-05-03 19:00 | 2022-05-03 20:00 | Spring | TRUE | nonsummer
2022-05-03 20:00 | 2022-05-03 21:00 | Spring | TRUE | nonsummer
2022-05-03 21:00 | 2022-05-03 22:00 | Spring | TRUE | nonsummer
2022-05-03 22:00 | 2022-05-03 23:00 | Spring | FALSE | nonsummer
2022-05-03 23:00 | 2022-05-04 | Spring | FALSE | nonsummer
2022-05-04 | 2022-05-04 01:00 | Spring | FALSE | nonsummer
2022-05-04 01:00 | 2022-05-04 02:00 | Spring | FALSE | nonsummer
2022-05-04 02:00 | 2022-05-04 03:00 | Spring | FALSE | nonsummer
2022-05-04 03:00 | 2022-05-04 04:00 | Spring | FALSE | nonsummer
2022-05-04 04:00 | 2022-05-04 05:00 | Spring | FALSE | nonsummer
2022-05-04 05:00 | 2022-05-04 06:00 | Spring | FALSE | nonsummer
2022-05-04 06:00 | 2022-05-04 07:00 | Spring | FALSE | nonsummer
2022-05-04 07:00 | 2022-05-04 08:00 | Spring | FALSE | nonsummer
2022-05-04 08:00 | 2022-05-04 09:00 | Spring | FALSE | nonsummer
2022-05-04 09:00 | 2022-05-04 10:00 | Spring | FALSE | nonsummer
2022-05-04 10:00 | 2022-05-04 11:00 | Spring | FALSE | nonsummer
2022-05-04 11:00 | 2022-05-04 12:00 | Spring | FALSE | nonsummer
2022-05-04 12:00 | 2022-05-04 13:00 | Spring | FALSE | nonsummer
2022-05-04 13:00 | 2022-05-04 14:00 | Spring | FALSE | nonsummer
2022-05-04 14:00 | 2022-05-04 15:00 | Spring | FALSE | nonsummer
2022-05-04 15:00 | 2022-05-04 16:00 | Spring | FALSE | nonsummer
2022-05-04 16:00 | 2022-05-04 17:00 | Spring | FALSE | nonsummer
2022-05-04 17:00 | 2022-05-04 18:00 | Spring | TRUE | nonsummer
2022-05-04 18:00 | 2022-05-04 19:00 | Spring | TRUE | nonsummer
2022-05-04 19:00 | 2022-05-04 20:00 | Spring | TRUE | nonsummer
2022-05-04 20:00 | 2022-05-04 21:00 | Spring | TRUE | nonsummer
2022-05-04 21:00 | 2022-05-04 22:00 | Spring | TRUE | nonsummer
2022-05-04 22:00 | 2022-05-04 23:00 | Spring | FALSE | nonsummer
2022-05-04 23:00 | 2022-05-05 | Spring | FALSE | nonsummer
2022-05-05 | 2022-05-05 01:00 | Spring | FALSE | nonsummer
2022-05-05 01:00 | 2022-05-05 02:00 | Spring | FALSE | nonsummer
2022-05-05 02:00 | 2022-05-05 03:00 | Spring | FALSE | nonsummer
2022-05-05 03:00 | 2022-05-05 04:00 | Spring | FALSE | nonsummer
2022-05-05 04:00 | 2022-05-05 05:00 | Spring | FALSE | nonsummer
2022-05-05 05:00 | 2022-05-05 06:00 | Spring | FALSE | nonsummer
2022-05-05 06:00 | 2022-05-05 07:00 | Spring | FALSE | nonsummer
2022-05-05 07:00 | 2022-05-05 08:00 | Spring | FALSE | nonsummer
2022-05-05 08:00 | 2022-05-05 09:00 | Spring | FALSE | nonsummer
2022-05-05 09:00 | 2022-05-05 10:00 | Spring | FALSE | nonsummer
2022-05-05 10:00 | 2022-05-05 11:00 | Spring | FALSE | nonsummer
2022-05-05 11:00 | 2022-05-05 12:00 | Spring | FALSE | nonsummer
2022-05-05 12:00 | 2022-05-05 13:00 | Spring | FALSE | nonsummer
2022-05-05 13:00 | 2022-05-05 14:00 | Spring | FALSE | nonsummer
2022-05-05 14:00 | 2022-05-05 15:00 | Spring | FALSE | nonsummer
2022-05-05 15:00 | 2022-05-05 16:00 | Spring | FALSE | nonsummer
2022-05-05 16:00 | 2022-05-05 17:00 | Spring | FALSE | nonsummer
2022-05-05 17:00 | 2022-05-05 18:00 | Spring | TRUE | nonsummer
2022-05-05 18:00 | 2022-05-05 19:00 | Spring | TRUE | nonsummer
2022-05-05 19:00 | 2022-05-05 20:00 | Spring | TRUE | nonsummer
2022-05-05 20:00 | 2022-05-05 21:00 | Spring | TRUE | nonsummer
2022-05-05 21:00 | 2022-05-05 22:00 | Spring | TRUE | nonsummer
2022-05-05 22:00 | 2022-05-05 23:00 | Spring | FALSE | nonsummer
2022-05-05 23:00 | 2022-05-06 | Spring | FALSE | nonsummer
2022-05-06 | 2022-05-06 01:00 | Spring | FALSE | nonsummer
2022-05-06 01:00 | 2022-05-06 02:00 | Spring | FALSE | nonsummer
2022-05-06 02:00 | 2022-05-06 03:00 | Spring | FALSE | nonsummer
2022-05-06 03:00 | 2022-05-06 04:00 | Spring | FALSE | nonsummer
2022-05-06 04:00 | 2022-05-06 05:00 | Spring | FALSE | nonsummer
2022-05-06 05:00 | 2022-05-06 06:00 | Spring | FALSE | nonsummer
2022-05-06 06:00 | 2022-05-06 07:00 | Spring | FALSE | nonsummer
2022-05-06 07:00 | 2022-05-06 08:00 | Spring | FALSE | nonsummer
2022-05-06 08:00 | 2022-05-06 09:00 | Spring | FALSE | nonsummer
2022-05-06 09:00 | 2022-05-06 10:00 | Spring | FALSE | nonsummer
2022-05-06 10:00 | 2022-05-06 11:00 | Spring | FALSE | nonsummer
2022-05-06 11:00 | 2022-05-06 12:00 | Spring | FALSE | nonsummer
2022-05-06 12:00 | 2022-05-06 13:00 | Spring | FALSE | nonsummer
2022-05-06 13:00 | 2022-05-06 14:00 | Spring | FALSE | nonsummer
2022-05-06 14:00 | 2022-05-06 15:00 | Spring | FALSE | nonsummer
2022-05-06 15:00 | 2022-05-06 16:00 | Spring | FALSE | nonsummer
2022-05-06 16:00 | 2022-05-06 17:00 | Spring | FALSE | nonsummer
2022-05-06 17:00 | 2022-05-06 18:00 | Spring | TRUE | nonsummer
2022-05-06 18:00 | 2022-05-06 19:00 | Spring | TRUE | nonsummer
2022-05-06 19:00 | 2022-05-06 20:00 | Spring | TRUE | nonsummer
2022-05-06 20:00 | 2022-05-06 21:00 | Spring | TRUE | nonsummer
2022-05-06 21:00 | 2022-05-06 22:00 | Spring | TRUE | nonsummer
2022-05-06 22:00 | 2022-05-06 23:00 | Spring | FALSE | nonsummer
2022-05-06 23:00 | 2022-05-07 | Spring | FALSE | nonsummer
2022-05-07 | 2022-05-07 01:00 | Spring | FALSE | nonsummer
2022-05-07 01:00 | 2022-05-07 02:00 | Spring | FALSE | nonsummer
2022-05-07 02:00 | 2022-05-07 03:00 | Spring | FALSE | nonsummer
2022-05-07 03:00 | 2022-05-07 04:00 | Spring | FALSE | nonsummer
2022-05-07 04:00 | 2022-05-07 05:00 | Spring | FALSE | nonsummer
2022-05-07 05:00 | 2022-05-07 06:00 | Spring | FALSE | nonsummer
2022-05-07 06:00 | 2022-05-07 07:00 | Spring | FALSE | nonsummer
2022-05-07 07:00 | 2022-05-07 08:00 | Spring | FALSE | nonsummer
2022-05-07 08:00 | 2022-05-07 09:00 | Spring | FALSE | nonsummer
2022-05-07 09:00 | 2022-05-07 10:00 | Spring | FALSE | nonsummer
2022-05-07 10:00 | 2022-05-07 11:00 | Spring | FALSE | nonsummer
2022-05-07 11:00 | 2022-05-07 12:00 | Spring | FALSE | nonsummer
2022-05-07 12:00 | 2022-05-07 13:00 | Spring | FALSE | nonsummer
2022-05-07 13:00 | 2022-05-07 14:00 | Spring | FALSE | nonsummer
2022-05-07 14:00 | 2022-05-07 15:00 | Spring | FALSE | nonsummer
2022-05-07 15:00 | 2022-05-07 16:00 | Spring | FALSE | nonsummer
2022-05-07 16:00 | 2022-05-07 17:00 | Spring | FALSE | nonsummer
2022-05-07 17:00 | 2022-05-07 18:00 | Spring | TRUE | nonsummer
2022-05-07 18:00 | 2022-05-07 19:00 | Spring | TRUE | nonsummer
2022-05-07 19:00 | 2022-05-07 20:00 | Spring | TRUE | nonsummer
2022-05-07 20:00 | 2022-05-07 21:00 | Spring | TRUE | nonsummer
2022-05-07 21:00 | 2022-05-07 22:00 | Spring | TRUE | nonsummer
2022-05-07 22:00 | 2022-05-07 23:00 | Spring | FALSE | nonsummer
2022-05-07 23:00 | 2022-05-08 | Spring | FALSE | nonsummer
2022-05-08 | 2022-05-08 01:00 | Spring | FALSE | nonsummer
2022-05-08 01:00 | 2022-05-08 02:00 | Spring | FALSE | nonsummer
2022-05-08 02:00 | 2022-05-08 03:00 | Spring | FALSE | nonsummer
2022-05-08 03:00 | 2022-05-08 04:00 | Spring | FALSE | nonsummer
2022-05-08 04:00 | 2022-05-08 05:00 | Spring | FALSE | nonsummer
2022-05-08 05:00 | 2022-05-08 06:00 | Spring | FALSE | nonsummer
2022-05-08 06:00 | 2022-05-08 07:00 | Spring | FALSE | nonsummer
2022-05-08 07:00 | 2022-05-08 08:00 | Spring | FALSE | nonsummer
2022-05-08 08:00 | 2022-05-08 09:00 | Spring | FALSE | nonsummer
2022-05-08 09:00 | 2022-05-08 10:00 | Spring | FALSE | nonsummer
2022-05-08 10:00 | 2022-05-08 11:00 | Spring | FALSE | nonsummer
2022-05-08 11:00 | 2022-05-08 12:00 | Spring | FALSE | nonsummer
2022-05-08 12:00 | 2022-05-08 13:00 | Spring | FALSE | nonsummer
2022-05-08 13:00 | 2022-05-08 14:00 | Spring | FALSE | nonsummer
2022-05-08 14:00 | 2022-05-08 15:00 | Spring | FALSE | nonsummer
2022-05-08 15:00 | 2022-05-08 16:00 | Spring | FALSE | nonsummer
2022-05-08 16:00 | 2022-05-08 17:00 | Spring | FALSE | nonsummer
2022-05-08 17:00 | 2022-05-08 18:00 | Spring | TRUE | nonsummer
2022-05-08 18:00 | 2022-05-08 19:00 | Spring | TRUE | nonsummer
2022-05-08 19:00 | 2022-05-08 20:00 | Spring | TRUE | nonsummer
2022-05-08 20:00 | 2022-05-08 21:00 | Spring | TRUE | nonsummer
2022-05-08 21:00 | 2022-05-08 22:00 | Spring | TRUE | nonsummer
2022-05-08 22:00 | 2022-05-08 23:00 | Spring | FALSE | nonsummer
2022-05-08 23:00 | 2022-05-09 | Spring | FALSE | nonsummer
2022-05-09 | 2022-05-09 01:00 | Spring | FALSE | nonsummer
2022-05-09 01:00 | 2022-05-09 02:00 | Spring | FALSE | nonsummer
2022-05-09 02:00 | 2022-05-09 03:00 | Spring | FALSE | nonsummer
2022-05-09 03:00 | 2022-05-09 04:00 | Spring | FALSE | nonsummer
2022-05-09 04:00 | 2022-05-09 05:00 | Spring | FALSE | nonsummer
2022-05-09 05:00 | 2022-05-09 06:00 | Spring | FALSE | nonsummer
2022-05-09 06:00 | 2022-05-09 07:00 | Spring | FALSE | nonsummer
2022-05-09 07:00 | 2022-05-09 08:00 | Spring | FALSE | nonsummer
2022-05-09 08:00 | 2022-05-09 09:00 | Spring | FALSE | nonsummer
2022-05-09 09:00 | 2022-05-09 10:00 | Spring | FALSE | nonsummer
2022-05-09 10:00 | 2022-05-09 11:00 | Spring | FALSE | nonsummer
2022-05-09 11:00 | 2022-05-09 12:00 | Spring | FALSE | nonsummer
2022-05-09 12:00 | 2022-05-09 13:00 | Spring | FALSE | nonsummer
2022-05-09 13:00 | 2022-05-09 14:00 | Spring | FALSE | nonsummer
2022-05-09 14:00 | 2022-05-09 15:00 | Spring | FALSE | nonsummer
2022-05-09 15:00 | 2022-05-09 16:00 | Spring | FALSE | nonsummer
2022-05-09 16:00 | 2022-05-09 17:00 | Spring | FALSE | nonsummer
2022-05-09 17:00 | 2022-05-09 18:00 | Spring | TRUE | nonsummer
2022-05-09 18:00 | 2022-05-09 19:00 | Spring | TRUE | nonsummer
2022-05-09 19:00 | 2022-05-09 20:00 | Spring | TRUE | nonsummer
2022-05-09 20:00 | 2022-05-09 21:00 | Spring | TRUE | nonsummer
2022-05-09 21:00 | 2022-05-09 22:00 | Spring | TRUE | nonsummer
2022-05-09 22:00 | 2022-05-09 23:00 | Spring | FALSE | nonsummer
2022-05-09 23:00 | 2022-05-10 | Spring | FALSE | nonsummer
2022-05-10 | 2022-05-10 01:00 | Spring | FALSE | nonsummer
2022-05-10 01:00 | 2022-05-10 02:00 | Spring | FALSE | nonsummer
2022-05-10 02:00 | 2022-05-10 03:00 | Spring | FALSE | nonsummer
2022-05-10 03:00 | 2022-05-10 04:00 | Spring | FALSE | nonsummer
2022-05-10 04:00 | 2022-05-10 05:00 | Spring | FALSE | nonsummer
2022-05-10 05:00 | 2022-05-10 06:00 | Spring | FALSE | nonsummer
2022-05-10 06:00 | 2022-05-10 07:00 | Spring | FALSE | nonsummer
2022-05-10 07:00 | 2022-05-10 08:00 | Spring | FALSE | nonsummer
2022-05-10 08:00 | 2022-05-10 09:00 | Spring | FALSE | nonsummer
2022-05-10 09:00 | 2022-05-10 10:00 | Spring | FALSE | nonsummer
2022-05-10 10:00 | 2022-05-10 11:00 | Spring | FALSE | nonsummer
2022-05-10 11:00 | 2022-05-10 12:00 | Spring | FALSE | nonsummer
2022-05-10 12:00 | 2022-05-10 13:00 | Spring | FALSE | nonsummer
2022-05-10 13:00 | 2022-05-10 14:00 | Spring | FALSE | nonsummer
2022-05-10 14:00 | 2022-05-10 15:00 | Spring | FALSE | nonsummer
2022-05-10 15:00 | 2022-05-10 16:00 | Spring | FALSE | nonsummer
2022-05-10 16:00 | 2022-05-10 17:00 | Spring | FALSE | nonsummer
2022-05-10 17:00 | 2022-05-10 18:00 | Spring | TRUE | nonsummer
2022-05-10 18:00 | 2022-05-10 19:00 | Spring | TRUE | nonsummer
2022-05-10 19:00 | 2022-05-10 20:00 | Spring | TRUE | nonsummer
2022-05-10 20:00 | 2022-05-10 21:00 | Spring | TRUE | nonsummer
2022-05-10 21:00 | 2022-05-10 22:00 | Spring | TRUE | nonsummer
2022-05-10 22:00 | 2022-05-10 23:00 | Spring | FALSE | nonsummer
2022-05-10 23:00 | 2022-05-11 | Spring | FALSE | nonsummer
2022-05-11 | 2022-05-11 01:00 | Spring | FALSE | nonsummer
2022-05-11 01:00 | 2022-05-11 02:00 | Spring | FALSE | nonsummer
2022-05-11 02:00 | 2022-05-11 03:00 | Spring | FALSE | nonsummer
2022-05-11 03:00 | 2022-05-11 04:00 | Spring | FALSE | nonsummer
2022-05-11 04:00 | 2022-05-11 05:00 | Spring | FALSE | nonsummer
2022-05-11 05:00 | 2022-05-11 06:00 | Spring | FALSE | nonsummer
2022-05-11 06:00 | 2022-05-11 07:00 | Spring | FALSE | nonsummer
2022-05-11 07:00 | 2022-05-11 08:00 | Spring | FALSE | nonsummer
2022-05-11 08:00 | 2022-05-11 09:00 | Spring | FALSE | nonsummer
2022-05-11 09:00 | 2022-05-11 10:00 | Spring | FALSE | nonsummer
2022-05-11 10:00 | 2022-05-11 11:00 | Spring | FALSE | nonsummer
2022-05-11 11:00 | 2022-05-11 12:00 | Spring | FALSE | nonsummer
2022-05-11 12:00 | 2022-05-11 13:00 | Spring | FALSE | nonsummer
2022-05-11 13:00 | 2022-05-11 14:00 | Spring | FALSE | nonsummer
2022-05-11 14:00 | 2022-05-11 15:00 | Spring | FALSE | nonsummer
2022-05-11 15:00 | 2022-05-11 16:00 | Spring | FALSE | nonsummer
2022-05-11 16:00 | 2022-05-11 17:00 | Spring | FALSE | nonsummer
2022-05-11 17:00 | 2022-05-11 18:00 | Spring | TRUE | nonsummer
2022-05-11 18:00 | 2022-05-11 19:00 | Spring | TRUE | nonsummer
2022-05-11 19:00 | 2022-05-11 20:00 | Spring | TRUE | nonsummer
2022-05-11 20:00 | 2022-05-11 21:00 | Spring | TRUE | nonsummer
2022-05-11 21:00 | 2022-05-11 22:00 | Spring | TRUE | nonsummer
2022-05-11 22:00 | 2022-05-11 23:00 | Spring | FALSE | nonsummer
2022-05-11 23:00 | 2022-05-12 | Spring | FALSE | nonsummer
2022-05-12 | 2022-05-12 01:00 | Spring | FALSE | nonsummer
2022-05-12 01:00 | 2022-05-12 02:00 | Spring | FALSE | nonsummer
2022-05-12 02:00 | 2022-05-12 03:00 | Spring | FALSE | nonsummer
2022-05-12 03:00 | 2022-05-12 04:00 | Spring | FALSE | nonsummer
2022-05-12 04:00 | 2022-05-12 05:00 | Spring | FALSE | nonsummer
2022-05-12 05:00 | 2022-05-12 06:00 | Spring | FALSE | nonsummer
2022-05-12 06:00 | 2022-05-12 07:00 | Spring | FALSE | nonsummer
2022-05-12 07:00 | 2022-05-12 08:00 | Spring | FALSE | nonsummer
2022-05-12 08:00 | 2022-05-12 09:00 | Spring | FALSE | nonsummer
2022-05-12 09:00 | 2022-05-12 10:00 | Spring | FALSE | nonsummer
2022-05-12 10:00 | 2022-05-12 11:00 | Spring | FALSE | nonsummer
2022-05-12 11:00 | 2022-05-12 12:00 | Spring | FALSE | nonsummer
2022-05-12 12:00 | 2022-05-12 13:00 | Spring | FALSE | nonsummer
2022-05-12 13:00 | 2022-05-12 14:00 | Spring | FALSE | nonsummer
2022-05-12 14:00 | 2022-05-12 15:00 | Spring | FALSE | nonsummer
2022-05-12 15:00 | 2022-05-12 16:00 | Spring | FALSE | nonsummer
2022-05-12 16:00 | 2022-05-12 17:00 | Spring | FALSE | nonsummer
2022-05-12 17:00 | 2022-05-12 18:00 | Spring | TRUE | nonsummer
2022-05-12 18:00 | 2022-05-12 19:00 | Spring | TRUE | nonsummer
2022-05-12 19:00 | 2022-05-12 20:00 | Spring | TRUE | nonsummer
2022-05-12 20:00 | 2022-05-12 21:00 | Spring | TRUE | nonsummer
2022-05-12 21:00 | 2022-05-12 22:00 | Spring | TRUE | nonsummer
2022-05-12 22:00 | 2022-05-12 23:00 | Spring | FALSE | nonsummer
2022-05-12 23:00 | 2022-05-13 | Spring | FALSE | nonsummer
2022-05-13 | 2022-05-13 01:00 | Spring | FALSE | nonsummer
2022-05-13 01:00 | 2022-05-13 02:00 | Spring | FALSE | nonsummer
2022-05-13 02:00 | 2022-05-13 03:00 | Spring | FALSE | nonsummer
2022-05-13 03:00 | 2022-05-13 04:00 | Spring | FALSE | nonsummer
2022-05-13 04:00 | 2022-05-13 05:00 | Spring | FALSE | nonsummer
2022-05-13 05:00 | 2022-05-13 06:00 | Spring | FALSE | nonsummer
2022-05-13 06:00 | 2022-05-13 07:00 | Spring | FALSE | nonsummer
2022-05-13 07:00 | 2022-05-13 08:00 | Spring | FALSE | nonsummer
2022-05-13 08:00 | 2022-05-13 09:00 | Spring | FALSE | nonsummer
2022-05-13 09:00 | 2022-05-13 10:00 | Spring | FALSE | nonsummer
2022-05-13 10:00 | 2022-05-13 11:00 | Spring | FALSE | nonsummer
2022-05-13 11:00 | 2022-05-13 12:00 | Spring | FALSE | nonsummer
2022-05-13 12:00 | 2022-05-13 13:00 | Spring | FALSE | nonsummer
2022-05-13 13:00 | 2022-05-13 14:00 | Spring | FALSE | nonsummer
2022-05-13 14:00 | 2022-05-13 15:00 | Spring | FALSE | nonsummer
2022-05-13 15:00 | 2022-05-13 16:00 | Spring | FALSE | nonsummer
2022-05-13 16:00 | 2022-05-13 17:00 | Spring | FALSE | nonsummer
2022-05-13 17:00 | 2022-05-13 18:00 | Spring | TRUE | nonsummer
2022-05-13 18:00 | 2022-05-13 19:00 | Spring | TRUE | nonsummer
2022-05-13 19:00 | 2022-05-13 20:00 | Spring | TRUE | nonsummer
2022-05-13 20:00 | 2022-05-13 21:00 | Spring | TRUE | nonsummer
2022-05-13 21:00 | 2022-05-13 22:00 | Spring | TRUE | nonsummer
2022-05-13 22:00 | 2022-05-13 23:00 | Spring | FALSE | nonsummer
2022-05-13 23:00 | 2022-05-14 | Spring | FALSE | nonsummer
2022-05-14 | 2022-05-14 01:00 | Spring | FALSE | nonsummer
2022-05-14 01:00 | 2022-05-14 02:00 | Spring | FALSE | nonsummer
2022-05-14 02:00 | 2022-05-14 03:00 | Spring | FALSE | nonsummer
2022-05-14 03:00 | 2022-05-14 04:00 | Spring | FALSE | nonsummer
2022-05-14 04:00 | 2022-05-14 05:00 | Spring | FALSE | nonsummer
2022-05-14 05:00 | 2022-05-14 06:00 | Spring | FALSE | nonsummer
2022-05-14 06:00 | 2022-05-14 07:00 | Spring | FALSE | nonsummer
2022-05-14 07:00 | 2022-05-14 08:00 | Spring | FALSE | nonsummer
2022-05-14 08:00 | 2022-05-14 09:00 | Spring | FALSE | nonsummer
2022-05-14 09:00 | 2022-05-14 10:00 | Spring | FALSE | nonsummer
2022-05-14 10:00 | 2022-05-14 11:00 | Spring | FALSE | nonsummer
2022-05-14 11:00 | 2022-05-14 12:00 | Spring | FALSE | nonsummer
2022-05-14 12:00 | 2022-05-14 13:00 | Spring | FALSE | nonsummer
2022-05-14 13:00 | 2022-05-14 14:00 | Spring | FALSE | nonsummer
2022-05-14 14:00 | 2022-05-14 15:00 | Spring | FALSE | nonsummer
2022-05-14 15:00 | 2022-05-14 16:00 | Spring | FALSE | nonsummer
2022-05-14 16:00 | 2022-05-14 17:00 | Spring | FALSE | nonsummer
2022-05-14 17:00 | 2022-05-14 18:00 | Spring | TRUE | nonsummer
2022-05-14 18:00 | 2022-05-14 19:00 | Spring | TRUE | nonsummer
2022-05-14 19:00 | 2022-05-14 20:00 | Spring | TRUE | nonsummer
2022-05-14 20:00 | 2022-05-14 21:00 | Spring | TRUE | nonsummer
2022-05-14 21:00 | 2022-05-14 22:00 | Spring | TRUE | nonsummer
2022-05-14 22:00 | 2022-05-14 23:00 | Spring | FALSE | nonsummer
2022-05-14 23:00 | 2022-05-15 | Spring | FALSE | nonsummer
2022-05-15 | 2022-05-15 01:00 | Spring | FALSE | nonsummer
2022-05-15 01:00 | 2022-05-15 02:00 | Spring | FALSE | nonsummer
2022-05-15 02:00 | 2022-05-15 03:00 | Spring | FALSE | nonsummer
2022-05-15 03:00 | 2022-05-15 04:00 | Spring | FALSE | nonsummer
2022-05-15 04:00 | 2022-05-15 05:00 | Spring | FALSE | nonsummer
2022-05-15 05:00 | 2022-05-15 06:00 | Spring | FALSE | nonsummer
2022-05-15 06:00 | 2022-05-15 07:00 | Spring | FALSE | nonsummer
2022-05-15 07:00 | 2022-05-15 08:00 | Spring | FALSE | nonsummer
2022-05-15 08:00 | 2022-05-15 09:00 | Spring | FALSE | nonsummer
2022-05-15 09:00 | 2022-05-15 10:00 | Spring | FALSE | nonsummer
2022-05-15 10:00 | 2022-05-15 11:00 | Spring | FALSE | nonsummer
2022-05-15 11:00 | 2022-05-15 12:00 | Spring | FALSE | nonsummer
2022-05-15 12:00 | 2022-05-15 13:00 | Spring | FALSE | nonsummer
2022-05-15 13:00 | 2022-05-15 14:00 | Spring | FALSE | nonsummer
2022-05-15 14:00 | 2022-05-15 15:00 | Spring | FALSE | nonsummer
2022-05-15 15:00 | 2022-05-15 16:00 | Spring | FALSE | nonsummer
2022-05-15 16:00 | 2022-05-15 17:00 | Spring | FALSE | nonsummer
2022-05-15 17:00 | 2022-05-15 18:00 | Spring | TRUE | nonsummer
2022-05-15 18:00 | 2022-05-15 19:00 | Spring | TRUE | nonsummer
2022-05-15 19:00 | 2022-05-15 20:00 | Spring | TRUE | nonsummer
2022-05-15 20:00 | 2022-05-15 21:00 | Spring | TRUE | nonsummer
2022-05-15 21:00 | 2022-05-15 22:00 | Spring | TRUE | nonsummer
2022-05-15 22:00 | 2022-05-15 23:00 | Spring | FALSE | nonsummer
2022-05-15 23:00 | 2022-05-16 | Spring | FALSE | nonsummer
2022-05-16 | 2022-05-16 01:00 | Spring | FALSE | nonsummer
2022-05-16 01:00 | 2022-05-16 02:00 | Spring | FALSE | nonsummer
2022-05-16 02:00 | 2022-05-16 03:00 | Spring | FALSE | nonsummer
2022-05-16 03:00 | 2022-05-16 04:00 | Spring | FALSE | nonsummer
2022-05-16 04:00 | 2022-05-16 05:00 | Spring | FALSE | nonsummer
2022-05-16 05:00 | 2022-05-16 06:00 | Spring | FALSE | nonsummer
2022-05-16 06:00 | 2022-05-16 07:00 | Spring | FALSE | nonsummer
2022-05-16 07:00 | 2022-05-16 08:00 | Spring | FALSE | nonsummer
2022-05-16 08:00 | 2022-05-16 09:00 | Spring | FALSE | nonsummer
2022-05-16 09:00 | 2022-05-16 10:00 | Spring | FALSE | nonsummer
2022-05-16 10:00 | 2022-05-16 11:00 | Spring | FALSE | nonsummer
2022-05-16 11:00 | 2022-05-16 12:00 | Spring | FALSE | nonsummer
2022-05-16 12:00 | 2022-05-16 13:00 | Spring | FALSE | nonsummer
2022-05-16 13:00 | 2022-05-16 14:00 | Spring | FALSE | nonsummer
2022-05-16 14:00 | 2022-05-16 15:00 | Spring | FALSE | nonsummer
2022-05-16 15:00 | 2022-05-16 16:00 | Spring | FALSE | nonsummer
2022-05-16 16:00 | 2022-05-16 17:00 | Spring | FALSE | nonsummer
2022-05-16 17:00 | 2022-05-16 18:00 | Spring | TRUE | nonsummer
2022-05-16 18:00 | 2022-05-16 19:00 | Spring | TRUE | nonsummer
2022-05-16 19:00 | 2022-05-16 20:00 | Spring | TRUE | nonsummer
2022-05-16 20:00 | 2022-05-16 21:00 | Spring | TRUE | nonsummer
2022-05-16 21:00 | 2022-05-16 22:00 | Spring | TRUE | nonsummer
2022-05-16 22:00 | 2022-05-16 23:00 | Spring | FALSE | nonsummer
2022-05-16 23:00 | 2022-05-17 | Spring | FALSE | nonsummer
2022-05-17 | 2022-05-17 01:00 | Spring | FALSE | nonsummer
2022-05-17 01:00 | 2022-05-17 02:00 | Spring | FALSE | nonsummer
2022-05-17 02:00 | 2022-05-17 03:00 | Spring | FALSE | nonsummer
2022-05-17 03:00 | 2022-05-17 04:00 | Spring | FALSE | nonsummer
2022-05-17 04:00 | 2022-05-17 05:00 | Spring | FALSE | nonsummer
2022-05-17 05:00 | 2022-05-17 06:00 | Spring | FALSE | nonsummer
2022-05-17 06:00 | 2022-05-17 07:00 | Spring | FALSE | nonsummer
2022-05-17 07:00 | 2022-05-17 08:00 | Spring | FALSE | nonsummer
2022-05-17 08:00 | 2022-05-17 09:00 | Spring | FALSE | nonsummer
2022-05-17 09:00 | 2022-05-17 10:00 | Spring | FALSE | nonsummer
2022-05-17 10:00 | 2022-05-17 11:00 | Spring | FALSE | nonsummer
2022-05-17 11:00 | 2022-05-17 12:00 | Spring | FALSE | nonsummer
2022-05-17 12:00 | 2022-05-17 13:00 | Spring | FALSE | nonsummer
2022-05-17 13:00 | 2022-05-17 14:00 | Spring | FALSE | nonsummer
2022-05-17 14:00 | 2022-05-17 15:00 | Spring | FALSE | nonsummer
2022-05-17 15:00 | 2022-05-17 16:00 | Spring | FALSE | nonsummer
2022-05-17 16:00 | 2022-05-17 17:00 | Spring | FALSE | nonsummer
2022-05-17 17:00 | 2022-05-17 18:00 | Spring | TRUE | nonsummer
2022-05-17 18:00 | 2022-05-17 19:00 | Spring | TRUE | nonsummer
2022-05-17 19:00 | 2022-05-17 20:00 | Spring | TRUE | nonsummer
2022-05-17 20:00 | 2022-05-17 21:00 | Spring | TRUE | nonsummer
2022-05-17 21:00 | 2022-05-17 22:00 | Spring | TRUE | nonsummer
2022-05-17 22:00 | 2022-05-17 23:00 | Spring | FALSE | nonsummer
2022-05-17 23:00 | 2022-05-18 | Spring | FALSE | nonsummer
2022-05-18 | 2022-05-18 01:00 | Spring | FALSE | nonsummer
2022-05-18 01:00 | 2022-05-18 02:00 | Spring | FALSE | nonsummer
2022-05-18 02:00 | 2022-05-18 03:00 | Spring | FALSE | nonsummer
2022-05-18 03:00 | 2022-05-18 04:00 | Spring | FALSE | nonsummer
2022-05-18 04:00 | 2022-05-18 05:00 | Spring | FALSE | nonsummer
2022-05-18 05:00 | 2022-05-18 06:00 | Spring | FALSE | nonsummer
2022-05-18 06:00 | 2022-05-18 07:00 | Spring | FALSE | nonsummer
2022-05-18 07:00 | 2022-05-18 08:00 | Spring | FALSE | nonsummer
2022-05-18 08:00 | 2022-05-18 09:00 | Spring | FALSE | nonsummer
2022-05-18 09:00 | 2022-05-18 10:00 | Spring | FALSE | nonsummer
2022-05-18 10:00 | 2022-05-18 11:00 | Spring | FALSE | nonsummer
2022-05-18 11:00 | 2022-05-18 12:00 | Spring | FALSE | nonsummer
2022-05-18 12:00 | 2022-05-18 13:00 | Spring | FALSE | nonsummer
2022-05-18 13:00 | 2022-05-18 14:00 | Spring | FALSE | nonsummer
2022-05-18 14:00 | 2022-05-18 15:00 | Spring | FALSE | nonsummer
2022-05-18 15:00 | 2022-05-18 16:00 | Spring | FALSE | nonsummer
2022-05-18 16:00 | 2022-05-18 17:00 | Spring | FALSE | nonsummer
2022-05-18 17:00 | 2022-05-18 18:00 | Spring | TRUE | nonsummer
2022-05-18 18:00 | 2022-05-18 19:00 | Spring | TRUE | nonsummer
2022-05-18 19:00 | 2022-05-18 20:00 | Spring | TRUE | nonsummer
2022-05-18 20:00 | 2022-05-18 21:00 | Spring | TRUE | nonsummer
2022-05-18 21:00 | 2022-05-18 22:00 | Spring | TRUE | nonsummer
2022-05-18 22:00 | 2022-05-18 23:00 | Spring | FALSE | nonsummer
2022-05-18 23:00 | 2022-05-19 | Spring | FALSE | nonsummer
2022-05-19 | 2022-05-19 01:00 | Spring | FALSE | nonsummer
2022-05-19 01:00 | 2022-05-19 02:00 | Spring | FALSE | nonsummer
2022-05-19 02:00 | 2022-05-19 03:00 | Spring | FALSE | nonsummer
2022-05-19 03:00 | 2022-05-19 04:00 | Spring | FALSE | nonsummer
2022-05-19 04:00 | 2022-05-19 05:00 | Spring | FALSE | nonsummer
2022-05-19 05:00 | 2022-05-19 06:00 | Spring | FALSE | nonsummer
2022-05-19 06:00 | 2022-05-19 07:00 | Spring | FALSE | nonsummer
2022-05-19 07:00 | 2022-05-19 08:00 | Spring | FALSE | nonsummer
2022-05-19 08:00 | 2022-05-19 09:00 | Spring | FALSE | nonsummer
2022-05-19 09:00 | 2022-05-19 10:00 | Spring | FALSE | nonsummer
2022-05-19 10:00 | 2022-05-19 11:00 | Spring | FALSE | nonsummer
2022-05-19 11:00 | 2022-05-19 12:00 | Spring | FALSE | nonsummer
2022-05-19 12:00 | 2022-05-19 13:00 | Spring | FALSE | nonsummer
2022-05-19 13:00 | 2022-05-19 14:00 | Spring | FALSE | nonsummer
2022-05-19 14:00 | 2022-05-19 15:00 | Spring | FALSE | nonsummer
2022-05-19 15:00 | 2022-05-19 16:00 | Spring | FALSE | nonsummer
2022-05-19 16:00 | 2022-05-19 17:00 | Spring | FALSE | nonsummer
2022-05-19 17:00 | 2022-05-19 18:00 | Spring | TRUE | nonsummer
2022-05-19 18:00 | 2022-05-19 19:00 | Spring | TRUE | nonsummer
2022-05-19 19:00 | 2022-05-19 20:00 | Spring | TRUE | nonsummer
2022-05-19 20:00 | 2022-05-19 21:00 | Spring | TRUE | nonsummer
2022-05-19 21:00 | 2022-05-19 22:00 | Spring | TRUE | nonsummer
2022-05-19 22:00 | 2022-05-19 23:00 | Spring | FALSE | nonsummer
2022-05-19 23:00 | 2022-05-20 | Spring | FALSE | nonsummer
2022-05-20 | 2022-05-20 01:00 | Spring | FALSE | nonsummer
2022-05-20 01:00 | 2022-05-20 02:00 | Spring | FALSE | nonsummer
2022-05-20 02:00 | 2022-05-20 03:00 | Spring | FALSE | nonsummer
2022-05-20 03:00 | 2022-05-20 04:00 | Spring | FALSE | nonsummer
2022-05-20 04:00 | 2022-05-20 05:00 | Spring | FALSE | nonsummer
2022-05-20 05:00 | 2022-05-20 06:00 | Spring | FALSE | nonsummer
2022-05-20 06:00 | 2022-05-20 07:00 | Spring | FALSE | nonsummer
2022-05-20 07:00 | 2022-05-20 08:00 | Spring | FALSE | nonsummer
2022-05-20 08:00 | 2022-05-20 09:00 | Spring | FALSE | nonsummer
2022-05-20 09:00 | 2022-05-20 10:00 | Spring | FALSE | nonsummer
2022-05-20 10:00 | 2022-05-20 11:00 | Spring | FALSE | nonsummer
2022-05-20 11:00 | 2022-05-20 12:00 | Spring | FALSE | nonsummer
2022-05-20 12:00 | 2022-05-20 13:00 | Spring | FALSE | nonsummer
2022-05-20 13:00 | 2022-05-20 14:00 | Spring | FALSE | nonsummer
2022-05-20 14:00 | 2022-05-20 15:00 | Spring | FALSE | nonsummer
2022-05-20 15:00 | 2022-05-20 16:00 | Spring | FALSE | nonsummer
2022-05-20 16:00 | 2022-05-20 17:00 | Spring | FALSE | nonsummer
2022-05-20 17:00 | 2022-05-20 18:00 | Spring | TRUE | nonsummer
2022-05-20 18:00 | 2022-05-20 19:00 | Spring | TRUE | nonsummer
2022-05-20 19:00 | 2022-05-20 20:00 | Spring | TRUE | nonsummer
2022-05-20 20:00 | 2022-05-20 21:00 | Spring | TRUE | nonsummer
2022-05-20 21:00 | 2022-05-20 22:00 | Spring | TRUE | nonsummer
2022-05-20 22:00 | 2022-05-20 23:00 | Spring | FALSE | nonsummer
2022-05-20 23:00 | 2022-05-21 | Spring | FALSE | nonsummer
2022-05-21 | 2022-05-21 01:00 | Spring | FALSE | nonsummer
2022-05-21 01:00 | 2022-05-21 02:00 | Spring | FALSE | nonsummer
2022-05-21 02:00 | 2022-05-21 03:00 | Spring | FALSE | nonsummer
2022-05-21 03:00 | 2022-05-21 04:00 | Spring | FALSE | nonsummer
2022-05-21 04:00 | 2022-05-21 05:00 | Spring | FALSE | nonsummer
2022-05-21 05:00 | 2022-05-21 06:00 | Spring | FALSE | nonsummer
2022-05-21 06:00 | 2022-05-21 07:00 | Spring | FALSE | nonsummer
2022-05-21 07:00 | 2022-05-21 08:00 | Spring | FALSE | nonsummer
2022-05-21 08:00 | 2022-05-21 09:00 | Spring | FALSE | nonsummer
2022-05-21 09:00 | 2022-05-21 10:00 | Spring | FALSE | nonsummer
2022-05-21 10:00 | 2022-05-21 11:00 | Spring | FALSE | nonsummer
2022-05-21 11:00 | 2022-05-21 12:00 | Spring | FALSE | nonsummer
2022-05-21 12:00 | 2022-05-21 13:00 | Spring | FALSE | nonsummer
2022-05-21 13:00 | 2022-05-21 14:00 | Spring | FALSE | nonsummer
2022-05-21 14:00 | 2022-05-21 15:00 | Spring | FALSE | nonsummer
2022-05-21 15:00 | 2022-05-21 16:00 | Spring | FALSE | nonsummer
2022-05-21 16:00 | 2022-05-21 17:00 | Spring | FALSE | nonsummer
2022-05-21 17:00 | 2022-05-21 18:00 | Spring | TRUE | nonsummer
2022-05-21 18:00 | 2022-05-21 19:00 | Spring | TRUE | nonsummer
2022-05-21 19:00 | 2022-05-21 20:00 | Spring | TRUE | nonsummer
2022-05-21 20:00 | 2022-05-21 21:00 | Spring | TRUE | nonsummer
2022-05-21 21:00 | 2022-05-21 22:00 | Spring | TRUE | nonsummer
2022-05-21 22:00 | 2022-05-21 23:00 | Spring | FALSE | nonsummer
2022-05-21 23:00 | 2022-05-22 | Spring | FALSE | nonsummer
2022-05-22 | 2022-05-22 01:00 | Spring | FALSE | nonsummer
2022-05-22 01:00 | 2022-05-22 02:00 | Spring | FALSE | nonsummer
2022-05-22 02:00 | 2022-05-22 03:00 | Spring | FALSE | nonsummer
2022-05-22 03:00 | 2022-05-22 04:00 | Spring | FALSE | nonsummer
2022-05-22 04:00 | 2022-05-22 05:00 | Spring | FALSE | nonsummer
2022-05-22 05:00 | 2022-05-22 06:00 | Spring | FALSE | nonsummer
2022-05-22 06:00 | 2022-05-22 07:00 | Spring | FALSE | nonsummer
2022-05-22 07:00 | 2022-05-22 08:00 | Spring | FALSE | nonsummer
2022-05-22 08:00 | 2022-05-22 09:00 | Spring | FALSE | nonsummer
2022-05-22 09:00 | 2022-05-22 10:00 | Spring | FALSE | nonsummer
2022-05-22 10:00 | 2022-05-22 11:00 | Spring | FALSE | nonsummer
2022-05-22 11:00 | 2022-05-22 12:00 | Spring | FALSE | nonsummer
2022-05-22 12:00 | 2022-05-22 13:00 | Spring | FALSE | nonsummer
2022-05-22 13:00 | 2022-05-22 14:00 | Spring | FALSE | nonsummer
2022-05-22 14:00 | 2022-05-22 15:00 | Spring | FALSE | nonsummer
2022-05-22 15:00 | 2022-05-22 16:00 | Spring | FALSE | nonsummer
2022-05-22 16:00 | 2022-05-22 17:00 | Spring | FALSE | nonsummer
2022-05-22 17:00 | 2022-05-22 18:00 | Spring | TRUE | nonsummer
2022-05-22 18:00 | 2022-05-22 19:00 | Spring | TRUE | nonsummer
2022-05-22 19:00 | 2022-05-22 20:00 | Spring | TRUE | nonsummer
2022-05-22 20:00 | 2022-05-22 21:00 | Spring | TRUE | nonsummer
2022-05-22 21:00 | 2022-05-22 22:00 | Spring | TRUE | nonsummer
2022-05-22 22:00 | 2022-05-22 23:00 | Spring | FALSE | nonsummer
2022-05-22 23:00 | 2022-05-23 | Spring | FALSE | nonsummer
2022-05-23 | 2022-05-23 01:00 | Spring | FALSE | nonsummer
2022-05-23 01:00 | 2022-05-23 02:00 | Spring | FALSE | nonsummer
2022-05-23 02:00 | 2022-05-23 03:00 | Spring | FALSE | nonsummer
2022-05-23 03:00 | 2022-05-23 04:00 | Spring | FALSE | nonsummer
2022-05-23 04:00 | 2022-05-23 05:00 | Spring | FALSE | nonsummer
2022-05-23 05:00 | 2022-05-23 06:00 | Spring | FALSE | nonsummer
2022-05-23 06:00 | 2022-05-23 07:00 | Spring | FALSE | nonsummer
2022-05-23 07:00 | 2022-05-23 08:00 | Spring | FALSE | nonsummer
2022-05-23 08:00 | 2022-05-23 09:00 | Spring | FALSE | nonsummer
2022-05-23 09:00 | 2022-05-23 10:00 | Spring | FALSE | nonsummer
2022-05-23 10:00 | 2022-05-23 11:00 | Spring | FALSE | nonsummer
2022-05-23 11:00 | 2022-05-23 12:00 | Spring | FALSE | nonsummer
2022-05-23 12:00 | 2022-05-23 13:00 | Spring | FALSE | nonsummer
2022-05-23 13:00 | 2022-05-23 14:00 | Spring | FALSE | nonsummer
2022-05-23 14:00 | 2022-05-23 15:00 | Spring | FALSE | nonsummer
2022-05-23 15:00 | 2022-05-23 16:00 | Spring | FALSE | nonsummer
2022-05-23 16:00 | 2022-05-23 17:00 | Spring | FALSE | nonsummer
2022-05-23 17:00 | 2022-05-23 18:00 | Spring | TRUE | nonsummer
2022-05-23 18:00 | 2022-05-23 19:00 | Spring | TRUE | nonsummer
2022-05-23 19:00 | 2022-05-23 20:00 | Spring | TRUE | nonsummer
2022-05-23 20:00 | 2022-05-23 21:00 | Spring | TRUE | nonsummer
2022-05-23 21:00 | 2022-05-23 22:00 | Spring | TRUE | nonsummer
2022-05-23 22:00 | 2022-05-23 23:00 | Spring | FALSE | nonsummer
2022-05-23 23:00 | 2022-05-24 | Spring | FALSE | nonsummer
2022-05-24 | 2022-05-24 01:00 | Spring | FALSE | nonsummer
2022-05-24 01:00 | 2022-05-24 02:00 | Spring | FALSE | nonsummer
2022-05-24 02:00 | 2022-05-24 03:00 | Spring | FALSE | nonsummer
2022-05-24 03:00 | 2022-05-24 04:00 | Spring | FALSE | nonsummer
2022-05-24 04:00 | 2022-05-24 05:00 | Spring | FALSE | nonsummer
2022-05-24 05:00 | 2022-05-24 06:00 | Spring | FALSE | nonsummer
2022-05-24 06:00 | 2022-05-24 07:00 | Spring | FALSE | nonsummer
2022-05-24 07:00 | 2022-05-24 08:00 | Spring | FALSE | nonsummer
2022-05-24 08:00 | 2022-05-24 09:00 | Spring | FALSE | nonsummer
2022-05-24 09:00 | 2022-05-24 10:00 | Spring | FALSE | nonsummer
2022-05-24 10:00 | 2022-05-24 11:00 | Spring | FALSE | nonsummer
2022-05-24 11:00 | 2022-05-24 12:00 | Spring | FALSE | nonsummer
2022-05-24 12:00 | 2022-05-24 13:00 | Spring | FALSE | nonsummer
2022-05-24 13:00 | 2022-05-24 14:00 | Spring | FALSE | nonsummer
2022-05-24 14:00 | 2022-05-24 15:00 | Spring | FALSE | nonsummer
2022-05-24 15:00 | 2022-05-24 16:00 | Spring | FALSE | nonsummer
2022-05-24 16:00 | 2022-05-24 17:00 | Spring | FALSE | nonsummer
2022-05-24 17:00 | 2022-05-24 18:00 | Spring | TRUE | nonsummer
2022-05-24 18:00 | 2022-05-24 19:00 | Spring | TRUE | nonsummer
2022-05-24 19:00 | 2022-05-24 20:00 | Spring | TRUE | nonsummer
2022-05-24 20:00 | 2022-05-24 21:00 | Spring | TRUE | nonsummer
2022-05-24 21:00 | 2022-05-24 22:00 | Spring | TRUE | nonsummer
2022-05-24 22:00 | 2022-05-24 23:00 | Spring | FALSE | nonsummer
2022-05-24 23:00 | 2022-05-25 | Spring | FALSE | nonsummer
2022-05-25 | 2022-05-25 01:00 | Spring | FALSE | nonsummer
2022-05-25 01:00 | 2022-05-25 02:00 | Spring | FALSE | nonsummer
2022-05-25 02:00 | 2022-05-25 03:00 | Spring | FALSE | nonsummer
2022-05-25 03:00 | 2022-05-25 04:00 | Spring | FALSE | nonsummer
2022-05-25 04:00 | 2022-05-25 05:00 | Spring | FALSE | nonsummer
2022-05-25 05:00 | 2022-05-25 06:00 | Spring | FALSE | nonsummer
2022-05-25 06:00 | 2022-05-25 07:00 | Spring | FALSE | nonsummer
2022-05-25 07:00 | 2022-05-25 08:00 | Spring | FALSE | nonsummer
2022-05-25 08:00 | 2022-05-25 09:00 | Spring | FALSE | nonsummer
2022-05-25 09:00 | 2022-05-25 10:00 | Spring | FALSE | nonsummer
2022-05-25 10:00 | 2022-05-25 11:00 | Spring | FALSE | nonsummer
2022-05-25 11:00 | 2022-05-25 12:00 | Spring | FALSE | nonsummer
2022-05-25 12:00 | 2022-05-25 13:00 | Spring | FALSE | nonsummer
2022-05-25 13:00 | 2022-05-25 14:00 | Spring | FALSE | nonsummer
2022-05-25 14:00 | 2022-05-25 15:00 | Spring | FALSE | nonsummer
2022-05-25 15:00 | 2022-05-25 16:00 | Spring | FALSE | nonsummer
2022-05-25 16:00 | 2022-05-25 17:00 | Spring | FALSE | nonsummer
2022-05-25 17:00 | 2022-05-25 18:00 | Spring | TRUE | nonsummer
2022-05-25 18:00 | 2022-05-25 19:00 | Spring | TRUE | nonsummer
2022-05-25 19:00 | 2022-05-25 20:00 | Spring | TRUE | nonsummer
2022-05-25 20:00 | 2022-05-25 21:00 | Spring | TRUE | nonsummer
2022-05-25 21:00 | 2022-05-25 22:00 | Spring | TRUE | nonsummer
2022-05-25 22:00 | 2022-05-25 23:00 | Spring | FALSE | nonsummer
2022-05-25 23:00 | 2022-05-26 | Spring | FALSE | nonsummer
2022-05-26 | 2022-05-26 01:00 | Spring | FALSE | nonsummer
2022-05-26 01:00 | 2022-05-26 02:00 | Spring | FALSE | nonsummer
2022-05-26 02:00 | 2022-05-26 03:00 | Spring | FALSE | nonsummer
2022-05-26 03:00 | 2022-05-26 04:00 | Spring | FALSE | nonsummer
2022-05-26 04:00 | 2022-05-26 05:00 | Spring | FALSE | nonsummer
2022-05-26 05:00 | 2022-05-26 06:00 | Spring | FALSE | nonsummer
2022-05-26 06:00 | 2022-05-26 07:00 | Spring | FALSE | nonsummer
2022-05-26 07:00 | 2022-05-26 08:00 | Spring | FALSE | nonsummer
2022-05-26 08:00 | 2022-05-26 09:00 | Spring | FALSE | nonsummer
2022-05-26 09:00 | 2022-05-26 10:00 | Spring | FALSE | nonsummer
2022-05-26 10:00 | 2022-05-26 11:00 | Spring | FALSE | nonsummer
2022-05-26 11:00 | 2022-05-26 12:00 | Spring | FALSE | nonsummer
2022-05-26 12:00 | 2022-05-26 13:00 | Spring | FALSE | nonsummer
2022-05-26 13:00 | 2022-05-26 14:00 | Spring | FALSE | nonsummer
2022-05-26 14:00 | 2022-05-26 15:00 | Spring | FALSE | nonsummer
2022-05-26 15:00 | 2022-05-26 16:00 | Spring | FALSE | nonsummer
2022-05-26 16:00 | 2022-05-26 17:00 | Spring | FALSE | nonsummer
2022-05-26 17:00 | 2022-05-26 18:00 | Spring | TRUE | nonsummer
2022-05-26 18:00 | 2022-05-26 19:00 | Spring | TRUE | nonsummer
2022-05-26 19:00 | 2022-05-26 20:00 | Spring | TRUE | nonsummer
2022-05-26 20:00 | 2022-05-26 21:00 | Spring | TRUE | nonsummer
2022-05-26 21:00 | 2022-05-26 22:00 | Spring | TRUE | nonsummer
2022-05-26 22:00 | 2022-05-26 23:00 | Spring | FALSE | nonsummer
2022-05-26 23:00 | 2022-05-27 | Spring | FALSE | nonsummer
2022-05-27 | 2022-05-27 01:00 | Spring | FALSE | nonsummer
2022-05-27 01:00 | 2022-05-27 02:00 | Spring | FALSE | nonsummer
2022-05-27 02:00 | 2022-05-27 03:00 | Spring | FALSE | nonsummer
2022-05-27 03:00 | 2022-05-27 04:00 | Spring | FALSE | nonsummer
2022-05-27 04:00 | 2022-05-27 05:00 | Spring | FALSE | nonsummer
2022-05-27 05:00 | 2022-05-27 06:00 | Spring | FALSE | nonsummer
2022-05-27 06:00 | 2022-05-27 07:00 | Spring | FALSE | nonsummer
2022-05-27 07:00 | 2022-05-27 08:00 | Spring | FALSE | nonsummer
2022-05-27 08:00 | 2022-05-27 09:00 | Spring | FALSE | nonsummer
2022-05-27 09:00 | 2022-05-27 10:00 | Spring | FALSE | nonsummer
2022-05-27 10:00 | 2022-05-27 11:00 | Spring | FALSE | nonsummer
2022-05-27 11:00 | 2022-05-27 12:00 | Spring | FALSE | nonsummer
2022-05-27 12:00 | 2022-05-27 13:00 | Spring | FALSE | nonsummer
2022-05-27 13:00 | 2022-05-27 14:00 | Spring | FALSE | nonsummer
2022-05-27 14:00 | 2022-05-27 15:00 | Spring | FALSE | nonsummer
2022-05-27 15:00 | 2022-05-27 16:00 | Spring | FALSE | nonsummer
2022-05-27 16:00 | 2022-05-27 17:00 | Spring | FALSE | nonsummer
2022-05-27 17:00 | 2022-05-27 18:00 | Spring | TRUE | nonsummer
2022-05-27 18:00 | 2022-05-27 19:00 | Spring | TRUE | nonsummer
2022-05-27 19:00 | 2022-05-27 20:00 | Spring | TRUE | nonsummer
2022-05-27 20:00 | 2022-05-27 21:00 | Spring | TRUE | nonsummer
2022-05-27 21:00 | 2022-05-27 22:00 | Spring | TRUE | nonsummer
2022-05-27 22:00 | 2022-05-27 23:00 | Spring | FALSE | nonsummer
2022-05-27 23:00 | 2022-05-28 | Spring | FALSE | nonsummer
2022-05-28 | 2022-05-28 01:00 | Spring | FALSE | nonsummer
2022-05-28 01:00 | 2022-05-28 02:00 | Spring | FALSE | nonsummer
2022-05-28 02:00 | 2022-05-28 03:00 | Spring | FALSE | nonsummer
2022-05-28 03:00 | 2022-05-28 04:00 | Spring | FALSE | nonsummer
2022-05-28 04:00 | 2022-05-28 05:00 | Spring | FALSE | nonsummer
2022-05-28 05:00 | 2022-05-28 06:00 | Spring | FALSE | nonsummer
2022-05-28 06:00 | 2022-05-28 07:00 | Spring | FALSE | nonsummer
2022-05-28 07:00 | 2022-05-28 08:00 | Spring | FALSE | nonsummer
2022-05-28 08:00 | 2022-05-28 09:00 | Spring | FALSE | nonsummer
2022-05-28 09:00 | 2022-05-28 10:00 | Spring | FALSE | nonsummer
2022-05-28 10:00 | 2022-05-28 11:00 | Spring | FALSE | nonsummer
2022-05-28 11:00 | 2022-05-28 12:00 | Spring | FALSE | nonsummer
2022-05-28 12:00 | 2022-05-28 13:00 | Spring | FALSE | nonsummer
2022-05-28 13:00 | 2022-05-28 14:00 | Spring | FALSE | nonsummer
2022-05-28 14:00 | 2022-05-28 15:00 | Spring | FALSE | nonsummer
2022-05-28 15:00 | 2022-05-28 16:00 | Spring | FALSE | nonsummer
2022-05-28 16:00 | 2022-05-28 17:00 | Spring | FALSE | nonsummer
2022-05-28 17:00 | 2022-05-28 18:00 | Spring | TRUE | nonsummer
2022-05-28 18:00 | 2022-05-28 19:00 | Spring | TRUE | nonsummer
2022-05-28 19:00 | 2022-05-28 20:00 | Spring | TRUE | nonsummer
2022-05-28 20:00 | 2022-05-28 21:00 | Spring | TRUE | nonsummer
2022-05-28 21:00 | 2022-05-28 22:00 | Spring | TRUE | nonsummer
2022-05-28 22:00 | 2022-05-28 23:00 | Spring | FALSE | nonsummer
2022-05-28 23:00 | 2022-05-29 | Spring | FALSE | nonsummer
2022-05-29 | 2022-05-29 01:00 | Spring | FALSE | nonsummer
2022-05-29 01:00 | 2022-05-29 02:00 | Spring | FALSE | nonsummer
2022-05-29 02:00 | 2022-05-29 03:00 | Spring | FALSE | nonsummer
2022-05-29 03:00 | 2022-05-29 04:00 | Spring | FALSE | nonsummer
2022-05-29 04:00 | 2022-05-29 05:00 | Spring | FALSE | nonsummer
2022-05-29 05:00 | 2022-05-29 06:00 | Spring | FALSE | nonsummer
2022-05-29 06:00 | 2022-05-29 07:00 | Spring | FALSE | nonsummer
2022-05-29 07:00 | 2022-05-29 08:00 | Spring | FALSE | nonsummer
2022-05-29 08:00 | 2022-05-29 09:00 | Spring | FALSE | nonsummer
2022-05-29 09:00 | 2022-05-29 10:00 | Spring | FALSE | nonsummer
2022-05-29 10:00 | 2022-05-29 11:00 | Spring | FALSE | nonsummer
2022-05-29 11:00 | 2022-05-29 12:00 | Spring | FALSE | nonsummer
2022-05-29 12:00 | 2022-05-29 13:00 | Spring | FALSE | nonsummer
2022-05-29 13:00 | 2022-05-29 14:00 | Spring | FALSE | nonsummer
2022-05-29 14:00 | 2022-05-29 15:00 | Spring | FALSE | nonsummer
2022-05-29 15:00 | 2022-05-29 16:00 | Spring | FALSE | nonsummer
2022-05-29 16:00 | 2022-05-29 17:00 | Spring | FALSE | nonsummer
2022-05-29 17:00 | 2022-05-29 18:00 | Spring | TRUE | nonsummer
2022-05-29 18:00 | 2022-05-29 19:00 | Spring | TRUE | nonsummer
2022-05-29 19:00 | 2022-05-29 20:00 | Spring | TRUE | nonsummer
2022-05-29 20:00 | 2022-05-29 21:00 | Spring | TRUE | nonsummer
2022-05-29 21:00 | 2022-05-29 22:00 | Spring | TRUE | nonsummer
2022-05-29 22:00 | 2022-05-29 23:00 | Spring | FALSE | nonsummer
2022-05-29 23:00 | 2022-05-30 | Spring | FALSE | nonsummer
2022-05-30 | 2022-05-30 01:00 | Spring | FALSE | nonsummer
2022-05-30 01:00 | 2022-05-30 02:00 | Spring | FALSE | nonsummer
2022-05-30 02:00 | 2022-05-30 03:00 | Spring | FALSE | nonsummer
2022-05-30 03:00 | 2022-05-30 04:00 | Spring | FALSE | nonsummer
2022-05-30 04:00 | 2022-05-30 05:00 | Spring | FALSE | nonsummer
2022-05-30 05:00 | 2022-05-30 06:00 | Spring | FALSE | nonsummer
2022-05-30 06:00 | 2022-05-30 07:00 | Spring | FALSE | nonsummer
2022-05-30 07:00 | 2022-05-30 08:00 | Spring | FALSE | nonsummer
2022-05-30 08:00 | 2022-05-30 09:00 | Spring | FALSE | nonsummer
2022-05-30 09:00 | 2022-05-30 10:00 | Spring | FALSE | nonsummer
2022-05-30 10:00 | 2022-05-30 11:00 | Spring | FALSE | nonsummer
2022-05-30 11:00 | 2022-05-30 12:00 | Spring | FALSE | nonsummer
2022-05-30 12:00 | 2022-05-30 13:00 | Spring | FALSE | nonsummer
2022-05-30 13:00 | 2022-05-30 14:00 | Spring | FALSE | nonsummer
2022-05-30 14:00 | 2022-05-30 15:00 | Spring | FALSE | nonsummer
2022-05-30 15:00 | 2022-05-30 16:00 | Spring | FALSE | nonsummer
2022-05-30 16:00 | 2022-05-30 17:00 | Spring | FALSE | nonsummer
2022-05-30 17:00 | 2022-05-30 18:00 | Spring | TRUE | nonsummer
2022-05-30 18:00 | 2022-05-30 19:00 | Spring | TRUE | nonsummer
2022-05-30 19:00 | 2022-05-30 20:00 | Spring | TRUE | nonsummer
2022-05-30 20:00 | 2022-05-30 21:00 | Spring | TRUE | nonsummer
2022-05-30 21:00 | 2022-05-30 22:00 | Spring | TRUE | nonsummer
2022-05-30 22:00 | 2022-05-30 23:00 | Spring | FALSE | nonsummer
2022-05-30 23:00 | 2022-05-31 | Spring | FALSE | nonsummer
2022-05-31 | 2022-05-31 01:00 | Spring | FALSE | nonsummer
2022-05-31 01:00 | 2022-05-31 02:00 | Spring | FALSE | nonsummer
2022-05-31 02:00 | 2022-05-31 03:00 | Spring | FALSE | nonsummer
2022-05-31 03:00 | 2022-05-31 04:00 | Spring | FALSE | nonsummer
2022-05-31 04:00 | 2022-05-31 05:00 | Spring | FALSE | nonsummer
2022-05-31 05:00 | 2022-05-31 06:00 | Spring | FALSE | nonsummer
2022-05-31 06:00 | 2022-05-31 07:00 | Spring | FALSE | nonsummer
2022-05-31 07:00 | 2022-05-31 08:00 | Spring | FALSE | nonsummer
2022-05-31 08:00 | 2022-05-31 09:00 | Spring | FALSE | nonsummer
2022-05-31 09:00 | 2022-05-31 10:00 | Spring | FALSE | nonsummer
2022-05-31 10:00 | 2022-05-31 11:00 | Spring | FALSE | nonsummer
2022-05-31 11:00 | 2022-05-31 12:00 | Spring | FALSE | nonsummer
2022-05-31 12:00 | 2022-05-31 13:00 | Spring | FALSE | nonsummer
2022-05-31 13:00 | 2022-05-31 14:00 | Spring | FALSE | nonsummer
2022-05-31 14:00 | 2022-05-31 15:00 | Spring | FALSE | nonsummer
2022-05-31 15:00 | 2022-05-31 16:00 | Spring | FALSE | nonsummer
2022-05-31 16:00 | 2022-05-31 17:00 | Spring | FALSE | nonsummer
2022-05-31 17:00 | 2022-05-31 18:00 | Spring | TRUE | nonsummer
2022-05-31 18:00 | 2022-05-31 19:00 | Spring | TRUE | nonsummer
2022-05-31 19:00 | 2022-05-31 20:00 | Spring | TRUE | nonsummer
2022-05-31 20:00 | 2022-05-31 21:00 | Spring | TRUE | nonsummer
2022-05-31 21:00 | 2022-05-31 22:00 | Spring | TRUE | nonsummer
2022-05-31 22:00 | 2022-05-31 23:00 | Spring | FALSE | nonsummer
2022-05-31 23:00 | 2022-06-01 | Spring | FALSE | nonsummer
2022-06-01 | 2022-06-01 01:00 | Summer | FALSE | summer
2022-06-01 01:00 | 2022-06-01 02:00 | Summer | FALSE | summer
2022-06-01 02:00 | 2022-06-01 03:00 | Summer | FALSE | summer
2022-06-01 03:00 | 2022-06-01 04:00 | Summer | FALSE | summer
2022-06-01 04:00 | 2022-06-01 05:00 | Summer | FALSE | summer
2022-06-01 05:00 | 2022-06-01 06:00 | Summer | FALSE | summer
2022-06-01 06:00 | 2022-06-01 07:00 | Summer | FALSE | summer
2022-06-01 07:00 | 2022-06-01 08:00 | Summer | FALSE | summer
2022-06-01 08:00 | 2022-06-01 09:00 | Summer | FALSE | summer
2022-06-01 09:00 | 2022-06-01 10:00 | Summer | FALSE | summer
2022-06-01 10:00 | 2022-06-01 11:00 | Summer | FALSE | summer
2022-06-01 11:00 | 2022-06-01 12:00 | Summer | FALSE | summer
2022-06-01 12:00 | 2022-06-01 13:00 | Summer | FALSE | summer
2022-06-01 13:00 | 2022-06-01 14:00 | Summer | FALSE | summer
2022-06-01 14:00 | 2022-06-01 15:00 | Summer | FALSE | summer
2022-06-01 15:00 | 2022-06-01 16:00 | Summer | FALSE | summer
2022-06-01 16:00 | 2022-06-01 17:00 | Summer | TRUE | summer
2022-06-01 17:00 | 2022-06-01 18:00 | Summer | TRUE | summer
2022-06-01 18:00 | 2022-06-01 19:00 | Summer | TRUE | summer
2022-06-01 19:00 | 2022-06-01 20:00 | Summer | TRUE | summer
2022-06-01 20:00 | 2022-06-01 21:00 | Summer | TRUE | summer
2022-06-01 21:00 | 2022-06-01 22:00 | Summer | FALSE | summer
2022-06-01 22:00 | 2022-06-01 23:00 | Summer | FALSE | summer
2022-06-01 23:00 | 2022-06-02 | Summer | FALSE | summer
2022-06-02 | 2022-06-02 01:00 | Summer | FALSE | summer
2022-06-02 01:00 | 2022-06-02 02:00 | Summer | FALSE | summer
2022-06-02 02:00 | 2022-06-02 03:00 | Summer | FALSE | summer
2022-06-02 03:00 | 2022-06-02 04:00 | Summer | FALSE | summer
2022-06-02 04:00 | 2022-06-02 05:00 | Summer | FALSE | summer
2022-06-02 05:00 | 2022-06-02 06:00 | Summer | FALSE | summer
2022-06-02 06:00 | 2022-06-02 07:00 | Summer | FALSE | summer
2022-06-02 07:00 | 2022-06-02 08:00 | Summer | FALSE | summer
2022-06-02 08:00 | 2022-06-02 09:00 | Summer | FALSE | summer
2022-06-02 09:00 | 2022-06-02 10:00 | Summer | FALSE | summer
2022-06-02 10:00 | 2022-06-02 11:00 | Summer | FALSE | summer
2022-06-02 11:00 | 2022-06-02 12:00 | Summer | FALSE | summer
2022-06-02 12:00 | 2022-06-02 13:00 | Summer | FALSE | summer
2022-06-02 13:00 | 2022-06-02 14:00 | Summer | FALSE | summer
2022-06-02 14:00 | 2022-06-02 15:00 | Summer | FALSE | summer
2022-06-02 15:00 | 2022-06-02 16:00 | Summer | FALSE | summer
2022-06-02 16:00 | 2022-06-02 17:00 | Summer | TRUE | summer
2022-06-02 17:00 | 2022-06-02 18:00 | Summer | TRUE | summer
2022-06-02 18:00 | 2022-06-02 19:00 | Summer | TRUE | summer
2022-06-02 19:00 | 2022-06-02 20:00 | Summer | TRUE | summer
2022-06-02 20:00 | 2022-06-02 21:00 | Summer | TRUE | summer
2022-06-02 21:00 | 2022-06-02 22:00 | Summer | FALSE | summer
2022-06-02 22:00 | 2022-06-02 23:00 | Summer | FALSE | summer
2022-06-02 23:00 | 2022-06-03 | Summer | FALSE | summer
2022-06-03 | 2022-06-03 01:00 | Summer | FALSE | summer
2022-06-03 01:00 | 2022-06-03 02:00 | Summer | FALSE | summer
2022-06-03 02:00 | 2022-06-03 03:00 | Summer | FALSE | summer
2022-06-03 03:00 | 2022-06-03 04:00 | Summer | FALSE | summer
2022-06-03 04:00 | 2022-06-03 05:00 | Summer | FALSE | summer
2022-06-03 05:00 | 2022-06-03 06:00 | Summer | FALSE | summer
2022-06-03 06:00 | 2022-06-03 07:00 | Summer | FALSE | summer
2022-06-03 07:00 | 2022-06-03 08:00 | Summer | FALSE | summer
2022-06-03 08:00 | 2022-06-03 09:00 | Summer | FALSE | summer
2022-06-03 09:00 | 2022-06-03 10:00 | Summer | FALSE | summer
2022-06-03 10:00 | 2022-06-03 11:00 | Summer | FALSE | summer
2022-06-03 11:00 | 2022-06-03 12:00 | Summer | FALSE | summer
2022-06-03 12:00 | 2022-06-03 13:00 | Summer | FALSE | summer
2022-06-03 13:00 | 2022-06-03 14:00 | Summer | FALSE | summer
2022-06-03 14:00 | 2022-06-03 15:00 | Summer | FALSE | summer
2022-06-03 15:00 | 2022-06-03 16:00 | Summer | FALSE | summer
2022-06-03 16:00 | 2022-06-03 17:00 | Summer | TRUE | summer
2022-06-03 17:00 | 2022-06-03 18:00 | Summer | TRUE | summer
2022-06-03 18:00 | 2022-06-03 19:00 | Summer | TRUE | summer
2022-06-03 19:00 | 2022-06-03 20:00 | Summer | TRUE | summer
2022-06-03 20:00 | 2022-06-03 21:00 | Summer | TRUE | summer
2022-06-03 21:00 | 2022-06-03 22:00 | Summer | FALSE | summer
2022-06-03 22:00 | 2022-06-03 23:00 | Summer | FALSE | summer
2022-06-03 23:00 | 2022-06-04 | Summer | FALSE | summer
2022-06-04 | 2022-06-04 01:00 | Summer | FALSE | summer
2022-06-04 01:00 | 2022-06-04 02:00 | Summer | FALSE | summer
2022-06-04 02:00 | 2022-06-04 03:00 | Summer | FALSE | summer
2022-06-04 03:00 | 2022-06-04 04:00 | Summer | FALSE | summer
2022-06-04 04:00 | 2022-06-04 05:00 | Summer | FALSE | summer
2022-06-04 05:00 | 2022-06-04 06:00 | Summer | FALSE | summer
2022-06-04 06:00 | 2022-06-04 07:00 | Summer | FALSE | summer
2022-06-04 07:00 | 2022-06-04 08:00 | Summer | FALSE | summer
2022-06-04 08:00 | 2022-06-04 09:00 | Summer | FALSE | summer
2022-06-04 09:00 | 2022-06-04 10:00 | Summer | FALSE | summer
2022-06-04 10:00 | 2022-06-04 11:00 | Summer | FALSE | summer
2022-06-04 11:00 | 2022-06-04 12:00 | Summer | FALSE | summer
2022-06-04 12:00 | 2022-06-04 13:00 | Summer | FALSE | summer
2022-06-04 13:00 | 2022-06-04 14:00 | Summer | FALSE | summer
2022-06-04 14:00 | 2022-06-04 15:00 | Summer | FALSE | summer
2022-06-04 15:00 | 2022-06-04 16:00 | Summer | FALSE | summer
2022-06-04 16:00 | 2022-06-04 17:00 | Summer | TRUE | summer
2022-06-04 17:00 | 2022-06-04 18:00 | Summer | TRUE | summer
2022-06-04 18:00 | 2022-06-04 19:00 | Summer | TRUE | summer
2022-06-04 19:00 | 2022-06-04 20:00 | Summer | TRUE | summer
2022-06-04 20:00 | 2022-06-04 21:00 | Summer | TRUE | summer
2022-06-04 21:00 | 2022-06-04 22:00 | Summer | FALSE | summer
2022-06-04 22:00 | 2022-06-04 23:00 | Summer | FALSE | summer
2022-06-04 23:00 | 2022-06-05 | Summer | FALSE | summer
2022-06-05 | 2022-06-05 01:00 | Summer | FALSE | summer
2022-06-05 01:00 | 2022-06-05 02:00 | Summer | FALSE | summer
2022-06-05 02:00 | 2022-06-05 03:00 | Summer | FALSE | summer
2022-06-05 03:00 | 2022-06-05 04:00 | Summer | FALSE | summer
2022-06-05 04:00 | 2022-06-05 05:00 | Summer | FALSE | summer
2022-06-05 05:00 | 2022-06-05 06:00 | Summer | FALSE | summer
2022-06-05 06:00 | 2022-06-05 07:00 | Summer | FALSE | summer
2022-06-05 07:00 | 2022-06-05 08:00 | Summer | FALSE | summer
2022-06-05 08:00 | 2022-06-05 09:00 | Summer | FALSE | summer
2022-06-05 09:00 | 2022-06-05 10:00 | Summer | FALSE | summer
2022-06-05 10:00 | 2022-06-05 11:00 | Summer | FALSE | summer
2022-06-05 11:00 | 2022-06-05 12:00 | Summer | FALSE | summer
2022-06-05 12:00 | 2022-06-05 13:00 | Summer | FALSE | summer
2022-06-05 13:00 | 2022-06-05 14:00 | Summer | FALSE | summer
2022-06-05 14:00 | 2022-06-05 15:00 | Summer | FALSE | summer
2022-06-05 15:00 | 2022-06-05 16:00 | Summer | FALSE | summer
2022-06-05 16:00 | 2022-06-05 17:00 | Summer | TRUE | summer
2022-06-05 17:00 | 2022-06-05 18:00 | Summer | TRUE | summer
2022-06-05 18:00 | 2022-06-05 19:00 | Summer | TRUE | summer
2022-06-05 19:00 | 2022-06-05 20:00 | Summer | TRUE | summer
2022-06-05 20:00 | 2022-06-05 21:00 | Summer | TRUE | summer
2022-06-05 21:00 | 2022-06-05 22:00 | Summer | FALSE | summer
2022-06-05 22:00 | 2022-06-05 23:00 | Summer | FALSE | summer
2022-06-05 23:00 | 2022-06-06 | Summer | FALSE | summer
2022-06-06 | 2022-06-06 01:00 | Summer | FALSE | summer
2022-06-06 01:00 | 2022-06-06 02:00 | Summer | FALSE | summer
2022-06-06 02:00 | 2022-06-06 03:00 | Summer | FALSE | summer
2022-06-06 03:00 | 2022-06-06 04:00 | Summer | FALSE | summer
2022-06-06 04:00 | 2022-06-06 05:00 | Summer | FALSE | summer
2022-06-06 05:00 | 2022-06-06 06:00 | Summer | FALSE | summer
2022-06-06 06:00 | 2022-06-06 07:00 | Summer | FALSE | summer
2022-06-06 07:00 | 2022-06-06 08:00 | Summer | FALSE | summer
2022-06-06 08:00 | 2022-06-06 09:00 | Summer | FALSE | summer
2022-06-06 09:00 | 2022-06-06 10:00 | Summer | FALSE | summer
2022-06-06 10:00 | 2022-06-06 11:00 | Summer | FALSE | summer
2022-06-06 11:00 | 2022-06-06 12:00 | Summer | FALSE | summer
2022-06-06 12:00 | 2022-06-06 13:00 | Summer | FALSE | summer
2022-06-06 13:00 | 2022-06-06 14:00 | Summer | FALSE | summer
2022-06-06 14:00 | 2022-06-06 15:00 | Summer | FALSE | summer
2022-06-06 15:00 | 2022-06-06 16:00 | Summer | FALSE | summer
2022-06-06 16:00 | 2022-06-06 17:00 | Summer | TRUE | summer
2022-06-06 17:00 | 2022-06-06 18:00 | Summer | TRUE | summer
2022-06-06 18:00 | 2022-06-06 19:00 | Summer | TRUE | summer
2022-06-06 19:00 | 2022-06-06 20:00 | Summer | TRUE | summer
2022-06-06 20:00 | 2022-06-06 21:00 | Summer | TRUE | summer
2022-06-06 21:00 | 2022-06-06 22:00 | Summer | FALSE | summer
2022-06-06 22:00 | 2022-06-06 23:00 | Summer | FALSE | summer
2022-06-06 23:00 | 2022-06-07 | Summer | FALSE | summer
2022-06-07 | 2022-06-07 01:00 | Summer | FALSE | summer
2022-06-07 01:00 | 2022-06-07 02:00 | Summer | FALSE | summer
2022-06-07 02:00 | 2022-06-07 03:00 | Summer | FALSE | summer
2022-06-07 03:00 | 2022-06-07 04:00 | Summer | FALSE | summer
2022-06-07 04:00 | 2022-06-07 05:00 | Summer | FALSE | summer
2022-06-07 05:00 | 2022-06-07 06:00 | Summer | FALSE | summer
2022-06-07 06:00 | 2022-06-07 07:00 | Summer | FALSE | summer
2022-06-07 07:00 | 2022-06-07 08:00 | Summer | FALSE | summer
2022-06-07 08:00 | 2022-06-07 09:00 | Summer | FALSE | summer
2022-06-07 09:00 | 2022-06-07 10:00 | Summer | FALSE | summer
2022-06-07 10:00 | 2022-06-07 11:00 | Summer | FALSE | summer
2022-06-07 11:00 | 2022-06-07 12:00 | Summer | FALSE | summer
2022-06-07 12:00 | 2022-06-07 13:00 | Summer | FALSE | summer
2022-06-07 13:00 | 2022-06-07 14:00 | Summer | FALSE | summer
2022-06-07 14:00 | 2022-06-07 15:00 | Summer | FALSE | summer
2022-06-07 15:00 | 2022-06-07 16:00 | Summer | FALSE | summer
2022-06-07 16:00 | 2022-06-07 17:00 | Summer | TRUE | summer
2022-06-07 17:00 | 2022-06-07 18:00 | Summer | TRUE | summer
2022-06-07 18:00 | 2022-06-07 19:00 | Summer | TRUE | summer
2022-06-07 19:00 | 2022-06-07 20:00 | Summer | TRUE | summer
2022-06-07 20:00 | 2022-06-07 21:00 | Summer | TRUE | summer
2022-06-07 21:00 | 2022-06-07 22:00 | Summer | FALSE | summer
2022-06-07 22:00 | 2022-06-07 23:00 | Summer | FALSE | summer
2022-06-07 23:00 | 2022-06-08 | Summer | FALSE | summer
2022-06-08 | 2022-06-08 01:00 | Summer | FALSE | summer
2022-06-08 01:00 | 2022-06-08 02:00 | Summer | FALSE | summer
2022-06-08 02:00 | 2022-06-08 03:00 | Summer | FALSE | summer
2022-06-08 03:00 | 2022-06-08 04:00 | Summer | FALSE | summer
2022-06-08 04:00 | 2022-06-08 05:00 | Summer | FALSE | summer
2022-06-08 05:00 | 2022-06-08 06:00 | Summer | FALSE | summer
2022-06-08 06:00 | 2022-06-08 07:00 | Summer | FALSE | summer
2022-06-08 07:00 | 2022-06-08 08:00 | Summer | FALSE | summer
2022-06-08 08:00 | 2022-06-08 09:00 | Summer | FALSE | summer
2022-06-08 09:00 | 2022-06-08 10:00 | Summer | FALSE | summer
2022-06-08 10:00 | 2022-06-08 11:00 | Summer | FALSE | summer
2022-06-08 11:00 | 2022-06-08 12:00 | Summer | FALSE | summer
2022-06-08 12:00 | 2022-06-08 13:00 | Summer | FALSE | summer
2022-06-08 13:00 | 2022-06-08 14:00 | Summer | FALSE | summer
2022-06-08 14:00 | 2022-06-08 15:00 | Summer | FALSE | summer
2022-06-08 15:00 | 2022-06-08 16:00 | Summer | FALSE | summer
2022-06-08 16:00 | 2022-06-08 17:00 | Summer | TRUE | summer
2022-06-08 17:00 | 2022-06-08 18:00 | Summer | TRUE | summer
2022-06-08 18:00 | 2022-06-08 19:00 | Summer | TRUE | summer
2022-06-08 19:00 | 2022-06-08 20:00 | Summer | TRUE | summer
2022-06-08 20:00 | 2022-06-08 21:00 | Summer | TRUE | summer
2022-06-08 21:00 | 2022-06-08 22:00 | Summer | FALSE | summer
2022-06-08 22:00 | 2022-06-08 23:00 | Summer | FALSE | summer
2022-06-08 23:00 | 2022-06-09 | Summer | FALSE | summer
2022-06-09 | 2022-06-09 01:00 | Summer | FALSE | summer
2022-06-09 01:00 | 2022-06-09 02:00 | Summer | FALSE | summer
2022-06-09 02:00 | 2022-06-09 03:00 | Summer | FALSE | summer
2022-06-09 03:00 | 2022-06-09 04:00 | Summer | FALSE | summer
2022-06-09 04:00 | 2022-06-09 05:00 | Summer | FALSE | summer
2022-06-09 05:00 | 2022-06-09 06:00 | Summer | FALSE | summer
2022-06-09 06:00 | 2022-06-09 07:00 | Summer | FALSE | summer
2022-06-09 07:00 | 2022-06-09 08:00 | Summer | FALSE | summer
2022-06-09 08:00 | 2022-06-09 09:00 | Summer | FALSE | summer
2022-06-09 09:00 | 2022-06-09 10:00 | Summer | FALSE | summer
2022-06-09 10:00 | 2022-06-09 11:00 | Summer | FALSE | summer
2022-06-09 11:00 | 2022-06-09 12:00 | Summer | FALSE | summer
2022-06-09 12:00 | 2022-06-09 13:00 | Summer | FALSE | summer
2022-06-09 13:00 | 2022-06-09 14:00 | Summer | FALSE | summer
2022-06-09 14:00 | 2022-06-09 15:00 | Summer | FALSE | summer
2022-06-09 15:00 | 2022-06-09 16:00 | Summer | FALSE | summer
2022-06-09 16:00 | 2022-06-09 17:00 | Summer | TRUE | summer
2022-06-09 17:00 | 2022-06-09 18:00 | Summer | TRUE | summer
2022-06-09 18:00 | 2022-06-09 19:00 | Summer | TRUE | summer
2022-06-09 19:00 | 2022-06-09 20:00 | Summer | TRUE | summer
2022-06-09 20:00 | 2022-06-09 21:00 | Summer | TRUE | summer
2022-06-09 21:00 | 2022-06-09 22:00 | Summer | FALSE | summer
2022-06-09 22:00 | 2022-06-09 23:00 | Summer | FALSE | summer
2022-06-09 23:00 | 2022-06-10 | Summer | FALSE | summer
2022-06-10 | 2022-06-10 01:00 | Summer | FALSE | summer
2022-06-10 01:00 | 2022-06-10 02:00 | Summer | FALSE | summer
2022-06-10 02:00 | 2022-06-10 03:00 | Summer | FALSE | summer
2022-06-10 03:00 | 2022-06-10 04:00 | Summer | FALSE | summer
2022-06-10 04:00 | 2022-06-10 05:00 | Summer | FALSE | summer
2022-06-10 05:00 | 2022-06-10 06:00 | Summer | FALSE | summer
2022-06-10 06:00 | 2022-06-10 07:00 | Summer | FALSE | summer
2022-06-10 07:00 | 2022-06-10 08:00 | Summer | FALSE | summer
2022-06-10 08:00 | 2022-06-10 09:00 | Summer | FALSE | summer
2022-06-10 09:00 | 2022-06-10 10:00 | Summer | FALSE | summer
2022-06-10 10:00 | 2022-06-10 11:00 | Summer | FALSE | summer
2022-06-10 11:00 | 2022-06-10 12:00 | Summer | FALSE | summer
2022-06-10 12:00 | 2022-06-10 13:00 | Summer | FALSE | summer
2022-06-10 13:00 | 2022-06-10 14:00 | Summer | FALSE | summer
2022-06-10 14:00 | 2022-06-10 15:00 | Summer | FALSE | summer
2022-06-10 15:00 | 2022-06-10 16:00 | Summer | FALSE | summer
2022-06-10 16:00 | 2022-06-10 17:00 | Summer | TRUE | summer
2022-06-10 17:00 | 2022-06-10 18:00 | Summer | TRUE | summer
2022-06-10 18:00 | 2022-06-10 19:00 | Summer | TRUE | summer
2022-06-10 19:00 | 2022-06-10 20:00 | Summer | TRUE | summer
2022-06-10 20:00 | 2022-06-10 21:00 | Summer | TRUE | summer
2022-06-10 21:00 | 2022-06-10 22:00 | Summer | FALSE | summer
2022-06-10 22:00 | 2022-06-10 23:00 | Summer | FALSE | summer
2022-06-10 23:00 | 2022-06-11 | Summer | FALSE | summer
2022-06-11 | 2022-06-11 01:00 | Summer | FALSE | summer
2022-06-11 01:00 | 2022-06-11 02:00 | Summer | FALSE | summer
2022-06-11 02:00 | 2022-06-11 03:00 | Summer | FALSE | summer
2022-06-11 03:00 | 2022-06-11 04:00 | Summer | FALSE | summer
2022-06-11 04:00 | 2022-06-11 05:00 | Summer | FALSE | summer
2022-06-11 05:00 | 2022-06-11 06:00 | Summer | FALSE | summer
2022-06-11 06:00 | 2022-06-11 07:00 | Summer | FALSE | summer
2022-06-11 07:00 | 2022-06-11 08:00 | Summer | FALSE | summer
2022-06-11 08:00 | 2022-06-11 09:00 | Summer | FALSE | summer
2022-06-11 09:00 | 2022-06-11 10:00 | Summer | FALSE | summer
2022-06-11 10:00 | 2022-06-11 11:00 | Summer | FALSE | summer
2022-06-11 11:00 | 2022-06-11 12:00 | Summer | FALSE | summer
2022-06-11 12:00 | 2022-06-11 13:00 | Summer | FALSE | summer
2022-06-11 13:00 | 2022-06-11 14:00 | Summer | FALSE | summer
2022-06-11 14:00 | 2022-06-11 15:00 | Summer | FALSE | summer
2022-06-11 15:00 | 2022-06-11 16:00 | Summer | FALSE | summer
2022-06-11 16:00 | 2022-06-11 17:00 | Summer | TRUE | summer
2022-06-11 17:00 | 2022-06-11 18:00 | Summer | TRUE | summer
2022-06-11 18:00 | 2022-06-11 19:00 | Summer | TRUE | summer
2022-06-11 19:00 | 2022-06-11 20:00 | Summer | TRUE | summer
2022-06-11 20:00 | 2022-06-11 21:00 | Summer | TRUE | summer
2022-06-11 21:00 | 2022-06-11 22:00 | Summer | FALSE | summer
2022-06-11 22:00 | 2022-06-11 23:00 | Summer | FALSE | summer
2022-06-11 23:00 | 2022-06-12 | Summer | FALSE | summer
2022-06-12 | 2022-06-12 01:00 | Summer | FALSE | summer
2022-06-12 01:00 | 2022-06-12 02:00 | Summer | FALSE | summer
2022-06-12 02:00 | 2022-06-12 03:00 | Summer | FALSE | summer
2022-06-12 03:00 | 2022-06-12 04:00 | Summer | FALSE | summer
2022-06-12 04:00 | 2022-06-12 05:00 | Summer | FALSE | summer
2022-06-12 05:00 | 2022-06-12 06:00 | Summer | FALSE | summer
2022-06-12 06:00 | 2022-06-12 07:00 | Summer | FALSE | summer
2022-06-12 07:00 | 2022-06-12 08:00 | Summer | FALSE | summer
2022-06-12 08:00 | 2022-06-12 09:00 | Summer | FALSE | summer
2022-06-12 09:00 | 2022-06-12 10:00 | Summer | FALSE | summer
2022-06-12 10:00 | 2022-06-12 11:00 | Summer | FALSE | summer
2022-06-12 11:00 | 2022-06-12 12:00 | Summer | FALSE | summer
2022-06-12 12:00 | 2022-06-12 13:00 | Summer | FALSE | summer
2022-06-12 13:00 | 2022-06-12 14:00 | Summer | FALSE | summer
2022-06-12 14:00 | 2022-06-12 15:00 | Summer | FALSE | summer
2022-06-12 15:00 | 2022-06-12 16:00 | Summer | FALSE | summer
2022-06-12 16:00 | 2022-06-12 17:00 | Summer | TRUE | summer
2022-06-12 17:00 | 2022-06-12 18:00 | Summer | TRUE | summer
2022-06-12 18:00 | 2022-06-12 19:00 | Summer | TRUE | summer
2022-06-12 19:00 | 2022-06-12 20:00 | Summer | TRUE | summer
2022-06-12 20:00 | 2022-06-12 21:00 | Summer | TRUE | summer
2022-06-12 21:00 | 2022-06-12 22:00 | Summer | FALSE | summer
2022-06-12 22:00 | 2022-06-12 23:00 | Summer | FALSE | summer
2022-06-12 23:00 | 2022-06-13 | Summer | FALSE | summer
2022-06-13 | 2022-06-13 01:00 | Summer | FALSE | summer
2022-06-13 01:00 | 2022-06-13 02:00 | Summer | FALSE | summer
2022-06-13 02:00 | 2022-06-13 03:00 | Summer | FALSE | summer
2022-06-13 03:00 | 2022-06-13 04:00 | Summer | FALSE | summer
2022-06-13 04:00 | 2022-06-13 05:00 | Summer | FALSE | summer
2022-06-13 05:00 | 2022-06-13 06:00 | Summer | FALSE | summer
2022-06-13 06:00 | 2022-06-13 07:00 | Summer | FALSE | summer
2022-06-13 07:00 | 2022-06-13 08:00 | Summer | FALSE | summer
2022-06-13 08:00 | 2022-06-13 09:00 | Summer | FALSE | summer
2022-06-13 09:00 | 2022-06-13 10:00 | Summer | FALSE | summer
2022-06-13 10:00 | 2022-06-13 11:00 | Summer | FALSE | summer
2022-06-13 11:00 | 2022-06-13 12:00 | Summer | FALSE | summer
2022-06-13 12:00 | 2022-06-13 13:00 | Summer | FALSE | summer
2022-06-13 13:00 | 2022-06-13 14:00 | Summer | FALSE | summer
2022-06-13 14:00 | 2022-06-13 15:00 | Summer | FALSE | summer
2022-06-13 15:00 | 2022-06-13 16:00 | Summer | FALSE | summer
2022-06-13 16:00 | 2022-06-13 17:00 | Summer | TRUE | summer
2022-06-13 17:00 | 2022-06-13 18:00 | Summer | TRUE | summer
2022-06-13 18:00 | 2022-06-13 19:00 | Summer | TRUE | summer
2022-06-13 19:00 | 2022-06-13 20:00 | Summer | TRUE | summer
2022-06-13 20:00 | 2022-06-13 21:00 | Summer | TRUE | summer
2022-06-13 21:00 | 2022-06-13 22:00 | Summer | FALSE | summer
2022-06-13 22:00 | 2022-06-13 23:00 | Summer | FALSE | summer
2022-06-13 23:00 | 2022-06-14 | Summer | FALSE | summer
2022-06-14 | 2022-06-14 01:00 | Summer | FALSE | summer
2022-06-14 01:00 | 2022-06-14 02:00 | Summer | FALSE | summer
2022-06-14 02:00 | 2022-06-14 03:00 | Summer | FALSE | summer
2022-06-14 03:00 | 2022-06-14 04:00 | Summer | FALSE | summer
2022-06-14 04:00 | 2022-06-14 05:00 | Summer | FALSE | summer
2022-06-14 05:00 | 2022-06-14 06:00 | Summer | FALSE | summer
2022-06-14 06:00 | 2022-06-14 07:00 | Summer | FALSE | summer
2022-06-14 07:00 | 2022-06-14 08:00 | Summer | FALSE | summer
2022-06-14 08:00 | 2022-06-14 09:00 | Summer | FALSE | summer
2022-06-14 09:00 | 2022-06-14 10:00 | Summer | FALSE | summer
2022-06-14 10:00 | 2022-06-14 11:00 | Summer | FALSE | summer
2022-06-14 11:00 | 2022-06-14 12:00 | Summer | FALSE | summer
2022-06-14 12:00 | 2022-06-14 13:00 | Summer | FALSE | summer
2022-06-14 13:00 | 2022-06-14 14:00 | Summer | FALSE | summer
2022-06-14 14:00 | 2022-06-14 15:00 | Summer | FALSE | summer
2022-06-14 15:00 | 2022-06-14 16:00 | Summer | FALSE | summer
2022-06-14 16:00 | 2022-06-14 17:00 | Summer | TRUE | summer
2022-06-14 17:00 | 2022-06-14 18:00 | Summer | TRUE | summer
2022-06-14 18:00 | 2022-06-14 19:00 | Summer | TRUE | summer
2022-06-14 19:00 | 2022-06-14 20:00 | Summer | TRUE | summer
2022-06-14 20:00 | 2022-06-14 21:00 | Summer | TRUE | summer
2022-06-14 21:00 | 2022-06-14 22:00 | Summer | FALSE | summer
2022-06-14 22:00 | 2022-06-14 23:00 | Summer | FALSE | summer
2022-06-14 23:00 | 2022-06-15 | Summer | FALSE | summer
2022-06-15 | 2022-06-15 01:00 | Summer | FALSE | summer
2022-06-15 01:00 | 2022-06-15 02:00 | Summer | FALSE | summer
2022-06-15 02:00 | 2022-06-15 03:00 | Summer | FALSE | summer
2022-06-15 03:00 | 2022-06-15 04:00 | Summer | FALSE | summer
2022-06-15 04:00 | 2022-06-15 05:00 | Summer | FALSE | summer
2022-06-15 05:00 | 2022-06-15 06:00 | Summer | FALSE | summer
2022-06-15 06:00 | 2022-06-15 07:00 | Summer | FALSE | summer
2022-06-15 07:00 | 2022-06-15 08:00 | Summer | FALSE | summer
2022-06-15 08:00 | 2022-06-15 09:00 | Summer | FALSE | summer
2022-06-15 09:00 | 2022-06-15 10:00 | Summer | FALSE | summer
2022-06-15 10:00 | 2022-06-15 11:00 | Summer | FALSE | summer
2022-06-15 11:00 | 2022-06-15 12:00 | Summer | FALSE | summer
2022-06-15 12:00 | 2022-06-15 13:00 | Summer | FALSE | summer
2022-06-15 13:00 | 2022-06-15 14:00 | Summer | FALSE | summer
2022-06-15 14:00 | 2022-06-15 15:00 | Summer | FALSE | summer
2022-06-15 15:00 | 2022-06-15 16:00 | Summer | FALSE | summer
2022-06-15 16:00 | 2022-06-15 17:00 | Summer | TRUE | summer
2022-06-15 17:00 | 2022-06-15 18:00 | Summer | TRUE | summer
2022-06-15 18:00 | 2022-06-15 19:00 | Summer | TRUE | summer
2022-06-15 19:00 | 2022-06-15 20:00 | Summer | TRUE | summer
2022-06-15 20:00 | 2022-06-15 21:00 | Summer | TRUE | summer
2022-06-15 21:00 | 2022-06-15 22:00 | Summer | FALSE | summer
2022-06-15 22:00 | 2022-06-15 23:00 | Summer | FALSE | summer
2022-06-15 23:00 | 2022-06-16 | Summer | FALSE | summer
2022-06-16 | 2022-06-16 01:00 | Summer | FALSE | summer
2022-06-16 01:00 | 2022-06-16 02:00 | Summer | FALSE | summer
2022-06-16 02:00 | 2022-06-16 03:00 | Summer | FALSE | summer
2022-06-16 03:00 | 2022-06-16 04:00 | Summer | FALSE | summer
2022-06-16 04:00 | 2022-06-16 05:00 | Summer | FALSE | summer
2022-06-16 05:00 | 2022-06-16 06:00 | Summer | FALSE | summer
2022-06-16 06:00 | 2022-06-16 07:00 | Summer | FALSE | summer
2022-06-16 07:00 | 2022-06-16 08:00 | Summer | FALSE | summer
2022-06-16 08:00 | 2022-06-16 09:00 | Summer | FALSE | summer
2022-06-16 09:00 | 2022-06-16 10:00 | Summer | FALSE | summer
2022-06-16 10:00 | 2022-06-16 11:00 | Summer | FALSE | summer
2022-06-16 11:00 | 2022-06-16 12:00 | Summer | FALSE | summer
2022-06-16 12:00 | 2022-06-16 13:00 | Summer | FALSE | summer
2022-06-16 13:00 | 2022-06-16 14:00 | Summer | FALSE | summer
2022-06-16 14:00 | 2022-06-16 15:00 | Summer | FALSE | summer
2022-06-16 15:00 | 2022-06-16 16:00 | Summer | FALSE | summer
2022-06-16 16:00 | 2022-06-16 17:00 | Summer | TRUE | summer
2022-06-16 17:00 | 2022-06-16 18:00 | Summer | TRUE | summer
2022-06-16 18:00 | 2022-06-16 19:00 | Summer | TRUE | summer
2022-06-16 19:00 | 2022-06-16 20:00 | Summer | TRUE | summer
2022-06-16 20:00 | 2022-06-16 21:00 | Summer | TRUE | summer
2022-06-16 21:00 | 2022-06-16 22:00 | Summer | FALSE | summer
2022-06-16 22:00 | 2022-06-16 23:00 | Summer | FALSE | summer
2022-06-16 23:00 | 2022-06-17 | Summer | FALSE | summer
2022-06-17 | 2022-06-17 01:00 | Summer | FALSE | summer
2022-06-17 01:00 | 2022-06-17 02:00 | Summer | FALSE | summer
2022-06-17 02:00 | 2022-06-17 03:00 | Summer | FALSE | summer
2022-06-17 03:00 | 2022-06-17 04:00 | Summer | FALSE | summer
2022-06-17 04:00 | 2022-06-17 05:00 | Summer | FALSE | summer
2022-06-17 05:00 | 2022-06-17 06:00 | Summer | FALSE | summer
2022-06-17 06:00 | 2022-06-17 07:00 | Summer | FALSE | summer
2022-06-17 07:00 | 2022-06-17 08:00 | Summer | FALSE | summer
2022-06-17 08:00 | 2022-06-17 09:00 | Summer | FALSE | summer
2022-06-17 09:00 | 2022-06-17 10:00 | Summer | FALSE | summer
2022-06-17 10:00 | 2022-06-17 11:00 | Summer | FALSE | summer
2022-06-17 11:00 | 2022-06-17 12:00 | Summer | FALSE | summer
2022-06-17 12:00 | 2022-06-17 13:00 | Summer | FALSE | summer
2022-06-17 13:00 | 2022-06-17 14:00 | Summer | FALSE | summer
2022-06-17 14:00 | 2022-06-17 15:00 | Summer | FALSE | summer
2022-06-17 15:00 | 2022-06-17 16:00 | Summer | FALSE | summer
2022-06-17 16:00 | 2022-06-17 17:00 | Summer | TRUE | summer
2022-06-17 17:00 | 2022-06-17 18:00 | Summer | TRUE | summer
2022-06-17 18:00 | 2022-06-17 19:00 | Summer | TRUE | summer
2022-06-17 19:00 | 2022-06-17 20:00 | Summer | TRUE | summer
2022-06-17 20:00 | 2022-06-17 21:00 | Summer | TRUE | summer
2022-06-17 21:00 | 2022-06-17 22:00 | Summer | FALSE | summer
2022-06-17 22:00 | 2022-06-17 23:00 | Summer | FALSE | summer
2022-06-17 23:00 | 2022-06-18 | Summer | FALSE | summer
2022-06-18 | 2022-06-18 01:00 | Summer | FALSE | summer
2022-06-18 01:00 | 2022-06-18 02:00 | Summer | FALSE | summer
2022-06-18 02:00 | 2022-06-18 03:00 | Summer | FALSE | summer
2022-06-18 03:00 | 2022-06-18 04:00 | Summer | FALSE | summer
2022-06-18 04:00 | 2022-06-18 05:00 | Summer | FALSE | summer
2022-06-18 05:00 | 2022-06-18 06:00 | Summer | FALSE | summer
2022-06-18 06:00 | 2022-06-18 07:00 | Summer | FALSE | summer
2022-06-18 07:00 | 2022-06-18 08:00 | Summer | FALSE | summer
2022-06-18 08:00 | 2022-06-18 09:00 | Summer | FALSE | summer
2022-06-18 09:00 | 2022-06-18 10:00 | Summer | FALSE | summer
2022-06-18 10:00 | 2022-06-18 11:00 | Summer | FALSE | summer
2022-06-18 11:00 | 2022-06-18 12:00 | Summer | FALSE | summer
2022-06-18 12:00 | 2022-06-18 13:00 | Summer | FALSE | summer
2022-06-18 13:00 | 2022-06-18 14:00 | Summer | FALSE | summer
2022-06-18 14:00 | 2022-06-18 15:00 | Summer | FALSE | summer
2022-06-18 15:00 | 2022-06-18 16:00 | Summer | FALSE | summer
2022-06-18 16:00 | 2022-06-18 17:00 | Summer | TRUE | summer
2022-06-18 17:00 | 2022-06-18 18:00 | Summer | TRUE | summer
2022-06-18 18:00 | 2022-06-18 19:00 | Summer | TRUE | summer
2022-06-18 19:00 | 2022-06-18 20:00 | Summer | TRUE | summer
2022-06-18 20:00 | 2022-06-18 21:00 | Summer | TRUE | summer
2022-06-18 21:00 | 2022-06-18 22:00 | Summer | FALSE | summer
2022-06-18 22:00 | 2022-06-18 23:00 | Summer | FALSE | summer
2022-06-18 23:00 | 2022-06-19 | Summer | FALSE | summer
2022-06-19 | 2022-06-19 01:00 | Summer | FALSE | summer
2022-06-19 01:00 | 2022-06-19 02:00 | Summer | FALSE | summer
2022-06-19 02:00 | 2022-06-19 03:00 | Summer | FALSE | summer
2022-06-19 03:00 | 2022-06-19 04:00 | Summer | FALSE | summer
2022-06-19 04:00 | 2022-06-19 05:00 | Summer | FALSE | summer
2022-06-19 05:00 | 2022-06-19 06:00 | Summer | FALSE | summer
2022-06-19 06:00 | 2022-06-19 07:00 | Summer | FALSE | summer
2022-06-19 07:00 | 2022-06-19 08:00 | Summer | FALSE | summer
2022-06-19 08:00 | 2022-06-19 09:00 | Summer | FALSE | summer
2022-06-19 09:00 | 2022-06-19 10:00 | Summer | FALSE | summer
2022-06-19 10:00 | 2022-06-19 11:00 | Summer | FALSE | summer
2022-06-19 11:00 | 2022-06-19 12:00 | Summer | FALSE | summer
2022-06-19 12:00 | 2022-06-19 13:00 | Summer | FALSE | summer
2022-06-19 13:00 | 2022-06-19 14:00 | Summer | FALSE | summer
2022-06-19 14:00 | 2022-06-19 15:00 | Summer | FALSE | summer
2022-06-19 15:00 | 2022-06-19 16:00 | Summer | FALSE | summer
2022-06-19 16:00 | 2022-06-19 17:00 | Summer | TRUE | summer
2022-06-19 17:00 | 2022-06-19 18:00 | Summer | TRUE | summer
2022-06-19 18:00 | 2022-06-19 19:00 | Summer | TRUE | summer
2022-06-19 19:00 | 2022-06-19 20:00 | Summer | TRUE | summer
2022-06-19 20:00 | 2022-06-19 21:00 | Summer | TRUE | summer
2022-06-19 21:00 | 2022-06-19 22:00 | Summer | FALSE | summer
2022-06-19 22:00 | 2022-06-19 23:00 | Summer | FALSE | summer
2022-06-19 23:00 | 2022-06-20 | Summer | FALSE | summer
2022-06-20 | 2022-06-20 01:00 | Summer | FALSE | summer
2022-06-20 01:00 | 2022-06-20 02:00 | Summer | FALSE | summer
2022-06-20 02:00 | 2022-06-20 03:00 | Summer | FALSE | summer
2022-06-20 03:00 | 2022-06-20 04:00 | Summer | FALSE | summer
2022-06-20 04:00 | 2022-06-20 05:00 | Summer | FALSE | summer
2022-06-20 05:00 | 2022-06-20 06:00 | Summer | FALSE | summer
2022-06-20 06:00 | 2022-06-20 07:00 | Summer | FALSE | summer
2022-06-20 07:00 | 2022-06-20 08:00 | Summer | FALSE | summer
2022-06-20 08:00 | 2022-06-20 09:00 | Summer | FALSE | summer
2022-06-20 09:00 | 2022-06-20 10:00 | Summer | FALSE | summer
2022-06-20 10:00 | 2022-06-20 11:00 | Summer | FALSE | summer
2022-06-20 11:00 | 2022-06-20 12:00 | Summer | FALSE | summer
2022-06-20 12:00 | 2022-06-20 13:00 | Summer | FALSE | summer
2022-06-20 13:00 | 2022-06-20 14:00 | Summer | FALSE | summer
2022-06-20 14:00 | 2022-06-20 15:00 | Summer | FALSE | summer
2022-06-20 15:00 | 2022-06-20 16:00 | Summer | FALSE | summer
2022-06-20 16:00 | 2022-06-20 17:00 | Summer | TRUE | summer
2022-06-20 17:00 | 2022-06-20 18:00 | Summer | TRUE | summer
2022-06-20 18:00 | 2022-06-20 19:00 | Summer | TRUE | summer
2022-06-20 19:00 | 2022-06-20 20:00 | Summer | TRUE | summer
2022-06-20 20:00 | 2022-06-20 21:00 | Summer | TRUE | summer
2022-06-20 21:00 | 2022-06-20 22:00 | Summer | FALSE | summer
2022-06-20 22:00 | 2022-06-20 23:00 | Summer | FALSE | summer
2022-06-20 23:00 | 2022-06-21 | Summer | FALSE | summer
2022-06-21 | 2022-06-21 01:00 | Summer | FALSE | summer
2022-06-21 01:00 | 2022-06-21 02:00 | Summer | FALSE | summer
2022-06-21 02:00 | 2022-06-21 03:00 | Summer | FALSE | summer
2022-06-21 03:00 | 2022-06-21 04:00 | Summer | FALSE | summer
2022-06-21 04:00 | 2022-06-21 05:00 | Summer | FALSE | summer
2022-06-21 05:00 | 2022-06-21 06:00 | Summer | FALSE | summer
2022-06-21 06:00 | 2022-06-21 07:00 | Summer | FALSE | summer
2022-06-21 07:00 | 2022-06-21 08:00 | Summer | FALSE | summer
2022-06-21 08:00 | 2022-06-21 09:00 | Summer | FALSE | summer
2022-06-21 09:00 | 2022-06-21 10:00 | Summer | FALSE | summer
2022-06-21 10:00 | 2022-06-21 11:00 | Summer | FALSE | summer
2022-06-21 11:00 | 2022-06-21 12:00 | Summer | FALSE | summer
2022-06-21 12:00 | 2022-06-21 13:00 | Summer | FALSE | summer
2022-06-21 13:00 | 2022-06-21 14:00 | Summer | FALSE | summer
2022-06-21 14:00 | 2022-06-21 15:00 | Summer | FALSE | summer
2022-06-21 15:00 | 2022-06-21 16:00 | Summer | FALSE | summer
2022-06-21 16:00 | 2022-06-21 17:00 | Summer | TRUE | summer
2022-06-21 17:00 | 2022-06-21 18:00 | Summer | TRUE | summer
2022-06-21 18:00 | 2022-06-21 19:00 | Summer | TRUE | summer
2022-06-21 19:00 | 2022-06-21 20:00 | Summer | TRUE | summer
2022-06-21 20:00 | 2022-06-21 21:00 | Summer | TRUE | summer
2022-06-21 21:00 | 2022-06-21 22:00 | Summer | FALSE | summer
2022-06-21 22:00 | 2022-06-21 23:00 | Summer | FALSE | summer
2022-06-21 23:00 | 2022-06-22 | Summer | FALSE | summer
2022-06-22 | 2022-06-22 01:00 | Summer | FALSE | summer
2022-06-22 01:00 | 2022-06-22 02:00 | Summer | FALSE | summer
2022-06-22 02:00 | 2022-06-22 03:00 | Summer | FALSE | summer
2022-06-22 03:00 | 2022-06-22 04:00 | Summer | FALSE | summer
2022-06-22 04:00 | 2022-06-22 05:00 | Summer | FALSE | summer
2022-06-22 05:00 | 2022-06-22 06:00 | Summer | FALSE | summer
2022-06-22 06:00 | 2022-06-22 07:00 | Summer | FALSE | summer
2022-06-22 07:00 | 2022-06-22 08:00 | Summer | FALSE | summer
2022-06-22 08:00 | 2022-06-22 09:00 | Summer | FALSE | summer
2022-06-22 09:00 | 2022-06-22 10:00 | Summer | FALSE | summer
2022-06-22 10:00 | 2022-06-22 11:00 | Summer | FALSE | summer
2022-06-22 11:00 | 2022-06-22 12:00 | Summer | FALSE | summer
2022-06-22 12:00 | 2022-06-22 13:00 | Summer | FALSE | summer
2022-06-22 13:00 | 2022-06-22 14:00 | Summer | FALSE | summer
2022-06-22 14:00 | 2022-06-22 15:00 | Summer | FALSE | summer
2022-06-22 15:00 | 2022-06-22 16:00 | Summer | FALSE | summer
2022-06-22 16:00 | 2022-06-22 17:00 | Summer | TRUE | summer
2022-06-22 17:00 | 2022-06-22 18:00 | Summer | TRUE | summer
2022-06-22 18:00 | 2022-06-22 19:00 | Summer | TRUE | summer
2022-06-22 19:00 | 2022-06-22 20:00 | Summer | TRUE | summer
2022-06-22 20:00 | 2022-06-22 21:00 | Summer | TRUE | summer
2022-06-22 21:00 | 2022-06-22 22:00 | Summer | FALSE | summer
2022-06-22 22:00 | 2022-06-22 23:00 | Summer | FALSE | summer
2022-06-22 23:00 | 2022-06-23 | Summer | FALSE | summer
2022-06-23 | 2022-06-23 01:00 | Summer | FALSE | summer
2022-06-23 01:00 | 2022-06-23 02:00 | Summer | FALSE | summer
2022-06-23 02:00 | 2022-06-23 03:00 | Summer | FALSE | summer
2022-06-23 03:00 | 2022-06-23 04:00 | Summer | FALSE | summer
2022-06-23 04:00 | 2022-06-23 05:00 | Summer | FALSE | summer
2022-06-23 05:00 | 2022-06-23 06:00 | Summer | FALSE | summer
2022-06-23 06:00 | 2022-06-23 07:00 | Summer | FALSE | summer
2022-06-23 07:00 | 2022-06-23 08:00 | Summer | FALSE | summer
2022-06-23 08:00 | 2022-06-23 09:00 | Summer | FALSE | summer
2022-06-23 09:00 | 2022-06-23 10:00 | Summer | FALSE | summer
2022-06-23 10:00 | 2022-06-23 11:00 | Summer | FALSE | summer
2022-06-23 11:00 | 2022-06-23 12:00 | Summer | FALSE | summer
2022-06-23 12:00 | 2022-06-23 13:00 | Summer | FALSE | summer
2022-06-23 13:00 | 2022-06-23 14:00 | Summer | FALSE | summer
2022-06-23 14:00 | 2022-06-23 15:00 | Summer | FALSE | summer
2022-06-23 15:00 | 2022-06-23 16:00 | Summer | FALSE | summer
2022-06-23 16:00 | 2022-06-23 17:00 | Summer | TRUE | summer
2022-06-23 17:00 | 2022-06-23 18:00 | Summer | TRUE | summer
2022-06-23 18:00 | 2022-06-23 19:00 | Summer | TRUE | summer
2022-06-23 19:00 | 2022-06-23 20:00 | Summer | TRUE | summer
2022-06-23 20:00 | 2022-06-23 21:00 | Summer | TRUE | summer
2022-06-23 21:00 | 2022-06-23 22:00 | Summer | FALSE | summer
2022-06-23 22:00 | 2022-06-23 23:00 | Summer | FALSE | summer
2022-06-23 23:00 | 2022-06-24 | Summer | FALSE | summer
2022-06-24 | 2022-06-24 01:00 | Summer | FALSE | summer
2022-06-24 01:00 | 2022-06-24 02:00 | Summer | FALSE | summer
2022-06-24 02:00 | 2022-06-24 03:00 | Summer | FALSE | summer
2022-06-24 03:00 | 2022-06-24 04:00 | Summer | FALSE | summer
2022-06-24 04:00 | 2022-06-24 05:00 | Summer | FALSE | summer
2022-06-24 05:00 | 2022-06-24 06:00 | Summer | FALSE | summer
2022-06-24 06:00 | 2022-06-24 07:00 | Summer | FALSE | summer
2022-06-24 07:00 | 2022-06-24 08:00 | Summer | FALSE | summer
2022-06-24 08:00 | 2022-06-24 09:00 | Summer | FALSE | summer
2022-06-24 09:00 | 2022-06-24 10:00 | Summer | FALSE | summer
2022-06-24 10:00 | 2022-06-24 11:00 | Summer | FALSE | summer
2022-06-24 11:00 | 2022-06-24 12:00 | Summer | FALSE | summer
2022-06-24 12:00 | 2022-06-24 13:00 | Summer | FALSE | summer
2022-06-24 13:00 | 2022-06-24 14:00 | Summer | FALSE | summer
2022-06-24 14:00 | 2022-06-24 15:00 | Summer | FALSE | summer
2022-06-24 15:00 | 2022-06-24 16:00 | Summer | FALSE | summer
2022-06-24 16:00 | 2022-06-24 17:00 | Summer | TRUE | summer
2022-06-24 17:00 | 2022-06-24 18:00 | Summer | TRUE | summer
2022-06-24 18:00 | 2022-06-24 19:00 | Summer | TRUE | summer
2022-06-24 19:00 | 2022-06-24 20:00 | Summer | TRUE | summer
2022-06-24 20:00 | 2022-06-24 21:00 | Summer | TRUE | summer
2022-06-24 21:00 | 2022-06-24 22:00 | Summer | FALSE | summer
2022-06-24 22:00 | 2022-06-24 23:00 | Summer | FALSE | summer
2022-06-24 23:00 | 2022-06-25 | Summer | FALSE | summer
2022-06-25 | 2022-06-25 01:00 | Summer | FALSE | summer
2022-06-25 01:00 | 2022-06-25 02:00 | Summer | FALSE | summer
2022-06-25 02:00 | 2022-06-25 03:00 | Summer | FALSE | summer
2022-06-25 03:00 | 2022-06-25 04:00 | Summer | FALSE | summer
2022-06-25 04:00 | 2022-06-25 05:00 | Summer | FALSE | summer
2022-06-25 05:00 | 2022-06-25 06:00 | Summer | FALSE | summer
2022-06-25 06:00 | 2022-06-25 07:00 | Summer | FALSE | summer
2022-06-25 07:00 | 2022-06-25 08:00 | Summer | FALSE | summer
2022-06-25 08:00 | 2022-06-25 09:00 | Summer | FALSE | summer
2022-06-25 09:00 | 2022-06-25 10:00 | Summer | FALSE | summer
2022-06-25 10:00 | 2022-06-25 11:00 | Summer | FALSE | summer
2022-06-25 11:00 | 2022-06-25 12:00 | Summer | FALSE | summer
2022-06-25 12:00 | 2022-06-25 13:00 | Summer | FALSE | summer
2022-06-25 13:00 | 2022-06-25 14:00 | Summer | FALSE | summer
2022-06-25 14:00 | 2022-06-25 15:00 | Summer | FALSE | summer
2022-06-25 15:00 | 2022-06-25 16:00 | Summer | FALSE | summer
2022-06-25 16:00 | 2022-06-25 17:00 | Summer | TRUE | summer
2022-06-25 17:00 | 2022-06-25 18:00 | Summer | TRUE | summer
2022-06-25 18:00 | 2022-06-25 19:00 | Summer | TRUE | summer
2022-06-25 19:00 | 2022-06-25 20:00 | Summer | TRUE | summer
2022-06-25 20:00 | 2022-06-25 21:00 | Summer | TRUE | summer
2022-06-25 21:00 | 2022-06-25 22:00 | Summer | FALSE | summer
2022-06-25 22:00 | 2022-06-25 23:00 | Summer | FALSE | summer
2022-06-25 23:00 | 2022-06-26 | Summer | FALSE | summer
2022-06-26 | 2022-06-26 01:00 | Summer | FALSE | summer
2022-06-26 01:00 | 2022-06-26 02:00 | Summer | FALSE | summer
2022-06-26 02:00 | 2022-06-26 03:00 | Summer | FALSE | summer
2022-06-26 03:00 | 2022-06-26 04:00 | Summer | FALSE | summer
2022-06-26 04:00 | 2022-06-26 05:00 | Summer | FALSE | summer
2022-06-26 05:00 | 2022-06-26 06:00 | Summer | FALSE | summer
2022-06-26 06:00 | 2022-06-26 07:00 | Summer | FALSE | summer
2022-06-26 07:00 | 2022-06-26 08:00 | Summer | FALSE | summer
2022-06-26 08:00 | 2022-06-26 09:00 | Summer | FALSE | summer
2022-06-26 09:00 | 2022-06-26 10:00 | Summer | FALSE | summer
2022-06-26 10:00 | 2022-06-26 11:00 | Summer | FALSE | summer
2022-06-26 11:00 | 2022-06-26 12:00 | Summer | FALSE | summer
2022-06-26 12:00 | 2022-06-26 13:00 | Summer | FALSE | summer
2022-06-26 13:00 | 2022-06-26 14:00 | Summer | FALSE | summer
2022-06-26 14:00 | 2022-06-26 15:00 | Summer | FALSE | summer
2022-06-26 15:00 | 2022-06-26 16:00 | Summer | FALSE | summer
2022-06-26 16:00 | 2022-06-26 17:00 | Summer | TRUE | summer
2022-06-26 17:00 | 2022-06-26 18:00 | Summer | TRUE | summer
2022-06-26 18:00 | 2022-06-26 19:00 | Summer | TRUE | summer
2022-06-26 19:00 | 2022-06-26 20:00 | Summer | TRUE | summer
2022-06-26 20:00 | 2022-06-26 21:00 | Summer | TRUE | summer
2022-06-26 21:00 | 2022-06-26 22:00 | Summer | FALSE | summer
2022-06-26 22:00 | 2022-06-26 23:00 | Summer | FALSE | summer
2022-06-26 23:00 | 2022-06-27 | Summer | FALSE | summer
2022-06-27 | 2022-06-27 01:00 | Summer | FALSE | summer
2022-06-27 01:00 | 2022-06-27 02:00 | Summer | FALSE | summer
2022-06-27 02:00 | 2022-06-27 03:00 | Summer | FALSE | summer
2022-06-27 03:00 | 2022-06-27 04:00 | Summer | FALSE | summer
2022-06-27 04:00 | 2022-06-27 05:00 | Summer | FALSE | summer
2022-06-27 05:00 | 2022-06-27 06:00 | Summer | FALSE | summer
2022-06-27 06:00 | 2022-06-27 07:00 | Summer | FALSE | summer
2022-06-27 07:00 | 2022-06-27 08:00 | Summer | FALSE | summer
2022-06-27 08:00 | 2022-06-27 09:00 | Summer | FALSE | summer
2022-06-27 09:00 | 2022-06-27 10:00 | Summer | FALSE | summer
2022-06-27 10:00 | 2022-06-27 11:00 | Summer | FALSE | summer
2022-06-27 11:00 | 2022-06-27 12:00 | Summer | FALSE | summer
2022-06-27 12:00 | 2022-06-27 13:00 | Summer | FALSE | summer
2022-06-27 13:00 | 2022-06-27 14:00 | Summer | FALSE | summer
2022-06-27 14:00 | 2022-06-27 15:00 | Summer | FALSE | summer
2022-06-27 15:00 | 2022-06-27 16:00 | Summer | FALSE | summer
2022-06-27 16:00 | 2022-06-27 17:00 | Summer | TRUE | summer
2022-06-27 17:00 | 2022-06-27 18:00 | Summer | TRUE | summer
2022-06-27 18:00 | 2022-06-27 19:00 | Summer | TRUE | summer
2022-06-27 19:00 | 2022-06-27 20:00 | Summer | TRUE | summer
2022-06-27 20:00 | 2022-06-27 21:00 | Summer | TRUE | summer
2022-06-27 21:00 | 2022-06-27 22:00 | Summer | FALSE | summer
2022-06-27 22:00 | 2022-06-27 23:00 | Summer | FALSE | summer
2022-06-27 23:00 | 2022-06-28 | Summer | FALSE | summer
2022-06-28 | 2022-06-28 01:00 | Summer | FALSE | summer
2022-06-28 01:00 | 2022-06-28 02:00 | Summer | FALSE | summer
2022-06-28 02:00 | 2022-06-28 03:00 | Summer | FALSE | summer
2022-06-28 03:00 | 2022-06-28 04:00 | Summer | FALSE | summer
2022-06-28 04:00 | 2022-06-28 05:00 | Summer | FALSE | summer
2022-06-28 05:00 | 2022-06-28 06:00 | Summer | FALSE | summer
2022-06-28 06:00 | 2022-06-28 07:00 | Summer | FALSE | summer
2022-06-28 07:00 | 2022-06-28 08:00 | Summer | FALSE | summer
2022-06-28 08:00 | 2022-06-28 09:00 | Summer | FALSE | summer
2022-06-28 09:00 | 2022-06-28 10:00 | Summer | FALSE | summer
2022-06-28 10:00 | 2022-06-28 11:00 | Summer | FALSE | summer
2022-06-28 11:00 | 2022-06-28 12:00 | Summer | FALSE | summer
2022-06-28 12:00 | 2022-06-28 13:00 | Summer | FALSE | summer
2022-06-28 13:00 | 2022-06-28 14:00 | Summer | FALSE | summer
2022-06-28 14:00 | 2022-06-28 15:00 | Summer | FALSE | summer
2022-06-28 15:00 | 2022-06-28 16:00 | Summer | FALSE | summer
2022-06-28 16:00 | 2022-06-28 17:00 | Summer | TRUE | summer
2022-06-28 17:00 | 2022-06-28 18:00 | Summer | TRUE | summer
2022-06-28 18:00 | 2022-06-28 19:00 | Summer | TRUE | summer
2022-06-28 19:00 | 2022-06-28 20:00 | Summer | TRUE | summer
2022-06-28 20:00 | 2022-06-28 21:00 | Summer | TRUE | summer
2022-06-28 21:00 | 2022-06-28 22:00 | Summer | FALSE | summer
2022-06-28 22:00 | 2022-06-28 23:00 | Summer | FALSE | summer
2022-06-28 23:00 | 2022-06-29 | Summer | FALSE | summer
2022-06-29 | 2022-06-29 01:00 | Summer | FALSE | summer
2022-06-29 01:00 | 2022-06-29 02:00 | Summer | FALSE | summer
2022-06-29 02:00 | 2022-06-29 03:00 | Summer | FALSE | summer
2022-06-29 03:00 | 2022-06-29 04:00 | Summer | FALSE | summer
2022-06-29 04:00 | 2022-06-29 05:00 | Summer | FALSE | summer
2022-06-29 05:00 | 2022-06-29 06:00 | Summer | FALSE | summer
2022-06-29 06:00 | 2022-06-29 07:00 | Summer | FALSE | summer
2022-06-29 07:00 | 2022-06-29 08:00 | Summer | FALSE | summer
2022-06-29 08:00 | 2022-06-29 09:00 | Summer | FALSE | summer
2022-06-29 09:00 | 2022-06-29 10:00 | Summer | FALSE | summer
2022-06-29 10:00 | 2022-06-29 11:00 | Summer | FALSE | summer
2022-06-29 11:00 | 2022-06-29 12:00 | Summer | FALSE | summer
2022-06-29 12:00 | 2022-06-29 13:00 | Summer | FALSE | summer
2022-06-29 13:00 | 2022-06-29 14:00 | Summer | FALSE | summer
2022-06-29 14:00 | 2022-06-29 15:00 | Summer | FALSE | summer
2022-06-29 15:00 | 2022-06-29 16:00 | Summer | FALSE | summer
2022-06-29 16:00 | 2022-06-29 17:00 | Summer | TRUE | summer
2022-06-29 17:00 | 2022-06-29 18:00 | Summer | TRUE | summer
2022-06-29 18:00 | 2022-06-29 19:00 | Summer | TRUE | summer
2022-06-29 19:00 | 2022-06-29 20:00 | Summer | TRUE | summer
2022-06-29 20:00 | 2022-06-29 21:00 | Summer | TRUE | summer
2022-06-29 21:00 | 2022-06-29 22:00 | Summer | FALSE | summer
2022-06-29 22:00 | 2022-06-29 23:00 | Summer | FALSE | summer
2022-06-29 23:00 | 2022-06-30 | Summer | FALSE | summer
2022-06-30 | 2022-06-30 01:00 | Summer | FALSE | summer
2022-06-30 01:00 | 2022-06-30 02:00 | Summer | FALSE | summer
2022-06-30 02:00 | 2022-06-30 03:00 | Summer | FALSE | summer
2022-06-30 03:00 | 2022-06-30 04:00 | Summer | FALSE | summer
2022-06-30 04:00 | 2022-06-30 05:00 | Summer | FALSE | summer
2022-06-30 05:00 | 2022-06-30 06:00 | Summer | FALSE | summer
2022-06-30 06:00 | 2022-06-30 07:00 | Summer | FALSE | summer
2022-06-30 07:00 | 2022-06-30 08:00 | Summer | FALSE | summer
2022-06-30 08:00 | 2022-06-30 09:00 | Summer | FALSE | summer
2022-06-30 09:00 | 2022-06-30 10:00 | Summer | FALSE | summer
2022-06-30 10:00 | 2022-06-30 11:00 | Summer | FALSE | summer
2022-06-30 11:00 | 2022-06-30 12:00 | Summer | FALSE | summer
2022-06-30 12:00 | 2022-06-30 13:00 | Summer | FALSE | summer
2022-06-30 13:00 | 2022-06-30 14:00 | Summer | FALSE | summer
2022-06-30 14:00 | 2022-06-30 15:00 | Summer | FALSE | summer
2022-06-30 15:00 | 2022-06-30 16:00 | Summer | FALSE | summer
2022-06-30 16:00 | 2022-06-30 17:00 | Summer | TRUE | summer
2022-06-30 17:00 | 2022-06-30 18:00 | Summer | TRUE | summer
2022-06-30 18:00 | 2022-06-30 19:00 | Summer | TRUE | summer
2022-06-30 19:00 | 2022-06-30 20:00 | Summer | TRUE | summer
2022-06-30 20:00 | 2022-06-30 21:00 | Summer | TRUE | summer
2022-06-30 21:00 | 2022-06-30 22:00 | Summer | FALSE | summer
2022-06-30 22:00 | 2022-06-30 23:00 | Summer | FALSE | summer
2022-06-30 23:00 | 2022-07-01 | Summer | FALSE | summer
2022-07-01 | 2022-07-01 01:00 | Summer | FALSE | summer
2022-07-01 01:00 | 2022-07-01 02:00 | Summer | FALSE | summer
2022-07-01 02:00 | 2022-07-01 03:00 | Summer | FALSE | summer
2022-07-01 03:00 | 2022-07-01 04:00 | Summer | FALSE | summer
2022-07-01 04:00 | 2022-07-01 05:00 | Summer | FALSE | summer
2022-07-01 05:00 | 2022-07-01 06:00 | Summer | FALSE | summer
2022-07-01 06:00 | 2022-07-01 07:00 | Summer | FALSE | summer
2022-07-01 07:00 | 2022-07-01 08:00 | Summer | FALSE | summer
2022-07-01 08:00 | 2022-07-01 09:00 | Summer | FALSE | summer
2022-07-01 09:00 | 2022-07-01 10:00 | Summer | FALSE | summer
2022-07-01 10:00 | 2022-07-01 11:00 | Summer | FALSE | summer
2022-07-01 11:00 | 2022-07-01 12:00 | Summer | FALSE | summer
2022-07-01 12:00 | 2022-07-01 13:00 | Summer | FALSE | summer
2022-07-01 13:00 | 2022-07-01 14:00 | Summer | FALSE | summer
2022-07-01 14:00 | 2022-07-01 15:00 | Summer | FALSE | summer
2022-07-01 15:00 | 2022-07-01 16:00 | Summer | FALSE | summer
2022-07-01 16:00 | 2022-07-01 17:00 | Summer | TRUE | summer
2022-07-01 17:00 | 2022-07-01 18:00 | Summer | TRUE | summer
2022-07-01 18:00 | 2022-07-01 19:00 | Summer | TRUE | summer
2022-07-01 19:00 | 2022-07-01 20:00 | Summer | TRUE | summer
2022-07-01 20:00 | 2022-07-01 21:00 | Summer | TRUE | summer
2022-07-01 21:00 | 2022-07-01 22:00 | Summer | FALSE | summer
2022-07-01 22:00 | 2022-07-01 23:00 | Summer | FALSE | summer
2022-07-01 23:00 | 2022-07-02 | Summer | FALSE | summer
2022-07-02 | 2022-07-02 01:00 | Summer | FALSE | summer
2022-07-02 01:00 | 2022-07-02 02:00 | Summer | FALSE | summer
2022-07-02 02:00 | 2022-07-02 03:00 | Summer | FALSE | summer
2022-07-02 03:00 | 2022-07-02 04:00 | Summer | FALSE | summer
2022-07-02 04:00 | 2022-07-02 05:00 | Summer | FALSE | summer
2022-07-02 05:00 | 2022-07-02 06:00 | Summer | FALSE | summer
2022-07-02 06:00 | 2022-07-02 07:00 | Summer | FALSE | summer
2022-07-02 07:00 | 2022-07-02 08:00 | Summer | FALSE | summer
2022-07-02 08:00 | 2022-07-02 09:00 | Summer | FALSE | summer
2022-07-02 09:00 | 2022-07-02 10:00 | Summer | FALSE | summer
2022-07-02 10:00 | 2022-07-02 11:00 | Summer | FALSE | summer
2022-07-02 11:00 | 2022-07-02 12:00 | Summer | FALSE | summer
2022-07-02 12:00 | 2022-07-02 13:00 | Summer | FALSE | summer
2022-07-02 13:00 | 2022-07-02 14:00 | Summer | FALSE | summer
2022-07-02 14:00 | 2022-07-02 15:00 | Summer | FALSE | summer
2022-07-02 15:00 | 2022-07-02 16:00 | Summer | FALSE | summer
2022-07-02 16:00 | 2022-07-02 17:00 | Summer | TRUE | summer
2022-07-02 17:00 | 2022-07-02 18:00 | Summer | TRUE | summer
2022-07-02 18:00 | 2022-07-02 19:00 | Summer | TRUE | summer
2022-07-02 19:00 | 2022-07-02 20:00 | Summer | TRUE | summer
2022-07-02 20:00 | 2022-07-02 21:00 | Summer | TRUE | summer
2022-07-02 21:00 | 2022-07-02 22:00 | Summer | FALSE | summer
2022-07-02 22:00 | 2022-07-02 23:00 | Summer | FALSE | summer
2022-07-02 23:00 | 2022-07-03 | Summer | FALSE | summer
2022-07-03 | 2022-07-03 01:00 | Summer | FALSE | summer
2022-07-03 01:00 | 2022-07-03 02:00 | Summer | FALSE | summer
2022-07-03 02:00 | 2022-07-03 03:00 | Summer | FALSE | summer
2022-07-03 03:00 | 2022-07-03 04:00 | Summer | FALSE | summer
2022-07-03 04:00 | 2022-07-03 05:00 | Summer | FALSE | summer
2022-07-03 05:00 | 2022-07-03 06:00 | Summer | FALSE | summer
2022-07-03 06:00 | 2022-07-03 07:00 | Summer | FALSE | summer
2022-07-03 07:00 | 2022-07-03 08:00 | Summer | FALSE | summer
2022-07-03 08:00 | 2022-07-03 09:00 | Summer | FALSE | summer
2022-07-03 09:00 | 2022-07-03 10:00 | Summer | FALSE | summer
2022-07-03 10:00 | 2022-07-03 11:00 | Summer | FALSE | summer
2022-07-03 11:00 | 2022-07-03 12:00 | Summer | FALSE | summer
2022-07-03 12:00 | 2022-07-03 13:00 | Summer | FALSE | summer
2022-07-03 13:00 | 2022-07-03 14:00 | Summer | FALSE | summer
2022-07-03 14:00 | 2022-07-03 15:00 | Summer | FALSE | summer
2022-07-03 15:00 | 2022-07-03 16:00 | Summer | FALSE | summer
2022-07-03 16:00 | 2022-07-03 17:00 | Summer | TRUE | summer
2022-07-03 17:00 | 2022-07-03 18:00 | Summer | TRUE | summer
2022-07-03 18:00 | 2022-07-03 19:00 | Summer | TRUE | summer
2022-07-03 19:00 | 2022-07-03 20:00 | Summer | TRUE | summer
2022-07-03 20:00 | 2022-07-03 21:00 | Summer | TRUE | summer
2022-07-03 21:00 | 2022-07-03 22:00 | Summer | FALSE | summer
2022-07-03 22:00 | 2022-07-03 23:00 | Summer | FALSE | summer
2022-07-03 23:00 | 2022-07-04 | Summer | FALSE | summer
2022-07-04 | 2022-07-04 01:00 | Summer | FALSE | summer
2022-07-04 01:00 | 2022-07-04 02:00 | Summer | FALSE | summer
2022-07-04 02:00 | 2022-07-04 03:00 | Summer | FALSE | summer
2022-07-04 03:00 | 2022-07-04 04:00 | Summer | FALSE | summer
2022-07-04 04:00 | 2022-07-04 05:00 | Summer | FALSE | summer
2022-07-04 05:00 | 2022-07-04 06:00 | Summer | FALSE | summer
2022-07-04 06:00 | 2022-07-04 07:00 | Summer | FALSE | summer
2022-07-04 07:00 | 2022-07-04 08:00 | Summer | FALSE | summer
2022-07-04 08:00 | 2022-07-04 09:00 | Summer | FALSE | summer
2022-07-04 09:00 | 2022-07-04 10:00 | Summer | FALSE | summer
2022-07-04 10:00 | 2022-07-04 11:00 | Summer | FALSE | summer
2022-07-04 11:00 | 2022-07-04 12:00 | Summer | FALSE | summer
2022-07-04 12:00 | 2022-07-04 13:00 | Summer | FALSE | summer
2022-07-04 13:00 | 2022-07-04 14:00 | Summer | FALSE | summer
2022-07-04 14:00 | 2022-07-04 15:00 | Summer | FALSE | summer
2022-07-04 15:00 | 2022-07-04 16:00 | Summer | FALSE | summer
2022-07-04 16:00 | 2022-07-04 17:00 | Summer | TRUE | summer
2022-07-04 17:00 | 2022-07-04 18:00 | Summer | TRUE | summer
2022-07-04 18:00 | 2022-07-04 19:00 | Summer | TRUE | summer
2022-07-04 19:00 | 2022-07-04 20:00 | Summer | TRUE | summer
2022-07-04 20:00 | 2022-07-04 21:00 | Summer | TRUE | summer
2022-07-04 21:00 | 2022-07-04 22:00 | Summer | FALSE | summer
2022-07-04 22:00 | 2022-07-04 23:00 | Summer | FALSE | summer
2022-07-04 23:00 | 2022-07-05 | Summer | FALSE | summer
2022-07-05 | 2022-07-05 01:00 | Summer | FALSE | summer
2022-07-05 01:00 | 2022-07-05 02:00 | Summer | FALSE | summer
2022-07-05 02:00 | 2022-07-05 03:00 | Summer | FALSE | summer
2022-07-05 03:00 | 2022-07-05 04:00 | Summer | FALSE | summer
2022-07-05 04:00 | 2022-07-05 05:00 | Summer | FALSE | summer
2022-07-05 05:00 | 2022-07-05 06:00 | Summer | FALSE | summer
2022-07-05 06:00 | 2022-07-05 07:00 | Summer | FALSE | summer
2022-07-05 07:00 | 2022-07-05 08:00 | Summer | FALSE | summer
2022-07-05 08:00 | 2022-07-05 09:00 | Summer | FALSE | summer
2022-07-05 09:00 | 2022-07-05 10:00 | Summer | FALSE | summer
2022-07-05 10:00 | 2022-07-05 11:00 | Summer | FALSE | summer
2022-07-05 11:00 | 2022-07-05 12:00 | Summer | FALSE | summer
2022-07-05 12:00 | 2022-07-05 13:00 | Summer | FALSE | summer
2022-07-05 13:00 | 2022-07-05 14:00 | Summer | FALSE | summer
2022-07-05 14:00 | 2022-07-05 15:00 | Summer | FALSE | summer
2022-07-05 15:00 | 2022-07-05 16:00 | Summer | FALSE | summer
2022-07-05 16:00 | 2022-07-05 17:00 | Summer | TRUE | summer
2022-07-05 17:00 | 2022-07-05 18:00 | Summer | TRUE | summer
2022-07-05 18:00 | 2022-07-05 19:00 | Summer | TRUE | summer
2022-07-05 19:00 | 2022-07-05 20:00 | Summer | TRUE | summer
2022-07-05 20:00 | 2022-07-05 21:00 | Summer | TRUE | summer
2022-07-05 21:00 | 2022-07-05 22:00 | Summer | FALSE | summer
2022-07-05 22:00 | 2022-07-05 23:00 | Summer | FALSE | summer
2022-07-05 23:00 | 2022-07-06 | Summer | FALSE | summer
2022-07-06 | 2022-07-06 01:00 | Summer | FALSE | summer
2022-07-06 01:00 | 2022-07-06 02:00 | Summer | FALSE | summer
2022-07-06 02:00 | 2022-07-06 03:00 | Summer | FALSE | summer
2022-07-06 03:00 | 2022-07-06 04:00 | Summer | FALSE | summer
2022-07-06 04:00 | 2022-07-06 05:00 | Summer | FALSE | summer
2022-07-06 05:00 | 2022-07-06 06:00 | Summer | FALSE | summer
2022-07-06 06:00 | 2022-07-06 07:00 | Summer | FALSE | summer
2022-07-06 07:00 | 2022-07-06 08:00 | Summer | FALSE | summer
2022-07-06 08:00 | 2022-07-06 09:00 | Summer | FALSE | summer
2022-07-06 09:00 | 2022-07-06 10:00 | Summer | FALSE | summer
2022-07-06 10:00 | 2022-07-06 11:00 | Summer | FALSE | summer
2022-07-06 11:00 | 2022-07-06 12:00 | Summer | FALSE | summer
2022-07-06 12:00 | 2022-07-06 13:00 | Summer | FALSE | summer
2022-07-06 13:00 | 2022-07-06 14:00 | Summer | FALSE | summer
2022-07-06 14:00 | 2022-07-06 15:00 | Summer | FALSE | summer
2022-07-06 15:00 | 2022-07-06 16:00 | Summer | FALSE | summer
2022-07-06 16:00 | 2022-07-06 17:00 | Summer | TRUE | summer
2022-07-06 17:00 | 2022-07-06 18:00 | Summer | TRUE | summer
2022-07-06 18:00 | 2022-07-06 19:00 | Summer | TRUE | summer
2022-07-06 19:00 | 2022-07-06 20:00 | Summer | TRUE | summer
2022-07-06 20:00 | 2022-07-06 21:00 | Summer | TRUE | summer
2022-07-06 21:00 | 2022-07-06 22:00 | Summer | FALSE | summer
2022-07-06 22:00 | 2022-07-06 23:00 | Summer | FALSE | summer
2022-07-06 23:00 | 2022-07-07 | Summer | FALSE | summer
2022-07-07 | 2022-07-07 01:00 | Summer | FALSE | summer
2022-07-07 01:00 | 2022-07-07 02:00 | Summer | FALSE | summer
2022-07-07 02:00 | 2022-07-07 03:00 | Summer | FALSE | summer
2022-07-07 03:00 | 2022-07-07 04:00 | Summer | FALSE | summer
2022-07-07 04:00 | 2022-07-07 05:00 | Summer | FALSE | summer
2022-07-07 05:00 | 2022-07-07 06:00 | Summer | FALSE | summer
2022-07-07 06:00 | 2022-07-07 07:00 | Summer | FALSE | summer
2022-07-07 07:00 | 2022-07-07 08:00 | Summer | FALSE | summer
2022-07-07 08:00 | 2022-07-07 09:00 | Summer | FALSE | summer
2022-07-07 09:00 | 2022-07-07 10:00 | Summer | FALSE | summer
2022-07-07 10:00 | 2022-07-07 11:00 | Summer | FALSE | summer
2022-07-07 11:00 | 2022-07-07 12:00 | Summer | FALSE | summer
2022-07-07 12:00 | 2022-07-07 13:00 | Summer | FALSE | summer
2022-07-07 13:00 | 2022-07-07 14:00 | Summer | FALSE | summer
2022-07-07 14:00 | 2022-07-07 15:00 | Summer | FALSE | summer
2022-07-07 15:00 | 2022-07-07 16:00 | Summer | FALSE | summer
2022-07-07 16:00 | 2022-07-07 17:00 | Summer | TRUE | summer
2022-07-07 17:00 | 2022-07-07 18:00 | Summer | TRUE | summer
2022-07-07 18:00 | 2022-07-07 19:00 | Summer | TRUE | summer
2022-07-07 19:00 | 2022-07-07 20:00 | Summer | TRUE | summer
2022-07-07 20:00 | 2022-07-07 21:00 | Summer | TRUE | summer
2022-07-07 21:00 | 2022-07-07 22:00 | Summer | FALSE | summer
2022-07-07 22:00 | 2022-07-07 23:00 | Summer | FALSE | summer
2022-07-07 23:00 | 2022-07-08 | Summer | FALSE | summer
2022-07-08 | 2022-07-08 01:00 | Summer | FALSE | summer
2022-07-08 01:00 | 2022-07-08 02:00 | Summer | FALSE | summer
2022-07-08 02:00 | 2022-07-08 03:00 | Summer | FALSE | summer
2022-07-08 03:00 | 2022-07-08 04:00 | Summer | FALSE | summer
2022-07-08 04:00 | 2022-07-08 05:00 | Summer | FALSE | summer
2022-07-08 05:00 | 2022-07-08 06:00 | Summer | FALSE | summer
2022-07-08 06:00 | 2022-07-08 07:00 | Summer | FALSE | summer
2022-07-08 07:00 | 2022-07-08 08:00 | Summer | FALSE | summer
2022-07-08 08:00 | 2022-07-08 09:00 | Summer | FALSE | summer
2022-07-08 09:00 | 2022-07-08 10:00 | Summer | FALSE | summer
2022-07-08 10:00 | 2022-07-08 11:00 | Summer | FALSE | summer
2022-07-08 11:00 | 2022-07-08 12:00 | Summer | FALSE | summer
2022-07-08 12:00 | 2022-07-08 13:00 | Summer | FALSE | summer
2022-07-08 13:00 | 2022-07-08 14:00 | Summer | FALSE | summer
2022-07-08 14:00 | 2022-07-08 15:00 | Summer | FALSE | summer
2022-07-08 15:00 | 2022-07-08 16:00 | Summer | FALSE | summer
2022-07-08 16:00 | 2022-07-08 17:00 | Summer | TRUE | summer
2022-07-08 17:00 | 2022-07-08 18:00 | Summer | TRUE | summer
2022-07-08 18:00 | 2022-07-08 19:00 | Summer | TRUE | summer
2022-07-08 19:00 | 2022-07-08 20:00 | Summer | TRUE | summer
2022-07-08 20:00 | 2022-07-08 21:00 | Summer | TRUE | summer
2022-07-08 21:00 | 2022-07-08 22:00 | Summer | FALSE | summer
2022-07-08 22:00 | 2022-07-08 23:00 | Summer | FALSE | summer
2022-07-08 23:00 | 2022-07-09 | Summer | FALSE | summer
2022-07-09 | 2022-07-09 01:00 | Summer | FALSE | summer
2022-07-09 01:00 | 2022-07-09 02:00 | Summer | FALSE | summer
2022-07-09 02:00 | 2022-07-09 03:00 | Summer | FALSE | summer
2022-07-09 03:00 | 2022-07-09 04:00 | Summer | FALSE | summer
2022-07-09 04:00 | 2022-07-09 05:00 | Summer | FALSE | summer
2022-07-09 05:00 | 2022-07-09 06:00 | Summer | FALSE | summer
2022-07-09 06:00 | 2022-07-09 07:00 | Summer | FALSE | summer
2022-07-09 07:00 | 2022-07-09 08:00 | Summer | FALSE | summer
2022-07-09 08:00 | 2022-07-09 09:00 | Summer | FALSE | summer
2022-07-09 09:00 | 2022-07-09 10:00 | Summer | FALSE | summer
2022-07-09 10:00 | 2022-07-09 11:00 | Summer | FALSE | summer
2022-07-09 11:00 | 2022-07-09 12:00 | Summer | FALSE | summer
2022-07-09 12:00 | 2022-07-09 13:00 | Summer | FALSE | summer
2022-07-09 13:00 | 2022-07-09 14:00 | Summer | FALSE | summer
2022-07-09 14:00 | 2022-07-09 15:00 | Summer | FALSE | summer
2022-07-09 15:00 | 2022-07-09 16:00 | Summer | FALSE | summer
2022-07-09 16:00 | 2022-07-09 17:00 | Summer | TRUE | summer
2022-07-09 17:00 | 2022-07-09 18:00 | Summer | TRUE | summer
2022-07-09 18:00 | 2022-07-09 19:00 | Summer | TRUE | summer
2022-07-09 19:00 | 2022-07-09 20:00 | Summer | TRUE | summer
2022-07-09 20:00 | 2022-07-09 21:00 | Summer | TRUE | summer
2022-07-09 21:00 | 2022-07-09 22:00 | Summer | FALSE | summer
2022-07-09 22:00 | 2022-07-09 23:00 | Summer | FALSE | summer
2022-07-09 23:00 | 2022-07-10 | Summer | FALSE | summer
2022-07-10 | 2022-07-10 01:00 | Summer | FALSE | summer
2022-07-10 01:00 | 2022-07-10 02:00 | Summer | FALSE | summer
2022-07-10 02:00 | 2022-07-10 03:00 | Summer | FALSE | summer
2022-07-10 03:00 | 2022-07-10 04:00 | Summer | FALSE | summer
2022-07-10 04:00 | 2022-07-10 05:00 | Summer | FALSE | summer
2022-07-10 05:00 | 2022-07-10 06:00 | Summer | FALSE | summer
2022-07-10 06:00 | 2022-07-10 07:00 | Summer | FALSE | summer
2022-07-10 07:00 | 2022-07-10 08:00 | Summer | FALSE | summer
2022-07-10 08:00 | 2022-07-10 09:00 | Summer | FALSE | summer
2022-07-10 09:00 | 2022-07-10 10:00 | Summer | FALSE | summer
2022-07-10 10:00 | 2022-07-10 11:00 | Summer | FALSE | summer
2022-07-10 11:00 | 2022-07-10 12:00 | Summer | FALSE | summer
2022-07-10 12:00 | 2022-07-10 13:00 | Summer | FALSE | summer
2022-07-10 13:00 | 2022-07-10 14:00 | Summer | FALSE | summer
2022-07-10 14:00 | 2022-07-10 15:00 | Summer | FALSE | summer
2022-07-10 15:00 | 2022-07-10 16:00 | Summer | FALSE | summer
2022-07-10 16:00 | 2022-07-10 17:00 | Summer | TRUE | summer
2022-07-10 17:00 | 2022-07-10 18:00 | Summer | TRUE | summer
2022-07-10 18:00 | 2022-07-10 19:00 | Summer | TRUE | summer
2022-07-10 19:00 | 2022-07-10 20:00 | Summer | TRUE | summer
2022-07-10 20:00 | 2022-07-10 21:00 | Summer | TRUE | summer
2022-07-10 21:00 | 2022-07-10 22:00 | Summer | FALSE | summer
2022-07-10 22:00 | 2022-07-10 23:00 | Summer | FALSE | summer
2022-07-10 23:00 | 2022-07-11 | Summer | FALSE | summer
2022-07-11 | 2022-07-11 01:00 | Summer | FALSE | summer
2022-07-11 01:00 | 2022-07-11 02:00 | Summer | FALSE | summer
2022-07-11 02:00 | 2022-07-11 03:00 | Summer | FALSE | summer
2022-07-11 03:00 | 2022-07-11 04:00 | Summer | FALSE | summer
2022-07-11 04:00 | 2022-07-11 05:00 | Summer | FALSE | summer
2022-07-11 05:00 | 2022-07-11 06:00 | Summer | FALSE | summer
2022-07-11 06:00 | 2022-07-11 07:00 | Summer | FALSE | summer
2022-07-11 07:00 | 2022-07-11 08:00 | Summer | FALSE | summer
2022-07-11 08:00 | 2022-07-11 09:00 | Summer | FALSE | summer
2022-07-11 09:00 | 2022-07-11 10:00 | Summer | FALSE | summer
2022-07-11 10:00 | 2022-07-11 11:00 | Summer | FALSE | summer
2022-07-11 11:00 | 2022-07-11 12:00 | Summer | FALSE | summer
2022-07-11 12:00 | 2022-07-11 13:00 | Summer | FALSE | summer
2022-07-11 13:00 | 2022-07-11 14:00 | Summer | FALSE | summer
2022-07-11 14:00 | 2022-07-11 15:00 | Summer | FALSE | summer
2022-07-11 15:00 | 2022-07-11 16:00 | Summer | FALSE | summer
2022-07-11 16:00 | 2022-07-11 17:00 | Summer | TRUE | summer
2022-07-11 17:00 | 2022-07-11 18:00 | Summer | TRUE | summer
2022-07-11 18:00 | 2022-07-11 19:00 | Summer | TRUE | summer
2022-07-11 19:00 | 2022-07-11 20:00 | Summer | TRUE | summer
2022-07-11 20:00 | 2022-07-11 21:00 | Summer | TRUE | summer
2022-07-11 21:00 | 2022-07-11 22:00 | Summer | FALSE | summer
2022-07-11 22:00 | 2022-07-11 23:00 | Summer | FALSE | summer
2022-07-11 23:00 | 2022-07-12 | Summer | FALSE | summer
2022-07-12 | 2022-07-12 01:00 | Summer | FALSE | summer
2022-07-12 01:00 | 2022-07-12 02:00 | Summer | FALSE | summer
2022-07-12 02:00 | 2022-07-12 03:00 | Summer | FALSE | summer
2022-07-12 03:00 | 2022-07-12 04:00 | Summer | FALSE | summer
2022-07-12 04:00 | 2022-07-12 05:00 | Summer | FALSE | summer
2022-07-12 05:00 | 2022-07-12 06:00 | Summer | FALSE | summer
2022-07-12 06:00 | 2022-07-12 07:00 | Summer | FALSE | summer
2022-07-12 07:00 | 2022-07-12 08:00 | Summer | FALSE | summer
2022-07-12 08:00 | 2022-07-12 09:00 | Summer | FALSE | summer
2022-07-12 09:00 | 2022-07-12 10:00 | Summer | FALSE | summer
2022-07-12 10:00 | 2022-07-12 11:00 | Summer | FALSE | summer
2022-07-12 11:00 | 2022-07-12 12:00 | Summer | FALSE | summer
2022-07-12 12:00 | 2022-07-12 13:00 | Summer | FALSE | summer
2022-07-12 13:00 | 2022-07-12 14:00 | Summer | FALSE | summer
2022-07-12 14:00 | 2022-07-12 15:00 | Summer | FALSE | summer
2022-07-12 15:00 | 2022-07-12 16:00 | Summer | FALSE | summer
2022-07-12 16:00 | 2022-07-12 17:00 | Summer | TRUE | summer
2022-07-12 17:00 | 2022-07-12 18:00 | Summer | TRUE | summer
2022-07-12 18:00 | 2022-07-12 19:00 | Summer | TRUE | summer
2022-07-12 19:00 | 2022-07-12 20:00 | Summer | TRUE | summer
2022-07-12 20:00 | 2022-07-12 21:00 | Summer | TRUE | summer
2022-07-12 21:00 | 2022-07-12 22:00 | Summer | FALSE | summer
2022-07-12 22:00 | 2022-07-12 23:00 | Summer | FALSE | summer
2022-07-12 23:00 | 2022-07-13 | Summer | FALSE | summer
2022-07-13 | 2022-07-13 01:00 | Summer | FALSE | summer
2022-07-13 01:00 | 2022-07-13 02:00 | Summer | FALSE | summer
2022-07-13 02:00 | 2022-07-13 03:00 | Summer | FALSE | summer
2022-07-13 03:00 | 2022-07-13 04:00 | Summer | FALSE | summer
2022-07-13 04:00 | 2022-07-13 05:00 | Summer | FALSE | summer
2022-07-13 05:00 | 2022-07-13 06:00 | Summer | FALSE | summer
2022-07-13 06:00 | 2022-07-13 07:00 | Summer | FALSE | summer
2022-07-13 07:00 | 2022-07-13 08:00 | Summer | FALSE | summer
2022-07-13 08:00 | 2022-07-13 09:00 | Summer | FALSE | summer
2022-07-13 09:00 | 2022-07-13 10:00 | Summer | FALSE | summer
2022-07-13 10:00 | 2022-07-13 11:00 | Summer | FALSE | summer
2022-07-13 11:00 | 2022-07-13 12:00 | Summer | FALSE | summer
2022-07-13 12:00 | 2022-07-13 13:00 | Summer | FALSE | summer
2022-07-13 13:00 | 2022-07-13 14:00 | Summer | FALSE | summer
2022-07-13 14:00 | 2022-07-13 15:00 | Summer | FALSE | summer
2022-07-13 15:00 | 2022-07-13 16:00 | Summer | FALSE | summer
2022-07-13 16:00 | 2022-07-13 17:00 | Summer | TRUE | summer
2022-07-13 17:00 | 2022-07-13 18:00 | Summer | TRUE | summer
2022-07-13 18:00 | 2022-07-13 19:00 | Summer | TRUE | summer
2022-07-13 19:00 | 2022-07-13 20:00 | Summer | TRUE | summer
2022-07-13 20:00 | 2022-07-13 21:00 | Summer | TRUE | summer
2022-07-13 21:00 | 2022-07-13 22:00 | Summer | FALSE | summer
2022-07-13 22:00 | 2022-07-13 23:00 | Summer | FALSE | summer
2022-07-13 23:00 | 2022-07-14 | Summer | FALSE | summer
2022-07-14 | 2022-07-14 01:00 | Summer | FALSE | summer
2022-07-14 01:00 | 2022-07-14 02:00 | Summer | FALSE | summer
2022-07-14 02:00 | 2022-07-14 03:00 | Summer | FALSE | summer
2022-07-14 03:00 | 2022-07-14 04:00 | Summer | FALSE | summer
2022-07-14 04:00 | 2022-07-14 05:00 | Summer | FALSE | summer
2022-07-14 05:00 | 2022-07-14 06:00 | Summer | FALSE | summer
2022-07-14 06:00 | 2022-07-14 07:00 | Summer | FALSE | summer
2022-07-14 07:00 | 2022-07-14 08:00 | Summer | FALSE | summer
2022-07-14 08:00 | 2022-07-14 09:00 | Summer | FALSE | summer
2022-07-14 09:00 | 2022-07-14 10:00 | Summer | FALSE | summer
2022-07-14 10:00 | 2022-07-14 11:00 | Summer | FALSE | summer
2022-07-14 11:00 | 2022-07-14 12:00 | Summer | FALSE | summer
2022-07-14 12:00 | 2022-07-14 13:00 | Summer | FALSE | summer
2022-07-14 13:00 | 2022-07-14 14:00 | Summer | FALSE | summer
2022-07-14 14:00 | 2022-07-14 15:00 | Summer | FALSE | summer
2022-07-14 15:00 | 2022-07-14 16:00 | Summer | FALSE | summer
2022-07-14 16:00 | 2022-07-14 17:00 | Summer | TRUE | summer
2022-07-14 17:00 | 2022-07-14 18:00 | Summer | TRUE | summer
2022-07-14 18:00 | 2022-07-14 19:00 | Summer | TRUE | summer
2022-07-14 19:00 | 2022-07-14 20:00 | Summer | TRUE | summer
2022-07-14 20:00 | 2022-07-14 21:00 | Summer | TRUE | summer
2022-07-14 21:00 | 2022-07-14 22:00 | Summer | FALSE | summer
2022-07-14 22:00 | 2022-07-14 23:00 | Summer | FALSE | summer
2022-07-14 23:00 | 2022-07-15 | Summer | FALSE | summer
2022-07-15 | 2022-07-15 01:00 | Summer | FALSE | summer
2022-07-15 01:00 | 2022-07-15 02:00 | Summer | FALSE | summer
2022-07-15 02:00 | 2022-07-15 03:00 | Summer | FALSE | summer
2022-07-15 03:00 | 2022-07-15 04:00 | Summer | FALSE | summer
2022-07-15 04:00 | 2022-07-15 05:00 | Summer | FALSE | summer
2022-07-15 05:00 | 2022-07-15 06:00 | Summer | FALSE | summer
2022-07-15 06:00 | 2022-07-15 07:00 | Summer | FALSE | summer
2022-07-15 07:00 | 2022-07-15 08:00 | Summer | FALSE | summer
2022-07-15 08:00 | 2022-07-15 09:00 | Summer | FALSE | summer
2022-07-15 09:00 | 2022-07-15 10:00 | Summer | FALSE | summer
2022-07-15 10:00 | 2022-07-15 11:00 | Summer | FALSE | summer
2022-07-15 11:00 | 2022-07-15 12:00 | Summer | FALSE | summer
2022-07-15 12:00 | 2022-07-15 13:00 | Summer | FALSE | summer
2022-07-15 13:00 | 2022-07-15 14:00 | Summer | FALSE | summer
2022-07-15 14:00 | 2022-07-15 15:00 | Summer | FALSE | summer
2022-07-15 15:00 | 2022-07-15 16:00 | Summer | FALSE | summer
2022-07-15 16:00 | 2022-07-15 17:00 | Summer | TRUE | summer
2022-07-15 17:00 | 2022-07-15 18:00 | Summer | TRUE | summer
2022-07-15 18:00 | 2022-07-15 19:00 | Summer | TRUE | summer
2022-07-15 19:00 | 2022-07-15 20:00 | Summer | TRUE | summer
2022-07-15 20:00 | 2022-07-15 21:00 | Summer | TRUE | summer
2022-07-15 21:00 | 2022-07-15 22:00 | Summer | FALSE | summer
2022-07-15 22:00 | 2022-07-15 23:00 | Summer | FALSE | summer
2022-07-15 23:00 | 2022-07-16 | Summer | FALSE | summer
2022-07-16 | 2022-07-16 01:00 | Summer | FALSE | summer
2022-07-16 01:00 | 2022-07-16 02:00 | Summer | FALSE | summer
2022-07-16 02:00 | 2022-07-16 03:00 | Summer | FALSE | summer
2022-07-16 03:00 | 2022-07-16 04:00 | Summer | FALSE | summer
2022-07-16 04:00 | 2022-07-16 05:00 | Summer | FALSE | summer
2022-07-16 05:00 | 2022-07-16 06:00 | Summer | FALSE | summer
2022-07-16 06:00 | 2022-07-16 07:00 | Summer | FALSE | summer
2022-07-16 07:00 | 2022-07-16 08:00 | Summer | FALSE | summer
2022-07-16 08:00 | 2022-07-16 09:00 | Summer | FALSE | summer
2022-07-16 09:00 | 2022-07-16 10:00 | Summer | FALSE | summer
2022-07-16 10:00 | 2022-07-16 11:00 | Summer | FALSE | summer
2022-07-16 11:00 | 2022-07-16 12:00 | Summer | FALSE | summer
2022-07-16 12:00 | 2022-07-16 13:00 | Summer | FALSE | summer
2022-07-16 13:00 | 2022-07-16 14:00 | Summer | FALSE | summer
2022-07-16 14:00 | 2022-07-16 15:00 | Summer | FALSE | summer
2022-07-16 15:00 | 2022-07-16 16:00 | Summer | FALSE | summer
2022-07-16 16:00 | 2022-07-16 17:00 | Summer | TRUE | summer
2022-07-16 17:00 | 2022-07-16 18:00 | Summer | TRUE | summer
2022-07-16 18:00 | 2022-07-16 19:00 | Summer | TRUE | summer
2022-07-16 19:00 | 2022-07-16 20:00 | Summer | TRUE | summer
2022-07-16 20:00 | 2022-07-16 21:00 | Summer | TRUE | summer
2022-07-16 21:00 | 2022-07-16 22:00 | Summer | FALSE | summer
2022-07-16 22:00 | 2022-07-16 23:00 | Summer | FALSE | summer
2022-07-16 23:00 | 2022-07-17 | Summer | FALSE | summer
2022-07-17 | 2022-07-17 01:00 | Summer | FALSE | summer
2022-07-17 01:00 | 2022-07-17 02:00 | Summer | FALSE | summer
2022-07-17 02:00 | 2022-07-17 03:00 | Summer | FALSE | summer
2022-07-17 03:00 | 2022-07-17 04:00 | Summer | FALSE | summer
2022-07-17 04:00 | 2022-07-17 05:00 | Summer | FALSE | summer
2022-07-17 05:00 | 2022-07-17 06:00 | Summer | FALSE | summer
2022-07-17 06:00 | 2022-07-17 07:00 | Summer | FALSE | summer
2022-07-17 07:00 | 2022-07-17 08:00 | Summer | FALSE | summer
2022-07-17 08:00 | 2022-07-17 09:00 | Summer | FALSE | summer
2022-07-17 09:00 | 2022-07-17 10:00 | Summer | FALSE | summer
2022-07-17 10:00 | 2022-07-17 11:00 | Summer | FALSE | summer
2022-07-17 11:00 | 2022-07-17 12:00 | Summer | FALSE | summer
2022-07-17 12:00 | 2022-07-17 13:00 | Summer | FALSE | summer
2022-07-17 13:00 | 2022-07-17 14:00 | Summer | FALSE | summer
2022-07-17 14:00 | 2022-07-17 15:00 | Summer | FALSE | summer
2022-07-17 15:00 | 2022-07-17 16:00 | Summer | FALSE | summer
2022-07-17 16:00 | 2022-07-17 17:00 | Summer | TRUE | summer
2022-07-17 17:00 | 2022-07-17 18:00 | Summer | TRUE | summer
2022-07-17 18:00 | 2022-07-17 19:00 | Summer | TRUE | summer
2022-07-17 19:00 | 2022-07-17 20:00 | Summer | TRUE | summer
2022-07-17 20:00 | 2022-07-17 21:00 | Summer | TRUE | summer
2022-07-17 21:00 | 2022-07-17 22:00 | Summer | FALSE | summer
2022-07-17 22:00 | 2022-07-17 23:00 | Summer | FALSE | summer
2022-07-17 23:00 | 2022-07-18 | Summer | FALSE | summer
2022-07-18 | 2022-07-18 01:00 | Summer | FALSE | summer
2022-07-18 01:00 | 2022-07-18 02:00 | Summer | FALSE | summer
2022-07-18 02:00 | 2022-07-18 03:00 | Summer | FALSE | summer
2022-07-18 03:00 | 2022-07-18 04:00 | Summer | FALSE | summer
2022-07-18 04:00 | 2022-07-18 05:00 | Summer | FALSE | summer
2022-07-18 05:00 | 2022-07-18 06:00 | Summer | FALSE | summer
2022-07-18 06:00 | 2022-07-18 07:00 | Summer | FALSE | summer
2022-07-18 07:00 | 2022-07-18 08:00 | Summer | FALSE | summer
2022-07-18 08:00 | 2022-07-18 09:00 | Summer | FALSE | summer
2022-07-18 09:00 | 2022-07-18 10:00 | Summer | FALSE | summer
2022-07-18 10:00 | 2022-07-18 11:00 | Summer | FALSE | summer
2022-07-18 11:00 | 2022-07-18 12:00 | Summer | FALSE | summer
2022-07-18 12:00 | 2022-07-18 13:00 | Summer | FALSE | summer
2022-07-18 13:00 | 2022-07-18 14:00 | Summer | FALSE | summer
2022-07-18 14:00 | 2022-07-18 15:00 | Summer | FALSE | summer
2022-07-18 15:00 | 2022-07-18 16:00 | Summer | FALSE | summer
2022-07-18 16:00 | 2022-07-18 17:00 | Summer | TRUE | summer
2022-07-18 17:00 | 2022-07-18 18:00 | Summer | TRUE | summer
2022-07-18 18:00 | 2022-07-18 19:00 | Summer | TRUE | summer
2022-07-18 19:00 | 2022-07-18 20:00 | Summer | TRUE | summer
2022-07-18 20:00 | 2022-07-18 21:00 | Summer | TRUE | summer
2022-07-18 21:00 | 2022-07-18 22:00 | Summer | FALSE | summer
2022-07-18 22:00 | 2022-07-18 23:00 | Summer | FALSE | summer
2022-07-18 23:00 | 2022-07-19 | Summer | FALSE | summer
2022-07-19 | 2022-07-19 01:00 | Summer | FALSE | summer
2022-07-19 01:00 | 2022-07-19 02:00 | Summer | FALSE | summer
2022-07-19 02:00 | 2022-07-19 03:00 | Summer | FALSE | summer
2022-07-19 03:00 | 2022-07-19 04:00 | Summer | FALSE | summer
2022-07-19 04:00 | 2022-07-19 05:00 | Summer | FALSE | summer
2022-07-19 05:00 | 2022-07-19 06:00 | Summer | FALSE | summer
2022-07-19 06:00 | 2022-07-19 07:00 | Summer | FALSE | summer
2022-07-19 07:00 | 2022-07-19 08:00 | Summer | FALSE | summer
2022-07-19 08:00 | 2022-07-19 09:00 | Summer | FALSE | summer
2022-07-19 09:00 | 2022-07-19 10:00 | Summer | FALSE | summer
2022-07-19 10:00 | 2022-07-19 11:00 | Summer | FALSE | summer
2022-07-19 11:00 | 2022-07-19 12:00 | Summer | FALSE | summer
2022-07-19 12:00 | 2022-07-19 13:00 | Summer | FALSE | summer
2022-07-19 13:00 | 2022-07-19 14:00 | Summer | FALSE | summer
2022-07-19 14:00 | 2022-07-19 15:00 | Summer | FALSE | summer
2022-07-19 15:00 | 2022-07-19 16:00 | Summer | FALSE | summer
2022-07-19 16:00 | 2022-07-19 17:00 | Summer | TRUE | summer
2022-07-19 17:00 | 2022-07-19 18:00 | Summer | TRUE | summer
2022-07-19 18:00 | 2022-07-19 19:00 | Summer | TRUE | summer
2022-07-19 19:00 | 2022-07-19 20:00 | Summer | TRUE | summer
2022-07-19 20:00 | 2022-07-19 21:00 | Summer | TRUE | summer
2022-07-19 21:00 | 2022-07-19 22:00 | Summer | FALSE | summer
2022-07-19 22:00 | 2022-07-19 23:00 | Summer | FALSE | summer
2022-07-19 23:00 | 2022-07-20 | Summer | FALSE | summer
2022-07-20 | 2022-07-20 01:00 | Summer | FALSE | summer
2022-07-20 01:00 | 2022-07-20 02:00 | Summer | FALSE | summer
2022-07-20 02:00 | 2022-07-20 03:00 | Summer | FALSE | summer
2022-07-20 03:00 | 2022-07-20 04:00 | Summer | FALSE | summer
2022-07-20 04:00 | 2022-07-20 05:00 | Summer | FALSE | summer
2022-07-20 05:00 | 2022-07-20 06:00 | Summer | FALSE | summer
2022-07-20 06:00 | 2022-07-20 07:00 | Summer | FALSE | summer
2022-07-20 07:00 | 2022-07-20 08:00 | Summer | FALSE | summer
2022-07-20 08:00 | 2022-07-20 09:00 | Summer | FALSE | summer
2022-07-20 09:00 | 2022-07-20 10:00 | Summer | FALSE | summer
2022-07-20 10:00 | 2022-07-20 11:00 | Summer | FALSE | summer
2022-07-20 11:00 | 2022-07-20 12:00 | Summer | FALSE | summer
2022-07-20 12:00 | 2022-07-20 13:00 | Summer | FALSE | summer
2022-07-20 13:00 | 2022-07-20 14:00 | Summer | FALSE | summer
2022-07-20 14:00 | 2022-07-20 15:00 | Summer | FALSE | summer
2022-07-20 15:00 | 2022-07-20 16:00 | Summer | FALSE | summer
2022-07-20 16:00 | 2022-07-20 17:00 | Summer | TRUE | summer
2022-07-20 17:00 | 2022-07-20 18:00 | Summer | TRUE | summer
2022-07-20 18:00 | 2022-07-20 19:00 | Summer | TRUE | summer
2022-07-20 19:00 | 2022-07-20 20:00 | Summer | TRUE | summer
2022-07-20 20:00 | 2022-07-20 21:00 | Summer | TRUE | summer
2022-07-20 21:00 | 2022-07-20 22:00 | Summer | FALSE | summer
2022-07-20 22:00 | 2022-07-20 23:00 | Summer | FALSE | summer
2022-07-20 23:00 | 2022-07-21 | Summer | FALSE | summer
2022-07-21 | 2022-07-21 01:00 | Summer | FALSE | summer
2022-07-21 01:00 | 2022-07-21 02:00 | Summer | FALSE | summer
2022-07-21 02:00 | 2022-07-21 03:00 | Summer | FALSE | summer
2022-07-21 03:00 | 2022-07-21 04:00 | Summer | FALSE | summer
2022-07-21 04:00 | 2022-07-21 05:00 | Summer | FALSE | summer
2022-07-21 05:00 | 2022-07-21 06:00 | Summer | FALSE | summer
2022-07-21 06:00 | 2022-07-21 07:00 | Summer | FALSE | summer
2022-07-21 07:00 | 2022-07-21 08:00 | Summer | FALSE | summer
2022-07-21 08:00 | 2022-07-21 09:00 | Summer | FALSE | summer
2022-07-21 09:00 | 2022-07-21 10:00 | Summer | FALSE | summer
2022-07-21 10:00 | 2022-07-21 11:00 | Summer | FALSE | summer
2022-07-21 11:00 | 2022-07-21 12:00 | Summer | FALSE | summer
2022-07-21 12:00 | 2022-07-21 13:00 | Summer | FALSE | summer
2022-07-21 13:00 | 2022-07-21 14:00 | Summer | FALSE | summer
2022-07-21 14:00 | 2022-07-21 15:00 | Summer | FALSE | summer
2022-07-21 15:00 | 2022-07-21 16:00 | Summer | FALSE | summer
2022-07-21 16:00 | 2022-07-21 17:00 | Summer | TRUE | summer
2022-07-21 17:00 | 2022-07-21 18:00 | Summer | TRUE | summer
2022-07-21 18:00 | 2022-07-21 19:00 | Summer | TRUE | summer
2022-07-21 19:00 | 2022-07-21 20:00 | Summer | TRUE | summer
2022-07-21 20:00 | 2022-07-21 21:00 | Summer | TRUE | summer
2022-07-21 21:00 | 2022-07-21 22:00 | Summer | FALSE | summer
2022-07-21 22:00 | 2022-07-21 23:00 | Summer | FALSE | summer
2022-07-21 23:00 | 2022-07-22 | Summer | FALSE | summer
2022-07-22 | 2022-07-22 01:00 | Summer | FALSE | summer
2022-07-22 01:00 | 2022-07-22 02:00 | Summer | FALSE | summer
2022-07-22 02:00 | 2022-07-22 03:00 | Summer | FALSE | summer
2022-07-22 03:00 | 2022-07-22 04:00 | Summer | FALSE | summer
2022-07-22 04:00 | 2022-07-22 05:00 | Summer | FALSE | summer
2022-07-22 05:00 | 2022-07-22 06:00 | Summer | FALSE | summer
2022-07-22 06:00 | 2022-07-22 07:00 | Summer | FALSE | summer
2022-07-22 07:00 | 2022-07-22 08:00 | Summer | FALSE | summer
2022-07-22 08:00 | 2022-07-22 09:00 | Summer | FALSE | summer
2022-07-22 09:00 | 2022-07-22 10:00 | Summer | FALSE | summer
2022-07-22 10:00 | 2022-07-22 11:00 | Summer | FALSE | summer
2022-07-22 11:00 | 2022-07-22 12:00 | Summer | FALSE | summer
2022-07-22 12:00 | 2022-07-22 13:00 | Summer | FALSE | summer
2022-07-22 13:00 | 2022-07-22 14:00 | Summer | FALSE | summer
2022-07-22 14:00 | 2022-07-22 15:00 | Summer | FALSE | summer
2022-07-22 15:00 | 2022-07-22 16:00 | Summer | FALSE | summer
2022-07-22 16:00 | 2022-07-22 17:00 | Summer | TRUE | summer
2022-07-22 17:00 | 2022-07-22 18:00 | Summer | TRUE | summer
2022-07-22 18:00 | 2022-07-22 19:00 | Summer | TRUE | summer
2022-07-22 19:00 | 2022-07-22 20:00 | Summer | TRUE | summer
2022-07-22 20:00 | 2022-07-22 21:00 | Summer | TRUE | summer
2022-07-22 21:00 | 2022-07-22 22:00 | Summer | FALSE | summer
2022-07-22 22:00 | 2022-07-22 23:00 | Summer | FALSE | summer
2022-07-22 23:00 | 2022-07-23 | Summer | FALSE | summer
2022-07-23 | 2022-07-23 01:00 | Summer | FALSE | summer
2022-07-23 01:00 | 2022-07-23 02:00 | Summer | FALSE | summer
2022-07-23 02:00 | 2022-07-23 03:00 | Summer | FALSE | summer
2022-07-23 03:00 | 2022-07-23 04:00 | Summer | FALSE | summer
2022-07-23 04:00 | 2022-07-23 05:00 | Summer | FALSE | summer
2022-07-23 05:00 | 2022-07-23 06:00 | Summer | FALSE | summer
2022-07-23 06:00 | 2022-07-23 07:00 | Summer | FALSE | summer
2022-07-23 07:00 | 2022-07-23 08:00 | Summer | FALSE | summer
2022-07-23 08:00 | 2022-07-23 09:00 | Summer | FALSE | summer
2022-07-23 09:00 | 2022-07-23 10:00 | Summer | FALSE | summer
2022-07-23 10:00 | 2022-07-23 11:00 | Summer | FALSE | summer
2022-07-23 11:00 | 2022-07-23 12:00 | Summer | FALSE | summer
2022-07-23 12:00 | 2022-07-23 13:00 | Summer | FALSE | summer
2022-07-23 13:00 | 2022-07-23 14:00 | Summer | FALSE | summer
2022-07-23 14:00 | 2022-07-23 15:00 | Summer | FALSE | summer
2022-07-23 15:00 | 2022-07-23 16:00 | Summer | FALSE | summer
2022-07-23 16:00 | 2022-07-23 17:00 | Summer | TRUE | summer
2022-07-23 17:00 | 2022-07-23 18:00 | Summer | TRUE | summer
2022-07-23 18:00 | 2022-07-23 19:00 | Summer | TRUE | summer
2022-07-23 19:00 | 2022-07-23 20:00 | Summer | TRUE | summer
2022-07-23 20:00 | 2022-07-23 21:00 | Summer | TRUE | summer
2022-07-23 21:00 | 2022-07-23 22:00 | Summer | FALSE | summer
2022-07-23 22:00 | 2022-07-23 23:00 | Summer | FALSE | summer
2022-07-23 23:00 | 2022-07-24 | Summer | FALSE | summer
2022-07-24 | 2022-07-24 01:00 | Summer | FALSE | summer
2022-07-24 01:00 | 2022-07-24 02:00 | Summer | FALSE | summer
2022-07-24 02:00 | 2022-07-24 03:00 | Summer | FALSE | summer
2022-07-24 03:00 | 2022-07-24 04:00 | Summer | FALSE | summer
2022-07-24 04:00 | 2022-07-24 05:00 | Summer | FALSE | summer
2022-07-24 05:00 | 2022-07-24 06:00 | Summer | FALSE | summer
2022-07-24 06:00 | 2022-07-24 07:00 | Summer | FALSE | summer
2022-07-24 07:00 | 2022-07-24 08:00 | Summer | FALSE | summer
2022-07-24 08:00 | 2022-07-24 09:00 | Summer | FALSE | summer
2022-07-24 09:00 | 2022-07-24 10:00 | Summer | FALSE | summer
2022-07-24 10:00 | 2022-07-24 11:00 | Summer | FALSE | summer
2022-07-24 11:00 | 2022-07-24 12:00 | Summer | FALSE | summer
2022-07-24 12:00 | 2022-07-24 13:00 | Summer | FALSE | summer
2022-07-24 13:00 | 2022-07-24 14:00 | Summer | FALSE | summer
2022-07-24 14:00 | 2022-07-24 15:00 | Summer | FALSE | summer
2022-07-24 15:00 | 2022-07-24 16:00 | Summer | FALSE | summer
2022-07-24 16:00 | 2022-07-24 17:00 | Summer | TRUE | summer
2022-07-24 17:00 | 2022-07-24 18:00 | Summer | TRUE | summer
2022-07-24 18:00 | 2022-07-24 19:00 | Summer | TRUE | summer
2022-07-24 19:00 | 2022-07-24 20:00 | Summer | TRUE | summer
2022-07-24 20:00 | 2022-07-24 21:00 | Summer | TRUE | summer
2022-07-24 21:00 | 2022-07-24 22:00 | Summer | FALSE | summer
2022-07-24 22:00 | 2022-07-24 23:00 | Summer | FALSE | summer
2022-07-24 23:00 | 2022-07-25 | Summer | FALSE | summer
2022-07-25 | 2022-07-25 01:00 | Summer | FALSE | summer
2022-07-25 01:00 | 2022-07-25 02:00 | Summer | FALSE | summer
2022-07-25 02:00 | 2022-07-25 03:00 | Summer | FALSE | summer
2022-07-25 03:00 | 2022-07-25 04:00 | Summer | FALSE | summer
2022-07-25 04:00 | 2022-07-25 05:00 | Summer | FALSE | summer
2022-07-25 05:00 | 2022-07-25 06:00 | Summer | FALSE | summer
2022-07-25 06:00 | 2022-07-25 07:00 | Summer | FALSE | summer
2022-07-25 07:00 | 2022-07-25 08:00 | Summer | FALSE | summer
2022-07-25 08:00 | 2022-07-25 09:00 | Summer | FALSE | summer
2022-07-25 09:00 | 2022-07-25 10:00 | Summer | FALSE | summer
2022-07-25 10:00 | 2022-07-25 11:00 | Summer | FALSE | summer
2022-07-25 11:00 | 2022-07-25 12:00 | Summer | FALSE | summer
2022-07-25 12:00 | 2022-07-25 13:00 | Summer | FALSE | summer
2022-07-25 13:00 | 2022-07-25 14:00 | Summer | FALSE | summer
2022-07-25 14:00 | 2022-07-25 15:00 | Summer | FALSE | summer
2022-07-25 15:00 | 2022-07-25 16:00 | Summer | FALSE | summer
2022-07-25 16:00 | 2022-07-25 17:00 | Summer | TRUE | summer
2022-07-25 17:00 | 2022-07-25 18:00 | Summer | TRUE | summer
2022-07-25 18:00 | 2022-07-25 19:00 | Summer | TRUE | summer
2022-07-25 19:00 | 2022-07-25 20:00 | Summer | TRUE | summer
2022-07-25 20:00 | 2022-07-25 21:00 | Summer | TRUE | summer
2022-07-25 21:00 | 2022-07-25 22:00 | Summer | FALSE | summer
2022-07-25 22:00 | 2022-07-25 23:00 | Summer | FALSE | summer
2022-07-25 23:00 | 2022-07-26 | Summer | FALSE | summer
2022-07-26 | 2022-07-26 01:00 | Summer | FALSE | summer
2022-07-26 01:00 | 2022-07-26 02:00 | Summer | FALSE | summer
2022-07-26 02:00 | 2022-07-26 03:00 | Summer | FALSE | summer
2022-07-26 03:00 | 2022-07-26 04:00 | Summer | FALSE | summer
2022-07-26 04:00 | 2022-07-26 05:00 | Summer | FALSE | summer
2022-07-26 05:00 | 2022-07-26 06:00 | Summer | FALSE | summer
2022-07-26 06:00 | 2022-07-26 07:00 | Summer | FALSE | summer
2022-07-26 07:00 | 2022-07-26 08:00 | Summer | FALSE | summer
2022-07-26 08:00 | 2022-07-26 09:00 | Summer | FALSE | summer
2022-07-26 09:00 | 2022-07-26 10:00 | Summer | FALSE | summer
2022-07-26 10:00 | 2022-07-26 11:00 | Summer | FALSE | summer
2022-07-26 11:00 | 2022-07-26 12:00 | Summer | FALSE | summer
2022-07-26 12:00 | 2022-07-26 13:00 | Summer | FALSE | summer
2022-07-26 13:00 | 2022-07-26 14:00 | Summer | FALSE | summer
2022-07-26 14:00 | 2022-07-26 15:00 | Summer | FALSE | summer
2022-07-26 15:00 | 2022-07-26 16:00 | Summer | FALSE | summer
2022-07-26 16:00 | 2022-07-26 17:00 | Summer | TRUE | summer
2022-07-26 17:00 | 2022-07-26 18:00 | Summer | TRUE | summer
2022-07-26 18:00 | 2022-07-26 19:00 | Summer | TRUE | summer
2022-07-26 19:00 | 2022-07-26 20:00 | Summer | TRUE | summer
2022-07-26 20:00 | 2022-07-26 21:00 | Summer | TRUE | summer
2022-07-26 21:00 | 2022-07-26 22:00 | Summer | FALSE | summer
2022-07-26 22:00 | 2022-07-26 23:00 | Summer | FALSE | summer
2022-07-26 23:00 | 2022-07-27 | Summer | FALSE | summer
2022-07-27 | 2022-07-27 01:00 | Summer | FALSE | summer
2022-07-27 01:00 | 2022-07-27 02:00 | Summer | FALSE | summer
2022-07-27 02:00 | 2022-07-27 03:00 | Summer | FALSE | summer
2022-07-27 03:00 | 2022-07-27 04:00 | Summer | FALSE | summer
2022-07-27 04:00 | 2022-07-27 05:00 | Summer | FALSE | summer
2022-07-27 05:00 | 2022-07-27 06:00 | Summer | FALSE | summer
2022-07-27 06:00 | 2022-07-27 07:00 | Summer | FALSE | summer
2022-07-27 07:00 | 2022-07-27 08:00 | Summer | FALSE | summer
2022-07-27 08:00 | 2022-07-27 09:00 | Summer | FALSE | summer
2022-07-27 09:00 | 2022-07-27 10:00 | Summer | FALSE | summer
2022-07-27 10:00 | 2022-07-27 11:00 | Summer | FALSE | summer
2022-07-27 11:00 | 2022-07-27 12:00 | Summer | FALSE | summer
2022-07-27 12:00 | 2022-07-27 13:00 | Summer | FALSE | summer
2022-07-27 13:00 | 2022-07-27 14:00 | Summer | FALSE | summer
2022-07-27 14:00 | 2022-07-27 15:00 | Summer | FALSE | summer
2022-07-27 15:00 | 2022-07-27 16:00 | Summer | FALSE | summer
2022-07-27 16:00 | 2022-07-27 17:00 | Summer | TRUE | summer
2022-07-27 17:00 | 2022-07-27 18:00 | Summer | TRUE | summer
2022-07-27 18:00 | 2022-07-27 19:00 | Summer | TRUE | summer
2022-07-27 19:00 | 2022-07-27 20:00 | Summer | TRUE | summer
2022-07-27 20:00 | 2022-07-27 21:00 | Summer | TRUE | summer
2022-07-27 21:00 | 2022-07-27 22:00 | Summer | FALSE | summer
2022-07-27 22:00 | 2022-07-27 23:00 | Summer | FALSE | summer
2022-07-27 23:00 | 2022-07-28 | Summer | FALSE | summer
2022-07-28 | 2022-07-28 01:00 | Summer | FALSE | summer
2022-07-28 01:00 | 2022-07-28 02:00 | Summer | FALSE | summer
2022-07-28 02:00 | 2022-07-28 03:00 | Summer | FALSE | summer
2022-07-28 03:00 | 2022-07-28 04:00 | Summer | FALSE | summer
2022-07-28 04:00 | 2022-07-28 05:00 | Summer | FALSE | summer
2022-07-28 05:00 | 2022-07-28 06:00 | Summer | FALSE | summer
2022-07-28 06:00 | 2022-07-28 07:00 | Summer | FALSE | summer
2022-07-28 07:00 | 2022-07-28 08:00 | Summer | FALSE | summer
2022-07-28 08:00 | 2022-07-28 09:00 | Summer | FALSE | summer
2022-07-28 09:00 | 2022-07-28 10:00 | Summer | FALSE | summer
2022-07-28 10:00 | 2022-07-28 11:00 | Summer | FALSE | summer
2022-07-28 11:00 | 2022-07-28 12:00 | Summer | FALSE | summer
2022-07-28 12:00 | 2022-07-28 13:00 | Summer | FALSE | summer
2022-07-28 13:00 | 2022-07-28 14:00 | Summer | FALSE | summer
2022-07-28 14:00 | 2022-07-28 15:00 | Summer | FALSE | summer
2022-07-28 15:00 | 2022-07-28 16:00 | Summer | FALSE | summer
2022-07-28 16:00 | 2022-07-28 17:00 | Summer | TRUE | summer
2022-07-28 17:00 | 2022-07-28 18:00 | Summer | TRUE | summer
2022-07-28 18:00 | 2022-07-28 19:00 | Summer | TRUE | summer
2022-07-28 19:00 | 2022-07-28 20:00 | Summer | TRUE | summer
2022-07-28 20:00 | 2022-07-28 21:00 | Summer | TRUE | summer
2022-07-28 21:00 | 2022-07-28 22:00 | Summer | FALSE | summer
2022-07-28 22:00 | 2022-07-28 23:00 | Summer | FALSE | summer
2022-07-28 23:00 | 2022-07-29 | Summer | FALSE | summer
2022-07-29 | 2022-07-29 01:00 | Summer | FALSE | summer
2022-07-29 01:00 | 2022-07-29 02:00 | Summer | FALSE | summer
2022-07-29 02:00 | 2022-07-29 03:00 | Summer | FALSE | summer
2022-07-29 03:00 | 2022-07-29 04:00 | Summer | FALSE | summer
2022-07-29 04:00 | 2022-07-29 05:00 | Summer | FALSE | summer
2022-07-29 05:00 | 2022-07-29 06:00 | Summer | FALSE | summer
2022-07-29 06:00 | 2022-07-29 07:00 | Summer | FALSE | summer
2022-07-29 07:00 | 2022-07-29 08:00 | Summer | FALSE | summer
2022-07-29 08:00 | 2022-07-29 09:00 | Summer | FALSE | summer
2022-07-29 09:00 | 2022-07-29 10:00 | Summer | FALSE | summer
2022-07-29 10:00 | 2022-07-29 11:00 | Summer | FALSE | summer
2022-07-29 11:00 | 2022-07-29 12:00 | Summer | FALSE | summer
2022-07-29 12:00 | 2022-07-29 13:00 | Summer | FALSE | summer
2022-07-29 13:00 | 2022-07-29 14:00 | Summer | FALSE | summer
2022-07-29 14:00 | 2022-07-29 15:00 | Summer | FALSE | summer
2022-07-29 15:00 | 2022-07-29 16:00 | Summer | FALSE | summer
2022-07-29 16:00 | 2022-07-29 17:00 | Summer | TRUE | summer
2022-07-29 17:00 | 2022-07-29 18:00 | Summer | TRUE | summer
2022-07-29 18:00 | 2022-07-29 19:00 | Summer | TRUE | summer
2022-07-29 19:00 | 2022-07-29 20:00 | Summer | TRUE | summer
2022-07-29 20:00 | 2022-07-29 21:00 | Summer | TRUE | summer
2022-07-29 21:00 | 2022-07-29 22:00 | Summer | FALSE | summer
2022-07-29 22:00 | 2022-07-29 23:00 | Summer | FALSE | summer
2022-07-29 23:00 | 2022-07-30 | Summer | FALSE | summer
2022-07-30 | 2022-07-30 01:00 | Summer | FALSE | summer
2022-07-30 01:00 | 2022-07-30 02:00 | Summer | FALSE | summer
2022-07-30 02:00 | 2022-07-30 03:00 | Summer | FALSE | summer
2022-07-30 03:00 | 2022-07-30 04:00 | Summer | FALSE | summer
2022-07-30 04:00 | 2022-07-30 05:00 | Summer | FALSE | summer
2022-07-30 05:00 | 2022-07-30 06:00 | Summer | FALSE | summer
2022-07-30 06:00 | 2022-07-30 07:00 | Summer | FALSE | summer
2022-07-30 07:00 | 2022-07-30 08:00 | Summer | FALSE | summer
2022-07-30 08:00 | 2022-07-30 09:00 | Summer | FALSE | summer
2022-07-30 09:00 | 2022-07-30 10:00 | Summer | FALSE | summer
2022-07-30 10:00 | 2022-07-30 11:00 | Summer | FALSE | summer
2022-07-30 11:00 | 2022-07-30 12:00 | Summer | FALSE | summer
2022-07-30 12:00 | 2022-07-30 13:00 | Summer | FALSE | summer
2022-07-30 13:00 | 2022-07-30 14:00 | Summer | FALSE | summer
2022-07-30 14:00 | 2022-07-30 15:00 | Summer | FALSE | summer
2022-07-30 15:00 | 2022-07-30 16:00 | Summer | FALSE | summer
2022-07-30 16:00 | 2022-07-30 17:00 | Summer | TRUE | summer
2022-07-30 17:00 | 2022-07-30 18:00 | Summer | TRUE | summer
2022-07-30 18:00 | 2022-07-30 19:00 | Summer | TRUE | summer
2022-07-30 19:00 | 2022-07-30 20:00 | Summer | TRUE | summer
2022-07-30 20:00 | 2022-07-30 21:00 | Summer | TRUE | summer
2022-07-30 21:00 | 2022-07-30 22:00 | Summer | FALSE | summer
2022-07-30 22:00 | 2022-07-30 23:00 | Summer | FALSE | summer
2022-07-30 23:00 | 2022-07-31 | Summer | FALSE | summer
2022-07-31 | 2022-07-31 01:00 | Summer | FALSE | summer
2022-07-31 01:00 | 2022-07-31 02:00 | Summer | FALSE | summer
2022-07-31 02:00 | 2022-07-31 03:00 | Summer | FALSE | summer
2022-07-31 03:00 | 2022-07-31 04:00 | Summer | FALSE | summer
2022-07-31 04:00 | 2022-07-31 05:00 | Summer | FALSE | summer
2022-07-31 05:00 | 2022-07-31 06:00 | Summer | FALSE | summer
2022-07-31 06:00 | 2022-07-31 07:00 | Summer | FALSE | summer
2022-07-31 07:00 | 2022-07-31 08:00 | Summer | FALSE | summer
2022-07-31 08:00 | 2022-07-31 09:00 | Summer | FALSE | summer
2022-07-31 09:00 | 2022-07-31 10:00 | Summer | FALSE | summer
2022-07-31 10:00 | 2022-07-31 11:00 | Summer | FALSE | summer
2022-07-31 11:00 | 2022-07-31 12:00 | Summer | FALSE | summer
2022-07-31 12:00 | 2022-07-31 13:00 | Summer | FALSE | summer
2022-07-31 13:00 | 2022-07-31 14:00 | Summer | FALSE | summer
2022-07-31 14:00 | 2022-07-31 15:00 | Summer | FALSE | summer
2022-07-31 15:00 | 2022-07-31 16:00 | Summer | FALSE | summer
2022-07-31 16:00 | 2022-07-31 17:00 | Summer | TRUE | summer
2022-07-31 17:00 | 2022-07-31 18:00 | Summer | TRUE | summer
2022-07-31 18:00 | 2022-07-31 19:00 | Summer | TRUE | summer
2022-07-31 19:00 | 2022-07-31 20:00 | Summer | TRUE | summer
2022-07-31 20:00 | 2022-07-31 21:00 | Summer | TRUE | summer
2022-07-31 21:00 | 2022-07-31 22:00 | Summer | FALSE | summer
2022-07-31 22:00 | 2022-07-31 23:00 | Summer | FALSE | summer
2022-07-31 23:00 | 2022-08-01 | Summer | FALSE | summer
2022-08-01 | 2022-08-01 01:00 | Summer | FALSE | summer
2022-08-01 01:00 | 2022-08-01 02:00 | Summer | FALSE | summer
2022-08-01 02:00 | 2022-08-01 03:00 | Summer | FALSE | summer
2022-08-01 03:00 | 2022-08-01 04:00 | Summer | FALSE | summer
2022-08-01 04:00 | 2022-08-01 05:00 | Summer | FALSE | summer
2022-08-01 05:00 | 2022-08-01 06:00 | Summer | FALSE | summer
2022-08-01 06:00 | 2022-08-01 07:00 | Summer | FALSE | summer
2022-08-01 07:00 | 2022-08-01 08:00 | Summer | FALSE | summer
2022-08-01 08:00 | 2022-08-01 09:00 | Summer | FALSE | summer
2022-08-01 09:00 | 2022-08-01 10:00 | Summer | FALSE | summer
2022-08-01 10:00 | 2022-08-01 11:00 | Summer | FALSE | summer
2022-08-01 11:00 | 2022-08-01 12:00 | Summer | FALSE | summer
2022-08-01 12:00 | 2022-08-01 13:00 | Summer | FALSE | summer
2022-08-01 13:00 | 2022-08-01 14:00 | Summer | FALSE | summer
2022-08-01 14:00 | 2022-08-01 15:00 | Summer | FALSE | summer
2022-08-01 15:00 | 2022-08-01 16:00 | Summer | FALSE | summer
2022-08-01 16:00 | 2022-08-01 17:00 | Summer | TRUE | summer
2022-08-01 17:00 | 2022-08-01 18:00 | Summer | TRUE | summer
2022-08-01 18:00 | 2022-08-01 19:00 | Summer | TRUE | summer
2022-08-01 19:00 | 2022-08-01 20:00 | Summer | TRUE | summer
2022-08-01 20:00 | 2022-08-01 21:00 | Summer | TRUE | summer
2022-08-01 21:00 | 2022-08-01 22:00 | Summer | FALSE | summer
2022-08-01 22:00 | 2022-08-01 23:00 | Summer | FALSE | summer
2022-08-01 23:00 | 2022-08-02 | Summer | FALSE | summer
2022-08-02 | 2022-08-02 01:00 | Summer | FALSE | summer
2022-08-02 01:00 | 2022-08-02 02:00 | Summer | FALSE | summer
2022-08-02 02:00 | 2022-08-02 03:00 | Summer | FALSE | summer
2022-08-02 03:00 | 2022-08-02 04:00 | Summer | FALSE | summer
2022-08-02 04:00 | 2022-08-02 05:00 | Summer | FALSE | summer
2022-08-02 05:00 | 2022-08-02 06:00 | Summer | FALSE | summer
2022-08-02 06:00 | 2022-08-02 07:00 | Summer | FALSE | summer
2022-08-02 07:00 | 2022-08-02 08:00 | Summer | FALSE | summer
2022-08-02 08:00 | 2022-08-02 09:00 | Summer | FALSE | summer
2022-08-02 09:00 | 2022-08-02 10:00 | Summer | FALSE | summer
2022-08-02 10:00 | 2022-08-02 11:00 | Summer | FALSE | summer
2022-08-02 11:00 | 2022-08-02 12:00 | Summer | FALSE | summer
2022-08-02 12:00 | 2022-08-02 13:00 | Summer | FALSE | summer
2022-08-02 13:00 | 2022-08-02 14:00 | Summer | FALSE | summer
2022-08-02 14:00 | 2022-08-02 15:00 | Summer | FALSE | summer
2022-08-02 15:00 | 2022-08-02 16:00 | Summer | FALSE | summer
2022-08-02 16:00 | 2022-08-02 17:00 | Summer | TRUE | summer
2022-08-02 17:00 | 2022-08-02 18:00 | Summer | TRUE | summer
2022-08-02 18:00 | 2022-08-02 19:00 | Summer | TRUE | summer
2022-08-02 19:00 | 2022-08-02 20:00 | Summer | TRUE | summer
2022-08-02 20:00 | 2022-08-02 21:00 | Summer | TRUE | summer
2022-08-02 21:00 | 2022-08-02 22:00 | Summer | FALSE | summer
2022-08-02 22:00 | 2022-08-02 23:00 | Summer | FALSE | summer
2022-08-02 23:00 | 2022-08-03 | Summer | FALSE | summer
2022-08-03 | 2022-08-03 01:00 | Summer | FALSE | summer
2022-08-03 01:00 | 2022-08-03 02:00 | Summer | FALSE | summer
2022-08-03 02:00 | 2022-08-03 03:00 | Summer | FALSE | summer
2022-08-03 03:00 | 2022-08-03 04:00 | Summer | FALSE | summer
2022-08-03 04:00 | 2022-08-03 05:00 | Summer | FALSE | summer
2022-08-03 05:00 | 2022-08-03 06:00 | Summer | FALSE | summer
2022-08-03 06:00 | 2022-08-03 07:00 | Summer | FALSE | summer
2022-08-03 07:00 | 2022-08-03 08:00 | Summer | FALSE | summer
2022-08-03 08:00 | 2022-08-03 09:00 | Summer | FALSE | summer
2022-08-03 09:00 | 2022-08-03 10:00 | Summer | FALSE | summer
2022-08-03 10:00 | 2022-08-03 11:00 | Summer | FALSE | summer
2022-08-03 11:00 | 2022-08-03 12:00 | Summer | FALSE | summer
2022-08-03 12:00 | 2022-08-03 13:00 | Summer | FALSE | summer
2022-08-03 13:00 | 2022-08-03 14:00 | Summer | FALSE | summer
2022-08-03 14:00 | 2022-08-03 15:00 | Summer | FALSE | summer
2022-08-03 15:00 | 2022-08-03 16:00 | Summer | FALSE | summer
2022-08-03 16:00 | 2022-08-03 17:00 | Summer | TRUE | summer
2022-08-03 17:00 | 2022-08-03 18:00 | Summer | TRUE | summer
2022-08-03 18:00 | 2022-08-03 19:00 | Summer | TRUE | summer
2022-08-03 19:00 | 2022-08-03 20:00 | Summer | TRUE | summer
2022-08-03 20:00 | 2022-08-03 21:00 | Summer | TRUE | summer
2022-08-03 21:00 | 2022-08-03 22:00 | Summer | FALSE | summer
2022-08-03 22:00 | 2022-08-03 23:00 | Summer | FALSE | summer
2022-08-03 23:00 | 2022-08-04 | Summer | FALSE | summer
2022-08-04 | 2022-08-04 01:00 | Summer | FALSE | summer
2022-08-04 01:00 | 2022-08-04 02:00 | Summer | FALSE | summer
2022-08-04 02:00 | 2022-08-04 03:00 | Summer | FALSE | summer
2022-08-04 03:00 | 2022-08-04 04:00 | Summer | FALSE | summer
2022-08-04 04:00 | 2022-08-04 05:00 | Summer | FALSE | summer
2022-08-04 05:00 | 2022-08-04 06:00 | Summer | FALSE | summer
2022-08-04 06:00 | 2022-08-04 07:00 | Summer | FALSE | summer
2022-08-04 07:00 | 2022-08-04 08:00 | Summer | FALSE | summer
2022-08-04 08:00 | 2022-08-04 09:00 | Summer | FALSE | summer
2022-08-04 09:00 | 2022-08-04 10:00 | Summer | FALSE | summer
2022-08-04 10:00 | 2022-08-04 11:00 | Summer | FALSE | summer
2022-08-04 11:00 | 2022-08-04 12:00 | Summer | FALSE | summer
2022-08-04 12:00 | 2022-08-04 13:00 | Summer | FALSE | summer
2022-08-04 13:00 | 2022-08-04 14:00 | Summer | FALSE | summer
2022-08-04 14:00 | 2022-08-04 15:00 | Summer | FALSE | summer
2022-08-04 15:00 | 2022-08-04 16:00 | Summer | FALSE | summer
2022-08-04 16:00 | 2022-08-04 17:00 | Summer | TRUE | summer
2022-08-04 17:00 | 2022-08-04 18:00 | Summer | TRUE | summer
2022-08-04 18:00 | 2022-08-04 19:00 | Summer | TRUE | summer
2022-08-04 19:00 | 2022-08-04 20:00 | Summer | TRUE | summer
2022-08-04 20:00 | 2022-08-04 21:00 | Summer | TRUE | summer
2022-08-04 21:00 | 2022-08-04 22:00 | Summer | FALSE | summer
2022-08-04 22:00 | 2022-08-04 23:00 | Summer | FALSE | summer
2022-08-04 23:00 | 2022-08-05 | Summer | FALSE | summer
2022-08-05 | 2022-08-05 01:00 | Summer | FALSE | summer
2022-08-05 01:00 | 2022-08-05 02:00 | Summer | FALSE | summer
2022-08-05 02:00 | 2022-08-05 03:00 | Summer | FALSE | summer
2022-08-05 03:00 | 2022-08-05 04:00 | Summer | FALSE | summer
2022-08-05 04:00 | 2022-08-05 05:00 | Summer | FALSE | summer
2022-08-05 05:00 | 2022-08-05 06:00 | Summer | FALSE | summer
2022-08-05 06:00 | 2022-08-05 07:00 | Summer | FALSE | summer
2022-08-05 07:00 | 2022-08-05 08:00 | Summer | FALSE | summer
2022-08-05 08:00 | 2022-08-05 09:00 | Summer | FALSE | summer
2022-08-05 09:00 | 2022-08-05 10:00 | Summer | FALSE | summer
2022-08-05 10:00 | 2022-08-05 11:00 | Summer | FALSE | summer
2022-08-05 11:00 | 2022-08-05 12:00 | Summer | FALSE | summer
2022-08-05 12:00 | 2022-08-05 13:00 | Summer | FALSE | summer
2022-08-05 13:00 | 2022-08-05 14:00 | Summer | FALSE | summer
2022-08-05 14:00 | 2022-08-05 15:00 | Summer | FALSE | summer
2022-08-05 15:00 | 2022-08-05 16:00 | Summer | FALSE | summer
2022-08-05 16:00 | 2022-08-05 17:00 | Summer | TRUE | summer
2022-08-05 17:00 | 2022-08-05 18:00 | Summer | TRUE | summer
2022-08-05 18:00 | 2022-08-05 19:00 | Summer | TRUE | summer
2022-08-05 19:00 | 2022-08-05 20:00 | Summer | TRUE | summer
2022-08-05 20:00 | 2022-08-05 21:00 | Summer | TRUE | summer
2022-08-05 21:00 | 2022-08-05 22:00 | Summer | FALSE | summer
2022-08-05 22:00 | 2022-08-05 23:00 | Summer | FALSE | summer
2022-08-05 23:00 | 2022-08-06 | Summer | FALSE | summer
2022-08-06 | 2022-08-06 01:00 | Summer | FALSE | summer
2022-08-06 01:00 | 2022-08-06 02:00 | Summer | FALSE | summer
2022-08-06 02:00 | 2022-08-06 03:00 | Summer | FALSE | summer
2022-08-06 03:00 | 2022-08-06 04:00 | Summer | FALSE | summer
2022-08-06 04:00 | 2022-08-06 05:00 | Summer | FALSE | summer
2022-08-06 05:00 | 2022-08-06 06:00 | Summer | FALSE | summer
2022-08-06 06:00 | 2022-08-06 07:00 | Summer | FALSE | summer
2022-08-06 07:00 | 2022-08-06 08:00 | Summer | FALSE | summer
2022-08-06 08:00 | 2022-08-06 09:00 | Summer | FALSE | summer
2022-08-06 09:00 | 2022-08-06 10:00 | Summer | FALSE | summer
2022-08-06 10:00 | 2022-08-06 11:00 | Summer | FALSE | summer
2022-08-06 11:00 | 2022-08-06 12:00 | Summer | FALSE | summer
2022-08-06 12:00 | 2022-08-06 13:00 | Summer | FALSE | summer
2022-08-06 13:00 | 2022-08-06 14:00 | Summer | FALSE | summer
2022-08-06 14:00 | 2022-08-06 15:00 | Summer | FALSE | summer
2022-08-06 15:00 | 2022-08-06 16:00 | Summer | FALSE | summer
2022-08-06 16:00 | 2022-08-06 17:00 | Summer | TRUE | summer
2022-08-06 17:00 | 2022-08-06 18:00 | Summer | TRUE | summer
2022-08-06 18:00 | 2022-08-06 19:00 | Summer | TRUE | summer
2022-08-06 19:00 | 2022-08-06 20:00 | Summer | TRUE | summer
2022-08-06 20:00 | 2022-08-06 21:00 | Summer | TRUE | summer
2022-08-06 21:00 | 2022-08-06 22:00 | Summer | FALSE | summer
2022-08-06 22:00 | 2022-08-06 23:00 | Summer | FALSE | summer
2022-08-06 23:00 | 2022-08-07 | Summer | FALSE | summer
2022-08-07 | 2022-08-07 01:00 | Summer | FALSE | summer
2022-08-07 01:00 | 2022-08-07 02:00 | Summer | FALSE | summer
2022-08-07 02:00 | 2022-08-07 03:00 | Summer | FALSE | summer
2022-08-07 03:00 | 2022-08-07 04:00 | Summer | FALSE | summer
2022-08-07 04:00 | 2022-08-07 05:00 | Summer | FALSE | summer
2022-08-07 05:00 | 2022-08-07 06:00 | Summer | FALSE | summer
2022-08-07 06:00 | 2022-08-07 07:00 | Summer | FALSE | summer
2022-08-07 07:00 | 2022-08-07 08:00 | Summer | FALSE | summer
2022-08-07 08:00 | 2022-08-07 09:00 | Summer | FALSE | summer
2022-08-07 09:00 | 2022-08-07 10:00 | Summer | FALSE | summer
2022-08-07 10:00 | 2022-08-07 11:00 | Summer | FALSE | summer
2022-08-07 11:00 | 2022-08-07 12:00 | Summer | FALSE | summer
2022-08-07 12:00 | 2022-08-07 13:00 | Summer | FALSE | summer
2022-08-07 13:00 | 2022-08-07 14:00 | Summer | FALSE | summer
2022-08-07 14:00 | 2022-08-07 15:00 | Summer | FALSE | summer
2022-08-07 15:00 | 2022-08-07 16:00 | Summer | FALSE | summer
2022-08-07 16:00 | 2022-08-07 17:00 | Summer | TRUE | summer
2022-08-07 17:00 | 2022-08-07 18:00 | Summer | TRUE | summer
2022-08-07 18:00 | 2022-08-07 19:00 | Summer | TRUE | summer
2022-08-07 19:00 | 2022-08-07 20:00 | Summer | TRUE | summer
2022-08-07 20:00 | 2022-08-07 21:00 | Summer | TRUE | summer
2022-08-07 21:00 | 2022-08-07 22:00 | Summer | FALSE | summer
2022-08-07 22:00 | 2022-08-07 23:00 | Summer | FALSE | summer
2022-08-07 23:00 | 2022-08-08 | Summer | FALSE | summer
2022-08-08 | 2022-08-08 01:00 | Summer | FALSE | summer
2022-08-08 01:00 | 2022-08-08 02:00 | Summer | FALSE | summer
2022-08-08 02:00 | 2022-08-08 03:00 | Summer | FALSE | summer
2022-08-08 03:00 | 2022-08-08 04:00 | Summer | FALSE | summer
2022-08-08 04:00 | 2022-08-08 05:00 | Summer | FALSE | summer
2022-08-08 05:00 | 2022-08-08 06:00 | Summer | FALSE | summer
2022-08-08 06:00 | 2022-08-08 07:00 | Summer | FALSE | summer
2022-08-08 07:00 | 2022-08-08 08:00 | Summer | FALSE | summer
2022-08-08 08:00 | 2022-08-08 09:00 | Summer | FALSE | summer
2022-08-08 09:00 | 2022-08-08 10:00 | Summer | FALSE | summer
2022-08-08 10:00 | 2022-08-08 11:00 | Summer | FALSE | summer
2022-08-08 11:00 | 2022-08-08 12:00 | Summer | FALSE | summer
2022-08-08 12:00 | 2022-08-08 13:00 | Summer | FALSE | summer
2022-08-08 13:00 | 2022-08-08 14:00 | Summer | FALSE | summer
2022-08-08 14:00 | 2022-08-08 15:00 | Summer | FALSE | summer
2022-08-08 15:00 | 2022-08-08 16:00 | Summer | FALSE | summer
2022-08-08 16:00 | 2022-08-08 17:00 | Summer | TRUE | summer
2022-08-08 17:00 | 2022-08-08 18:00 | Summer | TRUE | summer
2022-08-08 18:00 | 2022-08-08 19:00 | Summer | TRUE | summer
2022-08-08 19:00 | 2022-08-08 20:00 | Summer | TRUE | summer
2022-08-08 20:00 | 2022-08-08 21:00 | Summer | TRUE | summer
2022-08-08 21:00 | 2022-08-08 22:00 | Summer | FALSE | summer
2022-08-08 22:00 | 2022-08-08 23:00 | Summer | FALSE | summer
2022-08-08 23:00 | 2022-08-09 | Summer | FALSE | summer
2022-08-09 | 2022-08-09 01:00 | Summer | FALSE | summer
2022-08-09 01:00 | 2022-08-09 02:00 | Summer | FALSE | summer
2022-08-09 02:00 | 2022-08-09 03:00 | Summer | FALSE | summer
2022-08-09 03:00 | 2022-08-09 04:00 | Summer | FALSE | summer
2022-08-09 04:00 | 2022-08-09 05:00 | Summer | FALSE | summer
2022-08-09 05:00 | 2022-08-09 06:00 | Summer | FALSE | summer
2022-08-09 06:00 | 2022-08-09 07:00 | Summer | FALSE | summer
2022-08-09 07:00 | 2022-08-09 08:00 | Summer | FALSE | summer
2022-08-09 08:00 | 2022-08-09 09:00 | Summer | FALSE | summer
2022-08-09 09:00 | 2022-08-09 10:00 | Summer | FALSE | summer
2022-08-09 10:00 | 2022-08-09 11:00 | Summer | FALSE | summer
2022-08-09 11:00 | 2022-08-09 12:00 | Summer | FALSE | summer
2022-08-09 12:00 | 2022-08-09 13:00 | Summer | FALSE | summer
2022-08-09 13:00 | 2022-08-09 14:00 | Summer | FALSE | summer
2022-08-09 14:00 | 2022-08-09 15:00 | Summer | FALSE | summer
2022-08-09 15:00 | 2022-08-09 16:00 | Summer | FALSE | summer
2022-08-09 16:00 | 2022-08-09 17:00 | Summer | TRUE | summer
2022-08-09 17:00 | 2022-08-09 18:00 | Summer | TRUE | summer
2022-08-09 18:00 | 2022-08-09 19:00 | Summer | TRUE | summer
2022-08-09 19:00 | 2022-08-09 20:00 | Summer | TRUE | summer
2022-08-09 20:00 | 2022-08-09 21:00 | Summer | TRUE | summer
2022-08-09 21:00 | 2022-08-09 22:00 | Summer | FALSE | summer
2022-08-09 22:00 | 2022-08-09 23:00 | Summer | FALSE | summer
2022-08-09 23:00 | 2022-08-10 | Summer | FALSE | summer
2022-08-10 | 2022-08-10 01:00 | Summer | FALSE | summer
2022-08-10 01:00 | 2022-08-10 02:00 | Summer | FALSE | summer
2022-08-10 02:00 | 2022-08-10 03:00 | Summer | FALSE | summer
2022-08-10 03:00 | 2022-08-10 04:00 | Summer | FALSE | summer
2022-08-10 04:00 | 2022-08-10 05:00 | Summer | FALSE | summer
2022-08-10 05:00 | 2022-08-10 06:00 | Summer | FALSE | summer
2022-08-10 06:00 | 2022-08-10 07:00 | Summer | FALSE | summer
2022-08-10 07:00 | 2022-08-10 08:00 | Summer | FALSE | summer
2022-08-10 08:00 | 2022-08-10 09:00 | Summer | FALSE | summer
2022-08-10 09:00 | 2022-08-10 10:00 | Summer | FALSE | summer
2022-08-10 10:00 | 2022-08-10 11:00 | Summer | FALSE | summer
2022-08-10 11:00 | 2022-08-10 12:00 | Summer | FALSE | summer
2022-08-10 12:00 | 2022-08-10 13:00 | Summer | FALSE | summer
2022-08-10 13:00 | 2022-08-10 14:00 | Summer | FALSE | summer
2022-08-10 14:00 | 2022-08-10 15:00 | Summer | FALSE | summer
2022-08-10 15:00 | 2022-08-10 16:00 | Summer | FALSE | summer
2022-08-10 16:00 | 2022-08-10 17:00 | Summer | TRUE | summer
2022-08-10 17:00 | 2022-08-10 18:00 | Summer | TRUE | summer
2022-08-10 18:00 | 2022-08-10 19:00 | Summer | TRUE | summer
2022-08-10 19:00 | 2022-08-10 20:00 | Summer | TRUE | summer
2022-08-10 20:00 | 2022-08-10 21:00 | Summer | TRUE | summer
2022-08-10 21:00 | 2022-08-10 22:00 | Summer | FALSE | summer
2022-08-10 22:00 | 2022-08-10 23:00 | Summer | FALSE | summer
2022-08-10 23:00 | 2022-08-11 | Summer | FALSE | summer
2022-08-11 | 2022-08-11 01:00 | Summer | FALSE | summer
2022-08-11 01:00 | 2022-08-11 02:00 | Summer | FALSE | summer
2022-08-11 02:00 | 2022-08-11 03:00 | Summer | FALSE | summer
2022-08-11 03:00 | 2022-08-11 04:00 | Summer | FALSE | summer
2022-08-11 04:00 | 2022-08-11 05:00 | Summer | FALSE | summer
2022-08-11 05:00 | 2022-08-11 06:00 | Summer | FALSE | summer
2022-08-11 06:00 | 2022-08-11 07:00 | Summer | FALSE | summer
2022-08-11 07:00 | 2022-08-11 08:00 | Summer | FALSE | summer
2022-08-11 08:00 | 2022-08-11 09:00 | Summer | FALSE | summer
2022-08-11 09:00 | 2022-08-11 10:00 | Summer | FALSE | summer
2022-08-11 10:00 | 2022-08-11 11:00 | Summer | FALSE | summer
2022-08-11 11:00 | 2022-08-11 12:00 | Summer | FALSE | summer
2022-08-11 12:00 | 2022-08-11 13:00 | Summer | FALSE | summer
2022-08-11 13:00 | 2022-08-11 14:00 | Summer | FALSE | summer
2022-08-11 14:00 | 2022-08-11 15:00 | Summer | FALSE | summer
2022-08-11 15:00 | 2022-08-11 16:00 | Summer | FALSE | summer
2022-08-11 16:00 | 2022-08-11 17:00 | Summer | TRUE | summer
2022-08-11 17:00 | 2022-08-11 18:00 | Summer | TRUE | summer
2022-08-11 18:00 | 2022-08-11 19:00 | Summer | TRUE | summer
2022-08-11 19:00 | 2022-08-11 20:00 | Summer | TRUE | summer
2022-08-11 20:00 | 2022-08-11 21:00 | Summer | TRUE | summer
2022-08-11 21:00 | 2022-08-11 22:00 | Summer | FALSE | summer
2022-08-11 22:00 | 2022-08-11 23:00 | Summer | FALSE | summer
2022-08-11 23:00 | 2022-08-12 | Summer | FALSE | summer
2022-08-12 | 2022-08-12 01:00 | Summer | FALSE | summer
2022-08-12 01:00 | 2022-08-12 02:00 | Summer | FALSE | summer
2022-08-12 02:00 | 2022-08-12 03:00 | Summer | FALSE | summer
2022-08-12 03:00 | 2022-08-12 04:00 | Summer | FALSE | summer
2022-08-12 04:00 | 2022-08-12 05:00 | Summer | FALSE | summer
2022-08-12 05:00 | 2022-08-12 06:00 | Summer | FALSE | summer
2022-08-12 06:00 | 2022-08-12 07:00 | Summer | FALSE | summer
2022-08-12 07:00 | 2022-08-12 08:00 | Summer | FALSE | summer
2022-08-12 08:00 | 2022-08-12 09:00 | Summer | FALSE | summer
2022-08-12 09:00 | 2022-08-12 10:00 | Summer | FALSE | summer
2022-08-12 10:00 | 2022-08-12 11:00 | Summer | FALSE | summer
2022-08-12 11:00 | 2022-08-12 12:00 | Summer | FALSE | summer
2022-08-12 12:00 | 2022-08-12 13:00 | Summer | FALSE | summer
2022-08-12 13:00 | 2022-08-12 14:00 | Summer | FALSE | summer
2022-08-12 14:00 | 2022-08-12 15:00 | Summer | FALSE | summer
2022-08-12 15:00 | 2022-08-12 16:00 | Summer | FALSE | summer
2022-08-12 16:00 | 2022-08-12 17:00 | Summer | TRUE | summer
2022-08-12 17:00 | 2022-08-12 18:00 | Summer | TRUE | summer
2022-08-12 18:00 | 2022-08-12 19:00 | Summer | TRUE | summer
2022-08-12 19:00 | 2022-08-12 20:00 | Summer | TRUE | summer
2022-08-12 20:00 | 2022-08-12 21:00 | Summer | TRUE | summer
2022-08-12 21:00 | 2022-08-12 22:00 | Summer | FALSE | summer
2022-08-12 22:00 | 2022-08-12 23:00 | Summer | FALSE | summer
2022-08-12 23:00 | 2022-08-13 | Summer | FALSE | summer
2022-08-13 | 2022-08-13 01:00 | Summer | FALSE | summer
2022-08-13 01:00 | 2022-08-13 02:00 | Summer | FALSE | summer
2022-08-13 02:00 | 2022-08-13 03:00 | Summer | FALSE | summer
2022-08-13 03:00 | 2022-08-13 04:00 | Summer | FALSE | summer
2022-08-13 04:00 | 2022-08-13 05:00 | Summer | FALSE | summer
2022-08-13 05:00 | 2022-08-13 06:00 | Summer | FALSE | summer
2022-08-13 06:00 | 2022-08-13 07:00 | Summer | FALSE | summer
2022-08-13 07:00 | 2022-08-13 08:00 | Summer | FALSE | summer
2022-08-13 08:00 | 2022-08-13 09:00 | Summer | FALSE | summer
2022-08-13 09:00 | 2022-08-13 10:00 | Summer | FALSE | summer
2022-08-13 10:00 | 2022-08-13 11:00 | Summer | FALSE | summer
2022-08-13 11:00 | 2022-08-13 12:00 | Summer | FALSE | summer
2022-08-13 12:00 | 2022-08-13 13:00 | Summer | FALSE | summer
2022-08-13 13:00 | 2022-08-13 14:00 | Summer | FALSE | summer
2022-08-13 14:00 | 2022-08-13 15:00 | Summer | FALSE | summer
2022-08-13 15:00 | 2022-08-13 16:00 | Summer | FALSE | summer
2022-08-13 16:00 | 2022-08-13 17:00 | Summer | TRUE | summer
2022-08-13 17:00 | 2022-08-13 18:00 | Summer | TRUE | summer
2022-08-13 18:00 | 2022-08-13 19:00 | Summer | TRUE | summer
2022-08-13 19:00 | 2022-08-13 20:00 | Summer | TRUE | summer
2022-08-13 20:00 | 2022-08-13 21:00 | Summer | TRUE | summer
2022-08-13 21:00 | 2022-08-13 22:00 | Summer | FALSE | summer
2022-08-13 22:00 | 2022-08-13 23:00 | Summer | FALSE | summer
2022-08-13 23:00 | 2022-08-14 | Summer | FALSE | summer
2022-08-14 | 2022-08-14 01:00 | Summer | FALSE | summer
2022-08-14 01:00 | 2022-08-14 02:00 | Summer | FALSE | summer
2022-08-14 02:00 | 2022-08-14 03:00 | Summer | FALSE | summer
2022-08-14 03:00 | 2022-08-14 04:00 | Summer | FALSE | summer
2022-08-14 04:00 | 2022-08-14 05:00 | Summer | FALSE | summer
2022-08-14 05:00 | 2022-08-14 06:00 | Summer | FALSE | summer
2022-08-14 06:00 | 2022-08-14 07:00 | Summer | FALSE | summer
2022-08-14 07:00 | 2022-08-14 08:00 | Summer | FALSE | summer
2022-08-14 08:00 | 2022-08-14 09:00 | Summer | FALSE | summer
2022-08-14 09:00 | 2022-08-14 10:00 | Summer | FALSE | summer
2022-08-14 10:00 | 2022-08-14 11:00 | Summer | FALSE | summer
2022-08-14 11:00 | 2022-08-14 12:00 | Summer | FALSE | summer
2022-08-14 12:00 | 2022-08-14 13:00 | Summer | FALSE | summer
2022-08-14 13:00 | 2022-08-14 14:00 | Summer | FALSE | summer
2022-08-14 14:00 | 2022-08-14 15:00 | Summer | FALSE | summer
2022-08-14 15:00 | 2022-08-14 16:00 | Summer | FALSE | summer
2022-08-14 16:00 | 2022-08-14 17:00 | Summer | TRUE | summer
2022-08-14 17:00 | 2022-08-14 18:00 | Summer | TRUE | summer
2022-08-14 18:00 | 2022-08-14 19:00 | Summer | TRUE | summer
2022-08-14 19:00 | 2022-08-14 20:00 | Summer | TRUE | summer
2022-08-14 20:00 | 2022-08-14 21:00 | Summer | TRUE | summer
2022-08-14 21:00 | 2022-08-14 22:00 | Summer | FALSE | summer
2022-08-14 22:00 | 2022-08-14 23:00 | Summer | FALSE | summer
2022-08-14 23:00 | 2022-08-15 | Summer | FALSE | summer
2022-08-15 | 2022-08-15 01:00 | Summer | FALSE | summer
2022-08-15 01:00 | 2022-08-15 02:00 | Summer | FALSE | summer
2022-08-15 02:00 | 2022-08-15 03:00 | Summer | FALSE | summer
2022-08-15 03:00 | 2022-08-15 04:00 | Summer | FALSE | summer
2022-08-15 04:00 | 2022-08-15 05:00 | Summer | FALSE | summer
2022-08-15 05:00 | 2022-08-15 06:00 | Summer | FALSE | summer
2022-08-15 06:00 | 2022-08-15 07:00 | Summer | FALSE | summer
2022-08-15 07:00 | 2022-08-15 08:00 | Summer | FALSE | summer
2022-08-15 08:00 | 2022-08-15 09:00 | Summer | FALSE | summer
2022-08-15 09:00 | 2022-08-15 10:00 | Summer | FALSE | summer
2022-08-15 10:00 | 2022-08-15 11:00 | Summer | FALSE | summer
2022-08-15 11:00 | 2022-08-15 12:00 | Summer | FALSE | summer
2022-08-15 12:00 | 2022-08-15 13:00 | Summer | FALSE | summer
2022-08-15 13:00 | 2022-08-15 14:00 | Summer | FALSE | summer
2022-08-15 14:00 | 2022-08-15 15:00 | Summer | FALSE | summer
2022-08-15 15:00 | 2022-08-15 16:00 | Summer | FALSE | summer
2022-08-15 16:00 | 2022-08-15 17:00 | Summer | TRUE | summer
2022-08-15 17:00 | 2022-08-15 18:00 | Summer | TRUE | summer
2022-08-15 18:00 | 2022-08-15 19:00 | Summer | TRUE | summer
2022-08-15 19:00 | 2022-08-15 20:00 | Summer | TRUE | summer
2022-08-15 20:00 | 2022-08-15 21:00 | Summer | TRUE | summer
2022-08-15 21:00 | 2022-08-15 22:00 | Summer | FALSE | summer
2022-08-15 22:00 | 2022-08-15 23:00 | Summer | FALSE | summer
2022-08-15 23:00 | 2022-08-16 | Summer | FALSE | summer
2022-08-16 | 2022-08-16 01:00 | Summer | FALSE | summer
2022-08-16 01:00 | 2022-08-16 02:00 | Summer | FALSE | summer
2022-08-16 02:00 | 2022-08-16 03:00 | Summer | FALSE | summer
2022-08-16 03:00 | 2022-08-16 04:00 | Summer | FALSE | summer
2022-08-16 04:00 | 2022-08-16 05:00 | Summer | FALSE | summer
2022-08-16 05:00 | 2022-08-16 06:00 | Summer | FALSE | summer
2022-08-16 06:00 | 2022-08-16 07:00 | Summer | FALSE | summer
2022-08-16 07:00 | 2022-08-16 08:00 | Summer | FALSE | summer
2022-08-16 08:00 | 2022-08-16 09:00 | Summer | FALSE | summer
2022-08-16 09:00 | 2022-08-16 10:00 | Summer | FALSE | summer
2022-08-16 10:00 | 2022-08-16 11:00 | Summer | FALSE | summer
2022-08-16 11:00 | 2022-08-16 12:00 | Summer | FALSE | summer
2022-08-16 12:00 | 2022-08-16 13:00 | Summer | FALSE | summer
2022-08-16 13:00 | 2022-08-16 14:00 | Summer | FALSE | summer
2022-08-16 14:00 | 2022-08-16 15:00 | Summer | FALSE | summer
2022-08-16 15:00 | 2022-08-16 16:00 | Summer | FALSE | summer
2022-08-16 16:00 | 2022-08-16 17:00 | Summer | TRUE | summer
2022-08-16 17:00 | 2022-08-16 18:00 | Summer | TRUE | summer
2022-08-16 18:00 | 2022-08-16 19:00 | Summer | TRUE | summer
2022-08-16 19:00 | 2022-08-16 20:00 | Summer | TRUE | summer
2022-08-16 20:00 | 2022-08-16 21:00 | Summer | TRUE | summer
2022-08-16 21:00 | 2022-08-16 22:00 | Summer | FALSE | summer
2022-08-16 22:00 | 2022-08-16 23:00 | Summer | FALSE | summer
2022-08-16 23:00 | 2022-08-17 | Summer | FALSE | summer
2022-08-17 | 2022-08-17 01:00 | Summer | FALSE | summer
2022-08-17 01:00 | 2022-08-17 02:00 | Summer | FALSE | summer
2022-08-17 02:00 | 2022-08-17 03:00 | Summer | FALSE | summer
2022-08-17 03:00 | 2022-08-17 04:00 | Summer | FALSE | summer
2022-08-17 04:00 | 2022-08-17 05:00 | Summer | FALSE | summer
2022-08-17 05:00 | 2022-08-17 06:00 | Summer | FALSE | summer
2022-08-17 06:00 | 2022-08-17 07:00 | Summer | FALSE | summer
2022-08-17 07:00 | 2022-08-17 08:00 | Summer | FALSE | summer
2022-08-17 08:00 | 2022-08-17 09:00 | Summer | FALSE | summer
2022-08-17 09:00 | 2022-08-17 10:00 | Summer | FALSE | summer
2022-08-17 10:00 | 2022-08-17 11:00 | Summer | FALSE | summer
2022-08-17 11:00 | 2022-08-17 12:00 | Summer | FALSE | summer
2022-08-17 12:00 | 2022-08-17 13:00 | Summer | FALSE | summer
2022-08-17 13:00 | 2022-08-17 14:00 | Summer | FALSE | summer
2022-08-17 14:00 | 2022-08-17 15:00 | Summer | FALSE | summer
2022-08-17 15:00 | 2022-08-17 16:00 | Summer | FALSE | summer
2022-08-17 16:00 | 2022-08-17 17:00 | Summer | TRUE | summer
2022-08-17 17:00 | 2022-08-17 18:00 | Summer | TRUE | summer
2022-08-17 18:00 | 2022-08-17 19:00 | Summer | TRUE | summer
2022-08-17 19:00 | 2022-08-17 20:00 | Summer | TRUE | summer
2022-08-17 20:00 | 2022-08-17 21:00 | Summer | TRUE | summer
2022-08-17 21:00 | 2022-08-17 22:00 | Summer | FALSE | summer
2022-08-17 22:00 | 2022-08-17 23:00 | Summer | FALSE | summer
2022-08-17 23:00 | 2022-08-18 | Summer | FALSE | summer
2022-08-18 | 2022-08-18 01:00 | Summer | FALSE | summer
2022-08-18 01:00 | 2022-08-18 02:00 | Summer | FALSE | summer
2022-08-18 02:00 | 2022-08-18 03:00 | Summer | FALSE | summer
2022-08-18 03:00 | 2022-08-18 04:00 | Summer | FALSE | summer
2022-08-18 04:00 | 2022-08-18 05:00 | Summer | FALSE | summer
2022-08-18 05:00 | 2022-08-18 06:00 | Summer | FALSE | summer
2022-08-18 06:00 | 2022-08-18 07:00 | Summer | FALSE | summer
2022-08-18 07:00 | 2022-08-18 08:00 | Summer | FALSE | summer
2022-08-18 08:00 | 2022-08-18 09:00 | Summer | FALSE | summer
2022-08-18 09:00 | 2022-08-18 10:00 | Summer | FALSE | summer
2022-08-18 10:00 | 2022-08-18 11:00 | Summer | FALSE | summer
2022-08-18 11:00 | 2022-08-18 12:00 | Summer | FALSE | summer
2022-08-18 12:00 | 2022-08-18 13:00 | Summer | FALSE | summer
2022-08-18 13:00 | 2022-08-18 14:00 | Summer | FALSE | summer
2022-08-18 14:00 | 2022-08-18 15:00 | Summer | FALSE | summer
2022-08-18 15:00 | 2022-08-18 16:00 | Summer | FALSE | summer
2022-08-18 16:00 | 2022-08-18 17:00 | Summer | TRUE | summer
2022-08-18 17:00 | 2022-08-18 18:00 | Summer | TRUE | summer
2022-08-18 18:00 | 2022-08-18 19:00 | Summer | TRUE | summer
2022-08-18 19:00 | 2022-08-18 20:00 | Summer | TRUE | summer
2022-08-18 20:00 | 2022-08-18 21:00 | Summer | TRUE | summer
2022-08-18 21:00 | 2022-08-18 22:00 | Summer | FALSE | summer
2022-08-18 22:00 | 2022-08-18 23:00 | Summer | FALSE | summer
2022-08-18 23:00 | 2022-08-19 | Summer | FALSE | summer
2022-08-19 | 2022-08-19 01:00 | Summer | FALSE | summer
2022-08-19 01:00 | 2022-08-19 02:00 | Summer | FALSE | summer
2022-08-19 02:00 | 2022-08-19 03:00 | Summer | FALSE | summer
2022-08-19 03:00 | 2022-08-19 04:00 | Summer | FALSE | summer
2022-08-19 04:00 | 2022-08-19 05:00 | Summer | FALSE | summer
2022-08-19 05:00 | 2022-08-19 06:00 | Summer | FALSE | summer
2022-08-19 06:00 | 2022-08-19 07:00 | Summer | FALSE | summer
2022-08-19 07:00 | 2022-08-19 08:00 | Summer | FALSE | summer
2022-08-19 08:00 | 2022-08-19 09:00 | Summer | FALSE | summer
2022-08-19 09:00 | 2022-08-19 10:00 | Summer | FALSE | summer
2022-08-19 10:00 | 2022-08-19 11:00 | Summer | FALSE | summer
2022-08-19 11:00 | 2022-08-19 12:00 | Summer | FALSE | summer
2022-08-19 12:00 | 2022-08-19 13:00 | Summer | FALSE | summer
2022-08-19 13:00 | 2022-08-19 14:00 | Summer | FALSE | summer
2022-08-19 14:00 | 2022-08-19 15:00 | Summer | FALSE | summer
2022-08-19 15:00 | 2022-08-19 16:00 | Summer | FALSE | summer
2022-08-19 16:00 | 2022-08-19 17:00 | Summer | TRUE | summer
2022-08-19 17:00 | 2022-08-19 18:00 | Summer | TRUE | summer
2022-08-19 18:00 | 2022-08-19 19:00 | Summer | TRUE | summer
2022-08-19 19:00 | 2022-08-19 20:00 | Summer | TRUE | summer
2022-08-19 20:00 | 2022-08-19 21:00 | Summer | TRUE | summer
2022-08-19 21:00 | 2022-08-19 22:00 | Summer | FALSE | summer
2022-08-19 22:00 | 2022-08-19 23:00 | Summer | FALSE | summer
2022-08-19 23:00 | 2022-08-20 | Summer | FALSE | summer
2022-08-20 | 2022-08-20 01:00 | Summer | FALSE | summer
2022-08-20 01:00 | 2022-08-20 02:00 | Summer | FALSE | summer
2022-08-20 02:00 | 2022-08-20 03:00 | Summer | FALSE | summer
2022-08-20 03:00 | 2022-08-20 04:00 | Summer | FALSE | summer
2022-08-20 04:00 | 2022-08-20 05:00 | Summer | FALSE | summer
2022-08-20 05:00 | 2022-08-20 06:00 | Summer | FALSE | summer
2022-08-20 06:00 | 2022-08-20 07:00 | Summer | FALSE | summer
2022-08-20 07:00 | 2022-08-20 08:00 | Summer | FALSE | summer
2022-08-20 08:00 | 2022-08-20 09:00 | Summer | FALSE | summer
2022-08-20 09:00 | 2022-08-20 10:00 | Summer | FALSE | summer
2022-08-20 10:00 | 2022-08-20 11:00 | Summer | FALSE | summer
2022-08-20 11:00 | 2022-08-20 12:00 | Summer | FALSE | summer
2022-08-20 12:00 | 2022-08-20 13:00 | Summer | FALSE | summer
2022-08-20 13:00 | 2022-08-20 14:00 | Summer | FALSE | summer
2022-08-20 14:00 | 2022-08-20 15:00 | Summer | FALSE | summer
2022-08-20 15:00 | 2022-08-20 16:00 | Summer | FALSE | summer
2022-08-20 16:00 | 2022-08-20 17:00 | Summer | TRUE | summer
2022-08-20 17:00 | 2022-08-20 18:00 | Summer | TRUE | summer
2022-08-20 18:00 | 2022-08-20 19:00 | Summer | TRUE | summer
2022-08-20 19:00 | 2022-08-20 20:00 | Summer | TRUE | summer
2022-08-20 20:00 | 2022-08-20 21:00 | Summer | TRUE | summer
2022-08-20 21:00 | 2022-08-20 22:00 | Summer | FALSE | summer
2022-08-20 22:00 | 2022-08-20 23:00 | Summer | FALSE | summer
2022-08-20 23:00 | 2022-08-21 | Summer | FALSE | summer
2022-08-21 | 2022-08-21 01:00 | Summer | FALSE | summer
2022-08-21 01:00 | 2022-08-21 02:00 | Summer | FALSE | summer
2022-08-21 02:00 | 2022-08-21 03:00 | Summer | FALSE | summer
2022-08-21 03:00 | 2022-08-21 04:00 | Summer | FALSE | summer
2022-08-21 04:00 | 2022-08-21 05:00 | Summer | FALSE | summer
2022-08-21 05:00 | 2022-08-21 06:00 | Summer | FALSE | summer
2022-08-21 06:00 | 2022-08-21 07:00 | Summer | FALSE | summer
2022-08-21 07:00 | 2022-08-21 08:00 | Summer | FALSE | summer
2022-08-21 08:00 | 2022-08-21 09:00 | Summer | FALSE | summer
2022-08-21 09:00 | 2022-08-21 10:00 | Summer | FALSE | summer
2022-08-21 10:00 | 2022-08-21 11:00 | Summer | FALSE | summer
2022-08-21 11:00 | 2022-08-21 12:00 | Summer | FALSE | summer
2022-08-21 12:00 | 2022-08-21 13:00 | Summer | FALSE | summer
2022-08-21 13:00 | 2022-08-21 14:00 | Summer | FALSE | summer
2022-08-21 14:00 | 2022-08-21 15:00 | Summer | FALSE | summer
2022-08-21 15:00 | 2022-08-21 16:00 | Summer | FALSE | summer
2022-08-21 16:00 | 2022-08-21 17:00 | Summer | TRUE | summer
2022-08-21 17:00 | 2022-08-21 18:00 | Summer | TRUE | summer
2022-08-21 18:00 | 2022-08-21 19:00 | Summer | TRUE | summer
2022-08-21 19:00 | 2022-08-21 20:00 | Summer | TRUE | summer
2022-08-21 20:00 | 2022-08-21 21:00 | Summer | TRUE | summer
2022-08-21 21:00 | 2022-08-21 22:00 | Summer | FALSE | summer
2022-08-21 22:00 | 2022-08-21 23:00 | Summer | FALSE | summer
2022-08-21 23:00 | 2022-08-22 | Summer | FALSE | summer
2022-08-22 | 2022-08-22 01:00 | Summer | FALSE | summer
2022-08-22 01:00 | 2022-08-22 02:00 | Summer | FALSE | summer
2022-08-22 02:00 | 2022-08-22 03:00 | Summer | FALSE | summer
2022-08-22 03:00 | 2022-08-22 04:00 | Summer | FALSE | summer
2022-08-22 04:00 | 2022-08-22 05:00 | Summer | FALSE | summer
2022-08-22 05:00 | 2022-08-22 06:00 | Summer | FALSE | summer
2022-08-22 06:00 | 2022-08-22 07:00 | Summer | FALSE | summer
2022-08-22 07:00 | 2022-08-22 08:00 | Summer | FALSE | summer
2022-08-22 08:00 | 2022-08-22 09:00 | Summer | FALSE | summer
2022-08-22 09:00 | 2022-08-22 10:00 | Summer | FALSE | summer
2022-08-22 10:00 | 2022-08-22 11:00 | Summer | FALSE | summer
2022-08-22 11:00 | 2022-08-22 12:00 | Summer | FALSE | summer
2022-08-22 12:00 | 2022-08-22 13:00 | Summer | FALSE | summer
2022-08-22 13:00 | 2022-08-22 14:00 | Summer | FALSE | summer
2022-08-22 14:00 | 2022-08-22 15:00 | Summer | FALSE | summer
2022-08-22 15:00 | 2022-08-22 16:00 | Summer | FALSE | summer
2022-08-22 16:00 | 2022-08-22 17:00 | Summer | TRUE | summer
2022-08-22 17:00 | 2022-08-22 18:00 | Summer | TRUE | summer
2022-08-22 18:00 | 2022-08-22 19:00 | Summer | TRUE | summer
2022-08-22 19:00 | 2022-08-22 20:00 | Summer | TRUE | summer
2022-08-22 20:00 | 2022-08-22 21:00 | Summer | TRUE | summer
2022-08-22 21:00 | 2022-08-22 22:00 | Summer | FALSE | summer
2022-08-22 22:00 | 2022-08-22 23:00 | Summer | FALSE | summer
2022-08-22 23:00 | 2022-08-23 | Summer | FALSE | summer
2022-08-23 | 2022-08-23 01:00 | Summer | FALSE | summer
2022-08-23 01:00 | 2022-08-23 02:00 | Summer | FALSE | summer
2022-08-23 02:00 | 2022-08-23 03:00 | Summer | FALSE | summer
2022-08-23 03:00 | 2022-08-23 04:00 | Summer | FALSE | summer
2022-08-23 04:00 | 2022-08-23 05:00 | Summer | FALSE | summer
2022-08-23 05:00 | 2022-08-23 06:00 | Summer | FALSE | summer
2022-08-23 06:00 | 2022-08-23 07:00 | Summer | FALSE | summer
2022-08-23 07:00 | 2022-08-23 08:00 | Summer | FALSE | summer
2022-08-23 08:00 | 2022-08-23 09:00 | Summer | FALSE | summer
2022-08-23 09:00 | 2022-08-23 10:00 | Summer | FALSE | summer
2022-08-23 10:00 | 2022-08-23 11:00 | Summer | FALSE | summer
2022-08-23 11:00 | 2022-08-23 12:00 | Summer | FALSE | summer
2022-08-23 12:00 | 2022-08-23 13:00 | Summer | FALSE | summer
2022-08-23 13:00 | 2022-08-23 14:00 | Summer | FALSE | summer
2022-08-23 14:00 | 2022-08-23 15:00 | Summer | FALSE | summer
2022-08-23 15:00 | 2022-08-23 16:00 | Summer | FALSE | summer
2022-08-23 16:00 | 2022-08-23 17:00 | Summer | TRUE | summer
2022-08-23 17:00 | 2022-08-23 18:00 | Summer | TRUE | summer
2022-08-23 18:00 | 2022-08-23 19:00 | Summer | TRUE | summer
2022-08-23 19:00 | 2022-08-23 20:00 | Summer | TRUE | summer
2022-08-23 20:00 | 2022-08-23 21:00 | Summer | TRUE | summer
2022-08-23 21:00 | 2022-08-23 22:00 | Summer | FALSE | summer
2022-08-23 22:00 | 2022-08-23 23:00 | Summer | FALSE | summer
2022-08-23 23:00 | 2022-08-24 | Summer | FALSE | summer
2022-08-24 | 2022-08-24 01:00 | Summer | FALSE | summer
2022-08-24 01:00 | 2022-08-24 02:00 | Summer | FALSE | summer
2022-08-24 02:00 | 2022-08-24 03:00 | Summer | FALSE | summer
2022-08-24 03:00 | 2022-08-24 04:00 | Summer | FALSE | summer
2022-08-24 04:00 | 2022-08-24 05:00 | Summer | FALSE | summer
2022-08-24 05:00 | 2022-08-24 06:00 | Summer | FALSE | summer
2022-08-24 06:00 | 2022-08-24 07:00 | Summer | FALSE | summer
2022-08-24 07:00 | 2022-08-24 08:00 | Summer | FALSE | summer
2022-08-24 08:00 | 2022-08-24 09:00 | Summer | FALSE | summer
2022-08-24 09:00 | 2022-08-24 10:00 | Summer | FALSE | summer
2022-08-24 10:00 | 2022-08-24 11:00 | Summer | FALSE | summer
2022-08-24 11:00 | 2022-08-24 12:00 | Summer | FALSE | summer
2022-08-24 12:00 | 2022-08-24 13:00 | Summer | FALSE | summer
2022-08-24 13:00 | 2022-08-24 14:00 | Summer | FALSE | summer
2022-08-24 14:00 | 2022-08-24 15:00 | Summer | FALSE | summer
2022-08-24 15:00 | 2022-08-24 16:00 | Summer | FALSE | summer
2022-08-24 16:00 | 2022-08-24 17:00 | Summer | TRUE | summer
2022-08-24 17:00 | 2022-08-24 18:00 | Summer | TRUE | summer
2022-08-24 18:00 | 2022-08-24 19:00 | Summer | TRUE | summer
2022-08-24 19:00 | 2022-08-24 20:00 | Summer | TRUE | summer
2022-08-24 20:00 | 2022-08-24 21:00 | Summer | TRUE | summer
2022-08-24 21:00 | 2022-08-24 22:00 | Summer | FALSE | summer
2022-08-24 22:00 | 2022-08-24 23:00 | Summer | FALSE | summer
2022-08-24 23:00 | 2022-08-25 | Summer | FALSE | summer
2022-08-25 | 2022-08-25 01:00 | Summer | FALSE | summer
2022-08-25 01:00 | 2022-08-25 02:00 | Summer | FALSE | summer
2022-08-25 02:00 | 2022-08-25 03:00 | Summer | FALSE | summer
2022-08-25 03:00 | 2022-08-25 04:00 | Summer | FALSE | summer
2022-08-25 04:00 | 2022-08-25 05:00 | Summer | FALSE | summer
2022-08-25 05:00 | 2022-08-25 06:00 | Summer | FALSE | summer
2022-08-25 06:00 | 2022-08-25 07:00 | Summer | FALSE | summer
2022-08-25 07:00 | 2022-08-25 08:00 | Summer | FALSE | summer
2022-08-25 08:00 | 2022-08-25 09:00 | Summer | FALSE | summer
2022-08-25 09:00 | 2022-08-25 10:00 | Summer | FALSE | summer
2022-08-25 10:00 | 2022-08-25 11:00 | Summer | FALSE | summer
2022-08-25 11:00 | 2022-08-25 12:00 | Summer | FALSE | summer
2022-08-25 12:00 | 2022-08-25 13:00 | Summer | FALSE | summer
2022-08-25 13:00 | 2022-08-25 14:00 | Summer | FALSE | summer
2022-08-25 14:00 | 2022-08-25 15:00 | Summer | FALSE | summer
2022-08-25 15:00 | 2022-08-25 16:00 | Summer | FALSE | summer
2022-08-25 16:00 | 2022-08-25 17:00 | Summer | TRUE | summer
2022-08-25 17:00 | 2022-08-25 18:00 | Summer | TRUE | summer
2022-08-25 18:00 | 2022-08-25 19:00 | Summer | TRUE | summer
2022-08-25 19:00 | 2022-08-25 20:00 | Summer | TRUE | summer
2022-08-25 20:00 | 2022-08-25 21:00 | Summer | TRUE | summer
2022-08-25 21:00 | 2022-08-25 22:00 | Summer | FALSE | summer
2022-08-25 22:00 | 2022-08-25 23:00 | Summer | FALSE | summer
2022-08-25 23:00 | 2022-08-26 | Summer | FALSE | summer
2022-08-26 | 2022-08-26 01:00 | Summer | FALSE | summer
2022-08-26 01:00 | 2022-08-26 02:00 | Summer | FALSE | summer
2022-08-26 02:00 | 2022-08-26 03:00 | Summer | FALSE | summer
2022-08-26 03:00 | 2022-08-26 04:00 | Summer | FALSE | summer
2022-08-26 04:00 | 2022-08-26 05:00 | Summer | FALSE | summer
2022-08-26 05:00 | 2022-08-26 06:00 | Summer | FALSE | summer
2022-08-26 06:00 | 2022-08-26 07:00 | Summer | FALSE | summer
2022-08-26 07:00 | 2022-08-26 08:00 | Summer | FALSE | summer
2022-08-26 08:00 | 2022-08-26 09:00 | Summer | FALSE | summer
2022-08-26 09:00 | 2022-08-26 10:00 | Summer | FALSE | summer
2022-08-26 10:00 | 2022-08-26 11:00 | Summer | FALSE | summer
2022-08-26 11:00 | 2022-08-26 12:00 | Summer | FALSE | summer
2022-08-26 12:00 | 2022-08-26 13:00 | Summer | FALSE | summer
2022-08-26 13:00 | 2022-08-26 14:00 | Summer | FALSE | summer
2022-08-26 14:00 | 2022-08-26 15:00 | Summer | FALSE | summer
2022-08-26 15:00 | 2022-08-26 16:00 | Summer | FALSE | summer
2022-08-26 16:00 | 2022-08-26 17:00 | Summer | TRUE | summer
2022-08-26 17:00 | 2022-08-26 18:00 | Summer | TRUE | summer
2022-08-26 18:00 | 2022-08-26 19:00 | Summer | TRUE | summer
2022-08-26 19:00 | 2022-08-26 20:00 | Summer | TRUE | summer
2022-08-26 20:00 | 2022-08-26 21:00 | Summer | TRUE | summer
2022-08-26 21:00 | 2022-08-26 22:00 | Summer | FALSE | summer
2022-08-26 22:00 | 2022-08-26 23:00 | Summer | FALSE | summer
2022-08-26 23:00 | 2022-08-27 | Summer | FALSE | summer
2022-08-27 | 2022-08-27 01:00 | Summer | FALSE | summer
2022-08-27 01:00 | 2022-08-27 02:00 | Summer | FALSE | summer
2022-08-27 02:00 | 2022-08-27 03:00 | Summer | FALSE | summer
2022-08-27 03:00 | 2022-08-27 04:00 | Summer | FALSE | summer
2022-08-27 04:00 | 2022-08-27 05:00 | Summer | FALSE | summer
2022-08-27 05:00 | 2022-08-27 06:00 | Summer | FALSE | summer
2022-08-27 06:00 | 2022-08-27 07:00 | Summer | FALSE | summer
2022-08-27 07:00 | 2022-08-27 08:00 | Summer | FALSE | summer
2022-08-27 08:00 | 2022-08-27 09:00 | Summer | FALSE | summer
2022-08-27 09:00 | 2022-08-27 10:00 | Summer | FALSE | summer
2022-08-27 10:00 | 2022-08-27 11:00 | Summer | FALSE | summer
2022-08-27 11:00 | 2022-08-27 12:00 | Summer | FALSE | summer
2022-08-27 12:00 | 2022-08-27 13:00 | Summer | FALSE | summer
2022-08-27 13:00 | 2022-08-27 14:00 | Summer | FALSE | summer
2022-08-27 14:00 | 2022-08-27 15:00 | Summer | FALSE | summer
2022-08-27 15:00 | 2022-08-27 16:00 | Summer | FALSE | summer
2022-08-27 16:00 | 2022-08-27 17:00 | Summer | TRUE | summer
2022-08-27 17:00 | 2022-08-27 18:00 | Summer | TRUE | summer
2022-08-27 18:00 | 2022-08-27 19:00 | Summer | TRUE | summer
2022-08-27 19:00 | 2022-08-27 20:00 | Summer | TRUE | summer
2022-08-27 20:00 | 2022-08-27 21:00 | Summer | TRUE | summer
2022-08-27 21:00 | 2022-08-27 22:00 | Summer | FALSE | summer
2022-08-27 22:00 | 2022-08-27 23:00 | Summer | FALSE | summer
2022-08-27 23:00 | 2022-08-28 | Summer | FALSE | summer
2022-08-28 | 2022-08-28 01:00 | Summer | FALSE | summer
2022-08-28 01:00 | 2022-08-28 02:00 | Summer | FALSE | summer
2022-08-28 02:00 | 2022-08-28 03:00 | Summer | FALSE | summer
2022-08-28 03:00 | 2022-08-28 04:00 | Summer | FALSE | summer
2022-08-28 04:00 | 2022-08-28 05:00 | Summer | FALSE | summer
2022-08-28 05:00 | 2022-08-28 06:00 | Summer | FALSE | summer
2022-08-28 06:00 | 2022-08-28 07:00 | Summer | FALSE | summer
2022-08-28 07:00 | 2022-08-28 08:00 | Summer | FALSE | summer
2022-08-28 08:00 | 2022-08-28 09:00 | Summer | FALSE | summer
2022-08-28 09:00 | 2022-08-28 10:00 | Summer | FALSE | summer
2022-08-28 10:00 | 2022-08-28 11:00 | Summer | FALSE | summer
2022-08-28 11:00 | 2022-08-28 12:00 | Summer | FALSE | summer
2022-08-28 12:00 | 2022-08-28 13:00 | Summer | FALSE | summer
2022-08-28 13:00 | 2022-08-28 14:00 | Summer | FALSE | summer
2022-08-28 14:00 | 2022-08-28 15:00 | Summer | FALSE | summer
2022-08-28 15:00 | 2022-08-28 16:00 | Summer | FALSE | summer
2022-08-28 16:00 | 2022-08-28 17:00 | Summer | TRUE | summer
2022-08-28 17:00 | 2022-08-28 18:00 | Summer | TRUE | summer
2022-08-28 18:00 | 2022-08-28 19:00 | Summer | TRUE | summer
2022-08-28 19:00 | 2022-08-28 20:00 | Summer | TRUE | summer
2022-08-28 20:00 | 2022-08-28 21:00 | Summer | TRUE | summer
2022-08-28 21:00 | 2022-08-28 22:00 | Summer | FALSE | summer
2022-08-28 22:00 | 2022-08-28 23:00 | Summer | FALSE | summer
2022-08-28 23:00 | 2022-08-29 | Summer | FALSE | summer
2022-08-29 | 2022-08-29 01:00 | Summer | FALSE | summer
2022-08-29 01:00 | 2022-08-29 02:00 | Summer | FALSE | summer
2022-08-29 02:00 | 2022-08-29 03:00 | Summer | FALSE | summer
2022-08-29 03:00 | 2022-08-29 04:00 | Summer | FALSE | summer
2022-08-29 04:00 | 2022-08-29 05:00 | Summer | FALSE | summer
2022-08-29 05:00 | 2022-08-29 06:00 | Summer | FALSE | summer
2022-08-29 06:00 | 2022-08-29 07:00 | Summer | FALSE | summer
2022-08-29 07:00 | 2022-08-29 08:00 | Summer | FALSE | summer
2022-08-29 08:00 | 2022-08-29 09:00 | Summer | FALSE | summer
2022-08-29 09:00 | 2022-08-29 10:00 | Summer | FALSE | summer
2022-08-29 10:00 | 2022-08-29 11:00 | Summer | FALSE | summer
2022-08-29 11:00 | 2022-08-29 12:00 | Summer | FALSE | summer
2022-08-29 12:00 | 2022-08-29 13:00 | Summer | FALSE | summer
2022-08-29 13:00 | 2022-08-29 14:00 | Summer | FALSE | summer
2022-08-29 14:00 | 2022-08-29 15:00 | Summer | FALSE | summer
2022-08-29 15:00 | 2022-08-29 16:00 | Summer | FALSE | summer
2022-08-29 16:00 | 2022-08-29 17:00 | Summer | TRUE | summer
2022-08-29 17:00 | 2022-08-29 18:00 | Summer | TRUE | summer
2022-08-29 18:00 | 2022-08-29 19:00 | Summer | TRUE | summer
2022-08-29 19:00 | 2022-08-29 20:00 | Summer | TRUE | summer
2022-08-29 20:00 | 2022-08-29 21:00 | Summer | TRUE | summer
2022-08-29 21:00 | 2022-08-29 22:00 | Summer | FALSE | summer
2022-08-29 22:00 | 2022-08-29 23:00 | Summer | FALSE | summer
2022-08-29 23:00 | 2022-08-30 | Summer | FALSE | summer
2022-08-30 | 2022-08-30 01:00 | Summer | FALSE | summer
2022-08-30 01:00 | 2022-08-30 02:00 | Summer | FALSE | summer
2022-08-30 02:00 | 2022-08-30 03:00 | Summer | FALSE | summer
2022-08-30 03:00 | 2022-08-30 04:00 | Summer | FALSE | summer
2022-08-30 04:00 | 2022-08-30 05:00 | Summer | FALSE | summer
2022-08-30 05:00 | 2022-08-30 06:00 | Summer | FALSE | summer
2022-08-30 06:00 | 2022-08-30 07:00 | Summer | FALSE | summer
2022-08-30 07:00 | 2022-08-30 08:00 | Summer | FALSE | summer
2022-08-30 08:00 | 2022-08-30 09:00 | Summer | FALSE | summer
2022-08-30 09:00 | 2022-08-30 10:00 | Summer | FALSE | summer
2022-08-30 10:00 | 2022-08-30 11:00 | Summer | FALSE | summer
2022-08-30 11:00 | 2022-08-30 12:00 | Summer | FALSE | summer
2022-08-30 12:00 | 2022-08-30 13:00 | Summer | FALSE | summer
2022-08-30 13:00 | 2022-08-30 14:00 | Summer | FALSE | summer
2022-08-30 14:00 | 2022-08-30 15:00 | Summer | FALSE | summer
2022-08-30 15:00 | 2022-08-30 16:00 | Summer | FALSE | summer
2022-08-30 16:00 | 2022-08-30 17:00 | Summer | TRUE | summer
2022-08-30 17:00 | 2022-08-30 18:00 | Summer | TRUE | summer
2022-08-30 18:00 | 2022-08-30 19:00 | Summer | TRUE | summer
2022-08-30 19:00 | 2022-08-30 20:00 | Summer | TRUE | summer
2022-08-30 20:00 | 2022-08-30 21:00 | Summer | TRUE | summer
2022-08-30 21:00 | 2022-08-30 22:00 | Summer | FALSE | summer
2022-08-30 22:00 | 2022-08-30 23:00 | Summer | FALSE | summer
2022-08-30 23:00 | 2022-08-31 | Summer | FALSE | summer
2022-08-31 | 2022-08-31 01:00 | Summer | FALSE | summer
2022-08-31 01:00 | 2022-08-31 02:00 | Summer | FALSE | summer
2022-08-31 02:00 | 2022-08-31 03:00 | Summer | FALSE | summer
2022-08-31 03:00 | 2022-08-31 04:00 | Summer | FALSE | summer
2022-08-31 04:00 | 2022-08-31 05:00 | Summer | FALSE | summer
2022-08-31 05:00 | 2022-08-31 06:00 | Summer | FALSE | summer
2022-08-31 06:00 | 2022-08-31 07:00 | Summer | FALSE | summer
2022-08-31 07:00 | 2022-08-31 08:00 | Summer | FALSE | summer
2022-08-31 08:00 | 2022-08-31 09:00 | Summer | FALSE | summer
2022-08-31 09:00 | 2022-08-31 10:00 | Summer | FALSE | summer
2022-08-31 10:00 | 2022-08-31 11:00 | Summer | FALSE | summer
2022-08-31 11:00 | 2022-08-31 12:00 | Summer | FALSE | summer
2022-08-31 12:00 | 2022-08-31 13:00 | Summer | FALSE | summer
2022-08-31 13:00 | 2022-08-31 14:00 | Summer | FALSE | summer
2022-08-31 14:00 | 2022-08-31 15:00 | Summer | FALSE | summer
2022-08-31 15:00 | 2022-08-31 16:00 | Summer | FALSE | summer
2022-08-31 16:00 | 2022-08-31 17:00 | Summer | TRUE | summer
2022-08-31 17:00 | 2022-08-31 18:00 | Summer | TRUE | summer
2022-08-31 18:00 | 2022-08-31 19:00 | Summer | TRUE | summer
2022-08-31 19:00 | 2022-08-31 20:00 | Summer | TRUE | summer
2022-08-31 20:00 | 2022-08-31 21:00 | Summer | TRUE | summer
2022-08-31 21:00 | 2022-08-31 22:00 | Summer | FALSE | summer
2022-08-31 22:00 | 2022-08-31 23:00 | Summer | FALSE | summer
2022-08-31 23:00 | 2022-09-01 | Summer | FALSE | summer
2022-09-01 | 2022-09-01 01:00 | Summer | FALSE | summer
2022-09-01 01:00 | 2022-09-01 02:00 | Summer | FALSE | summer
2022-09-01 02:00 | 2022-09-01 03:00 | Summer | FALSE | summer
2022-09-01 03:00 | 2022-09-01 04:00 | Summer | FALSE | summer
2022-09-01 04:00 | 2022-09-01 05:00 | Summer | FALSE | summer
2022-09-01 05:00 | 2022-09-01 06:00 | Summer | FALSE | summer
2022-09-01 06:00 | 2022-09-01 07:00 | Summer | FALSE | summer
2022-09-01 07:00 | 2022-09-01 08:00 | Summer | FALSE | summer
2022-09-01 08:00 | 2022-09-01 09:00 | Summer | FALSE | summer
2022-09-01 09:00 | 2022-09-01 10:00 | Summer | FALSE | summer
2022-09-01 10:00 | 2022-09-01 11:00 | Summer | FALSE | summer
2022-09-01 11:00 | 2022-09-01 12:00 | Summer | FALSE | summer
2022-09-01 12:00 | 2022-09-01 13:00 | Summer | FALSE | summer
2022-09-01 13:00 | 2022-09-01 14:00 | Summer | FALSE | summer
2022-09-01 14:00 | 2022-09-01 15:00 | Summer | FALSE | summer
2022-09-01 15:00 | 2022-09-01 16:00 | Summer | FALSE | summer
2022-09-01 16:00 | 2022-09-01 17:00 | Summer | TRUE | summer
2022-09-01 17:00 | 2022-09-01 18:00 | Summer | TRUE | summer
2022-09-01 18:00 | 2022-09-01 19:00 | Summer | TRUE | summer
2022-09-01 19:00 | 2022-09-01 20:00 | Summer | TRUE | summer
2022-09-01 20:00 | 2022-09-01 21:00 | Summer | TRUE | summer
2022-09-01 21:00 | 2022-09-01 22:00 | Summer | FALSE | summer
2022-09-01 22:00 | 2022-09-01 23:00 | Summer | FALSE | summer
2022-09-01 23:00 | 2022-09-02 | Summer | FALSE | summer
2022-09-02 | 2022-09-02 01:00 | Summer | FALSE | summer
2022-09-02 01:00 | 2022-09-02 02:00 | Summer | FALSE | summer
2022-09-02 02:00 | 2022-09-02 03:00 | Summer | FALSE | summer
2022-09-02 03:00 | 2022-09-02 04:00 | Summer | FALSE | summer
2022-09-02 04:00 | 2022-09-02 05:00 | Summer | FALSE | summer
2022-09-02 05:00 | 2022-09-02 06:00 | Summer | FALSE | summer
2022-09-02 06:00 | 2022-09-02 07:00 | Summer | FALSE | summer
2022-09-02 07:00 | 2022-09-02 08:00 | Summer | FALSE | summer
2022-09-02 08:00 | 2022-09-02 09:00 | Summer | FALSE | summer
2022-09-02 09:00 | 2022-09-02 10:00 | Summer | FALSE | summer
2022-09-02 10:00 | 2022-09-02 11:00 | Summer | FALSE | summer
2022-09-02 11:00 | 2022-09-02 12:00 | Summer | FALSE | summer
2022-09-02 12:00 | 2022-09-02 13:00 | Summer | FALSE | summer
2022-09-02 13:00 | 2022-09-02 14:00 | Summer | FALSE | summer
2022-09-02 14:00 | 2022-09-02 15:00 | Summer | FALSE | summer
2022-09-02 15:00 | 2022-09-02 16:00 | Summer | FALSE | summer
2022-09-02 16:00 | 2022-09-02 17:00 | Summer | TRUE | summer
2022-09-02 17:00 | 2022-09-02 18:00 | Summer | TRUE | summer
2022-09-02 18:00 | 2022-09-02 19:00 | Summer | TRUE | summer
2022-09-02 19:00 | 2022-09-02 20:00 | Summer | TRUE | summer
2022-09-02 20:00 | 2022-09-02 21:00 | Summer | TRUE | summer
2022-09-02 21:00 | 2022-09-02 22:00 | Summer | FALSE | summer
2022-09-02 22:00 | 2022-09-02 23:00 | Summer | FALSE | summer
2022-09-02 23:00 | 2022-09-03 | Summer | FALSE | summer
2022-09-03 | 2022-09-03 01:00 | Summer | FALSE | summer
2022-09-03 01:00 | 2022-09-03 02:00 | Summer | FALSE | summer
2022-09-03 02:00 | 2022-09-03 03:00 | Summer | FALSE | summer
2022-09-03 03:00 | 2022-09-03 04:00 | Summer | FALSE | summer
2022-09-03 04:00 | 2022-09-03 05:00 | Summer | FALSE | summer
2022-09-03 05:00 | 2022-09-03 06:00 | Summer | FALSE | summer
2022-09-03 06:00 | 2022-09-03 07:00 | Summer | FALSE | summer
2022-09-03 07:00 | 2022-09-03 08:00 | Summer | FALSE | summer
2022-09-03 08:00 | 2022-09-03 09:00 | Summer | FALSE | summer
2022-09-03 09:00 | 2022-09-03 10:00 | Summer | FALSE | summer
2022-09-03 10:00 | 2022-09-03 11:00 | Summer | FALSE | summer
2022-09-03 11:00 | 2022-09-03 12:00 | Summer | FALSE | summer
2022-09-03 12:00 | 2022-09-03 13:00 | Summer | FALSE | summer
2022-09-03 13:00 | 2022-09-03 14:00 | Summer | FALSE | summer
2022-09-03 14:00 | 2022-09-03 15:00 | Summer | FALSE | summer
2022-09-03 15:00 | 2022-09-03 16:00 | Summer | FALSE | summer
2022-09-03 16:00 | 2022-09-03 17:00 | Summer | TRUE | summer
2022-09-03 17:00 | 2022-09-03 18:00 | Summer | TRUE | summer
2022-09-03 18:00 | 2022-09-03 19:00 | Summer | TRUE | summer
2022-09-03 19:00 | 2022-09-03 20:00 | Summer | TRUE | summer
2022-09-03 20:00 | 2022-09-03 21:00 | Summer | TRUE | summer
2022-09-03 21:00 | 2022-09-03 22:00 | Summer | FALSE | summer
2022-09-03 22:00 | 2022-09-03 23:00 | Summer | FALSE | summer
2022-09-03 23:00 | 2022-09-04 | Summer | FALSE | summer
2022-09-04 | 2022-09-04 01:00 | Summer | FALSE | summer
2022-09-04 01:00 | 2022-09-04 02:00 | Summer | FALSE | summer
2022-09-04 02:00 | 2022-09-04 03:00 | Summer | FALSE | summer
2022-09-04 03:00 | 2022-09-04 04:00 | Summer | FALSE | summer
2022-09-04 04:00 | 2022-09-04 05:00 | Summer | FALSE | summer
2022-09-04 05:00 | 2022-09-04 06:00 | Summer | FALSE | summer
2022-09-04 06:00 | 2022-09-04 07:00 | Summer | FALSE | summer
2022-09-04 07:00 | 2022-09-04 08:00 | Summer | FALSE | summer
2022-09-04 08:00 | 2022-09-04 09:00 | Summer | FALSE | summer
2022-09-04 09:00 | 2022-09-04 10:00 | Summer | FALSE | summer
2022-09-04 10:00 | 2022-09-04 11:00 | Summer | FALSE | summer
2022-09-04 11:00 | 2022-09-04 12:00 | Summer | FALSE | summer
2022-09-04 12:00 | 2022-09-04 13:00 | Summer | FALSE | summer
2022-09-04 13:00 | 2022-09-04 14:00 | Summer | FALSE | summer
2022-09-04 14:00 | 2022-09-04 15:00 | Summer | FALSE | summer
2022-09-04 15:00 | 2022-09-04 16:00 | Summer | FALSE | summer
2022-09-04 16:00 | 2022-09-04 17:00 | Summer | TRUE | summer
2022-09-04 17:00 | 2022-09-04 18:00 | Summer | TRUE | summer
2022-09-04 18:00 | 2022-09-04 19:00 | Summer | TRUE | summer
2022-09-04 19:00 | 2022-09-04 20:00 | Summer | TRUE | summer
2022-09-04 20:00 | 2022-09-04 21:00 | Summer | TRUE | summer
2022-09-04 21:00 | 2022-09-04 22:00 | Summer | FALSE | summer
2022-09-04 22:00 | 2022-09-04 23:00 | Summer | FALSE | summer
2022-09-04 23:00 | 2022-09-05 | Summer | FALSE | summer
2022-09-05 | 2022-09-05 01:00 | Summer | FALSE | summer
2022-09-05 01:00 | 2022-09-05 02:00 | Summer | FALSE | summer
2022-09-05 02:00 | 2022-09-05 03:00 | Summer | FALSE | summer
2022-09-05 03:00 | 2022-09-05 04:00 | Summer | FALSE | summer
2022-09-05 04:00 | 2022-09-05 05:00 | Summer | FALSE | summer
2022-09-05 05:00 | 2022-09-05 06:00 | Summer | FALSE | summer
2022-09-05 06:00 | 2022-09-05 07:00 | Summer | FALSE | summer
2022-09-05 07:00 | 2022-09-05 08:00 | Summer | FALSE | summer
2022-09-05 08:00 | 2022-09-05 09:00 | Summer | FALSE | summer
2022-09-05 09:00 | 2022-09-05 10:00 | Summer | FALSE | summer
2022-09-05 10:00 | 2022-09-05 11:00 | Summer | FALSE | summer
2022-09-05 11:00 | 2022-09-05 12:00 | Summer | FALSE | summer
2022-09-05 12:00 | 2022-09-05 13:00 | Summer | FALSE | summer
2022-09-05 13:00 | 2022-09-05 14:00 | Summer | FALSE | summer
2022-09-05 14:00 | 2022-09-05 15:00 | Summer | FALSE | summer
2022-09-05 15:00 | 2022-09-05 16:00 | Summer | FALSE | summer
2022-09-05 16:00 | 2022-09-05 17:00 | Summer | TRUE | summer
2022-09-05 17:00 | 2022-09-05 18:00 | Summer | TRUE | summer
2022-09-05 18:00 | 2022-09-05 19:00 | Summer | TRUE | summer
2022-09-05 19:00 | 2022-09-05 20:00 | Summer | TRUE | summer
2022-09-05 20:00 | 2022-09-05 21:00 | Summer | TRUE | summer
2022-09-05 21:00 | 2022-09-05 22:00 | Summer | FALSE | summer
2022-09-05 22:00 | 2022-09-05 23:00 | Summer | FALSE | summer
2022-09-05 23:00 | 2022-09-06 | Summer | FALSE | summer
2022-09-06 | 2022-09-06 01:00 | Summer | FALSE | summer
2022-09-06 01:00 | 2022-09-06 02:00 | Summer | FALSE | summer
2022-09-06 02:00 | 2022-09-06 03:00 | Summer | FALSE | summer
2022-09-06 03:00 | 2022-09-06 04:00 | Summer | FALSE | summer
2022-09-06 04:00 | 2022-09-06 05:00 | Summer | FALSE | summer
2022-09-06 05:00 | 2022-09-06 06:00 | Summer | FALSE | summer
2022-09-06 06:00 | 2022-09-06 07:00 | Summer | FALSE | summer
2022-09-06 07:00 | 2022-09-06 08:00 | Summer | FALSE | summer
2022-09-06 08:00 | 2022-09-06 09:00 | Summer | FALSE | summer
2022-09-06 09:00 | 2022-09-06 10:00 | Summer | FALSE | summer
2022-09-06 10:00 | 2022-09-06 11:00 | Summer | FALSE | summer
2022-09-06 11:00 | 2022-09-06 12:00 | Summer | FALSE | summer
2022-09-06 12:00 | 2022-09-06 13:00 | Summer | FALSE | summer
2022-09-06 13:00 | 2022-09-06 14:00 | Summer | FALSE | summer
2022-09-06 14:00 | 2022-09-06 15:00 | Summer | FALSE | summer
2022-09-06 15:00 | 2022-09-06 16:00 | Summer | FALSE | summer
2022-09-06 16:00 | 2022-09-06 17:00 | Summer | TRUE | summer
2022-09-06 17:00 | 2022-09-06 18:00 | Summer | TRUE | summer
2022-09-06 18:00 | 2022-09-06 19:00 | Summer | TRUE | summer
2022-09-06 19:00 | 2022-09-06 20:00 | Summer | TRUE | summer
2022-09-06 20:00 | 2022-09-06 21:00 | Summer | TRUE | summer
2022-09-06 21:00 | 2022-09-06 22:00 | Summer | FALSE | summer
2022-09-06 22:00 | 2022-09-06 23:00 | Summer | FALSE | summer
2022-09-06 23:00 | 2022-09-07 | Summer | FALSE | summer
2022-09-07 | 2022-09-07 01:00 | Summer | FALSE | summer
2022-09-07 01:00 | 2022-09-07 02:00 | Summer | FALSE | summer
2022-09-07 02:00 | 2022-09-07 03:00 | Summer | FALSE | summer
2022-09-07 03:00 | 2022-09-07 04:00 | Summer | FALSE | summer
2022-09-07 04:00 | 2022-09-07 05:00 | Summer | FALSE | summer
2022-09-07 05:00 | 2022-09-07 06:00 | Summer | FALSE | summer
2022-09-07 06:00 | 2022-09-07 07:00 | Summer | FALSE | summer
2022-09-07 07:00 | 2022-09-07 08:00 | Summer | FALSE | summer
2022-09-07 08:00 | 2022-09-07 09:00 | Summer | FALSE | summer
2022-09-07 09:00 | 2022-09-07 10:00 | Summer | FALSE | summer
2022-09-07 10:00 | 2022-09-07 11:00 | Summer | FALSE | summer
2022-09-07 11:00 | 2022-09-07 12:00 | Summer | FALSE | summer
2022-09-07 12:00 | 2022-09-07 13:00 | Summer | FALSE | summer
2022-09-07 13:00 | 2022-09-07 14:00 | Summer | FALSE | summer
2022-09-07 14:00 | 2022-09-07 15:00 | Summer | FALSE | summer
2022-09-07 15:00 | 2022-09-07 16:00 | Summer | FALSE | summer
2022-09-07 16:00 | 2022-09-07 17:00 | Summer | TRUE | summer
2022-09-07 17:00 | 2022-09-07 18:00 | Summer | TRUE | summer
2022-09-07 18:00 | 2022-09-07 19:00 | Summer | TRUE | summer
2022-09-07 19:00 | 2022-09-07 20:00 | Summer | TRUE | summer
2022-09-07 20:00 | 2022-09-07 21:00 | Summer | TRUE | summer
2022-09-07 21:00 | 2022-09-07 22:00 | Summer | FALSE | summer
2022-09-07 22:00 | 2022-09-07 23:00 | Summer | FALSE | summer
2022-09-07 23:00 | 2022-09-08 | Summer | FALSE | summer
2022-09-08 | 2022-09-08 01:00 | Summer | FALSE | summer
2022-09-08 01:00 | 2022-09-08 02:00 | Summer | FALSE | summer
2022-09-08 02:00 | 2022-09-08 03:00 | Summer | FALSE | summer
2022-09-08 03:00 | 2022-09-08 04:00 | Summer | FALSE | summer
2022-09-08 04:00 | 2022-09-08 05:00 | Summer | FALSE | summer
2022-09-08 05:00 | 2022-09-08 06:00 | Summer | FALSE | summer
2022-09-08 06:00 | 2022-09-08 07:00 | Summer | FALSE | summer
2022-09-08 07:00 | 2022-09-08 08:00 | Summer | FALSE | summer
2022-09-08 08:00 | 2022-09-08 09:00 | Summer | FALSE | summer
2022-09-08 09:00 | 2022-09-08 10:00 | Summer | FALSE | summer
2022-09-08 10:00 | 2022-09-08 11:00 | Summer | FALSE | summer
2022-09-08 11:00 | 2022-09-08 12:00 | Summer | FALSE | summer
2022-09-08 12:00 | 2022-09-08 13:00 | Summer | FALSE | summer
2022-09-08 13:00 | 2022-09-08 14:00 | Summer | FALSE | summer
2022-09-08 14:00 | 2022-09-08 15:00 | Summer | FALSE | summer
2022-09-08 15:00 | 2022-09-08 16:00 | Summer | FALSE | summer
2022-09-08 16:00 | 2022-09-08 17:00 | Summer | TRUE | summer
2022-09-08 17:00 | 2022-09-08 18:00 | Summer | TRUE | summer
2022-09-08 18:00 | 2022-09-08 19:00 | Summer | TRUE | summer
2022-09-08 19:00 | 2022-09-08 20:00 | Summer | TRUE | summer
2022-09-08 20:00 | 2022-09-08 21:00 | Summer | TRUE | summer
2022-09-08 21:00 | 2022-09-08 22:00 | Summer | FALSE | summer
2022-09-08 22:00 | 2022-09-08 23:00 | Summer | FALSE | summer
2022-09-08 23:00 | 2022-09-09 | Summer | FALSE | summer
2022-09-09 | 2022-09-09 01:00 | Summer | FALSE | summer
2022-09-09 01:00 | 2022-09-09 02:00 | Summer | FALSE | summer
2022-09-09 02:00 | 2022-09-09 03:00 | Summer | FALSE | summer
2022-09-09 03:00 | 2022-09-09 04:00 | Summer | FALSE | summer
2022-09-09 04:00 | 2022-09-09 05:00 | Summer | FALSE | summer
2022-09-09 05:00 | 2022-09-09 06:00 | Summer | FALSE | summer
2022-09-09 06:00 | 2022-09-09 07:00 | Summer | FALSE | summer
2022-09-09 07:00 | 2022-09-09 08:00 | Summer | FALSE | summer
2022-09-09 08:00 | 2022-09-09 09:00 | Summer | FALSE | summer
2022-09-09 09:00 | 2022-09-09 10:00 | Summer | FALSE | summer
2022-09-09 10:00 | 2022-09-09 11:00 | Summer | FALSE | summer
2022-09-09 11:00 | 2022-09-09 12:00 | Summer | FALSE | summer
2022-09-09 12:00 | 2022-09-09 13:00 | Summer | FALSE | summer
2022-09-09 13:00 | 2022-09-09 14:00 | Summer | FALSE | summer
2022-09-09 14:00 | 2022-09-09 15:00 | Summer | FALSE | summer
2022-09-09 15:00 | 2022-09-09 16:00 | Summer | FALSE | summer
2022-09-09 16:00 | 2022-09-09 17:00 | Summer | TRUE | summer
2022-09-09 17:00 | 2022-09-09 18:00 | Summer | TRUE | summer
2022-09-09 18:00 | 2022-09-09 19:00 | Summer | TRUE | summer
2022-09-09 19:00 | 2022-09-09 20:00 | Summer | TRUE | summer
2022-09-09 20:00 | 2022-09-09 21:00 | Summer | TRUE | summer
2022-09-09 21:00 | 2022-09-09 22:00 | Summer | FALSE | summer
2022-09-09 22:00 | 2022-09-09 23:00 | Summer | FALSE | summer
2022-09-09 23:00 | 2022-09-10 | Summer | FALSE | summer
2022-09-10 | 2022-09-10 01:00 | Summer | FALSE | summer
2022-09-10 01:00 | 2022-09-10 02:00 | Summer | FALSE | summer
2022-09-10 02:00 | 2022-09-10 03:00 | Summer | FALSE | summer
2022-09-10 03:00 | 2022-09-10 04:00 | Summer | FALSE | summer
2022-09-10 04:00 | 2022-09-10 05:00 | Summer | FALSE | summer
2022-09-10 05:00 | 2022-09-10 06:00 | Summer | FALSE | summer
2022-09-10 06:00 | 2022-09-10 07:00 | Summer | FALSE | summer
2022-09-10 07:00 | 2022-09-10 08:00 | Summer | FALSE | summer
2022-09-10 08:00 | 2022-09-10 09:00 | Summer | FALSE | summer
2022-09-10 09:00 | 2022-09-10 10:00 | Summer | FALSE | summer
2022-09-10 10:00 | 2022-09-10 11:00 | Summer | FALSE | summer
2022-09-10 11:00 | 2022-09-10 12:00 | Summer | FALSE | summer
2022-09-10 12:00 | 2022-09-10 13:00 | Summer | FALSE | summer
2022-09-10 13:00 | 2022-09-10 14:00 | Summer | FALSE | summer
2022-09-10 14:00 | 2022-09-10 15:00 | Summer | FALSE | summer
2022-09-10 15:00 | 2022-09-10 16:00 | Summer | FALSE | summer
2022-09-10 16:00 | 2022-09-10 17:00 | Summer | TRUE | summer
2022-09-10 17:00 | 2022-09-10 18:00 | Summer | TRUE | summer
2022-09-10 18:00 | 2022-09-10 19:00 | Summer | TRUE | summer
2022-09-10 19:00 | 2022-09-10 20:00 | Summer | TRUE | summer
2022-09-10 20:00 | 2022-09-10 21:00 | Summer | TRUE | summer
2022-09-10 21:00 | 2022-09-10 22:00 | Summer | FALSE | summer
2022-09-10 22:00 | 2022-09-10 23:00 | Summer | FALSE | summer
2022-09-10 23:00 | 2022-09-11 | Summer | FALSE | summer
2022-09-11 | 2022-09-11 01:00 | Summer | FALSE | summer
2022-09-11 01:00 | 2022-09-11 02:00 | Summer | FALSE | summer
2022-09-11 02:00 | 2022-09-11 03:00 | Summer | FALSE | summer
2022-09-11 03:00 | 2022-09-11 04:00 | Summer | FALSE | summer
2022-09-11 04:00 | 2022-09-11 05:00 | Summer | FALSE | summer
2022-09-11 05:00 | 2022-09-11 06:00 | Summer | FALSE | summer
2022-09-11 06:00 | 2022-09-11 07:00 | Summer | FALSE | summer
2022-09-11 07:00 | 2022-09-11 08:00 | Summer | FALSE | summer
2022-09-11 08:00 | 2022-09-11 09:00 | Summer | FALSE | summer
2022-09-11 09:00 | 2022-09-11 10:00 | Summer | FALSE | summer
2022-09-11 10:00 | 2022-09-11 11:00 | Summer | FALSE | summer
2022-09-11 11:00 | 2022-09-11 12:00 | Summer | FALSE | summer
2022-09-11 12:00 | 2022-09-11 13:00 | Summer | FALSE | summer
2022-09-11 13:00 | 2022-09-11 14:00 | Summer | FALSE | summer
2022-09-11 14:00 | 2022-09-11 15:00 | Summer | FALSE | summer
2022-09-11 15:00 | 2022-09-11 16:00 | Summer | FALSE | summer
2022-09-11 16:00 | 2022-09-11 17:00 | Summer | TRUE | summer
2022-09-11 17:00 | 2022-09-11 18:00 | Summer | TRUE | summer
2022-09-11 18:00 | 2022-09-11 19:00 | Summer | TRUE | summer
2022-09-11 19:00 | 2022-09-11 20:00 | Summer | TRUE | summer
2022-09-11 20:00 | 2022-09-11 21:00 | Summer | TRUE | summer
2022-09-11 21:00 | 2022-09-11 22:00 | Summer | FALSE | summer
2022-09-11 22:00 | 2022-09-11 23:00 | Summer | FALSE | summer
2022-09-11 23:00 | 2022-09-12 | Summer | FALSE | summer
2022-09-12 | 2022-09-12 01:00 | Summer | FALSE | summer
2022-09-12 01:00 | 2022-09-12 02:00 | Summer | FALSE | summer
2022-09-12 02:00 | 2022-09-12 03:00 | Summer | FALSE | summer
2022-09-12 03:00 | 2022-09-12 04:00 | Summer | FALSE | summer
2022-09-12 04:00 | 2022-09-12 05:00 | Summer | FALSE | summer
2022-09-12 05:00 | 2022-09-12 06:00 | Summer | FALSE | summer
2022-09-12 06:00 | 2022-09-12 07:00 | Summer | FALSE | summer
2022-09-12 07:00 | 2022-09-12 08:00 | Summer | FALSE | summer
2022-09-12 08:00 | 2022-09-12 09:00 | Summer | FALSE | summer
2022-09-12 09:00 | 2022-09-12 10:00 | Summer | FALSE | summer
2022-09-12 10:00 | 2022-09-12 11:00 | Summer | FALSE | summer
2022-09-12 11:00 | 2022-09-12 12:00 | Summer | FALSE | summer
2022-09-12 12:00 | 2022-09-12 13:00 | Summer | FALSE | summer
2022-09-12 13:00 | 2022-09-12 14:00 | Summer | FALSE | summer
2022-09-12 14:00 | 2022-09-12 15:00 | Summer | FALSE | summer
2022-09-12 15:00 | 2022-09-12 16:00 | Summer | FALSE | summer
2022-09-12 16:00 | 2022-09-12 17:00 | Summer | TRUE | summer
2022-09-12 17:00 | 2022-09-12 18:00 | Summer | TRUE | summer
2022-09-12 18:00 | 2022-09-12 19:00 | Summer | TRUE | summer
2022-09-12 19:00 | 2022-09-12 20:00 | Summer | TRUE | summer
2022-09-12 20:00 | 2022-09-12 21:00 | Summer | TRUE | summer
2022-09-12 21:00 | 2022-09-12 22:00 | Summer | FALSE | summer
2022-09-12 22:00 | 2022-09-12 23:00 | Summer | FALSE | summer
2022-09-12 23:00 | 2022-09-13 | Summer | FALSE | summer
2022-09-13 | 2022-09-13 01:00 | Summer | FALSE | summer
2022-09-13 01:00 | 2022-09-13 02:00 | Summer | FALSE | summer
2022-09-13 02:00 | 2022-09-13 03:00 | Summer | FALSE | summer
2022-09-13 03:00 | 2022-09-13 04:00 | Summer | FALSE | summer
2022-09-13 04:00 | 2022-09-13 05:00 | Summer | FALSE | summer
2022-09-13 05:00 | 2022-09-13 06:00 | Summer | FALSE | summer
2022-09-13 06:00 | 2022-09-13 07:00 | Summer | FALSE | summer
2022-09-13 07:00 | 2022-09-13 08:00 | Summer | FALSE | summer
2022-09-13 08:00 | 2022-09-13 09:00 | Summer | FALSE | summer
2022-09-13 09:00 | 2022-09-13 10:00 | Summer | FALSE | summer
2022-09-13 10:00 | 2022-09-13 11:00 | Summer | FALSE | summer
2022-09-13 11:00 | 2022-09-13 12:00 | Summer | FALSE | summer
2022-09-13 12:00 | 2022-09-13 13:00 | Summer | FALSE | summer
2022-09-13 13:00 | 2022-09-13 14:00 | Summer | FALSE | summer
2022-09-13 14:00 | 2022-09-13 15:00 | Summer | FALSE | summer
2022-09-13 15:00 | 2022-09-13 16:00 | Summer | FALSE | summer
2022-09-13 16:00 | 2022-09-13 17:00 | Summer | TRUE | summer
2022-09-13 17:00 | 2022-09-13 18:00 | Summer | TRUE | summer
2022-09-13 18:00 | 2022-09-13 19:00 | Summer | TRUE | summer
2022-09-13 19:00 | 2022-09-13 20:00 | Summer | TRUE | summer
2022-09-13 20:00 | 2022-09-13 21:00 | Summer | TRUE | summer
2022-09-13 21:00 | 2022-09-13 22:00 | Summer | FALSE | summer
2022-09-13 22:00 | 2022-09-13 23:00 | Summer | FALSE | summer
2022-09-13 23:00 | 2022-09-14 | Summer | FALSE | summer
2022-09-14 | 2022-09-14 01:00 | Summer | FALSE | summer
2022-09-14 01:00 | 2022-09-14 02:00 | Summer | FALSE | summer
2022-09-14 02:00 | 2022-09-14 03:00 | Summer | FALSE | summer
2022-09-14 03:00 | 2022-09-14 04:00 | Summer | FALSE | summer
2022-09-14 04:00 | 2022-09-14 05:00 | Summer | FALSE | summer
2022-09-14 05:00 | 2022-09-14 06:00 | Summer | FALSE | summer
2022-09-14 06:00 | 2022-09-14 07:00 | Summer | FALSE | summer
2022-09-14 07:00 | 2022-09-14 08:00 | Summer | FALSE | summer
2022-09-14 08:00 | 2022-09-14 09:00 | Summer | FALSE | summer
2022-09-14 09:00 | 2022-09-14 10:00 | Summer | FALSE | summer
2022-09-14 10:00 | 2022-09-14 11:00 | Summer | FALSE | summer
2022-09-14 11:00 | 2022-09-14 12:00 | Summer | FALSE | summer
2022-09-14 12:00 | 2022-09-14 13:00 | Summer | FALSE | summer
2022-09-14 13:00 | 2022-09-14 14:00 | Summer | FALSE | summer
2022-09-14 14:00 | 2022-09-14 15:00 | Summer | FALSE | summer
2022-09-14 15:00 | 2022-09-14 16:00 | Summer | FALSE | summer
2022-09-14 16:00 | 2022-09-14 17:00 | Summer | TRUE | summer
2022-09-14 17:00 | 2022-09-14 18:00 | Summer | TRUE | summer
2022-09-14 18:00 | 2022-09-14 19:00 | Summer | TRUE | summer
2022-09-14 19:00 | 2022-09-14 20:00 | Summer | TRUE | summer
2022-09-14 20:00 | 2022-09-14 21:00 | Summer | TRUE | summer
2022-09-14 21:00 | 2022-09-14 22:00 | Summer | FALSE | summer
2022-09-14 22:00 | 2022-09-14 23:00 | Summer | FALSE | summer
2022-09-14 23:00 | 2022-09-15 | Summer | FALSE | summer
2022-09-15 | 2022-09-15 01:00 | Summer | FALSE | summer
2022-09-15 01:00 | 2022-09-15 02:00 | Summer | FALSE | summer
2022-09-15 02:00 | 2022-09-15 03:00 | Summer | FALSE | summer
2022-09-15 03:00 | 2022-09-15 04:00 | Summer | FALSE | summer
2022-09-15 04:00 | 2022-09-15 05:00 | Summer | FALSE | summer
2022-09-15 05:00 | 2022-09-15 06:00 | Summer | FALSE | summer
2022-09-15 06:00 | 2022-09-15 07:00 | Summer | FALSE | summer
2022-09-15 07:00 | 2022-09-15 08:00 | Summer | FALSE | summer
2022-09-15 08:00 | 2022-09-15 09:00 | Summer | FALSE | summer
2022-09-15 09:00 | 2022-09-15 10:00 | Summer | FALSE | summer
2022-09-15 10:00 | 2022-09-15 11:00 | Summer | FALSE | summer
2022-09-15 11:00 | 2022-09-15 12:00 | Summer | FALSE | summer
2022-09-15 12:00 | 2022-09-15 13:00 | Summer | FALSE | summer
2022-09-15 13:00 | 2022-09-15 14:00 | Summer | FALSE | summer
2022-09-15 14:00 | 2022-09-15 15:00 | Summer | FALSE | summer
2022-09-15 15:00 | 2022-09-15 16:00 | Summer | FALSE | summer
2022-09-15 16:00 | 2022-09-15 17:00 | Summer | TRUE | summer
2022-09-15 17:00 | 2022-09-15 18:00 | Summer | TRUE | summer
2022-09-15 18:00 | 2022-09-15 19:00 | Summer | TRUE | summer
2022-09-15 19:00 | 2022-09-15 20:00 | Summer | TRUE | summer
2022-09-15 20:00 | 2022-09-15 21:00 | Summer | TRUE | summer
2022-09-15 21:00 | 2022-09-15 22:00 | Summer | FALSE | summer
2022-09-15 22:00 | 2022-09-15 23:00 | Summer | FALSE | summer
2022-09-15 23:00 | 2022-09-16 | Summer | FALSE | summer
2022-09-16 | 2022-09-16 01:00 | Summer | FALSE | summer
2022-09-16 01:00 | 2022-09-16 02:00 | Summer | FALSE | summer
2022-09-16 02:00 | 2022-09-16 03:00 | Summer | FALSE | summer
2022-09-16 03:00 | 2022-09-16 04:00 | Summer | FALSE | summer
2022-09-16 04:00 | 2022-09-16 05:00 | Summer | FALSE | summer
2022-09-16 05:00 | 2022-09-16 06:00 | Summer | FALSE | summer
2022-09-16 06:00 | 2022-09-16 07:00 | Summer | FALSE | summer
2022-09-16 07:00 | 2022-09-16 08:00 | Summer | FALSE | summer
2022-09-16 08:00 | 2022-09-16 09:00 | Summer | FALSE | summer
2022-09-16 09:00 | 2022-09-16 10:00 | Summer | FALSE | summer
2022-09-16 10:00 | 2022-09-16 11:00 | Summer | FALSE | summer
2022-09-16 11:00 | 2022-09-16 12:00 | Summer | FALSE | summer
2022-09-16 12:00 | 2022-09-16 13:00 | Summer | FALSE | summer
2022-09-16 13:00 | 2022-09-16 14:00 | Summer | FALSE | summer
2022-09-16 14:00 | 2022-09-16 15:00 | Summer | FALSE | summer
2022-09-16 15:00 | 2022-09-16 16:00 | Summer | FALSE | summer
2022-09-16 16:00 | 2022-09-16 17:00 | Summer | TRUE | summer
2022-09-16 17:00 | 2022-09-16 18:00 | Summer | TRUE | summer
2022-09-16 18:00 | 2022-09-16 19:00 | Summer | TRUE | summer
2022-09-16 19:00 | 2022-09-16 20:00 | Summer | TRUE | summer
2022-09-16 20:00 | 2022-09-16 21:00 | Summer | TRUE | summer
2022-09-16 21:00 | 2022-09-16 22:00 | Summer | FALSE | summer
2022-09-16 22:00 | 2022-09-16 23:00 | Summer | FALSE | summer
2022-09-16 23:00 | 2022-09-17 | Summer | FALSE | summer
2022-09-17 | 2022-09-17 01:00 | Summer | FALSE | summer
2022-09-17 01:00 | 2022-09-17 02:00 | Summer | FALSE | summer
2022-09-17 02:00 | 2022-09-17 03:00 | Summer | FALSE | summer
2022-09-17 03:00 | 2022-09-17 04:00 | Summer | FALSE | summer
2022-09-17 04:00 | 2022-09-17 05:00 | Summer | FALSE | summer
2022-09-17 05:00 | 2022-09-17 06:00 | Summer | FALSE | summer
2022-09-17 06:00 | 2022-09-17 07:00 | Summer | FALSE | summer
2022-09-17 07:00 | 2022-09-17 08:00 | Summer | FALSE | summer
2022-09-17 08:00 | 2022-09-17 09:00 | Summer | FALSE | summer
2022-09-17 09:00 | 2022-09-17 10:00 | Summer | FALSE | summer
2022-09-17 10:00 | 2022-09-17 11:00 | Summer | FALSE | summer
2022-09-17 11:00 | 2022-09-17 12:00 | Summer | FALSE | summer
2022-09-17 12:00 | 2022-09-17 13:00 | Summer | FALSE | summer
2022-09-17 13:00 | 2022-09-17 14:00 | Summer | FALSE | summer
2022-09-17 14:00 | 2022-09-17 15:00 | Summer | FALSE | summer
2022-09-17 15:00 | 2022-09-17 16:00 | Summer | FALSE | summer
2022-09-17 16:00 | 2022-09-17 17:00 | Summer | TRUE | summer
2022-09-17 17:00 | 2022-09-17 18:00 | Summer | TRUE | summer
2022-09-17 18:00 | 2022-09-17 19:00 | Summer | TRUE | summer
2022-09-17 19:00 | 2022-09-17 20:00 | Summer | TRUE | summer
2022-09-17 20:00 | 2022-09-17 21:00 | Summer | TRUE | summer
2022-09-17 21:00 | 2022-09-17 22:00 | Summer | FALSE | summer
2022-09-17 22:00 | 2022-09-17 23:00 | Summer | FALSE | summer
2022-09-17 23:00 | 2022-09-18 | Summer | FALSE | summer
2022-09-18 | 2022-09-18 01:00 | Summer | FALSE | summer
2022-09-18 01:00 | 2022-09-18 02:00 | Summer | FALSE | summer
2022-09-18 02:00 | 2022-09-18 03:00 | Summer | FALSE | summer
2022-09-18 03:00 | 2022-09-18 04:00 | Summer | FALSE | summer
2022-09-18 04:00 | 2022-09-18 05:00 | Summer | FALSE | summer
2022-09-18 05:00 | 2022-09-18 06:00 | Summer | FALSE | summer
2022-09-18 06:00 | 2022-09-18 07:00 | Summer | FALSE | summer
2022-09-18 07:00 | 2022-09-18 08:00 | Summer | FALSE | summer
2022-09-18 08:00 | 2022-09-18 09:00 | Summer | FALSE | summer
2022-09-18 09:00 | 2022-09-18 10:00 | Summer | FALSE | summer
2022-09-18 10:00 | 2022-09-18 11:00 | Summer | FALSE | summer
2022-09-18 11:00 | 2022-09-18 12:00 | Summer | FALSE | summer
2022-09-18 12:00 | 2022-09-18 13:00 | Summer | FALSE | summer
2022-09-18 13:00 | 2022-09-18 14:00 | Summer | FALSE | summer
2022-09-18 14:00 | 2022-09-18 15:00 | Summer | FALSE | summer
2022-09-18 15:00 | 2022-09-18 16:00 | Summer | FALSE | summer
2022-09-18 16:00 | 2022-09-18 17:00 | Summer | TRUE | summer
2022-09-18 17:00 | 2022-09-18 18:00 | Summer | TRUE | summer
2022-09-18 18:00 | 2022-09-18 19:00 | Summer | TRUE | summer
2022-09-18 19:00 | 2022-09-18 20:00 | Summer | TRUE | summer
2022-09-18 20:00 | 2022-09-18 21:00 | Summer | TRUE | summer
2022-09-18 21:00 | 2022-09-18 22:00 | Summer | FALSE | summer
2022-09-18 22:00 | 2022-09-18 23:00 | Summer | FALSE | summer
2022-09-18 23:00 | 2022-09-19 | Summer | FALSE | summer
2022-09-19 | 2022-09-19 01:00 | Summer | FALSE | summer
2022-09-19 01:00 | 2022-09-19 02:00 | Summer | FALSE | summer
2022-09-19 02:00 | 2022-09-19 03:00 | Summer | FALSE | summer
2022-09-19 03:00 | 2022-09-19 04:00 | Summer | FALSE | summer
2022-09-19 04:00 | 2022-09-19 05:00 | Summer | FALSE | summer
2022-09-19 05:00 | 2022-09-19 06:00 | Summer | FALSE | summer
2022-09-19 06:00 | 2022-09-19 07:00 | Summer | FALSE | summer
2022-09-19 07:00 | 2022-09-19 08:00 | Summer | FALSE | summer
2022-09-19 08:00 | 2022-09-19 09:00 | Summer | FALSE | summer
2022-09-19 09:00 | 2022-09-19 10:00 | Summer | FALSE | summer
2022-09-19 10:00 | 2022-09-19 11:00 | Summer | FALSE | summer
2022-09-19 11:00 | 2022-09-19 12:00 | Summer | FALSE | summer
2022-09-19 12:00 | 2022-09-19 13:00 | Summer | FALSE | summer
2022-09-19 13:00 | 2022-09-19 14:00 | Summer | FALSE | summer
2022-09-19 14:00 | 2022-09-19 15:00 | Summer | FALSE | summer
2022-09-19 15:00 | 2022-09-19 16:00 | Summer | FALSE | summer
2022-09-19 16:00 | 2022-09-19 17:00 | Summer | TRUE | summer
2022-09-19 17:00 | 2022-09-19 18:00 | Summer | TRUE | summer
2022-09-19 18:00 | 2022-09-19 19:00 | Summer | TRUE | summer
2022-09-19 19:00 | 2022-09-19 20:00 | Summer | TRUE | summer
2022-09-19 20:00 | 2022-09-19 21:00 | Summer | TRUE | summer
2022-09-19 21:00 | 2022-09-19 22:00 | Summer | FALSE | summer
2022-09-19 22:00 | 2022-09-19 23:00 | Summer | FALSE | summer
2022-09-19 23:00 | 2022-09-20 | Summer | FALSE | summer
2022-09-20 | 2022-09-20 01:00 | Summer | FALSE | summer
2022-09-20 01:00 | 2022-09-20 02:00 | Summer | FALSE | summer
2022-09-20 02:00 | 2022-09-20 03:00 | Summer | FALSE | summer
2022-09-20 03:00 | 2022-09-20 04:00 | Summer | FALSE | summer
2022-09-20 04:00 | 2022-09-20 05:00 | Summer | FALSE | summer
2022-09-20 05:00 | 2022-09-20 06:00 | Summer | FALSE | summer
2022-09-20 06:00 | 2022-09-20 07:00 | Summer | FALSE | summer
2022-09-20 07:00 | 2022-09-20 08:00 | Summer | FALSE | summer
2022-09-20 08:00 | 2022-09-20 09:00 | Summer | FALSE | summer
2022-09-20 09:00 | 2022-09-20 10:00 | Summer | FALSE | summer
2022-09-20 10:00 | 2022-09-20 11:00 | Summer | FALSE | summer
2022-09-20 11:00 | 2022-09-20 12:00 | Summer | FALSE | summer
2022-09-20 12:00 | 2022-09-20 13:00 | Summer | FALSE | summer
2022-09-20 13:00 | 2022-09-20 14:00 | Summer | FALSE | summer
2022-09-20 14:00 | 2022-09-20 15:00 | Summer | FALSE | summer
2022-09-20 15:00 | 2022-09-20 16:00 | Summer | FALSE | summer
2022-09-20 16:00 | 2022-09-20 17:00 | Summer | TRUE | summer
2022-09-20 17:00 | 2022-09-20 18:00 | Summer | TRUE | summer
2022-09-20 18:00 | 2022-09-20 19:00 | Summer | TRUE | summer
2022-09-20 19:00 | 2022-09-20 20:00 | Summer | TRUE | summer
2022-09-20 20:00 | 2022-09-20 21:00 | Summer | TRUE | summer
2022-09-20 21:00 | 2022-09-20 22:00 | Summer | FALSE | summer
2022-09-20 22:00 | 2022-09-20 23:00 | Summer | FALSE | summer
2022-09-20 23:00 | 2022-09-21 | Summer | FALSE | summer
2022-09-21 | 2022-09-21 01:00 | Summer | FALSE | summer
2022-09-21 01:00 | 2022-09-21 02:00 | Summer | FALSE | summer
2022-09-21 02:00 | 2022-09-21 03:00 | Summer | FALSE | summer
2022-09-21 03:00 | 2022-09-21 04:00 | Summer | FALSE | summer
2022-09-21 04:00 | 2022-09-21 05:00 | Summer | FALSE | summer
2022-09-21 05:00 | 2022-09-21 06:00 | Summer | FALSE | summer
2022-09-21 06:00 | 2022-09-21 07:00 | Summer | FALSE | summer
2022-09-21 07:00 | 2022-09-21 08:00 | Summer | FALSE | summer
2022-09-21 08:00 | 2022-09-21 09:00 | Summer | FALSE | summer
2022-09-21 09:00 | 2022-09-21 10:00 | Summer | FALSE | summer
2022-09-21 10:00 | 2022-09-21 11:00 | Summer | FALSE | summer
2022-09-21 11:00 | 2022-09-21 12:00 | Summer | FALSE | summer
2022-09-21 12:00 | 2022-09-21 13:00 | Summer | FALSE | summer
2022-09-21 13:00 | 2022-09-21 14:00 | Summer | FALSE | summer
2022-09-21 14:00 | 2022-09-21 15:00 | Summer | FALSE | summer
2022-09-21 15:00 | 2022-09-21 16:00 | Summer | FALSE | summer
2022-09-21 16:00 | 2022-09-21 17:00 | Summer | TRUE | summer
2022-09-21 17:00 | 2022-09-21 18:00 | Summer | TRUE | summer
2022-09-21 18:00 | 2022-09-21 19:00 | Summer | TRUE | summer
2022-09-21 19:00 | 2022-09-21 20:00 | Summer | TRUE | summer
2022-09-21 20:00 | 2022-09-21 21:00 | Summer | TRUE | summer
2022-09-21 21:00 | 2022-09-21 22:00 | Summer | FALSE | summer
2022-09-21 22:00 | 2022-09-21 23:00 | Summer | FALSE | summer
2022-09-21 23:00 | 2022-09-22 | Summer | FALSE | summer
2022-09-22 | 2022-09-22 01:00 | Summer | FALSE | summer
2022-09-22 01:00 | 2022-09-22 02:00 | Summer | FALSE | summer
2022-09-22 02:00 | 2022-09-22 03:00 | Summer | FALSE | summer
2022-09-22 03:00 | 2022-09-22 04:00 | Summer | FALSE | summer
2022-09-22 04:00 | 2022-09-22 05:00 | Summer | FALSE | summer
2022-09-22 05:00 | 2022-09-22 06:00 | Summer | FALSE | summer
2022-09-22 06:00 | 2022-09-22 07:00 | Summer | FALSE | summer
2022-09-22 07:00 | 2022-09-22 08:00 | Summer | FALSE | summer
2022-09-22 08:00 | 2022-09-22 09:00 | Summer | FALSE | summer
2022-09-22 09:00 | 2022-09-22 10:00 | Summer | FALSE | summer
2022-09-22 10:00 | 2022-09-22 11:00 | Summer | FALSE | summer
2022-09-22 11:00 | 2022-09-22 12:00 | Summer | FALSE | summer
2022-09-22 12:00 | 2022-09-22 13:00 | Summer | FALSE | summer
2022-09-22 13:00 | 2022-09-22 14:00 | Summer | FALSE | summer
2022-09-22 14:00 | 2022-09-22 15:00 | Summer | FALSE | summer
2022-09-22 15:00 | 2022-09-22 16:00 | Summer | FALSE | summer
2022-09-22 16:00 | 2022-09-22 17:00 | Summer | TRUE | summer
2022-09-22 17:00 | 2022-09-22 18:00 | Summer | TRUE | summer
2022-09-22 18:00 | 2022-09-22 19:00 | Summer | TRUE | summer
2022-09-22 19:00 | 2022-09-22 20:00 | Summer | TRUE | summer
2022-09-22 20:00 | 2022-09-22 21:00 | Summer | TRUE | summer
2022-09-22 21:00 | 2022-09-22 22:00 | Summer | FALSE | summer
2022-09-22 22:00 | 2022-09-22 23:00 | Summer | FALSE | summer
2022-09-22 23:00 | 2022-09-23 | Summer | FALSE | summer
2022-09-23 | 2022-09-23 01:00 | Summer | FALSE | summer
2022-09-23 01:00 | 2022-09-23 02:00 | Summer | FALSE | summer
2022-09-23 02:00 | 2022-09-23 03:00 | Summer | FALSE | summer
2022-09-23 03:00 | 2022-09-23 04:00 | Summer | FALSE | summer
2022-09-23 04:00 | 2022-09-23 05:00 | Summer | FALSE | summer
2022-09-23 05:00 | 2022-09-23 06:00 | Summer | FALSE | summer
2022-09-23 06:00 | 2022-09-23 07:00 | Summer | FALSE | summer
2022-09-23 07:00 | 2022-09-23 08:00 | Summer | FALSE | summer
2022-09-23 08:00 | 2022-09-23 09:00 | Summer | FALSE | summer
2022-09-23 09:00 | 2022-09-23 10:00 | Summer | FALSE | summer
2022-09-23 10:00 | 2022-09-23 11:00 | Summer | FALSE | summer
2022-09-23 11:00 | 2022-09-23 12:00 | Summer | FALSE | summer
2022-09-23 12:00 | 2022-09-23 13:00 | Summer | FALSE | summer
2022-09-23 13:00 | 2022-09-23 14:00 | Summer | FALSE | summer
2022-09-23 14:00 | 2022-09-23 15:00 | Summer | FALSE | summer
2022-09-23 15:00 | 2022-09-23 16:00 | Summer | FALSE | summer
2022-09-23 16:00 | 2022-09-23 17:00 | Summer | TRUE | summer
2022-09-23 17:00 | 2022-09-23 18:00 | Summer | TRUE | summer
2022-09-23 18:00 | 2022-09-23 19:00 | Summer | TRUE | summer
2022-09-23 19:00 | 2022-09-23 20:00 | Summer | TRUE | summer
2022-09-23 20:00 | 2022-09-23 21:00 | Summer | TRUE | summer
2022-09-23 21:00 | 2022-09-23 22:00 | Summer | FALSE | summer
2022-09-23 22:00 | 2022-09-23 23:00 | Summer | FALSE | summer
2022-09-23 23:00 | 2022-09-24 | Summer | FALSE | summer
2022-09-24 | 2022-09-24 01:00 | Summer | FALSE | summer
2022-09-24 01:00 | 2022-09-24 02:00 | Summer | FALSE | summer
2022-09-24 02:00 | 2022-09-24 03:00 | Summer | FALSE | summer
2022-09-24 03:00 | 2022-09-24 04:00 | Summer | FALSE | summer
2022-09-24 04:00 | 2022-09-24 05:00 | Summer | FALSE | summer
2022-09-24 05:00 | 2022-09-24 06:00 | Summer | FALSE | summer
2022-09-24 06:00 | 2022-09-24 07:00 | Summer | FALSE | summer
2022-09-24 07:00 | 2022-09-24 08:00 | Summer | FALSE | summer
2022-09-24 08:00 | 2022-09-24 09:00 | Summer | FALSE | summer
2022-09-24 09:00 | 2022-09-24 10:00 | Summer | FALSE | summer
2022-09-24 10:00 | 2022-09-24 11:00 | Summer | FALSE | summer
2022-09-24 11:00 | 2022-09-24 12:00 | Summer | FALSE | summer
2022-09-24 12:00 | 2022-09-24 13:00 | Summer | FALSE | summer
2022-09-24 13:00 | 2022-09-24 14:00 | Summer | FALSE | summer
2022-09-24 14:00 | 2022-09-24 15:00 | Summer | FALSE | summer
2022-09-24 15:00 | 2022-09-24 16:00 | Summer | FALSE | summer
2022-09-24 16:00 | 2022-09-24 17:00 | Summer | TRUE | summer
2022-09-24 17:00 | 2022-09-24 18:00 | Summer | TRUE | summer
2022-09-24 18:00 | 2022-09-24 19:00 | Summer | TRUE | summer
2022-09-24 19:00 | 2022-09-24 20:00 | Summer | TRUE | summer
2022-09-24 20:00 | 2022-09-24 21:00 | Summer | TRUE | summer
2022-09-24 21:00 | 2022-09-24 22:00 | Summer | FALSE | summer
2022-09-24 22:00 | 2022-09-24 23:00 | Summer | FALSE | summer
2022-09-24 23:00 | 2022-09-25 | Summer | FALSE | summer
2022-09-25 | 2022-09-25 01:00 | Summer | FALSE | summer
2022-09-25 01:00 | 2022-09-25 02:00 | Summer | FALSE | summer
2022-09-25 02:00 | 2022-09-25 03:00 | Summer | FALSE | summer
2022-09-25 03:00 | 2022-09-25 04:00 | Summer | FALSE | summer
2022-09-25 04:00 | 2022-09-25 05:00 | Summer | FALSE | summer
2022-09-25 05:00 | 2022-09-25 06:00 | Summer | FALSE | summer
2022-09-25 06:00 | 2022-09-25 07:00 | Summer | FALSE | summer
2022-09-25 07:00 | 2022-09-25 08:00 | Summer | FALSE | summer
2022-09-25 08:00 | 2022-09-25 09:00 | Summer | FALSE | summer
2022-09-25 09:00 | 2022-09-25 10:00 | Summer | FALSE | summer
2022-09-25 10:00 | 2022-09-25 11:00 | Summer | FALSE | summer
2022-09-25 11:00 | 2022-09-25 12:00 | Summer | FALSE | summer
2022-09-25 12:00 | 2022-09-25 13:00 | Summer | FALSE | summer
2022-09-25 13:00 | 2022-09-25 14:00 | Summer | FALSE | summer
2022-09-25 14:00 | 2022-09-25 15:00 | Summer | FALSE | summer
2022-09-25 15:00 | 2022-09-25 16:00 | Summer | FALSE | summer
2022-09-25 16:00 | 2022-09-25 17:00 | Summer | TRUE | summer
2022-09-25 17:00 | 2022-09-25 18:00 | Summer | TRUE | summer
2022-09-25 18:00 | 2022-09-25 19:00 | Summer | TRUE | summer
2022-09-25 19:00 | 2022-09-25 20:00 | Summer | TRUE | summer
2022-09-25 20:00 | 2022-09-25 21:00 | Summer | TRUE | summer
2022-09-25 21:00 | 2022-09-25 22:00 | Summer | FALSE | summer
2022-09-25 22:00 | 2022-09-25 23:00 | Summer | FALSE | summer
2022-09-25 23:00 | 2022-09-26 | Summer | FALSE | summer
2022-09-26 | 2022-09-26 01:00 | Summer | FALSE | summer
2022-09-26 01:00 | 2022-09-26 02:00 | Summer | FALSE | summer
2022-09-26 02:00 | 2022-09-26 03:00 | Summer | FALSE | summer
2022-09-26 03:00 | 2022-09-26 04:00 | Summer | FALSE | summer
2022-09-26 04:00 | 2022-09-26 05:00 | Summer | FALSE | summer
2022-09-26 05:00 | 2022-09-26 06:00 | Summer | FALSE | summer
2022-09-26 06:00 | 2022-09-26 07:00 | Summer | FALSE | summer
2022-09-26 07:00 | 2022-09-26 08:00 | Summer | FALSE | summer
2022-09-26 08:00 | 2022-09-26 09:00 | Summer | FALSE | summer
2022-09-26 09:00 | 2022-09-26 10:00 | Summer | FALSE | summer
2022-09-26 10:00 | 2022-09-26 11:00 | Summer | FALSE | summer
2022-09-26 11:00 | 2022-09-26 12:00 | Summer | FALSE | summer
2022-09-26 12:00 | 2022-09-26 13:00 | Summer | FALSE | summer
2022-09-26 13:00 | 2022-09-26 14:00 | Summer | FALSE | summer
2022-09-26 14:00 | 2022-09-26 15:00 | Summer | FALSE | summer
2022-09-26 15:00 | 2022-09-26 16:00 | Summer | FALSE | summer
2022-09-26 16:00 | 2022-09-26 17:00 | Summer | TRUE | summer
2022-09-26 17:00 | 2022-09-26 18:00 | Summer | TRUE | summer
2022-09-26 18:00 | 2022-09-26 19:00 | Summer | TRUE | summer
2022-09-26 19:00 | 2022-09-26 20:00 | Summer | TRUE | summer
2022-09-26 20:00 | 2022-09-26 21:00 | Summer | TRUE | summer
2022-09-26 21:00 | 2022-09-26 22:00 | Summer | FALSE | summer
2022-09-26 22:00 | 2022-09-26 23:00 | Summer | FALSE | summer
2022-09-26 23:00 | 2022-09-27 | Summer | FALSE | summer
2022-09-27 | 2022-09-27 01:00 | Summer | FALSE | summer
2022-09-27 01:00 | 2022-09-27 02:00 | Summer | FALSE | summer
2022-09-27 02:00 | 2022-09-27 03:00 | Summer | FALSE | summer
2022-09-27 03:00 | 2022-09-27 04:00 | Summer | FALSE | summer
2022-09-27 04:00 | 2022-09-27 05:00 | Summer | FALSE | summer
2022-09-27 05:00 | 2022-09-27 06:00 | Summer | FALSE | summer
2022-09-27 06:00 | 2022-09-27 07:00 | Summer | FALSE | summer
2022-09-27 07:00 | 2022-09-27 08:00 | Summer | FALSE | summer
2022-09-27 08:00 | 2022-09-27 09:00 | Summer | FALSE | summer
2022-09-27 09:00 | 2022-09-27 10:00 | Summer | FALSE | summer
2022-09-27 10:00 | 2022-09-27 11:00 | Summer | FALSE | summer
2022-09-27 11:00 | 2022-09-27 12:00 | Summer | FALSE | summer
2022-09-27 12:00 | 2022-09-27 13:00 | Summer | FALSE | summer
2022-09-27 13:00 | 2022-09-27 14:00 | Summer | FALSE | summer
2022-09-27 14:00 | 2022-09-27 15:00 | Summer | FALSE | summer
2022-09-27 15:00 | 2022-09-27 16:00 | Summer | FALSE | summer
2022-09-27 16:00 | 2022-09-27 17:00 | Summer | TRUE | summer
2022-09-27 17:00 | 2022-09-27 18:00 | Summer | TRUE | summer
2022-09-27 18:00 | 2022-09-27 19:00 | Summer | TRUE | summer
2022-09-27 19:00 | 2022-09-27 20:00 | Summer | TRUE | summer
2022-09-27 20:00 | 2022-09-27 21:00 | Summer | TRUE | summer
2022-09-27 21:00 | 2022-09-27 22:00 | Summer | FALSE | summer
2022-09-27 22:00 | 2022-09-27 23:00 | Summer | FALSE | summer
2022-09-27 23:00 | 2022-09-28 | Summer | FALSE | summer
2022-09-28 | 2022-09-28 01:00 | Summer | FALSE | summer
2022-09-28 01:00 | 2022-09-28 02:00 | Summer | FALSE | summer
2022-09-28 02:00 | 2022-09-28 03:00 | Summer | FALSE | summer
2022-09-28 03:00 | 2022-09-28 04:00 | Summer | FALSE | summer
2022-09-28 04:00 | 2022-09-28 05:00 | Summer | FALSE | summer
2022-09-28 05:00 | 2022-09-28 06:00 | Summer | FALSE | summer
2022-09-28 06:00 | 2022-09-28 07:00 | Summer | FALSE | summer
2022-09-28 07:00 | 2022-09-28 08:00 | Summer | FALSE | summer
2022-09-28 08:00 | 2022-09-28 09:00 | Summer | FALSE | summer
2022-09-28 09:00 | 2022-09-28 10:00 | Summer | FALSE | summer
2022-09-28 10:00 | 2022-09-28 11:00 | Summer | FALSE | summer
2022-09-28 11:00 | 2022-09-28 12:00 | Summer | FALSE | summer
2022-09-28 12:00 | 2022-09-28 13:00 | Summer | FALSE | summer
2022-09-28 13:00 | 2022-09-28 14:00 | Summer | FALSE | summer
2022-09-28 14:00 | 2022-09-28 15:00 | Summer | FALSE | summer
2022-09-28 15:00 | 2022-09-28 16:00 | Summer | FALSE | summer
2022-09-28 16:00 | 2022-09-28 17:00 | Summer | TRUE | summer
2022-09-28 17:00 | 2022-09-28 18:00 | Summer | TRUE | summer
2022-09-28 18:00 | 2022-09-28 19:00 | Summer | TRUE | summer
2022-09-28 19:00 | 2022-09-28 20:00 | Summer | TRUE | summer
2022-09-28 20:00 | 2022-09-28 21:00 | Summer | TRUE | summer
2022-09-28 21:00 | 2022-09-28 22:00 | Summer | FALSE | summer
2022-09-28 22:00 | 2022-09-28 23:00 | Summer | FALSE | summer
2022-09-28 23:00 | 2022-09-29 | Summer | FALSE | summer
2022-09-29 | 2022-09-29 01:00 | Summer | FALSE | summer
2022-09-29 01:00 | 2022-09-29 02:00 | Summer | FALSE | summer
2022-09-29 02:00 | 2022-09-29 03:00 | Summer | FALSE | summer
2022-09-29 03:00 | 2022-09-29 04:00 | Summer | FALSE | summer
2022-09-29 04:00 | 2022-09-29 05:00 | Summer | FALSE | summer
2022-09-29 05:00 | 2022-09-29 06:00 | Summer | FALSE | summer
2022-09-29 06:00 | 2022-09-29 07:00 | Summer | FALSE | summer
2022-09-29 07:00 | 2022-09-29 08:00 | Summer | FALSE | summer
2022-09-29 08:00 | 2022-09-29 09:00 | Summer | FALSE | summer
2022-09-29 09:00 | 2022-09-29 10:00 | Summer | FALSE | summer
2022-09-29 10:00 | 2022-09-29 11:00 | Summer | FALSE | summer
2022-09-29 11:00 | 2022-09-29 12:00 | Summer | FALSE | summer
2022-09-29 12:00 | 2022-09-29 13:00 | Summer | FALSE | summer
2022-09-29 13:00 | 2022-09-29 14:00 | Summer | FALSE | summer
2022-09-29 14:00 | 2022-09-29 15:00 | Summer | FALSE | summer
2022-09-29 15:00 | 2022-09-29 16:00 | Summer | FALSE | summer
2022-09-29 16:00 | 2022-09-29 17:00 | Summer | TRUE | summer
2022-09-29 17:00 | 2022-09-29 18:00 | Summer | TRUE | summer
2022-09-29 18:00 | 2022-09-29 19:00 | Summer | TRUE | summer
2022-09-29 19:00 | 2022-09-29 20:00 | Summer | TRUE | summer
2022-09-29 20:00 | 2022-09-29 21:00 | Summer | TRUE | summer
2022-09-29 21:00 | 2022-09-29 22:00 | Summer | FALSE | summer
2022-09-29 22:00 | 2022-09-29 23:00 | Summer | FALSE | summer
2022-09-29 23:00 | 2022-09-30 | Summer | FALSE | summer
2022-09-30 | 2022-09-30 01:00 | Summer | FALSE | summer
2022-09-30 01:00 | 2022-09-30 02:00 | Summer | FALSE | summer
2022-09-30 02:00 | 2022-09-30 03:00 | Summer | FALSE | summer
2022-09-30 03:00 | 2022-09-30 04:00 | Summer | FALSE | summer
2022-09-30 04:00 | 2022-09-30 05:00 | Summer | FALSE | summer
2022-09-30 05:00 | 2022-09-30 06:00 | Summer | FALSE | summer
2022-09-30 06:00 | 2022-09-30 07:00 | Summer | FALSE | summer
2022-09-30 07:00 | 2022-09-30 08:00 | Summer | FALSE | summer
2022-09-30 08:00 | 2022-09-30 09:00 | Summer | FALSE | summer
2022-09-30 09:00 | 2022-09-30 10:00 | Summer | FALSE | summer
2022-09-30 10:00 | 2022-09-30 11:00 | Summer | FALSE | summer
2022-09-30 11:00 | 2022-09-30 12:00 | Summer | FALSE | summer
2022-09-30 12:00 | 2022-09-30 13:00 | Summer | FALSE | summer
2022-09-30 13:00 | 2022-09-30 14:00 | Summer | FALSE | summer
2022-09-30 14:00 | 2022-09-30 15:00 | Summer | FALSE | summer
2022-09-30 15:00 | 2022-09-30 16:00 | Summer | FALSE | summer
2022-09-30 16:00 | 2022-09-30 17:00 | Summer | TRUE | summer
2022-09-30 17:00 | 2022-09-30 18:00 | Summer | TRUE | summer
2022-09-30 18:00 | 2022-09-30 19:00 | Summer | TRUE | summer
2022-09-30 19:00 | 2022-09-30 20:00 | Summer | TRUE | summer
2022-09-30 20:00 | 2022-09-30 21:00 | Summer | TRUE | summer
2022-09-30 21:00 | 2022-09-30 22:00 | Summer | FALSE | summer
2022-09-30 22:00 | 2022-09-30 23:00 | Summer | FALSE | summer
2022-09-30 23:00 | 2022-10-01 | Summer | FALSE | summer
2022-10-01 | 2022-10-01 01:00 | Winter | FALSE | summer
2022-10-01 01:00 | 2022-10-01 02:00 | Winter | FALSE | summer
2022-10-01 02:00 | 2022-10-01 03:00 | Winter | FALSE | summer
2022-10-01 03:00 | 2022-10-01 04:00 | Winter | FALSE | summer
2022-10-01 04:00 | 2022-10-01 05:00 | Winter | FALSE | summer
2022-10-01 05:00 | 2022-10-01 06:00 | Winter | FALSE | summer
2022-10-01 06:00 | 2022-10-01 07:00 | Winter | FALSE | summer
2022-10-01 07:00 | 2022-10-01 08:00 | Winter | FALSE | summer
2022-10-01 08:00 | 2022-10-01 09:00 | Winter | FALSE | summer
2022-10-01 09:00 | 2022-10-01 10:00 | Winter | FALSE | summer
2022-10-01 10:00 | 2022-10-01 11:00 | Winter | FALSE | summer
2022-10-01 11:00 | 2022-10-01 12:00 | Winter | FALSE | summer
2022-10-01 12:00 | 2022-10-01 13:00 | Winter | FALSE | summer
2022-10-01 13:00 | 2022-10-01 14:00 | Winter | FALSE | summer
2022-10-01 14:00 | 2022-10-01 15:00 | Winter | FALSE | summer
2022-10-01 15:00 | 2022-10-01 16:00 | Winter | FALSE | summer
2022-10-01 16:00 | 2022-10-01 17:00 | Winter | TRUE | summer
2022-10-01 17:00 | 2022-10-01 18:00 | Winter | TRUE | summer
2022-10-01 18:00 | 2022-10-01 19:00 | Winter | TRUE | summer
2022-10-01 19:00 | 2022-10-01 20:00 | Winter | TRUE | summer
2022-10-01 20:00 | 2022-10-01 21:00 | Winter | TRUE | summer
2022-10-01 21:00 | 2022-10-01 22:00 | Winter | FALSE | summer
2022-10-01 22:00 | 2022-10-01 23:00 | Winter | FALSE | summer
2022-10-01 23:00 | 2022-10-02 | Winter | FALSE | summer
2022-10-02 | 2022-10-02 01:00 | Winter | FALSE | summer
2022-10-02 01:00 | 2022-10-02 02:00 | Winter | FALSE | summer
2022-10-02 02:00 | 2022-10-02 03:00 | Winter | FALSE | summer
2022-10-02 03:00 | 2022-10-02 04:00 | Winter | FALSE | summer
2022-10-02 04:00 | 2022-10-02 05:00 | Winter | FALSE | summer
2022-10-02 05:00 | 2022-10-02 06:00 | Winter | FALSE | summer
2022-10-02 06:00 | 2022-10-02 07:00 | Winter | FALSE | summer
2022-10-02 07:00 | 2022-10-02 08:00 | Winter | FALSE | summer
2022-10-02 08:00 | 2022-10-02 09:00 | Winter | FALSE | summer
2022-10-02 09:00 | 2022-10-02 10:00 | Winter | FALSE | summer
2022-10-02 10:00 | 2022-10-02 11:00 | Winter | FALSE | summer
2022-10-02 11:00 | 2022-10-02 12:00 | Winter | FALSE | summer
2022-10-02 12:00 | 2022-10-02 13:00 | Winter | FALSE | summer
2022-10-02 13:00 | 2022-10-02 14:00 | Winter | FALSE | summer
2022-10-02 14:00 | 2022-10-02 15:00 | Winter | FALSE | summer
2022-10-02 15:00 | 2022-10-02 16:00 | Winter | FALSE | summer
2022-10-02 16:00 | 2022-10-02 17:00 | Winter | TRUE | summer
2022-10-02 17:00 | 2022-10-02 18:00 | Winter | TRUE | summer
2022-10-02 18:00 | 2022-10-02 19:00 | Winter | TRUE | summer
2022-10-02 19:00 | 2022-10-02 20:00 | Winter | TRUE | summer
2022-10-02 20:00 | 2022-10-02 21:00 | Winter | TRUE | summer
2022-10-02 21:00 | 2022-10-02 22:00 | Winter | FALSE | summer
2022-10-02 22:00 | 2022-10-02 23:00 | Winter | FALSE | summer
2022-10-02 23:00 | 2022-10-03 | Winter | FALSE | summer
2022-10-03 | 2022-10-03 01:00 | Winter | FALSE | summer
2022-10-03 01:00 | 2022-10-03 02:00 | Winter | FALSE | summer
2022-10-03 02:00 | 2022-10-03 03:00 | Winter | FALSE | summer
2022-10-03 03:00 | 2022-10-03 04:00 | Winter | FALSE | summer
2022-10-03 04:00 | 2022-10-03 05:00 | Winter | FALSE | summer
2022-10-03 05:00 | 2022-10-03 06:00 | Winter | FALSE | summer
2022-10-03 06:00 | 2022-10-03 07:00 | Winter | FALSE | summer
2022-10-03 07:00 | 2022-10-03 08:00 | Winter | FALSE | summer
2022-10-03 08:00 | 2022-10-03 09:00 | Winter | FALSE | summer
2022-10-03 09:00 | 2022-10-03 10:00 | Winter | FALSE | summer
2022-10-03 10:00 | 2022-10-03 11:00 | Winter | FALSE | summer
2022-10-03 11:00 | 2022-10-03 12:00 | Winter | FALSE | summer
2022-10-03 12:00 | 2022-10-03 13:00 | Winter | FALSE | summer
2022-10-03 13:00 | 2022-10-03 14:00 | Winter | FALSE | summer
2022-10-03 14:00 | 2022-10-03 15:00 | Winter | FALSE | summer
2022-10-03 15:00 | 2022-10-03 16:00 | Winter | FALSE | summer
2022-10-03 16:00 | 2022-10-03 17:00 | Winter | TRUE | summer
2022-10-03 17:00 | 2022-10-03 18:00 | Winter | TRUE | summer
2022-10-03 18:00 | 2022-10-03 19:00 | Winter | TRUE | summer
2022-10-03 19:00 | 2022-10-03 20:00 | Winter | TRUE | summer
2022-10-03 20:00 | 2022-10-03 21:00 | Winter | TRUE | summer
2022-10-03 21:00 | 2022-10-03 22:00 | Winter | FALSE | summer
2022-10-03 22:00 | 2022-10-03 23:00 | Winter | FALSE | summer
2022-10-03 23:00 | 2022-10-04 | Winter | FALSE | summer
2022-10-04 | 2022-10-04 01:00 | Winter | FALSE | summer
2022-10-04 01:00 | 2022-10-04 02:00 | Winter | FALSE | summer
2022-10-04 02:00 | 2022-10-04 03:00 | Winter | FALSE | summer
2022-10-04 03:00 | 2022-10-04 04:00 | Winter | FALSE | summer
2022-10-04 04:00 | 2022-10-04 05:00 | Winter | FALSE | summer
2022-10-04 05:00 | 2022-10-04 06:00 | Winter | FALSE | summer
2022-10-04 06:00 | 2022-10-04 07:00 | Winter | FALSE | summer
2022-10-04 07:00 | 2022-10-04 08:00 | Winter | FALSE | summer
2022-10-04 08:00 | 2022-10-04 09:00 | Winter | FALSE | summer
2022-10-04 09:00 | 2022-10-04 10:00 | Winter | FALSE | summer
2022-10-04 10:00 | 2022-10-04 11:00 | Winter | FALSE | summer
2022-10-04 11:00 | 2022-10-04 12:00 | Winter | FALSE | summer
2022-10-04 12:00 | 2022-10-04 13:00 | Winter | FALSE | summer
2022-10-04 13:00 | 2022-10-04 14:00 | Winter | FALSE | summer
2022-10-04 14:00 | 2022-10-04 15:00 | Winter | FALSE | summer
2022-10-04 15:00 | 2022-10-04 16:00 | Winter | FALSE | summer
2022-10-04 16:00 | 2022-10-04 17:00 | Winter | TRUE | summer
2022-10-04 17:00 | 2022-10-04 18:00 | Winter | TRUE | summer
2022-10-04 18:00 | 2022-10-04 19:00 | Winter | TRUE | summer
2022-10-04 19:00 | 2022-10-04 20:00 | Winter | TRUE | summer
2022-10-04 20:00 | 2022-10-04 21:00 | Winter | TRUE | summer
2022-10-04 21:00 | 2022-10-04 22:00 | Winter | FALSE | summer
2022-10-04 22:00 | 2022-10-04 23:00 | Winter | FALSE | summer
2022-10-04 23:00 | 2022-10-05 | Winter | FALSE | summer
2022-10-05 | 2022-10-05 01:00 | Winter | FALSE | summer
2022-10-05 01:00 | 2022-10-05 02:00 | Winter | FALSE | summer
2022-10-05 02:00 | 2022-10-05 03:00 | Winter | FALSE | summer
2022-10-05 03:00 | 2022-10-05 04:00 | Winter | FALSE | summer
2022-10-05 04:00 | 2022-10-05 05:00 | Winter | FALSE | summer
2022-10-05 05:00 | 2022-10-05 06:00 | Winter | FALSE | summer
2022-10-05 06:00 | 2022-10-05 07:00 | Winter | FALSE | summer
2022-10-05 07:00 | 2022-10-05 08:00 | Winter | FALSE | summer
2022-10-05 08:00 | 2022-10-05 09:00 | Winter | FALSE | summer
2022-10-05 09:00 | 2022-10-05 10:00 | Winter | FALSE | summer
2022-10-05 10:00 | 2022-10-05 11:00 | Winter | FALSE | summer
2022-10-05 11:00 | 2022-10-05 12:00 | Winter | FALSE | summer
2022-10-05 12:00 | 2022-10-05 13:00 | Winter | FALSE | summer
2022-10-05 13:00 | 2022-10-05 14:00 | Winter | FALSE | summer
2022-10-05 14:00 | 2022-10-05 15:00 | Winter | FALSE | summer
2022-10-05 15:00 | 2022-10-05 16:00 | Winter | FALSE | summer
2022-10-05 16:00 | 2022-10-05 17:00 | Winter | TRUE | summer
2022-10-05 17:00 | 2022-10-05 18:00 | Winter | TRUE | summer
2022-10-05 18:00 | 2022-10-05 19:00 | Winter | TRUE | summer
2022-10-05 19:00 | 2022-10-05 20:00 | Winter | TRUE | summer
2022-10-05 20:00 | 2022-10-05 21:00 | Winter | TRUE | summer
2022-10-05 21:00 | 2022-10-05 22:00 | Winter | FALSE | summer
2022-10-05 22:00 | 2022-10-05 23:00 | Winter | FALSE | summer
2022-10-05 23:00 | 2022-10-06 | Winter | FALSE | summer
2022-10-06 | 2022-10-06 01:00 | Winter | FALSE | summer
2022-10-06 01:00 | 2022-10-06 02:00 | Winter | FALSE | summer
2022-10-06 02:00 | 2022-10-06 03:00 | Winter | FALSE | summer
2022-10-06 03:00 | 2022-10-06 04:00 | Winter | FALSE | summer
2022-10-06 04:00 | 2022-10-06 05:00 | Winter | FALSE | summer
2022-10-06 05:00 | 2022-10-06 06:00 | Winter | FALSE | summer
2022-10-06 06:00 | 2022-10-06 07:00 | Winter | FALSE | summer
2022-10-06 07:00 | 2022-10-06 08:00 | Winter | FALSE | summer
2022-10-06 08:00 | 2022-10-06 09:00 | Winter | FALSE | summer
2022-10-06 09:00 | 2022-10-06 10:00 | Winter | FALSE | summer
2022-10-06 10:00 | 2022-10-06 11:00 | Winter | FALSE | summer
2022-10-06 11:00 | 2022-10-06 12:00 | Winter | FALSE | summer
2022-10-06 12:00 | 2022-10-06 13:00 | Winter | FALSE | summer
2022-10-06 13:00 | 2022-10-06 14:00 | Winter | FALSE | summer
2022-10-06 14:00 | 2022-10-06 15:00 | Winter | FALSE | summer
2022-10-06 15:00 | 2022-10-06 16:00 | Winter | FALSE | summer
2022-10-06 16:00 | 2022-10-06 17:00 | Winter | TRUE | summer
2022-10-06 17:00 | 2022-10-06 18:00 | Winter | TRUE | summer
2022-10-06 18:00 | 2022-10-06 19:00 | Winter | TRUE | summer
2022-10-06 19:00 | 2022-10-06 20:00 | Winter | TRUE | summer
2022-10-06 20:00 | 2022-10-06 21:00 | Winter | TRUE | summer
2022-10-06 21:00 | 2022-10-06 22:00 | Winter | FALSE | summer
2022-10-06 22:00 | 2022-10-06 23:00 | Winter | FALSE | summer
2022-10-06 23:00 | 2022-10-07 | Winter | FALSE | summer
2022-10-07 | 2022-10-07 01:00 | Winter | FALSE | summer
2022-10-07 01:00 | 2022-10-07 02:00 | Winter | FALSE | summer
2022-10-07 02:00 | 2022-10-07 03:00 | Winter | FALSE | summer
2022-10-07 03:00 | 2022-10-07 04:00 | Winter | FALSE | summer
2022-10-07 04:00 | 2022-10-07 05:00 | Winter | FALSE | summer
2022-10-07 05:00 | 2022-10-07 06:00 | Winter | FALSE | summer
2022-10-07 06:00 | 2022-10-07 07:00 | Winter | FALSE | summer
2022-10-07 07:00 | 2022-10-07 08:00 | Winter | FALSE | summer
2022-10-07 08:00 | 2022-10-07 09:00 | Winter | FALSE | summer
2022-10-07 09:00 | 2022-10-07 10:00 | Winter | FALSE | summer
2022-10-07 10:00 | 2022-10-07 11:00 | Winter | FALSE | summer
2022-10-07 11:00 | 2022-10-07 12:00 | Winter | FALSE | summer
2022-10-07 12:00 | 2022-10-07 13:00 | Winter | FALSE | summer
2022-10-07 13:00 | 2022-10-07 14:00 | Winter | FALSE | summer
2022-10-07 14:00 | 2022-10-07 15:00 | Winter | FALSE | summer
2022-10-07 15:00 | 2022-10-07 16:00 | Winter | FALSE | summer
2022-10-07 16:00 | 2022-10-07 17:00 | Winter | TRUE | summer
2022-10-07 17:00 | 2022-10-07 18:00 | Winter | TRUE | summer
2022-10-07 18:00 | 2022-10-07 19:00 | Winter | TRUE | summer
2022-10-07 19:00 | 2022-10-07 20:00 | Winter | TRUE | summer
2022-10-07 20:00 | 2022-10-07 21:00 | Winter | TRUE | summer
2022-10-07 21:00 | 2022-10-07 22:00 | Winter | FALSE | summer
2022-10-07 22:00 | 2022-10-07 23:00 | Winter | FALSE | summer
2022-10-07 23:00 | 2022-10-08 | Winter | FALSE | summer
2022-10-08 | 2022-10-08 01:00 | Winter | FALSE | summer
2022-10-08 01:00 | 2022-10-08 02:00 | Winter | FALSE | summer
2022-10-08 02:00 | 2022-10-08 03:00 | Winter | FALSE | summer
2022-10-08 03:00 | 2022-10-08 04:00 | Winter | FALSE | summer
2022-10-08 04:00 | 2022-10-08 05:00 | Winter | FALSE | summer
2022-10-08 05:00 | 2022-10-08 06:00 | Winter | FALSE | summer
2022-10-08 06:00 | 2022-10-08 07:00 | Winter | FALSE | summer
2022-10-08 07:00 | 2022-10-08 08:00 | Winter | FALSE | summer
2022-10-08 08:00 | 2022-10-08 09:00 | Winter | FALSE | summer
2022-10-08 09:00 | 2022-10-08 10:00 | Winter | FALSE | summer
2022-10-08 10:00 | 2022-10-08 11:00 | Winter | FALSE | summer
2022-10-08 11:00 | 2022-10-08 12:00 | Winter | FALSE | summer
2022-10-08 12:00 | 2022-10-08 13:00 | Winter | FALSE | summer
2022-10-08 13:00 | 2022-10-08 14:00 | Winter | FALSE | summer
2022-10-08 14:00 | 2022-10-08 15:00 | Winter | FALSE | summer
2022-10-08 15:00 | 2022-10-08 16:00 | Winter | FALSE | summer
2022-10-08 16:00 | 2022-10-08 17:00 | Winter | TRUE | summer
2022-10-08 17:00 | 2022-10-08 18:00 | Winter | TRUE | summer
2022-10-08 18:00 | 2022-10-08 19:00 | Winter | TRUE | summer
2022-10-08 19:00 | 2022-10-08 20:00 | Winter | TRUE | summer
2022-10-08 20:00 | 2022-10-08 21:00 | Winter | TRUE | summer
2022-10-08 21:00 | 2022-10-08 22:00 | Winter | FALSE | summer
2022-10-08 22:00 | 2022-10-08 23:00 | Winter | FALSE | summer
2022-10-08 23:00 | 2022-10-09 | Winter | FALSE | summer
2022-10-09 | 2022-10-09 01:00 | Winter | FALSE | summer
2022-10-09 01:00 | 2022-10-09 02:00 | Winter | FALSE | summer
2022-10-09 02:00 | 2022-10-09 03:00 | Winter | FALSE | summer
2022-10-09 03:00 | 2022-10-09 04:00 | Winter | FALSE | summer
2022-10-09 04:00 | 2022-10-09 05:00 | Winter | FALSE | summer
2022-10-09 05:00 | 2022-10-09 06:00 | Winter | FALSE | summer
2022-10-09 06:00 | 2022-10-09 07:00 | Winter | FALSE | summer
2022-10-09 07:00 | 2022-10-09 08:00 | Winter | FALSE | summer
2022-10-09 08:00 | 2022-10-09 09:00 | Winter | FALSE | summer
2022-10-09 09:00 | 2022-10-09 10:00 | Winter | FALSE | summer
2022-10-09 10:00 | 2022-10-09 11:00 | Winter | FALSE | summer
2022-10-09 11:00 | 2022-10-09 12:00 | Winter | FALSE | summer
2022-10-09 12:00 | 2022-10-09 13:00 | Winter | FALSE | summer
2022-10-09 13:00 | 2022-10-09 14:00 | Winter | FALSE | summer
2022-10-09 14:00 | 2022-10-09 15:00 | Winter | FALSE | summer
2022-10-09 15:00 | 2022-10-09 16:00 | Winter | FALSE | summer
2022-10-09 16:00 | 2022-10-09 17:00 | Winter | TRUE | summer
2022-10-09 17:00 | 2022-10-09 18:00 | Winter | TRUE | summer
2022-10-09 18:00 | 2022-10-09 19:00 | Winter | TRUE | summer
2022-10-09 19:00 | 2022-10-09 20:00 | Winter | TRUE | summer
2022-10-09 20:00 | 2022-10-09 21:00 | Winter | TRUE | summer
2022-10-09 21:00 | 2022-10-09 22:00 | Winter | FALSE | summer
2022-10-09 22:00 | 2022-10-09 23:00 | Winter | FALSE | summer
2022-10-09 23:00 | 2022-10-10 | Winter | FALSE | summer
2022-10-10 | 2022-10-10 01:00 | Winter | FALSE | summer
2022-10-10 01:00 | 2022-10-10 02:00 | Winter | FALSE | summer
2022-10-10 02:00 | 2022-10-10 03:00 | Winter | FALSE | summer
2022-10-10 03:00 | 2022-10-10 04:00 | Winter | FALSE | summer
2022-10-10 04:00 | 2022-10-10 05:00 | Winter | FALSE | summer
2022-10-10 05:00 | 2022-10-10 06:00 | Winter | FALSE | summer
2022-10-10 06:00 | 2022-10-10 07:00 | Winter | FALSE | summer
2022-10-10 07:00 | 2022-10-10 08:00 | Winter | FALSE | summer
2022-10-10 08:00 | 2022-10-10 09:00 | Winter | FALSE | summer
2022-10-10 09:00 | 2022-10-10 10:00 | Winter | FALSE | summer
2022-10-10 10:00 | 2022-10-10 11:00 | Winter | FALSE | summer
2022-10-10 11:00 | 2022-10-10 12:00 | Winter | FALSE | summer
2022-10-10 12:00 | 2022-10-10 13:00 | Winter | FALSE | summer
2022-10-10 13:00 | 2022-10-10 14:00 | Winter | FALSE | summer
2022-10-10 14:00 | 2022-10-10 15:00 | Winter | FALSE | summer
2022-10-10 15:00 | 2022-10-10 16:00 | Winter | FALSE | summer
2022-10-10 16:00 | 2022-10-10 17:00 | Winter | TRUE | summer
2022-10-10 17:00 | 2022-10-10 18:00 | Winter | TRUE | summer
2022-10-10 18:00 | 2022-10-10 19:00 | Winter | TRUE | summer
2022-10-10 19:00 | 2022-10-10 20:00 | Winter | TRUE | summer
2022-10-10 20:00 | 2022-10-10 21:00 | Winter | TRUE | summer
2022-10-10 21:00 | 2022-10-10 22:00 | Winter | FALSE | summer
2022-10-10 22:00 | 2022-10-10 23:00 | Winter | FALSE | summer
2022-10-10 23:00 | 2022-10-11 | Winter | FALSE | summer
2022-10-11 | 2022-10-11 01:00 | Winter | FALSE | summer
2022-10-11 01:00 | 2022-10-11 02:00 | Winter | FALSE | summer
2022-10-11 02:00 | 2022-10-11 03:00 | Winter | FALSE | summer
2022-10-11 03:00 | 2022-10-11 04:00 | Winter | FALSE | summer
2022-10-11 04:00 | 2022-10-11 05:00 | Winter | FALSE | summer
2022-10-11 05:00 | 2022-10-11 06:00 | Winter | FALSE | summer
2022-10-11 06:00 | 2022-10-11 07:00 | Winter | FALSE | summer
2022-10-11 07:00 | 2022-10-11 08:00 | Winter | FALSE | summer
2022-10-11 08:00 | 2022-10-11 09:00 | Winter | FALSE | summer
2022-10-11 09:00 | 2022-10-11 10:00 | Winter | FALSE | summer
2022-10-11 10:00 | 2022-10-11 11:00 | Winter | FALSE | summer
2022-10-11 11:00 | 2022-10-11 12:00 | Winter | FALSE | summer
2022-10-11 12:00 | 2022-10-11 13:00 | Winter | FALSE | summer
2022-10-11 13:00 | 2022-10-11 14:00 | Winter | FALSE | summer
2022-10-11 14:00 | 2022-10-11 15:00 | Winter | FALSE | summer
2022-10-11 15:00 | 2022-10-11 16:00 | Winter | FALSE | summer
2022-10-11 16:00 | 2022-10-11 17:00 | Winter | TRUE | summer
2022-10-11 17:00 | 2022-10-11 18:00 | Winter | TRUE | summer
2022-10-11 18:00 | 2022-10-11 19:00 | Winter | TRUE | summer
2022-10-11 19:00 | 2022-10-11 20:00 | Winter | TRUE | summer
2022-10-11 20:00 | 2022-10-11 21:00 | Winter | TRUE | summer
2022-10-11 21:00 | 2022-10-11 22:00 | Winter | FALSE | summer
2022-10-11 22:00 | 2022-10-11 23:00 | Winter | FALSE | summer
2022-10-11 23:00 | 2022-10-12 | Winter | FALSE | summer
2022-10-12 | 2022-10-12 01:00 | Winter | FALSE | summer
2022-10-12 01:00 | 2022-10-12 02:00 | Winter | FALSE | summer
2022-10-12 02:00 | 2022-10-12 03:00 | Winter | FALSE | summer
2022-10-12 03:00 | 2022-10-12 04:00 | Winter | FALSE | summer
2022-10-12 04:00 | 2022-10-12 05:00 | Winter | FALSE | summer
2022-10-12 05:00 | 2022-10-12 06:00 | Winter | FALSE | summer
2022-10-12 06:00 | 2022-10-12 07:00 | Winter | FALSE | summer
2022-10-12 07:00 | 2022-10-12 08:00 | Winter | FALSE | summer
2022-10-12 08:00 | 2022-10-12 09:00 | Winter | FALSE | summer
2022-10-12 09:00 | 2022-10-12 10:00 | Winter | FALSE | summer
2022-10-12 10:00 | 2022-10-12 11:00 | Winter | FALSE | summer
2022-10-12 11:00 | 2022-10-12 12:00 | Winter | FALSE | summer
2022-10-12 12:00 | 2022-10-12 13:00 | Winter | FALSE | summer
2022-10-12 13:00 | 2022-10-12 14:00 | Winter | FALSE | summer
2022-10-12 14:00 | 2022-10-12 15:00 | Winter | FALSE | summer
2022-10-12 15:00 | 2022-10-12 16:00 | Winter | FALSE | summer
2022-10-12 16:00 | 2022-10-12 17:00 | Winter | TRUE | summer
2022-10-12 17:00 | 2022-10-12 18:00 | Winter | TRUE | summer
2022-10-12 18:00 | 2022-10-12 19:00 | Winter | TRUE | summer
2022-10-12 19:00 | 2022-10-12 20:00 | Winter | TRUE | summer
2022-10-12 20:00 | 2022-10-12 21:00 | Winter | TRUE | summer
2022-10-12 21:00 | 2022-10-12 22:00 | Winter | FALSE | summer
2022-10-12 22:00 | 2022-10-12 23:00 | Winter | FALSE | summer
2022-10-12 23:00 | 2022-10-13 | Winter | FALSE | summer
2022-10-13 | 2022-10-13 01:00 | Winter | FALSE | summer
2022-10-13 01:00 | 2022-10-13 02:00 | Winter | FALSE | summer
2022-10-13 02:00 | 2022-10-13 03:00 | Winter | FALSE | summer
2022-10-13 03:00 | 2022-10-13 04:00 | Winter | FALSE | summer
2022-10-13 04:00 | 2022-10-13 05:00 | Winter | FALSE | summer
2022-10-13 05:00 | 2022-10-13 06:00 | Winter | FALSE | summer
2022-10-13 06:00 | 2022-10-13 07:00 | Winter | FALSE | summer
2022-10-13 07:00 | 2022-10-13 08:00 | Winter | FALSE | summer
2022-10-13 08:00 | 2022-10-13 09:00 | Winter | FALSE | summer
2022-10-13 09:00 | 2022-10-13 10:00 | Winter | FALSE | summer
2022-10-13 10:00 | 2022-10-13 11:00 | Winter | FALSE | summer
2022-10-13 11:00 | 2022-10-13 12:00 | Winter | FALSE | summer
2022-10-13 12:00 | 2022-10-13 13:00 | Winter | FALSE | summer
2022-10-13 13:00 | 2022-10-13 14:00 | Winter | FALSE | summer
2022-10-13 14:00 | 2022-10-13 15:00 | Winter | FALSE | summer
2022-10-13 15:00 | 2022-10-13 16:00 | Winter | FALSE | summer
2022-10-13 16:00 | 2022-10-13 17:00 | Winter | TRUE | summer
2022-10-13 17:00 | 2022-10-13 18:00 | Winter | TRUE | summer
2022-10-13 18:00 | 2022-10-13 19:00 | Winter | TRUE | summer
2022-10-13 19:00 | 2022-10-13 20:00 | Winter | TRUE | summer
2022-10-13 20:00 | 2022-10-13 21:00 | Winter | TRUE | summer
2022-10-13 21:00 | 2022-10-13 22:00 | Winter | FALSE | summer
2022-10-13 22:00 | 2022-10-13 23:00 | Winter | FALSE | summer
2022-10-13 23:00 | 2022-10-14 | Winter | FALSE | summer
2022-10-14 | 2022-10-14 01:00 | Winter | FALSE | summer
2022-10-14 01:00 | 2022-10-14 02:00 | Winter | FALSE | summer
2022-10-14 02:00 | 2022-10-14 03:00 | Winter | FALSE | summer
2022-10-14 03:00 | 2022-10-14 04:00 | Winter | FALSE | summer
2022-10-14 04:00 | 2022-10-14 05:00 | Winter | FALSE | summer
2022-10-14 05:00 | 2022-10-14 06:00 | Winter | FALSE | summer
2022-10-14 06:00 | 2022-10-14 07:00 | Winter | FALSE | summer
2022-10-14 07:00 | 2022-10-14 08:00 | Winter | FALSE | summer
2022-10-14 08:00 | 2022-10-14 09:00 | Winter | FALSE | summer
2022-10-14 09:00 | 2022-10-14 10:00 | Winter | FALSE | summer
2022-10-14 10:00 | 2022-10-14 11:00 | Winter | FALSE | summer
2022-10-14 11:00 | 2022-10-14 12:00 | Winter | FALSE | summer
2022-10-14 12:00 | 2022-10-14 13:00 | Winter | FALSE | summer
2022-10-14 13:00 | 2022-10-14 14:00 | Winter | FALSE | summer
2022-10-14 14:00 | 2022-10-14 15:00 | Winter | FALSE | summer
2022-10-14 15:00 | 2022-10-14 16:00 | Winter | FALSE | summer
2022-10-14 16:00 | 2022-10-14 17:00 | Winter | TRUE | summer
2022-10-14 17:00 | 2022-10-14 18:00 | Winter | TRUE | summer
2022-10-14 18:00 | 2022-10-14 19:00 | Winter | TRUE | summer
2022-10-14 19:00 | 2022-10-14 20:00 | Winter | TRUE | summer
2022-10-14 20:00 | 2022-10-14 21:00 | Winter | TRUE | summer
2022-10-14 21:00 | 2022-10-14 22:00 | Winter | FALSE | summer
2022-10-14 22:00 | 2022-10-14 23:00 | Winter | FALSE | summer
2022-10-14 23:00 | 2022-10-15 | Winter | FALSE | summer
2022-10-15 | 2022-10-15 01:00 | Winter | FALSE | summer
2022-10-15 01:00 | 2022-10-15 02:00 | Winter | FALSE | summer
2022-10-15 02:00 | 2022-10-15 03:00 | Winter | FALSE | summer
2022-10-15 03:00 | 2022-10-15 04:00 | Winter | FALSE | summer
2022-10-15 04:00 | 2022-10-15 05:00 | Winter | FALSE | summer
2022-10-15 05:00 | 2022-10-15 06:00 | Winter | FALSE | summer
2022-10-15 06:00 | 2022-10-15 07:00 | Winter | FALSE | summer
2022-10-15 07:00 | 2022-10-15 08:00 | Winter | FALSE | summer
2022-10-15 08:00 | 2022-10-15 09:00 | Winter | FALSE | summer
2022-10-15 09:00 | 2022-10-15 10:00 | Winter | FALSE | summer
2022-10-15 10:00 | 2022-10-15 11:00 | Winter | FALSE | summer
2022-10-15 11:00 | 2022-10-15 12:00 | Winter | FALSE | summer
2022-10-15 12:00 | 2022-10-15 13:00 | Winter | FALSE | summer
2022-10-15 13:00 | 2022-10-15 14:00 | Winter | FALSE | summer
2022-10-15 14:00 | 2022-10-15 15:00 | Winter | FALSE | summer
2022-10-15 15:00 | 2022-10-15 16:00 | Winter | FALSE | summer
2022-10-15 16:00 | 2022-10-15 17:00 | Winter | TRUE | summer
2022-10-15 17:00 | 2022-10-15 18:00 | Winter | TRUE | summer
2022-10-15 18:00 | 2022-10-15 19:00 | Winter | TRUE | summer
2022-10-15 19:00 | 2022-10-15 20:00 | Winter | TRUE | summer
2022-10-15 20:00 | 2022-10-15 21:00 | Winter | TRUE | summer
2022-10-15 21:00 | 2022-10-15 22:00 | Winter | FALSE | summer
2022-10-15 22:00 | 2022-10-15 23:00 | Winter | FALSE | summer
2022-10-15 23:00 | 2022-10-16 | Winter | FALSE | summer
2022-10-16 | 2022-10-16 01:00 | Winter | FALSE | summer
2022-10-16 01:00 | 2022-10-16 02:00 | Winter | FALSE | summer
2022-10-16 02:00 | 2022-10-16 03:00 | Winter | FALSE | summer
2022-10-16 03:00 | 2022-10-16 04:00 | Winter | FALSE | summer
2022-10-16 04:00 | 2022-10-16 05:00 | Winter | FALSE | summer
2022-10-16 05:00 | 2022-10-16 06:00 | Winter | FALSE | summer
2022-10-16 06:00 | 2022-10-16 07:00 | Winter | FALSE | summer
2022-10-16 07:00 | 2022-10-16 08:00 | Winter | FALSE | summer
2022-10-16 08:00 | 2022-10-16 09:00 | Winter | FALSE | summer
2022-10-16 09:00 | 2022-10-16 10:00 | Winter | FALSE | summer
2022-10-16 10:00 | 2022-10-16 11:00 | Winter | FALSE | summer
2022-10-16 11:00 | 2022-10-16 12:00 | Winter | FALSE | summer
2022-10-16 12:00 | 2022-10-16 13:00 | Winter | FALSE | summer
2022-10-16 13:00 | 2022-10-16 14:00 | Winter | FALSE | summer
2022-10-16 14:00 | 2022-10-16 15:00 | Winter | FALSE | summer
2022-10-16 15:00 | 2022-10-16 16:00 | Winter | FALSE | summer
2022-10-16 16:00 | 2022-10-16 17:00 | Winter | TRUE | summer
2022-10-16 17:00 | 2022-10-16 18:00 | Winter | TRUE | summer
2022-10-16 18:00 | 2022-10-16 19:00 | Winter | TRUE | summer
2022-10-16 19:00 | 2022-10-16 20:00 | Winter | TRUE | summer
2022-10-16 20:00 | 2022-10-16 21:00 | Winter | TRUE | summer
2022-10-16 21:00 | 2022-10-16 22:00 | Winter | FALSE | summer
2022-10-16 22:00 | 2022-10-16 23:00 | Winter | FALSE | summer
2022-10-16 23:00 | 2022-10-17 | Winter | FALSE | summer
2022-10-17 | 2022-10-17 01:00 | Winter | FALSE | summer
2022-10-17 01:00 | 2022-10-17 02:00 | Winter | FALSE | summer
2022-10-17 02:00 | 2022-10-17 03:00 | Winter | FALSE | summer
2022-10-17 03:00 | 2022-10-17 04:00 | Winter | FALSE | summer
2022-10-17 04:00 | 2022-10-17 05:00 | Winter | FALSE | summer
2022-10-17 05:00 | 2022-10-17 06:00 | Winter | FALSE | summer
2022-10-17 06:00 | 2022-10-17 07:00 | Winter | FALSE | summer
2022-10-17 07:00 | 2022-10-17 08:00 | Winter | FALSE | summer
2022-10-17 08:00 | 2022-10-17 09:00 | Winter | FALSE | summer
2022-10-17 09:00 | 2022-10-17 10:00 | Winter | FALSE | summer
2022-10-17 10:00 | 2022-10-17 11:00 | Winter | FALSE | summer
2022-10-17 11:00 | 2022-10-17 12:00 | Winter | FALSE | summer
2022-10-17 12:00 | 2022-10-17 13:00 | Winter | FALSE | summer
2022-10-17 13:00 | 2022-10-17 14:00 | Winter | FALSE | summer
2022-10-17 14:00 | 2022-10-17 15:00 | Winter | FALSE | summer
2022-10-17 15:00 | 2022-10-17 16:00 | Winter | FALSE | summer
2022-10-17 16:00 | 2022-10-17 17:00 | Winter | TRUE | summer
2022-10-17 17:00 | 2022-10-17 18:00 | Winter | TRUE | summer
2022-10-17 18:00 | 2022-10-17 19:00 | Winter | TRUE | summer
2022-10-17 19:00 | 2022-10-17 20:00 | Winter | TRUE | summer
2022-10-17 20:00 | 2022-10-17 21:00 | Winter | TRUE | summer
2022-10-17 21:00 | 2022-10-17 22:00 | Winter | FALSE | summer
2022-10-17 22:00 | 2022-10-17 23:00 | Winter | FALSE | summer
2022-10-17 23:00 | 2022-10-18 | Winter | FALSE | summer
2022-10-18 | 2022-10-18 01:00 | Winter | FALSE | summer
2022-10-18 01:00 | 2022-10-18 02:00 | Winter | FALSE | summer
2022-10-18 02:00 | 2022-10-18 03:00 | Winter | FALSE | summer
2022-10-18 03:00 | 2022-10-18 04:00 | Winter | FALSE | summer
2022-10-18 04:00 | 2022-10-18 05:00 | Winter | FALSE | summer
2022-10-18 05:00 | 2022-10-18 06:00 | Winter | FALSE | summer
2022-10-18 06:00 | 2022-10-18 07:00 | Winter | FALSE | summer
2022-10-18 07:00 | 2022-10-18 08:00 | Winter | FALSE | summer
2022-10-18 08:00 | 2022-10-18 09:00 | Winter | FALSE | summer
2022-10-18 09:00 | 2022-10-18 10:00 | Winter | FALSE | summer
2022-10-18 10:00 | 2022-10-18 11:00 | Winter | FALSE | summer
2022-10-18 11:00 | 2022-10-18 12:00 | Winter | FALSE | summer
2022-10-18 12:00 | 2022-10-18 13:00 | Winter | FALSE | summer
2022-10-18 13:00 | 2022-10-18 14:00 | Winter | FALSE | summer
2022-10-18 14:00 | 2022-10-18 15:00 | Winter | FALSE | summer
2022-10-18 15:00 | 2022-10-18 16:00 | Winter | FALSE | summer
2022-10-18 16:00 | 2022-10-18 17:00 | Winter | TRUE | summer
2022-10-18 17:00 | 2022-10-18 18:00 | Winter | TRUE | summer
2022-10-18 18:00 | 2022-10-18 19:00 | Winter | TRUE | summer
2022-10-18 19:00 | 2022-10-18 20:00 | Winter | TRUE | summer
2022-10-18 20:00 | 2022-10-18 21:00 | Winter | TRUE | summer
2022-10-18 21:00 | 2022-10-18 22:00 | Winter | FALSE | summer
2022-10-18 22:00 | 2022-10-18 23:00 | Winter | FALSE | summer
2022-10-18 23:00 | 2022-10-19 | Winter | FALSE | summer
2022-10-19 | 2022-10-19 01:00 | Winter | FALSE | summer
2022-10-19 01:00 | 2022-10-19 02:00 | Winter | FALSE | summer
2022-10-19 02:00 | 2022-10-19 03:00 | Winter | FALSE | summer
2022-10-19 03:00 | 2022-10-19 04:00 | Winter | FALSE | summer
2022-10-19 04:00 | 2022-10-19 05:00 | Winter | FALSE | summer
2022-10-19 05:00 | 2022-10-19 06:00 | Winter | FALSE | summer
2022-10-19 06:00 | 2022-10-19 07:00 | Winter | FALSE | summer
2022-10-19 07:00 | 2022-10-19 08:00 | Winter | FALSE | summer
2022-10-19 08:00 | 2022-10-19 09:00 | Winter | FALSE | summer
2022-10-19 09:00 | 2022-10-19 10:00 | Winter | FALSE | summer
2022-10-19 10:00 | 2022-10-19 11:00 | Winter | FALSE | summer
2022-10-19 11:00 | 2022-10-19 12:00 | Winter | FALSE | summer
2022-10-19 12:00 | 2022-10-19 13:00 | Winter | FALSE | summer
2022-10-19 13:00 | 2022-10-19 14:00 | Winter | FALSE | summer
2022-10-19 14:00 | 2022-10-19 15:00 | Winter | FALSE | summer
2022-10-19 15:00 | 2022-10-19 16:00 | Winter | FALSE | summer
2022-10-19 16:00 | 2022-10-19 17:00 | Winter | TRUE | summer
2022-10-19 17:00 | 2022-10-19 18:00 | Winter | TRUE | summer
2022-10-19 18:00 | 2022-10-19 19:00 | Winter | TRUE | summer
2022-10-19 19:00 | 2022-10-19 20:00 | Winter | TRUE | summer
2022-10-19 20:00 | 2022-10-19 21:00 | Winter | TRUE | summer
2022-10-19 21:00 | 2022-10-19 22:00 | Winter | FALSE | summer
2022-10-19 22:00 | 2022-10-19 23:00 | Winter | FALSE | summer
2022-10-19 23:00 | 2022-10-20 | Winter | FALSE | summer
2022-10-20 | 2022-10-20 01:00 | Winter | FALSE | summer
2022-10-20 01:00 | 2022-10-20 02:00 | Winter | FALSE | summer
2022-10-20 02:00 | 2022-10-20 03:00 | Winter | FALSE | summer
2022-10-20 03:00 | 2022-10-20 04:00 | Winter | FALSE | summer
2022-10-20 04:00 | 2022-10-20 05:00 | Winter | FALSE | summer
2022-10-20 05:00 | 2022-10-20 06:00 | Winter | FALSE | summer
2022-10-20 06:00 | 2022-10-20 07:00 | Winter | FALSE | summer
2022-10-20 07:00 | 2022-10-20 08:00 | Winter | FALSE | summer
2022-10-20 08:00 | 2022-10-20 09:00 | Winter | FALSE | summer
2022-10-20 09:00 | 2022-10-20 10:00 | Winter | FALSE | summer
2022-10-20 10:00 | 2022-10-20 11:00 | Winter | FALSE | summer
2022-10-20 11:00 | 2022-10-20 12:00 | Winter | FALSE | summer
2022-10-20 12:00 | 2022-10-20 13:00 | Winter | FALSE | summer
2022-10-20 13:00 | 2022-10-20 14:00 | Winter | FALSE | summer
2022-10-20 14:00 | 2022-10-20 15:00 | Winter | FALSE | summer
2022-10-20 15:00 | 2022-10-20 16:00 | Winter | FALSE | summer
2022-10-20 16:00 | 2022-10-20 17:00 | Winter | TRUE | summer
2022-10-20 17:00 | 2022-10-20 18:00 | Winter | TRUE | summer
2022-10-20 18:00 | 2022-10-20 19:00 | Winter | TRUE | summer
2022-10-20 19:00 | 2022-10-20 20:00 | Winter | TRUE | summer
2022-10-20 20:00 | 2022-10-20 21:00 | Winter | TRUE | summer
2022-10-20 21:00 | 2022-10-20 22:00 | Winter | FALSE | summer
2022-10-20 22:00 | 2022-10-20 23:00 | Winter | FALSE | summer
2022-10-20 23:00 | 2022-10-21 | Winter | FALSE | summer
2022-10-21 | 2022-10-21 01:00 | Winter | FALSE | summer
2022-10-21 01:00 | 2022-10-21 02:00 | Winter | FALSE | summer
2022-10-21 02:00 | 2022-10-21 03:00 | Winter | FALSE | summer
2022-10-21 03:00 | 2022-10-21 04:00 | Winter | FALSE | summer
2022-10-21 04:00 | 2022-10-21 05:00 | Winter | FALSE | summer
2022-10-21 05:00 | 2022-10-21 06:00 | Winter | FALSE | summer
2022-10-21 06:00 | 2022-10-21 07:00 | Winter | FALSE | summer
2022-10-21 07:00 | 2022-10-21 08:00 | Winter | FALSE | summer
2022-10-21 08:00 | 2022-10-21 09:00 | Winter | FALSE | summer
2022-10-21 09:00 | 2022-10-21 10:00 | Winter | FALSE | summer
2022-10-21 10:00 | 2022-10-21 11:00 | Winter | FALSE | summer
2022-10-21 11:00 | 2022-10-21 12:00 | Winter | FALSE | summer
2022-10-21 12:00 | 2022-10-21 13:00 | Winter | FALSE | summer
2022-10-21 13:00 | 2022-10-21 14:00 | Winter | FALSE | summer
2022-10-21 14:00 | 2022-10-21 15:00 | Winter | FALSE | summer
2022-10-21 15:00 | 2022-10-21 16:00 | Winter | FALSE | summer
2022-10-21 16:00 | 2022-10-21 17:00 | Winter | TRUE | summer
2022-10-21 17:00 | 2022-10-21 18:00 | Winter | TRUE | summer
2022-10-21 18:00 | 2022-10-21 19:00 | Winter | TRUE | summer
2022-10-21 19:00 | 2022-10-21 20:00 | Winter | TRUE | summer
2022-10-21 20:00 | 2022-10-21 21:00 | Winter | TRUE | summer
2022-10-21 21:00 | 2022-10-21 22:00 | Winter | FALSE | summer
2022-10-21 22:00 | 2022-10-21 23:00 | Winter | FALSE | summer
2022-10-21 23:00 | 2022-10-22 | Winter | FALSE | summer
2022-10-22 | 2022-10-22 01:00 | Winter | FALSE | summer
2022-10-22 01:00 | 2022-10-22 02:00 | Winter | FALSE | summer
2022-10-22 02:00 | 2022-10-22 03:00 | Winter | FALSE | summer
2022-10-22 03:00 | 2022-10-22 04:00 | Winter | FALSE | summer
2022-10-22 04:00 | 2022-10-22 05:00 | Winter | FALSE | summer
2022-10-22 05:00 | 2022-10-22 06:00 | Winter | FALSE | summer
2022-10-22 06:00 | 2022-10-22 07:00 | Winter | FALSE | summer
2022-10-22 07:00 | 2022-10-22 08:00 | Winter | FALSE | summer
2022-10-22 08:00 | 2022-10-22 09:00 | Winter | FALSE | summer
2022-10-22 09:00 | 2022-10-22 10:00 | Winter | FALSE | summer
2022-10-22 10:00 | 2022-10-22 11:00 | Winter | FALSE | summer
2022-10-22 11:00 | 2022-10-22 12:00 | Winter | FALSE | summer
2022-10-22 12:00 | 2022-10-22 13:00 | Winter | FALSE | summer
2022-10-22 13:00 | 2022-10-22 14:00 | Winter | FALSE | summer
2022-10-22 14:00 | 2022-10-22 15:00 | Winter | FALSE | summer
2022-10-22 15:00 | 2022-10-22 16:00 | Winter | FALSE | summer
2022-10-22 16:00 | 2022-10-22 17:00 | Winter | TRUE | summer
2022-10-22 17:00 | 2022-10-22 18:00 | Winter | TRUE | summer
2022-10-22 18:00 | 2022-10-22 19:00 | Winter | TRUE | summer
2022-10-22 19:00 | 2022-10-22 20:00 | Winter | TRUE | summer
2022-10-22 20:00 | 2022-10-22 21:00 | Winter | TRUE | summer
2022-10-22 21:00 | 2022-10-22 22:00 | Winter | FALSE | summer
2022-10-22 22:00 | 2022-10-22 23:00 | Winter | FALSE | summer
2022-10-22 23:00 | 2022-10-23 | Winter | FALSE | summer
2022-10-23 | 2022-10-23 01:00 | Winter | FALSE | summer
2022-10-23 01:00 | 2022-10-23 02:00 | Winter | FALSE | summer
2022-10-23 02:00 | 2022-10-23 03:00 | Winter | FALSE | summer
2022-10-23 03:00 | 2022-10-23 04:00 | Winter | FALSE | summer
2022-10-23 04:00 | 2022-10-23 05:00 | Winter | FALSE | summer
2022-10-23 05:00 | 2022-10-23 06:00 | Winter | FALSE | summer
2022-10-23 06:00 | 2022-10-23 07:00 | Winter | FALSE | summer
2022-10-23 07:00 | 2022-10-23 08:00 | Winter | FALSE | summer
2022-10-23 08:00 | 2022-10-23 09:00 | Winter | FALSE | summer
2022-10-23 09:00 | 2022-10-23 10:00 | Winter | FALSE | summer
2022-10-23 10:00 | 2022-10-23 11:00 | Winter | FALSE | summer
2022-10-23 11:00 | 2022-10-23 12:00 | Winter | FALSE | summer
2022-10-23 12:00 | 2022-10-23 13:00 | Winter | FALSE | summer
2022-10-23 13:00 | 2022-10-23 14:00 | Winter | FALSE | summer
2022-10-23 14:00 | 2022-10-23 15:00 | Winter | FALSE | summer
2022-10-23 15:00 | 2022-10-23 16:00 | Winter | FALSE | summer
2022-10-23 16:00 | 2022-10-23 17:00 | Winter | TRUE | summer
2022-10-23 17:00 | 2022-10-23 18:00 | Winter | TRUE | summer
2022-10-23 18:00 | 2022-10-23 19:00 | Winter | TRUE | summer
2022-10-23 19:00 | 2022-10-23 20:00 | Winter | TRUE | summer
2022-10-23 20:00 | 2022-10-23 21:00 | Winter | TRUE | summer
2022-10-23 21:00 | 2022-10-23 22:00 | Winter | FALSE | summer
2022-10-23 22:00 | 2022-10-23 23:00 | Winter | FALSE | summer
2022-10-23 23:00 | 2022-10-24 | Winter | FALSE | summer
2022-10-24 | 2022-10-24 01:00 | Winter | FALSE | summer
2022-10-24 01:00 | 2022-10-24 02:00 | Winter | FALSE | summer
2022-10-24 02:00 | 2022-10-24 03:00 | Winter | FALSE | summer
2022-10-24 03:00 | 2022-10-24 04:00 | Winter | FALSE | summer
2022-10-24 04:00 | 2022-10-24 05:00 | Winter | FALSE | summer
2022-10-24 05:00 | 2022-10-24 06:00 | Winter | FALSE | summer
2022-10-24 06:00 | 2022-10-24 07:00 | Winter | FALSE | summer
2022-10-24 07:00 | 2022-10-24 08:00 | Winter | FALSE | summer
2022-10-24 08:00 | 2022-10-24 09:00 | Winter | FALSE | summer
2022-10-24 09:00 | 2022-10-24 10:00 | Winter | FALSE | summer
2022-10-24 10:00 | 2022-10-24 11:00 | Winter | FALSE | summer
2022-10-24 11:00 | 2022-10-24 12:00 | Winter | FALSE | summer
2022-10-24 12:00 | 2022-10-24 13:00 | Winter | FALSE | summer
2022-10-24 13:00 | 2022-10-24 14:00 | Winter | FALSE | summer
2022-10-24 14:00 | 2022-10-24 15:00 | Winter | FALSE | summer
2022-10-24 15:00 | 2022-10-24 16:00 | Winter | FALSE | summer
2022-10-24 16:00 | 2022-10-24 17:00 | Winter | TRUE | summer
2022-10-24 17:00 | 2022-10-24 18:00 | Winter | TRUE | summer
2022-10-24 18:00 | 2022-10-24 19:00 | Winter | TRUE | summer
2022-10-24 19:00 | 2022-10-24 20:00 | Winter | TRUE | summer
2022-10-24 20:00 | 2022-10-24 21:00 | Winter | TRUE | summer
2022-10-24 21:00 | 2022-10-24 22:00 | Winter | FALSE | summer
2022-10-24 22:00 | 2022-10-24 23:00 | Winter | FALSE | summer
2022-10-24 23:00 | 2022-10-25 | Winter | FALSE | summer
2022-10-25 | 2022-10-25 01:00 | Winter | FALSE | summer
2022-10-25 01:00 | 2022-10-25 02:00 | Winter | FALSE | summer
2022-10-25 02:00 | 2022-10-25 03:00 | Winter | FALSE | summer
2022-10-25 03:00 | 2022-10-25 04:00 | Winter | FALSE | summer
2022-10-25 04:00 | 2022-10-25 05:00 | Winter | FALSE | summer
2022-10-25 05:00 | 2022-10-25 06:00 | Winter | FALSE | summer
2022-10-25 06:00 | 2022-10-25 07:00 | Winter | FALSE | summer
2022-10-25 07:00 | 2022-10-25 08:00 | Winter | FALSE | summer
2022-10-25 08:00 | 2022-10-25 09:00 | Winter | FALSE | summer
2022-10-25 09:00 | 2022-10-25 10:00 | Winter | FALSE | summer
2022-10-25 10:00 | 2022-10-25 11:00 | Winter | FALSE | summer
2022-10-25 11:00 | 2022-10-25 12:00 | Winter | FALSE | summer
2022-10-25 12:00 | 2022-10-25 13:00 | Winter | FALSE | summer
2022-10-25 13:00 | 2022-10-25 14:00 | Winter | FALSE | summer
2022-10-25 14:00 | 2022-10-25 15:00 | Winter | FALSE | summer
2022-10-25 15:00 | 2022-10-25 16:00 | Winter | FALSE | summer
2022-10-25 16:00 | 2022-10-25 17:00 | Winter | TRUE | summer
2022-10-25 17:00 | 2022-10-25 18:00 | Winter | TRUE | summer
2022-10-25 18:00 | 2022-10-25 19:00 | Winter | TRUE | summer
2022-10-25 19:00 | 2022-10-25 20:00 | Winter | TRUE | summer
2022-10-25 20:00 | 2022-10-25 21:00 | Winter | TRUE | summer
2022-10-25 21:00 | 2022-10-25 22:00 | Winter | FALSE | summer
2022-10-25 22:00 | 2022-10-25 23:00 | Winter | FALSE | summer
2022-10-25 23:00 | 2022-10-26 | Winter | FALSE | summer
2022-10-26 | 2022-10-26 01:00 | Winter | FALSE | summer
2022-10-26 01:00 | 2022-10-26 02:00 | Winter | FALSE | summer
2022-10-26 02:00 | 2022-10-26 03:00 | Winter | FALSE | summer
2022-10-26 03:00 | 2022-10-26 04:00 | Winter | FALSE | summer
2022-10-26 04:00 | 2022-10-26 05:00 | Winter | FALSE | summer
2022-10-26 05:00 | 2022-10-26 06:00 | Winter | FALSE | summer
2022-10-26 06:00 | 2022-10-26 07:00 | Winter | FALSE | summer
2022-10-26 07:00 | 2022-10-26 08:00 | Winter | FALSE | summer
2022-10-26 08:00 | 2022-10-26 09:00 | Winter | FALSE | summer
2022-10-26 09:00 | 2022-10-26 10:00 | Winter | FALSE | summer
2022-10-26 10:00 | 2022-10-26 11:00 | Winter | FALSE | summer
2022-10-26 11:00 | 2022-10-26 12:00 | Winter | FALSE | summer
2022-10-26 12:00 | 2022-10-26 13:00 | Winter | FALSE | summer
2022-10-26 13:00 | 2022-10-26 14:00 | Winter | FALSE | summer
2022-10-26 14:00 | 2022-10-26 15:00 | Winter | FALSE | summer
2022-10-26 15:00 | 2022-10-26 16:00 | Winter | FALSE | summer
2022-10-26 16:00 | 2022-10-26 17:00 | Winter | TRUE | summer
2022-10-26 17:00 | 2022-10-26 18:00 | Winter | TRUE | summer
2022-10-26 18:00 | 2022-10-26 19:00 | Winter | TRUE | summer
2022-10-26 19:00 | 2022-10-26 20:00 | Winter | TRUE | summer
2022-10-26 20:00 | 2022-10-26 21:00 | Winter | TRUE | summer
2022-10-26 21:00 | 2022-10-26 22:00 | Winter | FALSE | summer
2022-10-26 22:00 | 2022-10-26 23:00 | Winter | FALSE | summer
2022-10-26 23:00 | 2022-10-27 | Winter | FALSE | summer
2022-10-27 | 2022-10-27 01:00 | Winter | FALSE | summer
2022-10-27 01:00 | 2022-10-27 02:00 | Winter | FALSE | summer
2022-10-27 02:00 | 2022-10-27 03:00 | Winter | FALSE | summer
2022-10-27 03:00 | 2022-10-27 04:00 | Winter | FALSE | summer
2022-10-27 04:00 | 2022-10-27 05:00 | Winter | FALSE | summer
2022-10-27 05:00 | 2022-10-27 06:00 | Winter | FALSE | summer
2022-10-27 06:00 | 2022-10-27 07:00 | Winter | FALSE | summer
2022-10-27 07:00 | 2022-10-27 08:00 | Winter | FALSE | summer
2022-10-27 08:00 | 2022-10-27 09:00 | Winter | FALSE | summer
2022-10-27 09:00 | 2022-10-27 10:00 | Winter | FALSE | summer
2022-10-27 10:00 | 2022-10-27 11:00 | Winter | FALSE | summer
2022-10-27 11:00 | 2022-10-27 12:00 | Winter | FALSE | summer
2022-10-27 12:00 | 2022-10-27 13:00 | Winter | FALSE | summer
2022-10-27 13:00 | 2022-10-27 14:00 | Winter | FALSE | summer
2022-10-27 14:00 | 2022-10-27 15:00 | Winter | FALSE | summer
2022-10-27 15:00 | 2022-10-27 16:00 | Winter | FALSE | summer
2022-10-27 16:00 | 2022-10-27 17:00 | Winter | TRUE | summer
2022-10-27 17:00 | 2022-10-27 18:00 | Winter | TRUE | summer
2022-10-27 18:00 | 2022-10-27 19:00 | Winter | TRUE | summer
2022-10-27 19:00 | 2022-10-27 20:00 | Winter | TRUE | summer
2022-10-27 20:00 | 2022-10-27 21:00 | Winter | TRUE | summer
2022-10-27 21:00 | 2022-10-27 22:00 | Winter | FALSE | summer
2022-10-27 22:00 | 2022-10-27 23:00 | Winter | FALSE | summer
2022-10-27 23:00 | 2022-10-28 | Winter | FALSE | summer
2022-10-28 | 2022-10-28 01:00 | Winter | FALSE | summer
2022-10-28 01:00 | 2022-10-28 02:00 | Winter | FALSE | summer
2022-10-28 02:00 | 2022-10-28 03:00 | Winter | FALSE | summer
2022-10-28 03:00 | 2022-10-28 04:00 | Winter | FALSE | summer
2022-10-28 04:00 | 2022-10-28 05:00 | Winter | FALSE | summer
2022-10-28 05:00 | 2022-10-28 06:00 | Winter | FALSE | summer
2022-10-28 06:00 | 2022-10-28 07:00 | Winter | FALSE | summer
2022-10-28 07:00 | 2022-10-28 08:00 | Winter | FALSE | summer
2022-10-28 08:00 | 2022-10-28 09:00 | Winter | FALSE | summer
2022-10-28 09:00 | 2022-10-28 10:00 | Winter | FALSE | summer
2022-10-28 10:00 | 2022-10-28 11:00 | Winter | FALSE | summer
2022-10-28 11:00 | 2022-10-28 12:00 | Winter | FALSE | summer
2022-10-28 12:00 | 2022-10-28 13:00 | Winter | FALSE | summer
2022-10-28 13:00 | 2022-10-28 14:00 | Winter | FALSE | summer
2022-10-28 14:00 | 2022-10-28 15:00 | Winter | FALSE | summer
2022-10-28 15:00 | 2022-10-28 16:00 | Winter | FALSE | summer
2022-10-28 16:00 | 2022-10-28 17:00 | Winter | TRUE | summer
2022-10-28 17:00 | 2022-10-28 18:00 | Winter | TRUE | summer
2022-10-28 18:00 | 2022-10-28 19:00 | Winter | TRUE | summer
2022-10-28 19:00 | 2022-10-28 20:00 | Winter | TRUE | summer
2022-10-28 20:00 | 2022-10-28 21:00 | Winter | TRUE | summer
2022-10-28 21:00 | 2022-10-28 22:00 | Winter | FALSE | summer
2022-10-28 22:00 | 2022-10-28 23:00 | Winter | FALSE | summer
2022-10-28 23:00 | 2022-10-29 | Winter | FALSE | summer
2022-10-29 | 2022-10-29 01:00 | Winter | FALSE | summer
2022-10-29 01:00 | 2022-10-29 02:00 | Winter | FALSE | summer
2022-10-29 02:00 | 2022-10-29 03:00 | Winter | FALSE | summer
2022-10-29 03:00 | 2022-10-29 04:00 | Winter | FALSE | summer
2022-10-29 04:00 | 2022-10-29 05:00 | Winter | FALSE | summer
2022-10-29 05:00 | 2022-10-29 06:00 | Winter | FALSE | summer
2022-10-29 06:00 | 2022-10-29 07:00 | Winter | FALSE | summer
2022-10-29 07:00 | 2022-10-29 08:00 | Winter | FALSE | summer
2022-10-29 08:00 | 2022-10-29 09:00 | Winter | FALSE | summer
2022-10-29 09:00 | 2022-10-29 10:00 | Winter | FALSE | summer
2022-10-29 10:00 | 2022-10-29 11:00 | Winter | FALSE | summer
2022-10-29 11:00 | 2022-10-29 12:00 | Winter | FALSE | summer
2022-10-29 12:00 | 2022-10-29 13:00 | Winter | FALSE | summer
2022-10-29 13:00 | 2022-10-29 14:00 | Winter | FALSE | summer
2022-10-29 14:00 | 2022-10-29 15:00 | Winter | FALSE | summer
2022-10-29 15:00 | 2022-10-29 16:00 | Winter | FALSE | summer
2022-10-29 16:00 | 2022-10-29 17:00 | Winter | TRUE | summer
2022-10-29 17:00 | 2022-10-29 18:00 | Winter | TRUE | summer
2022-10-29 18:00 | 2022-10-29 19:00 | Winter | TRUE | summer
2022-10-29 19:00 | 2022-10-29 20:00 | Winter | TRUE | summer
2022-10-29 20:00 | 2022-10-29 21:00 | Winter | TRUE | summer
2022-10-29 21:00 | 2022-10-29 22:00 | Winter | FALSE | summer
2022-10-29 22:00 | 2022-10-29 23:00 | Winter | FALSE | summer
2022-10-29 23:00 | 2022-10-30 | Winter | FALSE | summer
2022-10-30 | 2022-10-30 01:00 | Winter | FALSE | summer
2022-10-30 01:00 | 2022-10-30 02:00 | Winter | FALSE | summer
2022-10-30 02:00 | 2022-10-30 03:00 | Winter | FALSE | summer
2022-10-30 03:00 | 2022-10-30 04:00 | Winter | FALSE | summer
2022-10-30 04:00 | 2022-10-30 05:00 | Winter | FALSE | summer
2022-10-30 05:00 | 2022-10-30 06:00 | Winter | FALSE | summer
2022-10-30 06:00 | 2022-10-30 07:00 | Winter | FALSE | summer
2022-10-30 07:00 | 2022-10-30 08:00 | Winter | FALSE | summer
2022-10-30 08:00 | 2022-10-30 09:00 | Winter | FALSE | summer
2022-10-30 09:00 | 2022-10-30 10:00 | Winter | FALSE | summer
2022-10-30 10:00 | 2022-10-30 11:00 | Winter | FALSE | summer
2022-10-30 11:00 | 2022-10-30 12:00 | Winter | FALSE | summer
2022-10-30 12:00 | 2022-10-30 13:00 | Winter | FALSE | summer
2022-10-30 13:00 | 2022-10-30 14:00 | Winter | FALSE | summer
2022-10-30 14:00 | 2022-10-30 15:00 | Winter | FALSE | summer
2022-10-30 15:00 | 2022-10-30 16:00 | Winter | FALSE | summer
2022-10-30 16:00 | 2022-10-30 17:00 | Winter | TRUE | summer
2022-10-30 17:00 | 2022-10-30 18:00 | Winter | TRUE | summer
2022-10-30 18:00 | 2022-10-30 19:00 | Winter | TRUE | summer
2022-10-30 19:00 | 2022-10-30 20:00 | Winter | TRUE | summer
2022-10-30 20:00 | 2022-10-30 21:00 | Winter | TRUE | summer
2022-10-30 21:00 | 2022-10-30 22:00 | Winter | FALSE | summer
2022-10-30 22:00 | 2022-10-30 23:00 | Winter | FALSE | summer
2022-10-30 23:00 | 2022-10-31 | Winter | FALSE | summer
2022-10-31 | 2022-10-31 01:00 | Winter | FALSE | summer
2022-10-31 01:00 | 2022-10-31 02:00 | Winter | FALSE | summer
2022-10-31 02:00 | 2022-10-31 03:00 | Winter | FALSE | summer
2022-10-31 03:00 | 2022-10-31 04:00 | Winter | FALSE | summer
2022-10-31 04:00 | 2022-10-31 05:00 | Winter | FALSE | summer
2022-10-31 05:00 | 2022-10-31 06:00 | Winter | FALSE | summer
2022-10-31 06:00 | 2022-10-31 07:00 | Winter | FALSE | summer
2022-10-31 07:00 | 2022-10-31 08:00 | Winter | FALSE | summer
2022-10-31 08:00 | 2022-10-31 09:00 | Winter | FALSE | summer
2022-10-31 09:00 | 2022-10-31 10:00 | Winter | FALSE | summer
2022-10-31 10:00 | 2022-10-31 11:00 | Winter | FALSE | summer
2022-10-31 11:00 | 2022-10-31 12:00 | Winter | FALSE | summer
2022-10-31 12:00 | 2022-10-31 13:00 | Winter | FALSE | summer
2022-10-31 13:00 | 2022-10-31 14:00 | Winter | FALSE | summer
2022-10-31 14:00 | 2022-10-31 15:00 | Winter | FALSE | summer
2022-10-31 15:00 | 2022-10-31 16:00 | Winter | FALSE | summer
2022-10-31 16:00 | 2022-10-31 17:00 | Winter | TRUE | summer
2022-10-31 17:00 | 2022-10-31 18:00 | Winter | TRUE | summer
2022-10-31 18:00 | 2022-10-31 19:00 | Winter | TRUE | summer
2022-10-31 19:00 | 2022-10-31 20:00 | Winter | TRUE | summer
2022-10-31 20:00 | 2022-10-31 21:00 | Winter | TRUE | summer
2022-10-31 21:00 | 2022-10-31 22:00 | Winter | FALSE | summer
2022-10-31 22:00 | 2022-10-31 23:00 | Winter | FALSE | summer
2022-10-31 23:00 | 2022-11-01 | Winter | FALSE | summer
2022-11-01 | 2022-11-01 01:00 | Winter | FALSE | nonsummer
2022-11-01 01:00 | 2022-11-01 02:00 | Winter | FALSE | nonsummer
2022-11-01 02:00 | 2022-11-01 03:00 | Winter | FALSE | nonsummer
2022-11-01 03:00 | 2022-11-01 04:00 | Winter | FALSE | nonsummer
2022-11-01 04:00 | 2022-11-01 05:00 | Winter | FALSE | nonsummer
2022-11-01 05:00 | 2022-11-01 06:00 | Winter | FALSE | nonsummer
2022-11-01 06:00 | 2022-11-01 07:00 | Winter | FALSE | nonsummer
2022-11-01 07:00 | 2022-11-01 08:00 | Winter | FALSE | nonsummer
2022-11-01 08:00 | 2022-11-01 09:00 | Winter | FALSE | nonsummer
2022-11-01 09:00 | 2022-11-01 10:00 | Winter | FALSE | nonsummer
2022-11-01 10:00 | 2022-11-01 11:00 | Winter | FALSE | nonsummer
2022-11-01 11:00 | 2022-11-01 12:00 | Winter | FALSE | nonsummer
2022-11-01 12:00 | 2022-11-01 13:00 | Winter | FALSE | nonsummer
2022-11-01 13:00 | 2022-11-01 14:00 | Winter | FALSE | nonsummer
2022-11-01 14:00 | 2022-11-01 15:00 | Winter | FALSE | nonsummer
2022-11-01 15:00 | 2022-11-01 16:00 | Winter | FALSE | nonsummer
2022-11-01 16:00 | 2022-11-01 17:00 | Winter | TRUE | nonsummer
2022-11-01 17:00 | 2022-11-01 18:00 | Winter | TRUE | nonsummer
2022-11-01 18:00 | 2022-11-01 19:00 | Winter | TRUE | nonsummer
2022-11-01 19:00 | 2022-11-01 20:00 | Winter | TRUE | nonsummer
2022-11-01 20:00 | 2022-11-01 21:00 | Winter | TRUE | nonsummer
2022-11-01 21:00 | 2022-11-01 22:00 | Winter | FALSE | nonsummer
2022-11-01 22:00 | 2022-11-01 23:00 | Winter | FALSE | nonsummer
2022-11-01 23:00 | 2022-11-02 | Winter | FALSE | nonsummer
2022-11-02 | 2022-11-02 01:00 | Winter | FALSE | nonsummer
2022-11-02 01:00 | 2022-11-02 02:00 | Winter | FALSE | nonsummer
2022-11-02 02:00 | 2022-11-02 03:00 | Winter | FALSE | nonsummer
2022-11-02 03:00 | 2022-11-02 04:00 | Winter | FALSE | nonsummer
2022-11-02 04:00 | 2022-11-02 05:00 | Winter | FALSE | nonsummer
2022-11-02 05:00 | 2022-11-02 06:00 | Winter | FALSE | nonsummer
2022-11-02 06:00 | 2022-11-02 07:00 | Winter | FALSE | nonsummer
2022-11-02 07:00 | 2022-11-02 08:00 | Winter | FALSE | nonsummer
2022-11-02 08:00 | 2022-11-02 09:00 | Winter | FALSE | nonsummer
2022-11-02 09:00 | 2022-11-02 10:00 | Winter | FALSE | nonsummer
2022-11-02 10:00 | 2022-11-02 11:00 | Winter | FALSE | nonsummer
2022-11-02 11:00 | 2022-11-02 12:00 | Winter | FALSE | nonsummer
2022-11-02 12:00 | 2022-11-02 13:00 | Winter | FALSE | nonsummer
2022-11-02 13:00 | 2022-11-02 14:00 | Winter | FALSE | nonsummer
2022-11-02 14:00 | 2022-11-02 15:00 | Winter | FALSE | nonsummer
2022-11-02 15:00 | 2022-11-02 16:00 | Winter | FALSE | nonsummer
2022-11-02 16:00 | 2022-11-02 17:00 | Winter | TRUE | nonsummer
2022-11-02 17:00 | 2022-11-02 18:00 | Winter | TRUE | nonsummer
2022-11-02 18:00 | 2022-11-02 19:00 | Winter | TRUE | nonsummer
2022-11-02 19:00 | 2022-11-02 20:00 | Winter | TRUE | nonsummer
2022-11-02 20:00 | 2022-11-02 21:00 | Winter | TRUE | nonsummer
2022-11-02 21:00 | 2022-11-02 22:00 | Winter | FALSE | nonsummer
2022-11-02 22:00 | 2022-11-02 23:00 | Winter | FALSE | nonsummer
2022-11-02 23:00 | 2022-11-03 | Winter | FALSE | nonsummer
2022-11-03 | 2022-11-03 01:00 | Winter | FALSE | nonsummer
2022-11-03 01:00 | 2022-11-03 02:00 | Winter | FALSE | nonsummer
2022-11-03 02:00 | 2022-11-03 03:00 | Winter | FALSE | nonsummer
2022-11-03 03:00 | 2022-11-03 04:00 | Winter | FALSE | nonsummer
2022-11-03 04:00 | 2022-11-03 05:00 | Winter | FALSE | nonsummer
2022-11-03 05:00 | 2022-11-03 06:00 | Winter | FALSE | nonsummer
2022-11-03 06:00 | 2022-11-03 07:00 | Winter | FALSE | nonsummer
2022-11-03 07:00 | 2022-11-03 08:00 | Winter | FALSE | nonsummer
2022-11-03 08:00 | 2022-11-03 09:00 | Winter | FALSE | nonsummer
2022-11-03 09:00 | 2022-11-03 10:00 | Winter | FALSE | nonsummer
2022-11-03 10:00 | 2022-11-03 11:00 | Winter | FALSE | nonsummer
2022-11-03 11:00 | 2022-11-03 12:00 | Winter | FALSE | nonsummer
2022-11-03 12:00 | 2022-11-03 13:00 | Winter | FALSE | nonsummer
2022-11-03 13:00 | 2022-11-03 14:00 | Winter | FALSE | nonsummer
2022-11-03 14:00 | 2022-11-03 15:00 | Winter | FALSE | nonsummer
2022-11-03 15:00 | 2022-11-03 16:00 | Winter | FALSE | nonsummer
2022-11-03 16:00 | 2022-11-03 17:00 | Winter | TRUE | nonsummer
2022-11-03 17:00 | 2022-11-03 18:00 | Winter | TRUE | nonsummer
2022-11-03 18:00 | 2022-11-03 19:00 | Winter | TRUE | nonsummer
2022-11-03 19:00 | 2022-11-03 20:00 | Winter | TRUE | nonsummer
2022-11-03 20:00 | 2022-11-03 21:00 | Winter | TRUE | nonsummer
2022-11-03 21:00 | 2022-11-03 22:00 | Winter | FALSE | nonsummer
2022-11-03 22:00 | 2022-11-03 23:00 | Winter | FALSE | nonsummer
2022-11-03 23:00 | 2022-11-04 | Winter | FALSE | nonsummer
2022-11-04 | 2022-11-04 01:00 | Winter | FALSE | nonsummer
2022-11-04 01:00 | 2022-11-04 02:00 | Winter | FALSE | nonsummer
2022-11-04 02:00 | 2022-11-04 03:00 | Winter | FALSE | nonsummer
2022-11-04 03:00 | 2022-11-04 04:00 | Winter | FALSE | nonsummer
2022-11-04 04:00 | 2022-11-04 05:00 | Winter | FALSE | nonsummer
2022-11-04 05:00 | 2022-11-04 06:00 | Winter | FALSE | nonsummer
2022-11-04 06:00 | 2022-11-04 07:00 | Winter | FALSE | nonsummer
2022-11-04 07:00 | 2022-11-04 08:00 | Winter | FALSE | nonsummer
2022-11-04 08:00 | 2022-11-04 09:00 | Winter | FALSE | nonsummer
2022-11-04 09:00 | 2022-11-04 10:00 | Winter | FALSE | nonsummer
2022-11-04 10:00 | 2022-11-04 11:00 | Winter | FALSE | nonsummer
2022-11-04 11:00 | 2022-11-04 12:00 | Winter | FALSE | nonsummer
2022-11-04 12:00 | 2022-11-04 13:00 | Winter | FALSE | nonsummer
2022-11-04 13:00 | 2022-11-04 14:00 | Winter | FALSE | nonsummer
2022-11-04 14:00 | 2022-11-04 15:00 | Winter | FALSE | nonsummer
2022-11-04 15:00 | 2022-11-04 16:00 | Winter | FALSE | nonsummer
2022-11-04 16:00 | 2022-11-04 17:00 | Winter | TRUE | nonsummer
2022-11-04 17:00 | 2022-11-04 18:00 | Winter | TRUE | nonsummer
2022-11-04 18:00 | 2022-11-04 19:00 | Winter | TRUE | nonsummer
2022-11-04 19:00 | 2022-11-04 20:00 | Winter | TRUE | nonsummer
2022-11-04 20:00 | 2022-11-04 21:00 | Winter | TRUE | nonsummer
2022-11-04 21:00 | 2022-11-04 22:00 | Winter | FALSE | nonsummer
2022-11-04 22:00 | 2022-11-04 23:00 | Winter | FALSE | nonsummer
2022-11-04 23:00 | 2022-11-05 | Winter | FALSE | nonsummer
2022-11-05 | 2022-11-05 01:00 | Winter | FALSE | nonsummer
2022-11-05 01:00 | 2022-11-05 02:00 | Winter | FALSE | nonsummer
2022-11-05 02:00 | 2022-11-05 03:00 | Winter | FALSE | nonsummer
2022-11-05 03:00 | 2022-11-05 04:00 | Winter | FALSE | nonsummer
2022-11-05 04:00 | 2022-11-05 05:00 | Winter | FALSE | nonsummer
2022-11-05 05:00 | 2022-11-05 06:00 | Winter | FALSE | nonsummer
2022-11-05 06:00 | 2022-11-05 07:00 | Winter | FALSE | nonsummer
2022-11-05 07:00 | 2022-11-05 08:00 | Winter | FALSE | nonsummer
2022-11-05 08:00 | 2022-11-05 09:00 | Winter | FALSE | nonsummer
2022-11-05 09:00 | 2022-11-05 10:00 | Winter | FALSE | nonsummer
2022-11-05 10:00 | 2022-11-05 11:00 | Winter | FALSE | nonsummer
2022-11-05 11:00 | 2022-11-05 12:00 | Winter | FALSE | nonsummer
2022-11-05 12:00 | 2022-11-05 13:00 | Winter | FALSE | nonsummer
2022-11-05 13:00 | 2022-11-05 14:00 | Winter | FALSE | nonsummer
2022-11-05 14:00 | 2022-11-05 15:00 | Winter | FALSE | nonsummer
2022-11-05 15:00 | 2022-11-05 16:00 | Winter | FALSE | nonsummer
2022-11-05 16:00 | 2022-11-05 17:00 | Winter | TRUE | nonsummer
2022-11-05 17:00 | 2022-11-05 18:00 | Winter | TRUE | nonsummer
2022-11-05 18:00 | 2022-11-05 19:00 | Winter | TRUE | nonsummer
2022-11-05 19:00 | 2022-11-05 20:00 | Winter | TRUE | nonsummer
2022-11-05 20:00 | 2022-11-05 21:00 | Winter | TRUE | nonsummer
2022-11-05 21:00 | 2022-11-05 22:00 | Winter | FALSE | nonsummer
2022-11-05 22:00 | 2022-11-05 23:00 | Winter | FALSE | nonsummer
2022-11-05 23:00 | 2022-11-06 | Winter | FALSE | nonsummer
2022-11-06 | 2022-11-06 01:00 | Winter | FALSE | nonsummer
2022-11-06 01:00 | 2022-11-06 02:00 | Winter | FALSE | nonsummer
2022-11-06 02:00 | 2022-11-06 03:00 | Winter | FALSE | nonsummer
2022-11-06 03:00 | 2022-11-06 04:00 | Winter | FALSE | nonsummer
2022-11-06 04:00 | 2022-11-06 05:00 | Winter | FALSE | nonsummer
2022-11-06 05:00 | 2022-11-06 06:00 | Winter | FALSE | nonsummer
2022-11-06 06:00 | 2022-11-06 07:00 | Winter | FALSE | nonsummer
2022-11-06 07:00 | 2022-11-06 08:00 | Winter | FALSE | nonsummer
2022-11-06 08:00 | 2022-11-06 09:00 | Winter | FALSE | nonsummer
2022-11-06 09:00 | 2022-11-06 10:00 | Winter | FALSE | nonsummer
2022-11-06 10:00 | 2022-11-06 11:00 | Winter | FALSE | nonsummer
2022-11-06 11:00 | 2022-11-06 12:00 | Winter | FALSE | nonsummer
2022-11-06 12:00 | 2022-11-06 13:00 | Winter | FALSE | nonsummer
2022-11-06 13:00 | 2022-11-06 14:00 | Winter | FALSE | nonsummer
2022-11-06 14:00 | 2022-11-06 15:00 | Winter | FALSE | nonsummer
2022-11-06 15:00 | 2022-11-06 16:00 | Winter | FALSE | nonsummer
2022-11-06 16:00 | 2022-11-06 17:00 | Winter | TRUE | nonsummer
2022-11-06 17:00 | 2022-11-06 18:00 | Winter | TRUE | nonsummer
2022-11-06 18:00 | 2022-11-06 19:00 | Winter | TRUE | nonsummer
2022-11-06 19:00 | 2022-11-06 20:00 | Winter | TRUE | nonsummer
2022-11-06 20:00 | 2022-11-06 21:00 | Winter | TRUE | nonsummer
2022-11-06 21:00 | 2022-11-06 22:00 | Winter | FALSE | nonsummer
2022-11-06 22:00 | 2022-11-06 23:00 | Winter | FALSE | nonsummer
2022-11-06 23:00 | 2022-11-07 | Winter | FALSE | nonsummer
2022-11-07 | 2022-11-07 01:00 | Winter | FALSE | nonsummer
2022-11-07 01:00 | 2022-11-07 02:00 | Winter | FALSE | nonsummer
2022-11-07 02:00 | 2022-11-07 03:00 | Winter | FALSE | nonsummer
2022-11-07 03:00 | 2022-11-07 04:00 | Winter | FALSE | nonsummer
2022-11-07 04:00 | 2022-11-07 05:00 | Winter | FALSE | nonsummer
2022-11-07 05:00 | 2022-11-07 06:00 | Winter | FALSE | nonsummer
2022-11-07 06:00 | 2022-11-07 07:00 | Winter | FALSE | nonsummer
2022-11-07 07:00 | 2022-11-07 08:00 | Winter | FALSE | nonsummer
2022-11-07 08:00 | 2022-11-07 09:00 | Winter | FALSE | nonsummer
2022-11-07 09:00 | 2022-11-07 10:00 | Winter | FALSE | nonsummer
2022-11-07 10:00 | 2022-11-07 11:00 | Winter | FALSE | nonsummer
2022-11-07 11:00 | 2022-11-07 12:00 | Winter | FALSE | nonsummer
2022-11-07 12:00 | 2022-11-07 13:00 | Winter | FALSE | nonsummer
2022-11-07 13:00 | 2022-11-07 14:00 | Winter | FALSE | nonsummer
2022-11-07 14:00 | 2022-11-07 15:00 | Winter | FALSE | nonsummer
2022-11-07 15:00 | 2022-11-07 16:00 | Winter | FALSE | nonsummer
2022-11-07 16:00 | 2022-11-07 17:00 | Winter | TRUE | nonsummer
2022-11-07 17:00 | 2022-11-07 18:00 | Winter | TRUE | nonsummer
2022-11-07 18:00 | 2022-11-07 19:00 | Winter | TRUE | nonsummer
2022-11-07 19:00 | 2022-11-07 20:00 | Winter | TRUE | nonsummer
2022-11-07 20:00 | 2022-11-07 21:00 | Winter | TRUE | nonsummer
2022-11-07 21:00 | 2022-11-07 22:00 | Winter | FALSE | nonsummer
2022-11-07 22:00 | 2022-11-07 23:00 | Winter | FALSE | nonsummer
2022-11-07 23:00 | 2022-11-08 | Winter | FALSE | nonsummer
2022-11-08 | 2022-11-08 01:00 | Winter | FALSE | nonsummer
2022-11-08 01:00 | 2022-11-08 02:00 | Winter | FALSE | nonsummer
2022-11-08 02:00 | 2022-11-08 03:00 | Winter | FALSE | nonsummer
2022-11-08 03:00 | 2022-11-08 04:00 | Winter | FALSE | nonsummer
2022-11-08 04:00 | 2022-11-08 05:00 | Winter | FALSE | nonsummer
2022-11-08 05:00 | 2022-11-08 06:00 | Winter | FALSE | nonsummer
2022-11-08 06:00 | 2022-11-08 07:00 | Winter | FALSE | nonsummer
2022-11-08 07:00 | 2022-11-08 08:00 | Winter | FALSE | nonsummer
2022-11-08 08:00 | 2022-11-08 09:00 | Winter | FALSE | nonsummer
2022-11-08 09:00 | 2022-11-08 10:00 | Winter | FALSE | nonsummer
2022-11-08 10:00 | 2022-11-08 11:00 | Winter | FALSE | nonsummer
2022-11-08 11:00 | 2022-11-08 12:00 | Winter | FALSE | nonsummer
2022-11-08 12:00 | 2022-11-08 13:00 | Winter | FALSE | nonsummer
2022-11-08 13:00 | 2022-11-08 14:00 | Winter | FALSE | nonsummer
2022-11-08 14:00 | 2022-11-08 15:00 | Winter | FALSE | nonsummer
2022-11-08 15:00 | 2022-11-08 16:00 | Winter | FALSE | nonsummer
2022-11-08 16:00 | 2022-11-08 17:00 | Winter | TRUE | nonsummer
2022-11-08 17:00 | 2022-11-08 18:00 | Winter | TRUE | nonsummer
2022-11-08 18:00 | 2022-11-08 19:00 | Winter | TRUE | nonsummer
2022-11-08 19:00 | 2022-11-08 20:00 | Winter | TRUE | nonsummer
2022-11-08 20:00 | 2022-11-08 21:00 | Winter | TRUE | nonsummer
2022-11-08 21:00 | 2022-11-08 22:00 | Winter | FALSE | nonsummer
2022-11-08 22:00 | 2022-11-08 23:00 | Winter | FALSE | nonsummer
2022-11-08 23:00 | 2022-11-09 | Winter | FALSE | nonsummer
2022-11-09 | 2022-11-09 01:00 | Winter | FALSE | nonsummer
2022-11-09 01:00 | 2022-11-09 02:00 | Winter | FALSE | nonsummer
2022-11-09 02:00 | 2022-11-09 03:00 | Winter | FALSE | nonsummer
2022-11-09 03:00 | 2022-11-09 04:00 | Winter | FALSE | nonsummer
2022-11-09 04:00 | 2022-11-09 05:00 | Winter | FALSE | nonsummer
2022-11-09 05:00 | 2022-11-09 06:00 | Winter | FALSE | nonsummer
2022-11-09 06:00 | 2022-11-09 07:00 | Winter | FALSE | nonsummer
2022-11-09 07:00 | 2022-11-09 08:00 | Winter | FALSE | nonsummer
2022-11-09 08:00 | 2022-11-09 09:00 | Winter | FALSE | nonsummer
2022-11-09 09:00 | 2022-11-09 10:00 | Winter | FALSE | nonsummer
2022-11-09 10:00 | 2022-11-09 11:00 | Winter | FALSE | nonsummer
2022-11-09 11:00 | 2022-11-09 12:00 | Winter | FALSE | nonsummer
2022-11-09 12:00 | 2022-11-09 13:00 | Winter | FALSE | nonsummer
2022-11-09 13:00 | 2022-11-09 14:00 | Winter | FALSE | nonsummer
2022-11-09 14:00 | 2022-11-09 15:00 | Winter | FALSE | nonsummer
2022-11-09 15:00 | 2022-11-09 16:00 | Winter | FALSE | nonsummer
2022-11-09 16:00 | 2022-11-09 17:00 | Winter | TRUE | nonsummer
2022-11-09 17:00 | 2022-11-09 18:00 | Winter | TRUE | nonsummer
2022-11-09 18:00 | 2022-11-09 19:00 | Winter | TRUE | nonsummer
2022-11-09 19:00 | 2022-11-09 20:00 | Winter | TRUE | nonsummer
2022-11-09 20:00 | 2022-11-09 21:00 | Winter | TRUE | nonsummer
2022-11-09 21:00 | 2022-11-09 22:00 | Winter | FALSE | nonsummer
2022-11-09 22:00 | 2022-11-09 23:00 | Winter | FALSE | nonsummer
2022-11-09 23:00 | 2022-11-10 | Winter | FALSE | nonsummer
2022-11-10 | 2022-11-10 01:00 | Winter | FALSE | nonsummer
2022-11-10 01:00 | 2022-11-10 02:00 | Winter | FALSE | nonsummer
2022-11-10 02:00 | 2022-11-10 03:00 | Winter | FALSE | nonsummer
2022-11-10 03:00 | 2022-11-10 04:00 | Winter | FALSE | nonsummer
2022-11-10 04:00 | 2022-11-10 05:00 | Winter | FALSE | nonsummer
2022-11-10 05:00 | 2022-11-10 06:00 | Winter | FALSE | nonsummer
2022-11-10 06:00 | 2022-11-10 07:00 | Winter | FALSE | nonsummer
2022-11-10 07:00 | 2022-11-10 08:00 | Winter | FALSE | nonsummer
2022-11-10 08:00 | 2022-11-10 09:00 | Winter | FALSE | nonsummer
2022-11-10 09:00 | 2022-11-10 10:00 | Winter | FALSE | nonsummer
2022-11-10 10:00 | 2022-11-10 11:00 | Winter | FALSE | nonsummer
2022-11-10 11:00 | 2022-11-10 12:00 | Winter | FALSE | nonsummer
2022-11-10 12:00 | 2022-11-10 13:00 | Winter | FALSE | nonsummer
2022-11-10 13:00 | 2022-11-10 14:00 | Winter | FALSE | nonsummer
2022-11-10 14:00 | 2022-11-10 15:00 | Winter | FALSE | nonsummer
2022-11-10 15:00 | 2022-11-10 16:00 | Winter | FALSE | nonsummer
2022-11-10 16:00 | 2022-11-10 17:00 | Winter | TRUE | nonsummer
2022-11-10 17:00 | 2022-11-10 18:00 | Winter | TRUE | nonsummer
2022-11-10 18:00 | 2022-11-10 19:00 | Winter | TRUE | nonsummer
2022-11-10 19:00 | 2022-11-10 20:00 | Winter | TRUE | nonsummer
2022-11-10 20:00 | 2022-11-10 21:00 | Winter | TRUE | nonsummer
2022-11-10 21:00 | 2022-11-10 22:00 | Winter | FALSE | nonsummer
2022-11-10 22:00 | 2022-11-10 23:00 | Winter | FALSE | nonsummer
2022-11-10 23:00 | 2022-11-11 | Winter | FALSE | nonsummer
2022-11-11 | 2022-11-11 01:00 | Winter | FALSE | nonsummer
2022-11-11 01:00 | 2022-11-11 02:00 | Winter | FALSE | nonsummer
2022-11-11 02:00 | 2022-11-11 03:00 | Winter | FALSE | nonsummer
2022-11-11 03:00 | 2022-11-11 04:00 | Winter | FALSE | nonsummer
2022-11-11 04:00 | 2022-11-11 05:00 | Winter | FALSE | nonsummer
2022-11-11 05:00 | 2022-11-11 06:00 | Winter | FALSE | nonsummer
2022-11-11 06:00 | 2022-11-11 07:00 | Winter | FALSE | nonsummer
2022-11-11 07:00 | 2022-11-11 08:00 | Winter | FALSE | nonsummer
2022-11-11 08:00 | 2022-11-11 09:00 | Winter | FALSE | nonsummer
2022-11-11 09:00 | 2022-11-11 10:00 | Winter | FALSE | nonsummer
2022-11-11 10:00 | 2022-11-11 11:00 | Winter | FALSE | nonsummer
2022-11-11 11:00 | 2022-11-11 12:00 | Winter | FALSE | nonsummer
2022-11-11 12:00 | 2022-11-11 13:00 | Winter | FALSE | nonsummer
2022-11-11 13:00 | 2022-11-11 14:00 | Winter | FALSE | nonsummer
2022-11-11 14:00 | 2022-11-11 15:00 | Winter | FALSE | nonsummer
2022-11-11 15:00 | 2022-11-11 16:00 | Winter | FALSE | nonsummer
2022-11-11 16:00 | 2022-11-11 17:00 | Winter | TRUE | nonsummer
2022-11-11 17:00 | 2022-11-11 18:00 | Winter | TRUE | nonsummer
2022-11-11 18:00 | 2022-11-11 19:00 | Winter | TRUE | nonsummer
2022-11-11 19:00 | 2022-11-11 20:00 | Winter | TRUE | nonsummer
2022-11-11 20:00 | 2022-11-11 21:00 | Winter | TRUE | nonsummer
2022-11-11 21:00 | 2022-11-11 22:00 | Winter | FALSE | nonsummer
2022-11-11 22:00 | 2022-11-11 23:00 | Winter | FALSE | nonsummer
2022-11-11 23:00 | 2022-11-12 | Winter | FALSE | nonsummer
2022-11-12 | 2022-11-12 01:00 | Winter | FALSE | nonsummer
2022-11-12 01:00 | 2022-11-12 02:00 | Winter | FALSE | nonsummer
2022-11-12 02:00 | 2022-11-12 03:00 | Winter | FALSE | nonsummer
2022-11-12 03:00 | 2022-11-12 04:00 | Winter | FALSE | nonsummer
2022-11-12 04:00 | 2022-11-12 05:00 | Winter | FALSE | nonsummer
2022-11-12 05:00 | 2022-11-12 06:00 | Winter | FALSE | nonsummer
2022-11-12 06:00 | 2022-11-12 07:00 | Winter | FALSE | nonsummer
2022-11-12 07:00 | 2022-11-12 08:00 | Winter | FALSE | nonsummer
2022-11-12 08:00 | 2022-11-12 09:00 | Winter | FALSE | nonsummer
2022-11-12 09:00 | 2022-11-12 10:00 | Winter | FALSE | nonsummer
2022-11-12 10:00 | 2022-11-12 11:00 | Winter | FALSE | nonsummer
2022-11-12 11:00 | 2022-11-12 12:00 | Winter | FALSE | nonsummer
2022-11-12 12:00 | 2022-11-12 13:00 | Winter | FALSE | nonsummer
2022-11-12 13:00 | 2022-11-12 14:00 | Winter | FALSE | nonsummer
2022-11-12 14:00 | 2022-11-12 15:00 | Winter | FALSE | nonsummer
2022-11-12 15:00 | 2022-11-12 16:00 | Winter | FALSE | nonsummer
2022-11-12 16:00 | 2022-11-12 17:00 | Winter | TRUE | nonsummer
2022-11-12 17:00 | 2022-11-12 18:00 | Winter | TRUE | nonsummer
2022-11-12 18:00 | 2022-11-12 19:00 | Winter | TRUE | nonsummer
2022-11-12 19:00 | 2022-11-12 20:00 | Winter | TRUE | nonsummer
2022-11-12 20:00 | 2022-11-12 21:00 | Winter | TRUE | nonsummer
2022-11-12 21:00 | 2022-11-12 22:00 | Winter | FALSE | nonsummer
2022-11-12 22:00 | 2022-11-12 23:00 | Winter | FALSE | nonsummer
2022-11-12 23:00 | 2022-11-13 | Winter | FALSE | nonsummer
2022-11-13 | 2022-11-13 01:00 | Winter | FALSE | nonsummer
2022-11-13 01:00 | 2022-11-13 02:00 | Winter | FALSE | nonsummer
2022-11-13 02:00 | 2022-11-13 03:00 | Winter | FALSE | nonsummer
2022-11-13 03:00 | 2022-11-13 04:00 | Winter | FALSE | nonsummer
2022-11-13 04:00 | 2022-11-13 05:00 | Winter | FALSE | nonsummer
2022-11-13 05:00 | 2022-11-13 06:00 | Winter | FALSE | nonsummer
2022-11-13 06:00 | 2022-11-13 07:00 | Winter | FALSE | nonsummer
2022-11-13 07:00 | 2022-11-13 08:00 | Winter | FALSE | nonsummer
2022-11-13 08:00 | 2022-11-13 09:00 | Winter | FALSE | nonsummer
2022-11-13 09:00 | 2022-11-13 10:00 | Winter | FALSE | nonsummer
2022-11-13 10:00 | 2022-11-13 11:00 | Winter | FALSE | nonsummer
2022-11-13 11:00 | 2022-11-13 12:00 | Winter | FALSE | nonsummer
2022-11-13 12:00 | 2022-11-13 13:00 | Winter | FALSE | nonsummer
2022-11-13 13:00 | 2022-11-13 14:00 | Winter | FALSE | nonsummer
2022-11-13 14:00 | 2022-11-13 15:00 | Winter | FALSE | nonsummer
2022-11-13 15:00 | 2022-11-13 16:00 | Winter | FALSE | nonsummer
2022-11-13 16:00 | 2022-11-13 17:00 | Winter | TRUE | nonsummer
2022-11-13 17:00 | 2022-11-13 18:00 | Winter | TRUE | nonsummer
2022-11-13 18:00 | 2022-11-13 19:00 | Winter | TRUE | nonsummer
2022-11-13 19:00 | 2022-11-13 20:00 | Winter | TRUE | nonsummer
2022-11-13 20:00 | 2022-11-13 21:00 | Winter | TRUE | nonsummer
2022-11-13 21:00 | 2022-11-13 22:00 | Winter | FALSE | nonsummer
2022-11-13 22:00 | 2022-11-13 23:00 | Winter | FALSE | nonsummer
2022-11-13 23:00 | 2022-11-14 | Winter | FALSE | nonsummer
2022-11-14 | 2022-11-14 01:00 | Winter | FALSE | nonsummer
2022-11-14 01:00 | 2022-11-14 02:00 | Winter | FALSE | nonsummer
2022-11-14 02:00 | 2022-11-14 03:00 | Winter | FALSE | nonsummer
2022-11-14 03:00 | 2022-11-14 04:00 | Winter | FALSE | nonsummer
2022-11-14 04:00 | 2022-11-14 05:00 | Winter | FALSE | nonsummer
2022-11-14 05:00 | 2022-11-14 06:00 | Winter | FALSE | nonsummer
2022-11-14 06:00 | 2022-11-14 07:00 | Winter | FALSE | nonsummer
2022-11-14 07:00 | 2022-11-14 08:00 | Winter | FALSE | nonsummer
2022-11-14 08:00 | 2022-11-14 09:00 | Winter | FALSE | nonsummer
2022-11-14 09:00 | 2022-11-14 10:00 | Winter | FALSE | nonsummer
2022-11-14 10:00 | 2022-11-14 11:00 | Winter | FALSE | nonsummer
2022-11-14 11:00 | 2022-11-14 12:00 | Winter | FALSE | nonsummer
2022-11-14 12:00 | 2022-11-14 13:00 | Winter | FALSE | nonsummer
2022-11-14 13:00 | 2022-11-14 14:00 | Winter | FALSE | nonsummer
2022-11-14 14:00 | 2022-11-14 15:00 | Winter | FALSE | nonsummer
2022-11-14 15:00 | 2022-11-14 16:00 | Winter | FALSE | nonsummer
2022-11-14 16:00 | 2022-11-14 17:00 | Winter | TRUE | nonsummer
2022-11-14 17:00 | 2022-11-14 18:00 | Winter | TRUE | nonsummer
2022-11-14 18:00 | 2022-11-14 19:00 | Winter | TRUE | nonsummer
2022-11-14 19:00 | 2022-11-14 20:00 | Winter | TRUE | nonsummer
2022-11-14 20:00 | 2022-11-14 21:00 | Winter | TRUE | nonsummer
2022-11-14 21:00 | 2022-11-14 22:00 | Winter | FALSE | nonsummer
2022-11-14 22:00 | 2022-11-14 23:00 | Winter | FALSE | nonsummer
2022-11-14 23:00 | 2022-11-15 | Winter | FALSE | nonsummer
2022-11-15 | 2022-11-15 01:00 | Winter | FALSE | nonsummer
2022-11-15 01:00 | 2022-11-15 02:00 | Winter | FALSE | nonsummer
2022-11-15 02:00 | 2022-11-15 03:00 | Winter | FALSE | nonsummer
2022-11-15 03:00 | 2022-11-15 04:00 | Winter | FALSE | nonsummer
2022-11-15 04:00 | 2022-11-15 05:00 | Winter | FALSE | nonsummer
2022-11-15 05:00 | 2022-11-15 06:00 | Winter | FALSE | nonsummer
2022-11-15 06:00 | 2022-11-15 07:00 | Winter | FALSE | nonsummer
2022-11-15 07:00 | 2022-11-15 08:00 | Winter | FALSE | nonsummer
2022-11-15 08:00 | 2022-11-15 09:00 | Winter | FALSE | nonsummer
2022-11-15 09:00 | 2022-11-15 10:00 | Winter | FALSE | nonsummer
2022-11-15 10:00 | 2022-11-15 11:00 | Winter | FALSE | nonsummer
2022-11-15 11:00 | 2022-11-15 12:00 | Winter | FALSE | nonsummer
2022-11-15 12:00 | 2022-11-15 13:00 | Winter | FALSE | nonsummer
2022-11-15 13:00 | 2022-11-15 14:00 | Winter | FALSE | nonsummer
2022-11-15 14:00 | 2022-11-15 15:00 | Winter | FALSE | nonsummer
2022-11-15 15:00 | 2022-11-15 16:00 | Winter | FALSE | nonsummer
2022-11-15 16:00 | 2022-11-15 17:00 | Winter | TRUE | nonsummer
2022-11-15 17:00 | 2022-11-15 18:00 | Winter | TRUE | nonsummer
2022-11-15 18:00 | 2022-11-15 19:00 | Winter | TRUE | nonsummer
2022-11-15 19:00 | 2022-11-15 20:00 | Winter | TRUE | nonsummer
2022-11-15 20:00 | 2022-11-15 21:00 | Winter | TRUE | nonsummer
2022-11-15 21:00 | 2022-11-15 22:00 | Winter | FALSE | nonsummer
2022-11-15 22:00 | 2022-11-15 23:00 | Winter | FALSE | nonsummer
2022-11-15 23:00 | 2022-11-16 | Winter | FALSE | nonsummer
2022-11-16 | 2022-11-16 01:00 | Winter | FALSE | nonsummer
2022-11-16 01:00 | 2022-11-16 02:00 | Winter | FALSE | nonsummer
2022-11-16 02:00 | 2022-11-16 03:00 | Winter | FALSE | nonsummer
2022-11-16 03:00 | 2022-11-16 04:00 | Winter | FALSE | nonsummer
2022-11-16 04:00 | 2022-11-16 05:00 | Winter | FALSE | nonsummer
2022-11-16 05:00 | 2022-11-16 06:00 | Winter | FALSE | nonsummer
2022-11-16 06:00 | 2022-11-16 07:00 | Winter | FALSE | nonsummer
2022-11-16 07:00 | 2022-11-16 08:00 | Winter | FALSE | nonsummer
2022-11-16 08:00 | 2022-11-16 09:00 | Winter | FALSE | nonsummer
2022-11-16 09:00 | 2022-11-16 10:00 | Winter | FALSE | nonsummer
2022-11-16 10:00 | 2022-11-16 11:00 | Winter | FALSE | nonsummer
2022-11-16 11:00 | 2022-11-16 12:00 | Winter | FALSE | nonsummer
2022-11-16 12:00 | 2022-11-16 13:00 | Winter | FALSE | nonsummer
2022-11-16 13:00 | 2022-11-16 14:00 | Winter | FALSE | nonsummer
2022-11-16 14:00 | 2022-11-16 15:00 | Winter | FALSE | nonsummer
2022-11-16 15:00 | 2022-11-16 16:00 | Winter | FALSE | nonsummer
2022-11-16 16:00 | 2022-11-16 17:00 | Winter | TRUE | nonsummer
2022-11-16 17:00 | 2022-11-16 18:00 | Winter | TRUE | nonsummer
2022-11-16 18:00 | 2022-11-16 19:00 | Winter | TRUE | nonsummer
2022-11-16 19:00 | 2022-11-16 20:00 | Winter | TRUE | nonsummer
2022-11-16 20:00 | 2022-11-16 21:00 | Winter | TRUE | nonsummer
2022-11-16 21:00 | 2022-11-16 22:00 | Winter | FALSE | nonsummer
2022-11-16 22:00 | 2022-11-16 23:00 | Winter | FALSE | nonsummer
2022-11-16 23:00 | 2022-11-17 | Winter | FALSE | nonsummer
2022-11-17 | 2022-11-17 01:00 | Winter | FALSE | nonsummer
2022-11-17 01:00 | 2022-11-17 02:00 | Winter | FALSE | nonsummer
2022-11-17 02:00 | 2022-11-17 03:00 | Winter | FALSE | nonsummer
2022-11-17 03:00 | 2022-11-17 04:00 | Winter | FALSE | nonsummer
2022-11-17 04:00 | 2022-11-17 05:00 | Winter | FALSE | nonsummer
2022-11-17 05:00 | 2022-11-17 06:00 | Winter | FALSE | nonsummer
2022-11-17 06:00 | 2022-11-17 07:00 | Winter | FALSE | nonsummer
2022-11-17 07:00 | 2022-11-17 08:00 | Winter | FALSE | nonsummer
2022-11-17 08:00 | 2022-11-17 09:00 | Winter | FALSE | nonsummer
2022-11-17 09:00 | 2022-11-17 10:00 | Winter | FALSE | nonsummer
2022-11-17 10:00 | 2022-11-17 11:00 | Winter | FALSE | nonsummer
2022-11-17 11:00 | 2022-11-17 12:00 | Winter | FALSE | nonsummer
2022-11-17 12:00 | 2022-11-17 13:00 | Winter | FALSE | nonsummer
2022-11-17 13:00 | 2022-11-17 14:00 | Winter | FALSE | nonsummer
2022-11-17 14:00 | 2022-11-17 15:00 | Winter | FALSE | nonsummer
2022-11-17 15:00 | 2022-11-17 16:00 | Winter | FALSE | nonsummer
2022-11-17 16:00 | 2022-11-17 17:00 | Winter | TRUE | nonsummer
2022-11-17 17:00 | 2022-11-17 18:00 | Winter | TRUE | nonsummer
2022-11-17 18:00 | 2022-11-17 19:00 | Winter | TRUE | nonsummer
2022-11-17 19:00 | 2022-11-17 20:00 | Winter | TRUE | nonsummer
2022-11-17 20:00 | 2022-11-17 21:00 | Winter | TRUE | nonsummer
2022-11-17 21:00 | 2022-11-17 22:00 | Winter | FALSE | nonsummer
2022-11-17 22:00 | 2022-11-17 23:00 | Winter | FALSE | nonsummer
2022-11-17 23:00 | 2022-11-18 | Winter | FALSE | nonsummer
2022-11-18 | 2022-11-18 01:00 | Winter | FALSE | nonsummer
2022-11-18 01:00 | 2022-11-18 02:00 | Winter | FALSE | nonsummer
2022-11-18 02:00 | 2022-11-18 03:00 | Winter | FALSE | nonsummer
2022-11-18 03:00 | 2022-11-18 04:00 | Winter | FALSE | nonsummer
2022-11-18 04:00 | 2022-11-18 05:00 | Winter | FALSE | nonsummer
2022-11-18 05:00 | 2022-11-18 06:00 | Winter | FALSE | nonsummer
2022-11-18 06:00 | 2022-11-18 07:00 | Winter | FALSE | nonsummer
2022-11-18 07:00 | 2022-11-18 08:00 | Winter | FALSE | nonsummer
2022-11-18 08:00 | 2022-11-18 09:00 | Winter | FALSE | nonsummer
2022-11-18 09:00 | 2022-11-18 10:00 | Winter | FALSE | nonsummer
2022-11-18 10:00 | 2022-11-18 11:00 | Winter | FALSE | nonsummer
2022-11-18 11:00 | 2022-11-18 12:00 | Winter | FALSE | nonsummer
2022-11-18 12:00 | 2022-11-18 13:00 | Winter | FALSE | nonsummer
2022-11-18 13:00 | 2022-11-18 14:00 | Winter | FALSE | nonsummer
2022-11-18 14:00 | 2022-11-18 15:00 | Winter | FALSE | nonsummer
2022-11-18 15:00 | 2022-11-18 16:00 | Winter | FALSE | nonsummer
2022-11-18 16:00 | 2022-11-18 17:00 | Winter | TRUE | nonsummer
2022-11-18 17:00 | 2022-11-18 18:00 | Winter | TRUE | nonsummer
2022-11-18 18:00 | 2022-11-18 19:00 | Winter | TRUE | nonsummer
2022-11-18 19:00 | 2022-11-18 20:00 | Winter | TRUE | nonsummer
2022-11-18 20:00 | 2022-11-18 21:00 | Winter | TRUE | nonsummer
2022-11-18 21:00 | 2022-11-18 22:00 | Winter | FALSE | nonsummer
2022-11-18 22:00 | 2022-11-18 23:00 | Winter | FALSE | nonsummer
2022-11-18 23:00 | 2022-11-19 | Winter | FALSE | nonsummer
2022-11-19 | 2022-11-19 01:00 | Winter | FALSE | nonsummer
2022-11-19 01:00 | 2022-11-19 02:00 | Winter | FALSE | nonsummer
2022-11-19 02:00 | 2022-11-19 03:00 | Winter | FALSE | nonsummer
2022-11-19 03:00 | 2022-11-19 04:00 | Winter | FALSE | nonsummer
2022-11-19 04:00 | 2022-11-19 05:00 | Winter | FALSE | nonsummer
2022-11-19 05:00 | 2022-11-19 06:00 | Winter | FALSE | nonsummer
2022-11-19 06:00 | 2022-11-19 07:00 | Winter | FALSE | nonsummer
2022-11-19 07:00 | 2022-11-19 08:00 | Winter | FALSE | nonsummer
2022-11-19 08:00 | 2022-11-19 09:00 | Winter | FALSE | nonsummer
2022-11-19 09:00 | 2022-11-19 10:00 | Winter | FALSE | nonsummer
2022-11-19 10:00 | 2022-11-19 11:00 | Winter | FALSE | nonsummer
2022-11-19 11:00 | 2022-11-19 12:00 | Winter | FALSE | nonsummer
2022-11-19 12:00 | 2022-11-19 13:00 | Winter | FALSE | nonsummer
2022-11-19 13:00 | 2022-11-19 14:00 | Winter | FALSE | nonsummer
2022-11-19 14:00 | 2022-11-19 15:00 | Winter | FALSE | nonsummer
2022-11-19 15:00 | 2022-11-19 16:00 | Winter | FALSE | nonsummer
2022-11-19 16:00 | 2022-11-19 17:00 | Winter | TRUE | nonsummer
2022-11-19 17:00 | 2022-11-19 18:00 | Winter | TRUE | nonsummer
2022-11-19 18:00 | 2022-11-19 19:00 | Winter | TRUE | nonsummer
2022-11-19 19:00 | 2022-11-19 20:00 | Winter | TRUE | nonsummer
2022-11-19 20:00 | 2022-11-19 21:00 | Winter | TRUE | nonsummer
2022-11-19 21:00 | 2022-11-19 22:00 | Winter | FALSE | nonsummer
2022-11-19 22:00 | 2022-11-19 23:00 | Winter | FALSE | nonsummer
2022-11-19 23:00 | 2022-11-20 | Winter | FALSE | nonsummer
2022-11-20 | 2022-11-20 01:00 | Winter | FALSE | nonsummer
2022-11-20 01:00 | 2022-11-20 02:00 | Winter | FALSE | nonsummer
2022-11-20 02:00 | 2022-11-20 03:00 | Winter | FALSE | nonsummer
2022-11-20 03:00 | 2022-11-20 04:00 | Winter | FALSE | nonsummer
2022-11-20 04:00 | 2022-11-20 05:00 | Winter | FALSE | nonsummer
2022-11-20 05:00 | 2022-11-20 06:00 | Winter | FALSE | nonsummer
2022-11-20 06:00 | 2022-11-20 07:00 | Winter | FALSE | nonsummer
2022-11-20 07:00 | 2022-11-20 08:00 | Winter | FALSE | nonsummer
2022-11-20 08:00 | 2022-11-20 09:00 | Winter | FALSE | nonsummer
2022-11-20 09:00 | 2022-11-20 10:00 | Winter | FALSE | nonsummer
2022-11-20 10:00 | 2022-11-20 11:00 | Winter | FALSE | nonsummer
2022-11-20 11:00 | 2022-11-20 12:00 | Winter | FALSE | nonsummer
2022-11-20 12:00 | 2022-11-20 13:00 | Winter | FALSE | nonsummer
2022-11-20 13:00 | 2022-11-20 14:00 | Winter | FALSE | nonsummer
2022-11-20 14:00 | 2022-11-20 15:00 | Winter | FALSE | nonsummer
2022-11-20 15:00 | 2022-11-20 16:00 | Winter | FALSE | nonsummer
2022-11-20 16:00 | 2022-11-20 17:00 | Winter | TRUE | nonsummer
2022-11-20 17:00 | 2022-11-20 18:00 | Winter | TRUE | nonsummer
2022-11-20 18:00 | 2022-11-20 19:00 | Winter | TRUE | nonsummer
2022-11-20 19:00 | 2022-11-20 20:00 | Winter | TRUE | nonsummer
2022-11-20 20:00 | 2022-11-20 21:00 | Winter | TRUE | nonsummer
2022-11-20 21:00 | 2022-11-20 22:00 | Winter | FALSE | nonsummer
2022-11-20 22:00 | 2022-11-20 23:00 | Winter | FALSE | nonsummer
2022-11-20 23:00 | 2022-11-21 | Winter | FALSE | nonsummer
2022-11-21 | 2022-11-21 01:00 | Winter | FALSE | nonsummer
2022-11-21 01:00 | 2022-11-21 02:00 | Winter | FALSE | nonsummer
2022-11-21 02:00 | 2022-11-21 03:00 | Winter | FALSE | nonsummer
2022-11-21 03:00 | 2022-11-21 04:00 | Winter | FALSE | nonsummer
2022-11-21 04:00 | 2022-11-21 05:00 | Winter | FALSE | nonsummer
2022-11-21 05:00 | 2022-11-21 06:00 | Winter | FALSE | nonsummer
2022-11-21 06:00 | 2022-11-21 07:00 | Winter | FALSE | nonsummer
2022-11-21 07:00 | 2022-11-21 08:00 | Winter | FALSE | nonsummer
2022-11-21 08:00 | 2022-11-21 09:00 | Winter | FALSE | nonsummer
2022-11-21 09:00 | 2022-11-21 10:00 | Winter | FALSE | nonsummer
2022-11-21 10:00 | 2022-11-21 11:00 | Winter | FALSE | nonsummer
2022-11-21 11:00 | 2022-11-21 12:00 | Winter | FALSE | nonsummer
2022-11-21 12:00 | 2022-11-21 13:00 | Winter | FALSE | nonsummer
2022-11-21 13:00 | 2022-11-21 14:00 | Winter | FALSE | nonsummer
2022-11-21 14:00 | 2022-11-21 15:00 | Winter | FALSE | nonsummer
2022-11-21 15:00 | 2022-11-21 16:00 | Winter | FALSE | nonsummer
2022-11-21 16:00 | 2022-11-21 17:00 | Winter | TRUE | nonsummer
2022-11-21 17:00 | 2022-11-21 18:00 | Winter | TRUE | nonsummer
2022-11-21 18:00 | 2022-11-21 19:00 | Winter | TRUE | nonsummer
2022-11-21 19:00 | 2022-11-21 20:00 | Winter | TRUE | nonsummer
2022-11-21 20:00 | 2022-11-21 21:00 | Winter | TRUE | nonsummer
2022-11-21 21:00 | 2022-11-21 22:00 | Winter | FALSE | nonsummer
2022-11-21 22:00 | 2022-11-21 23:00 | Winter | FALSE | nonsummer
2022-11-21 23:00 | 2022-11-22 | Winter | FALSE | nonsummer
2022-11-22 | 2022-11-22 01:00 | Winter | FALSE | nonsummer
2022-11-22 01:00 | 2022-11-22 02:00 | Winter | FALSE | nonsummer
2022-11-22 02:00 | 2022-11-22 03:00 | Winter | FALSE | nonsummer
2022-11-22 03:00 | 2022-11-22 04:00 | Winter | FALSE | nonsummer
2022-11-22 04:00 | 2022-11-22 05:00 | Winter | FALSE | nonsummer
2022-11-22 05:00 | 2022-11-22 06:00 | Winter | FALSE | nonsummer
2022-11-22 06:00 | 2022-11-22 07:00 | Winter | FALSE | nonsummer
2022-11-22 07:00 | 2022-11-22 08:00 | Winter | FALSE | nonsummer
2022-11-22 08:00 | 2022-11-22 09:00 | Winter | FALSE | nonsummer
2022-11-22 09:00 | 2022-11-22 10:00 | Winter | FALSE | nonsummer
2022-11-22 10:00 | 2022-11-22 11:00 | Winter | FALSE | nonsummer
2022-11-22 11:00 | 2022-11-22 12:00 | Winter | FALSE | nonsummer
2022-11-22 12:00 | 2022-11-22 13:00 | Winter | FALSE | nonsummer
2022-11-22 13:00 | 2022-11-22 14:00 | Winter | FALSE | nonsummer
2022-11-22 14:00 | 2022-11-22 15:00 | Winter | FALSE | nonsummer
2022-11-22 15:00 | 2022-11-22 16:00 | Winter | FALSE | nonsummer
2022-11-22 16:00 | 2022-11-22 17:00 | Winter | TRUE | nonsummer
2022-11-22 17:00 | 2022-11-22 18:00 | Winter | TRUE | nonsummer
2022-11-22 18:00 | 2022-11-22 19:00 | Winter | TRUE | nonsummer
2022-11-22 19:00 | 2022-11-22 20:00 | Winter | TRUE | nonsummer
2022-11-22 20:00 | 2022-11-22 21:00 | Winter | TRUE | nonsummer
2022-11-22 21:00 | 2022-11-22 22:00 | Winter | FALSE | nonsummer
2022-11-22 22:00 | 2022-11-22 23:00 | Winter | FALSE | nonsummer
2022-11-22 23:00 | 2022-11-23 | Winter | FALSE | nonsummer
2022-11-23 | 2022-11-23 01:00 | Winter | FALSE | nonsummer
2022-11-23 01:00 | 2022-11-23 02:00 | Winter | FALSE | nonsummer
2022-11-23 02:00 | 2022-11-23 03:00 | Winter | FALSE | nonsummer
2022-11-23 03:00 | 2022-11-23 04:00 | Winter | FALSE | nonsummer
2022-11-23 04:00 | 2022-11-23 05:00 | Winter | FALSE | nonsummer
2022-11-23 05:00 | 2022-11-23 06:00 | Winter | FALSE | nonsummer
2022-11-23 06:00 | 2022-11-23 07:00 | Winter | FALSE | nonsummer
2022-11-23 07:00 | 2022-11-23 08:00 | Winter | FALSE | nonsummer
2022-11-23 08:00 | 2022-11-23 09:00 | Winter | FALSE | nonsummer
2022-11-23 09:00 | 2022-11-23 10:00 | Winter | FALSE | nonsummer
2022-11-23 10:00 | 2022-11-23 11:00 | Winter | FALSE | nonsummer
2022-11-23 11:00 | 2022-11-23 12:00 | Winter | FALSE | nonsummer
2022-11-23 12:00 | 2022-11-23 13:00 | Winter | FALSE | nonsummer
2022-11-23 13:00 | 2022-11-23 14:00 | Winter | FALSE | nonsummer
2022-11-23 14:00 | 2022-11-23 15:00 | Winter | FALSE | nonsummer
2022-11-23 15:00 | 2022-11-23 16:00 | Winter | FALSE | nonsummer
2022-11-23 16:00 | 2022-11-23 17:00 | Winter | TRUE | nonsummer
2022-11-23 17:00 | 2022-11-23 18:00 | Winter | TRUE | nonsummer
2022-11-23 18:00 | 2022-11-23 19:00 | Winter | TRUE | nonsummer
2022-11-23 19:00 | 2022-11-23 20:00 | Winter | TRUE | nonsummer
2022-11-23 20:00 | 2022-11-23 21:00 | Winter | TRUE | nonsummer
2022-11-23 21:00 | 2022-11-23 22:00 | Winter | FALSE | nonsummer
2022-11-23 22:00 | 2022-11-23 23:00 | Winter | FALSE | nonsummer
2022-11-23 23:00 | 2022-11-24 | Winter | FALSE | nonsummer
2022-11-24 | 2022-11-24 01:00 | Winter | FALSE | nonsummer
2022-11-24 01:00 | 2022-11-24 02:00 | Winter | FALSE | nonsummer
2022-11-24 02:00 | 2022-11-24 03:00 | Winter | FALSE | nonsummer
2022-11-24 03:00 | 2022-11-24 04:00 | Winter | FALSE | nonsummer
2022-11-24 04:00 | 2022-11-24 05:00 | Winter | FALSE | nonsummer
2022-11-24 05:00 | 2022-11-24 06:00 | Winter | FALSE | nonsummer
2022-11-24 06:00 | 2022-11-24 07:00 | Winter | FALSE | nonsummer
2022-11-24 07:00 | 2022-11-24 08:00 | Winter | FALSE | nonsummer
2022-11-24 08:00 | 2022-11-24 09:00 | Winter | FALSE | nonsummer
2022-11-24 09:00 | 2022-11-24 10:00 | Winter | FALSE | nonsummer
2022-11-24 10:00 | 2022-11-24 11:00 | Winter | FALSE | nonsummer
2022-11-24 11:00 | 2022-11-24 12:00 | Winter | FALSE | nonsummer
2022-11-24 12:00 | 2022-11-24 13:00 | Winter | FALSE | nonsummer
2022-11-24 13:00 | 2022-11-24 14:00 | Winter | FALSE | nonsummer
2022-11-24 14:00 | 2022-11-24 15:00 | Winter | FALSE | nonsummer
2022-11-24 15:00 | 2022-11-24 16:00 | Winter | FALSE | nonsummer
2022-11-24 16:00 | 2022-11-24 17:00 | Winter | TRUE | nonsummer
2022-11-24 17:00 | 2022-11-24 18:00 | Winter | TRUE | nonsummer
2022-11-24 18:00 | 2022-11-24 19:00 | Winter | TRUE | nonsummer
2022-11-24 19:00 | 2022-11-24 20:00 | Winter | TRUE | nonsummer
2022-11-24 20:00 | 2022-11-24 21:00 | Winter | TRUE | nonsummer
2022-11-24 21:00 | 2022-11-24 22:00 | Winter | FALSE | nonsummer
2022-11-24 22:00 | 2022-11-24 23:00 | Winter | FALSE | nonsummer
2022-11-24 23:00 | 2022-11-25 | Winter | FALSE | nonsummer
2022-11-25 | 2022-11-25 01:00 | Winter | FALSE | nonsummer
2022-11-25 01:00 | 2022-11-25 02:00 | Winter | FALSE | nonsummer
2022-11-25 02:00 | 2022-11-25 03:00 | Winter | FALSE | nonsummer
2022-11-25 03:00 | 2022-11-25 04:00 | Winter | FALSE | nonsummer
2022-11-25 04:00 | 2022-11-25 05:00 | Winter | FALSE | nonsummer
2022-11-25 05:00 | 2022-11-25 06:00 | Winter | FALSE | nonsummer
2022-11-25 06:00 | 2022-11-25 07:00 | Winter | FALSE | nonsummer
2022-11-25 07:00 | 2022-11-25 08:00 | Winter | FALSE | nonsummer
2022-11-25 08:00 | 2022-11-25 09:00 | Winter | FALSE | nonsummer
2022-11-25 09:00 | 2022-11-25 10:00 | Winter | FALSE | nonsummer
2022-11-25 10:00 | 2022-11-25 11:00 | Winter | FALSE | nonsummer
2022-11-25 11:00 | 2022-11-25 12:00 | Winter | FALSE | nonsummer
2022-11-25 12:00 | 2022-11-25 13:00 | Winter | FALSE | nonsummer
2022-11-25 13:00 | 2022-11-25 14:00 | Winter | FALSE | nonsummer
2022-11-25 14:00 | 2022-11-25 15:00 | Winter | FALSE | nonsummer
2022-11-25 15:00 | 2022-11-25 16:00 | Winter | FALSE | nonsummer
2022-11-25 16:00 | 2022-11-25 17:00 | Winter | TRUE | nonsummer
2022-11-25 17:00 | 2022-11-25 18:00 | Winter | TRUE | nonsummer
2022-11-25 18:00 | 2022-11-25 19:00 | Winter | TRUE | nonsummer
2022-11-25 19:00 | 2022-11-25 20:00 | Winter | TRUE | nonsummer
2022-11-25 20:00 | 2022-11-25 21:00 | Winter | TRUE | nonsummer
2022-11-25 21:00 | 2022-11-25 22:00 | Winter | FALSE | nonsummer
2022-11-25 22:00 | 2022-11-25 23:00 | Winter | FALSE | nonsummer
2022-11-25 23:00 | 2022-11-26 | Winter | FALSE | nonsummer
2022-11-26 | 2022-11-26 01:00 | Winter | FALSE | nonsummer
2022-11-26 01:00 | 2022-11-26 02:00 | Winter | FALSE | nonsummer
2022-11-26 02:00 | 2022-11-26 03:00 | Winter | FALSE | nonsummer
2022-11-26 03:00 | 2022-11-26 04:00 | Winter | FALSE | nonsummer
2022-11-26 04:00 | 2022-11-26 05:00 | Winter | FALSE | nonsummer
2022-11-26 05:00 | 2022-11-26 06:00 | Winter | FALSE | nonsummer
2022-11-26 06:00 | 2022-11-26 07:00 | Winter | FALSE | nonsummer
2022-11-26 07:00 | 2022-11-26 08:00 | Winter | FALSE | nonsummer
2022-11-26 08:00 | 2022-11-26 09:00 | Winter | FALSE | nonsummer
2022-11-26 09:00 | 2022-11-26 10:00 | Winter | FALSE | nonsummer
2022-11-26 10:00 | 2022-11-26 11:00 | Winter | FALSE | nonsummer
2022-11-26 11:00 | 2022-11-26 12:00 | Winter | FALSE | nonsummer
2022-11-26 12:00 | 2022-11-26 13:00 | Winter | FALSE | nonsummer
2022-11-26 13:00 | 2022-11-26 14:00 | Winter | FALSE | nonsummer
2022-11-26 14:00 | 2022-11-26 15:00 | Winter | FALSE | nonsummer
2022-11-26 15:00 | 2022-11-26 16:00 | Winter | FALSE | nonsummer
2022-11-26 16:00 | 2022-11-26 17:00 | Winter | TRUE | nonsummer
2022-11-26 17:00 | 2022-11-26 18:00 | Winter | TRUE | nonsummer
2022-11-26 18:00 | 2022-11-26 19:00 | Winter | TRUE | nonsummer
2022-11-26 19:00 | 2022-11-26 20:00 | Winter | TRUE | nonsummer
2022-11-26 20:00 | 2022-11-26 21:00 | Winter | TRUE | nonsummer
2022-11-26 21:00 | 2022-11-26 22:00 | Winter | FALSE | nonsummer
2022-11-26 22:00 | 2022-11-26 23:00 | Winter | FALSE | nonsummer
2022-11-26 23:00 | 2022-11-27 | Winter | FALSE | nonsummer
2022-11-27 | 2022-11-27 01:00 | Winter | FALSE | nonsummer
2022-11-27 01:00 | 2022-11-27 02:00 | Winter | FALSE | nonsummer
2022-11-27 02:00 | 2022-11-27 03:00 | Winter | FALSE | nonsummer
2022-11-27 03:00 | 2022-11-27 04:00 | Winter | FALSE | nonsummer
2022-11-27 04:00 | 2022-11-27 05:00 | Winter | FALSE | nonsummer
2022-11-27 05:00 | 2022-11-27 06:00 | Winter | FALSE | nonsummer
2022-11-27 06:00 | 2022-11-27 07:00 | Winter | FALSE | nonsummer
2022-11-27 07:00 | 2022-11-27 08:00 | Winter | FALSE | nonsummer
2022-11-27 08:00 | 2022-11-27 09:00 | Winter | FALSE | nonsummer
2022-11-27 09:00 | 2022-11-27 10:00 | Winter | FALSE | nonsummer
2022-11-27 10:00 | 2022-11-27 11:00 | Winter | FALSE | nonsummer
2022-11-27 11:00 | 2022-11-27 12:00 | Winter | FALSE | nonsummer
2022-11-27 12:00 | 2022-11-27 13:00 | Winter | FALSE | nonsummer
2022-11-27 13:00 | 2022-11-27 14:00 | Winter | FALSE | nonsummer
2022-11-27 14:00 | 2022-11-27 15:00 | Winter | FALSE | nonsummer
2022-11-27 15:00 | 2022-11-27 16:00 | Winter | FALSE | nonsummer
2022-11-27 16:00 | 2022-11-27 17:00 | Winter | TRUE | nonsummer
2022-11-27 17:00 | 2022-11-27 18:00 | Winter | TRUE | nonsummer
2022-11-27 18:00 | 2022-11-27 19:00 | Winter | TRUE | nonsummer
2022-11-27 19:00 | 2022-11-27 20:00 | Winter | TRUE | nonsummer
2022-11-27 20:00 | 2022-11-27 21:00 | Winter | TRUE | nonsummer
2022-11-27 21:00 | 2022-11-27 22:00 | Winter | FALSE | nonsummer
2022-11-27 22:00 | 2022-11-27 23:00 | Winter | FALSE | nonsummer
2022-11-27 23:00 | 2022-11-28 | Winter | FALSE | nonsummer
2022-11-28 | 2022-11-28 01:00 | Winter | FALSE | nonsummer
2022-11-28 01:00 | 2022-11-28 02:00 | Winter | FALSE | nonsummer
2022-11-28 02:00 | 2022-11-28 03:00 | Winter | FALSE | nonsummer
2022-11-28 03:00 | 2022-11-28 04:00 | Winter | FALSE | nonsummer
2022-11-28 04:00 | 2022-11-28 05:00 | Winter | FALSE | nonsummer
2022-11-28 05:00 | 2022-11-28 06:00 | Winter | FALSE | nonsummer
2022-11-28 06:00 | 2022-11-28 07:00 | Winter | FALSE | nonsummer
2022-11-28 07:00 | 2022-11-28 08:00 | Winter | FALSE | nonsummer
2022-11-28 08:00 | 2022-11-28 09:00 | Winter | FALSE | nonsummer
2022-11-28 09:00 | 2022-11-28 10:00 | Winter | FALSE | nonsummer
2022-11-28 10:00 | 2022-11-28 11:00 | Winter | FALSE | nonsummer
2022-11-28 11:00 | 2022-11-28 12:00 | Winter | FALSE | nonsummer
2022-11-28 12:00 | 2022-11-28 13:00 | Winter | FALSE | nonsummer
2022-11-28 13:00 | 2022-11-28 14:00 | Winter | FALSE | nonsummer
2022-11-28 14:00 | 2022-11-28 15:00 | Winter | FALSE | nonsummer
2022-11-28 15:00 | 2022-11-28 16:00 | Winter | FALSE | nonsummer
2022-11-28 16:00 | 2022-11-28 17:00 | Winter | TRUE | nonsummer
2022-11-28 17:00 | 2022-11-28 18:00 | Winter | TRUE | nonsummer
2022-11-28 18:00 | 2022-11-28 19:00 | Winter | TRUE | nonsummer
2022-11-28 19:00 | 2022-11-28 20:00 | Winter | TRUE | nonsummer
2022-11-28 20:00 | 2022-11-28 21:00 | Winter | TRUE | nonsummer
2022-11-28 21:00 | 2022-11-28 22:00 | Winter | FALSE | nonsummer
2022-11-28 22:00 | 2022-11-28 23:00 | Winter | FALSE | nonsummer
2022-11-28 23:00 | 2022-11-29 | Winter | FALSE | nonsummer
2022-11-29 | 2022-11-29 01:00 | Winter | FALSE | nonsummer
2022-11-29 01:00 | 2022-11-29 02:00 | Winter | FALSE | nonsummer
2022-11-29 02:00 | 2022-11-29 03:00 | Winter | FALSE | nonsummer
2022-11-29 03:00 | 2022-11-29 04:00 | Winter | FALSE | nonsummer
2022-11-29 04:00 | 2022-11-29 05:00 | Winter | FALSE | nonsummer
2022-11-29 05:00 | 2022-11-29 06:00 | Winter | FALSE | nonsummer
2022-11-29 06:00 | 2022-11-29 07:00 | Winter | FALSE | nonsummer
2022-11-29 07:00 | 2022-11-29 08:00 | Winter | FALSE | nonsummer
2022-11-29 08:00 | 2022-11-29 09:00 | Winter | FALSE | nonsummer
2022-11-29 09:00 | 2022-11-29 10:00 | Winter | FALSE | nonsummer
2022-11-29 10:00 | 2022-11-29 11:00 | Winter | FALSE | nonsummer
2022-11-29 11:00 | 2022-11-29 12:00 | Winter | FALSE | nonsummer
2022-11-29 12:00 | 2022-11-29 13:00 | Winter | FALSE | nonsummer
2022-11-29 13:00 | 2022-11-29 14:00 | Winter | FALSE | nonsummer
2022-11-29 14:00 | 2022-11-29 15:00 | Winter | FALSE | nonsummer
2022-11-29 15:00 | 2022-11-29 16:00 | Winter | FALSE | nonsummer
2022-11-29 16:00 | 2022-11-29 17:00 | Winter | TRUE | nonsummer
2022-11-29 17:00 | 2022-11-29 18:00 | Winter | TRUE | nonsummer
2022-11-29 18:00 | 2022-11-29 19:00 | Winter | TRUE | nonsummer
2022-11-29 19:00 | 2022-11-29 20:00 | Winter | TRUE | nonsummer
2022-11-29 20:00 | 2022-11-29 21:00 | Winter | TRUE | nonsummer
2022-11-29 21:00 | 2022-11-29 22:00 | Winter | FALSE | nonsummer
2022-11-29 22:00 | 2022-11-29 23:00 | Winter | FALSE | nonsummer
2022-11-29 23:00 | 2022-11-30 | Winter | FALSE | nonsummer
2022-11-30 | 2022-11-30 01:00 | Winter | FALSE | nonsummer
2022-11-30 01:00 | 2022-11-30 02:00 | Winter | FALSE | nonsummer
2022-11-30 02:00 | 2022-11-30 03:00 | Winter | FALSE | nonsummer
2022-11-30 03:00 | 2022-11-30 04:00 | Winter | FALSE | nonsummer
2022-11-30 04:00 | 2022-11-30 05:00 | Winter | FALSE | nonsummer
2022-11-30 05:00 | 2022-11-30 06:00 | Winter | FALSE | nonsummer
2022-11-30 06:00 | 2022-11-30 07:00 | Winter | FALSE | nonsummer
2022-11-30 07:00 | 2022-11-30 08:00 | Winter | FALSE | nonsummer
2022-11-30 08:00 | 2022-11-30 09:00 | Winter | FALSE | nonsummer
2022-11-30 09:00 | 2022-11-30 10:00 | Winter | FALSE | nonsummer
2022-11-30 10:00 | 2022-11-30 11:00 | Winter | FALSE | nonsummer
2022-11-30 11:00 | 2022-11-30 12:00 | Winter | FALSE | nonsummer
2022-11-30 12:00 | 2022-11-30 13:00 | Winter | FALSE | nonsummer
2022-11-30 13:00 | 2022-11-30 14:00 | Winter | FALSE | nonsummer
2022-11-30 14:00 | 2022-11-30 15:00 | Winter | FALSE | nonsummer
2022-11-30 15:00 | 2022-11-30 16:00 | Winter | FALSE | nonsummer
2022-11-30 16:00 | 2022-11-30 17:00 | Winter | TRUE | nonsummer
2022-11-30 17:00 | 2022-11-30 18:00 | Winter | TRUE | nonsummer
2022-11-30 18:00 | 2022-11-30 19:00 | Winter | TRUE | nonsummer
2022-11-30 19:00 | 2022-11-30 20:00 | Winter | TRUE | nonsummer
2022-11-30 20:00 | 2022-11-30 21:00 | Winter | TRUE | nonsummer
2022-11-30 21:00 | 2022-11-30 22:00 | Winter | FALSE | nonsummer
2022-11-30 22:00 | 2022-11-30 23:00 | Winter | FALSE | nonsummer
2022-11-30 23:00 | 2022-12-01 | Winter | FALSE | nonsummer
2022-12-01 | 2022-12-01 01:00 | Winter | FALSE | nonsummer
2022-12-01 01:00 | 2022-12-01 02:00 | Winter | FALSE | nonsummer
2022-12-01 02:00 | 2022-12-01 03:00 | Winter | FALSE | nonsummer
2022-12-01 03:00 | 2022-12-01 04:00 | Winter | FALSE | nonsummer
2022-12-01 04:00 | 2022-12-01 05:00 | Winter | FALSE | nonsummer
2022-12-01 05:00 | 2022-12-01 06:00 | Winter | FALSE | nonsummer
2022-12-01 06:00 | 2022-12-01 07:00 | Winter | FALSE | nonsummer
2022-12-01 07:00 | 2022-12-01 08:00 | Winter | FALSE | nonsummer
2022-12-01 08:00 | 2022-12-01 09:00 | Winter | FALSE | nonsummer
2022-12-01 09:00 | 2022-12-01 10:00 | Winter | FALSE | nonsummer
2022-12-01 10:00 | 2022-12-01 11:00 | Winter | FALSE | nonsummer
2022-12-01 11:00 | 2022-12-01 12:00 | Winter | FALSE | nonsummer
2022-12-01 12:00 | 2022-12-01 13:00 | Winter | FALSE | nonsummer
2022-12-01 13:00 | 2022-12-01 14:00 | Winter | FALSE | nonsummer
2022-12-01 14:00 | 2022-12-01 15:00 | Winter | FALSE | nonsummer
2022-12-01 15:00 | 2022-12-01 16:00 | Winter | FALSE | nonsummer
2022-12-01 16:00 | 2022-12-01 17:00 | Winter | TRUE | nonsummer
2022-12-01 17:00 | 2022-12-01 18:00 | Winter | TRUE | nonsummer
2022-12-01 18:00 | 2022-12-01 19:00 | Winter | TRUE | nonsummer
2022-12-01 19:00 | 2022-12-01 20:00 | Winter | TRUE | nonsummer
2022-12-01 20:00 | 2022-12-01 21:00 | Winter | TRUE | nonsummer
2022-12-01 21:00 | 2022-12-01 22:00 | Winter | FALSE | nonsummer
2022-12-01 22:00 | 2022-12-01 23:00 | Winter | FALSE | nonsummer
2022-12-01 23:00 | 2022-12-02 | Winter | FALSE | nonsummer
2022-12-02 | 2022-12-02 01:00 | Winter | FALSE | nonsummer
2022-12-02 01:00 | 2022-12-02 02:00 | Winter | FALSE | nonsummer
2022-12-02 02:00 | 2022-12-02 03:00 | Winter | FALSE | nonsummer
2022-12-02 03:00 | 2022-12-02 04:00 | Winter | FALSE | nonsummer
2022-12-02 04:00 | 2022-12-02 05:00 | Winter | FALSE | nonsummer
2022-12-02 05:00 | 2022-12-02 06:00 | Winter | FALSE | nonsummer
2022-12-02 06:00 | 2022-12-02 07:00 | Winter | FALSE | nonsummer
2022-12-02 07:00 | 2022-12-02 08:00 | Winter | FALSE | nonsummer
2022-12-02 08:00 | 2022-12-02 09:00 | Winter | FALSE | nonsummer
2022-12-02 09:00 | 2022-12-02 10:00 | Winter | FALSE | nonsummer
2022-12-02 10:00 | 2022-12-02 11:00 | Winter | FALSE | nonsummer
2022-12-02 11:00 | 2022-12-02 12:00 | Winter | FALSE | nonsummer
2022-12-02 12:00 | 2022-12-02 13:00 | Winter | FALSE | nonsummer
2022-12-02 13:00 | 2022-12-02 14:00 | Winter | FALSE | nonsummer
2022-12-02 14:00 | 2022-12-02 15:00 | Winter | FALSE | nonsummer
2022-12-02 15:00 | 2022-12-02 16:00 | Winter | FALSE | nonsummer
2022-12-02 16:00 | 2022-12-02 17:00 | Winter | TRUE | nonsummer
2022-12-02 17:00 | 2022-12-02 18:00 | Winter | TRUE | nonsummer
2022-12-02 18:00 | 2022-12-02 19:00 | Winter | TRUE | nonsummer
2022-12-02 19:00 | 2022-12-02 20:00 | Winter | TRUE | nonsummer
2022-12-02 20:00 | 2022-12-02 21:00 | Winter | TRUE | nonsummer
2022-12-02 21:00 | 2022-12-02 22:00 | Winter | FALSE | nonsummer
2022-12-02 22:00 | 2022-12-02 23:00 | Winter | FALSE | nonsummer
2022-12-02 23:00 | 2022-12-03 | Winter | FALSE | nonsummer
2022-12-03 | 2022-12-03 01:00 | Winter | FALSE | nonsummer
2022-12-03 01:00 | 2022-12-03 02:00 | Winter | FALSE | nonsummer
2022-12-03 02:00 | 2022-12-03 03:00 | Winter | FALSE | nonsummer
2022-12-03 03:00 | 2022-12-03 04:00 | Winter | FALSE | nonsummer
2022-12-03 04:00 | 2022-12-03 05:00 | Winter | FALSE | nonsummer
2022-12-03 05:00 | 2022-12-03 06:00 | Winter | FALSE | nonsummer
2022-12-03 06:00 | 2022-12-03 07:00 | Winter | FALSE | nonsummer
2022-12-03 07:00 | 2022-12-03 08:00 | Winter | FALSE | nonsummer
2022-12-03 08:00 | 2022-12-03 09:00 | Winter | FALSE | nonsummer
2022-12-03 09:00 | 2022-12-03 10:00 | Winter | FALSE | nonsummer
2022-12-03 10:00 | 2022-12-03 11:00 | Winter | FALSE | nonsummer
2022-12-03 11:00 | 2022-12-03 12:00 | Winter | FALSE | nonsummer
2022-12-03 12:00 | 2022-12-03 13:00 | Winter | FALSE | nonsummer
2022-12-03 13:00 | 2022-12-03 14:00 | Winter | FALSE | nonsummer
2022-12-03 14:00 | 2022-12-03 15:00 | Winter | FALSE | nonsummer
2022-12-03 15:00 | 2022-12-03 16:00 | Winter | FALSE | nonsummer
2022-12-03 16:00 | 2022-12-03 17:00 | Winter | TRUE | nonsummer
2022-12-03 17:00 | 2022-12-03 18:00 | Winter | TRUE | nonsummer
2022-12-03 18:00 | 2022-12-03 19:00 | Winter | TRUE | nonsummer
2022-12-03 19:00 | 2022-12-03 20:00 | Winter | TRUE | nonsummer
2022-12-03 20:00 | 2022-12-03 21:00 | Winter | TRUE | nonsummer
2022-12-03 21:00 | 2022-12-03 22:00 | Winter | FALSE | nonsummer
2022-12-03 22:00 | 2022-12-03 23:00 | Winter | FALSE | nonsummer
2022-12-03 23:00 | 2022-12-04 | Winter | FALSE | nonsummer
2022-12-04 | 2022-12-04 01:00 | Winter | FALSE | nonsummer
2022-12-04 01:00 | 2022-12-04 02:00 | Winter | FALSE | nonsummer
2022-12-04 02:00 | 2022-12-04 03:00 | Winter | FALSE | nonsummer
2022-12-04 03:00 | 2022-12-04 04:00 | Winter | FALSE | nonsummer
2022-12-04 04:00 | 2022-12-04 05:00 | Winter | FALSE | nonsummer
2022-12-04 05:00 | 2022-12-04 06:00 | Winter | FALSE | nonsummer
2022-12-04 06:00 | 2022-12-04 07:00 | Winter | FALSE | nonsummer
2022-12-04 07:00 | 2022-12-04 08:00 | Winter | FALSE | nonsummer
2022-12-04 08:00 | 2022-12-04 09:00 | Winter | FALSE | nonsummer
2022-12-04 09:00 | 2022-12-04 10:00 | Winter | FALSE | nonsummer
2022-12-04 10:00 | 2022-12-04 11:00 | Winter | FALSE | nonsummer
2022-12-04 11:00 | 2022-12-04 12:00 | Winter | FALSE | nonsummer
2022-12-04 12:00 | 2022-12-04 13:00 | Winter | FALSE | nonsummer
2022-12-04 13:00 | 2022-12-04 14:00 | Winter | FALSE | nonsummer
2022-12-04 14:00 | 2022-12-04 15:00 | Winter | FALSE | nonsummer
2022-12-04 15:00 | 2022-12-04 16:00 | Winter | FALSE | nonsummer
2022-12-04 16:00 | 2022-12-04 17:00 | Winter | TRUE | nonsummer
2022-12-04 17:00 | 2022-12-04 18:00 | Winter | TRUE | nonsummer
2022-12-04 18:00 | 2022-12-04 19:00 | Winter | TRUE | nonsummer
2022-12-04 19:00 | 2022-12-04 20:00 | Winter | TRUE | nonsummer
2022-12-04 20:00 | 2022-12-04 21:00 | Winter | TRUE | nonsummer
2022-12-04 21:00 | 2022-12-04 22:00 | Winter | FALSE | nonsummer
2022-12-04 22:00 | 2022-12-04 23:00 | Winter | FALSE | nonsummer
2022-12-04 23:00 | 2022-12-05 | Winter | FALSE | nonsummer
2022-12-05 | 2022-12-05 01:00 | Winter | FALSE | nonsummer
2022-12-05 01:00 | 2022-12-05 02:00 | Winter | FALSE | nonsummer
2022-12-05 02:00 | 2022-12-05 03:00 | Winter | FALSE | nonsummer
2022-12-05 03:00 | 2022-12-05 04:00 | Winter | FALSE | nonsummer
2022-12-05 04:00 | 2022-12-05 05:00 | Winter | FALSE | nonsummer
2022-12-05 05:00 | 2022-12-05 06:00 | Winter | FALSE | nonsummer
2022-12-05 06:00 | 2022-12-05 07:00 | Winter | FALSE | nonsummer
2022-12-05 07:00 | 2022-12-05 08:00 | Winter | FALSE | nonsummer
2022-12-05 08:00 | 2022-12-05 09:00 | Winter | FALSE | nonsummer
2022-12-05 09:00 | 2022-12-05 10:00 | Winter | FALSE | nonsummer
2022-12-05 10:00 | 2022-12-05 11:00 | Winter | FALSE | nonsummer
2022-12-05 11:00 | 2022-12-05 12:00 | Winter | FALSE | nonsummer
2022-12-05 12:00 | 2022-12-05 13:00 | Winter | FALSE | nonsummer
2022-12-05 13:00 | 2022-12-05 14:00 | Winter | FALSE | nonsummer
2022-12-05 14:00 | 2022-12-05 15:00 | Winter | FALSE | nonsummer
2022-12-05 15:00 | 2022-12-05 16:00 | Winter | FALSE | nonsummer
2022-12-05 16:00 | 2022-12-05 17:00 | Winter | TRUE | nonsummer
2022-12-05 17:00 | 2022-12-05 18:00 | Winter | TRUE | nonsummer
2022-12-05 18:00 | 2022-12-05 19:00 | Winter | TRUE | nonsummer
2022-12-05 19:00 | 2022-12-05 20:00 | Winter | TRUE | nonsummer
2022-12-05 20:00 | 2022-12-05 21:00 | Winter | TRUE | nonsummer
2022-12-05 21:00 | 2022-12-05 22:00 | Winter | FALSE | nonsummer
2022-12-05 22:00 | 2022-12-05 23:00 | Winter | FALSE | nonsummer
2022-12-05 23:00 | 2022-12-06 | Winter | FALSE | nonsummer
2022-12-06 | 2022-12-06 01:00 | Winter | FALSE | nonsummer
2022-12-06 01:00 | 2022-12-06 02:00 | Winter | FALSE | nonsummer
2022-12-06 02:00 | 2022-12-06 03:00 | Winter | FALSE | nonsummer
2022-12-06 03:00 | 2022-12-06 04:00 | Winter | FALSE | nonsummer
2022-12-06 04:00 | 2022-12-06 05:00 | Winter | FALSE | nonsummer
2022-12-06 05:00 | 2022-12-06 06:00 | Winter | FALSE | nonsummer
2022-12-06 06:00 | 2022-12-06 07:00 | Winter | FALSE | nonsummer
2022-12-06 07:00 | 2022-12-06 08:00 | Winter | FALSE | nonsummer
2022-12-06 08:00 | 2022-12-06 09:00 | Winter | FALSE | nonsummer
2022-12-06 09:00 | 2022-12-06 10:00 | Winter | FALSE | nonsummer
2022-12-06 10:00 | 2022-12-06 11:00 | Winter | FALSE | nonsummer
2022-12-06 11:00 | 2022-12-06 12:00 | Winter | FALSE | nonsummer
2022-12-06 12:00 | 2022-12-06 13:00 | Winter | FALSE | nonsummer
2022-12-06 13:00 | 2022-12-06 14:00 | Winter | FALSE | nonsummer
2022-12-06 14:00 | 2022-12-06 15:00 | Winter | FALSE | nonsummer
2022-12-06 15:00 | 2022-12-06 16:00 | Winter | FALSE | nonsummer
2022-12-06 16:00 | 2022-12-06 17:00 | Winter | TRUE | nonsummer
2022-12-06 17:00 | 2022-12-06 18:00 | Winter | TRUE | nonsummer
2022-12-06 18:00 | 2022-12-06 19:00 | Winter | TRUE | nonsummer
2022-12-06 19:00 | 2022-12-06 20:00 | Winter | TRUE | nonsummer
2022-12-06 20:00 | 2022-12-06 21:00 | Winter | TRUE | nonsummer
2022-12-06 21:00 | 2022-12-06 22:00 | Winter | FALSE | nonsummer
2022-12-06 22:00 | 2022-12-06 23:00 | Winter | FALSE | nonsummer
2022-12-06 23:00 | 2022-12-07 | Winter | FALSE | nonsummer
2022-12-07 | 2022-12-07 01:00 | Winter | FALSE | nonsummer
2022-12-07 01:00 | 2022-12-07 02:00 | Winter | FALSE | nonsummer
2022-12-07 02:00 | 2022-12-07 03:00 | Winter | FALSE | nonsummer
2022-12-07 03:00 | 2022-12-07 04:00 | Winter | FALSE | nonsummer
2022-12-07 04:00 | 2022-12-07 05:00 | Winter | FALSE | nonsummer
2022-12-07 05:00 | 2022-12-07 06:00 | Winter | FALSE | nonsummer
2022-12-07 06:00 | 2022-12-07 07:00 | Winter | FALSE | nonsummer
2022-12-07 07:00 | 2022-12-07 08:00 | Winter | FALSE | nonsummer
2022-12-07 08:00 | 2022-12-07 09:00 | Winter | FALSE | nonsummer
2022-12-07 09:00 | 2022-12-07 10:00 | Winter | FALSE | nonsummer
2022-12-07 10:00 | 2022-12-07 11:00 | Winter | FALSE | nonsummer
2022-12-07 11:00 | 2022-12-07 12:00 | Winter | FALSE | nonsummer
2022-12-07 12:00 | 2022-12-07 13:00 | Winter | FALSE | nonsummer
2022-12-07 13:00 | 2022-12-07 14:00 | Winter | FALSE | nonsummer
2022-12-07 14:00 | 2022-12-07 15:00 | Winter | FALSE | nonsummer
2022-12-07 15:00 | 2022-12-07 16:00 | Winter | FALSE | nonsummer
2022-12-07 16:00 | 2022-12-07 17:00 | Winter | TRUE | nonsummer
2022-12-07 17:00 | 2022-12-07 18:00 | Winter | TRUE | nonsummer
2022-12-07 18:00 | 2022-12-07 19:00 | Winter | TRUE | nonsummer
2022-12-07 19:00 | 2022-12-07 20:00 | Winter | TRUE | nonsummer
2022-12-07 20:00 | 2022-12-07 21:00 | Winter | TRUE | nonsummer
2022-12-07 21:00 | 2022-12-07 22:00 | Winter | FALSE | nonsummer
2022-12-07 22:00 | 2022-12-07 23:00 | Winter | FALSE | nonsummer
2022-12-07 23:00 | 2022-12-08 | Winter | FALSE | nonsummer
2022-12-08 | 2022-12-08 01:00 | Winter | FALSE | nonsummer
2022-12-08 01:00 | 2022-12-08 02:00 | Winter | FALSE | nonsummer
2022-12-08 02:00 | 2022-12-08 03:00 | Winter | FALSE | nonsummer
2022-12-08 03:00 | 2022-12-08 04:00 | Winter | FALSE | nonsummer
2022-12-08 04:00 | 2022-12-08 05:00 | Winter | FALSE | nonsummer
2022-12-08 05:00 | 2022-12-08 06:00 | Winter | FALSE | nonsummer
2022-12-08 06:00 | 2022-12-08 07:00 | Winter | FALSE | nonsummer
2022-12-08 07:00 | 2022-12-08 08:00 | Winter | FALSE | nonsummer
2022-12-08 08:00 | 2022-12-08 09:00 | Winter | FALSE | nonsummer
2022-12-08 09:00 | 2022-12-08 10:00 | Winter | FALSE | nonsummer
2022-12-08 10:00 | 2022-12-08 11:00 | Winter | FALSE | nonsummer
2022-12-08 11:00 | 2022-12-08 12:00 | Winter | FALSE | nonsummer
2022-12-08 12:00 | 2022-12-08 13:00 | Winter | FALSE | nonsummer
2022-12-08 13:00 | 2022-12-08 14:00 | Winter | FALSE | nonsummer
2022-12-08 14:00 | 2022-12-08 15:00 | Winter | FALSE | nonsummer
2022-12-08 15:00 | 2022-12-08 16:00 | Winter | FALSE | nonsummer
2022-12-08 16:00 | 2022-12-08 17:00 | Winter | TRUE | nonsummer
2022-12-08 17:00 | 2022-12-08 18:00 | Winter | TRUE | nonsummer
2022-12-08 18:00 | 2022-12-08 19:00 | Winter | TRUE | nonsummer
2022-12-08 19:00 | 2022-12-08 20:00 | Winter | TRUE | nonsummer
2022-12-08 20:00 | 2022-12-08 21:00 | Winter | TRUE | nonsummer
2022-12-08 21:00 | 2022-12-08 22:00 | Winter | FALSE | nonsummer
2022-12-08 22:00 | 2022-12-08 23:00 | Winter | FALSE | nonsummer
2022-12-08 23:00 | 2022-12-09 | Winter | FALSE | nonsummer
2022-12-09 | 2022-12-09 01:00 | Winter | FALSE | nonsummer
2022-12-09 01:00 | 2022-12-09 02:00 | Winter | FALSE | nonsummer
2022-12-09 02:00 | 2022-12-09 03:00 | Winter | FALSE | nonsummer
2022-12-09 03:00 | 2022-12-09 04:00 | Winter | FALSE | nonsummer
2022-12-09 04:00 | 2022-12-09 05:00 | Winter | FALSE | nonsummer
2022-12-09 05:00 | 2022-12-09 06:00 | Winter | FALSE | nonsummer
2022-12-09 06:00 | 2022-12-09 07:00 | Winter | FALSE | nonsummer
2022-12-09 07:00 | 2022-12-09 08:00 | Winter | FALSE | nonsummer
2022-12-09 08:00 | 2022-12-09 09:00 | Winter | FALSE | nonsummer
2022-12-09 09:00 | 2022-12-09 10:00 | Winter | FALSE | nonsummer
2022-12-09 10:00 | 2022-12-09 11:00 | Winter | FALSE | nonsummer
2022-12-09 11:00 | 2022-12-09 12:00 | Winter | FALSE | nonsummer
2022-12-09 12:00 | 2022-12-09 13:00 | Winter | FALSE | nonsummer
2022-12-09 13:00 | 2022-12-09 14:00 | Winter | FALSE | nonsummer
2022-12-09 14:00 | 2022-12-09 15:00 | Winter | FALSE | nonsummer
2022-12-09 15:00 | 2022-12-09 16:00 | Winter | FALSE | nonsummer
2022-12-09 16:00 | 2022-12-09 17:00 | Winter | TRUE | nonsummer
2022-12-09 17:00 | 2022-12-09 18:00 | Winter | TRUE | nonsummer
2022-12-09 18:00 | 2022-12-09 19:00 | Winter | TRUE | nonsummer
2022-12-09 19:00 | 2022-12-09 20:00 | Winter | TRUE | nonsummer
2022-12-09 20:00 | 2022-12-09 21:00 | Winter | TRUE | nonsummer
2022-12-09 21:00 | 2022-12-09 22:00 | Winter | FALSE | nonsummer
2022-12-09 22:00 | 2022-12-09 23:00 | Winter | FALSE | nonsummer
2022-12-09 23:00 | 2022-12-10 | Winter | FALSE | nonsummer
2022-12-10 | 2022-12-10 01:00 | Winter | FALSE | nonsummer
2022-12-10 01:00 | 2022-12-10 02:00 | Winter | FALSE | nonsummer
2022-12-10 02:00 | 2022-12-10 03:00 | Winter | FALSE | nonsummer
2022-12-10 03:00 | 2022-12-10 04:00 | Winter | FALSE | nonsummer
2022-12-10 04:00 | 2022-12-10 05:00 | Winter | FALSE | nonsummer
2022-12-10 05:00 | 2022-12-10 06:00 | Winter | FALSE | nonsummer
2022-12-10 06:00 | 2022-12-10 07:00 | Winter | FALSE | nonsummer
2022-12-10 07:00 | 2022-12-10 08:00 | Winter | FALSE | nonsummer
2022-12-10 08:00 | 2022-12-10 09:00 | Winter | FALSE | nonsummer
2022-12-10 09:00 | 2022-12-10 10:00 | Winter | FALSE | nonsummer
2022-12-10 10:00 | 2022-12-10 11:00 | Winter | FALSE | nonsummer
2022-12-10 11:00 | 2022-12-10 12:00 | Winter | FALSE | nonsummer
2022-12-10 12:00 | 2022-12-10 13:00 | Winter | FALSE | nonsummer
2022-12-10 13:00 | 2022-12-10 14:00 | Winter | FALSE | nonsummer
2022-12-10 14:00 | 2022-12-10 15:00 | Winter | FALSE | nonsummer
2022-12-10 15:00 | 2022-12-10 16:00 | Winter | FALSE | nonsummer
2022-12-10 16:00 | 2022-12-10 17:00 | Winter | TRUE | nonsummer
2022-12-10 17:00 | 2022-12-10 18:00 | Winter | TRUE | nonsummer
2022-12-10 18:00 | 2022-12-10 19:00 | Winter | TRUE | nonsummer
2022-12-10 19:00 | 2022-12-10 20:00 | Winter | TRUE | nonsummer
2022-12-10 20:00 | 2022-12-10 21:00 | Winter | TRUE | nonsummer
2022-12-10 21:00 | 2022-12-10 22:00 | Winter | FALSE | nonsummer
2022-12-10 22:00 | 2022-12-10 23:00 | Winter | FALSE | nonsummer
2022-12-10 23:00 | 2022-12-11 | Winter | FALSE | nonsummer
2022-12-11 | 2022-12-11 01:00 | Winter | FALSE | nonsummer
2022-12-11 01:00 | 2022-12-11 02:00 | Winter | FALSE | nonsummer
2022-12-11 02:00 | 2022-12-11 03:00 | Winter | FALSE | nonsummer
2022-12-11 03:00 | 2022-12-11 04:00 | Winter | FALSE | nonsummer
2022-12-11 04:00 | 2022-12-11 05:00 | Winter | FALSE | nonsummer
2022-12-11 05:00 | 2022-12-11 06:00 | Winter | FALSE | nonsummer
2022-12-11 06:00 | 2022-12-11 07:00 | Winter | FALSE | nonsummer
2022-12-11 07:00 | 2022-12-11 08:00 | Winter | FALSE | nonsummer
2022-12-11 08:00 | 2022-12-11 09:00 | Winter | FALSE | nonsummer
2022-12-11 09:00 | 2022-12-11 10:00 | Winter | FALSE | nonsummer
2022-12-11 10:00 | 2022-12-11 11:00 | Winter | FALSE | nonsummer
2022-12-11 11:00 | 2022-12-11 12:00 | Winter | FALSE | nonsummer
2022-12-11 12:00 | 2022-12-11 13:00 | Winter | FALSE | nonsummer
2022-12-11 13:00 | 2022-12-11 14:00 | Winter | FALSE | nonsummer
2022-12-11 14:00 | 2022-12-11 15:00 | Winter | FALSE | nonsummer
2022-12-11 15:00 | 2022-12-11 16:00 | Winter | FALSE | nonsummer
2022-12-11 16:00 | 2022-12-11 17:00 | Winter | TRUE | nonsummer
2022-12-11 17:00 | 2022-12-11 18:00 | Winter | TRUE | nonsummer
2022-12-11 18:00 | 2022-12-11 19:00 | Winter | TRUE | nonsummer
2022-12-11 19:00 | 2022-12-11 20:00 | Winter | TRUE | nonsummer
2022-12-11 20:00 | 2022-12-11 21:00 | Winter | TRUE | nonsummer
2022-12-11 21:00 | 2022-12-11 22:00 | Winter | FALSE | nonsummer
2022-12-11 22:00 | 2022-12-11 23:00 | Winter | FALSE | nonsummer
2022-12-11 23:00 | 2022-12-12 | Winter | FALSE | nonsummer
2022-12-12 | 2022-12-12 01:00 | Winter | FALSE | nonsummer
2022-12-12 01:00 | 2022-12-12 02:00 | Winter | FALSE | nonsummer
2022-12-12 02:00 | 2022-12-12 03:00 | Winter | FALSE | nonsummer
2022-12-12 03:00 | 2022-12-12 04:00 | Winter | FALSE | nonsummer
2022-12-12 04:00 | 2022-12-12 05:00 | Winter | FALSE | nonsummer
2022-12-12 05:00 | 2022-12-12 06:00 | Winter | FALSE | nonsummer
2022-12-12 06:00 | 2022-12-12 07:00 | Winter | FALSE | nonsummer
2022-12-12 07:00 | 2022-12-12 08:00 | Winter | FALSE | nonsummer
2022-12-12 08:00 | 2022-12-12 09:00 | Winter | FALSE | nonsummer
2022-12-12 09:00 | 2022-12-12 10:00 | Winter | FALSE | nonsummer
2022-12-12 10:00 | 2022-12-12 11:00 | Winter | FALSE | nonsummer
2022-12-12 11:00 | 2022-12-12 12:00 | Winter | FALSE | nonsummer
2022-12-12 12:00 | 2022-12-12 13:00 | Winter | FALSE | nonsummer
2022-12-12 13:00 | 2022-12-12 14:00 | Winter | FALSE | nonsummer
2022-12-12 14:00 | 2022-12-12 15:00 | Winter | FALSE | nonsummer
2022-12-12 15:00 | 2022-12-12 16:00 | Winter | FALSE | nonsummer
2022-12-12 16:00 | 2022-12-12 17:00 | Winter | TRUE | nonsummer
2022-12-12 17:00 | 2022-12-12 18:00 | Winter | TRUE | nonsummer
2022-12-12 18:00 | 2022-12-12 19:00 | Winter | TRUE | nonsummer
2022-12-12 19:00 | 2022-12-12 20:00 | Winter | TRUE | nonsummer
2022-12-12 20:00 | 2022-12-12 21:00 | Winter | TRUE | nonsummer
2022-12-12 21:00 | 2022-12-12 22:00 | Winter | FALSE | nonsummer
2022-12-12 22:00 | 2022-12-12 23:00 | Winter | FALSE | nonsummer
2022-12-12 23:00 | 2022-12-13 | Winter | FALSE | nonsummer
2022-12-13 | 2022-12-13 01:00 | Winter | FALSE | nonsummer
2022-12-13 01:00 | 2022-12-13 02:00 | Winter | FALSE | nonsummer
2022-12-13 02:00 | 2022-12-13 03:00 | Winter | FALSE | nonsummer
2022-12-13 03:00 | 2022-12-13 04:00 | Winter | FALSE | nonsummer
2022-12-13 04:00 | 2022-12-13 05:00 | Winter | FALSE | nonsummer
2022-12-13 05:00 | 2022-12-13 06:00 | Winter | FALSE | nonsummer
2022-12-13 06:00 | 2022-12-13 07:00 | Winter | FALSE | nonsummer
2022-12-13 07:00 | 2022-12-13 08:00 | Winter | FALSE | nonsummer
2022-12-13 08:00 | 2022-12-13 09:00 | Winter | FALSE | nonsummer
2022-12-13 09:00 | 2022-12-13 10:00 | Winter | FALSE | nonsummer
2022-12-13 10:00 | 2022-12-13 11:00 | Winter | FALSE | nonsummer
2022-12-13 11:00 | 2022-12-13 12:00 | Winter | FALSE | nonsummer
2022-12-13 12:00 | 2022-12-13 13:00 | Winter | FALSE | nonsummer
2022-12-13 13:00 | 2022-12-13 14:00 | Winter | FALSE | nonsummer
2022-12-13 14:00 | 2022-12-13 15:00 | Winter | FALSE | nonsummer
2022-12-13 15:00 | 2022-12-13 16:00 | Winter | FALSE | nonsummer
2022-12-13 16:00 | 2022-12-13 17:00 | Winter | TRUE | nonsummer
2022-12-13 17:00 | 2022-12-13 18:00 | Winter | TRUE | nonsummer
2022-12-13 18:00 | 2022-12-13 19:00 | Winter | TRUE | nonsummer
2022-12-13 19:00 | 2022-12-13 20:00 | Winter | TRUE | nonsummer
2022-12-13 20:00 | 2022-12-13 21:00 | Winter | TRUE | nonsummer
2022-12-13 21:00 | 2022-12-13 22:00 | Winter | FALSE | nonsummer
2022-12-13 22:00 | 2022-12-13 23:00 | Winter | FALSE | nonsummer
2022-12-13 23:00 | 2022-12-14 | Winter | FALSE | nonsummer
2022-12-14 | 2022-12-14 01:00 | Winter | FALSE | nonsummer
2022-12-14 01:00 | 2022-12-14 02:00 | Winter | FALSE | nonsummer
2022-12-14 02:00 | 2022-12-14 03:00 | Winter | FALSE | nonsummer
2022-12-14 03:00 | 2022-12-14 04:00 | Winter | FALSE | nonsummer
2022-12-14 04:00 | 2022-12-14 05:00 | Winter | FALSE | nonsummer
2022-12-14 05:00 | 2022-12-14 06:00 | Winter | FALSE | nonsummer
2022-12-14 06:00 | 2022-12-14 07:00 | Winter | FALSE | nonsummer
2022-12-14 07:00 | 2022-12-14 08:00 | Winter | FALSE | nonsummer
2022-12-14 08:00 | 2022-12-14 09:00 | Winter | FALSE | nonsummer
2022-12-14 09:00 | 2022-12-14 10:00 | Winter | FALSE | nonsummer
2022-12-14 10:00 | 2022-12-14 11:00 | Winter | FALSE | nonsummer
2022-12-14 11:00 | 2022-12-14 12:00 | Winter | FALSE | nonsummer
2022-12-14 12:00 | 2022-12-14 13:00 | Winter | FALSE | nonsummer
2022-12-14 13:00 | 2022-12-14 14:00 | Winter | FALSE | nonsummer
2022-12-14 14:00 | 2022-12-14 15:00 | Winter | FALSE | nonsummer
2022-12-14 15:00 | 2022-12-14 16:00 | Winter | FALSE | nonsummer
2022-12-14 16:00 | 2022-12-14 17:00 | Winter | TRUE | nonsummer
2022-12-14 17:00 | 2022-12-14 18:00 | Winter | TRUE | nonsummer
2022-12-14 18:00 | 2022-12-14 19:00 | Winter | TRUE | nonsummer
2022-12-14 19:00 | 2022-12-14 20:00 | Winter | TRUE | nonsummer
2022-12-14 20:00 | 2022-12-14 21:00 | Winter | TRUE | nonsummer
2022-12-14 21:00 | 2022-12-14 22:00 | Winter | FALSE | nonsummer
2022-12-14 22:00 | 2022-12-14 23:00 | Winter | FALSE | nonsummer
2022-12-14 23:00 | 2022-12-15 | Winter | FALSE | nonsummer
2022-12-15 | 2022-12-15 01:00 | Winter | FALSE | nonsummer
2022-12-15 01:00 | 2022-12-15 02:00 | Winter | FALSE | nonsummer
2022-12-15 02:00 | 2022-12-15 03:00 | Winter | FALSE | nonsummer
2022-12-15 03:00 | 2022-12-15 04:00 | Winter | FALSE | nonsummer
2022-12-15 04:00 | 2022-12-15 05:00 | Winter | FALSE | nonsummer
2022-12-15 05:00 | 2022-12-15 06:00 | Winter | FALSE | nonsummer
2022-12-15 06:00 | 2022-12-15 07:00 | Winter | FALSE | nonsummer
2022-12-15 07:00 | 2022-12-15 08:00 | Winter | FALSE | nonsummer
2022-12-15 08:00 | 2022-12-15 09:00 | Winter | FALSE | nonsummer
2022-12-15 09:00 | 2022-12-15 10:00 | Winter | FALSE | nonsummer
2022-12-15 10:00 | 2022-12-15 11:00 | Winter | FALSE | nonsummer
2022-12-15 11:00 | 2022-12-15 12:00 | Winter | FALSE | nonsummer
2022-12-15 12:00 | 2022-12-15 13:00 | Winter | FALSE | nonsummer
2022-12-15 13:00 | 2022-12-15 14:00 | Winter | FALSE | nonsummer
2022-12-15 14:00 | 2022-12-15 15:00 | Winter | FALSE | nonsummer
2022-12-15 15:00 | 2022-12-15 16:00 | Winter | FALSE | nonsummer
2022-12-15 16:00 | 2022-12-15 17:00 | Winter | TRUE | nonsummer
2022-12-15 17:00 | 2022-12-15 18:00 | Winter | TRUE | nonsummer
2022-12-15 18:00 | 2022-12-15 19:00 | Winter | TRUE | nonsummer
2022-12-15 19:00 | 2022-12-15 20:00 | Winter | TRUE | nonsummer
2022-12-15 20:00 | 2022-12-15 21:00 | Winter | TRUE | nonsummer
2022-12-15 21:00 | 2022-12-15 22:00 | Winter | FALSE | nonsummer
2022-12-15 22:00 | 2022-12-15 23:00 | Winter | FALSE | nonsummer
2022-12-15 23:00 | 2022-12-16 | Winter | FALSE | nonsummer
2022-12-16 | 2022-12-16 01:00 | Winter | FALSE | nonsummer
2022-12-16 01:00 | 2022-12-16 02:00 | Winter | FALSE | nonsummer
2022-12-16 02:00 | 2022-12-16 03:00 | Winter | FALSE | nonsummer
2022-12-16 03:00 | 2022-12-16 04:00 | Winter | FALSE | nonsummer
2022-12-16 04:00 | 2022-12-16 05:00 | Winter | FALSE | nonsummer
2022-12-16 05:00 | 2022-12-16 06:00 | Winter | FALSE | nonsummer
2022-12-16 06:00 | 2022-12-16 07:00 | Winter | FALSE | nonsummer
2022-12-16 07:00 | 2022-12-16 08:00 | Winter | FALSE | nonsummer
2022-12-16 08:00 | 2022-12-16 09:00 | Winter | FALSE | nonsummer
2022-12-16 09:00 | 2022-12-16 10:00 | Winter | FALSE | nonsummer
2022-12-16 10:00 | 2022-12-16 11:00 | Winter | FALSE | nonsummer
2022-12-16 11:00 | 2022-12-16 12:00 | Winter | FALSE | nonsummer
2022-12-16 12:00 | 2022-12-16 13:00 | Winter | FALSE | nonsummer
2022-12-16 13:00 | 2022-12-16 14:00 | Winter | FALSE | nonsummer
2022-12-16 14:00 | 2022-12-16 15:00 | Winter | FALSE | nonsummer
2022-12-16 15:00 | 2022-12-16 16:00 | Winter | FALSE | nonsummer
2022-12-16 16:00 | 2022-12-16 17:00 | Winter | TRUE | nonsummer
2022-12-16 17:00 | 2022-12-16 18:00 | Winter | TRUE | nonsummer
2022-12-16 18:00 | 2022-12-16 19:00 | Winter | TRUE | nonsummer
2022-12-16 19:00 | 2022-12-16 20:00 | Winter | TRUE | nonsummer
2022-12-16 20:00 | 2022-12-16 21:00 | Winter | TRUE | nonsummer
2022-12-16 21:00 | 2022-12-16 22:00 | Winter | FALSE | nonsummer
2022-12-16 22:00 | 2022-12-16 23:00 | Winter | FALSE | nonsummer
2022-12-16 23:00 | 2022-12-17 | Winter | FALSE | nonsummer
2022-12-17 | 2022-12-17 01:00 | Winter | FALSE | nonsummer
2022-12-17 01:00 | 2022-12-17 02:00 | Winter | FALSE | nonsummer
2022-12-17 02:00 | 2022-12-17 03:00 | Winter | FALSE | nonsummer
2022-12-17 03:00 | 2022-12-17 04:00 | Winter | FALSE | nonsummer
2022-12-17 04:00 | 2022-12-17 05:00 | Winter | FALSE | nonsummer
2022-12-17 05:00 | 2022-12-17 06:00 | Winter | FALSE | nonsummer
2022-12-17 06:00 | 2022-12-17 07:00 | Winter | FALSE | nonsummer
2022-12-17 07:00 | 2022-12-17 08:00 | Winter | FALSE | nonsummer
2022-12-17 08:00 | 2022-12-17 09:00 | Winter | FALSE | nonsummer
2022-12-17 09:00 | 2022-12-17 10:00 | Winter | FALSE | nonsummer
2022-12-17 10:00 | 2022-12-17 11:00 | Winter | FALSE | nonsummer
2022-12-17 11:00 | 2022-12-17 12:00 | Winter | FALSE | nonsummer
2022-12-17 12:00 | 2022-12-17 13:00 | Winter | FALSE | nonsummer
2022-12-17 13:00 | 2022-12-17 14:00 | Winter | FALSE | nonsummer
2022-12-17 14:00 | 2022-12-17 15:00 | Winter | FALSE | nonsummer
2022-12-17 15:00 | 2022-12-17 16:00 | Winter | FALSE | nonsummer
2022-12-17 16:00 | 2022-12-17 17:00 | Winter | TRUE | nonsummer
2022-12-17 17:00 | 2022-12-17 18:00 | Winter | TRUE | nonsummer
2022-12-17 18:00 | 2022-12-17 19:00 | Winter | TRUE | nonsummer
2022-12-17 19:00 | 2022-12-17 20:00 | Winter | TRUE | nonsummer
2022-12-17 20:00 | 2022-12-17 21:00 | Winter | TRUE | nonsummer
2022-12-17 21:00 | 2022-12-17 22:00 | Winter | FALSE | nonsummer
2022-12-17 22:00 | 2022-12-17 23:00 | Winter | FALSE | nonsummer
2022-12-17 23:00 | 2022-12-18 | Winter | FALSE | nonsummer
2022-12-18 | 2022-12-18 01:00 | Winter | FALSE | nonsummer
2022-12-18 01:00 | 2022-12-18 02:00 | Winter | FALSE | nonsummer
2022-12-18 02:00 | 2022-12-18 03:00 | Winter | FALSE | nonsummer
2022-12-18 03:00 | 2022-12-18 04:00 | Winter | FALSE | nonsummer
2022-12-18 04:00 | 2022-12-18 05:00 | Winter | FALSE | nonsummer
2022-12-18 05:00 | 2022-12-18 06:00 | Winter | FALSE | nonsummer
2022-12-18 06:00 | 2022-12-18 07:00 | Winter | FALSE | nonsummer
2022-12-18 07:00 | 2022-12-18 08:00 | Winter | FALSE | nonsummer
2022-12-18 08:00 | 2022-12-18 09:00 | Winter | FALSE | nonsummer
2022-12-18 09:00 | 2022-12-18 10:00 | Winter | FALSE | nonsummer
2022-12-18 10:00 | 2022-12-18 11:00 | Winter | FALSE | nonsummer
2022-12-18 11:00 | 2022-12-18 12:00 | Winter | FALSE | nonsummer
2022-12-18 12:00 | 2022-12-18 13:00 | Winter | FALSE | nonsummer
2022-12-18 13:00 | 2022-12-18 14:00 | Winter | FALSE | nonsummer
2022-12-18 14:00 | 2022-12-18 15:00 | Winter | FALSE | nonsummer
2022-12-18 15:00 | 2022-12-18 16:00 | Winter | FALSE | nonsummer
2022-12-18 16:00 | 2022-12-18 17:00 | Winter | TRUE | nonsummer
2022-12-18 17:00 | 2022-12-18 18:00 | Winter | TRUE | nonsummer
2022-12-18 18:00 | 2022-12-18 19:00 | Winter | TRUE | nonsummer
2022-12-18 19:00 | 2022-12-18 20:00 | Winter | TRUE | nonsummer
2022-12-18 20:00 | 2022-12-18 21:00 | Winter | TRUE | nonsummer
2022-12-18 21:00 | 2022-12-18 22:00 | Winter | FALSE | nonsummer
2022-12-18 22:00 | 2022-12-18 23:00 | Winter | FALSE | nonsummer
2022-12-18 23:00 | 2022-12-19 | Winter | FALSE | nonsummer
2022-12-19 | 2022-12-19 01:00 | Winter | FALSE | nonsummer
2022-12-19 01:00 | 2022-12-19 02:00 | Winter | FALSE | nonsummer
2022-12-19 02:00 | 2022-12-19 03:00 | Winter | FALSE | nonsummer
2022-12-19 03:00 | 2022-12-19 04:00 | Winter | FALSE | nonsummer
2022-12-19 04:00 | 2022-12-19 05:00 | Winter | FALSE | nonsummer
2022-12-19 05:00 | 2022-12-19 06:00 | Winter | FALSE | nonsummer
2022-12-19 06:00 | 2022-12-19 07:00 | Winter | FALSE | nonsummer
2022-12-19 07:00 | 2022-12-19 08:00 | Winter | FALSE | nonsummer
2022-12-19 08:00 | 2022-12-19 09:00 | Winter | FALSE | nonsummer
2022-12-19 09:00 | 2022-12-19 10:00 | Winter | FALSE | nonsummer
2022-12-19 10:00 | 2022-12-19 11:00 | Winter | FALSE | nonsummer
2022-12-19 11:00 | 2022-12-19 12:00 | Winter | FALSE | nonsummer
2022-12-19 12:00 | 2022-12-19 13:00 | Winter | FALSE | nonsummer
2022-12-19 13:00 | 2022-12-19 14:00 | Winter | FALSE | nonsummer
2022-12-19 14:00 | 2022-12-19 15:00 | Winter | FALSE | nonsummer
2022-12-19 15:00 | 2022-12-19 16:00 | Winter | FALSE | nonsummer
2022-12-19 16:00 | 2022-12-19 17:00 | Winter | TRUE | nonsummer
2022-12-19 17:00 | 2022-12-19 18:00 | Winter | TRUE | nonsummer
2022-12-19 18:00 | 2022-12-19 19:00 | Winter | TRUE | nonsummer
2022-12-19 19:00 | 2022-12-19 20:00 | Winter | TRUE | nonsummer
2022-12-19 20:00 | 2022-12-19 21:00 | Winter | TRUE | nonsummer
2022-12-19 21:00 | 2022-12-19 22:00 | Winter | FALSE | nonsummer
2022-12-19 22:00 | 2022-12-19 23:00 | Winter | FALSE | nonsummer
2022-12-19 23:00 | 2022-12-20 | Winter | FALSE | nonsummer
2022-12-20 | 2022-12-20 01:00 | Winter | FALSE | nonsummer
2022-12-20 01:00 | 2022-12-20 02:00 | Winter | FALSE | nonsummer
2022-12-20 02:00 | 2022-12-20 03:00 | Winter | FALSE | nonsummer
2022-12-20 03:00 | 2022-12-20 04:00 | Winter | FALSE | nonsummer
2022-12-20 04:00 | 2022-12-20 05:00 | Winter | FALSE | nonsummer
2022-12-20 05:00 | 2022-12-20 06:00 | Winter | FALSE | nonsummer
2022-12-20 06:00 | 2022-12-20 07:00 | Winter | FALSE | nonsummer
2022-12-20 07:00 | 2022-12-20 08:00 | Winter | FALSE | nonsummer
2022-12-20 08:00 | 2022-12-20 09:00 | Winter | FALSE | nonsummer
2022-12-20 09:00 | 2022-12-20 10:00 | Winter | FALSE | nonsummer
2022-12-20 10:00 | 2022-12-20 11:00 | Winter | FALSE | nonsummer
2022-12-20 11:00 | 2022-12-20 12:00 | Winter | FALSE | nonsummer
2022-12-20 12:00 | 2022-12-20 13:00 | Winter | FALSE | nonsummer
2022-12-20 13:00 | 2022-12-20 14:00 | Winter | FALSE | nonsummer
2022-12-20 14:00 | 2022-12-20 15:00 | Winter | FALSE | nonsummer
2022-12-20 15:00 | 2022-12-20 16:00 | Winter | FALSE | nonsummer
2022-12-20 16:00 | 2022-12-20 17:00 | Winter | TRUE | nonsummer
2022-12-20 17:00 | 2022-12-20 18:00 | Winter | TRUE | nonsummer
2022-12-20 18:00 | 2022-12-20 19:00 | Winter | TRUE | nonsummer
2022-12-20 19:00 | 2022-12-20 20:00 | Winter | TRUE | nonsummer
2022-12-20 20:00 | 2022-12-20 21:00 | Winter | TRUE | nonsummer
2022-12-20 21:00 | 2022-12-20 22:00 | Winter | FALSE | nonsummer
2022-12-20 22:00 | 2022-12-20 23:00 | Winter | FALSE | nonsummer
2022-12-20 23:00 | 2022-12-21 | Winter | FALSE | nonsummer
2022-12-21 | 2022-12-21 01:00 | Winter | FALSE | nonsummer
2022-12-21 01:00 | 2022-12-21 02:00 | Winter | FALSE | nonsummer
2022-12-21 02:00 | 2022-12-21 03:00 | Winter | FALSE | nonsummer
2022-12-21 03:00 | 2022-12-21 04:00 | Winter | FALSE | nonsummer
2022-12-21 04:00 | 2022-12-21 05:00 | Winter | FALSE | nonsummer
2022-12-21 05:00 | 2022-12-21 06:00 | Winter | FALSE | nonsummer
2022-12-21 06:00 | 2022-12-21 07:00 | Winter | FALSE | nonsummer
2022-12-21 07:00 | 2022-12-21 08:00 | Winter | FALSE | nonsummer
2022-12-21 08:00 | 2022-12-21 09:00 | Winter | FALSE | nonsummer
2022-12-21 09:00 | 2022-12-21 10:00 | Winter | FALSE | nonsummer
2022-12-21 10:00 | 2022-12-21 11:00 | Winter | FALSE | nonsummer
2022-12-21 11:00 | 2022-12-21 12:00 | Winter | FALSE | nonsummer
2022-12-21 12:00 | 2022-12-21 13:00 | Winter | FALSE | nonsummer
2022-12-21 13:00 | 2022-12-21 14:00 | Winter | FALSE | nonsummer
2022-12-21 14:00 | 2022-12-21 15:00 | Winter | FALSE | nonsummer
2022-12-21 15:00 | 2022-12-21 16:00 | Winter | FALSE | nonsummer
2022-12-21 16:00 | 2022-12-21 17:00 | Winter | TRUE | nonsummer
2022-12-21 17:00 | 2022-12-21 18:00 | Winter | TRUE | nonsummer
2022-12-21 18:00 | 2022-12-21 19:00 | Winter | TRUE | nonsummer
2022-12-21 19:00 | 2022-12-21 20:00 | Winter | TRUE | nonsummer
2022-12-21 20:00 | 2022-12-21 21:00 | Winter | TRUE | nonsummer
2022-12-21 21:00 | 2022-12-21 22:00 | Winter | FALSE | nonsummer
2022-12-21 22:00 | 2022-12-21 23:00 | Winter | FALSE | nonsummer
2022-12-21 23:00 | 2022-12-22 | Winter | FALSE | nonsummer
2022-12-22 | 2022-12-22 01:00 | Winter | FALSE | nonsummer
2022-12-22 01:00 | 2022-12-22 02:00 | Winter | FALSE | nonsummer
2022-12-22 02:00 | 2022-12-22 03:00 | Winter | FALSE | nonsummer
2022-12-22 03:00 | 2022-12-22 04:00 | Winter | FALSE | nonsummer
2022-12-22 04:00 | 2022-12-22 05:00 | Winter | FALSE | nonsummer
2022-12-22 05:00 | 2022-12-22 06:00 | Winter | FALSE | nonsummer
2022-12-22 06:00 | 2022-12-22 07:00 | Winter | FALSE | nonsummer
2022-12-22 07:00 | 2022-12-22 08:00 | Winter | FALSE | nonsummer
2022-12-22 08:00 | 2022-12-22 09:00 | Winter | FALSE | nonsummer
2022-12-22 09:00 | 2022-12-22 10:00 | Winter | FALSE | nonsummer
2022-12-22 10:00 | 2022-12-22 11:00 | Winter | FALSE | nonsummer
2022-12-22 11:00 | 2022-12-22 12:00 | Winter | FALSE | nonsummer
2022-12-22 12:00 | 2022-12-22 13:00 | Winter | FALSE | nonsummer
2022-12-22 13:00 | 2022-12-22 14:00 | Winter | FALSE | nonsummer
2022-12-22 14:00 | 2022-12-22 15:00 | Winter | FALSE | nonsummer
2022-12-22 15:00 | 2022-12-22 16:00 | Winter | FALSE | nonsummer
2022-12-22 16:00 | 2022-12-22 17:00 | Winter | TRUE | nonsummer
2022-12-22 17:00 | 2022-12-22 18:00 | Winter | TRUE | nonsummer
2022-12-22 18:00 | 2022-12-22 19:00 | Winter | TRUE | nonsummer
2022-12-22 19:00 | 2022-12-22 20:00 | Winter | TRUE | nonsummer
2022-12-22 20:00 | 2022-12-22 21:00 | Winter | TRUE | nonsummer
2022-12-22 21:00 | 2022-12-22 22:00 | Winter | FALSE | nonsummer
2022-12-22 22:00 | 2022-12-22 23:00 | Winter | FALSE | nonsummer
2022-12-22 23:00 | 2022-12-23 | Winter | FALSE | nonsummer
2022-12-23 | 2022-12-23 01:00 | Winter | FALSE | nonsummer
2022-12-23 01:00 | 2022-12-23 02:00 | Winter | FALSE | nonsummer
2022-12-23 02:00 | 2022-12-23 03:00 | Winter | FALSE | nonsummer
2022-12-23 03:00 | 2022-12-23 04:00 | Winter | FALSE | nonsummer
2022-12-23 04:00 | 2022-12-23 05:00 | Winter | FALSE | nonsummer
2022-12-23 05:00 | 2022-12-23 06:00 | Winter | FALSE | nonsummer
2022-12-23 06:00 | 2022-12-23 07:00 | Winter | FALSE | nonsummer
2022-12-23 07:00 | 2022-12-23 08:00 | Winter | FALSE | nonsummer
2022-12-23 08:00 | 2022-12-23 09:00 | Winter | FALSE | nonsummer
2022-12-23 09:00 | 2022-12-23 10:00 | Winter | FALSE | nonsummer
2022-12-23 10:00 | 2022-12-23 11:00 | Winter | FALSE | nonsummer
2022-12-23 11:00 | 2022-12-23 12:00 | Winter | FALSE | nonsummer
2022-12-23 12:00 | 2022-12-23 13:00 | Winter | FALSE | nonsummer
2022-12-23 13:00 | 2022-12-23 14:00 | Winter | FALSE | nonsummer
2022-12-23 14:00 | 2022-12-23 15:00 | Winter | FALSE | nonsummer
2022-12-23 15:00 | 2022-12-23 16:00 | Winter | FALSE | nonsummer
2022-12-23 16:00 | 2022-12-23 17:00 | Winter | TRUE | nonsummer
2022-12-23 17:00 | 2022-12-23 18:00 | Winter | TRUE | nonsummer
2022-12-23 18:00 | 2022-12-23 19:00 | Winter | TRUE | nonsummer
2022-12-23 19:00 | 2022-12-23 20:00 | Winter | TRUE | nonsummer
2022-12-23 20:00 | 2022-12-23 21:00 | Winter | TRUE | nonsummer
2022-12-23 21:00 | 2022-12-23 22:00 | Winter | FALSE | nonsummer
2022-12-23 22:00 | 2022-12-23 23:00 | Winter | FALSE | nonsummer
2022-12-23 23:00 | 2022-12-24 | Winter | FALSE | nonsummer
2022-12-24 | 2022-12-24 01:00 | Winter | FALSE | nonsummer
2022-12-24 01:00 | 2022-12-24 02:00 | Winter | FALSE | nonsummer
2022-12-24 02:00 | 2022-12-24 03:00 | Winter | FALSE | nonsummer
2022-12-24 03:00 | 2022-12-24 04:00 | Winter | FALSE | nonsummer
2022-12-24 04:00 | 2022-12-24 05:00 | Winter | FALSE | nonsummer
2022-12-24 05:00 | 2022-12-24 06:00 | Winter | FALSE | nonsummer
2022-12-24 06:00 | 2022-12-24 07:00 | Winter | FALSE | nonsummer
2022-12-24 07:00 | 2022-12-24 08:00 | Winter | FALSE | nonsummer
2022-12-24 08:00 | 2022-12-24 09:00 | Winter | FALSE | nonsummer
2022-12-24 09:00 | 2022-12-24 10:00 | Winter | FALSE | nonsummer
2022-12-24 10:00 | 2022-12-24 11:00 | Winter | FALSE | nonsummer
2022-12-24 11:00 | 2022-12-24 12:00 | Winter | FALSE | nonsummer
2022-12-24 12:00 | 2022-12-24 13:00 | Winter | FALSE | nonsummer
2022-12-24 13:00 | 2022-12-24 14:00 | Winter | FALSE | nonsummer
2022-12-24 14:00 | 2022-12-24 15:00 | Winter | FALSE | nonsummer
2022-12-24 15:00 | 2022-12-24 16:00 | Winter | FALSE | nonsummer
2022-12-24 16:00 | 2022-12-24 17:00 | Winter | TRUE | nonsummer
2022-12-24 17:00 | 2022-12-24 18:00 | Winter | TRUE | nonsummer
2022-12-24 18:00 | 2022-12-24 19:00 | Winter | TRUE | nonsummer
2022-12-24 19:00 | 2022-12-24 20:00 | Winter | TRUE | nonsummer
2022-12-24 20:00 | 2022-12-24 21:00 | Winter | TRUE | nonsummer
2022-12-24 21:00 | 2022-12-24 22:00 | Winter | FALSE | nonsummer
2022-12-24 22:00 | 2022-12-24 23:00 | Winter | FALSE | nonsummer
2022-12-24 23:00 | 2022-12-25 | Winter | FALSE | nonsummer
2022-12-25 | 2022-12-25 01:00 | Winter | FALSE | nonsummer
2022-12-25 01:00 | 2022-12-25 02:00 | Winter | FALSE | nonsummer
2022-12-25 02:00 | 2022-12-25 03:00 | Winter | FALSE | nonsummer
2022-12-25 03:00 | 2022-12-25 04:00 | Winter | FALSE | nonsummer
2022-12-25 04:00 | 2022-12-25 05:00 | Winter | FALSE | nonsummer
2022-12-25 05:00 | 2022-12-25 06:00 | Winter | FALSE | nonsummer
2022-12-25 06:00 | 2022-12-25 07:00 | Winter | FALSE | nonsummer
2022-12-25 07:00 | 2022-12-25 08:00 | Winter | FALSE | nonsummer
2022-12-25 08:00 | 2022-12-25 09:00 | Winter | FALSE | nonsummer
2022-12-25 09:00 | 2022-12-25 10:00 | Winter | FALSE | nonsummer
2022-12-25 10:00 | 2022-12-25 11:00 | Winter | FALSE | nonsummer
2022-12-25 11:00 | 2022-12-25 12:00 | Winter | FALSE | nonsummer
2022-12-25 12:00 | 2022-12-25 13:00 | Winter | FALSE | nonsummer
2022-12-25 13:00 | 2022-12-25 14:00 | Winter | FALSE | nonsummer
2022-12-25 14:00 | 2022-12-25 15:00 | Winter | FALSE | nonsummer
2022-12-25 15:00 | 2022-12-25 16:00 | Winter | FALSE | nonsummer
2022-12-25 16:00 | 2022-12-25 17:00 | Winter | TRUE | nonsummer
2022-12-25 17:00 | 2022-12-25 18:00 | Winter | TRUE | nonsummer
2022-12-25 18:00 | 2022-12-25 19:00 | Winter | TRUE | nonsummer
2022-12-25 19:00 | 2022-12-25 20:00 | Winter | TRUE | nonsummer
2022-12-25 20:00 | 2022-12-25 21:00 | Winter | TRUE | nonsummer
2022-12-25 21:00 | 2022-12-25 22:00 | Winter | FALSE | nonsummer
2022-12-25 22:00 | 2022-12-25 23:00 | Winter | FALSE | nonsummer
2022-12-25 23:00 | 2022-12-26 | Winter | FALSE | nonsummer
2022-12-26 | 2022-12-26 01:00 | Winter | FALSE | nonsummer
2022-12-26 01:00 | 2022-12-26 02:00 | Winter | FALSE | nonsummer
2022-12-26 02:00 | 2022-12-26 03:00 | Winter | FALSE | nonsummer
2022-12-26 03:00 | 2022-12-26 04:00 | Winter | FALSE | nonsummer
2022-12-26 04:00 | 2022-12-26 05:00 | Winter | FALSE | nonsummer
2022-12-26 05:00 | 2022-12-26 06:00 | Winter | FALSE | nonsummer
2022-12-26 06:00 | 2022-12-26 07:00 | Winter | FALSE | nonsummer
2022-12-26 07:00 | 2022-12-26 08:00 | Winter | FALSE | nonsummer
2022-12-26 08:00 | 2022-12-26 09:00 | Winter | FALSE | nonsummer
2022-12-26 09:00 | 2022-12-26 10:00 | Winter | FALSE | nonsummer
2022-12-26 10:00 | 2022-12-26 11:00 | Winter | FALSE | nonsummer
2022-12-26 11:00 | 2022-12-26 12:00 | Winter | FALSE | nonsummer
2022-12-26 12:00 | 2022-12-26 13:00 | Winter | FALSE | nonsummer
2022-12-26 13:00 | 2022-12-26 14:00 | Winter | FALSE | nonsummer
2022-12-26 14:00 | 2022-12-26 15:00 | Winter | FALSE | nonsummer
2022-12-26 15:00 | 2022-12-26 16:00 | Winter | FALSE | nonsummer
2022-12-26 16:00 | 2022-12-26 17:00 | Winter | TRUE | nonsummer
2022-12-26 17:00 | 2022-12-26 18:00 | Winter | TRUE | nonsummer
2022-12-26 18:00 | 2022-12-26 19:00 | Winter | TRUE | nonsummer
2022-12-26 19:00 | 2022-12-26 20:00 | Winter | TRUE | nonsummer
2022-12-26 20:00 | 2022-12-26 21:00 | Winter | TRUE | nonsummer
2022-12-26 21:00 | 2022-12-26 22:00 | Winter | FALSE | nonsummer
2022-12-26 22:00 | 2022-12-26 23:00 | Winter | FALSE | nonsummer
2022-12-26 23:00 | 2022-12-27 | Winter | FALSE | nonsummer
2022-12-27 | 2022-12-27 01:00 | Winter | FALSE | nonsummer
2022-12-27 01:00 | 2022-12-27 02:00 | Winter | FALSE | nonsummer
2022-12-27 02:00 | 2022-12-27 03:00 | Winter | FALSE | nonsummer
2022-12-27 03:00 | 2022-12-27 04:00 | Winter | FALSE | nonsummer
2022-12-27 04:00 | 2022-12-27 05:00 | Winter | FALSE | nonsummer
2022-12-27 05:00 | 2022-12-27 06:00 | Winter | FALSE | nonsummer
2022-12-27 06:00 | 2022-12-27 07:00 | Winter | FALSE | nonsummer
2022-12-27 07:00 | 2022-12-27 08:00 | Winter | FALSE | nonsummer
2022-12-27 08:00 | 2022-12-27 09:00 | Winter | FALSE | nonsummer
2022-12-27 09:00 | 2022-12-27 10:00 | Winter | FALSE | nonsummer
2022-12-27 10:00 | 2022-12-27 11:00 | Winter | FALSE | nonsummer
2022-12-27 11:00 | 2022-12-27 12:00 | Winter | FALSE | nonsummer
2022-12-27 12:00 | 2022-12-27 13:00 | Winter | FALSE | nonsummer
2022-12-27 13:00 | 2022-12-27 14:00 | Winter | FALSE | nonsummer
2022-12-27 14:00 | 2022-12-27 15:00 | Winter | FALSE | nonsummer
2022-12-27 15:00 | 2022-12-27 16:00 | Winter | FALSE | nonsummer
2022-12-27 16:00 | 2022-12-27 17:00 | Winter | TRUE | nonsummer
2022-12-27 17:00 | 2022-12-27 18:00 | Winter | TRUE | nonsummer
2022-12-27 18:00 | 2022-12-27 19:00 | Winter | TRUE | nonsummer
2022-12-27 19:00 | 2022-12-27 20:00 | Winter | TRUE | nonsummer
2022-12-27 20:00 | 2022-12-27 21:00 | Winter | TRUE | nonsummer
2022-12-27 21:00 | 2022-12-27 22:00 | Winter | FALSE | nonsummer
2022-12-27 22:00 | 2022-12-27 23:00 | Winter | FALSE | nonsummer
2022-12-27 23:00 | 2022-12-28 | Winter | FALSE | nonsummer
2022-12-28 | 2022-12-28 01:00 | Winter | FALSE | nonsummer
2022-12-28 01:00 | 2022-12-28 02:00 | Winter | FALSE | nonsummer
2022-12-28 02:00 | 2022-12-28 03:00 | Winter | FALSE | nonsummer
2022-12-28 03:00 | 2022-12-28 04:00 | Winter | FALSE | nonsummer
2022-12-28 04:00 | 2022-12-28 05:00 | Winter | FALSE | nonsummer
2022-12-28 05:00 | 2022-12-28 06:00 | Winter | FALSE | nonsummer
2022-12-28 06:00 | 2022-12-28 07:00 | Winter | FALSE | nonsummer
2022-12-28 07:00 | 2022-12-28 08:00 | Winter | FALSE | nonsummer
2022-12-28 08:00 | 2022-12-28 09:00 | Winter | FALSE | nonsummer
2022-12-28 09:00 | 2022-12-28 10:00 | Winter | FALSE | nonsummer
2022-12-28 10:00 | 2022-12-28 11:00 | Winter | FALSE | nonsummer
2022-12-28 11:00 | 2022-12-28 12:00 | Winter | FALSE | nonsummer
2022-12-28 12:00 | 2022-12-28 13:00 | Winter | FALSE | nonsummer
2022-12-28 13:00 | 2022-12-28 14:00 | Winter | FALSE | nonsummer
2022-12-28 14:00 | 2022-12-28 15:00 | Winter | FALSE | nonsummer
2022-12-28 15:00 | 2022-12-28 16:00 | Winter | FALSE | nonsummer
2022-12-28 16:00 | 2022-12-28 17:00 | Winter | TRUE | nonsummer
2022-12-28 17:00 | 2022-12-28 18:00 | Winter | TRUE | nonsummer
2022-12-28 18:00 | 2022-12-28 19:00 | Winter | TRUE | nonsummer
2022-12-28 19:00 | 2022-12-28 20:00 | Winter | TRUE | nonsummer
2022-12-28 20:00 | 2022-12-28 21:00 | Winter | TRUE | nonsummer
2022-12-28 21:00 | 2022-12-28 22:00 | Winter | FALSE | nonsummer
2022-12-28 22:00 | 2022-12-28 23:00 | Winter | FALSE | nonsummer
2022-12-28 23:00 | 2022-12-29 | Winter | FALSE | nonsummer
2022-12-29 | 2022-12-29 01:00 | Winter | FALSE | nonsummer
2022-12-29 01:00 | 2022-12-29 02:00 | Winter | FALSE | nonsummer
2022-12-29 02:00 | 2022-12-29 03:00 | Winter | FALSE | nonsummer
2022-12-29 03:00 | 2022-12-29 04:00 | Winter | FALSE | nonsummer
2022-12-29 04:00 | 2022-12-29 05:00 | Winter | FALSE | nonsummer
2022-12-29 05:00 | 2022-12-29 06:00 | Winter | FALSE | nonsummer
2022-12-29 06:00 | 2022-12-29 07:00 | Winter | FALSE | nonsummer
2022-12-29 07:00 | 2022-12-29 08:00 | Winter | FALSE | nonsummer
2022-12-29 08:00 | 2022-12-29 09:00 | Winter | FALSE | nonsummer
2022-12-29 09:00 | 2022-12-29 10:00 | Winter | FALSE | nonsummer
2022-12-29 10:00 | 2022-12-29 11:00 | Winter | FALSE | nonsummer
2022-12-29 11:00 | 2022-12-29 12:00 | Winter | FALSE | nonsummer
2022-12-29 12:00 | 2022-12-29 13:00 | Winter | FALSE | nonsummer
2022-12-29 13:00 | 2022-12-29 14:00 | Winter | FALSE | nonsummer
2022-12-29 14:00 | 2022-12-29 15:00 | Winter | FALSE | nonsummer
2022-12-29 15:00 | 2022-12-29 16:00 | Winter | FALSE | nonsummer
2022-12-29 16:00 | 2022-12-29 17:00 | Winter | TRUE | nonsummer
2022-12-29 17:00 | 2022-12-29 18:00 | Winter | TRUE | nonsummer
2022-12-29 18:00 | 2022-12-29 19:00 | Winter | TRUE | nonsummer
2022-12-29 19:00 | 2022-12-29 20:00 | Winter | TRUE | nonsummer
2022-12-29 20:00 | 2022-12-29 21:00 | Winter | TRUE | nonsummer
2022-12-29 21:00 | 2022-12-29 22:00 | Winter | FALSE | nonsummer
2022-12-29 22:00 | 2022-12-29 23:00 | Winter | FALSE | nonsummer
2022-12-29 23:00 | 2022-12-30 | Winter | FALSE | nonsummer
2022-12-30 | 2022-12-30 01:00 | Winter | FALSE | nonsummer
2022-12-30 01:00 | 2022-12-30 02:00 | Winter | FALSE | nonsummer
2022-12-30 02:00 | 2022-12-30 03:00 | Winter | FALSE | nonsummer
2022-12-30 03:00 | 2022-12-30 04:00 | Winter | FALSE | nonsummer
2022-12-30 04:00 | 2022-12-30 05:00 | Winter | FALSE | nonsummer
2022-12-30 05:00 | 2022-12-30 06:00 | Winter | FALSE | nonsummer
2022-12-30 06:00 | 2022-12-30 07:00 | Winter | FALSE | nonsummer
2022-12-30 07:00 | 2022-12-30 08:00 | Winter | FALSE | nonsummer
2022-12-30 08:00 | 2022-12-30 09:00 | Winter | FALSE | nonsummer
2022-12-30 09:00 | 2022-12-30 10:00 | Winter | FALSE | nonsummer
2022-12-30 10:00 | 2022-12-30 11:00 | Winter | FALSE | nonsummer
2022-12-30 11:00 | 2022-12-30 12:00 | Winter | FALSE | nonsummer
2022-12-30 12:00 | 2022-12-30 13:00 | Winter | FALSE | nonsummer
2022-12-30 13:00 | 2022-12-30 14:00 | Winter | FALSE | nonsummer
2022-12-30 14:00 | 2022-12-30 15:00 | Winter | FALSE | nonsummer
2022-12-30 15:00 | 2022-12-30 16:00 | Winter | FALSE | nonsummer
2022-12-30 16:00 | 2022-12-30 17:00 | Winter | TRUE | nonsummer
2022-12-30 17:00 | 2022-12-30 18:00 | Winter | TRUE | nonsummer
2022-12-30 18:00 | 2022-12-30 19:00 | Winter | TRUE | nonsummer
2022-12-30 19:00 | 2022-12-30 20:00 | Winter | TRUE | nonsummer
2022-12-30 20:00 | 2022-12-30 21:00 | Winter | TRUE | nonsummer
2022-12-30 21:00 | 2022-12-30 22:00 | Winter | FALSE | nonsummer
2022-12-30 22:00 | 2022-12-30 23:00 | Winter | FALSE | nonsummer
2022-12-30 23:00 | 2022-12-31 | Winter | FALSE | nonsummer
2022-12-31 | 2022-12-31 01:00 | Winter | FALSE | nonsummer
2022-12-31 01:00 | 2022-12-31 02:00 | Winter | FALSE | nonsummer
2022-12-31 02:00 | 2022-12-31 03:00 | Winter | FALSE | nonsummer
2022-12-31 03:00 | 2022-12-31 04:00 | Winter | FALSE | nonsummer
2022-12-31 04:00 | 2022-12-31 05:00 | Winter | FALSE | nonsummer
2022-12-31 05:00 | 2022-12-31 06:00 | Winter | FALSE | nonsummer
2022-12-31 06:00 | 2022-12-31 07:00 | Winter | FALSE | nonsummer
2022-12-31 07:00 | 2022-12-31 08:00 | Winter | FALSE | nonsummer
2022-12-31 08:00 | 2022-12-31 09:00 | Winter | FALSE | nonsummer
2022-12-31 09:00 | 2022-12-31 10:00 | Winter | FALSE | nonsummer
2022-12-31 10:00 | 2022-12-31 11:00 | Winter | FALSE | nonsummer
2022-12-31 11:00 | 2022-12-31 12:00 | Winter | FALSE | nonsummer
2022-12-31 12:00 | 2022-12-31 13:00 | Winter | FALSE | nonsummer
2022-12-31 13:00 | 2022-12-31 14:00 | Winter | FALSE | nonsummer
2022-12-31 14:00 | 2022-12-31 15:00 | Winter | FALSE | nonsummer
2022-12-31 15:00 | 2022-12-31 16:00 | Winter | FALSE | nonsummer
2022-12-31 16:00 | 2022-12-31 17:00 | Winter | TRUE | nonsummer
2022-12-31 17:00 | 2022-12-31 18:00 | Winter | TRUE | nonsummer
2022-12-31 18:00 | 2022-12-31 19:00 | Winter | TRUE | nonsummer
2022-12-31 19:00 | 2022-12-31 20:00 | Winter | TRUE | nonsummer
2022-12-31 20:00 | 2022-12-31 21:00 | Winter | TRUE | nonsummer
2022-12-31 21:00 | 2022-12-31 22:00 | Winter | FALSE | nonsummer
2022-12-31 22:00 | 2022-12-31 23:00 | Winter | FALSE | nonsummer
2022-12-31 23:00 | 2023-01-01 | Winter | FALSE | nonsummer
2023-01-01 | 2023-01-01 01:00 | Winter | FALSE | nonsummer
2023-01-01 01:00 | 2023-01-01 02:00 | Winter | FALSE | nonsummer
2023-01-01 02:00 | 2023-01-01 03:00 | Winter | FALSE | nonsummer
2023-01-01 03:00 | 2023-01-01 04:00 | Winter | FALSE | nonsummer
2023-01-01 04:00 | 2023-01-01 05:00 | Winter | FALSE | nonsummer
2023-01-01 05:00 | 2023-01-01 06:00 | Winter | FALSE | nonsummer
2023-01-01 06:00 | 2023-01-01 07:00 | Winter | FALSE | nonsummer
2023-01-01 07:00 | 2023-01-01 08:00 | Winter | FALSE | nonsummer
2023-01-01 08:00 | 2023-01-01 09:00 | Winter | FALSE | nonsummer
2023-01-01 09:00 | 2023-01-01 10:00 | Winter | FALSE | nonsummer
2023-01-01 10:00 | 2023-01-01 11:00 | Winter | FALSE | nonsummer
2023-01-01 11:00 | 2023-01-01 12:00 | Winter | FALSE | nonsummer
2023-01-01 12:00 | 2023-01-01 13:00 | Winter | FALSE | nonsummer
2023-01-01 13:00 | 2023-01-01 14:00 | Winter | FALSE | nonsummer
2023-01-01 14:00 | 2023-01-01 15:00 | Winter | FALSE | nonsummer
2023-01-01 15:00 | 2023-01-01 16:00 | Winter | FALSE | nonsummer
2023-01-01 16:00 | 2023-01-01 17:00 | Winter | TRUE | nonsummer
2023-01-01 17:00 | 2023-01-01 18:00 | Winter | TRUE | nonsummer
2023-01-01 18:00 | 2023-01-01 19:00 | Winter | TRUE | nonsummer
2023-01-01 19:00 | 2023-01-01 20:00 | Winter | TRUE | nonsummer
2023-01-01 20:00 | 2023-01-01 21:00 | Winter | TRUE | nonsummer
2023-01-01 21:00 | 2023-01-01 22:00 | Winter | FALSE | nonsummer
2023-01-01 22:00 | 2023-01-01 23:00 | Winter | FALSE | nonsummer
2023-01-01 23:00 | 2023-01-02 | Winter | FALSE | nonsummer
2023-01-02 | 2023-01-02 01:00 | Winter | FALSE | nonsummer
2023-01-02 01:00 | 2023-01-02 02:00 | Winter | FALSE | nonsummer
2023-01-02 02:00 | 2023-01-02 03:00 | Winter | FALSE | nonsummer
2023-01-02 03:00 | 2023-01-02 04:00 | Winter | FALSE | nonsummer
2023-01-02 04:00 | 2023-01-02 05:00 | Winter | FALSE | nonsummer
2023-01-02 05:00 | 2023-01-02 06:00 | Winter | FALSE | nonsummer
2023-01-02 06:00 | 2023-01-02 07:00 | Winter | FALSE | nonsummer
2023-01-02 07:00 | 2023-01-02 08:00 | Winter | FALSE | nonsummer
2023-01-02 08:00 | 2023-01-02 09:00 | Winter | FALSE | nonsummer
2023-01-02 09:00 | 2023-01-02 10:00 | Winter | FALSE | nonsummer
2023-01-02 10:00 | 2023-01-02 11:00 | Winter | FALSE | nonsummer
2023-01-02 11:00 | 2023-01-02 12:00 | Winter | FALSE | nonsummer
2023-01-02 12:00 | 2023-01-02 13:00 | Winter | FALSE | nonsummer
2023-01-02 13:00 | 2023-01-02 14:00 | Winter | FALSE | nonsummer
2023-01-02 14:00 | 2023-01-02 15:00 | Winter | FALSE | nonsummer
2023-01-02 15:00 | 2023-01-02 16:00 | Winter | FALSE | nonsummer
2023-01-02 16:00 | 2023-01-02 17:00 | Winter | TRUE | nonsummer
2023-01-02 17:00 | 2023-01-02 18:00 | Winter | TRUE | nonsummer
2023-01-02 18:00 | 2023-01-02 19:00 | Winter | TRUE | nonsummer
2023-01-02 19:00 | 2023-01-02 20:00 | Winter | TRUE | nonsummer
2023-01-02 20:00 | 2023-01-02 21:00 | Winter | TRUE | nonsummer
2023-01-02 21:00 | 2023-01-02 22:00 | Winter | FALSE | nonsummer
2023-01-02 22:00 | 2023-01-02 23:00 | Winter | FALSE | nonsummer
2023-01-02 23:00 | 2023-01-03 | Winter | FALSE | nonsummer
2023-01-03 | 2023-01-03 01:00 | Winter | FALSE | nonsummer
2023-01-03 01:00 | 2023-01-03 02:00 | Winter | FALSE | nonsummer
2023-01-03 02:00 | 2023-01-03 03:00 | Winter | FALSE | nonsummer
2023-01-03 03:00 | 2023-01-03 04:00 | Winter | FALSE | nonsummer
2023-01-03 04:00 | 2023-01-03 05:00 | Winter | FALSE | nonsummer
2023-01-03 05:00 | 2023-01-03 06:00 | Winter | FALSE | nonsummer
2023-01-03 06:00 | 2023-01-03 07:00 | Winter | FALSE | nonsummer
2023-01-03 07:00 | 2023-01-03 08:00 | Winter | FALSE | nonsummer
2023-01-03 08:00 | 2023-01-03 09:00 | Winter | FALSE | nonsummer
2023-01-03 09:00 | 2023-01-03 10:00 | Winter | FALSE | nonsummer
2023-01-03 10:00 | 2023-01-03 11:00 | Winter | FALSE | nonsummer
2023-01-03 11:00 | 2023-01-03 12:00 | Winter | FALSE | nonsummer
2023-01-03 12:00 | 2023-01-03 13:00 | Winter | FALSE | nonsummer
2023-01-03 13:00 | 2023-01-03 14:00 | Winter | FALSE | nonsummer
2023-01-03 14:00 | 2023-01-03 15:00 | Winter | FALSE | nonsummer
2023-01-03 15:00 | 2023-01-03 16:00 | Winter | FALSE | nonsummer
2023-01-03 16:00 | 2023-01-03 17:00 | Winter | TRUE | nonsummer
2023-01-03 17:00 | 2023-01-03 18:00 | Winter | TRUE | nonsummer
2023-01-03 18:00 | 2023-01-03 19:00 | Winter | TRUE | nonsummer
2023-01-03 19:00 | 2023-01-03 20:00 | Winter | TRUE | nonsummer
2023-01-03 20:00 | 2023-01-03 21:00 | Winter | TRUE | nonsummer
2023-01-03 21:00 | 2023-01-03 22:00 | Winter | FALSE | nonsummer
2023-01-03 22:00 | 2023-01-03 23:00 | Winter | FALSE | nonsummer
2023-01-03 23:00 | 2023-01-04 | Winter | FALSE | nonsummer
2023-01-04 | 2023-01-04 01:00 | Winter | FALSE | nonsummer
2023-01-04 01:00 | 2023-01-04 02:00 | Winter | FALSE | nonsummer
2023-01-04 02:00 | 2023-01-04 03:00 | Winter | FALSE | nonsummer
2023-01-04 03:00 | 2023-01-04 04:00 | Winter | FALSE | nonsummer
2023-01-04 04:00 | 2023-01-04 05:00 | Winter | FALSE | nonsummer
2023-01-04 05:00 | 2023-01-04 06:00 | Winter | FALSE | nonsummer
2023-01-04 06:00 | 2023-01-04 07:00 | Winter | FALSE | nonsummer
2023-01-04 07:00 | 2023-01-04 08:00 | Winter | FALSE | nonsummer
2023-01-04 08:00 | 2023-01-04 09:00 | Winter | FALSE | nonsummer
2023-01-04 09:00 | 2023-01-04 10:00 | Winter | FALSE | nonsummer
2023-01-04 10:00 | 2023-01-04 11:00 | Winter | FALSE | nonsummer
2023-01-04 11:00 | 2023-01-04 12:00 | Winter | FALSE | nonsummer
2023-01-04 12:00 | 2023-01-04 13:00 | Winter | FALSE | nonsummer
2023-01-04 13:00 | 2023-01-04 14:00 | Winter | FALSE | nonsummer
2023-01-04 14:00 | 2023-01-04 15:00 | Winter | FALSE | nonsummer
2023-01-04 15:00 | 2023-01-04 16:00 | Winter | FALSE | nonsummer
2023-01-04 16:00 | 2023-01-04 17:00 | Winter | TRUE | nonsummer
2023-01-04 17:00 | 2023-01-04 18:00 | Winter | TRUE | nonsummer
2023-01-04 18:00 | 2023-01-04 19:00 | Winter | TRUE | nonsummer
2023-01-04 19:00 | 2023-01-04 20:00 | Winter | TRUE | nonsummer
2023-01-04 20:00 | 2023-01-04 21:00 | Winter | TRUE | nonsummer
2023-01-04 21:00 | 2023-01-04 22:00 | Winter | FALSE | nonsummer
2023-01-04 22:00 | 2023-01-04 23:00 | Winter | FALSE | nonsummer
2023-01-04 23:00 | 2023-01-05 | Winter | FALSE | nonsummer
2023-01-05 | 2023-01-05 01:00 | Winter | FALSE | nonsummer
2023-01-05 01:00 | 2023-01-05 02:00 | Winter | FALSE | nonsummer
2023-01-05 02:00 | 2023-01-05 03:00 | Winter | FALSE | nonsummer
2023-01-05 03:00 | 2023-01-05 04:00 | Winter | FALSE | nonsummer
2023-01-05 04:00 | 2023-01-05 05:00 | Winter | FALSE | nonsummer
2023-01-05 05:00 | 2023-01-05 06:00 | Winter | FALSE | nonsummer
2023-01-05 06:00 | 2023-01-05 07:00 | Winter | FALSE | nonsummer
2023-01-05 07:00 | 2023-01-05 08:00 | Winter | FALSE | nonsummer
2023-01-05 08:00 | 2023-01-05 09:00 | Winter | FALSE | nonsummer
2023-01-05 09:00 | 2023-01-05 10:00 | Winter | FALSE | nonsummer
2023-01-05 10:00 | 2023-01-05 11:00 | Winter | FALSE | nonsummer
2023-01-05 11:00 | 2023-01-05 12:00 | Winter | FALSE | nonsummer
2023-01-05 12:00 | 2023-01-05 13:00 | Winter | FALSE | nonsummer
2023-01-05 13:00 | 2023-01-05 14:00 | Winter | FALSE | nonsummer
2023-01-05 14:00 | 2023-01-05 15:00 | Winter | FALSE | nonsummer
2023-01-05 15:00 | 2023-01-05 16:00 | Winter | FALSE | nonsummer
2023-01-05 16:00 | 2023-01-05 17:00 | Winter | TRUE | nonsummer
2023-01-05 17:00 | 2023-01-05 18:00 | Winter | TRUE | nonsummer
2023-01-05 18:00 | 2023-01-05 19:00 | Winter | TRUE | nonsummer
2023-01-05 19:00 | 2023-01-05 20:00 | Winter | TRUE | nonsummer
2023-01-05 20:00 | 2023-01-05 21:00 | Winter | TRUE | nonsummer
2023-01-05 21:00 | 2023-01-05 22:00 | Winter | FALSE | nonsummer
2023-01-05 22:00 | 2023-01-05 23:00 | Winter | FALSE | nonsummer
2023-01-05 23:00 | 2023-01-06 | Winter | FALSE | nonsummer
2023-01-06 | 2023-01-06 01:00 | Winter | FALSE | nonsummer
2023-01-06 01:00 | 2023-01-06 02:00 | Winter | FALSE | nonsummer
2023-01-06 02:00 | 2023-01-06 03:00 | Winter | FALSE | nonsummer
2023-01-06 03:00 | 2023-01-06 04:00 | Winter | FALSE | nonsummer
2023-01-06 04:00 | 2023-01-06 05:00 | Winter | FALSE | nonsummer
2023-01-06 05:00 | 2023-01-06 06:00 | Winter | FALSE | nonsummer
2023-01-06 06:00 | 2023-01-06 07:00 | Winter | FALSE | nonsummer
2023-01-06 07:00 | 2023-01-06 08:00 | Winter | FALSE | nonsummer
2023-01-06 08:00 | 2023-01-06 09:00 | Winter | FALSE | nonsummer
2023-01-06 09:00 | 2023-01-06 10:00 | Winter | FALSE | nonsummer
2023-01-06 10:00 | 2023-01-06 11:00 | Winter | FALSE | nonsummer
2023-01-06 11:00 | 2023-01-06 12:00 | Winter | FALSE | nonsummer
2023-01-06 12:00 | 2023-01-06 13:00 | Winter | FALSE | nonsummer
2023-01-06 13:00 | 2023-01-06 14:00 | Winter | FALSE | nonsummer
2023-01-06 14:00 | 2023-01-06 15:00 | Winter | FALSE | nonsummer
2023-01-06 15:00 | 2023-01-06 16:00 | Winter | FALSE | nonsummer
2023-01-06 16:00 | 2023-01-06 17:00 | Winter | TRUE | nonsummer
2023-01-06 17:00 | 2023-01-06 18:00 | Winter | TRUE | nonsummer
2023-01-06 18:00 | 2023-01-06 19:00 | Winter | TRUE | nonsummer
2023-01-06 19:00 | 2023-01-06 20:00 | Winter | TRUE | nonsummer
2023-01-06 20:00 | 2023-01-06 21:00 | Winter | TRUE | nonsummer
2023-01-06 21:00 | 2023-01-06 22:00 | Winter | FALSE | nonsummer
2023-01-06 22:00 | 2023-01-06 23:00 | Winter | FALSE | nonsummer
2023-01-06 23:00 | 2023-01-07 | Winter | FALSE | nonsummer
2023-01-07 | 2023-01-07 01:00 | Winter | FALSE | nonsummer
2023-01-07 01:00 | 2023-01-07 02:00 | Winter | FALSE | nonsummer
2023-01-07 02:00 | 2023-01-07 03:00 | Winter | FALSE | nonsummer
2023-01-07 03:00 | 2023-01-07 04:00 | Winter | FALSE | nonsummer
2023-01-07 04:00 | 2023-01-07 05:00 | Winter | FALSE | nonsummer
2023-01-07 05:00 | 2023-01-07 06:00 | Winter | FALSE | nonsummer
2023-01-07 06:00 | 2023-01-07 07:00 | Winter | FALSE | nonsummer
2023-01-07 07:00 | 2023-01-07 08:00 | Winter | FALSE | nonsummer
2023-01-07 08:00 | 2023-01-07 09:00 | Winter | FALSE | nonsummer
2023-01-07 09:00 | 2023-01-07 10:00 | Winter | FALSE | nonsummer
2023-01-07 10:00 | 2023-01-07 11:00 | Winter | FALSE | nonsummer
2023-01-07 11:00 | 2023-01-07 12:00 | Winter | FALSE | nonsummer
2023-01-07 12:00 | 2023-01-07 13:00 | Winter | FALSE | nonsummer
2023-01-07 13:00 | 2023-01-07 14:00 | Winter | FALSE | nonsummer
2023-01-07 14:00 | 2023-01-07 15:00 | Winter | FALSE | nonsummer
2023-01-07 15:00 | 2023-01-07 16:00 | Winter | FALSE | nonsummer
2023-01-07 16:00 | 2023-01-07 17:00 | Winter | TRUE | nonsummer
2023-01-07 17:00 | 2023-01-07 18:00 | Winter | TRUE | nonsummer
2023-01-07 18:00 | 2023-01-07 19:00 | Winter | TRUE | nonsummer
2023-01-07 19:00 | 2023-01-07 20:00 | Winter | TRUE | nonsummer
2023-01-07 20:00 | 2023-01-07 21:00 | Winter | TRUE | nonsummer
2023-01-07 21:00 | 2023-01-07 22:00 | Winter | FALSE | nonsummer
2023-01-07 22:00 | 2023-01-07 23:00 | Winter | FALSE | nonsummer
2023-01-07 23:00 | 2023-01-08 | Winter | FALSE | nonsummer
2023-01-08 | 2023-01-08 01:00 | Winter | FALSE | nonsummer
2023-01-08 01:00 | 2023-01-08 02:00 | Winter | FALSE | nonsummer
2023-01-08 02:00 | 2023-01-08 03:00 | Winter | FALSE | nonsummer
2023-01-08 03:00 | 2023-01-08 04:00 | Winter | FALSE | nonsummer
2023-01-08 04:00 | 2023-01-08 05:00 | Winter | FALSE | nonsummer
2023-01-08 05:00 | 2023-01-08 06:00 | Winter | FALSE | nonsummer
2023-01-08 06:00 | 2023-01-08 07:00 | Winter | FALSE | nonsummer
2023-01-08 07:00 | 2023-01-08 08:00 | Winter | FALSE | nonsummer
2023-01-08 08:00 | 2023-01-08 09:00 | Winter | FALSE | nonsummer
2023-01-08 09:00 | 2023-01-08 10:00 | Winter | FALSE | nonsummer
2023-01-08 10:00 | 2023-01-08 11:00 | Winter | FALSE | nonsummer
2023-01-08 11:00 | 2023-01-08 12:00 | Winter | FALSE | nonsummer
2023-01-08 12:00 | 2023-01-08 13:00 | Winter | FALSE | nonsummer
2023-01-08 13:00 | 2023-01-08 14:00 | Winter | FALSE | nonsummer
2023-01-08 14:00 | 2023-01-08 15:00 | Winter | FALSE | nonsummer
2023-01-08 15:00 | 2023-01-08 16:00 | Winter | FALSE | nonsummer
2023-01-08 16:00 | 2023-01-08 17:00 | Winter | TRUE | nonsummer
2023-01-08 17:00 | 2023-01-08 18:00 | Winter | TRUE | nonsummer
2023-01-08 18:00 | 2023-01-08 19:00 | Winter | TRUE | nonsummer
2023-01-08 19:00 | 2023-01-08 20:00 | Winter | TRUE | nonsummer
2023-01-08 20:00 | 2023-01-08 21:00 | Winter | TRUE | nonsummer
2023-01-08 21:00 | 2023-01-08 22:00 | Winter | FALSE | nonsummer
2023-01-08 22:00 | 2023-01-08 23:00 | Winter | FALSE | nonsummer
2023-01-08 23:00 | 2023-01-09 | Winter | FALSE | nonsummer
2023-01-09 | 2023-01-09 01:00 | Winter | FALSE | nonsummer
2023-01-09 01:00 | 2023-01-09 02:00 | Winter | FALSE | nonsummer
2023-01-09 02:00 | 2023-01-09 03:00 | Winter | FALSE | nonsummer
2023-01-09 03:00 | 2023-01-09 04:00 | Winter | FALSE | nonsummer
2023-01-09 04:00 | 2023-01-09 05:00 | Winter | FALSE | nonsummer
2023-01-09 05:00 | 2023-01-09 06:00 | Winter | FALSE | nonsummer
2023-01-09 06:00 | 2023-01-09 07:00 | Winter | FALSE | nonsummer
2023-01-09 07:00 | 2023-01-09 08:00 | Winter | FALSE | nonsummer
2023-01-09 08:00 | 2023-01-09 09:00 | Winter | FALSE | nonsummer
2023-01-09 09:00 | 2023-01-09 10:00 | Winter | FALSE | nonsummer
2023-01-09 10:00 | 2023-01-09 11:00 | Winter | FALSE | nonsummer
2023-01-09 11:00 | 2023-01-09 12:00 | Winter | FALSE | nonsummer
2023-01-09 12:00 | 2023-01-09 13:00 | Winter | FALSE | nonsummer
2023-01-09 13:00 | 2023-01-09 14:00 | Winter | FALSE | nonsummer
2023-01-09 14:00 | 2023-01-09 15:00 | Winter | FALSE | nonsummer
2023-01-09 15:00 | 2023-01-09 16:00 | Winter | FALSE | nonsummer
2023-01-09 16:00 | 2023-01-09 17:00 | Winter | TRUE | nonsummer
2023-01-09 17:00 | 2023-01-09 18:00 | Winter | TRUE | nonsummer
2023-01-09 18:00 | 2023-01-09 19:00 | Winter | TRUE | nonsummer
2023-01-09 19:00 | 2023-01-09 20:00 | Winter | TRUE | nonsummer
2023-01-09 20:00 | 2023-01-09 21:00 | Winter | TRUE | nonsummer
2023-01-09 21:00 | 2023-01-09 22:00 | Winter | FALSE | nonsummer
2023-01-09 22:00 | 2023-01-09 23:00 | Winter | FALSE | nonsummer
2023-01-09 23:00 | 2023-01-10 | Winter | FALSE | nonsummer
2023-01-10 | 2023-01-10 01:00 | Winter | FALSE | nonsummer
2023-01-10 01:00 | 2023-01-10 02:00 | Winter | FALSE | nonsummer
2023-01-10 02:00 | 2023-01-10 03:00 | Winter | FALSE | nonsummer
2023-01-10 03:00 | 2023-01-10 04:00 | Winter | FALSE | nonsummer
2023-01-10 04:00 | 2023-01-10 05:00 | Winter | FALSE | nonsummer
2023-01-10 05:00 | 2023-01-10 06:00 | Winter | FALSE | nonsummer
2023-01-10 06:00 | 2023-01-10 07:00 | Winter | FALSE | nonsummer
2023-01-10 07:00 | 2023-01-10 08:00 | Winter | FALSE | nonsummer
2023-01-10 08:00 | 2023-01-10 09:00 | Winter | FALSE | nonsummer
2023-01-10 09:00 | 2023-01-10 10:00 | Winter | FALSE | nonsummer
2023-01-10 10:00 | 2023-01-10 11:00 | Winter | FALSE | nonsummer
2023-01-10 11:00 | 2023-01-10 12:00 | Winter | FALSE | nonsummer
2023-01-10 12:00 | 2023-01-10 13:00 | Winter | FALSE | nonsummer
2023-01-10 13:00 | 2023-01-10 14:00 | Winter | FALSE | nonsummer
2023-01-10 14:00 | 2023-01-10 15:00 | Winter | FALSE | nonsummer
2023-01-10 15:00 | 2023-01-10 16:00 | Winter | FALSE | nonsummer
2023-01-10 16:00 | 2023-01-10 17:00 | Winter | TRUE | nonsummer
2023-01-10 17:00 | 2023-01-10 18:00 | Winter | TRUE | nonsummer
2023-01-10 18:00 | 2023-01-10 19:00 | Winter | TRUE | nonsummer
2023-01-10 19:00 | 2023-01-10 20:00 | Winter | TRUE | nonsummer
2023-01-10 20:00 | 2023-01-10 21:00 | Winter | TRUE | nonsummer
2023-01-10 21:00 | 2023-01-10 22:00 | Winter | FALSE | nonsummer
2023-01-10 22:00 | 2023-01-10 23:00 | Winter | FALSE | nonsummer
2023-01-10 23:00 | 2023-01-11 | Winter | FALSE | nonsummer
2023-01-11 | 2023-01-11 01:00 | Winter | FALSE | nonsummer
2023-01-11 01:00 | 2023-01-11 02:00 | Winter | FALSE | nonsummer
2023-01-11 02:00 | 2023-01-11 03:00 | Winter | FALSE | nonsummer
2023-01-11 03:00 | 2023-01-11 04:00 | Winter | FALSE | nonsummer
2023-01-11 04:00 | 2023-01-11 05:00 | Winter | FALSE | nonsummer
2023-01-11 05:00 | 2023-01-11 06:00 | Winter | FALSE | nonsummer
2023-01-11 06:00 | 2023-01-11 07:00 | Winter | FALSE | nonsummer
2023-01-11 07:00 | 2023-01-11 08:00 | Winter | FALSE | nonsummer
2023-01-11 08:00 | 2023-01-11 09:00 | Winter | FALSE | nonsummer
2023-01-11 09:00 | 2023-01-11 10:00 | Winter | FALSE | nonsummer
2023-01-11 10:00 | 2023-01-11 11:00 | Winter | FALSE | nonsummer
2023-01-11 11:00 | 2023-01-11 12:00 | Winter | FALSE | nonsummer
2023-01-11 12:00 | 2023-01-11 13:00 | Winter | FALSE | nonsummer
2023-01-11 13:00 | 2023-01-11 14:00 | Winter | FALSE | nonsummer
2023-01-11 14:00 | 2023-01-11 15:00 | Winter | FALSE | nonsummer
2023-01-11 15:00 | 2023-01-11 16:00 | Winter | FALSE | nonsummer
2023-01-11 16:00 | 2023-01-11 17:00 | Winter | TRUE | nonsummer
2023-01-11 17:00 | 2023-01-11 18:00 | Winter | TRUE | nonsummer
2023-01-11 18:00 | 2023-01-11 19:00 | Winter | TRUE | nonsummer
2023-01-11 19:00 | 2023-01-11 20:00 | Winter | TRUE | nonsummer
2023-01-11 20:00 | 2023-01-11 21:00 | Winter | TRUE | nonsummer
2023-01-11 21:00 | 2023-01-11 22:00 | Winter | FALSE | nonsummer
2023-01-11 22:00 | 2023-01-11 23:00 | Winter | FALSE | nonsummer
2023-01-11 23:00 | 2023-01-12 | Winter | FALSE | nonsummer
2023-01-12 | 2023-01-12 01:00 | Winter | FALSE | nonsummer
2023-01-12 01:00 | 2023-01-12 02:00 | Winter | FALSE | nonsummer
2023-01-12 02:00 | 2023-01-12 03:00 | Winter | FALSE | nonsummer
2023-01-12 03:00 | 2023-01-12 04:00 | Winter | FALSE | nonsummer
2023-01-12 04:00 | 2023-01-12 05:00 | Winter | FALSE | nonsummer
2023-01-12 05:00 | 2023-01-12 06:00 | Winter | FALSE | nonsummer
2023-01-12 06:00 | 2023-01-12 07:00 | Winter | FALSE | nonsummer
2023-01-12 07:00 | 2023-01-12 08:00 | Winter | FALSE | nonsummer
2023-01-12 08:00 | 2023-01-12 09:00 | Winter | FALSE | nonsummer
2023-01-12 09:00 | 2023-01-12 10:00 | Winter | FALSE | nonsummer
2023-01-12 10:00 | 2023-01-12 11:00 | Winter | FALSE | nonsummer
2023-01-12 11:00 | 2023-01-12 12:00 | Winter | FALSE | nonsummer
2023-01-12 12:00 | 2023-01-12 13:00 | Winter | FALSE | nonsummer
2023-01-12 13:00 | 2023-01-12 14:00 | Winter | FALSE | nonsummer
2023-01-12 14:00 | 2023-01-12 15:00 | Winter | FALSE | nonsummer
2023-01-12 15:00 | 2023-01-12 16:00 | Winter | FALSE | nonsummer
2023-01-12 16:00 | 2023-01-12 17:00 | Winter | TRUE | nonsummer
2023-01-12 17:00 | 2023-01-12 18:00 | Winter | TRUE | nonsummer
2023-01-12 18:00 | 2023-01-12 19:00 | Winter | TRUE | nonsummer
2023-01-12 19:00 | 2023-01-12 20:00 | Winter | TRUE | nonsummer
2023-01-12 20:00 | 2023-01-12 21:00 | Winter | TRUE | nonsummer
2023-01-12 21:00 | 2023-01-12 22:00 | Winter | FALSE | nonsummer
2023-01-12 22:00 | 2023-01-12 23:00 | Winter | FALSE | nonsummer
2023-01-12 23:00 | 2023-01-13 | Winter | FALSE | nonsummer
2023-01-13 | 2023-01-13 01:00 | Winter | FALSE | nonsummer
2023-01-13 01:00 | 2023-01-13 02:00 | Winter | FALSE | nonsummer
2023-01-13 02:00 | 2023-01-13 03:00 | Winter | FALSE | nonsummer
2023-01-13 03:00 | 2023-01-13 04:00 | Winter | FALSE | nonsummer
2023-01-13 04:00 | 2023-01-13 05:00 | Winter | FALSE | nonsummer
2023-01-13 05:00 | 2023-01-13 06:00 | Winter | FALSE | nonsummer
2023-01-13 06:00 | 2023-01-13 07:00 | Winter | FALSE | nonsummer
2023-01-13 07:00 | 2023-01-13 08:00 | Winter | FALSE | nonsummer
2023-01-13 08:00 | 2023-01-13 09:00 | Winter | FALSE | nonsummer
2023-01-13 09:00 | 2023-01-13 10:00 | Winter | FALSE | nonsummer
2023-01-13 10:00 | 2023-01-13 11:00 | Winter | FALSE | nonsummer
2023-01-13 11:00 | 2023-01-13 12:00 | Winter | FALSE | nonsummer
2023-01-13 12:00 | 2023-01-13 13:00 | Winter | FALSE | nonsummer
2023-01-13 13:00 | 2023-01-13 14:00 | Winter | FALSE | nonsummer
2023-01-13 14:00 | 2023-01-13 15:00 | Winter | FALSE | nonsummer
2023-01-13 15:00 | 2023-01-13 16:00 | Winter | FALSE | nonsummer
2023-01-13 16:00 | 2023-01-13 17:00 | Winter | TRUE | nonsummer
2023-01-13 17:00 | 2023-01-13 18:00 | Winter | TRUE | nonsummer
2023-01-13 18:00 | 2023-01-13 19:00 | Winter | TRUE | nonsummer
2023-01-13 19:00 | 2023-01-13 20:00 | Winter | TRUE | nonsummer
2023-01-13 20:00 | 2023-01-13 21:00 | Winter | TRUE | nonsummer
2023-01-13 21:00 | 2023-01-13 22:00 | Winter | FALSE | nonsummer
2023-01-13 22:00 | 2023-01-13 23:00 | Winter | FALSE | nonsummer
2023-01-13 23:00 | 2023-01-14 | Winter | FALSE | nonsummer
2023-01-14 | 2023-01-14 01:00 | Winter | FALSE | nonsummer
2023-01-14 01:00 | 2023-01-14 02:00 | Winter | FALSE | nonsummer
2023-01-14 02:00 | 2023-01-14 03:00 | Winter | FALSE | nonsummer
2023-01-14 03:00 | 2023-01-14 04:00 | Winter | FALSE | nonsummer
2023-01-14 04:00 | 2023-01-14 05:00 | Winter | FALSE | nonsummer
2023-01-14 05:00 | 2023-01-14 06:00 | Winter | FALSE | nonsummer
2023-01-14 06:00 | 2023-01-14 07:00 | Winter | FALSE | nonsummer
2023-01-14 07:00 | 2023-01-14 08:00 | Winter | FALSE | nonsummer
2023-01-14 08:00 | 2023-01-14 09:00 | Winter | FALSE | nonsummer
2023-01-14 09:00 | 2023-01-14 10:00 | Winter | FALSE | nonsummer
2023-01-14 10:00 | 2023-01-14 11:00 | Winter | FALSE | nonsummer
2023-01-14 11:00 | 2023-01-14 12:00 | Winter | FALSE | nonsummer
2023-01-14 12:00 | 2023-01-14 13:00 | Winter | FALSE | nonsummer
2023-01-14 13:00 | 2023-01-14 14:00 | Winter | FALSE | nonsummer
2023-01-14 14:00 | 2023-01-14 15:00 | Winter | FALSE | nonsummer
2023-01-14 15:00 | 2023-01-14 16:00 | Winter | FALSE | nonsummer
2023-01-14 16:00 | 2023-01-14 17:00 | Winter | TRUE | nonsummer
2023-01-14 17:00 | 2023-01-14 18:00 | Winter | TRUE | nonsummer
2023-01-14 18:00 | 2023-01-14 19:00 | Winter | TRUE | nonsummer
2023-01-14 19:00 | 2023-01-14 20:00 | Winter | TRUE | nonsummer
2023-01-14 20:00 | 2023-01-14 21:00 | Winter | TRUE | nonsummer
2023-01-14 21:00 | 2023-01-14 22:00 | Winter | FALSE | nonsummer
2023-01-14 22:00 | 2023-01-14 23:00 | Winter | FALSE | nonsummer
2023-01-14 23:00 | 2023-01-15 | Winter | FALSE | nonsummer
2023-01-15 | 2023-01-15 01:00 | Winter | FALSE | nonsummer
2023-01-15 01:00 | 2023-01-15 02:00 | Winter | FALSE | nonsummer
2023-01-15 02:00 | 2023-01-15 03:00 | Winter | FALSE | nonsummer
2023-01-15 03:00 | 2023-01-15 04:00 | Winter | FALSE | nonsummer
2023-01-15 04:00 | 2023-01-15 05:00 | Winter | FALSE | nonsummer
2023-01-15 05:00 | 2023-01-15 06:00 | Winter | FALSE | nonsummer
2023-01-15 06:00 | 2023-01-15 07:00 | Winter | FALSE | nonsummer
2023-01-15 07:00 | 2023-01-15 08:00 | Winter | FALSE | nonsummer
2023-01-15 08:00 | 2023-01-15 09:00 | Winter | FALSE | nonsummer
2023-01-15 09:00 | 2023-01-15 10:00 | Winter | FALSE | nonsummer
2023-01-15 10:00 | 2023-01-15 11:00 | Winter | FALSE | nonsummer
2023-01-15 11:00 | 2023-01-15 12:00 | Winter | FALSE | nonsummer
2023-01-15 12:00 | 2023-01-15 13:00 | Winter | FALSE | nonsummer
2023-01-15 13:00 | 2023-01-15 14:00 | Winter | FALSE | nonsummer
2023-01-15 14:00 | 2023-01-15 15:00 | Winter | FALSE | nonsummer
2023-01-15 15:00 | 2023-01-15 16:00 | Winter | FALSE | nonsummer
2023-01-15 16:00 | 2023-01-15 17:00 | Winter | TRUE | nonsummer
2023-01-15 17:00 | 2023-01-15 18:00 | Winter | TRUE | nonsummer
2023-01-15 18:00 | 2023-01-15 19:00 | Winter | TRUE | nonsummer
2023-01-15 19:00 | 2023-01-15 20:00 | Winter | TRUE | nonsummer
2023-01-15 20:00 | 2023-01-15 21:00 | Winter | TRUE | nonsummer
2023-01-15 21:00 | 2023-01-15 22:00 | Winter | FALSE | nonsummer
2023-01-15 22:00 | 2023-01-15 23:00 | Winter | FALSE | nonsummer
2023-01-15 23:00 | 2023-01-16 | Winter | FALSE | nonsummer
2023-01-16 | 2023-01-16 01:00 | Winter | FALSE | nonsummer
2023-01-16 01:00 | 2023-01-16 02:00 | Winter | FALSE | nonsummer
2023-01-16 02:00 | 2023-01-16 03:00 | Winter | FALSE | nonsummer
2023-01-16 03:00 | 2023-01-16 04:00 | Winter | FALSE | nonsummer
2023-01-16 04:00 | 2023-01-16 05:00 | Winter | FALSE | nonsummer
2023-01-16 05:00 | 2023-01-16 06:00 | Winter | FALSE | nonsummer
2023-01-16 06:00 | 2023-01-16 07:00 | Winter | FALSE | nonsummer
2023-01-16 07:00 | 2023-01-16 08:00 | Winter | FALSE | nonsummer
2023-01-16 08:00 | 2023-01-16 09:00 | Winter | FALSE | nonsummer
2023-01-16 09:00 | 2023-01-16 10:00 | Winter | FALSE | nonsummer
2023-01-16 10:00 | 2023-01-16 11:00 | Winter | FALSE | nonsummer
2023-01-16 11:00 | 2023-01-16 12:00 | Winter | FALSE | nonsummer
2023-01-16 12:00 | 2023-01-16 13:00 | Winter | FALSE | nonsummer
2023-01-16 13:00 | 2023-01-16 14:00 | Winter | FALSE | nonsummer
2023-01-16 14:00 | 2023-01-16 15:00 | Winter | FALSE | nonsummer
2023-01-16 15:00 | 2023-01-16 16:00 | Winter | FALSE | nonsummer
2023-01-16 16:00 | 2023-01-16 17:00 | Winter | TRUE | nonsummer
2023-01-16 17:00 | 2023-01-16 18:00 | Winter | TRUE | nonsummer
2023-01-16 18:00 | 2023-01-16 19:00 | Winter | TRUE | nonsummer
2023-01-16 19:00 | 2023-01-16 20:00 | Winter | TRUE | nonsummer
2023-01-16 20:00 | 2023-01-16 21:00 | Winter | TRUE | nonsummer
2023-01-16 21:00 | 2023-01-16 22:00 | Winter | FALSE | nonsummer
2023-01-16 22:00 | 2023-01-16 23:00 | Winter | FALSE | nonsummer
2023-01-16 23:00 | 2023-01-17 | Winter | FALSE | nonsummer
2023-01-17 | 2023-01-17 01:00 | Winter | FALSE | nonsummer
2023-01-17 01:00 | 2023-01-17 02:00 | Winter | FALSE | nonsummer
2023-01-17 02:00 | 2023-01-17 03:00 | Winter | FALSE | nonsummer
2023-01-17 03:00 | 2023-01-17 04:00 | Winter | FALSE | nonsummer
2023-01-17 04:00 | 2023-01-17 05:00 | Winter | FALSE | nonsummer
2023-01-17 05:00 | 2023-01-17 06:00 | Winter | FALSE | nonsummer
2023-01-17 06:00 | 2023-01-17 07:00 | Winter | FALSE | nonsummer
2023-01-17 07:00 | 2023-01-17 08:00 | Winter | FALSE | nonsummer
2023-01-17 08:00 | 2023-01-17 09:00 | Winter | FALSE | nonsummer
2023-01-17 09:00 | 2023-01-17 10:00 | Winter | FALSE | nonsummer
2023-01-17 10:00 | 2023-01-17 11:00 | Winter | FALSE | nonsummer
2023-01-17 11:00 | 2023-01-17 12:00 | Winter | FALSE | nonsummer
2023-01-17 12:00 | 2023-01-17 13:00 | Winter | FALSE | nonsummer
2023-01-17 13:00 | 2023-01-17 14:00 | Winter | FALSE | nonsummer
2023-01-17 14:00 | 2023-01-17 15:00 | Winter | FALSE | nonsummer
2023-01-17 15:00 | 2023-01-17 16:00 | Winter | FALSE | nonsummer
2023-01-17 16:00 | 2023-01-17 17:00 | Winter | TRUE | nonsummer
2023-01-17 17:00 | 2023-01-17 18:00 | Winter | TRUE | nonsummer
2023-01-17 18:00 | 2023-01-17 19:00 | Winter | TRUE | nonsummer
2023-01-17 19:00 | 2023-01-17 20:00 | Winter | TRUE | nonsummer
2023-01-17 20:00 | 2023-01-17 21:00 | Winter | TRUE | nonsummer
2023-01-17 21:00 | 2023-01-17 22:00 | Winter | FALSE | nonsummer
2023-01-17 22:00 | 2023-01-17 23:00 | Winter | FALSE | nonsummer
2023-01-17 23:00 | 2023-01-18 | Winter | FALSE | nonsummer
2023-01-18 | 2023-01-18 01:00 | Winter | FALSE | nonsummer
2023-01-18 01:00 | 2023-01-18 02:00 | Winter | FALSE | nonsummer
2023-01-18 02:00 | 2023-01-18 03:00 | Winter | FALSE | nonsummer
2023-01-18 03:00 | 2023-01-18 04:00 | Winter | FALSE | nonsummer
2023-01-18 04:00 | 2023-01-18 05:00 | Winter | FALSE | nonsummer
2023-01-18 05:00 | 2023-01-18 06:00 | Winter | FALSE | nonsummer
2023-01-18 06:00 | 2023-01-18 07:00 | Winter | FALSE | nonsummer
2023-01-18 07:00 | 2023-01-18 08:00 | Winter | FALSE | nonsummer
2023-01-18 08:00 | 2023-01-18 09:00 | Winter | FALSE | nonsummer
2023-01-18 09:00 | 2023-01-18 10:00 | Winter | FALSE | nonsummer
2023-01-18 10:00 | 2023-01-18 11:00 | Winter | FALSE | nonsummer
2023-01-18 11:00 | 2023-01-18 12:00 | Winter | FALSE | nonsummer
2023-01-18 12:00 | 2023-01-18 13:00 | Winter | FALSE | nonsummer
2023-01-18 13:00 | 2023-01-18 14:00 | Winter | FALSE | nonsummer
2023-01-18 14:00 | 2023-01-18 15:00 | Winter | FALSE | nonsummer
2023-01-18 15:00 | 2023-01-18 16:00 | Winter | FALSE | nonsummer
2023-01-18 16:00 | 2023-01-18 17:00 | Winter | TRUE | nonsummer
2023-01-18 17:00 | 2023-01-18 18:00 | Winter | TRUE | nonsummer
2023-01-18 18:00 | 2023-01-18 19:00 | Winter | TRUE | nonsummer
2023-01-18 19:00 | 2023-01-18 20:00 | Winter | TRUE | nonsummer
2023-01-18 20:00 | 2023-01-18 21:00 | Winter | TRUE | nonsummer
2023-01-18 21:00 | 2023-01-18 22:00 | Winter | FALSE | nonsummer
2023-01-18 22:00 | 2023-01-18 23:00 | Winter | FALSE | nonsummer
2023-01-18 23:00 | 2023-01-19 | Winter | FALSE | nonsummer
2023-01-19 | 2023-01-19 01:00 | Winter | FALSE | nonsummer
2023-01-19 01:00 | 2023-01-19 02:00 | Winter | FALSE | nonsummer
2023-01-19 02:00 | 2023-01-19 03:00 | Winter | FALSE | nonsummer
2023-01-19 03:00 | 2023-01-19 04:00 | Winter | FALSE | nonsummer
2023-01-19 04:00 | 2023-01-19 05:00 | Winter | FALSE | nonsummer
2023-01-19 05:00 | 2023-01-19 06:00 | Winter | FALSE | nonsummer
2023-01-19 06:00 | 2023-01-19 07:00 | Winter | FALSE | nonsummer
2023-01-19 07:00 | 2023-01-19 08:00 | Winter | FALSE | nonsummer
2023-01-19 08:00 | 2023-01-19 09:00 | Winter | FALSE | nonsummer
2023-01-19 09:00 | 2023-01-19 10:00 | Winter | FALSE | nonsummer
2023-01-19 10:00 | 2023-01-19 11:00 | Winter | FALSE | nonsummer
2023-01-19 11:00 | 2023-01-19 12:00 | Winter | FALSE | nonsummer
2023-01-19 12:00 | 2023-01-19 13:00 | Winter | FALSE | nonsummer
2023-01-19 13:00 | 2023-01-19 14:00 | Winter | FALSE | nonsummer
2023-01-19 14:00 | 2023-01-19 15:00 | Winter | FALSE | nonsummer
2023-01-19 15:00 | 2023-01-19 16:00 | Winter | FALSE | nonsummer
2023-01-19 16:00 | 2023-01-19 17:00 | Winter | TRUE | nonsummer
2023-01-19 17:00 | 2023-01-19 18:00 | Winter | TRUE | nonsummer
2023-01-19 18:00 | 2023-01-19 19:00 | Winter | TRUE | nonsummer
2023-01-19 19:00 | 2023-01-19 20:00 | Winter | TRUE | nonsummer
2023-01-19 20:00 | 2023-01-19 21:00 | Winter | TRUE | nonsummer
2023-01-19 21:00 | 2023-01-19 22:00 | Winter | FALSE | nonsummer
2023-01-19 22:00 | 2023-01-19 23:00 | Winter | FALSE | nonsummer
2023-01-19 23:00 | 2023-01-20 | Winter | FALSE | nonsummer
2023-01-20 | 2023-01-20 01:00 | Winter | FALSE | nonsummer
2023-01-20 01:00 | 2023-01-20 02:00 | Winter | FALSE | nonsummer
2023-01-20 02:00 | 2023-01-20 03:00 | Winter | FALSE | nonsummer
2023-01-20 03:00 | 2023-01-20 04:00 | Winter | FALSE | nonsummer
2023-01-20 04:00 | 2023-01-20 05:00 | Winter | FALSE | nonsummer
2023-01-20 05:00 | 2023-01-20 06:00 | Winter | FALSE | nonsummer
2023-01-20 06:00 | 2023-01-20 07:00 | Winter | FALSE | nonsummer
2023-01-20 07:00 | 2023-01-20 08:00 | Winter | FALSE | nonsummer
2023-01-20 08:00 | 2023-01-20 09:00 | Winter | FALSE | nonsummer
2023-01-20 09:00 | 2023-01-20 10:00 | Winter | FALSE | nonsummer
2023-01-20 10:00 | 2023-01-20 11:00 | Winter | FALSE | nonsummer
2023-01-20 11:00 | 2023-01-20 12:00 | Winter | FALSE | nonsummer
2023-01-20 12:00 | 2023-01-20 13:00 | Winter | FALSE | nonsummer
2023-01-20 13:00 | 2023-01-20 14:00 | Winter | FALSE | nonsummer
2023-01-20 14:00 | 2023-01-20 15:00 | Winter | FALSE | nonsummer
2023-01-20 15:00 | 2023-01-20 16:00 | Winter | FALSE | nonsummer
2023-01-20 16:00 | 2023-01-20 17:00 | Winter | TRUE | nonsummer
2023-01-20 17:00 | 2023-01-20 18:00 | Winter | TRUE | nonsummer
2023-01-20 18:00 | 2023-01-20 19:00 | Winter | TRUE | nonsummer
2023-01-20 19:00 | 2023-01-20 20:00 | Winter | TRUE | nonsummer
2023-01-20 20:00 | 2023-01-20 21:00 | Winter | TRUE | nonsummer
2023-01-20 21:00 | 2023-01-20 22:00 | Winter | FALSE | nonsummer
2023-01-20 22:00 | 2023-01-20 23:00 | Winter | FALSE | nonsummer
2023-01-20 23:00 | 2023-01-21 | Winter | FALSE | nonsummer
2023-01-21 | 2023-01-21 01:00 | Winter | FALSE | nonsummer
2023-01-21 01:00 | 2023-01-21 02:00 | Winter | FALSE | nonsummer
2023-01-21 02:00 | 2023-01-21 03:00 | Winter | FALSE | nonsummer
2023-01-21 03:00 | 2023-01-21 04:00 | Winter | FALSE | nonsummer
2023-01-21 04:00 | 2023-01-21 05:00 | Winter | FALSE | nonsummer
2023-01-21 05:00 | 2023-01-21 06:00 | Winter | FALSE | nonsummer
2023-01-21 06:00 | 2023-01-21 07:00 | Winter | FALSE | nonsummer
2023-01-21 07:00 | 2023-01-21 08:00 | Winter | FALSE | nonsummer
2023-01-21 08:00 | 2023-01-21 09:00 | Winter | FALSE | nonsummer
2023-01-21 09:00 | 2023-01-21 10:00 | Winter | FALSE | nonsummer
2023-01-21 10:00 | 2023-01-21 11:00 | Winter | FALSE | nonsummer
2023-01-21 11:00 | 2023-01-21 12:00 | Winter | FALSE | nonsummer
2023-01-21 12:00 | 2023-01-21 13:00 | Winter | FALSE | nonsummer
2023-01-21 13:00 | 2023-01-21 14:00 | Winter | FALSE | nonsummer
2023-01-21 14:00 | 2023-01-21 15:00 | Winter | FALSE | nonsummer
2023-01-21 15:00 | 2023-01-21 16:00 | Winter | FALSE | nonsummer
2023-01-21 16:00 | 2023-01-21 17:00 | Winter | TRUE | nonsummer
2023-01-21 17:00 | 2023-01-21 18:00 | Winter | TRUE | nonsummer
2023-01-21 18:00 | 2023-01-21 19:00 | Winter | TRUE | nonsummer
2023-01-21 19:00 | 2023-01-21 20:00 | Winter | TRUE | nonsummer
2023-01-21 20:00 | 2023-01-21 21:00 | Winter | TRUE | nonsummer
2023-01-21 21:00 | 2023-01-21 22:00 | Winter | FALSE | nonsummer
2023-01-21 22:00 | 2023-01-21 23:00 | Winter | FALSE | nonsummer
2023-01-21 23:00 | 2023-01-22 | Winter | FALSE | nonsummer
2023-01-22 | 2023-01-22 01:00 | Winter | FALSE | nonsummer
2023-01-22 01:00 | 2023-01-22 02:00 | Winter | FALSE | nonsummer
2023-01-22 02:00 | 2023-01-22 03:00 | Winter | FALSE | nonsummer
2023-01-22 03:00 | 2023-01-22 04:00 | Winter | FALSE | nonsummer
2023-01-22 04:00 | 2023-01-22 05:00 | Winter | FALSE | nonsummer
2023-01-22 05:00 | 2023-01-22 06:00 | Winter | FALSE | nonsummer
2023-01-22 06:00 | 2023-01-22 07:00 | Winter | FALSE | nonsummer
2023-01-22 07:00 | 2023-01-22 08:00 | Winter | FALSE | nonsummer
2023-01-22 08:00 | 2023-01-22 09:00 | Winter | FALSE | nonsummer
2023-01-22 09:00 | 2023-01-22 10:00 | Winter | FALSE | nonsummer
2023-01-22 10:00 | 2023-01-22 11:00 | Winter | FALSE | nonsummer
2023-01-22 11:00 | 2023-01-22 12:00 | Winter | FALSE | nonsummer
2023-01-22 12:00 | 2023-01-22 13:00 | Winter | FALSE | nonsummer
2023-01-22 13:00 | 2023-01-22 14:00 | Winter | FALSE | nonsummer
2023-01-22 14:00 | 2023-01-22 15:00 | Winter | FALSE | nonsummer
2023-01-22 15:00 | 2023-01-22 16:00 | Winter | FALSE | nonsummer
2023-01-22 16:00 | 2023-01-22 17:00 | Winter | TRUE | nonsummer
2023-01-22 17:00 | 2023-01-22 18:00 | Winter | TRUE | nonsummer
2023-01-22 18:00 | 2023-01-22 19:00 | Winter | TRUE | nonsummer
2023-01-22 19:00 | 2023-01-22 20:00 | Winter | TRUE | nonsummer
2023-01-22 20:00 | 2023-01-22 21:00 | Winter | TRUE | nonsummer
2023-01-22 21:00 | 2023-01-22 22:00 | Winter | FALSE | nonsummer
2023-01-22 22:00 | 2023-01-22 23:00 | Winter | FALSE | nonsummer
2023-01-22 23:00 | 2023-01-23 | Winter | FALSE | nonsummer
2023-01-23 | 2023-01-23 01:00 | Winter | FALSE | nonsummer
2023-01-23 01:00 | 2023-01-23 02:00 | Winter | FALSE | nonsummer
2023-01-23 02:00 | 2023-01-23 03:00 | Winter | FALSE | nonsummer
2023-01-23 03:00 | 2023-01-23 04:00 | Winter | FALSE | nonsummer
2023-01-23 04:00 | 2023-01-23 05:00 | Winter | FALSE | nonsummer
2023-01-23 05:00 | 2023-01-23 06:00 | Winter | FALSE | nonsummer
2023-01-23 06:00 | 2023-01-23 07:00 | Winter | FALSE | nonsummer
2023-01-23 07:00 | 2023-01-23 08:00 | Winter | FALSE | nonsummer
2023-01-23 08:00 | 2023-01-23 09:00 | Winter | FALSE | nonsummer
2023-01-23 09:00 | 2023-01-23 10:00 | Winter | FALSE | nonsummer
2023-01-23 10:00 | 2023-01-23 11:00 | Winter | FALSE | nonsummer
2023-01-23 11:00 | 2023-01-23 12:00 | Winter | FALSE | nonsummer
2023-01-23 12:00 | 2023-01-23 13:00 | Winter | FALSE | nonsummer
2023-01-23 13:00 | 2023-01-23 14:00 | Winter | FALSE | nonsummer
2023-01-23 14:00 | 2023-01-23 15:00 | Winter | FALSE | nonsummer
2023-01-23 15:00 | 2023-01-23 16:00 | Winter | FALSE | nonsummer
2023-01-23 16:00 | 2023-01-23 17:00 | Winter | TRUE | nonsummer
2023-01-23 17:00 | 2023-01-23 18:00 | Winter | TRUE | nonsummer
2023-01-23 18:00 | 2023-01-23 19:00 | Winter | TRUE | nonsummer
2023-01-23 19:00 | 2023-01-23 20:00 | Winter | TRUE | nonsummer
2023-01-23 20:00 | 2023-01-23 21:00 | Winter | TRUE | nonsummer
2023-01-23 21:00 | 2023-01-23 22:00 | Winter | FALSE | nonsummer
2023-01-23 22:00 | 2023-01-23 23:00 | Winter | FALSE | nonsummer
2023-01-23 23:00 | 2023-01-24 | Winter | FALSE | nonsummer
2023-01-24 | 2023-01-24 01:00 | Winter | FALSE | nonsummer
2023-01-24 01:00 | 2023-01-24 02:00 | Winter | FALSE | nonsummer
2023-01-24 02:00 | 2023-01-24 03:00 | Winter | FALSE | nonsummer
2023-01-24 03:00 | 2023-01-24 04:00 | Winter | FALSE | nonsummer
2023-01-24 04:00 | 2023-01-24 05:00 | Winter | FALSE | nonsummer
2023-01-24 05:00 | 2023-01-24 06:00 | Winter | FALSE | nonsummer
2023-01-24 06:00 | 2023-01-24 07:00 | Winter | FALSE | nonsummer
2023-01-24 07:00 | 2023-01-24 08:00 | Winter | FALSE | nonsummer
2023-01-24 08:00 | 2023-01-24 09:00 | Winter | FALSE | nonsummer
2023-01-24 09:00 | 2023-01-24 10:00 | Winter | FALSE | nonsummer
2023-01-24 10:00 | 2023-01-24 11:00 | Winter | FALSE | nonsummer
2023-01-24 11:00 | 2023-01-24 12:00 | Winter | FALSE | nonsummer
2023-01-24 12:00 | 2023-01-24 13:00 | Winter | FALSE | nonsummer
2023-01-24 13:00 | 2023-01-24 14:00 | Winter | FALSE | nonsummer
2023-01-24 14:00 | 2023-01-24 15:00 | Winter | FALSE | nonsummer
2023-01-24 15:00 | 2023-01-24 16:00 | Winter | FALSE | nonsummer
2023-01-24 16:00 | 2023-01-24 17:00 | Winter | TRUE | nonsummer
2023-01-24 17:00 | 2023-01-24 18:00 | Winter | TRUE | nonsummer
2023-01-24 18:00 | 2023-01-24 19:00 | Winter | TRUE | nonsummer
2023-01-24 19:00 | 2023-01-24 20:00 | Winter | TRUE | nonsummer
2023-01-24 20:00 | 2023-01-24 21:00 | Winter | TRUE | nonsummer
2023-01-24 21:00 | 2023-01-24 22:00 | Winter | FALSE | nonsummer
2023-01-24 22:00 | 2023-01-24 23:00 | Winter | FALSE | nonsummer
2023-01-24 23:00 | 2023-01-25 | Winter | FALSE | nonsummer
2023-01-25 | 2023-01-25 01:00 | Winter | FALSE | nonsummer
2023-01-25 01:00 | 2023-01-25 02:00 | Winter | FALSE | nonsummer
2023-01-25 02:00 | 2023-01-25 03:00 | Winter | FALSE | nonsummer
2023-01-25 03:00 | 2023-01-25 04:00 | Winter | FALSE | nonsummer
2023-01-25 04:00 | 2023-01-25 05:00 | Winter | FALSE | nonsummer
2023-01-25 05:00 | 2023-01-25 06:00 | Winter | FALSE | nonsummer
2023-01-25 06:00 | 2023-01-25 07:00 | Winter | FALSE | nonsummer
2023-01-25 07:00 | 2023-01-25 08:00 | Winter | FALSE | nonsummer
2023-01-25 08:00 | 2023-01-25 09:00 | Winter | FALSE | nonsummer
2023-01-25 09:00 | 2023-01-25 10:00 | Winter | FALSE | nonsummer
2023-01-25 10:00 | 2023-01-25 11:00 | Winter | FALSE | nonsummer
2023-01-25 11:00 | 2023-01-25 12:00 | Winter | FALSE | nonsummer
2023-01-25 12:00 | 2023-01-25 13:00 | Winter | FALSE | nonsummer
2023-01-25 13:00 | 2023-01-25 14:00 | Winter | FALSE | nonsummer
2023-01-25 14:00 | 2023-01-25 15:00 | Winter | FALSE | nonsummer
2023-01-25 15:00 | 2023-01-25 16:00 | Winter | FALSE | nonsummer
2023-01-25 16:00 | 2023-01-25 17:00 | Winter | TRUE | nonsummer
2023-01-25 17:00 | 2023-01-25 18:00 | Winter | TRUE | nonsummer
2023-01-25 18:00 | 2023-01-25 19:00 | Winter | TRUE | nonsummer
2023-01-25 19:00 | 2023-01-25 20:00 | Winter | TRUE | nonsummer
2023-01-25 20:00 | 2023-01-25 21:00 | Winter | TRUE | nonsummer
2023-01-25 21:00 | 2023-01-25 22:00 | Winter | FALSE | nonsummer
2023-01-25 22:00 | 2023-01-25 23:00 | Winter | FALSE | nonsummer
2023-01-25 23:00 | 2023-01-26 | Winter | FALSE | nonsummer
2023-01-26 | 2023-01-26 01:00 | Winter | FALSE | nonsummer
2023-01-26 01:00 | 2023-01-26 02:00 | Winter | FALSE | nonsummer
2023-01-26 02:00 | 2023-01-26 03:00 | Winter | FALSE | nonsummer
2023-01-26 03:00 | 2023-01-26 04:00 | Winter | FALSE | nonsummer
2023-01-26 04:00 | 2023-01-26 05:00 | Winter | FALSE | nonsummer
2023-01-26 05:00 | 2023-01-26 06:00 | Winter | FALSE | nonsummer
2023-01-26 06:00 | 2023-01-26 07:00 | Winter | FALSE | nonsummer
2023-01-26 07:00 | 2023-01-26 08:00 | Winter | FALSE | nonsummer
2023-01-26 08:00 | 2023-01-26 09:00 | Winter | FALSE | nonsummer
2023-01-26 09:00 | 2023-01-26 10:00 | Winter | FALSE | nonsummer
2023-01-26 10:00 | 2023-01-26 11:00 | Winter | FALSE | nonsummer
2023-01-26 11:00 | 2023-01-26 12:00 | Winter | FALSE | nonsummer
2023-01-26 12:00 | 2023-01-26 13:00 | Winter | FALSE | nonsummer
2023-01-26 13:00 | 2023-01-26 14:00 | Winter | FALSE | nonsummer
2023-01-26 14:00 | 2023-01-26 15:00 | Winter | FALSE | nonsummer
2023-01-26 15:00 | 2023-01-26 16:00 | Winter | FALSE | nonsummer
2023-01-26 16:00 | 2023-01-26 17:00 | Winter | TRUE | nonsummer
2023-01-26 17:00 | 2023-01-26 18:00 | Winter | TRUE | nonsummer
2023-01-26 18:00 | 2023-01-26 19:00 | Winter | TRUE | nonsummer
2023-01-26 19:00 | 2023-01-26 20:00 | Winter | TRUE | nonsummer
2023-01-26 20:00 | 2023-01-26 21:00 | Winter | TRUE | nonsummer
2023-01-26 21:00 | 2023-01-26 22:00 | Winter | FALSE | nonsummer
2023-01-26 22:00 | 2023-01-26 23:00 | Winter | FALSE | nonsummer
2023-01-26 23:00 | 2023-01-27 | Winter | FALSE | nonsummer
2023-01-27 | 2023-01-27 01:00 | Winter | FALSE | nonsummer
2023-01-27 01:00 | 2023-01-27 02:00 | Winter | FALSE | nonsummer
2023-01-27 02:00 | 2023-01-27 03:00 | Winter | FALSE | nonsummer
2023-01-27 03:00 | 2023-01-27 04:00 | Winter | FALSE | nonsummer
2023-01-27 04:00 | 2023-01-27 05:00 | Winter | FALSE | nonsummer
2023-01-27 05:00 | 2023-01-27 06:00 | Winter | FALSE | nonsummer
2023-01-27 06:00 | 2023-01-27 07:00 | Winter | FALSE | nonsummer
2023-01-27 07:00 | 2023-01-27 08:00 | Winter | FALSE | nonsummer
2023-01-27 08:00 | 2023-01-27 09:00 | Winter | FALSE | nonsummer
2023-01-27 09:00 | 2023-01-27 10:00 | Winter | FALSE | nonsummer
2023-01-27 10:00 | 2023-01-27 11:00 | Winter | FALSE | nonsummer
2023-01-27 11:00 | 2023-01-27 12:00 | Winter | FALSE | nonsummer
2023-01-27 12:00 | 2023-01-27 13:00 | Winter | FALSE | nonsummer
2023-01-27 13:00 | 2023-01-27 14:00 | Winter | FALSE | nonsummer
2023-01-27 14:00 | 2023-01-27 15:00 | Winter | FALSE | nonsummer
2023-01-27 15:00 | 2023-01-27 16:00 | Winter | FALSE | nonsummer
2023-01-27 16:00 | 2023-01-27 17:00 | Winter | TRUE | nonsummer
2023-01-27 17:00 | 2023-01-27 18:00 | Winter | TRUE | nonsummer
2023-01-27 18:00 | 2023-01-27 19:00 | Winter | TRUE | nonsummer
2023-01-27 19:00 | 2023-01-27 20:00 | Winter | TRUE | nonsummer
2023-01-27 20:00 | 2023-01-27 21:00 | Winter | TRUE | nonsummer
2023-01-27 21:00 | 2023-01-27 22:00 | Winter | FALSE | nonsummer
2023-01-27 22:00 | 2023-01-27 23:00 | Winter | FALSE | nonsummer
2023-01-27 23:00 | 2023-01-28 | Winter | FALSE | nonsummer
2023-01-28 | 2023-01-28 01:00 | Winter | FALSE | nonsummer
2023-01-28 01:00 | 2023-01-28 02:00 | Winter | FALSE | nonsummer
2023-01-28 02:00 | 2023-01-28 03:00 | Winter | FALSE | nonsummer
2023-01-28 03:00 | 2023-01-28 04:00 | Winter | FALSE | nonsummer
2023-01-28 04:00 | 2023-01-28 05:00 | Winter | FALSE | nonsummer
2023-01-28 05:00 | 2023-01-28 06:00 | Winter | FALSE | nonsummer
2023-01-28 06:00 | 2023-01-28 07:00 | Winter | FALSE | nonsummer
2023-01-28 07:00 | 2023-01-28 08:00 | Winter | FALSE | nonsummer
2023-01-28 08:00 | 2023-01-28 09:00 | Winter | FALSE | nonsummer
2023-01-28 09:00 | 2023-01-28 10:00 | Winter | FALSE | nonsummer
2023-01-28 10:00 | 2023-01-28 11:00 | Winter | FALSE | nonsummer
2023-01-28 11:00 | 2023-01-28 12:00 | Winter | FALSE | nonsummer
2023-01-28 12:00 | 2023-01-28 13:00 | Winter | FALSE | nonsummer
2023-01-28 13:00 | 2023-01-28 14:00 | Winter | FALSE | nonsummer
2023-01-28 14:00 | 2023-01-28 15:00 | Winter | FALSE | nonsummer
2023-01-28 15:00 | 2023-01-28 16:00 | Winter | FALSE | nonsummer
2023-01-28 16:00 | 2023-01-28 17:00 | Winter | TRUE | nonsummer
2023-01-28 17:00 | 2023-01-28 18:00 | Winter | TRUE | nonsummer
2023-01-28 18:00 | 2023-01-28 19:00 | Winter | TRUE | nonsummer
2023-01-28 19:00 | 2023-01-28 20:00 | Winter | TRUE | nonsummer
2023-01-28 20:00 | 2023-01-28 21:00 | Winter | TRUE | nonsummer
2023-01-28 21:00 | 2023-01-28 22:00 | Winter | FALSE | nonsummer
2023-01-28 22:00 | 2023-01-28 23:00 | Winter | FALSE | nonsummer
2023-01-28 23:00 | 2023-01-29 | Winter | FALSE | nonsummer
2023-01-29 | 2023-01-29 01:00 | Winter | FALSE | nonsummer
2023-01-29 01:00 | 2023-01-29 02:00 | Winter | FALSE | nonsummer
2023-01-29 02:00 | 2023-01-29 03:00 | Winter | FALSE | nonsummer
2023-01-29 03:00 | 2023-01-29 04:00 | Winter | FALSE | nonsummer
2023-01-29 04:00 | 2023-01-29 05:00 | Winter | FALSE | nonsummer
2023-01-29 05:00 | 2023-01-29 06:00 | Winter | FALSE | nonsummer
2023-01-29 06:00 | 2023-01-29 07:00 | Winter | FALSE | nonsummer
2023-01-29 07:00 | 2023-01-29 08:00 | Winter | FALSE | nonsummer
2023-01-29 08:00 | 2023-01-29 09:00 | Winter | FALSE | nonsummer
2023-01-29 09:00 | 2023-01-29 10:00 | Winter | FALSE | nonsummer
2023-01-29 10:00 | 2023-01-29 11:00 | Winter | FALSE | nonsummer
2023-01-29 11:00 | 2023-01-29 12:00 | Winter | FALSE | nonsummer
2023-01-29 12:00 | 2023-01-29 13:00 | Winter | FALSE | nonsummer
2023-01-29 13:00 | 2023-01-29 14:00 | Winter | FALSE | nonsummer
2023-01-29 14:00 | 2023-01-29 15:00 | Winter | FALSE | nonsummer
2023-01-29 15:00 | 2023-01-29 16:00 | Winter | FALSE | nonsummer
2023-01-29 16:00 | 2023-01-29 17:00 | Winter | TRUE | nonsummer
2023-01-29 17:00 | 2023-01-29 18:00 | Winter | TRUE | nonsummer
2023-01-29 18:00 | 2023-01-29 19:00 | Winter | TRUE | nonsummer
2023-01-29 19:00 | 2023-01-29 20:00 | Winter | TRUE | nonsummer
2023-01-29 20:00 | 2023-01-29 21:00 | Winter | TRUE | nonsummer
2023-01-29 21:00 | 2023-01-29 22:00 | Winter | FALSE | nonsummer
2023-01-29 22:00 | 2023-01-29 23:00 | Winter | FALSE | nonsummer
2023-01-29 23:00 | 2023-01-30 | Winter | FALSE | nonsummer
2023-01-30 | 2023-01-30 01:00 | Winter | FALSE | nonsummer
2023-01-30 01:00 | 2023-01-30 02:00 | Winter | FALSE | nonsummer
2023-01-30 02:00 | 2023-01-30 03:00 | Winter | FALSE | nonsummer
2023-01-30 03:00 | 2023-01-30 04:00 | Winter | FALSE | nonsummer
2023-01-30 04:00 | 2023-01-30 05:00 | Winter | FALSE | nonsummer
2023-01-30 05:00 | 2023-01-30 06:00 | Winter | FALSE | nonsummer
2023-01-30 06:00 | 2023-01-30 07:00 | Winter | FALSE | nonsummer
2023-01-30 07:00 | 2023-01-30 08:00 | Winter | FALSE | nonsummer
2023-01-30 08:00 | 2023-01-30 09:00 | Winter | FALSE | nonsummer
2023-01-30 09:00 | 2023-01-30 10:00 | Winter | FALSE | nonsummer
2023-01-30 10:00 | 2023-01-30 11:00 | Winter | FALSE | nonsummer
2023-01-30 11:00 | 2023-01-30 12:00 | Winter | FALSE | nonsummer
2023-01-30 12:00 | 2023-01-30 13:00 | Winter | FALSE | nonsummer
2023-01-30 13:00 | 2023-01-30 14:00 | Winter | FALSE | nonsummer
2023-01-30 14:00 | 2023-01-30 15:00 | Winter | FALSE | nonsummer
2023-01-30 15:00 | 2023-01-30 16:00 | Winter | FALSE | nonsummer
2023-01-30 16:00 | 2023-01-30 17:00 | Winter | TRUE | nonsummer
2023-01-30 17:00 | 2023-01-30 18:00 | Winter | TRUE | nonsummer
2023-01-30 18:00 | 2023-01-30 19:00 | Winter | TRUE | nonsummer
2023-01-30 19:00 | 2023-01-30 20:00 | Winter | TRUE | nonsummer
2023-01-30 20:00 | 2023-01-30 21:00 | Winter | TRUE | nonsummer
2023-01-30 21:00 | 2023-01-30 22:00 | Winter | FALSE | nonsummer
2023-01-30 22:00 | 2023-01-30 23:00 | Winter | FALSE | nonsummer
2023-01-30 23:00 | 2023-01-31 | Winter | FALSE | nonsummer
2023-01-31 | 2023-01-31 01:00 | Winter | FALSE | nonsummer
2023-01-31 01:00 | 2023-01-31 02:00 | Winter | FALSE | nonsummer
2023-01-31 02:00 | 2023-01-31 03:00 | Winter | FALSE | nonsummer
2023-01-31 03:00 | 2023-01-31 04:00 | Winter | FALSE | nonsummer
2023-01-31 04:00 | 2023-01-31 05:00 | Winter | FALSE | nonsummer
2023-01-31 05:00 | 2023-01-31 06:00 | Winter | FALSE | nonsummer
2023-01-31 06:00 | 2023-01-31 07:00 | Winter | FALSE | nonsummer
2023-01-31 07:00 | 2023-01-31 08:00 | Winter | FALSE | nonsummer
2023-01-31 08:00 | 2023-01-31 09:00 | Winter | FALSE | nonsummer
2023-01-31 09:00 | 2023-01-31 10:00 | Winter | FALSE | nonsummer
2023-01-31 10:00 | 2023-01-31 11:00 | Winter | FALSE | nonsummer
2023-01-31 11:00 | 2023-01-31 12:00 | Winter | FALSE | nonsummer
2023-01-31 12:00 | 2023-01-31 13:00 | Winter | FALSE | nonsummer
2023-01-31 13:00 | 2023-01-31 14:00 | Winter | FALSE | nonsummer
2023-01-31 14:00 | 2023-01-31 15:00 | Winter | FALSE | nonsummer
2023-01-31 15:00 | 2023-01-31 16:00 | Winter | FALSE | nonsummer
2023-01-31 16:00 | 2023-01-31 17:00 | Winter | TRUE | nonsummer
2023-01-31 17:00 | 2023-01-31 18:00 | Winter | TRUE | nonsummer
2023-01-31 18:00 | 2023-01-31 19:00 | Winter | TRUE | nonsummer
2023-01-31 19:00 | 2023-01-31 20:00 | Winter | TRUE | nonsummer
2023-01-31 20:00 | 2023-01-31 21:00 | Winter | TRUE | nonsummer
2023-01-31 21:00 | 2023-01-31 22:00 | Winter | FALSE | nonsummer
2023-01-31 22:00 | 2023-01-31 23:00 | Winter | FALSE | nonsummer
2023-01-31 23:00 | 2023-02-01 | Winter | FALSE | nonsummer
2023-02-01 | 2023-02-01 01:00 | Winter | FALSE | nonsummer
2023-02-01 01:00 | 2023-02-01 02:00 | Winter | FALSE | nonsummer
2023-02-01 02:00 | 2023-02-01 03:00 | Winter | FALSE | nonsummer
2023-02-01 03:00 | 2023-02-01 04:00 | Winter | FALSE | nonsummer
2023-02-01 04:00 | 2023-02-01 05:00 | Winter | FALSE | nonsummer
2023-02-01 05:00 | 2023-02-01 06:00 | Winter | FALSE | nonsummer
2023-02-01 06:00 | 2023-02-01 07:00 | Winter | FALSE | nonsummer
2023-02-01 07:00 | 2023-02-01 08:00 | Winter | FALSE | nonsummer
2023-02-01 08:00 | 2023-02-01 09:00 | Winter | FALSE | nonsummer
2023-02-01 09:00 | 2023-02-01 10:00 | Winter | FALSE | nonsummer
2023-02-01 10:00 | 2023-02-01 11:00 | Winter | FALSE | nonsummer
2023-02-01 11:00 | 2023-02-01 12:00 | Winter | FALSE | nonsummer
2023-02-01 12:00 | 2023-02-01 13:00 | Winter | FALSE | nonsummer
2023-02-01 13:00 | 2023-02-01 14:00 | Winter | FALSE | nonsummer
2023-02-01 14:00 | 2023-02-01 15:00 | Winter | FALSE | nonsummer
2023-02-01 15:00 | 2023-02-01 16:00 | Winter | FALSE | nonsummer
2023-02-01 16:00 | 2023-02-01 17:00 | Winter | TRUE | nonsummer
2023-02-01 17:00 | 2023-02-01 18:00 | Winter | TRUE | nonsummer
2023-02-01 18:00 | 2023-02-01 19:00 | Winter | TRUE | nonsummer
2023-02-01 19:00 | 2023-02-01 20:00 | Winter | TRUE | nonsummer
2023-02-01 20:00 | 2023-02-01 21:00 | Winter | TRUE | nonsummer
2023-02-01 21:00 | 2023-02-01 22:00 | Winter | FALSE | nonsummer
2023-02-01 22:00 | 2023-02-01 23:00 | Winter | FALSE | nonsummer
2023-02-01 23:00 | 2023-02-02 | Winter | FALSE | nonsummer
2023-02-02 | 2023-02-02 01:00 | Winter | FALSE | nonsummer
2023-02-02 01:00 | 2023-02-02 02:00 | Winter | FALSE | nonsummer
2023-02-02 02:00 | 2023-02-02 03:00 | Winter | FALSE | nonsummer
2023-02-02 03:00 | 2023-02-02 04:00 | Winter | FALSE | nonsummer
2023-02-02 04:00 | 2023-02-02 05:00 | Winter | FALSE | nonsummer
2023-02-02 05:00 | 2023-02-02 06:00 | Winter | FALSE | nonsummer
2023-02-02 06:00 | 2023-02-02 07:00 | Winter | FALSE | nonsummer
2023-02-02 07:00 | 2023-02-02 08:00 | Winter | FALSE | nonsummer
2023-02-02 08:00 | 2023-02-02 09:00 | Winter | FALSE | nonsummer
2023-02-02 09:00 | 2023-02-02 10:00 | Winter | FALSE | nonsummer
2023-02-02 10:00 | 2023-02-02 11:00 | Winter | FALSE | nonsummer
2023-02-02 11:00 | 2023-02-02 12:00 | Winter | FALSE | nonsummer
2023-02-02 12:00 | 2023-02-02 13:00 | Winter | FALSE | nonsummer
2023-02-02 13:00 | 2023-02-02 14:00 | Winter | FALSE | nonsummer
2023-02-02 14:00 | 2023-02-02 15:00 | Winter | FALSE | nonsummer
2023-02-02 15:00 | 2023-02-02 16:00 | Winter | FALSE | nonsummer
2023-02-02 16:00 | 2023-02-02 17:00 | Winter | TRUE | nonsummer
2023-02-02 17:00 | 2023-02-02 18:00 | Winter | TRUE | nonsummer
2023-02-02 18:00 | 2023-02-02 19:00 | Winter | TRUE | nonsummer
2023-02-02 19:00 | 2023-02-02 20:00 | Winter | TRUE | nonsummer
2023-02-02 20:00 | 2023-02-02 21:00 | Winter | TRUE | nonsummer
2023-02-02 21:00 | 2023-02-02 22:00 | Winter | FALSE | nonsummer
2023-02-02 22:00 | 2023-02-02 23:00 | Winter | FALSE | nonsummer
2023-02-02 23:00 | 2023-02-03 | Winter | FALSE | nonsummer
2023-02-03 | 2023-02-03 01:00 | Winter | FALSE | nonsummer
2023-02-03 01:00 | 2023-02-03 02:00 | Winter | FALSE | nonsummer
2023-02-03 02:00 | 2023-02-03 03:00 | Winter | FALSE | nonsummer
2023-02-03 03:00 | 2023-02-03 04:00 | Winter | FALSE | nonsummer
2023-02-03 04:00 | 2023-02-03 05:00 | Winter | FALSE | nonsummer
2023-02-03 05:00 | 2023-02-03 06:00 | Winter | FALSE | nonsummer
2023-02-03 06:00 | 2023-02-03 07:00 | Winter | FALSE | nonsummer
2023-02-03 07:00 | 2023-02-03 08:00 | Winter | FALSE | nonsummer
2023-02-03 08:00 | 2023-02-03 09:00 | Winter | FALSE | nonsummer
2023-02-03 09:00 | 2023-02-03 10:00 | Winter | FALSE | nonsummer
2023-02-03 10:00 | 2023-02-03 11:00 | Winter | FALSE | nonsummer
2023-02-03 11:00 | 2023-02-03 12:00 | Winter | FALSE | nonsummer
2023-02-03 12:00 | 2023-02-03 13:00 | Winter | FALSE | nonsummer
2023-02-03 13:00 | 2023-02-03 14:00 | Winter | FALSE | nonsummer
2023-02-03 14:00 | 2023-02-03 15:00 | Winter | FALSE | nonsummer
2023-02-03 15:00 | 2023-02-03 16:00 | Winter | FALSE | nonsummer
2023-02-03 16:00 | 2023-02-03 17:00 | Winter | TRUE | nonsummer
2023-02-03 17:00 | 2023-02-03 18:00 | Winter | TRUE | nonsummer
2023-02-03 18:00 | 2023-02-03 19:00 | Winter | TRUE | nonsummer
2023-02-03 19:00 | 2023-02-03 20:00 | Winter | TRUE | nonsummer
2023-02-03 20:00 | 2023-02-03 21:00 | Winter | TRUE | nonsummer
2023-02-03 21:00 | 2023-02-03 22:00 | Winter | FALSE | nonsummer
2023-02-03 22:00 | 2023-02-03 23:00 | Winter | FALSE | nonsummer
2023-02-03 23:00 | 2023-02-04 | Winter | FALSE | nonsummer
2023-02-04 | 2023-02-04 01:00 | Winter | FALSE | nonsummer
2023-02-04 01:00 | 2023-02-04 02:00 | Winter | FALSE | nonsummer
2023-02-04 02:00 | 2023-02-04 03:00 | Winter | FALSE | nonsummer
2023-02-04 03:00 | 2023-02-04 04:00 | Winter | FALSE | nonsummer
2023-02-04 04:00 | 2023-02-04 05:00 | Winter | FALSE | nonsummer
2023-02-04 05:00 | 2023-02-04 06:00 | Winter | FALSE | nonsummer
2023-02-04 06:00 | 2023-02-04 07:00 | Winter | FALSE | nonsummer
2023-02-04 07:00 | 2023-02-04 08:00 | Winter | FALSE | nonsummer
2023-02-04 08:00 | 2023-02-04 09:00 | Winter | FALSE | nonsummer
2023-02-04 09:00 | 2023-02-04 10:00 | Winter | FALSE | nonsummer
2023-02-04 10:00 | 2023-02-04 11:00 | Winter | FALSE | nonsummer
2023-02-04 11:00 | 2023-02-04 12:00 | Winter | FALSE | nonsummer
2023-02-04 12:00 | 2023-02-04 13:00 | Winter | FALSE | nonsummer
2023-02-04 13:00 | 2023-02-04 14:00 | Winter | FALSE | nonsummer
2023-02-04 14:00 | 2023-02-04 15:00 | Winter | FALSE | nonsummer
2023-02-04 15:00 | 2023-02-04 16:00 | Winter | FALSE | nonsummer
2023-02-04 16:00 | 2023-02-04 17:00 | Winter | TRUE | nonsummer
2023-02-04 17:00 | 2023-02-04 18:00 | Winter | TRUE | nonsummer
2023-02-04 18:00 | 2023-02-04 19:00 | Winter | TRUE | nonsummer
2023-02-04 19:00 | 2023-02-04 20:00 | Winter | TRUE | nonsummer
2023-02-04 20:00 | 2023-02-04 21:00 | Winter | TRUE | nonsummer
2023-02-04 21:00 | 2023-02-04 22:00 | Winter | FALSE | nonsummer
2023-02-04 22:00 | 2023-02-04 23:00 | Winter | FALSE | nonsummer
2023-02-04 23:00 | 2023-02-05 | Winter | FALSE | nonsummer
2023-02-05 | 2023-02-05 01:00 | Winter | FALSE | nonsummer
2023-02-05 01:00 | 2023-02-05 02:00 | Winter | FALSE | nonsummer
2023-02-05 02:00 | 2023-02-05 03:00 | Winter | FALSE | nonsummer
2023-02-05 03:00 | 2023-02-05 04:00 | Winter | FALSE | nonsummer
2023-02-05 04:00 | 2023-02-05 05:00 | Winter | FALSE | nonsummer
2023-02-05 05:00 | 2023-02-05 06:00 | Winter | FALSE | nonsummer
2023-02-05 06:00 | 2023-02-05 07:00 | Winter | FALSE | nonsummer
2023-02-05 07:00 | 2023-02-05 08:00 | Winter | FALSE | nonsummer
2023-02-05 08:00 | 2023-02-05 09:00 | Winter | FALSE | nonsummer
2023-02-05 09:00 | 2023-02-05 10:00 | Winter | FALSE | nonsummer
2023-02-05 10:00 | 2023-02-05 11:00 | Winter | FALSE | nonsummer
2023-02-05 11:00 | 2023-02-05 12:00 | Winter | FALSE | nonsummer
2023-02-05 12:00 | 2023-02-05 13:00 | Winter | FALSE | nonsummer
2023-02-05 13:00 | 2023-02-05 14:00 | Winter | FALSE | nonsummer
2023-02-05 14:00 | 2023-02-05 15:00 | Winter | FALSE | nonsummer
2023-02-05 15:00 | 2023-02-05 16:00 | Winter | FALSE | nonsummer
2023-02-05 16:00 | 2023-02-05 17:00 | Winter | TRUE | nonsummer
2023-02-05 17:00 | 2023-02-05 18:00 | Winter | TRUE | nonsummer
2023-02-05 18:00 | 2023-02-05 19:00 | Winter | TRUE | nonsummer
2023-02-05 19:00 | 2023-02-05 20:00 | Winter | TRUE | nonsummer
2023-02-05 20:00 | 2023-02-05 21:00 | Winter | TRUE | nonsummer
2023-02-05 21:00 | 2023-02-05 22:00 | Winter | FALSE | nonsummer
2023-02-05 22:00 | 2023-02-05 23:00 | Winter | FALSE | nonsummer
2023-02-05 23:00 | 2023-02-06 | Winter | FALSE | nonsummer
2023-02-06 | 2023-02-06 01:00 | Winter | FALSE | nonsummer
2023-02-06 01:00 | 2023-02-06 02:00 | Winter | FALSE | nonsummer
2023-02-06 02:00 | 2023-02-06 03:00 | Winter | FALSE | nonsummer
2023-02-06 03:00 | 2023-02-06 04:00 | Winter | FALSE | nonsummer
2023-02-06 04:00 | 2023-02-06 05:00 | Winter | FALSE | nonsummer
2023-02-06 05:00 | 2023-02-06 06:00 | Winter | FALSE | nonsummer
2023-02-06 06:00 | 2023-02-06 07:00 | Winter | FALSE | nonsummer
2023-02-06 07:00 | 2023-02-06 08:00 | Winter | FALSE | nonsummer
2023-02-06 08:00 | 2023-02-06 09:00 | Winter | FALSE | nonsummer
2023-02-06 09:00 | 2023-02-06 10:00 | Winter | FALSE | nonsummer
2023-02-06 10:00 | 2023-02-06 11:00 | Winter | FALSE | nonsummer
2023-02-06 11:00 | 2023-02-06 12:00 | Winter | FALSE | nonsummer
2023-02-06 12:00 | 2023-02-06 13:00 | Winter | FALSE | nonsummer
2023-02-06 13:00 | 2023-02-06 14:00 | Winter | FALSE | nonsummer
2023-02-06 14:00 | 2023-02-06 15:00 | Winter | FALSE | nonsummer
2023-02-06 15:00 | 2023-02-06 16:00 | Winter | FALSE | nonsummer
2023-02-06 16:00 | 2023-02-06 17:00 | Winter | TRUE | nonsummer
2023-02-06 17:00 | 2023-02-06 18:00 | Winter | TRUE | nonsummer
2023-02-06 18:00 | 2023-02-06 19:00 | Winter | TRUE | nonsummer
2023-02-06 19:00 | 2023-02-06 20:00 | Winter | TRUE | nonsummer
2023-02-06 20:00 | 2023-02-06 21:00 | Winter | TRUE | nonsummer
2023-02-06 21:00 | 2023-02-06 22:00 | Winter | FALSE | nonsummer
2023-02-06 22:00 | 2023-02-06 23:00 | Winter | FALSE | nonsummer
2023-02-06 23:00 | 2023-02-07 | Winter | FALSE | nonsummer
2023-02-07 | 2023-02-07 01:00 | Winter | FALSE | nonsummer
2023-02-07 01:00 | 2023-02-07 02:00 | Winter | FALSE | nonsummer
2023-02-07 02:00 | 2023-02-07 03:00 | Winter | FALSE | nonsummer
2023-02-07 03:00 | 2023-02-07 04:00 | Winter | FALSE | nonsummer
2023-02-07 04:00 | 2023-02-07 05:00 | Winter | FALSE | nonsummer
2023-02-07 05:00 | 2023-02-07 06:00 | Winter | FALSE | nonsummer
2023-02-07 06:00 | 2023-02-07 07:00 | Winter | FALSE | nonsummer
2023-02-07 07:00 | 2023-02-07 08:00 | Winter | FALSE | nonsummer
2023-02-07 08:00 | 2023-02-07 09:00 | Winter | FALSE | nonsummer
2023-02-07 09:00 | 2023-02-07 10:00 | Winter | FALSE | nonsummer
2023-02-07 10:00 | 2023-02-07 11:00 | Winter | FALSE | nonsummer
2023-02-07 11:00 | 2023-02-07 12:00 | Winter | FALSE | nonsummer
2023-02-07 12:00 | 2023-02-07 13:00 | Winter | FALSE | nonsummer
2023-02-07 13:00 | 2023-02-07 14:00 | Winter | FALSE | nonsummer
2023-02-07 14:00 | 2023-02-07 15:00 | Winter | FALSE | nonsummer
2023-02-07 15:00 | 2023-02-07 16:00 | Winter | FALSE | nonsummer
2023-02-07 16:00 | 2023-02-07 17:00 | Winter | TRUE | nonsummer
2023-02-07 17:00 | 2023-02-07 18:00 | Winter | TRUE | nonsummer
2023-02-07 18:00 | 2023-02-07 19:00 | Winter | TRUE | nonsummer
2023-02-07 19:00 | 2023-02-07 20:00 | Winter | TRUE | nonsummer
2023-02-07 20:00 | 2023-02-07 21:00 | Winter | TRUE | nonsummer
2023-02-07 21:00 | 2023-02-07 22:00 | Winter | FALSE | nonsummer
2023-02-07 22:00 | 2023-02-07 23:00 | Winter | FALSE | nonsummer
2023-02-07 23:00 | 2023-02-08 | Winter | FALSE | nonsummer
2023-02-08 | 2023-02-08 01:00 | Winter | FALSE | nonsummer
2023-02-08 01:00 | 2023-02-08 02:00 | Winter | FALSE | nonsummer
2023-02-08 02:00 | 2023-02-08 03:00 | Winter | FALSE | nonsummer
2023-02-08 03:00 | 2023-02-08 04:00 | Winter | FALSE | nonsummer
2023-02-08 04:00 | 2023-02-08 05:00 | Winter | FALSE | nonsummer
2023-02-08 05:00 | 2023-02-08 06:00 | Winter | FALSE | nonsummer
2023-02-08 06:00 | 2023-02-08 07:00 | Winter | FALSE | nonsummer
2023-02-08 07:00 | 2023-02-08 08:00 | Winter | FALSE | nonsummer
2023-02-08 08:00 | 2023-02-08 09:00 | Winter | FALSE | nonsummer
2023-02-08 09:00 | 2023-02-08 10:00 | Winter | FALSE | nonsummer
2023-02-08 10:00 | 2023-02-08 11:00 | Winter | FALSE | nonsummer
2023-02-08 11:00 | 2023-02-08 12:00 | Winter | FALSE | nonsummer
2023-02-08 12:00 | 2023-02-08 13:00 | Winter | FALSE | nonsummer
2023-02-08 13:00 | 2023-02-08 14:00 | Winter | FALSE | nonsummer
2023-02-08 14:00 | 2023-02-08 15:00 | Winter | FALSE | nonsummer
2023-02-08 15:00 | 2023-02-08 16:00 | Winter | FALSE | nonsummer
2023-02-08 16:00 | 2023-02-08 17:00 | Winter | TRUE | nonsummer
2023-02-08 17:00 | 2023-02-08 18:00 | Winter | TRUE | nonsummer
2023-02-08 18:00 | 2023-02-08 19:00 | Winter | TRUE | nonsummer
2023-02-08 19:00 | 2023-02-08 20:00 | Winter | TRUE | nonsummer
2023-02-08 20:00 | 2023-02-08 21:00 | Winter | TRUE | nonsummer
2023-02-08 21:00 | 2023-02-08 22:00 | Winter | FALSE | nonsummer
2023-02-08 22:00 | 2023-02-08 23:00 | Winter | FALSE | nonsummer
2023-02-08 23:00 | 2023-02-09 | Winter | FALSE | nonsummer
2023-02-09 | 2023-02-09 01:00 | Winter | FALSE | nonsummer
2023-02-09 01:00 | 2023-02-09 02:00 | Winter | FALSE | nonsummer
2023-02-09 02:00 | 2023-02-09 03:00 | Winter | FALSE | nonsummer
2023-02-09 03:00 | 2023-02-09 04:00 | Winter | FALSE | nonsummer
2023-02-09 04:00 | 2023-02-09 05:00 | Winter | FALSE | nonsummer
2023-02-09 05:00 | 2023-02-09 06:00 | Winter | FALSE | nonsummer
2023-02-09 06:00 | 2023-02-09 07:00 | Winter | FALSE | nonsummer
2023-02-09 07:00 | 2023-02-09 08:00 | Winter | FALSE | nonsummer
2023-02-09 08:00 | 2023-02-09 09:00 | Winter | FALSE | nonsummer
2023-02-09 09:00 | 2023-02-09 10:00 | Winter | FALSE | nonsummer
2023-02-09 10:00 | 2023-02-09 11:00 | Winter | FALSE | nonsummer
2023-02-09 11:00 | 2023-02-09 12:00 | Winter | FALSE | nonsummer
2023-02-09 12:00 | 2023-02-09 13:00 | Winter | FALSE | nonsummer
2023-02-09 13:00 | 2023-02-09 14:00 | Winter | FALSE | nonsummer
2023-02-09 14:00 | 2023-02-09 15:00 | Winter | FALSE | nonsummer
2023-02-09 15:00 | 2023-02-09 16:00 | Winter | FALSE | nonsummer
2023-02-09 16:00 | 2023-02-09 17:00 | Winter | TRUE | nonsummer
2023-02-09 17:00 | 2023-02-09 18:00 | Winter | TRUE | nonsummer
2023-02-09 18:00 | 2023-02-09 19:00 | Winter | TRUE | nonsummer
2023-02-09 19:00 | 2023-02-09 20:00 | Winter | TRUE | nonsummer
2023-02-09 20:00 | 2023-02-09 21:00 | Winter | TRUE | nonsummer
2023-02-09 21:00 | 2023-02-09 22:00 | Winter | FALSE | nonsummer
2023-02-09 22:00 | 2023-02-09 23:00 | Winter | FALSE | nonsummer
2023-02-09 23:00 | 2023-02-10 | Winter | FALSE | nonsummer
2023-02-10 | 2023-02-10 01:00 | Winter | FALSE | nonsummer
2023-02-10 01:00 | 2023-02-10 02:00 | Winter | FALSE | nonsummer
2023-02-10 02:00 | 2023-02-10 03:00 | Winter | FALSE | nonsummer
2023-02-10 03:00 | 2023-02-10 04:00 | Winter | FALSE | nonsummer
2023-02-10 04:00 | 2023-02-10 05:00 | Winter | FALSE | nonsummer
2023-02-10 05:00 | 2023-02-10 06:00 | Winter | FALSE | nonsummer
2023-02-10 06:00 | 2023-02-10 07:00 | Winter | FALSE | nonsummer
2023-02-10 07:00 | 2023-02-10 08:00 | Winter | FALSE | nonsummer
2023-02-10 08:00 | 2023-02-10 09:00 | Winter | FALSE | nonsummer
2023-02-10 09:00 | 2023-02-10 10:00 | Winter | FALSE | nonsummer
2023-02-10 10:00 | 2023-02-10 11:00 | Winter | FALSE | nonsummer
2023-02-10 11:00 | 2023-02-10 12:00 | Winter | FALSE | nonsummer
2023-02-10 12:00 | 2023-02-10 13:00 | Winter | FALSE | nonsummer
2023-02-10 13:00 | 2023-02-10 14:00 | Winter | FALSE | nonsummer
2023-02-10 14:00 | 2023-02-10 15:00 | Winter | FALSE | nonsummer
2023-02-10 15:00 | 2023-02-10 16:00 | Winter | FALSE | nonsummer
2023-02-10 16:00 | 2023-02-10 17:00 | Winter | TRUE | nonsummer
2023-02-10 17:00 | 2023-02-10 18:00 | Winter | TRUE | nonsummer
2023-02-10 18:00 | 2023-02-10 19:00 | Winter | TRUE | nonsummer
2023-02-10 19:00 | 2023-02-10 20:00 | Winter | TRUE | nonsummer
2023-02-10 20:00 | 2023-02-10 21:00 | Winter | TRUE | nonsummer
2023-02-10 21:00 | 2023-02-10 22:00 | Winter | FALSE | nonsummer
2023-02-10 22:00 | 2023-02-10 23:00 | Winter | FALSE | nonsummer
2023-02-10 23:00 | 2023-02-11 | Winter | FALSE | nonsummer
2023-02-11 | 2023-02-11 01:00 | Winter | FALSE | nonsummer
2023-02-11 01:00 | 2023-02-11 02:00 | Winter | FALSE | nonsummer
2023-02-11 02:00 | 2023-02-11 03:00 | Winter | FALSE | nonsummer
2023-02-11 03:00 | 2023-02-11 04:00 | Winter | FALSE | nonsummer
2023-02-11 04:00 | 2023-02-11 05:00 | Winter | FALSE | nonsummer
2023-02-11 05:00 | 2023-02-11 06:00 | Winter | FALSE | nonsummer
2023-02-11 06:00 | 2023-02-11 07:00 | Winter | FALSE | nonsummer
2023-02-11 07:00 | 2023-02-11 08:00 | Winter | FALSE | nonsummer
2023-02-11 08:00 | 2023-02-11 09:00 | Winter | FALSE | nonsummer
2023-02-11 09:00 | 2023-02-11 10:00 | Winter | FALSE | nonsummer
2023-02-11 10:00 | 2023-02-11 11:00 | Winter | FALSE | nonsummer
2023-02-11 11:00 | 2023-02-11 12:00 | Winter | FALSE | nonsummer
2023-02-11 12:00 | 2023-02-11 13:00 | Winter | FALSE | nonsummer
2023-02-11 13:00 | 2023-02-11 14:00 | Winter | FALSE | nonsummer
2023-02-11 14:00 | 2023-02-11 15:00 | Winter | FALSE | nonsummer
2023-02-11 15:00 | 2023-02-11 16:00 | Winter | FALSE | nonsummer
2023-02-11 16:00 | 2023-02-11 17:00 | Winter | TRUE | nonsummer
2023-02-11 17:00 | 2023-02-11 18:00 | Winter | TRUE | nonsummer
2023-02-11 18:00 | 2023-02-11 19:00 | Winter | TRUE | nonsummer
2023-02-11 19:00 | 2023-02-11 20:00 | Winter | TRUE | nonsummer
2023-02-11 20:00 | 2023-02-11 21:00 | Winter | TRUE | nonsummer
2023-02-11 21:00 | 2023-02-11 22:00 | Winter | FALSE | nonsummer
2023-02-11 22:00 | 2023-02-11 23:00 | Winter | FALSE | nonsummer
2023-02-11 23:00 | 2023-02-12 | Winter | FALSE | nonsummer
2023-02-12 | 2023-02-12 01:00 | Winter | FALSE | nonsummer
2023-02-12 01:00 | 2023-02-12 02:00 | Winter | FALSE | nonsummer
2023-02-12 02:00 | 2023-02-12 03:00 | Winter | FALSE | nonsummer
2023-02-12 03:00 | 2023-02-12 04:00 | Winter | FALSE | nonsummer
2023-02-12 04:00 | 2023-02-12 05:00 | Winter | FALSE | nonsummer
2023-02-12 05:00 | 2023-02-12 06:00 | Winter | FALSE | nonsummer
2023-02-12 06:00 | 2023-02-12 07:00 | Winter | FALSE | nonsummer
2023-02-12 07:00 | 2023-02-12 08:00 | Winter | FALSE | nonsummer
2023-02-12 08:00 | 2023-02-12 09:00 | Winter | FALSE | nonsummer
2023-02-12 09:00 | 2023-02-12 10:00 | Winter | FALSE | nonsummer
2023-02-12 10:00 | 2023-02-12 11:00 | Winter | FALSE | nonsummer
2023-02-12 11:00 | 2023-02-12 12:00 | Winter | FALSE | nonsummer
2023-02-12 12:00 | 2023-02-12 13:00 | Winter | FALSE | nonsummer
2023-02-12 13:00 | 2023-02-12 14:00 | Winter | FALSE | nonsummer
2023-02-12 14:00 | 2023-02-12 15:00 | Winter | FALSE | nonsummer
2023-02-12 15:00 | 2023-02-12 16:00 | Winter | FALSE | nonsummer
2023-02-12 16:00 | 2023-02-12 17:00 | Winter | TRUE | nonsummer
2023-02-12 17:00 | 2023-02-12 18:00 | Winter | TRUE | nonsummer
2023-02-12 18:00 | 2023-02-12 19:00 | Winter | TRUE | nonsummer
2023-02-12 19:00 | 2023-02-12 20:00 | Winter | TRUE | nonsummer
2023-02-12 20:00 | 2023-02-12 21:00 | Winter | TRUE | nonsummer
2023-02-12 21:00 | 2023-02-12 22:00 | Winter | FALSE | nonsummer
2023-02-12 22:00 | 2023-02-12 23:00 | Winter | FALSE | nonsummer
2023-02-12 23:00 | 2023-02-13 | Winter | FALSE | nonsummer
2023-02-13 | 2023-02-13 01:00 | Winter | FALSE | nonsummer
2023-02-13 01:00 | 2023-02-13 02:00 | Winter | FALSE | nonsummer
2023-02-13 02:00 | 2023-02-13 03:00 | Winter | FALSE | nonsummer
2023-02-13 03:00 | 2023-02-13 04:00 | Winter | FALSE | nonsummer
2023-02-13 04:00 | 2023-02-13 05:00 | Winter | FALSE | nonsummer
2023-02-13 05:00 | 2023-02-13 06:00 | Winter | FALSE | nonsummer
2023-02-13 06:00 | 2023-02-13 07:00 | Winter | FALSE | nonsummer
2023-02-13 07:00 | 2023-02-13 08:00 | Winter | FALSE | nonsummer
2023-02-13 08:00 | 2023-02-13 09:00 | Winter | FALSE | nonsummer
2023-02-13 09:00 | 2023-02-13 10:00 | Winter | FALSE | nonsummer
2023-02-13 10:00 | 2023-02-13 11:00 | Winter | FALSE | nonsummer
2023-02-13 11:00 | 2023-02-13 12:00 | Winter | FALSE | nonsummer
2023-02-13 12:00 | 2023-02-13 13:00 | Winter | FALSE | nonsummer
2023-02-13 13:00 | 2023-02-13 14:00 | Winter | FALSE | nonsummer
2023-02-13 14:00 | 2023-02-13 15:00 | Winter | FALSE | nonsummer
2023-02-13 15:00 | 2023-02-13 16:00 | Winter | FALSE | nonsummer
2023-02-13 16:00 | 2023-02-13 17:00 | Winter | TRUE | nonsummer
2023-02-13 17:00 | 2023-02-13 18:00 | Winter | TRUE | nonsummer
2023-02-13 18:00 | 2023-02-13 19:00 | Winter | TRUE | nonsummer
2023-02-13 19:00 | 2023-02-13 20:00 | Winter | TRUE | nonsummer
2023-02-13 20:00 | 2023-02-13 21:00 | Winter | TRUE | nonsummer
2023-02-13 21:00 | 2023-02-13 22:00 | Winter | FALSE | nonsummer
2023-02-13 22:00 | 2023-02-13 23:00 | Winter | FALSE | nonsummer
2023-02-13 23:00 | 2023-02-14 | Winter | FALSE | nonsummer
2023-02-14 | 2023-02-14 01:00 | Winter | FALSE | nonsummer
2023-02-14 01:00 | 2023-02-14 02:00 | Winter | FALSE | nonsummer
2023-02-14 02:00 | 2023-02-14 03:00 | Winter | FALSE | nonsummer
2023-02-14 03:00 | 2023-02-14 04:00 | Winter | FALSE | nonsummer
2023-02-14 04:00 | 2023-02-14 05:00 | Winter | FALSE | nonsummer
2023-02-14 05:00 | 2023-02-14 06:00 | Winter | FALSE | nonsummer
2023-02-14 06:00 | 2023-02-14 07:00 | Winter | FALSE | nonsummer
2023-02-14 07:00 | 2023-02-14 08:00 | Winter | FALSE | nonsummer
2023-02-14 08:00 | 2023-02-14 09:00 | Winter | FALSE | nonsummer
2023-02-14 09:00 | 2023-02-14 10:00 | Winter | FALSE | nonsummer
2023-02-14 10:00 | 2023-02-14 11:00 | Winter | FALSE | nonsummer
2023-02-14 11:00 | 2023-02-14 12:00 | Winter | FALSE | nonsummer
2023-02-14 12:00 | 2023-02-14 13:00 | Winter | FALSE | nonsummer
2023-02-14 13:00 | 2023-02-14 14:00 | Winter | FALSE | nonsummer
2023-02-14 14:00 | 2023-02-14 15:00 | Winter | FALSE | nonsummer
2023-02-14 15:00 | 2023-02-14 16:00 | Winter | FALSE | nonsummer
2023-02-14 16:00 | 2023-02-14 17:00 | Winter | TRUE | nonsummer
2023-02-14 17:00 | 2023-02-14 18:00 | Winter | TRUE | nonsummer
2023-02-14 18:00 | 2023-02-14 19:00 | Winter | TRUE | nonsummer
2023-02-14 19:00 | 2023-02-14 20:00 | Winter | TRUE | nonsummer
2023-02-14 20:00 | 2023-02-14 21:00 | Winter | TRUE | nonsummer
2023-02-14 21:00 | 2023-02-14 22:00 | Winter | FALSE | nonsummer
2023-02-14 22:00 | 2023-02-14 23:00 | Winter | FALSE | nonsummer
2023-02-14 23:00 | 2023-02-15 | Winter | FALSE | nonsummer
2023-02-15 | 2023-02-15 01:00 | Winter | FALSE | nonsummer
2023-02-15 01:00 | 2023-02-15 02:00 | Winter | FALSE | nonsummer
2023-02-15 02:00 | 2023-02-15 03:00 | Winter | FALSE | nonsummer
2023-02-15 03:00 | 2023-02-15 04:00 | Winter | FALSE | nonsummer
2023-02-15 04:00 | 2023-02-15 05:00 | Winter | FALSE | nonsummer
2023-02-15 05:00 | 2023-02-15 06:00 | Winter | FALSE | nonsummer
2023-02-15 06:00 | 2023-02-15 07:00 | Winter | FALSE | nonsummer
2023-02-15 07:00 | 2023-02-15 08:00 | Winter | FALSE | nonsummer
2023-02-15 08:00 | 2023-02-15 09:00 | Winter | FALSE | nonsummer
2023-02-15 09:00 | 2023-02-15 10:00 | Winter | FALSE | nonsummer
2023-02-15 10:00 | 2023-02-15 11:00 | Winter | FALSE | nonsummer
2023-02-15 11:00 | 2023-02-15 12:00 | Winter | FALSE | nonsummer
2023-02-15 12:00 | 2023-02-15 13:00 | Winter | FALSE | nonsummer
2023-02-15 13:00 | 2023-02-15 14:00 | Winter | FALSE | nonsummer
2023-02-15 14:00 | 2023-02-15 15:00 | Winter | FALSE | nonsummer
2023-02-15 15:00 | 2023-02-15 16:00 | Winter | FALSE | nonsummer
2023-02-15 16:00 | 2023-02-15 17:00 | Winter | TRUE | nonsummer
2023-02-15 17:00 | 2023-02-15 18:00 | Winter | TRUE | nonsummer
2023-02-15 18:00 | 2023-02-15 19:00 | Winter | TRUE | nonsummer
2023-02-15 19:00 | 2023-02-15 20:00 | Winter | TRUE | nonsummer
2023-02-15 20:00 | 2023-02-15 21:00 | Winter | TRUE | nonsummer
2023-02-15 21:00 | 2023-02-15 22:00 | Winter | FALSE | nonsummer
2023-02-15 22:00 | 2023-02-15 23:00 | Winter | FALSE | nonsummer
2023-02-15 23:00 | 2023-02-16 | Winter | FALSE | nonsummer
2023-02-16 | 2023-02-16 01:00 | Winter | FALSE | nonsummer
2023-02-16 01:00 | 2023-02-16 02:00 | Winter | FALSE | nonsummer
2023-02-16 02:00 | 2023-02-16 03:00 | Winter | FALSE | nonsummer
2023-02-16 03:00 | 2023-02-16 04:00 | Winter | FALSE | nonsummer
2023-02-16 04:00 | 2023-02-16 05:00 | Winter | FALSE | nonsummer
2023-02-16 05:00 | 2023-02-16 06:00 | Winter | FALSE | nonsummer
2023-02-16 06:00 | 2023-02-16 07:00 | Winter | FALSE | nonsummer
2023-02-16 07:00 | 2023-02-16 08:00 | Winter | FALSE | nonsummer
2023-02-16 08:00 | 2023-02-16 09:00 | Winter | FALSE | nonsummer
2023-02-16 09:00 | 2023-02-16 10:00 | Winter | FALSE | nonsummer
2023-02-16 10:00 | 2023-02-16 11:00 | Winter | FALSE | nonsummer
2023-02-16 11:00 | 2023-02-16 12:00 | Winter | FALSE | nonsummer
2023-02-16 12:00 | 2023-02-16 13:00 | Winter | FALSE | nonsummer
2023-02-16 13:00 | 2023-02-16 14:00 | Winter | FALSE | nonsummer
2023-02-16 14:00 | 2023-02-16 15:00 | Winter | FALSE | nonsummer
2023-02-16 15:00 | 2023-02-16 16:00 | Winter | FALSE | nonsummer
2023-02-16 16:00 | 2023-02-16 17:00 | Winter | TRUE | nonsummer
2023-02-16 17:00 | 2023-02-16 18:00 | Winter | TRUE | nonsummer
2023-02-16 18:00 | 2023-02-16 19:00 | Winter | TRUE | nonsummer
2023-02-16 19:00 | 2023-02-16 20:00 | Winter | TRUE | nonsummer
2023-02-16 20:00 | 2023-02-16 21:00 | Winter | TRUE | nonsummer
2023-02-16 21:00 | 2023-02-16 22:00 | Winter | FALSE | nonsummer
2023-02-16 22:00 | 2023-02-16 23:00 | Winter | FALSE | nonsummer
2023-02-16 23:00 | 2023-02-17 | Winter | FALSE | nonsummer
2023-02-17 | 2023-02-17 01:00 | Winter | FALSE | nonsummer
2023-02-17 01:00 | 2023-02-17 02:00 | Winter | FALSE | nonsummer
2023-02-17 02:00 | 2023-02-17 03:00 | Winter | FALSE | nonsummer
2023-02-17 03:00 | 2023-02-17 04:00 | Winter | FALSE | nonsummer
2023-02-17 04:00 | 2023-02-17 05:00 | Winter | FALSE | nonsummer
2023-02-17 05:00 | 2023-02-17 06:00 | Winter | FALSE | nonsummer
2023-02-17 06:00 | 2023-02-17 07:00 | Winter | FALSE | nonsummer
2023-02-17 07:00 | 2023-02-17 08:00 | Winter | FALSE | nonsummer
2023-02-17 08:00 | 2023-02-17 09:00 | Winter | FALSE | nonsummer
2023-02-17 09:00 | 2023-02-17 10:00 | Winter | FALSE | nonsummer
2023-02-17 10:00 | 2023-02-17 11:00 | Winter | FALSE | nonsummer
2023-02-17 11:00 | 2023-02-17 12:00 | Winter | FALSE | nonsummer
2023-02-17 12:00 | 2023-02-17 13:00 | Winter | FALSE | nonsummer
2023-02-17 13:00 | 2023-02-17 14:00 | Winter | FALSE | nonsummer
2023-02-17 14:00 | 2023-02-17 15:00 | Winter | FALSE | nonsummer
2023-02-17 15:00 | 2023-02-17 16:00 | Winter | FALSE | nonsummer
2023-02-17 16:00 | 2023-02-17 17:00 | Winter | TRUE | nonsummer
2023-02-17 17:00 | 2023-02-17 18:00 | Winter | TRUE | nonsummer
2023-02-17 18:00 | 2023-02-17 19:00 | Winter | TRUE | nonsummer
2023-02-17 19:00 | 2023-02-17 20:00 | Winter | TRUE | nonsummer
2023-02-17 20:00 | 2023-02-17 21:00 | Winter | TRUE | nonsummer
2023-02-17 21:00 | 2023-02-17 22:00 | Winter | FALSE | nonsummer
2023-02-17 22:00 | 2023-02-17 23:00 | Winter | FALSE | nonsummer
2023-02-17 23:00 | 2023-02-18 | Winter | FALSE | nonsummer
2023-02-18 | 2023-02-18 01:00 | Winter | FALSE | nonsummer
2023-02-18 01:00 | 2023-02-18 02:00 | Winter | FALSE | nonsummer
2023-02-18 02:00 | 2023-02-18 03:00 | Winter | FALSE | nonsummer
2023-02-18 03:00 | 2023-02-18 04:00 | Winter | FALSE | nonsummer
2023-02-18 04:00 | 2023-02-18 05:00 | Winter | FALSE | nonsummer
2023-02-18 05:00 | 2023-02-18 06:00 | Winter | FALSE | nonsummer
2023-02-18 06:00 | 2023-02-18 07:00 | Winter | FALSE | nonsummer
2023-02-18 07:00 | 2023-02-18 08:00 | Winter | FALSE | nonsummer
2023-02-18 08:00 | 2023-02-18 09:00 | Winter | FALSE | nonsummer
2023-02-18 09:00 | 2023-02-18 10:00 | Winter | FALSE | nonsummer
2023-02-18 10:00 | 2023-02-18 11:00 | Winter | FALSE | nonsummer
2023-02-18 11:00 | 2023-02-18 12:00 | Winter | FALSE | nonsummer
2023-02-18 12:00 | 2023-02-18 13:00 | Winter | FALSE | nonsummer
2023-02-18 13:00 | 2023-02-18 14:00 | Winter | FALSE | nonsummer
2023-02-18 14:00 | 2023-02-18 15:00 | Winter | FALSE | nonsummer
2023-02-18 15:00 | 2023-02-18 16:00 | Winter | FALSE | nonsummer
2023-02-18 16:00 | 2023-02-18 17:00 | Winter | TRUE | nonsummer
2023-02-18 17:00 | 2023-02-18 18:00 | Winter | TRUE | nonsummer
2023-02-18 18:00 | 2023-02-18 19:00 | Winter | TRUE | nonsummer
2023-02-18 19:00 | 2023-02-18 20:00 | Winter | TRUE | nonsummer
2023-02-18 20:00 | 2023-02-18 21:00 | Winter | TRUE | nonsummer
2023-02-18 21:00 | 2023-02-18 22:00 | Winter | FALSE | nonsummer
2023-02-18 22:00 | 2023-02-18 23:00 | Winter | FALSE | nonsummer
2023-02-18 23:00 | 2023-02-19 | Winter | FALSE | nonsummer
2023-02-19 | 2023-02-19 01:00 | Winter | FALSE | nonsummer
2023-02-19 01:00 | 2023-02-19 02:00 | Winter | FALSE | nonsummer
2023-02-19 02:00 | 2023-02-19 03:00 | Winter | FALSE | nonsummer
2023-02-19 03:00 | 2023-02-19 04:00 | Winter | FALSE | nonsummer
2023-02-19 04:00 | 2023-02-19 05:00 | Winter | FALSE | nonsummer
2023-02-19 05:00 | 2023-02-19 06:00 | Winter | FALSE | nonsummer
2023-02-19 06:00 | 2023-02-19 07:00 | Winter | FALSE | nonsummer
2023-02-19 07:00 | 2023-02-19 08:00 | Winter | FALSE | nonsummer
2023-02-19 08:00 | 2023-02-19 09:00 | Winter | FALSE | nonsummer
2023-02-19 09:00 | 2023-02-19 10:00 | Winter | FALSE | nonsummer
2023-02-19 10:00 | 2023-02-19 11:00 | Winter | FALSE | nonsummer
2023-02-19 11:00 | 2023-02-19 12:00 | Winter | FALSE | nonsummer
2023-02-19 12:00 | 2023-02-19 13:00 | Winter | FALSE | nonsummer
2023-02-19 13:00 | 2023-02-19 14:00 | Winter | FALSE | nonsummer
2023-02-19 14:00 | 2023-02-19 15:00 | Winter | FALSE | nonsummer
2023-02-19 15:00 | 2023-02-19 16:00 | Winter | FALSE | nonsummer
2023-02-19 16:00 | 2023-02-19 17:00 | Winter | TRUE | nonsummer
2023-02-19 17:00 | 2023-02-19 18:00 | Winter | TRUE | nonsummer
2023-02-19 18:00 | 2023-02-19 19:00 | Winter | TRUE | nonsummer
2023-02-19 19:00 | 2023-02-19 20:00 | Winter | TRUE | nonsummer
2023-02-19 20:00 | 2023-02-19 21:00 | Winter | TRUE | nonsummer
2023-02-19 21:00 | 2023-02-19 22:00 | Winter | FALSE | nonsummer
2023-02-19 22:00 | 2023-02-19 23:00 | Winter | FALSE | nonsummer
2023-02-19 23:00 | 2023-02-20 | Winter | FALSE | nonsummer
2023-02-20 | 2023-02-20 01:00 | Winter | FALSE | nonsummer
2023-02-20 01:00 | 2023-02-20 02:00 | Winter | FALSE | nonsummer
2023-02-20 02:00 | 2023-02-20 03:00 | Winter | FALSE | nonsummer
2023-02-20 03:00 | 2023-02-20 04:00 | Winter | FALSE | nonsummer
2023-02-20 04:00 | 2023-02-20 05:00 | Winter | FALSE | nonsummer
2023-02-20 05:00 | 2023-02-20 06:00 | Winter | FALSE | nonsummer
2023-02-20 06:00 | 2023-02-20 07:00 | Winter | FALSE | nonsummer
2023-02-20 07:00 | 2023-02-20 08:00 | Winter | FALSE | nonsummer
2023-02-20 08:00 | 2023-02-20 09:00 | Winter | FALSE | nonsummer
2023-02-20 09:00 | 2023-02-20 10:00 | Winter | FALSE | nonsummer
2023-02-20 10:00 | 2023-02-20 11:00 | Winter | FALSE | nonsummer
2023-02-20 11:00 | 2023-02-20 12:00 | Winter | FALSE | nonsummer
2023-02-20 12:00 | 2023-02-20 13:00 | Winter | FALSE | nonsummer
2023-02-20 13:00 | 2023-02-20 14:00 | Winter | FALSE | nonsummer
2023-02-20 14:00 | 2023-02-20 15:00 | Winter | FALSE | nonsummer
2023-02-20 15:00 | 2023-02-20 16:00 | Winter | FALSE | nonsummer
2023-02-20 16:00 | 2023-02-20 17:00 | Winter | TRUE | nonsummer
2023-02-20 17:00 | 2023-02-20 18:00 | Winter | TRUE | nonsummer
2023-02-20 18:00 | 2023-02-20 19:00 | Winter | TRUE | nonsummer
2023-02-20 19:00 | 2023-02-20 20:00 | Winter | TRUE | nonsummer
2023-02-20 20:00 | 2023-02-20 21:00 | Winter | TRUE | nonsummer
2023-02-20 21:00 | 2023-02-20 22:00 | Winter | FALSE | nonsummer
2023-02-20 22:00 | 2023-02-20 23:00 | Winter | FALSE | nonsummer
2023-02-20 23:00 | 2023-02-21 | Winter | FALSE | nonsummer
2023-02-21 | 2023-02-21 01:00 | Winter | FALSE | nonsummer
2023-02-21 01:00 | 2023-02-21 02:00 | Winter | FALSE | nonsummer
2023-02-21 02:00 | 2023-02-21 03:00 | Winter | FALSE | nonsummer
2023-02-21 03:00 | 2023-02-21 04:00 | Winter | FALSE | nonsummer
2023-02-21 04:00 | 2023-02-21 05:00 | Winter | FALSE | nonsummer
2023-02-21 05:00 | 2023-02-21 06:00 | Winter | FALSE | nonsummer
2023-02-21 06:00 | 2023-02-21 07:00 | Winter | FALSE | nonsummer
2023-02-21 07:00 | 2023-02-21 08:00 | Winter | FALSE | nonsummer
2023-02-21 08:00 | 2023-02-21 09:00 | Winter | FALSE | nonsummer
2023-02-21 09:00 | 2023-02-21 10:00 | Winter | FALSE | nonsummer
2023-02-21 10:00 | 2023-02-21 11:00 | Winter | FALSE | nonsummer
2023-02-21 11:00 | 2023-02-21 12:00 | Winter | FALSE | nonsummer
2023-02-21 12:00 | 2023-02-21 13:00 | Winter | FALSE | nonsummer
2023-02-21 13:00 | 2023-02-21 14:00 | Winter | FALSE | nonsummer
2023-02-21 14:00 | 2023-02-21 15:00 | Winter | FALSE | nonsummer
2023-02-21 15:00 | 2023-02-21 16:00 | Winter | FALSE | nonsummer
2023-02-21 16:00 | 2023-02-21 17:00 | Winter | TRUE | nonsummer
2023-02-21 17:00 | 2023-02-21 18:00 | Winter | TRUE | nonsummer
2023-02-21 18:00 | 2023-02-21 19:00 | Winter | TRUE | nonsummer
2023-02-21 19:00 | 2023-02-21 20:00 | Winter | TRUE | nonsummer
2023-02-21 20:00 | 2023-02-21 21:00 | Winter | TRUE | nonsummer
2023-02-21 21:00 | 2023-02-21 22:00 | Winter | FALSE | nonsummer
2023-02-21 22:00 | 2023-02-21 23:00 | Winter | FALSE | nonsummer
2023-02-21 23:00 | 2023-02-22 | Winter | FALSE | nonsummer
2023-02-22 | 2023-02-22 01:00 | Winter | FALSE | nonsummer
2023-02-22 01:00 | 2023-02-22 02:00 | Winter | FALSE | nonsummer
2023-02-22 02:00 | 2023-02-22 03:00 | Winter | FALSE | nonsummer
2023-02-22 03:00 | 2023-02-22 04:00 | Winter | FALSE | nonsummer
2023-02-22 04:00 | 2023-02-22 05:00 | Winter | FALSE | nonsummer
2023-02-22 05:00 | 2023-02-22 06:00 | Winter | FALSE | nonsummer
2023-02-22 06:00 | 2023-02-22 07:00 | Winter | FALSE | nonsummer
2023-02-22 07:00 | 2023-02-22 08:00 | Winter | FALSE | nonsummer
2023-02-22 08:00 | 2023-02-22 09:00 | Winter | FALSE | nonsummer
2023-02-22 09:00 | 2023-02-22 10:00 | Winter | FALSE | nonsummer
2023-02-22 10:00 | 2023-02-22 11:00 | Winter | FALSE | nonsummer
2023-02-22 11:00 | 2023-02-22 12:00 | Winter | FALSE | nonsummer
2023-02-22 12:00 | 2023-02-22 13:00 | Winter | FALSE | nonsummer
2023-02-22 13:00 | 2023-02-22 14:00 | Winter | FALSE | nonsummer
2023-02-22 14:00 | 2023-02-22 15:00 | Winter | FALSE | nonsummer
2023-02-22 15:00 | 2023-02-22 16:00 | Winter | FALSE | nonsummer
2023-02-22 16:00 | 2023-02-22 17:00 | Winter | TRUE | nonsummer
2023-02-22 17:00 | 2023-02-22 18:00 | Winter | TRUE | nonsummer
2023-02-22 18:00 | 2023-02-22 19:00 | Winter | TRUE | nonsummer
2023-02-22 19:00 | 2023-02-22 20:00 | Winter | TRUE | nonsummer
2023-02-22 20:00 | 2023-02-22 21:00 | Winter | TRUE | nonsummer
2023-02-22 21:00 | 2023-02-22 22:00 | Winter | FALSE | nonsummer
2023-02-22 22:00 | 2023-02-22 23:00 | Winter | FALSE | nonsummer
2023-02-22 23:00 | 2023-02-23 | Winter | FALSE | nonsummer
2023-02-23 | 2023-02-23 01:00 | Winter | FALSE | nonsummer
2023-02-23 01:00 | 2023-02-23 02:00 | Winter | FALSE | nonsummer
2023-02-23 02:00 | 2023-02-23 03:00 | Winter | FALSE | nonsummer
2023-02-23 03:00 | 2023-02-23 04:00 | Winter | FALSE | nonsummer
2023-02-23 04:00 | 2023-02-23 05:00 | Winter | FALSE | nonsummer
2023-02-23 05:00 | 2023-02-23 06:00 | Winter | FALSE | nonsummer
2023-02-23 06:00 | 2023-02-23 07:00 | Winter | FALSE | nonsummer
2023-02-23 07:00 | 2023-02-23 08:00 | Winter | FALSE | nonsummer
2023-02-23 08:00 | 2023-02-23 09:00 | Winter | FALSE | nonsummer
2023-02-23 09:00 | 2023-02-23 10:00 | Winter | FALSE | nonsummer
2023-02-23 10:00 | 2023-02-23 11:00 | Winter | FALSE | nonsummer
2023-02-23 11:00 | 2023-02-23 12:00 | Winter | FALSE | nonsummer
2023-02-23 12:00 | 2023-02-23 13:00 | Winter | FALSE | nonsummer
2023-02-23 13:00 | 2023-02-23 14:00 | Winter | FALSE | nonsummer
2023-02-23 14:00 | 2023-02-23 15:00 | Winter | FALSE | nonsummer
2023-02-23 15:00 | 2023-02-23 16:00 | Winter | FALSE | nonsummer
2023-02-23 16:00 | 2023-02-23 17:00 | Winter | TRUE | nonsummer
2023-02-23 17:00 | 2023-02-23 18:00 | Winter | TRUE | nonsummer
2023-02-23 18:00 | 2023-02-23 19:00 | Winter | TRUE | nonsummer
2023-02-23 19:00 | 2023-02-23 20:00 | Winter | TRUE | nonsummer
2023-02-23 20:00 | 2023-02-23 21:00 | Winter | TRUE | nonsummer
2023-02-23 21:00 | 2023-02-23 22:00 | Winter | FALSE | nonsummer
2023-02-23 22:00 | 2023-02-23 23:00 | Winter | FALSE | nonsummer
2023-02-23 23:00 | 2023-02-24 | Winter | FALSE | nonsummer
2023-02-24 | 2023-02-24 01:00 | Winter | FALSE | nonsummer
2023-02-24 01:00 | 2023-02-24 02:00 | Winter | FALSE | nonsummer
2023-02-24 02:00 | 2023-02-24 03:00 | Winter | FALSE | nonsummer
2023-02-24 03:00 | 2023-02-24 04:00 | Winter | FALSE | nonsummer
2023-02-24 04:00 | 2023-02-24 05:00 | Winter | FALSE | nonsummer
2023-02-24 05:00 | 2023-02-24 06:00 | Winter | FALSE | nonsummer
2023-02-24 06:00 | 2023-02-24 07:00 | Winter | FALSE | nonsummer
2023-02-24 07:00 | 2023-02-24 08:00 | Winter | FALSE | nonsummer
2023-02-24 08:00 | 2023-02-24 09:00 | Winter | FALSE | nonsummer
2023-02-24 09:00 | 2023-02-24 10:00 | Winter | FALSE | nonsummer
2023-02-24 10:00 | 2023-02-24 11:00 | Winter | FALSE | nonsummer
2023-02-24 11:00 | 2023-02-24 12:00 | Winter | FALSE | nonsummer
2023-02-24 12:00 | 2023-02-24 13:00 | Winter | FALSE | nonsummer
2023-02-24 13:00 | 2023-02-24 14:00 | Winter | FALSE | nonsummer
2023-02-24 14:00 | 2023-02-24 15:00 | Winter | FALSE | nonsummer
2023-02-24 15:00 | 2023-02-24 16:00 | Winter | FALSE | nonsummer
2023-02-24 16:00 | 2023-02-24 17:00 | Winter | TRUE | nonsummer
2023-02-24 17:00 | 2023-02-24 18:00 | Winter | TRUE | nonsummer
2023-02-24 18:00 | 2023-02-24 19:00 | Winter | TRUE | nonsummer
2023-02-24 19:00 | 2023-02-24 20:00 | Winter | TRUE | nonsummer
2023-02-24 20:00 | 2023-02-24 21:00 | Winter | TRUE | nonsummer
2023-02-24 21:00 | 2023-02-24 22:00 | Winter | FALSE | nonsummer
2023-02-24 22:00 | 2023-02-24 23:00 | Winter | FALSE | nonsummer
2023-02-24 23:00 | 2023-02-25 | Winter | FALSE | nonsummer
2023-02-25 | 2023-02-25 01:00 | Winter | FALSE | nonsummer
2023-02-25 01:00 | 2023-02-25 02:00 | Winter | FALSE | nonsummer
2023-02-25 02:00 | 2023-02-25 03:00 | Winter | FALSE | nonsummer
2023-02-25 03:00 | 2023-02-25 04:00 | Winter | FALSE | nonsummer
2023-02-25 04:00 | 2023-02-25 05:00 | Winter | FALSE | nonsummer
2023-02-25 05:00 | 2023-02-25 06:00 | Winter | FALSE | nonsummer
2023-02-25 06:00 | 2023-02-25 07:00 | Winter | FALSE | nonsummer
2023-02-25 07:00 | 2023-02-25 08:00 | Winter | FALSE | nonsummer
2023-02-25 08:00 | 2023-02-25 09:00 | Winter | FALSE | nonsummer
2023-02-25 09:00 | 2023-02-25 10:00 | Winter | FALSE | nonsummer
2023-02-25 10:00 | 2023-02-25 11:00 | Winter | FALSE | nonsummer
2023-02-25 11:00 | 2023-02-25 12:00 | Winter | FALSE | nonsummer
2023-02-25 12:00 | 2023-02-25 13:00 | Winter | FALSE | nonsummer
2023-02-25 13:00 | 2023-02-25 14:00 | Winter | FALSE | nonsummer
2023-02-25 14:00 | 2023-02-25 15:00 | Winter | FALSE | nonsummer
2023-02-25 15:00 | 2023-02-25 16:00 | Winter | FALSE | nonsummer
2023-02-25 16:00 | 2023-02-25 17:00 | Winter | TRUE | nonsummer
2023-02-25 17:00 | 2023-02-25 18:00 | Winter | TRUE | nonsummer
2023-02-25 18:00 | 2023-02-25 19:00 | Winter | TRUE | nonsummer
2023-02-25 19:00 | 2023-02-25 20:00 | Winter | TRUE | nonsummer
2023-02-25 20:00 | 2023-02-25 21:00 | Winter | TRUE | nonsummer
2023-02-25 21:00 | 2023-02-25 22:00 | Winter | FALSE | nonsummer
2023-02-25 22:00 | 2023-02-25 23:00 | Winter | FALSE | nonsummer
2023-02-25 23:00 | 2023-02-26 | Winter | FALSE | nonsummer
2023-02-26 | 2023-02-26 01:00 | Winter | FALSE | nonsummer
2023-02-26 01:00 | 2023-02-26 02:00 | Winter | FALSE | nonsummer
2023-02-26 02:00 | 2023-02-26 03:00 | Winter | FALSE | nonsummer
2023-02-26 03:00 | 2023-02-26 04:00 | Winter | FALSE | nonsummer
2023-02-26 04:00 | 2023-02-26 05:00 | Winter | FALSE | nonsummer
2023-02-26 05:00 | 2023-02-26 06:00 | Winter | FALSE | nonsummer
2023-02-26 06:00 | 2023-02-26 07:00 | Winter | FALSE | nonsummer
2023-02-26 07:00 | 2023-02-26 08:00 | Winter | FALSE | nonsummer
2023-02-26 08:00 | 2023-02-26 09:00 | Winter | FALSE | nonsummer
2023-02-26 09:00 | 2023-02-26 10:00 | Winter | FALSE | nonsummer
2023-02-26 10:00 | 2023-02-26 11:00 | Winter | FALSE | nonsummer
2023-02-26 11:00 | 2023-02-26 12:00 | Winter | FALSE | nonsummer
2023-02-26 12:00 | 2023-02-26 13:00 | Winter | FALSE | nonsummer
2023-02-26 13:00 | 2023-02-26 14:00 | Winter | FALSE | nonsummer
2023-02-26 14:00 | 2023-02-26 15:00 | Winter | FALSE | nonsummer
2023-02-26 15:00 | 2023-02-26 16:00 | Winter | FALSE | nonsummer
2023-02-26 16:00 | 2023-02-26 17:00 | Winter | TRUE | nonsummer
2023-02-26 17:00 | 2023-02-26 18:00 | Winter | TRUE | nonsummer
2023-02-26 18:00 | 2023-02-26 19:00 | Winter | TRUE | nonsummer
2023-02-26 19:00 | 2023-02-26 20:00 | Winter | TRUE | nonsummer
2023-02-26 20:00 | 2023-02-26 21:00 | Winter | TRUE | nonsummer
2023-02-26 21:00 | 2023-02-26 22:00 | Winter | FALSE | nonsummer
2023-02-26 22:00 | 2023-02-26 23:00 | Winter | FALSE | nonsummer
2023-02-26 23:00 | 2023-02-27 | Winter | FALSE | nonsummer
2023-02-27 | 2023-02-27 01:00 | Winter | FALSE | nonsummer
2023-02-27 01:00 | 2023-02-27 02:00 | Winter | FALSE | nonsummer
2023-02-27 02:00 | 2023-02-27 03:00 | Winter | FALSE | nonsummer
2023-02-27 03:00 | 2023-02-27 04:00 | Winter | FALSE | nonsummer
2023-02-27 04:00 | 2023-02-27 05:00 | Winter | FALSE | nonsummer
2023-02-27 05:00 | 2023-02-27 06:00 | Winter | FALSE | nonsummer
2023-02-27 06:00 | 2023-02-27 07:00 | Winter | FALSE | nonsummer
2023-02-27 07:00 | 2023-02-27 08:00 | Winter | FALSE | nonsummer
2023-02-27 08:00 | 2023-02-27 09:00 | Winter | FALSE | nonsummer
2023-02-27 09:00 | 2023-02-27 10:00 | Winter | FALSE | nonsummer
2023-02-27 10:00 | 2023-02-27 11:00 | Winter | FALSE | nonsummer
2023-02-27 11:00 | 2023-02-27 12:00 | Winter | FALSE | nonsummer
2023-02-27 12:00 | 2023-02-27 13:00 | Winter | FALSE | nonsummer
2023-02-27 13:00 | 2023-02-27 14:00 | Winter | FALSE | nonsummer
2023-02-27 14:00 | 2023-02-27 15:00 | Winter | FALSE | nonsummer
2023-02-27 15:00 | 2023-02-27 16:00 | Winter | FALSE | nonsummer
2023-02-27 16:00 | 2023-02-27 17:00 | Winter | TRUE | nonsummer
2023-02-27 17:00 | 2023-02-27 18:00 | Winter | TRUE | nonsummer
2023-02-27 18:00 | 2023-02-27 19:00 | Winter | TRUE | nonsummer
2023-02-27 19:00 | 2023-02-27 20:00 | Winter | TRUE | nonsummer
2023-02-27 20:00 | 2023-02-27 21:00 | Winter | TRUE | nonsummer
2023-02-27 21:00 | 2023-02-27 22:00 | Winter | FALSE | nonsummer
2023-02-27 22:00 | 2023-02-27 23:00 | Winter | FALSE | nonsummer
2023-02-27 23:00 | 2023-02-28 | Winter | FALSE | nonsummer
2023-02-28 | 2023-02-28 01:00 | Winter | FALSE | nonsummer
2023-02-28 01:00 | 2023-02-28 02:00 | Winter | FALSE | nonsummer
2023-02-28 02:00 | 2023-02-28 03:00 | Winter | FALSE | nonsummer
2023-02-28 03:00 | 2023-02-28 04:00 | Winter | FALSE | nonsummer
2023-02-28 04:00 | 2023-02-28 05:00 | Winter | FALSE | nonsummer
2023-02-28 05:00 | 2023-02-28 06:00 | Winter | FALSE | nonsummer
2023-02-28 06:00 | 2023-02-28 07:00 | Winter | FALSE | nonsummer
2023-02-28 07:00 | 2023-02-28 08:00 | Winter | FALSE | nonsummer
2023-02-28 08:00 | 2023-02-28 09:00 | Winter | FALSE | nonsummer
2023-02-28 09:00 | 2023-02-28 10:00 | Winter | FALSE | nonsummer
2023-02-28 10:00 | 2023-02-28 11:00 | Winter | FALSE | nonsummer
2023-02-28 11:00 | 2023-02-28 12:00 | Winter | FALSE | nonsummer
2023-02-28 12:00 | 2023-02-28 13:00 | Winter | FALSE | nonsummer
2023-02-28 13:00 | 2023-02-28 14:00 | Winter | FALSE | nonsummer
2023-02-28 14:00 | 2023-02-28 15:00 | Winter | FALSE | nonsummer
2023-02-28 15:00 | 2023-02-28 16:00 | Winter | FALSE | nonsummer
2023-02-28 16:00 | 2023-02-28 17:00 | Winter | TRUE | nonsummer
2023-02-28 17:00 | 2023-02-28 18:00 | Winter | TRUE | nonsummer
2023-02-28 18:00 | 2023-02-28 19:00 | Winter | TRUE | nonsummer
2023-02-28 19:00 | 2023-02-28 20:00 | Winter | TRUE | nonsummer
2023-02-28 20:00 | 2023-02-28 21:00 | Winter | TRUE | nonsummer
2023-02-28 21:00 | 2023-02-28 22:00 | Winter | FALSE | nonsummer
2023-02-28 22:00 | 2023-02-28 23:00 | Winter | FALSE | nonsummer
2023-02-28 23:00 | 2023-03-01 | Winter | FALSE | nonsummer
2023-03-01 | 2023-03-01 01:00 | Spring | FALSE | nonsummer
2023-03-01 01:00 | 2023-03-01 02:00 | Spring | FALSE | nonsummer
2023-03-01 02:00 | 2023-03-01 03:00 | Spring | FALSE | nonsummer
2023-03-01 03:00 | 2023-03-01 04:00 | Spring | FALSE | nonsummer
2023-03-01 04:00 | 2023-03-01 05:00 | Spring | FALSE | nonsummer
2023-03-01 05:00 | 2023-03-01 06:00 | Spring | FALSE | nonsummer
2023-03-01 06:00 | 2023-03-01 07:00 | Spring | FALSE | nonsummer
2023-03-01 07:00 | 2023-03-01 08:00 | Spring | FALSE | nonsummer
2023-03-01 08:00 | 2023-03-01 09:00 | Spring | FALSE | nonsummer
2023-03-01 09:00 | 2023-03-01 10:00 | Spring | FALSE | nonsummer
2023-03-01 10:00 | 2023-03-01 11:00 | Spring | FALSE | nonsummer
2023-03-01 11:00 | 2023-03-01 12:00 | Spring | FALSE | nonsummer
2023-03-01 12:00 | 2023-03-01 13:00 | Spring | FALSE | nonsummer
2023-03-01 13:00 | 2023-03-01 14:00 | Spring | FALSE | nonsummer
2023-03-01 14:00 | 2023-03-01 15:00 | Spring | FALSE | nonsummer
2023-03-01 15:00 | 2023-03-01 16:00 | Spring | FALSE | nonsummer
2023-03-01 16:00 | 2023-03-01 17:00 | Spring | FALSE | nonsummer
2023-03-01 17:00 | 2023-03-01 18:00 | Spring | TRUE | nonsummer
2023-03-01 18:00 | 2023-03-01 19:00 | Spring | TRUE | nonsummer
2023-03-01 19:00 | 2023-03-01 20:00 | Spring | TRUE | nonsummer
2023-03-01 20:00 | 2023-03-01 21:00 | Spring | TRUE | nonsummer
2023-03-01 21:00 | 2023-03-01 22:00 | Spring | TRUE | nonsummer
2023-03-01 22:00 | 2023-03-01 23:00 | Spring | FALSE | nonsummer
2023-03-01 23:00 | 2023-03-02 | Spring | FALSE | nonsummer
2023-03-02 | 2023-03-02 01:00 | Spring | FALSE | nonsummer
2023-03-02 01:00 | 2023-03-02 02:00 | Spring | FALSE | nonsummer
2023-03-02 02:00 | 2023-03-02 03:00 | Spring | FALSE | nonsummer
2023-03-02 03:00 | 2023-03-02 04:00 | Spring | FALSE | nonsummer
2023-03-02 04:00 | 2023-03-02 05:00 | Spring | FALSE | nonsummer
2023-03-02 05:00 | 2023-03-02 06:00 | Spring | FALSE | nonsummer
2023-03-02 06:00 | 2023-03-02 07:00 | Spring | FALSE | nonsummer
2023-03-02 07:00 | 2023-03-02 08:00 | Spring | FALSE | nonsummer
2023-03-02 08:00 | 2023-03-02 09:00 | Spring | FALSE | nonsummer
2023-03-02 09:00 | 2023-03-02 10:00 | Spring | FALSE | nonsummer
2023-03-02 10:00 | 2023-03-02 11:00 | Spring | FALSE | nonsummer
2023-03-02 11:00 | 2023-03-02 12:00 | Spring | FALSE | nonsummer
2023-03-02 12:00 | 2023-03-02 13:00 | Spring | FALSE | nonsummer
2023-03-02 13:00 | 2023-03-02 14:00 | Spring | FALSE | nonsummer
2023-03-02 14:00 | 2023-03-02 15:00 | Spring | FALSE | nonsummer
2023-03-02 15:00 | 2023-03-02 16:00 | Spring | FALSE | nonsummer
2023-03-02 16:00 | 2023-03-02 17:00 | Spring | FALSE | nonsummer
2023-03-02 17:00 | 2023-03-02 18:00 | Spring | TRUE | nonsummer
2023-03-02 18:00 | 2023-03-02 19:00 | Spring | TRUE | nonsummer
2023-03-02 19:00 | 2023-03-02 20:00 | Spring | TRUE | nonsummer
2023-03-02 20:00 | 2023-03-02 21:00 | Spring | TRUE | nonsummer
2023-03-02 21:00 | 2023-03-02 22:00 | Spring | TRUE | nonsummer
2023-03-02 22:00 | 2023-03-02 23:00 | Spring | FALSE | nonsummer
2023-03-02 23:00 | 2023-03-03 | Spring | FALSE | nonsummer
2023-03-03 | 2023-03-03 01:00 | Spring | FALSE | nonsummer
2023-03-03 01:00 | 2023-03-03 02:00 | Spring | FALSE | nonsummer
2023-03-03 02:00 | 2023-03-03 03:00 | Spring | FALSE | nonsummer
2023-03-03 03:00 | 2023-03-03 04:00 | Spring | FALSE | nonsummer
2023-03-03 04:00 | 2023-03-03 05:00 | Spring | FALSE | nonsummer
2023-03-03 05:00 | 2023-03-03 06:00 | Spring | FALSE | nonsummer
2023-03-03 06:00 | 2023-03-03 07:00 | Spring | FALSE | nonsummer
2023-03-03 07:00 | 2023-03-03 08:00 | Spring | FALSE | nonsummer
2023-03-03 08:00 | 2023-03-03 09:00 | Spring | FALSE | nonsummer
2023-03-03 09:00 | 2023-03-03 10:00 | Spring | FALSE | nonsummer
2023-03-03 10:00 | 2023-03-03 11:00 | Spring | FALSE | nonsummer
2023-03-03 11:00 | 2023-03-03 12:00 | Spring | FALSE | nonsummer
2023-03-03 12:00 | 2023-03-03 13:00 | Spring | FALSE | nonsummer
2023-03-03 13:00 | 2023-03-03 14:00 | Spring | FALSE | nonsummer
2023-03-03 14:00 | 2023-03-03 15:00 | Spring | FALSE | nonsummer
2023-03-03 15:00 | 2023-03-03 16:00 | Spring | FALSE | nonsummer
2023-03-03 16:00 | 2023-03-03 17:00 | Spring | FALSE | nonsummer
2023-03-03 17:00 | 2023-03-03 18:00 | Spring | TRUE | nonsummer
2023-03-03 18:00 | 2023-03-03 19:00 | Spring | TRUE | nonsummer
2023-03-03 19:00 | 2023-03-03 20:00 | Spring | TRUE | nonsummer
2023-03-03 20:00 | 2023-03-03 21:00 | Spring | TRUE | nonsummer
2023-03-03 21:00 | 2023-03-03 22:00 | Spring | TRUE | nonsummer
2023-03-03 22:00 | 2023-03-03 23:00 | Spring | FALSE | nonsummer
2023-03-03 23:00 | 2023-03-04 | Spring | FALSE | nonsummer
2023-03-04 | 2023-03-04 01:00 | Spring | FALSE | nonsummer
2023-03-04 01:00 | 2023-03-04 02:00 | Spring | FALSE | nonsummer
2023-03-04 02:00 | 2023-03-04 03:00 | Spring | FALSE | nonsummer
2023-03-04 03:00 | 2023-03-04 04:00 | Spring | FALSE | nonsummer
2023-03-04 04:00 | 2023-03-04 05:00 | Spring | FALSE | nonsummer
2023-03-04 05:00 | 2023-03-04 06:00 | Spring | FALSE | nonsummer
2023-03-04 06:00 | 2023-03-04 07:00 | Spring | FALSE | nonsummer
2023-03-04 07:00 | 2023-03-04 08:00 | Spring | FALSE | nonsummer
2023-03-04 08:00 | 2023-03-04 09:00 | Spring | FALSE | nonsummer
2023-03-04 09:00 | 2023-03-04 10:00 | Spring | FALSE | nonsummer
2023-03-04 10:00 | 2023-03-04 11:00 | Spring | FALSE | nonsummer
2023-03-04 11:00 | 2023-03-04 12:00 | Spring | FALSE | nonsummer
2023-03-04 12:00 | 2023-03-04 13:00 | Spring | FALSE | nonsummer
2023-03-04 13:00 | 2023-03-04 14:00 | Spring | FALSE | nonsummer
2023-03-04 14:00 | 2023-03-04 15:00 | Spring | FALSE | nonsummer
2023-03-04 15:00 | 2023-03-04 16:00 | Spring | FALSE | nonsummer
2023-03-04 16:00 | 2023-03-04 17:00 | Spring | FALSE | nonsummer
2023-03-04 17:00 | 2023-03-04 18:00 | Spring | TRUE | nonsummer
2023-03-04 18:00 | 2023-03-04 19:00 | Spring | TRUE | nonsummer
2023-03-04 19:00 | 2023-03-04 20:00 | Spring | TRUE | nonsummer
2023-03-04 20:00 | 2023-03-04 21:00 | Spring | TRUE | nonsummer
2023-03-04 21:00 | 2023-03-04 22:00 | Spring | TRUE | nonsummer
2023-03-04 22:00 | 2023-03-04 23:00 | Spring | FALSE | nonsummer
2023-03-04 23:00 | 2023-03-05 | Spring | FALSE | nonsummer
2023-03-05 | 2023-03-05 01:00 | Spring | FALSE | nonsummer
2023-03-05 01:00 | 2023-03-05 02:00 | Spring | FALSE | nonsummer
2023-03-05 02:00 | 2023-03-05 03:00 | Spring | FALSE | nonsummer
2023-03-05 03:00 | 2023-03-05 04:00 | Spring | FALSE | nonsummer
2023-03-05 04:00 | 2023-03-05 05:00 | Spring | FALSE | nonsummer
2023-03-05 05:00 | 2023-03-05 06:00 | Spring | FALSE | nonsummer
2023-03-05 06:00 | 2023-03-05 07:00 | Spring | FALSE | nonsummer
2023-03-05 07:00 | 2023-03-05 08:00 | Spring | FALSE | nonsummer
2023-03-05 08:00 | 2023-03-05 09:00 | Spring | FALSE | nonsummer
2023-03-05 09:00 | 2023-03-05 10:00 | Spring | FALSE | nonsummer
2023-03-05 10:00 | 2023-03-05 11:00 | Spring | FALSE | nonsummer
2023-03-05 11:00 | 2023-03-05 12:00 | Spring | FALSE | nonsummer
2023-03-05 12:00 | 2023-03-05 13:00 | Spring | FALSE | nonsummer
2023-03-05 13:00 | 2023-03-05 14:00 | Spring | FALSE | nonsummer
2023-03-05 14:00 | 2023-03-05 15:00 | Spring | FALSE | nonsummer
2023-03-05 15:00 | 2023-03-05 16:00 | Spring | FALSE | nonsummer
2023-03-05 16:00 | 2023-03-05 17:00 | Spring | FALSE | nonsummer
2023-03-05 17:00 | 2023-03-05 18:00 | Spring | TRUE | nonsummer
2023-03-05 18:00 | 2023-03-05 19:00 | Spring | TRUE | nonsummer
2023-03-05 19:00 | 2023-03-05 20:00 | Spring | TRUE | nonsummer
2023-03-05 20:00 | 2023-03-05 21:00 | Spring | TRUE | nonsummer
2023-03-05 21:00 | 2023-03-05 22:00 | Spring | TRUE | nonsummer
2023-03-05 22:00 | 2023-03-05 23:00 | Spring | FALSE | nonsummer
2023-03-05 23:00 | 2023-03-06 | Spring | FALSE | nonsummer
2023-03-06 | 2023-03-06 01:00 | Spring | FALSE | nonsummer
2023-03-06 01:00 | 2023-03-06 02:00 | Spring | FALSE | nonsummer
2023-03-06 02:00 | 2023-03-06 03:00 | Spring | FALSE | nonsummer
2023-03-06 03:00 | 2023-03-06 04:00 | Spring | FALSE | nonsummer
2023-03-06 04:00 | 2023-03-06 05:00 | Spring | FALSE | nonsummer
2023-03-06 05:00 | 2023-03-06 06:00 | Spring | FALSE | nonsummer
2023-03-06 06:00 | 2023-03-06 07:00 | Spring | FALSE | nonsummer
2023-03-06 07:00 | 2023-03-06 08:00 | Spring | FALSE | nonsummer
2023-03-06 08:00 | 2023-03-06 09:00 | Spring | FALSE | nonsummer
2023-03-06 09:00 | 2023-03-06 10:00 | Spring | FALSE | nonsummer
2023-03-06 10:00 | 2023-03-06 11:00 | Spring | FALSE | nonsummer
2023-03-06 11:00 | 2023-03-06 12:00 | Spring | FALSE | nonsummer
2023-03-06 12:00 | 2023-03-06 13:00 | Spring | FALSE | nonsummer
2023-03-06 13:00 | 2023-03-06 14:00 | Spring | FALSE | nonsummer
2023-03-06 14:00 | 2023-03-06 15:00 | Spring | FALSE | nonsummer
2023-03-06 15:00 | 2023-03-06 16:00 | Spring | FALSE | nonsummer
2023-03-06 16:00 | 2023-03-06 17:00 | Spring | FALSE | nonsummer
2023-03-06 17:00 | 2023-03-06 18:00 | Spring | TRUE | nonsummer
2023-03-06 18:00 | 2023-03-06 19:00 | Spring | TRUE | nonsummer
2023-03-06 19:00 | 2023-03-06 20:00 | Spring | TRUE | nonsummer
2023-03-06 20:00 | 2023-03-06 21:00 | Spring | TRUE | nonsummer
2023-03-06 21:00 | 2023-03-06 22:00 | Spring | TRUE | nonsummer
2023-03-06 22:00 | 2023-03-06 23:00 | Spring | FALSE | nonsummer
2023-03-06 23:00 | 2023-03-07 | Spring | FALSE | nonsummer
2023-03-07 | 2023-03-07 01:00 | Spring | FALSE | nonsummer
2023-03-07 01:00 | 2023-03-07 02:00 | Spring | FALSE | nonsummer
2023-03-07 02:00 | 2023-03-07 03:00 | Spring | FALSE | nonsummer
2023-03-07 03:00 | 2023-03-07 04:00 | Spring | FALSE | nonsummer
2023-03-07 04:00 | 2023-03-07 05:00 | Spring | FALSE | nonsummer
2023-03-07 05:00 | 2023-03-07 06:00 | Spring | FALSE | nonsummer
2023-03-07 06:00 | 2023-03-07 07:00 | Spring | FALSE | nonsummer
2023-03-07 07:00 | 2023-03-07 08:00 | Spring | FALSE | nonsummer
2023-03-07 08:00 | 2023-03-07 09:00 | Spring | FALSE | nonsummer
2023-03-07 09:00 | 2023-03-07 10:00 | Spring | FALSE | nonsummer
2023-03-07 10:00 | 2023-03-07 11:00 | Spring | FALSE | nonsummer
2023-03-07 11:00 | 2023-03-07 12:00 | Spring | FALSE | nonsummer
2023-03-07 12:00 | 2023-03-07 13:00 | Spring | FALSE | nonsummer
2023-03-07 13:00 | 2023-03-07 14:00 | Spring | FALSE | nonsummer
2023-03-07 14:00 | 2023-03-07 15:00 | Spring | FALSE | nonsummer
2023-03-07 15:00 | 2023-03-07 16:00 | Spring | FALSE | nonsummer
2023-03-07 16:00 | 2023-03-07 17:00 | Spring | FALSE | nonsummer
2023-03-07 17:00 | 2023-03-07 18:00 | Spring | TRUE | nonsummer
2023-03-07 18:00 | 2023-03-07 19:00 | Spring | TRUE | nonsummer
2023-03-07 19:00 | 2023-03-07 20:00 | Spring | TRUE | nonsummer
2023-03-07 20:00 | 2023-03-07 21:00 | Spring | TRUE | nonsummer
2023-03-07 21:00 | 2023-03-07 22:00 | Spring | TRUE | nonsummer
2023-03-07 22:00 | 2023-03-07 23:00 | Spring | FALSE | nonsummer
2023-03-07 23:00 | 2023-03-08 | Spring | FALSE | nonsummer
2023-03-08 | 2023-03-08 01:00 | Spring | FALSE | nonsummer
2023-03-08 01:00 | 2023-03-08 02:00 | Spring | FALSE | nonsummer
2023-03-08 02:00 | 2023-03-08 03:00 | Spring | FALSE | nonsummer
2023-03-08 03:00 | 2023-03-08 04:00 | Spring | FALSE | nonsummer
2023-03-08 04:00 | 2023-03-08 05:00 | Spring | FALSE | nonsummer
2023-03-08 05:00 | 2023-03-08 06:00 | Spring | FALSE | nonsummer
2023-03-08 06:00 | 2023-03-08 07:00 | Spring | FALSE | nonsummer
2023-03-08 07:00 | 2023-03-08 08:00 | Spring | FALSE | nonsummer
2023-03-08 08:00 | 2023-03-08 09:00 | Spring | FALSE | nonsummer
2023-03-08 09:00 | 2023-03-08 10:00 | Spring | FALSE | nonsummer
2023-03-08 10:00 | 2023-03-08 11:00 | Spring | FALSE | nonsummer
2023-03-08 11:00 | 2023-03-08 12:00 | Spring | FALSE | nonsummer
2023-03-08 12:00 | 2023-03-08 13:00 | Spring | FALSE | nonsummer
2023-03-08 13:00 | 2023-03-08 14:00 | Spring | FALSE | nonsummer
2023-03-08 14:00 | 2023-03-08 15:00 | Spring | FALSE | nonsummer
2023-03-08 15:00 | 2023-03-08 16:00 | Spring | FALSE | nonsummer
2023-03-08 16:00 | 2023-03-08 17:00 | Spring | FALSE | nonsummer
2023-03-08 17:00 | 2023-03-08 18:00 | Spring | TRUE | nonsummer
2023-03-08 18:00 | 2023-03-08 19:00 | Spring | TRUE | nonsummer
2023-03-08 19:00 | 2023-03-08 20:00 | Spring | TRUE | nonsummer
2023-03-08 20:00 | 2023-03-08 21:00 | Spring | TRUE | nonsummer
2023-03-08 21:00 | 2023-03-08 22:00 | Spring | TRUE | nonsummer
2023-03-08 22:00 | 2023-03-08 23:00 | Spring | FALSE | nonsummer
2023-03-08 23:00 | 2023-03-09 | Spring | FALSE | nonsummer
2023-03-09 | 2023-03-09 01:00 | Spring | FALSE | nonsummer
2023-03-09 01:00 | 2023-03-09 02:00 | Spring | FALSE | nonsummer
2023-03-09 02:00 | 2023-03-09 03:00 | Spring | FALSE | nonsummer
2023-03-09 03:00 | 2023-03-09 04:00 | Spring | FALSE | nonsummer
2023-03-09 04:00 | 2023-03-09 05:00 | Spring | FALSE | nonsummer
2023-03-09 05:00 | 2023-03-09 06:00 | Spring | FALSE | nonsummer
2023-03-09 06:00 | 2023-03-09 07:00 | Spring | FALSE | nonsummer
2023-03-09 07:00 | 2023-03-09 08:00 | Spring | FALSE | nonsummer
2023-03-09 08:00 | 2023-03-09 09:00 | Spring | FALSE | nonsummer
2023-03-09 09:00 | 2023-03-09 10:00 | Spring | FALSE | nonsummer
2023-03-09 10:00 | 2023-03-09 11:00 | Spring | FALSE | nonsummer
2023-03-09 11:00 | 2023-03-09 12:00 | Spring | FALSE | nonsummer
2023-03-09 12:00 | 2023-03-09 13:00 | Spring | FALSE | nonsummer
2023-03-09 13:00 | 2023-03-09 14:00 | Spring | FALSE | nonsummer
2023-03-09 14:00 | 2023-03-09 15:00 | Spring | FALSE | nonsummer
2023-03-09 15:00 | 2023-03-09 16:00 | Spring | FALSE | nonsummer
2023-03-09 16:00 | 2023-03-09 17:00 | Spring | FALSE | nonsummer
2023-03-09 17:00 | 2023-03-09 18:00 | Spring | TRUE | nonsummer
2023-03-09 18:00 | 2023-03-09 19:00 | Spring | TRUE | nonsummer
2023-03-09 19:00 | 2023-03-09 20:00 | Spring | TRUE | nonsummer
2023-03-09 20:00 | 2023-03-09 21:00 | Spring | TRUE | nonsummer
2023-03-09 21:00 | 2023-03-09 22:00 | Spring | TRUE | nonsummer
2023-03-09 22:00 | 2023-03-09 23:00 | Spring | FALSE | nonsummer
2023-03-09 23:00 | 2023-03-10 | Spring | FALSE | nonsummer
2023-03-10 | 2023-03-10 01:00 | Spring | FALSE | nonsummer
2023-03-10 01:00 | 2023-03-10 02:00 | Spring | FALSE | nonsummer
2023-03-10 02:00 | 2023-03-10 03:00 | Spring | FALSE | nonsummer
2023-03-10 03:00 | 2023-03-10 04:00 | Spring | FALSE | nonsummer
2023-03-10 04:00 | 2023-03-10 05:00 | Spring | FALSE | nonsummer
2023-03-10 05:00 | 2023-03-10 06:00 | Spring | FALSE | nonsummer
2023-03-10 06:00 | 2023-03-10 07:00 | Spring | FALSE | nonsummer
2023-03-10 07:00 | 2023-03-10 08:00 | Spring | FALSE | nonsummer
2023-03-10 08:00 | 2023-03-10 09:00 | Spring | FALSE | nonsummer
2023-03-10 09:00 | 2023-03-10 10:00 | Spring | FALSE | nonsummer
2023-03-10 10:00 | 2023-03-10 11:00 | Spring | FALSE | nonsummer
2023-03-10 11:00 | 2023-03-10 12:00 | Spring | FALSE | nonsummer
2023-03-10 12:00 | 2023-03-10 13:00 | Spring | FALSE | nonsummer
2023-03-10 13:00 | 2023-03-10 14:00 | Spring | FALSE | nonsummer
2023-03-10 14:00 | 2023-03-10 15:00 | Spring | FALSE | nonsummer
2023-03-10 15:00 | 2023-03-10 16:00 | Spring | FALSE | nonsummer
2023-03-10 16:00 | 2023-03-10 17:00 | Spring | FALSE | nonsummer
2023-03-10 17:00 | 2023-03-10 18:00 | Spring | TRUE | nonsummer
2023-03-10 18:00 | 2023-03-10 19:00 | Spring | TRUE | nonsummer
2023-03-10 19:00 | 2023-03-10 20:00 | Spring | TRUE | nonsummer
2023-03-10 20:00 | 2023-03-10 21:00 | Spring | TRUE | nonsummer
2023-03-10 21:00 | 2023-03-10 22:00 | Spring | TRUE | nonsummer
2023-03-10 22:00 | 2023-03-10 23:00 | Spring | FALSE | nonsummer
2023-03-10 23:00 | 2023-03-11 | Spring | FALSE | nonsummer
2023-03-11 | 2023-03-11 01:00 | Spring | FALSE | nonsummer
2023-03-11 01:00 | 2023-03-11 02:00 | Spring | FALSE | nonsummer
2023-03-11 02:00 | 2023-03-11 03:00 | Spring | FALSE | nonsummer
2023-03-11 03:00 | 2023-03-11 04:00 | Spring | FALSE | nonsummer
2023-03-11 04:00 | 2023-03-11 05:00 | Spring | FALSE | nonsummer
2023-03-11 05:00 | 2023-03-11 06:00 | Spring | FALSE | nonsummer
2023-03-11 06:00 | 2023-03-11 07:00 | Spring | FALSE | nonsummer
2023-03-11 07:00 | 2023-03-11 08:00 | Spring | FALSE | nonsummer
2023-03-11 08:00 | 2023-03-11 09:00 | Spring | FALSE | nonsummer
2023-03-11 09:00 | 2023-03-11 10:00 | Spring | FALSE | nonsummer
2023-03-11 10:00 | 2023-03-11 11:00 | Spring | FALSE | nonsummer
2023-03-11 11:00 | 2023-03-11 12:00 | Spring | FALSE | nonsummer
2023-03-11 12:00 | 2023-03-11 13:00 | Spring | FALSE | nonsummer
2023-03-11 13:00 | 2023-03-11 14:00 | Spring | FALSE | nonsummer
2023-03-11 14:00 | 2023-03-11 15:00 | Spring | FALSE | nonsummer
2023-03-11 15:00 | 2023-03-11 16:00 | Spring | FALSE | nonsummer
2023-03-11 16:00 | 2023-03-11 17:00 | Spring | FALSE | nonsummer
2023-03-11 17:00 | 2023-03-11 18:00 | Spring | TRUE | nonsummer
2023-03-11 18:00 | 2023-03-11 19:00 | Spring | TRUE | nonsummer
2023-03-11 19:00 | 2023-03-11 20:00 | Spring | TRUE | nonsummer
2023-03-11 20:00 | 2023-03-11 21:00 | Spring | TRUE | nonsummer
2023-03-11 21:00 | 2023-03-11 22:00 | Spring | TRUE | nonsummer
2023-03-11 22:00 | 2023-03-11 23:00 | Spring | FALSE | nonsummer
2023-03-11 23:00 | 2023-03-12 | Spring | FALSE | nonsummer
2023-03-12 | 2023-03-12 01:00 | Spring | FALSE | nonsummer
2023-03-12 01:00 | 2023-03-12 02:00 | Spring | FALSE | nonsummer
2023-03-12 02:00 | 2023-03-12 03:00 | Spring | FALSE | nonsummer
2023-03-12 03:00 | 2023-03-12 04:00 | Spring | FALSE | nonsummer
2023-03-12 04:00 | 2023-03-12 05:00 | Spring | FALSE | nonsummer
2023-03-12 05:00 | 2023-03-12 06:00 | Spring | FALSE | nonsummer
2023-03-12 06:00 | 2023-03-12 07:00 | Spring | FALSE | nonsummer
2023-03-12 07:00 | 2023-03-12 08:00 | Spring | FALSE | nonsummer
2023-03-12 08:00 | 2023-03-12 09:00 | Spring | FALSE | nonsummer
2023-03-12 09:00 | 2023-03-12 10:00 | Spring | FALSE | nonsummer
2023-03-12 10:00 | 2023-03-12 11:00 | Spring | FALSE | nonsummer
2023-03-12 11:00 | 2023-03-12 12:00 | Spring | FALSE | nonsummer
2023-03-12 12:00 | 2023-03-12 13:00 | Spring | FALSE | nonsummer
2023-03-12 13:00 | 2023-03-12 14:00 | Spring | FALSE | nonsummer
2023-03-12 14:00 | 2023-03-12 15:00 | Spring | FALSE | nonsummer
2023-03-12 15:00 | 2023-03-12 16:00 | Spring | FALSE | nonsummer
2023-03-12 16:00 | 2023-03-12 17:00 | Spring | FALSE | nonsummer
2023-03-12 17:00 | 2023-03-12 18:00 | Spring | TRUE | nonsummer
2023-03-12 18:00 | 2023-03-12 19:00 | Spring | TRUE | nonsummer
2023-03-12 19:00 | 2023-03-12 20:00 | Spring | TRUE | nonsummer
2023-03-12 20:00 | 2023-03-12 21:00 | Spring | TRUE | nonsummer
2023-03-12 21:00 | 2023-03-12 22:00 | Spring | TRUE | nonsummer
2023-03-12 22:00 | 2023-03-12 23:00 | Spring | FALSE | nonsummer
2023-03-12 23:00 | 2023-03-13 | Spring | FALSE | nonsummer
2023-03-13 | 2023-03-13 01:00 | Spring | FALSE | nonsummer
2023-03-13 01:00 | 2023-03-13 02:00 | Spring | FALSE | nonsummer
2023-03-13 02:00 | 2023-03-13 03:00 | Spring | FALSE | nonsummer
2023-03-13 03:00 | 2023-03-13 04:00 | Spring | FALSE | nonsummer
2023-03-13 04:00 | 2023-03-13 05:00 | Spring | FALSE | nonsummer
2023-03-13 05:00 | 2023-03-13 06:00 | Spring | FALSE | nonsummer
2023-03-13 06:00 | 2023-03-13 07:00 | Spring | FALSE | nonsummer
2023-03-13 07:00 | 2023-03-13 08:00 | Spring | FALSE | nonsummer
2023-03-13 08:00 | 2023-03-13 09:00 | Spring | FALSE | nonsummer
2023-03-13 09:00 | 2023-03-13 10:00 | Spring | FALSE | nonsummer
2023-03-13 10:00 | 2023-03-13 11:00 | Spring | FALSE | nonsummer
2023-03-13 11:00 | 2023-03-13 12:00 | Spring | FALSE | nonsummer
2023-03-13 12:00 | 2023-03-13 13:00 | Spring | FALSE | nonsummer
2023-03-13 13:00 | 2023-03-13 14:00 | Spring | FALSE | nonsummer
2023-03-13 14:00 | 2023-03-13 15:00 | Spring | FALSE | nonsummer
2023-03-13 15:00 | 2023-03-13 16:00 | Spring | FALSE | nonsummer
2023-03-13 16:00 | 2023-03-13 17:00 | Spring | FALSE | nonsummer
2023-03-13 17:00 | 2023-03-13 18:00 | Spring | TRUE | nonsummer
2023-03-13 18:00 | 2023-03-13 19:00 | Spring | TRUE | nonsummer
2023-03-13 19:00 | 2023-03-13 20:00 | Spring | TRUE | nonsummer
2023-03-13 20:00 | 2023-03-13 21:00 | Spring | TRUE | nonsummer
2023-03-13 21:00 | 2023-03-13 22:00 | Spring | TRUE | nonsummer
2023-03-13 22:00 | 2023-03-13 23:00 | Spring | FALSE | nonsummer
2023-03-13 23:00 | 2023-03-14 | Spring | FALSE | nonsummer
2023-03-14 | 2023-03-14 01:00 | Spring | FALSE | nonsummer
2023-03-14 01:00 | 2023-03-14 02:00 | Spring | FALSE | nonsummer
2023-03-14 02:00 | 2023-03-14 03:00 | Spring | FALSE | nonsummer
2023-03-14 03:00 | 2023-03-14 04:00 | Spring | FALSE | nonsummer
2023-03-14 04:00 | 2023-03-14 05:00 | Spring | FALSE | nonsummer
2023-03-14 05:00 | 2023-03-14 06:00 | Spring | FALSE | nonsummer
2023-03-14 06:00 | 2023-03-14 07:00 | Spring | FALSE | nonsummer
2023-03-14 07:00 | 2023-03-14 08:00 | Spring | FALSE | nonsummer
2023-03-14 08:00 | 2023-03-14 09:00 | Spring | FALSE | nonsummer
2023-03-14 09:00 | 2023-03-14 10:00 | Spring | FALSE | nonsummer
2023-03-14 10:00 | 2023-03-14 11:00 | Spring | FALSE | nonsummer
2023-03-14 11:00 | 2023-03-14 12:00 | Spring | FALSE | nonsummer
2023-03-14 12:00 | 2023-03-14 13:00 | Spring | FALSE | nonsummer
2023-03-14 13:00 | 2023-03-14 14:00 | Spring | FALSE | nonsummer
2023-03-14 14:00 | 2023-03-14 15:00 | Spring | FALSE | nonsummer
2023-03-14 15:00 | 2023-03-14 16:00 | Spring | FALSE | nonsummer
2023-03-14 16:00 | 2023-03-14 17:00 | Spring | FALSE | nonsummer
2023-03-14 17:00 | 2023-03-14 18:00 | Spring | TRUE | nonsummer
2023-03-14 18:00 | 2023-03-14 19:00 | Spring | TRUE | nonsummer
2023-03-14 19:00 | 2023-03-14 20:00 | Spring | TRUE | nonsummer
2023-03-14 20:00 | 2023-03-14 21:00 | Spring | TRUE | nonsummer
2023-03-14 21:00 | 2023-03-14 22:00 | Spring | TRUE | nonsummer
2023-03-14 22:00 | 2023-03-14 23:00 | Spring | FALSE | nonsummer
2023-03-14 23:00 | 2023-03-15 | Spring | FALSE | nonsummer
2023-03-15 | 2023-03-15 01:00 | Spring | FALSE | nonsummer
2023-03-15 01:00 | 2023-03-15 02:00 | Spring | FALSE | nonsummer
2023-03-15 02:00 | 2023-03-15 03:00 | Spring | FALSE | nonsummer
2023-03-15 03:00 | 2023-03-15 04:00 | Spring | FALSE | nonsummer
2023-03-15 04:00 | 2023-03-15 05:00 | Spring | FALSE | nonsummer
2023-03-15 05:00 | 2023-03-15 06:00 | Spring | FALSE | nonsummer
2023-03-15 06:00 | 2023-03-15 07:00 | Spring | FALSE | nonsummer
2023-03-15 07:00 | 2023-03-15 08:00 | Spring | FALSE | nonsummer
2023-03-15 08:00 | 2023-03-15 09:00 | Spring | FALSE | nonsummer
2023-03-15 09:00 | 2023-03-15 10:00 | Spring | FALSE | nonsummer
2023-03-15 10:00 | 2023-03-15 11:00 | Spring | FALSE | nonsummer
2023-03-15 11:00 | 2023-03-15 12:00 | Spring | FALSE | nonsummer
2023-03-15 12:00 | 2023-03-15 13:00 | Spring | FALSE | nonsummer
2023-03-15 13:00 | 2023-03-15 14:00 | Spring | FALSE | nonsummer
2023-03-15 14:00 | 2023-03-15 15:00 | Spring | FALSE | nonsummer
2023-03-15 15:00 | 2023-03-15 16:00 | Spring | FALSE | nonsummer
2023-03-15 16:00 | 2023-03-15 17:00 | Spring | FALSE | nonsummer
2023-03-15 17:00 | 2023-03-15 18:00 | Spring | TRUE | nonsummer
2023-03-15 18:00 | 2023-03-15 19:00 | Spring | TRUE | nonsummer
2023-03-15 19:00 | 2023-03-15 20:00 | Spring | TRUE | nonsummer
2023-03-15 20:00 | 2023-03-15 21:00 | Spring | TRUE | nonsummer
2023-03-15 21:00 | 2023-03-15 22:00 | Spring | TRUE | nonsummer
2023-03-15 22:00 | 2023-03-15 23:00 | Spring | FALSE | nonsummer
2023-03-15 23:00 | 2023-03-16 | Spring | FALSE | nonsummer
2023-03-16 | 2023-03-16 01:00 | Spring | FALSE | nonsummer
2023-03-16 01:00 | 2023-03-16 02:00 | Spring | FALSE | nonsummer
2023-03-16 02:00 | 2023-03-16 03:00 | Spring | FALSE | nonsummer
2023-03-16 03:00 | 2023-03-16 04:00 | Spring | FALSE | nonsummer
2023-03-16 04:00 | 2023-03-16 05:00 | Spring | FALSE | nonsummer
2023-03-16 05:00 | 2023-03-16 06:00 | Spring | FALSE | nonsummer
2023-03-16 06:00 | 2023-03-16 07:00 | Spring | FALSE | nonsummer
2023-03-16 07:00 | 2023-03-16 08:00 | Spring | FALSE | nonsummer
2023-03-16 08:00 | 2023-03-16 09:00 | Spring | FALSE | nonsummer
2023-03-16 09:00 | 2023-03-16 10:00 | Spring | FALSE | nonsummer
2023-03-16 10:00 | 2023-03-16 11:00 | Spring | FALSE | nonsummer
2023-03-16 11:00 | 2023-03-16 12:00 | Spring | FALSE | nonsummer
2023-03-16 12:00 | 2023-03-16 13:00 | Spring | FALSE | nonsummer
2023-03-16 13:00 | 2023-03-16 14:00 | Spring | FALSE | nonsummer
2023-03-16 14:00 | 2023-03-16 15:00 | Spring | FALSE | nonsummer
2023-03-16 15:00 | 2023-03-16 16:00 | Spring | FALSE | nonsummer
2023-03-16 16:00 | 2023-03-16 17:00 | Spring | FALSE | nonsummer
2023-03-16 17:00 | 2023-03-16 18:00 | Spring | TRUE | nonsummer
2023-03-16 18:00 | 2023-03-16 19:00 | Spring | TRUE | nonsummer
2023-03-16 19:00 | 2023-03-16 20:00 | Spring | TRUE | nonsummer
2023-03-16 20:00 | 2023-03-16 21:00 | Spring | TRUE | nonsummer
2023-03-16 21:00 | 2023-03-16 22:00 | Spring | TRUE | nonsummer
2023-03-16 22:00 | 2023-03-16 23:00 | Spring | FALSE | nonsummer
2023-03-16 23:00 | 2023-03-17 | Spring | FALSE | nonsummer
2023-03-17 | 2023-03-17 01:00 | Spring | FALSE | nonsummer
2023-03-17 01:00 | 2023-03-17 02:00 | Spring | FALSE | nonsummer
2023-03-17 02:00 | 2023-03-17 03:00 | Spring | FALSE | nonsummer
2023-03-17 03:00 | 2023-03-17 04:00 | Spring | FALSE | nonsummer
2023-03-17 04:00 | 2023-03-17 05:00 | Spring | FALSE | nonsummer
2023-03-17 05:00 | 2023-03-17 06:00 | Spring | FALSE | nonsummer
2023-03-17 06:00 | 2023-03-17 07:00 | Spring | FALSE | nonsummer
2023-03-17 07:00 | 2023-03-17 08:00 | Spring | FALSE | nonsummer
2023-03-17 08:00 | 2023-03-17 09:00 | Spring | FALSE | nonsummer
2023-03-17 09:00 | 2023-03-17 10:00 | Spring | FALSE | nonsummer
2023-03-17 10:00 | 2023-03-17 11:00 | Spring | FALSE | nonsummer
2023-03-17 11:00 | 2023-03-17 12:00 | Spring | FALSE | nonsummer
2023-03-17 12:00 | 2023-03-17 13:00 | Spring | FALSE | nonsummer
2023-03-17 13:00 | 2023-03-17 14:00 | Spring | FALSE | nonsummer
2023-03-17 14:00 | 2023-03-17 15:00 | Spring | FALSE | nonsummer
2023-03-17 15:00 | 2023-03-17 16:00 | Spring | FALSE | nonsummer
2023-03-17 16:00 | 2023-03-17 17:00 | Spring | FALSE | nonsummer
2023-03-17 17:00 | 2023-03-17 18:00 | Spring | TRUE | nonsummer
2023-03-17 18:00 | 2023-03-17 19:00 | Spring | TRUE | nonsummer
2023-03-17 19:00 | 2023-03-17 20:00 | Spring | TRUE | nonsummer
2023-03-17 20:00 | 2023-03-17 21:00 | Spring | TRUE | nonsummer
2023-03-17 21:00 | 2023-03-17 22:00 | Spring | TRUE | nonsummer
2023-03-17 22:00 | 2023-03-17 23:00 | Spring | FALSE | nonsummer
2023-03-17 23:00 | 2023-03-18 | Spring | FALSE | nonsummer
2023-03-18 | 2023-03-18 01:00 | Spring | FALSE | nonsummer
2023-03-18 01:00 | 2023-03-18 02:00 | Spring | FALSE | nonsummer
2023-03-18 02:00 | 2023-03-18 03:00 | Spring | FALSE | nonsummer
2023-03-18 03:00 | 2023-03-18 04:00 | Spring | FALSE | nonsummer
2023-03-18 04:00 | 2023-03-18 05:00 | Spring | FALSE | nonsummer
2023-03-18 05:00 | 2023-03-18 06:00 | Spring | FALSE | nonsummer
2023-03-18 06:00 | 2023-03-18 07:00 | Spring | FALSE | nonsummer
2023-03-18 07:00 | 2023-03-18 08:00 | Spring | FALSE | nonsummer
2023-03-18 08:00 | 2023-03-18 09:00 | Spring | FALSE | nonsummer
2023-03-18 09:00 | 2023-03-18 10:00 | Spring | FALSE | nonsummer
2023-03-18 10:00 | 2023-03-18 11:00 | Spring | FALSE | nonsummer
2023-03-18 11:00 | 2023-03-18 12:00 | Spring | FALSE | nonsummer
2023-03-18 12:00 | 2023-03-18 13:00 | Spring | FALSE | nonsummer
2023-03-18 13:00 | 2023-03-18 14:00 | Spring | FALSE | nonsummer
2023-03-18 14:00 | 2023-03-18 15:00 | Spring | FALSE | nonsummer
2023-03-18 15:00 | 2023-03-18 16:00 | Spring | FALSE | nonsummer
2023-03-18 16:00 | 2023-03-18 17:00 | Spring | FALSE | nonsummer
2023-03-18 17:00 | 2023-03-18 18:00 | Spring | TRUE | nonsummer
2023-03-18 18:00 | 2023-03-18 19:00 | Spring | TRUE | nonsummer
2023-03-18 19:00 | 2023-03-18 20:00 | Spring | TRUE | nonsummer
2023-03-18 20:00 | 2023-03-18 21:00 | Spring | TRUE | nonsummer
2023-03-18 21:00 | 2023-03-18 22:00 | Spring | TRUE | nonsummer
2023-03-18 22:00 | 2023-03-18 23:00 | Spring | FALSE | nonsummer
2023-03-18 23:00 | 2023-03-19 | Spring | FALSE | nonsummer
2023-03-19 | 2023-03-19 01:00 | Spring | FALSE | nonsummer
2023-03-19 01:00 | 2023-03-19 02:00 | Spring | FALSE | nonsummer
2023-03-19 02:00 | 2023-03-19 03:00 | Spring | FALSE | nonsummer
2023-03-19 03:00 | 2023-03-19 04:00 | Spring | FALSE | nonsummer
2023-03-19 04:00 | 2023-03-19 05:00 | Spring | FALSE | nonsummer
2023-03-19 05:00 | 2023-03-19 06:00 | Spring | FALSE | nonsummer
2023-03-19 06:00 | 2023-03-19 07:00 | Spring | FALSE | nonsummer
2023-03-19 07:00 | 2023-03-19 08:00 | Spring | FALSE | nonsummer
2023-03-19 08:00 | 2023-03-19 09:00 | Spring | FALSE | nonsummer
2023-03-19 09:00 | 2023-03-19 10:00 | Spring | FALSE | nonsummer
2023-03-19 10:00 | 2023-03-19 11:00 | Spring | FALSE | nonsummer
2023-03-19 11:00 | 2023-03-19 12:00 | Spring | FALSE | nonsummer
2023-03-19 12:00 | 2023-03-19 13:00 | Spring | FALSE | nonsummer
2023-03-19 13:00 | 2023-03-19 14:00 | Spring | FALSE | nonsummer
2023-03-19 14:00 | 2023-03-19 15:00 | Spring | FALSE | nonsummer
2023-03-19 15:00 | 2023-03-19 16:00 | Spring | FALSE | nonsummer
2023-03-19 16:00 | 2023-03-19 17:00 | Spring | FALSE | nonsummer
2023-03-19 17:00 | 2023-03-19 18:00 | Spring | TRUE | nonsummer
2023-03-19 18:00 | 2023-03-19 19:00 | Spring | TRUE | nonsummer
2023-03-19 19:00 | 2023-03-19 20:00 | Spring | TRUE | nonsummer
2023-03-19 20:00 | 2023-03-19 21:00 | Spring | TRUE | nonsummer
2023-03-19 21:00 | 2023-03-19 22:00 | Spring | TRUE | nonsummer
2023-03-19 22:00 | 2023-03-19 23:00 | Spring | FALSE | nonsummer
2023-03-19 23:00 | 2023-03-20 | Spring | FALSE | nonsummer
2023-03-20 | 2023-03-20 01:00 | Spring | FALSE | nonsummer
2023-03-20 01:00 | 2023-03-20 02:00 | Spring | FALSE | nonsummer
2023-03-20 02:00 | 2023-03-20 03:00 | Spring | FALSE | nonsummer
2023-03-20 03:00 | 2023-03-20 04:00 | Spring | FALSE | nonsummer
2023-03-20 04:00 | 2023-03-20 05:00 | Spring | FALSE | nonsummer
2023-03-20 05:00 | 2023-03-20 06:00 | Spring | FALSE | nonsummer
2023-03-20 06:00 | 2023-03-20 07:00 | Spring | FALSE | nonsummer
2023-03-20 07:00 | 2023-03-20 08:00 | Spring | FALSE | nonsummer
2023-03-20 08:00 | 2023-03-20 09:00 | Spring | FALSE | nonsummer
2023-03-20 09:00 | 2023-03-20 10:00 | Spring | FALSE | nonsummer
2023-03-20 10:00 | 2023-03-20 11:00 | Spring | FALSE | nonsummer
2023-03-20 11:00 | 2023-03-20 12:00 | Spring | FALSE | nonsummer
2023-03-20 12:00 | 2023-03-20 13:00 | Spring | FALSE | nonsummer
2023-03-20 13:00 | 2023-03-20 14:00 | Spring | FALSE | nonsummer
2023-03-20 14:00 | 2023-03-20 15:00 | Spring | FALSE | nonsummer
2023-03-20 15:00 | 2023-03-20 16:00 | Spring | FALSE | nonsummer
2023-03-20 16:00 | 2023-03-20 17:00 | Spring | FALSE | nonsummer
2023-03-20 17:00 | 2023-03-20 18:00 | Spring | TRUE | nonsummer
2023-03-20 18:00 | 2023-03-20 19:00 | Spring | TRUE | nonsummer
2023-03-20 19:00 | 2023-03-20 20:00 | Spring | TRUE | nonsummer
2023-03-20 20:00 | 2023-03-20 21:00 | Spring | TRUE | nonsummer
2023-03-20 21:00 | 2023-03-20 22:00 | Spring | TRUE | nonsummer
2023-03-20 22:00 | 2023-03-20 23:00 | Spring | FALSE | nonsummer
2023-03-20 23:00 | 2023-03-21 | Spring | FALSE | nonsummer
2023-03-21 | 2023-03-21 01:00 | Spring | FALSE | nonsummer
2023-03-21 01:00 | 2023-03-21 02:00 | Spring | FALSE | nonsummer
2023-03-21 02:00 | 2023-03-21 03:00 | Spring | FALSE | nonsummer
2023-03-21 03:00 | 2023-03-21 04:00 | Spring | FALSE | nonsummer
2023-03-21 04:00 | 2023-03-21 05:00 | Spring | FALSE | nonsummer
2023-03-21 05:00 | 2023-03-21 06:00 | Spring | FALSE | nonsummer
2023-03-21 06:00 | 2023-03-21 07:00 | Spring | FALSE | nonsummer
2023-03-21 07:00 | 2023-03-21 08:00 | Spring | FALSE | nonsummer
2023-03-21 08:00 | 2023-03-21 09:00 | Spring | FALSE | nonsummer
2023-03-21 09:00 | 2023-03-21 10:00 | Spring | FALSE | nonsummer
2023-03-21 10:00 | 2023-03-21 11:00 | Spring | FALSE | nonsummer
2023-03-21 11:00 | 2023-03-21 12:00 | Spring | FALSE | nonsummer
2023-03-21 12:00 | 2023-03-21 13:00 | Spring | FALSE | nonsummer
2023-03-21 13:00 | 2023-03-21 14:00 | Spring | FALSE | nonsummer
2023-03-21 14:00 | 2023-03-21 15:00 | Spring | FALSE | nonsummer
2023-03-21 15:00 | 2023-03-21 16:00 | Spring | FALSE | nonsummer
2023-03-21 16:00 | 2023-03-21 17:00 | Spring | FALSE | nonsummer
2023-03-21 17:00 | 2023-03-21 18:00 | Spring | TRUE | nonsummer
2023-03-21 18:00 | 2023-03-21 19:00 | Spring | TRUE | nonsummer
2023-03-21 19:00 | 2023-03-21 20:00 | Spring | TRUE | nonsummer
2023-03-21 20:00 | 2023-03-21 21:00 | Spring | TRUE | nonsummer
2023-03-21 21:00 | 2023-03-21 22:00 | Spring | TRUE | nonsummer
2023-03-21 22:00 | 2023-03-21 23:00 | Spring | FALSE | nonsummer
2023-03-21 23:00 | 2023-03-22 | Spring | FALSE | nonsummer
2023-03-22 | 2023-03-22 01:00 | Spring | FALSE | nonsummer
2023-03-22 01:00 | 2023-03-22 02:00 | Spring | FALSE | nonsummer
2023-03-22 02:00 | 2023-03-22 03:00 | Spring | FALSE | nonsummer
2023-03-22 03:00 | 2023-03-22 04:00 | Spring | FALSE | nonsummer
2023-03-22 04:00 | 2023-03-22 05:00 | Spring | FALSE | nonsummer
2023-03-22 05:00 | 2023-03-22 06:00 | Spring | FALSE | nonsummer
2023-03-22 06:00 | 2023-03-22 07:00 | Spring | FALSE | nonsummer
2023-03-22 07:00 | 2023-03-22 08:00 | Spring | FALSE | nonsummer
2023-03-22 08:00 | 2023-03-22 09:00 | Spring | FALSE | nonsummer
2023-03-22 09:00 | 2023-03-22 10:00 | Spring | FALSE | nonsummer
2023-03-22 10:00 | 2023-03-22 11:00 | Spring | FALSE | nonsummer
2023-03-22 11:00 | 2023-03-22 12:00 | Spring | FALSE | nonsummer
2023-03-22 12:00 | 2023-03-22 13:00 | Spring | FALSE | nonsummer
2023-03-22 13:00 | 2023-03-22 14:00 | Spring | FALSE | nonsummer
2023-03-22 14:00 | 2023-03-22 15:00 | Spring | FALSE | nonsummer
2023-03-22 15:00 | 2023-03-22 16:00 | Spring | FALSE | nonsummer
2023-03-22 16:00 | 2023-03-22 17:00 | Spring | FALSE | nonsummer
2023-03-22 17:00 | 2023-03-22 18:00 | Spring | TRUE | nonsummer
2023-03-22 18:00 | 2023-03-22 19:00 | Spring | TRUE | nonsummer
2023-03-22 19:00 | 2023-03-22 20:00 | Spring | TRUE | nonsummer
2023-03-22 20:00 | 2023-03-22 21:00 | Spring | TRUE | nonsummer
2023-03-22 21:00 | 2023-03-22 22:00 | Spring | TRUE | nonsummer
2023-03-22 22:00 | 2023-03-22 23:00 | Spring | FALSE | nonsummer
2023-03-22 23:00 | 2023-03-23 | Spring | FALSE | nonsummer
2023-03-23 | 2023-03-23 01:00 | Spring | FALSE | nonsummer
2023-03-23 01:00 | 2023-03-23 02:00 | Spring | FALSE | nonsummer
2023-03-23 02:00 | 2023-03-23 03:00 | Spring | FALSE | nonsummer
2023-03-23 03:00 | 2023-03-23 04:00 | Spring | FALSE | nonsummer
2023-03-23 04:00 | 2023-03-23 05:00 | Spring | FALSE | nonsummer
2023-03-23 05:00 | 2023-03-23 06:00 | Spring | FALSE | nonsummer
2023-03-23 06:00 | 2023-03-23 07:00 | Spring | FALSE | nonsummer
2023-03-23 07:00 | 2023-03-23 08:00 | Spring | FALSE | nonsummer
2023-03-23 08:00 | 2023-03-23 09:00 | Spring | FALSE | nonsummer
2023-03-23 09:00 | 2023-03-23 10:00 | Spring | FALSE | nonsummer
2023-03-23 10:00 | 2023-03-23 11:00 | Spring | FALSE | nonsummer
2023-03-23 11:00 | 2023-03-23 12:00 | Spring | FALSE | nonsummer
2023-03-23 12:00 | 2023-03-23 13:00 | Spring | FALSE | nonsummer
2023-03-23 13:00 | 2023-03-23 14:00 | Spring | FALSE | nonsummer
2023-03-23 14:00 | 2023-03-23 15:00 | Spring | FALSE | nonsummer
2023-03-23 15:00 | 2023-03-23 16:00 | Spring | FALSE | nonsummer
2023-03-23 16:00 | 2023-03-23 17:00 | Spring | FALSE | nonsummer
2023-03-23 17:00 | 2023-03-23 18:00 | Spring | TRUE | nonsummer
2023-03-23 18:00 | 2023-03-23 19:00 | Spring | TRUE | nonsummer
2023-03-23 19:00 | 2023-03-23 20:00 | Spring | TRUE | nonsummer
2023-03-23 20:00 | 2023-03-23 21:00 | Spring | TRUE | nonsummer
2023-03-23 21:00 | 2023-03-23 22:00 | Spring | TRUE | nonsummer
2023-03-23 22:00 | 2023-03-23 23:00 | Spring | FALSE | nonsummer
2023-03-23 23:00 | 2023-03-24 | Spring | FALSE | nonsummer
2023-03-24 | 2023-03-24 01:00 | Spring | FALSE | nonsummer
2023-03-24 01:00 | 2023-03-24 02:00 | Spring | FALSE | nonsummer
2023-03-24 02:00 | 2023-03-24 03:00 | Spring | FALSE | nonsummer
2023-03-24 03:00 | 2023-03-24 04:00 | Spring | FALSE | nonsummer
2023-03-24 04:00 | 2023-03-24 05:00 | Spring | FALSE | nonsummer
2023-03-24 05:00 | 2023-03-24 06:00 | Spring | FALSE | nonsummer
2023-03-24 06:00 | 2023-03-24 07:00 | Spring | FALSE | nonsummer
2023-03-24 07:00 | 2023-03-24 08:00 | Spring | FALSE | nonsummer
2023-03-24 08:00 | 2023-03-24 09:00 | Spring | FALSE | nonsummer
2023-03-24 09:00 | 2023-03-24 10:00 | Spring | FALSE | nonsummer
2023-03-24 10:00 | 2023-03-24 11:00 | Spring | FALSE | nonsummer
2023-03-24 11:00 | 2023-03-24 12:00 | Spring | FALSE | nonsummer
2023-03-24 12:00 | 2023-03-24 13:00 | Spring | FALSE | nonsummer
2023-03-24 13:00 | 2023-03-24 14:00 | Spring | FALSE | nonsummer
2023-03-24 14:00 | 2023-03-24 15:00 | Spring | FALSE | nonsummer
2023-03-24 15:00 | 2023-03-24 16:00 | Spring | FALSE | nonsummer
2023-03-24 16:00 | 2023-03-24 17:00 | Spring | FALSE | nonsummer
2023-03-24 17:00 | 2023-03-24 18:00 | Spring | TRUE | nonsummer
2023-03-24 18:00 | 2023-03-24 19:00 | Spring | TRUE | nonsummer
2023-03-24 19:00 | 2023-03-24 20:00 | Spring | TRUE | nonsummer
2023-03-24 20:00 | 2023-03-24 21:00 | Spring | TRUE | nonsummer
2023-03-24 21:00 | 2023-03-24 22:00 | Spring | TRUE | nonsummer
2023-03-24 22:00 | 2023-03-24 23:00 | Spring | FALSE | nonsummer
2023-03-24 23:00 | 2023-03-25 | Spring | FALSE | nonsummer
2023-03-25 | 2023-03-25 01:00 | Spring | FALSE | nonsummer
2023-03-25 01:00 | 2023-03-25 02:00 | Spring | FALSE | nonsummer
2023-03-25 02:00 | 2023-03-25 03:00 | Spring | FALSE | nonsummer
2023-03-25 03:00 | 2023-03-25 04:00 | Spring | FALSE | nonsummer
2023-03-25 04:00 | 2023-03-25 05:00 | Spring | FALSE | nonsummer
2023-03-25 05:00 | 2023-03-25 06:00 | Spring | FALSE | nonsummer
2023-03-25 06:00 | 2023-03-25 07:00 | Spring | FALSE | nonsummer
2023-03-25 07:00 | 2023-03-25 08:00 | Spring | FALSE | nonsummer
2023-03-25 08:00 | 2023-03-25 09:00 | Spring | FALSE | nonsummer
2023-03-25 09:00 | 2023-03-25 10:00 | Spring | FALSE | nonsummer
2023-03-25 10:00 | 2023-03-25 11:00 | Spring | FALSE | nonsummer
2023-03-25 11:00 | 2023-03-25 12:00 | Spring | FALSE | nonsummer
2023-03-25 12:00 | 2023-03-25 13:00 | Spring | FALSE | nonsummer
2023-03-25 13:00 | 2023-03-25 14:00 | Spring | FALSE | nonsummer
2023-03-25 14:00 | 2023-03-25 15:00 | Spring | FALSE | nonsummer
2023-03-25 15:00 | 2023-03-25 16:00 | Spring | FALSE | nonsummer
2023-03-25 16:00 | 2023-03-25 17:00 | Spring | FALSE | nonsummer
2023-03-25 17:00 | 2023-03-25 18:00 | Spring | TRUE | nonsummer
2023-03-25 18:00 | 2023-03-25 19:00 | Spring | TRUE | nonsummer
2023-03-25 19:00 | 2023-03-25 20:00 | Spring | TRUE | nonsummer
2023-03-25 20:00 | 2023-03-25 21:00 | Spring | TRUE | nonsummer
2023-03-25 21:00 | 2023-03-25 22:00 | Spring | TRUE | nonsummer
2023-03-25 22:00 | 2023-03-25 23:00 | Spring | FALSE | nonsummer
2023-03-25 23:00 | 2023-03-26 | Spring | FALSE | nonsummer
2023-03-26 | 2023-03-26 01:00 | Spring | FALSE | nonsummer
2023-03-26 01:00 | 2023-03-26 02:00 | Spring | FALSE | nonsummer
2023-03-26 02:00 | 2023-03-26 03:00 | Spring | FALSE | nonsummer
2023-03-26 03:00 | 2023-03-26 04:00 | Spring | FALSE | nonsummer
2023-03-26 04:00 | 2023-03-26 05:00 | Spring | FALSE | nonsummer
2023-03-26 05:00 | 2023-03-26 06:00 | Spring | FALSE | nonsummer
2023-03-26 06:00 | 2023-03-26 07:00 | Spring | FALSE | nonsummer
2023-03-26 07:00 | 2023-03-26 08:00 | Spring | FALSE | nonsummer
2023-03-26 08:00 | 2023-03-26 09:00 | Spring | FALSE | nonsummer
2023-03-26 09:00 | 2023-03-26 10:00 | Spring | FALSE | nonsummer
2023-03-26 10:00 | 2023-03-26 11:00 | Spring | FALSE | nonsummer
2023-03-26 11:00 | 2023-03-26 12:00 | Spring | FALSE | nonsummer
2023-03-26 12:00 | 2023-03-26 13:00 | Spring | FALSE | nonsummer
2023-03-26 13:00 | 2023-03-26 14:00 | Spring | FALSE | nonsummer
2023-03-26 14:00 | 2023-03-26 15:00 | Spring | FALSE | nonsummer
2023-03-26 15:00 | 2023-03-26 16:00 | Spring | FALSE | nonsummer
2023-03-26 16:00 | 2023-03-26 17:00 | Spring | FALSE | nonsummer
2023-03-26 17:00 | 2023-03-26 18:00 | Spring | TRUE | nonsummer
2023-03-26 18:00 | 2023-03-26 19:00 | Spring | TRUE | nonsummer
2023-03-26 19:00 | 2023-03-26 20:00 | Spring | TRUE | nonsummer
2023-03-26 20:00 | 2023-03-26 21:00 | Spring | TRUE | nonsummer
2023-03-26 21:00 | 2023-03-26 22:00 | Spring | TRUE | nonsummer
2023-03-26 22:00 | 2023-03-26 23:00 | Spring | FALSE | nonsummer
2023-03-26 23:00 | 2023-03-27 | Spring | FALSE | nonsummer
2023-03-27 | 2023-03-27 01:00 | Spring | FALSE | nonsummer
2023-03-27 01:00 | 2023-03-27 02:00 | Spring | FALSE | nonsummer
2023-03-27 02:00 | 2023-03-27 03:00 | Spring | FALSE | nonsummer
2023-03-27 03:00 | 2023-03-27 04:00 | Spring | FALSE | nonsummer
2023-03-27 04:00 | 2023-03-27 05:00 | Spring | FALSE | nonsummer
2023-03-27 05:00 | 2023-03-27 06:00 | Spring | FALSE | nonsummer
2023-03-27 06:00 | 2023-03-27 07:00 | Spring | FALSE | nonsummer
2023-03-27 07:00 | 2023-03-27 08:00 | Spring | FALSE | nonsummer
2023-03-27 08:00 | 2023-03-27 09:00 | Spring | FALSE | nonsummer
2023-03-27 09:00 | 2023-03-27 10:00 | Spring | FALSE | nonsummer
2023-03-27 10:00 | 2023-03-27 11:00 | Spring | FALSE | nonsummer
2023-03-27 11:00 | 2023-03-27 12:00 | Spring | FALSE | nonsummer
2023-03-27 12:00 | 2023-03-27 13:00 | Spring | FALSE | nonsummer
2023-03-27 13:00 | 2023-03-27 14:00 | Spring | FALSE | nonsummer
2023-03-27 14:00 | 2023-03-27 15:00 | Spring | FALSE | nonsummer
2023-03-27 15:00 | 2023-03-27 16:00 | Spring | FALSE | nonsummer
2023-03-27 16:00 | 2023-03-27 17:00 | Spring | FALSE | nonsummer
2023-03-27 17:00 | 2023-03-27 18:00 | Spring | TRUE | nonsummer
2023-03-27 18:00 | 2023-03-27 19:00 | Spring | TRUE | nonsummer
2023-03-27 19:00 | 2023-03-27 20:00 | Spring | TRUE | nonsummer
2023-03-27 20:00 | 2023-03-27 21:00 | Spring | TRUE | nonsummer
2023-03-27 21:00 | 2023-03-27 22:00 | Spring | TRUE | nonsummer
2023-03-27 22:00 | 2023-03-27 23:00 | Spring | FALSE | nonsummer
2023-03-27 23:00 | 2023-03-28 | Spring | FALSE | nonsummer
2023-03-28 | 2023-03-28 01:00 | Spring | FALSE | nonsummer
2023-03-28 01:00 | 2023-03-28 02:00 | Spring | FALSE | nonsummer
2023-03-28 02:00 | 2023-03-28 03:00 | Spring | FALSE | nonsummer
2023-03-28 03:00 | 2023-03-28 04:00 | Spring | FALSE | nonsummer
2023-03-28 04:00 | 2023-03-28 05:00 | Spring | FALSE | nonsummer
2023-03-28 05:00 | 2023-03-28 06:00 | Spring | FALSE | nonsummer
2023-03-28 06:00 | 2023-03-28 07:00 | Spring | FALSE | nonsummer
2023-03-28 07:00 | 2023-03-28 08:00 | Spring | FALSE | nonsummer
2023-03-28 08:00 | 2023-03-28 09:00 | Spring | FALSE | nonsummer
2023-03-28 09:00 | 2023-03-28 10:00 | Spring | FALSE | nonsummer
2023-03-28 10:00 | 2023-03-28 11:00 | Spring | FALSE | nonsummer
2023-03-28 11:00 | 2023-03-28 12:00 | Spring | FALSE | nonsummer
2023-03-28 12:00 | 2023-03-28 13:00 | Spring | FALSE | nonsummer
2023-03-28 13:00 | 2023-03-28 14:00 | Spring | FALSE | nonsummer
2023-03-28 14:00 | 2023-03-28 15:00 | Spring | FALSE | nonsummer
2023-03-28 15:00 | 2023-03-28 16:00 | Spring | FALSE | nonsummer
2023-03-28 16:00 | 2023-03-28 17:00 | Spring | FALSE | nonsummer
2023-03-28 17:00 | 2023-03-28 18:00 | Spring | TRUE | nonsummer
2023-03-28 18:00 | 2023-03-28 19:00 | Spring | TRUE | nonsummer
2023-03-28 19:00 | 2023-03-28 20:00 | Spring | TRUE | nonsummer
2023-03-28 20:00 | 2023-03-28 21:00 | Spring | TRUE | nonsummer
2023-03-28 21:00 | 2023-03-28 22:00 | Spring | TRUE | nonsummer
2023-03-28 22:00 | 2023-03-28 23:00 | Spring | FALSE | nonsummer
2023-03-28 23:00 | 2023-03-29 | Spring | FALSE | nonsummer
2023-03-29 | 2023-03-29 01:00 | Spring | FALSE | nonsummer
2023-03-29 01:00 | 2023-03-29 02:00 | Spring | FALSE | nonsummer
2023-03-29 02:00 | 2023-03-29 03:00 | Spring | FALSE | nonsummer
2023-03-29 03:00 | 2023-03-29 04:00 | Spring | FALSE | nonsummer
2023-03-29 04:00 | 2023-03-29 05:00 | Spring | FALSE | nonsummer
2023-03-29 05:00 | 2023-03-29 06:00 | Spring | FALSE | nonsummer
2023-03-29 06:00 | 2023-03-29 07:00 | Spring | FALSE | nonsummer
2023-03-29 07:00 | 2023-03-29 08:00 | Spring | FALSE | nonsummer
2023-03-29 08:00 | 2023-03-29 09:00 | Spring | FALSE | nonsummer
2023-03-29 09:00 | 2023-03-29 10:00 | Spring | FALSE | nonsummer
2023-03-29 10:00 | 2023-03-29 11:00 | Spring | FALSE | nonsummer
2023-03-29 11:00 | 2023-03-29 12:00 | Spring | FALSE | nonsummer
2023-03-29 12:00 | 2023-03-29 13:00 | Spring | FALSE | nonsummer
2023-03-29 13:00 | 2023-03-29 14:00 | Spring | FALSE | nonsummer
2023-03-29 14:00 | 2023-03-29 15:00 | Spring | FALSE | nonsummer
2023-03-29 15:00 | 2023-03-29 16:00 | Spring | FALSE | nonsummer
2023-03-29 16:00 | 2023-03-29 17:00 | Spring | FALSE | nonsummer
2023-03-29 17:00 | 2023-03-29 18:00 | Spring | TRUE | nonsummer
2023-03-29 18:00 | 2023-03-29 19:00 | Spring | TRUE | nonsummer
2023-03-29 19:00 | 2023-03-29 20:00 | Spring | TRUE | nonsummer
2023-03-29 20:00 | 2023-03-29 21:00 | Spring | TRUE | nonsummer
2023-03-29 21:00 | 2023-03-29 22:00 | Spring | TRUE | nonsummer
2023-03-29 22:00 | 2023-03-29 23:00 | Spring | FALSE | nonsummer
2023-03-29 23:00 | 2023-03-30 | Spring | FALSE | nonsummer
2023-03-30 | 2023-03-30 01:00 | Spring | FALSE | nonsummer
2023-03-30 01:00 | 2023-03-30 02:00 | Spring | FALSE | nonsummer
2023-03-30 02:00 | 2023-03-30 03:00 | Spring | FALSE | nonsummer
2023-03-30 03:00 | 2023-03-30 04:00 | Spring | FALSE | nonsummer
2023-03-30 04:00 | 2023-03-30 05:00 | Spring | FALSE | nonsummer
2023-03-30 05:00 | 2023-03-30 06:00 | Spring | FALSE | nonsummer
2023-03-30 06:00 | 2023-03-30 07:00 | Spring | FALSE | nonsummer
2023-03-30 07:00 | 2023-03-30 08:00 | Spring | FALSE | nonsummer
2023-03-30 08:00 | 2023-03-30 09:00 | Spring | FALSE | nonsummer
2023-03-30 09:00 | 2023-03-30 10:00 | Spring | FALSE | nonsummer
2023-03-30 10:00 | 2023-03-30 11:00 | Spring | FALSE | nonsummer
2023-03-30 11:00 | 2023-03-30 12:00 | Spring | FALSE | nonsummer
2023-03-30 12:00 | 2023-03-30 13:00 | Spring | FALSE | nonsummer
2023-03-30 13:00 | 2023-03-30 14:00 | Spring | FALSE | nonsummer
2023-03-30 14:00 | 2023-03-30 15:00 | Spring | FALSE | nonsummer
2023-03-30 15:00 | 2023-03-30 16:00 | Spring | FALSE | nonsummer
2023-03-30 16:00 | 2023-03-30 17:00 | Spring | FALSE | nonsummer
2023-03-30 17:00 | 2023-03-30 18:00 | Spring | TRUE | nonsummer
2023-03-30 18:00 | 2023-03-30 19:00 | Spring | TRUE | nonsummer
2023-03-30 19:00 | 2023-03-30 20:00 | Spring | TRUE | nonsummer
2023-03-30 20:00 | 2023-03-30 21:00 | Spring | TRUE | nonsummer
2023-03-30 21:00 | 2023-03-30 22:00 | Spring | TRUE | nonsummer
2023-03-30 22:00 | 2023-03-30 23:00 | Spring | FALSE | nonsummer
2023-03-30 23:00 | 2023-03-31 | Spring | FALSE | nonsummer
2023-03-31 | 2023-03-31 01:00 | Spring | FALSE | nonsummer
2023-03-31 01:00 | 2023-03-31 02:00 | Spring | FALSE | nonsummer
2023-03-31 02:00 | 2023-03-31 03:00 | Spring | FALSE | nonsummer
2023-03-31 03:00 | 2023-03-31 04:00 | Spring | FALSE | nonsummer
2023-03-31 04:00 | 2023-03-31 05:00 | Spring | FALSE | nonsummer
2023-03-31 05:00 | 2023-03-31 06:00 | Spring | FALSE | nonsummer
2023-03-31 06:00 | 2023-03-31 07:00 | Spring | FALSE | nonsummer
2023-03-31 07:00 | 2023-03-31 08:00 | Spring | FALSE | nonsummer
2023-03-31 08:00 | 2023-03-31 09:00 | Spring | FALSE | nonsummer
2023-03-31 09:00 | 2023-03-31 10:00 | Spring | FALSE | nonsummer
2023-03-31 10:00 | 2023-03-31 11:00 | Spring | FALSE | nonsummer
2023-03-31 11:00 | 2023-03-31 12:00 | Spring | FALSE | nonsummer
2023-03-31 12:00 | 2023-03-31 13:00 | Spring | FALSE | nonsummer
2023-03-31 13:00 | 2023-03-31 14:00 | Spring | FALSE | nonsummer
2023-03-31 14:00 | 2023-03-31 15:00 | Spring | FALSE | nonsummer
2023-03-31 15:00 | 2023-03-31 16:00 | Spring | FALSE | nonsummer
2023-03-31 16:00 | 2023-03-31 17:00 | Spring | FALSE | nonsummer
2023-03-31 17:00 | 2023-03-31 18:00 | Spring | TRUE | nonsummer
2023-03-31 18:00 | 2023-03-31 19:00 | Spring | TRUE | nonsummer
2023-03-31 19:00 | 2023-03-31 20:00 | Spring | TRUE | nonsummer
2023-03-31 20:00 | 2023-03-31 21:00 | Spring | TRUE | nonsummer
2023-03-31 21:00 | 2023-03-31 22:00 | Spring | TRUE | nonsummer
2023-03-31 22:00 | 2023-03-31 23:00 | Spring | FALSE | nonsummer
2023-03-31 23:00 | 2023-04-01 | Spring | FALSE | nonsummer
2023-04-01 | 2023-04-01 01:00 | Spring | FALSE | nonsummer
2023-04-01 01:00 | 2023-04-01 02:00 | Spring | FALSE | nonsummer
2023-04-01 02:00 | 2023-04-01 03:00 | Spring | FALSE | nonsummer
2023-04-01 03:00 | 2023-04-01 04:00 | Spring | FALSE | nonsummer
2023-04-01 04:00 | 2023-04-01 05:00 | Spring | FALSE | nonsummer
2023-04-01 05:00 | 2023-04-01 06:00 | Spring | FALSE | nonsummer
2023-04-01 06:00 | 2023-04-01 07:00 | Spring | FALSE | nonsummer
2023-04-01 07:00 | 2023-04-01 08:00 | Spring | FALSE | nonsummer
2023-04-01 08:00 | 2023-04-01 09:00 | Spring | FALSE | nonsummer
2023-04-01 09:00 | 2023-04-01 10:00 | Spring | FALSE | nonsummer
2023-04-01 10:00 | 2023-04-01 11:00 | Spring | FALSE | nonsummer
2023-04-01 11:00 | 2023-04-01 12:00 | Spring | FALSE | nonsummer
2023-04-01 12:00 | 2023-04-01 13:00 | Spring | FALSE | nonsummer
2023-04-01 13:00 | 2023-04-01 14:00 | Spring | FALSE | nonsummer
2023-04-01 14:00 | 2023-04-01 15:00 | Spring | FALSE | nonsummer
2023-04-01 15:00 | 2023-04-01 16:00 | Spring | FALSE | nonsummer
2023-04-01 16:00 | 2023-04-01 17:00 | Spring | FALSE | nonsummer
2023-04-01 17:00 | 2023-04-01 18:00 | Spring | TRUE | nonsummer
2023-04-01 18:00 | 2023-04-01 19:00 | Spring | TRUE | nonsummer
2023-04-01 19:00 | 2023-04-01 20:00 | Spring | TRUE | nonsummer
2023-04-01 20:00 | 2023-04-01 21:00 | Spring | TRUE | nonsummer
2023-04-01 21:00 | 2023-04-01 22:00 | Spring | TRUE | nonsummer
2023-04-01 22:00 | 2023-04-01 23:00 | Spring | FALSE | nonsummer
2023-04-01 23:00 | 2023-04-02 | Spring | FALSE | nonsummer
2023-04-02 | 2023-04-02 01:00 | Spring | FALSE | nonsummer
2023-04-02 01:00 | 2023-04-02 02:00 | Spring | FALSE | nonsummer
2023-04-02 02:00 | 2023-04-02 03:00 | Spring | FALSE | nonsummer
2023-04-02 03:00 | 2023-04-02 04:00 | Spring | FALSE | nonsummer
2023-04-02 04:00 | 2023-04-02 05:00 | Spring | FALSE | nonsummer
2023-04-02 05:00 | 2023-04-02 06:00 | Spring | FALSE | nonsummer
2023-04-02 06:00 | 2023-04-02 07:00 | Spring | FALSE | nonsummer
2023-04-02 07:00 | 2023-04-02 08:00 | Spring | FALSE | nonsummer
2023-04-02 08:00 | 2023-04-02 09:00 | Spring | FALSE | nonsummer
2023-04-02 09:00 | 2023-04-02 10:00 | Spring | FALSE | nonsummer
2023-04-02 10:00 | 2023-04-02 11:00 | Spring | FALSE | nonsummer
2023-04-02 11:00 | 2023-04-02 12:00 | Spring | FALSE | nonsummer
2023-04-02 12:00 | 2023-04-02 13:00 | Spring | FALSE | nonsummer
2023-04-02 13:00 | 2023-04-02 14:00 | Spring | FALSE | nonsummer
2023-04-02 14:00 | 2023-04-02 15:00 | Spring | FALSE | nonsummer
2023-04-02 15:00 | 2023-04-02 16:00 | Spring | FALSE | nonsummer
2023-04-02 16:00 | 2023-04-02 17:00 | Spring | FALSE | nonsummer
2023-04-02 17:00 | 2023-04-02 18:00 | Spring | TRUE | nonsummer
2023-04-02 18:00 | 2023-04-02 19:00 | Spring | TRUE | nonsummer
2023-04-02 19:00 | 2023-04-02 20:00 | Spring | TRUE | nonsummer
2023-04-02 20:00 | 2023-04-02 21:00 | Spring | TRUE | nonsummer
2023-04-02 21:00 | 2023-04-02 22:00 | Spring | TRUE | nonsummer
2023-04-02 22:00 | 2023-04-02 23:00 | Spring | FALSE | nonsummer
2023-04-02 23:00 | 2023-04-03 | Spring | FALSE | nonsummer
2023-04-03 | 2023-04-03 01:00 | Spring | FALSE | nonsummer
2023-04-03 01:00 | 2023-04-03 02:00 | Spring | FALSE | nonsummer
2023-04-03 02:00 | 2023-04-03 03:00 | Spring | FALSE | nonsummer
2023-04-03 03:00 | 2023-04-03 04:00 | Spring | FALSE | nonsummer
2023-04-03 04:00 | 2023-04-03 05:00 | Spring | FALSE | nonsummer
2023-04-03 05:00 | 2023-04-03 06:00 | Spring | FALSE | nonsummer
2023-04-03 06:00 | 2023-04-03 07:00 | Spring | FALSE | nonsummer
2023-04-03 07:00 | 2023-04-03 08:00 | Spring | FALSE | nonsummer
2023-04-03 08:00 | 2023-04-03 09:00 | Spring | FALSE | nonsummer
2023-04-03 09:00 | 2023-04-03 10:00 | Spring | FALSE | nonsummer
2023-04-03 10:00 | 2023-04-03 11:00 | Spring | FALSE | nonsummer
2023-04-03 11:00 | 2023-04-03 12:00 | Spring | FALSE | nonsummer
2023-04-03 12:00 | 2023-04-03 13:00 | Spring | FALSE | nonsummer
2023-04-03 13:00 | 2023-04-03 14:00 | Spring | FALSE | nonsummer
2023-04-03 14:00 | 2023-04-03 15:00 | Spring | FALSE | nonsummer
2023-04-03 15:00 | 2023-04-03 16:00 | Spring | FALSE | nonsummer
2023-04-03 16:00 | 2023-04-03 17:00 | Spring | FALSE | nonsummer
2023-04-03 17:00 | 2023-04-03 18:00 | Spring | TRUE | nonsummer
2023-04-03 18:00 | 2023-04-03 19:00 | Spring | TRUE | nonsummer
2023-04-03 19:00 | 2023-04-03 20:00 | Spring | TRUE | nonsummer
2023-04-03 20:00 | 2023-04-03 21:00 | Spring | TRUE | nonsummer
2023-04-03 21:00 | 2023-04-03 22:00 | Spring | TRUE | nonsummer
2023-04-03 22:00 | 2023-04-03 23:00 | Spring | FALSE | nonsummer
2023-04-03 23:00 | 2023-04-04 | Spring | FALSE | nonsummer
2023-04-04 | 2023-04-04 01:00 | Spring | FALSE | nonsummer
2023-04-04 01:00 | 2023-04-04 02:00 | Spring | FALSE | nonsummer
2023-04-04 02:00 | 2023-04-04 03:00 | Spring | FALSE | nonsummer
2023-04-04 03:00 | 2023-04-04 04:00 | Spring | FALSE | nonsummer
2023-04-04 04:00 | 2023-04-04 05:00 | Spring | FALSE | nonsummer
2023-04-04 05:00 | 2023-04-04 06:00 | Spring | FALSE | nonsummer
2023-04-04 06:00 | 2023-04-04 07:00 | Spring | FALSE | nonsummer
2023-04-04 07:00 | 2023-04-04 08:00 | Spring | FALSE | nonsummer
2023-04-04 08:00 | 2023-04-04 09:00 | Spring | FALSE | nonsummer
2023-04-04 09:00 | 2023-04-04 10:00 | Spring | FALSE | nonsummer
2023-04-04 10:00 | 2023-04-04 11:00 | Spring | FALSE | nonsummer
2023-04-04 11:00 | 2023-04-04 12:00 | Spring | FALSE | nonsummer
2023-04-04 12:00 | 2023-04-04 13:00 | Spring | FALSE | nonsummer
2023-04-04 13:00 | 2023-04-04 14:00 | Spring | FALSE | nonsummer
2023-04-04 14:00 | 2023-04-04 15:00 | Spring | FALSE | nonsummer
2023-04-04 15:00 | 2023-04-04 16:00 | Spring | FALSE | nonsummer
2023-04-04 16:00 | 2023-04-04 17:00 | Spring | FALSE | nonsummer
2023-04-04 17:00 | 2023-04-04 18:00 | Spring | TRUE | nonsummer
2023-04-04 18:00 | 2023-04-04 19:00 | Spring | TRUE | nonsummer
2023-04-04 19:00 | 2023-04-04 20:00 | Spring | TRUE | nonsummer
2023-04-04 20:00 | 2023-04-04 21:00 | Spring | TRUE | nonsummer
2023-04-04 21:00 | 2023-04-04 22:00 | Spring | TRUE | nonsummer
2023-04-04 22:00 | 2023-04-04 23:00 | Spring | FALSE | nonsummer
2023-04-04 23:00 | 2023-04-05 | Spring | FALSE | nonsummer
2023-04-05 | 2023-04-05 01:00 | Spring | FALSE | nonsummer
2023-04-05 01:00 | 2023-04-05 02:00 | Spring | FALSE | nonsummer
2023-04-05 02:00 | 2023-04-05 03:00 | Spring | FALSE | nonsummer
2023-04-05 03:00 | 2023-04-05 04:00 | Spring | FALSE | nonsummer
2023-04-05 04:00 | 2023-04-05 05:00 | Spring | FALSE | nonsummer
2023-04-05 05:00 | 2023-04-05 06:00 | Spring | FALSE | nonsummer
2023-04-05 06:00 | 2023-04-05 07:00 | Spring | FALSE | nonsummer
2023-04-05 07:00 | 2023-04-05 08:00 | Spring | FALSE | nonsummer
2023-04-05 08:00 | 2023-04-05 09:00 | Spring | FALSE | nonsummer
2023-04-05 09:00 | 2023-04-05 10:00 | Spring | FALSE | nonsummer
2023-04-05 10:00 | 2023-04-05 11:00 | Spring | FALSE | nonsummer
2023-04-05 11:00 | 2023-04-05 12:00 | Spring | FALSE | nonsummer
2023-04-05 12:00 | 2023-04-05 13:00 | Spring | FALSE | nonsummer
2023-04-05 13:00 | 2023-04-05 14:00 | Spring | FALSE | nonsummer
2023-04-05 14:00 | 2023-04-05 15:00 | Spring | FALSE | nonsummer
2023-04-05 15:00 | 2023-04-05 16:00 | Spring | FALSE | nonsummer
2023-04-05 16:00 | 2023-04-05 17:00 | Spring | FALSE | nonsummer
2023-04-05 17:00 | 2023-04-05 18:00 | Spring | TRUE | nonsummer
2023-04-05 18:00 | 2023-04-05 19:00 | Spring | TRUE | nonsummer
2023-04-05 19:00 | 2023-04-05 20:00 | Spring | TRUE | nonsummer
2023-04-05 20:00 | 2023-04-05 21:00 | Spring | TRUE | nonsummer
2023-04-05 21:00 | 2023-04-05 22:00 | Spring | TRUE | nonsummer
2023-04-05 22:00 | 2023-04-05 23:00 | Spring | FALSE | nonsummer
2023-04-05 23:00 | 2023-04-06 | Spring | FALSE | nonsummer
2023-04-06 | 2023-04-06 01:00 | Spring | FALSE | nonsummer
2023-04-06 01:00 | 2023-04-06 02:00 | Spring | FALSE | nonsummer
2023-04-06 02:00 | 2023-04-06 03:00 | Spring | FALSE | nonsummer
2023-04-06 03:00 | 2023-04-06 04:00 | Spring | FALSE | nonsummer
2023-04-06 04:00 | 2023-04-06 05:00 | Spring | FALSE | nonsummer
2023-04-06 05:00 | 2023-04-06 06:00 | Spring | FALSE | nonsummer
2023-04-06 06:00 | 2023-04-06 07:00 | Spring | FALSE | nonsummer
2023-04-06 07:00 | 2023-04-06 08:00 | Spring | FALSE | nonsummer
2023-04-06 08:00 | 2023-04-06 09:00 | Spring | FALSE | nonsummer
2023-04-06 09:00 | 2023-04-06 10:00 | Spring | FALSE | nonsummer
2023-04-06 10:00 | 2023-04-06 11:00 | Spring | FALSE | nonsummer
2023-04-06 11:00 | 2023-04-06 12:00 | Spring | FALSE | nonsummer
2023-04-06 12:00 | 2023-04-06 13:00 | Spring | FALSE | nonsummer
2023-04-06 13:00 | 2023-04-06 14:00 | Spring | FALSE | nonsummer
2023-04-06 14:00 | 2023-04-06 15:00 | Spring | FALSE | nonsummer
2023-04-06 15:00 | 2023-04-06 16:00 | Spring | FALSE | nonsummer
2023-04-06 16:00 | 2023-04-06 17:00 | Spring | FALSE | nonsummer
2023-04-06 17:00 | 2023-04-06 18:00 | Spring | TRUE | nonsummer
2023-04-06 18:00 | 2023-04-06 19:00 | Spring | TRUE | nonsummer
2023-04-06 19:00 | 2023-04-06 20:00 | Spring | TRUE | nonsummer
2023-04-06 20:00 | 2023-04-06 21:00 | Spring | TRUE | nonsummer
2023-04-06 21:00 | 2023-04-06 22:00 | Spring | TRUE | nonsummer
2023-04-06 22:00 | 2023-04-06 23:00 | Spring | FALSE | nonsummer
2023-04-06 23:00 | 2023-04-07 | Spring | FALSE | nonsummer
2023-04-07 | 2023-04-07 01:00 | Spring | FALSE | nonsummer
2023-04-07 01:00 | 2023-04-07 02:00 | Spring | FALSE | nonsummer
2023-04-07 02:00 | 2023-04-07 03:00 | Spring | FALSE | nonsummer
2023-04-07 03:00 | 2023-04-07 04:00 | Spring | FALSE | nonsummer
2023-04-07 04:00 | 2023-04-07 05:00 | Spring | FALSE | nonsummer
2023-04-07 05:00 | 2023-04-07 06:00 | Spring | FALSE | nonsummer
2023-04-07 06:00 | 2023-04-07 07:00 | Spring | FALSE | nonsummer
2023-04-07 07:00 | 2023-04-07 08:00 | Spring | FALSE | nonsummer
2023-04-07 08:00 | 2023-04-07 09:00 | Spring | FALSE | nonsummer
2023-04-07 09:00 | 2023-04-07 10:00 | Spring | FALSE | nonsummer
2023-04-07 10:00 | 2023-04-07 11:00 | Spring | FALSE | nonsummer
2023-04-07 11:00 | 2023-04-07 12:00 | Spring | FALSE | nonsummer
2023-04-07 12:00 | 2023-04-07 13:00 | Spring | FALSE | nonsummer
2023-04-07 13:00 | 2023-04-07 14:00 | Spring | FALSE | nonsummer
2023-04-07 14:00 | 2023-04-07 15:00 | Spring | FALSE | nonsummer
2023-04-07 15:00 | 2023-04-07 16:00 | Spring | FALSE | nonsummer
2023-04-07 16:00 | 2023-04-07 17:00 | Spring | FALSE | nonsummer
2023-04-07 17:00 | 2023-04-07 18:00 | Spring | TRUE | nonsummer
2023-04-07 18:00 | 2023-04-07 19:00 | Spring | TRUE | nonsummer
2023-04-07 19:00 | 2023-04-07 20:00 | Spring | TRUE | nonsummer
2023-04-07 20:00 | 2023-04-07 21:00 | Spring | TRUE | nonsummer
2023-04-07 21:00 | 2023-04-07 22:00 | Spring | TRUE | nonsummer
2023-04-07 22:00 | 2023-04-07 23:00 | Spring | FALSE | nonsummer
2023-04-07 23:00 | 2023-04-08 | Spring | FALSE | nonsummer
2023-04-08 | 2023-04-08 01:00 | Spring | FALSE | nonsummer
2023-04-08 01:00 | 2023-04-08 02:00 | Spring | FALSE | nonsummer
2023-04-08 02:00 | 2023-04-08 03:00 | Spring | FALSE | nonsummer
2023-04-08 03:00 | 2023-04-08 04:00 | Spring | FALSE | nonsummer
2023-04-08 04:00 | 2023-04-08 05:00 | Spring | FALSE | nonsummer
2023-04-08 05:00 | 2023-04-08 06:00 | Spring | FALSE | nonsummer
2023-04-08 06:00 | 2023-04-08 07:00 | Spring | FALSE | nonsummer
2023-04-08 07:00 | 2023-04-08 08:00 | Spring | FALSE | nonsummer
2023-04-08 08:00 | 2023-04-08 09:00 | Spring | FALSE | nonsummer
2023-04-08 09:00 | 2023-04-08 10:00 | Spring | FALSE | nonsummer
2023-04-08 10:00 | 2023-04-08 11:00 | Spring | FALSE | nonsummer
2023-04-08 11:00 | 2023-04-08 12:00 | Spring | FALSE | nonsummer
2023-04-08 12:00 | 2023-04-08 13:00 | Spring | FALSE | nonsummer
2023-04-08 13:00 | 2023-04-08 14:00 | Spring | FALSE | nonsummer
2023-04-08 14:00 | 2023-04-08 15:00 | Spring | FALSE | nonsummer
2023-04-08 15:00 | 2023-04-08 16:00 | Spring | FALSE | nonsummer
2023-04-08 16:00 | 2023-04-08 17:00 | Spring | FALSE | nonsummer
2023-04-08 17:00 | 2023-04-08 18:00 | Spring | TRUE | nonsummer
2023-04-08 18:00 | 2023-04-08 19:00 | Spring | TRUE | nonsummer
2023-04-08 19:00 | 2023-04-08 20:00 | Spring | TRUE | nonsummer
2023-04-08 20:00 | 2023-04-08 21:00 | Spring | TRUE | nonsummer
2023-04-08 21:00 | 2023-04-08 22:00 | Spring | TRUE | nonsummer
2023-04-08 22:00 | 2023-04-08 23:00 | Spring | FALSE | nonsummer
2023-04-08 23:00 | 2023-04-09 | Spring | FALSE | nonsummer
2023-04-09 | 2023-04-09 01:00 | Spring | FALSE | nonsummer
2023-04-09 01:00 | 2023-04-09 02:00 | Spring | FALSE | nonsummer
2023-04-09 02:00 | 2023-04-09 03:00 | Spring | FALSE | nonsummer
2023-04-09 03:00 | 2023-04-09 04:00 | Spring | FALSE | nonsummer
2023-04-09 04:00 | 2023-04-09 05:00 | Spring | FALSE | nonsummer
2023-04-09 05:00 | 2023-04-09 06:00 | Spring | FALSE | nonsummer
2023-04-09 06:00 | 2023-04-09 07:00 | Spring | FALSE | nonsummer
2023-04-09 07:00 | 2023-04-09 08:00 | Spring | FALSE | nonsummer
2023-04-09 08:00 | 2023-04-09 09:00 | Spring | FALSE | nonsummer
2023-04-09 09:00 | 2023-04-09 10:00 | Spring | FALSE | nonsummer
2023-04-09 10:00 | 2023-04-09 11:00 | Spring | FALSE | nonsummer
2023-04-09 11:00 | 2023-04-09 12:00 | Spring | FALSE | nonsummer
2023-04-09 12:00 | 2023-04-09 13:00 | Spring | FALSE | nonsummer
2023-04-09 13:00 | 2023-04-09 14:00 | Spring | FALSE | nonsummer
2023-04-09 14:00 | 2023-04-09 15:00 | Spring | FALSE | nonsummer
2023-04-09 15:00 | 2023-04-09 16:00 | Spring | FALSE | nonsummer
2023-04-09 16:00 | 2023-04-09 17:00 | Spring | FALSE | nonsummer
2023-04-09 17:00 | 2023-04-09 18:00 | Spring | TRUE | nonsummer
2023-04-09 18:00 | 2023-04-09 19:00 | Spring | TRUE | nonsummer
2023-04-09 19:00 | 2023-04-09 20:00 | Spring | TRUE | nonsummer
2023-04-09 20:00 | 2023-04-09 21:00 | Spring | TRUE | nonsummer
2023-04-09 21:00 | 2023-04-09 22:00 | Spring | TRUE | nonsummer
2023-04-09 22:00 | 2023-04-09 23:00 | Spring | FALSE | nonsummer
2023-04-09 23:00 | 2023-04-10 | Spring | FALSE | nonsummer
2023-04-10 | 2023-04-10 01:00 | Spring | FALSE | nonsummer
2023-04-10 01:00 | 2023-04-10 02:00 | Spring | FALSE | nonsummer
2023-04-10 02:00 | 2023-04-10 03:00 | Spring | FALSE | nonsummer
2023-04-10 03:00 | 2023-04-10 04:00 | Spring | FALSE | nonsummer
2023-04-10 04:00 | 2023-04-10 05:00 | Spring | FALSE | nonsummer
2023-04-10 05:00 | 2023-04-10 06:00 | Spring | FALSE | nonsummer
2023-04-10 06:00 | 2023-04-10 07:00 | Spring | FALSE | nonsummer
2023-04-10 07:00 | 2023-04-10 08:00 | Spring | FALSE | nonsummer
2023-04-10 08:00 | 2023-04-10 09:00 | Spring | FALSE | nonsummer
2023-04-10 09:00 | 2023-04-10 10:00 | Spring | FALSE | nonsummer
2023-04-10 10:00 | 2023-04-10 11:00 | Spring | FALSE | nonsummer
2023-04-10 11:00 | 2023-04-10 12:00 | Spring | FALSE | nonsummer
2023-04-10 12:00 | 2023-04-10 13:00 | Spring | FALSE | nonsummer
2023-04-10 13:00 | 2023-04-10 14:00 | Spring | FALSE | nonsummer
2023-04-10 14:00 | 2023-04-10 15:00 | Spring | FALSE | nonsummer
2023-04-10 15:00 | 2023-04-10 16:00 | Spring | FALSE | nonsummer
2023-04-10 16:00 | 2023-04-10 17:00 | Spring | FALSE | nonsummer
2023-04-10 17:00 | 2023-04-10 18:00 | Spring | TRUE | nonsummer
2023-04-10 18:00 | 2023-04-10 19:00 | Spring | TRUE | nonsummer
2023-04-10 19:00 | 2023-04-10 20:00 | Spring | TRUE | nonsummer
2023-04-10 20:00 | 2023-04-10 21:00 | Spring | TRUE | nonsummer
2023-04-10 21:00 | 2023-04-10 22:00 | Spring | TRUE | nonsummer
2023-04-10 22:00 | 2023-04-10 23:00 | Spring | FALSE | nonsummer
2023-04-10 23:00 | 2023-04-11 | Spring | FALSE | nonsummer
2023-04-11 | 2023-04-11 01:00 | Spring | FALSE | nonsummer
2023-04-11 01:00 | 2023-04-11 02:00 | Spring | FALSE | nonsummer
2023-04-11 02:00 | 2023-04-11 03:00 | Spring | FALSE | nonsummer
2023-04-11 03:00 | 2023-04-11 04:00 | Spring | FALSE | nonsummer
2023-04-11 04:00 | 2023-04-11 05:00 | Spring | FALSE | nonsummer
2023-04-11 05:00 | 2023-04-11 06:00 | Spring | FALSE | nonsummer
2023-04-11 06:00 | 2023-04-11 07:00 | Spring | FALSE | nonsummer
2023-04-11 07:00 | 2023-04-11 08:00 | Spring | FALSE | nonsummer
2023-04-11 08:00 | 2023-04-11 09:00 | Spring | FALSE | nonsummer
2023-04-11 09:00 | 2023-04-11 10:00 | Spring | FALSE | nonsummer
2023-04-11 10:00 | 2023-04-11 11:00 | Spring | FALSE | nonsummer
2023-04-11 11:00 | 2023-04-11 12:00 | Spring | FALSE | nonsummer
2023-04-11 12:00 | 2023-04-11 13:00 | Spring | FALSE | nonsummer
2023-04-11 13:00 | 2023-04-11 14:00 | Spring | FALSE | nonsummer
2023-04-11 14:00 | 2023-04-11 15:00 | Spring | FALSE | nonsummer
2023-04-11 15:00 | 2023-04-11 16:00 | Spring | FALSE | nonsummer
2023-04-11 16:00 | 2023-04-11 17:00 | Spring | FALSE | nonsummer
2023-04-11 17:00 | 2023-04-11 18:00 | Spring | TRUE | nonsummer
2023-04-11 18:00 | 2023-04-11 19:00 | Spring | TRUE | nonsummer
2023-04-11 19:00 | 2023-04-11 20:00 | Spring | TRUE | nonsummer
2023-04-11 20:00 | 2023-04-11 21:00 | Spring | TRUE | nonsummer
2023-04-11 21:00 | 2023-04-11 22:00 | Spring | TRUE | nonsummer
2023-04-11 22:00 | 2023-04-11 23:00 | Spring | FALSE | nonsummer
2023-04-11 23:00 | 2023-04-12 | Spring | FALSE | nonsummer
2023-04-12 | 2023-04-12 01:00 | Spring | FALSE | nonsummer
2023-04-12 01:00 | 2023-04-12 02:00 | Spring | FALSE | nonsummer
2023-04-12 02:00 | 2023-04-12 03:00 | Spring | FALSE | nonsummer
2023-04-12 03:00 | 2023-04-12 04:00 | Spring | FALSE | nonsummer
2023-04-12 04:00 | 2023-04-12 05:00 | Spring | FALSE | nonsummer
2023-04-12 05:00 | 2023-04-12 06:00 | Spring | FALSE | nonsummer
2023-04-12 06:00 | 2023-04-12 07:00 | Spring | FALSE | nonsummer
2023-04-12 07:00 | 2023-04-12 08:00 | Spring | FALSE | nonsummer
2023-04-12 08:00 | 2023-04-12 09:00 | Spring | FALSE | nonsummer
2023-04-12 09:00 | 2023-04-12 10:00 | Spring | FALSE | nonsummer
2023-04-12 10:00 | 2023-04-12 11:00 | Spring | FALSE | nonsummer
2023-04-12 11:00 | 2023-04-12 12:00 | Spring | FALSE | nonsummer
2023-04-12 12:00 | 2023-04-12 13:00 | Spring | FALSE | nonsummer
2023-04-12 13:00 | 2023-04-12 14:00 | Spring | FALSE | nonsummer
2023-04-12 14:00 | 2023-04-12 15:00 | Spring | FALSE | nonsummer
2023-04-12 15:00 | 2023-04-12 16:00 | Spring | FALSE | nonsummer
2023-04-12 16:00 | 2023-04-12 17:00 | Spring | FALSE | nonsummer
2023-04-12 17:00 | 2023-04-12 18:00 | Spring | TRUE | nonsummer
2023-04-12 18:00 | 2023-04-12 19:00 | Spring | TRUE | nonsummer
2023-04-12 19:00 | 2023-04-12 20:00 | Spring | TRUE | nonsummer
2023-04-12 20:00 | 2023-04-12 21:00 | Spring | TRUE | nonsummer
2023-04-12 21:00 | 2023-04-12 22:00 | Spring | TRUE | nonsummer
2023-04-12 22:00 | 2023-04-12 23:00 | Spring | FALSE | nonsummer
2023-04-12 23:00 | 2023-04-13 | Spring | FALSE | nonsummer
2023-04-13 | 2023-04-13 01:00 | Spring | FALSE | nonsummer
2023-04-13 01:00 | 2023-04-13 02:00 | Spring | FALSE | nonsummer
2023-04-13 02:00 | 2023-04-13 03:00 | Spring | FALSE | nonsummer
2023-04-13 03:00 | 2023-04-13 04:00 | Spring | FALSE | nonsummer
2023-04-13 04:00 | 2023-04-13 05:00 | Spring | FALSE | nonsummer
2023-04-13 05:00 | 2023-04-13 06:00 | Spring | FALSE | nonsummer
2023-04-13 06:00 | 2023-04-13 07:00 | Spring | FALSE | nonsummer
2023-04-13 07:00 | 2023-04-13 08:00 | Spring | FALSE | nonsummer
2023-04-13 08:00 | 2023-04-13 09:00 | Spring | FALSE | nonsummer
2023-04-13 09:00 | 2023-04-13 10:00 | Spring | FALSE | nonsummer
2023-04-13 10:00 | 2023-04-13 11:00 | Spring | FALSE | nonsummer
2023-04-13 11:00 | 2023-04-13 12:00 | Spring | FALSE | nonsummer
2023-04-13 12:00 | 2023-04-13 13:00 | Spring | FALSE | nonsummer
2023-04-13 13:00 | 2023-04-13 14:00 | Spring | FALSE | nonsummer
2023-04-13 14:00 | 2023-04-13 15:00 | Spring | FALSE | nonsummer
2023-04-13 15:00 | 2023-04-13 16:00 | Spring | FALSE | nonsummer
2023-04-13 16:00 | 2023-04-13 17:00 | Spring | FALSE | nonsummer
2023-04-13 17:00 | 2023-04-13 18:00 | Spring | TRUE | nonsummer
2023-04-13 18:00 | 2023-04-13 19:00 | Spring | TRUE | nonsummer
2023-04-13 19:00 | 2023-04-13 20:00 | Spring | TRUE | nonsummer
2023-04-13 20:00 | 2023-04-13 21:00 | Spring | TRUE | nonsummer
2023-04-13 21:00 | 2023-04-13 22:00 | Spring | TRUE | nonsummer
2023-04-13 22:00 | 2023-04-13 23:00 | Spring | FALSE | nonsummer
2023-04-13 23:00 | 2023-04-14 | Spring | FALSE | nonsummer
2023-04-14 | 2023-04-14 01:00 | Spring | FALSE | nonsummer
2023-04-14 01:00 | 2023-04-14 02:00 | Spring | FALSE | nonsummer
2023-04-14 02:00 | 2023-04-14 03:00 | Spring | FALSE | nonsummer
2023-04-14 03:00 | 2023-04-14 04:00 | Spring | FALSE | nonsummer
2023-04-14 04:00 | 2023-04-14 05:00 | Spring | FALSE | nonsummer
2023-04-14 05:00 | 2023-04-14 06:00 | Spring | FALSE | nonsummer
2023-04-14 06:00 | 2023-04-14 07:00 | Spring | FALSE | nonsummer
2023-04-14 07:00 | 2023-04-14 08:00 | Spring | FALSE | nonsummer
2023-04-14 08:00 | 2023-04-14 09:00 | Spring | FALSE | nonsummer
2023-04-14 09:00 | 2023-04-14 10:00 | Spring | FALSE | nonsummer
2023-04-14 10:00 | 2023-04-14 11:00 | Spring | FALSE | nonsummer
2023-04-14 11:00 | 2023-04-14 12:00 | Spring | FALSE | nonsummer
2023-04-14 12:00 | 2023-04-14 13:00 | Spring | FALSE | nonsummer
2023-04-14 13:00 | 2023-04-14 14:00 | Spring | FALSE | nonsummer
2023-04-14 14:00 | 2023-04-14 15:00 | Spring | FALSE | nonsummer
2023-04-14 15:00 | 2023-04-14 16:00 | Spring | FALSE | nonsummer
2023-04-14 16:00 | 2023-04-14 17:00 | Spring | FALSE | nonsummer
2023-04-14 17:00 | 2023-04-14 18:00 | Spring | TRUE | nonsummer
2023-04-14 18:00 | 2023-04-14 19:00 | Spring | TRUE | nonsummer
2023-04-14 19:00 | 2023-04-14 20:00 | Spring | TRUE | nonsummer
2023-04-14 20:00 | 2023-04-14 21:00 | Spring | TRUE | nonsummer
2023-04-14 21:00 | 2023-04-14 22:00 | Spring | TRUE | nonsummer
2023-04-14 22:00 | 2023-04-14 23:00 | Spring | FALSE | nonsummer
2023-04-14 23:00 | 2023-04-15 | Spring | FALSE | nonsummer
2023-04-15 | 2023-04-15 01:00 | Spring | FALSE | nonsummer
2023-04-15 01:00 | 2023-04-15 02:00 | Spring | FALSE | nonsummer
2023-04-15 02:00 | 2023-04-15 03:00 | Spring | FALSE | nonsummer
2023-04-15 03:00 | 2023-04-15 04:00 | Spring | FALSE | nonsummer
2023-04-15 04:00 | 2023-04-15 05:00 | Spring | FALSE | nonsummer
2023-04-15 05:00 | 2023-04-15 06:00 | Spring | FALSE | nonsummer
2023-04-15 06:00 | 2023-04-15 07:00 | Spring | FALSE | nonsummer
2023-04-15 07:00 | 2023-04-15 08:00 | Spring | FALSE | nonsummer
2023-04-15 08:00 | 2023-04-15 09:00 | Spring | FALSE | nonsummer
2023-04-15 09:00 | 2023-04-15 10:00 | Spring | FALSE | nonsummer
2023-04-15 10:00 | 2023-04-15 11:00 | Spring | FALSE | nonsummer
2023-04-15 11:00 | 2023-04-15 12:00 | Spring | FALSE | nonsummer
2023-04-15 12:00 | 2023-04-15 13:00 | Spring | FALSE | nonsummer
2023-04-15 13:00 | 2023-04-15 14:00 | Spring | FALSE | nonsummer
2023-04-15 14:00 | 2023-04-15 15:00 | Spring | FALSE | nonsummer
2023-04-15 15:00 | 2023-04-15 16:00 | Spring | FALSE | nonsummer
2023-04-15 16:00 | 2023-04-15 17:00 | Spring | FALSE | nonsummer
2023-04-15 17:00 | 2023-04-15 18:00 | Spring | TRUE | nonsummer
2023-04-15 18:00 | 2023-04-15 19:00 | Spring | TRUE | nonsummer
2023-04-15 19:00 | 2023-04-15 20:00 | Spring | TRUE | nonsummer
2023-04-15 20:00 | 2023-04-15 21:00 | Spring | TRUE | nonsummer
2023-04-15 21:00 | 2023-04-15 22:00 | Spring | TRUE | nonsummer
2023-04-15 22:00 | 2023-04-15 23:00 | Spring | FALSE | nonsummer
2023-04-15 23:00 | 2023-04-16 | Spring | FALSE | nonsummer
2023-04-16 | 2023-04-16 01:00 | Spring | FALSE | nonsummer
2023-04-16 01:00 | 2023-04-16 02:00 | Spring | FALSE | nonsummer
2023-04-16 02:00 | 2023-04-16 03:00 | Spring | FALSE | nonsummer
2023-04-16 03:00 | 2023-04-16 04:00 | Spring | FALSE | nonsummer
2023-04-16 04:00 | 2023-04-16 05:00 | Spring | FALSE | nonsummer
2023-04-16 05:00 | 2023-04-16 06:00 | Spring | FALSE | nonsummer
2023-04-16 06:00 | 2023-04-16 07:00 | Spring | FALSE | nonsummer
2023-04-16 07:00 | 2023-04-16 08:00 | Spring | FALSE | nonsummer
2023-04-16 08:00 | 2023-04-16 09:00 | Spring | FALSE | nonsummer
2023-04-16 09:00 | 2023-04-16 10:00 | Spring | FALSE | nonsummer
2023-04-16 10:00 | 2023-04-16 11:00 | Spring | FALSE | nonsummer
2023-04-16 11:00 | 2023-04-16 12:00 | Spring | FALSE | nonsummer
2023-04-16 12:00 | 2023-04-16 13:00 | Spring | FALSE | nonsummer
2023-04-16 13:00 | 2023-04-16 14:00 | Spring | FALSE | nonsummer
2023-04-16 14:00 | 2023-04-16 15:00 | Spring | FALSE | nonsummer
2023-04-16 15:00 | 2023-04-16 16:00 | Spring | FALSE | nonsummer
2023-04-16 16:00 | 2023-04-16 17:00 | Spring | FALSE | nonsummer
2023-04-16 17:00 | 2023-04-16 18:00 | Spring | TRUE | nonsummer
2023-04-16 18:00 | 2023-04-16 19:00 | Spring | TRUE | nonsummer
2023-04-16 19:00 | 2023-04-16 20:00 | Spring | TRUE | nonsummer
2023-04-16 20:00 | 2023-04-16 21:00 | Spring | TRUE | nonsummer
2023-04-16 21:00 | 2023-04-16 22:00 | Spring | TRUE | nonsummer
2023-04-16 22:00 | 2023-04-16 23:00 | Spring | FALSE | nonsummer
2023-04-16 23:00 | 2023-04-17 | Spring | FALSE | nonsummer
2023-04-17 | 2023-04-17 01:00 | Spring | FALSE | nonsummer
2023-04-17 01:00 | 2023-04-17 02:00 | Spring | FALSE | nonsummer
2023-04-17 02:00 | 2023-04-17 03:00 | Spring | FALSE | nonsummer
2023-04-17 03:00 | 2023-04-17 04:00 | Spring | FALSE | nonsummer
2023-04-17 04:00 | 2023-04-17 05:00 | Spring | FALSE | nonsummer
2023-04-17 05:00 | 2023-04-17 06:00 | Spring | FALSE | nonsummer
2023-04-17 06:00 | 2023-04-17 07:00 | Spring | FALSE | nonsummer
2023-04-17 07:00 | 2023-04-17 08:00 | Spring | FALSE | nonsummer
2023-04-17 08:00 | 2023-04-17 09:00 | Spring | FALSE | nonsummer
2023-04-17 09:00 | 2023-04-17 10:00 | Spring | FALSE | nonsummer
2023-04-17 10:00 | 2023-04-17 11:00 | Spring | FALSE | nonsummer
2023-04-17 11:00 | 2023-04-17 12:00 | Spring | FALSE | nonsummer
2023-04-17 12:00 | 2023-04-17 13:00 | Spring | FALSE | nonsummer
2023-04-17 13:00 | 2023-04-17 14:00 | Spring | FALSE | nonsummer
2023-04-17 14:00 | 2023-04-17 15:00 | Spring | FALSE | nonsummer
2023-04-17 15:00 | 2023-04-17 16:00 | Spring | FALSE | nonsummer
2023-04-17 16:00 | 2023-04-17 17:00 | Spring | FALSE | nonsummer
2023-04-17 17:00 | 2023-04-17 18:00 | Spring | TRUE | nonsummer
2023-04-17 18:00 | 2023-04-17 19:00 | Spring | TRUE | nonsummer
2023-04-17 19:00 | 2023-04-17 20:00 | Spring | TRUE | nonsummer
2023-04-17 20:00 | 2023-04-17 21:00 | Spring | TRUE | nonsummer
2023-04-17 21:00 | 2023-04-17 22:00 | Spring | TRUE | nonsummer
2023-04-17 22:00 | 2023-04-17 23:00 | Spring | FALSE | nonsummer
2023-04-17 23:00 | 2023-04-18 | Spring | FALSE | nonsummer
2023-04-18 | 2023-04-18 01:00 | Spring | FALSE | nonsummer
2023-04-18 01:00 | 2023-04-18 02:00 | Spring | FALSE | nonsummer
2023-04-18 02:00 | 2023-04-18 03:00 | Spring | FALSE | nonsummer
2023-04-18 03:00 | 2023-04-18 04:00 | Spring | FALSE | nonsummer
2023-04-18 04:00 | 2023-04-18 05:00 | Spring | FALSE | nonsummer
2023-04-18 05:00 | 2023-04-18 06:00 | Spring | FALSE | nonsummer
2023-04-18 06:00 | 2023-04-18 07:00 | Spring | FALSE | nonsummer
2023-04-18 07:00 | 2023-04-18 08:00 | Spring | FALSE | nonsummer
2023-04-18 08:00 | 2023-04-18 09:00 | Spring | FALSE | nonsummer
2023-04-18 09:00 | 2023-04-18 10:00 | Spring | FALSE | nonsummer
2023-04-18 10:00 | 2023-04-18 11:00 | Spring | FALSE | nonsummer
2023-04-18 11:00 | 2023-04-18 12:00 | Spring | FALSE | nonsummer
2023-04-18 12:00 | 2023-04-18 13:00 | Spring | FALSE | nonsummer
2023-04-18 13:00 | 2023-04-18 14:00 | Spring | FALSE | nonsummer
2023-04-18 14:00 | 2023-04-18 15:00 | Spring | FALSE | nonsummer
2023-04-18 15:00 | 2023-04-18 16:00 | Spring | FALSE | nonsummer
2023-04-18 16:00 | 2023-04-18 17:00 | Spring | FALSE | nonsummer
2023-04-18 17:00 | 2023-04-18 18:00 | Spring | TRUE | nonsummer
2023-04-18 18:00 | 2023-04-18 19:00 | Spring | TRUE | nonsummer
2023-04-18 19:00 | 2023-04-18 20:00 | Spring | TRUE | nonsummer
2023-04-18 20:00 | 2023-04-18 21:00 | Spring | TRUE | nonsummer
2023-04-18 21:00 | 2023-04-18 22:00 | Spring | TRUE | nonsummer
2023-04-18 22:00 | 2023-04-18 23:00 | Spring | FALSE | nonsummer
2023-04-18 23:00 | 2023-04-19 | Spring | FALSE | nonsummer
2023-04-19 | 2023-04-19 01:00 | Spring | FALSE | nonsummer
2023-04-19 01:00 | 2023-04-19 02:00 | Spring | FALSE | nonsummer
2023-04-19 02:00 | 2023-04-19 03:00 | Spring | FALSE | nonsummer
2023-04-19 03:00 | 2023-04-19 04:00 | Spring | FALSE | nonsummer
2023-04-19 04:00 | 2023-04-19 05:00 | Spring | FALSE | nonsummer
2023-04-19 05:00 | 2023-04-19 06:00 | Spring | FALSE | nonsummer
2023-04-19 06:00 | 2023-04-19 07:00 | Spring | FALSE | nonsummer
2023-04-19 07:00 | 2023-04-19 08:00 | Spring | FALSE | nonsummer
2023-04-19 08:00 | 2023-04-19 09:00 | Spring | FALSE | nonsummer
2023-04-19 09:00 | 2023-04-19 10:00 | Spring | FALSE | nonsummer
2023-04-19 10:00 | 2023-04-19 11:00 | Spring | FALSE | nonsummer
2023-04-19 11:00 | 2023-04-19 12:00 | Spring | FALSE | nonsummer
2023-04-19 12:00 | 2023-04-19 13:00 | Spring | FALSE | nonsummer
2023-04-19 13:00 | 2023-04-19 14:00 | Spring | FALSE | nonsummer
2023-04-19 14:00 | 2023-04-19 15:00 | Spring | FALSE | nonsummer
2023-04-19 15:00 | 2023-04-19 16:00 | Spring | FALSE | nonsummer
2023-04-19 16:00 | 2023-04-19 17:00 | Spring | FALSE | nonsummer
2023-04-19 17:00 | 2023-04-19 18:00 | Spring | TRUE | nonsummer
2023-04-19 18:00 | 2023-04-19 19:00 | Spring | TRUE | nonsummer
2023-04-19 19:00 | 2023-04-19 20:00 | Spring | TRUE | nonsummer
2023-04-19 20:00 | 2023-04-19 21:00 | Spring | TRUE | nonsummer
2023-04-19 21:00 | 2023-04-19 22:00 | Spring | TRUE | nonsummer
2023-04-19 22:00 | 2023-04-19 23:00 | Spring | FALSE | nonsummer
2023-04-19 23:00 | 2023-04-20 | Spring | FALSE | nonsummer
2023-04-20 | 2023-04-20 01:00 | Spring | FALSE | nonsummer
2023-04-20 01:00 | 2023-04-20 02:00 | Spring | FALSE | nonsummer
2023-04-20 02:00 | 2023-04-20 03:00 | Spring | FALSE | nonsummer
2023-04-20 03:00 | 2023-04-20 04:00 | Spring | FALSE | nonsummer
2023-04-20 04:00 | 2023-04-20 05:00 | Spring | FALSE | nonsummer
2023-04-20 05:00 | 2023-04-20 06:00 | Spring | FALSE | nonsummer
2023-04-20 06:00 | 2023-04-20 07:00 | Spring | FALSE | nonsummer
2023-04-20 07:00 | 2023-04-20 08:00 | Spring | FALSE | nonsummer
2023-04-20 08:00 | 2023-04-20 09:00 | Spring | FALSE | nonsummer
2023-04-20 09:00 | 2023-04-20 10:00 | Spring | FALSE | nonsummer
2023-04-20 10:00 | 2023-04-20 11:00 | Spring | FALSE | nonsummer
2023-04-20 11:00 | 2023-04-20 12:00 | Spring | FALSE | nonsummer
2023-04-20 12:00 | 2023-04-20 13:00 | Spring | FALSE | nonsummer
2023-04-20 13:00 | 2023-04-20 14:00 | Spring | FALSE | nonsummer
2023-04-20 14:00 | 2023-04-20 15:00 | Spring | FALSE | nonsummer
2023-04-20 15:00 | 2023-04-20 16:00 | Spring | FALSE | nonsummer
2023-04-20 16:00 | 2023-04-20 17:00 | Spring | FALSE | nonsummer
2023-04-20 17:00 | 2023-04-20 18:00 | Spring | TRUE | nonsummer
2023-04-20 18:00 | 2023-04-20 19:00 | Spring | TRUE | nonsummer
2023-04-20 19:00 | 2023-04-20 20:00 | Spring | TRUE | nonsummer
2023-04-20 20:00 | 2023-04-20 21:00 | Spring | TRUE | nonsummer
2023-04-20 21:00 | 2023-04-20 22:00 | Spring | TRUE | nonsummer
2023-04-20 22:00 | 2023-04-20 23:00 | Spring | FALSE | nonsummer
2023-04-20 23:00 | 2023-04-21 | Spring | FALSE | nonsummer
2023-04-21 | 2023-04-21 01:00 | Spring | FALSE | nonsummer
2023-04-21 01:00 | 2023-04-21 02:00 | Spring | FALSE | nonsummer
2023-04-21 02:00 | 2023-04-21 03:00 | Spring | FALSE | nonsummer
2023-04-21 03:00 | 2023-04-21 04:00 | Spring | FALSE | nonsummer
2023-04-21 04:00 | 2023-04-21 05:00 | Spring | FALSE | nonsummer
2023-04-21 05:00 | 2023-04-21 06:00 | Spring | FALSE | nonsummer
2023-04-21 06:00 | 2023-04-21 07:00 | Spring | FALSE | nonsummer
2023-04-21 07:00 | 2023-04-21 08:00 | Spring | FALSE | nonsummer
2023-04-21 08:00 | 2023-04-21 09:00 | Spring | FALSE | nonsummer
2023-04-21 09:00 | 2023-04-21 10:00 | Spring | FALSE | nonsummer
2023-04-21 10:00 | 2023-04-21 11:00 | Spring | FALSE | nonsummer
2023-04-21 11:00 | 2023-04-21 12:00 | Spring | FALSE | nonsummer
2023-04-21 12:00 | 2023-04-21 13:00 | Spring | FALSE | nonsummer
2023-04-21 13:00 | 2023-04-21 14:00 | Spring | FALSE | nonsummer
2023-04-21 14:00 | 2023-04-21 15:00 | Spring | FALSE | nonsummer
2023-04-21 15:00 | 2023-04-21 16:00 | Spring | FALSE | nonsummer
2023-04-21 16:00 | 2023-04-21 17:00 | Spring | FALSE | nonsummer
2023-04-21 17:00 | 2023-04-21 18:00 | Spring | TRUE | nonsummer
2023-04-21 18:00 | 2023-04-21 19:00 | Spring | TRUE | nonsummer
2023-04-21 19:00 | 2023-04-21 20:00 | Spring | TRUE | nonsummer
2023-04-21 20:00 | 2023-04-21 21:00 | Spring | TRUE | nonsummer
2023-04-21 21:00 | 2023-04-21 22:00 | Spring | TRUE | nonsummer
2023-04-21 22:00 | 2023-04-21 23:00 | Spring | FALSE | nonsummer
2023-04-21 23:00 | 2023-04-22 | Spring | FALSE | nonsummer
2023-04-22 | 2023-04-22 01:00 | Spring | FALSE | nonsummer
2023-04-22 01:00 | 2023-04-22 02:00 | Spring | FALSE | nonsummer
2023-04-22 02:00 | 2023-04-22 03:00 | Spring | FALSE | nonsummer
2023-04-22 03:00 | 2023-04-22 04:00 | Spring | FALSE | nonsummer
2023-04-22 04:00 | 2023-04-22 05:00 | Spring | FALSE | nonsummer
2023-04-22 05:00 | 2023-04-22 06:00 | Spring | FALSE | nonsummer
2023-04-22 06:00 | 2023-04-22 07:00 | Spring | FALSE | nonsummer
2023-04-22 07:00 | 2023-04-22 08:00 | Spring | FALSE | nonsummer
2023-04-22 08:00 | 2023-04-22 09:00 | Spring | FALSE | nonsummer
2023-04-22 09:00 | 2023-04-22 10:00 | Spring | FALSE | nonsummer
2023-04-22 10:00 | 2023-04-22 11:00 | Spring | FALSE | nonsummer
2023-04-22 11:00 | 2023-04-22 12:00 | Spring | FALSE | nonsummer
2023-04-22 12:00 | 2023-04-22 13:00 | Spring | FALSE | nonsummer
2023-04-22 13:00 | 2023-04-22 14:00 | Spring | FALSE | nonsummer
2023-04-22 14:00 | 2023-04-22 15:00 | Spring | FALSE | nonsummer
2023-04-22 15:00 | 2023-04-22 16:00 | Spring | FALSE | nonsummer
2023-04-22 16:00 | 2023-04-22 17:00 | Spring | FALSE | nonsummer
2023-04-22 17:00 | 2023-04-22 18:00 | Spring | TRUE | nonsummer
2023-04-22 18:00 | 2023-04-22 19:00 | Spring | TRUE | nonsummer
2023-04-22 19:00 | 2023-04-22 20:00 | Spring | TRUE | nonsummer
2023-04-22 20:00 | 2023-04-22 21:00 | Spring | TRUE | nonsummer
2023-04-22 21:00 | 2023-04-22 22:00 | Spring | TRUE | nonsummer
2023-04-22 22:00 | 2023-04-22 23:00 | Spring | FALSE | nonsummer
2023-04-22 23:00 | 2023-04-23 | Spring | FALSE | nonsummer
2023-04-23 | 2023-04-23 01:00 | Spring | FALSE | nonsummer
2023-04-23 01:00 | 2023-04-23 02:00 | Spring | FALSE | nonsummer
2023-04-23 02:00 | 2023-04-23 03:00 | Spring | FALSE | nonsummer
2023-04-23 03:00 | 2023-04-23 04:00 | Spring | FALSE | nonsummer
2023-04-23 04:00 | 2023-04-23 05:00 | Spring | FALSE | nonsummer
2023-04-23 05:00 | 2023-04-23 06:00 | Spring | FALSE | nonsummer
2023-04-23 06:00 | 2023-04-23 07:00 | Spring | FALSE | nonsummer
2023-04-23 07:00 | 2023-04-23 08:00 | Spring | FALSE | nonsummer
2023-04-23 08:00 | 2023-04-23 09:00 | Spring | FALSE | nonsummer
2023-04-23 09:00 | 2023-04-23 10:00 | Spring | FALSE | nonsummer
2023-04-23 10:00 | 2023-04-23 11:00 | Spring | FALSE | nonsummer
2023-04-23 11:00 | 2023-04-23 12:00 | Spring | FALSE | nonsummer
2023-04-23 12:00 | 2023-04-23 13:00 | Spring | FALSE | nonsummer
2023-04-23 13:00 | 2023-04-23 14:00 | Spring | FALSE | nonsummer
2023-04-23 14:00 | 2023-04-23 15:00 | Spring | FALSE | nonsummer
2023-04-23 15:00 | 2023-04-23 16:00 | Spring | FALSE | nonsummer
2023-04-23 16:00 | 2023-04-23 17:00 | Spring | FALSE | nonsummer
2023-04-23 17:00 | 2023-04-23 18:00 | Spring | TRUE | nonsummer
2023-04-23 18:00 | 2023-04-23 19:00 | Spring | TRUE | nonsummer
2023-04-23 19:00 | 2023-04-23 20:00 | Spring | TRUE | nonsummer
2023-04-23 20:00 | 2023-04-23 21:00 | Spring | TRUE | nonsummer
2023-04-23 21:00 | 2023-04-23 22:00 | Spring | TRUE | nonsummer
2023-04-23 22:00 | 2023-04-23 23:00 | Spring | FALSE | nonsummer
2023-04-23 23:00 | 2023-04-24 | Spring | FALSE | nonsummer
2023-04-24 | 2023-04-24 01:00 | Spring | FALSE | nonsummer
2023-04-24 01:00 | 2023-04-24 02:00 | Spring | FALSE | nonsummer
2023-04-24 02:00 | 2023-04-24 03:00 | Spring | FALSE | nonsummer
2023-04-24 03:00 | 2023-04-24 04:00 | Spring | FALSE | nonsummer
2023-04-24 04:00 | 2023-04-24 05:00 | Spring | FALSE | nonsummer
2023-04-24 05:00 | 2023-04-24 06:00 | Spring | FALSE | nonsummer
2023-04-24 06:00 | 2023-04-24 07:00 | Spring | FALSE | nonsummer
2023-04-24 07:00 | 2023-04-24 08:00 | Spring | FALSE | nonsummer
2023-04-24 08:00 | 2023-04-24 09:00 | Spring | FALSE | nonsummer
2023-04-24 09:00 | 2023-04-24 10:00 | Spring | FALSE | nonsummer
2023-04-24 10:00 | 2023-04-24 11:00 | Spring | FALSE | nonsummer
2023-04-24 11:00 | 2023-04-24 12:00 | Spring | FALSE | nonsummer
2023-04-24 12:00 | 2023-04-24 13:00 | Spring | FALSE | nonsummer
2023-04-24 13:00 | 2023-04-24 14:00 | Spring | FALSE | nonsummer
2023-04-24 14:00 | 2023-04-24 15:00 | Spring | FALSE | nonsummer
2023-04-24 15:00 | 2023-04-24 16:00 | Spring | FALSE | nonsummer
2023-04-24 16:00 | 2023-04-24 17:00 | Spring | FALSE | nonsummer
2023-04-24 17:00 | 2023-04-24 18:00 | Spring | TRUE | nonsummer
2023-04-24 18:00 | 2023-04-24 19:00 | Spring | TRUE | nonsummer
2023-04-24 19:00 | 2023-04-24 20:00 | Spring | TRUE | nonsummer
2023-04-24 20:00 | 2023-04-24 21:00 | Spring | TRUE | nonsummer
2023-04-24 21:00 | 2023-04-24 22:00 | Spring | TRUE | nonsummer
2023-04-24 22:00 | 2023-04-24 23:00 | Spring | FALSE | nonsummer
2023-04-24 23:00 | 2023-04-25 | Spring | FALSE | nonsummer
2023-04-25 | 2023-04-25 01:00 | Spring | FALSE | nonsummer
2023-04-25 01:00 | 2023-04-25 02:00 | Spring | FALSE | nonsummer
2023-04-25 02:00 | 2023-04-25 03:00 | Spring | FALSE | nonsummer
2023-04-25 03:00 | 2023-04-25 04:00 | Spring | FALSE | nonsummer
2023-04-25 04:00 | 2023-04-25 05:00 | Spring | FALSE | nonsummer
2023-04-25 05:00 | 2023-04-25 06:00 | Spring | FALSE | nonsummer
2023-04-25 06:00 | 2023-04-25 07:00 | Spring | FALSE | nonsummer
2023-04-25 07:00 | 2023-04-25 08:00 | Spring | FALSE | nonsummer
2023-04-25 08:00 | 2023-04-25 09:00 | Spring | FALSE | nonsummer
2023-04-25 09:00 | 2023-04-25 10:00 | Spring | FALSE | nonsummer
2023-04-25 10:00 | 2023-04-25 11:00 | Spring | FALSE | nonsummer
2023-04-25 11:00 | 2023-04-25 12:00 | Spring | FALSE | nonsummer
2023-04-25 12:00 | 2023-04-25 13:00 | Spring | FALSE | nonsummer
2023-04-25 13:00 | 2023-04-25 14:00 | Spring | FALSE | nonsummer
2023-04-25 14:00 | 2023-04-25 15:00 | Spring | FALSE | nonsummer
2023-04-25 15:00 | 2023-04-25 16:00 | Spring | FALSE | nonsummer
2023-04-25 16:00 | 2023-04-25 17:00 | Spring | FALSE | nonsummer
2023-04-25 17:00 | 2023-04-25 18:00 | Spring | TRUE | nonsummer
2023-04-25 18:00 | 2023-04-25 19:00 | Spring | TRUE | nonsummer
2023-04-25 19:00 | 2023-04-25 20:00 | Spring | TRUE | nonsummer
2023-04-25 20:00 | 2023-04-25 21:00 | Spring | TRUE | nonsummer
2023-04-25 21:00 | 2023-04-25 22:00 | Spring | TRUE | nonsummer
2023-04-25 22:00 | 2023-04-25 23:00 | Spring | FALSE | nonsummer
2023-04-25 23:00 | 2023-04-26 | Spring | FALSE | nonsummer
2023-04-26 | 2023-04-26 01:00 | Spring | FALSE | nonsummer
2023-04-26 01:00 | 2023-04-26 02:00 | Spring | FALSE | nonsummer
2023-04-26 02:00 | 2023-04-26 03:00 | Spring | FALSE | nonsummer
2023-04-26 03:00 | 2023-04-26 04:00 | Spring | FALSE | nonsummer
2023-04-26 04:00 | 2023-04-26 05:00 | Spring | FALSE | nonsummer
2023-04-26 05:00 | 2023-04-26 06:00 | Spring | FALSE | nonsummer
2023-04-26 06:00 | 2023-04-26 07:00 | Spring | FALSE | nonsummer
2023-04-26 07:00 | 2023-04-26 08:00 | Spring | FALSE | nonsummer
2023-04-26 08:00 | 2023-04-26 09:00 | Spring | FALSE | nonsummer
2023-04-26 09:00 | 2023-04-26 10:00 | Spring | FALSE | nonsummer
2023-04-26 10:00 | 2023-04-26 11:00 | Spring | FALSE | nonsummer
2023-04-26 11:00 | 2023-04-26 12:00 | Spring | FALSE | nonsummer
2023-04-26 12:00 | 2023-04-26 13:00 | Spring | FALSE | nonsummer
2023-04-26 13:00 | 2023-04-26 14:00 | Spring | FALSE | nonsummer
2023-04-26 14:00 | 2023-04-26 15:00 | Spring | FALSE | nonsummer
2023-04-26 15:00 | 2023-04-26 16:00 | Spring | FALSE | nonsummer
2023-04-26 16:00 | 2023-04-26 17:00 | Spring | FALSE | nonsummer
2023-04-26 17:00 | 2023-04-26 18:00 | Spring | TRUE | nonsummer
2023-04-26 18:00 | 2023-04-26 19:00 | Spring | TRUE | nonsummer
2023-04-26 19:00 | 2023-04-26 20:00 | Spring | TRUE | nonsummer
2023-04-26 20:00 | 2023-04-26 21:00 | Spring | TRUE | nonsummer
2023-04-26 21:00 | 2023-04-26 22:00 | Spring | TRUE | nonsummer
2023-04-26 22:00 | 2023-04-26 23:00 | Spring | FALSE | nonsummer
2023-04-26 23:00 | 2023-04-27 | Spring | FALSE | nonsummer
2023-04-27 | 2023-04-27 01:00 | Spring | FALSE | nonsummer
2023-04-27 01:00 | 2023-04-27 02:00 | Spring | FALSE | nonsummer
2023-04-27 02:00 | 2023-04-27 03:00 | Spring | FALSE | nonsummer
2023-04-27 03:00 | 2023-04-27 04:00 | Spring | FALSE | nonsummer
2023-04-27 04:00 | 2023-04-27 05:00 | Spring | FALSE | nonsummer
2023-04-27 05:00 | 2023-04-27 06:00 | Spring | FALSE | nonsummer
2023-04-27 06:00 | 2023-04-27 07:00 | Spring | FALSE | nonsummer
2023-04-27 07:00 | 2023-04-27 08:00 | Spring | FALSE | nonsummer
2023-04-27 08:00 | 2023-04-27 09:00 | Spring | FALSE | nonsummer
2023-04-27 09:00 | 2023-04-27 10:00 | Spring | FALSE | nonsummer
2023-04-27 10:00 | 2023-04-27 11:00 | Spring | FALSE | nonsummer
2023-04-27 11:00 | 2023-04-27 12:00 | Spring | FALSE | nonsummer
2023-04-27 12:00 | 2023-04-27 13:00 | Spring | FALSE | nonsummer
2023-04-27 13:00 | 2023-04-27 14:00 | Spring | FALSE | nonsummer
2023-04-27 14:00 | 2023-04-27 15:00 | Spring | FALSE | nonsummer
2023-04-27 15:00 | 2023-04-27 16:00 | Spring | FALSE | nonsummer
2023-04-27 16:00 | 2023-04-27 17:00 | Spring | FALSE | nonsummer
2023-04-27 17:00 | 2023-04-27 18:00 | Spring | TRUE | nonsummer
2023-04-27 18:00 | 2023-04-27 19:00 | Spring | TRUE | nonsummer
2023-04-27 19:00 | 2023-04-27 20:00 | Spring | TRUE | nonsummer
2023-04-27 20:00 | 2023-04-27 21:00 | Spring | TRUE | nonsummer
2023-04-27 21:00 | 2023-04-27 22:00 | Spring | TRUE | nonsummer
2023-04-27 22:00 | 2023-04-27 23:00 | Spring | FALSE | nonsummer
2023-04-27 23:00 | 2023-04-28 | Spring | FALSE | nonsummer
2023-04-28 | 2023-04-28 01:00 | Spring | FALSE | nonsummer
2023-04-28 01:00 | 2023-04-28 02:00 | Spring | FALSE | nonsummer
2023-04-28 02:00 | 2023-04-28 03:00 | Spring | FALSE | nonsummer
2023-04-28 03:00 | 2023-04-28 04:00 | Spring | FALSE | nonsummer
2023-04-28 04:00 | 2023-04-28 05:00 | Spring | FALSE | nonsummer
2023-04-28 05:00 | 2023-04-28 06:00 | Spring | FALSE | nonsummer
2023-04-28 06:00 | 2023-04-28 07:00 | Spring | FALSE | nonsummer
2023-04-28 07:00 | 2023-04-28 08:00 | Spring | FALSE | nonsummer
2023-04-28 08:00 | 2023-04-28 09:00 | Spring | FALSE | nonsummer
2023-04-28 09:00 | 2023-04-28 10:00 | Spring | FALSE | nonsummer
2023-04-28 10:00 | 2023-04-28 11:00 | Spring | FALSE | nonsummer
2023-04-28 11:00 | 2023-04-28 12:00 | Spring | FALSE | nonsummer
2023-04-28 12:00 | 2023-04-28 13:00 | Spring | FALSE | nonsummer
2023-04-28 13:00 | 2023-04-28 14:00 | Spring | FALSE | nonsummer
2023-04-28 14:00 | 2023-04-28 15:00 | Spring | FALSE | nonsummer
2023-04-28 15:00 | 2023-04-28 16:00 | Spring | FALSE | nonsummer
2023-04-28 16:00 | 2023-04-28 17:00 | Spring | FALSE | nonsummer
2023-04-28 17:00 | 2023-04-28 18:00 | Spring | TRUE | nonsummer
2023-04-28 18:00 | 2023-04-28 19:00 | Spring | TRUE | nonsummer
2023-04-28 19:00 | 2023-04-28 20:00 | Spring | TRUE | nonsummer
2023-04-28 20:00 | 2023-04-28 21:00 | Spring | TRUE | nonsummer
2023-04-28 21:00 | 2023-04-28 22:00 | Spring | TRUE | nonsummer
2023-04-28 22:00 | 2023-04-28 23:00 | Spring | FALSE | nonsummer
2023-04-28 23:00 | 2023-04-29 | Spring | FALSE | nonsummer
2023-04-29 | 2023-04-29 01:00 | Spring | FALSE | nonsummer
2023-04-29 01:00 | 2023-04-29 02:00 | Spring | FALSE | nonsummer
2023-04-29 02:00 | 2023-04-29 03:00 | Spring | FALSE | nonsummer
2023-04-29 03:00 | 2023-04-29 04:00 | Spring | FALSE | nonsummer
2023-04-29 04:00 | 2023-04-29 05:00 | Spring | FALSE | nonsummer
2023-04-29 05:00 | 2023-04-29 06:00 | Spring | FALSE | nonsummer
2023-04-29 06:00 | 2023-04-29 07:00 | Spring | FALSE | nonsummer
2023-04-29 07:00 | 2023-04-29 08:00 | Spring | FALSE | nonsummer
2023-04-29 08:00 | 2023-04-29 09:00 | Spring | FALSE | nonsummer
2023-04-29 09:00 | 2023-04-29 10:00 | Spring | FALSE | nonsummer
2023-04-29 10:00 | 2023-04-29 11:00 | Spring | FALSE | nonsummer
2023-04-29 11:00 | 2023-04-29 12:00 | Spring | FALSE | nonsummer
2023-04-29 12:00 | 2023-04-29 13:00 | Spring | FALSE | nonsummer
2023-04-29 13:00 | 2023-04-29 14:00 | Spring | FALSE | nonsummer
2023-04-29 14:00 | 2023-04-29 15:00 | Spring | FALSE | nonsummer
2023-04-29 15:00 | 2023-04-29 16:00 | Spring | FALSE | nonsummer
2023-04-29 16:00 | 2023-04-29 17:00 | Spring | FALSE | nonsummer
2023-04-29 17:00 | 2023-04-29 18:00 | Spring | TRUE | nonsummer
2023-04-29 18:00 | 2023-04-29 19:00 | Spring | TRUE | nonsummer
2023-04-29 19:00 | 2023-04-29 20:00 | Spring | TRUE | nonsummer
2023-04-29 20:00 | 2023-04-29 21:00 | Spring | TRUE | nonsummer
2023-04-29 21:00 | 2023-04-29 22:00 | Spring | TRUE | nonsummer
2023-04-29 22:00 | 2023-04-29 23:00 | Spring | FALSE | nonsummer
2023-04-29 23:00 | 2023-04-30 | Spring | FALSE | nonsummer
2023-04-30 | 2023-04-30 01:00 | Spring | FALSE | nonsummer
2023-04-30 01:00 | 2023-04-30 02:00 | Spring | FALSE | nonsummer
2023-04-30 02:00 | 2023-04-30 03:00 | Spring | FALSE | nonsummer
2023-04-30 03:00 | 2023-04-30 04:00 | Spring | FALSE | nonsummer
2023-04-30 04:00 | 2023-04-30 05:00 | Spring | FALSE | nonsummer
2023-04-30 05:00 | 2023-04-30 06:00 | Spring | FALSE | nonsummer
2023-04-30 06:00 | 2023-04-30 07:00 | Spring | FALSE | nonsummer
2023-04-30 07:00 | 2023-04-30 08:00 | Spring | FALSE | nonsummer
2023-04-30 08:00 | 2023-04-30 09:00 | Spring | FALSE | nonsummer
2023-04-30 09:00 | 2023-04-30 10:00 | Spring | FALSE | nonsummer
2023-04-30 10:00 | 2023-04-30 11:00 | Spring | FALSE | nonsummer
2023-04-30 11:00 | 2023-04-30 12:00 | Spring | FALSE | nonsummer
2023-04-30 12:00 | 2023-04-30 13:00 | Spring | FALSE | nonsummer
2023-04-30 13:00 | 2023-04-30 14:00 | Spring | FALSE | nonsummer
2023-04-30 14:00 | 2023-04-30 15:00 | Spring | FALSE | nonsummer
2023-04-30 15:00 | 2023-04-30 16:00 | Spring | FALSE | nonsummer
2023-04-30 16:00 | 2023-04-30 17:00 | Spring | FALSE | nonsummer
2023-04-30 17:00 | 2023-04-30 18:00 | Spring | TRUE | nonsummer
2023-04-30 18:00 | 2023-04-30 19:00 | Spring | TRUE | nonsummer
2023-04-30 19:00 | 2023-04-30 20:00 | Spring | TRUE | nonsummer
2023-04-30 20:00 | 2023-04-30 21:00 | Spring | TRUE | nonsummer
2023-04-30 21:00 | 2023-04-30 22:00 | Spring | TRUE | nonsummer
2023-04-30 22:00 | 2023-04-30 23:00 | Spring | FALSE | nonsummer
2023-04-30 23:00 | 2023-05-01 | Spring | FALSE | nonsummer
2023-05-01 | 2023-05-01 01:00 | Spring | FALSE | nonsummer
2023-05-01 01:00 | 2023-05-01 02:00 | Spring | FALSE | nonsummer
2023-05-01 02:00 | 2023-05-01 03:00 | Spring | FALSE | nonsummer
2023-05-01 03:00 | 2023-05-01 04:00 | Spring | FALSE | nonsummer
2023-05-01 04:00 | 2023-05-01 05:00 | Spring | FALSE | nonsummer
2023-05-01 05:00 | 2023-05-01 06:00 | Spring | FALSE | nonsummer
2023-05-01 06:00 | 2023-05-01 07:00 | Spring | FALSE | nonsummer
2023-05-01 07:00 | 2023-05-01 08:00 | Spring | FALSE | nonsummer
2023-05-01 08:00 | 2023-05-01 09:00 | Spring | FALSE | nonsummer
2023-05-01 09:00 | 2023-05-01 10:00 | Spring | FALSE | nonsummer
2023-05-01 10:00 | 2023-05-01 11:00 | Spring | FALSE | nonsummer
2023-05-01 11:00 | 2023-05-01 12:00 | Spring | FALSE | nonsummer
2023-05-01 12:00 | 2023-05-01 13:00 | Spring | FALSE | nonsummer
2023-05-01 13:00 | 2023-05-01 14:00 | Spring | FALSE | nonsummer
2023-05-01 14:00 | 2023-05-01 15:00 | Spring | FALSE | nonsummer
2023-05-01 15:00 | 2023-05-01 16:00 | Spring | FALSE | nonsummer
2023-05-01 16:00 | 2023-05-01 17:00 | Spring | FALSE | nonsummer
2023-05-01 17:00 | 2023-05-01 18:00 | Spring | TRUE | nonsummer
2023-05-01 18:00 | 2023-05-01 19:00 | Spring | TRUE | nonsummer
2023-05-01 19:00 | 2023-05-01 20:00 | Spring | TRUE | nonsummer
2023-05-01 20:00 | 2023-05-01 21:00 | Spring | TRUE | nonsummer
2023-05-01 21:00 | 2023-05-01 22:00 | Spring | TRUE | nonsummer
2023-05-01 22:00 | 2023-05-01 23:00 | Spring | FALSE | nonsummer
2023-05-01 23:00 | 2023-05-02 | Spring | FALSE | nonsummer
2023-05-02 | 2023-05-02 01:00 | Spring | FALSE | nonsummer
2023-05-02 01:00 | 2023-05-02 02:00 | Spring | FALSE | nonsummer
2023-05-02 02:00 | 2023-05-02 03:00 | Spring | FALSE | nonsummer
2023-05-02 03:00 | 2023-05-02 04:00 | Spring | FALSE | nonsummer
2023-05-02 04:00 | 2023-05-02 05:00 | Spring | FALSE | nonsummer
2023-05-02 05:00 | 2023-05-02 06:00 | Spring | FALSE | nonsummer
2023-05-02 06:00 | 2023-05-02 07:00 | Spring | FALSE | nonsummer
2023-05-02 07:00 | 2023-05-02 08:00 | Spring | FALSE | nonsummer
2023-05-02 08:00 | 2023-05-02 09:00 | Spring | FALSE | nonsummer
2023-05-02 09:00 | 2023-05-02 10:00 | Spring | FALSE | nonsummer
2023-05-02 10:00 | 2023-05-02 11:00 | Spring | FALSE | nonsummer
2023-05-02 11:00 | 2023-05-02 12:00 | Spring | FALSE | nonsummer
2023-05-02 12:00 | 2023-05-02 13:00 | Spring | FALSE | nonsummer
2023-05-02 13:00 | 2023-05-02 14:00 | Spring | FALSE | nonsummer
2023-05-02 14:00 | 2023-05-02 15:00 | Spring | FALSE | nonsummer
2023-05-02 15:00 | 2023-05-02 16:00 | Spring | FALSE | nonsummer
2023-05-02 16:00 | 2023-05-02 17:00 | Spring | FALSE | nonsummer
2023-05-02 17:00 | 2023-05-02 18:00 | Spring | TRUE | nonsummer
2023-05-02 18:00 | 2023-05-02 19:00 | Spring | TRUE | nonsummer
2023-05-02 19:00 | 2023-05-02 20:00 | Spring | TRUE | nonsummer
2023-05-02 20:00 | 2023-05-02 21:00 | Spring | TRUE | nonsummer
2023-05-02 21:00 | 2023-05-02 22:00 | Spring | TRUE | nonsummer
2023-05-02 22:00 | 2023-05-02 23:00 | Spring | FALSE | nonsummer
2023-05-02 23:00 | 2023-05-03 | Spring | FALSE | nonsummer
2023-05-03 | 2023-05-03 01:00 | Spring | FALSE | nonsummer
2023-05-03 01:00 | 2023-05-03 02:00 | Spring | FALSE | nonsummer
2023-05-03 02:00 | 2023-05-03 03:00 | Spring | FALSE | nonsummer
2023-05-03 03:00 | 2023-05-03 04:00 | Spring | FALSE | nonsummer
2023-05-03 04:00 | 2023-05-03 05:00 | Spring | FALSE | nonsummer
2023-05-03 05:00 | 2023-05-03 06:00 | Spring | FALSE | nonsummer
2023-05-03 06:00 | 2023-05-03 07:00 | Spring | FALSE | nonsummer
2023-05-03 07:00 | 2023-05-03 08:00 | Spring | FALSE | nonsummer
2023-05-03 08:00 | 2023-05-03 09:00 | Spring | FALSE | nonsummer
2023-05-03 09:00 | 2023-05-03 10:00 | Spring | FALSE | nonsummer
2023-05-03 10:00 | 2023-05-03 11:00 | Spring | FALSE | nonsummer
2023-05-03 11:00 | 2023-05-03 12:00 | Spring | FALSE | nonsummer
2023-05-03 12:00 | 2023-05-03 13:00 | Spring | FALSE | nonsummer
2023-05-03 13:00 | 2023-05-03 14:00 | Spring | FALSE | nonsummer
2023-05-03 14:00 | 2023-05-03 15:00 | Spring | FALSE | nonsummer
2023-05-03 15:00 | 2023-05-03 16:00 | Spring | FALSE | nonsummer
2023-05-03 16:00 | 2023-05-03 17:00 | Spring | FALSE | nonsummer
2023-05-03 17:00 | 2023-05-03 18:00 | Spring | TRUE | nonsummer
2023-05-03 18:00 | 2023-05-03 19:00 | Spring | TRUE | nonsummer
2023-05-03 19:00 | 2023-05-03 20:00 | Spring | TRUE | nonsummer
2023-05-03 20:00 | 2023-05-03 21:00 | Spring | TRUE | nonsummer
2023-05-03 21:00 | 2023-05-03 22:00 | Spring | TRUE | nonsummer
2023-05-03 22:00 | 2023-05-03 23:00 | Spring | FALSE | nonsummer
2023-05-03 23:00 | 2023-05-04 | Spring | FALSE | nonsummer
2023-05-04 | 2023-05-04 01:00 | Spring | FALSE | nonsummer
2023-05-04 01:00 | 2023-05-04 02:00 | Spring | FALSE | nonsummer
2023-05-04 02:00 | 2023-05-04 03:00 | Spring | FALSE | nonsummer
2023-05-04 03:00 | 2023-05-04 04:00 | Spring | FALSE | nonsummer
2023-05-04 04:00 | 2023-05-04 05:00 | Spring | FALSE | nonsummer
2023-05-04 05:00 | 2023-05-04 06:00 | Spring | FALSE | nonsummer
2023-05-04 06:00 | 2023-05-04 07:00 | Spring | FALSE | nonsummer
2023-05-04 07:00 | 2023-05-04 08:00 | Spring | FALSE | nonsummer
2023-05-04 08:00 | 2023-05-04 09:00 | Spring | FALSE | nonsummer
2023-05-04 09:00 | 2023-05-04 10:00 | Spring | FALSE | nonsummer
2023-05-04 10:00 | 2023-05-04 11:00 | Spring | FALSE | nonsummer
2023-05-04 11:00 | 2023-05-04 12:00 | Spring | FALSE | nonsummer
2023-05-04 12:00 | 2023-05-04 13:00 | Spring | FALSE | nonsummer
2023-05-04 13:00 | 2023-05-04 14:00 | Spring | FALSE | nonsummer
2023-05-04 14:00 | 2023-05-04 15:00 | Spring | FALSE | nonsummer
2023-05-04 15:00 | 2023-05-04 16:00 | Spring | FALSE | nonsummer
2023-05-04 16:00 | 2023-05-04 17:00 | Spring | FALSE | nonsummer
2023-05-04 17:00 | 2023-05-04 18:00 | Spring | TRUE | nonsummer
2023-05-04 18:00 | 2023-05-04 19:00 | Spring | TRUE | nonsummer
2023-05-04 19:00 | 2023-05-04 20:00 | Spring | TRUE | nonsummer
2023-05-04 20:00 | 2023-05-04 21:00 | Spring | TRUE | nonsummer
2023-05-04 21:00 | 2023-05-04 22:00 | Spring | TRUE | nonsummer
2023-05-04 22:00 | 2023-05-04 23:00 | Spring | FALSE | nonsummer
2023-05-04 23:00 | 2023-05-05 | Spring | FALSE | nonsummer
2023-05-05 | 2023-05-05 01:00 | Spring | FALSE | nonsummer
2023-05-05 01:00 | 2023-05-05 02:00 | Spring | FALSE | nonsummer
2023-05-05 02:00 | 2023-05-05 03:00 | Spring | FALSE | nonsummer
2023-05-05 03:00 | 2023-05-05 04:00 | Spring | FALSE | nonsummer
2023-05-05 04:00 | 2023-05-05 05:00 | Spring | FALSE | nonsummer
2023-05-05 05:00 | 2023-05-05 06:00 | Spring | FALSE | nonsummer
2023-05-05 06:00 | 2023-05-05 07:00 | Spring | FALSE | nonsummer
2023-05-05 07:00 | 2023-05-05 08:00 | Spring | FALSE | nonsummer
2023-05-05 08:00 | 2023-05-05 09:00 | Spring | FALSE | nonsummer
2023-05-05 09:00 | 2023-05-05 10:00 | Spring | FALSE | nonsummer
2023-05-05 10:00 | 2023-05-05 11:00 | Spring | FALSE | nonsummer
2023-05-05 11:00 | 2023-05-05 12:00 | Spring | FALSE | nonsummer
2023-05-05 12:00 | 2023-05-05 13:00 | Spring | FALSE | nonsummer
2023-05-05 13:00 | 2023-05-05 14:00 | Spring | FALSE | nonsummer
2023-05-05 14:00 | 2023-05-05 15:00 | Spring | FALSE | nonsummer
2023-05-05 15:00 | 2023-05-05 16:00 | Spring | FALSE | nonsummer
2023-05-05 16:00 | 2023-05-05 17:00 | Spring | FALSE | nonsummer
2023-05-05 17:00 | 2023-05-05 18:00 | Spring | TRUE | nonsummer
2023-05-05 18:00 | 2023-05-05 19:00 | Spring | TRUE | nonsummer
2023-05-05 19:00 | 2023-05-05 20:00 | Spring | TRUE | nonsummer
2023-05-05 20:00 | 2023-05-05 21:00 | Spring | TRUE | nonsummer
2023-05-05 21:00 | 2023-05-05 22:00 | Spring | TRUE | nonsummer
2023-05-05 22:00 | 2023-05-05 23:00 | Spring | FALSE | nonsummer
2023-05-05 23:00 | 2023-05-06 | Spring | FALSE | nonsummer
2023-05-06 | 2023-05-06 01:00 | Spring | FALSE | nonsummer
2023-05-06 01:00 | 2023-05-06 02:00 | Spring | FALSE | nonsummer
2023-05-06 02:00 | 2023-05-06 03:00 | Spring | FALSE | nonsummer
2023-05-06 03:00 | 2023-05-06 04:00 | Spring | FALSE | nonsummer
2023-05-06 04:00 | 2023-05-06 05:00 | Spring | FALSE | nonsummer
2023-05-06 05:00 | 2023-05-06 06:00 | Spring | FALSE | nonsummer
2023-05-06 06:00 | 2023-05-06 07:00 | Spring | FALSE | nonsummer
2023-05-06 07:00 | 2023-05-06 08:00 | Spring | FALSE | nonsummer
2023-05-06 08:00 | 2023-05-06 09:00 | Spring | FALSE | nonsummer
2023-05-06 09:00 | 2023-05-06 10:00 | Spring | FALSE | nonsummer
2023-05-06 10:00 | 2023-05-06 11:00 | Spring | FALSE | nonsummer
2023-05-06 11:00 | 2023-05-06 12:00 | Spring | FALSE | nonsummer
2023-05-06 12:00 | 2023-05-06 13:00 | Spring | FALSE | nonsummer
2023-05-06 13:00 | 2023-05-06 14:00 | Spring | FALSE | nonsummer
2023-05-06 14:00 | 2023-05-06 15:00 | Spring | FALSE | nonsummer
2023-05-06 15:00 | 2023-05-06 16:00 | Spring | FALSE | nonsummer
2023-05-06 16:00 | 2023-05-06 17:00 | Spring | FALSE | nonsummer
2023-05-06 17:00 | 2023-05-06 18:00 | Spring | TRUE | nonsummer
2023-05-06 18:00 | 2023-05-06 19:00 | Spring | TRUE | nonsummer
2023-05-06 19:00 | 2023-05-06 20:00 | Spring | TRUE | nonsummer
2023-05-06 20:00 | 2023-05-06 21:00 | Spring | TRUE | nonsummer
2023-05-06 21:00 | 2023-05-06 22:00 | Spring | TRUE | nonsummer
2023-05-06 22:00 | 2023-05-06 23:00 | Spring | FALSE | nonsummer
2023-05-06 23:00 | 2023-05-07 | Spring | FALSE | nonsummer
2023-05-07 | 2023-05-07 01:00 | Spring | FALSE | nonsummer
2023-05-07 01:00 | 2023-05-07 02:00 | Spring | FALSE | nonsummer
2023-05-07 02:00 | 2023-05-07 03:00 | Spring | FALSE | nonsummer
2023-05-07 03:00 | 2023-05-07 04:00 | Spring | FALSE | nonsummer
2023-05-07 04:00 | 2023-05-07 05:00 | Spring | FALSE | nonsummer
2023-05-07 05:00 | 2023-05-07 06:00 | Spring | FALSE | nonsummer
2023-05-07 06:00 | 2023-05-07 07:00 | Spring | FALSE | nonsummer
2023-05-07 07:00 | 2023-05-07 08:00 | Spring | FALSE | nonsummer
2023-05-07 08:00 | 2023-05-07 09:00 | Spring | FALSE | nonsummer
2023-05-07 09:00 | 2023-05-07 10:00 | Spring | FALSE | nonsummer
2023-05-07 10:00 | 2023-05-07 11:00 | Spring | FALSE | nonsummer
2023-05-07 11:00 | 2023-05-07 12:00 | Spring | FALSE | nonsummer
2023-05-07 12:00 | 2023-05-07 13:00 | Spring | FALSE | nonsummer
2023-05-07 13:00 | 2023-05-07 14:00 | Spring | FALSE | nonsummer
2023-05-07 14:00 | 2023-05-07 15:00 | Spring | FALSE | nonsummer
2023-05-07 15:00 | 2023-05-07 16:00 | Spring | FALSE | nonsummer
2023-05-07 16:00 | 2023-05-07 17:00 | Spring | FALSE | nonsummer
2023-05-07 17:00 | 2023-05-07 18:00 | Spring | TRUE | nonsummer
2023-05-07 18:00 | 2023-05-07 19:00 | Spring | TRUE | nonsummer
2023-05-07 19:00 | 2023-05-07 20:00 | Spring | TRUE | nonsummer
2023-05-07 20:00 | 2023-05-07 21:00 | Spring | TRUE | nonsummer
2023-05-07 21:00 | 2023-05-07 22:00 | Spring | TRUE | nonsummer
2023-05-07 22:00 | 2023-05-07 23:00 | Spring | FALSE | nonsummer
2023-05-07 23:00 | 2023-05-08 | Spring | FALSE | nonsummer
2023-05-08 | 2023-05-08 01:00 | Spring | FALSE | nonsummer
2023-05-08 01:00 | 2023-05-08 02:00 | Spring | FALSE | nonsummer
2023-05-08 02:00 | 2023-05-08 03:00 | Spring | FALSE | nonsummer
2023-05-08 03:00 | 2023-05-08 04:00 | Spring | FALSE | nonsummer
2023-05-08 04:00 | 2023-05-08 05:00 | Spring | FALSE | nonsummer
2023-05-08 05:00 | 2023-05-08 06:00 | Spring | FALSE | nonsummer
2023-05-08 06:00 | 2023-05-08 07:00 | Spring | FALSE | nonsummer
2023-05-08 07:00 | 2023-05-08 08:00 | Spring | FALSE | nonsummer
2023-05-08 08:00 | 2023-05-08 09:00 | Spring | FALSE | nonsummer
2023-05-08 09:00 | 2023-05-08 10:00 | Spring | FALSE | nonsummer
2023-05-08 10:00 | 2023-05-08 11:00 | Spring | FALSE | nonsummer
2023-05-08 11:00 | 2023-05-08 12:00 | Spring | FALSE | nonsummer
2023-05-08 12:00 | 2023-05-08 13:00 | Spring | FALSE | nonsummer
2023-05-08 13:00 | 2023-05-08 14:00 | Spring | FALSE | nonsummer
2023-05-08 14:00 | 2023-05-08 15:00 | Spring | FALSE | nonsummer
2023-05-08 15:00 | 2023-05-08 16:00 | Spring | FALSE | nonsummer
2023-05-08 16:00 | 2023-05-08 17:00 | Spring | FALSE | nonsummer
2023-05-08 17:00 | 2023-05-08 18:00 | Spring | TRUE | nonsummer
2023-05-08 18:00 | 2023-05-08 19:00 | Spring | TRUE | nonsummer
2023-05-08 19:00 | 2023-05-08 20:00 | Spring | TRUE | nonsummer
2023-05-08 20:00 | 2023-05-08 21:00 | Spring | TRUE | nonsummer
2023-05-08 21:00 | 2023-05-08 22:00 | Spring | TRUE | nonsummer
2023-05-08 22:00 | 2023-05-08 23:00 | Spring | FALSE | nonsummer
2023-05-08 23:00 | 2023-05-09 | Spring | FALSE | nonsummer
2023-05-09 | 2023-05-09 01:00 | Spring | FALSE | nonsummer
2023-05-09 01:00 | 2023-05-09 02:00 | Spring | FALSE | nonsummer
2023-05-09 02:00 | 2023-05-09 03:00 | Spring | FALSE | nonsummer
2023-05-09 03:00 | 2023-05-09 04:00 | Spring | FALSE | nonsummer
2023-05-09 04:00 | 2023-05-09 05:00 | Spring | FALSE | nonsummer
2023-05-09 05:00 | 2023-05-09 06:00 | Spring | FALSE | nonsummer
2023-05-09 06:00 | 2023-05-09 07:00 | Spring | FALSE | nonsummer
2023-05-09 07:00 | 2023-05-09 08:00 | Spring | FALSE | nonsummer
2023-05-09 08:00 | 2023-05-09 09:00 | Spring | FALSE | nonsummer
2023-05-09 09:00 | 2023-05-09 10:00 | Spring | FALSE | nonsummer
2023-05-09 10:00 | 2023-05-09 11:00 | Spring | FALSE | nonsummer
2023-05-09 11:00 | 2023-05-09 12:00 | Spring | FALSE | nonsummer
2023-05-09 12:00 | 2023-05-09 13:00 | Spring | FALSE | nonsummer
2023-05-09 13:00 | 2023-05-09 14:00 | Spring | FALSE | nonsummer
2023-05-09 14:00 | 2023-05-09 15:00 | Spring | FALSE | nonsummer
2023-05-09 15:00 | 2023-05-09 16:00 | Spring | FALSE | nonsummer
2023-05-09 16:00 | 2023-05-09 17:00 | Spring | FALSE | nonsummer
2023-05-09 17:00 | 2023-05-09 18:00 | Spring | TRUE | nonsummer
2023-05-09 18:00 | 2023-05-09 19:00 | Spring | TRUE | nonsummer
2023-05-09 19:00 | 2023-05-09 20:00 | Spring | TRUE | nonsummer
2023-05-09 20:00 | 2023-05-09 21:00 | Spring | TRUE | nonsummer
2023-05-09 21:00 | 2023-05-09 22:00 | Spring | TRUE | nonsummer
2023-05-09 22:00 | 2023-05-09 23:00 | Spring | FALSE | nonsummer
2023-05-09 23:00 | 2023-05-10 | Spring | FALSE | nonsummer
2023-05-10 | 2023-05-10 01:00 | Spring | FALSE | nonsummer
2023-05-10 01:00 | 2023-05-10 02:00 | Spring | FALSE | nonsummer
2023-05-10 02:00 | 2023-05-10 03:00 | Spring | FALSE | nonsummer
2023-05-10 03:00 | 2023-05-10 04:00 | Spring | FALSE | nonsummer
2023-05-10 04:00 | 2023-05-10 05:00 | Spring | FALSE | nonsummer
2023-05-10 05:00 | 2023-05-10 06:00 | Spring | FALSE | nonsummer
2023-05-10 06:00 | 2023-05-10 07:00 | Spring | FALSE | nonsummer
2023-05-10 07:00 | 2023-05-10 08:00 | Spring | FALSE | nonsummer
2023-05-10 08:00 | 2023-05-10 09:00 | Spring | FALSE | nonsummer
2023-05-10 09:00 | 2023-05-10 10:00 | Spring | FALSE | nonsummer
2023-05-10 10:00 | 2023-05-10 11:00 | Spring | FALSE | nonsummer
2023-05-10 11:00 | 2023-05-10 12:00 | Spring | FALSE | nonsummer
2023-05-10 12:00 | 2023-05-10 13:00 | Spring | FALSE | nonsummer
2023-05-10 13:00 | 2023-05-10 14:00 | Spring | FALSE | nonsummer
2023-05-10 14:00 | 2023-05-10 15:00 | Spring | FALSE | nonsummer
2023-05-10 15:00 | 2023-05-10 16:00 | Spring | FALSE | nonsummer
2023-05-10 16:00 | 2023-05-10 17:00 | Spring | FALSE | nonsummer
2023-05-10 17:00 | 2023-05-10 18:00 | Spring | TRUE | nonsummer
2023-05-10 18:00 | 2023-05-10 19:00 | Spring | TRUE | nonsummer
2023-05-10 19:00 | 2023-05-10 20:00 | Spring | TRUE | nonsummer
2023-05-10 20:00 | 2023-05-10 21:00 | Spring | TRUE | nonsummer
2023-05-10 21:00 | 2023-05-10 22:00 | Spring | TRUE | nonsummer
2023-05-10 22:00 | 2023-05-10 23:00 | Spring | FALSE | nonsummer
2023-05-10 23:00 | 2023-05-11 | Spring | FALSE | nonsummer
2023-05-11 | 2023-05-11 01:00 | Spring | FALSE | nonsummer
2023-05-11 01:00 | 2023-05-11 02:00 | Spring | FALSE | nonsummer
2023-05-11 02:00 | 2023-05-11 03:00 | Spring | FALSE | nonsummer
2023-05-11 03:00 | 2023-05-11 04:00 | Spring | FALSE | nonsummer
2023-05-11 04:00 | 2023-05-11 05:00 | Spring | FALSE | nonsummer
2023-05-11 05:00 | 2023-05-11 06:00 | Spring | FALSE | nonsummer
2023-05-11 06:00 | 2023-05-11 07:00 | Spring | FALSE | nonsummer
2023-05-11 07:00 | 2023-05-11 08:00 | Spring | FALSE | nonsummer
2023-05-11 08:00 | 2023-05-11 09:00 | Spring | FALSE | nonsummer
2023-05-11 09:00 | 2023-05-11 10:00 | Spring | FALSE | nonsummer
2023-05-11 10:00 | 2023-05-11 11:00 | Spring | FALSE | nonsummer
2023-05-11 11:00 | 2023-05-11 12:00 | Spring | FALSE | nonsummer
2023-05-11 12:00 | 2023-05-11 13:00 | Spring | FALSE | nonsummer
2023-05-11 13:00 | 2023-05-11 14:00 | Spring | FALSE | nonsummer
2023-05-11 14:00 | 2023-05-11 15:00 | Spring | FALSE | nonsummer
2023-05-11 15:00 | 2023-05-11 16:00 | Spring | FALSE | nonsummer
2023-05-11 16:00 | 2023-05-11 17:00 | Spring | FALSE | nonsummer
2023-05-11 17:00 | 2023-05-11 18:00 | Spring | TRUE | nonsummer
2023-05-11 18:00 | 2023-05-11 19:00 | Spring | TRUE | nonsummer
2023-05-11 19:00 | 2023-05-11 20:00 | Spring | TRUE | nonsummer
2023-05-11 20:00 | 2023-05-11 21:00 | Spring | TRUE | nonsummer
2023-05-11 21:00 | 2023-05-11 22:00 | Spring | TRUE | nonsummer
2023-05-11 22:00 | 2023-05-11 23:00 | Spring | FALSE | nonsummer
2023-05-11 23:00 | 2023-05-12 | Spring | FALSE | nonsummer
2023-05-12 | 2023-05-12 01:00 | Spring | FALSE | nonsummer
2023-05-12 01:00 | 2023-05-12 02:00 | Spring | FALSE | nonsummer
2023-05-12 02:00 | 2023-05-12 03:00 | Spring | FALSE | nonsummer
2023-05-12 03:00 | 2023-05-12 04:00 | Spring | FALSE | nonsummer
2023-05-12 04:00 | 2023-05-12 05:00 | Spring | FALSE | nonsummer
2023-05-12 05:00 | 2023-05-12 06:00 | Spring | FALSE | nonsummer
2023-05-12 06:00 | 2023-05-12 07:00 | Spring | FALSE | nonsummer
2023-05-12 07:00 | 2023-05-12 08:00 | Spring | FALSE | nonsummer
2023-05-12 08:00 | 2023-05-12 09:00 | Spring | FALSE | nonsummer
2023-05-12 09:00 | 2023-05-12 10:00 | Spring | FALSE | nonsummer
2023-05-12 10:00 | 2023-05-12 11:00 | Spring | FALSE | nonsummer
2023-05-12 11:00 | 2023-05-12 12:00 | Spring | FALSE | nonsummer
2023-05-12 12:00 | 2023-05-12 13:00 | Spring | FALSE | nonsummer
2023-05-12 13:00 | 2023-05-12 14:00 | Spring | FALSE | nonsummer
2023-05-12 14:00 | 2023-05-12 15:00 | Spring | FALSE | nonsummer
2023-05-12 15:00 | 2023-05-12 16:00 | Spring | FALSE | nonsummer
2023-05-12 16:00 | 2023-05-12 17:00 | Spring | FALSE | nonsummer
2023-05-12 17:00 | 2023-05-12 18:00 | Spring | TRUE | nonsummer
2023-05-12 18:00 | 2023-05-12 19:00 | Spring | TRUE | nonsummer
2023-05-12 19:00 | 2023-05-12 20:00 | Spring | TRUE | nonsummer
2023-05-12 20:00 | 2023-05-12 21:00 | Spring | TRUE | nonsummer
2023-05-12 21:00 | 2023-05-12 22:00 | Spring | TRUE | nonsummer
2023-05-12 22:00 | 2023-05-12 23:00 | Spring | FALSE | nonsummer
2023-05-12 23:00 | 2023-05-13 | Spring | FALSE | nonsummer
2023-05-13 | 2023-05-13 01:00 | Spring | FALSE | nonsummer
2023-05-13 01:00 | 2023-05-13 02:00 | Spring | FALSE | nonsummer
2023-05-13 02:00 | 2023-05-13 03:00 | Spring | FALSE | nonsummer
2023-05-13 03:00 | 2023-05-13 04:00 | Spring | FALSE | nonsummer
2023-05-13 04:00 | 2023-05-13 05:00 | Spring | FALSE | nonsummer
2023-05-13 05:00 | 2023-05-13 06:00 | Spring | FALSE | nonsummer
2023-05-13 06:00 | 2023-05-13 07:00 | Spring | FALSE | nonsummer
2023-05-13 07:00 | 2023-05-13 08:00 | Spring | FALSE | nonsummer
2023-05-13 08:00 | 2023-05-13 09:00 | Spring | FALSE | nonsummer
2023-05-13 09:00 | 2023-05-13 10:00 | Spring | FALSE | nonsummer
2023-05-13 10:00 | 2023-05-13 11:00 | Spring | FALSE | nonsummer
2023-05-13 11:00 | 2023-05-13 12:00 | Spring | FALSE | nonsummer
2023-05-13 12:00 | 2023-05-13 13:00 | Spring | FALSE | nonsummer
2023-05-13 13:00 | 2023-05-13 14:00 | Spring | FALSE | nonsummer
2023-05-13 14:00 | 2023-05-13 15:00 | Spring | FALSE | nonsummer
2023-05-13 15:00 | 2023-05-13 16:00 | Spring | FALSE | nonsummer
2023-05-13 16:00 | 2023-05-13 17:00 | Spring | FALSE | nonsummer
2023-05-13 17:00 | 2023-05-13 18:00 | Spring | TRUE | nonsummer
2023-05-13 18:00 | 2023-05-13 19:00 | Spring | TRUE | nonsummer
2023-05-13 19:00 | 2023-05-13 20:00 | Spring | TRUE | nonsummer
2023-05-13 20:00 | 2023-05-13 21:00 | Spring | TRUE | nonsummer
2023-05-13 21:00 | 2023-05-13 22:00 | Spring | TRUE | nonsummer
2023-05-13 22:00 | 2023-05-13 23:00 | Spring | FALSE | nonsummer
2023-05-13 23:00 | 2023-05-14 | Spring | FALSE | nonsummer
2023-05-14 | 2023-05-14 01:00 | Spring | FALSE | nonsummer
2023-05-14 01:00 | 2023-05-14 02:00 | Spring | FALSE | nonsummer
2023-05-14 02:00 | 2023-05-14 03:00 | Spring | FALSE | nonsummer
2023-05-14 03:00 | 2023-05-14 04:00 | Spring | FALSE | nonsummer
2023-05-14 04:00 | 2023-05-14 05:00 | Spring | FALSE | nonsummer
2023-05-14 05:00 | 2023-05-14 06:00 | Spring | FALSE | nonsummer
2023-05-14 06:00 | 2023-05-14 07:00 | Spring | FALSE | nonsummer
2023-05-14 07:00 | 2023-05-14 08:00 | Spring | FALSE | nonsummer
2023-05-14 08:00 | 2023-05-14 09:00 | Spring | FALSE | nonsummer
2023-05-14 09:00 | 2023-05-14 10:00 | Spring | FALSE | nonsummer
2023-05-14 10:00 | 2023-05-14 11:00 | Spring | FALSE | nonsummer
2023-05-14 11:00 | 2023-05-14 12:00 | Spring | FALSE | nonsummer
2023-05-14 12:00 | 2023-05-14 13:00 | Spring | FALSE | nonsummer
2023-05-14 13:00 | 2023-05-14 14:00 | Spring | FALSE | nonsummer
2023-05-14 14:00 | 2023-05-14 15:00 | Spring | FALSE | nonsummer
2023-05-14 15:00 | 2023-05-14 16:00 | Spring | FALSE | nonsummer
2023-05-14 16:00 | 2023-05-14 17:00 | Spring | FALSE | nonsummer
2023-05-14 17:00 | 2023-05-14 18:00 | Spring | TRUE | nonsummer
2023-05-14 18:00 | 2023-05-14 19:00 | Spring | TRUE | nonsummer
2023-05-14 19:00 | 2023-05-14 20:00 | Spring | TRUE | nonsummer
2023-05-14 20:00 | 2023-05-14 21:00 | Spring | TRUE | nonsummer
2023-05-14 21:00 | 2023-05-14 22:00 | Spring | TRUE | nonsummer
2023-05-14 22:00 | 2023-05-14 23:00 | Spring | FALSE | nonsummer
2023-05-14 23:00 | 2023-05-15 | Spring | FALSE | nonsummer
2023-05-15 | 2023-05-15 01:00 | Spring | FALSE | nonsummer
2023-05-15 01:00 | 2023-05-15 02:00 | Spring | FALSE | nonsummer
2023-05-15 02:00 | 2023-05-15 03:00 | Spring | FALSE | nonsummer
2023-05-15 03:00 | 2023-05-15 04:00 | Spring | FALSE | nonsummer
2023-05-15 04:00 | 2023-05-15 05:00 | Spring | FALSE | nonsummer
2023-05-15 05:00 | 2023-05-15 06:00 | Spring | FALSE | nonsummer
2023-05-15 06:00 | 2023-05-15 07:00 | Spring | FALSE | nonsummer
2023-05-15 07:00 | 2023-05-15 08:00 | Spring | FALSE | nonsummer
2023-05-15 08:00 | 2023-05-15 09:00 | Spring | FALSE | nonsummer
2023-05-15 09:00 | 2023-05-15 10:00 | Spring | FALSE | nonsummer
2023-05-15 10:00 | 2023-05-15 11:00 | Spring | FALSE | nonsummer
2023-05-15 11:00 | 2023-05-15 12:00 | Spring | FALSE | nonsummer
2023-05-15 12:00 | 2023-05-15 13:00 | Spring | FALSE | nonsummer
2023-05-15 13:00 | 2023-05-15 14:00 | Spring | FALSE | nonsummer
2023-05-15 14:00 | 2023-05-15 15:00 | Spring | FALSE | nonsummer
2023-05-15 15:00 | 2023-05-15 16:00 | Spring | FALSE | nonsummer
2023-05-15 16:00 | 2023-05-15 17:00 | Spring | FALSE | nonsummer
2023-05-15 17:00 | 2023-05-15 18:00 | Spring | TRUE | nonsummer
2023-05-15 18:00 | 2023-05-15 19:00 | Spring | TRUE | nonsummer
2023-05-15 19:00 | 2023-05-15 20:00 | Spring | TRUE | nonsummer
2023-05-15 20:00 | 2023-05-15 21:00 | Spring | TRUE | nonsummer
2023-05-15 21:00 | 2023-05-15 22:00 | Spring | TRUE | nonsummer
2023-05-15 22:00 | 2023-05-15 23:00 | Spring | FALSE | nonsummer
2023-05-15 23:00 | 2023-05-16 | Spring | FALSE | nonsummer
2023-05-16 | 2023-05-16 01:00 | Spring | FALSE | nonsummer
2023-05-16 01:00 | 2023-05-16 02:00 | Spring | FALSE | nonsummer
2023-05-16 02:00 | 2023-05-16 03:00 | Spring | FALSE | nonsummer
2023-05-16 03:00 | 2023-05-16 04:00 | Spring | FALSE | nonsummer
2023-05-16 04:00 | 2023-05-16 05:00 | Spring | FALSE | nonsummer
2023-05-16 05:00 | 2023-05-16 06:00 | Spring | FALSE | nonsummer
2023-05-16 06:00 | 2023-05-16 07:00 | Spring | FALSE | nonsummer
2023-05-16 07:00 | 2023-05-16 08:00 | Spring | FALSE | nonsummer
2023-05-16 08:00 | 2023-05-16 09:00 | Spring | FALSE | nonsummer
2023-05-16 09:00 | 2023-05-16 10:00 | Spring | FALSE | nonsummer
2023-05-16 10:00 | 2023-05-16 11:00 | Spring | FALSE | nonsummer
2023-05-16 11:00 | 2023-05-16 12:00 | Spring | FALSE | nonsummer
2023-05-16 12:00 | 2023-05-16 13:00 | Spring | FALSE | nonsummer
2023-05-16 13:00 | 2023-05-16 14:00 | Spring | FALSE | nonsummer
2023-05-16 14:00 | 2023-05-16 15:00 | Spring | FALSE | nonsummer
2023-05-16 15:00 | 2023-05-16 16:00 | Spring | FALSE | nonsummer
2023-05-16 16:00 | 2023-05-16 17:00 | Spring | FALSE | nonsummer
2023-05-16 17:00 | 2023-05-16 18:00 | Spring | TRUE | nonsummer
2023-05-16 18:00 | 2023-05-16 19:00 | Spring | TRUE | nonsummer
2023-05-16 19:00 | 2023-05-16 20:00 | Spring | TRUE | nonsummer
2023-05-16 20:00 | 2023-05-16 21:00 | Spring | TRUE | nonsummer
2023-05-16 21:00 | 2023-05-16 22:00 | Spring | TRUE | nonsummer
2023-05-16 22:00 | 2023-05-16 23:00 | Spring | FALSE | nonsummer
2023-05-16 23:00 | 2023-05-17 | Spring | FALSE | nonsummer
2023-05-17 | 2023-05-17 01:00 | Spring | FALSE | nonsummer
2023-05-17 01:00 | 2023-05-17 02:00 | Spring | FALSE | nonsummer
2023-05-17 02:00 | 2023-05-17 03:00 | Spring | FALSE | nonsummer
2023-05-17 03:00 | 2023-05-17 04:00 | Spring | FALSE | nonsummer
2023-05-17 04:00 | 2023-05-17 05:00 | Spring | FALSE | nonsummer
2023-05-17 05:00 | 2023-05-17 06:00 | Spring | FALSE | nonsummer
2023-05-17 06:00 | 2023-05-17 07:00 | Spring | FALSE | nonsummer
2023-05-17 07:00 | 2023-05-17 08:00 | Spring | FALSE | nonsummer
2023-05-17 08:00 | 2023-05-17 09:00 | Spring | FALSE | nonsummer
2023-05-17 09:00 | 2023-05-17 10:00 | Spring | FALSE | nonsummer
2023-05-17 10:00 | 2023-05-17 11:00 | Spring | FALSE | nonsummer
2023-05-17 11:00 | 2023-05-17 12:00 | Spring | FALSE | nonsummer
2023-05-17 12:00 | 2023-05-17 13:00 | Spring | FALSE | nonsummer
2023-05-17 13:00 | 2023-05-17 14:00 | Spring | FALSE | nonsummer
2023-05-17 14:00 | 2023-05-17 15:00 | Spring | FALSE | nonsummer
2023-05-17 15:00 | 2023-05-17 16:00 | Spring | FALSE | nonsummer
2023-05-17 16:00 | 2023-05-17 17:00 | Spring | FALSE | nonsummer
2023-05-17 17:00 | 2023-05-17 18:00 | Spring | TRUE | nonsummer
2023-05-17 18:00 | 2023-05-17 19:00 | Spring | TRUE | nonsummer
2023-05-17 19:00 | 2023-05-17 20:00 | Spring | TRUE | nonsummer
2023-05-17 20:00 | 2023-05-17 21:00 | Spring | TRUE | nonsummer
2023-05-17 21:00 | 2023-05-17 22:00 | Spring | TRUE | nonsummer
2023-05-17 22:00 | 2023-05-17 23:00 | Spring | FALSE | nonsummer
2023-05-17 23:00 | 2023-05-18 | Spring | FALSE | nonsummer
2023-05-18 | 2023-05-18 01:00 | Spring | FALSE | nonsummer
2023-05-18 01:00 | 2023-05-18 02:00 | Spring | FALSE | nonsummer
2023-05-18 02:00 | 2023-05-18 03:00 | Spring | FALSE | nonsummer
2023-05-18 03:00 | 2023-05-18 04:00 | Spring | FALSE | nonsummer
2023-05-18 04:00 | 2023-05-18 05:00 | Spring | FALSE | nonsummer
2023-05-18 05:00 | 2023-05-18 06:00 | Spring | FALSE | nonsummer
2023-05-18 06:00 | 2023-05-18 07:00 | Spring | FALSE | nonsummer
2023-05-18 07:00 | 2023-05-18 08:00 | Spring | FALSE | nonsummer
2023-05-18 08:00 | 2023-05-18 09:00 | Spring | FALSE | nonsummer
2023-05-18 09:00 | 2023-05-18 10:00 | Spring | FALSE | nonsummer
2023-05-18 10:00 | 2023-05-18 11:00 | Spring | FALSE | nonsummer
2023-05-18 11:00 | 2023-05-18 12:00 | Spring | FALSE | nonsummer
2023-05-18 12:00 | 2023-05-18 13:00 | Spring | FALSE | nonsummer
2023-05-18 13:00 | 2023-05-18 14:00 | Spring | FALSE | nonsummer
2023-05-18 14:00 | 2023-05-18 15:00 | Spring | FALSE | nonsummer
2023-05-18 15:00 | 2023-05-18 16:00 | Spring | FALSE | nonsummer
2023-05-18 16:00 | 2023-05-18 17:00 | Spring | FALSE | nonsummer
2023-05-18 17:00 | 2023-05-18 18:00 | Spring | TRUE | nonsummer
2023-05-18 18:00 | 2023-05-18 19:00 | Spring | TRUE | nonsummer
2023-05-18 19:00 | 2023-05-18 20:00 | Spring | TRUE | nonsummer
2023-05-18 20:00 | 2023-05-18 21:00 | Spring | TRUE | nonsummer
2023-05-18 21:00 | 2023-05-18 22:00 | Spring | TRUE | nonsummer
2023-05-18 22:00 | 2023-05-18 23:00 | Spring | FALSE | nonsummer
2023-05-18 23:00 | 2023-05-19 | Spring | FALSE | nonsummer
2023-05-19 | 2023-05-19 01:00 | Spring | FALSE | nonsummer
2023-05-19 01:00 | 2023-05-19 02:00 | Spring | FALSE | nonsummer
2023-05-19 02:00 | 2023-05-19 03:00 | Spring | FALSE | nonsummer
2023-05-19 03:00 | 2023-05-19 04:00 | Spring | FALSE | nonsummer
2023-05-19 04:00 | 2023-05-19 05:00 | Spring | FALSE | nonsummer
2023-05-19 05:00 | 2023-05-19 06:00 | Spring | FALSE | nonsummer
2023-05-19 06:00 | 2023-05-19 07:00 | Spring | FALSE | nonsummer
2023-05-19 07:00 | 2023-05-19 08:00 | Spring | FALSE | nonsummer
2023-05-19 08:00 | 2023-05-19 09:00 | Spring | FALSE | nonsummer
2023-05-19 09:00 | 2023-05-19 10:00 | Spring | FALSE | nonsummer
2023-05-19 10:00 | 2023-05-19 11:00 | Spring | FALSE | nonsummer
2023-05-19 11:00 | 2023-05-19 12:00 | Spring | FALSE | nonsummer
2023-05-19 12:00 | 2023-05-19 13:00 | Spring | FALSE | nonsummer
2023-05-19 13:00 | 2023-05-19 14:00 | Spring | FALSE | nonsummer
2023-05-19 14:00 | 2023-05-19 15:00 | Spring | FALSE | nonsummer
2023-05-19 15:00 | 2023-05-19 16:00 | Spring | FALSE | nonsummer
2023-05-19 16:00 | 2023-05-19 17:00 | Spring | FALSE | nonsummer
2023-05-19 17:00 | 2023-05-19 18:00 | Spring | TRUE | nonsummer
2023-05-19 18:00 | 2023-05-19 19:00 | Spring | TRUE | nonsummer
2023-05-19 19:00 | 2023-05-19 20:00 | Spring | TRUE | nonsummer
2023-05-19 20:00 | 2023-05-19 21:00 | Spring | TRUE | nonsummer
2023-05-19 21:00 | 2023-05-19 22:00 | Spring | TRUE | nonsummer
2023-05-19 22:00 | 2023-05-19 23:00 | Spring | FALSE | nonsummer
2023-05-19 23:00 | 2023-05-20 | Spring | FALSE | nonsummer
2023-05-20 | 2023-05-20 01:00 | Spring | FALSE | nonsummer
2023-05-20 01:00 | 2023-05-20 02:00 | Spring | FALSE | nonsummer
2023-05-20 02:00 | 2023-05-20 03:00 | Spring | FALSE | nonsummer
2023-05-20 03:00 | 2023-05-20 04:00 | Spring | FALSE | nonsummer
2023-05-20 04:00 | 2023-05-20 05:00 | Spring | FALSE | nonsummer
2023-05-20 05:00 | 2023-05-20 06:00 | Spring | FALSE | nonsummer
2023-05-20 06:00 | 2023-05-20 07:00 | Spring | FALSE | nonsummer
2023-05-20 07:00 | 2023-05-20 08:00 | Spring | FALSE | nonsummer
2023-05-20 08:00 | 2023-05-20 09:00 | Spring | FALSE | nonsummer
2023-05-20 09:00 | 2023-05-20 10:00 | Spring | FALSE | nonsummer
2023-05-20 10:00 | 2023-05-20 11:00 | Spring | FALSE | nonsummer
2023-05-20 11:00 | 2023-05-20 12:00 | Spring | FALSE | nonsummer
2023-05-20 12:00 | 2023-05-20 13:00 | Spring | FALSE | nonsummer
2023-05-20 13:00 | 2023-05-20 14:00 | Spring | FALSE | nonsummer
2023-05-20 14:00 | 2023-05-20 15:00 | Spring | FALSE | nonsummer
2023-05-20 15:00 | 2023-05-20 16:00 | Spring | FALSE | nonsummer
2023-05-20 16:00 | 2023-05-20 17:00 | Spring | FALSE | nonsummer
2023-05-20 17:00 | 2023-05-20 18:00 | Spring | TRUE | nonsummer
2023-05-20 18:00 | 2023-05-20 19:00 | Spring | TRUE | nonsummer
2023-05-20 19:00 | 2023-05-20 20:00 | Spring | TRUE | nonsummer
2023-05-20 20:00 | 2023-05-20 21:00 | Spring | TRUE | nonsummer
2023-05-20 21:00 | 2023-05-20 22:00 | Spring | TRUE | nonsummer
2023-05-20 22:00 | 2023-05-20 23:00 | Spring | FALSE | nonsummer
2023-05-20 23:00 | 2023-05-21 | Spring | FALSE | nonsummer
2023-05-21 | 2023-05-21 01:00 | Spring | FALSE | nonsummer
2023-05-21 01:00 | 2023-05-21 02:00 | Spring | FALSE | nonsummer
2023-05-21 02:00 | 2023-05-21 03:00 | Spring | FALSE | nonsummer
2023-05-21 03:00 | 2023-05-21 04:00 | Spring | FALSE | nonsummer
2023-05-21 04:00 | 2023-05-21 05:00 | Spring | FALSE | nonsummer
2023-05-21 05:00 | 2023-05-21 06:00 | Spring | FALSE | nonsummer
2023-05-21 06:00 | 2023-05-21 07:00 | Spring | FALSE | nonsummer
2023-05-21 07:00 | 2023-05-21 08:00 | Spring | FALSE | nonsummer
2023-05-21 08:00 | 2023-05-21 09:00 | Spring | FALSE | nonsummer
2023-05-21 09:00 | 2023-05-21 10:00 | Spring | FALSE | nonsummer
2023-05-21 10:00 | 2023-05-21 11:00 | Spring | FALSE | nonsummer
2023-05-21 11:00 | 2023-05-21 12:00 | Spring | FALSE | nonsummer
2023-05-21 12:00 | 2023-05-21 13:00 | Spring | FALSE | nonsummer
2023-05-21 13:00 | 2023-05-21 14:00 | Spring | FALSE | nonsummer
2023-05-21 14:00 | 2023-05-21 15:00 | Spring | FALSE | nonsummer
2023-05-21 15:00 | 2023-05-21 16:00 | Spring | FALSE | nonsummer
2023-05-21 16:00 | 2023-05-21 17:00 | Spring | FALSE | nonsummer
2023-05-21 17:00 | 2023-05-21 18:00 | Spring | TRUE | nonsummer
2023-05-21 18:00 | 2023-05-21 19:00 | Spring | TRUE | nonsummer
2023-05-21 19:00 | 2023-05-21 20:00 | Spring | TRUE | nonsummer
2023-05-21 20:00 | 2023-05-21 21:00 | Spring | TRUE | nonsummer
2023-05-21 21:00 | 2023-05-21 22:00 | Spring | TRUE | nonsummer
2023-05-21 22:00 | 2023-05-21 23:00 | Spring | FALSE | nonsummer
2023-05-21 23:00 | 2023-05-22 | Spring | FALSE | nonsummer
2023-05-22 | 2023-05-22 01:00 | Spring | FALSE | nonsummer
2023-05-22 01:00 | 2023-05-22 02:00 | Spring | FALSE | nonsummer
2023-05-22 02:00 | 2023-05-22 03:00 | Spring | FALSE | nonsummer
2023-05-22 03:00 | 2023-05-22 04:00 | Spring | FALSE | nonsummer
2023-05-22 04:00 | 2023-05-22 05:00 | Spring | FALSE | nonsummer
2023-05-22 05:00 | 2023-05-22 06:00 | Spring | FALSE | nonsummer
2023-05-22 06:00 | 2023-05-22 07:00 | Spring | FALSE | nonsummer
2023-05-22 07:00 | 2023-05-22 08:00 | Spring | FALSE | nonsummer
2023-05-22 08:00 | 2023-05-22 09:00 | Spring | FALSE | nonsummer
2023-05-22 09:00 | 2023-05-22 10:00 | Spring | FALSE | nonsummer
2023-05-22 10:00 | 2023-05-22 11:00 | Spring | FALSE | nonsummer
2023-05-22 11:00 | 2023-05-22 12:00 | Spring | FALSE | nonsummer
2023-05-22 12:00 | 2023-05-22 13:00 | Spring | FALSE | nonsummer
2023-05-22 13:00 | 2023-05-22 14:00 | Spring | FALSE | nonsummer
2023-05-22 14:00 | 2023-05-22 15:00 | Spring | FALSE | nonsummer
2023-05-22 15:00 | 2023-05-22 16:00 | Spring | FALSE | nonsummer
2023-05-22 16:00 | 2023-05-22 17:00 | Spring | FALSE | nonsummer
2023-05-22 17:00 | 2023-05-22 18:00 | Spring | TRUE | nonsummer
2023-05-22 18:00 | 2023-05-22 19:00 | Spring | TRUE | nonsummer
2023-05-22 19:00 | 2023-05-22 20:00 | Spring | TRUE | nonsummer
2023-05-22 20:00 | 2023-05-22 21:00 | Spring | TRUE | nonsummer
2023-05-22 21:00 | 2023-05-22 22:00 | Spring | TRUE | nonsummer
2023-05-22 22:00 | 2023-05-22 23:00 | Spring | FALSE | nonsummer
2023-05-22 23:00 | 2023-05-23 | Spring | FALSE | nonsummer
2023-05-23 | 2023-05-23 01:00 | Spring | FALSE | nonsummer
2023-05-23 01:00 | 2023-05-23 02:00 | Spring | FALSE | nonsummer
2023-05-23 02:00 | 2023-05-23 03:00 | Spring | FALSE | nonsummer
2023-05-23 03:00 | 2023-05-23 04:00 | Spring | FALSE | nonsummer
2023-05-23 04:00 | 2023-05-23 05:00 | Spring | FALSE | nonsummer
2023-05-23 05:00 | 2023-05-23 06:00 | Spring | FALSE | nonsummer
2023-05-23 06:00 | 2023-05-23 07:00 | Spring | FALSE | nonsummer
2023-05-23 07:00 | 2023-05-23 08:00 | Spring | FALSE | nonsummer
2023-05-23 08:00 | 2023-05-23 09:00 | Spring | FALSE | nonsummer
2023-05-23 09:00 | 2023-05-23 10:00 | Spring | FALSE | nonsummer
2023-05-23 10:00 | 2023-05-23 11:00 | Spring | FALSE | nonsummer
2023-05-23 11:00 | 2023-05-23 12:00 | Spring | FALSE | nonsummer
2023-05-23 12:00 | 2023-05-23 13:00 | Spring | FALSE | nonsummer
2023-05-23 13:00 | 2023-05-23 14:00 | Spring | FALSE | nonsummer
2023-05-23 14:00 | 2023-05-23 15:00 | Spring | FALSE | nonsummer
2023-05-23 15:00 | 2023-05-23 16:00 | Spring | FALSE | nonsummer
2023-05-23 16:00 | 2023-05-23 17:00 | Spring | FALSE | nonsummer
2023-05-23 17:00 | 2023-05-23 18:00 | Spring | TRUE | nonsummer
2023-05-23 18:00 | 2023-05-23 19:00 | Spring | TRUE | nonsummer
2023-05-23 19:00 | 2023-05-23 20:00 | Spring | TRUE | nonsummer
2023-05-23 20:00 | 2023-05-23 21:00 | Spring | TRUE | nonsummer
2023-05-23 21:00 | 2023-05-23 22:00 | Spring | TRUE | nonsummer
2023-05-23 22:00 | 2023-05-23 23:00 | Spring | FALSE | nonsummer
2023-05-23 23:00 | 2023-05-24 | Spring | FALSE | nonsummer
2023-05-24 | 2023-05-24 01:00 | Spring | FALSE | nonsummer
2023-05-24 01:00 | 2023-05-24 02:00 | Spring | FALSE | nonsummer
2023-05-24 02:00 | 2023-05-24 03:00 | Spring | FALSE | nonsummer
2023-05-24 03:00 | 2023-05-24 04:00 | Spring | FALSE | nonsummer
2023-05-24 04:00 | 2023-05-24 05:00 | Spring | FALSE | nonsummer
2023-05-24 05:00 | 2023-05-24 06:00 | Spring | FALSE | nonsummer
2023-05-24 06:00 | 2023-05-24 07:00 | Spring | FALSE | nonsummer
2023-05-24 07:00 | 2023-05-24 08:00 | Spring | FALSE | nonsummer
2023-05-24 08:00 | 2023-05-24 09:00 | Spring | FALSE | nonsummer
2023-05-24 09:00 | 2023-05-24 10:00 | Spring | FALSE | nonsummer
2023-05-24 10:00 | 2023-05-24 11:00 | Spring | FALSE | nonsummer
2023-05-24 11:00 | 2023-05-24 12:00 | Spring | FALSE | nonsummer
2023-05-24 12:00 | 2023-05-24 13:00 | Spring | FALSE | nonsummer
2023-05-24 13:00 | 2023-05-24 14:00 | Spring | FALSE | nonsummer
2023-05-24 14:00 | 2023-05-24 15:00 | Spring | FALSE | nonsummer
2023-05-24 15:00 | 2023-05-24 16:00 | Spring | FALSE | nonsummer
2023-05-24 16:00 | 2023-05-24 17:00 | Spring | FALSE | nonsummer
2023-05-24 17:00 | 2023-05-24 18:00 | Spring | TRUE | nonsummer
2023-05-24 18:00 | 2023-05-24 19:00 | Spring | TRUE | nonsummer
2023-05-24 19:00 | 2023-05-24 20:00 | Spring | TRUE | nonsummer
2023-05-24 20:00 | 2023-05-24 21:00 | Spring | TRUE | nonsummer
2023-05-24 21:00 | 2023-05-24 22:00 | Spring | TRUE | nonsummer
2023-05-24 22:00 | 2023-05-24 23:00 | Spring | FALSE | nonsummer
2023-05-24 23:00 | 2023-05-25 | Spring | FALSE | nonsummer
2023-05-25 | 2023-05-25 01:00 | Spring | FALSE | nonsummer
2023-05-25 01:00 | 2023-05-25 02:00 | Spring | FALSE | nonsummer
2023-05-25 02:00 | 2023-05-25 03:00 | Spring | FALSE | nonsummer
2023-05-25 03:00 | 2023-05-25 04:00 | Spring | FALSE | nonsummer
2023-05-25 04:00 | 2023-05-25 05:00 | Spring | FALSE | nonsummer
2023-05-25 05:00 | 2023-05-25 06:00 | Spring | FALSE | nonsummer
2023-05-25 06:00 | 2023-05-25 07:00 | Spring | FALSE | nonsummer
2023-05-25 07:00 | 2023-05-25 08:00 | Spring | FALSE | nonsummer
2023-05-25 08:00 | 2023-05-25 09:00 | Spring | FALSE | nonsummer
2023-05-25 09:00 | 2023-05-25 10:00 | Spring | FALSE | nonsummer
2023-05-25 10:00 | 2023-05-25 11:00 | Spring | FALSE | nonsummer
2023-05-25 11:00 | 2023-05-25 12:00 | Spring | FALSE | nonsummer
2023-05-25 12:00 | 2023-05-25 13:00 | Spring | FALSE | nonsummer
2023-05-25 13:00 | 2023-05-25 14:00 | Spring | FALSE | nonsummer
2023-05-25 14:00 | 2023-05-25 15:00 | Spring | FALSE | nonsummer
2023-05-25 15:00 | 2023-05-25 16:00 | Spring | FALSE | nonsummer
2023-05-25 16:00 | 2023-05-25 17:00 | Spring | FALSE | nonsummer
2023-05-25 17:00 | 2023-05-25 18:00 | Spring | TRUE | nonsummer
2023-05-25 18:00 | 2023-05-25 19:00 | Spring | TRUE | nonsummer
2023-05-25 19:00 | 2023-05-25 20:00 | Spring | TRUE | nonsummer
2023-05-25 20:00 | 2023-05-25 21:00 | Spring | TRUE | nonsummer
2023-05-25 21:00 | 2023-05-25 22:00 | Spring | TRUE | nonsummer
2023-05-25 22:00 | 2023-05-25 23:00 | Spring | FALSE | nonsummer
2023-05-25 23:00 | 2023-05-26 | Spring | FALSE | nonsummer
2023-05-26 | 2023-05-26 01:00 | Spring | FALSE | nonsummer
2023-05-26 01:00 | 2023-05-26 02:00 | Spring | FALSE | nonsummer
2023-05-26 02:00 | 2023-05-26 03:00 | Spring | FALSE | nonsummer
2023-05-26 03:00 | 2023-05-26 04:00 | Spring | FALSE | nonsummer
2023-05-26 04:00 | 2023-05-26 05:00 | Spring | FALSE | nonsummer
2023-05-26 05:00 | 2023-05-26 06:00 | Spring | FALSE | nonsummer
2023-05-26 06:00 | 2023-05-26 07:00 | Spring | FALSE | nonsummer
2023-05-26 07:00 | 2023-05-26 08:00 | Spring | FALSE | nonsummer
2023-05-26 08:00 | 2023-05-26 09:00 | Spring | FALSE | nonsummer
2023-05-26 09:00 | 2023-05-26 10:00 | Spring | FALSE | nonsummer
2023-05-26 10:00 | 2023-05-26 11:00 | Spring | FALSE | nonsummer
2023-05-26 11:00 | 2023-05-26 12:00 | Spring | FALSE | nonsummer
2023-05-26 12:00 | 2023-05-26 13:00 | Spring | FALSE | nonsummer
2023-05-26 13:00 | 2023-05-26 14:00 | Spring | FALSE | nonsummer
2023-05-26 14:00 | 2023-05-26 15:00 | Spring | FALSE | nonsummer
2023-05-26 15:00 | 2023-05-26 16:00 | Spring | FALSE | nonsummer
2023-05-26 16:00 | 2023-05-26 17:00 | Spring | FALSE | nonsummer
2023-05-26 17:00 | 2023-05-26 18:00 | Spring | TRUE | nonsummer
2023-05-26 18:00 | 2023-05-26 19:00 | Spring | TRUE | nonsummer
2023-05-26 19:00 | 2023-05-26 20:00 | Spring | TRUE | nonsummer
2023-05-26 20:00 | 2023-05-26 21:00 | Spring | TRUE | nonsummer
2023-05-26 21:00 | 2023-05-26 22:00 | Spring | TRUE | nonsummer
2023-05-26 22:00 | 2023-05-26 23:00 | Spring | FALSE | nonsummer
2023-05-26 23:00 | 2023-05-27 | Spring | FALSE | nonsummer
2023-05-27 | 2023-05-27 01:00 | Spring | FALSE | nonsummer
2023-05-27 01:00 | 2023-05-27 02:00 | Spring | FALSE | nonsummer
2023-05-27 02:00 | 2023-05-27 03:00 | Spring | FALSE | nonsummer
2023-05-27 03:00 | 2023-05-27 04:00 | Spring | FALSE | nonsummer
2023-05-27 04:00 | 2023-05-27 05:00 | Spring | FALSE | nonsummer
2023-05-27 05:00 | 2023-05-27 06:00 | Spring | FALSE | nonsummer
2023-05-27 06:00 | 2023-05-27 07:00 | Spring | FALSE | nonsummer
2023-05-27 07:00 | 2023-05-27 08:00 | Spring | FALSE | nonsummer
2023-05-27 08:00 | 2023-05-27 09:00 | Spring | FALSE | nonsummer
2023-05-27 09:00 | 2023-05-27 10:00 | Spring | FALSE | nonsummer
2023-05-27 10:00 | 2023-05-27 11:00 | Spring | FALSE | nonsummer
2023-05-27 11:00 | 2023-05-27 12:00 | Spring | FALSE | nonsummer
2023-05-27 12:00 | 2023-05-27 13:00 | Spring | FALSE | nonsummer
2023-05-27 13:00 | 2023-05-27 14:00 | Spring | FALSE | nonsummer
2023-05-27 14:00 | 2023-05-27 15:00 | Spring | FALSE | nonsummer
2023-05-27 15:00 | 2023-05-27 16:00 | Spring | FALSE | nonsummer
2023-05-27 16:00 | 2023-05-27 17:00 | Spring | FALSE | nonsummer
2023-05-27 17:00 | 2023-05-27 18:00 | Spring | TRUE | nonsummer
2023-05-27 18:00 | 2023-05-27 19:00 | Spring | TRUE | nonsummer
2023-05-27 19:00 | 2023-05-27 20:00 | Spring | TRUE | nonsummer
2023-05-27 20:00 | 2023-05-27 21:00 | Spring | TRUE | nonsummer
2023-05-27 21:00 | 2023-05-27 22:00 | Spring | TRUE | nonsummer
2023-05-27 22:00 | 2023-05-27 23:00 | Spring | FALSE | nonsummer
2023-05-27 23:00 | 2023-05-28 | Spring | FALSE | nonsummer
2023-05-28 | 2023-05-28 01:00 | Spring | FALSE | nonsummer
2023-05-28 01:00 | 2023-05-28 02:00 | Spring | FALSE | nonsummer
2023-05-28 02:00 | 2023-05-28 03:00 | Spring | FALSE | nonsummer
2023-05-28 03:00 | 2023-05-28 04:00 | Spring | FALSE | nonsummer
2023-05-28 04:00 | 2023-05-28 05:00 | Spring | FALSE | nonsummer
2023-05-28 05:00 | 2023-05-28 06:00 | Spring | FALSE | nonsummer
2023-05-28 06:00 | 2023-05-28 07:00 | Spring | FALSE | nonsummer
2023-05-28 07:00 | 2023-05-28 08:00 | Spring | FALSE | nonsummer
2023-05-28 08:00 | 2023-05-28 09:00 | Spring | FALSE | nonsummer
2023-05-28 09:00 | 2023-05-28 10:00 | Spring | FALSE | nonsummer
2023-05-28 10:00 | 2023-05-28 11:00 | Spring | FALSE | nonsummer
2023-05-28 11:00 | 2023-05-28 12:00 | Spring | FALSE | nonsummer
2023-05-28 12:00 | 2023-05-28 13:00 | Spring | FALSE | nonsummer
2023-05-28 13:00 | 2023-05-28 14:00 | Spring | FALSE | nonsummer
2023-05-28 14:00 | 2023-05-28 15:00 | Spring | FALSE | nonsummer
2023-05-28 15:00 | 2023-05-28 16:00 | Spring | FALSE | nonsummer
2023-05-28 16:00 | 2023-05-28 17:00 | Spring | FALSE | nonsummer
2023-05-28 17:00 | 2023-05-28 18:00 | Spring | TRUE | nonsummer
2023-05-28 18:00 | 2023-05-28 19:00 | Spring | TRUE | nonsummer
2023-05-28 19:00 | 2023-05-28 20:00 | Spring | TRUE | nonsummer
2023-05-28 20:00 | 2023-05-28 21:00 | Spring | TRUE | nonsummer
2023-05-28 21:00 | 2023-05-28 22:00 | Spring | TRUE | nonsummer
2023-05-28 22:00 | 2023-05-28 23:00 | Spring | FALSE | nonsummer
2023-05-28 23:00 | 2023-05-29 | Spring | FALSE | nonsummer
2023-05-29 | 2023-05-29 01:00 | Spring | FALSE | nonsummer
2023-05-29 01:00 | 2023-05-29 02:00 | Spring | FALSE | nonsummer
2023-05-29 02:00 | 2023-05-29 03:00 | Spring | FALSE | nonsummer
2023-05-29 03:00 | 2023-05-29 04:00 | Spring | FALSE | nonsummer
2023-05-29 04:00 | 2023-05-29 05:00 | Spring | FALSE | nonsummer
2023-05-29 05:00 | 2023-05-29 06:00 | Spring | FALSE | nonsummer
2023-05-29 06:00 | 2023-05-29 07:00 | Spring | FALSE | nonsummer
2023-05-29 07:00 | 2023-05-29 08:00 | Spring | FALSE | nonsummer
2023-05-29 08:00 | 2023-05-29 09:00 | Spring | FALSE | nonsummer
2023-05-29 09:00 | 2023-05-29 10:00 | Spring | FALSE | nonsummer
2023-05-29 10:00 | 2023-05-29 11:00 | Spring | FALSE | nonsummer
2023-05-29 11:00 | 2023-05-29 12:00 | Spring | FALSE | nonsummer
2023-05-29 12:00 | 2023-05-29 13:00 | Spring | FALSE | nonsummer
2023-05-29 13:00 | 2023-05-29 14:00 | Spring | FALSE | nonsummer
2023-05-29 14:00 | 2023-05-29 15:00 | Spring | FALSE | nonsummer
2023-05-29 15:00 | 2023-05-29 16:00 | Spring | FALSE | nonsummer
2023-05-29 16:00 | 2023-05-29 17:00 | Spring | FALSE | nonsummer
2023-05-29 17:00 | 2023-05-29 18:00 | Spring | TRUE | nonsummer
2023-05-29 18:00 | 2023-05-29 19:00 | Spring | TRUE | nonsummer
2023-05-29 19:00 | 2023-05-29 20:00 | Spring | TRUE | nonsummer
2023-05-29 20:00 | 2023-05-29 21:00 | Spring | TRUE | nonsummer
2023-05-29 21:00 | 2023-05-29 22:00 | Spring | TRUE | nonsummer
2023-05-29 22:00 | 2023-05-29 23:00 | Spring | FALSE | nonsummer
2023-05-29 23:00 | 2023-05-30 | Spring | FALSE | nonsummer
2023-05-30 | 2023-05-30 01:00 | Spring | FALSE | nonsummer
2023-05-30 01:00 | 2023-05-30 02:00 | Spring | FALSE | nonsummer
2023-05-30 02:00 | 2023-05-30 03:00 | Spring | FALSE | nonsummer
2023-05-30 03:00 | 2023-05-30 04:00 | Spring | FALSE | nonsummer
2023-05-30 04:00 | 2023-05-30 05:00 | Spring | FALSE | nonsummer
2023-05-30 05:00 | 2023-05-30 06:00 | Spring | FALSE | nonsummer
2023-05-30 06:00 | 2023-05-30 07:00 | Spring | FALSE | nonsummer
2023-05-30 07:00 | 2023-05-30 08:00 | Spring | FALSE | nonsummer
2023-05-30 08:00 | 2023-05-30 09:00 | Spring | FALSE | nonsummer
2023-05-30 09:00 | 2023-05-30 10:00 | Spring | FALSE | nonsummer
2023-05-30 10:00 | 2023-05-30 11:00 | Spring | FALSE | nonsummer
2023-05-30 11:00 | 2023-05-30 12:00 | Spring | FALSE | nonsummer
2023-05-30 12:00 | 2023-05-30 13:00 | Spring | FALSE | nonsummer
2023-05-30 13:00 | 2023-05-30 14:00 | Spring | FALSE | nonsummer
2023-05-30 14:00 | 2023-05-30 15:00 | Spring | FALSE | nonsummer
2023-05-30 15:00 | 2023-05-30 16:00 | Spring | FALSE | nonsummer
2023-05-30 16:00 | 2023-05-30 17:00 | Spring | FALSE | nonsummer
2023-05-30 17:00 | 2023-05-30 18:00 | Spring | TRUE | nonsummer
2023-05-30 18:00 | 2023-05-30 19:00 | Spring | TRUE | nonsummer
2023-05-30 19:00 | 2023-05-30 20:00 | Spring | TRUE | nonsummer
2023-05-30 20:00 | 2023-05-30 21:00 | Spring | TRUE | nonsummer
2023-05-30 21:00 | 2023-05-30 22:00 | Spring | TRUE | nonsummer
2023-05-30 22:00 | 2023-05-30 23:00 | Spring | FALSE | nonsummer
2023-05-30 23:00 | 2023-05-31 | Spring | FALSE | nonsummer
2023-05-31 | 2023-05-31 01:00 | Spring | FALSE | nonsummer
2023-05-31 01:00 | 2023-05-31 02:00 | Spring | FALSE | nonsummer
2023-05-31 02:00 | 2023-05-31 03:00 | Spring | FALSE | nonsummer
2023-05-31 03:00 | 2023-05-31 04:00 | Spring | FALSE | nonsummer
2023-05-31 04:00 | 2023-05-31 05:00 | Spring | FALSE | nonsummer
2023-05-31 05:00 | 2023-05-31 06:00 | Spring | FALSE | nonsummer
2023-05-31 06:00 | 2023-05-31 07:00 | Spring | FALSE | nonsummer
2023-05-31 07:00 | 2023-05-31 08:00 | Spring | FALSE | nonsummer
2023-05-31 08:00 | 2023-05-31 09:00 | Spring | FALSE | nonsummer
2023-05-31 09:00 | 2023-05-31 10:00 | Spring | FALSE | nonsummer
2023-05-31 10:00 | 2023-05-31 11:00 | Spring | FALSE | nonsummer
2023-05-31 11:00 | 2023-05-31 12:00 | Spring | FALSE | nonsummer
2023-05-31 12:00 | 2023-05-31 13:00 | Spring | FALSE | nonsummer
2023-05-31 13:00 | 2023-05-31 14:00 | Spring | FALSE | nonsummer
2023-05-31 14:00 | 2023-05-31 15:00 | Spring | FALSE | nonsummer
2023-05-31 15:00 | 2023-05-31 16:00 | Spring | FALSE | nonsummer
2023-05-31 16:00 | 2023-05-31 17:00 | Spring | FALSE | nonsummer
2023-05-31 17:00 | 2023-05-31 18:00 | Spring | TRUE | nonsummer
2023-05-31 18:00 | 2023-05-31 19:00 | Spring | TRUE | nonsummer
2023-05-31 19:00 | 2023-05-31 20:00 | Spring | TRUE | nonsummer
2023-05-31 20:00 | 2023-05-31 21:00 | Spring | TRUE | nonsummer
2023-05-31 21:00 | 2023-05-31 22:00 | Spring | TRUE | nonsummer
2023-05-31 22:00 | 2023-05-31 23:00 | Spring | FALSE | nonsummer
2023-05-31 23:00 | 2023-06-01 | Spring | FALSE | nonsummer
2023-06-01 | 2023-06-01 01:00 | Summer | FALSE | summer
2023-06-01 01:00 | 2023-06-01 02:00 | Summer | FALSE | summer
2023-06-01 02:00 | 2023-06-01 03:00 | Summer | FALSE | summer
2023-06-01 03:00 | 2023-06-01 04:00 | Summer | FALSE | summer
2023-06-01 04:00 | 2023-06-01 05:00 | Summer | FALSE | summer
2023-06-01 05:00 | 2023-06-01 06:00 | Summer | FALSE | summer
2023-06-01 06:00 | 2023-06-01 07:00 | Summer | FALSE | summer
2023-06-01 07:00 | 2023-06-01 08:00 | Summer | FALSE | summer
2023-06-01 08:00 | 2023-06-01 09:00 | Summer | FALSE | summer
2023-06-01 09:00 | 2023-06-01 10:00 | Summer | FALSE | summer
2023-06-01 10:00 | 2023-06-01 11:00 | Summer | FALSE | summer
2023-06-01 11:00 | 2023-06-01 12:00 | Summer | FALSE | summer
2023-06-01 12:00 | 2023-06-01 13:00 | Summer | FALSE | summer
2023-06-01 13:00 | 2023-06-01 14:00 | Summer | FALSE | summer
2023-06-01 14:00 | 2023-06-01 15:00 | Summer | FALSE | summer
2023-06-01 15:00 | 2023-06-01 16:00 | Summer | FALSE | summer
2023-06-01 16:00 | 2023-06-01 17:00 | Summer | TRUE | summer
2023-06-01 17:00 | 2023-06-01 18:00 | Summer | TRUE | summer
2023-06-01 18:00 | 2023-06-01 19:00 | Summer | TRUE | summer
2023-06-01 19:00 | 2023-06-01 20:00 | Summer | TRUE | summer
2023-06-01 20:00 | 2023-06-01 21:00 | Summer | TRUE | summer
2023-06-01 21:00 | 2023-06-01 22:00 | Summer | FALSE | summer
2023-06-01 22:00 | 2023-06-01 23:00 | Summer | FALSE | summer
2023-06-01 23:00 | 2023-06-02 | Summer | FALSE | summer
2023-06-02 | 2023-06-02 01:00 | Summer | FALSE | summer
2023-06-02 01:00 | 2023-06-02 02:00 | Summer | FALSE | summer
2023-06-02 02:00 | 2023-06-02 03:00 | Summer | FALSE | summer
2023-06-02 03:00 | 2023-06-02 04:00 | Summer | FALSE | summer
2023-06-02 04:00 | 2023-06-02 05:00 | Summer | FALSE | summer
2023-06-02 05:00 | 2023-06-02 06:00 | Summer | FALSE | summer
2023-06-02 06:00 | 2023-06-02 07:00 | Summer | FALSE | summer
2023-06-02 07:00 | 2023-06-02 08:00 | Summer | FALSE | summer
2023-06-02 08:00 | 2023-06-02 09:00 | Summer | FALSE | summer
2023-06-02 09:00 | 2023-06-02 10:00 | Summer | FALSE | summer
2023-06-02 10:00 | 2023-06-02 11:00 | Summer | FALSE | summer
2023-06-02 11:00 | 2023-06-02 12:00 | Summer | FALSE | summer
2023-06-02 12:00 | 2023-06-02 13:00 | Summer | FALSE | summer
2023-06-02 13:00 | 2023-06-02 14:00 | Summer | FALSE | summer
2023-06-02 14:00 | 2023-06-02 15:00 | Summer | FALSE | summer
2023-06-02 15:00 | 2023-06-02 16:00 | Summer | FALSE | summer
2023-06-02 16:00 | 2023-06-02 17:00 | Summer | TRUE | summer
2023-06-02 17:00 | 2023-06-02 18:00 | Summer | TRUE | summer
2023-06-02 18:00 | 2023-06-02 19:00 | Summer | TRUE | summer
2023-06-02 19:00 | 2023-06-02 20:00 | Summer | TRUE | summer
2023-06-02 20:00 | 2023-06-02 21:00 | Summer | TRUE | summer
2023-06-02 21:00 | 2023-06-02 22:00 | Summer | FALSE | summer
2023-06-02 22:00 | 2023-06-02 23:00 | Summer | FALSE | summer
2023-06-02 23:00 | 2023-06-03 | Summer | FALSE | summer
2023-06-03 | 2023-06-03 01:00 | Summer | FALSE | summer
2023-06-03 01:00 | 2023-06-03 02:00 | Summer | FALSE | summer
2023-06-03 02:00 | 2023-06-03 03:00 | Summer | FALSE | summer
2023-06-03 03:00 | 2023-06-03 04:00 | Summer | FALSE | summer
2023-06-03 04:00 | 2023-06-03 05:00 | Summer | FALSE | summer
2023-06-03 05:00 | 2023-06-03 06:00 | Summer | FALSE | summer
2023-06-03 06:00 | 2023-06-03 07:00 | Summer | FALSE | summer
2023-06-03 07:00 | 2023-06-03 08:00 | Summer | FALSE | summer
2023-06-03 08:00 | 2023-06-03 09:00 | Summer | FALSE | summer
2023-06-03 09:00 | 2023-06-03 10:00 | Summer | FALSE | summer
2023-06-03 10:00 | 2023-06-03 11:00 | Summer | FALSE | summer
2023-06-03 11:00 | 2023-06-03 12:00 | Summer | FALSE | summer
2023-06-03 12:00 | 2023-06-03 13:00 | Summer | FALSE | summer
2023-06-03 13:00 | 2023-06-03 14:00 | Summer | FALSE | summer
2023-06-03 14:00 | 2023-06-03 15:00 | Summer | FALSE | summer
2023-06-03 15:00 | 2023-06-03 16:00 | Summer | FALSE | summer
2023-06-03 16:00 | 2023-06-03 17:00 | Summer | TRUE | summer
2023-06-03 17:00 | 2023-06-03 18:00 | Summer | TRUE | summer
2023-06-03 18:00 | 2023-06-03 19:00 | Summer | TRUE | summer
2023-06-03 19:00 | 2023-06-03 20:00 | Summer | TRUE | summer
2023-06-03 20:00 | 2023-06-03 21:00 | Summer | TRUE | summer
2023-06-03 21:00 | 2023-06-03 22:00 | Summer | FALSE | summer
2023-06-03 22:00 | 2023-06-03 23:00 | Summer | FALSE | summer
2023-06-03 23:00 | 2023-06-04 | Summer | FALSE | summer
2023-06-04 | 2023-06-04 01:00 | Summer | FALSE | summer
2023-06-04 01:00 | 2023-06-04 02:00 | Summer | FALSE | summer
2023-06-04 02:00 | 2023-06-04 03:00 | Summer | FALSE | summer
2023-06-04 03:00 | 2023-06-04 04:00 | Summer | FALSE | summer
2023-06-04 04:00 | 2023-06-04 05:00 | Summer | FALSE | summer
2023-06-04 05:00 | 2023-06-04 06:00 | Summer | FALSE | summer
2023-06-04 06:00 | 2023-06-04 07:00 | Summer | FALSE | summer
2023-06-04 07:00 | 2023-06-04 08:00 | Summer | FALSE | summer
2023-06-04 08:00 | 2023-06-04 09:00 | Summer | FALSE | summer
2023-06-04 09:00 | 2023-06-04 10:00 | Summer | FALSE | summer
2023-06-04 10:00 | 2023-06-04 11:00 | Summer | FALSE | summer
2023-06-04 11:00 | 2023-06-04 12:00 | Summer | FALSE | summer
2023-06-04 12:00 | 2023-06-04 13:00 | Summer | FALSE | summer
2023-06-04 13:00 | 2023-06-04 14:00 | Summer | FALSE | summer
2023-06-04 14:00 | 2023-06-04 15:00 | Summer | FALSE | summer
2023-06-04 15:00 | 2023-06-04 16:00 | Summer | FALSE | summer
2023-06-04 16:00 | 2023-06-04 17:00 | Summer | TRUE | summer
2023-06-04 17:00 | 2023-06-04 18:00 | Summer | TRUE | summer
2023-06-04 18:00 | 2023-06-04 19:00 | Summer | TRUE | summer
2023-06-04 19:00 | 2023-06-04 20:00 | Summer | TRUE | summer
2023-06-04 20:00 | 2023-06-04 21:00 | Summer | TRUE | summer
2023-06-04 21:00 | 2023-06-04 22:00 | Summer | FALSE | summer
2023-06-04 22:00 | 2023-06-04 23:00 | Summer | FALSE | summer
2023-06-04 23:00 | 2023-06-05 | Summer | FALSE | summer
2023-06-05 | 2023-06-05 01:00 | Summer | FALSE | summer
2023-06-05 01:00 | 2023-06-05 02:00 | Summer | FALSE | summer
2023-06-05 02:00 | 2023-06-05 03:00 | Summer | FALSE | summer
2023-06-05 03:00 | 2023-06-05 04:00 | Summer | FALSE | summer
2023-06-05 04:00 | 2023-06-05 05:00 | Summer | FALSE | summer
2023-06-05 05:00 | 2023-06-05 06:00 | Summer | FALSE | summer
2023-06-05 06:00 | 2023-06-05 07:00 | Summer | FALSE | summer
2023-06-05 07:00 | 2023-06-05 08:00 | Summer | FALSE | summer
2023-06-05 08:00 | 2023-06-05 09:00 | Summer | FALSE | summer
2023-06-05 09:00 | 2023-06-05 10:00 | Summer | FALSE | summer
2023-06-05 10:00 | 2023-06-05 11:00 | Summer | FALSE | summer
2023-06-05 11:00 | 2023-06-05 12:00 | Summer | FALSE | summer
2023-06-05 12:00 | 2023-06-05 13:00 | Summer | FALSE | summer
2023-06-05 13:00 | 2023-06-05 14:00 | Summer | FALSE | summer
2023-06-05 14:00 | 2023-06-05 15:00 | Summer | FALSE | summer
2023-06-05 15:00 | 2023-06-05 16:00 | Summer | FALSE | summer
2023-06-05 16:00 | 2023-06-05 17:00 | Summer | TRUE | summer
2023-06-05 17:00 | 2023-06-05 18:00 | Summer | TRUE | summer
2023-06-05 18:00 | 2023-06-05 19:00 | Summer | TRUE | summer
2023-06-05 19:00 | 2023-06-05 20:00 | Summer | TRUE | summer
2023-06-05 20:00 | 2023-06-05 21:00 | Summer | TRUE | summer
2023-06-05 21:00 | 2023-06-05 22:00 | Summer | FALSE | summer
2023-06-05 22:00 | 2023-06-05 23:00 | Summer | FALSE | summer
2023-06-05 23:00 | 2023-06-06 | Summer | FALSE | summer
2023-06-06 | 2023-06-06 01:00 | Summer | FALSE | summer
2023-06-06 01:00 | 2023-06-06 02:00 | Summer | FALSE | summer
2023-06-06 02:00 | 2023-06-06 03:00 | Summer | FALSE | summer
2023-06-06 03:00 | 2023-06-06 04:00 | Summer | FALSE | summer
2023-06-06 04:00 | 2023-06-06 05:00 | Summer | FALSE | summer
2023-06-06 05:00 | 2023-06-06 06:00 | Summer | FALSE | summer
2023-06-06 06:00 | 2023-06-06 07:00 | Summer | FALSE | summer
2023-06-06 07:00 | 2023-06-06 08:00 | Summer | FALSE | summer
2023-06-06 08:00 | 2023-06-06 09:00 | Summer | FALSE | summer
2023-06-06 09:00 | 2023-06-06 10:00 | Summer | FALSE | summer
2023-06-06 10:00 | 2023-06-06 11:00 | Summer | FALSE | summer
2023-06-06 11:00 | 2023-06-06 12:00 | Summer | FALSE | summer
2023-06-06 12:00 | 2023-06-06 13:00 | Summer | FALSE | summer
2023-06-06 13:00 | 2023-06-06 14:00 | Summer | FALSE | summer
2023-06-06 14:00 | 2023-06-06 15:00 | Summer | FALSE | summer
2023-06-06 15:00 | 2023-06-06 16:00 | Summer | FALSE | summer
2023-06-06 16:00 | 2023-06-06 17:00 | Summer | TRUE | summer
2023-06-06 17:00 | 2023-06-06 18:00 | Summer | TRUE | summer
2023-06-06 18:00 | 2023-06-06 19:00 | Summer | TRUE | summer
2023-06-06 19:00 | 2023-06-06 20:00 | Summer | TRUE | summer
2023-06-06 20:00 | 2023-06-06 21:00 | Summer | TRUE | summer
2023-06-06 21:00 | 2023-06-06 22:00 | Summer | FALSE | summer
2023-06-06 22:00 | 2023-06-06 23:00 | Summer | FALSE | summer
2023-06-06 23:00 | 2023-06-07 | Summer | FALSE | summer
2023-06-07 | 2023-06-07 01:00 | Summer | FALSE | summer
2023-06-07 01:00 | 2023-06-07 02:00 | Summer | FALSE | summer
2023-06-07 02:00 | 2023-06-07 03:00 | Summer | FALSE | summer
2023-06-07 03:00 | 2023-06-07 04:00 | Summer | FALSE | summer
2023-06-07 04:00 | 2023-06-07 05:00 | Summer | FALSE | summer
2023-06-07 05:00 | 2023-06-07 06:00 | Summer | FALSE | summer
2023-06-07 06:00 | 2023-06-07 07:00 | Summer | FALSE | summer
2023-06-07 07:00 | 2023-06-07 08:00 | Summer | FALSE | summer
2023-06-07 08:00 | 2023-06-07 09:00 | Summer | FALSE | summer
2023-06-07 09:00 | 2023-06-07 10:00 | Summer | FALSE | summer
2023-06-07 10:00 | 2023-06-07 11:00 | Summer | FALSE | summer
2023-06-07 11:00 | 2023-06-07 12:00 | Summer | FALSE | summer
2023-06-07 12:00 | 2023-06-07 13:00 | Summer | FALSE | summer
2023-06-07 13:00 | 2023-06-07 14:00 | Summer | FALSE | summer
2023-06-07 14:00 | 2023-06-07 15:00 | Summer | FALSE | summer
2023-06-07 15:00 | 2023-06-07 16:00 | Summer | FALSE | summer
2023-06-07 16:00 | 2023-06-07 17:00 | Summer | TRUE | summer
2023-06-07 17:00 | 2023-06-07 18:00 | Summer | TRUE | summer
2023-06-07 18:00 | 2023-06-07 19:00 | Summer | TRUE | summer
2023-06-07 19:00 | 2023-06-07 20:00 | Summer | TRUE | summer
2023-06-07 20:00 | 2023-06-07 21:00 | Summer | TRUE | summer
2023-06-07 21:00 | 2023-06-07 22:00 | Summer | FALSE | summer
2023-06-07 22:00 | 2023-06-07 23:00 | Summer | FALSE | summer
2023-06-07 23:00 | 2023-06-08 | Summer | FALSE | summer
2023-06-08 | 2023-06-08 01:00 | Summer | FALSE | summer
2023-06-08 01:00 | 2023-06-08 02:00 | Summer | FALSE | summer
2023-06-08 02:00 | 2023-06-08 03:00 | Summer | FALSE | summer
2023-06-08 03:00 | 2023-06-08 04:00 | Summer | FALSE | summer
2023-06-08 04:00 | 2023-06-08 05:00 | Summer | FALSE | summer
2023-06-08 05:00 | 2023-06-08 06:00 | Summer | FALSE | summer
2023-06-08 06:00 | 2023-06-08 07:00 | Summer | FALSE | summer
2023-06-08 07:00 | 2023-06-08 08:00 | Summer | FALSE | summer
2023-06-08 08:00 | 2023-06-08 09:00 | Summer | FALSE | summer
2023-06-08 09:00 | 2023-06-08 10:00 | Summer | FALSE | summer
2023-06-08 10:00 | 2023-06-08 11:00 | Summer | FALSE | summer
2023-06-08 11:00 | 2023-06-08 12:00 | Summer | FALSE | summer
2023-06-08 12:00 | 2023-06-08 13:00 | Summer | FALSE | summer
2023-06-08 13:00 | 2023-06-08 14:00 | Summer | FALSE | summer
2023-06-08 14:00 | 2023-06-08 15:00 | Summer | FALSE | summer
2023-06-08 15:00 | 2023-06-08 16:00 | Summer | FALSE | summer
2023-06-08 16:00 | 2023-06-08 17:00 | Summer | TRUE | summer
2023-06-08 17:00 | 2023-06-08 18:00 | Summer | TRUE | summer
2023-06-08 18:00 | 2023-06-08 19:00 | Summer | TRUE | summer
2023-06-08 19:00 | 2023-06-08 20:00 | Summer | TRUE | summer
2023-06-08 20:00 | 2023-06-08 21:00 | Summer | TRUE | summer
2023-06-08 21:00 | 2023-06-08 22:00 | Summer | FALSE | summer
2023-06-08 22:00 | 2023-06-08 23:00 | Summer | FALSE | summer
2023-06-08 23:00 | 2023-06-09 | Summer | FALSE | summer
2023-06-09 | 2023-06-09 01:00 | Summer | FALSE | summer
2023-06-09 01:00 | 2023-06-09 02:00 | Summer | FALSE | summer
2023-06-09 02:00 | 2023-06-09 03:00 | Summer | FALSE | summer
2023-06-09 03:00 | 2023-06-09 04:00 | Summer | FALSE | summer
2023-06-09 04:00 | 2023-06-09 05:00 | Summer | FALSE | summer
2023-06-09 05:00 | 2023-06-09 06:00 | Summer | FALSE | summer
2023-06-09 06:00 | 2023-06-09 07:00 | Summer | FALSE | summer
2023-06-09 07:00 | 2023-06-09 08:00 | Summer | FALSE | summer
2023-06-09 08:00 | 2023-06-09 09:00 | Summer | FALSE | summer
2023-06-09 09:00 | 2023-06-09 10:00 | Summer | FALSE | summer
2023-06-09 10:00 | 2023-06-09 11:00 | Summer | FALSE | summer
2023-06-09 11:00 | 2023-06-09 12:00 | Summer | FALSE | summer
2023-06-09 12:00 | 2023-06-09 13:00 | Summer | FALSE | summer
2023-06-09 13:00 | 2023-06-09 14:00 | Summer | FALSE | summer
2023-06-09 14:00 | 2023-06-09 15:00 | Summer | FALSE | summer
2023-06-09 15:00 | 2023-06-09 16:00 | Summer | FALSE | summer
2023-06-09 16:00 | 2023-06-09 17:00 | Summer | TRUE | summer
2023-06-09 17:00 | 2023-06-09 18:00 | Summer | TRUE | summer
2023-06-09 18:00 | 2023-06-09 19:00 | Summer | TRUE | summer
2023-06-09 19:00 | 2023-06-09 20:00 | Summer | TRUE | summer
2023-06-09 20:00 | 2023-06-09 21:00 | Summer | TRUE | summer
2023-06-09 21:00 | 2023-06-09 22:00 | Summer | FALSE | summer
2023-06-09 22:00 | 2023-06-09 23:00 | Summer | FALSE | summer
2023-06-09 23:00 | 2023-06-10 | Summer | FALSE | summer
2023-06-10 | 2023-06-10 01:00 | Summer | FALSE | summer
2023-06-10 01:00 | 2023-06-10 02:00 | Summer | FALSE | summer
2023-06-10 02:00 | 2023-06-10 03:00 | Summer | FALSE | summer
2023-06-10 03:00 | 2023-06-10 04:00 | Summer | FALSE | summer
2023-06-10 04:00 | 2023-06-10 05:00 | Summer | FALSE | summer
2023-06-10 05:00 | 2023-06-10 06:00 | Summer | FALSE | summer
2023-06-10 06:00 | 2023-06-10 07:00 | Summer | FALSE | summer
2023-06-10 07:00 | 2023-06-10 08:00 | Summer | FALSE | summer
2023-06-10 08:00 | 2023-06-10 09:00 | Summer | FALSE | summer
2023-06-10 09:00 | 2023-06-10 10:00 | Summer | FALSE | summer
2023-06-10 10:00 | 2023-06-10 11:00 | Summer | FALSE | summer
2023-06-10 11:00 | 2023-06-10 12:00 | Summer | FALSE | summer
2023-06-10 12:00 | 2023-06-10 13:00 | Summer | FALSE | summer
2023-06-10 13:00 | 2023-06-10 14:00 | Summer | FALSE | summer
2023-06-10 14:00 | 2023-06-10 15:00 | Summer | FALSE | summer
2023-06-10 15:00 | 2023-06-10 16:00 | Summer | FALSE | summer
2023-06-10 16:00 | 2023-06-10 17:00 | Summer | TRUE | summer
2023-06-10 17:00 | 2023-06-10 18:00 | Summer | TRUE | summer
2023-06-10 18:00 | 2023-06-10 19:00 | Summer | TRUE | summer
2023-06-10 19:00 | 2023-06-10 20:00 | Summer | TRUE | summer
2023-06-10 20:00 | 2023-06-10 21:00 | Summer | TRUE | summer
2023-06-10 21:00 | 2023-06-10 22:00 | Summer | FALSE | summer
2023-06-10 22:00 | 2023-06-10 23:00 | Summer | FALSE | summer
2023-06-10 23:00 | 2023-06-11 | Summer | FALSE | summer
2023-06-11 | 2023-06-11 01:00 | Summer | FALSE | summer
2023-06-11 01:00 | 2023-06-11 02:00 | Summer | FALSE | summer
2023-06-11 02:00 | 2023-06-11 03:00 | Summer | FALSE | summer
2023-06-11 03:00 | 2023-06-11 04:00 | Summer | FALSE | summer
2023-06-11 04:00 | 2023-06-11 05:00 | Summer | FALSE | summer
2023-06-11 05:00 | 2023-06-11 06:00 | Summer | FALSE | summer
2023-06-11 06:00 | 2023-06-11 07:00 | Summer | FALSE | summer
2023-06-11 07:00 | 2023-06-11 08:00 | Summer | FALSE | summer
2023-06-11 08:00 | 2023-06-11 09:00 | Summer | FALSE | summer
2023-06-11 09:00 | 2023-06-11 10:00 | Summer | FALSE | summer
2023-06-11 10:00 | 2023-06-11 11:00 | Summer | FALSE | summer
2023-06-11 11:00 | 2023-06-11 12:00 | Summer | FALSE | summer
2023-06-11 12:00 | 2023-06-11 13:00 | Summer | FALSE | summer
2023-06-11 13:00 | 2023-06-11 14:00 | Summer | FALSE | summer
2023-06-11 14:00 | 2023-06-11 15:00 | Summer | FALSE | summer
2023-06-11 15:00 | 2023-06-11 16:00 | Summer | FALSE | summer
2023-06-11 16:00 | 2023-06-11 17:00 | Summer | TRUE | summer
2023-06-11 17:00 | 2023-06-11 18:00 | Summer | TRUE | summer
2023-06-11 18:00 | 2023-06-11 19:00 | Summer | TRUE | summer
2023-06-11 19:00 | 2023-06-11 20:00 | Summer | TRUE | summer
2023-06-11 20:00 | 2023-06-11 21:00 | Summer | TRUE | summer
2023-06-11 21:00 | 2023-06-11 22:00 | Summer | FALSE | summer
2023-06-11 22:00 | 2023-06-11 23:00 | Summer | FALSE | summer
2023-06-11 23:00 | 2023-06-12 | Summer | FALSE | summer
2023-06-12 | 2023-06-12 01:00 | Summer | FALSE | summer
2023-06-12 01:00 | 2023-06-12 02:00 | Summer | FALSE | summer
2023-06-12 02:00 | 2023-06-12 03:00 | Summer | FALSE | summer
2023-06-12 03:00 | 2023-06-12 04:00 | Summer | FALSE | summer
2023-06-12 04:00 | 2023-06-12 05:00 | Summer | FALSE | summer
2023-06-12 05:00 | 2023-06-12 06:00 | Summer | FALSE | summer
2023-06-12 06:00 | 2023-06-12 07:00 | Summer | FALSE | summer
2023-06-12 07:00 | 2023-06-12 08:00 | Summer | FALSE | summer
2023-06-12 08:00 | 2023-06-12 09:00 | Summer | FALSE | summer
2023-06-12 09:00 | 2023-06-12 10:00 | Summer | FALSE | summer
2023-06-12 10:00 | 2023-06-12 11:00 | Summer | FALSE | summer
2023-06-12 11:00 | 2023-06-12 12:00 | Summer | FALSE | summer
2023-06-12 12:00 | 2023-06-12 13:00 | Summer | FALSE | summer
2023-06-12 13:00 | 2023-06-12 14:00 | Summer | FALSE | summer
2023-06-12 14:00 | 2023-06-12 15:00 | Summer | FALSE | summer
2023-06-12 15:00 | 2023-06-12 16:00 | Summer | FALSE | summer
2023-06-12 16:00 | 2023-06-12 17:00 | Summer | TRUE | summer
2023-06-12 17:00 | 2023-06-12 18:00 | Summer | TRUE | summer
2023-06-12 18:00 | 2023-06-12 19:00 | Summer | TRUE | summer
2023-06-12 19:00 | 2023-06-12 20:00 | Summer | TRUE | summer
2023-06-12 20:00 | 2023-06-12 21:00 | Summer | TRUE | summer
2023-06-12 21:00 | 2023-06-12 22:00 | Summer | FALSE | summer
2023-06-12 22:00 | 2023-06-12 23:00 | Summer | FALSE | summer
2023-06-12 23:00 | 2023-06-13 | Summer | FALSE | summer
2023-06-13 | 2023-06-13 01:00 | Summer | FALSE | summer
2023-06-13 01:00 | 2023-06-13 02:00 | Summer | FALSE | summer
2023-06-13 02:00 | 2023-06-13 03:00 | Summer | FALSE | summer
2023-06-13 03:00 | 2023-06-13 04:00 | Summer | FALSE | summer
2023-06-13 04:00 | 2023-06-13 05:00 | Summer | FALSE | summer
2023-06-13 05:00 | 2023-06-13 06:00 | Summer | FALSE | summer
2023-06-13 06:00 | 2023-06-13 07:00 | Summer | FALSE | summer
2023-06-13 07:00 | 2023-06-13 08:00 | Summer | FALSE | summer
2023-06-13 08:00 | 2023-06-13 09:00 | Summer | FALSE | summer
2023-06-13 09:00 | 2023-06-13 10:00 | Summer | FALSE | summer
2023-06-13 10:00 | 2023-06-13 11:00 | Summer | FALSE | summer
2023-06-13 11:00 | 2023-06-13 12:00 | Summer | FALSE | summer
2023-06-13 12:00 | 2023-06-13 13:00 | Summer | FALSE | summer
2023-06-13 13:00 | 2023-06-13 14:00 | Summer | FALSE | summer
2023-06-13 14:00 | 2023-06-13 15:00 | Summer | FALSE | summer
2023-06-13 15:00 | 2023-06-13 16:00 | Summer | FALSE | summer
2023-06-13 16:00 | 2023-06-13 17:00 | Summer | TRUE | summer
2023-06-13 17:00 | 2023-06-13 18:00 | Summer | TRUE | summer
2023-06-13 18:00 | 2023-06-13 19:00 | Summer | TRUE | summer
2023-06-13 19:00 | 2023-06-13 20:00 | Summer | TRUE | summer
2023-06-13 20:00 | 2023-06-13 21:00 | Summer | TRUE | summer
2023-06-13 21:00 | 2023-06-13 22:00 | Summer | FALSE | summer
2023-06-13 22:00 | 2023-06-13 23:00 | Summer | FALSE | summer
2023-06-13 23:00 | 2023-06-14 | Summer | FALSE | summer
2023-06-14 | 2023-06-14 01:00 | Summer | FALSE | summer
2023-06-14 01:00 | 2023-06-14 02:00 | Summer | FALSE | summer
2023-06-14 02:00 | 2023-06-14 03:00 | Summer | FALSE | summer
2023-06-14 03:00 | 2023-06-14 04:00 | Summer | FALSE | summer
2023-06-14 04:00 | 2023-06-14 05:00 | Summer | FALSE | summer
2023-06-14 05:00 | 2023-06-14 06:00 | Summer | FALSE | summer
2023-06-14 06:00 | 2023-06-14 07:00 | Summer | FALSE | summer
2023-06-14 07:00 | 2023-06-14 08:00 | Summer | FALSE | summer
2023-06-14 08:00 | 2023-06-14 09:00 | Summer | FALSE | summer
2023-06-14 09:00 | 2023-06-14 10:00 | Summer | FALSE | summer
2023-06-14 10:00 | 2023-06-14 11:00 | Summer | FALSE | summer
2023-06-14 11:00 | 2023-06-14 12:00 | Summer | FALSE | summer
2023-06-14 12:00 | 2023-06-14 13:00 | Summer | FALSE | summer
2023-06-14 13:00 | 2023-06-14 14:00 | Summer | FALSE | summer
2023-06-14 14:00 | 2023-06-14 15:00 | Summer | FALSE | summer
2023-06-14 15:00 | 2023-06-14 16:00 | Summer | FALSE | summer
2023-06-14 16:00 | 2023-06-14 17:00 | Summer | TRUE | summer
2023-06-14 17:00 | 2023-06-14 18:00 | Summer | TRUE | summer
2023-06-14 18:00 | 2023-06-14 19:00 | Summer | TRUE | summer
2023-06-14 19:00 | 2023-06-14 20:00 | Summer | TRUE | summer
2023-06-14 20:00 | 2023-06-14 21:00 | Summer | TRUE | summer
2023-06-14 21:00 | 2023-06-14 22:00 | Summer | FALSE | summer
2023-06-14 22:00 | 2023-06-14 23:00 | Summer | FALSE | summer
2023-06-14 23:00 | 2023-06-15 | Summer | FALSE | summer
2023-06-15 | 2023-06-15 01:00 | Summer | FALSE | summer
2023-06-15 01:00 | 2023-06-15 02:00 | Summer | FALSE | summer
2023-06-15 02:00 | 2023-06-15 03:00 | Summer | FALSE | summer
2023-06-15 03:00 | 2023-06-15 04:00 | Summer | FALSE | summer
2023-06-15 04:00 | 2023-06-15 05:00 | Summer | FALSE | summer
2023-06-15 05:00 | 2023-06-15 06:00 | Summer | FALSE | summer
2023-06-15 06:00 | 2023-06-15 07:00 | Summer | FALSE | summer
2023-06-15 07:00 | 2023-06-15 08:00 | Summer | FALSE | summer
2023-06-15 08:00 | 2023-06-15 09:00 | Summer | FALSE | summer
2023-06-15 09:00 | 2023-06-15 10:00 | Summer | FALSE | summer
2023-06-15 10:00 | 2023-06-15 11:00 | Summer | FALSE | summer
2023-06-15 11:00 | 2023-06-15 12:00 | Summer | FALSE | summer
2023-06-15 12:00 | 2023-06-15 13:00 | Summer | FALSE | summer
2023-06-15 13:00 | 2023-06-15 14:00 | Summer | FALSE | summer
2023-06-15 14:00 | 2023-06-15 15:00 | Summer | FALSE | summer
2023-06-15 15:00 | 2023-06-15 16:00 | Summer | FALSE | summer
2023-06-15 16:00 | 2023-06-15 17:00 | Summer | TRUE | summer
2023-06-15 17:00 | 2023-06-15 18:00 | Summer | TRUE | summer
2023-06-15 18:00 | 2023-06-15 19:00 | Summer | TRUE | summer
2023-06-15 19:00 | 2023-06-15 20:00 | Summer | TRUE | summer
2023-06-15 20:00 | 2023-06-15 21:00 | Summer | TRUE | summer
2023-06-15 21:00 | 2023-06-15 22:00 | Summer | FALSE | summer
2023-06-15 22:00 | 2023-06-15 23:00 | Summer | FALSE | summer
2023-06-15 23:00 | 2023-06-16 | Summer | FALSE | summer
2023-06-16 | 2023-06-16 01:00 | Summer | FALSE | summer
2023-06-16 01:00 | 2023-06-16 02:00 | Summer | FALSE | summer
2023-06-16 02:00 | 2023-06-16 03:00 | Summer | FALSE | summer
2023-06-16 03:00 | 2023-06-16 04:00 | Summer | FALSE | summer
2023-06-16 04:00 | 2023-06-16 05:00 | Summer | FALSE | summer
2023-06-16 05:00 | 2023-06-16 06:00 | Summer | FALSE | summer
2023-06-16 06:00 | 2023-06-16 07:00 | Summer | FALSE | summer
2023-06-16 07:00 | 2023-06-16 08:00 | Summer | FALSE | summer
2023-06-16 08:00 | 2023-06-16 09:00 | Summer | FALSE | summer
2023-06-16 09:00 | 2023-06-16 10:00 | Summer | FALSE | summer
2023-06-16 10:00 | 2023-06-16 11:00 | Summer | FALSE | summer
2023-06-16 11:00 | 2023-06-16 12:00 | Summer | FALSE | summer
2023-06-16 12:00 | 2023-06-16 13:00 | Summer | FALSE | summer
2023-06-16 13:00 | 2023-06-16 14:00 | Summer | FALSE | summer
2023-06-16 14:00 | 2023-06-16 15:00 | Summer | FALSE | summer
2023-06-16 15:00 | 2023-06-16 16:00 | Summer | FALSE | summer
2023-06-16 16:00 | 2023-06-16 17:00 | Summer | TRUE | summer
2023-06-16 17:00 | 2023-06-16 18:00 | Summer | TRUE | summer
2023-06-16 18:00 | 2023-06-16 19:00 | Summer | TRUE | summer
2023-06-16 19:00 | 2023-06-16 20:00 | Summer | TRUE | summer
2023-06-16 20:00 | 2023-06-16 21:00 | Summer | TRUE | summer
2023-06-16 21:00 | 2023-06-16 22:00 | Summer | FALSE | summer
2023-06-16 22:00 | 2023-06-16 23:00 | Summer | FALSE | summer
2023-06-16 23:00 | 2023-06-17 | Summer | FALSE | summer
2023-06-17 | 2023-06-17 01:00 | Summer | FALSE | summer
2023-06-17 01:00 | 2023-06-17 02:00 | Summer | FALSE | summer
2023-06-17 02:00 | 2023-06-17 03:00 | Summer | FALSE | summer
2023-06-17 03:00 | 2023-06-17 04:00 | Summer | FALSE | summer
2023-06-17 04:00 | 2023-06-17 05:00 | Summer | FALSE | summer
2023-06-17 05:00 | 2023-06-17 06:00 | Summer | FALSE | summer
2023-06-17 06:00 | 2023-06-17 07:00 | Summer | FALSE | summer
2023-06-17 07:00 | 2023-06-17 08:00 | Summer | FALSE | summer
2023-06-17 08:00 | 2023-06-17 09:00 | Summer | FALSE | summer
2023-06-17 09:00 | 2023-06-17 10:00 | Summer | FALSE | summer
2023-06-17 10:00 | 2023-06-17 11:00 | Summer | FALSE | summer
2023-06-17 11:00 | 2023-06-17 12:00 | Summer | FALSE | summer
2023-06-17 12:00 | 2023-06-17 13:00 | Summer | FALSE | summer
2023-06-17 13:00 | 2023-06-17 14:00 | Summer | FALSE | summer
2023-06-17 14:00 | 2023-06-17 15:00 | Summer | FALSE | summer
2023-06-17 15:00 | 2023-06-17 16:00 | Summer | FALSE | summer
2023-06-17 16:00 | 2023-06-17 17:00 | Summer | TRUE | summer
2023-06-17 17:00 | 2023-06-17 18:00 | Summer | TRUE | summer
2023-06-17 18:00 | 2023-06-17 19:00 | Summer | TRUE | summer
2023-06-17 19:00 | 2023-06-17 20:00 | Summer | TRUE | summer
2023-06-17 20:00 | 2023-06-17 21:00 | Summer | TRUE | summer
2023-06-17 21:00 | 2023-06-17 22:00 | Summer | FALSE | summer
2023-06-17 22:00 | 2023-06-17 23:00 | Summer | FALSE | summer
2023-06-17 23:00 | 2023-06-18 | Summer | FALSE | summer
2023-06-18 | 2023-06-18 01:00 | Summer | FALSE | summer
2023-06-18 01:00 | 2023-06-18 02:00 | Summer | FALSE | summer
2023-06-18 02:00 | 2023-06-18 03:00 | Summer | FALSE | summer
2023-06-18 03:00 | 2023-06-18 04:00 | Summer | FALSE | summer
2023-06-18 04:00 | 2023-06-18 05:00 | Summer | FALSE | summer
2023-06-18 05:00 | 2023-06-18 06:00 | Summer | FALSE | summer
2023-06-18 06:00 | 2023-06-18 07:00 | Summer | FALSE | summer
2023-06-18 07:00 | 2023-06-18 08:00 | Summer | FALSE | summer
2023-06-18 08:00 | 2023-06-18 09:00 | Summer | FALSE | summer
2023-06-18 09:00 | 2023-06-18 10:00 | Summer | FALSE | summer
2023-06-18 10:00 | 2023-06-18 11:00 | Summer | FALSE | summer
2023-06-18 11:00 | 2023-06-18 12:00 | Summer | FALSE | summer
2023-06-18 12:00 | 2023-06-18 13:00 | Summer | FALSE | summer
2023-06-18 13:00 | 2023-06-18 14:00 | Summer | FALSE | summer
2023-06-18 14:00 | 2023-06-18 15:00 | Summer | FALSE | summer
2023-06-18 15:00 | 2023-06-18 16:00 | Summer | FALSE | summer
2023-06-18 16:00 | 2023-06-18 17:00 | Summer | TRUE | summer
2023-06-18 17:00 | 2023-06-18 18:00 | Summer | TRUE | summer
2023-06-18 18:00 | 2023-06-18 19:00 | Summer | TRUE | summer
2023-06-18 19:00 | 2023-06-18 20:00 | Summer | TRUE | summer
2023-06-18 20:00 | 2023-06-18 21:00 | Summer | TRUE | summer
2023-06-18 21:00 | 2023-06-18 22:00 | Summer | FALSE | summer
2023-06-18 22:00 | 2023-06-18 23:00 | Summer | FALSE | summer
2023-06-18 23:00 | 2023-06-19 | Summer | FALSE | summer
2023-06-19 | 2023-06-19 01:00 | Summer | FALSE | summer
2023-06-19 01:00 | 2023-06-19 02:00 | Summer | FALSE | summer
2023-06-19 02:00 | 2023-06-19 03:00 | Summer | FALSE | summer
2023-06-19 03:00 | 2023-06-19 04:00 | Summer | FALSE | summer
2023-06-19 04:00 | 2023-06-19 05:00 | Summer | FALSE | summer
2023-06-19 05:00 | 2023-06-19 06:00 | Summer | FALSE | summer
2023-06-19 06:00 | 2023-06-19 07:00 | Summer | FALSE | summer
2023-06-19 07:00 | 2023-06-19 08:00 | Summer | FALSE | summer
2023-06-19 08:00 | 2023-06-19 09:00 | Summer | FALSE | summer
2023-06-19 09:00 | 2023-06-19 10:00 | Summer | FALSE | summer
2023-06-19 10:00 | 2023-06-19 11:00 | Summer | FALSE | summer
2023-06-19 11:00 | 2023-06-19 12:00 | Summer | FALSE | summer
2023-06-19 12:00 | 2023-06-19 13:00 | Summer | FALSE | summer
2023-06-19 13:00 | 2023-06-19 14:00 | Summer | FALSE | summer
2023-06-19 14:00 | 2023-06-19 15:00 | Summer | FALSE | summer
2023-06-19 15:00 | 2023-06-19 16:00 | Summer | FALSE | summer
2023-06-19 16:00 | 2023-06-19 17:00 | Summer | TRUE | summer
2023-06-19 17:00 | 2023-06-19 18:00 | Summer | TRUE | summer
2023-06-19 18:00 | 2023-06-19 19:00 | Summer | TRUE | summer
2023-06-19 19:00 | 2023-06-19 20:00 | Summer | TRUE | summer
2023-06-19 20:00 | 2023-06-19 21:00 | Summer | TRUE | summer
2023-06-19 21:00 | 2023-06-19 22:00 | Summer | FALSE | summer
2023-06-19 22:00 | 2023-06-19 23:00 | Summer | FALSE | summer
2023-06-19 23:00 | 2023-06-20 | Summer | FALSE | summer
2023-06-20 | 2023-06-20 01:00 | Summer | FALSE | summer
2023-06-20 01:00 | 2023-06-20 02:00 | Summer | FALSE | summer
2023-06-20 02:00 | 2023-06-20 03:00 | Summer | FALSE | summer
2023-06-20 03:00 | 2023-06-20 04:00 | Summer | FALSE | summer
2023-06-20 04:00 | 2023-06-20 05:00 | Summer | FALSE | summer
2023-06-20 05:00 | 2023-06-20 06:00 | Summer | FALSE | summer
2023-06-20 06:00 | 2023-06-20 07:00 | Summer | FALSE | summer
2023-06-20 07:00 | 2023-06-20 08:00 | Summer | FALSE | summer
2023-06-20 08:00 | 2023-06-20 09:00 | Summer | FALSE | summer
2023-06-20 09:00 | 2023-06-20 10:00 | Summer | FALSE | summer
2023-06-20 10:00 | 2023-06-20 11:00 | Summer | FALSE | summer
2023-06-20 11:00 | 2023-06-20 12:00 | Summer | FALSE | summer
2023-06-20 12:00 | 2023-06-20 13:00 | Summer | FALSE | summer
2023-06-20 13:00 | 2023-06-20 14:00 | Summer | FALSE | summer
2023-06-20 14:00 | 2023-06-20 15:00 | Summer | FALSE | summer
2023-06-20 15:00 | 2023-06-20 16:00 | Summer | FALSE | summer
2023-06-20 16:00 | 2023-06-20 17:00 | Summer | TRUE | summer
2023-06-20 17:00 | 2023-06-20 18:00 | Summer | TRUE | summer
2023-06-20 18:00 | 2023-06-20 19:00 | Summer | TRUE | summer
2023-06-20 19:00 | 2023-06-20 20:00 | Summer | TRUE | summer
2023-06-20 20:00 | 2023-06-20 21:00 | Summer | TRUE | summer
2023-06-20 21:00 | 2023-06-20 22:00 | Summer | FALSE | summer
2023-06-20 22:00 | 2023-06-20 23:00 | Summer | FALSE | summer
2023-06-20 23:00 | 2023-06-21 | Summer | FALSE | summer
2023-06-21 | 2023-06-21 01:00 | Summer | FALSE | summer
2023-06-21 01:00 | 2023-06-21 02:00 | Summer | FALSE | summer
2023-06-21 02:00 | 2023-06-21 03:00 | Summer | FALSE | summer
2023-06-21 03:00 | 2023-06-21 04:00 | Summer | FALSE | summer
2023-06-21 04:00 | 2023-06-21 05:00 | Summer | FALSE | summer
2023-06-21 05:00 | 2023-06-21 06:00 | Summer | FALSE | summer
2023-06-21 06:00 | 2023-06-21 07:00 | Summer | FALSE | summer
2023-06-21 07:00 | 2023-06-21 08:00 | Summer | FALSE | summer
2023-06-21 08:00 | 2023-06-21 09:00 | Summer | FALSE | summer
2023-06-21 09:00 | 2023-06-21 10:00 | Summer | FALSE | summer
2023-06-21 10:00 | 2023-06-21 11:00 | Summer | FALSE | summer
2023-06-21 11:00 | 2023-06-21 12:00 | Summer | FALSE | summer
2023-06-21 12:00 | 2023-06-21 13:00 | Summer | FALSE | summer
2023-06-21 13:00 | 2023-06-21 14:00 | Summer | FALSE | summer
2023-06-21 14:00 | 2023-06-21 15:00 | Summer | FALSE | summer
2023-06-21 15:00 | 2023-06-21 16:00 | Summer | FALSE | summer
2023-06-21 16:00 | 2023-06-21 17:00 | Summer | TRUE | summer
2023-06-21 17:00 | 2023-06-21 18:00 | Summer | TRUE | summer
2023-06-21 18:00 | 2023-06-21 19:00 | Summer | TRUE | summer
2023-06-21 19:00 | 2023-06-21 20:00 | Summer | TRUE | summer
2023-06-21 20:00 | 2023-06-21 21:00 | Summer | TRUE | summer
2023-06-21 21:00 | 2023-06-21 22:00 | Summer | FALSE | summer
2023-06-21 22:00 | 2023-06-21 23:00 | Summer | FALSE | summer
2023-06-21 23:00 | 2023-06-22 | Summer | FALSE | summer
2023-06-22 | 2023-06-22 01:00 | Summer | FALSE | summer
2023-06-22 01:00 | 2023-06-22 02:00 | Summer | FALSE | summer
2023-06-22 02:00 | 2023-06-22 03:00 | Summer | FALSE | summer
2023-06-22 03:00 | 2023-06-22 04:00 | Summer | FALSE | summer
2023-06-22 04:00 | 2023-06-22 05:00 | Summer | FALSE | summer
2023-06-22 05:00 | 2023-06-22 06:00 | Summer | FALSE | summer
2023-06-22 06:00 | 2023-06-22 07:00 | Summer | FALSE | summer
2023-06-22 07:00 | 2023-06-22 08:00 | Summer | FALSE | summer
2023-06-22 08:00 | 2023-06-22 09:00 | Summer | FALSE | summer
2023-06-22 09:00 | 2023-06-22 10:00 | Summer | FALSE | summer
2023-06-22 10:00 | 2023-06-22 11:00 | Summer | FALSE | summer
2023-06-22 11:00 | 2023-06-22 12:00 | Summer | FALSE | summer
2023-06-22 12:00 | 2023-06-22 13:00 | Summer | FALSE | summer
2023-06-22 13:00 | 2023-06-22 14:00 | Summer | FALSE | summer
2023-06-22 14:00 | 2023-06-22 15:00 | Summer | FALSE | summer
2023-06-22 15:00 | 2023-06-22 16:00 | Summer | FALSE | summer
2023-06-22 16:00 | 2023-06-22 17:00 | Summer | TRUE | summer
2023-06-22 17:00 | 2023-06-22 18:00 | Summer | TRUE | summer
2023-06-22 18:00 | 2023-06-22 19:00 | Summer | TRUE | summer
2023-06-22 19:00 | 2023-06-22 20:00 | Summer | TRUE | summer
2023-06-22 20:00 | 2023-06-22 21:00 | Summer | TRUE | summer
2023-06-22 21:00 | 2023-06-22 22:00 | Summer | FALSE | summer
2023-06-22 22:00 | 2023-06-22 23:00 | Summer | FALSE | summer
2023-06-22 23:00 | 2023-06-23 | Summer | FALSE | summer
2023-06-23 | 2023-06-23 01:00 | Summer | FALSE | summer
2023-06-23 01:00 | 2023-06-23 02:00 | Summer | FALSE | summer
2023-06-23 02:00 | 2023-06-23 03:00 | Summer | FALSE | summer
2023-06-23 03:00 | 2023-06-23 04:00 | Summer | FALSE | summer
2023-06-23 04:00 | 2023-06-23 05:00 | Summer | FALSE | summer
2023-06-23 05:00 | 2023-06-23 06:00 | Summer | FALSE | summer
2023-06-23 06:00 | 2023-06-23 07:00 | Summer | FALSE | summer
2023-06-23 07:00 | 2023-06-23 08:00 | Summer | FALSE | summer
2023-06-23 08:00 | 2023-06-23 09:00 | Summer | FALSE | summer
2023-06-23 09:00 | 2023-06-23 10:00 | Summer | FALSE | summer
2023-06-23 10:00 | 2023-06-23 11:00 | Summer | FALSE | summer
2023-06-23 11:00 | 2023-06-23 12:00 | Summer | FALSE | summer
2023-06-23 12:00 | 2023-06-23 13:00 | Summer | FALSE | summer
2023-06-23 13:00 | 2023-06-23 14:00 | Summer | FALSE | summer
2023-06-23 14:00 | 2023-06-23 15:00 | Summer | FALSE | summer
2023-06-23 15:00 | 2023-06-23 16:00 | Summer | FALSE | summer
2023-06-23 16:00 | 2023-06-23 17:00 | Summer | TRUE | summer
2023-06-23 17:00 | 2023-06-23 18:00 | Summer | TRUE | summer
2023-06-23 18:00 | 2023-06-23 19:00 | Summer | TRUE | summer
2023-06-23 19:00 | 2023-06-23 20:00 | Summer | TRUE | summer
2023-06-23 20:00 | 2023-06-23 21:00 | Summer | TRUE | summer
2023-06-23 21:00 | 2023-06-23 22:00 | Summer | FALSE | summer
2023-06-23 22:00 | 2023-06-23 23:00 | Summer | FALSE | summer
2023-06-23 23:00 | 2023-06-24 | Summer | FALSE | summer
2023-06-24 | 2023-06-24 01:00 | Summer | FALSE | summer
2023-06-24 01:00 | 2023-06-24 02:00 | Summer | FALSE | summer
2023-06-24 02:00 | 2023-06-24 03:00 | Summer | FALSE | summer
2023-06-24 03:00 | 2023-06-24 04:00 | Summer | FALSE | summer
2023-06-24 04:00 | 2023-06-24 05:00 | Summer | FALSE | summer
2023-06-24 05:00 | 2023-06-24 06:00 | Summer | FALSE | summer
2023-06-24 06:00 | 2023-06-24 07:00 | Summer | FALSE | summer
2023-06-24 07:00 | 2023-06-24 08:00 | Summer | FALSE | summer
2023-06-24 08:00 | 2023-06-24 09:00 | Summer | FALSE | summer
2023-06-24 09:00 | 2023-06-24 10:00 | Summer | FALSE | summer
2023-06-24 10:00 | 2023-06-24 11:00 | Summer | FALSE | summer
2023-06-24 11:00 | 2023-06-24 12:00 | Summer | FALSE | summer
2023-06-24 12:00 | 2023-06-24 13:00 | Summer | FALSE | summer
2023-06-24 13:00 | 2023-06-24 14:00 | Summer | FALSE | summer
2023-06-24 14:00 | 2023-06-24 15:00 | Summer | FALSE | summer
2023-06-24 15:00 | 2023-06-24 16:00 | Summer | FALSE | summer
2023-06-24 16:00 | 2023-06-24 17:00 | Summer | TRUE | summer
2023-06-24 17:00 | 2023-06-24 18:00 | Summer | TRUE | summer
2023-06-24 18:00 | 2023-06-24 19:00 | Summer | TRUE | summer
2023-06-24 19:00 | 2023-06-24 20:00 | Summer | TRUE | summer
2023-06-24 20:00 | 2023-06-24 21:00 | Summer | TRUE | summer
2023-06-24 21:00 | 2023-06-24 22:00 | Summer | FALSE | summer
2023-06-24 22:00 | 2023-06-24 23:00 | Summer | FALSE | summer
2023-06-24 23:00 | 2023-06-25 | Summer | FALSE | summer
2023-06-25 | 2023-06-25 01:00 | Summer | FALSE | summer
2023-06-25 01:00 | 2023-06-25 02:00 | Summer | FALSE | summer
2023-06-25 02:00 | 2023-06-25 03:00 | Summer | FALSE | summer
2023-06-25 03:00 | 2023-06-25 04:00 | Summer | FALSE | summer
2023-06-25 04:00 | 2023-06-25 05:00 | Summer | FALSE | summer
2023-06-25 05:00 | 2023-06-25 06:00 | Summer | FALSE | summer
2023-06-25 06:00 | 2023-06-25 07:00 | Summer | FALSE | summer
2023-06-25 07:00 | 2023-06-25 08:00 | Summer | FALSE | summer
2023-06-25 08:00 | 2023-06-25 09:00 | Summer | FALSE | summer
2023-06-25 09:00 | 2023-06-25 10:00 | Summer | FALSE | summer
2023-06-25 10:00 | 2023-06-25 11:00 | Summer | FALSE | summer
2023-06-25 11:00 | 2023-06-25 12:00 | Summer | FALSE | summer
2023-06-25 12:00 | 2023-06-25 13:00 | Summer | FALSE | summer
2023-06-25 13:00 | 2023-06-25 14:00 | Summer | FALSE | summer
2023-06-25 14:00 | 2023-06-25 15:00 | Summer | FALSE | summer
2023-06-25 15:00 | 2023-06-25 16:00 | Summer | FALSE | summer
2023-06-25 16:00 | 2023-06-25 17:00 | Summer | TRUE | summer
2023-06-25 17:00 | 2023-06-25 18:00 | Summer | TRUE | summer
2023-06-25 18:00 | 2023-06-25 19:00 | Summer | TRUE | summer
2023-06-25 19:00 | 2023-06-25 20:00 | Summer | TRUE | summer
2023-06-25 20:00 | 2023-06-25 21:00 | Summer | TRUE | summer
2023-06-25 21:00 | 2023-06-25 22:00 | Summer | FALSE | summer
2023-06-25 22:00 | 2023-06-25 23:00 | Summer | FALSE | summer
2023-06-25 23:00 | 2023-06-26 | Summer | FALSE | summer
2023-06-26 | 2023-06-26 01:00 | Summer | FALSE | summer
2023-06-26 01:00 | 2023-06-26 02:00 | Summer | FALSE | summer
2023-06-26 02:00 | 2023-06-26 03:00 | Summer | FALSE | summer
2023-06-26 03:00 | 2023-06-26 04:00 | Summer | FALSE | summer
2023-06-26 04:00 | 2023-06-26 05:00 | Summer | FALSE | summer
2023-06-26 05:00 | 2023-06-26 06:00 | Summer | FALSE | summer
2023-06-26 06:00 | 2023-06-26 07:00 | Summer | FALSE | summer
2023-06-26 07:00 | 2023-06-26 08:00 | Summer | FALSE | summer
2023-06-26 08:00 | 2023-06-26 09:00 | Summer | FALSE | summer
2023-06-26 09:00 | 2023-06-26 10:00 | Summer | FALSE | summer
2023-06-26 10:00 | 2023-06-26 11:00 | Summer | FALSE | summer
2023-06-26 11:00 | 2023-06-26 12:00 | Summer | FALSE | summer
2023-06-26 12:00 | 2023-06-26 13:00 | Summer | FALSE | summer
2023-06-26 13:00 | 2023-06-26 14:00 | Summer | FALSE | summer
2023-06-26 14:00 | 2023-06-26 15:00 | Summer | FALSE | summer
2023-06-26 15:00 | 2023-06-26 16:00 | Summer | FALSE | summer
2023-06-26 16:00 | 2023-06-26 17:00 | Summer | TRUE | summer
2023-06-26 17:00 | 2023-06-26 18:00 | Summer | TRUE | summer
2023-06-26 18:00 | 2023-06-26 19:00 | Summer | TRUE | summer
2023-06-26 19:00 | 2023-06-26 20:00 | Summer | TRUE | summer
2023-06-26 20:00 | 2023-06-26 21:00 | Summer | TRUE | summer
2023-06-26 21:00 | 2023-06-26 22:00 | Summer | FALSE | summer
2023-06-26 22:00 | 2023-06-26 23:00 | Summer | FALSE | summer
2023-06-26 23:00 | 2023-06-27 | Summer | FALSE | summer
2023-06-27 | 2023-06-27 01:00 | Summer | FALSE | summer
2023-06-27 01:00 | 2023-06-27 02:00 | Summer | FALSE | summer
2023-06-27 02:00 | 2023-06-27 03:00 | Summer | FALSE | summer
2023-06-27 03:00 | 2023-06-27 04:00 | Summer | FALSE | summer
2023-06-27 04:00 | 2023-06-27 05:00 | Summer | FALSE | summer
2023-06-27 05:00 | 2023-06-27 06:00 | Summer | FALSE | summer
2023-06-27 06:00 | 2023-06-27 07:00 | Summer | FALSE | summer
2023-06-27 07:00 | 2023-06-27 08:00 | Summer | FALSE | summer
2023-06-27 08:00 | 2023-06-27 09:00 | Summer | FALSE | summer
2023-06-27 09:00 | 2023-06-27 10:00 | Summer | FALSE | summer
2023-06-27 10:00 | 2023-06-27 11:00 | Summer | FALSE | summer
2023-06-27 11:00 | 2023-06-27 12:00 | Summer | FALSE | summer
2023-06-27 12:00 | 2023-06-27 13:00 | Summer | FALSE | summer
2023-06-27 13:00 | 2023-06-27 14:00 | Summer | FALSE | summer
2023-06-27 14:00 | 2023-06-27 15:00 | Summer | FALSE | summer
2023-06-27 15:00 | 2023-06-27 16:00 | Summer | FALSE | summer
2023-06-27 16:00 | 2023-06-27 17:00 | Summer | TRUE | summer
2023-06-27 17:00 | 2023-06-27 18:00 | Summer | TRUE | summer
2023-06-27 18:00 | 2023-06-27 19:00 | Summer | TRUE | summer
2023-06-27 19:00 | 2023-06-27 20:00 | Summer | TRUE | summer
2023-06-27 20:00 | 2023-06-27 21:00 | Summer | TRUE | summer
2023-06-27 21:00 | 2023-06-27 22:00 | Summer | FALSE | summer
2023-06-27 22:00 | 2023-06-27 23:00 | Summer | FALSE | summer
2023-06-27 23:00 | 2023-06-28 | Summer | FALSE | summer
2023-06-28 | 2023-06-28 01:00 | Summer | FALSE | summer
2023-06-28 01:00 | 2023-06-28 02:00 | Summer | FALSE | summer
2023-06-28 02:00 | 2023-06-28 03:00 | Summer | FALSE | summer
2023-06-28 03:00 | 2023-06-28 04:00 | Summer | FALSE | summer
2023-06-28 04:00 | 2023-06-28 05:00 | Summer | FALSE | summer
2023-06-28 05:00 | 2023-06-28 06:00 | Summer | FALSE | summer
2023-06-28 06:00 | 2023-06-28 07:00 | Summer | FALSE | summer
2023-06-28 07:00 | 2023-06-28 08:00 | Summer | FALSE | summer
2023-06-28 08:00 | 2023-06-28 09:00 | Summer | FALSE | summer
2023-06-28 09:00 | 2023-06-28 10:00 | Summer | FALSE | summer
2023-06-28 10:00 | 2023-06-28 11:00 | Summer | FALSE | summer
2023-06-28 11:00 | 2023-06-28 12:00 | Summer | FALSE | summer
2023-06-28 12:00 | 2023-06-28 13:00 | Summer | FALSE | summer
2023-06-28 13:00 | 2023-06-28 14:00 | Summer | FALSE | summer
2023-06-28 14:00 | 2023-06-28 15:00 | Summer | FALSE | summer
2023-06-28 15:00 | 2023-06-28 16:00 | Summer | FALSE | summer
2023-06-28 16:00 | 2023-06-28 17:00 | Summer | TRUE | summer
2023-06-28 17:00 | 2023-06-28 18:00 | Summer | TRUE | summer
2023-06-28 18:00 | 2023-06-28 19:00 | Summer | TRUE | summer
2023-06-28 19:00 | 2023-06-28 20:00 | Summer | TRUE | summer
2023-06-28 20:00 | 2023-06-28 21:00 | Summer | TRUE | summer
2023-06-28 21:00 | 2023-06-28 22:00 | Summer | FALSE | summer
2023-06-28 22:00 | 2023-06-28 23:00 | Summer | FALSE | summer
2023-06-28 23:00 | 2023-06-29 | Summer | FALSE | summer
2023-06-29 | 2023-06-29 01:00 | Summer | FALSE | summer
2023-06-29 01:00 | 2023-06-29 02:00 | Summer | FALSE | summer
2023-06-29 02:00 | 2023-06-29 03:00 | Summer | FALSE | summer
2023-06-29 03:00 | 2023-06-29 04:00 | Summer | FALSE | summer
2023-06-29 04:00 | 2023-06-29 05:00 | Summer | FALSE | summer
2023-06-29 05:00 | 2023-06-29 06:00 | Summer | FALSE | summer
2023-06-29 06:00 | 2023-06-29 07:00 | Summer | FALSE | summer
2023-06-29 07:00 | 2023-06-29 08:00 | Summer | FALSE | summer
2023-06-29 08:00 | 2023-06-29 09:00 | Summer | FALSE | summer
2023-06-29 09:00 | 2023-06-29 10:00 | Summer | FALSE | summer
2023-06-29 10:00 | 2023-06-29 11:00 | Summer | FALSE | summer
2023-06-29 11:00 | 2023-06-29 12:00 | Summer | FALSE | summer
2023-06-29 12:00 | 2023-06-29 13:00 | Summer | FALSE | summer
2023-06-29 13:00 | 2023-06-29 14:00 | Summer | FALSE | summer
2023-06-29 14:00 | 2023-06-29 15:00 | Summer | FALSE | summer
2023-06-29 15:00 | 2023-06-29 16:00 | Summer | FALSE | summer
2023-06-29 16:00 | 2023-06-29 17:00 | Summer | TRUE | summer
2023-06-29 17:00 | 2023-06-29 18:00 | Summer | TRUE | summer
2023-06-29 18:00 | 2023-06-29 19:00 | Summer | TRUE | summer
2023-06-29 19:00 | 2023-06-29 20:00 | Summer | TRUE | summer
2023-06-29 20:00 | 2023-06-29 21:00 | Summer | TRUE | summer
2023-06-29 21:00 | 2023-06-29 22:00 | Summer | FALSE | summer
2023-06-29 22:00 | 2023-06-29 23:00 | Summer | FALSE | summer
2023-06-29 23:00 | 2023-06-30 | Summer | FALSE | summer
2023-06-30 | 2023-06-30 01:00 | Summer | FALSE | summer
2023-06-30 01:00 | 2023-06-30 02:00 | Summer | FALSE | summer
2023-06-30 02:00 | 2023-06-30 03:00 | Summer | FALSE | summer
2023-06-30 03:00 | 2023-06-30 04:00 | Summer | FALSE | summer
2023-06-30 04:00 | 2023-06-30 05:00 | Summer | FALSE | summer
2023-06-30 05:00 | 2023-06-30 06:00 | Summer | FALSE | summer
2023-06-30 06:00 | 2023-06-30 07:00 | Summer | FALSE | summer
2023-06-30 07:00 | 2023-06-30 08:00 | Summer | FALSE | summer
2023-06-30 08:00 | 2023-06-30 09:00 | Summer | FALSE | summer
2023-06-30 09:00 | 2023-06-30 10:00 | Summer | FALSE | summer
2023-06-30 10:00 | 2023-06-30 11:00 | Summer | FALSE | summer
2023-06-30 11:00 | 2023-06-30 12:00 | Summer | FALSE | summer
2023-06-30 12:00 | 2023-06-30 13:00 | Summer | FALSE | summer
2023-06-30 13:00 | 2023-06-30 14:00 | Summer | FALSE | summer
2023-06-30 14:00 | 2023-06-30 15:00 | Summer | FALSE | summer
2023-06-30 15:00 | 2023-06-30 16:00 | Summer | FALSE | summer
2023-06-30 16:00 | 2023-06-30 17:00 | Summer | TRUE | summer
2023-06-30 17:00 | 2023-06-30 18:00 | Summer | TRUE | summer
2023-06-30 18:00 | 2023-06-30 19:00 | Summer | TRUE | summer
2023-06-30 19:00 | 2023-06-30 20:00 | Summer | TRUE | summer
2023-06-30 20:00 | 2023-06-30 21:00 | Summer | TRUE | summer
2023-06-30 21:00 | 2023-06-30 22:00 | Summer | FALSE | summer
2023-06-30 22:00 | 2023-06-30 23:00 | Summer | FALSE | summer
2023-06-30 23:00 | 2023-07-01 | Summer | FALSE | summer
2023-07-01 | 2023-07-01 01:00 | Summer | FALSE | summer
2023-07-01 01:00 | 2023-07-01 02:00 | Summer | FALSE | summer
2023-07-01 02:00 | 2023-07-01 03:00 | Summer | FALSE | summer
2023-07-01 03:00 | 2023-07-01 04:00 | Summer | FALSE | summer
2023-07-01 04:00 | 2023-07-01 05:00 | Summer | FALSE | summer
2023-07-01 05:00 | 2023-07-01 06:00 | Summer | FALSE | summer
2023-07-01 06:00 | 2023-07-01 07:00 | Summer | FALSE | summer
2023-07-01 07:00 | 2023-07-01 08:00 | Summer | FALSE | summer
2023-07-01 08:00 | 2023-07-01 09:00 | Summer | FALSE | summer
2023-07-01 09:00 | 2023-07-01 10:00 | Summer | FALSE | summer
2023-07-01 10:00 | 2023-07-01 11:00 | Summer | FALSE | summer
2023-07-01 11:00 | 2023-07-01 12:00 | Summer | FALSE | summer
2023-07-01 12:00 | 2023-07-01 13:00 | Summer | FALSE | summer
2023-07-01 13:00 | 2023-07-01 14:00 | Summer | FALSE | summer
2023-07-01 14:00 | 2023-07-01 15:00 | Summer | FALSE | summer
2023-07-01 15:00 | 2023-07-01 16:00 | Summer | FALSE | summer
2023-07-01 16:00 | 2023-07-01 17:00 | Summer | TRUE | summer
2023-07-01 17:00 | 2023-07-01 18:00 | Summer | TRUE | summer
2023-07-01 18:00 | 2023-07-01 19:00 | Summer | TRUE | summer
2023-07-01 19:00 | 2023-07-01 20:00 | Summer | TRUE | summer
2023-07-01 20:00 | 2023-07-01 21:00 | Summer | TRUE | summer
2023-07-01 21:00 | 2023-07-01 22:00 | Summer | FALSE | summer
2023-07-01 22:00 | 2023-07-01 23:00 | Summer | FALSE | summer
2023-07-01 23:00 | 2023-07-02 | Summer | FALSE | summer
2023-07-02 | 2023-07-02 01:00 | Summer | FALSE | summer
2023-07-02 01:00 | 2023-07-02 02:00 | Summer | FALSE | summer
2023-07-02 02:00 | 2023-07-02 03:00 | Summer | FALSE | summer
2023-07-02 03:00 | 2023-07-02 04:00 | Summer | FALSE | summer
2023-07-02 04:00 | 2023-07-02 05:00 | Summer | FALSE | summer
2023-07-02 05:00 | 2023-07-02 06:00 | Summer | FALSE | summer
2023-07-02 06:00 | 2023-07-02 07:00 | Summer | FALSE | summer
2023-07-02 07:00 | 2023-07-02 08:00 | Summer | FALSE | summer
2023-07-02 08:00 | 2023-07-02 09:00 | Summer | FALSE | summer
2023-07-02 09:00 | 2023-07-02 10:00 | Summer | FALSE | summer
2023-07-02 10:00 | 2023-07-02 11:00 | Summer | FALSE | summer
2023-07-02 11:00 | 2023-07-02 12:00 | Summer | FALSE | summer
2023-07-02 12:00 | 2023-07-02 13:00 | Summer | FALSE | summer
2023-07-02 13:00 | 2023-07-02 14:00 | Summer | FALSE | summer
2023-07-02 14:00 | 2023-07-02 15:00 | Summer | FALSE | summer
2023-07-02 15:00 | 2023-07-02 16:00 | Summer | FALSE | summer
2023-07-02 16:00 | 2023-07-02 17:00 | Summer | TRUE | summer
2023-07-02 17:00 | 2023-07-02 18:00 | Summer | TRUE | summer
2023-07-02 18:00 | 2023-07-02 19:00 | Summer | TRUE | summer
2023-07-02 19:00 | 2023-07-02 20:00 | Summer | TRUE | summer
2023-07-02 20:00 | 2023-07-02 21:00 | Summer | TRUE | summer
2023-07-02 21:00 | 2023-07-02 22:00 | Summer | FALSE | summer
2023-07-02 22:00 | 2023-07-02 23:00 | Summer | FALSE | summer
2023-07-02 23:00 | 2023-07-03 | Summer | FALSE | summer
2023-07-03 | 2023-07-03 01:00 | Summer | FALSE | summer
2023-07-03 01:00 | 2023-07-03 02:00 | Summer | FALSE | summer
2023-07-03 02:00 | 2023-07-03 03:00 | Summer | FALSE | summer
2023-07-03 03:00 | 2023-07-03 04:00 | Summer | FALSE | summer
2023-07-03 04:00 | 2023-07-03 05:00 | Summer | FALSE | summer
2023-07-03 05:00 | 2023-07-03 06:00 | Summer | FALSE | summer
2023-07-03 06:00 | 2023-07-03 07:00 | Summer | FALSE | summer
2023-07-03 07:00 | 2023-07-03 08:00 | Summer | FALSE | summer
2023-07-03 08:00 | 2023-07-03 09:00 | Summer | FALSE | summer
2023-07-03 09:00 | 2023-07-03 10:00 | Summer | FALSE | summer
2023-07-03 10:00 | 2023-07-03 11:00 | Summer | FALSE | summer
2023-07-03 11:00 | 2023-07-03 12:00 | Summer | FALSE | summer
2023-07-03 12:00 | 2023-07-03 13:00 | Summer | FALSE | summer
2023-07-03 13:00 | 2023-07-03 14:00 | Summer | FALSE | summer
2023-07-03 14:00 | 2023-07-03 15:00 | Summer | FALSE | summer
2023-07-03 15:00 | 2023-07-03 16:00 | Summer | FALSE | summer
2023-07-03 16:00 | 2023-07-03 17:00 | Summer | TRUE | summer
2023-07-03 17:00 | 2023-07-03 18:00 | Summer | TRUE | summer
2023-07-03 18:00 | 2023-07-03 19:00 | Summer | TRUE | summer
2023-07-03 19:00 | 2023-07-03 20:00 | Summer | TRUE | summer
2023-07-03 20:00 | 2023-07-03 21:00 | Summer | TRUE | summer
2023-07-03 21:00 | 2023-07-03 22:00 | Summer | FALSE | summer
2023-07-03 22:00 | 2023-07-03 23:00 | Summer | FALSE | summer
2023-07-03 23:00 | 2023-07-04 | Summer | FALSE | summer
2023-07-04 | 2023-07-04 01:00 | Summer | FALSE | summer
2023-07-04 01:00 | 2023-07-04 02:00 | Summer | FALSE | summer
2023-07-04 02:00 | 2023-07-04 03:00 | Summer | FALSE | summer
2023-07-04 03:00 | 2023-07-04 04:00 | Summer | FALSE | summer
2023-07-04 04:00 | 2023-07-04 05:00 | Summer | FALSE | summer
2023-07-04 05:00 | 2023-07-04 06:00 | Summer | FALSE | summer
2023-07-04 06:00 | 2023-07-04 07:00 | Summer | FALSE | summer
2023-07-04 07:00 | 2023-07-04 08:00 | Summer | FALSE | summer
2023-07-04 08:00 | 2023-07-04 09:00 | Summer | FALSE | summer
2023-07-04 09:00 | 2023-07-04 10:00 | Summer | FALSE | summer
2023-07-04 10:00 | 2023-07-04 11:00 | Summer | FALSE | summer
2023-07-04 11:00 | 2023-07-04 12:00 | Summer | FALSE | summer
2023-07-04 12:00 | 2023-07-04 13:00 | Summer | FALSE | summer
2023-07-04 13:00 | 2023-07-04 14:00 | Summer | FALSE | summer
2023-07-04 14:00 | 2023-07-04 15:00 | Summer | FALSE | summer
2023-07-04 15:00 | 2023-07-04 16:00 | Summer | FALSE | summer
2023-07-04 16:00 | 2023-07-04 17:00 | Summer | TRUE | summer
2023-07-04 17:00 | 2023-07-04 18:00 | Summer | TRUE | summer
2023-07-04 18:00 | 2023-07-04 19:00 | Summer | TRUE | summer
2023-07-04 19:00 | 2023-07-04 20:00 | Summer | TRUE | summer
2023-07-04 20:00 | 2023-07-04 21:00 | Summer | TRUE | summer
2023-07-04 21:00 | 2023-07-04 22:00 | Summer | FALSE | summer
2023-07-04 22:00 | 2023-07-04 23:00 | Summer | FALSE | summer
2023-07-04 23:00 | 2023-07-05 | Summer | FALSE | summer
2023-07-05 | 2023-07-05 01:00 | Summer | FALSE | summer
2023-07-05 01:00 | 2023-07-05 02:00 | Summer | FALSE | summer
2023-07-05 02:00 | 2023-07-05 03:00 | Summer | FALSE | summer
2023-07-05 03:00 | 2023-07-05 04:00 | Summer | FALSE | summer
2023-07-05 04:00 | 2023-07-05 05:00 | Summer | FALSE | summer
2023-07-05 05:00 | 2023-07-05 06:00 | Summer | FALSE | summer
2023-07-05 06:00 | 2023-07-05 07:00 | Summer | FALSE | summer
2023-07-05 07:00 | 2023-07-05 08:00 | Summer | FALSE | summer
2023-07-05 08:00 | 2023-07-05 09:00 | Summer | FALSE | summer
2023-07-05 09:00 | 2023-07-05 10:00 | Summer | FALSE | summer
2023-07-05 10:00 | 2023-07-05 11:00 | Summer | FALSE | summer
2023-07-05 11:00 | 2023-07-05 12:00 | Summer | FALSE | summer
2023-07-05 12:00 | 2023-07-05 13:00 | Summer | FALSE | summer
2023-07-05 13:00 | 2023-07-05 14:00 | Summer | FALSE | summer
2023-07-05 14:00 | 2023-07-05 15:00 | Summer | FALSE | summer
2023-07-05 15:00 | 2023-07-05 16:00 | Summer | FALSE | summer
2023-07-05 16:00 | 2023-07-05 17:00 | Summer | TRUE | summer
2023-07-05 17:00 | 2023-07-05 18:00 | Summer | TRUE | summer
2023-07-05 18:00 | 2023-07-05 19:00 | Summer | TRUE | summer
2023-07-05 19:00 | 2023-07-05 20:00 | Summer | TRUE | summer
2023-07-05 20:00 | 2023-07-05 21:00 | Summer | TRUE | summer
2023-07-05 21:00 | 2023-07-05 22:00 | Summer | FALSE | summer
2023-07-05 22:00 | 2023-07-05 23:00 | Summer | FALSE | summer
2023-07-05 23:00 | 2023-07-06 | Summer | FALSE | summer
2023-07-06 | 2023-07-06 01:00 | Summer | FALSE | summer
2023-07-06 01:00 | 2023-07-06 02:00 | Summer | FALSE | summer
2023-07-06 02:00 | 2023-07-06 03:00 | Summer | FALSE | summer
2023-07-06 03:00 | 2023-07-06 04:00 | Summer | FALSE | summer
2023-07-06 04:00 | 2023-07-06 05:00 | Summer | FALSE | summer
2023-07-06 05:00 | 2023-07-06 06:00 | Summer | FALSE | summer
2023-07-06 06:00 | 2023-07-06 07:00 | Summer | FALSE | summer
2023-07-06 07:00 | 2023-07-06 08:00 | Summer | FALSE | summer
2023-07-06 08:00 | 2023-07-06 09:00 | Summer | FALSE | summer
2023-07-06 09:00 | 2023-07-06 10:00 | Summer | FALSE | summer
2023-07-06 10:00 | 2023-07-06 11:00 | Summer | FALSE | summer
2023-07-06 11:00 | 2023-07-06 12:00 | Summer | FALSE | summer
2023-07-06 12:00 | 2023-07-06 13:00 | Summer | FALSE | summer
2023-07-06 13:00 | 2023-07-06 14:00 | Summer | FALSE | summer
2023-07-06 14:00 | 2023-07-06 15:00 | Summer | FALSE | summer
2023-07-06 15:00 | 2023-07-06 16:00 | Summer | FALSE | summer
2023-07-06 16:00 | 2023-07-06 17:00 | Summer | TRUE | summer
2023-07-06 17:00 | 2023-07-06 18:00 | Summer | TRUE | summer
2023-07-06 18:00 | 2023-07-06 19:00 | Summer | TRUE | summer
2023-07-06 19:00 | 2023-07-06 20:00 | Summer | TRUE | summer
2023-07-06 20:00 | 2023-07-06 21:00 | Summer | TRUE | summer
2023-07-06 21:00 | 2023-07-06 22:00 | Summer | FALSE | summer
2023-07-06 22:00 | 2023-07-06 23:00 | Summer | FALSE | summer
2023-07-06 23:00 | 2023-07-07 | Summer | FALSE | summer
2023-07-07 | 2023-07-07 01:00 | Summer | FALSE | summer
2023-07-07 01:00 | 2023-07-07 02:00 | Summer | FALSE | summer
2023-07-07 02:00 | 2023-07-07 03:00 | Summer | FALSE | summer
2023-07-07 03:00 | 2023-07-07 04:00 | Summer | FALSE | summer
2023-07-07 04:00 | 2023-07-07 05:00 | Summer | FALSE | summer
2023-07-07 05:00 | 2023-07-07 06:00 | Summer | FALSE | summer
2023-07-07 06:00 | 2023-07-07 07:00 | Summer | FALSE | summer
2023-07-07 07:00 | 2023-07-07 08:00 | Summer | FALSE | summer
2023-07-07 08:00 | 2023-07-07 09:00 | Summer | FALSE | summer
2023-07-07 09:00 | 2023-07-07 10:00 | Summer | FALSE | summer
2023-07-07 10:00 | 2023-07-07 11:00 | Summer | FALSE | summer
2023-07-07 11:00 | 2023-07-07 12:00 | Summer | FALSE | summer
2023-07-07 12:00 | 2023-07-07 13:00 | Summer | FALSE | summer
2023-07-07 13:00 | 2023-07-07 14:00 | Summer | FALSE | summer
2023-07-07 14:00 | 2023-07-07 15:00 | Summer | FALSE | summer
2023-07-07 15:00 | 2023-07-07 16:00 | Summer | FALSE | summer
2023-07-07 16:00 | 2023-07-07 17:00 | Summer | TRUE | summer
2023-07-07 17:00 | 2023-07-07 18:00 | Summer | TRUE | summer
2023-07-07 18:00 | 2023-07-07 19:00 | Summer | TRUE | summer
2023-07-07 19:00 | 2023-07-07 20:00 | Summer | TRUE | summer
2023-07-07 20:00 | 2023-07-07 21:00 | Summer | TRUE | summer
2023-07-07 21:00 | 2023-07-07 22:00 | Summer | FALSE | summer
2023-07-07 22:00 | 2023-07-07 23:00 | Summer | FALSE | summer
2023-07-07 23:00 | 2023-07-08 | Summer | FALSE | summer
2023-07-08 | 2023-07-08 01:00 | Summer | FALSE | summer
2023-07-08 01:00 | 2023-07-08 02:00 | Summer | FALSE | summer
2023-07-08 02:00 | 2023-07-08 03:00 | Summer | FALSE | summer
2023-07-08 03:00 | 2023-07-08 04:00 | Summer | FALSE | summer
2023-07-08 04:00 | 2023-07-08 05:00 | Summer | FALSE | summer
2023-07-08 05:00 | 2023-07-08 06:00 | Summer | FALSE | summer
2023-07-08 06:00 | 2023-07-08 07:00 | Summer | FALSE | summer
2023-07-08 07:00 | 2023-07-08 08:00 | Summer | FALSE | summer
2023-07-08 08:00 | 2023-07-08 09:00 | Summer | FALSE | summer
2023-07-08 09:00 | 2023-07-08 10:00 | Summer | FALSE | summer
2023-07-08 10:00 | 2023-07-08 11:00 | Summer | FALSE | summer
2023-07-08 11:00 | 2023-07-08 12:00 | Summer | FALSE | summer
2023-07-08 12:00 | 2023-07-08 13:00 | Summer | FALSE | summer
2023-07-08 13:00 | 2023-07-08 14:00 | Summer | FALSE | summer
2023-07-08 14:00 | 2023-07-08 15:00 | Summer | FALSE | summer
2023-07-08 15:00 | 2023-07-08 16:00 | Summer | FALSE | summer
2023-07-08 16:00 | 2023-07-08 17:00 | Summer | TRUE | summer
2023-07-08 17:00 | 2023-07-08 18:00 | Summer | TRUE | summer
2023-07-08 18:00 | 2023-07-08 19:00 | Summer | TRUE | summer
2023-07-08 19:00 | 2023-07-08 20:00 | Summer | TRUE | summer
2023-07-08 20:00 | 2023-07-08 21:00 | Summer | TRUE | summer
2023-07-08 21:00 | 2023-07-08 22:00 | Summer | FALSE | summer
2023-07-08 22:00 | 2023-07-08 23:00 | Summer | FALSE | summer
2023-07-08 23:00 | 2023-07-09 | Summer | FALSE | summer
2023-07-09 | 2023-07-09 01:00 | Summer | FALSE | summer
2023-07-09 01:00 | 2023-07-09 02:00 | Summer | FALSE | summer
2023-07-09 02:00 | 2023-07-09 03:00 | Summer | FALSE | summer
2023-07-09 03:00 | 2023-07-09 04:00 | Summer | FALSE | summer
2023-07-09 04:00 | 2023-07-09 05:00 | Summer | FALSE | summer
2023-07-09 05:00 | 2023-07-09 06:00 | Summer | FALSE | summer
2023-07-09 06:00 | 2023-07-09 07:00 | Summer | FALSE | summer
2023-07-09 07:00 | 2023-07-09 08:00 | Summer | FALSE | summer
2023-07-09 08:00 | 2023-07-09 09:00 | Summer | FALSE | summer
2023-07-09 09:00 | 2023-07-09 10:00 | Summer | FALSE | summer
2023-07-09 10:00 | 2023-07-09 11:00 | Summer | FALSE | summer
2023-07-09 11:00 | 2023-07-09 12:00 | Summer | FALSE | summer
2023-07-09 12:00 | 2023-07-09 13:00 | Summer | FALSE | summer
2023-07-09 13:00 | 2023-07-09 14:00 | Summer | FALSE | summer
2023-07-09 14:00 | 2023-07-09 15:00 | Summer | FALSE | summer
2023-07-09 15:00 | 2023-07-09 16:00 | Summer | FALSE | summer
2023-07-09 16:00 | 2023-07-09 17:00 | Summer | TRUE | summer
2023-07-09 17:00 | 2023-07-09 18:00 | Summer | TRUE | summer
2023-07-09 18:00 | 2023-07-09 19:00 | Summer | TRUE | summer
2023-07-09 19:00 | 2023-07-09 20:00 | Summer | TRUE | summer
2023-07-09 20:00 | 2023-07-09 21:00 | Summer | TRUE | summer
2023-07-09 21:00 | 2023-07-09 22:00 | Summer | FALSE | summer
2023-07-09 22:00 | 2023-07-09 23:00 | Summer | FALSE | summer
2023-07-09 23:00 | 2023-07-10 | Summer | FALSE | summer
2023-07-10 | 2023-07-10 01:00 | Summer | FALSE | summer
2023-07-10 01:00 | 2023-07-10 02:00 | Summer | FALSE | summer
2023-07-10 02:00 | 2023-07-10 03:00 | Summer | FALSE | summer
2023-07-10 03:00 | 2023-07-10 04:00 | Summer | FALSE | summer
2023-07-10 04:00 | 2023-07-10 05:00 | Summer | FALSE | summer
2023-07-10 05:00 | 2023-07-10 06:00 | Summer | FALSE | summer
2023-07-10 06:00 | 2023-07-10 07:00 | Summer | FALSE | summer
2023-07-10 07:00 | 2023-07-10 08:00 | Summer | FALSE | summer
2023-07-10 08:00 | 2023-07-10 09:00 | Summer | FALSE | summer
2023-07-10 09:00 | 2023-07-10 10:00 | Summer | FALSE | summer
2023-07-10 10:00 | 2023-07-10 11:00 | Summer | FALSE | summer
2023-07-10 11:00 | 2023-07-10 12:00 | Summer | FALSE | summer
2023-07-10 12:00 | 2023-07-10 13:00 | Summer | FALSE | summer
2023-07-10 13:00 | 2023-07-10 14:00 | Summer | FALSE | summer
2023-07-10 14:00 | 2023-07-10 15:00 | Summer | FALSE | summer
2023-07-10 15:00 | 2023-07-10 16:00 | Summer | FALSE | summer
2023-07-10 16:00 | 2023-07-10 17:00 | Summer | TRUE | summer
2023-07-10 17:00 | 2023-07-10 18:00 | Summer | TRUE | summer
2023-07-10 18:00 | 2023-07-10 19:00 | Summer | TRUE | summer
2023-07-10 19:00 | 2023-07-10 20:00 | Summer | TRUE | summer
2023-07-10 20:00 | 2023-07-10 21:00 | Summer | TRUE | summer
2023-07-10 21:00 | 2023-07-10 22:00 | Summer | FALSE | summer
2023-07-10 22:00 | 2023-07-10 23:00 | Summer | FALSE | summer
2023-07-10 23:00 | 2023-07-11 | Summer | FALSE | summer
2023-07-11 | 2023-07-11 01:00 | Summer | FALSE | summer
2023-07-11 01:00 | 2023-07-11 02:00 | Summer | FALSE | summer
2023-07-11 02:00 | 2023-07-11 03:00 | Summer | FALSE | summer
2023-07-11 03:00 | 2023-07-11 04:00 | Summer | FALSE | summer
2023-07-11 04:00 | 2023-07-11 05:00 | Summer | FALSE | summer
2023-07-11 05:00 | 2023-07-11 06:00 | Summer | FALSE | summer
2023-07-11 06:00 | 2023-07-11 07:00 | Summer | FALSE | summer
2023-07-11 07:00 | 2023-07-11 08:00 | Summer | FALSE | summer
2023-07-11 08:00 | 2023-07-11 09:00 | Summer | FALSE | summer
2023-07-11 09:00 | 2023-07-11 10:00 | Summer | FALSE | summer
2023-07-11 10:00 | 2023-07-11 11:00 | Summer | FALSE | summer
2023-07-11 11:00 | 2023-07-11 12:00 | Summer | FALSE | summer
2023-07-11 12:00 | 2023-07-11 13:00 | Summer | FALSE | summer
2023-07-11 13:00 | 2023-07-11 14:00 | Summer | FALSE | summer
2023-07-11 14:00 | 2023-07-11 15:00 | Summer | FALSE | summer
2023-07-11 15:00 | 2023-07-11 16:00 | Summer | FALSE | summer
2023-07-11 16:00 | 2023-07-11 17:00 | Summer | TRUE | summer
2023-07-11 17:00 | 2023-07-11 18:00 | Summer | TRUE | summer
2023-07-11 18:00 | 2023-07-11 19:00 | Summer | TRUE | summer
2023-07-11 19:00 | 2023-07-11 20:00 | Summer | TRUE | summer
2023-07-11 20:00 | 2023-07-11 21:00 | Summer | TRUE | summer
2023-07-11 21:00 | 2023-07-11 22:00 | Summer | FALSE | summer
2023-07-11 22:00 | 2023-07-11 23:00 | Summer | FALSE | summer
2023-07-11 23:00 | 2023-07-12 | Summer | FALSE | summer
2023-07-12 | 2023-07-12 01:00 | Summer | FALSE | summer
2023-07-12 01:00 | 2023-07-12 02:00 | Summer | FALSE | summer
2023-07-12 02:00 | 2023-07-12 03:00 | Summer | FALSE | summer
2023-07-12 03:00 | 2023-07-12 04:00 | Summer | FALSE | summer
2023-07-12 04:00 | 2023-07-12 05:00 | Summer | FALSE | summer
2023-07-12 05:00 | 2023-07-12 06:00 | Summer | FALSE | summer
2023-07-12 06:00 | 2023-07-12 07:00 | Summer | FALSE | summer
2023-07-12 07:00 | 2023-07-12 08:00 | Summer | FALSE | summer
2023-07-12 08:00 | 2023-07-12 09:00 | Summer | FALSE | summer
2023-07-12 09:00 | 2023-07-12 10:00 | Summer | FALSE | summer
2023-07-12 10:00 | 2023-07-12 11:00 | Summer | FALSE | summer
2023-07-12 11:00 | 2023-07-12 12:00 | Summer | FALSE | summer
2023-07-12 12:00 | 2023-07-12 13:00 | Summer | FALSE | summer
2023-07-12 13:00 | 2023-07-12 14:00 | Summer | FALSE | summer
2023-07-12 14:00 | 2023-07-12 15:00 | Summer | FALSE | summer
2023-07-12 15:00 | 2023-07-12 16:00 | Summer | FALSE | summer
2023-07-12 16:00 | 2023-07-12 17:00 | Summer | TRUE | summer
2023-07-12 17:00 | 2023-07-12 18:00 | Summer | TRUE | summer
2023-07-12 18:00 | 2023-07-12 19:00 | Summer | TRUE | summer
2023-07-12 19:00 | 2023-07-12 20:00 | Summer | TRUE | summer
2023-07-12 20:00 | 2023-07-12 21:00 | Summer | TRUE | summer
2023-07-12 21:00 | 2023-07-12 22:00 | Summer | FALSE | summer
2023-07-12 22:00 | 2023-07-12 23:00 | Summer | FALSE | summer
2023-07-12 23:00 | 2023-07-13 | Summer | FALSE | summer
2023-07-13 | 2023-07-13 01:00 | Summer | FALSE | summer
2023-07-13 01:00 | 2023-07-13 02:00 | Summer | FALSE | summer
2023-07-13 02:00 | 2023-07-13 03:00 | Summer | FALSE | summer
2023-07-13 03:00 | 2023-07-13 04:00 | Summer | FALSE | summer
2023-07-13 04:00 | 2023-07-13 05:00 | Summer | FALSE | summer
2023-07-13 05:00 | 2023-07-13 06:00 | Summer | FALSE | summer
2023-07-13 06:00 | 2023-07-13 07:00 | Summer | FALSE | summer
2023-07-13 07:00 | 2023-07-13 08:00 | Summer | FALSE | summer
2023-07-13 08:00 | 2023-07-13 09:00 | Summer | FALSE | summer
2023-07-13 09:00 | 2023-07-13 10:00 | Summer | FALSE | summer
2023-07-13 10:00 | 2023-07-13 11:00 | Summer | FALSE | summer
2023-07-13 11:00 | 2023-07-13 12:00 | Summer | FALSE | summer
2023-07-13 12:00 | 2023-07-13 13:00 | Summer | FALSE | summer
2023-07-13 13:00 | 2023-07-13 14:00 | Summer | FALSE | summer
2023-07-13 14:00 | 2023-07-13 15:00 | Summer | FALSE | summer
2023-07-13 15:00 | 2023-07-13 16:00 | Summer | FALSE | summer
2023-07-13 16:00 | 2023-07-13 17:00 | Summer | TRUE | summer
2023-07-13 17:00 | 2023-07-13 18:00 | Summer | TRUE | summer
2023-07-13 18:00 | 2023-07-13 19:00 | Summer | TRUE | summer
2023-07-13 19:00 | 2023-07-13 20:00 | Summer | TRUE | summer
2023-07-13 20:00 | 2023-07-13 21:00 | Summer | TRUE | summer
2023-07-13 21:00 | 2023-07-13 22:00 | Summer | FALSE | summer
2023-07-13 22:00 | 2023-07-13 23:00 | Summer | FALSE | summer
2023-07-13 23:00 | 2023-07-14 | Summer | FALSE | summer
2023-07-14 | 2023-07-14 01:00 | Summer | FALSE | summer
2023-07-14 01:00 | 2023-07-14 02:00 | Summer | FALSE | summer
2023-07-14 02:00 | 2023-07-14 03:00 | Summer | FALSE | summer
2023-07-14 03:00 | 2023-07-14 04:00 | Summer | FALSE | summer
2023-07-14 04:00 | 2023-07-14 05:00 | Summer | FALSE | summer
2023-07-14 05:00 | 2023-07-14 06:00 | Summer | FALSE | summer
2023-07-14 06:00 | 2023-07-14 07:00 | Summer | FALSE | summer
2023-07-14 07:00 | 2023-07-14 08:00 | Summer | FALSE | summer
2023-07-14 08:00 | 2023-07-14 09:00 | Summer | FALSE | summer
2023-07-14 09:00 | 2023-07-14 10:00 | Summer | FALSE | summer
2023-07-14 10:00 | 2023-07-14 11:00 | Summer | FALSE | summer
2023-07-14 11:00 | 2023-07-14 12:00 | Summer | FALSE | summer
2023-07-14 12:00 | 2023-07-14 13:00 | Summer | FALSE | summer
2023-07-14 13:00 | 2023-07-14 14:00 | Summer | FALSE | summer
2023-07-14 14:00 | 2023-07-14 15:00 | Summer | FALSE | summer
2023-07-14 15:00 | 2023-07-14 16:00 | Summer | FALSE | summer
2023-07-14 16:00 | 2023-07-14 17:00 | Summer | TRUE | summer
2023-07-14 17:00 | 2023-07-14 18:00 | Summer | TRUE | summer
2023-07-14 18:00 | 2023-07-14 19:00 | Summer | TRUE | summer
2023-07-14 19:00 | 2023-07-14 20:00 | Summer | TRUE | summer
2023-07-14 20:00 | 2023-07-14 21:00 | Summer | TRUE | summer
2023-07-14 21:00 | 2023-07-14 22:00 | Summer | FALSE | summer
2023-07-14 22:00 | 2023-07-14 23:00 | Summer | FALSE | summer
2023-07-14 23:00 | 2023-07-15 | Summer | FALSE | summer
2023-07-15 | 2023-07-15 01:00 | Summer | FALSE | summer
2023-07-15 01:00 | 2023-07-15 02:00 | Summer | FALSE | summer
2023-07-15 02:00 | 2023-07-15 03:00 | Summer | FALSE | summer
2023-07-15 03:00 | 2023-07-15 04:00 | Summer | FALSE | summer
2023-07-15 04:00 | 2023-07-15 05:00 | Summer | FALSE | summer
2023-07-15 05:00 | 2023-07-15 06:00 | Summer | FALSE | summer
2023-07-15 06:00 | 2023-07-15 07:00 | Summer | FALSE | summer
2023-07-15 07:00 | 2023-07-15 08:00 | Summer | FALSE | summer
2023-07-15 08:00 | 2023-07-15 09:00 | Summer | FALSE | summer
2023-07-15 09:00 | 2023-07-15 10:00 | Summer | FALSE | summer
2023-07-15 10:00 | 2023-07-15 11:00 | Summer | FALSE | summer
2023-07-15 11:00 | 2023-07-15 12:00 | Summer | FALSE | summer
2023-07-15 12:00 | 2023-07-15 13:00 | Summer | FALSE | summer
2023-07-15 13:00 | 2023-07-15 14:00 | Summer | FALSE | summer
2023-07-15 14:00 | 2023-07-15 15:00 | Summer | FALSE | summer
2023-07-15 15:00 | 2023-07-15 16:00 | Summer | FALSE | summer
2023-07-15 16:00 | 2023-07-15 17:00 | Summer | TRUE | summer
2023-07-15 17:00 | 2023-07-15 18:00 | Summer | TRUE | summer
2023-07-15 18:00 | 2023-07-15 19:00 | Summer | TRUE | summer
2023-07-15 19:00 | 2023-07-15 20:00 | Summer | TRUE | summer
2023-07-15 20:00 | 2023-07-15 21:00 | Summer | TRUE | summer
2023-07-15 21:00 | 2023-07-15 22:00 | Summer | FALSE | summer
2023-07-15 22:00 | 2023-07-15 23:00 | Summer | FALSE | summer
2023-07-15 23:00 | 2023-07-16 | Summer | FALSE | summer
2023-07-16 | 2023-07-16 01:00 | Summer | FALSE | summer
2023-07-16 01:00 | 2023-07-16 02:00 | Summer | FALSE | summer
2023-07-16 02:00 | 2023-07-16 03:00 | Summer | FALSE | summer
2023-07-16 03:00 | 2023-07-16 04:00 | Summer | FALSE | summer
2023-07-16 04:00 | 2023-07-16 05:00 | Summer | FALSE | summer
2023-07-16 05:00 | 2023-07-16 06:00 | Summer | FALSE | summer
2023-07-16 06:00 | 2023-07-16 07:00 | Summer | FALSE | summer
2023-07-16 07:00 | 2023-07-16 08:00 | Summer | FALSE | summer
2023-07-16 08:00 | 2023-07-16 09:00 | Summer | FALSE | summer
2023-07-16 09:00 | 2023-07-16 10:00 | Summer | FALSE | summer
2023-07-16 10:00 | 2023-07-16 11:00 | Summer | FALSE | summer
2023-07-16 11:00 | 2023-07-16 12:00 | Summer | FALSE | summer
2023-07-16 12:00 | 2023-07-16 13:00 | Summer | FALSE | summer
2023-07-16 13:00 | 2023-07-16 14:00 | Summer | FALSE | summer
2023-07-16 14:00 | 2023-07-16 15:00 | Summer | FALSE | summer
2023-07-16 15:00 | 2023-07-16 16:00 | Summer | FALSE | summer
2023-07-16 16:00 | 2023-07-16 17:00 | Summer | TRUE | summer
2023-07-16 17:00 | 2023-07-16 18:00 | Summer | TRUE | summer
2023-07-16 18:00 | 2023-07-16 19:00 | Summer | TRUE | summer
2023-07-16 19:00 | 2023-07-16 20:00 | Summer | TRUE | summer
2023-07-16 20:00 | 2023-07-16 21:00 | Summer | TRUE | summer
2023-07-16 21:00 | 2023-07-16 22:00 | Summer | FALSE | summer
2023-07-16 22:00 | 2023-07-16 23:00 | Summer | FALSE | summer
2023-07-16 23:00 | 2023-07-17 | Summer | FALSE | summer
2023-07-17 | 2023-07-17 01:00 | Summer | FALSE | summer
2023-07-17 01:00 | 2023-07-17 02:00 | Summer | FALSE | summer
2023-07-17 02:00 | 2023-07-17 03:00 | Summer | FALSE | summer
2023-07-17 03:00 | 2023-07-17 04:00 | Summer | FALSE | summer
2023-07-17 04:00 | 2023-07-17 05:00 | Summer | FALSE | summer
2023-07-17 05:00 | 2023-07-17 06:00 | Summer | FALSE | summer
2023-07-17 06:00 | 2023-07-17 07:00 | Summer | FALSE | summer
2023-07-17 07:00 | 2023-07-17 08:00 | Summer | FALSE | summer
2023-07-17 08:00 | 2023-07-17 09:00 | Summer | FALSE | summer
2023-07-17 09:00 | 2023-07-17 10:00 | Summer | FALSE | summer
2023-07-17 10:00 | 2023-07-17 11:00 | Summer | FALSE | summer
2023-07-17 11:00 | 2023-07-17 12:00 | Summer | FALSE | summer
2023-07-17 12:00 | 2023-07-17 13:00 | Summer | FALSE | summer
2023-07-17 13:00 | 2023-07-17 14:00 | Summer | FALSE | summer
2023-07-17 14:00 | 2023-07-17 15:00 | Summer | FALSE | summer
2023-07-17 15:00 | 2023-07-17 16:00 | Summer | FALSE | summer
2023-07-17 16:00 | 2023-07-17 17:00 | Summer | TRUE | summer
2023-07-17 17:00 | 2023-07-17 18:00 | Summer | TRUE | summer
2023-07-17 18:00 | 2023-07-17 19:00 | Summer | TRUE | summer
2023-07-17 19:00 | 2023-07-17 20:00 | Summer | TRUE | summer
2023-07-17 20:00 | 2023-07-17 21:00 | Summer | TRUE | summer
2023-07-17 21:00 | 2023-07-17 22:00 | Summer | FALSE | summer
2023-07-17 22:00 | 2023-07-17 23:00 | Summer | FALSE | summer
2023-07-17 23:00 | 2023-07-18 | Summer | FALSE | summer
2023-07-18 | 2023-07-18 01:00 | Summer | FALSE | summer
2023-07-18 01:00 | 2023-07-18 02:00 | Summer | FALSE | summer
2023-07-18 02:00 | 2023-07-18 03:00 | Summer | FALSE | summer
2023-07-18 03:00 | 2023-07-18 04:00 | Summer | FALSE | summer
2023-07-18 04:00 | 2023-07-18 05:00 | Summer | FALSE | summer
2023-07-18 05:00 | 2023-07-18 06:00 | Summer | FALSE | summer
2023-07-18 06:00 | 2023-07-18 07:00 | Summer | FALSE | summer
2023-07-18 07:00 | 2023-07-18 08:00 | Summer | FALSE | summer
2023-07-18 08:00 | 2023-07-18 09:00 | Summer | FALSE | summer
2023-07-18 09:00 | 2023-07-18 10:00 | Summer | FALSE | summer
2023-07-18 10:00 | 2023-07-18 11:00 | Summer | FALSE | summer
2023-07-18 11:00 | 2023-07-18 12:00 | Summer | FALSE | summer
2023-07-18 12:00 | 2023-07-18 13:00 | Summer | FALSE | summer
2023-07-18 13:00 | 2023-07-18 14:00 | Summer | FALSE | summer
2023-07-18 14:00 | 2023-07-18 15:00 | Summer | FALSE | summer
2023-07-18 15:00 | 2023-07-18 16:00 | Summer | FALSE | summer
2023-07-18 16:00 | 2023-07-18 17:00 | Summer | TRUE | summer
2023-07-18 17:00 | 2023-07-18 18:00 | Summer | TRUE | summer
2023-07-18 18:00 | 2023-07-18 19:00 | Summer | TRUE | summer
2023-07-18 19:00 | 2023-07-18 20:00 | Summer | TRUE | summer
2023-07-18 20:00 | 2023-07-18 21:00 | Summer | TRUE | summer
2023-07-18 21:00 | 2023-07-18 22:00 | Summer | FALSE | summer
2023-07-18 22:00 | 2023-07-18 23:00 | Summer | FALSE | summer
2023-07-18 23:00 | 2023-07-19 | Summer | FALSE | summer
2023-07-19 | 2023-07-19 01:00 | Summer | FALSE | summer
2023-07-19 01:00 | 2023-07-19 02:00 | Summer | FALSE | summer
2023-07-19 02:00 | 2023-07-19 03:00 | Summer | FALSE | summer
2023-07-19 03:00 | 2023-07-19 04:00 | Summer | FALSE | summer
2023-07-19 04:00 | 2023-07-19 05:00 | Summer | FALSE | summer
2023-07-19 05:00 | 2023-07-19 06:00 | Summer | FALSE | summer
2023-07-19 06:00 | 2023-07-19 07:00 | Summer | FALSE | summer
2023-07-19 07:00 | 2023-07-19 08:00 | Summer | FALSE | summer
2023-07-19 08:00 | 2023-07-19 09:00 | Summer | FALSE | summer
2023-07-19 09:00 | 2023-07-19 10:00 | Summer | FALSE | summer
2023-07-19 10:00 | 2023-07-19 11:00 | Summer | FALSE | summer
2023-07-19 11:00 | 2023-07-19 12:00 | Summer | FALSE | summer
2023-07-19 12:00 | 2023-07-19 13:00 | Summer | FALSE | summer
2023-07-19 13:00 | 2023-07-19 14:00 | Summer | FALSE | summer
2023-07-19 14:00 | 2023-07-19 15:00 | Summer | FALSE | summer
2023-07-19 15:00 | 2023-07-19 16:00 | Summer | FALSE | summer
2023-07-19 16:00 | 2023-07-19 17:00 | Summer | TRUE | summer
2023-07-19 17:00 | 2023-07-19 18:00 | Summer | TRUE | summer
2023-07-19 18:00 | 2023-07-19 19:00 | Summer | TRUE | summer
2023-07-19 19:00 | 2023-07-19 20:00 | Summer | TRUE | summer
2023-07-19 20:00 | 2023-07-19 21:00 | Summer | TRUE | summer
2023-07-19 21:00 | 2023-07-19 22:00 | Summer | FALSE | summer
2023-07-19 22:00 | 2023-07-19 23:00 | Summer | FALSE | summer
2023-07-19 23:00 | 2023-07-20 | Summer | FALSE | summer
2023-07-20 | 2023-07-20 01:00 | Summer | FALSE | summer
2023-07-20 01:00 | 2023-07-20 02:00 | Summer | FALSE | summer
2023-07-20 02:00 | 2023-07-20 03:00 | Summer | FALSE | summer
2023-07-20 03:00 | 2023-07-20 04:00 | Summer | FALSE | summer
2023-07-20 04:00 | 2023-07-20 05:00 | Summer | FALSE | summer
2023-07-20 05:00 | 2023-07-20 06:00 | Summer | FALSE | summer
2023-07-20 06:00 | 2023-07-20 07:00 | Summer | FALSE | summer
2023-07-20 07:00 | 2023-07-20 08:00 | Summer | FALSE | summer
2023-07-20 08:00 | 2023-07-20 09:00 | Summer | FALSE | summer
2023-07-20 09:00 | 2023-07-20 10:00 | Summer | FALSE | summer
2023-07-20 10:00 | 2023-07-20 11:00 | Summer | FALSE | summer
2023-07-20 11:00 | 2023-07-20 12:00 | Summer | FALSE | summer
2023-07-20 12:00 | 2023-07-20 13:00 | Summer | FALSE | summer
2023-07-20 13:00 | 2023-07-20 14:00 | Summer | FALSE | summer
2023-07-20 14:00 | 2023-07-20 15:00 | Summer | FALSE | summer
2023-07-20 15:00 | 2023-07-20 16:00 | Summer | FALSE | summer
2023-07-20 16:00 | 2023-07-20 17:00 | Summer | TRUE | summer
2023-07-20 17:00 | 2023-07-20 18:00 | Summer | TRUE | summer
2023-07-20 18:00 | 2023-07-20 19:00 | Summer | TRUE | summer
2023-07-20 19:00 | 2023-07-20 20:00 | Summer | TRUE | summer
2023-07-20 20:00 | 2023-07-20 21:00 | Summer | TRUE | summer
2023-07-20 21:00 | 2023-07-20 22:00 | Summer | FALSE | summer
2023-07-20 22:00 | 2023-07-20 23:00 | Summer | FALSE | summer
2023-07-20 23:00 | 2023-07-21 | Summer | FALSE | summer
2023-07-21 | 2023-07-21 01:00 | Summer | FALSE | summer
2023-07-21 01:00 | 2023-07-21 02:00 | Summer | FALSE | summer
2023-07-21 02:00 | 2023-07-21 03:00 | Summer | FALSE | summer
2023-07-21 03:00 | 2023-07-21 04:00 | Summer | FALSE | summer
2023-07-21 04:00 | 2023-07-21 05:00 | Summer | FALSE | summer
2023-07-21 05:00 | 2023-07-21 06:00 | Summer | FALSE | summer
2023-07-21 06:00 | 2023-07-21 07:00 | Summer | FALSE | summer
2023-07-21 07:00 | 2023-07-21 08:00 | Summer | FALSE | summer
2023-07-21 08:00 | 2023-07-21 09:00 | Summer | FALSE | summer
2023-07-21 09:00 | 2023-07-21 10:00 | Summer | FALSE | summer
2023-07-21 10:00 | 2023-07-21 11:00 | Summer | FALSE | summer
2023-07-21 11:00 | 2023-07-21 12:00 | Summer | FALSE | summer
2023-07-21 12:00 | 2023-07-21 13:00 | Summer | FALSE | summer
2023-07-21 13:00 | 2023-07-21 14:00 | Summer | FALSE | summer
2023-07-21 14:00 | 2023-07-21 15:00 | Summer | FALSE | summer
2023-07-21 15:00 | 2023-07-21 16:00 | Summer | FALSE | summer
2023-07-21 16:00 | 2023-07-21 17:00 | Summer | TRUE | summer
2023-07-21 17:00 | 2023-07-21 18:00 | Summer | TRUE | summer
2023-07-21 18:00 | 2023-07-21 19:00 | Summer | TRUE | summer
2023-07-21 19:00 | 2023-07-21 20:00 | Summer | TRUE | summer
2023-07-21 20:00 | 2023-07-21 21:00 | Summer | TRUE | summer
2023-07-21 21:00 | 2023-07-21 22:00 | Summer | FALSE | summer
2023-07-21 22:00 | 2023-07-21 23:00 | Summer | FALSE | summer
2023-07-21 23:00 | 2023-07-22 | Summer | FALSE | summer
2023-07-22 | 2023-07-22 01:00 | Summer | FALSE | summer
2023-07-22 01:00 | 2023-07-22 02:00 | Summer | FALSE | summer
2023-07-22 02:00 | 2023-07-22 03:00 | Summer | FALSE | summer
2023-07-22 03:00 | 2023-07-22 04:00 | Summer | FALSE | summer
2023-07-22 04:00 | 2023-07-22 05:00 | Summer | FALSE | summer
2023-07-22 05:00 | 2023-07-22 06:00 | Summer | FALSE | summer
2023-07-22 06:00 | 2023-07-22 07:00 | Summer | FALSE | summer
2023-07-22 07:00 | 2023-07-22 08:00 | Summer | FALSE | summer
2023-07-22 08:00 | 2023-07-22 09:00 | Summer | FALSE | summer
2023-07-22 09:00 | 2023-07-22 10:00 | Summer | FALSE | summer
2023-07-22 10:00 | 2023-07-22 11:00 | Summer | FALSE | summer
2023-07-22 11:00 | 2023-07-22 12:00 | Summer | FALSE | summer
2023-07-22 12:00 | 2023-07-22 13:00 | Summer | FALSE | summer
2023-07-22 13:00 | 2023-07-22 14:00 | Summer | FALSE | summer
2023-07-22 14:00 | 2023-07-22 15:00 | Summer | FALSE | summer
2023-07-22 15:00 | 2023-07-22 16:00 | Summer | FALSE | summer
2023-07-22 16:00 | 2023-07-22 17:00 | Summer | TRUE | summer
2023-07-22 17:00 | 2023-07-22 18:00 | Summer | TRUE | summer
2023-07-22 18:00 | 2023-07-22 19:00 | Summer | TRUE | summer
2023-07-22 19:00 | 2023-07-22 20:00 | Summer | TRUE | summer
2023-07-22 20:00 | 2023-07-22 21:00 | Summer | TRUE | summer
2023-07-22 21:00 | 2023-07-22 22:00 | Summer | FALSE | summer
2023-07-22 22:00 | 2023-07-22 23:00 | Summer | FALSE | summer
2023-07-22 23:00 | 2023-07-23 | Summer | FALSE | summer
2023-07-23 | 2023-07-23 01:00 | Summer | FALSE | summer
2023-07-23 01:00 | 2023-07-23 02:00 | Summer | FALSE | summer
2023-07-23 02:00 | 2023-07-23 03:00 | Summer | FALSE | summer
2023-07-23 03:00 | 2023-07-23 04:00 | Summer | FALSE | summer
2023-07-23 04:00 | 2023-07-23 05:00 | Summer | FALSE | summer
2023-07-23 05:00 | 2023-07-23 06:00 | Summer | FALSE | summer
2023-07-23 06:00 | 2023-07-23 07:00 | Summer | FALSE | summer
2023-07-23 07:00 | 2023-07-23 08:00 | Summer | FALSE | summer
2023-07-23 08:00 | 2023-07-23 09:00 | Summer | FALSE | summer
2023-07-23 09:00 | 2023-07-23 10:00 | Summer | FALSE | summer
2023-07-23 10:00 | 2023-07-23 11:00 | Summer | FALSE | summer
2023-07-23 11:00 | 2023-07-23 12:00 | Summer | FALSE | summer
2023-07-23 12:00 | 2023-07-23 13:00 | Summer | FALSE | summer
2023-07-23 13:00 | 2023-07-23 14:00 | Summer | FALSE | summer
2023-07-23 14:00 | 2023-07-23 15:00 | Summer | FALSE | summer
2023-07-23 15:00 | 2023-07-23 16:00 | Summer | FALSE | summer
2023-07-23 16:00 | 2023-07-23 17:00 | Summer | TRUE | summer
2023-07-23 17:00 | 2023-07-23 18:00 | Summer | TRUE | summer
2023-07-23 18:00 | 2023-07-23 19:00 | Summer | TRUE | summer
2023-07-23 19:00 | 2023-07-23 20:00 | Summer | TRUE | summer
2023-07-23 20:00 | 2023-07-23 21:00 | Summer | TRUE | summer
2023-07-23 21:00 | 2023-07-23 22:00 | Summer | FALSE | summer
2023-07-23 22:00 | 2023-07-23 23:00 | Summer | FALSE | summer
2023-07-23 23:00 | 2023-07-24 | Summer | FALSE | summer
2023-07-24 | 2023-07-24 01:00 | Summer | FALSE | summer
2023-07-24 01:00 | 2023-07-24 02:00 | Summer | FALSE | summer
2023-07-24 02:00 | 2023-07-24 03:00 | Summer | FALSE | summer
2023-07-24 03:00 | 2023-07-24 04:00 | Summer | FALSE | summer
2023-07-24 04:00 | 2023-07-24 05:00 | Summer | FALSE | summer
2023-07-24 05:00 | 2023-07-24 06:00 | Summer | FALSE | summer
2023-07-24 06:00 | 2023-07-24 07:00 | Summer | FALSE | summer
2023-07-24 07:00 | 2023-07-24 08:00 | Summer | FALSE | summer
2023-07-24 08:00 | 2023-07-24 09:00 | Summer | FALSE | summer
2023-07-24 09:00 | 2023-07-24 10:00 | Summer | FALSE | summer
2023-07-24 10:00 | 2023-07-24 11:00 | Summer | FALSE | summer
2023-07-24 11:00 | 2023-07-24 12:00 | Summer | FALSE | summer
2023-07-24 12:00 | 2023-07-24 13:00 | Summer | FALSE | summer
2023-07-24 13:00 | 2023-07-24 14:00 | Summer | FALSE | summer
2023-07-24 14:00 | 2023-07-24 15:00 | Summer | FALSE | summer
2023-07-24 15:00 | 2023-07-24 16:00 | Summer | FALSE | summer
2023-07-24 16:00 | 2023-07-24 17:00 | Summer | TRUE | summer
2023-07-24 17:00 | 2023-07-24 18:00 | Summer | TRUE | summer
2023-07-24 18:00 | 2023-07-24 19:00 | Summer | TRUE | summer
2023-07-24 19:00 | 2023-07-24 20:00 | Summer | TRUE | summer
2023-07-24 20:00 | 2023-07-24 21:00 | Summer | TRUE | summer
2023-07-24 21:00 | 2023-07-24 22:00 | Summer | FALSE | summer
2023-07-24 22:00 | 2023-07-24 23:00 | Summer | FALSE | summer
2023-07-24 23:00 | 2023-07-25 | Summer | FALSE | summer
2023-07-25 | 2023-07-25 01:00 | Summer | FALSE | summer
2023-07-25 01:00 | 2023-07-25 02:00 | Summer | FALSE | summer
2023-07-25 02:00 | 2023-07-25 03:00 | Summer | FALSE | summer
2023-07-25 03:00 | 2023-07-25 04:00 | Summer | FALSE | summer
2023-07-25 04:00 | 2023-07-25 05:00 | Summer | FALSE | summer
2023-07-25 05:00 | 2023-07-25 06:00 | Summer | FALSE | summer
2023-07-25 06:00 | 2023-07-25 07:00 | Summer | FALSE | summer
2023-07-25 07:00 | 2023-07-25 08:00 | Summer | FALSE | summer
2023-07-25 08:00 | 2023-07-25 09:00 | Summer | FALSE | summer
2023-07-25 09:00 | 2023-07-25 10:00 | Summer | FALSE | summer
2023-07-25 10:00 | 2023-07-25 11:00 | Summer | FALSE | summer
2023-07-25 11:00 | 2023-07-25 12:00 | Summer | FALSE | summer
2023-07-25 12:00 | 2023-07-25 13:00 | Summer | FALSE | summer
2023-07-25 13:00 | 2023-07-25 14:00 | Summer | FALSE | summer
2023-07-25 14:00 | 2023-07-25 15:00 | Summer | FALSE | summer
2023-07-25 15:00 | 2023-07-25 16:00 | Summer | FALSE | summer
2023-07-25 16:00 | 2023-07-25 17:00 | Summer | TRUE | summer
2023-07-25 17:00 | 2023-07-25 18:00 | Summer | TRUE | summer
2023-07-25 18:00 | 2023-07-25 19:00 | Summer | TRUE | summer
2023-07-25 19:00 | 2023-07-25 20:00 | Summer | TRUE | summer
2023-07-25 20:00 | 2023-07-25 21:00 | Summer | TRUE | summer
2023-07-25 21:00 | 2023-07-25 22:00 | Summer | FALSE | summer
2023-07-25 22:00 | 2023-07-25 23:00 | Summer | FALSE | summer
2023-07-25 23:00 | 2023-07-26 | Summer | FALSE | summer
2023-07-26 | 2023-07-26 01:00 | Summer | FALSE | summer
2023-07-26 01:00 | 2023-07-26 02:00 | Summer | FALSE | summer
2023-07-26 02:00 | 2023-07-26 03:00 | Summer | FALSE | summer
2023-07-26 03:00 | 2023-07-26 04:00 | Summer | FALSE | summer
2023-07-26 04:00 | 2023-07-26 05:00 | Summer | FALSE | summer
2023-07-26 05:00 | 2023-07-26 06:00 | Summer | FALSE | summer
2023-07-26 06:00 | 2023-07-26 07:00 | Summer | FALSE | summer
2023-07-26 07:00 | 2023-07-26 08:00 | Summer | FALSE | summer
2023-07-26 08:00 | 2023-07-26 09:00 | Summer | FALSE | summer
2023-07-26 09:00 | 2023-07-26 10:00 | Summer | FALSE | summer
2023-07-26 10:00 | 2023-07-26 11:00 | Summer | FALSE | summer
2023-07-26 11:00 | 2023-07-26 12:00 | Summer | FALSE | summer
2023-07-26 12:00 | 2023-07-26 13:00 | Summer | FALSE | summer
2023-07-26 13:00 | 2023-07-26 14:00 | Summer | FALSE | summer
2023-07-26 14:00 | 2023-07-26 15:00 | Summer | FALSE | summer
2023-07-26 15:00 | 2023-07-26 16:00 | Summer | FALSE | summer
2023-07-26 16:00 | 2023-07-26 17:00 | Summer | TRUE | summer
2023-07-26 17:00 | 2023-07-26 18:00 | Summer | TRUE | summer
2023-07-26 18:00 | 2023-07-26 19:00 | Summer | TRUE | summer
2023-07-26 19:00 | 2023-07-26 20:00 | Summer | TRUE | summer
2023-07-26 20:00 | 2023-07-26 21:00 | Summer | TRUE | summer
2023-07-26 21:00 | 2023-07-26 22:00 | Summer | FALSE | summer
2023-07-26 22:00 | 2023-07-26 23:00 | Summer | FALSE | summer
2023-07-26 23:00 | 2023-07-27 | Summer | FALSE | summer
2023-07-27 | 2023-07-27 01:00 | Summer | FALSE | summer
2023-07-27 01:00 | 2023-07-27 02:00 | Summer | FALSE | summer
2023-07-27 02:00 | 2023-07-27 03:00 | Summer | FALSE | summer
2023-07-27 03:00 | 2023-07-27 04:00 | Summer | FALSE | summer
2023-07-27 04:00 | 2023-07-27 05:00 | Summer | FALSE | summer
2023-07-27 05:00 | 2023-07-27 06:00 | Summer | FALSE | summer
2023-07-27 06:00 | 2023-07-27 07:00 | Summer | FALSE | summer
2023-07-27 07:00 | 2023-07-27 08:00 | Summer | FALSE | summer
2023-07-27 08:00 | 2023-07-27 09:00 | Summer | FALSE | summer
2023-07-27 09:00 | 2023-07-27 10:00 | Summer | FALSE | summer
2023-07-27 10:00 | 2023-07-27 11:00 | Summer | FALSE | summer
2023-07-27 11:00 | 2023-07-27 12:00 | Summer | FALSE | summer
2023-07-27 12:00 | 2023-07-27 13:00 | Summer | FALSE | summer
2023-07-27 13:00 | 2023-07-27 14:00 | Summer | FALSE | summer
2023-07-27 14:00 | 2023-07-27 15:00 | Summer | FALSE | summer
2023-07-27 15:00 | 2023-07-27 16:00 | Summer | FALSE | summer
2023-07-27 16:00 | 2023-07-27 17:00 | Summer | TRUE | summer
2023-07-27 17:00 | 2023-07-27 18:00 | Summer | TRUE | summer
2023-07-27 18:00 | 2023-07-27 19:00 | Summer | TRUE | summer
2023-07-27 19:00 | 2023-07-27 20:00 | Summer | TRUE | summer
2023-07-27 20:00 | 2023-07-27 21:00 | Summer | TRUE | summer
2023-07-27 21:00 | 2023-07-27 22:00 | Summer | FALSE | summer
2023-07-27 22:00 | 2023-07-27 23:00 | Summer | FALSE | summer
2023-07-27 23:00 | 2023-07-28 | Summer | FALSE | summer
2023-07-28 | 2023-07-28 01:00 | Summer | FALSE | summer
2023-07-28 01:00 | 2023-07-28 02:00 | Summer | FALSE | summer
2023-07-28 02:00 | 2023-07-28 03:00 | Summer | FALSE | summer
2023-07-28 03:00 | 2023-07-28 04:00 | Summer | FALSE | summer
2023-07-28 04:00 | 2023-07-28 05:00 | Summer | FALSE | summer
2023-07-28 05:00 | 2023-07-28 06:00 | Summer | FALSE | summer
2023-07-28 06:00 | 2023-07-28 07:00 | Summer | FALSE | summer
2023-07-28 07:00 | 2023-07-28 08:00 | Summer | FALSE | summer
2023-07-28 08:00 | 2023-07-28 09:00 | Summer | FALSE | summer
2023-07-28 09:00 | 2023-07-28 10:00 | Summer | FALSE | summer
2023-07-28 10:00 | 2023-07-28 11:00 | Summer | FALSE | summer
2023-07-28 11:00 | 2023-07-28 12:00 | Summer | FALSE | summer
2023-07-28 12:00 | 2023-07-28 13:00 | Summer | FALSE | summer
2023-07-28 13:00 | 2023-07-28 14:00 | Summer | FALSE | summer
2023-07-28 14:00 | 2023-07-28 15:00 | Summer | FALSE | summer
2023-07-28 15:00 | 2023-07-28 16:00 | Summer | FALSE | summer
2023-07-28 16:00 | 2023-07-28 17:00 | Summer | TRUE | summer
2023-07-28 17:00 | 2023-07-28 18:00 | Summer | TRUE | summer
2023-07-28 18:00 | 2023-07-28 19:00 | Summer | TRUE | summer
2023-07-28 19:00 | 2023-07-28 20:00 | Summer | TRUE | summer
2023-07-28 20:00 | 2023-07-28 21:00 | Summer | TRUE | summer
2023-07-28 21:00 | 2023-07-28 22:00 | Summer | FALSE | summer
2023-07-28 22:00 | 2023-07-28 23:00 | Summer | FALSE | summer
2023-07-28 23:00 | 2023-07-29 | Summer | FALSE | summer
2023-07-29 | 2023-07-29 01:00 | Summer | FALSE | summer
2023-07-29 01:00 | 2023-07-29 02:00 | Summer | FALSE | summer
2023-07-29 02:00 | 2023-07-29 03:00 | Summer | FALSE | summer
2023-07-29 03:00 | 2023-07-29 04:00 | Summer | FALSE | summer
2023-07-29 04:00 | 2023-07-29 05:00 | Summer | FALSE | summer
2023-07-29 05:00 | 2023-07-29 06:00 | Summer | FALSE | summer
2023-07-29 06:00 | 2023-07-29 07:00 | Summer | FALSE | summer
2023-07-29 07:00 | 2023-07-29 08:00 | Summer | FALSE | summer
2023-07-29 08:00 | 2023-07-29 09:00 | Summer | FALSE | summer
2023-07-29 09:00 | 2023-07-29 10:00 | Summer | FALSE | summer
2023-07-29 10:00 | 2023-07-29 11:00 | Summer | FALSE | summer
2023-07-29 11:00 | 2023-07-29 12:00 | Summer | FALSE | summer
2023-07-29 12:00 | 2023-07-29 13:00 | Summer | FALSE | summer
2023-07-29 13:00 | 2023-07-29 14:00 | Summer | FALSE | summer
2023-07-29 14:00 | 2023-07-29 15:00 | Summer | FALSE | summer
2023-07-29 15:00 | 2023-07-29 16:00 | Summer | FALSE | summer
2023-07-29 16:00 | 2023-07-29 17:00 | Summer | TRUE | summer
2023-07-29 17:00 | 2023-07-29 18:00 | Summer | TRUE | summer
2023-07-29 18:00 | 2023-07-29 19:00 | Summer | TRUE | summer
2023-07-29 19:00 | 2023-07-29 20:00 | Summer | TRUE | summer
2023-07-29 20:00 | 2023-07-29 21:00 | Summer | TRUE | summer
2023-07-29 21:00 | 2023-07-29 22:00 | Summer | FALSE | summer
2023-07-29 22:00 | 2023-07-29 23:00 | Summer | FALSE | summer
2023-07-29 23:00 | 2023-07-30 | Summer | FALSE | summer
2023-07-30 | 2023-07-30 01:00 | Summer | FALSE | summer
2023-07-30 01:00 | 2023-07-30 02:00 | Summer | FALSE | summer
2023-07-30 02:00 | 2023-07-30 03:00 | Summer | FALSE | summer
2023-07-30 03:00 | 2023-07-30 04:00 | Summer | FALSE | summer
2023-07-30 04:00 | 2023-07-30 05:00 | Summer | FALSE | summer
2023-07-30 05:00 | 2023-07-30 06:00 | Summer | FALSE | summer
2023-07-30 06:00 | 2023-07-30 07:00 | Summer | FALSE | summer
2023-07-30 07:00 | 2023-07-30 08:00 | Summer | FALSE | summer
2023-07-30 08:00 | 2023-07-30 09:00 | Summer | FALSE | summer
2023-07-30 09:00 | 2023-07-30 10:00 | Summer | FALSE | summer
2023-07-30 10:00 | 2023-07-30 11:00 | Summer | FALSE | summer
2023-07-30 11:00 | 2023-07-30 12:00 | Summer | FALSE | summer
2023-07-30 12:00 | 2023-07-30 13:00 | Summer | FALSE | summer
2023-07-30 13:00 | 2023-07-30 14:00 | Summer | FALSE | summer
2023-07-30 14:00 | 2023-07-30 15:00 | Summer | FALSE | summer
2023-07-30 15:00 | 2023-07-30 16:00 | Summer | FALSE | summer
2023-07-30 16:00 | 2023-07-30 17:00 | Summer | TRUE | summer
2023-07-30 17:00 | 2023-07-30 18:00 | Summer | TRUE | summer
2023-07-30 18:00 | 2023-07-30 19:00 | Summer | TRUE | summer
2023-07-30 19:00 | 2023-07-30 20:00 | Summer | TRUE | summer
2023-07-30 20:00 | 2023-07-30 21:00 | Summer | TRUE | summer
2023-07-30 21:00 | 2023-07-30 22:00 | Summer | FALSE | summer
2023-07-30 22:00 | 2023-07-30 23:00 | Summer | FALSE | summer
2023-07-30 23:00 | 2023-07-31 | Summer | FALSE | summer
2023-07-31 | 2023-07-31 01:00 | Summer | FALSE | summer
2023-07-31 01:00 | 2023-07-31 02:00 | Summer | FALSE | summer
2023-07-31 02:00 | 2023-07-31 03:00 | Summer | FALSE | summer
2023-07-31 03:00 | 2023-07-31 04:00 | Summer | FALSE | summer
2023-07-31 04:00 | 2023-07-31 05:00 | Summer | FALSE | summer
2023-07-31 05:00 | 2023-07-31 06:00 | Summer | FALSE | summer
2023-07-31 06:00 | 2023-07-31 07:00 | Summer | FALSE | summer
2023-07-31 07:00 | 2023-07-31 08:00 | Summer | FALSE | summer
2023-07-31 08:00 | 2023-07-31 09:00 | Summer | FALSE | summer
2023-07-31 09:00 | 2023-07-31 10:00 | Summer | FALSE | summer
2023-07-31 10:00 | 2023-07-31 11:00 | Summer | FALSE | summer
2023-07-31 11:00 | 2023-07-31 12:00 | Summer | FALSE | summer
2023-07-31 12:00 | 2023-07-31 13:00 | Summer | FALSE | summer
2023-07-31 13:00 | 2023-07-31 14:00 | Summer | FALSE | summer
2023-07-31 14:00 | 2023-07-31 15:00 | Summer | FALSE | summer
2023-07-31 15:00 | 2023-07-31 16:00 | Summer | FALSE | summer
2023-07-31 16:00 | 2023-07-31 17:00 | Summer | TRUE | summer
2023-07-31 17:00 | 2023-07-31 18:00 | Summer | TRUE | summer
2023-07-31 18:00 | 2023-07-31 19:00 | Summer | TRUE | summer
2023-07-31 19:00 | 2023-07-31 20:00 | Summer | TRUE | summer
2023-07-31 20:00 | 2023-07-31 21:00 | Summer | TRUE | summer
2023-07-31 21:00 | 2023-07-31 22:00 | Summer | FALSE | summer
2023-07-31 22:00 | 2023-07-31 23:00 | Summer | FALSE | summer
2023-07-31 23:00 | 2023-08-01 | Summer | FALSE | summer
2023-08-01 | 2023-08-01 01:00 | Summer | FALSE | summer
2023-08-01 01:00 | 2023-08-01 02:00 | Summer | FALSE | summer
2023-08-01 02:00 | 2023-08-01 03:00 | Summer | FALSE | summer
2023-08-01 03:00 | 2023-08-01 04:00 | Summer | FALSE | summer
2023-08-01 04:00 | 2023-08-01 05:00 | Summer | FALSE | summer
2023-08-01 05:00 | 2023-08-01 06:00 | Summer | FALSE | summer
2023-08-01 06:00 | 2023-08-01 07:00 | Summer | FALSE | summer
2023-08-01 07:00 | 2023-08-01 08:00 | Summer | FALSE | summer
2023-08-01 08:00 | 2023-08-01 09:00 | Summer | FALSE | summer
2023-08-01 09:00 | 2023-08-01 10:00 | Summer | FALSE | summer
2023-08-01 10:00 | 2023-08-01 11:00 | Summer | FALSE | summer
2023-08-01 11:00 | 2023-08-01 12:00 | Summer | FALSE | summer
2023-08-01 12:00 | 2023-08-01 13:00 | Summer | FALSE | summer
2023-08-01 13:00 | 2023-08-01 14:00 | Summer | FALSE | summer
2023-08-01 14:00 | 2023-08-01 15:00 | Summer | FALSE | summer
2023-08-01 15:00 | 2023-08-01 16:00 | Summer | FALSE | summer
2023-08-01 16:00 | 2023-08-01 17:00 | Summer | TRUE | summer
2023-08-01 17:00 | 2023-08-01 18:00 | Summer | TRUE | summer
2023-08-01 18:00 | 2023-08-01 19:00 | Summer | TRUE | summer
2023-08-01 19:00 | 2023-08-01 20:00 | Summer | TRUE | summer
2023-08-01 20:00 | 2023-08-01 21:00 | Summer | TRUE | summer
2023-08-01 21:00 | 2023-08-01 22:00 | Summer | FALSE | summer
2023-08-01 22:00 | 2023-08-01 23:00 | Summer | FALSE | summer
2023-08-01 23:00 | 2023-08-02 | Summer | FALSE | summer
2023-08-02 | 2023-08-02 01:00 | Summer | FALSE | summer
2023-08-02 01:00 | 2023-08-02 02:00 | Summer | FALSE | summer
2023-08-02 02:00 | 2023-08-02 03:00 | Summer | FALSE | summer
2023-08-02 03:00 | 2023-08-02 04:00 | Summer | FALSE | summer
2023-08-02 04:00 | 2023-08-02 05:00 | Summer | FALSE | summer
2023-08-02 05:00 | 2023-08-02 06:00 | Summer | FALSE | summer
2023-08-02 06:00 | 2023-08-02 07:00 | Summer | FALSE | summer
2023-08-02 07:00 | 2023-08-02 08:00 | Summer | FALSE | summer
2023-08-02 08:00 | 2023-08-02 09:00 | Summer | FALSE | summer
2023-08-02 09:00 | 2023-08-02 10:00 | Summer | FALSE | summer
2023-08-02 10:00 | 2023-08-02 11:00 | Summer | FALSE | summer
2023-08-02 11:00 | 2023-08-02 12:00 | Summer | FALSE | summer
2023-08-02 12:00 | 2023-08-02 13:00 | Summer | FALSE | summer
2023-08-02 13:00 | 2023-08-02 14:00 | Summer | FALSE | summer
2023-08-02 14:00 | 2023-08-02 15:00 | Summer | FALSE | summer
2023-08-02 15:00 | 2023-08-02 16:00 | Summer | FALSE | summer
2023-08-02 16:00 | 2023-08-02 17:00 | Summer | TRUE | summer
2023-08-02 17:00 | 2023-08-02 18:00 | Summer | TRUE | summer
2023-08-02 18:00 | 2023-08-02 19:00 | Summer | TRUE | summer
2023-08-02 19:00 | 2023-08-02 20:00 | Summer | TRUE | summer
2023-08-02 20:00 | 2023-08-02 21:00 | Summer | TRUE | summer
2023-08-02 21:00 | 2023-08-02 22:00 | Summer | FALSE | summer
2023-08-02 22:00 | 2023-08-02 23:00 | Summer | FALSE | summer
2023-08-02 23:00 | 2023-08-03 | Summer | FALSE | summer
2023-08-03 | 2023-08-03 01:00 | Summer | FALSE | summer
2023-08-03 01:00 | 2023-08-03 02:00 | Summer | FALSE | summer
2023-08-03 02:00 | 2023-08-03 03:00 | Summer | FALSE | summer
2023-08-03 03:00 | 2023-08-03 04:00 | Summer | FALSE | summer
2023-08-03 04:00 | 2023-08-03 05:00 | Summer | FALSE | summer
2023-08-03 05:00 | 2023-08-03 06:00 | Summer | FALSE | summer
2023-08-03 06:00 | 2023-08-03 07:00 | Summer | FALSE | summer
2023-08-03 07:00 | 2023-08-03 08:00 | Summer | FALSE | summer
2023-08-03 08:00 | 2023-08-03 09:00 | Summer | FALSE | summer
2023-08-03 09:00 | 2023-08-03 10:00 | Summer | FALSE | summer
2023-08-03 10:00 | 2023-08-03 11:00 | Summer | FALSE | summer
2023-08-03 11:00 | 2023-08-03 12:00 | Summer | FALSE | summer
2023-08-03 12:00 | 2023-08-03 13:00 | Summer | FALSE | summer
2023-08-03 13:00 | 2023-08-03 14:00 | Summer | FALSE | summer
2023-08-03 14:00 | 2023-08-03 15:00 | Summer | FALSE | summer
2023-08-03 15:00 | 2023-08-03 16:00 | Summer | FALSE | summer
2023-08-03 16:00 | 2023-08-03 17:00 | Summer | TRUE | summer
2023-08-03 17:00 | 2023-08-03 18:00 | Summer | TRUE | summer
2023-08-03 18:00 | 2023-08-03 19:00 | Summer | TRUE | summer
2023-08-03 19:00 | 2023-08-03 20:00 | Summer | TRUE | summer
2023-08-03 20:00 | 2023-08-03 21:00 | Summer | TRUE | summer
2023-08-03 21:00 | 2023-08-03 22:00 | Summer | FALSE | summer
2023-08-03 22:00 | 2023-08-03 23:00 | Summer | FALSE | summer
2023-08-03 23:00 | 2023-08-04 | Summer | FALSE | summer
2023-08-04 | 2023-08-04 01:00 | Summer | FALSE | summer
2023-08-04 01:00 | 2023-08-04 02:00 | Summer | FALSE | summer
2023-08-04 02:00 | 2023-08-04 03:00 | Summer | FALSE | summer
2023-08-04 03:00 | 2023-08-04 04:00 | Summer | FALSE | summer
2023-08-04 04:00 | 2023-08-04 05:00 | Summer | FALSE | summer
2023-08-04 05:00 | 2023-08-04 06:00 | Summer | FALSE | summer
2023-08-04 06:00 | 2023-08-04 07:00 | Summer | FALSE | summer
2023-08-04 07:00 | 2023-08-04 08:00 | Summer | FALSE | summer
2023-08-04 08:00 | 2023-08-04 09:00 | Summer | FALSE | summer
2023-08-04 09:00 | 2023-08-04 10:00 | Summer | FALSE | summer
2023-08-04 10:00 | 2023-08-04 11:00 | Summer | FALSE | summer
2023-08-04 11:00 | 2023-08-04 12:00 | Summer | FALSE | summer
2023-08-04 12:00 | 2023-08-04 13:00 | Summer | FALSE | summer
2023-08-04 13:00 | 2023-08-04 14:00 | Summer | FALSE | summer
2023-08-04 14:00 | 2023-08-04 15:00 | Summer | FALSE | summer
2023-08-04 15:00 | 2023-08-04 16:00 | Summer | FALSE | summer
2023-08-04 16:00 | 2023-08-04 17:00 | Summer | TRUE | summer
2023-08-04 17:00 | 2023-08-04 18:00 | Summer | TRUE | summer
2023-08-04 18:00 | 2023-08-04 19:00 | Summer | TRUE | summer
2023-08-04 19:00 | 2023-08-04 20:00 | Summer | TRUE | summer
2023-08-04 20:00 | 2023-08-04 21:00 | Summer | TRUE | summer
2023-08-04 21:00 | 2023-08-04 22:00 | Summer | FALSE | summer
2023-08-04 22:00 | 2023-08-04 23:00 | Summer | FALSE | summer
2023-08-04 23:00 | 2023-08-05 | Summer | FALSE | summer
2023-08-05 | 2023-08-05 01:00 | Summer | FALSE | summer
2023-08-05 01:00 | 2023-08-05 02:00 | Summer | FALSE | summer
2023-08-05 02:00 | 2023-08-05 03:00 | Summer | FALSE | summer
2023-08-05 03:00 | 2023-08-05 04:00 | Summer | FALSE | summer
2023-08-05 04:00 | 2023-08-05 05:00 | Summer | FALSE | summer
2023-08-05 05:00 | 2023-08-05 06:00 | Summer | FALSE | summer
2023-08-05 06:00 | 2023-08-05 07:00 | Summer | FALSE | summer
2023-08-05 07:00 | 2023-08-05 08:00 | Summer | FALSE | summer
2023-08-05 08:00 | 2023-08-05 09:00 | Summer | FALSE | summer
2023-08-05 09:00 | 2023-08-05 10:00 | Summer | FALSE | summer
2023-08-05 10:00 | 2023-08-05 11:00 | Summer | FALSE | summer
2023-08-05 11:00 | 2023-08-05 12:00 | Summer | FALSE | summer
2023-08-05 12:00 | 2023-08-05 13:00 | Summer | FALSE | summer
2023-08-05 13:00 | 2023-08-05 14:00 | Summer | FALSE | summer
2023-08-05 14:00 | 2023-08-05 15:00 | Summer | FALSE | summer
2023-08-05 15:00 | 2023-08-05 16:00 | Summer | FALSE | summer
2023-08-05 16:00 | 2023-08-05 17:00 | Summer | TRUE | summer
2023-08-05 17:00 | 2023-08-05 18:00 | Summer | TRUE | summer
2023-08-05 18:00 | 2023-08-05 19:00 | Summer | TRUE | summer
2023-08-05 19:00 | 2023-08-05 20:00 | Summer | TRUE | summer
2023-08-05 20:00 | 2023-08-05 21:00 | Summer | TRUE | summer
2023-08-05 21:00 | 2023-08-05 22:00 | Summer | FALSE | summer
2023-08-05 22:00 | 2023-08-05 23:00 | Summer | FALSE | summer
2023-08-05 23:00 | 2023-08-06 | Summer | FALSE | summer
2023-08-06 | 2023-08-06 01:00 | Summer | FALSE | summer
2023-08-06 01:00 | 2023-08-06 02:00 | Summer | FALSE | summer
2023-08-06 02:00 | 2023-08-06 03:00 | Summer | FALSE | summer
2023-08-06 03:00 | 2023-08-06 04:00 | Summer | FALSE | summer
2023-08-06 04:00 | 2023-08-06 05:00 | Summer | FALSE | summer
2023-08-06 05:00 | 2023-08-06 06:00 | Summer | FALSE | summer
2023-08-06 06:00 | 2023-08-06 07:00 | Summer | FALSE | summer
2023-08-06 07:00 | 2023-08-06 08:00 | Summer | FALSE | summer
2023-08-06 08:00 | 2023-08-06 09:00 | Summer | FALSE | summer
2023-08-06 09:00 | 2023-08-06 10:00 | Summer | FALSE | summer
2023-08-06 10:00 | 2023-08-06 11:00 | Summer | FALSE | summer
2023-08-06 11:00 | 2023-08-06 12:00 | Summer | FALSE | summer
2023-08-06 12:00 | 2023-08-06 13:00 | Summer | FALSE | summer
2023-08-06 13:00 | 2023-08-06 14:00 | Summer | FALSE | summer
2023-08-06 14:00 | 2023-08-06 15:00 | Summer | FALSE | summer
2023-08-06 15:00 | 2023-08-06 16:00 | Summer | FALSE | summer
2023-08-06 16:00 | 2023-08-06 17:00 | Summer | TRUE | summer
2023-08-06 17:00 | 2023-08-06 18:00 | Summer | TRUE | summer
2023-08-06 18:00 | 2023-08-06 19:00 | Summer | TRUE | summer
2023-08-06 19:00 | 2023-08-06 20:00 | Summer | TRUE | summer
2023-08-06 20:00 | 2023-08-06 21:00 | Summer | TRUE | summer
2023-08-06 21:00 | 2023-08-06 22:00 | Summer | FALSE | summer
2023-08-06 22:00 | 2023-08-06 23:00 | Summer | FALSE | summer
2023-08-06 23:00 | 2023-08-07 | Summer | FALSE | summer
2023-08-07 | 2023-08-07 01:00 | Summer | FALSE | summer
2023-08-07 01:00 | 2023-08-07 02:00 | Summer | FALSE | summer
2023-08-07 02:00 | 2023-08-07 03:00 | Summer | FALSE | summer
2023-08-07 03:00 | 2023-08-07 04:00 | Summer | FALSE | summer
2023-08-07 04:00 | 2023-08-07 05:00 | Summer | FALSE | summer
2023-08-07 05:00 | 2023-08-07 06:00 | Summer | FALSE | summer
2023-08-07 06:00 | 2023-08-07 07:00 | Summer | FALSE | summer
2023-08-07 07:00 | 2023-08-07 08:00 | Summer | FALSE | summer
2023-08-07 08:00 | 2023-08-07 09:00 | Summer | FALSE | summer
2023-08-07 09:00 | 2023-08-07 10:00 | Summer | FALSE | summer
2023-08-07 10:00 | 2023-08-07 11:00 | Summer | FALSE | summer
2023-08-07 11:00 | 2023-08-07 12:00 | Summer | FALSE | summer
2023-08-07 12:00 | 2023-08-07 13:00 | Summer | FALSE | summer
2023-08-07 13:00 | 2023-08-07 14:00 | Summer | FALSE | summer
2023-08-07 14:00 | 2023-08-07 15:00 | Summer | FALSE | summer
2023-08-07 15:00 | 2023-08-07 16:00 | Summer | FALSE | summer
2023-08-07 16:00 | 2023-08-07 17:00 | Summer | TRUE | summer
2023-08-07 17:00 | 2023-08-07 18:00 | Summer | TRUE | summer
2023-08-07 18:00 | 2023-08-07 19:00 | Summer | TRUE | summer
2023-08-07 19:00 | 2023-08-07 20:00 | Summer | TRUE | summer
2023-08-07 20:00 | 2023-08-07 21:00 | Summer | TRUE | summer
2023-08-07 21:00 | 2023-08-07 22:00 | Summer | FALSE | summer
2023-08-07 22:00 | 2023-08-07 23:00 | Summer | FALSE | summer
2023-08-07 23:00 | 2023-08-08 | Summer | FALSE | summer
2023-08-08 | 2023-08-08 01:00 | Summer | FALSE | summer
2023-08-08 01:00 | 2023-08-08 02:00 | Summer | FALSE | summer
2023-08-08 02:00 | 2023-08-08 03:00 | Summer | FALSE | summer
2023-08-08 03:00 | 2023-08-08 04:00 | Summer | FALSE | summer
2023-08-08 04:00 | 2023-08-08 05:00 | Summer | FALSE | summer
2023-08-08 05:00 | 2023-08-08 06:00 | Summer | FALSE | summer
2023-08-08 06:00 | 2023-08-08 07:00 | Summer | FALSE | summer
2023-08-08 07:00 | 2023-08-08 08:00 | Summer | FALSE | summer
2023-08-08 08:00 | 2023-08-08 09:00 | Summer | FALSE | summer
2023-08-08 09:00 | 2023-08-08 10:00 | Summer | FALSE | summer
2023-08-08 10:00 | 2023-08-08 11:00 | Summer | FALSE | summer
2023-08-08 11:00 | 2023-08-08 12:00 | Summer | FALSE | summer
2023-08-08 12:00 | 2023-08-08 13:00 | Summer | FALSE | summer
2023-08-08 13:00 | 2023-08-08 14:00 | Summer | FALSE | summer
2023-08-08 14:00 | 2023-08-08 15:00 | Summer | FALSE | summer
2023-08-08 15:00 | 2023-08-08 16:00 | Summer | FALSE | summer
2023-08-08 16:00 | 2023-08-08 17:00 | Summer | TRUE | summer
2023-08-08 17:00 | 2023-08-08 18:00 | Summer | TRUE | summer
2023-08-08 18:00 | 2023-08-08 19:00 | Summer | TRUE | summer
2023-08-08 19:00 | 2023-08-08 20:00 | Summer | TRUE | summer
2023-08-08 20:00 | 2023-08-08 21:00 | Summer | TRUE | summer
2023-08-08 21:00 | 2023-08-08 22:00 | Summer | FALSE | summer
2023-08-08 22:00 | 2023-08-08 23:00 | Summer | FALSE | summer
2023-08-08 23:00 | 2023-08-09 | Summer | FALSE | summer
2023-08-09 | 2023-08-09 01:00 | Summer | FALSE | summer
2023-08-09 01:00 | 2023-08-09 02:00 | Summer | FALSE | summer
2023-08-09 02:00 | 2023-08-09 03:00 | Summer | FALSE | summer
2023-08-09 03:00 | 2023-08-09 04:00 | Summer | FALSE | summer
2023-08-09 04:00 | 2023-08-09 05:00 | Summer | FALSE | summer
2023-08-09 05:00 | 2023-08-09 06:00 | Summer | FALSE | summer
2023-08-09 06:00 | 2023-08-09 07:00 | Summer | FALSE | summer
2023-08-09 07:00 | 2023-08-09 08:00 | Summer | FALSE | summer
2023-08-09 08:00 | 2023-08-09 09:00 | Summer | FALSE | summer
2023-08-09 09:00 | 2023-08-09 10:00 | Summer | FALSE | summer
2023-08-09 10:00 | 2023-08-09 11:00 | Summer | FALSE | summer
2023-08-09 11:00 | 2023-08-09 12:00 | Summer | FALSE | summer
2023-08-09 12:00 | 2023-08-09 13:00 | Summer | FALSE | summer
2023-08-09 13:00 | 2023-08-09 14:00 | Summer | FALSE | summer
2023-08-09 14:00 | 2023-08-09 15:00 | Summer | FALSE | summer
2023-08-09 15:00 | 2023-08-09 16:00 | Summer | FALSE | summer
2023-08-09 16:00 | 2023-08-09 17:00 | Summer | TRUE | summer
2023-08-09 17:00 | 2023-08-09 18:00 | Summer | TRUE | summer
2023-08-09 18:00 | 2023-08-09 19:00 | Summer | TRUE | summer
2023-08-09 19:00 | 2023-08-09 20:00 | Summer | TRUE | summer
2023-08-09 20:00 | 2023-08-09 21:00 | Summer | TRUE | summer
2023-08-09 21:00 | 2023-08-09 22:00 | Summer | FALSE | summer
2023-08-09 22:00 | 2023-08-09 23:00 | Summer | FALSE | summer
2023-08-09 23:00 | 2023-08-10 | Summer | FALSE | summer
2023-08-10 | 2023-08-10 01:00 | Summer | FALSE | summer
2023-08-10 01:00 | 2023-08-10 02:00 | Summer | FALSE | summer
2023-08-10 02:00 | 2023-08-10 03:00 | Summer | FALSE | summer
2023-08-10 03:00 | 2023-08-10 04:00 | Summer | FALSE | summer
2023-08-10 04:00 | 2023-08-10 05:00 | Summer | FALSE | summer
2023-08-10 05:00 | 2023-08-10 06:00 | Summer | FALSE | summer
2023-08-10 06:00 | 2023-08-10 07:00 | Summer | FALSE | summer
2023-08-10 07:00 | 2023-08-10 08:00 | Summer | FALSE | summer
2023-08-10 08:00 | 2023-08-10 09:00 | Summer | FALSE | summer
2023-08-10 09:00 | 2023-08-10 10:00 | Summer | FALSE | summer
2023-08-10 10:00 | 2023-08-10 11:00 | Summer | FALSE | summer
2023-08-10 11:00 | 2023-08-10 12:00 | Summer | FALSE | summer
2023-08-10 12:00 | 2023-08-10 13:00 | Summer | FALSE | summer
2023-08-10 13:00 | 2023-08-10 14:00 | Summer | FALSE | summer
2023-08-10 14:00 | 2023-08-10 15:00 | Summer | FALSE | summer
2023-08-10 15:00 | 2023-08-10 16:00 | Summer | FALSE | summer
2023-08-10 16:00 | 2023-08-10 17:00 | Summer | TRUE | summer
2023-08-10 17:00 | 2023-08-10 18:00 | Summer | TRUE | summer
2023-08-10 18:00 | 2023-08-10 19:00 | Summer | TRUE | summer
2023-08-10 19:00 | 2023-08-10 20:00 | Summer | TRUE | summer
2023-08-10 20:00 | 2023-08-10 21:00 | Summer | TRUE | summer
2023-08-10 21:00 | 2023-08-10 22:00 | Summer | FALSE | summer
2023-08-10 22:00 | 2023-08-10 23:00 | Summer | FALSE | summer
2023-08-10 23:00 | 2023-08-11 | Summer | FALSE | summer
2023-08-11 | 2023-08-11 01:00 | Summer | FALSE | summer
2023-08-11 01:00 | 2023-08-11 02:00 | Summer | FALSE | summer
2023-08-11 02:00 | 2023-08-11 03:00 | Summer | FALSE | summer
2023-08-11 03:00 | 2023-08-11 04:00 | Summer | FALSE | summer
2023-08-11 04:00 | 2023-08-11 05:00 | Summer | FALSE | summer
2023-08-11 05:00 | 2023-08-11 06:00 | Summer | FALSE | summer
2023-08-11 06:00 | 2023-08-11 07:00 | Summer | FALSE | summer
2023-08-11 07:00 | 2023-08-11 08:00 | Summer | FALSE | summer
2023-08-11 08:00 | 2023-08-11 09:00 | Summer | FALSE | summer
2023-08-11 09:00 | 2023-08-11 10:00 | Summer | FALSE | summer
2023-08-11 10:00 | 2023-08-11 11:00 | Summer | FALSE | summer
2023-08-11 11:00 | 2023-08-11 12:00 | Summer | FALSE | summer
2023-08-11 12:00 | 2023-08-11 13:00 | Summer | FALSE | summer
2023-08-11 13:00 | 2023-08-11 14:00 | Summer | FALSE | summer
2023-08-11 14:00 | 2023-08-11 15:00 | Summer | FALSE | summer
2023-08-11 15:00 | 2023-08-11 16:00 | Summer | FALSE | summer
2023-08-11 16:00 | 2023-08-11 17:00 | Summer | TRUE | summer
2023-08-11 17:00 | 2023-08-11 18:00 | Summer | TRUE | summer
2023-08-11 18:00 | 2023-08-11 19:00 | Summer | TRUE | summer
2023-08-11 19:00 | 2023-08-11 20:00 | Summer | TRUE | summer
2023-08-11 20:00 | 2023-08-11 21:00 | Summer | TRUE | summer
2023-08-11 21:00 | 2023-08-11 22:00 | Summer | FALSE | summer
2023-08-11 22:00 | 2023-08-11 23:00 | Summer | FALSE | summer
2023-08-11 23:00 | 2023-08-12 | Summer | FALSE | summer
2023-08-12 | 2023-08-12 01:00 | Summer | FALSE | summer
2023-08-12 01:00 | 2023-08-12 02:00 | Summer | FALSE | summer
2023-08-12 02:00 | 2023-08-12 03:00 | Summer | FALSE | summer
2023-08-12 03:00 | 2023-08-12 04:00 | Summer | FALSE | summer
2023-08-12 04:00 | 2023-08-12 05:00 | Summer | FALSE | summer
2023-08-12 05:00 | 2023-08-12 06:00 | Summer | FALSE | summer
2023-08-12 06:00 | 2023-08-12 07:00 | Summer | FALSE | summer
2023-08-12 07:00 | 2023-08-12 08:00 | Summer | FALSE | summer
2023-08-12 08:00 | 2023-08-12 09:00 | Summer | FALSE | summer
2023-08-12 09:00 | 2023-08-12 10:00 | Summer | FALSE | summer
2023-08-12 10:00 | 2023-08-12 11:00 | Summer | FALSE | summer
2023-08-12 11:00 | 2023-08-12 12:00 | Summer | FALSE | summer
2023-08-12 12:00 | 2023-08-12 13:00 | Summer | FALSE | summer
2023-08-12 13:00 | 2023-08-12 14:00 | Summer | FALSE | summer
2023-08-12 14:00 | 2023-08-12 15:00 | Summer | FALSE | summer
2023-08-12 15:00 | 2023-08-12 16:00 | Summer | FALSE | summer
2023-08-12 16:00 | 2023-08-12 17:00 | Summer | TRUE | summer
2023-08-12 17:00 | 2023-08-12 18:00 | Summer | TRUE | summer
2023-08-12 18:00 | 2023-08-12 19:00 | Summer | TRUE | summer
2023-08-12 19:00 | 2023-08-12 20:00 | Summer | TRUE | summer
2023-08-12 20:00 | 2023-08-12 21:00 | Summer | TRUE | summer
2023-08-12 21:00 | 2023-08-12 22:00 | Summer | FALSE | summer
2023-08-12 22:00 | 2023-08-12 23:00 | Summer | FALSE | summer
2023-08-12 23:00 | 2023-08-13 | Summer | FALSE | summer
2023-08-13 | 2023-08-13 01:00 | Summer | FALSE | summer
2023-08-13 01:00 | 2023-08-13 02:00 | Summer | FALSE | summer
2023-08-13 02:00 | 2023-08-13 03:00 | Summer | FALSE | summer
2023-08-13 03:00 | 2023-08-13 04:00 | Summer | FALSE | summer
2023-08-13 04:00 | 2023-08-13 05:00 | Summer | FALSE | summer
2023-08-13 05:00 | 2023-08-13 06:00 | Summer | FALSE | summer
2023-08-13 06:00 | 2023-08-13 07:00 | Summer | FALSE | summer
2023-08-13 07:00 | 2023-08-13 08:00 | Summer | FALSE | summer
2023-08-13 08:00 | 2023-08-13 09:00 | Summer | FALSE | summer
2023-08-13 09:00 | 2023-08-13 10:00 | Summer | FALSE | summer
2023-08-13 10:00 | 2023-08-13 11:00 | Summer | FALSE | summer
2023-08-13 11:00 | 2023-08-13 12:00 | Summer | FALSE | summer
2023-08-13 12:00 | 2023-08-13 13:00 | Summer | FALSE | summer
2023-08-13 13:00 | 2023-08-13 14:00 | Summer | FALSE | summer
2023-08-13 14:00 | 2023-08-13 15:00 | Summer | FALSE | summer
2023-08-13 15:00 | 2023-08-13 16:00 | Summer | FALSE | summer
2023-08-13 16:00 | 2023-08-13 17:00 | Summer | TRUE | summer
2023-08-13 17:00 | 2023-08-13 18:00 | Summer | TRUE | summer
2023-08-13 18:00 | 2023-08-13 19:00 | Summer | TRUE | summer
2023-08-13 19:00 | 2023-08-13 20:00 | Summer | TRUE | summer
2023-08-13 20:00 | 2023-08-13 21:00 | Summer | TRUE | summer
2023-08-13 21:00 | 2023-08-13 22:00 | Summer | FALSE | summer
2023-08-13 22:00 | 2023-08-13 23:00 | Summer | FALSE | summer
2023-08-13 23:00 | 2023-08-14 | Summer | FALSE | summer
2023-08-14 | 2023-08-14 01:00 | Summer | FALSE | summer
2023-08-14 01:00 | 2023-08-14 02:00 | Summer | FALSE | summer
2023-08-14 02:00 | 2023-08-14 03:00 | Summer | FALSE | summer
2023-08-14 03:00 | 2023-08-14 04:00 | Summer | FALSE | summer
2023-08-14 04:00 | 2023-08-14 05:00 | Summer | FALSE | summer
2023-08-14 05:00 | 2023-08-14 06:00 | Summer | FALSE | summer
2023-08-14 06:00 | 2023-08-14 07:00 | Summer | FALSE | summer
2023-08-14 07:00 | 2023-08-14 08:00 | Summer | FALSE | summer
2023-08-14 08:00 | 2023-08-14 09:00 | Summer | FALSE | summer
2023-08-14 09:00 | 2023-08-14 10:00 | Summer | FALSE | summer
2023-08-14 10:00 | 2023-08-14 11:00 | Summer | FALSE | summer
2023-08-14 11:00 | 2023-08-14 12:00 | Summer | FALSE | summer
2023-08-14 12:00 | 2023-08-14 13:00 | Summer | FALSE | summer
2023-08-14 13:00 | 2023-08-14 14:00 | Summer | FALSE | summer
2023-08-14 14:00 | 2023-08-14 15:00 | Summer | FALSE | summer
2023-08-14 15:00 | 2023-08-14 16:00 | Summer | FALSE | summer
2023-08-14 16:00 | 2023-08-14 17:00 | Summer | TRUE | summer
2023-08-14 17:00 | 2023-08-14 18:00 | Summer | TRUE | summer
2023-08-14 18:00 | 2023-08-14 19:00 | Summer | TRUE | summer
2023-08-14 19:00 | 2023-08-14 20:00 | Summer | TRUE | summer
2023-08-14 20:00 | 2023-08-14 21:00 | Summer | TRUE | summer
2023-08-14 21:00 | 2023-08-14 22:00 | Summer | FALSE | summer
2023-08-14 22:00 | 2023-08-14 23:00 | Summer | FALSE | summer
2023-08-14 23:00 | 2023-08-15 | Summer | FALSE | summer
2023-08-15 | 2023-08-15 01:00 | Summer | FALSE | summer
2023-08-15 01:00 | 2023-08-15 02:00 | Summer | FALSE | summer
2023-08-15 02:00 | 2023-08-15 03:00 | Summer | FALSE | summer
2023-08-15 03:00 | 2023-08-15 04:00 | Summer | FALSE | summer
2023-08-15 04:00 | 2023-08-15 05:00 | Summer | FALSE | summer
2023-08-15 05:00 | 2023-08-15 06:00 | Summer | FALSE | summer
2023-08-15 06:00 | 2023-08-15 07:00 | Summer | FALSE | summer
2023-08-15 07:00 | 2023-08-15 08:00 | Summer | FALSE | summer
2023-08-15 08:00 | 2023-08-15 09:00 | Summer | FALSE | summer
2023-08-15 09:00 | 2023-08-15 10:00 | Summer | FALSE | summer
2023-08-15 10:00 | 2023-08-15 11:00 | Summer | FALSE | summer
2023-08-15 11:00 | 2023-08-15 12:00 | Summer | FALSE | summer
2023-08-15 12:00 | 2023-08-15 13:00 | Summer | FALSE | summer
2023-08-15 13:00 | 2023-08-15 14:00 | Summer | FALSE | summer
2023-08-15 14:00 | 2023-08-15 15:00 | Summer | FALSE | summer
2023-08-15 15:00 | 2023-08-15 16:00 | Summer | FALSE | summer
2023-08-15 16:00 | 2023-08-15 17:00 | Summer | TRUE | summer
2023-08-15 17:00 | 2023-08-15 18:00 | Summer | TRUE | summer
2023-08-15 18:00 | 2023-08-15 19:00 | Summer | TRUE | summer
2023-08-15 19:00 | 2023-08-15 20:00 | Summer | TRUE | summer
2023-08-15 20:00 | 2023-08-15 21:00 | Summer | TRUE | summer
2023-08-15 21:00 | 2023-08-15 22:00 | Summer | FALSE | summer
2023-08-15 22:00 | 2023-08-15 23:00 | Summer | FALSE | summer
2023-08-15 23:00 | 2023-08-16 | Summer | FALSE | summer
2023-08-16 | 2023-08-16 01:00 | Summer | FALSE | summer
2023-08-16 01:00 | 2023-08-16 02:00 | Summer | FALSE | summer
2023-08-16 02:00 | 2023-08-16 03:00 | Summer | FALSE | summer
2023-08-16 03:00 | 2023-08-16 04:00 | Summer | FALSE | summer
2023-08-16 04:00 | 2023-08-16 05:00 | Summer | FALSE | summer
2023-08-16 05:00 | 2023-08-16 06:00 | Summer | FALSE | summer
2023-08-16 06:00 | 2023-08-16 07:00 | Summer | FALSE | summer
2023-08-16 07:00 | 2023-08-16 08:00 | Summer | FALSE | summer
2023-08-16 08:00 | 2023-08-16 09:00 | Summer | FALSE | summer
2023-08-16 09:00 | 2023-08-16 10:00 | Summer | FALSE | summer
2023-08-16 10:00 | 2023-08-16 11:00 | Summer | FALSE | summer
2023-08-16 11:00 | 2023-08-16 12:00 | Summer | FALSE | summer
2023-08-16 12:00 | 2023-08-16 13:00 | Summer | FALSE | summer
2023-08-16 13:00 | 2023-08-16 14:00 | Summer | FALSE | summer
2023-08-16 14:00 | 2023-08-16 15:00 | Summer | FALSE | summer
2023-08-16 15:00 | 2023-08-16 16:00 | Summer | FALSE | summer
2023-08-16 16:00 | 2023-08-16 17:00 | Summer | TRUE | summer
2023-08-16 17:00 | 2023-08-16 18:00 | Summer | TRUE | summer
2023-08-16 18:00 | 2023-08-16 19:00 | Summer | TRUE | summer
2023-08-16 19:00 | 2023-08-16 20:00 | Summer | TRUE | summer
2023-08-16 20:00 | 2023-08-16 21:00 | Summer | TRUE | summer
2023-08-16 21:00 | 2023-08-16 22:00 | Summer | FALSE | summer
2023-08-16 22:00 | 2023-08-16 23:00 | Summer | FALSE | summer
2023-08-16 23:00 | 2023-08-17 | Summer | FALSE | summer
2023-08-17 | 2023-08-17 01:00 | Summer | FALSE | summer
2023-08-17 01:00 | 2023-08-17 02:00 | Summer | FALSE | summer
2023-08-17 02:00 | 2023-08-17 03:00 | Summer | FALSE | summer
2023-08-17 03:00 | 2023-08-17 04:00 | Summer | FALSE | summer
2023-08-17 04:00 | 2023-08-17 05:00 | Summer | FALSE | summer
2023-08-17 05:00 | 2023-08-17 06:00 | Summer | FALSE | summer
2023-08-17 06:00 | 2023-08-17 07:00 | Summer | FALSE | summer
2023-08-17 07:00 | 2023-08-17 08:00 | Summer | FALSE | summer
2023-08-17 08:00 | 2023-08-17 09:00 | Summer | FALSE | summer
2023-08-17 09:00 | 2023-08-17 10:00 | Summer | FALSE | summer
2023-08-17 10:00 | 2023-08-17 11:00 | Summer | FALSE | summer
2023-08-17 11:00 | 2023-08-17 12:00 | Summer | FALSE | summer
2023-08-17 12:00 | 2023-08-17 13:00 | Summer | FALSE | summer
2023-08-17 13:00 | 2023-08-17 14:00 | Summer | FALSE | summer
2023-08-17 14:00 | 2023-08-17 15:00 | Summer | FALSE | summer
2023-08-17 15:00 | 2023-08-17 16:00 | Summer | FALSE | summer
2023-08-17 16:00 | 2023-08-17 17:00 | Summer | TRUE | summer
2023-08-17 17:00 | 2023-08-17 18:00 | Summer | TRUE | summer
2023-08-17 18:00 | 2023-08-17 19:00 | Summer | TRUE | summer
2023-08-17 19:00 | 2023-08-17 20:00 | Summer | TRUE | summer
2023-08-17 20:00 | 2023-08-17 21:00 | Summer | TRUE | summer
2023-08-17 21:00 | 2023-08-17 22:00 | Summer | FALSE | summer
2023-08-17 22:00 | 2023-08-17 23:00 | Summer | FALSE | summer
2023-08-17 23:00 | 2023-08-18 | Summer | FALSE | summer
2023-08-18 | 2023-08-18 01:00 | Summer | FALSE | summer
2023-08-18 01:00 | 2023-08-18 02:00 | Summer | FALSE | summer
2023-08-18 02:00 | 2023-08-18 03:00 | Summer | FALSE | summer
2023-08-18 03:00 | 2023-08-18 04:00 | Summer | FALSE | summer
2023-08-18 04:00 | 2023-08-18 05:00 | Summer | FALSE | summer
2023-08-18 05:00 | 2023-08-18 06:00 | Summer | FALSE | summer
2023-08-18 06:00 | 2023-08-18 07:00 | Summer | FALSE | summer
2023-08-18 07:00 | 2023-08-18 08:00 | Summer | FALSE | summer
2023-08-18 08:00 | 2023-08-18 09:00 | Summer | FALSE | summer
2023-08-18 09:00 | 2023-08-18 10:00 | Summer | FALSE | summer
2023-08-18 10:00 | 2023-08-18 11:00 | Summer | FALSE | summer
2023-08-18 11:00 | 2023-08-18 12:00 | Summer | FALSE | summer
2023-08-18 12:00 | 2023-08-18 13:00 | Summer | FALSE | summer
2023-08-18 13:00 | 2023-08-18 14:00 | Summer | FALSE | summer
2023-08-18 14:00 | 2023-08-18 15:00 | Summer | FALSE | summer
2023-08-18 15:00 | 2023-08-18 16:00 | Summer | FALSE | summer
2023-08-18 16:00 | 2023-08-18 17:00 | Summer | TRUE | summer
2023-08-18 17:00 | 2023-08-18 18:00 | Summer | TRUE | summer
2023-08-18 18:00 | 2023-08-18 19:00 | Summer | TRUE | summer
2023-08-18 19:00 | 2023-08-18 20:00 | Summer | TRUE | summer
2023-08-18 20:00 | 2023-08-18 21:00 | Summer | TRUE | summer
2023-08-18 21:00 | 2023-08-18 22:00 | Summer | FALSE | summer
2023-08-18 22:00 | 2023-08-18 23:00 | Summer | FALSE | summer
2023-08-18 23:00 | 2023-08-19 | Summer | FALSE | summer
2023-08-19 | 2023-08-19 01:00 | Summer | FALSE | summer
2023-08-19 01:00 | 2023-08-19 02:00 | Summer | FALSE | summer
2023-08-19 02:00 | 2023-08-19 03:00 | Summer | FALSE | summer
2023-08-19 03:00 | 2023-08-19 04:00 | Summer | FALSE | summer
2023-08-19 04:00 | 2023-08-19 05:00 | Summer | FALSE | summer
2023-08-19 05:00 | 2023-08-19 06:00 | Summer | FALSE | summer
2023-08-19 06:00 | 2023-08-19 07:00 | Summer | FALSE | summer
2023-08-19 07:00 | 2023-08-19 08:00 | Summer | FALSE | summer
2023-08-19 08:00 | 2023-08-19 09:00 | Summer | FALSE | summer
2023-08-19 09:00 | 2023-08-19 10:00 | Summer | FALSE | summer
2023-08-19 10:00 | 2023-08-19 11:00 | Summer | FALSE | summer
2023-08-19 11:00 | 2023-08-19 12:00 | Summer | FALSE | summer
2023-08-19 12:00 | 2023-08-19 13:00 | Summer | FALSE | summer
2023-08-19 13:00 | 2023-08-19 14:00 | Summer | FALSE | summer
2023-08-19 14:00 | 2023-08-19 15:00 | Summer | FALSE | summer
2023-08-19 15:00 | 2023-08-19 16:00 | Summer | FALSE | summer
2023-08-19 16:00 | 2023-08-19 17:00 | Summer | TRUE | summer
2023-08-19 17:00 | 2023-08-19 18:00 | Summer | TRUE | summer
2023-08-19 18:00 | 2023-08-19 19:00 | Summer | TRUE | summer
2023-08-19 19:00 | 2023-08-19 20:00 | Summer | TRUE | summer
2023-08-19 20:00 | 2023-08-19 21:00 | Summer | TRUE | summer
2023-08-19 21:00 | 2023-08-19 22:00 | Summer | FALSE | summer
2023-08-19 22:00 | 2023-08-19 23:00 | Summer | FALSE | summer
2023-08-19 23:00 | 2023-08-20 | Summer | FALSE | summer
2023-08-20 | 2023-08-20 01:00 | Summer | FALSE | summer
2023-08-20 01:00 | 2023-08-20 02:00 | Summer | FALSE | summer
2023-08-20 02:00 | 2023-08-20 03:00 | Summer | FALSE | summer
2023-08-20 03:00 | 2023-08-20 04:00 | Summer | FALSE | summer
2023-08-20 04:00 | 2023-08-20 05:00 | Summer | FALSE | summer
2023-08-20 05:00 | 2023-08-20 06:00 | Summer | FALSE | summer
2023-08-20 06:00 | 2023-08-20 07:00 | Summer | FALSE | summer
2023-08-20 07:00 | 2023-08-20 08:00 | Summer | FALSE | summer
2023-08-20 08:00 | 2023-08-20 09:00 | Summer | FALSE | summer
2023-08-20 09:00 | 2023-08-20 10:00 | Summer | FALSE | summer
2023-08-20 10:00 | 2023-08-20 11:00 | Summer | FALSE | summer
2023-08-20 11:00 | 2023-08-20 12:00 | Summer | FALSE | summer
2023-08-20 12:00 | 2023-08-20 13:00 | Summer | FALSE | summer
2023-08-20 13:00 | 2023-08-20 14:00 | Summer | FALSE | summer
2023-08-20 14:00 | 2023-08-20 15:00 | Summer | FALSE | summer
2023-08-20 15:00 | 2023-08-20 16:00 | Summer | FALSE | summer
2023-08-20 16:00 | 2023-08-20 17:00 | Summer | TRUE | summer
2023-08-20 17:00 | 2023-08-20 18:00 | Summer | TRUE | summer
2023-08-20 18:00 | 2023-08-20 19:00 | Summer | TRUE | summer
2023-08-20 19:00 | 2023-08-20 20:00 | Summer | TRUE | summer
2023-08-20 20:00 | 2023-08-20 21:00 | Summer | TRUE | summer
2023-08-20 21:00 | 2023-08-20 22:00 | Summer | FALSE | summer
2023-08-20 22:00 | 2023-08-20 23:00 | Summer | FALSE | summer
2023-08-20 23:00 | 2023-08-21 | Summer | FALSE | summer
2023-08-21 | 2023-08-21 01:00 | Summer | FALSE | summer
2023-08-21 01:00 | 2023-08-21 02:00 | Summer | FALSE | summer
2023-08-21 02:00 | 2023-08-21 03:00 | Summer | FALSE | summer
2023-08-21 03:00 | 2023-08-21 04:00 | Summer | FALSE | summer
2023-08-21 04:00 | 2023-08-21 05:00 | Summer | FALSE | summer
2023-08-21 05:00 | 2023-08-21 06:00 | Summer | FALSE | summer
2023-08-21 06:00 | 2023-08-21 07:00 | Summer | FALSE | summer
2023-08-21 07:00 | 2023-08-21 08:00 | Summer | FALSE | summer
2023-08-21 08:00 | 2023-08-21 09:00 | Summer | FALSE | summer
2023-08-21 09:00 | 2023-08-21 10:00 | Summer | FALSE | summer
2023-08-21 10:00 | 2023-08-21 11:00 | Summer | FALSE | summer
2023-08-21 11:00 | 2023-08-21 12:00 | Summer | FALSE | summer
2023-08-21 12:00 | 2023-08-21 13:00 | Summer | FALSE | summer
2023-08-21 13:00 | 2023-08-21 14:00 | Summer | FALSE | summer
2023-08-21 14:00 | 2023-08-21 15:00 | Summer | FALSE | summer
2023-08-21 15:00 | 2023-08-21 16:00 | Summer | FALSE | summer
2023-08-21 16:00 | 2023-08-21 17:00 | Summer | TRUE | summer
2023-08-21 17:00 | 2023-08-21 18:00 | Summer | TRUE | summer
2023-08-21 18:00 | 2023-08-21 19:00 | Summer | TRUE | summer
2023-08-21 19:00 | 2023-08-21 20:00 | Summer | TRUE | summer
2023-08-21 20:00 | 2023-08-21 21:00 | Summer | TRUE | summer
2023-08-21 21:00 | 2023-08-21 22:00 | Summer | FALSE | summer
2023-08-21 22:00 | 2023-08-21 23:00 | Summer | FALSE | summer
2023-08-21 23:00 | 2023-08-22 | Summer | FALSE | summer
2023-08-22 | 2023-08-22 01:00 | Summer | FALSE | summer
2023-08-22 01:00 | 2023-08-22 02:00 | Summer | FALSE | summer
2023-08-22 02:00 | 2023-08-22 03:00 | Summer | FALSE | summer
2023-08-22 03:00 | 2023-08-22 04:00 | Summer | FALSE | summer
2023-08-22 04:00 | 2023-08-22 05:00 | Summer | FALSE | summer
2023-08-22 05:00 | 2023-08-22 06:00 | Summer | FALSE | summer
2023-08-22 06:00 | 2023-08-22 07:00 | Summer | FALSE | summer
2023-08-22 07:00 | 2023-08-22 08:00 | Summer | FALSE | summer
2023-08-22 08:00 | 2023-08-22 09:00 | Summer | FALSE | summer
2023-08-22 09:00 | 2023-08-22 10:00 | Summer | FALSE | summer
2023-08-22 10:00 | 2023-08-22 11:00 | Summer | FALSE | summer
2023-08-22 11:00 | 2023-08-22 12:00 | Summer | FALSE | summer
2023-08-22 12:00 | 2023-08-22 13:00 | Summer | FALSE | summer
2023-08-22 13:00 | 2023-08-22 14:00 | Summer | FALSE | summer
2023-08-22 14:00 | 2023-08-22 15:00 | Summer | FALSE | summer
2023-08-22 15:00 | 2023-08-22 16:00 | Summer | FALSE | summer
2023-08-22 16:00 | 2023-08-22 17:00 | Summer | TRUE | summer
2023-08-22 17:00 | 2023-08-22 18:00 | Summer | TRUE | summer
2023-08-22 18:00 | 2023-08-22 19:00 | Summer | TRUE | summer
2023-08-22 19:00 | 2023-08-22 20:00 | Summer | TRUE | summer
2023-08-22 20:00 | 2023-08-22 21:00 | Summer | TRUE | summer
2023-08-22 21:00 | 2023-08-22 22:00 | Summer | FALSE | summer
2023-08-22 22:00 | 2023-08-22 23:00 | Summer | FALSE | summer
2023-08-22 23:00 | 2023-08-23 | Summer | FALSE | summer
2023-08-23 | 2023-08-23 01:00 | Summer | FALSE | summer
2023-08-23 01:00 | 2023-08-23 02:00 | Summer | FALSE | summer
2023-08-23 02:00 | 2023-08-23 03:00 | Summer | FALSE | summer
2023-08-23 03:00 | 2023-08-23 04:00 | Summer | FALSE | summer
2023-08-23 04:00 | 2023-08-23 05:00 | Summer | FALSE | summer
2023-08-23 05:00 | 2023-08-23 06:00 | Summer | FALSE | summer
2023-08-23 06:00 | 2023-08-23 07:00 | Summer | FALSE | summer
2023-08-23 07:00 | 2023-08-23 08:00 | Summer | FALSE | summer
2023-08-23 08:00 | 2023-08-23 09:00 | Summer | FALSE | summer
2023-08-23 09:00 | 2023-08-23 10:00 | Summer | FALSE | summer
2023-08-23 10:00 | 2023-08-23 11:00 | Summer | FALSE | summer
2023-08-23 11:00 | 2023-08-23 12:00 | Summer | FALSE | summer
2023-08-23 12:00 | 2023-08-23 13:00 | Summer | FALSE | summer
2023-08-23 13:00 | 2023-08-23 14:00 | Summer | FALSE | summer
2023-08-23 14:00 | 2023-08-23 15:00 | Summer | FALSE | summer
2023-08-23 15:00 | 2023-08-23 16:00 | Summer | FALSE | summer
2023-08-23 16:00 | 2023-08-23 17:00 | Summer | TRUE | summer
2023-08-23 17:00 | 2023-08-23 18:00 | Summer | TRUE | summer
2023-08-23 18:00 | 2023-08-23 19:00 | Summer | TRUE | summer
2023-08-23 19:00 | 2023-08-23 20:00 | Summer | TRUE | summer
2023-08-23 20:00 | 2023-08-23 21:00 | Summer | TRUE | summer
2023-08-23 21:00 | 2023-08-23 22:00 | Summer | FALSE | summer
2023-08-23 22:00 | 2023-08-23 23:00 | Summer | FALSE | summer
2023-08-23 23:00 | 2023-08-24 | Summer | FALSE | summer
2023-08-24 | 2023-08-24 01:00 | Summer | FALSE | summer
2023-08-24 01:00 | 2023-08-24 02:00 | Summer | FALSE | summer
2023-08-24 02:00 | 2023-08-24 03:00 | Summer | FALSE | summer
2023-08-24 03:00 | 2023-08-24 04:00 | Summer | FALSE | summer
2023-08-24 04:00 | 2023-08-24 05:00 | Summer | FALSE | summer
2023-08-24 05:00 | 2023-08-24 06:00 | Summer | FALSE | summer
2023-08-24 06:00 | 2023-08-24 07:00 | Summer | FALSE | summer
2023-08-24 07:00 | 2023-08-24 08:00 | Summer | FALSE | summer
2023-08-24 08:00 | 2023-08-24 09:00 | Summer | FALSE | summer
2023-08-24 09:00 | 2023-08-24 10:00 | Summer | FALSE | summer
2023-08-24 10:00 | 2023-08-24 11:00 | Summer | FALSE | summer
2023-08-24 11:00 | 2023-08-24 12:00 | Summer | FALSE | summer
2023-08-24 12:00 | 2023-08-24 13:00 | Summer | FALSE | summer
2023-08-24 13:00 | 2023-08-24 14:00 | Summer | FALSE | summer
2023-08-24 14:00 | 2023-08-24 15:00 | Summer | FALSE | summer
2023-08-24 15:00 | 2023-08-24 16:00 | Summer | FALSE | summer
2023-08-24 16:00 | 2023-08-24 17:00 | Summer | TRUE | summer
2023-08-24 17:00 | 2023-08-24 18:00 | Summer | TRUE | summer
2023-08-24 18:00 | 2023-08-24 19:00 | Summer | TRUE | summer
2023-08-24 19:00 | 2023-08-24 20:00 | Summer | TRUE | summer
2023-08-24 20:00 | 2023-08-24 21:00 | Summer | TRUE | summer
2023-08-24 21:00 | 2023-08-24 22:00 | Summer | FALSE | summer
2023-08-24 22:00 | 2023-08-24 23:00 | Summer | FALSE | summer
2023-08-24 23:00 | 2023-08-25 | Summer | FALSE | summer
2023-08-25 | 2023-08-25 01:00 | Summer | FALSE | summer
2023-08-25 01:00 | 2023-08-25 02:00 | Summer | FALSE | summer
2023-08-25 02:00 | 2023-08-25 03:00 | Summer | FALSE | summer
2023-08-25 03:00 | 2023-08-25 04:00 | Summer | FALSE | summer
2023-08-25 04:00 | 2023-08-25 05:00 | Summer | FALSE | summer
2023-08-25 05:00 | 2023-08-25 06:00 | Summer | FALSE | summer
2023-08-25 06:00 | 2023-08-25 07:00 | Summer | FALSE | summer
2023-08-25 07:00 | 2023-08-25 08:00 | Summer | FALSE | summer
2023-08-25 08:00 | 2023-08-25 09:00 | Summer | FALSE | summer
2023-08-25 09:00 | 2023-08-25 10:00 | Summer | FALSE | summer
2023-08-25 10:00 | 2023-08-25 11:00 | Summer | FALSE | summer
2023-08-25 11:00 | 2023-08-25 12:00 | Summer | FALSE | summer
2023-08-25 12:00 | 2023-08-25 13:00 | Summer | FALSE | summer
2023-08-25 13:00 | 2023-08-25 14:00 | Summer | FALSE | summer
2023-08-25 14:00 | 2023-08-25 15:00 | Summer | FALSE | summer
2023-08-25 15:00 | 2023-08-25 16:00 | Summer | FALSE | summer
2023-08-25 16:00 | 2023-08-25 17:00 | Summer | TRUE | summer
2023-08-25 17:00 | 2023-08-25 18:00 | Summer | TRUE | summer
2023-08-25 18:00 | 2023-08-25 19:00 | Summer | TRUE | summer
2023-08-25 19:00 | 2023-08-25 20:00 | Summer | TRUE | summer
2023-08-25 20:00 | 2023-08-25 21:00 | Summer | TRUE | summer
2023-08-25 21:00 | 2023-08-25 22:00 | Summer | FALSE | summer
2023-08-25 22:00 | 2023-08-25 23:00 | Summer | FALSE | summer
2023-08-25 23:00 | 2023-08-26 | Summer | FALSE | summer
2023-08-26 | 2023-08-26 01:00 | Summer | FALSE | summer
2023-08-26 01:00 | 2023-08-26 02:00 | Summer | FALSE | summer
2023-08-26 02:00 | 2023-08-26 03:00 | Summer | FALSE | summer
2023-08-26 03:00 | 2023-08-26 04:00 | Summer | FALSE | summer
2023-08-26 04:00 | 2023-08-26 05:00 | Summer | FALSE | summer
2023-08-26 05:00 | 2023-08-26 06:00 | Summer | FALSE | summer
2023-08-26 06:00 | 2023-08-26 07:00 | Summer | FALSE | summer
2023-08-26 07:00 | 2023-08-26 08:00 | Summer | FALSE | summer
2023-08-26 08:00 | 2023-08-26 09:00 | Summer | FALSE | summer
2023-08-26 09:00 | 2023-08-26 10:00 | Summer | FALSE | summer
2023-08-26 10:00 | 2023-08-26 11:00 | Summer | FALSE | summer
2023-08-26 11:00 | 2023-08-26 12:00 | Summer | FALSE | summer
2023-08-26 12:00 | 2023-08-26 13:00 | Summer | FALSE | summer
2023-08-26 13:00 | 2023-08-26 14:00 | Summer | FALSE | summer
2023-08-26 14:00 | 2023-08-26 15:00 | Summer | FALSE | summer
2023-08-26 15:00 | 2023-08-26 16:00 | Summer | FALSE | summer
2023-08-26 16:00 | 2023-08-26 17:00 | Summer | TRUE | summer
2023-08-26 17:00 | 2023-08-26 18:00 | Summer | TRUE | summer
2023-08-26 18:00 | 2023-08-26 19:00 | Summer | TRUE | summer
2023-08-26 19:00 | 2023-08-26 20:00 | Summer | TRUE | summer
2023-08-26 20:00 | 2023-08-26 21:00 | Summer | TRUE | summer
2023-08-26 21:00 | 2023-08-26 22:00 | Summer | FALSE | summer
2023-08-26 22:00 | 2023-08-26 23:00 | Summer | FALSE | summer
2023-08-26 23:00 | 2023-08-27 | Summer | FALSE | summer
2023-08-27 | 2023-08-27 01:00 | Summer | FALSE | summer
2023-08-27 01:00 | 2023-08-27 02:00 | Summer | FALSE | summer
2023-08-27 02:00 | 2023-08-27 03:00 | Summer | FALSE | summer
2023-08-27 03:00 | 2023-08-27 04:00 | Summer | FALSE | summer
2023-08-27 04:00 | 2023-08-27 05:00 | Summer | FALSE | summer
2023-08-27 05:00 | 2023-08-27 06:00 | Summer | FALSE | summer
2023-08-27 06:00 | 2023-08-27 07:00 | Summer | FALSE | summer
2023-08-27 07:00 | 2023-08-27 08:00 | Summer | FALSE | summer
2023-08-27 08:00 | 2023-08-27 09:00 | Summer | FALSE | summer
2023-08-27 09:00 | 2023-08-27 10:00 | Summer | FALSE | summer
2023-08-27 10:00 | 2023-08-27 11:00 | Summer | FALSE | summer
2023-08-27 11:00 | 2023-08-27 12:00 | Summer | FALSE | summer
2023-08-27 12:00 | 2023-08-27 13:00 | Summer | FALSE | summer
2023-08-27 13:00 | 2023-08-27 14:00 | Summer | FALSE | summer
2023-08-27 14:00 | 2023-08-27 15:00 | Summer | FALSE | summer
2023-08-27 15:00 | 2023-08-27 16:00 | Summer | FALSE | summer
2023-08-27 16:00 | 2023-08-27 17:00 | Summer | TRUE | summer
2023-08-27 17:00 | 2023-08-27 18:00 | Summer | TRUE | summer
2023-08-27 18:00 | 2023-08-27 19:00 | Summer | TRUE | summer
2023-08-27 19:00 | 2023-08-27 20:00 | Summer | TRUE | summer
2023-08-27 20:00 | 2023-08-27 21:00 | Summer | TRUE | summer
2023-08-27 21:00 | 2023-08-27 22:00 | Summer | FALSE | summer
2023-08-27 22:00 | 2023-08-27 23:00 | Summer | FALSE | summer
2023-08-27 23:00 | 2023-08-28 | Summer | FALSE | summer
2023-08-28 | 2023-08-28 01:00 | Summer | FALSE | summer
2023-08-28 01:00 | 2023-08-28 02:00 | Summer | FALSE | summer
2023-08-28 02:00 | 2023-08-28 03:00 | Summer | FALSE | summer
2023-08-28 03:00 | 2023-08-28 04:00 | Summer | FALSE | summer
2023-08-28 04:00 | 2023-08-28 05:00 | Summer | FALSE | summer
2023-08-28 05:00 | 2023-08-28 06:00 | Summer | FALSE | summer
2023-08-28 06:00 | 2023-08-28 07:00 | Summer | FALSE | summer
2023-08-28 07:00 | 2023-08-28 08:00 | Summer | FALSE | summer
2023-08-28 08:00 | 2023-08-28 09:00 | Summer | FALSE | summer
2023-08-28 09:00 | 2023-08-28 10:00 | Summer | FALSE | summer
2023-08-28 10:00 | 2023-08-28 11:00 | Summer | FALSE | summer
2023-08-28 11:00 | 2023-08-28 12:00 | Summer | FALSE | summer
2023-08-28 12:00 | 2023-08-28 13:00 | Summer | FALSE | summer
2023-08-28 13:00 | 2023-08-28 14:00 | Summer | FALSE | summer
2023-08-28 14:00 | 2023-08-28 15:00 | Summer | FALSE | summer
2023-08-28 15:00 | 2023-08-28 16:00 | Summer | FALSE | summer
2023-08-28 16:00 | 2023-08-28 17:00 | Summer | TRUE | summer
2023-08-28 17:00 | 2023-08-28 18:00 | Summer | TRUE | summer
2023-08-28 18:00 | 2023-08-28 19:00 | Summer | TRUE | summer
2023-08-28 19:00 | 2023-08-28 20:00 | Summer | TRUE | summer
2023-08-28 20:00 | 2023-08-28 21:00 | Summer | TRUE | summer
2023-08-28 21:00 | 2023-08-28 22:00 | Summer | FALSE | summer
2023-08-28 22:00 | 2023-08-28 23:00 | Summer | FALSE | summer
2023-08-28 23:00 | 2023-08-29 | Summer | FALSE | summer
2023-08-29 | 2023-08-29 01:00 | Summer | FALSE | summer
2023-08-29 01:00 | 2023-08-29 02:00 | Summer | FALSE | summer
2023-08-29 02:00 | 2023-08-29 03:00 | Summer | FALSE | summer
2023-08-29 03:00 | 2023-08-29 04:00 | Summer | FALSE | summer
2023-08-29 04:00 | 2023-08-29 05:00 | Summer | FALSE | summer
2023-08-29 05:00 | 2023-08-29 06:00 | Summer | FALSE | summer
2023-08-29 06:00 | 2023-08-29 07:00 | Summer | FALSE | summer
2023-08-29 07:00 | 2023-08-29 08:00 | Summer | FALSE | summer
2023-08-29 08:00 | 2023-08-29 09:00 | Summer | FALSE | summer
2023-08-29 09:00 | 2023-08-29 10:00 | Summer | FALSE | summer
2023-08-29 10:00 | 2023-08-29 11:00 | Summer | FALSE | summer
2023-08-29 11:00 | 2023-08-29 12:00 | Summer | FALSE | summer
2023-08-29 12:00 | 2023-08-29 13:00 | Summer | FALSE | summer
2023-08-29 13:00 | 2023-08-29 14:00 | Summer | FALSE | summer
2023-08-29 14:00 | 2023-08-29 15:00 | Summer | FALSE | summer
2023-08-29 15:00 | 2023-08-29 16:00 | Summer | FALSE | summer
2023-08-29 16:00 | 2023-08-29 17:00 | Summer | TRUE | summer
2023-08-29 17:00 | 2023-08-29 18:00 | Summer | TRUE | summer
2023-08-29 18:00 | 2023-08-29 19:00 | Summer | TRUE | summer
2023-08-29 19:00 | 2023-08-29 20:00 | Summer | TRUE | summer
2023-08-29 20:00 | 2023-08-29 21:00 | Summer | TRUE | summer
2023-08-29 21:00 | 2023-08-29 22:00 | Summer | FALSE | summer
2023-08-29 22:00 | 2023-08-29 23:00 | Summer | FALSE | summer
2023-08-29 23:00 | 2023-08-30 | Summer | FALSE | summer
2023-08-30 | 2023-08-30 01:00 | Summer | FALSE | summer
2023-08-30 01:00 | 2023-08-30 02:00 | Summer | FALSE | summer
2023-08-30 02:00 | 2023-08-30 03:00 | Summer | FALSE | summer
2023-08-30 03:00 | 2023-08-30 04:00 | Summer | FALSE | summer
2023-08-30 04:00 | 2023-08-30 05:00 | Summer | FALSE | summer
2023-08-30 05:00 | 2023-08-30 06:00 | Summer | FALSE | summer
2023-08-30 06:00 | 2023-08-30 07:00 | Summer | FALSE | summer
2023-08-30 07:00 | 2023-08-30 08:00 | Summer | FALSE | summer
2023-08-30 08:00 | 2023-08-30 09:00 | Summer | FALSE | summer
2023-08-30 09:00 | 2023-08-30 10:00 | Summer | FALSE | summer
2023-08-30 10:00 | 2023-08-30 11:00 | Summer | FALSE | summer
2023-08-30 11:00 | 2023-08-30 12:00 | Summer | FALSE | summer
2023-08-30 12:00 | 2023-08-30 13:00 | Summer | FALSE | summer
2023-08-30 13:00 | 2023-08-30 14:00 | Summer | FALSE | summer
2023-08-30 14:00 | 2023-08-30 15:00 | Summer | FALSE | summer
2023-08-30 15:00 | 2023-08-30 16:00 | Summer | FALSE | summer
2023-08-30 16:00 | 2023-08-30 17:00 | Summer | TRUE | summer
2023-08-30 17:00 | 2023-08-30 18:00 | Summer | TRUE | summer
2023-08-30 18:00 | 2023-08-30 19:00 | Summer | TRUE | summer
2023-08-30 19:00 | 2023-08-30 20:00 | Summer | TRUE | summer
2023-08-30 20:00 | 2023-08-30 21:00 | Summer | TRUE | summer
2023-08-30 21:00 | 2023-08-30 22:00 | Summer | FALSE | summer
2023-08-30 22:00 | 2023-08-30 23:00 | Summer | FALSE | summer
2023-08-30 23:00 | 2023-08-31 | Summer | FALSE | summer
2023-08-31 | 2023-08-31 01:00 | Summer | FALSE | summer
2023-08-31 01:00 | 2023-08-31 02:00 | Summer | FALSE | summer
2023-08-31 02:00 | 2023-08-31 03:00 | Summer | FALSE | summer
2023-08-31 03:00 | 2023-08-31 04:00 | Summer | FALSE | summer
2023-08-31 04:00 | 2023-08-31 05:00 | Summer | FALSE | summer
2023-08-31 05:00 | 2023-08-31 06:00 | Summer | FALSE | summer
2023-08-31 06:00 | 2023-08-31 07:00 | Summer | FALSE | summer
2023-08-31 07:00 | 2023-08-31 08:00 | Summer | FALSE | summer
2023-08-31 08:00 | 2023-08-31 09:00 | Summer | FALSE | summer
2023-08-31 09:00 | 2023-08-31 10:00 | Summer | FALSE | summer
2023-08-31 10:00 | 2023-08-31 11:00 | Summer | FALSE | summer
2023-08-31 11:00 | 2023-08-31 12:00 | Summer | FALSE | summer
2023-08-31 12:00 | 2023-08-31 13:00 | Summer | FALSE | summer
2023-08-31 13:00 | 2023-08-31 14:00 | Summer | FALSE | summer
2023-08-31 14:00 | 2023-08-31 15:00 | Summer | FALSE | summer
2023-08-31 15:00 | 2023-08-31 16:00 | Summer | FALSE | summer
2023-08-31 16:00 | 2023-08-31 17:00 | Summer | TRUE | summer
2023-08-31 17:00 | 2023-08-31 18:00 | Summer | TRUE | summer
2023-08-31 18:00 | 2023-08-31 19:00 | Summer | TRUE | summer
2023-08-31 19:00 | 2023-08-31 20:00 | Summer | TRUE | summer
2023-08-31 20:00 | 2023-08-31 21:00 | Summer | TRUE | summer
2023-08-31 21:00 | 2023-08-31 22:00 | Summer | FALSE | summer
2023-08-31 22:00 | 2023-08-31 23:00 | Summer | FALSE | summer
2023-08-31 23:00 | 2023-09-01 | Summer | FALSE | summer
2023-09-01 | 2023-09-01 01:00 | Summer | FALSE | summer
2023-09-01 01:00 | 2023-09-01 02:00 | Summer | FALSE | summer
2023-09-01 02:00 | 2023-09-01 03:00 | Summer | FALSE | summer
2023-09-01 03:00 | 2023-09-01 04:00 | Summer | FALSE | summer
2023-09-01 04:00 | 2023-09-01 05:00 | Summer | FALSE | summer
2023-09-01 05:00 | 2023-09-01 06:00 | Summer | FALSE | summer
2023-09-01 06:00 | 2023-09-01 07:00 | Summer | FALSE | summer
2023-09-01 07:00 | 2023-09-01 08:00 | Summer | FALSE | summer
2023-09-01 08:00 | 2023-09-01 09:00 | Summer | FALSE | summer
2023-09-01 09:00 | 2023-09-01 10:00 | Summer | FALSE | summer
2023-09-01 10:00 | 2023-09-01 11:00 | Summer | FALSE | summer
2023-09-01 11:00 | 2023-09-01 12:00 | Summer | FALSE | summer
2023-09-01 12:00 | 2023-09-01 13:00 | Summer | FALSE | summer
2023-09-01 13:00 | 2023-09-01 14:00 | Summer | FALSE | summer
2023-09-01 14:00 | 2023-09-01 15:00 | Summer | FALSE | summer
2023-09-01 15:00 | 2023-09-01 16:00 | Summer | FALSE | summer
2023-09-01 16:00 | 2023-09-01 17:00 | Summer | TRUE | summer
2023-09-01 17:00 | 2023-09-01 18:00 | Summer | TRUE | summer
2023-09-01 18:00 | 2023-09-01 19:00 | Summer | TRUE | summer
2023-09-01 19:00 | 2023-09-01 20:00 | Summer | TRUE | summer
2023-09-01 20:00 | 2023-09-01 21:00 | Summer | TRUE | summer
2023-09-01 21:00 | 2023-09-01 22:00 | Summer | FALSE | summer
2023-09-01 22:00 | 2023-09-01 23:00 | Summer | FALSE | summer
2023-09-01 23:00 | 2023-09-02 | Summer | FALSE | summer
2023-09-02 | 2023-09-02 01:00 | Summer | FALSE | summer
2023-09-02 01:00 | 2023-09-02 02:00 | Summer | FALSE | summer
2023-09-02 02:00 | 2023-09-02 03:00 | Summer | FALSE | summer
2023-09-02 03:00 | 2023-09-02 04:00 | Summer | FALSE | summer
2023-09-02 04:00 | 2023-09-02 05:00 | Summer | FALSE | summer
2023-09-02 05:00 | 2023-09-02 06:00 | Summer | FALSE | summer
2023-09-02 06:00 | 2023-09-02 07:00 | Summer | FALSE | summer
2023-09-02 07:00 | 2023-09-02 08:00 | Summer | FALSE | summer
2023-09-02 08:00 | 2023-09-02 09:00 | Summer | FALSE | summer
2023-09-02 09:00 | 2023-09-02 10:00 | Summer | FALSE | summer
2023-09-02 10:00 | 2023-09-02 11:00 | Summer | FALSE | summer
2023-09-02 11:00 | 2023-09-02 12:00 | Summer | FALSE | summer
2023-09-02 12:00 | 2023-09-02 13:00 | Summer | FALSE | summer
2023-09-02 13:00 | 2023-09-02 14:00 | Summer | FALSE | summer
2023-09-02 14:00 | 2023-09-02 15:00 | Summer | FALSE | summer
2023-09-02 15:00 | 2023-09-02 16:00 | Summer | FALSE | summer
2023-09-02 16:00 | 2023-09-02 17:00 | Summer | TRUE | summer
2023-09-02 17:00 | 2023-09-02 18:00 | Summer | TRUE | summer
2023-09-02 18:00 | 2023-09-02 19:00 | Summer | TRUE | summer
2023-09-02 19:00 | 2023-09-02 20:00 | Summer | TRUE | summer
2023-09-02 20:00 | 2023-09-02 21:00 | Summer | TRUE | summer
2023-09-02 21:00 | 2023-09-02 22:00 | Summer | FALSE | summer
2023-09-02 22:00 | 2023-09-02 23:00 | Summer | FALSE | summer
2023-09-02 23:00 | 2023-09-03 | Summer | FALSE | summer
2023-09-03 | 2023-09-03 01:00 | Summer | FALSE | summer
2023-09-03 01:00 | 2023-09-03 02:00 | Summer | FALSE | summer
2023-09-03 02:00 | 2023-09-03 03:00 | Summer | FALSE | summer
2023-09-03 03:00 | 2023-09-03 04:00 | Summer | FALSE | summer
2023-09-03 04:00 | 2023-09-03 05:00 | Summer | FALSE | summer
2023-09-03 05:00 | 2023-09-03 06:00 | Summer | FALSE | summer
2023-09-03 06:00 | 2023-09-03 07:00 | Summer | FALSE | summer
2023-09-03 07:00 | 2023-09-03 08:00 | Summer | FALSE | summer
2023-09-03 08:00 | 2023-09-03 09:00 | Summer | FALSE | summer
2023-09-03 09:00 | 2023-09-03 10:00 | Summer | FALSE | summer
2023-09-03 10:00 | 2023-09-03 11:00 | Summer | FALSE | summer
2023-09-03 11:00 | 2023-09-03 12:00 | Summer | FALSE | summer
2023-09-03 12:00 | 2023-09-03 13:00 | Summer | FALSE | summer
2023-09-03 13:00 | 2023-09-03 14:00 | Summer | FALSE | summer
2023-09-03 14:00 | 2023-09-03 15:00 | Summer | FALSE | summer
2023-09-03 15:00 | 2023-09-03 16:00 | Summer | FALSE | summer
2023-09-03 16:00 | 2023-09-03 17:00 | Summer | TRUE | summer
2023-09-03 17:00 | 2023-09-03 18:00 | Summer | TRUE | summer
2023-09-03 18:00 | 2023-09-03 19:00 | Summer | TRUE | summer
2023-09-03 19:00 | 2023-09-03 20:00 | Summer | TRUE | summer
2023-09-03 20:00 | 2023-09-03 21:00 | Summer | TRUE | summer
2023-09-03 21:00 | 2023-09-03 22:00 | Summer | FALSE | summer
2023-09-03 22:00 | 2023-09-03 23:00 | Summer | FALSE | summer
2023-09-03 23:00 | 2023-09-04 | Summer | FALSE | summer
2023-09-04 | 2023-09-04 01:00 | Summer | FALSE | summer
2023-09-04 01:00 | 2023-09-04 02:00 | Summer | FALSE | summer
2023-09-04 02:00 | 2023-09-04 03:00 | Summer | FALSE | summer
2023-09-04 03:00 | 2023-09-04 04:00 | Summer | FALSE | summer
2023-09-04 04:00 | 2023-09-04 05:00 | Summer | FALSE | summer
2023-09-04 05:00 | 2023-09-04 06:00 | Summer | FALSE | summer
2023-09-04 06:00 | 2023-09-04 07:00 | Summer | FALSE | summer
2023-09-04 07:00 | 2023-09-04 08:00 | Summer | FALSE | summer
2023-09-04 08:00 | 2023-09-04 09:00 | Summer | FALSE | summer
2023-09-04 09:00 | 2023-09-04 10:00 | Summer | FALSE | summer
2023-09-04 10:00 | 2023-09-04 11:00 | Summer | FALSE | summer
2023-09-04 11:00 | 2023-09-04 12:00 | Summer | FALSE | summer
2023-09-04 12:00 | 2023-09-04 13:00 | Summer | FALSE | summer
2023-09-04 13:00 | 2023-09-04 14:00 | Summer | FALSE | summer
2023-09-04 14:00 | 2023-09-04 15:00 | Summer | FALSE | summer
2023-09-04 15:00 | 2023-09-04 16:00 | Summer | FALSE | summer
2023-09-04 16:00 | 2023-09-04 17:00 | Summer | TRUE | summer
2023-09-04 17:00 | 2023-09-04 18:00 | Summer | TRUE | summer
2023-09-04 18:00 | 2023-09-04 19:00 | Summer | TRUE | summer
2023-09-04 19:00 | 2023-09-04 20:00 | Summer | TRUE | summer
2023-09-04 20:00 | 2023-09-04 21:00 | Summer | TRUE | summer
2023-09-04 21:00 | 2023-09-04 22:00 | Summer | FALSE | summer
2023-09-04 22:00 | 2023-09-04 23:00 | Summer | FALSE | summer
2023-09-04 23:00 | 2023-09-05 | Summer | FALSE | summer
2023-09-05 | 2023-09-05 01:00 | Summer | FALSE | summer
2023-09-05 01:00 | 2023-09-05 02:00 | Summer | FALSE | summer
2023-09-05 02:00 | 2023-09-05 03:00 | Summer | FALSE | summer
2023-09-05 03:00 | 2023-09-05 04:00 | Summer | FALSE | summer
2023-09-05 04:00 | 2023-09-05 05:00 | Summer | FALSE | summer
2023-09-05 05:00 | 2023-09-05 06:00 | Summer | FALSE | summer
2023-09-05 06:00 | 2023-09-05 07:00 | Summer | FALSE | summer
2023-09-05 07:00 | 2023-09-05 08:00 | Summer | FALSE | summer
2023-09-05 08:00 | 2023-09-05 09:00 | Summer | FALSE | summer
2023-09-05 09:00 | 2023-09-05 10:00 | Summer | FALSE | summer
2023-09-05 10:00 | 2023-09-05 11:00 | Summer | FALSE | summer
2023-09-05 11:00 | 2023-09-05 12:00 | Summer | FALSE | summer
2023-09-05 12:00 | 2023-09-05 13:00 | Summer | FALSE | summer
2023-09-05 13:00 | 2023-09-05 14:00 | Summer | FALSE | summer
2023-09-05 14:00 | 2023-09-05 15:00 | Summer | FALSE | summer
2023-09-05 15:00 | 2023-09-05 16:00 | Summer | FALSE | summer
2023-09-05 16:00 | 2023-09-05 17:00 | Summer | TRUE | summer
2023-09-05 17:00 | 2023-09-05 18:00 | Summer | TRUE | summer
2023-09-05 18:00 | 2023-09-05 19:00 | Summer | TRUE | summer
2023-09-05 19:00 | 2023-09-05 20:00 | Summer | TRUE | summer
2023-09-05 20:00 | 2023-09-05 21:00 | Summer | TRUE | summer
2023-09-05 21:00 | 2023-09-05 22:00 | Summer | FALSE | summer
2023-09-05 22:00 | 2023-09-05 23:00 | Summer | FALSE | summer
2023-09-05 23:00 | 2023-09-06 | Summer | FALSE | summer
2023-09-06 | 2023-09-06 01:00 | Summer | FALSE | summer
2023-09-06 01:00 | 2023-09-06 02:00 | Summer | FALSE | summer
2023-09-06 02:00 | 2023-09-06 03:00 | Summer | FALSE | summer
2023-09-06 03:00 | 2023-09-06 04:00 | Summer | FALSE | summer
2023-09-06 04:00 | 2023-09-06 05:00 | Summer | FALSE | summer
2023-09-06 05:00 | 2023-09-06 06:00 | Summer | FALSE | summer
2023-09-06 06:00 | 2023-09-06 07:00 | Summer | FALSE | summer
2023-09-06 07:00 | 2023-09-06 08:00 | Summer | FALSE | summer
2023-09-06 08:00 | 2023-09-06 09:00 | Summer | FALSE | summer
2023-09-06 09:00 | 2023-09-06 10:00 | Summer | FALSE | summer
2023-09-06 10:00 | 2023-09-06 11:00 | Summer | FALSE | summer
2023-09-06 11:00 | 2023-09-06 12:00 | Summer | FALSE | summer
2023-09-06 12:00 | 2023-09-06 13:00 | Summer | FALSE | summer
2023-09-06 13:00 | 2023-09-06 14:00 | Summer | FALSE | summer
2023-09-06 14:00 | 2023-09-06 15:00 | Summer | FALSE | summer
2023-09-06 15:00 | 2023-09-06 16:00 | Summer | FALSE | summer
2023-09-06 16:00 | 2023-09-06 17:00 | Summer | TRUE | summer
2023-09-06 17:00 | 2023-09-06 18:00 | Summer | TRUE | summer
2023-09-06 18:00 | 2023-09-06 19:00 | Summer | TRUE | summer
2023-09-06 19:00 | 2023-09-06 20:00 | Summer | TRUE | summer
2023-09-06 20:00 | 2023-09-06 21:00 | Summer | TRUE | summer
2023-09-06 21:00 | 2023-09-06 22:00 | Summer | FALSE | summer
2023-09-06 22:00 | 2023-09-06 23:00 | Summer | FALSE | summer
2023-09-06 23:00 | 2023-09-07 | Summer | FALSE | summer
2023-09-07 | 2023-09-07 01:00 | Summer | FALSE | summer
2023-09-07 01:00 | 2023-09-07 02:00 | Summer | FALSE | summer
2023-09-07 02:00 | 2023-09-07 03:00 | Summer | FALSE | summer
2023-09-07 03:00 | 2023-09-07 04:00 | Summer | FALSE | summer
2023-09-07 04:00 | 2023-09-07 05:00 | Summer | FALSE | summer
2023-09-07 05:00 | 2023-09-07 06:00 | Summer | FALSE | summer
2023-09-07 06:00 | 2023-09-07 07:00 | Summer | FALSE | summer
2023-09-07 07:00 | 2023-09-07 08:00 | Summer | FALSE | summer
2023-09-07 08:00 | 2023-09-07 09:00 | Summer | FALSE | summer
2023-09-07 09:00 | 2023-09-07 10:00 | Summer | FALSE | summer
2023-09-07 10:00 | 2023-09-07 11:00 | Summer | FALSE | summer
2023-09-07 11:00 | 2023-09-07 12:00 | Summer | FALSE | summer
2023-09-07 12:00 | 2023-09-07 13:00 | Summer | FALSE | summer
2023-09-07 13:00 | 2023-09-07 14:00 | Summer | FALSE | summer
2023-09-07 14:00 | 2023-09-07 15:00 | Summer | FALSE | summer
2023-09-07 15:00 | 2023-09-07 16:00 | Summer | FALSE | summer
2023-09-07 16:00 | 2023-09-07 17:00 | Summer | TRUE | summer
2023-09-07 17:00 | 2023-09-07 18:00 | Summer | TRUE | summer
2023-09-07 18:00 | 2023-09-07 19:00 | Summer | TRUE | summer
2023-09-07 19:00 | 2023-09-07 20:00 | Summer | TRUE | summer
2023-09-07 20:00 | 2023-09-07 21:00 | Summer | TRUE | summer
2023-09-07 21:00 | 2023-09-07 22:00 | Summer | FALSE | summer
2023-09-07 22:00 | 2023-09-07 23:00 | Summer | FALSE | summer
2023-09-07 23:00 | 2023-09-08 | Summer | FALSE | summer
2023-09-08 | 2023-09-08 01:00 | Summer | FALSE | summer
2023-09-08 01:00 | 2023-09-08 02:00 | Summer | FALSE | summer
2023-09-08 02:00 | 2023-09-08 03:00 | Summer | FALSE | summer
2023-09-08 03:00 | 2023-09-08 04:00 | Summer | FALSE | summer
2023-09-08 04:00 | 2023-09-08 05:00 | Summer | FALSE | summer
2023-09-08 05:00 | 2023-09-08 06:00 | Summer | FALSE | summer
2023-09-08 06:00 | 2023-09-08 07:00 | Summer | FALSE | summer
2023-09-08 07:00 | 2023-09-08 08:00 | Summer | FALSE | summer
2023-09-08 08:00 | 2023-09-08 09:00 | Summer | FALSE | summer
2023-09-08 09:00 | 2023-09-08 10:00 | Summer | FALSE | summer
2023-09-08 10:00 | 2023-09-08 11:00 | Summer | FALSE | summer
2023-09-08 11:00 | 2023-09-08 12:00 | Summer | FALSE | summer
2023-09-08 12:00 | 2023-09-08 13:00 | Summer | FALSE | summer
2023-09-08 13:00 | 2023-09-08 14:00 | Summer | FALSE | summer
2023-09-08 14:00 | 2023-09-08 15:00 | Summer | FALSE | summer
2023-09-08 15:00 | 2023-09-08 16:00 | Summer | FALSE | summer
2023-09-08 16:00 | 2023-09-08 17:00 | Summer | TRUE | summer
2023-09-08 17:00 | 2023-09-08 18:00 | Summer | TRUE | summer
2023-09-08 18:00 | 2023-09-08 19:00 | Summer | TRUE | summer
2023-09-08 19:00 | 2023-09-08 20:00 | Summer | TRUE | summer
2023-09-08 20:00 | 2023-09-08 21:00 | Summer | TRUE | summer
2023-09-08 21:00 | 2023-09-08 22:00 | Summer | FALSE | summer
2023-09-08 22:00 | 2023-09-08 23:00 | Summer | FALSE | summer
2023-09-08 23:00 | 2023-09-09 | Summer | FALSE | summer
2023-09-09 | 2023-09-09 01:00 | Summer | FALSE | summer
2023-09-09 01:00 | 2023-09-09 02:00 | Summer | FALSE | summer
2023-09-09 02:00 | 2023-09-09 03:00 | Summer | FALSE | summer
2023-09-09 03:00 | 2023-09-09 04:00 | Summer | FALSE | summer
2023-09-09 04:00 | 2023-09-09 05:00 | Summer | FALSE | summer
2023-09-09 05:00 | 2023-09-09 06:00 | Summer | FALSE | summer
2023-09-09 06:00 | 2023-09-09 07:00 | Summer | FALSE | summer
2023-09-09 07:00 | 2023-09-09 08:00 | Summer | FALSE | summer
2023-09-09 08:00 | 2023-09-09 09:00 | Summer | FALSE | summer
2023-09-09 09:00 | 2023-09-09 10:00 | Summer | FALSE | summer
2023-09-09 10:00 | 2023-09-09 11:00 | Summer | FALSE | summer
2023-09-09 11:00 | 2023-09-09 12:00 | Summer | FALSE | summer
2023-09-09 12:00 | 2023-09-09 13:00 | Summer | FALSE | summer
2023-09-09 13:00 | 2023-09-09 14:00 | Summer | FALSE | summer
2023-09-09 14:00 | 2023-09-09 15:00 | Summer | FALSE | summer
2023-09-09 15:00 | 2023-09-09 16:00 | Summer | FALSE | summer
2023-09-09 16:00 | 2023-09-09 17:00 | Summer | TRUE | summer
2023-09-09 17:00 | 2023-09-09 18:00 | Summer | TRUE | summer
2023-09-09 18:00 | 2023-09-09 19:00 | Summer | TRUE | summer
2023-09-09 19:00 | 2023-09-09 20:00 | Summer | TRUE | summer
2023-09-09 20:00 | 2023-09-09 21:00 | Summer | TRUE | summer
2023-09-09 21:00 | 2023-09-09 22:00 | Summer | FALSE | summer
2023-09-09 22:00 | 2023-09-09 23:00 | Summer | FALSE | summer
2023-09-09 23:00 | 2023-09-10 | Summer | FALSE | summer
2023-09-10 | 2023-09-10 01:00 | Summer | FALSE | summer
2023-09-10 01:00 | 2023-09-10 02:00 | Summer | FALSE | summer
2023-09-10 02:00 | 2023-09-10 03:00 | Summer | FALSE | summer
2023-09-10 03:00 | 2023-09-10 04:00 | Summer | FALSE | summer
2023-09-10 04:00 | 2023-09-10 05:00 | Summer | FALSE | summer
2023-09-10 05:00 | 2023-09-10 06:00 | Summer | FALSE | summer
2023-09-10 06:00 | 2023-09-10 07:00 | Summer | FALSE | summer
2023-09-10 07:00 | 2023-09-10 08:00 | Summer | FALSE | summer
2023-09-10 08:00 | 2023-09-10 09:00 | Summer | FALSE | summer
2023-09-10 09:00 | 2023-09-10 10:00 | Summer | FALSE | summer
2023-09-10 10:00 | 2023-09-10 11:00 | Summer | FALSE | summer
2023-09-10 11:00 | 2023-09-10 12:00 | Summer | FALSE | summer
2023-09-10 12:00 | 2023-09-10 13:00 | Summer | FALSE | summer
2023-09-10 13:00 | 2023-09-10 14:00 | Summer | FALSE | summer
2023-09-10 14:00 | 2023-09-10 15:00 | Summer | FALSE | summer
2023-09-10 15:00 | 2023-09-10 16:00 | Summer | FALSE | summer
2023-09-10 16:00 | 2023-09-10 17:00 | Summer | TRUE | summer
2023-09-10 17:00 | 2023-09-10 18:00 | Summer | TRUE | summer
2023-09-10 18:00 | 2023-09-10 19:00 | Summer | TRUE | summer
2023-09-10 19:00 | 2023-09-10 20:00 | Summer | TRUE | summer
2023-09-10 20:00 | 2023-09-10 21:00 | Summer | TRUE | summer
2023-09-10 21:00 | 2023-09-10 22:00 | Summer | FALSE | summer
2023-09-10 22:00 | 2023-09-10 23:00 | Summer | FALSE | summer
2023-09-10 23:00 | 2023-09-11 | Summer | FALSE | summer
2023-09-11 | 2023-09-11 01:00 | Summer | FALSE | summer
2023-09-11 01:00 | 2023-09-11 02:00 | Summer | FALSE | summer
2023-09-11 02:00 | 2023-09-11 03:00 | Summer | FALSE | summer
2023-09-11 03:00 | 2023-09-11 04:00 | Summer | FALSE | summer
2023-09-11 04:00 | 2023-09-11 05:00 | Summer | FALSE | summer
2023-09-11 05:00 | 2023-09-11 06:00 | Summer | FALSE | summer
2023-09-11 06:00 | 2023-09-11 07:00 | Summer | FALSE | summer
2023-09-11 07:00 | 2023-09-11 08:00 | Summer | FALSE | summer
2023-09-11 08:00 | 2023-09-11 09:00 | Summer | FALSE | summer
2023-09-11 09:00 | 2023-09-11 10:00 | Summer | FALSE | summer
2023-09-11 10:00 | 2023-09-11 11:00 | Summer | FALSE | summer
2023-09-11 11:00 | 2023-09-11 12:00 | Summer | FALSE | summer
2023-09-11 12:00 | 2023-09-11 13:00 | Summer | FALSE | summer
2023-09-11 13:00 | 2023-09-11 14:00 | Summer | FALSE | summer
2023-09-11 14:00 | 2023-09-11 15:00 | Summer | FALSE | summer
2023-09-11 15:00 | 2023-09-11 16:00 | Summer | FALSE | summer
2023-09-11 16:00 | 2023-09-11 17:00 | Summer | TRUE | summer
2023-09-11 17:00 | 2023-09-11 18:00 | Summer | TRUE | summer
2023-09-11 18:00 | 2023-09-11 19:00 | Summer | TRUE | summer
2023-09-11 19:00 | 2023-09-11 20:00 | Summer | TRUE | summer
2023-09-11 20:00 | 2023-09-11 21:00 | Summer | TRUE | summer
2023-09-11 21:00 | 2023-09-11 22:00 | Summer | FALSE | summer
2023-09-11 22:00 | 2023-09-11 23:00 | Summer | FALSE | summer
2023-09-11 23:00 | 2023-09-12 | Summer | FALSE | summer
2023-09-12 | 2023-09-12 01:00 | Summer | FALSE | summer
2023-09-12 01:00 | 2023-09-12 02:00 | Summer | FALSE | summer
2023-09-12 02:00 | 2023-09-12 03:00 | Summer | FALSE | summer
2023-09-12 03:00 | 2023-09-12 04:00 | Summer | FALSE | summer
2023-09-12 04:00 | 2023-09-12 05:00 | Summer | FALSE | summer
2023-09-12 05:00 | 2023-09-12 06:00 | Summer | FALSE | summer
2023-09-12 06:00 | 2023-09-12 07:00 | Summer | FALSE | summer
2023-09-12 07:00 | 2023-09-12 08:00 | Summer | FALSE | summer
2023-09-12 08:00 | 2023-09-12 09:00 | Summer | FALSE | summer
2023-09-12 09:00 | 2023-09-12 10:00 | Summer | FALSE | summer
2023-09-12 10:00 | 2023-09-12 11:00 | Summer | FALSE | summer
2023-09-12 11:00 | 2023-09-12 12:00 | Summer | FALSE | summer
2023-09-12 12:00 | 2023-09-12 13:00 | Summer | FALSE | summer
2023-09-12 13:00 | 2023-09-12 14:00 | Summer | FALSE | summer
2023-09-12 14:00 | 2023-09-12 15:00 | Summer | FALSE | summer
2023-09-12 15:00 | 2023-09-12 16:00 | Summer | FALSE | summer
2023-09-12 16:00 | 2023-09-12 17:00 | Summer | TRUE | summer
2023-09-12 17:00 | 2023-09-12 18:00 | Summer | TRUE | summer
2023-09-12 18:00 | 2023-09-12 19:00 | Summer | TRUE | summer
2023-09-12 19:00 | 2023-09-12 20:00 | Summer | TRUE | summer
2023-09-12 20:00 | 2023-09-12 21:00 | Summer | TRUE | summer
2023-09-12 21:00 | 2023-09-12 22:00 | Summer | FALSE | summer
2023-09-12 22:00 | 2023-09-12 23:00 | Summer | FALSE | summer
2023-09-12 23:00 | 2023-09-13 | Summer | FALSE | summer
2023-09-13 | 2023-09-13 01:00 | Summer | FALSE | summer
2023-09-13 01:00 | 2023-09-13 02:00 | Summer | FALSE | summer
2023-09-13 02:00 | 2023-09-13 03:00 | Summer | FALSE | summer
2023-09-13 03:00 | 2023-09-13 04:00 | Summer | FALSE | summer
2023-09-13 04:00 | 2023-09-13 05:00 | Summer | FALSE | summer
2023-09-13 05:00 | 2023-09-13 06:00 | Summer | FALSE | summer
2023-09-13 06:00 | 2023-09-13 07:00 | Summer | FALSE | summer
2023-09-13 07:00 | 2023-09-13 08:00 | Summer | FALSE | summer
2023-09-13 08:00 | 2023-09-13 09:00 | Summer | FALSE | summer
2023-09-13 09:00 | 2023-09-13 10:00 | Summer | FALSE | summer
2023-09-13 10:00 | 2023-09-13 11:00 | Summer | FALSE | summer
2023-09-13 11:00 | 2023-09-13 12:00 | Summer | FALSE | summer
2023-09-13 12:00 | 2023-09-13 13:00 | Summer | FALSE | summer
2023-09-13 13:00 | 2023-09-13 14:00 | Summer | FALSE | summer
2023-09-13 14:00 | 2023-09-13 15:00 | Summer | FALSE | summer
2023-09-13 15:00 | 2023-09-13 16:00 | Summer | FALSE | summer
2023-09-13 16:00 | 2023-09-13 17:00 | Summer | TRUE | summer
2023-09-13 17:00 | 2023-09-13 18:00 | Summer | TRUE | summer
2023-09-13 18:00 | 2023-09-13 19:00 | Summer | TRUE | summer
2023-09-13 19:00 | 2023-09-13 20:00 | Summer | TRUE | summer
2023-09-13 20:00 | 2023-09-13 21:00 | Summer | TRUE | summer
2023-09-13 21:00 | 2023-09-13 22:00 | Summer | FALSE | summer
2023-09-13 22:00 | 2023-09-13 23:00 | Summer | FALSE | summer
2023-09-13 23:00 | 2023-09-14 | Summer | FALSE | summer
2023-09-14 | 2023-09-14 01:00 | Summer | FALSE | summer
2023-09-14 01:00 | 2023-09-14 02:00 | Summer | FALSE | summer
2023-09-14 02:00 | 2023-09-14 03:00 | Summer | FALSE | summer
2023-09-14 03:00 | 2023-09-14 04:00 | Summer | FALSE | summer
2023-09-14 04:00 | 2023-09-14 05:00 | Summer | FALSE | summer
2023-09-14 05:00 | 2023-09-14 06:00 | Summer | FALSE | summer
2023-09-14 06:00 | 2023-09-14 07:00 | Summer | FALSE | summer
2023-09-14 07:00 | 2023-09-14 08:00 | Summer | FALSE | summer
2023-09-14 08:00 | 2023-09-14 09:00 | Summer | FALSE | summer
2023-09-14 09:00 | 2023-09-14 10:00 | Summer | FALSE | summer
2023-09-14 10:00 | 2023-09-14 11:00 | Summer | FALSE | summer
2023-09-14 11:00 | 2023-09-14 12:00 | Summer | FALSE | summer
2023-09-14 12:00 | 2023-09-14 13:00 | Summer | FALSE | summer
2023-09-14 13:00 | 2023-09-14 14:00 | Summer | FALSE | summer
2023-09-14 14:00 | 2023-09-14 15:00 | Summer | FALSE | summer
2023-09-14 15:00 | 2023-09-14 16:00 | Summer | FALSE | summer
2023-09-14 16:00 | 2023-09-14 17:00 | Summer | TRUE | summer
2023-09-14 17:00 | 2023-09-14 18:00 | Summer | TRUE | summer
2023-09-14 18:00 | 2023-09-14 19:00 | Summer | TRUE | summer
2023-09-14 19:00 | 2023-09-14 20:00 | Summer | TRUE | summer
2023-09-14 20:00 | 2023-09-14 21:00 | Summer | TRUE | summer
2023-09-14 21:00 | 2023-09-14 22:00 | Summer | FALSE | summer
2023-09-14 22:00 | 2023-09-14 23:00 | Summer | FALSE | summer
2023-09-14 23:00 | 2023-09-15 | Summer | FALSE | summer
2023-09-15 | 2023-09-15 01:00 | Summer | FALSE | summer
2023-09-15 01:00 | 2023-09-15 02:00 | Summer | FALSE | summer
2023-09-15 02:00 | 2023-09-15 03:00 | Summer | FALSE | summer
2023-09-15 03:00 | 2023-09-15 04:00 | Summer | FALSE | summer
2023-09-15 04:00 | 2023-09-15 05:00 | Summer | FALSE | summer
2023-09-15 05:00 | 2023-09-15 06:00 | Summer | FALSE | summer
2023-09-15 06:00 | 2023-09-15 07:00 | Summer | FALSE | summer
2023-09-15 07:00 | 2023-09-15 08:00 | Summer | FALSE | summer
2023-09-15 08:00 | 2023-09-15 09:00 | Summer | FALSE | summer
2023-09-15 09:00 | 2023-09-15 10:00 | Summer | FALSE | summer
2023-09-15 10:00 | 2023-09-15 11:00 | Summer | FALSE | summer
2023-09-15 11:00 | 2023-09-15 12:00 | Summer | FALSE | summer
2023-09-15 12:00 | 2023-09-15 13:00 | Summer | FALSE | summer
2023-09-15 13:00 | 2023-09-15 14:00 | Summer | FALSE | summer
2023-09-15 14:00 | 2023-09-15 15:00 | Summer | FALSE | summer
2023-09-15 15:00 | 2023-09-15 16:00 | Summer | FALSE | summer
2023-09-15 16:00 | 2023-09-15 17:00 | Summer | TRUE | summer
2023-09-15 17:00 | 2023-09-15 18:00 | Summer | TRUE | summer
2023-09-15 18:00 | 2023-09-15 19:00 | Summer | TRUE | summer
2023-09-15 19:00 | 2023-09-15 20:00 | Summer | TRUE | summer
2023-09-15 20:00 | 2023-09-15 21:00 | Summer | TRUE | summer
2023-09-15 21:00 | 2023-09-15 22:00 | Summer | FALSE | summer
2023-09-15 22:00 | 2023-09-15 23:00 | Summer | FALSE | summer
2023-09-15 23:00 | 2023-09-16 | Summer | FALSE | summer
2023-09-16 | 2023-09-16 01:00 | Summer | FALSE | summer
2023-09-16 01:00 | 2023-09-16 02:00 | Summer | FALSE | summer
2023-09-16 02:00 | 2023-09-16 03:00 | Summer | FALSE | summer
2023-09-16 03:00 | 2023-09-16 04:00 | Summer | FALSE | summer
2023-09-16 04:00 | 2023-09-16 05:00 | Summer | FALSE | summer
2023-09-16 05:00 | 2023-09-16 06:00 | Summer | FALSE | summer
2023-09-16 06:00 | 2023-09-16 07:00 | Summer | FALSE | summer
2023-09-16 07:00 | 2023-09-16 08:00 | Summer | FALSE | summer
2023-09-16 08:00 | 2023-09-16 09:00 | Summer | FALSE | summer
2023-09-16 09:00 | 2023-09-16 10:00 | Summer | FALSE | summer
2023-09-16 10:00 | 2023-09-16 11:00 | Summer | FALSE | summer
2023-09-16 11:00 | 2023-09-16 12:00 | Summer | FALSE | summer
2023-09-16 12:00 | 2023-09-16 13:00 | Summer | FALSE | summer
2023-09-16 13:00 | 2023-09-16 14:00 | Summer | FALSE | summer
2023-09-16 14:00 | 2023-09-16 15:00 | Summer | FALSE | summer
2023-09-16 15:00 | 2023-09-16 16:00 | Summer | FALSE | summer
2023-09-16 16:00 | 2023-09-16 17:00 | Summer | TRUE | summer
2023-09-16 17:00 | 2023-09-16 18:00 | Summer | TRUE | summer
2023-09-16 18:00 | 2023-09-16 19:00 | Summer | TRUE | summer
2023-09-16 19:00 | 2023-09-16 20:00 | Summer | TRUE | summer
2023-09-16 20:00 | 2023-09-16 21:00 | Summer | TRUE | summer
2023-09-16 21:00 | 2023-09-16 22:00 | Summer | FALSE | summer
2023-09-16 22:00 | 2023-09-16 23:00 | Summer | FALSE | summer
2023-09-16 23:00 | 2023-09-17 | Summer | FALSE | summer
2023-09-17 | 2023-09-17 01:00 | Summer | FALSE | summer
2023-09-17 01:00 | 2023-09-17 02:00 | Summer | FALSE | summer
2023-09-17 02:00 | 2023-09-17 03:00 | Summer | FALSE | summer
2023-09-17 03:00 | 2023-09-17 04:00 | Summer | FALSE | summer
2023-09-17 04:00 | 2023-09-17 05:00 | Summer | FALSE | summer
2023-09-17 05:00 | 2023-09-17 06:00 | Summer | FALSE | summer
2023-09-17 06:00 | 2023-09-17 07:00 | Summer | FALSE | summer
2023-09-17 07:00 | 2023-09-17 08:00 | Summer | FALSE | summer
2023-09-17 08:00 | 2023-09-17 09:00 | Summer | FALSE | summer
2023-09-17 09:00 | 2023-09-17 10:00 | Summer | FALSE | summer
2023-09-17 10:00 | 2023-09-17 11:00 | Summer | FALSE | summer
2023-09-17 11:00 | 2023-09-17 12:00 | Summer | FALSE | summer
2023-09-17 12:00 | 2023-09-17 13:00 | Summer | FALSE | summer
2023-09-17 13:00 | 2023-09-17 14:00 | Summer | FALSE | summer
2023-09-17 14:00 | 2023-09-17 15:00 | Summer | FALSE | summer
2023-09-17 15:00 | 2023-09-17 16:00 | Summer | FALSE | summer
2023-09-17 16:00 | 2023-09-17 17:00 | Summer | TRUE | summer
2023-09-17 17:00 | 2023-09-17 18:00 | Summer | TRUE | summer
2023-09-17 18:00 | 2023-09-17 19:00 | Summer | TRUE | summer
2023-09-17 19:00 | 2023-09-17 20:00 | Summer | TRUE | summer
2023-09-17 20:00 | 2023-09-17 21:00 | Summer | TRUE | summer
2023-09-17 21:00 | 2023-09-17 22:00 | Summer | FALSE | summer
2023-09-17 22:00 | 2023-09-17 23:00 | Summer | FALSE | summer
2023-09-17 23:00 | 2023-09-18 | Summer | FALSE | summer
2023-09-18 | 2023-09-18 01:00 | Summer | FALSE | summer
2023-09-18 01:00 | 2023-09-18 02:00 | Summer | FALSE | summer
2023-09-18 02:00 | 2023-09-18 03:00 | Summer | FALSE | summer
2023-09-18 03:00 | 2023-09-18 04:00 | Summer | FALSE | summer
2023-09-18 04:00 | 2023-09-18 05:00 | Summer | FALSE | summer
2023-09-18 05:00 | 2023-09-18 06:00 | Summer | FALSE | summer
2023-09-18 06:00 | 2023-09-18 07:00 | Summer | FALSE | summer
2023-09-18 07:00 | 2023-09-18 08:00 | Summer | FALSE | summer
2023-09-18 08:00 | 2023-09-18 09:00 | Summer | FALSE | summer
2023-09-18 09:00 | 2023-09-18 10:00 | Summer | FALSE | summer
2023-09-18 10:00 | 2023-09-18 11:00 | Summer | FALSE | summer
2023-09-18 11:00 | 2023-09-18 12:00 | Summer | FALSE | summer
2023-09-18 12:00 | 2023-09-18 13:00 | Summer | FALSE | summer
2023-09-18 13:00 | 2023-09-18 14:00 | Summer | FALSE | summer
2023-09-18 14:00 | 2023-09-18 15:00 | Summer | FALSE | summer
2023-09-18 15:00 | 2023-09-18 16:00 | Summer | FALSE | summer
2023-09-18 16:00 | 2023-09-18 17:00 | Summer | TRUE | summer
2023-09-18 17:00 | 2023-09-18 18:00 | Summer | TRUE | summer
2023-09-18 18:00 | 2023-09-18 19:00 | Summer | TRUE | summer
2023-09-18 19:00 | 2023-09-18 20:00 | Summer | TRUE | summer
2023-09-18 20:00 | 2023-09-18 21:00 | Summer | TRUE | summer
2023-09-18 21:00 | 2023-09-18 22:00 | Summer | FALSE | summer
2023-09-18 22:00 | 2023-09-18 23:00 | Summer | FALSE | summer
2023-09-18 23:00 | 2023-09-19 | Summer | FALSE | summer
2023-09-19 | 2023-09-19 01:00 | Summer | FALSE | summer
2023-09-19 01:00 | 2023-09-19 02:00 | Summer | FALSE | summer
2023-09-19 02:00 | 2023-09-19 03:00 | Summer | FALSE | summer
2023-09-19 03:00 | 2023-09-19 04:00 | Summer | FALSE | summer
2023-09-19 04:00 | 2023-09-19 05:00 | Summer | FALSE | summer
2023-09-19 05:00 | 2023-09-19 06:00 | Summer | FALSE | summer
2023-09-19 06:00 | 2023-09-19 07:00 | Summer | FALSE | summer
2023-09-19 07:00 | 2023-09-19 08:00 | Summer | FALSE | summer
2023-09-19 08:00 | 2023-09-19 09:00 | Summer | FALSE | summer
2023-09-19 09:00 | 2023-09-19 10:00 | Summer | FALSE | summer
2023-09-19 10:00 | 2023-09-19 11:00 | Summer | FALSE | summer
2023-09-19 11:00 | 2023-09-19 12:00 | Summer | FALSE | summer
2023-09-19 12:00 | 2023-09-19 13:00 | Summer | FALSE | summer
2023-09-19 13:00 | 2023-09-19 14:00 | Summer | FALSE | summer
2023-09-19 14:00 | 2023-09-19 15:00 | Summer | FALSE | summer
2023-09-19 15:00 | 2023-09-19 16:00 | Summer | FALSE | summer
2023-09-19 16:00 | 2023-09-19 17:00 | Summer | TRUE | summer
2023-09-19 17:00 | 2023-09-19 18:00 | Summer | TRUE | summer
2023-09-19 18:00 | 2023-09-19 19:00 | Summer | TRUE | summer
2023-09-19 19:00 | 2023-09-19 20:00 | Summer | TRUE | summer
2023-09-19 20:00 | 2023-09-19 21:00 | Summer | TRUE | summer
2023-09-19 21:00 | 2023-09-19 22:00 | Summer | FALSE | summer
2023-09-19 22:00 | 2023-09-19 23:00 | Summer | FALSE | summer
2023-09-19 23:00 | 2023-09-20 | Summer | FALSE | summer
2023-09-20 | 2023-09-20 01:00 | Summer | FALSE | summer
2023-09-20 01:00 | 2023-09-20 02:00 | Summer | FALSE | summer
2023-09-20 02:00 | 2023-09-20 03:00 | Summer | FALSE | summer
2023-09-20 03:00 | 2023-09-20 04:00 | Summer | FALSE | summer
2023-09-20 04:00 | 2023-09-20 05:00 | Summer | FALSE | summer
2023-09-20 05:00 | 2023-09-20 06:00 | Summer | FALSE | summer
2023-09-20 06:00 | 2023-09-20 07:00 | Summer | FALSE | summer
2023-09-20 07:00 | 2023-09-20 08:00 | Summer | FALSE | summer
2023-09-20 08:00 | 2023-09-20 09:00 | Summer | FALSE | summer
2023-09-20 09:00 | 2023-09-20 10:00 | Summer | FALSE | summer
2023-09-20 10:00 | 2023-09-20 11:00 | Summer | FALSE | summer
2023-09-20 11:00 | 2023-09-20 12:00 | Summer | FALSE | summer
2023-09-20 12:00 | 2023-09-20 13:00 | Summer | FALSE | summer
2023-09-20 13:00 | 2023-09-20 14:00 | Summer | FALSE | summer
2023-09-20 14:00 | 2023-09-20 15:00 | Summer | FALSE | summer
2023-09-20 15:00 | 2023-09-20 16:00 | Summer | FALSE | summer
2023-09-20 16:00 | 2023-09-20 17:00 | Summer | TRUE | summer
2023-09-20 17:00 | 2023-09-20 18:00 | Summer | TRUE | summer
2023-09-20 18:00 | 2023-09-20 19:00 | Summer | TRUE | summer
2023-09-20 19:00 | 2023-09-20 20:00 | Summer | TRUE | summer
2023-09-20 20:00 | 2023-09-20 21:00 | Summer | TRUE | summer
2023-09-20 21:00 | 2023-09-20 22:00 | Summer | FALSE | summer
2023-09-20 22:00 | 2023-09-20 23:00 | Summer | FALSE | summer
2023-09-20 23:00 | 2023-09-21 | Summer | FALSE | summer
2023-09-21 | 2023-09-21 01:00 | Summer | FALSE | summer
2023-09-21 01:00 | 2023-09-21 02:00 | Summer | FALSE | summer
2023-09-21 02:00 | 2023-09-21 03:00 | Summer | FALSE | summer
2023-09-21 03:00 | 2023-09-21 04:00 | Summer | FALSE | summer
2023-09-21 04:00 | 2023-09-21 05:00 | Summer | FALSE | summer
2023-09-21 05:00 | 2023-09-21 06:00 | Summer | FALSE | summer
2023-09-21 06:00 | 2023-09-21 07:00 | Summer | FALSE | summer
2023-09-21 07:00 | 2023-09-21 08:00 | Summer | FALSE | summer
2023-09-21 08:00 | 2023-09-21 09:00 | Summer | FALSE | summer
2023-09-21 09:00 | 2023-09-21 10:00 | Summer | FALSE | summer
2023-09-21 10:00 | 2023-09-21 11:00 | Summer | FALSE | summer
2023-09-21 11:00 | 2023-09-21 12:00 | Summer | FALSE | summer
2023-09-21 12:00 | 2023-09-21 13:00 | Summer | FALSE | summer
2023-09-21 13:00 | 2023-09-21 14:00 | Summer | FALSE | summer
2023-09-21 14:00 | 2023-09-21 15:00 | Summer | FALSE | summer
2023-09-21 15:00 | 2023-09-21 16:00 | Summer | FALSE | summer
2023-09-21 16:00 | 2023-09-21 17:00 | Summer | TRUE | summer
2023-09-21 17:00 | 2023-09-21 18:00 | Summer | TRUE | summer
2023-09-21 18:00 | 2023-09-21 19:00 | Summer | TRUE | summer
2023-09-21 19:00 | 2023-09-21 20:00 | Summer | TRUE | summer
2023-09-21 20:00 | 2023-09-21 21:00 | Summer | TRUE | summer
2023-09-21 21:00 | 2023-09-21 22:00 | Summer | FALSE | summer
2023-09-21 22:00 | 2023-09-21 23:00 | Summer | FALSE | summer
2023-09-21 23:00 | 2023-09-22 | Summer | FALSE | summer
2023-09-22 | 2023-09-22 01:00 | Summer | FALSE | summer
2023-09-22 01:00 | 2023-09-22 02:00 | Summer | FALSE | summer
2023-09-22 02:00 | 2023-09-22 03:00 | Summer | FALSE | summer
2023-09-22 03:00 | 2023-09-22 04:00 | Summer | FALSE | summer
2023-09-22 04:00 | 2023-09-22 05:00 | Summer | FALSE | summer
2023-09-22 05:00 | 2023-09-22 06:00 | Summer | FALSE | summer
2023-09-22 06:00 | 2023-09-22 07:00 | Summer | FALSE | summer
2023-09-22 07:00 | 2023-09-22 08:00 | Summer | FALSE | summer
2023-09-22 08:00 | 2023-09-22 09:00 | Summer | FALSE | summer
2023-09-22 09:00 | 2023-09-22 10:00 | Summer | FALSE | summer
2023-09-22 10:00 | 2023-09-22 11:00 | Summer | FALSE | summer
2023-09-22 11:00 | 2023-09-22 12:00 | Summer | FALSE | summer
2023-09-22 12:00 | 2023-09-22 13:00 | Summer | FALSE | summer
2023-09-22 13:00 | 2023-09-22 14:00 | Summer | FALSE | summer
2023-09-22 14:00 | 2023-09-22 15:00 | Summer | FALSE | summer
2023-09-22 15:00 | 2023-09-22 16:00 | Summer | FALSE | summer
2023-09-22 16:00 | 2023-09-22 17:00 | Summer | TRUE | summer
2023-09-22 17:00 | 2023-09-22 18:00 | Summer | TRUE | summer
2023-09-22 18:00 | 2023-09-22 19:00 | Summer | TRUE | summer
2023-09-22 19:00 | 2023-09-22 20:00 | Summer | TRUE | summer
2023-09-22 20:00 | 2023-09-22 21:00 | Summer | TRUE | summer
2023-09-22 21:00 | 2023-09-22 22:00 | Summer | FALSE | summer
2023-09-22 22:00 | 2023-09-22 23:00 | Summer | FALSE | summer
2023-09-22 23:00 | 2023-09-23 | Summer | FALSE | summer
2023-09-23 | 2023-09-23 01:00 | Summer | FALSE | summer
2023-09-23 01:00 | 2023-09-23 02:00 | Summer | FALSE | summer
2023-09-23 02:00 | 2023-09-23 03:00 | Summer | FALSE | summer
2023-09-23 03:00 | 2023-09-23 04:00 | Summer | FALSE | summer
2023-09-23 04:00 | 2023-09-23 05:00 | Summer | FALSE | summer
2023-09-23 05:00 | 2023-09-23 06:00 | Summer | FALSE | summer
2023-09-23 06:00 | 2023-09-23 07:00 | Summer | FALSE | summer
2023-09-23 07:00 | 2023-09-23 08:00 | Summer | FALSE | summer
2023-09-23 08:00 | 2023-09-23 09:00 | Summer | FALSE | summer
2023-09-23 09:00 | 2023-09-23 10:00 | Summer | FALSE | summer
2023-09-23 10:00 | 2023-09-23 11:00 | Summer | FALSE | summer
2023-09-23 11:00 | 2023-09-23 12:00 | Summer | FALSE | summer
2023-09-23 12:00 | 2023-09-23 13:00 | Summer | FALSE | summer
2023-09-23 13:00 | 2023-09-23 14:00 | Summer | FALSE | summer
2023-09-23 14:00 | 2023-09-23 15:00 | Summer | FALSE | summer
2023-09-23 15:00 | 2023-09-23 16:00 | Summer | FALSE | summer
2023-09-23 16:00 | 2023-09-23 17:00 | Summer | TRUE | summer
2023-09-23 17:00 | 2023-09-23 18:00 | Summer | TRUE | summer
2023-09-23 18:00 | 2023-09-23 19:00 | Summer | TRUE | summer
2023-09-23 19:00 | 2023-09-23 20:00 | Summer | TRUE | summer
2023-09-23 20:00 | 2023-09-23 21:00 | Summer | TRUE | summer
2023-09-23 21:00 | 2023-09-23 22:00 | Summer | FALSE | summer
2023-09-23 22:00 | 2023-09-23 23:00 | Summer | FALSE | summer
2023-09-23 23:00 | 2023-09-24 | Summer | FALSE | summer
2023-09-24 | 2023-09-24 01:00 | Summer | FALSE | summer
2023-09-24 01:00 | 2023-09-24 02:00 | Summer | FALSE | summer
2023-09-24 02:00 | 2023-09-24 03:00 | Summer | FALSE | summer
2023-09-24 03:00 | 2023-09-24 04:00 | Summer | FALSE | summer
2023-09-24 04:00 | 2023-09-24 05:00 | Summer | FALSE | summer
2023-09-24 05:00 | 2023-09-24 06:00 | Summer | FALSE | summer
2023-09-24 06:00 | 2023-09-24 07:00 | Summer | FALSE | summer
2023-09-24 07:00 | 2023-09-24 08:00 | Summer | FALSE | summer
2023-09-24 08:00 | 2023-09-24 09:00 | Summer | FALSE | summer
2023-09-24 09:00 | 2023-09-24 10:00 | Summer | FALSE | summer
2023-09-24 10:00 | 2023-09-24 11:00 | Summer | FALSE | summer
2023-09-24 11:00 | 2023-09-24 12:00 | Summer | FALSE | summer
2023-09-24 12:00 | 2023-09-24 13:00 | Summer | FALSE | summer
2023-09-24 13:00 | 2023-09-24 14:00 | Summer | FALSE | summer
2023-09-24 14:00 | 2023-09-24 15:00 | Summer | FALSE | summer
2023-09-24 15:00 | 2023-09-24 16:00 | Summer | FALSE | summer
2023-09-24 16:00 | 2023-09-24 17:00 | Summer | TRUE | summer
2023-09-24 17:00 | 2023-09-24 18:00 | Summer | TRUE | summer
2023-09-24 18:00 | 2023-09-24 19:00 | Summer | TRUE | summer
2023-09-24 19:00 | 2023-09-24 20:00 | Summer | TRUE | summer
2023-09-24 20:00 | 2023-09-24 21:00 | Summer | TRUE | summer
2023-09-24 21:00 | 2023-09-24 22:00 | Summer | FALSE | summer
2023-09-24 22:00 | 2023-09-24 23:00 | Summer | FALSE | summer
2023-09-24 23:00 | 2023-09-25 | Summer | FALSE | summer
2023-09-25 | 2023-09-25 01:00 | Summer | FALSE | summer
2023-09-25 01:00 | 2023-09-25 02:00 | Summer | FALSE | summer
2023-09-25 02:00 | 2023-09-25 03:00 | Summer | FALSE | summer
2023-09-25 03:00 | 2023-09-25 04:00 | Summer | FALSE | summer
2023-09-25 04:00 | 2023-09-25 05:00 | Summer | FALSE | summer
2023-09-25 05:00 | 2023-09-25 06:00 | Summer | FALSE | summer
2023-09-25 06:00 | 2023-09-25 07:00 | Summer | FALSE | summer
2023-09-25 07:00 | 2023-09-25 08:00 | Summer | FALSE | summer
2023-09-25 08:00 | 2023-09-25 09:00 | Summer | FALSE | summer
2023-09-25 09:00 | 2023-09-25 10:00 | Summer | FALSE | summer
2023-09-25 10:00 | 2023-09-25 11:00 | Summer | FALSE | summer
2023-09-25 11:00 | 2023-09-25 12:00 | Summer | FALSE | summer
2023-09-25 12:00 | 2023-09-25 13:00 | Summer | FALSE | summer
2023-09-25 13:00 | 2023-09-25 14:00 | Summer | FALSE | summer
2023-09-25 14:00 | 2023-09-25 15:00 | Summer | FALSE | summer
2023-09-25 15:00 | 2023-09-25 16:00 | Summer | FALSE | summer
2023-09-25 16:00 | 2023-09-25 17:00 | Summer | TRUE | summer
2023-09-25 17:00 | 2023-09-25 18:00 | Summer | TRUE | summer
2023-09-25 18:00 | 2023-09-25 19:00 | Summer | TRUE | summer
2023-09-25 19:00 | 2023-09-25 20:00 | Summer | TRUE | summer
2023-09-25 20:00 | 2023-09-25 21:00 | Summer | TRUE | summer
2023-09-25 21:00 | 2023-09-25 22:00 | Summer | FALSE | summer
2023-09-25 22:00 | 2023-09-25 23:00 | Summer | FALSE | summer
2023-09-25 23:00 | 2023-09-26 | Summer | FALSE | summer
2023-09-26 | 2023-09-26 01:00 | Summer | FALSE | summer
2023-09-26 01:00 | 2023-09-26 02:00 | Summer | FALSE | summer
2023-09-26 02:00 | 2023-09-26 03:00 | Summer | FALSE | summer
2023-09-26 03:00 | 2023-09-26 04:00 | Summer | FALSE | summer
2023-09-26 04:00 | 2023-09-26 05:00 | Summer | FALSE | summer
2023-09-26 05:00 | 2023-09-26 06:00 | Summer | FALSE | summer
2023-09-26 06:00 | 2023-09-26 07:00 | Summer | FALSE | summer
2023-09-26 07:00 | 2023-09-26 08:00 | Summer | FALSE | summer
2023-09-26 08:00 | 2023-09-26 09:00 | Summer | FALSE | summer
2023-09-26 09:00 | 2023-09-26 10:00 | Summer | FALSE | summer
2023-09-26 10:00 | 2023-09-26 11:00 | Summer | FALSE | summer
2023-09-26 11:00 | 2023-09-26 12:00 | Summer | FALSE | summer
2023-09-26 12:00 | 2023-09-26 13:00 | Summer | FALSE | summer
2023-09-26 13:00 | 2023-09-26 14:00 | Summer | FALSE | summer
2023-09-26 14:00 | 2023-09-26 15:00 | Summer | FALSE | summer
2023-09-26 15:00 | 2023-09-26 16:00 | Summer | FALSE | summer
2023-09-26 16:00 | 2023-09-26 17:00 | Summer | TRUE | summer
2023-09-26 17:00 | 2023-09-26 18:00 | Summer | TRUE | summer
2023-09-26 18:00 | 2023-09-26 19:00 | Summer | TRUE | summer
2023-09-26 19:00 | 2023-09-26 20:00 | Summer | TRUE | summer
2023-09-26 20:00 | 2023-09-26 21:00 | Summer | TRUE | summer
2023-09-26 21:00 | 2023-09-26 22:00 | Summer | FALSE | summer
2023-09-26 22:00 | 2023-09-26 23:00 | Summer | FALSE | summer
2023-09-26 23:00 | 2023-09-27 | Summer | FALSE | summer
2023-09-27 | 2023-09-27 01:00 | Summer | FALSE | summer
2023-09-27 01:00 | 2023-09-27 02:00 | Summer | FALSE | summer
2023-09-27 02:00 | 2023-09-27 03:00 | Summer | FALSE | summer
2023-09-27 03:00 | 2023-09-27 04:00 | Summer | FALSE | summer
2023-09-27 04:00 | 2023-09-27 05:00 | Summer | FALSE | summer
2023-09-27 05:00 | 2023-09-27 06:00 | Summer | FALSE | summer
2023-09-27 06:00 | 2023-09-27 07:00 | Summer | FALSE | summer
2023-09-27 07:00 | 2023-09-27 08:00 | Summer | FALSE | summer
2023-09-27 08:00 | 2023-09-27 09:00 | Summer | FALSE | summer
2023-09-27 09:00 | 2023-09-27 10:00 | Summer | FALSE | summer
2023-09-27 10:00 | 2023-09-27 11:00 | Summer | FALSE | summer
2023-09-27 11:00 | 2023-09-27 12:00 | Summer | FALSE | summer
2023-09-27 12:00 | 2023-09-27 13:00 | Summer | FALSE | summer
2023-09-27 13:00 | 2023-09-27 14:00 | Summer | FALSE | summer
2023-09-27 14:00 | 2023-09-27 15:00 | Summer | FALSE | summer
2023-09-27 15:00 | 2023-09-27 16:00 | Summer | FALSE | summer
2023-09-27 16:00 | 2023-09-27 17:00 | Summer | TRUE | summer
2023-09-27 17:00 | 2023-09-27 18:00 | Summer | TRUE | summer
2023-09-27 18:00 | 2023-09-27 19:00 | Summer | TRUE | summer
2023-09-27 19:00 | 2023-09-27 20:00 | Summer | TRUE | summer
2023-09-27 20:00 | 2023-09-27 21:00 | Summer | TRUE | summer
2023-09-27 21:00 | 2023-09-27 22:00 | Summer | FALSE | summer
2023-09-27 22:00 | 2023-09-27 23:00 | Summer | FALSE | summer
2023-09-27 23:00 | 2023-09-28 | Summer | FALSE | summer
2023-09-28 | 2023-09-28 01:00 | Summer | FALSE | summer
2023-09-28 01:00 | 2023-09-28 02:00 | Summer | FALSE | summer
2023-09-28 02:00 | 2023-09-28 03:00 | Summer | FALSE | summer
2023-09-28 03:00 | 2023-09-28 04:00 | Summer | FALSE | summer
2023-09-28 04:00 | 2023-09-28 05:00 | Summer | FALSE | summer
2023-09-28 05:00 | 2023-09-28 06:00 | Summer | FALSE | summer
2023-09-28 06:00 | 2023-09-28 07:00 | Summer | FALSE | summer
2023-09-28 07:00 | 2023-09-28 08:00 | Summer | FALSE | summer
2023-09-28 08:00 | 2023-09-28 09:00 | Summer | FALSE | summer
2023-09-28 09:00 | 2023-09-28 10:00 | Summer | FALSE | summer
2023-09-28 10:00 | 2023-09-28 11:00 | Summer | FALSE | summer
2023-09-28 11:00 | 2023-09-28 12:00 | Summer | FALSE | summer
2023-09-28 12:00 | 2023-09-28 13:00 | Summer | FALSE | summer
2023-09-28 13:00 | 2023-09-28 14:00 | Summer | FALSE | summer
2023-09-28 14:00 | 2023-09-28 15:00 | Summer | FALSE | summer
2023-09-28 15:00 | 2023-09-28 16:00 | Summer | FALSE | summer
2023-09-28 16:00 | 2023-09-28 17:00 | Summer | TRUE | summer
2023-09-28 17:00 | 2023-09-28 18:00 | Summer | TRUE | summer
2023-09-28 18:00 | 2023-09-28 19:00 | Summer | TRUE | summer
2023-09-28 19:00 | 2023-09-28 20:00 | Summer | TRUE | summer
2023-09-28 20:00 | 2023-09-28 21:00 | Summer | TRUE | summer
2023-09-28 21:00 | 2023-09-28 22:00 | Summer | FALSE | summer
2023-09-28 22:00 | 2023-09-28 23:00 | Summer | FALSE | summer
2023-09-28 23:00 | 2023-09-29 | Summer | FALSE | summer
2023-09-29 | 2023-09-29 01:00 | Summer | FALSE | summer
2023-09-29 01:00 | 2023-09-29 02:00 | Summer | FALSE | summer
2023-09-29 02:00 | 2023-09-29 03:00 | Summer | FALSE | summer
2023-09-29 03:00 | 2023-09-29 04:00 | Summer | FALSE | summer
2023-09-29 04:00 | 2023-09-29 05:00 | Summer | FALSE | summer
2023-09-29 05:00 | 2023-09-29 06:00 | Summer | FALSE | summer
2023-09-29 06:00 | 2023-09-29 07:00 | Summer | FALSE | summer
2023-09-29 07:00 | 2023-09-29 08:00 | Summer | FALSE | summer
2023-09-29 08:00 | 2023-09-29 09:00 | Summer | FALSE | summer
2023-09-29 09:00 | 2023-09-29 10:00 | Summer | FALSE | summer
2023-09-29 10:00 | 2023-09-29 11:00 | Summer | FALSE | summer
2023-09-29 11:00 | 2023-09-29 12:00 | Summer | FALSE | summer
2023-09-29 12:00 | 2023-09-29 13:00 | Summer | FALSE | summer
2023-09-29 13:00 | 2023-09-29 14:00 | Summer | FALSE | summer
2023-09-29 14:00 | 2023-09-29 15:00 | Summer | FALSE | summer
2023-09-29 15:00 | 2023-09-29 16:00 | Summer | FALSE | summer
2023-09-29 16:00 | 2023-09-29 17:00 | Summer | TRUE | summer
2023-09-29 17:00 | 2023-09-29 18:00 | Summer | TRUE | summer
2023-09-29 18:00 | 2023-09-29 19:00 | Summer | TRUE | summer
2023-09-29 19:00 | 2023-09-29 20:00 | Summer | TRUE | summer
2023-09-29 20:00 | 2023-09-29 21:00 | Summer | TRUE | summer
2023-09-29 21:00 | 2023-09-29 22:00 | Summer | FALSE | summer
2023-09-29 22:00 | 2023-09-29 23:00 | Summer | FALSE | summer
2023-09-29 23:00 | 2023-09-30 | Summer | FALSE | summer
2023-09-30 | 2023-09-30 01:00 | Summer | FALSE | summer
2023-09-30 01:00 | 2023-09-30 02:00 | Summer | FALSE | summer
2023-09-30 02:00 | 2023-09-30 03:00 | Summer | FALSE | summer
2023-09-30 03:00 | 2023-09-30 04:00 | Summer | FALSE | summer
2023-09-30 04:00 | 2023-09-30 05:00 | Summer | FALSE | summer
2023-09-30 05:00 | 2023-09-30 06:00 | Summer | FALSE | summer
2023-09-30 06:00 | 2023-09-30 07:00 | Summer | FALSE | summer
2023-09-30 07:00 | 2023-09-30 08:00 | Summer | FALSE | summer
2023-09-30 08:00 | 2023-09-30 09:00 | Summer | FALSE | summer
2023-09-30 09:00 | 2023-09-30 10:00 | Summer | FALSE | summer
2023-09-30 10:00 | 2023-09-30 11:00 | Summer | FALSE | summer
2023-09-30 11:00 | 2023-09-30 12:00 | Summer | FALSE | summer
2023-09-30 12:00 | 2023-09-30 13:00 | Summer | FALSE | summer
2023-09-30 13:00 | 2023-09-30 14:00 | Summer | FALSE | summer
2023-09-30 14:00 | 2023-09-30 15:00 | Summer | FALSE | summer
2023-09-30 15:00 | 2023-09-30 16:00 | Summer | FALSE | summer
2023-09-30 16:00 | 2023-09-30 17:00 | Summer | TRUE | summer
2023-09-30 17:00 | 2023-09-30 18:00 | Summer | TRUE | summer
2023-09-30 18:00 | 2023-09-30 19:00 | Summer | TRUE | summer
2023-09-30 19:00 | 2023-09-30 20:00 | Summer | TRUE | summer
2023-09-30 20:00 | 2023-09-30 21:00 | Summer | TRUE | summer
2023-09-30 21:00 | 2023-09-30 22:00 | Summer | FALSE | summer
2023-09-30 22:00 | 2023-09-30 23:00 | Summer | FALSE | summer
2023-09-30 23:00 | 2023-10-01 | Summer | FALSE | summer
2023-10-01 | 2023-10-01 01:00 | Winter | FALSE | summer
2023-10-01 01:00 | 2023-10-01 02:00 | Winter | FALSE | summer
2023-10-01 02:00 | 2023-10-01 03:00 | Winter | FALSE | summer
2023-10-01 03:00 | 2023-10-01 04:00 | Winter | FALSE | summer
2023-10-01 04:00 | 2023-10-01 05:00 | Winter | FALSE | summer
2023-10-01 05:00 | 2023-10-01 06:00 | Winter | FALSE | summer
2023-10-01 06:00 | 2023-10-01 07:00 | Winter | FALSE | summer
2023-10-01 07:00 | 2023-10-01 08:00 | Winter | FALSE | summer
2023-10-01 08:00 | 2023-10-01 09:00 | Winter | FALSE | summer
2023-10-01 09:00 | 2023-10-01 10:00 | Winter | FALSE | summer
2023-10-01 10:00 | 2023-10-01 11:00 | Winter | FALSE | summer
2023-10-01 11:00 | 2023-10-01 12:00 | Winter | FALSE | summer
2023-10-01 12:00 | 2023-10-01 13:00 | Winter | FALSE | summer
2023-10-01 13:00 | 2023-10-01 14:00 | Winter | FALSE | summer
2023-10-01 14:00 | 2023-10-01 15:00 | Winter | FALSE | summer
2023-10-01 15:00 | 2023-10-01 16:00 | Winter | FALSE | summer
2023-10-01 16:00 | 2023-10-01 17:00 | Winter | TRUE | summer
2023-10-01 17:00 | 2023-10-01 18:00 | Winter | TRUE | summer
2023-10-01 18:00 | 2023-10-01 19:00 | Winter | TRUE | summer
2023-10-01 19:00 | 2023-10-01 20:00 | Winter | TRUE | summer
2023-10-01 20:00 | 2023-10-01 21:00 | Winter | TRUE | summer
2023-10-01 21:00 | 2023-10-01 22:00 | Winter | FALSE | summer
2023-10-01 22:00 | 2023-10-01 23:00 | Winter | FALSE | summer
2023-10-01 23:00 | 2023-10-02 | Winter | FALSE | summer
2023-10-02 | 2023-10-02 01:00 | Winter | FALSE | summer
2023-10-02 01:00 | 2023-10-02 02:00 | Winter | FALSE | summer
2023-10-02 02:00 | 2023-10-02 03:00 | Winter | FALSE | summer
2023-10-02 03:00 | 2023-10-02 04:00 | Winter | FALSE | summer
2023-10-02 04:00 | 2023-10-02 05:00 | Winter | FALSE | summer
2023-10-02 05:00 | 2023-10-02 06:00 | Winter | FALSE | summer
2023-10-02 06:00 | 2023-10-02 07:00 | Winter | FALSE | summer
2023-10-02 07:00 | 2023-10-02 08:00 | Winter | FALSE | summer
2023-10-02 08:00 | 2023-10-02 09:00 | Winter | FALSE | summer
2023-10-02 09:00 | 2023-10-02 10:00 | Winter | FALSE | summer
2023-10-02 10:00 | 2023-10-02 11:00 | Winter | FALSE | summer
2023-10-02 11:00 | 2023-10-02 12:00 | Winter | FALSE | summer
2023-10-02 12:00 | 2023-10-02 13:00 | Winter | FALSE | summer
2023-10-02 13:00 | 2023-10-02 14:00 | Winter | FALSE | summer
2023-10-02 14:00 | 2023-10-02 15:00 | Winter | FALSE | summer
2023-10-02 15:00 | 2023-10-02 16:00 | Winter | FALSE | summer
2023-10-02 16:00 | 2023-10-02 17:00 | Winter | TRUE | summer
2023-10-02 17:00 | 2023-10-02 18:00 | Winter | TRUE | summer
2023-10-02 18:00 | 2023-10-02 19:00 | Winter | TRUE | summer
2023-10-02 19:00 | 2023-10-02 20:00 | Winter | TRUE | summer
2023-10-02 20:00 | 2023-10-02 21:00 | Winter | TRUE | summer
2023-10-02 21:00 | 2023-10-02 22:00 | Winter | FALSE | summer
2023-10-02 22:00 | 2023-10-02 23:00 | Winter | FALSE | summer
2023-10-02 23:00 | 2023-10-03 | Winter | FALSE | summer
2023-10-03 | 2023-10-03 01:00 | Winter | FALSE | summer
2023-10-03 01:00 | 2023-10-03 02:00 | Winter | FALSE | summer
2023-10-03 02:00 | 2023-10-03 03:00 | Winter | FALSE | summer
2023-10-03 03:00 | 2023-10-03 04:00 | Winter | FALSE | summer
2023-10-03 04:00 | 2023-10-03 05:00 | Winter | FALSE | summer
2023-10-03 05:00 | 2023-10-03 06:00 | Winter | FALSE | summer
2023-10-03 06:00 | 2023-10-03 07:00 | Winter | FALSE | summer
2023-10-03 07:00 | 2023-10-03 08:00 | Winter | FALSE | summer
2023-10-03 08:00 | 2023-10-03 09:00 | Winter | FALSE | summer
2023-10-03 09:00 | 2023-10-03 10:00 | Winter | FALSE | summer
2023-10-03 10:00 | 2023-10-03 11:00 | Winter | FALSE | summer
2023-10-03 11:00 | 2023-10-03 12:00 | Winter | FALSE | summer
2023-10-03 12:00 | 2023-10-03 13:00 | Winter | FALSE | summer
2023-10-03 13:00 | 2023-10-03 14:00 | Winter | FALSE | summer
2023-10-03 14:00 | 2023-10-03 15:00 | Winter | FALSE | summer
2023-10-03 15:00 | 2023-10-03 16:00 | Winter | FALSE | summer
2023-10-03 16:00 | 2023-10-03 17:00 | Winter | TRUE | summer
2023-10-03 17:00 | 2023-10-03 18:00 | Winter | TRUE | summer
2023-10-03 18:00 | 2023-10-03 19:00 | Winter | TRUE | summer
2023-10-03 19:00 | 2023-10-03 20:00 | Winter | TRUE | summer
2023-10-03 20:00 | 2023-10-03 21:00 | Winter | TRUE | summer
2023-10-03 21:00 | 2023-10-03 22:00 | Winter | FALSE | summer
2023-10-03 22:00 | 2023-10-03 23:00 | Winter | FALSE | summer
2023-10-03 23:00 | 2023-10-04 | Winter | FALSE | summer
2023-10-04 | 2023-10-04 01:00 | Winter | FALSE | summer
2023-10-04 01:00 | 2023-10-04 02:00 | Winter | FALSE | summer
2023-10-04 02:00 | 2023-10-04 03:00 | Winter | FALSE | summer
2023-10-04 03:00 | 2023-10-04 04:00 | Winter | FALSE | summer
2023-10-04 04:00 | 2023-10-04 05:00 | Winter | FALSE | summer
2023-10-04 05:00 | 2023-10-04 06:00 | Winter | FALSE | summer
2023-10-04 06:00 | 2023-10-04 07:00 | Winter | FALSE | summer
2023-10-04 07:00 | 2023-10-04 08:00 | Winter | FALSE | summer
2023-10-04 08:00 | 2023-10-04 09:00 | Winter | FALSE | summer
2023-10-04 09:00 | 2023-10-04 10:00 | Winter | FALSE | summer
2023-10-04 10:00 | 2023-10-04 11:00 | Winter | FALSE | summer
2023-10-04 11:00 | 2023-10-04 12:00 | Winter | FALSE | summer
2023-10-04 12:00 | 2023-10-04 13:00 | Winter | FALSE | summer
2023-10-04 13:00 | 2023-10-04 14:00 | Winter | FALSE | summer
2023-10-04 14:00 | 2023-10-04 15:00 | Winter | FALSE | summer
2023-10-04 15:00 | 2023-10-04 16:00 | Winter | FALSE | summer
2023-10-04 16:00 | 2023-10-04 17:00 | Winter | TRUE | summer
2023-10-04 17:00 | 2023-10-04 18:00 | Winter | TRUE | summer
2023-10-04 18:00 | 2023-10-04 19:00 | Winter | TRUE | summer
2023-10-04 19:00 | 2023-10-04 20:00 | Winter | TRUE | summer
2023-10-04 20:00 | 2023-10-04 21:00 | Winter | TRUE | summer
2023-10-04 21:00 | 2023-10-04 22:00 | Winter | FALSE | summer
2023-10-04 22:00 | 2023-10-04 23:00 | Winter | FALSE | summer
2023-10-04 23:00 | 2023-10-05 | Winter | FALSE | summer
2023-10-05 | 2023-10-05 01:00 | Winter | FALSE | summer
2023-10-05 01:00 | 2023-10-05 02:00 | Winter | FALSE | summer
2023-10-05 02:00 | 2023-10-05 03:00 | Winter | FALSE | summer
2023-10-05 03:00 | 2023-10-05 04:00 | Winter | FALSE | summer
2023-10-05 04:00 | 2023-10-05 05:00 | Winter | FALSE | summer
2023-10-05 05:00 | 2023-10-05 06:00 | Winter | FALSE | summer
2023-10-05 06:00 | 2023-10-05 07:00 | Winter | FALSE | summer
2023-10-05 07:00 | 2023-10-05 08:00 | Winter | FALSE | summer
2023-10-05 08:00 | 2023-10-05 09:00 | Winter | FALSE | summer
2023-10-05 09:00 | 2023-10-05 10:00 | Winter | FALSE | summer
2023-10-05 10:00 | 2023-10-05 11:00 | Winter | FALSE | summer
2023-10-05 11:00 | 2023-10-05 12:00 | Winter | FALSE | summer
2023-10-05 12:00 | 2023-10-05 13:00 | Winter | FALSE | summer
2023-10-05 13:00 | 2023-10-05 14:00 | Winter | FALSE | summer
2023-10-05 14:00 | 2023-10-05 15:00 | Winter | FALSE | summer
2023-10-05 15:00 | 2023-10-05 16:00 | Winter | FALSE | summer
2023-10-05 16:00 | 2023-10-05 17:00 | Winter | TRUE | summer
2023-10-05 17:00 | 2023-10-05 18:00 | Winter | TRUE | summer
2023-10-05 18:00 | 2023-10-05 19:00 | Winter | TRUE | summer
2023-10-05 19:00 | 2023-10-05 20:00 | Winter | TRUE | summer
2023-10-05 20:00 | 2023-10-05 21:00 | Winter | TRUE | summer
2023-10-05 21:00 | 2023-10-05 22:00 | Winter | FALSE | summer
2023-10-05 22:00 | 2023-10-05 23:00 | Winter | FALSE | summer
2023-10-05 23:00 | 2023-10-06 | Winter | FALSE | summer
2023-10-06 | 2023-10-06 01:00 | Winter | FALSE | summer
2023-10-06 01:00 | 2023-10-06 02:00 | Winter | FALSE | summer
2023-10-06 02:00 | 2023-10-06 03:00 | Winter | FALSE | summer
2023-10-06 03:00 | 2023-10-06 04:00 | Winter | FALSE | summer
2023-10-06 04:00 | 2023-10-06 05:00 | Winter | FALSE | summer
2023-10-06 05:00 | 2023-10-06 06:00 | Winter | FALSE | summer
2023-10-06 06:00 | 2023-10-06 07:00 | Winter | FALSE | summer
2023-10-06 07:00 | 2023-10-06 08:00 | Winter | FALSE | summer
2023-10-06 08:00 | 2023-10-06 09:00 | Winter | FALSE | summer
2023-10-06 09:00 | 2023-10-06 10:00 | Winter | FALSE | summer
2023-10-06 10:00 | 2023-10-06 11:00 | Winter | FALSE | summer
2023-10-06 11:00 | 2023-10-06 12:00 | Winter | FALSE | summer
2023-10-06 12:00 | 2023-10-06 13:00 | Winter | FALSE | summer
2023-10-06 13:00 | 2023-10-06 14:00 | Winter | FALSE | summer
2023-10-06 14:00 | 2023-10-06 15:00 | Winter | FALSE | summer
2023-10-06 15:00 | 2023-10-06 16:00 | Winter | FALSE | summer
2023-10-06 16:00 | 2023-10-06 17:00 | Winter | TRUE | summer
2023-10-06 17:00 | 2023-10-06 18:00 | Winter | TRUE | summer
2023-10-06 18:00 | 2023-10-06 19:00 | Winter | TRUE | summer
2023-10-06 19:00 | 2023-10-06 20:00 | Winter | TRUE | summer
2023-10-06 20:00 | 2023-10-06 21:00 | Winter | TRUE | summer
2023-10-06 21:00 | 2023-10-06 22:00 | Winter | FALSE | summer
2023-10-06 22:00 | 2023-10-06 23:00 | Winter | FALSE | summer
2023-10-06 23:00 | 2023-10-07 | Winter | FALSE | summer
2023-10-07 | 2023-10-07 01:00 | Winter | FALSE | summer
2023-10-07 01:00 | 2023-10-07 02:00 | Winter | FALSE | summer
2023-10-07 02:00 | 2023-10-07 03:00 | Winter | FALSE | summer
2023-10-07 03:00 | 2023-10-07 04:00 | Winter | FALSE | summer
2023-10-07 04:00 | 2023-10-07 05:00 | Winter | FALSE | summer
2023-10-07 05:00 | 2023-10-07 06:00 | Winter | FALSE | summer
2023-10-07 06:00 | 2023-10-07 07:00 | Winter | FALSE | summer
2023-10-07 07:00 | 2023-10-07 08:00 | Winter | FALSE | summer
2023-10-07 08:00 | 2023-10-07 09:00 | Winter | FALSE | summer
2023-10-07 09:00 | 2023-10-07 10:00 | Winter | FALSE | summer
2023-10-07 10:00 | 2023-10-07 11:00 | Winter | FALSE | summer
2023-10-07 11:00 | 2023-10-07 12:00 | Winter | FALSE | summer
2023-10-07 12:00 | 2023-10-07 13:00 | Winter | FALSE | summer
2023-10-07 13:00 | 2023-10-07 14:00 | Winter | FALSE | summer
2023-10-07 14:00 | 2023-10-07 15:00 | Winter | FALSE | summer
2023-10-07 15:00 | 2023-10-07 16:00 | Winter | FALSE | summer
2023-10-07 16:00 | 2023-10-07 17:00 | Winter | TRUE | summer
2023-10-07 17:00 | 2023-10-07 18:00 | Winter | TRUE | summer
2023-10-07 18:00 | 2023-10-07 19:00 | Winter | TRUE | summer
2023-10-07 19:00 | 2023-10-07 20:00 | Winter | TRUE | summer
2023-10-07 20:00 | 2023-10-07 21:00 | Winter | TRUE | summer
2023-10-07 21:00 | 2023-10-07 22:00 | Winter | FALSE | summer
2023-10-07 22:00 | 2023-10-07 23:00 | Winter | FALSE | summer
2023-10-07 23:00 | 2023-10-08 | Winter | FALSE | summer
2023-10-08 | 2023-10-08 01:00 | Winter | FALSE | summer
2023-10-08 01:00 | 2023-10-08 02:00 | Winter | FALSE | summer
2023-10-08 02:00 | 2023-10-08 03:00 | Winter | FALSE | summer
2023-10-08 03:00 | 2023-10-08 04:00 | Winter | FALSE | summer
2023-10-08 04:00 | 2023-10-08 05:00 | Winter | FALSE | summer
2023-10-08 05:00 | 2023-10-08 06:00 | Winter | FALSE | summer
2023-10-08 06:00 | 2023-10-08 07:00 | Winter | FALSE | summer
2023-10-08 07:00 | 2023-10-08 08:00 | Winter | FALSE | summer
2023-10-08 08:00 | 2023-10-08 09:00 | Winter | FALSE | summer
2023-10-08 09:00 | 2023-10-08 10:00 | Winter | FALSE | summer
2023-10-08 10:00 | 2023-10-08 11:00 | Winter | FALSE | summer
2023-10-08 11:00 | 2023-10-08 12:00 | Winter | FALSE | summer
2023-10-08 12:00 | 2023-10-08 13:00 | Winter | FALSE | summer
2023-10-08 13:00 | 2023-10-08 14:00 | Winter | FALSE | summer
2023-10-08 14:00 | 2023-10-08 15:00 | Winter | FALSE | summer
2023-10-08 15:00 | 2023-10-08 16:00 | Winter | FALSE | summer
2023-10-08 16:00 | 2023-10-08 17:00 | Winter | TRUE | summer
2023-10-08 17:00 | 2023-10-08 18:00 | Winter | TRUE | summer
2023-10-08 18:00 | 2023-10-08 19:00 | Winter | TRUE | summer
2023-10-08 19:00 | 2023-10-08 20:00 | Winter | TRUE | summer
2023-10-08 20:00 | 2023-10-08 21:00 | Winter | TRUE | summer
2023-10-08 21:00 | 2023-10-08 22:00 | Winter | FALSE | summer
2023-10-08 22:00 | 2023-10-08 23:00 | Winter | FALSE | summer
2023-10-08 23:00 | 2023-10-09 | Winter | FALSE | summer
2023-10-09 | 2023-10-09 01:00 | Winter | FALSE | summer
2023-10-09 01:00 | 2023-10-09 02:00 | Winter | FALSE | summer
2023-10-09 02:00 | 2023-10-09 03:00 | Winter | FALSE | summer
2023-10-09 03:00 | 2023-10-09 04:00 | Winter | FALSE | summer
2023-10-09 04:00 | 2023-10-09 05:00 | Winter | FALSE | summer
2023-10-09 05:00 | 2023-10-09 06:00 | Winter | FALSE | summer
2023-10-09 06:00 | 2023-10-09 07:00 | Winter | FALSE | summer
2023-10-09 07:00 | 2023-10-09 08:00 | Winter | FALSE | summer
2023-10-09 08:00 | 2023-10-09 09:00 | Winter | FALSE | summer
2023-10-09 09:00 | 2023-10-09 10:00 | Winter | FALSE | summer
2023-10-09 10:00 | 2023-10-09 11:00 | Winter | FALSE | summer
2023-10-09 11:00 | 2023-10-09 12:00 | Winter | FALSE | summer
2023-10-09 12:00 | 2023-10-09 13:00 | Winter | FALSE | summer
2023-10-09 13:00 | 2023-10-09 14:00 | Winter | FALSE | summer
2023-10-09 14:00 | 2023-10-09 15:00 | Winter | FALSE | summer
2023-10-09 15:00 | 2023-10-09 16:00 | Winter | FALSE | summer
2023-10-09 16:00 | 2023-10-09 17:00 | Winter | TRUE | summer
2023-10-09 17:00 | 2023-10-09 18:00 | Winter | TRUE | summer
2023-10-09 18:00 | 2023-10-09 19:00 | Winter | TRUE | summer
2023-10-09 19:00 | 2023-10-09 20:00 | Winter | TRUE | summer
2023-10-09 20:00 | 2023-10-09 21:00 | Winter | TRUE | summer
2023-10-09 21:00 | 2023-10-09 22:00 | Winter | FALSE | summer
2023-10-09 22:00 | 2023-10-09 23:00 | Winter | FALSE | summer
2023-10-09 23:00 | 2023-10-10 | Winter | FALSE | summer
2023-10-10 | 2023-10-10 01:00 | Winter | FALSE | summer
2023-10-10 01:00 | 2023-10-10 02:00 | Winter | FALSE | summer
2023-10-10 02:00 | 2023-10-10 03:00 | Winter | FALSE | summer
2023-10-10 03:00 | 2023-10-10 04:00 | Winter | FALSE | summer
2023-10-10 04:00 | 2023-10-10 05:00 | Winter | FALSE | summer
2023-10-10 05:00 | 2023-10-10 06:00 | Winter | FALSE | summer
2023-10-10 06:00 | 2023-10-10 07:00 | Winter | FALSE | summer
2023-10-10 07:00 | 2023-10-10 08:00 | Winter | FALSE | summer
2023-10-10 08:00 | 2023-10-10 09:00 | Winter | FALSE | summer
2023-10-10 09:00 | 2023-10-10 10:00 | Winter | FALSE | summer
2023-10-10 10:00 | 2023-10-10 11:00 | Winter | FALSE | summer
2023-10-10 11:00 | 2023-10-10 12:00 | Winter | FALSE | summer
2023-10-10 12:00 | 2023-10-10 13:00 | Winter | FALSE | summer
2023-10-10 13:00 | 2023-10-10 14:00 | Winter | FALSE | summer
2023-10-10 14:00 | 2023-10-10 15:00 | Winter | FALSE | summer
2023-10-10 15:00 | 2023-10-10 16:00 | Winter | FALSE | summer
2023-10-10 16:00 | 2023-10-10 17:00 | Winter | TRUE | summer
2023-10-10 17:00 | 2023-10-10 18:00 | Winter | TRUE | summer
2023-10-10 18:00 | 2023-10-10 19:00 | Winter | TRUE | summer
2023-10-10 19:00 | 2023-10-10 20:00 | Winter | TRUE | summer
2023-10-10 20:00 | 2023-10-10 21:00 | Winter | TRUE | summer
2023-10-10 21:00 | 2023-10-10 22:00 | Winter | FALSE | summer
2023-10-10 22:00 | 2023-10-10 23:00 | Winter | FALSE | summer
2023-10-10 23:00 | 2023-10-11 | Winter | FALSE | summer
2023-10-11 | 2023-10-11 01:00 | Winter | FALSE | summer
2023-10-11 01:00 | 2023-10-11 02:00 | Winter | FALSE | summer
2023-10-11 02:00 | 2023-10-11 03:00 | Winter | FALSE | summer
2023-10-11 03:00 | 2023-10-11 04:00 | Winter | FALSE | summer
2023-10-11 04:00 | 2023-10-11 05:00 | Winter | FALSE | summer
2023-10-11 05:00 | 2023-10-11 06:00 | Winter | FALSE | summer
2023-10-11 06:00 | 2023-10-11 07:00 | Winter | FALSE | summer
2023-10-11 07:00 | 2023-10-11 08:00 | Winter | FALSE | summer
2023-10-11 08:00 | 2023-10-11 09:00 | Winter | FALSE | summer
2023-10-11 09:00 | 2023-10-11 10:00 | Winter | FALSE | summer
2023-10-11 10:00 | 2023-10-11 11:00 | Winter | FALSE | summer
2023-10-11 11:00 | 2023-10-11 12:00 | Winter | FALSE | summer
2023-10-11 12:00 | 2023-10-11 13:00 | Winter | FALSE | summer
2023-10-11 13:00 | 2023-10-11 14:00 | Winter | FALSE | summer
2023-10-11 14:00 | 2023-10-11 15:00 | Winter | FALSE | summer
2023-10-11 15:00 | 2023-10-11 16:00 | Winter | FALSE | summer
2023-10-11 16:00 | 2023-10-11 17:00 | Winter | TRUE | summer
2023-10-11 17:00 | 2023-10-11 18:00 | Winter | TRUE | summer
2023-10-11 18:00 | 2023-10-11 19:00 | Winter | TRUE | summer
2023-10-11 19:00 | 2023-10-11 20:00 | Winter | TRUE | summer
2023-10-11 20:00 | 2023-10-11 21:00 | Winter | TRUE | summer
2023-10-11 21:00 | 2023-10-11 22:00 | Winter | FALSE | summer
2023-10-11 22:00 | 2023-10-11 23:00 | Winter | FALSE | summer
2023-10-11 23:00 | 2023-10-12 | Winter | FALSE | summer
2023-10-12 | 2023-10-12 01:00 | Winter | FALSE | summer
2023-10-12 01:00 | 2023-10-12 02:00 | Winter | FALSE | summer
2023-10-12 02:00 | 2023-10-12 03:00 | Winter | FALSE | summer
2023-10-12 03:00 | 2023-10-12 04:00 | Winter | FALSE | summer
2023-10-12 04:00 | 2023-10-12 05:00 | Winter | FALSE | summer
2023-10-12 05:00 | 2023-10-12 06:00 | Winter | FALSE | summer
2023-10-12 06:00 | 2023-10-12 07:00 | Winter | FALSE | summer
2023-10-12 07:00 | 2023-10-12 08:00 | Winter | FALSE | summer
2023-10-12 08:00 | 2023-10-12 09:00 | Winter | FALSE | summer
2023-10-12 09:00 | 2023-10-12 10:00 | Winter | FALSE | summer
2023-10-12 10:00 | 2023-10-12 11:00 | Winter | FALSE | summer
2023-10-12 11:00 | 2023-10-12 12:00 | Winter | FALSE | summer
2023-10-12 12:00 | 2023-10-12 13:00 | Winter | FALSE | summer
2023-10-12 13:00 | 2023-10-12 14:00 | Winter | FALSE | summer
2023-10-12 14:00 | 2023-10-12 15:00 | Winter | FALSE | summer
2023-10-12 15:00 | 2023-10-12 16:00 | Winter | FALSE | summer
2023-10-12 16:00 | 2023-10-12 17:00 | Winter | TRUE | summer
2023-10-12 17:00 | 2023-10-12 18:00 | Winter | TRUE | summer
2023-10-12 18:00 | 2023-10-12 19:00 | Winter | TRUE | summer
2023-10-12 19:00 | 2023-10-12 20:00 | Winter | TRUE | summer
2023-10-12 20:00 | 2023-10-12 21:00 | Winter | TRUE | summer
2023-10-12 21:00 | 2023-10-12 22:00 | Winter | FALSE | summer
2023-10-12 22:00 | 2023-10-12 23:00 | Winter | FALSE | summer
2023-10-12 23:00 | 2023-10-13 | Winter | FALSE | summer
2023-10-13 | 2023-10-13 01:00 | Winter | FALSE | summer
2023-10-13 01:00 | 2023-10-13 02:00 | Winter | FALSE | summer
2023-10-13 02:00 | 2023-10-13 03:00 | Winter | FALSE | summer
2023-10-13 03:00 | 2023-10-13 04:00 | Winter | FALSE | summer
2023-10-13 04:00 | 2023-10-13 05:00 | Winter | FALSE | summer
2023-10-13 05:00 | 2023-10-13 06:00 | Winter | FALSE | summer
2023-10-13 06:00 | 2023-10-13 07:00 | Winter | FALSE | summer
2023-10-13 07:00 | 2023-10-13 08:00 | Winter | FALSE | summer
2023-10-13 08:00 | 2023-10-13 09:00 | Winter | FALSE | summer
2023-10-13 09:00 | 2023-10-13 10:00 | Winter | FALSE | summer
2023-10-13 10:00 | 2023-10-13 11:00 | Winter | FALSE | summer
2023-10-13 11:00 | 2023-10-13 12:00 | Winter | FALSE | summer
2023-10-13 12:00 | 2023-10-13 13:00 | Winter | FALSE | summer
2023-10-13 13:00 | 2023-10-13 14:00 | Winter | FALSE | summer
2023-10-13 14:00 | 2023-10-13 15:00 | Winter | FALSE | summer
2023-10-13 15:00 | 2023-10-13 16:00 | Winter | FALSE | summer
2023-10-13 16:00 | 2023-10-13 17:00 | Winter | TRUE | summer
2023-10-13 17:00 | 2023-10-13 18:00 | Winter | TRUE | summer
2023-10-13 18:00 | 2023-10-13 19:00 | Winter | TRUE | summer
2023-10-13 19:00 | 2023-10-13 20:00 | Winter | TRUE | summer
2023-10-13 20:00 | 2023-10-13 21:00 | Winter | TRUE | summer
2023-10-13 21:00 | 2023-10-13 22:00 | Winter | FALSE | summer
2023-10-13 22:00 | 2023-10-13 23:00 | Winter | FALSE | summer
2023-10-13 23:00 | 2023-10-14 | Winter | FALSE | summer
2023-10-14 | 2023-10-14 01:00 | Winter | FALSE | summer
2023-10-14 01:00 | 2023-10-14 02:00 | Winter | FALSE | summer
2023-10-14 02:00 | 2023-10-14 03:00 | Winter | FALSE | summer
2023-10-14 03:00 | 2023-10-14 04:00 | Winter | FALSE | summer
2023-10-14 04:00 | 2023-10-14 05:00 | Winter | FALSE | summer
2023-10-14 05:00 | 2023-10-14 06:00 | Winter | FALSE | summer
2023-10-14 06:00 | 2023-10-14 07:00 | Winter | FALSE | summer
2023-10-14 07:00 | 2023-10-14 08:00 | Winter | FALSE | summer
2023-10-14 08:00 | 2023-10-14 09:00 | Winter | FALSE | summer
2023-10-14 09:00 | 2023-10-14 10:00 | Winter | FALSE | summer
2023-10-14 10:00 | 2023-10-14 11:00 | Winter | FALSE | summer
2023-10-14 11:00 | 2023-10-14 12:00 | Winter | FALSE | summer
2023-10-14 12:00 | 2023-10-14 13:00 | Winter | FALSE | summer
2023-10-14 13:00 | 2023-10-14 14:00 | Winter | FALSE | summer
2023-10-14 14:00 | 2023-10-14 15:00 | Winter | FALSE | summer
2023-10-14 15:00 | 2023-10-14 16:00 | Winter | FALSE | summer
2023-10-14 16:00 | 2023-10-14 17:00 | Winter | TRUE | summer
2023-10-14 17:00 | 2023-10-14 18:00 | Winter | TRUE | summer
2023-10-14 18:00 | 2023-10-14 19:00 | Winter | TRUE | summer
2023-10-14 19:00 | 2023-10-14 20:00 | Winter | TRUE | summer
2023-10-14 20:00 | 2023-10-14 21:00 | Winter | TRUE | summer
2023-10-14 21:00 | 2023-10-14 22:00 | Winter | FALSE | summer
2023-10-14 22:00 | 2023-10-14 23:00 | Winter | FALSE | summer
2023-10-14 23:00 | 2023-10-15 | Winter | FALSE | summer
2023-10-15 | 2023-10-15 01:00 | Winter | FALSE | summer
2023-10-15 01:00 | 2023-10-15 02:00 | Winter | FALSE | summer
2023-10-15 02:00 | 2023-10-15 03:00 | Winter | FALSE | summer
2023-10-15 03:00 | 2023-10-15 04:00 | Winter | FALSE | summer
2023-10-15 04:00 | 2023-10-15 05:00 | Winter | FALSE | summer
2023-10-15 05:00 | 2023-10-15 06:00 | Winter | FALSE | summer
2023-10-15 06:00 | 2023-10-15 07:00 | Winter | FALSE | summer
2023-10-15 07:00 | 2023-10-15 08:00 | Winter | FALSE | summer
2023-10-15 08:00 | 2023-10-15 09:00 | Winter | FALSE | summer
2023-10-15 09:00 | 2023-10-15 10:00 | Winter | FALSE | summer
2023-10-15 10:00 | 2023-10-15 11:00 | Winter | FALSE | summer
2023-10-15 11:00 | 2023-10-15 12:00 | Winter | FALSE | summer
2023-10-15 12:00 | 2023-10-15 13:00 | Winter | FALSE | summer
2023-10-15 13:00 | 2023-10-15 14:00 | Winter | FALSE | summer
2023-10-15 14:00 | 2023-10-15 15:00 | Winter | FALSE | summer
2023-10-15 15:00 | 2023-10-15 16:00 | Winter | FALSE | summer
2023-10-15 16:00 | 2023-10-15 17:00 | Winter | TRUE | summer
2023-10-15 17:00 | 2023-10-15 18:00 | Winter | TRUE | summer
2023-10-15 18:00 | 2023-10-15 19:00 | Winter | TRUE | summer
2023-10-15 19:00 | 2023-10-15 20:00 | Winter | TRUE | summer
2023-10-15 20:00 | 2023-10-15 21:00 | Winter | TRUE | summer
2023-10-15 21:00 | 2023-10-15 22:00 | Winter | FALSE | summer
2023-10-15 22:00 | 2023-10-15 23:00 | Winter | FALSE | summer
2023-10-15 23:00 | 2023-10-16 | Winter | FALSE | summer
2023-10-16 | 2023-10-16 01:00 | Winter | FALSE | summer
2023-10-16 01:00 | 2023-10-16 02:00 | Winter | FALSE | summer
2023-10-16 02:00 | 2023-10-16 03:00 | Winter | FALSE | summer
2023-10-16 03:00 | 2023-10-16 04:00 | Winter | FALSE | summer
2023-10-16 04:00 | 2023-10-16 05:00 | Winter | FALSE | summer
2023-10-16 05:00 | 2023-10-16 06:00 | Winter | FALSE | summer
2023-10-16 06:00 | 2023-10-16 07:00 | Winter | FALSE | summer
2023-10-16 07:00 | 2023-10-16 08:00 | Winter | FALSE | summer
2023-10-16 08:00 | 2023-10-16 09:00 | Winter | FALSE | summer
2023-10-16 09:00 | 2023-10-16 10:00 | Winter | FALSE | summer
2023-10-16 10:00 | 2023-10-16 11:00 | Winter | FALSE | summer
2023-10-16 11:00 | 2023-10-16 12:00 | Winter | FALSE | summer
2023-10-16 12:00 | 2023-10-16 13:00 | Winter | FALSE | summer
2023-10-16 13:00 | 2023-10-16 14:00 | Winter | FALSE | summer
2023-10-16 14:00 | 2023-10-16 15:00 | Winter | FALSE | summer
2023-10-16 15:00 | 2023-10-16 16:00 | Winter | FALSE | summer
2023-10-16 16:00 | 2023-10-16 17:00 | Winter | TRUE | summer
2023-10-16 17:00 | 2023-10-16 18:00 | Winter | TRUE | summer
2023-10-16 18:00 | 2023-10-16 19:00 | Winter | TRUE | summer
2023-10-16 19:00 | 2023-10-16 20:00 | Winter | TRUE | summer
2023-10-16 20:00 | 2023-10-16 21:00 | Winter | TRUE | summer
2023-10-16 21:00 | 2023-10-16 22:00 | Winter | FALSE | summer
2023-10-16 22:00 | 2023-10-16 23:00 | Winter | FALSE | summer
2023-10-16 23:00 | 2023-10-17 | Winter | FALSE | summer
2023-10-17 | 2023-10-17 01:00 | Winter | FALSE | summer
2023-10-17 01:00 | 2023-10-17 02:00 | Winter | FALSE | summer
2023-10-17 02:00 | 2023-10-17 03:00 | Winter | FALSE | summer
2023-10-17 03:00 | 2023-10-17 04:00 | Winter | FALSE | summer
2023-10-17 04:00 | 2023-10-17 05:00 | Winter | FALSE | summer
2023-10-17 05:00 | 2023-10-17 06:00 | Winter | FALSE | summer
2023-10-17 06:00 | 2023-10-17 07:00 | Winter | FALSE | summer
2023-10-17 07:00 | 2023-10-17 08:00 | Winter | FALSE | summer
2023-10-17 08:00 | 2023-10-17 09:00 | Winter | FALSE | summer
2023-10-17 09:00 | 2023-10-17 10:00 | Winter | FALSE | summer
2023-10-17 10:00 | 2023-10-17 11:00 | Winter | FALSE | summer
2023-10-17 11:00 | 2023-10-17 12:00 | Winter | FALSE | summer
2023-10-17 12:00 | 2023-10-17 13:00 | Winter | FALSE | summer
2023-10-17 13:00 | 2023-10-17 14:00 | Winter | FALSE | summer
2023-10-17 14:00 | 2023-10-17 15:00 | Winter | FALSE | summer
2023-10-17 15:00 | 2023-10-17 16:00 | Winter | FALSE | summer
2023-10-17 16:00 | 2023-10-17 17:00 | Winter | TRUE | summer
2023-10-17 17:00 | 2023-10-17 18:00 | Winter | TRUE | summer
2023-10-17 18:00 | 2023-10-17 19:00 | Winter | TRUE | summer
2023-10-17 19:00 | 2023-10-17 20:00 | Winter | TRUE | summer
2023-10-17 20:00 | 2023-10-17 21:00 | Winter | TRUE | summer
2023-10-17 21:00 | 2023-10-17 22:00 | Winter | FALSE | summer
2023-10-17 22:00 | 2023-10-17 23:00 | Winter | FALSE | summer
2023-10-17 23:00 | 2023-10-18 | Winter | FALSE | summer
2023-10-18 | 2023-10-18 01:00 | Winter | FALSE | summer
2023-10-18 01:00 | 2023-10-18 02:00 | Winter | FALSE | summer
2023-10-18 02:00 | 2023-10-18 03:00 | Winter | FALSE | summer
2023-10-18 03:00 | 2023-10-18 04:00 | Winter | FALSE | summer
2023-10-18 04:00 | 2023-10-18 05:00 | Winter | FALSE | summer
2023-10-18 05:00 | 2023-10-18 06:00 | Winter | FALSE | summer
2023-10-18 06:00 | 2023-10-18 07:00 | Winter | FALSE | summer
2023-10-18 07:00 | 2023-10-18 08:00 | Winter | FALSE | summer
2023-10-18 08:00 | 2023-10-18 09:00 | Winter | FALSE | summer
2023-10-18 09:00 | 2023-10-18 10:00 | Winter | FALSE | summer
2023-10-18 10:00 | 2023-10-18 11:00 | Winter | FALSE | summer
2023-10-18 11:00 | 2023-10-18 12:00 | Winter | FALSE | summer
2023-10-18 12:00 | 2023-10-18 13:00 | Winter | FALSE | summer
2023-10-18 13:00 | 2023-10-18 14:00 | Winter | FALSE | summer
2023-10-18 14:00 | 2023-10-18 15:00 | Winter | FALSE | summer
2023-10-18 15:00 | 2023-10-18 16:00 | Winter | FALSE | summer
2023-10-18 16:00 | 2023-10-18 17:00 | Winter | TRUE | summer
2023-10-18 17:00 | 2023-10-18 18:00 | Winter | TRUE | summer
2023-10-18 18:00 | 2023-10-18 19:00 | Winter | TRUE | summer
2023-10-18 19:00 | 2023-10-18 20:00 | Winter | TRUE | summer
2023-10-18 20:00 | 2023-10-18 21:00 | Winter | TRUE | summer
2023-10-18 21:00 | 2023-10-18 22:00 | Winter | FALSE | summer
2023-10-18 22:00 | 2023-10-18 23:00 | Winter | FALSE | summer
2023-10-18 23:00 | 2023-10-19 | Winter | FALSE | summer
2023-10-19 | 2023-10-19 01:00 | Winter | FALSE | summer
2023-10-19 01:00 | 2023-10-19 02:00 | Winter | FALSE | summer
2023-10-19 02:00 | 2023-10-19 03:00 | Winter | FALSE | summer
2023-10-19 03:00 | 2023-10-19 04:00 | Winter | FALSE | summer
2023-10-19 04:00 | 2023-10-19 05:00 | Winter | FALSE | summer
2023-10-19 05:00 | 2023-10-19 06:00 | Winter | FALSE | summer
2023-10-19 06:00 | 2023-10-19 07:00 | Winter | FALSE | summer
2023-10-19 07:00 | 2023-10-19 08:00 | Winter | FALSE | summer
2023-10-19 08:00 | 2023-10-19 09:00 | Winter | FALSE | summer
2023-10-19 09:00 | 2023-10-19 10:00 | Winter | FALSE | summer
2023-10-19 10:00 | 2023-10-19 11:00 | Winter | FALSE | summer
2023-10-19 11:00 | 2023-10-19 12:00 | Winter | FALSE | summer
2023-10-19 12:00 | 2023-10-19 13:00 | Winter | FALSE | summer
2023-10-19 13:00 | 2023-10-19 14:00 | Winter | FALSE | summer
2023-10-19 14:00 | 2023-10-19 15:00 | Winter | FALSE | summer
2023-10-19 15:00 | 2023-10-19 16:00 | Winter | FALSE | summer
2023-10-19 16:00 | 2023-10-19 17:00 | Winter | TRUE | summer
2023-10-19 17:00 | 2023-10-19 18:00 | Winter | TRUE | summer
2023-10-19 18:00 | 2023-10-19 19:00 | Winter | TRUE | summer
2023-10-19 19:00 | 2023-10-19 20:00 | Winter | TRUE | summer
2023-10-19 20:00 | 2023-10-19 21:00 | Winter | TRUE | summer
2023-10-19 21:00 | 2023-10-19 22:00 | Winter | FALSE | summer
2023-10-19 22:00 | 2023-10-19 23:00 | Winter | FALSE | summer
2023-10-19 23:00 | 2023-10-20 | Winter | FALSE | summer
2023-10-20 | 2023-10-20 01:00 | Winter | FALSE | summer
2023-10-20 01:00 | 2023-10-20 02:00 | Winter | FALSE | summer
2023-10-20 02:00 | 2023-10-20 03:00 | Winter | FALSE | summer
2023-10-20 03:00 | 2023-10-20 04:00 | Winter | FALSE | summer
2023-10-20 04:00 | 2023-10-20 05:00 | Winter | FALSE | summer
2023-10-20 05:00 | 2023-10-20 06:00 | Winter | FALSE | summer
2023-10-20 06:00 | 2023-10-20 07:00 | Winter | FALSE | summer
2023-10-20 07:00 | 2023-10-20 08:00 | Winter | FALSE | summer
2023-10-20 08:00 | 2023-10-20 09:00 | Winter | FALSE | summer
2023-10-20 09:00 | 2023-10-20 10:00 | Winter | FALSE | summer
2023-10-20 10:00 | 2023-10-20 11:00 | Winter | FALSE | summer
2023-10-20 11:00 | 2023-10-20 12:00 | Winter | FALSE | summer
2023-10-20 12:00 | 2023-10-20 13:00 | Winter | FALSE | summer
2023-10-20 13:00 | 2023-10-20 14:00 | Winter | FALSE | summer
2023-10-20 14:00 | 2023-10-20 15:00 | Winter | FALSE | summer
2023-10-20 15:00 | 2023-10-20 16:00 | Winter | FALSE | summer
2023-10-20 16:00 | 2023-10-20 17:00 | Winter | TRUE | summer
2023-10-20 17:00 | 2023-10-20 18:00 | Winter | TRUE | summer
2023-10-20 18:00 | 2023-10-20 19:00 | Winter | TRUE | summer
2023-10-20 19:00 | 2023-10-20 20:00 | Winter | TRUE | summer
2023-10-20 20:00 | 2023-10-20 21:00 | Winter | TRUE | summer
2023-10-20 21:00 | 2023-10-20 22:00 | Winter | FALSE | summer
2023-10-20 22:00 | 2023-10-20 23:00 | Winter | FALSE | summer
2023-10-20 23:00 | 2023-10-21 | Winter | FALSE | summer
2023-10-21 | 2023-10-21 01:00 | Winter | FALSE | summer
2023-10-21 01:00 | 2023-10-21 02:00 | Winter | FALSE | summer
2023-10-21 02:00 | 2023-10-21 03:00 | Winter | FALSE | summer
2023-10-21 03:00 | 2023-10-21 04:00 | Winter | FALSE | summer
2023-10-21 04:00 | 2023-10-21 05:00 | Winter | FALSE | summer
2023-10-21 05:00 | 2023-10-21 06:00 | Winter | FALSE | summer
2023-10-21 06:00 | 2023-10-21 07:00 | Winter | FALSE | summer
2023-10-21 07:00 | 2023-10-21 08:00 | Winter | FALSE | summer
2023-10-21 08:00 | 2023-10-21 09:00 | Winter | FALSE | summer
2023-10-21 09:00 | 2023-10-21 10:00 | Winter | FALSE | summer
2023-10-21 10:00 | 2023-10-21 11:00 | Winter | FALSE | summer
2023-10-21 11:00 | 2023-10-21 12:00 | Winter | FALSE | summer
2023-10-21 12:00 | 2023-10-21 13:00 | Winter | FALSE | summer
2023-10-21 13:00 | 2023-10-21 14:00 | Winter | FALSE | summer
2023-10-21 14:00 | 2023-10-21 15:00 | Winter | FALSE | summer
2023-10-21 15:00 | 2023-10-21 16:00 | Winter | FALSE | summer
2023-10-21 16:00 | 2023-10-21 17:00 | Winter | TRUE | summer
2023-10-21 17:00 | 2023-10-21 18:00 | Winter | TRUE | summer
2023-10-21 18:00 | 2023-10-21 19:00 | Winter | TRUE | summer
2023-10-21 19:00 | 2023-10-21 20:00 | Winter | TRUE | summer
2023-10-21 20:00 | 2023-10-21 21:00 | Winter | TRUE | summer
2023-10-21 21:00 | 2023-10-21 22:00 | Winter | FALSE | summer
2023-10-21 22:00 | 2023-10-21 23:00 | Winter | FALSE | summer
2023-10-21 23:00 | 2023-10-22 | Winter | FALSE | summer
2023-10-22 | 2023-10-22 01:00 | Winter | FALSE | summer
2023-10-22 01:00 | 2023-10-22 02:00 | Winter | FALSE | summer
2023-10-22 02:00 | 2023-10-22 03:00 | Winter | FALSE | summer
2023-10-22 03:00 | 2023-10-22 04:00 | Winter | FALSE | summer
2023-10-22 04:00 | 2023-10-22 05:00 | Winter | FALSE | summer
2023-10-22 05:00 | 2023-10-22 06:00 | Winter | FALSE | summer
2023-10-22 06:00 | 2023-10-22 07:00 | Winter | FALSE | summer
2023-10-22 07:00 | 2023-10-22 08:00 | Winter | FALSE | summer
2023-10-22 08:00 | 2023-10-22 09:00 | Winter | FALSE | summer
2023-10-22 09:00 | 2023-10-22 10:00 | Winter | FALSE | summer
2023-10-22 10:00 | 2023-10-22 11:00 | Winter | FALSE | summer
2023-10-22 11:00 | 2023-10-22 12:00 | Winter | FALSE | summer
2023-10-22 12:00 | 2023-10-22 13:00 | Winter | FALSE | summer
2023-10-22 13:00 | 2023-10-22 14:00 | Winter | FALSE | summer
2023-10-22 14:00 | 2023-10-22 15:00 | Winter | FALSE | summer
2023-10-22 15:00 | 2023-10-22 16:00 | Winter | FALSE | summer
2023-10-22 16:00 | 2023-10-22 17:00 | Winter | TRUE | summer
2023-10-22 17:00 | 2023-10-22 18:00 | Winter | TRUE | summer
2023-10-22 18:00 | 2023-10-22 19:00 | Winter | TRUE | summer
2023-10-22 19:00 | 2023-10-22 20:00 | Winter | TRUE | summer
2023-10-22 20:00 | 2023-10-22 21:00 | Winter | TRUE | summer
2023-10-22 21:00 | 2023-10-22 22:00 | Winter | FALSE | summer
2023-10-22 22:00 | 2023-10-22 23:00 | Winter | FALSE | summer
2023-10-22 23:00 | 2023-10-23 | Winter | FALSE | summer
2023-10-23 | 2023-10-23 01:00 | Winter | FALSE | summer
2023-10-23 01:00 | 2023-10-23 02:00 | Winter | FALSE | summer
2023-10-23 02:00 | 2023-10-23 03:00 | Winter | FALSE | summer
2023-10-23 03:00 | 2023-10-23 04:00 | Winter | FALSE | summer
2023-10-23 04:00 | 2023-10-23 05:00 | Winter | FALSE | summer
2023-10-23 05:00 | 2023-10-23 06:00 | Winter | FALSE | summer
2023-10-23 06:00 | 2023-10-23 07:00 | Winter | FALSE | summer
2023-10-23 07:00 | 2023-10-23 08:00 | Winter | FALSE | summer
2023-10-23 08:00 | 2023-10-23 09:00 | Winter | FALSE | summer
2023-10-23 09:00 | 2023-10-23 10:00 | Winter | FALSE | summer
2023-10-23 10:00 | 2023-10-23 11:00 | Winter | FALSE | summer
2023-10-23 11:00 | 2023-10-23 12:00 | Winter | FALSE | summer
2023-10-23 12:00 | 2023-10-23 13:00 | Winter | FALSE | summer
2023-10-23 13:00 | 2023-10-23 14:00 | Winter | FALSE | summer
2023-10-23 14:00 | 2023-10-23 15:00 | Winter | FALSE | summer
2023-10-23 15:00 | 2023-10-23 16:00 | Winter | FALSE | summer
2023-10-23 16:00 | 2023-10-23 17:00 | Winter | TRUE | summer
2023-10-23 17:00 | 2023-10-23 18:00 | Winter | TRUE | summer
2023-10-23 18:00 | 2023-10-23 19:00 | Winter | TRUE | summer
2023-10-23 19:00 | 2023-10-23 20:00 | Winter | TRUE | summer
2023-10-23 20:00 | 2023-10-23 21:00 | Winter | TRUE | summer
2023-10-23 21:00 | 2023-10-23 22:00 | Winter | FALSE | summer
2023-10-23 22:00 | 2023-10-23 23:00 | Winter | FALSE | summer
2023-10-23 23:00 | 2023-10-24 | Winter | FALSE | summer
2023-10-24 | 2023-10-24 01:00 | Winter | FALSE | summer
2023-10-24 01:00 | 2023-10-24 02:00 | Winter | FALSE | summer
2023-10-24 02:00 | 2023-10-24 03:00 | Winter | FALSE | summer
2023-10-24 03:00 | 2023-10-24 04:00 | Winter | FALSE | summer
2023-10-24 04:00 | 2023-10-24 05:00 | Winter | FALSE | summer
2023-10-24 05:00 | 2023-10-24 06:00 | Winter | FALSE | summer
2023-10-24 06:00 | 2023-10-24 07:00 | Winter | FALSE | summer
2023-10-24 07:00 | 2023-10-24 08:00 | Winter | FALSE | summer
2023-10-24 08:00 | 2023-10-24 09:00 | Winter | FALSE | summer
2023-10-24 09:00 | 2023-10-24 10:00 | Winter | FALSE | summer
2023-10-24 10:00 | 2023-10-24 11:00 | Winter | FALSE | summer
2023-10-24 11:00 | 2023-10-24 12:00 | Winter | FALSE | summer
2023-10-24 12:00 | 2023-10-24 13:00 | Winter | FALSE | summer
2023-10-24 13:00 | 2023-10-24 14:00 | Winter | FALSE | summer
2023-10-24 14:00 | 2023-10-24 15:00 | Winter | FALSE | summer
2023-10-24 15:00 | 2023-10-24 16:00 | Winter | FALSE | summer
2023-10-24 16:00 | 2023-10-24 17:00 | Winter | TRUE | summer
2023-10-24 17:00 | 2023-10-24 18:00 | Winter | TRUE | summer
2023-10-24 18:00 | 2023-10-24 19:00 | Winter | TRUE | summer
2023-10-24 19:00 | 2023-10-24 20:00 | Winter | TRUE | summer
2023-10-24 20:00 | 2023-10-24 21:00 | Winter | TRUE | summer
2023-10-24 21:00 | 2023-10-24 22:00 | Winter | FALSE | summer
2023-10-24 22:00 | 2023-10-24 23:00 | Winter | FALSE | summer
2023-10-24 23:00 | 2023-10-25 | Winter | FALSE | summer
2023-10-25 | 2023-10-25 01:00 | Winter | FALSE | summer
2023-10-25 01:00 | 2023-10-25 02:00 | Winter | FALSE | summer
2023-10-25 02:00 | 2023-10-25 03:00 | Winter | FALSE | summer
2023-10-25 03:00 | 2023-10-25 04:00 | Winter | FALSE | summer
2023-10-25 04:00 | 2023-10-25 05:00 | Winter | FALSE | summer
2023-10-25 05:00 | 2023-10-25 06:00 | Winter | FALSE | summer
2023-10-25 06:00 | 2023-10-25 07:00 | Winter | FALSE | summer
2023-10-25 07:00 | 2023-10-25 08:00 | Winter | FALSE | summer
2023-10-25 08:00 | 2023-10-25 09:00 | Winter | FALSE | summer
2023-10-25 09:00 | 2023-10-25 10:00 | Winter | FALSE | summer
2023-10-25 10:00 | 2023-10-25 11:00 | Winter | FALSE | summer
2023-10-25 11:00 | 2023-10-25 12:00 | Winter | FALSE | summer
2023-10-25 12:00 | 2023-10-25 13:00 | Winter | FALSE | summer
2023-10-25 13:00 | 2023-10-25 14:00 | Winter | FALSE | summer
2023-10-25 14:00 | 2023-10-25 15:00 | Winter | FALSE | summer
2023-10-25 15:00 | 2023-10-25 16:00 | Winter | FALSE | summer
2023-10-25 16:00 | 2023-10-25 17:00 | Winter | TRUE | summer
2023-10-25 17:00 | 2023-10-25 18:00 | Winter | TRUE | summer
2023-10-25 18:00 | 2023-10-25 19:00 | Winter | TRUE | summer
2023-10-25 19:00 | 2023-10-25 20:00 | Winter | TRUE | summer
2023-10-25 20:00 | 2023-10-25 21:00 | Winter | TRUE | summer
2023-10-25 21:00 | 2023-10-25 22:00 | Winter | FALSE | summer
2023-10-25 22:00 | 2023-10-25 23:00 | Winter | FALSE | summer
2023-10-25 23:00 | 2023-10-26 | Winter | FALSE | summer
2023-10-26 | 2023-10-26 01:00 | Winter | FALSE | summer
2023-10-26 01:00 | 2023-10-26 02:00 | Winter | FALSE | summer
2023-10-26 02:00 | 2023-10-26 03:00 | Winter | FALSE | summer
2023-10-26 03:00 | 2023-10-26 04:00 | Winter | FALSE | summer
2023-10-26 04:00 | 2023-10-26 05:00 | Winter | FALSE | summer
2023-10-26 05:00 | 2023-10-26 06:00 | Winter | FALSE | summer
2023-10-26 06:00 | 2023-10-26 07:00 | Winter | FALSE | summer
2023-10-26 07:00 | 2023-10-26 08:00 | Winter | FALSE | summer
2023-10-26 08:00 | 2023-10-26 09:00 | Winter | FALSE | summer
2023-10-26 09:00 | 2023-10-26 10:00 | Winter | FALSE | summer
2023-10-26 10:00 | 2023-10-26 11:00 | Winter | FALSE | summer
2023-10-26 11:00 | 2023-10-26 12:00 | Winter | FALSE | summer
2023-10-26 12:00 | 2023-10-26 13:00 | Winter | FALSE | summer
2023-10-26 13:00 | 2023-10-26 14:00 | Winter | FALSE | summer
2023-10-26 14:00 | 2023-10-26 15:00 | Winter | FALSE | summer
2023-10-26 15:00 | 2023-10-26 16:00 | Winter | FALSE | summer
2023-10-26 16:00 | 2023-10-26 17:00 | Winter | TRUE | summer
2023-10-26 17:00 | 2023-10-26 18:00 | Winter | TRUE | summer
2023-10-26 18:00 | 2023-10-26 19:00 | Winter | TRUE | summer
2023-10-26 19:00 | 2023-10-26 20:00 | Winter | TRUE | summer
2023-10-26 20:00 | 2023-10-26 21:00 | Winter | TRUE | summer
2023-10-26 21:00 | 2023-10-26 22:00 | Winter | FALSE | summer
2023-10-26 22:00 | 2023-10-26 23:00 | Winter | FALSE | summer
2023-10-26 23:00 | 2023-10-27 | Winter | FALSE | summer
2023-10-27 | 2023-10-27 01:00 | Winter | FALSE | summer
2023-10-27 01:00 | 2023-10-27 02:00 | Winter | FALSE | summer
2023-10-27 02:00 | 2023-10-27 03:00 | Winter | FALSE | summer
2023-10-27 03:00 | 2023-10-27 04:00 | Winter | FALSE | summer
2023-10-27 04:00 | 2023-10-27 05:00 | Winter | FALSE | summer
2023-10-27 05:00 | 2023-10-27 06:00 | Winter | FALSE | summer
2023-10-27 06:00 | 2023-10-27 07:00 | Winter | FALSE | summer
2023-10-27 07:00 | 2023-10-27 08:00 | Winter | FALSE | summer
2023-10-27 08:00 | 2023-10-27 09:00 | Winter | FALSE | summer
2023-10-27 09:00 | 2023-10-27 10:00 | Winter | FALSE | summer
2023-10-27 10:00 | 2023-10-27 11:00 | Winter | FALSE | summer
2023-10-27 11:00 | 2023-10-27 12:00 | Winter | FALSE | summer
2023-10-27 12:00 | 2023-10-27 13:00 | Winter | FALSE | summer
2023-10-27 13:00 | 2023-10-27 14:00 | Winter | FALSE | summer
2023-10-27 14:00 | 2023-10-27 15:00 | Winter | FALSE | summer
2023-10-27 15:00 | 2023-10-27 16:00 | Winter | FALSE | summer
2023-10-27 16:00 | 2023-10-27 17:00 | Winter | TRUE | summer
2023-10-27 17:00 | 2023-10-27 18:00 | Winter | TRUE | summer
2023-10-27 18:00 | 2023-10-27 19:00 | Winter | TRUE | summer
2023-10-27 19:00 | 2023-10-27 20:00 | Winter | TRUE | summer
2023-10-27 20:00 | 2023-10-27 21:00 | Winter | TRUE | summer
2023-10-27 21:00 | 2023-10-27 22:00 | Winter | FALSE | summer
2023-10-27 22:00 | 2023-10-27 23:00 | Winter | FALSE | summer
2023-10-27 23:00 | 2023-10-28 | Winter | FALSE | summer
2023-10-28 | 2023-10-28 01:00 | Winter | FALSE | summer
2023-10-28 01:00 | 2023-10-28 02:00 | Winter | FALSE | summer
2023-10-28 02:00 | 2023-10-28 03:00 | Winter | FALSE | summer
2023-10-28 03:00 | 2023-10-28 04:00 | Winter | FALSE | summer
2023-10-28 04:00 | 2023-10-28 05:00 | Winter | FALSE | summer
2023-10-28 05:00 | 2023-10-28 06:00 | Winter | FALSE | summer
2023-10-28 06:00 | 2023-10-28 07:00 | Winter | FALSE | summer
2023-10-28 07:00 | 2023-10-28 08:00 | Winter | FALSE | summer
2023-10-28 08:00 | 2023-10-28 09:00 | Winter | FALSE | summer
2023-10-28 09:00 | 2023-10-28 10:00 | Winter | FALSE | summer
2023-10-28 10:00 | 2023-10-28 11:00 | Winter | FALSE | summer
2023-10-28 11:00 | 2023-10-28 12:00 | Winter | FALSE | summer
2023-10-28 12:00 | 2023-10-28 13:00 | Winter | FALSE | summer
2023-10-28 13:00 | 2023-10-28 14:00 | Winter | FALSE | summer
2023-10-28 14:00 | 2023-10-28 15:00 | Winter | FALSE | summer
2023-10-28 15:00 | 2023-10-28 16:00 | Winter | FALSE | summer
2023-10-28 16:00 | 2023-10-28 17:00 | Winter | TRUE | summer
2023-10-28 17:00 | 2023-10-28 18:00 | Winter | TRUE | summer
2023-10-28 18:00 | 2023-10-28 19:00 | Winter | TRUE | summer
2023-10-28 19:00 | 2023-10-28 20:00 | Winter | TRUE | summer
2023-10-28 20:00 | 2023-10-28 21:00 | Winter | TRUE | summer
2023-10-28 21:00 | 2023-10-28 22:00 | Winter | FALSE | summer
2023-10-28 22:00 | 2023-10-28 23:00 | Winter | FALSE | summer
2023-10-28 23:00 | 2023-10-29 | Winter | FALSE | summer
2023-10-29 | 2023-10-29 01:00 | Winter | FALSE | summer
2023-10-29 01:00 | 2023-10-29 02:00 | Winter | FALSE | summer
2023-10-29 02:00 | 2023-10-29 03:00 | Winter | FALSE | summer
2023-10-29 03:00 | 2023-10-29 04:00 | Winter | FALSE | summer
2023-10-29 04:00 | 2023-10-29 05:00 | Winter | FALSE | summer
2023-10-29 05:00 | 2023-10-29 06:00 | Winter | FALSE | summer
2023-10-29 06:00 | 2023-10-29 07:00 | Winter | FALSE | summer
2023-10-29 07:00 | 2023-10-29 08:00 | Winter | FALSE | summer
2023-10-29 08:00 | 2023-10-29 09:00 | Winter | FALSE | summer
2023-10-29 09:00 | 2023-10-29 10:00 | Winter | FALSE | summer
2023-10-29 10:00 | 2023-10-29 11:00 | Winter | FALSE | summer
2023-10-29 11:00 | 2023-10-29 12:00 | Winter | FALSE | summer
2023-10-29 12:00 | 2023-10-29 13:00 | Winter | FALSE | summer
2023-10-29 13:00 | 2023-10-29 14:00 | Winter | FALSE | summer
2023-10-29 14:00 | 2023-10-29 15:00 | Winter | FALSE | summer
2023-10-29 15:00 | 2023-10-29 16:00 | Winter | FALSE | summer
2023-10-29 16:00 | 2023-10-29 17:00 | Winter | TRUE | summer
2023-10-29 17:00 | 2023-10-29 18:00 | Winter | TRUE | summer
2023-10-29 18:00 | 2023-10-29 19:00 | Winter | TRUE | summer
2023-10-29 19:00 | 2023-10-29 20:00 | Winter | TRUE | summer
2023-10-29 20:00 | 2023-10-29 21:00 | Winter | TRUE | summer
2023-10-29 21:00 | 2023-10-29 22:00 | Winter | FALSE | summer
2023-10-29 22:00 | 2023-10-29 23:00 | Winter | FALSE | summer
2023-10-29 23:00 | 2023-10-30 | Winter | FALSE | summer
2023-10-30 | 2023-10-30 01:00 | Winter | FALSE | summer
2023-10-30 01:00 | 2023-10-30 02:00 | Winter | FALSE | summer
2023-10-30 02:00 | 2023-10-30 03:00 | Winter | FALSE | summer
2023-10-30 03:00 | 2023-10-30 04:00 | Winter | FALSE | summer
2023-10-30 04:00 | 2023-10-30 05:00 | Winter | FALSE | summer
2023-10-30 05:00 | 2023-10-30 06:00 | Winter | FALSE | summer
2023-10-30 06:00 | 2023-10-30 07:00 | Winter | FALSE | summer
2023-10-30 07:00 | 2023-10-30 08:00 | Winter | FALSE | summer
2023-10-30 08:00 | 2023-10-30 09:00 | Winter | FALSE | summer
2023-10-30 09:00 | 2023-10-30 10:00 | Winter | FALSE | summer
2023-10-30 10:00 | 2023-10-30 11:00 | Winter | FALSE | summer
2023-10-30 11:00 | 2023-10-30 12:00 | Winter | FALSE | summer
2023-10-30 12:00 | 2023-10-30 13:00 | Winter | FALSE | summer
2023-10-30 13:00 | 2023-10-30 14:00 | Winter | FALSE | summer
2023-10-30 14:00 | 2023-10-30 15:00 | Winter | FALSE | summer
2023-10-30 15:00 | 2023-10-30 16:00 | Winter | FALSE | summer
2023-10-30 16:00 | 2023-10-30 17:00 | Winter | TRUE | summer
2023-10-30 17:00 | 2023-10-30 18:00 | Winter | TRUE | summer
2023-10-30 18:00 | 2023-10-30 19:00 | Winter | TRUE | summer
2023-10-30 19:00 | 2023-10-30 20:00 | Winter | TRUE | summer
2023-10-30 20:00 | 2023-10-30 21:00 | Winter | TRUE | summer
2023-10-30 21:00 | 2023-10-30 22:00 | Winter | FALSE | summer
2023-10-30 22:00 | 2023-10-30 23:00 | Winter | FALSE | summer
2023-10-30 23:00 | 2023-10-31 | Winter | FALSE | summer
2023-10-31 | 2023-10-31 01:00 | Winter | FALSE | summer
2023-10-31 01:00 | 2023-10-31 02:00 | Winter | FALSE | summer
2023-10-31 02:00 | 2023-10-31 03:00 | Winter | FALSE | summer
2023-10-31 03:00 | 2023-10-31 04:00 | Winter | FALSE | summer
2023-10-31 04:00 | 2023-10-31 05:00 | Winter | FALSE | summer
2023-10-31 05:00 | 2023-10-31 06:00 | Winter | FALSE | summer
2023-10-31 06:00 | 2023-10-31 07:00 | Winter | FALSE | summer
2023-10-31 07:00 | 2023-10-31 08:00 | Winter | FALSE | summer
2023-10-31 08:00 | 2023-10-31 09:00 | Winter | FALSE | summer
2023-10-31 09:00 | 2023-10-31 10:00 | Winter | FALSE | summer
2023-10-31 10:00 | 2023-10-31 11:00 | Winter | FALSE | summer
2023-10-31 11:00 | 2023-10-31 12:00 | Winter | FALSE | summer
2023-10-31 12:00 | 2023-10-31 13:00 | Winter | FALSE | summer
2023-10-31 13:00 | 2023-10-31 14:00 | Winter | FALSE | summer
2023-10-31 14:00 | 2023-10-31 15:00 | Winter | FALSE | summer
2023-10-31 15:00 | 2023-10-31 16:00 | Winter | FALSE | summer
2023-10-31 16:00 | 2023-10-31 17:00 | Winter | TRUE | summer
2023-10-31 17:00 | 2023-10-31 18:00 | Winter | TRUE | summer
2023-10-31 18:00 | 2023-10-31 19:00 | Winter | TRUE | summer
2023-10-31 19:00 | 2023-10-31 20:00 | Winter | TRUE | summer
2023-10-31 20:00 | 2023-10-31 21:00 | Winter | TRUE | summer
2023-10-31 21:00 | 2023-10-31 22:00 | Winter | FALSE | summer
2023-10-31 22:00 | 2023-10-31 23:00 | Winter | FALSE | summer
2023-10-31 23:00 | 2023-11-01 | Winter | FALSE | summer
2023-11-01 | 2023-11-01 01:00 | Winter | FALSE | nonsummer
2023-11-01 01:00 | 2023-11-01 02:00 | Winter | FALSE | nonsummer
2023-11-01 02:00 | 2023-11-01 03:00 | Winter | FALSE | nonsummer
2023-11-01 03:00 | 2023-11-01 04:00 | Winter | FALSE | nonsummer
2023-11-01 04:00 | 2023-11-01 05:00 | Winter | FALSE | nonsummer
2023-11-01 05:00 | 2023-11-01 06:00 | Winter | FALSE | nonsummer
2023-11-01 06:00 | 2023-11-01 07:00 | Winter | FALSE | nonsummer
2023-11-01 07:00 | 2023-11-01 08:00 | Winter | FALSE | nonsummer
2023-11-01 08:00 | 2023-11-01 09:00 | Winter | FALSE | nonsummer
2023-11-01 09:00 | 2023-11-01 10:00 | Winter | FALSE | nonsummer
2023-11-01 10:00 | 2023-11-01 11:00 | Winter | FALSE | nonsummer
2023-11-01 11:00 | 2023-11-01 12:00 | Winter | FALSE | nonsummer
2023-11-01 12:00 | 2023-11-01 13:00 | Winter | FALSE | nonsummer
2023-11-01 13:00 | 2023-11-01 14:00 | Winter | FALSE | nonsummer
2023-11-01 14:00 | 2023-11-01 15:00 | Winter | FALSE | nonsummer
2023-11-01 15:00 | 2023-11-01 16:00 | Winter | FALSE | nonsummer
2023-11-01 16:00 | 2023-11-01 17:00 | Winter | TRUE | nonsummer
2023-11-01 17:00 | 2023-11-01 18:00 | Winter | TRUE | nonsummer
2023-11-01 18:00 | 2023-11-01 19:00 | Winter | TRUE | nonsummer
2023-11-01 19:00 | 2023-11-01 20:00 | Winter | TRUE | nonsummer
2023-11-01 20:00 | 2023-11-01 21:00 | Winter | TRUE | nonsummer
2023-11-01 21:00 | 2023-11-01 22:00 | Winter | FALSE | nonsummer
2023-11-01 22:00 | 2023-11-01 23:00 | Winter | FALSE | nonsummer
2023-11-01 23:00 | 2023-11-02 | Winter | FALSE | nonsummer
2023-11-02 | 2023-11-02 01:00 | Winter | FALSE | nonsummer
2023-11-02 01:00 | 2023-11-02 02:00 | Winter | FALSE | nonsummer
2023-11-02 02:00 | 2023-11-02 03:00 | Winter | FALSE | nonsummer
2023-11-02 03:00 | 2023-11-02 04:00 | Winter | FALSE | nonsummer
2023-11-02 04:00 | 2023-11-02 05:00 | Winter | FALSE | nonsummer
2023-11-02 05:00 | 2023-11-02 06:00 | Winter | FALSE | nonsummer
2023-11-02 06:00 | 2023-11-02 07:00 | Winter | FALSE | nonsummer
2023-11-02 07:00 | 2023-11-02 08:00 | Winter | FALSE | nonsummer
2023-11-02 08:00 | 2023-11-02 09:00 | Winter | FALSE | nonsummer
2023-11-02 09:00 | 2023-11-02 10:00 | Winter | FALSE | nonsummer
2023-11-02 10:00 | 2023-11-02 11:00 | Winter | FALSE | nonsummer
2023-11-02 11:00 | 2023-11-02 12:00 | Winter | FALSE | nonsummer
2023-11-02 12:00 | 2023-11-02 13:00 | Winter | FALSE | nonsummer
2023-11-02 13:00 | 2023-11-02 14:00 | Winter | FALSE | nonsummer
2023-11-02 14:00 | 2023-11-02 15:00 | Winter | FALSE | nonsummer
2023-11-02 15:00 | 2023-11-02 16:00 | Winter | FALSE | nonsummer
2023-11-02 16:00 | 2023-11-02 17:00 | Winter | TRUE | nonsummer
2023-11-02 17:00 | 2023-11-02 18:00 | Winter | TRUE | nonsummer
2023-11-02 18:00 | 2023-11-02 19:00 | Winter | TRUE | nonsummer
2023-11-02 19:00 | 2023-11-02 20:00 | Winter | TRUE | nonsummer
2023-11-02 20:00 | 2023-11-02 21:00 | Winter | TRUE | nonsummer
2023-11-02 21:00 | 2023-11-02 22:00 | Winter | FALSE | nonsummer
2023-11-02 22:00 | 2023-11-02 23:00 | Winter | FALSE | nonsummer
2023-11-02 23:00 | 2023-11-03 | Winter | FALSE | nonsummer
2023-11-03 | 2023-11-03 01:00 | Winter | FALSE | nonsummer
2023-11-03 01:00 | 2023-11-03 02:00 | Winter | FALSE | nonsummer
2023-11-03 02:00 | 2023-11-03 03:00 | Winter | FALSE | nonsummer
2023-11-03 03:00 | 2023-11-03 04:00 | Winter | FALSE | nonsummer
2023-11-03 04:00 | 2023-11-03 05:00 | Winter | FALSE | nonsummer
2023-11-03 05:00 | 2023-11-03 06:00 | Winter | FALSE | nonsummer
2023-11-03 06:00 | 2023-11-03 07:00 | Winter | FALSE | nonsummer
2023-11-03 07:00 | 2023-11-03 08:00 | Winter | FALSE | nonsummer
2023-11-03 08:00 | 2023-11-03 09:00 | Winter | FALSE | nonsummer
2023-11-03 09:00 | 2023-11-03 10:00 | Winter | FALSE | nonsummer
2023-11-03 10:00 | 2023-11-03 11:00 | Winter | FALSE | nonsummer
2023-11-03 11:00 | 2023-11-03 12:00 | Winter | FALSE | nonsummer
2023-11-03 12:00 | 2023-11-03 13:00 | Winter | FALSE | nonsummer
2023-11-03 13:00 | 2023-11-03 14:00 | Winter | FALSE | nonsummer
2023-11-03 14:00 | 2023-11-03 15:00 | Winter | FALSE | nonsummer
2023-11-03 15:00 | 2023-11-03 16:00 | Winter | FALSE | nonsummer
2023-11-03 16:00 | 2023-11-03 17:00 | Winter | TRUE | nonsummer
2023-11-03 17:00 | 2023-11-03 18:00 | Winter | TRUE | nonsummer
2023-11-03 18:00 | 2023-11-03 19:00 | Winter | TRUE | nonsummer
2023-11-03 19:00 | 2023-11-03 20:00 | Winter | TRUE | nonsummer
2023-11-03 20:00 | 2023-11-03 21:00 | Winter | TRUE | nonsummer
2023-11-03 21:00 | 2023-11-03 22:00 | Winter | FALSE | nonsummer
2023-11-03 22:00 | 2023-11-03 23:00 | Winter | FALSE | nonsummer
2023-11-03 23:00 | 2023-11-04 | Winter | FALSE | nonsummer
2023-11-04 | 2023-11-04 01:00 | Winter | FALSE | nonsummer
2023-11-04 01:00 | 2023-11-04 02:00 | Winter | FALSE | nonsummer
2023-11-04 02:00 | 2023-11-04 03:00 | Winter | FALSE | nonsummer
2023-11-04 03:00 | 2023-11-04 04:00 | Winter | FALSE | nonsummer
2023-11-04 04:00 | 2023-11-04 05:00 | Winter | FALSE | nonsummer
2023-11-04 05:00 | 2023-11-04 06:00 | Winter | FALSE | nonsummer
2023-11-04 06:00 | 2023-11-04 07:00 | Winter | FALSE | nonsummer
2023-11-04 07:00 | 2023-11-04 08:00 | Winter | FALSE | nonsummer
2023-11-04 08:00 | 2023-11-04 09:00 | Winter | FALSE | nonsummer
2023-11-04 09:00 | 2023-11-04 10:00 | Winter | FALSE | nonsummer
2023-11-04 10:00 | 2023-11-04 11:00 | Winter | FALSE | nonsummer
2023-11-04 11:00 | 2023-11-04 12:00 | Winter | FALSE | nonsummer
2023-11-04 12:00 | 2023-11-04 13:00 | Winter | FALSE | nonsummer
2023-11-04 13:00 | 2023-11-04 14:00 | Winter | FALSE | nonsummer
2023-11-04 14:00 | 2023-11-04 15:00 | Winter | FALSE | nonsummer
2023-11-04 15:00 | 2023-11-04 16:00 | Winter | FALSE | nonsummer
2023-11-04 16:00 | 2023-11-04 17:00 | Winter | TRUE | nonsummer
2023-11-04 17:00 | 2023-11-04 18:00 | Winter | TRUE | nonsummer
2023-11-04 18:00 | 2023-11-04 19:00 | Winter | TRUE | nonsummer
2023-11-04 19:00 | 2023-11-04 20:00 | Winter | TRUE | nonsummer
2023-11-04 20:00 | 2023-11-04 21:00 | Winter | TRUE | nonsummer
2023-11-04 21:00 | 2023-11-04 22:00 | Winter | FALSE | nonsummer
2023-11-04 22:00 | 2023-11-04 23:00 | Winter | FALSE | nonsummer
2023-11-04 23:00 | 2023-11-05 | Winter | FALSE | nonsummer
2023-11-05 | 2023-11-05 01:00 | Winter | FALSE | nonsummer
2023-11-05 01:00 | 2023-11-05 02:00 | Winter | FALSE | nonsummer
2023-11-05 02:00 | 2023-11-05 03:00 | Winter | FALSE | nonsummer
2023-11-05 03:00 | 2023-11-05 04:00 | Winter | FALSE | nonsummer
2023-11-05 04:00 | 2023-11-05 05:00 | Winter | FALSE | nonsummer
2023-11-05 05:00 | 2023-11-05 06:00 | Winter | FALSE | nonsummer
2023-11-05 06:00 | 2023-11-05 07:00 | Winter | FALSE | nonsummer
2023-11-05 07:00 | 2023-11-05 08:00 | Winter | FALSE | nonsummer
2023-11-05 08:00 | 2023-11-05 09:00 | Winter | FALSE | nonsummer
2023-11-05 09:00 | 2023-11-05 10:00 | Winter | FALSE | nonsummer
2023-11-05 10:00 | 2023-11-05 11:00 | Winter | FALSE | nonsummer
2023-11-05 11:00 | 2023-11-05 12:00 | Winter | FALSE | nonsummer
2023-11-05 12:00 | 2023-11-05 13:00 | Winter | FALSE | nonsummer
2023-11-05 13:00 | 2023-11-05 14:00 | Winter | FALSE | nonsummer
2023-11-05 14:00 | 2023-11-05 15:00 | Winter | FALSE | nonsummer
2023-11-05 15:00 | 2023-11-05 16:00 | Winter | FALSE | nonsummer
2023-11-05 16:00 | 2023-11-05 17:00 | Winter | TRUE | nonsummer
2023-11-05 17:00 | 2023-11-05 18:00 | Winter | TRUE | nonsummer
2023-11-05 18:00 | 2023-11-05 19:00 | Winter | TRUE | nonsummer
2023-11-05 19:00 | 2023-11-05 20:00 | Winter | TRUE | nonsummer
2023-11-05 20:00 | 2023-11-05 21:00 | Winter | TRUE | nonsummer
2023-11-05 21:00 | 2023-11-05 22:00 | Winter | FALSE | nonsummer
2023-11-05 22:00 | 2023-11-05 23:00 | Winter | FALSE | nonsummer
2023-11-05 23:00 | 2023-11-06 | Winter | FALSE | nonsummer
2023-11-06 | 2023-11-06 01:00 | Winter | FALSE | nonsummer
2023-11-06 01:00 | 2023-11-06 02:00 | Winter | FALSE | nonsummer
2023-11-06 02:00 | 2023-11-06 03:00 | Winter | FALSE | nonsummer
2023-11-06 03:00 | 2023-11-06 04:00 | Winter | FALSE | nonsummer
2023-11-06 04:00 | 2023-11-06 05:00 | Winter | FALSE | nonsummer
2023-11-06 05:00 | 2023-11-06 06:00 | Winter | FALSE | nonsummer
2023-11-06 06:00 | 2023-11-06 07:00 | Winter | FALSE | nonsummer
2023-11-06 07:00 | 2023-11-06 08:00 | Winter | FALSE | nonsummer
2023-11-06 08:00 | 2023-11-06 09:00 | Winter | FALSE | nonsummer
2023-11-06 09:00 | 2023-11-06 10:00 | Winter | FALSE | nonsummer
2023-11-06 10:00 | 2023-11-06 11:00 | Winter | FALSE | nonsummer
2023-11-06 11:00 | 2023-11-06 12:00 | Winter | FALSE | nonsummer
2023-11-06 12:00 | 2023-11-06 13:00 | Winter | FALSE | nonsummer
2023-11-06 13:00 | 2023-11-06 14:00 | Winter | FALSE | nonsummer
2023-11-06 14:00 | 2023-11-06 15:00 | Winter | FALSE | nonsummer
2023-11-06 15:00 | 2023-11-06 16:00 | Winter | FALSE | nonsummer
2023-11-06 16:00 | 2023-11-06 17:00 | Winter | TRUE | nonsummer
2023-11-06 17:00 | 2023-11-06 18:00 | Winter | TRUE | nonsummer
2023-11-06 18:00 | 2023-11-06 19:00 | Winter | TRUE | nonsummer
2023-11-06 19:00 | 2023-11-06 20:00 | Winter | TRUE | nonsummer
2023-11-06 20:00 | 2023-11-06 21:00 | Winter | TRUE | nonsummer
2023-11-06 21:00 | 2023-11-06 22:00 | Winter | FALSE | nonsummer
2023-11-06 22:00 | 2023-11-06 23:00 | Winter | FALSE | nonsummer
2023-11-06 23:00 | 2023-11-07 | Winter | FALSE | nonsummer
2023-11-07 | 2023-11-07 01:00 | Winter | FALSE | nonsummer
2023-11-07 01:00 | 2023-11-07 02:00 | Winter | FALSE | nonsummer
2023-11-07 02:00 | 2023-11-07 03:00 | Winter | FALSE | nonsummer
2023-11-07 03:00 | 2023-11-07 04:00 | Winter | FALSE | nonsummer
2023-11-07 04:00 | 2023-11-07 05:00 | Winter | FALSE | nonsummer
2023-11-07 05:00 | 2023-11-07 06:00 | Winter | FALSE | nonsummer
2023-11-07 06:00 | 2023-11-07 07:00 | Winter | FALSE | nonsummer
2023-11-07 07:00 | 2023-11-07 08:00 | Winter | FALSE | nonsummer
2023-11-07 08:00 | 2023-11-07 09:00 | Winter | FALSE | nonsummer
2023-11-07 09:00 | 2023-11-07 10:00 | Winter | FALSE | nonsummer
2023-11-07 10:00 | 2023-11-07 11:00 | Winter | FALSE | nonsummer
2023-11-07 11:00 | 2023-11-07 12:00 | Winter | FALSE | nonsummer
2023-11-07 12:00 | 2023-11-07 13:00 | Winter | FALSE | nonsummer
2023-11-07 13:00 | 2023-11-07 14:00 | Winter | FALSE | nonsummer
2023-11-07 14:00 | 2023-11-07 15:00 | Winter | FALSE | nonsummer
2023-11-07 15:00 | 2023-11-07 16:00 | Winter | FALSE | nonsummer
2023-11-07 16:00 | 2023-11-07 17:00 | Winter | TRUE | nonsummer
2023-11-07 17:00 | 2023-11-07 18:00 | Winter | TRUE | nonsummer
2023-11-07 18:00 | 2023-11-07 19:00 | Winter | TRUE | nonsummer
2023-11-07 19:00 | 2023-11-07 20:00 | Winter | TRUE | nonsummer
2023-11-07 20:00 | 2023-11-07 21:00 | Winter | TRUE | nonsummer
2023-11-07 21:00 | 2023-11-07 22:00 | Winter | FALSE | nonsummer
2023-11-07 22:00 | 2023-11-07 23:00 | Winter | FALSE | nonsummer
2023-11-07 23:00 | 2023-11-08 | Winter | FALSE | nonsummer
2023-11-08 | 2023-11-08 01:00 | Winter | FALSE | nonsummer
2023-11-08 01:00 | 2023-11-08 02:00 | Winter | FALSE | nonsummer
2023-11-08 02:00 | 2023-11-08 03:00 | Winter | FALSE | nonsummer
2023-11-08 03:00 | 2023-11-08 04:00 | Winter | FALSE | nonsummer
2023-11-08 04:00 | 2023-11-08 05:00 | Winter | FALSE | nonsummer
2023-11-08 05:00 | 2023-11-08 06:00 | Winter | FALSE | nonsummer
2023-11-08 06:00 | 2023-11-08 07:00 | Winter | FALSE | nonsummer
2023-11-08 07:00 | 2023-11-08 08:00 | Winter | FALSE | nonsummer
2023-11-08 08:00 | 2023-11-08 09:00 | Winter | FALSE | nonsummer
2023-11-08 09:00 | 2023-11-08 10:00 | Winter | FALSE | nonsummer
2023-11-08 10:00 | 2023-11-08 11:00 | Winter | FALSE | nonsummer
2023-11-08 11:00 | 2023-11-08 12:00 | Winter | FALSE | nonsummer
2023-11-08 12:00 | 2023-11-08 13:00 | Winter | FALSE | nonsummer
2023-11-08 13:00 | 2023-11-08 14:00 | Winter | FALSE | nonsummer
2023-11-08 14:00 | 2023-11-08 15:00 | Winter | FALSE | nonsummer
2023-11-08 15:00 | 2023-11-08 16:00 | Winter | FALSE | nonsummer
2023-11-08 16:00 | 2023-11-08 17:00 | Winter | TRUE | nonsummer
2023-11-08 17:00 | 2023-11-08 18:00 | Winter | TRUE | nonsummer
2023-11-08 18:00 | 2023-11-08 19:00 | Winter | TRUE | nonsummer
2023-11-08 19:00 | 2023-11-08 20:00 | Winter | TRUE | nonsummer
2023-11-08 20:00 | 2023-11-08 21:00 | Winter | TRUE | nonsummer
2023-11-08 21:00 | 2023-11-08 22:00 | Winter | FALSE | nonsummer
2023-11-08 22:00 | 2023-11-08 23:00 | Winter | FALSE | nonsummer
2023-11-08 23:00 | 2023-11-09 | Winter | FALSE | nonsummer
2023-11-09 | 2023-11-09 01:00 | Winter | FALSE | nonsummer
2023-11-09 01:00 | 2023-11-09 02:00 | Winter | FALSE | nonsummer
2023-11-09 02:00 | 2023-11-09 03:00 | Winter | FALSE | nonsummer
2023-11-09 03:00 | 2023-11-09 04:00 | Winter | FALSE | nonsummer
2023-11-09 04:00 | 2023-11-09 05:00 | Winter | FALSE | nonsummer
2023-11-09 05:00 | 2023-11-09 06:00 | Winter | FALSE | nonsummer
2023-11-09 06:00 | 2023-11-09 07:00 | Winter | FALSE | nonsummer
2023-11-09 07:00 | 2023-11-09 08:00 | Winter | FALSE | nonsummer
2023-11-09 08:00 | 2023-11-09 09:00 | Winter | FALSE | nonsummer
2023-11-09 09:00 | 2023-11-09 10:00 | Winter | FALSE | nonsummer
2023-11-09 10:00 | 2023-11-09 11:00 | Winter | FALSE | nonsummer
2023-11-09 11:00 | 2023-11-09 12:00 | Winter | FALSE | nonsummer
2023-11-09 12:00 | 2023-11-09 13:00 | Winter | FALSE | nonsummer
2023-11-09 13:00 | 2023-11-09 14:00 | Winter | FALSE | nonsummer
2023-11-09 14:00 | 2023-11-09 15:00 | Winter | FALSE | nonsummer
2023-11-09 15:00 | 2023-11-09 16:00 | Winter | FALSE | nonsummer
2023-11-09 16:00 | 2023-11-09 17:00 | Winter | TRUE | nonsummer
2023-11-09 17:00 | 2023-11-09 18:00 | Winter | TRUE | nonsummer
2023-11-09 18:00 | 2023-11-09 19:00 | Winter | TRUE | nonsummer
2023-11-09 19:00 | 2023-11-09 20:00 | Winter | TRUE | nonsummer
2023-11-09 20:00 | 2023-11-09 21:00 | Winter | TRUE | nonsummer
2023-11-09 21:00 | 2023-11-09 22:00 | Winter | FALSE | nonsummer
2023-11-09 22:00 | 2023-11-09 23:00 | Winter | FALSE | nonsummer
2023-11-09 23:00 | 2023-11-10 | Winter | FALSE | nonsummer
2023-11-10 | 2023-11-10 01:00 | Winter | FALSE | nonsummer
2023-11-10 01:00 | 2023-11-10 02:00 | Winter | FALSE | nonsummer
2023-11-10 02:00 | 2023-11-10 03:00 | Winter | FALSE | nonsummer
2023-11-10 03:00 | 2023-11-10 04:00 | Winter | FALSE | nonsummer
2023-11-10 04:00 | 2023-11-10 05:00 | Winter | FALSE | nonsummer
2023-11-10 05:00 | 2023-11-10 06:00 | Winter | FALSE | nonsummer
2023-11-10 06:00 | 2023-11-10 07:00 | Winter | FALSE | nonsummer
2023-11-10 07:00 | 2023-11-10 08:00 | Winter | FALSE | nonsummer
2023-11-10 08:00 | 2023-11-10 09:00 | Winter | FALSE | nonsummer
2023-11-10 09:00 | 2023-11-10 10:00 | Winter | FALSE | nonsummer
2023-11-10 10:00 | 2023-11-10 11:00 | Winter | FALSE | nonsummer
2023-11-10 11:00 | 2023-11-10 12:00 | Winter | FALSE | nonsummer
2023-11-10 12:00 | 2023-11-10 13:00 | Winter | FALSE | nonsummer
2023-11-10 13:00 | 2023-11-10 14:00 | Winter | FALSE | nonsummer
2023-11-10 14:00 | 2023-11-10 15:00 | Winter | FALSE | nonsummer
2023-11-10 15:00 | 2023-11-10 16:00 | Winter | FALSE | nonsummer
2023-11-10 16:00 | 2023-11-10 17:00 | Winter | TRUE | nonsummer
2023-11-10 17:00 | 2023-11-10 18:00 | Winter | TRUE | nonsummer
2023-11-10 18:00 | 2023-11-10 19:00 | Winter | TRUE | nonsummer
2023-11-10 19:00 | 2023-11-10 20:00 | Winter | TRUE | nonsummer
2023-11-10 20:00 | 2023-11-10 21:00 | Winter | TRUE | nonsummer
2023-11-10 21:00 | 2023-11-10 22:00 | Winter | FALSE | nonsummer
2023-11-10 22:00 | 2023-11-10 23:00 | Winter | FALSE | nonsummer
2023-11-10 23:00 | 2023-11-11 | Winter | FALSE | nonsummer
2023-11-11 | 2023-11-11 01:00 | Winter | FALSE | nonsummer
2023-11-11 01:00 | 2023-11-11 02:00 | Winter | FALSE | nonsummer
2023-11-11 02:00 | 2023-11-11 03:00 | Winter | FALSE | nonsummer
2023-11-11 03:00 | 2023-11-11 04:00 | Winter | FALSE | nonsummer
2023-11-11 04:00 | 2023-11-11 05:00 | Winter | FALSE | nonsummer
2023-11-11 05:00 | 2023-11-11 06:00 | Winter | FALSE | nonsummer
2023-11-11 06:00 | 2023-11-11 07:00 | Winter | FALSE | nonsummer
2023-11-11 07:00 | 2023-11-11 08:00 | Winter | FALSE | nonsummer
2023-11-11 08:00 | 2023-11-11 09:00 | Winter | FALSE | nonsummer
2023-11-11 09:00 | 2023-11-11 10:00 | Winter | FALSE | nonsummer
2023-11-11 10:00 | 2023-11-11 11:00 | Winter | FALSE | nonsummer
2023-11-11 11:00 | 2023-11-11 12:00 | Winter | FALSE | nonsummer
2023-11-11 12:00 | 2023-11-11 13:00 | Winter | FALSE | nonsummer
2023-11-11 13:00 | 2023-11-11 14:00 | Winter | FALSE | nonsummer
2023-11-11 14:00 | 2023-11-11 15:00 | Winter | FALSE | nonsummer
2023-11-11 15:00 | 2023-11-11 16:00 | Winter | FALSE | nonsummer
2023-11-11 16:00 | 2023-11-11 17:00 | Winter | TRUE | nonsummer
2023-11-11 17:00 | 2023-11-11 18:00 | Winter | TRUE | nonsummer
2023-11-11 18:00 | 2023-11-11 19:00 | Winter | TRUE | nonsummer
2023-11-11 19:00 | 2023-11-11 20:00 | Winter | TRUE | nonsummer
2023-11-11 20:00 | 2023-11-11 21:00 | Winter | TRUE | nonsummer
2023-11-11 21:00 | 2023-11-11 22:00 | Winter | FALSE | nonsummer
2023-11-11 22:00 | 2023-11-11 23:00 | Winter | FALSE | nonsummer
2023-11-11 23:00 | 2023-11-12 | Winter | FALSE | nonsummer
2023-11-12 | 2023-11-12 01:00 | Winter | FALSE | nonsummer
2023-11-12 01:00 | 2023-11-12 02:00 | Winter | FALSE | nonsummer
2023-11-12 02:00 | 2023-11-12 03:00 | Winter | FALSE | nonsummer
2023-11-12 03:00 | 2023-11-12 04:00 | Winter | FALSE | nonsummer
2023-11-12 04:00 | 2023-11-12 05:00 | Winter | FALSE | nonsummer
2023-11-12 05:00 | 2023-11-12 06:00 | Winter | FALSE | nonsummer
2023-11-12 06:00 | 2023-11-12 07:00 | Winter | FALSE | nonsummer
2023-11-12 07:00 | 2023-11-12 08:00 | Winter | FALSE | nonsummer
2023-11-12 08:00 | 2023-11-12 09:00 | Winter | FALSE | nonsummer
2023-11-12 09:00 | 2023-11-12 10:00 | Winter | FALSE | nonsummer
2023-11-12 10:00 | 2023-11-12 11:00 | Winter | FALSE | nonsummer
2023-11-12 11:00 | 2023-11-12 12:00 | Winter | FALSE | nonsummer
2023-11-12 12:00 | 2023-11-12 13:00 | Winter | FALSE | nonsummer
2023-11-12 13:00 | 2023-11-12 14:00 | Winter | FALSE | nonsummer
2023-11-12 14:00 | 2023-11-12 15:00 | Winter | FALSE | nonsummer
2023-11-12 15:00 | 2023-11-12 16:00 | Winter | FALSE | nonsummer
2023-11-12 16:00 | 2023-11-12 17:00 | Winter | TRUE | nonsummer
2023-11-12 17:00 | 2023-11-12 18:00 | Winter | TRUE | nonsummer
2023-11-12 18:00 | 2023-11-12 19:00 | Winter | TRUE | nonsummer
2023-11-12 19:00 | 2023-11-12 20:00 | Winter | TRUE | nonsummer
2023-11-12 20:00 | 2023-11-12 21:00 | Winter | TRUE | nonsummer
2023-11-12 21:00 | 2023-11-12 22:00 | Winter | FALSE | nonsummer
2023-11-12 22:00 | 2023-11-12 23:00 | Winter | FALSE | nonsummer
2023-11-12 23:00 | 2023-11-13 | Winter | FALSE | nonsummer
2023-11-13 | 2023-11-13 01:00 | Winter | FALSE | nonsummer
2023-11-13 01:00 | 2023-11-13 02:00 | Winter | FALSE | nonsummer
2023-11-13 02:00 | 2023-11-13 03:00 | Winter | FALSE | nonsummer
2023-11-13 03:00 | 2023-11-13 04:00 | Winter | FALSE | nonsummer
2023-11-13 04:00 | 2023-11-13 05:00 | Winter | FALSE | nonsummer
2023-11-13 05:00 | 2023-11-13 06:00 | Winter | FALSE | nonsummer
2023-11-13 06:00 | 2023-11-13 07:00 | Winter | FALSE | nonsummer
2023-11-13 07:00 | 2023-11-13 08:00 | Winter | FALSE | nonsummer
2023-11-13 08:00 | 2023-11-13 09:00 | Winter | FALSE | nonsummer
2023-11-13 09:00 | 2023-11-13 10:00 | Winter | FALSE | nonsummer
2023-11-13 10:00 | 2023-11-13 11:00 | Winter | FALSE | nonsummer
2023-11-13 11:00 | 2023-11-13 12:00 | Winter | FALSE | nonsummer
2023-11-13 12:00 | 2023-11-13 13:00 | Winter | FALSE | nonsummer
2023-11-13 13:00 | 2023-11-13 14:00 | Winter | FALSE | nonsummer
2023-11-13 14:00 | 2023-11-13 15:00 | Winter | FALSE | nonsummer
2023-11-13 15:00 | 2023-11-13 16:00 | Winter | FALSE | nonsummer
2023-11-13 16:00 | 2023-11-13 17:00 | Winter | TRUE | nonsummer
2023-11-13 17:00 | 2023-11-13 18:00 | Winter | TRUE | nonsummer
2023-11-13 18:00 | 2023-11-13 19:00 | Winter | TRUE | nonsummer
2023-11-13 19:00 | 2023-11-13 20:00 | Winter | TRUE | nonsummer
2023-11-13 20:00 | 2023-11-13 21:00 | Winter | TRUE | nonsummer
2023-11-13 21:00 | 2023-11-13 22:00 | Winter | FALSE | nonsummer
2023-11-13 22:00 | 2023-11-13 23:00 | Winter | FALSE | nonsummer
2023-11-13 23:00 | 2023-11-14 | Winter | FALSE | nonsummer
2023-11-14 | 2023-11-14 01:00 | Winter | FALSE | nonsummer
2023-11-14 01:00 | 2023-11-14 02:00 | Winter | FALSE | nonsummer
2023-11-14 02:00 | 2023-11-14 03:00 | Winter | FALSE | nonsummer
2023-11-14 03:00 | 2023-11-14 04:00 | Winter | FALSE | nonsummer
2023-11-14 04:00 | 2023-11-14 05:00 | Winter | FALSE | nonsummer
2023-11-14 05:00 | 2023-11-14 06:00 | Winter | FALSE | nonsummer
2023-11-14 06:00 | 2023-11-14 07:00 | Winter | FALSE | nonsummer
2023-11-14 07:00 | 2023-11-14 08:00 | Winter | FALSE | nonsummer
2023-11-14 08:00 | 2023-11-14 09:00 | Winter | FALSE | nonsummer
2023-11-14 09:00 | 2023-11-14 10:00 | Winter | FALSE | nonsummer
2023-11-14 10:00 | 2023-11-14 11:00 | Winter | FALSE | nonsummer
2023-11-14 11:00 | 2023-11-14 12:00 | Winter | FALSE | nonsummer
2023-11-14 12:00 | 2023-11-14 13:00 | Winter | FALSE | nonsummer
2023-11-14 13:00 | 2023-11-14 14:00 | Winter | FALSE | nonsummer
2023-11-14 14:00 | 2023-11-14 15:00 | Winter | FALSE | nonsummer
2023-11-14 15:00 | 2023-11-14 16:00 | Winter | FALSE | nonsummer
2023-11-14 16:00 | 2023-11-14 17:00 | Winter | TRUE | nonsummer
2023-11-14 17:00 | 2023-11-14 18:00 | Winter | TRUE | nonsummer
2023-11-14 18:00 | 2023-11-14 19:00 | Winter | TRUE | nonsummer
2023-11-14 19:00 | 2023-11-14 20:00 | Winter | TRUE | nonsummer
2023-11-14 20:00 | 2023-11-14 21:00 | Winter | TRUE | nonsummer
2023-11-14 21:00 | 2023-11-14 22:00 | Winter | FALSE | nonsummer
2023-11-14 22:00 | 2023-11-14 23:00 | Winter | FALSE | nonsummer
2023-11-14 23:00 | 2023-11-15 | Winter | FALSE | nonsummer
2023-11-15 | 2023-11-15 01:00 | Winter | FALSE | nonsummer
2023-11-15 01:00 | 2023-11-15 02:00 | Winter | FALSE | nonsummer
2023-11-15 02:00 | 2023-11-15 03:00 | Winter | FALSE | nonsummer
2023-11-15 03:00 | 2023-11-15 04:00 | Winter | FALSE | nonsummer
2023-11-15 04:00 | 2023-11-15 05:00 | Winter | FALSE | nonsummer
2023-11-15 05:00 | 2023-11-15 06:00 | Winter | FALSE | nonsummer
2023-11-15 06:00 | 2023-11-15 07:00 | Winter | FALSE | nonsummer
2023-11-15 07:00 | 2023-11-15 08:00 | Winter | FALSE | nonsummer
2023-11-15 08:00 | 2023-11-15 09:00 | Winter | FALSE | nonsummer
2023-11-15 09:00 | 2023-11-15 10:00 | Winter | FALSE | nonsummer
2023-11-15 10:00 | 2023-11-15 11:00 | Winter | FALSE | nonsummer
2023-11-15 11:00 | 2023-11-15 12:00 | Winter | FALSE | nonsummer
2023-11-15 12:00 | 2023-11-15 13:00 | Winter | FALSE | nonsummer
2023-11-15 13:00 | 2023-11-15 14:00 | Winter | FALSE | nonsummer
2023-11-15 14:00 | 2023-11-15 15:00 | Winter | FALSE | nonsummer
2023-11-15 15:00 | 2023-11-15 16:00 | Winter | FALSE | nonsummer
2023-11-15 16:00 | 2023-11-15 17:00 | Winter | TRUE | nonsummer
2023-11-15 17:00 | 2023-11-15 18:00 | Winter | TRUE | nonsummer
2023-11-15 18:00 | 2023-11-15 19:00 | Winter | TRUE | nonsummer
2023-11-15 19:00 | 2023-11-15 20:00 | Winter | TRUE | nonsummer
2023-11-15 20:00 | 2023-11-15 21:00 | Winter | TRUE | nonsummer
2023-11-15 21:00 | 2023-11-15 22:00 | Winter | FALSE | nonsummer
2023-11-15 22:00 | 2023-11-15 23:00 | Winter | FALSE | nonsummer
2023-11-15 23:00 | 2023-11-16 | Winter | FALSE | nonsummer
2023-11-16 | 2023-11-16 01:00 | Winter | FALSE | nonsummer
2023-11-16 01:00 | 2023-11-16 02:00 | Winter | FALSE | nonsummer
2023-11-16 02:00 | 2023-11-16 03:00 | Winter | FALSE | nonsummer
2023-11-16 03:00 | 2023-11-16 04:00 | Winter | FALSE | nonsummer
2023-11-16 04:00 | 2023-11-16 05:00 | Winter | FALSE | nonsummer
2023-11-16 05:00 | 2023-11-16 06:00 | Winter | FALSE | nonsummer
2023-11-16 06:00 | 2023-11-16 07:00 | Winter | FALSE | nonsummer
2023-11-16 07:00 | 2023-11-16 08:00 | Winter | FALSE | nonsummer
2023-11-16 08:00 | 2023-11-16 09:00 | Winter | FALSE | nonsummer
2023-11-16 09:00 | 2023-11-16 10:00 | Winter | FALSE | nonsummer
2023-11-16 10:00 | 2023-11-16 11:00 | Winter | FALSE | nonsummer
2023-11-16 11:00 | 2023-11-16 12:00 | Winter | FALSE | nonsummer
2023-11-16 12:00 | 2023-11-16 13:00 | Winter | FALSE | nonsummer
2023-11-16 13:00 | 2023-11-16 14:00 | Winter | FALSE | nonsummer
2023-11-16 14:00 | 2023-11-16 15:00 | Winter | FALSE | nonsummer
2023-11-16 15:00 | 2023-11-16 16:00 | Winter | FALSE | nonsummer
2023-11-16 16:00 | 2023-11-16 17:00 | Winter | TRUE | nonsummer
2023-11-16 17:00 | 2023-11-16 18:00 | Winter | TRUE | nonsummer
2023-11-16 18:00 | 2023-11-16 19:00 | Winter | TRUE | nonsummer
2023-11-16 19:00 | 2023-11-16 20:00 | Winter | TRUE | nonsummer
2023-11-16 20:00 | 2023-11-16 21:00 | Winter | TRUE | nonsummer
2023-11-16 21:00 | 2023-11-16 22:00 | Winter | FALSE | nonsummer
2023-11-16 22:00 | 2023-11-16 23:00 | Winter | FALSE | nonsummer
2023-11-16 23:00 | 2023-11-17 | Winter | FALSE | nonsummer
2023-11-17 | 2023-11-17 01:00 | Winter | FALSE | nonsummer
2023-11-17 01:00 | 2023-11-17 02:00 | Winter | FALSE | nonsummer
2023-11-17 02:00 | 2023-11-17 03:00 | Winter | FALSE | nonsummer
2023-11-17 03:00 | 2023-11-17 04:00 | Winter | FALSE | nonsummer
2023-11-17 04:00 | 2023-11-17 05:00 | Winter | FALSE | nonsummer
2023-11-17 05:00 | 2023-11-17 06:00 | Winter | FALSE | nonsummer
2023-11-17 06:00 | 2023-11-17 07:00 | Winter | FALSE | nonsummer
2023-11-17 07:00 | 2023-11-17 08:00 | Winter | FALSE | nonsummer
2023-11-17 08:00 | 2023-11-17 09:00 | Winter | FALSE | nonsummer
2023-11-17 09:00 | 2023-11-17 10:00 | Winter | FALSE | nonsummer
2023-11-17 10:00 | 2023-11-17 11:00 | Winter | FALSE | nonsummer
2023-11-17 11:00 | 2023-11-17 12:00 | Winter | FALSE | nonsummer
2023-11-17 12:00 | 2023-11-17 13:00 | Winter | FALSE | nonsummer
2023-11-17 13:00 | 2023-11-17 14:00 | Winter | FALSE | nonsummer
2023-11-17 14:00 | 2023-11-17 15:00 | Winter | FALSE | nonsummer
2023-11-17 15:00 | 2023-11-17 16:00 | Winter | FALSE | nonsummer
2023-11-17 16:00 | 2023-11-17 17:00 | Winter | TRUE | nonsummer
2023-11-17 17:00 | 2023-11-17 18:00 | Winter | TRUE | nonsummer
2023-11-17 18:00 | 2023-11-17 19:00 | Winter | TRUE | nonsummer
2023-11-17 19:00 | 2023-11-17 20:00 | Winter | TRUE | nonsummer
2023-11-17 20:00 | 2023-11-17 21:00 | Winter | TRUE | nonsummer
2023-11-17 21:00 | 2023-11-17 22:00 | Winter | FALSE | nonsummer
2023-11-17 22:00 | 2023-11-17 23:00 | Winter | FALSE | nonsummer
2023-11-17 23:00 | 2023-11-18 | Winter | FALSE | nonsummer
2023-11-18 | 2023-11-18 01:00 | Winter | FALSE | nonsummer
2023-11-18 01:00 | 2023-11-18 02:00 | Winter | FALSE | nonsummer
2023-11-18 02:00 | 2023-11-18 03:00 | Winter | FALSE | nonsummer
2023-11-18 03:00 | 2023-11-18 04:00 | Winter | FALSE | nonsummer
2023-11-18 04:00 | 2023-11-18 05:00 | Winter | FALSE | nonsummer
2023-11-18 05:00 | 2023-11-18 06:00 | Winter | FALSE | nonsummer
2023-11-18 06:00 | 2023-11-18 07:00 | Winter | FALSE | nonsummer
2023-11-18 07:00 | 2023-11-18 08:00 | Winter | FALSE | nonsummer
2023-11-18 08:00 | 2023-11-18 09:00 | Winter | FALSE | nonsummer
2023-11-18 09:00 | 2023-11-18 10:00 | Winter | FALSE | nonsummer
2023-11-18 10:00 | 2023-11-18 11:00 | Winter | FALSE | nonsummer
2023-11-18 11:00 | 2023-11-18 12:00 | Winter | FALSE | nonsummer
2023-11-18 12:00 | 2023-11-18 13:00 | Winter | FALSE | nonsummer
2023-11-18 13:00 | 2023-11-18 14:00 | Winter | FALSE | nonsummer
2023-11-18 14:00 | 2023-11-18 15:00 | Winter | FALSE | nonsummer
2023-11-18 15:00 | 2023-11-18 16:00 | Winter | FALSE | nonsummer
2023-11-18 16:00 | 2023-11-18 17:00 | Winter | TRUE | nonsummer
2023-11-18 17:00 | 2023-11-18 18:00 | Winter | TRUE | nonsummer
2023-11-18 18:00 | 2023-11-18 19:00 | Winter | TRUE | nonsummer
2023-11-18 19:00 | 2023-11-18 20:00 | Winter | TRUE | nonsummer
2023-11-18 20:00 | 2023-11-18 21:00 | Winter | TRUE | nonsummer
2023-11-18 21:00 | 2023-11-18 22:00 | Winter | FALSE | nonsummer
2023-11-18 22:00 | 2023-11-18 23:00 | Winter | FALSE | nonsummer
2023-11-18 23:00 | 2023-11-19 | Winter | FALSE | nonsummer
2023-11-19 | 2023-11-19 01:00 | Winter | FALSE | nonsummer
2023-11-19 01:00 | 2023-11-19 02:00 | Winter | FALSE | nonsummer
2023-11-19 02:00 | 2023-11-19 03:00 | Winter | FALSE | nonsummer
2023-11-19 03:00 | 2023-11-19 04:00 | Winter | FALSE | nonsummer
2023-11-19 04:00 | 2023-11-19 05:00 | Winter | FALSE | nonsummer
2023-11-19 05:00 | 2023-11-19 06:00 | Winter | FALSE | nonsummer
2023-11-19 06:00 | 2023-11-19 07:00 | Winter | FALSE | nonsummer
2023-11-19 07:00 | 2023-11-19 08:00 | Winter | FALSE | nonsummer
2023-11-19 08:00 | 2023-11-19 09:00 | Winter | FALSE | nonsummer
2023-11-19 09:00 | 2023-11-19 10:00 | Winter | FALSE | nonsummer
2023-11-19 10:00 | 2023-11-19 11:00 | Winter | FALSE | nonsummer
2023-11-19 11:00 | 2023-11-19 12:00 | Winter | FALSE | nonsummer
2023-11-19 12:00 | 2023-11-19 13:00 | Winter | FALSE | nonsummer
2023-11-19 13:00 | 2023-11-19 14:00 | Winter | FALSE | nonsummer
2023-11-19 14:00 | 2023-11-19 15:00 | Winter | FALSE | nonsummer
2023-11-19 15:00 | 2023-11-19 16:00 | Winter | FALSE | nonsummer
2023-11-19 16:00 | 2023-11-19 17:00 | Winter | TRUE | nonsummer
2023-11-19 17:00 | 2023-11-19 18:00 | Winter | TRUE | nonsummer
2023-11-19 18:00 | 2023-11-19 19:00 | Winter | TRUE | nonsummer
2023-11-19 19:00 | 2023-11-19 20:00 | Winter | TRUE | nonsummer
2023-11-19 20:00 | 2023-11-19 21:00 | Winter | TRUE | nonsummer
2023-11-19 21:00 | 2023-11-19 22:00 | Winter | FALSE | nonsummer
2023-11-19 22:00 | 2023-11-19 23:00 | Winter | FALSE | nonsummer
2023-11-19 23:00 | 2023-11-20 | Winter | FALSE | nonsummer
2023-11-20 | 2023-11-20 01:00 | Winter | FALSE | nonsummer
2023-11-20 01:00 | 2023-11-20 02:00 | Winter | FALSE | nonsummer
2023-11-20 02:00 | 2023-11-20 03:00 | Winter | FALSE | nonsummer
2023-11-20 03:00 | 2023-11-20 04:00 | Winter | FALSE | nonsummer
2023-11-20 04:00 | 2023-11-20 05:00 | Winter | FALSE | nonsummer
2023-11-20 05:00 | 2023-11-20 06:00 | Winter | FALSE | nonsummer
2023-11-20 06:00 | 2023-11-20 07:00 | Winter | FALSE | nonsummer
2023-11-20 07:00 | 2023-11-20 08:00 | Winter | FALSE | nonsummer
2023-11-20 08:00 | 2023-11-20 09:00 | Winter | FALSE | nonsummer
2023-11-20 09:00 | 2023-11-20 10:00 | Winter | FALSE | nonsummer
2023-11-20 10:00 | 2023-11-20 11:00 | Winter | FALSE | nonsummer
2023-11-20 11:00 | 2023-11-20 12:00 | Winter | FALSE | nonsummer
2023-11-20 12:00 | 2023-11-20 13:00 | Winter | FALSE | nonsummer
2023-11-20 13:00 | 2023-11-20 14:00 | Winter | FALSE | nonsummer
2023-11-20 14:00 | 2023-11-20 15:00 | Winter | FALSE | nonsummer
2023-11-20 15:00 | 2023-11-20 16:00 | Winter | FALSE | nonsummer
2023-11-20 16:00 | 2023-11-20 17:00 | Winter | TRUE | nonsummer
2023-11-20 17:00 | 2023-11-20 18:00 | Winter | TRUE | nonsummer
2023-11-20 18:00 | 2023-11-20 19:00 | Winter | TRUE | nonsummer
2023-11-20 19:00 | 2023-11-20 20:00 | Winter | TRUE | nonsummer
2023-11-20 20:00 | 2023-11-20 21:00 | Winter | TRUE | nonsummer
2023-11-20 21:00 | 2023-11-20 22:00 | Winter | FALSE | nonsummer
2023-11-20 22:00 | 2023-11-20 23:00 | Winter | FALSE | nonsummer
2023-11-20 23:00 | 2023-11-21 | Winter | FALSE | nonsummer
2023-11-21 | 2023-11-21 01:00 | Winter | FALSE | nonsummer
2023-11-21 01:00 | 2023-11-21 02:00 | Winter | FALSE | nonsummer
2023-11-21 02:00 | 2023-11-21 03:00 | Winter | FALSE | nonsummer
2023-11-21 03:00 | 2023-11-21 04:00 | Winter | FALSE | nonsummer
2023-11-21 04:00 | 2023-11-21 05:00 | Winter | FALSE | nonsummer
2023-11-21 05:00 | 2023-11-21 06:00 | Winter | FALSE | nonsummer
2023-11-21 06:00 | 2023-11-21 07:00 | Winter | FALSE | nonsummer
2023-11-21 07:00 | 2023-11-21 08:00 | Winter | FALSE | nonsummer
2023-11-21 08:00 | 2023-11-21 09:00 | Winter | FALSE | nonsummer
2023-11-21 09:00 | 2023-11-21 10:00 | Winter | FALSE | nonsummer
2023-11-21 10:00 | 2023-11-21 11:00 | Winter | FALSE | nonsummer
2023-11-21 11:00 | 2023-11-21 12:00 | Winter | FALSE | nonsummer
2023-11-21 12:00 | 2023-11-21 13:00 | Winter | FALSE | nonsummer
2023-11-21 13:00 | 2023-11-21 14:00 | Winter | FALSE | nonsummer
2023-11-21 14:00 | 2023-11-21 15:00 | Winter | FALSE | nonsummer
2023-11-21 15:00 | 2023-11-21 16:00 | Winter | FALSE | nonsummer
2023-11-21 16:00 | 2023-11-21 17:00 | Winter | TRUE | nonsummer
2023-11-21 17:00 | 2023-11-21 18:00 | Winter | TRUE | nonsummer
2023-11-21 18:00 | 2023-11-21 19:00 | Winter | TRUE | nonsummer
2023-11-21 19:00 | 2023-11-21 20:00 | Winter | TRUE | nonsummer
2023-11-21 20:00 | 2023-11-21 21:00 | Winter | TRUE | nonsummer
2023-11-21 21:00 | 2023-11-21 22:00 | Winter | FALSE | nonsummer
2023-11-21 22:00 | 2023-11-21 23:00 | Winter | FALSE | nonsummer
2023-11-21 23:00 | 2023-11-22 | Winter | FALSE | nonsummer
2023-11-22 | 2023-11-22 01:00 | Winter | FALSE | nonsummer
2023-11-22 01:00 | 2023-11-22 02:00 | Winter | FALSE | nonsummer
2023-11-22 02:00 | 2023-11-22 03:00 | Winter | FALSE | nonsummer
2023-11-22 03:00 | 2023-11-22 04:00 | Winter | FALSE | nonsummer
2023-11-22 04:00 | 2023-11-22 05:00 | Winter | FALSE | nonsummer
2023-11-22 05:00 | 2023-11-22 06:00 | Winter | FALSE | nonsummer
2023-11-22 06:00 | 2023-11-22 07:00 | Winter | FALSE | nonsummer
2023-11-22 07:00 | 2023-11-22 08:00 | Winter | FALSE | nonsummer
2023-11-22 08:00 | 2023-11-22 09:00 | Winter | FALSE | nonsummer
2023-11-22 09:00 | 2023-11-22 10:00 | Winter | FALSE | nonsummer
2023-11-22 10:00 | 2023-11-22 11:00 | Winter | FALSE | nonsummer
2023-11-22 11:00 | 2023-11-22 12:00 | Winter | FALSE | nonsummer
2023-11-22 12:00 | 2023-11-22 13:00 | Winter | FALSE | nonsummer
2023-11-22 13:00 | 2023-11-22 14:00 | Winter | FALSE | nonsummer
2023-11-22 14:00 | 2023-11-22 15:00 | Winter | FALSE | nonsummer
2023-11-22 15:00 | 2023-11-22 16:00 | Winter | FALSE | nonsummer
2023-11-22 16:00 | 2023-11-22 17:00 | Winter | TRUE | nonsummer
2023-11-22 17:00 | 2023-11-22 18:00 | Winter | TRUE | nonsummer
2023-11-22 18:00 | 2023-11-22 19:00 | Winter | TRUE | nonsummer
2023-11-22 19:00 | 2023-11-22 20:00 | Winter | TRUE | nonsummer
2023-11-22 20:00 | 2023-11-22 21:00 | Winter | TRUE | nonsummer
2023-11-22 21:00 | 2023-11-22 22:00 | Winter | FALSE | nonsummer
2023-11-22 22:00 | 2023-11-22 23:00 | Winter | FALSE | nonsummer
2023-11-22 23:00 | 2023-11-23 | Winter | FALSE | nonsummer
2023-11-23 | 2023-11-23 01:00 | Winter | FALSE | nonsummer
2023-11-23 01:00 | 2023-11-23 02:00 | Winter | FALSE | nonsummer
2023-11-23 02:00 | 2023-11-23 03:00 | Winter | FALSE | nonsummer
2023-11-23 03:00 | 2023-11-23 04:00 | Winter | FALSE | nonsummer
2023-11-23 04:00 | 2023-11-23 05:00 | Winter | FALSE | nonsummer
2023-11-23 05:00 | 2023-11-23 06:00 | Winter | FALSE | nonsummer
2023-11-23 06:00 | 2023-11-23 07:00 | Winter | FALSE | nonsummer
2023-11-23 07:00 | 2023-11-23 08:00 | Winter | FALSE | nonsummer
2023-11-23 08:00 | 2023-11-23 09:00 | Winter | FALSE | nonsummer
2023-11-23 09:00 | 2023-11-23 10:00 | Winter | FALSE | nonsummer
2023-11-23 10:00 | 2023-11-23 11:00 | Winter | FALSE | nonsummer
2023-11-23 11:00 | 2023-11-23 12:00 | Winter | FALSE | nonsummer
2023-11-23 12:00 | 2023-11-23 13:00 | Winter | FALSE | nonsummer
2023-11-23 13:00 | 2023-11-23 14:00 | Winter | FALSE | nonsummer
2023-11-23 14:00 | 2023-11-23 15:00 | Winter | FALSE | nonsummer
2023-11-23 15:00 | 2023-11-23 16:00 | Winter | FALSE | nonsummer
2023-11-23 16:00 | 2023-11-23 17:00 | Winter | TRUE | nonsummer
2023-11-23 17:00 | 2023-11-23 18:00 | Winter | TRUE | nonsummer
2023-11-23 18:00 | 2023-11-23 19:00 | Winter | TRUE | nonsummer
2023-11-23 19:00 | 2023-11-23 20:00 | Winter | TRUE | nonsummer
2023-11-23 20:00 | 2023-11-23 21:00 | Winter | TRUE | nonsummer
2023-11-23 21:00 | 2023-11-23 22:00 | Winter | FALSE | nonsummer
2023-11-23 22:00 | 2023-11-23 23:00 | Winter | FALSE | nonsummer
2023-11-23 23:00 | 2023-11-24 | Winter | FALSE | nonsummer
2023-11-24 | 2023-11-24 01:00 | Winter | FALSE | nonsummer
2023-11-24 01:00 | 2023-11-24 02:00 | Winter | FALSE | nonsummer
2023-11-24 02:00 | 2023-11-24 03:00 | Winter | FALSE | nonsummer
2023-11-24 03:00 | 2023-11-24 04:00 | Winter | FALSE | nonsummer
2023-11-24 04:00 | 2023-11-24 05:00 | Winter | FALSE | nonsummer
2023-11-24 05:00 | 2023-11-24 06:00 | Winter | FALSE | nonsummer
2023-11-24 06:00 | 2023-11-24 07:00 | Winter | FALSE | nonsummer
2023-11-24 07:00 | 2023-11-24 08:00 | Winter | FALSE | nonsummer
2023-11-24 08:00 | 2023-11-24 09:00 | Winter | FALSE | nonsummer
2023-11-24 09:00 | 2023-11-24 10:00 | Winter | FALSE | nonsummer
2023-11-24 10:00 | 2023-11-24 11:00 | Winter | FALSE | nonsummer
2023-11-24 11:00 | 2023-11-24 12:00 | Winter | FALSE | nonsummer
2023-11-24 12:00 | 2023-11-24 13:00 | Winter | FALSE | nonsummer
2023-11-24 13:00 | 2023-11-24 14:00 | Winter | FALSE | nonsummer
2023-11-24 14:00 | 2023-11-24 15:00 | Winter | FALSE | nonsummer
2023-11-24 15:00 | 2023-11-24 16:00 | Winter | FALSE | nonsummer
2023-11-24 16:00 | 2023-11-24 17:00 | Winter | TRUE | nonsummer
2023-11-24 17:00 | 2023-11-24 18:00 | Winter | TRUE | nonsummer
2023-11-24 18:00 | 2023-11-24 19:00 | Winter | TRUE | nonsummer
2023-11-24 19:00 | 2023-11-24 20:00 | Winter | TRUE | nonsummer
2023-11-24 20:00 | 2023-11-24 21:00 | Winter | TRUE | nonsummer
2023-11-24 21:00 | 2023-11-24 22:00 | Winter | FALSE | nonsummer
2023-11-24 22:00 | 2023-11-24 23:00 | Winter | FALSE | nonsummer
2023-11-24 23:00 | 2023-11-25 | Winter | FALSE | nonsummer
2023-11-25 | 2023-11-25 01:00 | Winter | FALSE | nonsummer
2023-11-25 01:00 | 2023-11-25 02:00 | Winter | FALSE | nonsummer
2023-11-25 02:00 | 2023-11-25 03:00 | Winter | FALSE | nonsummer
2023-11-25 03:00 | 2023-11-25 04:00 | Winter | FALSE | nonsummer
2023-11-25 04:00 | 2023-11-25 05:00 | Winter | FALSE | nonsummer
2023-11-25 05:00 | 2023-11-25 06:00 | Winter | FALSE | nonsummer
2023-11-25 06:00 | 2023-11-25 07:00 | Winter | FALSE | nonsummer
2023-11-25 07:00 | 2023-11-25 08:00 | Winter | FALSE | nonsummer
2023-11-25 08:00 | 2023-11-25 09:00 | Winter | FALSE | nonsummer
2023-11-25 09:00 | 2023-11-25 10:00 | Winter | FALSE | nonsummer
2023-11-25 10:00 | 2023-11-25 11:00 | Winter | FALSE | nonsummer
2023-11-25 11:00 | 2023-11-25 12:00 | Winter | FALSE | nonsummer
2023-11-25 12:00 | 2023-11-25 13:00 | Winter | FALSE | nonsummer
2023-11-25 13:00 | 2023-11-25 14:00 | Winter | FALSE | nonsummer
2023-11-25 14:00 | 2023-11-25 15:00 | Winter | FALSE | nonsummer
2023-11-25 15:00 | 2023-11-25 16:00 | Winter | FALSE | nonsummer
2023-11-25 16:00 | 2023-11-25 17:00 | Winter | TRUE | nonsummer
2023-11-25 17:00 | 2023-11-25 18:00 | Winter | TRUE | nonsummer
2023-11-25 18:00 | 2023-11-25 19:00 | Winter | TRUE | nonsummer
2023-11-25 19:00 | 2023-11-25 20:00 | Winter | TRUE | nonsummer
2023-11-25 20:00 | 2023-11-25 21:00 | Winter | TRUE | nonsummer
2023-11-25 21:00 | 2023-11-25 22:00 | Winter | FALSE | nonsummer
2023-11-25 22:00 | 2023-11-25 23:00 | Winter | FALSE | nonsummer
2023-11-25 23:00 | 2023-11-26 | Winter | FALSE | nonsummer
2023-11-26 | 2023-11-26 01:00 | Winter | FALSE | nonsummer
2023-11-26 01:00 | 2023-11-26 02:00 | Winter | FALSE | nonsummer
2023-11-26 02:00 | 2023-11-26 03:00 | Winter | FALSE | nonsummer
2023-11-26 03:00 | 2023-11-26 04:00 | Winter | FALSE | nonsummer
2023-11-26 04:00 | 2023-11-26 05:00 | Winter | FALSE | nonsummer
2023-11-26 05:00 | 2023-11-26 06:00 | Winter | FALSE | nonsummer
2023-11-26 06:00 | 2023-11-26 07:00 | Winter | FALSE | nonsummer
2023-11-26 07:00 | 2023-11-26 08:00 | Winter | FALSE | nonsummer
2023-11-26 08:00 | 2023-11-26 09:00 | Winter | FALSE | nonsummer
2023-11-26 09:00 | 2023-11-26 10:00 | Winter | FALSE | nonsummer
2023-11-26 10:00 | 2023-11-26 11:00 | Winter | FALSE | nonsummer
2023-11-26 11:00 | 2023-11-26 12:00 | Winter | FALSE | nonsummer
2023-11-26 12:00 | 2023-11-26 13:00 | Winter | FALSE | nonsummer
2023-11-26 13:00 | 2023-11-26 14:00 | Winter | FALSE | nonsummer
2023-11-26 14:00 | 2023-11-26 15:00 | Winter | FALSE | nonsummer
2023-11-26 15:00 | 2023-11-26 16:00 | Winter | FALSE | nonsummer
2023-11-26 16:00 | 2023-11-26 17:00 | Winter | TRUE | nonsummer
2023-11-26 17:00 | 2023-11-26 18:00 | Winter | TRUE | nonsummer
2023-11-26 18:00 | 2023-11-26 19:00 | Winter | TRUE | nonsummer
2023-11-26 19:00 | 2023-11-26 20:00 | Winter | TRUE | nonsummer
2023-11-26 20:00 | 2023-11-26 21:00 | Winter | TRUE | nonsummer
2023-11-26 21:00 | 2023-11-26 22:00 | Winter | FALSE | nonsummer
2023-11-26 22:00 | 2023-11-26 23:00 | Winter | FALSE | nonsummer
2023-11-26 23:00 | 2023-11-27 | Winter | FALSE | nonsummer
2023-11-27 | 2023-11-27 01:00 | Winter | FALSE | nonsummer
2023-11-27 01:00 | 2023-11-27 02:00 | Winter | FALSE | nonsummer
2023-11-27 02:00 | 2023-11-27 03:00 | Winter | FALSE | nonsummer
2023-11-27 03:00 | 2023-11-27 04:00 | Winter | FALSE | nonsummer
2023-11-27 04:00 | 2023-11-27 05:00 | Winter | FALSE | nonsummer
2023-11-27 05:00 | 2023-11-27 06:00 | Winter | FALSE | nonsummer
2023-11-27 06:00 | 2023-11-27 07:00 | Winter | FALSE | nonsummer
2023-11-27 07:00 | 2023-11-27 08:00 | Winter | FALSE | nonsummer
2023-11-27 08:00 | 2023-11-27 09:00 | Winter | FALSE | nonsummer
2023-11-27 09:00 | 2023-11-27 10:00 | Winter | FALSE | nonsummer
2023-11-27 10:00 | 2023-11-27 11:00 | Winter | FALSE | nonsummer
2023-11-27 11:00 | 2023-11-27 12:00 | Winter | FALSE | nonsummer
2023-11-27 12:00 | 2023-11-27 13:00 | Winter | FALSE | nonsummer
2023-11-27 13:00 | 2023-11-27 14:00 | Winter | FALSE | nonsummer
2023-11-27 14:00 | 2023-11-27 15:00 | Winter | FALSE | nonsummer
2023-11-27 15:00 | 2023-11-27 16:00 | Winter | FALSE | nonsummer
2023-11-27 16:00 | 2023-11-27 17:00 | Winter | TRUE | nonsummer
2023-11-27 17:00 | 2023-11-27 18:00 | Winter | TRUE | nonsummer
2023-11-27 18:00 | 2023-11-27 19:00 | Winter | TRUE | nonsummer
2023-11-27 19:00 | 2023-11-27 20:00 | Winter | TRUE | nonsummer
2023-11-27 20:00 | 2023-11-27 21:00 | Winter | TRUE | nonsummer
2023-11-27 21:00 | 2023-11-27 22:00 | Winter | FALSE | nonsummer
2023-11-27 22:00 | 2023-11-27 23:00 | Winter | FALSE | nonsummer
2023-11-27 23:00 | 2023-11-28 | Winter | FALSE | nonsummer
2023-11-28 | 2023-11-28 01:00 | Winter | FALSE | nonsummer
2023-11-28 01:00 | 2023-11-28 02:00 | Winter | FALSE | nonsummer
2023-11-28 02:00 | 2023-11-28 03:00 | Winter | FALSE | nonsummer
2023-11-28 03:00 | 2023-11-28 04:00 | Winter | FALSE | nonsummer
2023-11-28 04:00 | 2023-11-28 05:00 | Winter | FALSE | nonsummer
2023-11-28 05:00 | 2023-11-28 06:00 | Winter | FALSE | nonsummer
2023-11-28 06:00 | 2023-11-28 07:00 | Winter | FALSE | nonsummer
2023-11-28 07:00 | 2023-11-28 08:00 | Winter | FALSE | nonsummer
2023-11-28 08:00 | 2023-11-28 09:00 | Winter | FALSE | nonsummer
2023-11-28 09:00 | 2023-11-28 10:00 | Winter | FALSE | nonsummer
2023-11-28 10:00 | 2023-11-28 11:00 | Winter | FALSE | nonsummer
2023-11-28 11:00 | 2023-11-28 12:00 | Winter | FALSE | nonsummer
2023-11-28 12:00 | 2023-11-28 13:00 | Winter | FALSE | nonsummer
2023-11-28 13:00 | 2023-11-28 14:00 | Winter | FALSE | nonsummer
2023-11-28 14:00 | 2023-11-28 15:00 | Winter | FALSE | nonsummer
2023-11-28 15:00 | 2023-11-28 16:00 | Winter | FALSE | nonsummer
2023-11-28 16:00 | 2023-11-28 17:00 | Winter | TRUE | nonsummer
2023-11-28 17:00 | 2023-11-28 18:00 | Winter | TRUE | nonsummer
2023-11-28 18:00 | 2023-11-28 19:00 | Winter | TRUE | nonsummer
2023-11-28 19:00 | 2023-11-28 20:00 | Winter | TRUE | nonsummer
2023-11-28 20:00 | 2023-11-28 21:00 | Winter | TRUE | nonsummer
2023-11-28 21:00 | 2023-11-28 22:00 | Winter | FALSE | nonsummer
2023-11-28 22:00 | 2023-11-28 23:00 | Winter | FALSE | nonsummer
2023-11-28 23:00 | 2023-11-29 | Winter | FALSE | nonsummer
2023-11-29 | 2023-11-29 01:00 | Winter | FALSE | nonsummer
2023-11-29 01:00 | 2023-11-29 02:00 | Winter | FALSE | nonsummer
2023-11-29 02:00 | 2023-11-29 03:00 | Winter | FALSE | nonsummer
2023-11-29 03:00 | 2023-11-29 04:00 | Winter | FALSE | nonsummer
2023-11-29 04:00 | 2023-11-29 05:00 | Winter | FALSE | nonsummer
2023-11-29 05:00 | 2023-11-29 06:00 | Winter | FALSE | nonsummer
2023-11-29 06:00 | 2023-11-29 07:00 | Winter | FALSE | nonsummer
2023-11-29 07:00 | 2023-11-29 08:00 | Winter | FALSE | nonsummer
2023-11-29 08:00 | 2023-11-29 09:00 | Winter | FALSE | nonsummer
2023-11-29 09:00 | 2023-11-29 10:00 | Winter | FALSE | nonsummer
2023-11-29 10:00 | 2023-11-29 11:00 | Winter | FALSE | nonsummer
2023-11-29 11:00 | 2023-11-29 12:00 | Winter | FALSE | nonsummer
2023-11-29 12:00 | 2023-11-29 13:00 | Winter | FALSE | nonsummer
2023-11-29 13:00 | 2023-11-29 14:00 | Winter | FALSE | nonsummer
2023-11-29 14:00 | 2023-11-29 15:00 | Winter | FALSE | nonsummer
2023-11-29 15:00 | 2023-11-29 16:00 | Winter | FALSE | nonsummer
2023-11-29 16:00 | 2023-11-29 17:00 | Winter | TRUE | nonsummer
2023-11-29 17:00 | 2023-11-29 18:00 | Winter | TRUE | nonsummer
2023-11-29 18:00 | 2023-11-29 19:00 | Winter | TRUE | nonsummer
2023-11-29 19:00 | 2023-11-29 20:00 | Winter | TRUE | nonsummer
2023-11-29 20:00 | 2023-11-29 21:00 | Winter | TRUE | nonsummer
2023-11-29 21:00 | 2023-11-29 22:00 | Winter | FALSE | nonsummer
2023-11-29 22:00 | 2023-11-29 23:00 | Winter | FALSE | nonsummer
2023-11-29 23:00 | 2023-11-30 | Winter | FALSE | nonsummer
2023-11-30 | 2023-11-30 01:00 | Winter | FALSE | nonsummer
2023-11-30 01:00 | 2023-11-30 02:00 | Winter | FALSE | nonsummer
2023-11-30 02:00 | 2023-11-30 03:00 | Winter | FALSE | nonsummer
2023-11-30 03:00 | 2023-11-30 04:00 | Winter | FALSE | nonsummer
2023-11-30 04:00 | 2023-11-30 05:00 | Winter | FALSE | nonsummer
2023-11-30 05:00 | 2023-11-30 06:00 | Winter | FALSE | nonsummer
2023-11-30 06:00 | 2023-11-30 07:00 | Winter | FALSE | nonsummer
2023-11-30 07:00 | 2023-11-30 08:00 | Winter | FALSE | nonsummer
2023-11-30 08:00 | 2023-11-30 09:00 | Winter | FALSE | nonsummer
2023-11-30 09:00 | 2023-11-30 10:00 | Winter | FALSE | nonsummer
2023-11-30 10:00 | 2023-11-30 11:00 | Winter | FALSE | nonsummer
2023-11-30 11:00 | 2023-11-30 12:00 | Winter | FALSE | nonsummer
2023-11-30 12:00 | 2023-11-30 13:00 | Winter | FALSE | nonsummer
2023-11-30 13:00 | 2023-11-30 14:00 | Winter | FALSE | nonsummer
2023-11-30 14:00 | 2023-11-30 15:00 | Winter | FALSE | nonsummer
2023-11-30 15:00 | 2023-11-30 16:00 | Winter | FALSE | nonsummer
2023-11-30 16:00 | 2023-11-30 17:00 | Winter | TRUE | nonsummer
2023-11-30 17:00 | 2023-11-30 18:00 | Winter | TRUE | nonsummer
2023-11-30 18:00 | 2023-11-30 19:00 | Winter | TRUE | nonsummer
2023-11-30 19:00 | 2023-11-30 20:00 | Winter | TRUE | nonsummer
2023-11-30 20:00 | 2023-11-30 21:00 | Winter | TRUE | nonsummer
2023-11-30 21:00 | 2023-11-30 22:00 | Winter | FALSE | nonsummer
2023-11-30 22:00 | 2023-11-30 23:00 | Winter | FALSE | nonsummer
2023-11-30 23:00 | 2023-12-01 | Winter | FALSE | nonsummer
2023-12-01 | 2023-12-01 01:00 | Winter | FALSE | nonsummer
2023-12-01 01:00 | 2023-12-01 02:00 | Winter | FALSE | nonsummer
2023-12-01 02:00 | 2023-12-01 03:00 | Winter | FALSE | nonsummer
2023-12-01 03:00 | 2023-12-01 04:00 | Winter | FALSE | nonsummer
2023-12-01 04:00 | 2023-12-01 05:00 | Winter | FALSE | nonsummer
2023-12-01 05:00 | 2023-12-01 06:00 | Winter | FALSE | nonsummer
2023-12-01 06:00 | 2023-12-01 07:00 | Winter | FALSE | nonsummer
2023-12-01 07:00 | 2023-12-01 08:00 | Winter | FALSE | nonsummer
2023-12-01 08:00 | 2023-12-01 09:00 | Winter | FALSE | nonsummer
2023-12-01 09:00 | 2023-12-01 10:00 | Winter | FALSE | nonsummer
2023-12-01 10:00 | 2023-12-01 11:00 | Winter | FALSE | nonsummer
2023-12-01 11:00 | 2023-12-01 12:00 | Winter | FALSE | nonsummer
2023-12-01 12:00 | 2023-12-01 13:00 | Winter | FALSE | nonsummer
2023-12-01 13:00 | 2023-12-01 14:00 | Winter | FALSE | nonsummer
2023-12-01 14:00 | 2023-12-01 15:00 | Winter | FALSE | nonsummer
2023-12-01 15:00 | 2023-12-01 16:00 | Winter | FALSE | nonsummer
2023-12-01 16:00 | 2023-12-01 17:00 | Winter | TRUE | nonsummer
2023-12-01 17:00 | 2023-12-01 18:00 | Winter | TRUE | nonsummer
2023-12-01 18:00 | 2023-12-01 19:00 | Winter | TRUE | nonsummer
2023-12-01 19:00 | 2023-12-01 20:00 | Winter | TRUE | nonsummer
2023-12-01 20:00 | 2023-12-01 21:00 | Winter | TRUE | nonsummer
2023-12-01 21:00 | 2023-12-01 22:00 | Winter | FALSE | nonsummer
2023-12-01 22:00 | 2023-12-01 23:00 | Winter | FALSE | nonsummer
2023-12-01 23:00 | 2023-12-02 | Winter | FALSE | nonsummer
2023-12-02 | 2023-12-02 01:00 | Winter | FALSE | nonsummer
2023-12-02 01:00 | 2023-12-02 02:00 | Winter | FALSE | nonsummer
2023-12-02 02:00 | 2023-12-02 03:00 | Winter | FALSE | nonsummer
2023-12-02 03:00 | 2023-12-02 04:00 | Winter | FALSE | nonsummer
2023-12-02 04:00 | 2023-12-02 05:00 | Winter | FALSE | nonsummer
2023-12-02 05:00 | 2023-12-02 06:00 | Winter | FALSE | nonsummer
2023-12-02 06:00 | 2023-12-02 07:00 | Winter | FALSE | nonsummer
2023-12-02 07:00 | 2023-12-02 08:00 | Winter | FALSE | nonsummer
2023-12-02 08:00 | 2023-12-02 09:00 | Winter | FALSE | nonsummer
2023-12-02 09:00 | 2023-12-02 10:00 | Winter | FALSE | nonsummer
2023-12-02 10:00 | 2023-12-02 11:00 | Winter | FALSE | nonsummer
2023-12-02 11:00 | 2023-12-02 12:00 | Winter | FALSE | nonsummer
2023-12-02 12:00 | 2023-12-02 13:00 | Winter | FALSE | nonsummer
2023-12-02 13:00 | 2023-12-02 14:00 | Winter | FALSE | nonsummer
2023-12-02 14:00 | 2023-12-02 15:00 | Winter | FALSE | nonsummer
2023-12-02 15:00 | 2023-12-02 16:00 | Winter | FALSE | nonsummer
2023-12-02 16:00 | 2023-12-02 17:00 | Winter | TRUE | nonsummer
2023-12-02 17:00 | 2023-12-02 18:00 | Winter | TRUE | nonsummer
2023-12-02 18:00 | 2023-12-02 19:00 | Winter | TRUE | nonsummer
2023-12-02 19:00 | 2023-12-02 20:00 | Winter | TRUE | nonsummer
2023-12-02 20:00 | 2023-12-02 21:00 | Winter | TRUE | nonsummer
2023-12-02 21:00 | 2023-12-02 22:00 | Winter | FALSE | nonsummer
2023-12-02 22:00 | 2023-12-02 23:00 | Winter | FALSE | nonsummer
2023-12-02 23:00 | 2023-12-03 | Winter | FALSE | nonsummer
2023-12-03 | 2023-12-03 01:00 | Winter | FALSE | nonsummer
2023-12-03 01:00 | 2023-12-03 02:00 | Winter | FALSE | nonsummer
2023-12-03 02:00 | 2023-12-03 03:00 | Winter | FALSE | nonsummer
2023-12-03 03:00 | 2023-12-03 04:00 | Winter | FALSE | nonsummer
2023-12-03 04:00 | 2023-12-03 05:00 | Winter | FALSE | nonsummer
2023-12-03 05:00 | 2023-12-03 06:00 | Winter | FALSE | nonsummer
2023-12-03 06:00 | 2023-12-03 07:00 | Winter | FALSE | nonsummer
2023-12-03 07:00 | 2023-12-03 08:00 | Winter | FALSE | nonsummer
2023-12-03 08:00 | 2023-12-03 09:00 | Winter | FALSE | nonsummer
2023-12-03 09:00 | 2023-12-03 10:00 | Winter | FALSE | nonsummer
2023-12-03 10:00 | 2023-12-03 11:00 | Winter | FALSE | nonsummer
2023-12-03 11:00 | 2023-12-03 12:00 | Winter | FALSE | nonsummer
2023-12-03 12:00 | 2023-12-03 13:00 | Winter | FALSE | nonsummer
2023-12-03 13:00 | 2023-12-03 14:00 | Winter | FALSE | nonsummer
2023-12-03 14:00 | 2023-12-03 15:00 | Winter | FALSE | nonsummer
2023-12-03 15:00 | 2023-12-03 16:00 | Winter | FALSE | nonsummer
2023-12-03 16:00 | 2023-12-03 17:00 | Winter | TRUE | nonsummer
2023-12-03 17:00 | 2023-12-03 18:00 | Winter | TRUE | nonsummer
2023-12-03 18:00 | 2023-12-03 19:00 | Winter | TRUE | nonsummer
2023-12-03 19:00 | 2023-12-03 20:00 | Winter | TRUE | nonsummer
2023-12-03 20:00 | 2023-12-03 21:00 | Winter | TRUE | nonsummer
2023-12-03 21:00 | 2023-12-03 22:00 | Winter | FALSE | nonsummer
2023-12-03 22:00 | 2023-12-03 23:00 | Winter | FALSE | nonsummer
2023-12-03 23:00 | 2023-12-04 | Winter | FALSE | nonsummer
2023-12-04 | 2023-12-04 01:00 | Winter | FALSE | nonsummer
2023-12-04 01:00 | 2023-12-04 02:00 | Winter | FALSE | nonsummer
2023-12-04 02:00 | 2023-12-04 03:00 | Winter | FALSE | nonsummer
2023-12-04 03:00 | 2023-12-04 04:00 | Winter | FALSE | nonsummer
2023-12-04 04:00 | 2023-12-04 05:00 | Winter | FALSE | nonsummer
2023-12-04 05:00 | 2023-12-04 06:00 | Winter | FALSE | nonsummer
2023-12-04 06:00 | 2023-12-04 07:00 | Winter | FALSE | nonsummer
2023-12-04 07:00 | 2023-12-04 08:00 | Winter | FALSE | nonsummer
2023-12-04 08:00 | 2023-12-04 09:00 | Winter | FALSE | nonsummer
2023-12-04 09:00 | 2023-12-04 10:00 | Winter | FALSE | nonsummer
2023-12-04 10:00 | 2023-12-04 11:00 | Winter | FALSE | nonsummer
2023-12-04 11:00 | 2023-12-04 12:00 | Winter | FALSE | nonsummer
2023-12-04 12:00 | 2023-12-04 13:00 | Winter | FALSE | nonsummer
2023-12-04 13:00 | 2023-12-04 14:00 | Winter | FALSE | nonsummer
2023-12-04 14:00 | 2023-12-04 15:00 | Winter | FALSE | nonsummer
2023-12-04 15:00 | 2023-12-04 16:00 | Winter | FALSE | nonsummer
2023-12-04 16:00 | 2023-12-04 17:00 | Winter | TRUE | nonsummer
2023-12-04 17:00 | 2023-12-04 18:00 | Winter | TRUE | nonsummer
2023-12-04 18:00 | 2023-12-04 19:00 | Winter | TRUE | nonsummer
2023-12-04 19:00 | 2023-12-04 20:00 | Winter | TRUE | nonsummer
2023-12-04 20:00 | 2023-12-04 21:00 | Winter | TRUE | nonsummer
2023-12-04 21:00 | 2023-12-04 22:00 | Winter | FALSE | nonsummer
2023-12-04 22:00 | 2023-12-04 23:00 | Winter | FALSE | nonsummer
2023-12-04 23:00 | 2023-12-05 | Winter | FALSE | nonsummer
2023-12-05 | 2023-12-05 01:00 | Winter | FALSE | nonsummer
2023-12-05 01:00 | 2023-12-05 02:00 | Winter | FALSE | nonsummer
2023-12-05 02:00 | 2023-12-05 03:00 | Winter | FALSE | nonsummer
2023-12-05 03:00 | 2023-12-05 04:00 | Winter | FALSE | nonsummer
2023-12-05 04:00 | 2023-12-05 05:00 | Winter | FALSE | nonsummer
2023-12-05 05:00 | 2023-12-05 06:00 | Winter | FALSE | nonsummer
2023-12-05 06:00 | 2023-12-05 07:00 | Winter | FALSE | nonsummer
2023-12-05 07:00 | 2023-12-05 08:00 | Winter | FALSE | nonsummer
2023-12-05 08:00 | 2023-12-05 09:00 | Winter | FALSE | nonsummer
2023-12-05 09:00 | 2023-12-05 10:00 | Winter | FALSE | nonsummer
2023-12-05 10:00 | 2023-12-05 11:00 | Winter | FALSE | nonsummer
2023-12-05 11:00 | 2023-12-05 12:00 | Winter | FALSE | nonsummer
2023-12-05 12:00 | 2023-12-05 13:00 | Winter | FALSE | nonsummer
2023-12-05 13:00 | 2023-12-05 14:00 | Winter | FALSE | nonsummer
2023-12-05 14:00 | 2023-12-05 15:00 | Winter | FALSE | nonsummer
2023-12-05 15:00 | 2023-12-05 16:00 | Winter | FALSE | nonsummer
2023-12-05 16:00 | 2023-12-05 17:00 | Winter | TRUE | nonsummer
2023-12-05 17:00 | 2023-12-05 18:00 | Winter | TRUE | nonsummer
2023-12-05 18:00 | 2023-12-05 19:00 | Winter | TRUE | nonsummer
2023-12-05 19:00 | 2023-12-05 20:00 | Winter | TRUE | nonsummer
2023-12-05 20:00 | 2023-12-05 21:00 | Winter | TRUE | nonsummer
2023-12-05 21:00 | 2023-12-05 22:00 | Winter | FALSE | nonsummer
2023-12-05 22:00 | 2023-12-05 23:00 | Winter | FALSE | nonsummer
2023-12-05 23:00 | 2023-12-06 | Winter | FALSE | nonsummer
2023-12-06 | 2023-12-06 01:00 | Winter | FALSE | nonsummer
2023-12-06 01:00 | 2023-12-06 02:00 | Winter | FALSE | nonsummer
2023-12-06 02:00 | 2023-12-06 03:00 | Winter | FALSE | nonsummer
2023-12-06 03:00 | 2023-12-06 04:00 | Winter | FALSE | nonsummer
2023-12-06 04:00 | 2023-12-06 05:00 | Winter | FALSE | nonsummer
2023-12-06 05:00 | 2023-12-06 06:00 | Winter | FALSE | nonsummer
2023-12-06 06:00 | 2023-12-06 07:00 | Winter | FALSE | nonsummer
2023-12-06 07:00 | 2023-12-06 08:00 | Winter | FALSE | nonsummer
2023-12-06 08:00 | 2023-12-06 09:00 | Winter | FALSE | nonsummer
2023-12-06 09:00 | 2023-12-06 10:00 | Winter | FALSE | nonsummer
2023-12-06 10:00 | 2023-12-06 11:00 | Winter | FALSE | nonsummer
2023-12-06 11:00 | 2023-12-06 12:00 | Winter | FALSE | nonsummer
2023-12-06 12:00 | 2023-12-06 13:00 | Winter | FALSE | nonsummer
2023-12-06 13:00 | 2023-12-06 14:00 | Winter | FALSE | nonsummer
2023-12-06 14:00 | 2023-12-06 15:00 | Winter | FALSE | nonsummer
2023-12-06 15:00 | 2023-12-06 16:00 | Winter | FALSE | nonsummer
2023-12-06 16:00 | 2023-12-06 17:00 | Winter | TRUE | nonsummer
2023-12-06 17:00 | 2023-12-06 18:00 | Winter | TRUE | nonsummer
2023-12-06 18:00 | 2023-12-06 19:00 | Winter | TRUE | nonsummer
2023-12-06 19:00 | 2023-12-06 20:00 | Winter | TRUE | nonsummer
2023-12-06 20:00 | 2023-12-06 21:00 | Winter | TRUE | nonsummer
2023-12-06 21:00 | 2023-12-06 22:00 | Winter | FALSE | nonsummer
2023-12-06 22:00 | 2023-12-06 23:00 | Winter | FALSE | nonsummer
2023-12-06 23:00 | 2023-12-07 | Winter | FALSE | nonsummer
2023-12-07 | 2023-12-07 01:00 | Winter | FALSE | nonsummer
2023-12-07 01:00 | 2023-12-07 02:00 | Winter | FALSE | nonsummer
2023-12-07 02:00 | 2023-12-07 03:00 | Winter | FALSE | nonsummer
2023-12-07 03:00 | 2023-12-07 04:00 | Winter | FALSE | nonsummer
2023-12-07 04:00 | 2023-12-07 05:00 | Winter | FALSE | nonsummer
2023-12-07 05:00 | 2023-12-07 06:00 | Winter | FALSE | nonsummer
2023-12-07 06:00 | 2023-12-07 07:00 | Winter | FALSE | nonsummer
2023-12-07 07:00 | 2023-12-07 08:00 | Winter | FALSE | nonsummer
2023-12-07 08:00 | 2023-12-07 09:00 | Winter | FALSE | nonsummer
2023-12-07 09:00 | 2023-12-07 10:00 | Winter | FALSE | nonsummer
2023-12-07 10:00 | 2023-12-07 11:00 | Winter | FALSE | nonsummer
2023-12-07 11:00 | 2023-12-07 12:00 | Winter | FALSE | nonsummer
2023-12-07 12:00 | 2023-12-07 13:00 | Winter | FALSE | nonsummer
2023-12-07 13:00 | 2023-12-07 14:00 | Winter | FALSE | nonsummer
2023-12-07 14:00 | 2023-12-07 15:00 | Winter | FALSE | nonsummer
2023-12-07 15:00 | 2023-12-07 16:00 | Winter | FALSE | nonsummer
2023-12-07 16:00 | 2023-12-07 17:00 | Winter | TRUE | nonsummer
2023-12-07 17:00 | 2023-12-07 18:00 | Winter | TRUE | nonsummer
2023-12-07 18:00 | 2023-12-07 19:00 | Winter | TRUE | nonsummer
2023-12-07 19:00 | 2023-12-07 20:00 | Winter | TRUE | nonsummer
2023-12-07 20:00 | 2023-12-07 21:00 | Winter | TRUE | nonsummer
2023-12-07 21:00 | 2023-12-07 22:00 | Winter | FALSE | nonsummer
2023-12-07 22:00 | 2023-12-07 23:00 | Winter | FALSE | nonsummer
2023-12-07 23:00 | 2023-12-08 | Winter | FALSE | nonsummer
2023-12-08 | 2023-12-08 01:00 | Winter | FALSE | nonsummer
2023-12-08 01:00 | 2023-12-08 02:00 | Winter | FALSE | nonsummer
2023-12-08 02:00 | 2023-12-08 03:00 | Winter | FALSE | nonsummer
2023-12-08 03:00 | 2023-12-08 04:00 | Winter | FALSE | nonsummer
2023-12-08 04:00 | 2023-12-08 05:00 | Winter | FALSE | nonsummer
2023-12-08 05:00 | 2023-12-08 06:00 | Winter | FALSE | nonsummer
2023-12-08 06:00 | 2023-12-08 07:00 | Winter | FALSE | nonsummer
2023-12-08 07:00 | 2023-12-08 08:00 | Winter | FALSE | nonsummer
2023-12-08 08:00 | 2023-12-08 09:00 | Winter | FALSE | nonsummer
2023-12-08 09:00 | 2023-12-08 10:00 | Winter | FALSE | nonsummer
2023-12-08 10:00 | 2023-12-08 11:00 | Winter | FALSE | nonsummer
2023-12-08 11:00 | 2023-12-08 12:00 | Winter | FALSE | nonsummer
2023-12-08 12:00 | 2023-12-08 13:00 | Winter | FALSE | nonsummer
2023-12-08 13:00 | 2023-12-08 14:00 | Winter | FALSE | nonsummer
2023-12-08 14:00 | 2023-12-08 15:00 | Winter | FALSE | nonsummer
2023-12-08 15:00 | 2023-12-08 16:00 | Winter | FALSE | nonsummer
2023-12-08 16:00 | 2023-12-08 17:00 | Winter | TRUE | nonsummer
2023-12-08 17:00 | 2023-12-08 18:00 | Winter | TRUE | nonsummer
2023-12-08 18:00 | 2023-12-08 19:00 | Winter | TRUE | nonsummer
2023-12-08 19:00 | 2023-12-08 20:00 | Winter | TRUE | nonsummer
2023-12-08 20:00 | 2023-12-08 21:00 | Winter | TRUE | nonsummer
2023-12-08 21:00 | 2023-12-08 22:00 | Winter | FALSE | nonsummer
2023-12-08 22:00 | 2023-12-08 23:00 | Winter | FALSE | nonsummer
2023-12-08 23:00 | 2023-12-09 | Winter | FALSE | nonsummer
2023-12-09 | 2023-12-09 01:00 | Winter | FALSE | nonsummer
2023-12-09 01:00 | 2023-12-09 02:00 | Winter | FALSE | nonsummer
2023-12-09 02:00 | 2023-12-09 03:00 | Winter | FALSE | nonsummer
2023-12-09 03:00 | 2023-12-09 04:00 | Winter | FALSE | nonsummer
2023-12-09 04:00 | 2023-12-09 05:00 | Winter | FALSE | nonsummer
2023-12-09 05:00 | 2023-12-09 06:00 | Winter | FALSE | nonsummer
2023-12-09 06:00 | 2023-12-09 07:00 | Winter | FALSE | nonsummer
2023-12-09 07:00 | 2023-12-09 08:00 | Winter | FALSE | nonsummer
2023-12-09 08:00 | 2023-12-09 09:00 | Winter | FALSE | nonsummer
2023-12-09 09:00 | 2023-12-09 10:00 | Winter | FALSE | nonsummer
2023-12-09 10:00 | 2023-12-09 11:00 | Winter | FALSE | nonsummer
2023-12-09 11:00 | 2023-12-09 12:00 | Winter | FALSE | nonsummer
2023-12-09 12:00 | 2023-12-09 13:00 | Winter | FALSE | nonsummer
2023-12-09 13:00 | 2023-12-09 14:00 | Winter | FALSE | nonsummer
2023-12-09 14:00 | 2023-12-09 15:00 | Winter | FALSE | nonsummer
2023-12-09 15:00 | 2023-12-09 16:00 | Winter | FALSE | nonsummer
2023-12-09 16:00 | 2023-12-09 17:00 | Winter | TRUE | nonsummer
2023-12-09 17:00 | 2023-12-09 18:00 | Winter | TRUE | nonsummer
2023-12-09 18:00 | 2023-12-09 19:00 | Winter | TRUE | nonsummer
2023-12-09 19:00 | 2023-12-09 20:00 | Winter | TRUE | nonsummer
2023-12-09 20:00 | 2023-12-09 21:00 | Winter | TRUE | nonsummer
2023-12-09 21:00 | 2023-12-09 22:00 | Winter | FALSE | nonsummer
2023-12-09 22:00 | 2023-12-09 23:00 | Winter | FALSE | nonsummer
2023-12-09 23:00 | 2023-12-10 | Winter | FALSE | nonsummer
2023-12-10 | 2023-12-10 01:00 | Winter | FALSE | nonsummer
2023-12-10 01:00 | 2023-12-10 02:00 | Winter | FALSE | nonsummer
2023-12-10 02:00 | 2023-12-10 03:00 | Winter | FALSE | nonsummer
2023-12-10 03:00 | 2023-12-10 04:00 | Winter | FALSE | nonsummer
2023-12-10 04:00 | 2023-12-10 05:00 | Winter | FALSE | nonsummer
2023-12-10 05:00 | 2023-12-10 06:00 | Winter | FALSE | nonsummer
2023-12-10 06:00 | 2023-12-10 07:00 | Winter | FALSE | nonsummer
2023-12-10 07:00 | 2023-12-10 08:00 | Winter | FALSE | nonsummer
2023-12-10 08:00 | 2023-12-10 09:00 | Winter | FALSE | nonsummer
2023-12-10 09:00 | 2023-12-10 10:00 | Winter | FALSE | nonsummer
2023-12-10 10:00 | 2023-12-10 11:00 | Winter | FALSE | nonsummer
2023-12-10 11:00 | 2023-12-10 12:00 | Winter | FALSE | nonsummer
2023-12-10 12:00 | 2023-12-10 13:00 | Winter | FALSE | nonsummer
2023-12-10 13:00 | 2023-12-10 14:00 | Winter | FALSE | nonsummer
2023-12-10 14:00 | 2023-12-10 15:00 | Winter | FALSE | nonsummer
2023-12-10 15:00 | 2023-12-10 16:00 | Winter | FALSE | nonsummer
2023-12-10 16:00 | 2023-12-10 17:00 | Winter | TRUE | nonsummer
2023-12-10 17:00 | 2023-12-10 18:00 | Winter | TRUE | nonsummer
2023-12-10 18:00 | 2023-12-10 19:00 | Winter | TRUE | nonsummer
2023-12-10 19:00 | 2023-12-10 20:00 | Winter | TRUE | nonsummer
2023-12-10 20:00 | 2023-12-10 21:00 | Winter | TRUE | nonsummer
2023-12-10 21:00 | 2023-12-10 22:00 | Winter | FALSE | nonsummer
2023-12-10 22:00 | 2023-12-10 23:00 | Winter | FALSE | nonsummer
2023-12-10 23:00 | 2023-12-11 | Winter | FALSE | nonsummer
2023-12-11 | 2023-12-11 01:00 | Winter | FALSE | nonsummer
2023-12-11 01:00 | 2023-12-11 02:00 | Winter | FALSE | nonsummer
2023-12-11 02:00 | 2023-12-11 03:00 | Winter | FALSE | nonsummer
2023-12-11 03:00 | 2023-12-11 04:00 | Winter | FALSE | nonsummer
2023-12-11 04:00 | 2023-12-11 05:00 | Winter | FALSE | nonsummer
2023-12-11 05:00 | 2023-12-11 06:00 | Winter | FALSE | nonsummer
2023-12-11 06:00 | 2023-12-11 07:00 | Winter | FALSE | nonsummer
2023-12-11 07:00 | 2023-12-11 08:00 | Winter | FALSE | nonsummer
2023-12-11 08:00 | 2023-12-11 09:00 | Winter | FALSE | nonsummer
2023-12-11 09:00 | 2023-12-11 10:00 | Winter | FALSE | nonsummer
2023-12-11 10:00 | 2023-12-11 11:00 | Winter | FALSE | nonsummer
2023-12-11 11:00 | 2023-12-11 12:00 | Winter | FALSE | nonsummer
2023-12-11 12:00 | 2023-12-11 13:00 | Winter | FALSE | nonsummer
2023-12-11 13:00 | 2023-12-11 14:00 | Winter | FALSE | nonsummer
2023-12-11 14:00 | 2023-12-11 15:00 | Winter | FALSE | nonsummer
2023-12-11 15:00 | 2023-12-11 16:00 | Winter | FALSE | nonsummer
2023-12-11 16:00 | 2023-12-11 17:00 | Winter | TRUE | nonsummer
2023-12-11 17:00 | 2023-12-11 18:00 | Winter | TRUE | nonsummer
2023-12-11 18:00 | 2023-12-11 19:00 | Winter | TRUE | nonsummer
2023-12-11 19:00 | 2023-12-11 20:00 | Winter | TRUE | nonsummer
2023-12-11 20:00 | 2023-12-11 21:00 | Winter | TRUE | nonsummer
2023-12-11 21:00 | 2023-12-11 22:00 | Winter | FALSE | nonsummer
2023-12-11 22:00 | 2023-12-11 23:00 | Winter | FALSE | nonsummer
2023-12-11 23:00 | 2023-12-12 | Winter | FALSE | nonsummer
2023-12-12 | 2023-12-12 01:00 | Winter | FALSE | nonsummer
2023-12-12 01:00 | 2023-12-12 02:00 | Winter | FALSE | nonsummer
2023-12-12 02:00 | 2023-12-12 03:00 | Winter | FALSE | nonsummer
2023-12-12 03:00 | 2023-12-12 04:00 | Winter | FALSE | nonsummer
2023-12-12 04:00 | 2023-12-12 05:00 | Winter | FALSE | nonsummer
2023-12-12 05:00 | 2023-12-12 06:00 | Winter | FALSE | nonsummer
2023-12-12 06:00 | 2023-12-12 07:00 | Winter | FALSE | nonsummer
2023-12-12 07:00 | 2023-12-12 08:00 | Winter | FALSE | nonsummer
2023-12-12 08:00 | 2023-12-12 09:00 | Winter | FALSE | nonsummer
2023-12-12 09:00 | 2023-12-12 10:00 | Winter | FALSE | nonsummer
2023-12-12 10:00 | 2023-12-12 11:00 | Winter | FALSE | nonsummer
2023-12-12 11:00 | 2023-12-12 12:00 | Winter | FALSE | nonsummer
2023-12-12 12:00 | 2023-12-12 13:00 | Winter | FALSE | nonsummer
2023-12-12 13:00 | 2023-12-12 14:00 | Winter | FALSE | nonsummer
2023-12-12 14:00 | 2023-12-12 15:00 | Winter | FALSE | nonsummer
2023-12-12 15:00 | 2023-12-12 16:00 | Winter | FALSE | nonsummer
2023-12-12 16:00 | 2023-12-12 17:00 | Winter | TRUE | nonsummer
2023-12-12 17:00 | 2023-12-12 18:00 | Winter | TRUE | nonsummer
2023-12-12 18:00 | 2023-12-12 19:00 | Winter | TRUE | nonsummer
2023-12-12 19:00 | 2023-12-12 20:00 | Winter | TRUE | nonsummer
2023-12-12 20:00 | 2023-12-12 21:00 | Winter | TRUE | nonsummer
2023-12-12 21:00 | 2023-12-12 22:00 | Winter | FALSE | nonsummer
2023-12-12 22:00 | 2023-12-12 23:00 | Winter | FALSE | nonsummer
2023-12-12 23:00 | 2023-12-13 | Winter | FALSE | nonsummer
2023-12-13 | 2023-12-13 01:00 | Winter | FALSE | nonsummer
2023-12-13 01:00 | 2023-12-13 02:00 | Winter | FALSE | nonsummer
2023-12-13 02:00 | 2023-12-13 03:00 | Winter | FALSE | nonsummer
2023-12-13 03:00 | 2023-12-13 04:00 | Winter | FALSE | nonsummer
2023-12-13 04:00 | 2023-12-13 05:00 | Winter | FALSE | nonsummer
2023-12-13 05:00 | 2023-12-13 06:00 | Winter | FALSE | nonsummer
2023-12-13 06:00 | 2023-12-13 07:00 | Winter | FALSE | nonsummer
2023-12-13 07:00 | 2023-12-13 08:00 | Winter | FALSE | nonsummer
2023-12-13 08:00 | 2023-12-13 09:00 | Winter | FALSE | nonsummer
2023-12-13 09:00 | 2023-12-13 10:00 | Winter | FALSE | nonsummer
2023-12-13 10:00 | 2023-12-13 11:00 | Winter | FALSE | nonsummer
2023-12-13 11:00 | 2023-12-13 12:00 | Winter | FALSE | nonsummer
2023-12-13 12:00 | 2023-12-13 13:00 | Winter | FALSE | nonsummer
2023-12-13 13:00 | 2023-12-13 14:00 | Winter | FALSE | nonsummer
2023-12-13 14:00 | 2023-12-13 15:00 | Winter | FALSE | nonsummer
2023-12-13 15:00 | 2023-12-13 16:00 | Winter | FALSE | nonsummer
2023-12-13 16:00 | 2023-12-13 17:00 | Winter | TRUE | nonsummer
2023-12-13 17:00 | 2023-12-13 18:00 | Winter | TRUE | nonsummer
2023-12-13 18:00 | 2023-12-13 19:00 | Winter | TRUE | nonsummer
2023-12-13 19:00 | 2023-12-13 20:00 | Winter | TRUE | nonsummer
2023-12-13 20:00 | 2023-12-13 21:00 | Winter | TRUE | nonsummer
2023-12-13 21:00 | 2023-12-13 22:00 | Winter | FALSE | nonsummer
2023-12-13 22:00 | 2023-12-13 23:00 | Winter | FALSE | nonsummer
2023-12-13 23:00 | 2023-12-14 | Winter | FALSE | nonsummer
2023-12-14 | 2023-12-14 01:00 | Winter | FALSE | nonsummer
2023-12-14 01:00 | 2023-12-14 02:00 | Winter | FALSE | nonsummer
2023-12-14 02:00 | 2023-12-14 03:00 | Winter | FALSE | nonsummer
2023-12-14 03:00 | 2023-12-14 04:00 | Winter | FALSE | nonsummer
2023-12-14 04:00 | 2023-12-14 05:00 | Winter | FALSE | nonsummer
2023-12-14 05:00 | 2023-12-14 06:00 | Winter | FALSE | nonsummer
2023-12-14 06:00 | 2023-12-14 07:00 | Winter | FALSE | nonsummer
2023-12-14 07:00 | 2023-12-14 08:00 | Winter | FALSE | nonsummer
2023-12-14 08:00 | 2023-12-14 09:00 | Winter | FALSE | nonsummer
2023-12-14 09:00 | 2023-12-14 10:00 | Winter | FALSE | nonsummer
2023-12-14 10:00 | 2023-12-14 11:00 | Winter | FALSE | nonsummer
2023-12-14 11:00 | 2023-12-14 12:00 | Winter | FALSE | nonsummer
2023-12-14 12:00 | 2023-12-14 13:00 | Winter | FALSE | nonsummer
2023-12-14 13:00 | 2023-12-14 14:00 | Winter | FALSE | nonsummer
2023-12-14 14:00 | 2023-12-14 15:00 | Winter | FALSE | nonsummer
2023-12-14 15:00 | 2023-12-14 16:00 | Winter | FALSE | nonsummer
2023-12-14 16:00 | 2023-12-14 17:00 | Winter | TRUE | nonsummer
2023-12-14 17:00 | 2023-12-14 18:00 | Winter | TRUE | nonsummer
2023-12-14 18:00 | 2023-12-14 19:00 | Winter | TRUE | nonsummer
2023-12-14 19:00 | 2023-12-14 20:00 | Winter | TRUE | nonsummer
2023-12-14 20:00 | 2023-12-14 21:00 | Winter | TRUE | nonsummer
2023-12-14 21:00 | 2023-12-14 22:00 | Winter | FALSE | nonsummer
2023-12-14 22:00 | 2023-12-14 23:00 | Winter | FALSE | nonsummer
2023-12-14 23:00 | 2023-12-15 | Winter | FALSE | nonsummer
2023-12-15 | 2023-12-15 01:00 | Winter | FALSE | nonsummer
2023-12-15 01:00 | 2023-12-15 02:00 | Winter | FALSE | nonsummer
2023-12-15 02:00 | 2023-12-15 03:00 | Winter | FALSE | nonsummer
2023-12-15 03:00 | 2023-12-15 04:00 | Winter | FALSE | nonsummer
2023-12-15 04:00 | 2023-12-15 05:00 | Winter | FALSE | nonsummer
2023-12-15 05:00 | 2023-12-15 06:00 | Winter | FALSE | nonsummer
2023-12-15 06:00 | 2023-12-15 07:00 | Winter | FALSE | nonsummer
2023-12-15 07:00 | 2023-12-15 08:00 | Winter | FALSE | nonsummer
2023-12-15 08:00 | 2023-12-15 09:00 | Winter | FALSE | nonsummer
2023-12-15 09:00 | 2023-12-15 10:00 | Winter | FALSE | nonsummer
2023-12-15 10:00 | 2023-12-15 11:00 | Winter | FALSE | nonsummer
2023-12-15 11:00 | 2023-12-15 12:00 | Winter | FALSE | nonsummer
2023-12-15 12:00 | 2023-12-15 13:00 | Winter | FALSE | nonsummer
2023-12-15 13:00 | 2023-12-15 14:00 | Winter | FALSE | nonsummer
2023-12-15 14:00 | 2023-12-15 15:00 | Winter | FALSE | nonsummer
2023-12-15 15:00 | 2023-12-15 16:00 | Winter | FALSE | nonsummer
2023-12-15 16:00 | 2023-12-15 17:00 | Winter | TRUE | nonsummer
2023-12-15 17:00 | 2023-12-15 18:00 | Winter | TRUE | nonsummer
2023-12-15 18:00 | 2023-12-15 19:00 | Winter | TRUE | nonsummer
2023-12-15 19:00 | 2023-12-15 20:00 | Winter | TRUE | nonsummer
2023-12-15 20:00 | 2023-12-15 21:00 | Winter | TRUE | nonsummer
2023-12-15 21:00 | 2023-12-15 22:00 | Winter | FALSE | nonsummer
2023-12-15 22:00 | 2023-12-15 23:00 | Winter | FALSE | nonsummer
2023-12-15 23:00 | 2023-12-16 | Winter | FALSE | nonsummer
2023-12-16 | 2023-12-16 01:00 | Winter | FALSE | nonsummer
2023-12-16 01:00 | 2023-12-16 02:00 | Winter | FALSE | nonsummer
2023-12-16 02:00 | 2023-12-16 03:00 | Winter | FALSE | nonsummer
2023-12-16 03:00 | 2023-12-16 04:00 | Winter | FALSE | nonsummer
2023-12-16 04:00 | 2023-12-16 05:00 | Winter | FALSE | nonsummer
2023-12-16 05:00 | 2023-12-16 06:00 | Winter | FALSE | nonsummer
2023-12-16 06:00 | 2023-12-16 07:00 | Winter | FALSE | nonsummer
2023-12-16 07:00 | 2023-12-16 08:00 | Winter | FALSE | nonsummer
2023-12-16 08:00 | 2023-12-16 09:00 | Winter | FALSE | nonsummer
2023-12-16 09:00 | 2023-12-16 10:00 | Winter | FALSE | nonsummer
2023-12-16 10:00 | 2023-12-16 11:00 | Winter | FALSE | nonsummer
2023-12-16 11:00 | 2023-12-16 12:00 | Winter | FALSE | nonsummer
2023-12-16 12:00 | 2023-12-16 13:00 | Winter | FALSE | nonsummer
2023-12-16 13:00 | 2023-12-16 14:00 | Winter | FALSE | nonsummer
2023-12-16 14:00 | 2023-12-16 15:00 | Winter | FALSE | nonsummer
2023-12-16 15:00 | 2023-12-16 16:00 | Winter | FALSE | nonsummer
2023-12-16 16:00 | 2023-12-16 17:00 | Winter | TRUE | nonsummer
2023-12-16 17:00 | 2023-12-16 18:00 | Winter | TRUE | nonsummer
2023-12-16 18:00 | 2023-12-16 19:00 | Winter | TRUE | nonsummer
2023-12-16 19:00 | 2023-12-16 20:00 | Winter | TRUE | nonsummer
2023-12-16 20:00 | 2023-12-16 21:00 | Winter | TRUE | nonsummer
2023-12-16 21:00 | 2023-12-16 22:00 | Winter | FALSE | nonsummer
2023-12-16 22:00 | 2023-12-16 23:00 | Winter | FALSE | nonsummer
2023-12-16 23:00 | 2023-12-17 | Winter | FALSE | nonsummer
2023-12-17 | 2023-12-17 01:00 | Winter | FALSE | nonsummer
2023-12-17 01:00 | 2023-12-17 02:00 | Winter | FALSE | nonsummer
2023-12-17 02:00 | 2023-12-17 03:00 | Winter | FALSE | nonsummer
2023-12-17 03:00 | 2023-12-17 04:00 | Winter | FALSE | nonsummer
2023-12-17 04:00 | 2023-12-17 05:00 | Winter | FALSE | nonsummer
2023-12-17 05:00 | 2023-12-17 06:00 | Winter | FALSE | nonsummer
2023-12-17 06:00 | 2023-12-17 07:00 | Winter | FALSE | nonsummer
2023-12-17 07:00 | 2023-12-17 08:00 | Winter | FALSE | nonsummer
2023-12-17 08:00 | 2023-12-17 09:00 | Winter | FALSE | nonsummer
2023-12-17 09:00 | 2023-12-17 10:00 | Winter | FALSE | nonsummer
2023-12-17 10:00 | 2023-12-17 11:00 | Winter | FALSE | nonsummer
2023-12-17 11:00 | 2023-12-17 12:00 | Winter | FALSE | nonsummer
2023-12-17 12:00 | 2023-12-17 13:00 | Winter | FALSE | nonsummer
2023-12-17 13:00 | 2023-12-17 14:00 | Winter | FALSE | nonsummer
2023-12-17 14:00 | 2023-12-17 15:00 | Winter | FALSE | nonsummer
2023-12-17 15:00 | 2023-12-17 16:00 | Winter | FALSE | nonsummer
2023-12-17 16:00 | 2023-12-17 17:00 | Winter | TRUE | nonsummer
2023-12-17 17:00 | 2023-12-17 18:00 | Winter | TRUE | nonsummer
2023-12-17 18:00 | 2023-12-17 19:00 | Winter | TRUE | nonsummer
2023-12-17 19:00 | 2023-12-17 20:00 | Winter | TRUE | nonsummer
2023-12-17 20:00 | 2023-12-17 21:00 | Winter | TRUE | nonsummer
2023-12-17 21:00 | 2023-12-17 22:00 | Winter | FALSE | nonsummer
2023-12-17 22:00 | 2023-12-17 23:00 | Winter | FALSE | nonsummer
2023-12-17 23:00 | 2023-12-18 | Winter | FALSE | nonsummer
2023-12-18 | 2023-12-18 01:00 | Winter | FALSE | nonsummer
2023-12-18 01:00 | 2023-12-18 02:00 | Winter | FALSE | nonsummer
2023-12-18 02:00 | 2023-12-18 03:00 | Winter | FALSE | nonsummer
2023-12-18 03:00 | 2023-12-18 04:00 | Winter | FALSE | nonsummer
2023-12-18 04:00 | 2023-12-18 05:00 | Winter | FALSE | nonsummer
2023-12-18 05:00 | 2023-12-18 06:00 | Winter | FALSE | nonsummer
2023-12-18 06:00 | 2023-12-18 07:00 | Winter | FALSE | nonsummer
2023-12-18 07:00 | 2023-12-18 08:00 | Winter | FALSE | nonsummer
2023-12-18 08:00 | 2023-12-18 09:00 | Winter | FALSE | nonsummer
2023-12-18 09:00 | 2023-12-18 10:00 | Winter | FALSE | nonsummer
2023-12-18 10:00 | 2023-12-18 11:00 | Winter | FALSE | nonsummer
2023-12-18 11:00 | 2023-12-18 12:00 | Winter | FALSE | nonsummer
2023-12-18 12:00 | 2023-12-18 13:00 | Winter | FALSE | nonsummer
2023-12-18 13:00 | 2023-12-18 14:00 | Winter | FALSE | nonsummer
2023-12-18 14:00 | 2023-12-18 15:00 | Winter | FALSE | nonsummer
2023-12-18 15:00 | 2023-12-18 16:00 | Winter | FALSE | nonsummer
2023-12-18 16:00 | 2023-12-18 17:00 | Winter | TRUE | nonsummer
2023-12-18 17:00 | 2023-12-18 18:00 | Winter | TRUE | nonsummer
2023-12-18 18:00 | 2023-12-18 19:00 | Winter | TRUE | nonsummer
2023-12-18 19:00 | 2023-12-18 20:00 | Winter | TRUE | nonsummer
2023-12-18 20:00 | 2023-12-18 21:00 | Winter | TRUE | nonsummer
2023-12-18 21:00 | 2023-12-18 22:00 | Winter | FALSE | nonsummer
2023-12-18 22:00 | 2023-12-18 23:00 | Winter | FALSE | nonsummer
2023-12-18 23:00 | 2023-12-19 | Winter | FALSE | nonsummer
2023-12-19 | 2023-12-19 01:00 | Winter | FALSE | nonsummer
2023-12-19 01:00 | 2023-12-19 02:00 | Winter | FALSE | nonsummer
2023-12-19 02:00 | 2023-12-19 03:00 | Winter | FALSE | nonsummer
2023-12-19 03:00 | 2023-12-19 04:00 | Winter | FALSE | nonsummer
2023-12-19 04:00 | 2023-12-19 05:00 | Winter | FALSE | nonsummer
2023-12-19 05:00 | 2023-12-19 06:00 | Winter | FALSE | nonsummer
2023-12-19 06:00 | 2023-12-19 07:00 | Winter | FALSE | nonsummer
2023-12-19 07:00 | 2023-12-19 08:00 | Winter | FALSE | nonsummer
2023-12-19 08:00 | 2023-12-19 09:00 | Winter | FALSE | nonsummer
2023-12-19 09:00 | 2023-12-19 10:00 | Winter | FALSE | nonsummer
2023-12-19 10:00 | 2023-12-19 11:00 | Winter | FALSE | nonsummer
2023-12-19 11:00 | 2023-12-19 12:00 | Winter | FALSE | nonsummer
2023-12-19 12:00 | 2023-12-19 13:00 | Winter | FALSE | nonsummer
2023-12-19 13:00 | 2023-12-19 14:00 | Winter | FALSE | nonsummer
2023-12-19 14:00 | 2023-12-19 15:00 | Winter | FALSE | nonsummer
2023-12-19 15:00 | 2023-12-19 16:00 | Winter | FALSE | nonsummer
2023-12-19 16:00 | 2023-12-19 17:00 | Winter | TRUE | nonsummer
2023-12-19 17:00 | 2023-12-19 18:00 | Winter | TRUE | nonsummer
2023-12-19 18:00 | 2023-12-19 19:00 | Winter | TRUE | nonsummer
2023-12-19 19:00 | 2023-12-19 20:00 | Winter | TRUE | nonsummer
2023-12-19 20:00 | 2023-12-19 21:00 | Winter | TRUE | nonsummer
2023-12-19 21:00 | 2023-12-19 22:00 | Winter | FALSE | nonsummer
2023-12-19 22:00 | 2023-12-19 23:00 | Winter | FALSE | nonsummer
2023-12-19 23:00 | 2023-12-20 | Winter | FALSE | nonsummer
2023-12-20 | 2023-12-20 01:00 | Winter | FALSE | nonsummer
2023-12-20 01:00 | 2023-12-20 02:00 | Winter | FALSE | nonsummer
2023-12-20 02:00 | 2023-12-20 03:00 | Winter | FALSE | nonsummer
2023-12-20 03:00 | 2023-12-20 04:00 | Winter | FALSE | nonsummer
2023-12-20 04:00 | 2023-12-20 05:00 | Winter | FALSE | nonsummer
2023-12-20 05:00 | 2023-12-20 06:00 | Winter | FALSE | nonsummer
2023-12-20 06:00 | 2023-12-20 07:00 | Winter | FALSE | nonsummer
2023-12-20 07:00 | 2023-12-20 08:00 | Winter | FALSE | nonsummer
2023-12-20 08:00 | 2023-12-20 09:00 | Winter | FALSE | nonsummer
2023-12-20 09:00 | 2023-12-20 10:00 | Winter | FALSE | nonsummer
2023-12-20 10:00 | 2023-12-20 11:00 | Winter | FALSE | nonsummer
2023-12-20 11:00 | 2023-12-20 12:00 | Winter | FALSE | nonsummer
2023-12-20 12:00 | 2023-12-20 13:00 | Winter | FALSE | nonsummer
2023-12-20 13:00 | 2023-12-20 14:00 | Winter | FALSE | nonsummer
2023-12-20 14:00 | 2023-12-20 15:00 | Winter | FALSE | nonsummer
2023-12-20 15:00 | 2023-12-20 16:00 | Winter | FALSE | nonsummer
2023-12-20 16:00 | 2023-12-20 17:00 | Winter | TRUE | nonsummer
2023-12-20 17:00 | 2023-12-20 18:00 | Winter | TRUE | nonsummer
2023-12-20 18:00 | 2023-12-20 19:00 | Winter | TRUE | nonsummer
2023-12-20 19:00 | 2023-12-20 20:00 | Winter | TRUE | nonsummer
2023-12-20 20:00 | 2023-12-20 21:00 | Winter | TRUE | nonsummer
2023-12-20 21:00 | 2023-12-20 22:00 | Winter | FALSE | nonsummer
2023-12-20 22:00 | 2023-12-20 23:00 | Winter | FALSE | nonsummer
2023-12-20 23:00 | 2023-12-21 | Winter | FALSE | nonsummer
2023-12-21 | 2023-12-21 01:00 | Winter | FALSE | nonsummer
2023-12-21 01:00 | 2023-12-21 02:00 | Winter | FALSE | nonsummer
2023-12-21 02:00 | 2023-12-21 03:00 | Winter | FALSE | nonsummer
2023-12-21 03:00 | 2023-12-21 04:00 | Winter | FALSE | nonsummer
2023-12-21 04:00 | 2023-12-21 05:00 | Winter | FALSE | nonsummer
2023-12-21 05:00 | 2023-12-21 06:00 | Winter | FALSE | nonsummer
2023-12-21 06:00 | 2023-12-21 07:00 | Winter | FALSE | nonsummer
2023-12-21 07:00 | 2023-12-21 08:00 | Winter | FALSE | nonsummer
2023-12-21 08:00 | 2023-12-21 09:00 | Winter | FALSE | nonsummer
2023-12-21 09:00 | 2023-12-21 10:00 | Winter | FALSE | nonsummer
2023-12-21 10:00 | 2023-12-21 11:00 | Winter | FALSE | nonsummer
2023-12-21 11:00 | 2023-12-21 12:00 | Winter | FALSE | nonsummer
2023-12-21 12:00 | 2023-12-21 13:00 | Winter | FALSE | nonsummer
2023-12-21 13:00 | 2023-12-21 14:00 | Winter | FALSE | nonsummer
2023-12-21 14:00 | 2023-12-21 15:00 | Winter | FALSE | nonsummer
2023-12-21 15:00 | 2023-12-21 16:00 | Winter | FALSE | nonsummer
2023-12-21 16:00 | 2023-12-21 17:00 | Winter | TRUE | nonsummer
2023-12-21 17:00 | 2023-12-21 18:00 | Winter | TRUE | nonsummer
2023-12-21 18:00 | 2023-12-21 19:00 | Winter | TRUE | nonsummer
2023-12-21 19:00 | 2023-12-21 20:00 | Winter | TRUE | nonsummer
2023-12-21 20:00 | 2023-12-21 21:00 | Winter | TRUE | nonsummer
2023-12-21 21:00 | 2023-12-21 22:00 | Winter | FALSE | nonsummer
2023-12-21 22:00 | 2023-12-21 23:00 | Winter | FALSE | nonsummer
2023-12-21 23:00 | 2023-12-22 | Winter | FALSE | nonsummer
2023-12-22 | 2023-12-22 01:00 | Winter | FALSE | nonsummer
2023-12-22 01:00 | 2023-12-22 02:00 | Winter | FALSE | nonsummer
2023-12-22 02:00 | 2023-12-22 03:00 | Winter | FALSE | nonsummer
2023-12-22 03:00 | 2023-12-22 04:00 | Winter | FALSE | nonsummer
2023-12-22 04:00 | 2023-12-22 05:00 | Winter | FALSE | nonsummer
2023-12-22 05:00 | 2023-12-22 06:00 | Winter | FALSE | nonsummer
2023-12-22 06:00 | 2023-12-22 07:00 | Winter | FALSE | nonsummer
2023-12-22 07:00 | 2023-12-22 08:00 | Winter | FALSE | nonsummer
2023-12-22 08:00 | 2023-12-22 09:00 | Winter | FALSE | nonsummer
2023-12-22 09:00 | 2023-12-22 10:00 | Winter | FALSE | nonsummer
2023-12-22 10:00 | 2023-12-22 11:00 | Winter | FALSE | nonsummer
2023-12-22 11:00 | 2023-12-22 12:00 | Winter | FALSE | nonsummer
2023-12-22 12:00 | 2023-12-22 13:00 | Winter | FALSE | nonsummer
2023-12-22 13:00 | 2023-12-22 14:00 | Winter | FALSE | nonsummer
2023-12-22 14:00 | 2023-12-22 15:00 | Winter | FALSE | nonsummer
2023-12-22 15:00 | 2023-12-22 16:00 | Winter | FALSE | nonsummer
2023-12-22 16:00 | 2023-12-22 17:00 | Winter | TRUE | nonsummer
2023-12-22 17:00 | 2023-12-22 18:00 | Winter | TRUE | nonsummer
2023-12-22 18:00 | 2023-12-22 19:00 | Winter | TRUE | nonsummer
2023-12-22 19:00 | 2023-12-22 20:00 | Winter | TRUE | nonsummer
2023-12-22 20:00 | 2023-12-22 21:00 | Winter | TRUE | nonsummer
2023-12-22 21:00 | 2023-12-22 22:00 | Winter | FALSE | nonsummer
2023-12-22 22:00 | 2023-12-22 23:00 | Winter | FALSE | nonsummer
2023-12-22 23:00 | 2023-12-23 | Winter | FALSE | nonsummer
2023-12-23 | 2023-12-23 01:00 | Winter | FALSE | nonsummer
2023-12-23 01:00 | 2023-12-23 02:00 | Winter | FALSE | nonsummer
2023-12-23 02:00 | 2023-12-23 03:00 | Winter | FALSE | nonsummer
2023-12-23 03:00 | 2023-12-23 04:00 | Winter | FALSE | nonsummer
2023-12-23 04:00 | 2023-12-23 05:00 | Winter | FALSE | nonsummer
2023-12-23 05:00 | 2023-12-23 06:00 | Winter | FALSE | nonsummer
2023-12-23 06:00 | 2023-12-23 07:00 | Winter | FALSE | nonsummer
2023-12-23 07:00 | 2023-12-23 08:00 | Winter | FALSE | nonsummer
2023-12-23 08:00 | 2023-12-23 09:00 | Winter | FALSE | nonsummer
2023-12-23 09:00 | 2023-12-23 10:00 | Winter | FALSE | nonsummer
2023-12-23 10:00 | 2023-12-23 11:00 | Winter | FALSE | nonsummer
2023-12-23 11:00 | 2023-12-23 12:00 | Winter | FALSE | nonsummer
2023-12-23 12:00 | 2023-12-23 13:00 | Winter | FALSE | nonsummer
2023-12-23 13:00 | 2023-12-23 14:00 | Winter | FALSE | nonsummer
2023-12-23 14:00 | 2023-12-23 15:00 | Winter | FALSE | nonsummer
2023-12-23 15:00 | 2023-12-23 16:00 | Winter | FALSE | nonsummer
2023-12-23 16:00 | 2023-12-23 17:00 | Winter | TRUE | nonsummer
2023-12-23 17:00 | 2023-12-23 18:00 | Winter | TRUE | nonsummer
2023-12-23 18:00 | 2023-12-23 19:00 | Winter | TRUE | nonsummer
2023-12-23 19:00 | 2023-12-23 20:00 | Winter | TRUE | nonsummer
2023-12-23 20:00 | 2023-12-23 21:00 | Winter | TRUE | nonsummer
2023-12-23 21:00 | 2023-12-23 22:00 | Winter | FALSE | nonsummer
2023-12-23 22:00 | 2023-12-23 23:00 | Winter | FALSE | nonsummer
2023-12-23 23:00 | 2023-12-24 | Winter | FALSE | nonsummer
2023-12-24 | 2023-12-24 01:00 | Winter | FALSE | nonsummer
2023-12-24 01:00 | 2023-12-24 02:00 | Winter | FALSE | nonsummer
2023-12-24 02:00 | 2023-12-24 03:00 | Winter | FALSE | nonsummer
2023-12-24 03:00 | 2023-12-24 04:00 | Winter | FALSE | nonsummer
2023-12-24 04:00 | 2023-12-24 05:00 | Winter | FALSE | nonsummer
2023-12-24 05:00 | 2023-12-24 06:00 | Winter | FALSE | nonsummer
2023-12-24 06:00 | 2023-12-24 07:00 | Winter | FALSE | nonsummer
2023-12-24 07:00 | 2023-12-24 08:00 | Winter | FALSE | nonsummer
2023-12-24 08:00 | 2023-12-24 09:00 | Winter | FALSE | nonsummer
2023-12-24 09:00 | 2023-12-24 10:00 | Winter | FALSE | nonsummer
2023-12-24 10:00 | 2023-12-24 11:00 | Winter | FALSE | nonsummer
2023-12-24 11:00 | 2023-12-24 12:00 | Winter | FALSE | nonsummer
2023-12-24 12:00 | 2023-12-24 13:00 | Winter | FALSE | nonsummer
2023-12-24 13:00 | 2023-12-24 14:00 | Winter | FALSE | nonsummer
2023-12-24 14:00 | 2023-12-24 15:00 | Winter | FALSE | nonsummer
2023-12-24 15:00 | 2023-12-24 16:00 | Winter | FALSE | nonsummer
2023-12-24 16:00 | 2023-12-24 17:00 | Winter | TRUE | nonsummer
2023-12-24 17:00 | 2023-12-24 18:00 | Winter | TRUE | nonsummer
2023-12-24 18:00 | 2023-12-24 19:00 | Winter | TRUE | nonsummer
2023-12-24 19:00 | 2023-12-24 20:00 | Winter | TRUE | nonsummer
2023-12-24 20:00 | 2023-12-24 21:00 | Winter | TRUE | nonsummer
2023-12-24 21:00 | 2023-12-24 22:00 | Winter | FALSE | nonsummer
2023-12-24 22:00 | 2023-12-24 23:00 | Winter | FALSE | nonsummer
2023-12-24 23:00 | 2023-12-25 | Winter | FALSE | nonsummer
2023-12-25 | 2023-12-25 01:00 | Winter | FALSE | nonsummer
2023-12-25 01:00 | 2023-12-25 02:00 | Winter | FALSE | nonsummer
2023-12-25 02:00 | 2023-12-25 03:00 | Winter | FALSE | nonsummer
2023-12-25 03:00 | 2023-12-25 04:00 | Winter | FALSE | nonsummer
2023-12-25 04:00 | 2023-12-25 05:00 | Winter | FALSE | nonsummer
2023-12-25 05:00 | 2023-12-25 06:00 | Winter | FALSE | nonsummer
2023-12-25 06:00 | 2023-12-25 07:00 | Winter | FALSE | nonsummer
2023-12-25 07:00 | 2023-12-25 08:00 | Winter | FALSE | nonsummer
2023-12-25 08:00 | 2023-12-25 09:00 | Winter | FALSE | nonsummer
2023-12-25 09:00 | 2023-12-25 10:00 | Winter | FALSE | nonsummer
2023-12-25 10:00 | 2023-12-25 11:00 | Winter | FALSE | nonsummer
2023-12-25 11:00 | 2023-12-25 12:00 | Winter | FALSE | nonsummer
2023-12-25 12:00 | 2023-12-25 13:00 | Winter | FALSE | nonsummer
2023-12-25 13:00 | 2023-12-25 14:00 | Winter | FALSE | nonsummer
2023-12-25 14:00 | 2023-12-25 15:00 | Winter | FALSE | nonsummer
2023-12-25 15:00 | 2023-12-25 16:00 | Winter | FALSE | nonsummer
2023-12-25 16:00 | 2023-12-25 17:00 | Winter | TRUE | nonsummer
2023-12-25 17:00 | 2023-12-25 18:00 | Winter | TRUE | nonsummer
2023-12-25 18:00 | 2023-12-25 19:00 | Winter | TRUE | nonsummer
2023-12-25 19:00 | 2023-12-25 20:00 | Winter | TRUE | nonsummer
2023-12-25 20:00 | 2023-12-25 21:00 | Winter | TRUE | nonsummer
2023-12-25 21:00 | 2023-12-25 22:00 | Winter | FALSE | nonsummer
2023-12-25 22:00 | 2023-12-25 23:00 | Winter | FALSE | nonsummer
2023-12-25 23:00 | 2023-12-26 | Winter | FALSE | nonsummer
2023-12-26 | 2023-12-26 01:00 | Winter | FALSE | nonsummer
2023-12-26 01:00 | 2023-12-26 02:00 | Winter | FALSE | nonsummer
2023-12-26 02:00 | 2023-12-26 03:00 | Winter | FALSE | nonsummer
2023-12-26 03:00 | 2023-12-26 04:00 | Winter | FALSE | nonsummer
2023-12-26 04:00 | 2023-12-26 05:00 | Winter | FALSE | nonsummer
2023-12-26 05:00 | 2023-12-26 06:00 | Winter | FALSE | nonsummer
2023-12-26 06:00 | 2023-12-26 07:00 | Winter | FALSE | nonsummer
2023-12-26 07:00 | 2023-12-26 08:00 | Winter | FALSE | nonsummer
2023-12-26 08:00 | 2023-12-26 09:00 | Winter | FALSE | nonsummer
2023-12-26 09:00 | 2023-12-26 10:00 | Winter | FALSE | nonsummer
2023-12-26 10:00 | 2023-12-26 11:00 | Winter | FALSE | nonsummer
2023-12-26 11:00 | 2023-12-26 12:00 | Winter | FALSE | nonsummer
2023-12-26 12:00 | 2023-12-26 13:00 | Winter | FALSE | nonsummer
2023-12-26 13:00 | 2023-12-26 14:00 | Winter | FALSE | nonsummer
2023-12-26 14:00 | 2023-12-26 15:00 | Winter | FALSE | nonsummer
2023-12-26 15:00 | 2023-12-26 16:00 | Winter | FALSE | nonsummer
2023-12-26 16:00 | 2023-12-26 17:00 | Winter | TRUE | nonsummer
2023-12-26 17:00 | 2023-12-26 18:00 | Winter | TRUE | nonsummer
2023-12-26 18:00 | 2023-12-26 19:00 | Winter | TRUE | nonsummer
2023-12-26 19:00 | 2023-12-26 20:00 | Winter | TRUE | nonsummer
2023-12-26 20:00 | 2023-12-26 21:00 | Winter | TRUE | nonsummer
2023-12-26 21:00 | 2023-12-26 22:00 | Winter | FALSE | nonsummer
2023-12-26 22:00 | 2023-12-26 23:00 | Winter | FALSE | nonsummer
2023-12-26 23:00 | 2023-12-27 | Winter | FALSE | nonsummer
2023-12-27 | 2023-12-27 01:00 | Winter | FALSE | nonsummer
2023-12-27 01:00 | 2023-12-27 02:00 | Winter | FALSE | nonsummer
2023-12-27 02:00 | 2023-12-27 03:00 | Winter | FALSE | nonsummer
2023-12-27 03:00 | 2023-12-27 04:00 | Winter | FALSE | nonsummer
2023-12-27 04:00 | 2023-12-27 05:00 | Winter | FALSE | nonsummer
2023-12-27 05:00 | 2023-12-27 06:00 | Winter | FALSE | nonsummer
2023-12-27 06:00 | 2023-12-27 07:00 | Winter | FALSE | nonsummer
2023-12-27 07:00 | 2023-12-27 08:00 | Winter | FALSE | nonsummer
2023-12-27 08:00 | 2023-12-27 09:00 | Winter | FALSE | nonsummer
2023-12-27 09:00 | 2023-12-27 10:00 | Winter | FALSE | nonsummer
2023-12-27 10:00 | 2023-12-27 11:00 | Winter | FALSE | nonsummer
2023-12-27 11:00 | 2023-12-27 12:00 | Winter | FALSE | nonsummer
2023-12-27 12:00 | 2023-12-27 13:00 | Winter | FALSE | nonsummer
2023-12-27 13:00 | 2023-12-27 14:00 | Winter | FALSE | nonsummer
2023-12-27 14:00 | 2023-12-27 15:00 | Winter | FALSE | nonsummer
2023-12-27 15:00 | 2023-12-27 16:00 | Winter | FALSE | nonsummer
2023-12-27 16:00 | 2023-12-27 17:00 | Winter | TRUE | nonsummer
2023-12-27 17:00 | 2023-12-27 18:00 | Winter | TRUE | nonsummer
2023-12-27 18:00 | 2023-12-27 19:00 | Winter | TRUE | nonsummer
2023-12-27 19:00 | 2023-12-27 20:00 | Winter | TRUE | nonsummer
2023-12-27 20:00 | 2023-12-27 21:00 | Winter | TRUE | nonsummer
2023-12-27 21:00 | 2023-12-27 22:00 | Winter | FALSE | nonsummer
2023-12-27 22:00 | 2023-12-27 23:00 | Winter | FALSE | nonsummer
2023-12-27 23:00 | 2023-12-28 | Winter | FALSE | nonsummer
2023-12-28 | 2023-12-28 01:00 | Winter | FALSE | nonsummer
2023-12-28 01:00 | 2023-12-28 02:00 | Winter | FALSE | nonsummer
2023-12-28 02:00 | 2023-12-28 03:00 | Winter | FALSE | nonsummer
2023-12-28 03:00 | 2023-12-28 04:00 | Winter | FALSE | nonsummer
2023-12-28 04:00 | 2023-12-28 05:00 | Winter | FALSE | nonsummer
2023-12-28 05:00 | 2023-12-28 06:00 | Winter | FALSE | nonsummer
2023-12-28 06:00 | 2023-12-28 07:00 | Winter | FALSE | nonsummer
2023-12-28 07:00 | 2023-12-28 08:00 | Winter | FALSE | nonsummer
2023-12-28 08:00 | 2023-12-28 09:00 | Winter | FALSE | nonsummer
2023-12-28 09:00 | 2023-12-28 10:00 | Winter | FALSE | nonsummer
2023-12-28 10:00 | 2023-12-28 11:00 | Winter | FALSE | nonsummer
2023-12-28 11:00 | 2023-12-28 12:00 | Winter | FALSE | nonsummer
2023-12-28 12:00 | 2023-12-28 13:00 | Winter | FALSE | nonsummer
2023-12-28 13:00 | 2023-12-28 14:00 | Winter | FALSE | nonsummer
2023-12-28 14:00 | 2023-12-28 15:00 | Winter | FALSE | nonsummer
2023-12-28 15:00 | 2023-12-28 16:00 | Winter | FALSE | nonsummer
2023-12-28 16:00 | 2023-12-28 17:00 | Winter | TRUE | nonsummer
2023-12-28 17:00 | 2023-12-28 18:00 | Winter | TRUE | nonsummer
2023-12-28 18:00 | 2023-12-28 19:00 | Winter | TRUE | nonsummer
2023-12-28 19:00 | 2023-12-28 20:00 | Winter | TRUE | nonsummer
2023-12-28 20:00 | 2023-12-28 21:00 | Winter | TRUE | nonsummer
2023-12-28 21:00 | 2023-12-28 22:00 | Winter | FALSE | nonsummer
2023-12-28 22:00 | 2023-12-28 23:00 | Winter | FALSE | nonsummer
2023-12-28 23:00 | 2023-12-29 | Winter | FALSE | nonsummer
2023-12-29 | 2023-12-29 01:00 | Winter | FALSE | nonsummer
2023-12-29 01:00 | 2023-12-29 02:00 | Winter | FALSE | nonsummer
2023-12-29 02:00 | 2023-12-29 03:00 | Winter | FALSE | nonsummer
2023-12-29 03:00 | 2023-12-29 04:00 | Winter | FALSE | nonsummer
2023-12-29 04:00 | 2023-12-29 05:00 | Winter | FALSE | nonsummer
2023-12-29 05:00 | 2023-12-29 06:00 | Winter | FALSE | nonsummer
2023-12-29 06:00 | 2023-12-29 07:00 | Winter | FALSE | nonsummer
2023-12-29 07:00 | 2023-12-29 08:00 | Winter | FALSE | nonsummer
2023-12-29 08:00 | 2023-12-29 09:00 | Winter | FALSE | nonsummer
2023-12-29 09:00 | 2023-12-29 10:00 | Winter | FALSE | nonsummer
2023-12-29 10:00 | 2023-12-29 11:00 | Winter | FALSE | nonsummer
2023-12-29 11:00 | 2023-12-29 12:00 | Winter | FALSE | nonsummer
2023-12-29 12:00 | 2023-12-29 13:00 | Winter | FALSE | nonsummer
2023-12-29 13:00 | 2023-12-29 14:00 | Winter | FALSE | nonsummer
2023-12-29 14:00 | 2023-12-29 15:00 | Winter | FALSE | nonsummer
2023-12-29 15:00 | 2023-12-29 16:00 | Winter | FALSE | nonsummer
2023-12-29 16:00 | 2023-12-29 17:00 | Winter | TRUE | nonsummer
2023-12-29 17:00 | 2023-12-29 18:00 | Winter | TRUE | nonsummer
2023-12-29 18:00 | 2023-12-29 19:00 | Winter | TRUE | nonsummer
2023-12-29 19:00 | 2023-12-29 20:00 | Winter | TRUE | nonsummer
2023-12-29 20:00 | 2023-12-29 21:00 | Winter | TRUE | nonsummer
2023-12-29 21:00 | 2023-12-29 22:00 | Winter | FALSE | nonsummer
2023-12-29 22:00 | 2023-12-29 23:00 | Winter | FALSE | nonsummer
2023-12-29 23:00 | 2023-12-30 | Winter | FALSE | nonsummer
2023-12-30 | 2023-12-30 01:00 | Winter | FALSE | nonsummer
2023-12-30 01:00 | 2023-12-30 02:00 | Winter | FALSE | nonsummer
2023-12-30 02:00 | 2023-12-30 03:00 | Winter | FALSE | nonsummer
2023-12-30 03:00 | 2023-12-30 04:00 | Winter | FALSE | nonsummer
2023-12-30 04:00 | 2023-12-30 05:00 | Winter | FALSE | nonsummer
2023-12-30 05:00 | 2023-12-30 06:00 | Winter | FALSE | nonsummer
2023-12-30 06:00 | 2023-12-30 07:00 | Winter | FALSE | nonsummer
2023-12-30 07:00 | 2023-12-30 08:00 | Winter | FALSE | nonsummer
2023-12-30 08:00 | 2023-12-30 09:00 | Winter | FALSE | nonsummer
2023-12-30 09:00 | 2023-12-30 10:00 | Winter | FALSE | nonsummer
2023-12-30 10:00 | 2023-12-30 11:00 | Winter | FALSE | nonsummer
2023-12-30 11:00 | 2023-12-30 12:00 | Winter | FALSE | nonsummer
2023-12-30 12:00 | 2023-12-30 13:00 | Winter | FALSE | nonsummer
2023-12-30 13:00 | 2023-12-30 14:00 | Winter | FALSE | nonsummer
2023-12-30 14:00 | 2023-12-30 15:00 | Winter | FALSE | nonsummer
2023-12-30 15:00 | 2023-12-30 16:00 | Winter | FALSE | nonsummer
2023-12-30 16:00 | 2023-12-30 17:00 | Winter | TRUE | nonsummer
2023-12-30 17:00 | 2023-12-30 18:00 | Winter | TRUE | nonsummer
2023-12-30 18:00 | 2023-12-30 19:00 | Winter | TRUE | nonsummer
2023-12-30 19:00 | 2023-12-30 20:00 | Winter | TRUE | nonsummer
2023-12-30 20:00 | 2023-12-30 21:00 | Winter | TRUE | nonsummer
2023-12-30 21:00 | 2023-12-30 22:00 | Winter | FALSE | nonsummer
2023-12-30 22:00 | 2023-12-30 23:00 | Winter | FALSE | nonsummer
2023-12-30 23:00 | 2023-12-31 | Winter | FALSE | nonsummer
2023-12-31 | 2023-12-31 01:00 | Winter | FALSE | nonsummer
2023-12-31 01:00 | 2023-12-31 02:00 | Winter | FALSE | nonsummer
2023-12-31 02:00 | 2023-12-31 03:00 | Winter | FALSE | nonsummer
2023-12-31 03:00 | 2023-12-31 04:00 | Winter | FALSE | nonsummer
2023-12-31 04:00 | 2023-12-31 05:00 | Winter | FALSE | nonsummer
2023-12-31 05:00 | 2023-12-31 06:00 | Winter | FALSE | nonsummer
2023-12-31 06:00 | 2023-12-31 07:00 | Winter | FALSE | nonsummer
2023-12-31 07:00 | 2023-12-31 08:00 | Winter | FALSE | nonsummer
2023-12-31 08:00 | 2023-12-31 09:00 | Winter | FALSE | nonsummer
2023-12-31 09:00 | 2023-12-31 10:00 | Winter | FALSE | nonsummer
2023-12-31 10:00 | 2023-12-31 11:00 | Winter | FALSE | nonsummer
2023-12-31 11:00 | 2023-12-31 12:00 | Winter | FALSE | nonsummer
2023-12-31 12:00 | 2023-12-31 13:00 | Winter | FALSE | nonsummer
2023-12-31 13:00 | 2023-12-31 14:00 | Winter | FALSE | nonsummer
2023-12-31 14:00 | 2023-12-31 15:00 | Winter | FALSE | nonsummer
2023-12-31 15:00 | 2023-12-31 16:00 | Winter | FALSE | nonsummer
2023-12-31 16:00 | 2023-12-31 17:00 | Winter | TRUE | nonsummer
2023-12-31 17:00 | 2023-12-31 18:00 | Winter | TRUE | nonsummer
2023-12-31 18:00 | 2023-12-31 19:00 | Winter | TRUE | nonsummer
2023-12-31 19:00 | 2023-12-31 20:00 | Winter | TRUE | nonsummer
2023-12-31 20:00 | 2023-12-31 21:00 | Winter | TRUE | nonsummer
2023-12-31 21:00 | 2023-12-31 22:00 | Winter | FALSE | nonsummer
2023-12-31 22:00 | 2023-12-31 23:00 | Winter | FALSE | nonsummer
2023-12-31 23:00 | 2024-01-01 | Winter | FALSE | nonsummer
2024-01-01 | 2024-01-01 01:00 | Winter | FALSE | nonsummer
2024-01-01 01:00 | 2024-01-01 02:00 | Winter | FALSE | nonsummer
2024-01-01 02:00 | 2024-01-01 03:00 | Winter | FALSE | nonsummer
2024-01-01 03:00 | 2024-01-01 04:00 | Winter | FALSE | nonsummer
2024-01-01 04:00 | 2024-01-01 05:00 | Winter | FALSE | nonsummer
2024-01-01 05:00 | 2024-01-01 06:00 | Winter | FALSE | nonsummer
2024-01-01 06:00 | 2024-01-01 07:00 | Winter | FALSE | nonsummer
2024-01-01 07:00 | 2024-01-01 08:00 | Winter | FALSE | nonsummer
2024-01-01 08:00 | 2024-01-01 09:00 | Winter | FALSE | nonsummer
2024-01-01 09:00 | 2024-01-01 10:00 | Winter | FALSE | nonsummer
2024-01-01 10:00 | 2024-01-01 11:00 | Winter | FALSE | nonsummer
2024-01-01 11:00 | 2024-01-01 12:00 | Winter | FALSE | nonsummer
2024-01-01 12:00 | 2024-01-01 13:00 | Winter | FALSE | nonsummer
2024-01-01 13:00 | 2024-01-01 14:00 | Winter | FALSE | nonsummer
2024-01-01 14:00 | 2024-01-01 15:00 | Winter | FALSE | nonsummer
2024-01-01 15:00 | 2024-01-01 16:00 | Winter | FALSE | nonsummer
2024-01-01 16:00 | 2024-01-01 17:00 | Winter | TRUE | nonsummer
2024-01-01 17:00 | 2024-01-01 18:00 | Winter | TRUE | nonsummer
2024-01-01 18:00 | 2024-01-01 19:00 | Winter | TRUE | nonsummer
2024-01-01 19:00 | 2024-01-01 20:00 | Winter | TRUE | nonsummer
2024-01-01 20:00 | 2024-01-01 21:00 | Winter | TRUE | nonsummer
2024-01-01 21:00 | 2024-01-01 22:00 | Winter | FALSE | nonsummer
2024-01-01 22:00 | 2024-01-01 23:00 | Winter | FALSE | nonsummer
2024-01-01 23:00 | 2024-01-02 | Winter | FALSE | nonsummer
2024-01-02 | 2024-01-02 01:00 | Winter | FALSE | nonsummer
2024-01-02 01:00 | 2024-01-02 02:00 | Winter | FALSE | nonsummer
2024-01-02 02:00 | 2024-01-02 03:00 | Winter | FALSE | nonsummer
2024-01-02 03:00 | 2024-01-02 04:00 | Winter | FALSE | nonsummer
2024-01-02 04:00 | 2024-01-02 05:00 | Winter | FALSE | nonsummer
2024-01-02 05:00 | 2024-01-02 06:00 | Winter | FALSE | nonsummer
2024-01-02 06:00 | 2024-01-02 07:00 | Winter | FALSE | nonsummer
2024-01-02 07:00 | 2024-01-02 08:00 | Winter | FALSE | nonsummer
2024-01-02 08:00 | 2024-01-02 09:00 | Winter | FALSE | nonsummer
2024-01-02 09:00 | 2024-01-02 10:00 | Winter | FALSE | nonsummer
2024-01-02 10:00 | 2024-01-02 11:00 | Winter | FALSE | nonsummer
2024-01-02 11:00 | 2024-01-02 12:00 | Winter | FALSE | nonsummer
2024-01-02 12:00 | 2024-01-02 13:00 | Winter | FALSE | nonsummer
2024-01-02 13:00 | 2024-01-02 14:00 | Winter | FALSE | nonsummer
2024-01-02 14:00 | 2024-01-02 15:00 | Winter | FALSE | nonsummer
2024-01-02 15:00 | 2024-01-02 16:00 | Winter | FALSE | nonsummer
2024-01-02 16:00 | 2024-01-02 17:00 | Winter | TRUE | nonsummer
2024-01-02 17:00 | 2024-01-02 18:00 | Winter | TRUE | nonsummer
2024-01-02 18:00 | 2024-01-02 19:00 | Winter | TRUE | nonsummer
2024-01-02 19:00 | 2024-01-02 20:00 | Winter | TRUE | nonsummer
2024-01-02 20:00 | 2024-01-02 21:00 | Winter | TRUE | nonsummer
2024-01-02 21:00 | 2024-01-02 22:00 | Winter | FALSE | nonsummer
2024-01-02 22:00 | 2024-01-02 23:00 | Winter | FALSE | nonsummer
2024-01-02 23:00 | 2024-01-03 | Winter | FALSE | nonsummer
2024-01-03 | 2024-01-03 01:00 | Winter | FALSE | nonsummer
2024-01-03 01:00 | 2024-01-03 02:00 | Winter | FALSE | nonsummer
2024-01-03 02:00 | 2024-01-03 03:00 | Winter | FALSE | nonsummer
2024-01-03 03:00 | 2024-01-03 04:00 | Winter | FALSE | nonsummer
2024-01-03 04:00 | 2024-01-03 05:00 | Winter | FALSE | nonsummer
2024-01-03 05:00 | 2024-01-03 06:00 | Winter | FALSE | nonsummer
2024-01-03 06:00 | 2024-01-03 07:00 | Winter | FALSE | nonsummer
2024-01-03 07:00 | 2024-01-03 08:00 | Winter | FALSE | nonsummer
2024-01-03 08:00 | 2024-01-03 09:00 | Winter | FALSE | nonsummer
2024-01-03 09:00 | 2024-01-03 10:00 | Winter | FALSE | nonsummer
2024-01-03 10:00 | 2024-01-03 11:00 | Winter | FALSE | nonsummer
2024-01-03 11:00 | 2024-01-03 12:00 | Winter | FALSE | nonsummer
2024-01-03 12:00 | 2024-01-03 13:00 | Winter | FALSE | nonsummer
2024-01-03 13:00 | 2024-01-03 14:00 | Winter | FALSE | nonsummer
2024-01-03 14:00 | 2024-01-03 15:00 | Winter | FALSE | nonsummer
2024-01-03 15:00 | 2024-01-03 16:00 | Winter | FALSE | nonsummer
2024-01-03 16:00 | 2024-01-03 17:00 | Winter | TRUE | nonsummer
2024-01-03 17:00 | 2024-01-03 18:00 | Winter | TRUE | nonsummer
2024-01-03 18:00 | 2024-01-03 19:00 | Winter | TRUE | nonsummer
2024-01-03 19:00 | 2024-01-03 20:00 | Winter | TRUE | nonsummer
2024-01-03 20:00 | 2024-01-03 21:00 | Winter | TRUE | nonsummer
2024-01-03 21:00 | 2024-01-03 22:00 | Winter | FALSE | nonsummer
2024-01-03 22:00 | 2024-01-03 23:00 | Winter | FALSE | nonsummer
2024-01-03 23:00 | 2024-01-04 | Winter | FALSE | nonsummer
2024-01-04 | 2024-01-04 01:00 | Winter | FALSE | nonsummer
2024-01-04 01:00 | 2024-01-04 02:00 | Winter | FALSE | nonsummer
2024-01-04 02:00 | 2024-01-04 03:00 | Winter | FALSE | nonsummer
2024-01-04 03:00 | 2024-01-04 04:00 | Winter | FALSE | nonsummer
2024-01-04 04:00 | 2024-01-04 05:00 | Winter | FALSE | nonsummer
2024-01-04 05:00 | 2024-01-04 06:00 | Winter | FALSE | nonsummer
2024-01-04 06:00 | 2024-01-04 07:00 | Winter | FALSE | nonsummer
2024-01-04 07:00 | 2024-01-04 08:00 | Winter | FALSE | nonsummer
2024-01-04 08:00 | 2024-01-04 09:00 | Winter | FALSE | nonsummer
2024-01-04 09:00 | 2024-01-04 10:00 | Winter | FALSE | nonsummer
2024-01-04 10:00 | 2024-01-04 11:00 | Winter | FALSE | nonsummer
2024-01-04 11:00 | 2024-01-04 12:00 | Winter | FALSE | nonsummer
2024-01-04 12:00 | 2024-01-04 13:00 | Winter | FALSE | nonsummer
2024-01-04 13:00 | 2024-01-04 14:00 | Winter | FALSE | nonsummer
2024-01-04 14:00 | 2024-01-04 15:00 | Winter | FALSE | nonsummer
2024-01-04 15:00 | 2024-01-04 16:00 | Winter | FALSE | nonsummer
2024-01-04 16:00 | 2024-01-04 17:00 | Winter | TRUE | nonsummer
2024-01-04 17:00 | 2024-01-04 18:00 | Winter | TRUE | nonsummer
2024-01-04 18:00 | 2024-01-04 19:00 | Winter | TRUE | nonsummer
2024-01-04 19:00 | 2024-01-04 20:00 | Winter | TRUE | nonsummer
2024-01-04 20:00 | 2024-01-04 21:00 | Winter | TRUE | nonsummer
2024-01-04 21:00 | 2024-01-04 22:00 | Winter | FALSE | nonsummer
2024-01-04 22:00 | 2024-01-04 23:00 | Winter | FALSE | nonsummer
2024-01-04 23:00 | 2024-01-05 | Winter | FALSE | nonsummer
2024-01-05 | 2024-01-05 01:00 | Winter | FALSE | nonsummer
2024-01-05 01:00 | 2024-01-05 02:00 | Winter | FALSE | nonsummer
2024-01-05 02:00 | 2024-01-05 03:00 | Winter | FALSE | nonsummer
2024-01-05 03:00 | 2024-01-05 04:00 | Winter | FALSE | nonsummer
2024-01-05 04:00 | 2024-01-05 05:00 | Winter | FALSE | nonsummer
2024-01-05 05:00 | 2024-01-05 06:00 | Winter | FALSE | nonsummer
2024-01-05 06:00 | 2024-01-05 07:00 | Winter | FALSE | nonsummer
2024-01-05 07:00 | 2024-01-05 08:00 | Winter | FALSE | nonsummer
2024-01-05 08:00 | 2024-01-05 09:00 | Winter | FALSE | nonsummer
2024-01-05 09:00 | 2024-01-05 10:00 | Winter | FALSE | nonsummer
2024-01-05 10:00 | 2024-01-05 11:00 | Winter | FALSE | nonsummer
2024-01-05 11:00 | 2024-01-05 12:00 | Winter | FALSE | nonsummer
2024-01-05 12:00 | 2024-01-05 13:00 | Winter | FALSE | nonsummer
2024-01-05 13:00 | 2024-01-05 14:00 | Winter | FALSE | nonsummer
2024-01-05 14:00 | 2024-01-05 15:00 | Winter | FALSE | nonsummer
2024-01-05 15:00 | 2024-01-05 16:00 | Winter | FALSE | nonsummer
2024-01-05 16:00 | 2024-01-05 17:00 | Winter | TRUE | nonsummer
2024-01-05 17:00 | 2024-01-05 18:00 | Winter | TRUE | nonsummer
2024-01-05 18:00 | 2024-01-05 19:00 | Winter | TRUE | nonsummer
2024-01-05 19:00 | 2024-01-05 20:00 | Winter | TRUE | nonsummer
2024-01-05 20:00 | 2024-01-05 21:00 | Winter | TRUE | nonsummer
2024-01-05 21:00 | 2024-01-05 22:00 | Winter | FALSE | nonsummer
2024-01-05 22:00 | 2024-01-05 23:00 | Winter | FALSE | nonsummer
2024-01-05 23:00 | 2024-01-06 | Winter | FALSE | nonsummer
2024-01-06 | 2024-01-06 01:00 | Winter | FALSE | nonsummer
2024-01-06 01:00 | 2024-01-06 02:00 | Winter | FALSE | nonsummer
2024-01-06 02:00 | 2024-01-06 03:00 | Winter | FALSE | nonsummer
2024-01-06 03:00 | 2024-01-06 04:00 | Winter | FALSE | nonsummer
2024-01-06 04:00 | 2024-01-06 05:00 | Winter | FALSE | nonsummer
2024-01-06 05:00 | 2024-01-06 06:00 | Winter | FALSE | nonsummer
2024-01-06 06:00 | 2024-01-06 07:00 | Winter | FALSE | nonsummer
2024-01-06 07:00 | 2024-01-06 08:00 | Winter | FALSE | nonsummer
2024-01-06 08:00 | 2024-01-06 09:00 | Winter | FALSE | nonsummer
2024-01-06 09:00 | 2024-01-06 10:00 | Winter | FALSE | nonsummer
2024-01-06 10:00 | 2024-01-06 11:00 | Winter | FALSE | nonsummer
2024-01-06 11:00 | 2024-01-06 12:00 | Winter | FALSE | nonsummer
2024-01-06 12:00 | 2024-01-06 13:00 | Winter | FALSE | nonsummer
2024-01-06 13:00 | 2024-01-06 14:00 | Winter | FALSE | nonsummer
2024-01-06 14:00 | 2024-01-06 15:00 | Winter | FALSE | nonsummer
2024-01-06 15:00 | 2024-01-06 16:00 | Winter | FALSE | nonsummer
2024-01-06 16:00 | 2024-01-06 17:00 | Winter | TRUE | nonsummer
2024-01-06 17:00 | 2024-01-06 18:00 | Winter | TRUE | nonsummer
2024-01-06 18:00 | 2024-01-06 19:00 | Winter | TRUE | nonsummer
2024-01-06 19:00 | 2024-01-06 20:00 | Winter | TRUE | nonsummer
2024-01-06 20:00 | 2024-01-06 21:00 | Winter | TRUE | nonsummer
2024-01-06 21:00 | 2024-01-06 22:00 | Winter | FALSE | nonsummer
2024-01-06 22:00 | 2024-01-06 23:00 | Winter | FALSE | nonsummer
2024-01-06 23:00 | 2024-01-07 | Winter | FALSE | nonsummer
2024-01-07 | 2024-01-07 01:00 | Winter | FALSE | nonsummer
2024-01-07 01:00 | 2024-01-07 02:00 | Winter | FALSE | nonsummer
2024-01-07 02:00 | 2024-01-07 03:00 | Winter | FALSE | nonsummer
2024-01-07 03:00 | 2024-01-07 04:00 | Winter | FALSE | nonsummer
2024-01-07 04:00 | 2024-01-07 05:00 | Winter | FALSE | nonsummer
2024-01-07 05:00 | 2024-01-07 06:00 | Winter | FALSE | nonsummer
2024-01-07 06:00 | 2024-01-07 07:00 | Winter | FALSE | nonsummer
2024-01-07 07:00 | 2024-01-07 08:00 | Winter | FALSE | nonsummer
2024-01-07 08:00 | 2024-01-07 09:00 | Winter | FALSE | nonsummer
2024-01-07 09:00 | 2024-01-07 10:00 | Winter | FALSE | nonsummer
2024-01-07 10:00 | 2024-01-07 11:00 | Winter | FALSE | nonsummer
2024-01-07 11:00 | 2024-01-07 12:00 | Winter | FALSE | nonsummer
2024-01-07 12:00 | 2024-01-07 13:00 | Winter | FALSE | nonsummer
2024-01-07 13:00 | 2024-01-07 14:00 | Winter | FALSE | nonsummer
2024-01-07 14:00 | 2024-01-07 15:00 | Winter | FALSE | nonsummer
2024-01-07 15:00 | 2024-01-07 16:00 | Winter | FALSE | nonsummer
2024-01-07 16:00 | 2024-01-07 17:00 | Winter | TRUE | nonsummer
2024-01-07 17:00 | 2024-01-07 18:00 | Winter | TRUE | nonsummer
2024-01-07 18:00 | 2024-01-07 19:00 | Winter | TRUE | nonsummer
2024-01-07 19:00 | 2024-01-07 20:00 | Winter | TRUE | nonsummer
2024-01-07 20:00 | 2024-01-07 21:00 | Winter | TRUE | nonsummer
2024-01-07 21:00 | 2024-01-07 22:00 | Winter | FALSE | nonsummer
2024-01-07 22:00 | 2024-01-07 23:00 | Winter | FALSE | nonsummer
2024-01-07 23:00 | 2024-01-08 | Winter | FALSE | nonsummer
2024-01-08 | 2024-01-08 01:00 | Winter | FALSE | nonsummer
2024-01-08 01:00 | 2024-01-08 02:00 | Winter | FALSE | nonsummer
2024-01-08 02:00 | 2024-01-08 03:00 | Winter | FALSE | nonsummer
2024-01-08 03:00 | 2024-01-08 04:00 | Winter | FALSE | nonsummer
2024-01-08 04:00 | 2024-01-08 05:00 | Winter | FALSE | nonsummer
2024-01-08 05:00 | 2024-01-08 06:00 | Winter | FALSE | nonsummer
2024-01-08 06:00 | 2024-01-08 07:00 | Winter | FALSE | nonsummer
2024-01-08 07:00 | 2024-01-08 08:00 | Winter | FALSE | nonsummer
2024-01-08 08:00 | 2024-01-08 09:00 | Winter | FALSE | nonsummer
2024-01-08 09:00 | 2024-01-08 10:00 | Winter | FALSE | nonsummer
2024-01-08 10:00 | 2024-01-08 11:00 | Winter | FALSE | nonsummer
2024-01-08 11:00 | 2024-01-08 12:00 | Winter | FALSE | nonsummer
2024-01-08 12:00 | 2024-01-08 13:00 | Winter | FALSE | nonsummer
2024-01-08 13:00 | 2024-01-08 14:00 | Winter | FALSE | nonsummer
2024-01-08 14:00 | 2024-01-08 15:00 | Winter | FALSE | nonsummer
2024-01-08 15:00 | 2024-01-08 16:00 | Winter | FALSE | nonsummer
2024-01-08 16:00 | 2024-01-08 17:00 | Winter | TRUE | nonsummer
2024-01-08 17:00 | 2024-01-08 18:00 | Winter | TRUE | nonsummer
2024-01-08 18:00 | 2024-01-08 19:00 | Winter | TRUE | nonsummer
2024-01-08 19:00 | 2024-01-08 20:00 | Winter | TRUE | nonsummer
2024-01-08 20:00 | 2024-01-08 21:00 | Winter | TRUE | nonsummer
2024-01-08 21:00 | 2024-01-08 22:00 | Winter | FALSE | nonsummer
2024-01-08 22:00 | 2024-01-08 23:00 | Winter | FALSE | nonsummer
2024-01-08 23:00 | 2024-01-09 | Winter | FALSE | nonsummer
2024-01-09 | 2024-01-09 01:00 | Winter | FALSE | nonsummer
2024-01-09 01:00 | 2024-01-09 02:00 | Winter | FALSE | nonsummer
2024-01-09 02:00 | 2024-01-09 03:00 | Winter | FALSE | nonsummer
2024-01-09 03:00 | 2024-01-09 04:00 | Winter | FALSE | nonsummer
2024-01-09 04:00 | 2024-01-09 05:00 | Winter | FALSE | nonsummer
2024-01-09 05:00 | 2024-01-09 06:00 | Winter | FALSE | nonsummer
2024-01-09 06:00 | 2024-01-09 07:00 | Winter | FALSE | nonsummer
2024-01-09 07:00 | 2024-01-09 08:00 | Winter | FALSE | nonsummer
2024-01-09 08:00 | 2024-01-09 09:00 | Winter | FALSE | nonsummer
2024-01-09 09:00 | 2024-01-09 10:00 | Winter | FALSE | nonsummer
2024-01-09 10:00 | 2024-01-09 11:00 | Winter | FALSE | nonsummer
2024-01-09 11:00 | 2024-01-09 12:00 | Winter | FALSE | nonsummer
2024-01-09 12:00 | 2024-01-09 13:00 | Winter | FALSE | nonsummer
2024-01-09 13:00 | 2024-01-09 14:00 | Winter | FALSE | nonsummer
2024-01-09 14:00 | 2024-01-09 15:00 | Winter | FALSE | nonsummer
2024-01-09 15:00 | 2024-01-09 16:00 | Winter | FALSE | nonsummer
2024-01-09 16:00 | 2024-01-09 17:00 | Winter | TRUE | nonsummer
2024-01-09 17:00 | 2024-01-09 18:00 | Winter | TRUE | nonsummer
2024-01-09 18:00 | 2024-01-09 19:00 | Winter | TRUE | nonsummer
2024-01-09 19:00 | 2024-01-09 20:00 | Winter | TRUE | nonsummer
2024-01-09 20:00 | 2024-01-09 21:00 | Winter | TRUE | nonsummer
2024-01-09 21:00 | 2024-01-09 22:00 | Winter | FALSE | nonsummer
2024-01-09 22:00 | 2024-01-09 23:00 | Winter | FALSE | nonsummer
2024-01-09 23:00 | 2024-01-10 | Winter | FALSE | nonsummer
2024-01-10 | 2024-01-10 01:00 | Winter | FALSE | nonsummer
2024-01-10 01:00 | 2024-01-10 02:00 | Winter | FALSE | nonsummer
2024-01-10 02:00 | 2024-01-10 03:00 | Winter | FALSE | nonsummer
2024-01-10 03:00 | 2024-01-10 04:00 | Winter | FALSE | nonsummer
2024-01-10 04:00 | 2024-01-10 05:00 | Winter | FALSE | nonsummer
2024-01-10 05:00 | 2024-01-10 06:00 | Winter | FALSE | nonsummer
2024-01-10 06:00 | 2024-01-10 07:00 | Winter | FALSE | nonsummer
2024-01-10 07:00 | 2024-01-10 08:00 | Winter | FALSE | nonsummer
2024-01-10 08:00 | 2024-01-10 09:00 | Winter | FALSE | nonsummer
2024-01-10 09:00 | 2024-01-10 10:00 | Winter | FALSE | nonsummer
2024-01-10 10:00 | 2024-01-10 11:00 | Winter | FALSE | nonsummer
2024-01-10 11:00 | 2024-01-10 12:00 | Winter | FALSE | nonsummer
2024-01-10 12:00 | 2024-01-10 13:00 | Winter | FALSE | nonsummer
2024-01-10 13:00 | 2024-01-10 14:00 | Winter | FALSE | nonsummer
2024-01-10 14:00 | 2024-01-10 15:00 | Winter | FALSE | nonsummer
2024-01-10 15:00 | 2024-01-10 16:00 | Winter | FALSE | nonsummer
2024-01-10 16:00 | 2024-01-10 17:00 | Winter | TRUE | nonsummer
2024-01-10 17:00 | 2024-01-10 18:00 | Winter | TRUE | nonsummer
2024-01-10 18:00 | 2024-01-10 19:00 | Winter | TRUE | nonsummer
2024-01-10 19:00 | 2024-01-10 20:00 | Winter | TRUE | nonsummer
2024-01-10 20:00 | 2024-01-10 21:00 | Winter | TRUE | nonsummer
2024-01-10 21:00 | 2024-01-10 22:00 | Winter | FALSE | nonsummer
2024-01-10 22:00 | 2024-01-10 23:00 | Winter | FALSE | nonsummer
2024-01-10 23:00 | 2024-01-11 | Winter | FALSE | nonsummer
2024-01-11 | 2024-01-11 01:00 | Winter | FALSE | nonsummer
2024-01-11 01:00 | 2024-01-11 02:00 | Winter | FALSE | nonsummer
2024-01-11 02:00 | 2024-01-11 03:00 | Winter | FALSE | nonsummer
2024-01-11 03:00 | 2024-01-11 04:00 | Winter | FALSE | nonsummer
2024-01-11 04:00 | 2024-01-11 05:00 | Winter | FALSE | nonsummer
2024-01-11 05:00 | 2024-01-11 06:00 | Winter | FALSE | nonsummer
2024-01-11 06:00 | 2024-01-11 07:00 | Winter | FALSE | nonsummer
2024-01-11 07:00 | 2024-01-11 08:00 | Winter | FALSE | nonsummer
2024-01-11 08:00 | 2024-01-11 09:00 | Winter | FALSE | nonsummer
2024-01-11 09:00 | 2024-01-11 10:00 | Winter | FALSE | nonsummer
2024-01-11 10:00 | 2024-01-11 11:00 | Winter | FALSE | nonsummer
2024-01-11 11:00 | 2024-01-11 12:00 | Winter | FALSE | nonsummer
2024-01-11 12:00 | 2024-01-11 13:00 | Winter | FALSE | nonsummer
2024-01-11 13:00 | 2024-01-11 14:00 | Winter | FALSE | nonsummer
2024-01-11 14:00 | 2024-01-11 15:00 | Winter | FALSE | nonsummer
2024-01-11 15:00 | 2024-01-11 16:00 | Winter | FALSE | nonsummer
2024-01-11 16:00 | 2024-01-11 17:00 | Winter | TRUE | nonsummer
2024-01-11 17:00 | 2024-01-11 18:00 | Winter | TRUE | nonsummer
2024-01-11 18:00 | 2024-01-11 19:00 | Winter | TRUE | nonsummer
2024-01-11 19:00 | 2024-01-11 20:00 | Winter | TRUE | nonsummer
2024-01-11 20:00 | 2024-01-11 21:00 | Winter | TRUE | nonsummer
2024-01-11 21:00 | 2024-01-11 22:00 | Winter | FALSE | nonsummer
2024-01-11 22:00 | 2024-01-11 23:00 | Winter | FALSE | nonsummer
2024-01-11 23:00 | 2024-01-12 | Winter | FALSE | nonsummer
2024-01-12 | 2024-01-12 01:00 | Winter | FALSE | nonsummer
2024-01-12 01:00 | 2024-01-12 02:00 | Winter | FALSE | nonsummer
2024-01-12 02:00 | 2024-01-12 03:00 | Winter | FALSE | nonsummer
2024-01-12 03:00 | 2024-01-12 04:00 | Winter | FALSE | nonsummer
2024-01-12 04:00 | 2024-01-12 05:00 | Winter | FALSE | nonsummer
2024-01-12 05:00 | 2024-01-12 06:00 | Winter | FALSE | nonsummer
2024-01-12 06:00 | 2024-01-12 07:00 | Winter | FALSE | nonsummer
2024-01-12 07:00 | 2024-01-12 08:00 | Winter | FALSE | nonsummer
2024-01-12 08:00 | 2024-01-12 09:00 | Winter | FALSE | nonsummer
2024-01-12 09:00 | 2024-01-12 10:00 | Winter | FALSE | nonsummer
2024-01-12 10:00 | 2024-01-12 11:00 | Winter | FALSE | nonsummer
2024-01-12 11:00 | 2024-01-12 12:00 | Winter | FALSE | nonsummer
2024-01-12 12:00 | 2024-01-12 13:00 | Winter | FALSE | nonsummer
2024-01-12 13:00 | 2024-01-12 14:00 | Winter | FALSE | nonsummer
2024-01-12 14:00 | 2024-01-12 15:00 | Winter | FALSE | nonsummer
2024-01-12 15:00 | 2024-01-12 16:00 | Winter | FALSE | nonsummer
2024-01-12 16:00 | 2024-01-12 17:00 | Winter | TRUE | nonsummer
2024-01-12 17:00 | 2024-01-12 18:00 | Winter | TRUE | nonsummer
2024-01-12 18:00 | 2024-01-12 19:00 | Winter | TRUE | nonsummer
2024-01-12 19:00 | 2024-01-12 20:00 | Winter | TRUE | nonsummer
2024-01-12 20:00 | 2024-01-12 21:00 | Winter | TRUE | nonsummer
2024-01-12 21:00 | 2024-01-12 22:00 | Winter | FALSE | nonsummer
2024-01-12 22:00 | 2024-01-12 23:00 | Winter | FALSE | nonsummer
2024-01-12 23:00 | 2024-01-13 | Winter | FALSE | nonsummer
2024-01-13 | 2024-01-13 01:00 | Winter | FALSE | nonsummer
2024-01-13 01:00 | 2024-01-13 02:00 | Winter | FALSE | nonsummer
2024-01-13 02:00 | 2024-01-13 03:00 | Winter | FALSE | nonsummer
2024-01-13 03:00 | 2024-01-13 04:00 | Winter | FALSE | nonsummer
2024-01-13 04:00 | 2024-01-13 05:00 | Winter | FALSE | nonsummer
2024-01-13 05:00 | 2024-01-13 06:00 | Winter | FALSE | nonsummer
2024-01-13 06:00 | 2024-01-13 07:00 | Winter | FALSE | nonsummer
2024-01-13 07:00 | 2024-01-13 08:00 | Winter | FALSE | nonsummer
2024-01-13 08:00 | 2024-01-13 09:00 | Winter | FALSE | nonsummer
2024-01-13 09:00 | 2024-01-13 10:00 | Winter | FALSE | nonsummer
2024-01-13 10:00 | 2024-01-13 11:00 | Winter | FALSE | nonsummer
2024-01-13 11:00 | 2024-01-13 12:00 | Winter | FALSE | nonsummer
2024-01-13 12:00 | 2024-01-13 13:00 | Winter | FALSE | nonsummer
2024-01-13 13:00 | 2024-01-13 14:00 | Winter | FALSE | nonsummer
2024-01-13 14:00 | 2024-01-13 15:00 | Winter | FALSE | nonsummer
2024-01-13 15:00 | 2024-01-13 16:00 | Winter | FALSE | nonsummer
2024-01-13 16:00 | 2024-01-13 17:00 | Winter | TRUE | nonsummer
2024-01-13 17:00 | 2024-01-13 18:00 | Winter | TRUE | nonsummer
2024-01-13 18:00 | 2024-01-13 19:00 | Winter | TRUE | nonsummer
2024-01-13 19:00 | 2024-01-13 20:00 | Winter | TRUE | nonsummer
2024-01-13 20:00 | 2024-01-13 21:00 | Winter | TRUE | nonsummer
2024-01-13 21:00 | 2024-01-13 22:00 | Winter | FALSE | nonsummer
2024-01-13 22:00 | 2024-01-13 23:00 | Winter | FALSE | nonsummer
2024-01-13 23:00 | 2024-01-14 | Winter | FALSE | nonsummer
2024-01-14 | 2024-01-14 01:00 | Winter | FALSE | nonsummer
2024-01-14 01:00 | 2024-01-14 02:00 | Winter | FALSE | nonsummer
2024-01-14 02:00 | 2024-01-14 03:00 | Winter | FALSE | nonsummer
2024-01-14 03:00 | 2024-01-14 04:00 | Winter | FALSE | nonsummer
2024-01-14 04:00 | 2024-01-14 05:00 | Winter | FALSE | nonsummer
2024-01-14 05:00 | 2024-01-14 06:00 | Winter | FALSE | nonsummer
2024-01-14 06:00 | 2024-01-14 07:00 | Winter | FALSE | nonsummer
2024-01-14 07:00 | 2024-01-14 08:00 | Winter | FALSE | nonsummer
2024-01-14 08:00 | 2024-01-14 09:00 | Winter | FALSE | nonsummer
2024-01-14 09:00 | 2024-01-14 10:00 | Winter | FALSE | nonsummer
2024-01-14 10:00 | 2024-01-14 11:00 | Winter | FALSE | nonsummer
2024-01-14 11:00 | 2024-01-14 12:00 | Winter | FALSE | nonsummer
2024-01-14 12:00 | 2024-01-14 13:00 | Winter | FALSE | nonsummer
2024-01-14 13:00 | 2024-01-14 14:00 | Winter | FALSE | nonsummer
2024-01-14 14:00 | 2024-01-14 15:00 | Winter | FALSE | nonsummer
2024-01-14 15:00 | 2024-01-14 16:00 | Winter | FALSE | nonsummer
2024-01-14 16:00 | 2024-01-14 17:00 | Winter | TRUE | nonsummer
2024-01-14 17:00 | 2024-01-14 18:00 | Winter | TRUE | nonsummer
2024-01-14 18:00 | 2024-01-14 19:00 | Winter | TRUE | nonsummer
2024-01-14 19:00 | 2024-01-14 20:00 | Winter | TRUE | nonsummer
2024-01-14 20:00 | 2024-01-14 21:00 | Winter | TRUE | nonsummer
2024-01-14 21:00 | 2024-01-14 22:00 | Winter | FALSE | nonsummer
2024-01-14 22:00 | 2024-01-14 23:00 | Winter | FALSE | nonsummer
2024-01-14 23:00 | 2024-01-15 | Winter | FALSE | nonsummer
2024-01-15 | 2024-01-15 01:00 | Winter | FALSE | nonsummer
2024-01-15 01:00 | 2024-01-15 02:00 | Winter | FALSE | nonsummer
2024-01-15 02:00 | 2024-01-15 03:00 | Winter | FALSE | nonsummer
2024-01-15 03:00 | 2024-01-15 04:00 | Winter | FALSE | nonsummer
2024-01-15 04:00 | 2024-01-15 05:00 | Winter | FALSE | nonsummer
2024-01-15 05:00 | 2024-01-15 06:00 | Winter | FALSE | nonsummer
2024-01-15 06:00 | 2024-01-15 07:00 | Winter | FALSE | nonsummer
2024-01-15 07:00 | 2024-01-15 08:00 | Winter | FALSE | nonsummer
2024-01-15 08:00 | 2024-01-15 09:00 | Winter | FALSE | nonsummer
2024-01-15 09:00 | 2024-01-15 10:00 | Winter | FALSE | nonsummer
2024-01-15 10:00 | 2024-01-15 11:00 | Winter | FALSE | nonsummer
2024-01-15 11:00 | 2024-01-15 12:00 | Winter | FALSE | nonsummer
2024-01-15 12:00 | 2024-01-15 13:00 | Winter | FALSE | nonsummer
2024-01-15 13:00 | 2024-01-15 14:00 | Winter | FALSE | nonsummer
2024-01-15 14:00 | 2024-01-15 15:00 | Winter | FALSE | nonsummer
2024-01-15 15:00 | 2024-01-15 16:00 | Winter | FALSE | nonsummer
2024-01-15 16:00 | 2024-01-15 17:00 | Winter | TRUE | nonsummer
2024-01-15 17:00 | 2024-01-15 18:00 | Winter | TRUE | nonsummer
2024-01-15 18:00 | 2024-01-15 19:00 | Winter | TRUE | nonsummer
2024-01-15 19:00 | 2024-01-15 20:00 | Winter | TRUE | nonsummer
2024-01-15 20:00 | 2024-01-15 21:00 | Winter | TRUE | nonsummer
2024-01-15 21:00 | 2024-01-15 22:00 | Winter | FALSE | nonsummer
2024-01-15 22:00 | 2024-01-15 23:00 | Winter | FALSE | nonsummer
2024-01-15 23:00 | 2024-01-16 | Winter | FALSE | nonsummer
2024-01-16 | 2024-01-16 01:00 | Winter | FALSE | nonsummer
2024-01-16 01:00 | 2024-01-16 02:00 | Winter | FALSE | nonsummer
2024-01-16 02:00 | 2024-01-16 03:00 | Winter | FALSE | nonsummer
2024-01-16 03:00 | 2024-01-16 04:00 | Winter | FALSE | nonsummer
2024-01-16 04:00 | 2024-01-16 05:00 | Winter | FALSE | nonsummer
2024-01-16 05:00 | 2024-01-16 06:00 | Winter | FALSE | nonsummer
2024-01-16 06:00 | 2024-01-16 07:00 | Winter | FALSE | nonsummer
2024-01-16 07:00 | 2024-01-16 08:00 | Winter | FALSE | nonsummer
2024-01-16 08:00 | 2024-01-16 09:00 | Winter | FALSE | nonsummer
2024-01-16 09:00 | 2024-01-16 10:00 | Winter | FALSE | nonsummer
2024-01-16 10:00 | 2024-01-16 11:00 | Winter | FALSE | nonsummer
2024-01-16 11:00 | 2024-01-16 12:00 | Winter | FALSE | nonsummer
2024-01-16 12:00 | 2024-01-16 13:00 | Winter | FALSE | nonsummer
2024-01-16 13:00 | 2024-01-16 14:00 | Winter | FALSE | nonsummer
2024-01-16 14:00 | 2024-01-16 15:00 | Winter | FALSE | nonsummer
2024-01-16 15:00 | 2024-01-16 16:00 | Winter | FALSE | nonsummer
2024-01-16 16:00 | 2024-01-16 17:00 | Winter | TRUE | nonsummer
2024-01-16 17:00 | 2024-01-16 18:00 | Winter | TRUE | nonsummer
2024-01-16 18:00 | 2024-01-16 19:00 | Winter | TRUE | nonsummer
2024-01-16 19:00 | 2024-01-16 20:00 | Winter | TRUE | nonsummer
2024-01-16 20:00 | 2024-01-16 21:00 | Winter | TRUE | nonsummer
2024-01-16 21:00 | 2024-01-16 22:00 | Winter | FALSE | nonsummer
2024-01-16 22:00 | 2024-01-16 23:00 | Winter | FALSE | nonsummer
2024-01-16 23:00 | 2024-01-17 | Winter | FALSE | nonsummer
2024-01-17 | 2024-01-17 01:00 | Winter | FALSE | nonsummer
2024-01-17 01:00 | 2024-01-17 02:00 | Winter | FALSE | nonsummer
2024-01-17 02:00 | 2024-01-17 03:00 | Winter | FALSE | nonsummer
2024-01-17 03:00 | 2024-01-17 04:00 | Winter | FALSE | nonsummer
2024-01-17 04:00 | 2024-01-17 05:00 | Winter | FALSE | nonsummer
2024-01-17 05:00 | 2024-01-17 06:00 | Winter | FALSE | nonsummer
2024-01-17 06:00 | 2024-01-17 07:00 | Winter | FALSE | nonsummer
2024-01-17 07:00 | 2024-01-17 08:00 | Winter | FALSE | nonsummer
2024-01-17 08:00 | 2024-01-17 09:00 | Winter | FALSE | nonsummer
2024-01-17 09:00 | 2024-01-17 10:00 | Winter | FALSE | nonsummer
2024-01-17 10:00 | 2024-01-17 11:00 | Winter | FALSE | nonsummer
2024-01-17 11:00 | 2024-01-17 12:00 | Winter | FALSE | nonsummer
2024-01-17 12:00 | 2024-01-17 13:00 | Winter | FALSE | nonsummer
2024-01-17 13:00 | 2024-01-17 14:00 | Winter | FALSE | nonsummer
2024-01-17 14:00 | 2024-01-17 15:00 | Winter | FALSE | nonsummer
2024-01-17 15:00 | 2024-01-17 16:00 | Winter | FALSE | nonsummer
2024-01-17 16:00 | 2024-01-17 17:00 | Winter | TRUE | nonsummer
2024-01-17 17:00 | 2024-01-17 18:00 | Winter | TRUE | nonsummer
2024-01-17 18:00 | 2024-01-17 19:00 | Winter | TRUE | nonsummer
2024-01-17 19:00 | 2024-01-17 20:00 | Winter | TRUE | nonsummer
2024-01-17 20:00 | 2024-01-17 21:00 | Winter | TRUE | nonsummer
2024-01-17 21:00 | 2024-01-17 22:00 | Winter | FALSE | nonsummer
2024-01-17 22:00 | 2024-01-17 23:00 | Winter | FALSE | nonsummer
2024-01-17 23:00 | 2024-01-18 | Winter | FALSE | nonsummer
2024-01-18 | 2024-01-18 01:00 | Winter | FALSE | nonsummer
2024-01-18 01:00 | 2024-01-18 02:00 | Winter | FALSE | nonsummer
2024-01-18 02:00 | 2024-01-18 03:00 | Winter | FALSE | nonsummer
2024-01-18 03:00 | 2024-01-18 04:00 | Winter | FALSE | nonsummer
2024-01-18 04:00 | 2024-01-18 05:00 | Winter | FALSE | nonsummer
2024-01-18 05:00 | 2024-01-18 06:00 | Winter | FALSE | nonsummer
2024-01-18 06:00 | 2024-01-18 07:00 | Winter | FALSE | nonsummer
2024-01-18 07:00 | 2024-01-18 08:00 | Winter | FALSE | nonsummer
2024-01-18 08:00 | 2024-01-18 09:00 | Winter | FALSE | nonsummer
2024-01-18 09:00 | 2024-01-18 10:00 | Winter | FALSE | nonsummer
2024-01-18 10:00 | 2024-01-18 11:00 | Winter | FALSE | nonsummer
2024-01-18 11:00 | 2024-01-18 12:00 | Winter | FALSE | nonsummer
2024-01-18 12:00 | 2024-01-18 13:00 | Winter | FALSE | nonsummer
2024-01-18 13:00 | 2024-01-18 14:00 | Winter | FALSE | nonsummer
2024-01-18 14:00 | 2024-01-18 15:00 | Winter | FALSE | nonsummer
2024-01-18 15:00 | 2024-01-18 16:00 | Winter | FALSE | nonsummer
2024-01-18 16:00 | 2024-01-18 17:00 | Winter | TRUE | nonsummer
2024-01-18 17:00 | 2024-01-18 18:00 | Winter | TRUE | nonsummer
2024-01-18 18:00 | 2024-01-18 19:00 | Winter | TRUE | nonsummer
2024-01-18 19:00 | 2024-01-18 20:00 | Winter | TRUE | nonsummer
2024-01-18 20:00 | 2024-01-18 21:00 | Winter | TRUE | nonsummer
2024-01-18 21:00 | 2024-01-18 22:00 | Winter | FALSE | nonsummer
2024-01-18 22:00 | 2024-01-18 23:00 | Winter | FALSE | nonsummer
2024-01-18 23:00 | 2024-01-19 | Winter | FALSE | nonsummer
2024-01-19 | 2024-01-19 01:00 | Winter | FALSE | nonsummer
2024-01-19 01:00 | 2024-01-19 02:00 | Winter | FALSE | nonsummer
2024-01-19 02:00 | 2024-01-19 03:00 | Winter | FALSE | nonsummer
2024-01-19 03:00 | 2024-01-19 04:00 | Winter | FALSE | nonsummer
2024-01-19 04:00 | 2024-01-19 05:00 | Winter | FALSE | nonsummer
2024-01-19 05:00 | 2024-01-19 06:00 | Winter | FALSE | nonsummer
2024-01-19 06:00 | 2024-01-19 07:00 | Winter | FALSE | nonsummer
2024-01-19 07:00 | 2024-01-19 08:00 | Winter | FALSE | nonsummer
2024-01-19 08:00 | 2024-01-19 09:00 | Winter | FALSE | nonsummer
2024-01-19 09:00 | 2024-01-19 10:00 | Winter | FALSE | nonsummer
2024-01-19 10:00 | 2024-01-19 11:00 | Winter | FALSE | nonsummer
2024-01-19 11:00 | 2024-01-19 12:00 | Winter | FALSE | nonsummer
2024-01-19 12:00 | 2024-01-19 13:00 | Winter | FALSE | nonsummer
2024-01-19 13:00 | 2024-01-19 14:00 | Winter | FALSE | nonsummer
2024-01-19 14:00 | 2024-01-19 15:00 | Winter | FALSE | nonsummer
2024-01-19 15:00 | 2024-01-19 16:00 | Winter | FALSE | nonsummer
2024-01-19 16:00 | 2024-01-19 17:00 | Winter | TRUE | nonsummer
2024-01-19 17:00 | 2024-01-19 18:00 | Winter | TRUE | nonsummer
2024-01-19 18:00 | 2024-01-19 19:00 | Winter | TRUE | nonsummer
2024-01-19 19:00 | 2024-01-19 20:00 | Winter | TRUE | nonsummer
2024-01-19 20:00 | 2024-01-19 21:00 | Winter | TRUE | nonsummer
2024-01-19 21:00 | 2024-01-19 22:00 | Winter | FALSE | nonsummer
2024-01-19 22:00 | 2024-01-19 23:00 | Winter | FALSE | nonsummer
2024-01-19 23:00 | 2024-01-20 | Winter | FALSE | nonsummer
2024-01-20 | 2024-01-20 01:00 | Winter | FALSE | nonsummer
2024-01-20 01:00 | 2024-01-20 02:00 | Winter | FALSE | nonsummer
2024-01-20 02:00 | 2024-01-20 03:00 | Winter | FALSE | nonsummer
2024-01-20 03:00 | 2024-01-20 04:00 | Winter | FALSE | nonsummer
2024-01-20 04:00 | 2024-01-20 05:00 | Winter | FALSE | nonsummer
2024-01-20 05:00 | 2024-01-20 06:00 | Winter | FALSE | nonsummer
2024-01-20 06:00 | 2024-01-20 07:00 | Winter | FALSE | nonsummer
2024-01-20 07:00 | 2024-01-20 08:00 | Winter | FALSE | nonsummer
2024-01-20 08:00 | 2024-01-20 09:00 | Winter | FALSE | nonsummer
2024-01-20 09:00 | 2024-01-20 10:00 | Winter | FALSE | nonsummer
2024-01-20 10:00 | 2024-01-20 11:00 | Winter | FALSE | nonsummer
2024-01-20 11:00 | 2024-01-20 12:00 | Winter | FALSE | nonsummer
2024-01-20 12:00 | 2024-01-20 13:00 | Winter | FALSE | nonsummer
2024-01-20 13:00 | 2024-01-20 14:00 | Winter | FALSE | nonsummer
2024-01-20 14:00 | 2024-01-20 15:00 | Winter | FALSE | nonsummer
2024-01-20 15:00 | 2024-01-20 16:00 | Winter | FALSE | nonsummer
2024-01-20 16:00 | 2024-01-20 17:00 | Winter | TRUE | nonsummer
2024-01-20 17:00 | 2024-01-20 18:00 | Winter | TRUE | nonsummer
2024-01-20 18:00 | 2024-01-20 19:00 | Winter | TRUE | nonsummer
2024-01-20 19:00 | 2024-01-20 20:00 | Winter | TRUE | nonsummer
2024-01-20 20:00 | 2024-01-20 21:00 | Winter | TRUE | nonsummer
2024-01-20 21:00 | 2024-01-20 22:00 | Winter | FALSE | nonsummer
2024-01-20 22:00 | 2024-01-20 23:00 | Winter | FALSE | nonsummer
2024-01-20 23:00 | 2024-01-21 | Winter | FALSE | nonsummer
2024-01-21 | 2024-01-21 01:00 | Winter | FALSE | nonsummer
2024-01-21 01:00 | 2024-01-21 02:00 | Winter | FALSE | nonsummer
2024-01-21 02:00 | 2024-01-21 03:00 | Winter | FALSE | nonsummer
2024-01-21 03:00 | 2024-01-21 04:00 | Winter | FALSE | nonsummer
2024-01-21 04:00 | 2024-01-21 05:00 | Winter | FALSE | nonsummer
2024-01-21 05:00 | 2024-01-21 06:00 | Winter | FALSE | nonsummer
2024-01-21 06:00 | 2024-01-21 07:00 | Winter | FALSE | nonsummer
2024-01-21 07:00 | 2024-01-21 08:00 | Winter | FALSE | nonsummer
2024-01-21 08:00 | 2024-01-21 09:00 | Winter | FALSE | nonsummer
2024-01-21 09:00 | 2024-01-21 10:00 | Winter | FALSE | nonsummer
2024-01-21 10:00 | 2024-01-21 11:00 | Winter | FALSE | nonsummer
2024-01-21 11:00 | 2024-01-21 12:00 | Winter | FALSE | nonsummer
2024-01-21 12:00 | 2024-01-21 13:00 | Winter | FALSE | nonsummer
2024-01-21 13:00 | 2024-01-21 14:00 | Winter | FALSE | nonsummer
2024-01-21 14:00 | 2024-01-21 15:00 | Winter | FALSE | nonsummer
2024-01-21 15:00 | 2024-01-21 16:00 | Winter | FALSE | nonsummer
2024-01-21 16:00 | 2024-01-21 17:00 | Winter | TRUE | nonsummer
2024-01-21 17:00 | 2024-01-21 18:00 | Winter | TRUE | nonsummer
2024-01-21 18:00 | 2024-01-21 19:00 | Winter | TRUE | nonsummer
2024-01-21 19:00 | 2024-01-21 20:00 | Winter | TRUE | nonsummer
2024-01-21 20:00 | 2024-01-21 21:00 | Winter | TRUE | nonsummer
2024-01-21 21:00 | 2024-01-21 22:00 | Winter | FALSE | nonsummer
2024-01-21 22:00 | 2024-01-21 23:00 | Winter | FALSE | nonsummer
2024-01-21 23:00 | 2024-01-22 | Winter | FALSE | nonsummer
2024-01-22 | 2024-01-22 01:00 | Winter | FALSE | nonsummer
2024-01-22 01:00 | 2024-01-22 02:00 | Winter | FALSE | nonsummer
2024-01-22 02:00 | 2024-01-22 03:00 | Winter | FALSE | nonsummer
2024-01-22 03:00 | 2024-01-22 04:00 | Winter | FALSE | nonsummer
2024-01-22 04:00 | 2024-01-22 05:00 | Winter | FALSE | nonsummer
2024-01-22 05:00 | 2024-01-22 06:00 | Winter | FALSE | nonsummer
2024-01-22 06:00 | 2024-01-22 07:00 | Winter | FALSE | nonsummer
2024-01-22 07:00 | 2024-01-22 08:00 | Winter | FALSE | nonsummer
2024-01-22 08:00 | 2024-01-22 09:00 | Winter | FALSE | nonsummer
2024-01-22 09:00 | 2024-01-22 10:00 | Winter | FALSE | nonsummer
2024-01-22 10:00 | 2024-01-22 11:00 | Winter | FALSE | nonsummer
2024-01-22 11:00 | 2024-01-22 12:00 | Winter | FALSE | nonsummer
2024-01-22 12:00 | 2024-01-22 13:00 | Winter | FALSE | nonsummer
2024-01-22 13:00 | 2024-01-22 14:00 | Winter | FALSE | nonsummer
2024-01-22 14:00 | 2024-01-22 15:00 | Winter | FALSE | nonsummer
2024-01-22 15:00 | 2024-01-22 16:00 | Winter | FALSE | nonsummer
2024-01-22 16:00 | 2024-01-22 17:00 | Winter | TRUE | nonsummer
2024-01-22 17:00 | 2024-01-22 18:00 | Winter | TRUE | nonsummer
2024-01-22 18:00 | 2024-01-22 19:00 | Winter | TRUE | nonsummer
2024-01-22 19:00 | 2024-01-22 20:00 | Winter | TRUE | nonsummer
2024-01-22 20:00 | 2024-01-22 21:00 | Winter | TRUE | nonsummer
2024-01-22 21:00 | 2024-01-22 22:00 | Winter | FALSE | nonsummer
2024-01-22 22:00 | 2024-01-22 23:00 | Winter | FALSE | nonsummer
2024-01-22 23:00 | 2024-01-23 | Winter | FALSE | nonsummer
2024-01-23 | 2024-01-23 01:00 | Winter | FALSE | nonsummer
2024-01-23 01:00 | 2024-01-23 02:00 | Winter | FALSE | nonsummer
2024-01-23 02:00 | 2024-01-23 03:00 | Winter | FALSE | nonsummer
2024-01-23 03:00 | 2024-01-23 04:00 | Winter | FALSE | nonsummer
2024-01-23 04:00 | 2024-01-23 05:00 | Winter | FALSE | nonsummer
2024-01-23 05:00 | 2024-01-23 06:00 | Winter | FALSE | nonsummer
2024-01-23 06:00 | 2024-01-23 07:00 | Winter | FALSE | nonsummer
2024-01-23 07:00 | 2024-01-23 08:00 | Winter | FALSE | nonsummer
2024-01-23 08:00 | 2024-01-23 09:00 | Winter | FALSE | nonsummer
2024-01-23 09:00 | 2024-01-23 10:00 | Winter | FALSE | nonsummer
2024-01-23 10:00 | 2024-01-23 11:00 | Winter | FALSE | nonsummer
2024-01-23 11:00 | 2024-01-23 12:00 | Winter | FALSE | nonsummer
2024-01-23 12:00 | 2024-01-23 13:00 | Winter | FALSE | nonsummer
2024-01-23 13:00 | 2024-01-23 14:00 | Winter | FALSE | nonsummer
2024-01-23 14:00 | 2024-01-23 15:00 | Winter | FALSE | nonsummer
2024-01-23 15:00 | 2024-01-23 16:00 | Winter | FALSE | nonsummer
2024-01-23 16:00 | 2024-01-23 17:00 | Winter | TRUE | nonsummer
2024-01-23 17:00 | 2024-01-23 18:00 | Winter | TRUE | nonsummer
2024-01-23 18:00 | 2024-01-23 19:00 | Winter | TRUE | nonsummer
2024-01-23 19:00 | 2024-01-23 20:00 | Winter | TRUE | nonsummer
2024-01-23 20:00 | 2024-01-23 21:00 | Winter | TRUE | nonsummer
2024-01-23 21:00 | 2024-01-23 22:00 | Winter | FALSE | nonsummer
2024-01-23 22:00 | 2024-01-23 23:00 | Winter | FALSE | nonsummer
2024-01-23 23:00 | 2024-01-24 | Winter | FALSE | nonsummer
2024-01-24 | 2024-01-24 01:00 | Winter | FALSE | nonsummer
2024-01-24 01:00 | 2024-01-24 02:00 | Winter | FALSE | nonsummer
2024-01-24 02:00 | 2024-01-24 03:00 | Winter | FALSE | nonsummer
2024-01-24 03:00 | 2024-01-24 04:00 | Winter | FALSE | nonsummer
2024-01-24 04:00 | 2024-01-24 05:00 | Winter | FALSE | nonsummer
2024-01-24 05:00 | 2024-01-24 06:00 | Winter | FALSE | nonsummer
2024-01-24 06:00 | 2024-01-24 07:00 | Winter | FALSE | nonsummer
2024-01-24 07:00 | 2024-01-24 08:00 | Winter | FALSE | nonsummer
2024-01-24 08:00 | 2024-01-24 09:00 | Winter | FALSE | nonsummer
2024-01-24 09:00 | 2024-01-24 10:00 | Winter | FALSE | nonsummer
2024-01-24 10:00 | 2024-01-24 11:00 | Winter | FALSE | nonsummer
2024-01-24 11:00 | 2024-01-24 12:00 | Winter | FALSE | nonsummer
2024-01-24 12:00 | 2024-01-24 13:00 | Winter | FALSE | nonsummer
2024-01-24 13:00 | 2024-01-24 14:00 | Winter | FALSE | nonsummer
2024-01-24 14:00 | 2024-01-24 15:00 | Winter | FALSE | nonsummer
2024-01-24 15:00 | 2024-01-24 16:00 | Winter | FALSE | nonsummer
2024-01-24 16:00 | 2024-01-24 17:00 | Winter | TRUE | nonsummer
2024-01-24 17:00 | 2024-01-24 18:00 | Winter | TRUE | nonsummer
2024-01-24 18:00 | 2024-01-24 19:00 | Winter | TRUE | nonsummer
2024-01-24 19:00 | 2024-01-24 20:00 | Winter | TRUE | nonsummer
2024-01-24 20:00 | 2024-01-24 21:00 | Winter | TRUE | nonsummer
2024-01-24 21:00 | 2024-01-24 22:00 | Winter | FALSE | nonsummer
2024-01-24 22:00 | 2024-01-24 23:00 | Winter | FALSE | nonsummer
2024-01-24 23:00 | 2024-01-25 | Winter | FALSE | nonsummer
2024-01-25 | 2024-01-25 01:00 | Winter | FALSE | nonsummer
2024-01-25 01:00 | 2024-01-25 02:00 | Winter | FALSE | nonsummer
2024-01-25 02:00 | 2024-01-25 03:00 | Winter | FALSE | nonsummer
2024-01-25 03:00 | 2024-01-25 04:00 | Winter | FALSE | nonsummer
2024-01-25 04:00 | 2024-01-25 05:00 | Winter | FALSE | nonsummer
2024-01-25 05:00 | 2024-01-25 06:00 | Winter | FALSE | nonsummer
2024-01-25 06:00 | 2024-01-25 07:00 | Winter | FALSE | nonsummer
2024-01-25 07:00 | 2024-01-25 08:00 | Winter | FALSE | nonsummer
2024-01-25 08:00 | 2024-01-25 09:00 | Winter | FALSE | nonsummer
2024-01-25 09:00 | 2024-01-25 10:00 | Winter | FALSE | nonsummer
2024-01-25 10:00 | 2024-01-25 11:00 | Winter | FALSE | nonsummer
2024-01-25 11:00 | 2024-01-25 12:00 | Winter | FALSE | nonsummer
2024-01-25 12:00 | 2024-01-25 13:00 | Winter | FALSE | nonsummer
2024-01-25 13:00 | 2024-01-25 14:00 | Winter | FALSE | nonsummer
2024-01-25 14:00 | 2024-01-25 15:00 | Winter | FALSE | nonsummer
2024-01-25 15:00 | 2024-01-25 16:00 | Winter | FALSE | nonsummer
2024-01-25 16:00 | 2024-01-25 17:00 | Winter | TRUE | nonsummer
2024-01-25 17:00 | 2024-01-25 18:00 | Winter | TRUE | nonsummer
2024-01-25 18:00 | 2024-01-25 19:00 | Winter | TRUE | nonsummer
2024-01-25 19:00 | 2024-01-25 20:00 | Winter | TRUE | nonsummer
2024-01-25 20:00 | 2024-01-25 21:00 | Winter | TRUE | nonsummer
2024-01-25 21:00 | 2024-01-25 22:00 | Winter | FALSE | nonsummer
2024-01-25 22:00 | 2024-01-25 23:00 | Winter | FALSE | nonsummer
2024-01-25 23:00 | 2024-01-26 | Winter | FALSE | nonsummer
2024-01-26 | 2024-01-26 01:00 | Winter | FALSE | nonsummer
2024-01-26 01:00 | 2024-01-26 02:00 | Winter | FALSE | nonsummer
2024-01-26 02:00 | 2024-01-26 03:00 | Winter | FALSE | nonsummer
2024-01-26 03:00 | 2024-01-26 04:00 | Winter | FALSE | nonsummer
2024-01-26 04:00 | 2024-01-26 05:00 | Winter | FALSE | nonsummer
2024-01-26 05:00 | 2024-01-26 06:00 | Winter | FALSE | nonsummer
2024-01-26 06:00 | 2024-01-26 07:00 | Winter | FALSE | nonsummer
2024-01-26 07:00 | 2024-01-26 08:00 | Winter | FALSE | nonsummer
2024-01-26 08:00 | 2024-01-26 09:00 | Winter | FALSE | nonsummer
2024-01-26 09:00 | 2024-01-26 10:00 | Winter | FALSE | nonsummer
2024-01-26 10:00 | 2024-01-26 11:00 | Winter | FALSE | nonsummer
2024-01-26 11:00 | 2024-01-26 12:00 | Winter | FALSE | nonsummer
2024-01-26 12:00 | 2024-01-26 13:00 | Winter | FALSE | nonsummer
2024-01-26 13:00 | 2024-01-26 14:00 | Winter | FALSE | nonsummer
2024-01-26 14:00 | 2024-01-26 15:00 | Winter | FALSE | nonsummer
2024-01-26 15:00 | 2024-01-26 16:00 | Winter | FALSE | nonsummer
2024-01-26 16:00 | 2024-01-26 17:00 | Winter | TRUE | nonsummer
2024-01-26 17:00 | 2024-01-26 18:00 | Winter | TRUE | nonsummer
2024-01-26 18:00 | 2024-01-26 19:00 | Winter | TRUE | nonsummer
2024-01-26 19:00 | 2024-01-26 20:00 | Winter | TRUE | nonsummer
2024-01-26 20:00 | 2024-01-26 21:00 | Winter | TRUE | nonsummer
2024-01-26 21:00 | 2024-01-26 22:00 | Winter | FALSE | nonsummer
2024-01-26 22:00 | 2024-01-26 23:00 | Winter | FALSE | nonsummer
2024-01-26 23:00 | 2024-01-27 | Winter | FALSE | nonsummer
2024-01-27 | 2024-01-27 01:00 | Winter | FALSE | nonsummer
2024-01-27 01:00 | 2024-01-27 02:00 | Winter | FALSE | nonsummer
2024-01-27 02:00 | 2024-01-27 03:00 | Winter | FALSE | nonsummer
2024-01-27 03:00 | 2024-01-27 04:00 | Winter | FALSE | nonsummer
2024-01-27 04:00 | 2024-01-27 05:00 | Winter | FALSE | nonsummer
2024-01-27 05:00 | 2024-01-27 06:00 | Winter | FALSE | nonsummer
2024-01-27 06:00 | 2024-01-27 07:00 | Winter | FALSE | nonsummer
2024-01-27 07:00 | 2024-01-27 08:00 | Winter | FALSE | nonsummer
2024-01-27 08:00 | 2024-01-27 09:00 | Winter | FALSE | nonsummer
2024-01-27 09:00 | 2024-01-27 10:00 | Winter | FALSE | nonsummer
2024-01-27 10:00 | 2024-01-27 11:00 | Winter | FALSE | nonsummer
2024-01-27 11:00 | 2024-01-27 12:00 | Winter | FALSE | nonsummer
2024-01-27 12:00 | 2024-01-27 13:00 | Winter | FALSE | nonsummer
2024-01-27 13:00 | 2024-01-27 14:00 | Winter | FALSE | nonsummer
2024-01-27 14:00 | 2024-01-27 15:00 | Winter | FALSE | nonsummer
2024-01-27 15:00 | 2024-01-27 16:00 | Winter | FALSE | nonsummer
2024-01-27 16:00 | 2024-01-27 17:00 | Winter | TRUE | nonsummer
2024-01-27 17:00 | 2024-01-27 18:00 | Winter | TRUE | nonsummer
2024-01-27 18:00 | 2024-01-27 19:00 | Winter | TRUE | nonsummer
2024-01-27 19:00 | 2024-01-27 20:00 | Winter | TRUE | nonsummer
2024-01-27 20:00 | 2024-01-27 21:00 | Winter | TRUE | nonsummer
2024-01-27 21:00 | 2024-01-27 22:00 | Winter | FALSE | nonsummer
2024-01-27 22:00 | 2024-01-27 23:00 | Winter | FALSE | nonsummer
2024-01-27 23:00 | 2024-01-28 | Winter | FALSE | nonsummer
2024-01-28 | 2024-01-28 01:00 | Winter | FALSE | nonsummer
2024-01-28 01:00 | 2024-01-28 02:00 | Winter | FALSE | nonsummer
2024-01-28 02:00 | 2024-01-28 03:00 | Winter | FALSE | nonsummer
2024-01-28 03:00 | 2024-01-28 04:00 | Winter | FALSE | nonsummer
2024-01-28 04:00 | 2024-01-28 05:00 | Winter | FALSE | nonsummer
2024-01-28 05:00 | 2024-01-28 06:00 | Winter | FALSE | nonsummer
2024-01-28 06:00 | 2024-01-28 07:00 | Winter | FALSE | nonsummer
2024-01-28 07:00 | 2024-01-28 08:00 | Winter | FALSE | nonsummer
2024-01-28 08:00 | 2024-01-28 09:00 | Winter | FALSE | nonsummer
2024-01-28 09:00 | 2024-01-28 10:00 | Winter | FALSE | nonsummer
2024-01-28 10:00 | 2024-01-28 11:00 | Winter | FALSE | nonsummer
2024-01-28 11:00 | 2024-01-28 12:00 | Winter | FALSE | nonsummer
2024-01-28 12:00 | 2024-01-28 13:00 | Winter | FALSE | nonsummer
2024-01-28 13:00 | 2024-01-28 14:00 | Winter | FALSE | nonsummer
2024-01-28 14:00 | 2024-01-28 15:00 | Winter | FALSE | nonsummer
2024-01-28 15:00 | 2024-01-28 16:00 | Winter | FALSE | nonsummer
2024-01-28 16:00 | 2024-01-28 17:00 | Winter | TRUE | nonsummer
2024-01-28 17:00 | 2024-01-28 18:00 | Winter | TRUE | nonsummer
2024-01-28 18:00 | 2024-01-28 19:00 | Winter | TRUE | nonsummer
2024-01-28 19:00 | 2024-01-28 20:00 | Winter | TRUE | nonsummer
2024-01-28 20:00 | 2024-01-28 21:00 | Winter | TRUE | nonsummer
2024-01-28 21:00 | 2024-01-28 22:00 | Winter | FALSE | nonsummer
2024-01-28 22:00 | 2024-01-28 23:00 | Winter | FALSE | nonsummer
2024-01-28 23:00 | 2024-01-29 | Winter | FALSE | nonsummer
2024-01-29 | 2024-01-29 01:00 | Winter | FALSE | nonsummer
2024-01-29 01:00 | 2024-01-29 02:00 | Winter | FALSE | nonsummer
2024-01-29 02:00 | 2024-01-29 03:00 | Winter | FALSE | nonsummer
2024-01-29 03:00 | 2024-01-29 04:00 | Winter | FALSE | nonsummer
2024-01-29 04:00 | 2024-01-29 05:00 | Winter | FALSE | nonsummer
2024-01-29 05:00 | 2024-01-29 06:00 | Winter | FALSE | nonsummer
2024-01-29 06:00 | 2024-01-29 07:00 | Winter | FALSE | nonsummer
2024-01-29 07:00 | 2024-01-29 08:00 | Winter | FALSE | nonsummer
2024-01-29 08:00 | 2024-01-29 09:00 | Winter | FALSE | nonsummer
2024-01-29 09:00 | 2024-01-29 10:00 | Winter | FALSE | nonsummer
2024-01-29 10:00 | 2024-01-29 11:00 | Winter | FALSE | nonsummer
2024-01-29 11:00 | 2024-01-29 12:00 | Winter | FALSE | nonsummer
2024-01-29 12:00 | 2024-01-29 13:00 | Winter | FALSE | nonsummer
2024-01-29 13:00 | 2024-01-29 14:00 | Winter | FALSE | nonsummer
2024-01-29 14:00 | 2024-01-29 15:00 | Winter | FALSE | nonsummer
2024-01-29 15:00 | 2024-01-29 16:00 | Winter | FALSE | nonsummer
2024-01-29 16:00 | 2024-01-29 17:00 | Winter | TRUE | nonsummer
2024-01-29 17:00 | 2024-01-29 18:00 | Winter | TRUE | nonsummer
2024-01-29 18:00 | 2024-01-29 19:00 | Winter | TRUE | nonsummer
2024-01-29 19:00 | 2024-01-29 20:00 | Winter | TRUE | nonsummer
2024-01-29 20:00 | 2024-01-29 21:00 | Winter | TRUE | nonsummer
2024-01-29 21:00 | 2024-01-29 22:00 | Winter | FALSE | nonsummer
2024-01-29 22:00 | 2024-01-29 23:00 | Winter | FALSE | nonsummer
2024-01-29 23:00 | 2024-01-30 | Winter | FALSE | nonsummer
2024-01-30 | 2024-01-30 01:00 | Winter | FALSE | nonsummer
2024-01-30 01:00 | 2024-01-30 02:00 | Winter | FALSE | nonsummer
2024-01-30 02:00 | 2024-01-30 03:00 | Winter | FALSE | nonsummer
2024-01-30 03:00 | 2024-01-30 04:00 | Winter | FALSE | nonsummer
2024-01-30 04:00 | 2024-01-30 05:00 | Winter | FALSE | nonsummer
2024-01-30 05:00 | 2024-01-30 06:00 | Winter | FALSE | nonsummer
2024-01-30 06:00 | 2024-01-30 07:00 | Winter | FALSE | nonsummer
2024-01-30 07:00 | 2024-01-30 08:00 | Winter | FALSE | nonsummer
2024-01-30 08:00 | 2024-01-30 09:00 | Winter | FALSE | nonsummer
2024-01-30 09:00 | 2024-01-30 10:00 | Winter | FALSE | nonsummer
2024-01-30 10:00 | 2024-01-30 11:00 | Winter | FALSE | nonsummer
2024-01-30 11:00 | 2024-01-30 12:00 | Winter | FALSE | nonsummer
2024-01-30 12:00 | 2024-01-30 13:00 | Winter | FALSE | nonsummer
2024-01-30 13:00 | 2024-01-30 14:00 | Winter | FALSE | nonsummer
2024-01-30 14:00 | 2024-01-30 15:00 | Winter | FALSE | nonsummer
2024-01-30 15:00 | 2024-01-30 16:00 | Winter | FALSE | nonsummer
2024-01-30 16:00 | 2024-01-30 17:00 | Winter | TRUE | nonsummer
2024-01-30 17:00 | 2024-01-30 18:00 | Winter | TRUE | nonsummer
2024-01-30 18:00 | 2024-01-30 19:00 | Winter | TRUE | nonsummer
2024-01-30 19:00 | 2024-01-30 20:00 | Winter | TRUE | nonsummer
2024-01-30 20:00 | 2024-01-30 21:00 | Winter | TRUE | nonsummer
2024-01-30 21:00 | 2024-01-30 22:00 | Winter | FALSE | nonsummer
2024-01-30 22:00 | 2024-01-30 23:00 | Winter | FALSE | nonsummer
2024-01-30 23:00 | 2024-01-31 | Winter | FALSE | nonsummer
2024-01-31 | 2024-01-31 01:00 | Winter | FALSE | nonsummer
2024-01-31 01:00 | 2024-01-31 02:00 | Winter | FALSE | nonsummer
2024-01-31 02:00 | 2024-01-31 03:00 | Winter | FALSE | nonsummer
2024-01-31 03:00 | 2024-01-31 04:00 | Winter | FALSE | nonsummer
2024-01-31 04:00 | 2024-01-31 05:00 | Winter | FALSE | nonsummer
2024-01-31 05:00 | 2024-01-31 06:00 | Winter | FALSE | nonsummer
2024-01-31 06:00 | 2024-01-31 07:00 | Winter | FALSE | nonsummer
2024-01-31 07:00 | 2024-01-31 08:00 | Winter | FALSE | nonsummer
2024-01-31 08:00 | 2024-01-31 09:00 | Winter | FALSE | nonsummer
2024-01-31 09:00 | 2024-01-31 10:00 | Winter | FALSE | nonsummer
2024-01-31 10:00 | 2024-01-31 11:00 | Winter | FALSE | nonsummer
2024-01-31 11:00 | 2024-01-31 12:00 | Winter | FALSE | nonsummer
2024-01-31 12:00 | 2024-01-31 13:00 | Winter | FALSE | nonsummer
2024-01-31 13:00 | 2024-01-31 14:00 | Winter | FALSE | nonsummer
2024-01-31 14:00 | 2024-01-31 15:00 | Winter | FALSE | nonsummer
2024-01-31 15:00 | 2024-01-31 16:00 | Winter | FALSE | nonsummer
2024-01-31 16:00 | 2024-01-31 17:00 | Winter | TRUE | nonsummer
2024-01-31 17:00 | 2024-01-31 18:00 | Winter | TRUE | nonsummer
2024-01-31 18:00 | 2024-01-31 19:00 | Winter | TRUE | nonsummer
2024-01-31 19:00 | 2024-01-31 20:00 | Winter | TRUE | nonsummer
2024-01-31 20:00 | 2024-01-31 21:00 | Winter | TRUE | nonsummer
2024-01-31 21:00 | 2024-01-31 22:00 | Winter | FALSE | nonsummer
2024-01-31 22:00 | 2024-01-31 23:00 | Winter | FALSE | nonsummer
2024-01-31 23:00 | 2024-02-01 | Winter | FALSE | nonsummer
2024-02-01 | 2024-02-01 01:00 | Winter | FALSE | nonsummer
2024-02-01 01:00 | 2024-02-01 02:00 | Winter | FALSE | nonsummer
2024-02-01 02:00 | 2024-02-01 03:00 | Winter | FALSE | nonsummer
2024-02-01 03:00 | 2024-02-01 04:00 | Winter | FALSE | nonsummer
2024-02-01 04:00 | 2024-02-01 05:00 | Winter | FALSE | nonsummer
2024-02-01 05:00 | 2024-02-01 06:00 | Winter | FALSE | nonsummer
2024-02-01 06:00 | 2024-02-01 07:00 | Winter | FALSE | nonsummer
2024-02-01 07:00 | 2024-02-01 08:00 | Winter | FALSE | nonsummer
2024-02-01 08:00 | 2024-02-01 09:00 | Winter | FALSE | nonsummer
2024-02-01 09:00 | 2024-02-01 10:00 | Winter | FALSE | nonsummer
2024-02-01 10:00 | 2024-02-01 11:00 | Winter | FALSE | nonsummer
2024-02-01 11:00 | 2024-02-01 12:00 | Winter | FALSE | nonsummer
2024-02-01 12:00 | 2024-02-01 13:00 | Winter | FALSE | nonsummer
2024-02-01 13:00 | 2024-02-01 14:00 | Winter | FALSE | nonsummer
2024-02-01 14:00 | 2024-02-01 15:00 | Winter | FALSE | nonsummer
2024-02-01 15:00 | 2024-02-01 16:00 | Winter | FALSE | nonsummer
2024-02-01 16:00 | 2024-02-01 17:00 | Winter | TRUE | nonsummer
2024-02-01 17:00 | 2024-02-01 18:00 | Winter | TRUE | nonsummer
2024-02-01 18:00 | 2024-02-01 19:00 | Winter | TRUE | nonsummer
2024-02-01 19:00 | 2024-02-01 20:00 | Winter | TRUE | nonsummer
2024-02-01 20:00 | 2024-02-01 21:00 | Winter | TRUE | nonsummer
2024-02-01 21:00 | 2024-02-01 22:00 | Winter | FALSE | nonsummer
2024-02-01 22:00 | 2024-02-01 23:00 | Winter | FALSE | nonsummer
2024-02-01 23:00 | 2024-02-02 | Winter | FALSE | nonsummer
2024-02-02 | 2024-02-02 01:00 | Winter | FALSE | nonsummer
2024-02-02 01:00 | 2024-02-02 02:00 | Winter | FALSE | nonsummer
2024-02-02 02:00 | 2024-02-02 03:00 | Winter | FALSE | nonsummer
2024-02-02 03:00 | 2024-02-02 04:00 | Winter | FALSE | nonsummer
2024-02-02 04:00 | 2024-02-02 05:00 | Winter | FALSE | nonsummer
2024-02-02 05:00 | 2024-02-02 06:00 | Winter | FALSE | nonsummer
2024-02-02 06:00 | 2024-02-02 07:00 | Winter | FALSE | nonsummer
2024-02-02 07:00 | 2024-02-02 08:00 | Winter | FALSE | nonsummer
2024-02-02 08:00 | 2024-02-02 09:00 | Winter | FALSE | nonsummer
2024-02-02 09:00 | 2024-02-02 10:00 | Winter | FALSE | nonsummer
2024-02-02 10:00 | 2024-02-02 11:00 | Winter | FALSE | nonsummer
2024-02-02 11:00 | 2024-02-02 12:00 | Winter | FALSE | nonsummer
2024-02-02 12:00 | 2024-02-02 13:00 | Winter | FALSE | nonsummer
2024-02-02 13:00 | 2024-02-02 14:00 | Winter | FALSE | nonsummer
2024-02-02 14:00 | 2024-02-02 15:00 | Winter | FALSE | nonsummer
2024-02-02 15:00 | 2024-02-02 16:00 | Winter | FALSE | nonsummer
2024-02-02 16:00 | 2024-02-02 17:00 | Winter | TRUE | nonsummer
2024-02-02 17:00 | 2024-02-02 18:00 | Winter | TRUE | nonsummer
2024-02-02 18:00 | 2024-02-02 19:00 | Winter | TRUE | nonsummer
2024-02-02 19:00 | 2024-02-02 20:00 | Winter | TRUE | nonsummer
2024-02-02 20:00 | 2024-02-02 21:00 | Winter | TRUE | nonsummer
2024-02-02 21:00 | 2024-02-02 22:00 | Winter | FALSE | nonsummer
2024-02-02 22:00 | 2024-02-02 23:00 | Winter | FALSE | nonsummer
2024-02-02 23:00 | 2024-02-03 | Winter | FALSE | nonsummer
2024-02-03 | 2024-02-03 01:00 | Winter | FALSE | nonsummer
2024-02-03 01:00 | 2024-02-03 02:00 | Winter | FALSE | nonsummer
2024-02-03 02:00 | 2024-02-03 03:00 | Winter | FALSE | nonsummer
2024-02-03 03:00 | 2024-02-03 04:00 | Winter | FALSE | nonsummer
2024-02-03 04:00 | 2024-02-03 05:00 | Winter | FALSE | nonsummer
2024-02-03 05:00 | 2024-02-03 06:00 | Winter | FALSE | nonsummer
2024-02-03 06:00 | 2024-02-03 07:00 | Winter | FALSE | nonsummer
2024-02-03 07:00 | 2024-02-03 08:00 | Winter | FALSE | nonsummer
2024-02-03 08:00 | 2024-02-03 09:00 | Winter | FALSE | nonsummer
2024-02-03 09:00 | 2024-02-03 10:00 | Winter | FALSE | nonsummer
2024-02-03 10:00 | 2024-02-03 11:00 | Winter | FALSE | nonsummer
2024-02-03 11:00 | 2024-02-03 12:00 | Winter | FALSE | nonsummer
2024-02-03 12:00 | 2024-02-03 13:00 | Winter | FALSE | nonsummer
2024-02-03 13:00 | 2024-02-03 14:00 | Winter | FALSE | nonsummer
2024-02-03 14:00 | 2024-02-03 15:00 | Winter | FALSE | nonsummer
2024-02-03 15:00 | 2024-02-03 16:00 | Winter | FALSE | nonsummer
2024-02-03 16:00 | 2024-02-03 17:00 | Winter | TRUE | nonsummer
2024-02-03 17:00 | 2024-02-03 18:00 | Winter | TRUE | nonsummer
2024-02-03 18:00 | 2024-02-03 19:00 | Winter | TRUE | nonsummer
2024-02-03 19:00 | 2024-02-03 20:00 | Winter | TRUE | nonsummer
2024-02-03 20:00 | 2024-02-03 21:00 | Winter | TRUE | nonsummer
2024-02-03 21:00 | 2024-02-03 22:00 | Winter | FALSE | nonsummer
2024-02-03 22:00 | 2024-02-03 23:00 | Winter | FALSE | nonsummer
2024-02-03 23:00 | 2024-02-04 | Winter | FALSE | nonsummer
2024-02-04 | 2024-02-04 01:00 | Winter | FALSE | nonsummer
2024-02-04 01:00 | 2024-02-04 02:00 | Winter | FALSE | nonsummer
2024-02-04 02:00 | 2024-02-04 03:00 | Winter | FALSE | nonsummer
2024-02-04 03:00 | 2024-02-04 04:00 | Winter | FALSE | nonsummer
2024-02-04 04:00 | 2024-02-04 05:00 | Winter | FALSE | nonsummer
2024-02-04 05:00 | 2024-02-04 06:00 | Winter | FALSE | nonsummer
2024-02-04 06:00 | 2024-02-04 07:00 | Winter | FALSE | nonsummer
2024-02-04 07:00 | 2024-02-04 08:00 | Winter | FALSE | nonsummer
2024-02-04 08:00 | 2024-02-04 09:00 | Winter | FALSE | nonsummer
2024-02-04 09:00 | 2024-02-04 10:00 | Winter | FALSE | nonsummer
2024-02-04 10:00 | 2024-02-04 11:00 | Winter | FALSE | nonsummer
2024-02-04 11:00 | 2024-02-04 12:00 | Winter | FALSE | nonsummer
2024-02-04 12:00 | 2024-02-04 13:00 | Winter | FALSE | nonsummer
2024-02-04 13:00 | 2024-02-04 14:00 | Winter | FALSE | nonsummer
2024-02-04 14:00 | 2024-02-04 15:00 | Winter | FALSE | nonsummer
2024-02-04 15:00 | 2024-02-04 16:00 | Winter | FALSE | nonsummer
2024-02-04 16:00 | 2024-02-04 17:00 | Winter | TRUE | nonsummer
2024-02-04 17:00 | 2024-02-04 18:00 | Winter | TRUE | nonsummer
2024-02-04 18:00 | 2024-02-04 19:00 | Winter | TRUE | nonsummer
2024-02-04 19:00 | 2024-02-04 20:00 | Winter | TRUE | nonsummer
2024-02-04 20:00 | 2024-02-04 21:00 | Winter | TRUE | nonsummer
2024-02-04 21:00 | 2024-02-04 22:00 | Winter | FALSE | nonsummer
2024-02-04 22:00 | 2024-02-04 23:00 | Winter | FALSE | nonsummer
2024-02-04 23:00 | 2024-02-05 | Winter | FALSE | nonsummer
2024-02-05 | 2024-02-05 01:00 | Winter | FALSE | nonsummer
2024-02-05 01:00 | 2024-02-05 02:00 | Winter | FALSE | nonsummer
2024-02-05 02:00 | 2024-02-05 03:00 | Winter | FALSE | nonsummer
2024-02-05 03:00 | 2024-02-05 04:00 | Winter | FALSE | nonsummer
2024-02-05 04:00 | 2024-02-05 05:00 | Winter | FALSE | nonsummer
2024-02-05 05:00 | 2024-02-05 06:00 | Winter | FALSE | nonsummer
2024-02-05 06:00 | 2024-02-05 07:00 | Winter | FALSE | nonsummer
2024-02-05 07:00 | 2024-02-05 08:00 | Winter | FALSE | nonsummer
2024-02-05 08:00 | 2024-02-05 09:00 | Winter | FALSE | nonsummer
2024-02-05 09:00 | 2024-02-05 10:00 | Winter | FALSE | nonsummer
2024-02-05 10:00 | 2024-02-05 11:00 | Winter | FALSE | nonsummer
2024-02-05 11:00 | 2024-02-05 12:00 | Winter | FALSE | nonsummer
2024-02-05 12:00 | 2024-02-05 13:00 | Winter | FALSE | nonsummer
2024-02-05 13:00 | 2024-02-05 14:00 | Winter | FALSE | nonsummer
2024-02-05 14:00 | 2024-02-05 15:00 | Winter | FALSE | nonsummer
2024-02-05 15:00 | 2024-02-05 16:00 | Winter | FALSE | nonsummer
2024-02-05 16:00 | 2024-02-05 17:00 | Winter | TRUE | nonsummer
2024-02-05 17:00 | 2024-02-05 18:00 | Winter | TRUE | nonsummer
2024-02-05 18:00 | 2024-02-05 19:00 | Winter | TRUE | nonsummer
2024-02-05 19:00 | 2024-02-05 20:00 | Winter | TRUE | nonsummer
2024-02-05 20:00 | 2024-02-05 21:00 | Winter | TRUE | nonsummer
2024-02-05 21:00 | 2024-02-05 22:00 | Winter | FALSE | nonsummer
2024-02-05 22:00 | 2024-02-05 23:00 | Winter | FALSE | nonsummer
2024-02-05 23:00 | 2024-02-06 | Winter | FALSE | nonsummer
2024-02-06 | 2024-02-06 01:00 | Winter | FALSE | nonsummer
2024-02-06 01:00 | 2024-02-06 02:00 | Winter | FALSE | nonsummer
2024-02-06 02:00 | 2024-02-06 03:00 | Winter | FALSE | nonsummer
2024-02-06 03:00 | 2024-02-06 04:00 | Winter | FALSE | nonsummer
2024-02-06 04:00 | 2024-02-06 05:00 | Winter | FALSE | nonsummer
2024-02-06 05:00 | 2024-02-06 06:00 | Winter | FALSE | nonsummer
2024-02-06 06:00 | 2024-02-06 07:00 | Winter | FALSE | nonsummer
2024-02-06 07:00 | 2024-02-06 08:00 | Winter | FALSE | nonsummer
2024-02-06 08:00 | 2024-02-06 09:00 | Winter | FALSE | nonsummer
2024-02-06 09:00 | 2024-02-06 10:00 | Winter | FALSE | nonsummer
2024-02-06 10:00 | 2024-02-06 11:00 | Winter | FALSE | nonsummer
2024-02-06 11:00 | 2024-02-06 12:00 | Winter | FALSE | nonsummer
2024-02-06 12:00 | 2024-02-06 13:00 | Winter | FALSE | nonsummer
2024-02-06 13:00 | 2024-02-06 14:00 | Winter | FALSE | nonsummer
2024-02-06 14:00 | 2024-02-06 15:00 | Winter | FALSE | nonsummer
2024-02-06 15:00 | 2024-02-06 16:00 | Winter | FALSE | nonsummer
2024-02-06 16:00 | 2024-02-06 17:00 | Winter | TRUE | nonsummer
2024-02-06 17:00 | 2024-02-06 18:00 | Winter | TRUE | nonsummer
2024-02-06 18:00 | 2024-02-06 19:00 | Winter | TRUE | nonsummer
2024-02-06 19:00 | 2024-02-06 20:00 | Winter | TRUE | nonsummer
2024-02-06 20:00 | 2024-02-06 21:00 | Winter | TRUE | nonsummer
2024-02-06 21:00 | 2024-02-06 22:00 | Winter | FALSE | nonsummer
2024-02-06 22:00 | 2024-02-06 23:00 | Winter | FALSE | nonsummer
2024-02-06 23:00 | 2024-02-07 | Winter | FALSE | nonsummer
2024-02-07 | 2024-02-07 01:00 | Winter | FALSE | nonsummer
2024-02-07 01:00 | 2024-02-07 02:00 | Winter | FALSE | nonsummer
2024-02-07 02:00 | 2024-02-07 03:00 | Winter | FALSE | nonsummer
2024-02-07 03:00 | 2024-02-07 04:00 | Winter | FALSE | nonsummer
2024-02-07 04:00 | 2024-02-07 05:00 | Winter | FALSE | nonsummer
2024-02-07 05:00 | 2024-02-07 06:00 | Winter | FALSE | nonsummer
2024-02-07 06:00 | 2024-02-07 07:00 | Winter | FALSE | nonsummer
2024-02-07 07:00 | 2024-02-07 08:00 | Winter | FALSE | nonsummer
2024-02-07 08:00 | 2024-02-07 09:00 | Winter | FALSE | nonsummer
2024-02-07 09:00 | 2024-02-07 10:00 | Winter | FALSE | nonsummer
2024-02-07 10:00 | 2024-02-07 11:00 | Winter | FALSE | nonsummer
2024-02-07 11:00 | 2024-02-07 12:00 | Winter | FALSE | nonsummer
2024-02-07 12:00 | 2024-02-07 13:00 | Winter | FALSE | nonsummer
2024-02-07 13:00 | 2024-02-07 14:00 | Winter | FALSE | nonsummer
2024-02-07 14:00 | 2024-02-07 15:00 | Winter | FALSE | nonsummer
2024-02-07 15:00 | 2024-02-07 16:00 | Winter | FALSE | nonsummer
2024-02-07 16:00 | 2024-02-07 17:00 | Winter | TRUE | nonsummer
2024-02-07 17:00 | 2024-02-07 18:00 | Winter | TRUE | nonsummer
2024-02-07 18:00 | 2024-02-07 19:00 | Winter | TRUE | nonsummer
2024-02-07 19:00 | 2024-02-07 20:00 | Winter | TRUE | nonsummer
2024-02-07 20:00 | 2024-02-07 21:00 | Winter | TRUE | nonsummer
2024-02-07 21:00 | 2024-02-07 22:00 | Winter | FALSE | nonsummer
2024-02-07 22:00 | 2024-02-07 23:00 | Winter | FALSE | nonsummer
2024-02-07 23:00 | 2024-02-08 | Winter | FALSE | nonsummer
2024-02-08 | 2024-02-08 01:00 | Winter | FALSE | nonsummer
2024-02-08 01:00 | 2024-02-08 02:00 | Winter | FALSE | nonsummer
2024-02-08 02:00 | 2024-02-08 03:00 | Winter | FALSE | nonsummer
2024-02-08 03:00 | 2024-02-08 04:00 | Winter | FALSE | nonsummer
2024-02-08 04:00 | 2024-02-08 05:00 | Winter | FALSE | nonsummer
2024-02-08 05:00 | 2024-02-08 06:00 | Winter | FALSE | nonsummer
2024-02-08 06:00 | 2024-02-08 07:00 | Winter | FALSE | nonsummer
2024-02-08 07:00 | 2024-02-08 08:00 | Winter | FALSE | nonsummer
2024-02-08 08:00 | 2024-02-08 09:00 | Winter | FALSE | nonsummer
2024-02-08 09:00 | 2024-02-08 10:00 | Winter | FALSE | nonsummer
2024-02-08 10:00 | 2024-02-08 11:00 | Winter | FALSE | nonsummer
2024-02-08 11:00 | 2024-02-08 12:00 | Winter | FALSE | nonsummer
2024-02-08 12:00 | 2024-02-08 13:00 | Winter | FALSE | nonsummer
2024-02-08 13:00 | 2024-02-08 14:00 | Winter | FALSE | nonsummer
2024-02-08 14:00 | 2024-02-08 15:00 | Winter | FALSE | nonsummer
2024-02-08 15:00 | 2024-02-08 16:00 | Winter | FALSE | nonsummer
2024-02-08 16:00 | 2024-02-08 17:00 | Winter | TRUE | nonsummer
2024-02-08 17:00 | 2024-02-08 18:00 | Winter | TRUE | nonsummer
2024-02-08 18:00 | 2024-02-08 19:00 | Winter | TRUE | nonsummer
2024-02-08 19:00 | 2024-02-08 20:00 | Winter | TRUE | nonsummer
2024-02-08 20:00 | 2024-02-08 21:00 | Winter | TRUE | nonsummer
2024-02-08 21:00 | 2024-02-08 22:00 | Winter | FALSE | nonsummer
2024-02-08 22:00 | 2024-02-08 23:00 | Winter | FALSE | nonsummer
2024-02-08 23:00 | 2024-02-09 | Winter | FALSE | nonsummer
2024-02-09 | 2024-02-09 01:00 | Winter | FALSE | nonsummer
2024-02-09 01:00 | 2024-02-09 02:00 | Winter | FALSE | nonsummer
2024-02-09 02:00 | 2024-02-09 03:00 | Winter | FALSE | nonsummer
2024-02-09 03:00 | 2024-02-09 04:00 | Winter | FALSE | nonsummer
2024-02-09 04:00 | 2024-02-09 05:00 | Winter | FALSE | nonsummer
2024-02-09 05:00 | 2024-02-09 06:00 | Winter | FALSE | nonsummer
2024-02-09 06:00 | 2024-02-09 07:00 | Winter | FALSE | nonsummer
2024-02-09 07:00 | 2024-02-09 08:00 | Winter | FALSE | nonsummer
2024-02-09 08:00 | 2024-02-09 09:00 | Winter | FALSE | nonsummer
2024-02-09 09:00 | 2024-02-09 10:00 | Winter | FALSE | nonsummer
2024-02-09 10:00 | 2024-02-09 11:00 | Winter | FALSE | nonsummer
2024-02-09 11:00 | 2024-02-09 12:00 | Winter | FALSE | nonsummer
2024-02-09 12:00 | 2024-02-09 13:00 | Winter | FALSE | nonsummer
2024-02-09 13:00 | 2024-02-09 14:00 | Winter | FALSE | nonsummer
2024-02-09 14:00 | 2024-02-09 15:00 | Winter | FALSE | nonsummer
2024-02-09 15:00 | 2024-02-09 16:00 | Winter | FALSE | nonsummer
2024-02-09 16:00 | 2024-02-09 17:00 | Winter | TRUE | nonsummer
2024-02-09 17:00 | 2024-02-09 18:00 | Winter | TRUE | nonsummer
2024-02-09 18:00 | 2024-02-09 19:00 | Winter | TRUE | nonsummer
2024-02-09 19:00 | 2024-02-09 20:00 | Winter | TRUE | nonsummer
2024-02-09 20:00 | 2024-02-09 21:00 | Winter | TRUE | nonsummer
2024-02-09 21:00 | 2024-02-09 22:00 | Winter | FALSE | nonsummer
2024-02-09 22:00 | 2024-02-09 23:00 | Winter | FALSE | nonsummer
2024-02-09 23:00 | 2024-02-10 | Winter | FALSE | nonsummer
2024-02-10 | 2024-02-10 01:00 | Winter | FALSE | nonsummer
2024-02-10 01:00 | 2024-02-10 02:00 | Winter | FALSE | nonsummer
2024-02-10 02:00 | 2024-02-10 03:00 | Winter | FALSE | nonsummer
2024-02-10 03:00 | 2024-02-10 04:00 | Winter | FALSE | nonsummer
2024-02-10 04:00 | 2024-02-10 05:00 | Winter | FALSE | nonsummer
2024-02-10 05:00 | 2024-02-10 06:00 | Winter | FALSE | nonsummer
2024-02-10 06:00 | 2024-02-10 07:00 | Winter | FALSE | nonsummer
2024-02-10 07:00 | 2024-02-10 08:00 | Winter | FALSE | nonsummer
2024-02-10 08:00 | 2024-02-10 09:00 | Winter | FALSE | nonsummer
2024-02-10 09:00 | 2024-02-10 10:00 | Winter | FALSE | nonsummer
2024-02-10 10:00 | 2024-02-10 11:00 | Winter | FALSE | nonsummer
2024-02-10 11:00 | 2024-02-10 12:00 | Winter | FALSE | nonsummer
2024-02-10 12:00 | 2024-02-10 13:00 | Winter | FALSE | nonsummer
2024-02-10 13:00 | 2024-02-10 14:00 | Winter | FALSE | nonsummer
2024-02-10 14:00 | 2024-02-10 15:00 | Winter | FALSE | nonsummer
2024-02-10 15:00 | 2024-02-10 16:00 | Winter | FALSE | nonsummer
2024-02-10 16:00 | 2024-02-10 17:00 | Winter | TRUE | nonsummer
2024-02-10 17:00 | 2024-02-10 18:00 | Winter | TRUE | nonsummer
2024-02-10 18:00 | 2024-02-10 19:00 | Winter | TRUE | nonsummer
2024-02-10 19:00 | 2024-02-10 20:00 | Winter | TRUE | nonsummer
2024-02-10 20:00 | 2024-02-10 21:00 | Winter | TRUE | nonsummer
2024-02-10 21:00 | 2024-02-10 22:00 | Winter | FALSE | nonsummer
2024-02-10 22:00 | 2024-02-10 23:00 | Winter | FALSE | nonsummer
2024-02-10 23:00 | 2024-02-11 | Winter | FALSE | nonsummer
2024-02-11 | 2024-02-11 01:00 | Winter | FALSE | nonsummer
2024-02-11 01:00 | 2024-02-11 02:00 | Winter | FALSE | nonsummer
2024-02-11 02:00 | 2024-02-11 03:00 | Winter | FALSE | nonsummer
2024-02-11 03:00 | 2024-02-11 04:00 | Winter | FALSE | nonsummer
2024-02-11 04:00 | 2024-02-11 05:00 | Winter | FALSE | nonsummer
2024-02-11 05:00 | 2024-02-11 06:00 | Winter | FALSE | nonsummer
2024-02-11 06:00 | 2024-02-11 07:00 | Winter | FALSE | nonsummer
2024-02-11 07:00 | 2024-02-11 08:00 | Winter | FALSE | nonsummer
2024-02-11 08:00 | 2024-02-11 09:00 | Winter | FALSE | nonsummer
2024-02-11 09:00 | 2024-02-11 10:00 | Winter | FALSE | nonsummer
2024-02-11 10:00 | 2024-02-11 11:00 | Winter | FALSE | nonsummer
2024-02-11 11:00 | 2024-02-11 12:00 | Winter | FALSE | nonsummer
2024-02-11 12:00 | 2024-02-11 13:00 | Winter | FALSE | nonsummer
2024-02-11 13:00 | 2024-02-11 14:00 | Winter | FALSE | nonsummer
2024-02-11 14:00 | 2024-02-11 15:00 | Winter | FALSE | nonsummer
2024-02-11 15:00 | 2024-02-11 16:00 | Winter | FALSE | nonsummer
2024-02-11 16:00 | 2024-02-11 17:00 | Winter | TRUE | nonsummer
2024-02-11 17:00 | 2024-02-11 18:00 | Winter | TRUE | nonsummer
2024-02-11 18:00 | 2024-02-11 19:00 | Winter | TRUE | nonsummer
2024-02-11 19:00 | 2024-02-11 20:00 | Winter | TRUE | nonsummer
2024-02-11 20:00 | 2024-02-11 21:00 | Winter | TRUE | nonsummer
2024-02-11 21:00 | 2024-02-11 22:00 | Winter | FALSE | nonsummer
2024-02-11 22:00 | 2024-02-11 23:00 | Winter | FALSE | nonsummer
2024-02-11 23:00 | 2024-02-12 | Winter | FALSE | nonsummer
2024-02-12 | 2024-02-12 01:00 | Winter | FALSE | nonsummer
2024-02-12 01:00 | 2024-02-12 02:00 | Winter | FALSE | nonsummer
2024-02-12 02:00 | 2024-02-12 03:00 | Winter | FALSE | nonsummer
2024-02-12 03:00 | 2024-02-12 04:00 | Winter | FALSE | nonsummer
2024-02-12 04:00 | 2024-02-12 05:00 | Winter | FALSE | nonsummer
2024-02-12 05:00 | 2024-02-12 06:00 | Winter | FALSE | nonsummer
2024-02-12 06:00 | 2024-02-12 07:00 | Winter | FALSE | nonsummer
2024-02-12 07:00 | 2024-02-12 08:00 | Winter | FALSE | nonsummer
2024-02-12 08:00 | 2024-02-12 09:00 | Winter | FALSE | nonsummer
2024-02-12 09:00 | 2024-02-12 10:00 | Winter | FALSE | nonsummer
2024-02-12 10:00 | 2024-02-12 11:00 | Winter | FALSE | nonsummer
2024-02-12 11:00 | 2024-02-12 12:00 | Winter | FALSE | nonsummer
2024-02-12 12:00 | 2024-02-12 13:00 | Winter | FALSE | nonsummer
2024-02-12 13:00 | 2024-02-12 14:00 | Winter | FALSE | nonsummer
2024-02-12 14:00 | 2024-02-12 15:00 | Winter | FALSE | nonsummer
2024-02-12 15:00 | 2024-02-12 16:00 | Winter | FALSE | nonsummer
2024-02-12 16:00 | 2024-02-12 17:00 | Winter | TRUE | nonsummer
2024-02-12 17:00 | 2024-02-12 18:00 | Winter | TRUE | nonsummer
2024-02-12 18:00 | 2024-02-12 19:00 | Winter | TRUE | nonsummer
2024-02-12 19:00 | 2024-02-12 20:00 | Winter | TRUE | nonsummer
2024-02-12 20:00 | 2024-02-12 21:00 | Winter | TRUE | nonsummer
2024-02-12 21:00 | 2024-02-12 22:00 | Winter | FALSE | nonsummer
2024-02-12 22:00 | 2024-02-12 23:00 | Winter | FALSE | nonsummer
2024-02-12 23:00 | 2024-02-13 | Winter | FALSE | nonsummer
2024-02-13 | 2024-02-13 01:00 | Winter | FALSE | nonsummer
2024-02-13 01:00 | 2024-02-13 02:00 | Winter | FALSE | nonsummer
2024-02-13 02:00 | 2024-02-13 03:00 | Winter | FALSE | nonsummer
2024-02-13 03:00 | 2024-02-13 04:00 | Winter | FALSE | nonsummer
2024-02-13 04:00 | 2024-02-13 05:00 | Winter | FALSE | nonsummer
2024-02-13 05:00 | 2024-02-13 06:00 | Winter | FALSE | nonsummer
2024-02-13 06:00 | 2024-02-13 07:00 | Winter | FALSE | nonsummer
2024-02-13 07:00 | 2024-02-13 08:00 | Winter | FALSE | nonsummer
2024-02-13 08:00 | 2024-02-13 09:00 | Winter | FALSE | nonsummer
2024-02-13 09:00 | 2024-02-13 10:00 | Winter | FALSE | nonsummer
2024-02-13 10:00 | 2024-02-13 11:00 | Winter | FALSE | nonsummer
2024-02-13 11:00 | 2024-02-13 12:00 | Winter | FALSE | nonsummer
2024-02-13 12:00 | 2024-02-13 13:00 | Winter | FALSE | nonsummer
2024-02-13 13:00 | 2024-02-13 14:00 | Winter | FALSE | nonsummer
2024-02-13 14:00 | 2024-02-13 15:00 | Winter | FALSE | nonsummer
2024-02-13 15:00 | 2024-02-13 16:00 | Winter | FALSE | nonsummer
2024-02-13 16:00 | 2024-02-13 17:00 | Winter | TRUE | nonsummer
2024-02-13 17:00 | 2024-02-13 18:00 | Winter | TRUE | nonsummer
2024-02-13 18:00 | 2024-02-13 19:00 | Winter | TRUE | nonsummer
2024-02-13 19:00 | 2024-02-13 20:00 | Winter | TRUE | nonsummer
2024-02-13 20:00 | 2024-02-13 21:00 | Winter | TRUE | nonsummer
2024-02-13 21:00 | 2024-02-13 22:00 | Winter | FALSE | nonsummer
2024-02-13 22:00 | 2024-02-13 23:00 | Winter | FALSE | nonsummer
2024-02-13 23:00 | 2024-02-14 | Winter | FALSE | nonsummer
2024-02-14 | 2024-02-14 01:00 | Winter | FALSE | nonsummer
2024-02-14 01:00 | 2024-02-14 02:00 | Winter | FALSE | nonsummer
2024-02-14 02:00 | 2024-02-14 03:00 | Winter | FALSE | nonsummer
2024-02-14 03:00 | 2024-02-14 04:00 | Winter | FALSE | nonsummer
2024-02-14 04:00 | 2024-02-14 05:00 | Winter | FALSE | nonsummer
2024-02-14 05:00 | 2024-02-14 06:00 | Winter | FALSE | nonsummer
2024-02-14 06:00 | 2024-02-14 07:00 | Winter | FALSE | nonsummer
2024-02-14 07:00 | 2024-02-14 08:00 | Winter | FALSE | nonsummer
2024-02-14 08:00 | 2024-02-14 09:00 | Winter | FALSE | nonsummer
2024-02-14 09:00 | 2024-02-14 10:00 | Winter | FALSE | nonsummer
2024-02-14 10:00 | 2024-02-14 11:00 | Winter | FALSE | nonsummer
2024-02-14 11:00 | 2024-02-14 12:00 | Winter | FALSE | nonsummer
2024-02-14 12:00 | 2024-02-14 13:00 | Winter | FALSE | nonsummer
2024-02-14 13:00 | 2024-02-14 14:00 | Winter | FALSE | nonsummer
2024-02-14 14:00 | 2024-02-14 15:00 | Winter | FALSE | nonsummer
2024-02-14 15:00 | 2024-02-14 16:00 | Winter | FALSE | nonsummer
2024-02-14 16:00 | 2024-02-14 17:00 | Winter | TRUE | nonsummer
2024-02-14 17:00 | 2024-02-14 18:00 | Winter | TRUE | nonsummer
2024-02-14 18:00 | 2024-02-14 19:00 | Winter | TRUE | nonsummer
2024-02-14 19:00 | 2024-02-14 20:00 | Winter | TRUE | nonsummer
2024-02-14 20:00 | 2024-02-14 21:00 | Winter | TRUE | nonsummer
2024-02-14 21:00 | 2024-02-14 22:00 | Winter | FALSE | nonsummer
2024-02-14 22:00 | 2024-02-14 23:00 | Winter | FALSE | nonsummer
2024-02-14 23:00 | 2024-02-15 | Winter | FALSE | nonsummer
2024-02-15 | 2024-02-15 01:00 | Winter | FALSE | nonsummer
2024-02-15 01:00 | 2024-02-15 02:00 | Winter | FALSE | nonsummer
2024-02-15 02:00 | 2024-02-15 03:00 | Winter | FALSE | nonsummer
2024-02-15 03:00 | 2024-02-15 04:00 | Winter | FALSE | nonsummer
2024-02-15 04:00 | 2024-02-15 05:00 | Winter | FALSE | nonsummer
2024-02-15 05:00 | 2024-02-15 06:00 | Winter | FALSE | nonsummer
2024-02-15 06:00 | 2024-02-15 07:00 | Winter | FALSE | nonsummer
2024-02-15 07:00 | 2024-02-15 08:00 | Winter | FALSE | nonsummer
2024-02-15 08:00 | 2024-02-15 09:00 | Winter | FALSE | nonsummer
2024-02-15 09:00 | 2024-02-15 10:00 | Winter | FALSE | nonsummer
2024-02-15 10:00 | 2024-02-15 11:00 | Winter | FALSE | nonsummer
2024-02-15 11:00 | 2024-02-15 12:00 | Winter | FALSE | nonsummer
2024-02-15 12:00 | 2024-02-15 13:00 | Winter | FALSE | nonsummer
2024-02-15 13:00 | 2024-02-15 14:00 | Winter | FALSE | nonsummer
2024-02-15 14:00 | 2024-02-15 15:00 | Winter | FALSE | nonsummer
2024-02-15 15:00 | 2024-02-15 16:00 | Winter | FALSE | nonsummer
2024-02-15 16:00 | 2024-02-15 17:00 | Winter | TRUE | nonsummer
2024-02-15 17:00 | 2024-02-15 18:00 | Winter | TRUE | nonsummer
2024-02-15 18:00 | 2024-02-15 19:00 | Winter | TRUE | nonsummer
2024-02-15 19:00 | 2024-02-15 20:00 | Winter | TRUE | nonsummer
2024-02-15 20:00 | 2024-02-15 21:00 | Winter | TRUE | nonsummer
2024-02-15 21:00 | 2024-02-15 22:00 | Winter | FALSE | nonsummer
2024-02-15 22:00 | 2024-02-15 23:00 | Winter | FALSE | nonsummer
2024-02-15 23:00 | 2024-02-16 | Winter | FALSE | nonsummer
2024-02-16 | 2024-02-16 01:00 | Winter | FALSE | nonsummer
2024-02-16 01:00 | 2024-02-16 02:00 | Winter | FALSE | nonsummer
2024-02-16 02:00 | 2024-02-16 03:00 | Winter | FALSE | nonsummer
2024-02-16 03:00 | 2024-02-16 04:00 | Winter | FALSE | nonsummer
2024-02-16 04:00 | 2024-02-16 05:00 | Winter | FALSE | nonsummer
2024-02-16 05:00 | 2024-02-16 06:00 | Winter | FALSE | nonsummer
2024-02-16 06:00 | 2024-02-16 07:00 | Winter | FALSE | nonsummer
2024-02-16 07:00 | 2024-02-16 08:00 | Winter | FALSE | nonsummer
2024-02-16 08:00 | 2024-02-16 09:00 | Winter | FALSE | nonsummer
2024-02-16 09:00 | 2024-02-16 10:00 | Winter | FALSE | nonsummer
2024-02-16 10:00 | 2024-02-16 11:00 | Winter | FALSE | nonsummer
2024-02-16 11:00 | 2024-02-16 12:00 | Winter | FALSE | nonsummer
2024-02-16 12:00 | 2024-02-16 13:00 | Winter | FALSE | nonsummer
2024-02-16 13:00 | 2024-02-16 14:00 | Winter | FALSE | nonsummer
2024-02-16 14:00 | 2024-02-16 15:00 | Winter | FALSE | nonsummer
2024-02-16 15:00 | 2024-02-16 16:00 | Winter | FALSE | nonsummer
2024-02-16 16:00 | 2024-02-16 17:00 | Winter | TRUE | nonsummer
2024-02-16 17:00 | 2024-02-16 18:00 | Winter | TRUE | nonsummer
2024-02-16 18:00 | 2024-02-16 19:00 | Winter | TRUE | nonsummer
2024-02-16 19:00 | 2024-02-16 20:00 | Winter | TRUE | nonsummer
2024-02-16 20:00 | 2024-02-16 21:00 | Winter | TRUE | nonsummer
2024-02-16 21:00 | 2024-02-16 22:00 | Winter | FALSE | nonsummer
2024-02-16 22:00 | 2024-02-16 23:00 | Winter | FALSE | nonsummer
2024-02-16 23:00 | 2024-02-17 | Winter | FALSE | nonsummer
2024-02-17 | 2024-02-17 01:00 | Winter | FALSE | nonsummer
2024-02-17 01:00 | 2024-02-17 02:00 | Winter | FALSE | nonsummer
2024-02-17 02:00 | 2024-02-17 03:00 | Winter | FALSE | nonsummer
2024-02-17 03:00 | 2024-02-17 04:00 | Winter | FALSE | nonsummer
2024-02-17 04:00 | 2024-02-17 05:00 | Winter | FALSE | nonsummer
2024-02-17 05:00 | 2024-02-17 06:00 | Winter | FALSE | nonsummer
2024-02-17 06:00 | 2024-02-17 07:00 | Winter | FALSE | nonsummer
2024-02-17 07:00 | 2024-02-17 08:00 | Winter | FALSE | nonsummer
2024-02-17 08:00 | 2024-02-17 09:00 | Winter | FALSE | nonsummer
2024-02-17 09:00 | 2024-02-17 10:00 | Winter | FALSE | nonsummer
2024-02-17 10:00 | 2024-02-17 11:00 | Winter | FALSE | nonsummer
2024-02-17 11:00 | 2024-02-17 12:00 | Winter | FALSE | nonsummer
2024-02-17 12:00 | 2024-02-17 13:00 | Winter | FALSE | nonsummer
2024-02-17 13:00 | 2024-02-17 14:00 | Winter | FALSE | nonsummer
2024-02-17 14:00 | 2024-02-17 15:00 | Winter | FALSE | nonsummer
2024-02-17 15:00 | 2024-02-17 16:00 | Winter | FALSE | nonsummer
2024-02-17 16:00 | 2024-02-17 17:00 | Winter | TRUE | nonsummer
2024-02-17 17:00 | 2024-02-17 18:00 | Winter | TRUE | nonsummer
2024-02-17 18:00 | 2024-02-17 19:00 | Winter | TRUE | nonsummer
2024-02-17 19:00 | 2024-02-17 20:00 | Winter | TRUE | nonsummer
2024-02-17 20:00 | 2024-02-17 21:00 | Winter | TRUE | nonsummer
2024-02-17 21:00 | 2024-02-17 22:00 | Winter | FALSE | nonsummer
2024-02-17 22:00 | 2024-02-17 23:00 | Winter | FALSE | nonsummer
2024-02-17 23:00 | 2024-02-18 | Winter | FALSE | nonsummer
2024-02-18 | 2024-02-18 01:00 | Winter | FALSE | nonsummer
2024-02-18 01:00 | 2024-02-18 02:00 | Winter | FALSE | nonsummer
2024-02-18 02:00 | 2024-02-18 03:00 | Winter | FALSE | nonsummer
2024-02-18 03:00 | 2024-02-18 04:00 | Winter | FALSE | nonsummer
2024-02-18 04:00 | 2024-02-18 05:00 | Winter | FALSE | nonsummer
2024-02-18 05:00 | 2024-02-18 06:00 | Winter | FALSE | nonsummer
2024-02-18 06:00 | 2024-02-18 07:00 | Winter | FALSE | nonsummer
2024-02-18 07:00 | 2024-02-18 08:00 | Winter | FALSE | nonsummer
2024-02-18 08:00 | 2024-02-18 09:00 | Winter | FALSE | nonsummer
2024-02-18 09:00 | 2024-02-18 10:00 | Winter | FALSE | nonsummer
2024-02-18 10:00 | 2024-02-18 11:00 | Winter | FALSE | nonsummer
2024-02-18 11:00 | 2024-02-18 12:00 | Winter | FALSE | nonsummer
2024-02-18 12:00 | 2024-02-18 13:00 | Winter | FALSE | nonsummer
2024-02-18 13:00 | 2024-02-18 14:00 | Winter | FALSE | nonsummer
2024-02-18 14:00 | 2024-02-18 15:00 | Winter | FALSE | nonsummer
2024-02-18 15:00 | 2024-02-18 16:00 | Winter | FALSE | nonsummer
2024-02-18 16:00 | 2024-02-18 17:00 | Winter | TRUE | nonsummer
2024-02-18 17:00 | 2024-02-18 18:00 | Winter | TRUE | nonsummer
2024-02-18 18:00 | 2024-02-18 19:00 | Winter | TRUE | nonsummer
2024-02-18 19:00 | 2024-02-18 20:00 | Winter | TRUE | nonsummer
2024-02-18 20:00 | 2024-02-18 21:00 | Winter | TRUE | nonsummer
2024-02-18 21:00 | 2024-02-18 22:00 | Winter | FALSE | nonsummer
2024-02-18 22:00 | 2024-02-18 23:00 | Winter | FALSE | nonsummer
2024-02-18 23:00 | 2024-02-19 | Winter | FALSE | nonsummer
2024-02-19 | 2024-02-19 01:00 | Winter | FALSE | nonsummer
2024-02-19 01:00 | 2024-02-19 02:00 | Winter | FALSE | nonsummer
2024-02-19 02:00 | 2024-02-19 03:00 | Winter | FALSE | nonsummer
2024-02-19 03:00 | 2024-02-19 04:00 | Winter | FALSE | nonsummer
2024-02-19 04:00 | 2024-02-19 05:00 | Winter | FALSE | nonsummer
2024-02-19 05:00 | 2024-02-19 06:00 | Winter | FALSE | nonsummer
2024-02-19 06:00 | 2024-02-19 07:00 | Winter | FALSE | nonsummer
2024-02-19 07:00 | 2024-02-19 08:00 | Winter | FALSE | nonsummer
2024-02-19 08:00 | 2024-02-19 09:00 | Winter | FALSE | nonsummer
2024-02-19 09:00 | 2024-02-19 10:00 | Winter | FALSE | nonsummer
2024-02-19 10:00 | 2024-02-19 11:00 | Winter | FALSE | nonsummer
2024-02-19 11:00 | 2024-02-19 12:00 | Winter | FALSE | nonsummer
2024-02-19 12:00 | 2024-02-19 13:00 | Winter | FALSE | nonsummer
2024-02-19 13:00 | 2024-02-19 14:00 | Winter | FALSE | nonsummer
2024-02-19 14:00 | 2024-02-19 15:00 | Winter | FALSE | nonsummer
2024-02-19 15:00 | 2024-02-19 16:00 | Winter | FALSE | nonsummer
2024-02-19 16:00 | 2024-02-19 17:00 | Winter | TRUE | nonsummer
2024-02-19 17:00 | 2024-02-19 18:00 | Winter | TRUE | nonsummer
2024-02-19 18:00 | 2024-02-19 19:00 | Winter | TRUE | nonsummer
2024-02-19 19:00 | 2024-02-19 20:00 | Winter | TRUE | nonsummer
2024-02-19 20:00 | 2024-02-19 21:00 | Winter | TRUE | nonsummer
2024-02-19 21:00 | 2024-02-19 22:00 | Winter | FALSE | nonsummer
2024-02-19 22:00 | 2024-02-19 23:00 | Winter | FALSE | nonsummer
2024-02-19 23:00 | 2024-02-20 | Winter | FALSE | nonsummer
2024-02-20 | 2024-02-20 01:00 | Winter | FALSE | nonsummer
2024-02-20 01:00 | 2024-02-20 02:00 | Winter | FALSE | nonsummer
2024-02-20 02:00 | 2024-02-20 03:00 | Winter | FALSE | nonsummer
2024-02-20 03:00 | 2024-02-20 04:00 | Winter | FALSE | nonsummer
2024-02-20 04:00 | 2024-02-20 05:00 | Winter | FALSE | nonsummer
2024-02-20 05:00 | 2024-02-20 06:00 | Winter | FALSE | nonsummer
2024-02-20 06:00 | 2024-02-20 07:00 | Winter | FALSE | nonsummer
2024-02-20 07:00 | 2024-02-20 08:00 | Winter | FALSE | nonsummer
2024-02-20 08:00 | 2024-02-20 09:00 | Winter | FALSE | nonsummer
2024-02-20 09:00 | 2024-02-20 10:00 | Winter | FALSE | nonsummer
2024-02-20 10:00 | 2024-02-20 11:00 | Winter | FALSE | nonsummer
2024-02-20 11:00 | 2024-02-20 12:00 | Winter | FALSE | nonsummer
2024-02-20 12:00 | 2024-02-20 13:00 | Winter | FALSE | nonsummer
2024-02-20 13:00 | 2024-02-20 14:00 | Winter | FALSE | nonsummer
2024-02-20 14:00 | 2024-02-20 15:00 | Winter | FALSE | nonsummer
2024-02-20 15:00 | 2024-02-20 16:00 | Winter | FALSE | nonsummer
2024-02-20 16:00 | 2024-02-20 17:00 | Winter | TRUE | nonsummer
2024-02-20 17:00 | 2024-02-20 18:00 | Winter | TRUE | nonsummer
2024-02-20 18:00 | 2024-02-20 19:00 | Winter | TRUE | nonsummer
2024-02-20 19:00 | 2024-02-20 20:00 | Winter | TRUE | nonsummer
2024-02-20 20:00 | 2024-02-20 21:00 | Winter | TRUE | nonsummer
2024-02-20 21:00 | 2024-02-20 22:00 | Winter | FALSE | nonsummer
2024-02-20 22:00 | 2024-02-20 23:00 | Winter | FALSE | nonsummer
2024-02-20 23:00 | 2024-02-21 | Winter | FALSE | nonsummer
2024-02-21 | 2024-02-21 01:00 | Winter | FALSE | nonsummer
2024-02-21 01:00 | 2024-02-21 02:00 | Winter | FALSE | nonsummer
2024-02-21 02:00 | 2024-02-21 03:00 | Winter | FALSE | nonsummer
2024-02-21 03:00 | 2024-02-21 04:00 | Winter | FALSE | nonsummer
2024-02-21 04:00 | 2024-02-21 05:00 | Winter | FALSE | nonsummer
2024-02-21 05:00 | 2024-02-21 06:00 | Winter | FALSE | nonsummer
2024-02-21 06:00 | 2024-02-21 07:00 | Winter | FALSE | nonsummer
2024-02-21 07:00 | 2024-02-21 08:00 | Winter | FALSE | nonsummer
2024-02-21 08:00 | 2024-02-21 09:00 | Winter | FALSE | nonsummer
2024-02-21 09:00 | 2024-02-21 10:00 | Winter | FALSE | nonsummer
2024-02-21 10:00 | 2024-02-21 11:00 | Winter | FALSE | nonsummer
2024-02-21 11:00 | 2024-02-21 12:00 | Winter | FALSE | nonsummer
2024-02-21 12:00 | 2024-02-21 13:00 | Winter | FALSE | nonsummer
2024-02-21 13:00 | 2024-02-21 14:00 | Winter | FALSE | nonsummer
2024-02-21 14:00 | 2024-02-21 15:00 | Winter | FALSE | nonsummer
2024-02-21 15:00 | 2024-02-21 16:00 | Winter | FALSE | nonsummer
2024-02-21 16:00 | 2024-02-21 17:00 | Winter | TRUE | nonsummer
2024-02-21 17:00 | 2024-02-21 18:00 | Winter | TRUE | nonsummer
2024-02-21 18:00 | 2024-02-21 19:00 | Winter | TRUE | nonsummer
2024-02-21 19:00 | 2024-02-21 20:00 | Winter | TRUE | nonsummer
2024-02-21 20:00 | 2024-02-21 21:00 | Winter | TRUE | nonsummer
2024-02-21 21:00 | 2024-02-21 22:00 | Winter | FALSE | nonsummer
2024-02-21 22:00 | 2024-02-21 23:00 | Winter | FALSE | nonsummer
2024-02-21 23:00 | 2024-02-22 | Winter | FALSE | nonsummer
2024-02-22 | 2024-02-22 01:00 | Winter | FALSE | nonsummer
2024-02-22 01:00 | 2024-02-22 02:00 | Winter | FALSE | nonsummer
2024-02-22 02:00 | 2024-02-22 03:00 | Winter | FALSE | nonsummer
2024-02-22 03:00 | 2024-02-22 04:00 | Winter | FALSE | nonsummer
2024-02-22 04:00 | 2024-02-22 05:00 | Winter | FALSE | nonsummer
2024-02-22 05:00 | 2024-02-22 06:00 | Winter | FALSE | nonsummer
2024-02-22 06:00 | 2024-02-22 07:00 | Winter | FALSE | nonsummer
2024-02-22 07:00 | 2024-02-22 08:00 | Winter | FALSE | nonsummer
2024-02-22 08:00 | 2024-02-22 09:00 | Winter | FALSE | nonsummer
2024-02-22 09:00 | 2024-02-22 10:00 | Winter | FALSE | nonsummer
2024-02-22 10:00 | 2024-02-22 11:00 | Winter | FALSE | nonsummer
2024-02-22 11:00 | 2024-02-22 12:00 | Winter | FALSE | nonsummer
2024-02-22 12:00 | 2024-02-22 13:00 | Winter | FALSE | nonsummer
2024-02-22 13:00 | 2024-02-22 14:00 | Winter | FALSE | nonsummer
2024-02-22 14:00 | 2024-02-22 15:00 | Winter | FALSE | nonsummer
2024-02-22 15:00 | 2024-02-22 16:00 | Winter | FALSE | nonsummer
2024-02-22 16:00 | 2024-02-22 17:00 | Winter | TRUE | nonsummer
2024-02-22 17:00 | 2024-02-22 18:00 | Winter | TRUE | nonsummer
2024-02-22 18:00 | 2024-02-22 19:00 | Winter | TRUE | nonsummer
2024-02-22 19:00 | 2024-02-22 20:00 | Winter | TRUE | nonsummer
2024-02-22 20:00 | 2024-02-22 21:00 | Winter | TRUE | nonsummer
2024-02-22 21:00 | 2024-02-22 22:00 | Winter | FALSE | nonsummer
2024-02-22 22:00 | 2024-02-22 23:00 | Winter | FALSE | nonsummer
2024-02-22 23:00 | 2024-02-23 | Winter | FALSE | nonsummer
2024-02-23 | 2024-02-23 01:00 | Winter | FALSE | nonsummer
2024-02-23 01:00 | 2024-02-23 02:00 | Winter | FALSE | nonsummer
2024-02-23 02:00 | 2024-02-23 03:00 | Winter | FALSE | nonsummer
2024-02-23 03:00 | 2024-02-23 04:00 | Winter | FALSE | nonsummer
2024-02-23 04:00 | 2024-02-23 05:00 | Winter | FALSE | nonsummer
2024-02-23 05:00 | 2024-02-23 06:00 | Winter | FALSE | nonsummer
2024-02-23 06:00 | 2024-02-23 07:00 | Winter | FALSE | nonsummer
2024-02-23 07:00 | 2024-02-23 08:00 | Winter | FALSE | nonsummer
2024-02-23 08:00 | 2024-02-23 09:00 | Winter | FALSE | nonsummer
2024-02-23 09:00 | 2024-02-23 10:00 | Winter | FALSE | nonsummer
2024-02-23 10:00 | 2024-02-23 11:00 | Winter | FALSE | nonsummer
2024-02-23 11:00 | 2024-02-23 12:00 | Winter | FALSE | nonsummer
2024-02-23 12:00 | 2024-02-23 13:00 | Winter | FALSE | nonsummer
2024-02-23 13:00 | 2024-02-23 14:00 | Winter | FALSE | nonsummer
2024-02-23 14:00 | 2024-02-23 15:00 | Winter | FALSE | nonsummer
2024-02-23 15:00 | 2024-02-23 16:00 | Winter | FALSE | nonsummer
2024-02-23 16:00 | 2024-02-23 17:00 | Winter | TRUE | nonsummer
2024-02-23 17:00 | 2024-02-23 18:00 | Winter | TRUE | nonsummer
2024-02-23 18:00 | 2024-02-23 19:00 | Winter | TRUE | nonsummer
2024-02-23 19:00 | 2024-02-23 20:00 | Winter | TRUE | nonsummer
2024-02-23 20:00 | 2024-02-23 21:00 | Winter | TRUE | nonsummer
2024-02-23 21:00 | 2024-02-23 22:00 | Winter | FALSE | nonsummer
2024-02-23 22:00 | 2024-02-23 23:00 | Winter | FALSE | nonsummer
2024-02-23 23:00 | 2024-02-24 | Winter | FALSE | nonsummer
2024-02-24 | 2024-02-24 01:00 | Winter | FALSE | nonsummer
2024-02-24 01:00 | 2024-02-24 02:00 | Winter | FALSE | nonsummer
2024-02-24 02:00 | 2024-02-24 03:00 | Winter | FALSE | nonsummer
2024-02-24 03:00 | 2024-02-24 04:00 | Winter | FALSE | nonsummer
2024-02-24 04:00 | 2024-02-24 05:00 | Winter | FALSE | nonsummer
2024-02-24 05:00 | 2024-02-24 06:00 | Winter | FALSE | nonsummer
2024-02-24 06:00 | 2024-02-24 07:00 | Winter | FALSE | nonsummer
2024-02-24 07:00 | 2024-02-24 08:00 | Winter | FALSE | nonsummer
2024-02-24 08:00 | 2024-02-24 09:00 | Winter | FALSE | nonsummer
2024-02-24 09:00 | 2024-02-24 10:00 | Winter | FALSE | nonsummer
2024-02-24 10:00 | 2024-02-24 11:00 | Winter | FALSE | nonsummer
2024-02-24 11:00 | 2024-02-24 12:00 | Winter | FALSE | nonsummer
2024-02-24 12:00 | 2024-02-24 13:00 | Winter | FALSE | nonsummer
2024-02-24 13:00 | 2024-02-24 14:00 | Winter | FALSE | nonsummer
2024-02-24 14:00 | 2024-02-24 15:00 | Winter | FALSE | nonsummer
2024-02-24 15:00 | 2024-02-24 16:00 | Winter | FALSE | nonsummer
2024-02-24 16:00 | 2024-02-24 17:00 | Winter | TRUE | nonsummer
2024-02-24 17:00 | 2024-02-24 18:00 | Winter | TRUE | nonsummer
2024-02-24 18:00 | 2024-02-24 19:00 | Winter | TRUE | nonsummer
2024-02-24 19:00 | 2024-02-24 20:00 | Winter | TRUE | nonsummer
2024-02-24 20:00 | 2024-02-24 21:00 | Winter | TRUE | nonsummer
2024-02-24 21:00 | 2024-02-24 22:00 | Winter | FALSE | nonsummer
2024-02-24 22:00 | 2024-02-24 23:00 | Winter | FALSE | nonsummer
2024-02-24 23:00 | 2024-02-25 | Winter | FALSE | nonsummer
2024-02-25 | 2024-02-25 01:00 | Winter | FALSE | nonsummer
2024-02-25 01:00 | 2024-02-25 02:00 | Winter | FALSE | nonsummer
2024-02-25 02:00 | 2024-02-25 03:00 | Winter | FALSE | nonsummer
2024-02-25 03:00 | 2024-02-25 04:00 | Winter | FALSE | nonsummer
2024-02-25 04:00 | 2024-02-25 05:00 | Winter | FALSE | nonsummer
2024-02-25 05:00 | 2024-02-25 06:00 | Winter | FALSE | nonsummer
2024-02-25 06:00 | 2024-02-25 07:00 | Winter | FALSE | nonsummer
2024-02-25 07:00 | 2024-02-25 08:00 | Winter | FALSE | nonsummer
2024-02-25 08:00 | 2024-02-25 09:00 | Winter | FALSE | nonsummer
2024-02-25 09:00 | 2024-02-25 10:00 | Winter | FALSE | nonsummer
2024-02-25 10:00 | 2024-02-25 11:00 | Winter | FALSE | nonsummer
2024-02-25 11:00 | 2024-02-25 12:00 | Winter | FALSE | nonsummer
2024-02-25 12:00 | 2024-02-25 13:00 | Winter | FALSE | nonsummer
2024-02-25 13:00 | 2024-02-25 14:00 | Winter | FALSE | nonsummer
2024-02-25 14:00 | 2024-02-25 15:00 | Winter | FALSE | nonsummer
2024-02-25 15:00 | 2024-02-25 16:00 | Winter | FALSE | nonsummer
2024-02-25 16:00 | 2024-02-25 17:00 | Winter | TRUE | nonsummer
2024-02-25 17:00 | 2024-02-25 18:00 | Winter | TRUE | nonsummer
2024-02-25 18:00 | 2024-02-25 19:00 | Winter | TRUE | nonsummer
2024-02-25 19:00 | 2024-02-25 20:00 | Winter | TRUE | nonsummer
2024-02-25 20:00 | 2024-02-25 21:00 | Winter | TRUE | nonsummer
2024-02-25 21:00 | 2024-02-25 22:00 | Winter | FALSE | nonsummer
2024-02-25 22:00 | 2024-02-25 23:00 | Winter | FALSE | nonsummer
2024-02-25 23:00 | 2024-02-26 | Winter | FALSE | nonsummer
2024-02-26 | 2024-02-26 01:00 | Winter | FALSE | nonsummer
2024-02-26 01:00 | 2024-02-26 02:00 | Winter | FALSE | nonsummer
2024-02-26 02:00 | 2024-02-26 03:00 | Winter | FALSE | nonsummer
2024-02-26 03:00 | 2024-02-26 04:00 | Winter | FALSE | nonsummer
2024-02-26 04:00 | 2024-02-26 05:00 | Winter | FALSE | nonsummer
2024-02-26 05:00 | 2024-02-26 06:00 | Winter | FALSE | nonsummer
2024-02-26 06:00 | 2024-02-26 07:00 | Winter | FALSE | nonsummer
2024-02-26 07:00 | 2024-02-26 08:00 | Winter | FALSE | nonsummer
2024-02-26 08:00 | 2024-02-26 09:00 | Winter | FALSE | nonsummer
2024-02-26 09:00 | 2024-02-26 10:00 | Winter | FALSE | nonsummer
2024-02-26 10:00 | 2024-02-26 11:00 | Winter | FALSE | nonsummer
2024-02-26 11:00 | 2024-02-26 12:00 | Winter | FALSE | nonsummer
2024-02-26 12:00 | 2024-02-26 13:00 | Winter | FALSE | nonsummer
2024-02-26 13:00 | 2024-02-26 14:00 | Winter | FALSE | nonsummer
2024-02-26 14:00 | 2024-02-26 15:00 | Winter | FALSE | nonsummer
2024-02-26 15:00 | 2024-02-26 16:00 | Winter | FALSE | nonsummer
2024-02-26 16:00 | 2024-02-26 17:00 | Winter | TRUE | nonsummer
2024-02-26 17:00 | 2024-02-26 18:00 | Winter | TRUE | nonsummer
2024-02-26 18:00 | 2024-02-26 19:00 | Winter | TRUE | nonsummer
2024-02-26 19:00 | 2024-02-26 20:00 | Winter | TRUE | nonsummer
2024-02-26 20:00 | 2024-02-26 21:00 | Winter | TRUE | nonsummer
2024-02-26 21:00 | 2024-02-26 22:00 | Winter | FALSE | nonsummer
2024-02-26 22:00 | 2024-02-26 23:00 | Winter | FALSE | nonsummer
2024-02-26 23:00 | 2024-02-27 | Winter | FALSE | nonsummer
2024-02-27 | 2024-02-27 01:00 | Winter | FALSE | nonsummer
2024-02-27 01:00 | 2024-02-27 02:00 | Winter | FALSE | nonsummer
2024-02-27 02:00 | 2024-02-27 03:00 | Winter | FALSE | nonsummer
2024-02-27 03:00 | 2024-02-27 04:00 | Winter | FALSE | nonsummer
2024-02-27 04:00 | 2024-02-27 05:00 | Winter | FALSE | nonsummer
2024-02-27 05:00 | 2024-02-27 06:00 | Winter | FALSE | nonsummer
2024-02-27 06:00 | 2024-02-27 07:00 | Winter | FALSE | nonsummer
2024-02-27 07:00 | 2024-02-27 08:00 | Winter | FALSE | nonsummer
2024-02-27 08:00 | 2024-02-27 09:00 | Winter | FALSE | nonsummer
2024-02-27 09:00 | 2024-02-27 10:00 | Winter | FALSE | nonsummer
2024-02-27 10:00 | 2024-02-27 11:00 | Winter | FALSE | nonsummer
2024-02-27 11:00 | 2024-02-27 12:00 | Winter | FALSE | nonsummer
2024-02-27 12:00 | 2024-02-27 13:00 | Winter | FALSE | nonsummer
2024-02-27 13:00 | 2024-02-27 14:00 | Winter | FALSE | nonsummer
2024-02-27 14:00 | 2024-02-27 15:00 | Winter | FALSE | nonsummer
2024-02-27 15:00 | 2024-02-27 16:00 | Winter | FALSE | nonsummer
2024-02-27 16:00 | 2024-02-27 17:00 | Winter | TRUE | nonsummer
2024-02-27 17:00 | 2024-02-27 18:00 | Winter | TRUE | nonsummer
2024-02-27 18:00 | 2024-02-27 19:00 | Winter | TRUE | nonsummer
2024-02-27 19:00 | 2024-02-27 20:00 | Winter | TRUE | nonsummer
2024-02-27 20:00 | 2024-02-27 21:00 | Winter | TRUE | nonsummer
2024-02-27 21:00 | 2024-02-27 22:00 | Winter | FALSE | nonsummer
2024-02-27 22:00 | 2024-02-27 23:00 | Winter | FALSE | nonsummer
2024-02-27 23:00 | 2024-02-28 | Winter | FALSE | nonsummer
2024-02-28 | 2024-02-28 01:00 | Winter | FALSE | nonsummer
2024-02-28 01:00 | 2024-02-28 02:00 | Winter | FALSE | nonsummer
2024-02-28 02:00 | 2024-02-28 03:00 | Winter | FALSE | nonsummer
2024-02-28 03:00 | 2024-02-28 04:00 | Winter | FALSE | nonsummer
2024-02-28 04:00 | 2024-02-28 05:00 | Winter | FALSE | nonsummer
2024-02-28 05:00 | 2024-02-28 06:00 | Winter | FALSE | nonsummer
2024-02-28 06:00 | 2024-02-28 07:00 | Winter | FALSE | nonsummer
2024-02-28 07:00 | 2024-02-28 08:00 | Winter | FALSE | nonsummer
2024-02-28 08:00 | 2024-02-28 09:00 | Winter | FALSE | nonsummer
2024-02-28 09:00 | 2024-02-28 10:00 | Winter | FALSE | nonsummer
2024-02-28 10:00 | 2024-02-28 11:00 | Winter | FALSE | nonsummer
2024-02-28 11:00 | 2024-02-28 12:00 | Winter | FALSE | nonsummer
2024-02-28 12:00 | 2024-02-28 13:00 | Winter | FALSE | nonsummer
2024-02-28 13:00 | 2024-02-28 14:00 | Winter | FALSE | nonsummer
2024-02-28 14:00 | 2024-02-28 15:00 | Winter | FALSE | nonsummer
2024-02-28 15:00 | 2024-02-28 16:00 | Winter | FALSE | nonsummer
2024-02-28 16:00 | 2024-02-28 17:00 | Winter | TRUE | nonsummer
2024-02-28 17:00 | 2024-02-28 18:00 | Winter | TRUE | nonsummer
2024-02-28 18:00 | 2024-02-28 19:00 | Winter | TRUE | nonsummer
2024-02-28 19:00 | 2024-02-28 20:00 | Winter | TRUE | nonsummer
2024-02-28 20:00 | 2024-02-28 21:00 | Winter | TRUE | nonsummer
2024-02-28 21:00 | 2024-02-28 22:00 | Winter | FALSE | nonsummer
2024-02-28 22:00 | 2024-02-28 23:00 | Winter | FALSE | nonsummer
2024-02-28 23:00 | 2024-02-29 | Winter | FALSE | nonsummer
2024-02-29 | 2024-02-29 01:00 | Winter | FALSE | nonsummer
2024-02-29 01:00 | 2024-02-29 02:00 | Winter | FALSE | nonsummer
2024-02-29 02:00 | 2024-02-29 03:00 | Winter | FALSE | nonsummer
2024-02-29 03:00 | 2024-02-29 04:00 | Winter | FALSE | nonsummer
2024-02-29 04:00 | 2024-02-29 05:00 | Winter | FALSE | nonsummer
2024-02-29 05:00 | 2024-02-29 06:00 | Winter | FALSE | nonsummer
2024-02-29 06:00 | 2024-02-29 07:00 | Winter | FALSE | nonsummer
2024-02-29 07:00 | 2024-02-29 08:00 | Winter | FALSE | nonsummer
2024-02-29 08:00 | 2024-02-29 09:00 | Winter | FALSE | nonsummer
2024-02-29 09:00 | 2024-02-29 10:00 | Winter | FALSE | nonsummer
2024-02-29 10:00 | 2024-02-29 11:00 | Winter | FALSE | nonsummer
2024-02-29 11:00 | 2024-02-29 12:00 | Winter | FALSE | nonsummer
2024-02-29 12:00 | 2024-02-29 13:00 | Winter | FALSE | nonsummer
2024-02-29 13:00 | 2024-02-29 14:00 | Winter | FALSE | nonsummer
2024-02-29 14:00 | 2024-02-29 15:00 | Winter | FALSE | nonsummer
2024-02-29 15:00 | 2024-02-29 16:00 | Winter | FALSE | nonsummer
2024-02-29 16:00 | 2024-02-29 17:00 | Winter | TRUE | nonsummer
2024-02-29 17:00 | 2024-02-29 18:00 | Winter | TRUE | nonsummer
2024-02-29 18:00 | 2024-02-29 19:00 | Winter | TRUE | nonsummer
2024-02-29 19:00 | 2024-02-29 20:00 | Winter | TRUE | nonsummer
2024-02-29 20:00 | 2024-02-29 21:00 | Winter | TRUE | nonsummer
2024-02-29 21:00 | 2024-02-29 22:00 | Winter | FALSE | nonsummer
2024-02-29 22:00 | 2024-02-29 23:00 | Winter | FALSE | nonsummer
2024-02-29 23:00 | 2024-03-01 | Winter | FALSE | nonsummer
2024-03-01 | 2024-03-01 01:00 | Spring | FALSE | nonsummer
2024-03-01 01:00 | 2024-03-01 02:00 | Spring | FALSE | nonsummer
2024-03-01 02:00 | 2024-03-01 03:00 | Spring | FALSE | nonsummer
2024-03-01 03:00 | 2024-03-01 04:00 | Spring | FALSE | nonsummer
2024-03-01 04:00 | 2024-03-01 05:00 | Spring | FALSE | nonsummer
2024-03-01 05:00 | 2024-03-01 06:00 | Spring | FALSE | nonsummer
2024-03-01 06:00 | 2024-03-01 07:00 | Spring | FALSE | nonsummer
2024-03-01 07:00 | 2024-03-01 08:00 | Spring | FALSE | nonsummer
2024-03-01 08:00 | 2024-03-01 09:00 | Spring | FALSE | nonsummer
2024-03-01 09:00 | 2024-03-01 10:00 | Spring | FALSE | nonsummer
2024-03-01 10:00 | 2024-03-01 11:00 | Spring | FALSE | nonsummer
2024-03-01 11:00 | 2024-03-01 12:00 | Spring | FALSE | nonsummer
2024-03-01 12:00 | 2024-03-01 13:00 | Spring | FALSE | nonsummer
2024-03-01 13:00 | 2024-03-01 14:00 | Spring | FALSE | nonsummer
2024-03-01 14:00 | 2024-03-01 15:00 | Spring | FALSE | nonsummer
2024-03-01 15:00 | 2024-03-01 16:00 | Spring | FALSE | nonsummer
2024-03-01 16:00 | 2024-03-01 17:00 | Spring | FALSE | nonsummer
2024-03-01 17:00 | 2024-03-01 18:00 | Spring | TRUE | nonsummer
2024-03-01 18:00 | 2024-03-01 19:00 | Spring | TRUE | nonsummer
2024-03-01 19:00 | 2024-03-01 20:00 | Spring | TRUE | nonsummer
2024-03-01 20:00 | 2024-03-01 21:00 | Spring | TRUE | nonsummer
2024-03-01 21:00 | 2024-03-01 22:00 | Spring | TRUE | nonsummer
2024-03-01 22:00 | 2024-03-01 23:00 | Spring | FALSE | nonsummer
2024-03-01 23:00 | 2024-03-02 | Spring | FALSE | nonsummer
2024-03-02 | 2024-03-02 01:00 | Spring | FALSE | nonsummer
2024-03-02 01:00 | 2024-03-02 02:00 | Spring | FALSE | nonsummer
2024-03-02 02:00 | 2024-03-02 03:00 | Spring | FALSE | nonsummer
2024-03-02 03:00 | 2024-03-02 04:00 | Spring | FALSE | nonsummer
2024-03-02 04:00 | 2024-03-02 05:00 | Spring | FALSE | nonsummer
2024-03-02 05:00 | 2024-03-02 06:00 | Spring | FALSE | nonsummer
2024-03-02 06:00 | 2024-03-02 07:00 | Spring | FALSE | nonsummer
2024-03-02 07:00 | 2024-03-02 08:00 | Spring | FALSE | nonsummer
2024-03-02 08:00 | 2024-03-02 09:00 | Spring | FALSE | nonsummer
2024-03-02 09:00 | 2024-03-02 10:00 | Spring | FALSE | nonsummer
2024-03-02 10:00 | 2024-03-02 11:00 | Spring | FALSE | nonsummer
2024-03-02 11:00 | 2024-03-02 12:00 | Spring | FALSE | nonsummer
2024-03-02 12:00 | 2024-03-02 13:00 | Spring | FALSE | nonsummer
2024-03-02 13:00 | 2024-03-02 14:00 | Spring | FALSE | nonsummer
2024-03-02 14:00 | 2024-03-02 15:00 | Spring | FALSE | nonsummer
2024-03-02 15:00 | 2024-03-02 16:00 | Spring | FALSE | nonsummer
2024-03-02 16:00 | 2024-03-02 17:00 | Spring | FALSE | nonsummer
2024-03-02 17:00 | 2024-03-02 18:00 | Spring | TRUE | nonsummer
2024-03-02 18:00 | 2024-03-02 19:00 | Spring | TRUE | nonsummer
2024-03-02 19:00 | 2024-03-02 20:00 | Spring | TRUE | nonsummer
2024-03-02 20:00 | 2024-03-02 21:00 | Spring | TRUE | nonsummer
2024-03-02 21:00 | 2024-03-02 22:00 | Spring | TRUE | nonsummer
2024-03-02 22:00 | 2024-03-02 23:00 | Spring | FALSE | nonsummer
2024-03-02 23:00 | 2024-03-03 | Spring | FALSE | nonsummer
2024-03-03 | 2024-03-03 01:00 | Spring | FALSE | nonsummer
2024-03-03 01:00 | 2024-03-03 02:00 | Spring | FALSE | nonsummer
2024-03-03 02:00 | 2024-03-03 03:00 | Spring | FALSE | nonsummer
2024-03-03 03:00 | 2024-03-03 04:00 | Spring | FALSE | nonsummer
2024-03-03 04:00 | 2024-03-03 05:00 | Spring | FALSE | nonsummer
2024-03-03 05:00 | 2024-03-03 06:00 | Spring | FALSE | nonsummer
2024-03-03 06:00 | 2024-03-03 07:00 | Spring | FALSE | nonsummer
2024-03-03 07:00 | 2024-03-03 08:00 | Spring | FALSE | nonsummer
2024-03-03 08:00 | 2024-03-03 09:00 | Spring | FALSE | nonsummer
2024-03-03 09:00 | 2024-03-03 10:00 | Spring | FALSE | nonsummer
2024-03-03 10:00 | 2024-03-03 11:00 | Spring | FALSE | nonsummer
2024-03-03 11:00 | 2024-03-03 12:00 | Spring | FALSE | nonsummer
2024-03-03 12:00 | 2024-03-03 13:00 | Spring | FALSE | nonsummer
2024-03-03 13:00 | 2024-03-03 14:00 | Spring | FALSE | nonsummer
2024-03-03 14:00 | 2024-03-03 15:00 | Spring | FALSE | nonsummer
2024-03-03 15:00 | 2024-03-03 16:00 | Spring | FALSE | nonsummer
2024-03-03 16:00 | 2024-03-03 17:00 | Spring | FALSE | nonsummer
2024-03-03 17:00 | 2024-03-03 18:00 | Spring | TRUE | nonsummer
2024-03-03 18:00 | 2024-03-03 19:00 | Spring | TRUE | nonsummer
2024-03-03 19:00 | 2024-03-03 20:00 | Spring | TRUE | nonsummer
2024-03-03 20:00 | 2024-03-03 21:00 | Spring | TRUE | nonsummer
2024-03-03 21:00 | 2024-03-03 22:00 | Spring | TRUE | nonsummer
2024-03-03 22:00 | 2024-03-03 23:00 | Spring | FALSE | nonsummer
2024-03-03 23:00 | 2024-03-04 | Spring | FALSE | nonsummer
2024-03-04 | 2024-03-04 01:00 | Spring | FALSE | nonsummer
2024-03-04 01:00 | 2024-03-04 02:00 | Spring | FALSE | nonsummer
2024-03-04 02:00 | 2024-03-04 03:00 | Spring | FALSE | nonsummer
2024-03-04 03:00 | 2024-03-04 04:00 | Spring | FALSE | nonsummer
2024-03-04 04:00 | 2024-03-04 05:00 | Spring | FALSE | nonsummer
2024-03-04 05:00 | 2024-03-04 06:00 | Spring | FALSE | nonsummer
2024-03-04 06:00 | 2024-03-04 07:00 | Spring | FALSE | nonsummer
2024-03-04 07:00 | 2024-03-04 08:00 | Spring | FALSE | nonsummer
2024-03-04 08:00 | 2024-03-04 09:00 | Spring | FALSE | nonsummer
2024-03-04 09:00 | 2024-03-04 10:00 | Spring | FALSE | nonsummer
2024-03-04 10:00 | 2024-03-04 11:00 | Spring | FALSE | nonsummer
2024-03-04 11:00 | 2024-03-04 12:00 | Spring | FALSE | nonsummer
2024-03-04 12:00 | 2024-03-04 13:00 | Spring | FALSE | nonsummer
2024-03-04 13:00 | 2024-03-04 14:00 | Spring | FALSE | nonsummer
2024-03-04 14:00 | 2024-03-04 15:00 | Spring | FALSE | nonsummer
2024-03-04 15:00 | 2024-03-04 16:00 | Spring | FALSE | nonsummer
2024-03-04 16:00 | 2024-03-04 17:00 | Spring | FALSE | nonsummer
2024-03-04 17:00 | 2024-03-04 18:00 | Spring | TRUE | nonsummer
2024-03-04 18:00 | 2024-03-04 19:00 | Spring | TRUE | nonsummer
2024-03-04 19:00 | 2024-03-04 20:00 | Spring | TRUE | nonsummer
2024-03-04 20:00 | 2024-03-04 21:00 | Spring | TRUE | nonsummer
2024-03-04 21:00 | 2024-03-04 22:00 | Spring | TRUE | nonsummer
2024-03-04 22:00 | 2024-03-04 23:00 | Spring | FALSE | nonsummer
2024-03-04 23:00 | 2024-03-05 | Spring | FALSE | nonsummer
2024-03-05 | 2024-03-05 01:00 | Spring | FALSE | nonsummer
2024-03-05 01:00 | 2024-03-05 02:00 | Spring | FALSE | nonsummer
2024-03-05 02:00 | 2024-03-05 03:00 | Spring | FALSE | nonsummer
2024-03-05 03:00 | 2024-03-05 04:00 | Spring | FALSE | nonsummer
2024-03-05 04:00 | 2024-03-05 05:00 | Spring | FALSE | nonsummer
2024-03-05 05:00 | 2024-03-05 06:00 | Spring | FALSE | nonsummer
2024-03-05 06:00 | 2024-03-05 07:00 | Spring | FALSE | nonsummer
2024-03-05 07:00 | 2024-03-05 08:00 | Spring | FALSE | nonsummer
2024-03-05 08:00 | 2024-03-05 09:00 | Spring | FALSE | nonsummer
2024-03-05 09:00 | 2024-03-05 10:00 | Spring | FALSE | nonsummer
2024-03-05 10:00 | 2024-03-05 11:00 | Spring | FALSE | nonsummer
2024-03-05 11:00 | 2024-03-05 12:00 | Spring | FALSE | nonsummer
2024-03-05 12:00 | 2024-03-05 13:00 | Spring | FALSE | nonsummer
2024-03-05 13:00 | 2024-03-05 14:00 | Spring | FALSE | nonsummer
2024-03-05 14:00 | 2024-03-05 15:00 | Spring | FALSE | nonsummer
2024-03-05 15:00 | 2024-03-05 16:00 | Spring | FALSE | nonsummer
2024-03-05 16:00 | 2024-03-05 17:00 | Spring | FALSE | nonsummer
2024-03-05 17:00 | 2024-03-05 18:00 | Spring | TRUE | nonsummer
2024-03-05 18:00 | 2024-03-05 19:00 | Spring | TRUE | nonsummer
2024-03-05 19:00 | 2024-03-05 20:00 | Spring | TRUE | nonsummer
2024-03-05 20:00 | 2024-03-05 21:00 | Spring | TRUE | nonsummer
2024-03-05 21:00 | 2024-03-05 22:00 | Spring | TRUE | nonsummer
2024-03-05 22:00 | 2024-03-05 23:00 | Spring | FALSE | nonsummer
2024-03-05 23:00 | 2024-03-06 | Spring | FALSE | nonsummer
2024-03-06 | 2024-03-06 01:00 | Spring | FALSE | nonsummer
2024-03-06 01:00 | 2024-03-06 02:00 | Spring | FALSE | nonsummer
2024-03-06 02:00 | 2024-03-06 03:00 | Spring | FALSE | nonsummer
2024-03-06 03:00 | 2024-03-06 04:00 | Spring | FALSE | nonsummer
2024-03-06 04:00 | 2024-03-06 05:00 | Spring | FALSE | nonsummer
2024-03-06 05:00 | 2024-03-06 06:00 | Spring | FALSE | nonsummer
2024-03-06 06:00 | 2024-03-06 07:00 | Spring | FALSE | nonsummer
2024-03-06 07:00 | 2024-03-06 08:00 | Spring | FALSE | nonsummer
2024-03-06 08:00 | 2024-03-06 09:00 | Spring | FALSE | nonsummer
2024-03-06 09:00 | 2024-03-06 10:00 | Spring | FALSE | nonsummer
2024-03-06 10:00 | 2024-03-06 11:00 | Spring | FALSE | nonsummer
2024-03-06 11:00 | 2024-03-06 12:00 | Spring | FALSE | nonsummer
2024-03-06 12:00 | 2024-03-06 13:00 | Spring | FALSE | nonsummer
2024-03-06 13:00 | 2024-03-06 14:00 | Spring | FALSE | nonsummer
2024-03-06 14:00 | 2024-03-06 15:00 | Spring | FALSE | nonsummer
2024-03-06 15:00 | 2024-03-06 16:00 | Spring | FALSE | nonsummer
2024-03-06 16:00 | 2024-03-06 17:00 | Spring | FALSE | nonsummer
2024-03-06 17:00 | 2024-03-06 18:00 | Spring | TRUE | nonsummer
2024-03-06 18:00 | 2024-03-06 19:00 | Spring | TRUE | nonsummer
2024-03-06 19:00 | 2024-03-06 20:00 | Spring | TRUE | nonsummer
2024-03-06 20:00 | 2024-03-06 21:00 | Spring | TRUE | nonsummer
2024-03-06 21:00 | 2024-03-06 22:00 | Spring | TRUE | nonsummer
2024-03-06 22:00 | 2024-03-06 23:00 | Spring | FALSE | nonsummer
2024-03-06 23:00 | 2024-03-07 | Spring | FALSE | nonsummer
2024-03-07 | 2024-03-07 01:00 | Spring | FALSE | nonsummer
2024-03-07 01:00 | 2024-03-07 02:00 | Spring | FALSE | nonsummer
2024-03-07 02:00 | 2024-03-07 03:00 | Spring | FALSE | nonsummer
2024-03-07 03:00 | 2024-03-07 04:00 | Spring | FALSE | nonsummer
2024-03-07 04:00 | 2024-03-07 05:00 | Spring | FALSE | nonsummer
2024-03-07 05:00 | 2024-03-07 06:00 | Spring | FALSE | nonsummer
2024-03-07 06:00 | 2024-03-07 07:00 | Spring | FALSE | nonsummer
2024-03-07 07:00 | 2024-03-07 08:00 | Spring | FALSE | nonsummer
2024-03-07 08:00 | 2024-03-07 09:00 | Spring | FALSE | nonsummer
2024-03-07 09:00 | 2024-03-07 10:00 | Spring | FALSE | nonsummer
2024-03-07 10:00 | 2024-03-07 11:00 | Spring | FALSE | nonsummer
2024-03-07 11:00 | 2024-03-07 12:00 | Spring | FALSE | nonsummer
2024-03-07 12:00 | 2024-03-07 13:00 | Spring | FALSE | nonsummer
2024-03-07 13:00 | 2024-03-07 14:00 | Spring | FALSE | nonsummer
2024-03-07 14:00 | 2024-03-07 15:00 | Spring | FALSE | nonsummer
2024-03-07 15:00 | 2024-03-07 16:00 | Spring | FALSE | nonsummer
2024-03-07 16:00 | 2024-03-07 17:00 | Spring | FALSE | nonsummer
2024-03-07 17:00 | 2024-03-07 18:00 | Spring | TRUE | nonsummer
2024-03-07 18:00 | 2024-03-07 19:00 | Spring | TRUE | nonsummer
2024-03-07 19:00 | 2024-03-07 20:00 | Spring | TRUE | nonsummer
2024-03-07 20:00 | 2024-03-07 21:00 | Spring | TRUE | nonsummer
2024-03-07 21:00 | 2024-03-07 22:00 | Spring | TRUE | nonsummer
2024-03-07 22:00 | 2024-03-07 23:00 | Spring | FALSE | nonsummer
2024-03-07 23:00 | 2024-03-08 | Spring | FALSE | nonsummer
2024-03-08 | 2024-03-08 01:00 | Spring | FALSE | nonsummer
2024-03-08 01:00 | 2024-03-08 02:00 | Spring | FALSE | nonsummer
2024-03-08 02:00 | 2024-03-08 03:00 | Spring | FALSE | nonsummer
2024-03-08 03:00 | 2024-03-08 04:00 | Spring | FALSE | nonsummer
2024-03-08 04:00 | 2024-03-08 05:00 | Spring | FALSE | nonsummer
2024-03-08 05:00 | 2024-03-08 06:00 | Spring | FALSE | nonsummer
2024-03-08 06:00 | 2024-03-08 07:00 | Spring | FALSE | nonsummer
2024-03-08 07:00 | 2024-03-08 08:00 | Spring | FALSE | nonsummer
2024-03-08 08:00 | 2024-03-08 09:00 | Spring | FALSE | nonsummer
2024-03-08 09:00 | 2024-03-08 10:00 | Spring | FALSE | nonsummer
2024-03-08 10:00 | 2024-03-08 11:00 | Spring | FALSE | nonsummer
2024-03-08 11:00 | 2024-03-08 12:00 | Spring | FALSE | nonsummer
2024-03-08 12:00 | 2024-03-08 13:00 | Spring | FALSE | nonsummer
2024-03-08 13:00 | 2024-03-08 14:00 | Spring | FALSE | nonsummer
2024-03-08 14:00 | 2024-03-08 15:00 | Spring | FALSE | nonsummer
2024-03-08 15:00 | 2024-03-08 16:00 | Spring | FALSE | nonsummer
2024-03-08 16:00 | 2024-03-08 17:00 | Spring | FALSE | nonsummer
2024-03-08 17:00 | 2024-03-08 18:00 | Spring | TRUE | nonsummer
2024-03-08 18:00 | 2024-03-08 19:00 | Spring | TRUE | nonsummer
2024-03-08 19:00 | 2024-03-08 20:00 | Spring | TRUE | nonsummer
2024-03-08 20:00 | 2024-03-08 21:00 | Spring | TRUE | nonsummer
2024-03-08 21:00 | 2024-03-08 22:00 | Spring | TRUE | nonsummer
2024-03-08 22:00 | 2024-03-08 23:00 | Spring | FALSE | nonsummer
2024-03-08 23:00 | 2024-03-09 | Spring | FALSE | nonsummer
2024-03-09 | 2024-03-09 01:00 | Spring | FALSE | nonsummer
2024-03-09 01:00 | 2024-03-09 02:00 | Spring | FALSE | nonsummer
2024-03-09 02:00 | 2024-03-09 03:00 | Spring | FALSE | nonsummer
2024-03-09 03:00 | 2024-03-09 04:00 | Spring | FALSE | nonsummer
2024-03-09 04:00 | 2024-03-09 05:00 | Spring | FALSE | nonsummer
2024-03-09 05:00 | 2024-03-09 06:00 | Spring | FALSE | nonsummer
2024-03-09 06:00 | 2024-03-09 07:00 | Spring | FALSE | nonsummer
2024-03-09 07:00 | 2024-03-09 08:00 | Spring | FALSE | nonsummer
2024-03-09 08:00 | 2024-03-09 09:00 | Spring | FALSE | nonsummer
2024-03-09 09:00 | 2024-03-09 10:00 | Spring | FALSE | nonsummer
2024-03-09 10:00 | 2024-03-09 11:00 | Spring | FALSE | nonsummer
2024-03-09 11:00 | 2024-03-09 12:00 | Spring | FALSE | nonsummer
2024-03-09 12:00 | 2024-03-09 13:00 | Spring | FALSE | nonsummer
2024-03-09 13:00 | 2024-03-09 14:00 | Spring | FALSE | nonsummer
2024-03-09 14:00 | 2024-03-09 15:00 | Spring | FALSE | nonsummer
2024-03-09 15:00 | 2024-03-09 16:00 | Spring | FALSE | nonsummer
2024-03-09 16:00 | 2024-03-09 17:00 | Spring | FALSE | nonsummer
2024-03-09 17:00 | 2024-03-09 18:00 | Spring | TRUE | nonsummer
2024-03-09 18:00 | 2024-03-09 19:00 | Spring | TRUE | nonsummer
2024-03-09 19:00 | 2024-03-09 20:00 | Spring | TRUE | nonsummer
2024-03-09 20:00 | 2024-03-09 21:00 | Spring | TRUE | nonsummer
2024-03-09 21:00 | 2024-03-09 22:00 | Spring | TRUE | nonsummer
2024-03-09 22:00 | 2024-03-09 23:00 | Spring | FALSE | nonsummer
2024-03-09 23:00 | 2024-03-10 | Spring | FALSE | nonsummer
2024-03-10 | 2024-03-10 01:00 | Spring | FALSE | nonsummer
2024-03-10 01:00 | 2024-03-10 02:00 | Spring | FALSE | nonsummer
2024-03-10 02:00 | 2024-03-10 03:00 | Spring | FALSE | nonsummer
2024-03-10 03:00 | 2024-03-10 04:00 | Spring | FALSE | nonsummer
2024-03-10 04:00 | 2024-03-10 05:00 | Spring | FALSE | nonsummer
2024-03-10 05:00 | 2024-03-10 06:00 | Spring | FALSE | nonsummer
2024-03-10 06:00 | 2024-03-10 07:00 | Spring | FALSE | nonsummer
2024-03-10 07:00 | 2024-03-10 08:00 | Spring | FALSE | nonsummer
2024-03-10 08:00 | 2024-03-10 09:00 | Spring | FALSE | nonsummer
2024-03-10 09:00 | 2024-03-10 10:00 | Spring | FALSE | nonsummer
2024-03-10 10:00 | 2024-03-10 11:00 | Spring | FALSE | nonsummer
2024-03-10 11:00 | 2024-03-10 12:00 | Spring | FALSE | nonsummer
2024-03-10 12:00 | 2024-03-10 13:00 | Spring | FALSE | nonsummer
2024-03-10 13:00 | 2024-03-10 14:00 | Spring | FALSE | nonsummer
2024-03-10 14:00 | 2024-03-10 15:00 | Spring | FALSE | nonsummer
2024-03-10 15:00 | 2024-03-10 16:00 | Spring | FALSE | nonsummer
2024-03-10 16:00 | 2024-03-10 17:00 | Spring | FALSE | nonsummer
2024-03-10 17:00 | 2024-03-10 18:00 | Spring | TRUE | nonsummer
2024-03-10 18:00 | 2024-03-10 19:00 | Spring | TRUE | nonsummer
2024-03-10 19:00 | 2024-03-10 20:00 | Spring | TRUE | nonsummer
2024-03-10 20:00 | 2024-03-10 21:00 | Spring | TRUE | nonsummer
2024-03-10 21:00 | 2024-03-10 22:00 | Spring | TRUE | nonsummer
2024-03-10 22:00 | 2024-03-10 23:00 | Spring | FALSE | nonsummer
2024-03-10 23:00 | 2024-03-11 | Spring | FALSE | nonsummer
2024-03-11 | 2024-03-11 01:00 | Spring | FALSE | nonsummer
2024-03-11 01:00 | 2024-03-11 02:00 | Spring | FALSE | nonsummer
2024-03-11 02:00 | 2024-03-11 03:00 | Spring | FALSE | nonsummer
2024-03-11 03:00 | 2024-03-11 04:00 | Spring | FALSE | nonsummer
2024-03-11 04:00 | 2024-03-11 05:00 | Spring | FALSE | nonsummer
2024-03-11 05:00 | 2024-03-11 06:00 | Spring | FALSE | nonsummer
2024-03-11 06:00 | 2024-03-11 07:00 | Spring | FALSE | nonsummer
2024-03-11 07:00 | 2024-03-11 08:00 | Spring | FALSE | nonsummer
2024-03-11 08:00 | 2024-03-11 09:00 | Spring | FALSE | nonsummer
2024-03-11 09:00 | 2024-03-11 10:00 | Spring | FALSE | nonsummer
2024-03-11 10:00 | 2024-03-11 11:00 | Spring | FALSE | nonsummer
2024-03-11 11:00 | 2024-03-11 12:00 | Spring | FALSE | nonsummer
2024-03-11 12:00 | 2024-03-11 13:00 | Spring | FALSE | nonsummer
2024-03-11 13:00 | 2024-03-11 14:00 | Spring | FALSE | nonsummer
2024-03-11 14:00 | 2024-03-11 15:00 | Spring | FALSE | nonsummer
2024-03-11 15:00 | 2024-03-11 16:00 | Spring | FALSE | nonsummer
2024-03-11 16:00 | 2024-03-11 17:00 | Spring | FALSE | nonsummer
2024-03-11 17:00 | 2024-03-11 18:00 | Spring | TRUE | nonsummer
2024-03-11 18:00 | 2024-03-11 19:00 | Spring | TRUE | nonsummer
2024-03-11 19:00 | 2024-03-11 20:00 | Spring | TRUE | nonsummer
2024-03-11 20:00 | 2024-03-11 21:00 | Spring | TRUE | nonsummer
2024-03-11 21:00 | 2024-03-11 22:00 | Spring | TRUE | nonsummer
2024-03-11 22:00 | 2024-03-11 23:00 | Spring | FALSE | nonsummer
2024-03-11 23:00 | 2024-03-12 | Spring | FALSE | nonsummer
2024-03-12 | 2024-03-12 01:00 | Spring | FALSE | nonsummer
2024-03-12 01:00 | 2024-03-12 02:00 | Spring | FALSE | nonsummer
2024-03-12 02:00 | 2024-03-12 03:00 | Spring | FALSE | nonsummer
2024-03-12 03:00 | 2024-03-12 04:00 | Spring | FALSE | nonsummer
2024-03-12 04:00 | 2024-03-12 05:00 | Spring | FALSE | nonsummer
2024-03-12 05:00 | 2024-03-12 06:00 | Spring | FALSE | nonsummer
2024-03-12 06:00 | 2024-03-12 07:00 | Spring | FALSE | nonsummer
2024-03-12 07:00 | 2024-03-12 08:00 | Spring | FALSE | nonsummer
2024-03-12 08:00 | 2024-03-12 09:00 | Spring | FALSE | nonsummer
2024-03-12 09:00 | 2024-03-12 10:00 | Spring | FALSE | nonsummer
2024-03-12 10:00 | 2024-03-12 11:00 | Spring | FALSE | nonsummer
2024-03-12 11:00 | 2024-03-12 12:00 | Spring | FALSE | nonsummer
2024-03-12 12:00 | 2024-03-12 13:00 | Spring | FALSE | nonsummer
2024-03-12 13:00 | 2024-03-12 14:00 | Spring | FALSE | nonsummer
2024-03-12 14:00 | 2024-03-12 15:00 | Spring | FALSE | nonsummer
2024-03-12 15:00 | 2024-03-12 16:00 | Spring | FALSE | nonsummer
2024-03-12 16:00 | 2024-03-12 17:00 | Spring | FALSE | nonsummer
2024-03-12 17:00 | 2024-03-12 18:00 | Spring | TRUE | nonsummer
2024-03-12 18:00 | 2024-03-12 19:00 | Spring | TRUE | nonsummer
2024-03-12 19:00 | 2024-03-12 20:00 | Spring | TRUE | nonsummer
2024-03-12 20:00 | 2024-03-12 21:00 | Spring | TRUE | nonsummer
2024-03-12 21:00 | 2024-03-12 22:00 | Spring | TRUE | nonsummer
2024-03-12 22:00 | 2024-03-12 23:00 | Spring | FALSE | nonsummer
2024-03-12 23:00 | 2024-03-13 | Spring | FALSE | nonsummer
2024-03-13 | 2024-03-13 01:00 | Spring | FALSE | nonsummer
2024-03-13 01:00 | 2024-03-13 02:00 | Spring | FALSE | nonsummer
2024-03-13 02:00 | 2024-03-13 03:00 | Spring | FALSE | nonsummer
2024-03-13 03:00 | 2024-03-13 04:00 | Spring | FALSE | nonsummer
2024-03-13 04:00 | 2024-03-13 05:00 | Spring | FALSE | nonsummer
2024-03-13 05:00 | 2024-03-13 06:00 | Spring | FALSE | nonsummer
2024-03-13 06:00 | 2024-03-13 07:00 | Spring | FALSE | nonsummer
2024-03-13 07:00 | 2024-03-13 08:00 | Spring | FALSE | nonsummer
2024-03-13 08:00 | 2024-03-13 09:00 | Spring | FALSE | nonsummer
2024-03-13 09:00 | 2024-03-13 10:00 | Spring | FALSE | nonsummer
2024-03-13 10:00 | 2024-03-13 11:00 | Spring | FALSE | nonsummer
2024-03-13 11:00 | 2024-03-13 12:00 | Spring | FALSE | nonsummer
2024-03-13 12:00 | 2024-03-13 13:00 | Spring | FALSE | nonsummer
2024-03-13 13:00 | 2024-03-13 14:00 | Spring | FALSE | nonsummer
2024-03-13 14:00 | 2024-03-13 15:00 | Spring | FALSE | nonsummer
2024-03-13 15:00 | 2024-03-13 16:00 | Spring | FALSE | nonsummer
2024-03-13 16:00 | 2024-03-13 17:00 | Spring | FALSE | nonsummer
2024-03-13 17:00 | 2024-03-13 18:00 | Spring | TRUE | nonsummer
2024-03-13 18:00 | 2024-03-13 19:00 | Spring | TRUE | nonsummer
2024-03-13 19:00 | 2024-03-13 20:00 | Spring | TRUE | nonsummer
2024-03-13 20:00 | 2024-03-13 21:00 | Spring | TRUE | nonsummer
2024-03-13 21:00 | 2024-03-13 22:00 | Spring | TRUE | nonsummer
2024-03-13 22:00 | 2024-03-13 23:00 | Spring | FALSE | nonsummer
2024-03-13 23:00 | 2024-03-14 | Spring | FALSE | nonsummer
2024-03-14 | 2024-03-14 01:00 | Spring | FALSE | nonsummer
2024-03-14 01:00 | 2024-03-14 02:00 | Spring | FALSE | nonsummer
2024-03-14 02:00 | 2024-03-14 03:00 | Spring | FALSE | nonsummer
2024-03-14 03:00 | 2024-03-14 04:00 | Spring | FALSE | nonsummer
2024-03-14 04:00 | 2024-03-14 05:00 | Spring | FALSE | nonsummer
2024-03-14 05:00 | 2024-03-14 06:00 | Spring | FALSE | nonsummer
2024-03-14 06:00 | 2024-03-14 07:00 | Spring | FALSE | nonsummer
2024-03-14 07:00 | 2024-03-14 08:00 | Spring | FALSE | nonsummer
2024-03-14 08:00 | 2024-03-14 09:00 | Spring | FALSE | nonsummer
2024-03-14 09:00 | 2024-03-14 10:00 | Spring | FALSE | nonsummer
2024-03-14 10:00 | 2024-03-14 11:00 | Spring | FALSE | nonsummer
2024-03-14 11:00 | 2024-03-14 12:00 | Spring | FALSE | nonsummer
2024-03-14 12:00 | 2024-03-14 13:00 | Spring | FALSE | nonsummer
2024-03-14 13:00 | 2024-03-14 14:00 | Spring | FALSE | nonsummer
2024-03-14 14:00 | 2024-03-14 15:00 | Spring | FALSE | nonsummer
2024-03-14 15:00 | 2024-03-14 16:00 | Spring | FALSE | nonsummer
2024-03-14 16:00 | 2024-03-14 17:00 | Spring | FALSE | nonsummer
2024-03-14 17:00 | 2024-03-14 18:00 | Spring | TRUE | nonsummer
2024-03-14 18:00 | 2024-03-14 19:00 | Spring | TRUE | nonsummer
2024-03-14 19:00 | 2024-03-14 20:00 | Spring | TRUE | nonsummer
2024-03-14 20:00 | 2024-03-14 21:00 | Spring | TRUE | nonsummer
2024-03-14 21:00 | 2024-03-14 22:00 | Spring | TRUE | nonsummer
2024-03-14 22:00 | 2024-03-14 23:00 | Spring | FALSE | nonsummer
2024-03-14 23:00 | 2024-03-15 | Spring | FALSE | nonsummer
2024-03-15 | 2024-03-15 01:00 | Spring | FALSE | nonsummer
2024-03-15 01:00 | 2024-03-15 02:00 | Spring | FALSE | nonsummer
2024-03-15 02:00 | 2024-03-15 03:00 | Spring | FALSE | nonsummer
2024-03-15 03:00 | 2024-03-15 04:00 | Spring | FALSE | nonsummer
2024-03-15 04:00 | 2024-03-15 05:00 | Spring | FALSE | nonsummer
2024-03-15 05:00 | 2024-03-15 06:00 | Spring | FALSE | nonsummer
2024-03-15 06:00 | 2024-03-15 07:00 | Spring | FALSE | nonsummer
2024-03-15 07:00 | 2024-03-15 08:00 | Spring | FALSE | nonsummer
2024-03-15 08:00 | 2024-03-15 09:00 | Spring | FALSE | nonsummer
2024-03-15 09:00 | 2024-03-15 10:00 | Spring | FALSE | nonsummer
2024-03-15 10:00 | 2024-03-15 11:00 | Spring | FALSE | nonsummer
2024-03-15 11:00 | 2024-03-15 12:00 | Spring | FALSE | nonsummer
2024-03-15 12:00 | 2024-03-15 13:00 | Spring | FALSE | nonsummer
2024-03-15 13:00 | 2024-03-15 14:00 | Spring | FALSE | nonsummer
2024-03-15 14:00 | 2024-03-15 15:00 | Spring | FALSE | nonsummer
2024-03-15 15:00 | 2024-03-15 16:00 | Spring | FALSE | nonsummer
2024-03-15 16:00 | 2024-03-15 17:00 | Spring | FALSE | nonsummer
2024-03-15 17:00 | 2024-03-15 18:00 | Spring | TRUE | nonsummer
2024-03-15 18:00 | 2024-03-15 19:00 | Spring | TRUE | nonsummer
2024-03-15 19:00 | 2024-03-15 20:00 | Spring | TRUE | nonsummer
2024-03-15 20:00 | 2024-03-15 21:00 | Spring | TRUE | nonsummer
2024-03-15 21:00 | 2024-03-15 22:00 | Spring | TRUE | nonsummer
2024-03-15 22:00 | 2024-03-15 23:00 | Spring | FALSE | nonsummer
2024-03-15 23:00 | 2024-03-16 | Spring | FALSE | nonsummer
2024-03-16 | 2024-03-16 01:00 | Spring | FALSE | nonsummer
2024-03-16 01:00 | 2024-03-16 02:00 | Spring | FALSE | nonsummer
2024-03-16 02:00 | 2024-03-16 03:00 | Spring | FALSE | nonsummer
2024-03-16 03:00 | 2024-03-16 04:00 | Spring | FALSE | nonsummer
2024-03-16 04:00 | 2024-03-16 05:00 | Spring | FALSE | nonsummer
2024-03-16 05:00 | 2024-03-16 06:00 | Spring | FALSE | nonsummer
2024-03-16 06:00 | 2024-03-16 07:00 | Spring | FALSE | nonsummer
2024-03-16 07:00 | 2024-03-16 08:00 | Spring | FALSE | nonsummer
2024-03-16 08:00 | 2024-03-16 09:00 | Spring | FALSE | nonsummer
2024-03-16 09:00 | 2024-03-16 10:00 | Spring | FALSE | nonsummer
2024-03-16 10:00 | 2024-03-16 11:00 | Spring | FALSE | nonsummer
2024-03-16 11:00 | 2024-03-16 12:00 | Spring | FALSE | nonsummer
2024-03-16 12:00 | 2024-03-16 13:00 | Spring | FALSE | nonsummer
2024-03-16 13:00 | 2024-03-16 14:00 | Spring | FALSE | nonsummer
2024-03-16 14:00 | 2024-03-16 15:00 | Spring | FALSE | nonsummer
2024-03-16 15:00 | 2024-03-16 16:00 | Spring | FALSE | nonsummer
2024-03-16 16:00 | 2024-03-16 17:00 | Spring | FALSE | nonsummer
2024-03-16 17:00 | 2024-03-16 18:00 | Spring | TRUE | nonsummer
2024-03-16 18:00 | 2024-03-16 19:00 | Spring | TRUE | nonsummer
2024-03-16 19:00 | 2024-03-16 20:00 | Spring | TRUE | nonsummer
2024-03-16 20:00 | 2024-03-16 21:00 | Spring | TRUE | nonsummer
2024-03-16 21:00 | 2024-03-16 22:00 | Spring | TRUE | nonsummer
2024-03-16 22:00 | 2024-03-16 23:00 | Spring | FALSE | nonsummer
2024-03-16 23:00 | 2024-03-17 | Spring | FALSE | nonsummer
2024-03-17 | 2024-03-17 01:00 | Spring | FALSE | nonsummer
2024-03-17 01:00 | 2024-03-17 02:00 | Spring | FALSE | nonsummer
2024-03-17 02:00 | 2024-03-17 03:00 | Spring | FALSE | nonsummer
2024-03-17 03:00 | 2024-03-17 04:00 | Spring | FALSE | nonsummer
2024-03-17 04:00 | 2024-03-17 05:00 | Spring | FALSE | nonsummer
2024-03-17 05:00 | 2024-03-17 06:00 | Spring | FALSE | nonsummer
2024-03-17 06:00 | 2024-03-17 07:00 | Spring | FALSE | nonsummer
2024-03-17 07:00 | 2024-03-17 08:00 | Spring | FALSE | nonsummer
2024-03-17 08:00 | 2024-03-17 09:00 | Spring | FALSE | nonsummer
2024-03-17 09:00 | 2024-03-17 10:00 | Spring | FALSE | nonsummer
2024-03-17 10:00 | 2024-03-17 11:00 | Spring | FALSE | nonsummer
2024-03-17 11:00 | 2024-03-17 12:00 | Spring | FALSE | nonsummer
2024-03-17 12:00 | 2024-03-17 13:00 | Spring | FALSE | nonsummer
2024-03-17 13:00 | 2024-03-17 14:00 | Spring | FALSE | nonsummer
2024-03-17 14:00 | 2024-03-17 15:00 | Spring | FALSE | nonsummer
2024-03-17 15:00 | 2024-03-17 16:00 | Spring | FALSE | nonsummer
2024-03-17 16:00 | 2024-03-17 17:00 | Spring | FALSE | nonsummer
2024-03-17 17:00 | 2024-03-17 18:00 | Spring | TRUE | nonsummer
2024-03-17 18:00 | 2024-03-17 19:00 | Spring | TRUE | nonsummer
2024-03-17 19:00 | 2024-03-17 20:00 | Spring | TRUE | nonsummer
2024-03-17 20:00 | 2024-03-17 21:00 | Spring | TRUE | nonsummer
2024-03-17 21:00 | 2024-03-17 22:00 | Spring | TRUE | nonsummer
2024-03-17 22:00 | 2024-03-17 23:00 | Spring | FALSE | nonsummer
2024-03-17 23:00 | 2024-03-18 | Spring | FALSE | nonsummer
2024-03-18 | 2024-03-18 01:00 | Spring | FALSE | nonsummer
2024-03-18 01:00 | 2024-03-18 02:00 | Spring | FALSE | nonsummer
2024-03-18 02:00 | 2024-03-18 03:00 | Spring | FALSE | nonsummer
2024-03-18 03:00 | 2024-03-18 04:00 | Spring | FALSE | nonsummer
2024-03-18 04:00 | 2024-03-18 05:00 | Spring | FALSE | nonsummer
2024-03-18 05:00 | 2024-03-18 06:00 | Spring | FALSE | nonsummer
2024-03-18 06:00 | 2024-03-18 07:00 | Spring | FALSE | nonsummer
2024-03-18 07:00 | 2024-03-18 08:00 | Spring | FALSE | nonsummer
2024-03-18 08:00 | 2024-03-18 09:00 | Spring | FALSE | nonsummer
2024-03-18 09:00 | 2024-03-18 10:00 | Spring | FALSE | nonsummer
2024-03-18 10:00 | 2024-03-18 11:00 | Spring | FALSE | nonsummer
2024-03-18 11:00 | 2024-03-18 12:00 | Spring | FALSE | nonsummer
2024-03-18 12:00 | 2024-03-18 13:00 | Spring | FALSE | nonsummer
2024-03-18 13:00 | 2024-03-18 14:00 | Spring | FALSE | nonsummer
2024-03-18 14:00 | 2024-03-18 15:00 | Spring | FALSE | nonsummer
2024-03-18 15:00 | 2024-03-18 16:00 | Spring | FALSE | nonsummer
2024-03-18 16:00 | 2024-03-18 17:00 | Spring | FALSE | nonsummer
2024-03-18 17:00 | 2024-03-18 18:00 | Spring | TRUE | nonsummer
2024-03-18 18:00 | 2024-03-18 19:00 | Spring | TRUE | nonsummer
2024-03-18 19:00 | 2024-03-18 20:00 | Spring | TRUE | nonsummer
2024-03-18 20:00 | 2024-03-18 21:00 | Spring | TRUE | nonsummer
2024-03-18 21:00 | 2024-03-18 22:00 | Spring | TRUE | nonsummer
2024-03-18 22:00 | 2024-03-18 23:00 | Spring | FALSE | nonsummer
2024-03-18 23:00 | 2024-03-19 | Spring | FALSE | nonsummer
2024-03-19 | 2024-03-19 01:00 | Spring | FALSE | nonsummer
2024-03-19 01:00 | 2024-03-19 02:00 | Spring | FALSE | nonsummer
2024-03-19 02:00 | 2024-03-19 03:00 | Spring | FALSE | nonsummer
2024-03-19 03:00 | 2024-03-19 04:00 | Spring | FALSE | nonsummer
2024-03-19 04:00 | 2024-03-19 05:00 | Spring | FALSE | nonsummer
2024-03-19 05:00 | 2024-03-19 06:00 | Spring | FALSE | nonsummer
2024-03-19 06:00 | 2024-03-19 07:00 | Spring | FALSE | nonsummer
2024-03-19 07:00 | 2024-03-19 08:00 | Spring | FALSE | nonsummer
2024-03-19 08:00 | 2024-03-19 09:00 | Spring | FALSE | nonsummer
2024-03-19 09:00 | 2024-03-19 10:00 | Spring | FALSE | nonsummer
2024-03-19 10:00 | 2024-03-19 11:00 | Spring | FALSE | nonsummer
2024-03-19 11:00 | 2024-03-19 12:00 | Spring | FALSE | nonsummer
2024-03-19 12:00 | 2024-03-19 13:00 | Spring | FALSE | nonsummer
2024-03-19 13:00 | 2024-03-19 14:00 | Spring | FALSE | nonsummer
2024-03-19 14:00 | 2024-03-19 15:00 | Spring | FALSE | nonsummer
2024-03-19 15:00 | 2024-03-19 16:00 | Spring | FALSE | nonsummer
2024-03-19 16:00 | 2024-03-19 17:00 | Spring | FALSE | nonsummer
2024-03-19 17:00 | 2024-03-19 18:00 | Spring | TRUE | nonsummer
2024-03-19 18:00 | 2024-03-19 19:00 | Spring | TRUE | nonsummer
2024-03-19 19:00 | 2024-03-19 20:00 | Spring | TRUE | nonsummer
2024-03-19 20:00 | 2024-03-19 21:00 | Spring | TRUE | nonsummer
2024-03-19 21:00 | 2024-03-19 22:00 | Spring | TRUE | nonsummer
2024-03-19 22:00 | 2024-03-19 23:00 | Spring | FALSE | nonsummer
2024-03-19 23:00 | 2024-03-20 | Spring | FALSE | nonsummer
2024-03-20 | 2024-03-20 01:00 | Spring | FALSE | nonsummer
2024-03-20 01:00 | 2024-03-20 02:00 | Spring | FALSE | nonsummer
2024-03-20 02:00 | 2024-03-20 03:00 | Spring | FALSE | nonsummer
2024-03-20 03:00 | 2024-03-20 04:00 | Spring | FALSE | nonsummer
2024-03-20 04:00 | 2024-03-20 05:00 | Spring | FALSE | nonsummer
2024-03-20 05:00 | 2024-03-20 06:00 | Spring | FALSE | nonsummer
2024-03-20 06:00 | 2024-03-20 07:00 | Spring | FALSE | nonsummer
2024-03-20 07:00 | 2024-03-20 08:00 | Spring | FALSE | nonsummer
2024-03-20 08:00 | 2024-03-20 09:00 | Spring | FALSE | nonsummer
2024-03-20 09:00 | 2024-03-20 10:00 | Spring | FALSE | nonsummer
2024-03-20 10:00 | 2024-03-20 11:00 | Spring | FALSE | nonsummer
2024-03-20 11:00 | 2024-03-20 12:00 | Spring | FALSE | nonsummer
2024-03-20 12:00 | 2024-03-20 13:00 | Spring | FALSE | nonsummer
2024-03-20 13:00 | 2024-03-20 14:00 | Spring | FALSE | nonsummer
2024-03-20 14:00 | 2024-03-20 15:00 | Spring | FALSE | nonsummer
2024-03-20 15:00 | 2024-03-20 16:00 | Spring | FALSE | nonsummer
2024-03-20 16:00 | 2024-03-20 17:00 | Spring | FALSE | nonsummer
2024-03-20 17:00 | 2024-03-20 18:00 | Spring | TRUE | nonsummer
2024-03-20 18:00 | 2024-03-20 19:00 | Spring | TRUE | nonsummer
2024-03-20 19:00 | 2024-03-20 20:00 | Spring | TRUE | nonsummer
2024-03-20 20:00 | 2024-03-20 21:00 | Spring | TRUE | nonsummer
2024-03-20 21:00 | 2024-03-20 22:00 | Spring | TRUE | nonsummer
2024-03-20 22:00 | 2024-03-20 23:00 | Spring | FALSE | nonsummer
2024-03-20 23:00 | 2024-03-21 | Spring | FALSE | nonsummer
2024-03-21 | 2024-03-21 01:00 | Spring | FALSE | nonsummer
2024-03-21 01:00 | 2024-03-21 02:00 | Spring | FALSE | nonsummer
2024-03-21 02:00 | 2024-03-21 03:00 | Spring | FALSE | nonsummer
2024-03-21 03:00 | 2024-03-21 04:00 | Spring | FALSE | nonsummer
2024-03-21 04:00 | 2024-03-21 05:00 | Spring | FALSE | nonsummer
2024-03-21 05:00 | 2024-03-21 06:00 | Spring | FALSE | nonsummer
2024-03-21 06:00 | 2024-03-21 07:00 | Spring | FALSE | nonsummer
2024-03-21 07:00 | 2024-03-21 08:00 | Spring | FALSE | nonsummer
2024-03-21 08:00 | 2024-03-21 09:00 | Spring | FALSE | nonsummer
2024-03-21 09:00 | 2024-03-21 10:00 | Spring | FALSE | nonsummer
2024-03-21 10:00 | 2024-03-21 11:00 | Spring | FALSE | nonsummer
2024-03-21 11:00 | 2024-03-21 12:00 | Spring | FALSE | nonsummer
2024-03-21 12:00 | 2024-03-21 13:00 | Spring | FALSE | nonsummer
2024-03-21 13:00 | 2024-03-21 14:00 | Spring | FALSE | nonsummer
2024-03-21 14:00 | 2024-03-21 15:00 | Spring | FALSE | nonsummer
2024-03-21 15:00 | 2024-03-21 16:00 | Spring | FALSE | nonsummer
2024-03-21 16:00 | 2024-03-21 17:00 | Spring | FALSE | nonsummer
2024-03-21 17:00 | 2024-03-21 18:00 | Spring | TRUE | nonsummer
2024-03-21 18:00 | 2024-03-21 19:00 | Spring | TRUE | nonsummer
2024-03-21 19:00 | 2024-03-21 20:00 | Spring | TRUE | nonsummer
2024-03-21 20:00 | 2024-03-21 21:00 | Spring | TRUE | nonsummer
2024-03-21 21:00 | 2024-03-21 22:00 | Spring | TRUE | nonsummer
2024-03-21 22:00 | 2024-03-21 23:00 | Spring | FALSE | nonsummer
2024-03-21 23:00 | 2024-03-22 | Spring | FALSE | nonsummer
2024-03-22 | 2024-03-22 01:00 | Spring | FALSE | nonsummer
2024-03-22 01:00 | 2024-03-22 02:00 | Spring | FALSE | nonsummer
2024-03-22 02:00 | 2024-03-22 03:00 | Spring | FALSE | nonsummer
2024-03-22 03:00 | 2024-03-22 04:00 | Spring | FALSE | nonsummer
2024-03-22 04:00 | 2024-03-22 05:00 | Spring | FALSE | nonsummer
2024-03-22 05:00 | 2024-03-22 06:00 | Spring | FALSE | nonsummer
2024-03-22 06:00 | 2024-03-22 07:00 | Spring | FALSE | nonsummer
2024-03-22 07:00 | 2024-03-22 08:00 | Spring | FALSE | nonsummer
2024-03-22 08:00 | 2024-03-22 09:00 | Spring | FALSE | nonsummer
2024-03-22 09:00 | 2024-03-22 10:00 | Spring | FALSE | nonsummer
2024-03-22 10:00 | 2024-03-22 11:00 | Spring | FALSE | nonsummer
2024-03-22 11:00 | 2024-03-22 12:00 | Spring | FALSE | nonsummer
2024-03-22 12:00 | 2024-03-22 13:00 | Spring | FALSE | nonsummer
2024-03-22 13:00 | 2024-03-22 14:00 | Spring | FALSE | nonsummer
2024-03-22 14:00 | 2024-03-22 15:00 | Spring | FALSE | nonsummer
2024-03-22 15:00 | 2024-03-22 16:00 | Spring | FALSE | nonsummer
2024-03-22 16:00 | 2024-03-22 17:00 | Spring | FALSE | nonsummer
2024-03-22 17:00 | 2024-03-22 18:00 | Spring | TRUE | nonsummer
2024-03-22 18:00 | 2024-03-22 19:00 | Spring | TRUE | nonsummer
2024-03-22 19:00 | 2024-03-22 20:00 | Spring | TRUE | nonsummer
2024-03-22 20:00 | 2024-03-22 21:00 | Spring | TRUE | nonsummer
2024-03-22 21:00 | 2024-03-22 22:00 | Spring | TRUE | nonsummer
2024-03-22 22:00 | 2024-03-22 23:00 | Spring | FALSE | nonsummer
2024-03-22 23:00 | 2024-03-23 | Spring | FALSE | nonsummer
2024-03-23 | 2024-03-23 01:00 | Spring | FALSE | nonsummer
2024-03-23 01:00 | 2024-03-23 02:00 | Spring | FALSE | nonsummer
2024-03-23 02:00 | 2024-03-23 03:00 | Spring | FALSE | nonsummer
2024-03-23 03:00 | 2024-03-23 04:00 | Spring | FALSE | nonsummer
2024-03-23 04:00 | 2024-03-23 05:00 | Spring | FALSE | nonsummer
2024-03-23 05:00 | 2024-03-23 06:00 | Spring | FALSE | nonsummer
2024-03-23 06:00 | 2024-03-23 07:00 | Spring | FALSE | nonsummer
2024-03-23 07:00 | 2024-03-23 08:00 | Spring | FALSE | nonsummer
2024-03-23 08:00 | 2024-03-23 09:00 | Spring | FALSE | nonsummer
2024-03-23 09:00 | 2024-03-23 10:00 | Spring | FALSE | nonsummer
2024-03-23 10:00 | 2024-03-23 11:00 | Spring | FALSE | nonsummer
2024-03-23 11:00 | 2024-03-23 12:00 | Spring | FALSE | nonsummer
2024-03-23 12:00 | 2024-03-23 13:00 | Spring | FALSE | nonsummer
2024-03-23 13:00 | 2024-03-23 14:00 | Spring | FALSE | nonsummer
2024-03-23 14:00 | 2024-03-23 15:00 | Spring | FALSE | nonsummer
2024-03-23 15:00 | 2024-03-23 16:00 | Spring | FALSE | nonsummer
2024-03-23 16:00 | 2024-03-23 17:00 | Spring | FALSE | nonsummer
2024-03-23 17:00 | 2024-03-23 18:00 | Spring | TRUE | nonsummer
2024-03-23 18:00 | 2024-03-23 19:00 | Spring | TRUE | nonsummer
2024-03-23 19:00 | 2024-03-23 20:00 | Spring | TRUE | nonsummer
2024-03-23 20:00 | 2024-03-23 21:00 | Spring | TRUE | nonsummer
2024-03-23 21:00 | 2024-03-23 22:00 | Spring | TRUE | nonsummer
2024-03-23 22:00 | 2024-03-23 23:00 | Spring | FALSE | nonsummer
2024-03-23 23:00 | 2024-03-24 | Spring | FALSE | nonsummer
2024-03-24 | 2024-03-24 01:00 | Spring | FALSE | nonsummer
2024-03-24 01:00 | 2024-03-24 02:00 | Spring | FALSE | nonsummer
2024-03-24 02:00 | 2024-03-24 03:00 | Spring | FALSE | nonsummer
2024-03-24 03:00 | 2024-03-24 04:00 | Spring | FALSE | nonsummer
2024-03-24 04:00 | 2024-03-24 05:00 | Spring | FALSE | nonsummer
2024-03-24 05:00 | 2024-03-24 06:00 | Spring | FALSE | nonsummer
2024-03-24 06:00 | 2024-03-24 07:00 | Spring | FALSE | nonsummer
2024-03-24 07:00 | 2024-03-24 08:00 | Spring | FALSE | nonsummer
2024-03-24 08:00 | 2024-03-24 09:00 | Spring | FALSE | nonsummer
2024-03-24 09:00 | 2024-03-24 10:00 | Spring | FALSE | nonsummer
2024-03-24 10:00 | 2024-03-24 11:00 | Spring | FALSE | nonsummer
2024-03-24 11:00 | 2024-03-24 12:00 | Spring | FALSE | nonsummer
2024-03-24 12:00 | 2024-03-24 13:00 | Spring | FALSE | nonsummer
2024-03-24 13:00 | 2024-03-24 14:00 | Spring | FALSE | nonsummer
2024-03-24 14:00 | 2024-03-24 15:00 | Spring | FALSE | nonsummer
2024-03-24 15:00 | 2024-03-24 16:00 | Spring | FALSE | nonsummer
2024-03-24 16:00 | 2024-03-24 17:00 | Spring | FALSE | nonsummer
2024-03-24 17:00 | 2024-03-24 18:00 | Spring | TRUE | nonsummer
2024-03-24 18:00 | 2024-03-24 19:00 | Spring | TRUE | nonsummer
2024-03-24 19:00 | 2024-03-24 20:00 | Spring | TRUE | nonsummer
2024-03-24 20:00 | 2024-03-24 21:00 | Spring | TRUE | nonsummer
2024-03-24 21:00 | 2024-03-24 22:00 | Spring | TRUE | nonsummer
2024-03-24 22:00 | 2024-03-24 23:00 | Spring | FALSE | nonsummer
2024-03-24 23:00 | 2024-03-25 | Spring | FALSE | nonsummer
2024-03-25 | 2024-03-25 01:00 | Spring | FALSE | nonsummer
2024-03-25 01:00 | 2024-03-25 02:00 | Spring | FALSE | nonsummer
2024-03-25 02:00 | 2024-03-25 03:00 | Spring | FALSE | nonsummer
2024-03-25 03:00 | 2024-03-25 04:00 | Spring | FALSE | nonsummer
2024-03-25 04:00 | 2024-03-25 05:00 | Spring | FALSE | nonsummer
2024-03-25 05:00 | 2024-03-25 06:00 | Spring | FALSE | nonsummer
2024-03-25 06:00 | 2024-03-25 07:00 | Spring | FALSE | nonsummer
2024-03-25 07:00 | 2024-03-25 08:00 | Spring | FALSE | nonsummer
2024-03-25 08:00 | 2024-03-25 09:00 | Spring | FALSE | nonsummer
2024-03-25 09:00 | 2024-03-25 10:00 | Spring | FALSE | nonsummer
2024-03-25 10:00 | 2024-03-25 11:00 | Spring | FALSE | nonsummer
2024-03-25 11:00 | 2024-03-25 12:00 | Spring | FALSE | nonsummer
2024-03-25 12:00 | 2024-03-25 13:00 | Spring | FALSE | nonsummer
2024-03-25 13:00 | 2024-03-25 14:00 | Spring | FALSE | nonsummer
2024-03-25 14:00 | 2024-03-25 15:00 | Spring | FALSE | nonsummer
2024-03-25 15:00 | 2024-03-25 16:00 | Spring | FALSE | nonsummer
2024-03-25 16:00 | 2024-03-25 17:00 | Spring | FALSE | nonsummer
2024-03-25 17:00 | 2024-03-25 18:00 | Spring | TRUE | nonsummer
2024-03-25 18:00 | 2024-03-25 19:00 | Spring | TRUE | nonsummer
2024-03-25 19:00 | 2024-03-25 20:00 | Spring | TRUE | nonsummer
2024-03-25 20:00 | 2024-03-25 21:00 | Spring | TRUE | nonsummer
2024-03-25 21:00 | 2024-03-25 22:00 | Spring | TRUE | nonsummer
2024-03-25 22:00 | 2024-03-25 23:00 | Spring | FALSE | nonsummer
2024-03-25 23:00 | 2024-03-26 | Spring | FALSE | nonsummer
2024-03-26 | 2024-03-26 01:00 | Spring | FALSE | nonsummer
2024-03-26 01:00 | 2024-03-26 02:00 | Spring | FALSE | nonsummer
2024-03-26 02:00 | 2024-03-26 03:00 | Spring | FALSE | nonsummer
2024-03-26 03:00 | 2024-03-26 04:00 | Spring | FALSE | nonsummer
2024-03-26 04:00 | 2024-03-26 05:00 | Spring | FALSE | nonsummer
2024-03-26 05:00 | 2024-03-26 06:00 | Spring | FALSE | nonsummer
2024-03-26 06:00 | 2024-03-26 07:00 | Spring | FALSE | nonsummer
2024-03-26 07:00 | 2024-03-26 08:00 | Spring | FALSE | nonsummer
2024-03-26 08:00 | 2024-03-26 09:00 | Spring | FALSE | nonsummer
2024-03-26 09:00 | 2024-03-26 10:00 | Spring | FALSE | nonsummer
2024-03-26 10:00 | 2024-03-26 11:00 | Spring | FALSE | nonsummer
2024-03-26 11:00 | 2024-03-26 12:00 | Spring | FALSE | nonsummer
2024-03-26 12:00 | 2024-03-26 13:00 | Spring | FALSE | nonsummer
2024-03-26 13:00 | 2024-03-26 14:00 | Spring | FALSE | nonsummer
2024-03-26 14:00 | 2024-03-26 15:00 | Spring | FALSE | nonsummer
2024-03-26 15:00 | 2024-03-26 16:00 | Spring | FALSE | nonsummer
2024-03-26 16:00 | 2024-03-26 17:00 | Spring | FALSE | nonsummer
2024-03-26 17:00 | 2024-03-26 18:00 | Spring | TRUE | nonsummer
2024-03-26 18:00 | 2024-03-26 19:00 | Spring | TRUE | nonsummer
2024-03-26 19:00 | 2024-03-26 20:00 | Spring | TRUE | nonsummer
2024-03-26 20:00 | 2024-03-26 21:00 | Spring | TRUE | nonsummer
2024-03-26 21:00 | 2024-03-26 22:00 | Spring | TRUE | nonsummer
2024-03-26 22:00 | 2024-03-26 23:00 | Spring | FALSE | nonsummer
2024-03-26 23:00 | 2024-03-27 | Spring | FALSE | nonsummer
2024-03-27 | 2024-03-27 01:00 | Spring | FALSE | nonsummer
2024-03-27 01:00 | 2024-03-27 02:00 | Spring | FALSE | nonsummer
2024-03-27 02:00 | 2024-03-27 03:00 | Spring | FALSE | nonsummer
2024-03-27 03:00 | 2024-03-27 04:00 | Spring | FALSE | nonsummer
2024-03-27 04:00 | 2024-03-27 05:00 | Spring | FALSE | nonsummer
2024-03-27 05:00 | 2024-03-27 06:00 | Spring | FALSE | nonsummer
2024-03-27 06:00 | 2024-03-27 07:00 | Spring | FALSE | nonsummer
2024-03-27 07:00 | 2024-03-27 08:00 | Spring | FALSE | nonsummer
2024-03-27 08:00 | 2024-03-27 09:00 | Spring | FALSE | nonsummer
2024-03-27 09:00 | 2024-03-27 10:00 | Spring | FALSE | nonsummer
2024-03-27 10:00 | 2024-03-27 11:00 | Spring | FALSE | nonsummer
2024-03-27 11:00 | 2024-03-27 12:00 | Spring | FALSE | nonsummer
2024-03-27 12:00 | 2024-03-27 13:00 | Spring | FALSE | nonsummer
2024-03-27 13:00 | 2024-03-27 14:00 | Spring | FALSE | nonsummer
2024-03-27 14:00 | 2024-03-27 15:00 | Spring | FALSE | nonsummer
2024-03-27 15:00 | 2024-03-27 16:00 | Spring | FALSE | nonsummer
2024-03-27 16:00 | 2024-03-27 17:00 | Spring | FALSE | nonsummer
2024-03-27 17:00 | 2024-03-27 18:00 | Spring | TRUE | nonsummer
2024-03-27 18:00 | 2024-03-27 19:00 | Spring | TRUE | nonsummer
2024-03-27 19:00 | 2024-03-27 20:00 | Spring | TRUE | nonsummer
2024-03-27 20:00 | 2024-03-27 21:00 | Spring | TRUE | nonsummer
2024-03-27 21:00 | 2024-03-27 22:00 | Spring | TRUE | nonsummer
2024-03-27 22:00 | 2024-03-27 23:00 | Spring | FALSE | nonsummer
2024-03-27 23:00 | 2024-03-28 | Spring | FALSE | nonsummer
2024-03-28 | 2024-03-28 01:00 | Spring | FALSE | nonsummer
2024-03-28 01:00 | 2024-03-28 02:00 | Spring | FALSE | nonsummer
2024-03-28 02:00 | 2024-03-28 03:00 | Spring | FALSE | nonsummer
2024-03-28 03:00 | 2024-03-28 04:00 | Spring | FALSE | nonsummer
2024-03-28 04:00 | 2024-03-28 05:00 | Spring | FALSE | nonsummer
2024-03-28 05:00 | 2024-03-28 06:00 | Spring | FALSE | nonsummer
2024-03-28 06:00 | 2024-03-28 07:00 | Spring | FALSE | nonsummer
2024-03-28 07:00 | 2024-03-28 08:00 | Spring | FALSE | nonsummer
2024-03-28 08:00 | 2024-03-28 09:00 | Spring | FALSE | nonsummer
2024-03-28 09:00 | 2024-03-28 10:00 | Spring | FALSE | nonsummer
2024-03-28 10:00 | 2024-03-28 11:00 | Spring | FALSE | nonsummer
2024-03-28 11:00 | 2024-03-28 12:00 | Spring | FALSE | nonsummer
2024-03-28 12:00 | 2024-03-28 13:00 | Spring | FALSE | nonsummer
2024-03-28 13:00 | 2024-03-28 14:00 | Spring | FALSE | nonsummer
2024-03-28 14:00 | 2024-03-28 15:00 | Spring | FALSE | nonsummer
2024-03-28 15:00 | 2024-03-28 16:00 | Spring | FALSE | nonsummer
2024-03-28 16:00 | 2024-03-28 17:00 | Spring | FALSE | nonsummer
2024-03-28 17:00 | 2024-03-28 18:00 | Spring | TRUE | nonsummer
2024-03-28 18:00 | 2024-03-28 19:00 | Spring | TRUE | nonsummer
2024-03-28 19:00 | 2024-03-28 20:00 | Spring | TRUE | nonsummer
2024-03-28 20:00 | 2024-03-28 21:00 | Spring | TRUE | nonsummer
2024-03-28 21:00 | 2024-03-28 22:00 | Spring | TRUE | nonsummer
2024-03-28 22:00 | 2024-03-28 23:00 | Spring | FALSE | nonsummer
2024-03-28 23:00 | 2024-03-29 | Spring | FALSE | nonsummer
2024-03-29 | 2024-03-29 01:00 | Spring | FALSE | nonsummer
2024-03-29 01:00 | 2024-03-29 02:00 | Spring | FALSE | nonsummer
2024-03-29 02:00 | 2024-03-29 03:00 | Spring | FALSE | nonsummer
2024-03-29 03:00 | 2024-03-29 04:00 | Spring | FALSE | nonsummer
2024-03-29 04:00 | 2024-03-29 05:00 | Spring | FALSE | nonsummer
2024-03-29 05:00 | 2024-03-29 06:00 | Spring | FALSE | nonsummer
2024-03-29 06:00 | 2024-03-29 07:00 | Spring | FALSE | nonsummer
2024-03-29 07:00 | 2024-03-29 08:00 | Spring | FALSE | nonsummer
2024-03-29 08:00 | 2024-03-29 09:00 | Spring | FALSE | nonsummer
2024-03-29 09:00 | 2024-03-29 10:00 | Spring | FALSE | nonsummer
2024-03-29 10:00 | 2024-03-29 11:00 | Spring | FALSE | nonsummer
2024-03-29 11:00 | 2024-03-29 12:00 | Spring | FALSE | nonsummer
2024-03-29 12:00 | 2024-03-29 13:00 | Spring | FALSE | nonsummer
2024-03-29 13:00 | 2024-03-29 14:00 | Spring | FALSE | nonsummer
2024-03-29 14:00 | 2024-03-29 15:00 | Spring | FALSE | nonsummer
2024-03-29 15:00 | 2024-03-29 16:00 | Spring | FALSE | nonsummer
2024-03-29 16:00 | 2024-03-29 17:00 | Spring | FALSE | nonsummer
2024-03-29 17:00 | 2024-03-29 18:00 | Spring | TRUE | nonsummer
2024-03-29 18:00 | 2024-03-29 19:00 | Spring | TRUE | nonsummer
2024-03-29 19:00 | 2024-03-29 20:00 | Spring | TRUE | nonsummer
2024-03-29 20:00 | 2024-03-29 21:00 | Spring | TRUE | nonsummer
2024-03-29 21:00 | 2024-03-29 22:00 | Spring | TRUE | nonsummer
2024-03-29 22:00 | 2024-03-29 23:00 | Spring | FALSE | nonsummer
2024-03-29 23:00 | 2024-03-30 | Spring | FALSE | nonsummer
2024-03-30 | 2024-03-30 01:00 | Spring | FALSE | nonsummer
2024-03-30 01:00 | 2024-03-30 02:00 | Spring | FALSE | nonsummer
2024-03-30 02:00 | 2024-03-30 03:00 | Spring | FALSE | nonsummer
2024-03-30 03:00 | 2024-03-30 04:00 | Spring | FALSE | nonsummer
2024-03-30 04:00 | 2024-03-30 05:00 | Spring | FALSE | nonsummer
2024-03-30 05:00 | 2024-03-30 06:00 | Spring | FALSE | nonsummer
2024-03-30 06:00 | 2024-03-30 07:00 | Spring | FALSE | nonsummer
2024-03-30 07:00 | 2024-03-30 08:00 | Spring | FALSE | nonsummer
2024-03-30 08:00 | 2024-03-30 09:00 | Spring | FALSE | nonsummer
2024-03-30 09:00 | 2024-03-30 10:00 | Spring | FALSE | nonsummer
2024-03-30 10:00 | 2024-03-30 11:00 | Spring | FALSE | nonsummer
2024-03-30 11:00 | 2024-03-30 12:00 | Spring | FALSE | nonsummer
2024-03-30 12:00 | 2024-03-30 13:00 | Spring | FALSE | nonsummer
2024-03-30 13:00 | 2024-03-30 14:00 | Spring | FALSE | nonsummer
2024-03-30 14:00 | 2024-03-30 15:00 | Spring | FALSE | nonsummer
2024-03-30 15:00 | 2024-03-30 16:00 | Spring | FALSE | nonsummer
2024-03-30 16:00 | 2024-03-30 17:00 | Spring | FALSE | nonsummer
2024-03-30 17:00 | 2024-03-30 18:00 | Spring | TRUE | nonsummer
2024-03-30 18:00 | 2024-03-30 19:00 | Spring | TRUE | nonsummer
2024-03-30 19:00 | 2024-03-30 20:00 | Spring | TRUE | nonsummer
2024-03-30 20:00 | 2024-03-30 21:00 | Spring | TRUE | nonsummer
2024-03-30 21:00 | 2024-03-30 22:00 | Spring | TRUE | nonsummer
2024-03-30 22:00 | 2024-03-30 23:00 | Spring | FALSE | nonsummer
2024-03-30 23:00 | 2024-03-31 | Spring | FALSE | nonsummer
2024-03-31 | 2024-03-31 01:00 | Spring | FALSE | nonsummer
2024-03-31 01:00 | 2024-03-31 02:00 | Spring | FALSE | nonsummer
2024-03-31 02:00 | 2024-03-31 03:00 | Spring | FALSE | nonsummer
2024-03-31 03:00 | 2024-03-31 04:00 | Spring | FALSE | nonsummer
2024-03-31 04:00 | 2024-03-31 05:00 | Spring | FALSE | nonsummer
2024-03-31 05:00 | 2024-03-31 06:00 | Spring | FALSE | nonsummer
2024-03-31 06:00 | 2024-03-31 07:00 | Spring | FALSE | nonsummer
2024-03-31 07:00 | 2024-03-31 08:00 | Spring | FALSE | nonsummer
2024-03-31 08:00 | 2024-03-31 09:00 | Spring | FALSE | nonsummer
2024-03-31 09:00 | 2024-03-31 10:00 | Spring | FALSE | nonsummer
2024-03-31 10:00 | 2024-03-31 11:00 | Spring | FALSE | nonsummer
2024-03-31 11:00 | 2024-03-31 12:00 | Spring | FALSE | nonsummer
2024-03-31 12:00 | 2024-03-31 13:00 | Spring | FALSE | nonsummer
2024-03-31 13:00 | 2024-03-31 14:00 | Spring | FALSE | nonsummer
2024-03-31 14:00 | 2024-03-31 15:00 | Spring | FALSE | nonsummer
2024-03-31 15:00 | 2024-03-31 16:00 | Spring | FALSE | nonsummer
2024-03-31 16:00 | 2024-03-31 17:00 | Spring | FALSE | nonsummer
2024-03-31 17:00 | 2024-03-31 18:00 | Spring | TRUE | nonsummer
2024-03-31 18:00 | 2024-03-31 19:00 | Spring | TRUE | nonsummer
2024-03-31 19:00 | 2024-03-31 20:00 | Spring | TRUE | nonsummer
2024-03-31 20:00 | 2024-03-31 21:00 | Spring | TRUE | nonsummer
2024-03-31 21:00 | 2024-03-31 22:00 | Spring | TRUE | nonsummer
2024-03-31 22:00 | 2024-03-31 23:00 | Spring | FALSE | nonsummer
2024-03-31 23:00 | 2024-04-01 | Spring | FALSE | nonsummer
2024-04-01 | 2024-04-01 01:00 | Spring | FALSE | nonsummer
2024-04-01 01:00 | 2024-04-01 02:00 | Spring | FALSE | nonsummer
2024-04-01 02:00 | 2024-04-01 03:00 | Spring | FALSE | nonsummer
2024-04-01 03:00 | 2024-04-01 04:00 | Spring | FALSE | nonsummer
2024-04-01 04:00 | 2024-04-01 05:00 | Spring | FALSE | nonsummer
2024-04-01 05:00 | 2024-04-01 06:00 | Spring | FALSE | nonsummer
2024-04-01 06:00 | 2024-04-01 07:00 | Spring | FALSE | nonsummer
2024-04-01 07:00 | 2024-04-01 08:00 | Spring | FALSE | nonsummer
2024-04-01 08:00 | 2024-04-01 09:00 | Spring | FALSE | nonsummer
2024-04-01 09:00 | 2024-04-01 10:00 | Spring | FALSE | nonsummer
2024-04-01 10:00 | 2024-04-01 11:00 | Spring | FALSE | nonsummer
2024-04-01 11:00 | 2024-04-01 12:00 | Spring | FALSE | nonsummer
2024-04-01 12:00 | 2024-04-01 13:00 | Spring | FALSE | nonsummer
2024-04-01 13:00 | 2024-04-01 14:00 | Spring | FALSE | nonsummer
2024-04-01 14:00 | 2024-04-01 15:00 | Spring | FALSE | nonsummer
2024-04-01 15:00 | 2024-04-01 16:00 | Spring | FALSE | nonsummer
2024-04-01 16:00 | 2024-04-01 17:00 | Spring | FALSE | nonsummer
2024-04-01 17:00 | 2024-04-01 18:00 | Spring | TRUE | nonsummer
2024-04-01 18:00 | 2024-04-01 19:00 | Spring | TRUE | nonsummer
2024-04-01 19:00 | 2024-04-01 20:00 | Spring | TRUE | nonsummer
2024-04-01 20:00 | 2024-04-01 21:00 | Spring | TRUE | nonsummer
2024-04-01 21:00 | 2024-04-01 22:00 | Spring | TRUE | nonsummer
2024-04-01 22:00 | 2024-04-01 23:00 | Spring | FALSE | nonsummer
2024-04-01 23:00 | 2024-04-02 | Spring | FALSE | nonsummer
2024-04-02 | 2024-04-02 01:00 | Spring | FALSE | nonsummer
2024-04-02 01:00 | 2024-04-02 02:00 | Spring | FALSE | nonsummer
2024-04-02 02:00 | 2024-04-02 03:00 | Spring | FALSE | nonsummer
2024-04-02 03:00 | 2024-04-02 04:00 | Spring | FALSE | nonsummer
2024-04-02 04:00 | 2024-04-02 05:00 | Spring | FALSE | nonsummer
2024-04-02 05:00 | 2024-04-02 06:00 | Spring | FALSE | nonsummer
2024-04-02 06:00 | 2024-04-02 07:00 | Spring | FALSE | nonsummer
2024-04-02 07:00 | 2024-04-02 08:00 | Spring | FALSE | nonsummer
2024-04-02 08:00 | 2024-04-02 09:00 | Spring | FALSE | nonsummer
2024-04-02 09:00 | 2024-04-02 10:00 | Spring | FALSE | nonsummer
2024-04-02 10:00 | 2024-04-02 11:00 | Spring | FALSE | nonsummer
2024-04-02 11:00 | 2024-04-02 12:00 | Spring | FALSE | nonsummer
2024-04-02 12:00 | 2024-04-02 13:00 | Spring | FALSE | nonsummer
2024-04-02 13:00 | 2024-04-02 14:00 | Spring | FALSE | nonsummer
2024-04-02 14:00 | 2024-04-02 15:00 | Spring | FALSE | nonsummer
2024-04-02 15:00 | 2024-04-02 16:00 | Spring | FALSE | nonsummer
2024-04-02 16:00 | 2024-04-02 17:00 | Spring | FALSE | nonsummer
2024-04-02 17:00 | 2024-04-02 18:00 | Spring | TRUE | nonsummer
2024-04-02 18:00 | 2024-04-02 19:00 | Spring | TRUE | nonsummer
2024-04-02 19:00 | 2024-04-02 20:00 | Spring | TRUE | nonsummer
2024-04-02 20:00 | 2024-04-02 21:00 | Spring | TRUE | nonsummer
2024-04-02 21:00 | 2024-04-02 22:00 | Spring | TRUE | nonsummer
2024-04-02 22:00 | 2024-04-02 23:00 | Spring | FALSE | nonsummer
2024-04-02 23:00 | 2024-04-03 | Spring | FALSE | nonsummer
2024-04-03 | 2024-04-03 01:00 | Spring | FALSE | nonsummer
2024-04-03 01:00 | 2024-04-03 02:00 | Spring | FALSE | nonsummer
2024-04-03 02:00 | 2024-04-03 03:00 | Spring | FALSE | nonsummer
2024-04-03 03:00 | 2024-04-03 04:00 | Spring | FALSE | nonsummer
2024-04-03 04:00 | 2024-04-03 05:00 | Spring | FALSE | nonsummer
2024-04-03 05:00 | 2024-04-03 06:00 | Spring | FALSE | nonsummer
2024-04-03 06:00 | 2024-04-03 07:00 | Spring | FALSE | nonsummer
2024-04-03 07:00 | 2024-04-03 08:00 | Spring | FALSE | nonsummer
2024-04-03 08:00 | 2024-04-03 09:00 | Spring | FALSE | nonsummer
2024-04-03 09:00 | 2024-04-03 10:00 | Spring | FALSE | nonsummer
2024-04-03 10:00 | 2024-04-03 11:00 | Spring | FALSE | nonsummer
2024-04-03 11:00 | 2024-04-03 12:00 | Spring | FALSE | nonsummer
2024-04-03 12:00 | 2024-04-03 13:00 | Spring | FALSE | nonsummer
2024-04-03 13:00 | 2024-04-03 14:00 | Spring | FALSE | nonsummer
2024-04-03 14:00 | 2024-04-03 15:00 | Spring | FALSE | nonsummer
2024-04-03 15:00 | 2024-04-03 16:00 | Spring | FALSE | nonsummer
2024-04-03 16:00 | 2024-04-03 17:00 | Spring | FALSE | nonsummer
2024-04-03 17:00 | 2024-04-03 18:00 | Spring | TRUE | nonsummer
2024-04-03 18:00 | 2024-04-03 19:00 | Spring | TRUE | nonsummer
2024-04-03 19:00 | 2024-04-03 20:00 | Spring | TRUE | nonsummer
2024-04-03 20:00 | 2024-04-03 21:00 | Spring | TRUE | nonsummer
2024-04-03 21:00 | 2024-04-03 22:00 | Spring | TRUE | nonsummer
2024-04-03 22:00 | 2024-04-03 23:00 | Spring | FALSE | nonsummer
2024-04-03 23:00 | 2024-04-04 | Spring | FALSE | nonsummer
2024-04-04 | 2024-04-04 01:00 | Spring | FALSE | nonsummer
2024-04-04 01:00 | 2024-04-04 02:00 | Spring | FALSE | nonsummer
2024-04-04 02:00 | 2024-04-04 03:00 | Spring | FALSE | nonsummer
2024-04-04 03:00 | 2024-04-04 04:00 | Spring | FALSE | nonsummer
2024-04-04 04:00 | 2024-04-04 05:00 | Spring | FALSE | nonsummer
2024-04-04 05:00 | 2024-04-04 06:00 | Spring | FALSE | nonsummer
2024-04-04 06:00 | 2024-04-04 07:00 | Spring | FALSE | nonsummer
2024-04-04 07:00 | 2024-04-04 08:00 | Spring | FALSE | nonsummer
2024-04-04 08:00 | 2024-04-04 09:00 | Spring | FALSE | nonsummer
2024-04-04 09:00 | 2024-04-04 10:00 | Spring | FALSE | nonsummer
2024-04-04 10:00 | 2024-04-04 11:00 | Spring | FALSE | nonsummer
2024-04-04 11:00 | 2024-04-04 12:00 | Spring | FALSE | nonsummer
2024-04-04 12:00 | 2024-04-04 13:00 | Spring | FALSE | nonsummer
2024-04-04 13:00 | 2024-04-04 14:00 | Spring | FALSE | nonsummer
2024-04-04 14:00 | 2024-04-04 15:00 | Spring | FALSE | nonsummer
2024-04-04 15:00 | 2024-04-04 16:00 | Spring | FALSE | nonsummer
2024-04-04 16:00 | 2024-04-04 17:00 | Spring | FALSE | nonsummer
2024-04-04 17:00 | 2024-04-04 18:00 | Spring | TRUE | nonsummer
2024-04-04 18:00 | 2024-04-04 19:00 | Spring | TRUE | nonsummer
2024-04-04 19:00 | 2024-04-04 20:00 | Spring | TRUE | nonsummer
2024-04-04 20:00 | 2024-04-04 21:00 | Spring | TRUE | nonsummer
2024-04-04 21:00 | 2024-04-04 22:00 | Spring | TRUE | nonsummer
2024-04-04 22:00 | 2024-04-04 23:00 | Spring | FALSE | nonsummer
2024-04-04 23:00 | 2024-04-05 | Spring | FALSE | nonsummer
2024-04-05 | 2024-04-05 01:00 | Spring | FALSE | nonsummer
2024-04-05 01:00 | 2024-04-05 02:00 | Spring | FALSE | nonsummer
2024-04-05 02:00 | 2024-04-05 03:00 | Spring | FALSE | nonsummer
2024-04-05 03:00 | 2024-04-05 04:00 | Spring | FALSE | nonsummer
2024-04-05 04:00 | 2024-04-05 05:00 | Spring | FALSE | nonsummer
2024-04-05 05:00 | 2024-04-05 06:00 | Spring | FALSE | nonsummer
2024-04-05 06:00 | 2024-04-05 07:00 | Spring | FALSE | nonsummer
2024-04-05 07:00 | 2024-04-05 08:00 | Spring | FALSE | nonsummer
2024-04-05 08:00 | 2024-04-05 09:00 | Spring | FALSE | nonsummer
2024-04-05 09:00 | 2024-04-05 10:00 | Spring | FALSE | nonsummer
2024-04-05 10:00 | 2024-04-05 11:00 | Spring | FALSE | nonsummer
2024-04-05 11:00 | 2024-04-05 12:00 | Spring | FALSE | nonsummer
2024-04-05 12:00 | 2024-04-05 13:00 | Spring | FALSE | nonsummer
2024-04-05 13:00 | 2024-04-05 14:00 | Spring | FALSE | nonsummer
2024-04-05 14:00 | 2024-04-05 15:00 | Spring | FALSE | nonsummer
2024-04-05 15:00 | 2024-04-05 16:00 | Spring | FALSE | nonsummer
2024-04-05 16:00 | 2024-04-05 17:00 | Spring | FALSE | nonsummer
2024-04-05 17:00 | 2024-04-05 18:00 | Spring | TRUE | nonsummer
2024-04-05 18:00 | 2024-04-05 19:00 | Spring | TRUE | nonsummer
2024-04-05 19:00 | 2024-04-05 20:00 | Spring | TRUE | nonsummer
2024-04-05 20:00 | 2024-04-05 21:00 | Spring | TRUE | nonsummer
2024-04-05 21:00 | 2024-04-05 22:00 | Spring | TRUE | nonsummer
2024-04-05 22:00 | 2024-04-05 23:00 | Spring | FALSE | nonsummer
2024-04-05 23:00 | 2024-04-06 | Spring | FALSE | nonsummer
2024-04-06 | 2024-04-06 01:00 | Spring | FALSE | nonsummer
2024-04-06 01:00 | 2024-04-06 02:00 | Spring | FALSE | nonsummer
2024-04-06 02:00 | 2024-04-06 03:00 | Spring | FALSE | nonsummer
2024-04-06 03:00 | 2024-04-06 04:00 | Spring | FALSE | nonsummer
2024-04-06 04:00 | 2024-04-06 05:00 | Spring | FALSE | nonsummer
2024-04-06 05:00 | 2024-04-06 06:00 | Spring | FALSE | nonsummer
2024-04-06 06:00 | 2024-04-06 07:00 | Spring | FALSE | nonsummer
2024-04-06 07:00 | 2024-04-06 08:00 | Spring | FALSE | nonsummer
2024-04-06 08:00 | 2024-04-06 09:00 | Spring | FALSE | nonsummer
2024-04-06 09:00 | 2024-04-06 10:00 | Spring | FALSE | nonsummer
2024-04-06 10:00 | 2024-04-06 11:00 | Spring | FALSE | nonsummer
2024-04-06 11:00 | 2024-04-06 12:00 | Spring | FALSE | nonsummer
2024-04-06 12:00 | 2024-04-06 13:00 | Spring | FALSE | nonsummer
2024-04-06 13:00 | 2024-04-06 14:00 | Spring | FALSE | nonsummer
2024-04-06 14:00 | 2024-04-06 15:00 | Spring | FALSE | nonsummer
2024-04-06 15:00 | 2024-04-06 16:00 | Spring | FALSE | nonsummer
2024-04-06 16:00 | 2024-04-06 17:00 | Spring | FALSE | nonsummer
2024-04-06 17:00 | 2024-04-06 18:00 | Spring | TRUE | nonsummer
2024-04-06 18:00 | 2024-04-06 19:00 | Spring | TRUE | nonsummer
2024-04-06 19:00 | 2024-04-06 20:00 | Spring | TRUE | nonsummer
2024-04-06 20:00 | 2024-04-06 21:00 | Spring | TRUE | nonsummer
2024-04-06 21:00 | 2024-04-06 22:00 | Spring | TRUE | nonsummer
2024-04-06 22:00 | 2024-04-06 23:00 | Spring | FALSE | nonsummer
2024-04-06 23:00 | 2024-04-07 | Spring | FALSE | nonsummer
2024-04-07 | 2024-04-07 01:00 | Spring | FALSE | nonsummer
2024-04-07 01:00 | 2024-04-07 02:00 | Spring | FALSE | nonsummer
2024-04-07 02:00 | 2024-04-07 03:00 | Spring | FALSE | nonsummer
2024-04-07 03:00 | 2024-04-07 04:00 | Spring | FALSE | nonsummer
2024-04-07 04:00 | 2024-04-07 05:00 | Spring | FALSE | nonsummer
2024-04-07 05:00 | 2024-04-07 06:00 | Spring | FALSE | nonsummer
2024-04-07 06:00 | 2024-04-07 07:00 | Spring | FALSE | nonsummer
2024-04-07 07:00 | 2024-04-07 08:00 | Spring | FALSE | nonsummer
2024-04-07 08:00 | 2024-04-07 09:00 | Spring | FALSE | nonsummer
2024-04-07 09:00 | 2024-04-07 10:00 | Spring | FALSE | nonsummer
2024-04-07 10:00 | 2024-04-07 11:00 | Spring | FALSE | nonsummer
2024-04-07 11:00 | 2024-04-07 12:00 | Spring | FALSE | nonsummer
2024-04-07 12:00 | 2024-04-07 13:00 | Spring | FALSE | nonsummer
2024-04-07 13:00 | 2024-04-07 14:00 | Spring | FALSE | nonsummer
2024-04-07 14:00 | 2024-04-07 15:00 | Spring | FALSE | nonsummer
2024-04-07 15:00 | 2024-04-07 16:00 | Spring | FALSE | nonsummer
2024-04-07 16:00 | 2024-04-07 17:00 | Spring | FALSE | nonsummer
2024-04-07 17:00 | 2024-04-07 18:00 | Spring | TRUE | nonsummer
2024-04-07 18:00 | 2024-04-07 19:00 | Spring | TRUE | nonsummer
2024-04-07 19:00 | 2024-04-07 20:00 | Spring | TRUE | nonsummer
2024-04-07 20:00 | 2024-04-07 21:00 | Spring | TRUE | nonsummer
2024-04-07 21:00 | 2024-04-07 22:00 | Spring | TRUE | nonsummer
2024-04-07 22:00 | 2024-04-07 23:00 | Spring | FALSE | nonsummer
2024-04-07 23:00 | 2024-04-08 | Spring | FALSE | nonsummer
2024-04-08 | 2024-04-08 01:00 | Spring | FALSE | nonsummer
2024-04-08 01:00 | 2024-04-08 02:00 | Spring | FALSE | nonsummer
2024-04-08 02:00 | 2024-04-08 03:00 | Spring | FALSE | nonsummer
2024-04-08 03:00 | 2024-04-08 04:00 | Spring | FALSE | nonsummer
2024-04-08 04:00 | 2024-04-08 05:00 | Spring | FALSE | nonsummer
2024-04-08 05:00 | 2024-04-08 06:00 | Spring | FALSE | nonsummer
2024-04-08 06:00 | 2024-04-08 07:00 | Spring | FALSE | nonsummer
2024-04-08 07:00 | 2024-04-08 08:00 | Spring | FALSE | nonsummer
2024-04-08 08:00 | 2024-04-08 09:00 | Spring | FALSE | nonsummer
2024-04-08 09:00 | 2024-04-08 10:00 | Spring | FALSE | nonsummer
2024-04-08 10:00 | 2024-04-08 11:00 | Spring | FALSE | nonsummer
2024-04-08 11:00 | 2024-04-08 12:00 | Spring | FALSE | nonsummer
2024-04-08 12:00 | 2024-04-08 13:00 | Spring | FALSE | nonsummer
2024-04-08 13:00 | 2024-04-08 14:00 | Spring | FALSE | nonsummer
2024-04-08 14:00 | 2024-04-08 15:00 | Spring | FALSE | nonsummer
2024-04-08 15:00 | 2024-04-08 16:00 | Spring | FALSE | nonsummer
2024-04-08 16:00 | 2024-04-08 17:00 | Spring | FALSE | nonsummer
2024-04-08 17:00 | 2024-04-08 18:00 | Spring | TRUE | nonsummer
2024-04-08 18:00 | 2024-04-08 19:00 | Spring | TRUE | nonsummer
2024-04-08 19:00 | 2024-04-08 20:00 | Spring | TRUE | nonsummer
2024-04-08 20:00 | 2024-04-08 21:00 | Spring | TRUE | nonsummer
2024-04-08 21:00 | 2024-04-08 22:00 | Spring | TRUE | nonsummer
2024-04-08 22:00 | 2024-04-08 23:00 | Spring | FALSE | nonsummer
2024-04-08 23:00 | 2024-04-09 | Spring | FALSE | nonsummer
2024-04-09 | 2024-04-09 01:00 | Spring | FALSE | nonsummer
2024-04-09 01:00 | 2024-04-09 02:00 | Spring | FALSE | nonsummer
2024-04-09 02:00 | 2024-04-09 03:00 | Spring | FALSE | nonsummer
2024-04-09 03:00 | 2024-04-09 04:00 | Spring | FALSE | nonsummer
2024-04-09 04:00 | 2024-04-09 05:00 | Spring | FALSE | nonsummer
2024-04-09 05:00 | 2024-04-09 06:00 | Spring | FALSE | nonsummer
2024-04-09 06:00 | 2024-04-09 07:00 | Spring | FALSE | nonsummer
2024-04-09 07:00 | 2024-04-09 08:00 | Spring | FALSE | nonsummer
2024-04-09 08:00 | 2024-04-09 09:00 | Spring | FALSE | nonsummer
2024-04-09 09:00 | 2024-04-09 10:00 | Spring | FALSE | nonsummer
2024-04-09 10:00 | 2024-04-09 11:00 | Spring | FALSE | nonsummer
2024-04-09 11:00 | 2024-04-09 12:00 | Spring | FALSE | nonsummer
2024-04-09 12:00 | 2024-04-09 13:00 | Spring | FALSE | nonsummer
2024-04-09 13:00 | 2024-04-09 14:00 | Spring | FALSE | nonsummer
2024-04-09 14:00 | 2024-04-09 15:00 | Spring | FALSE | nonsummer
2024-04-09 15:00 | 2024-04-09 16:00 | Spring | FALSE | nonsummer
2024-04-09 16:00 | 2024-04-09 17:00 | Spring | FALSE | nonsummer
2024-04-09 17:00 | 2024-04-09 18:00 | Spring | TRUE | nonsummer
2024-04-09 18:00 | 2024-04-09 19:00 | Spring | TRUE | nonsummer
2024-04-09 19:00 | 2024-04-09 20:00 | Spring | TRUE | nonsummer
2024-04-09 20:00 | 2024-04-09 21:00 | Spring | TRUE | nonsummer
2024-04-09 21:00 | 2024-04-09 22:00 | Spring | TRUE | nonsummer
2024-04-09 22:00 | 2024-04-09 23:00 | Spring | FALSE | nonsummer
2024-04-09 23:00 | 2024-04-10 | Spring | FALSE | nonsummer
2024-04-10 | 2024-04-10 01:00 | Spring | FALSE | nonsummer
2024-04-10 01:00 | 2024-04-10 02:00 | Spring | FALSE | nonsummer
2024-04-10 02:00 | 2024-04-10 03:00 | Spring | FALSE | nonsummer
2024-04-10 03:00 | 2024-04-10 04:00 | Spring | FALSE | nonsummer
2024-04-10 04:00 | 2024-04-10 05:00 | Spring | FALSE | nonsummer
2024-04-10 05:00 | 2024-04-10 06:00 | Spring | FALSE | nonsummer
2024-04-10 06:00 | 2024-04-10 07:00 | Spring | FALSE | nonsummer
2024-04-10 07:00 | 2024-04-10 08:00 | Spring | FALSE | nonsummer
2024-04-10 08:00 | 2024-04-10 09:00 | Spring | FALSE | nonsummer
2024-04-10 09:00 | 2024-04-10 10:00 | Spring | FALSE | nonsummer
2024-04-10 10:00 | 2024-04-10 11:00 | Spring | FALSE | nonsummer
2024-04-10 11:00 | 2024-04-10 12:00 | Spring | FALSE | nonsummer
2024-04-10 12:00 | 2024-04-10 13:00 | Spring | FALSE | nonsummer
2024-04-10 13:00 | 2024-04-10 14:00 | Spring | FALSE | nonsummer
2024-04-10 14:00 | 2024-04-10 15:00 | Spring | FALSE | nonsummer
2024-04-10 15:00 | 2024-04-10 16:00 | Spring | FALSE | nonsummer
2024-04-10 16:00 | 2024-04-10 17:00 | Spring | FALSE | nonsummer
2024-04-10 17:00 | 2024-04-10 18:00 | Spring | TRUE | nonsummer
2024-04-10 18:00 | 2024-04-10 19:00 | Spring | TRUE | nonsummer
2024-04-10 19:00 | 2024-04-10 20:00 | Spring | TRUE | nonsummer
2024-04-10 20:00 | 2024-04-10 21:00 | Spring | TRUE | nonsummer
2024-04-10 21:00 | 2024-04-10 22:00 | Spring | TRUE | nonsummer
2024-04-10 22:00 | 2024-04-10 23:00 | Spring | FALSE | nonsummer
2024-04-10 23:00 | 2024-04-11 | Spring | FALSE | nonsummer
2024-04-11 | 2024-04-11 01:00 | Spring | FALSE | nonsummer
2024-04-11 01:00 | 2024-04-11 02:00 | Spring | FALSE | nonsummer
2024-04-11 02:00 | 2024-04-11 03:00 | Spring | FALSE | nonsummer
2024-04-11 03:00 | 2024-04-11 04:00 | Spring | FALSE | nonsummer
2024-04-11 04:00 | 2024-04-11 05:00 | Spring | FALSE | nonsummer
2024-04-11 05:00 | 2024-04-11 06:00 | Spring | FALSE | nonsummer
2024-04-11 06:00 | 2024-04-11 07:00 | Spring | FALSE | nonsummer
2024-04-11 07:00 | 2024-04-11 08:00 | Spring | FALSE | nonsummer
2024-04-11 08:00 | 2024-04-11 09:00 | Spring | FALSE | nonsummer
2024-04-11 09:00 | 2024-04-11 10:00 | Spring | FALSE | nonsummer
2024-04-11 10:00 | 2024-04-11 11:00 | Spring | FALSE | nonsummer
2024-04-11 11:00 | 2024-04-11 12:00 | Spring | FALSE | nonsummer
2024-04-11 12:00 | 2024-04-11 13:00 | Spring | FALSE | nonsummer
2024-04-11 13:00 | 2024-04-11 14:00 | Spring | FALSE | nonsummer
2024-04-11 14:00 | 2024-04-11 15:00 | Spring | FALSE | nonsummer
2024-04-11 15:00 | 2024-04-11 16:00 | Spring | FALSE | nonsummer
2024-04-11 16:00 | 2024-04-11 17:00 | Spring | FALSE | nonsummer
2024-04-11 17:00 | 2024-04-11 18:00 | Spring | TRUE | nonsummer
2024-04-11 18:00 | 2024-04-11 19:00 | Spring | TRUE | nonsummer
2024-04-11 19:00 | 2024-04-11 20:00 | Spring | TRUE | nonsummer
2024-04-11 20:00 | 2024-04-11 21:00 | Spring | TRUE | nonsummer
2024-04-11 21:00 | 2024-04-11 22:00 | Spring | TRUE | nonsummer
2024-04-11 22:00 | 2024-04-11 23:00 | Spring | FALSE | nonsummer
2024-04-11 23:00 | 2024-04-12 | Spring | FALSE | nonsummer
2024-04-12 | 2024-04-12 01:00 | Spring | FALSE | nonsummer
2024-04-12 01:00 | 2024-04-12 02:00 | Spring | FALSE | nonsummer
2024-04-12 02:00 | 2024-04-12 03:00 | Spring | FALSE | nonsummer
2024-04-12 03:00 | 2024-04-12 04:00 | Spring | FALSE | nonsummer
2024-04-12 04:00 | 2024-04-12 05:00 | Spring | FALSE | nonsummer
2024-04-12 05:00 | 2024-04-12 06:00 | Spring | FALSE | nonsummer
2024-04-12 06:00 | 2024-04-12 07:00 | Spring | FALSE | nonsummer
2024-04-12 07:00 | 2024-04-12 08:00 | Spring | FALSE | nonsummer
2024-04-12 08:00 | 2024-04-12 09:00 | Spring | FALSE | nonsummer
2024-04-12 09:00 | 2024-04-12 10:00 | Spring | FALSE | nonsummer
2024-04-12 10:00 | 2024-04-12 11:00 | Spring | FALSE | nonsummer
2024-04-12 11:00 | 2024-04-12 12:00 | Spring | FALSE | nonsummer
2024-04-12 12:00 | 2024-04-12 13:00 | Spring | FALSE | nonsummer
2024-04-12 13:00 | 2024-04-12 14:00 | Spring | FALSE | nonsummer
2024-04-12 14:00 | 2024-04-12 15:00 | Spring | FALSE | nonsummer
2024-04-12 15:00 | 2024-04-12 16:00 | Spring | FALSE | nonsummer
2024-04-12 16:00 | 2024-04-12 17:00 | Spring | FALSE | nonsummer
2024-04-12 17:00 | 2024-04-12 18:00 | Spring | TRUE | nonsummer
2024-04-12 18:00 | 2024-04-12 19:00 | Spring | TRUE | nonsummer
2024-04-12 19:00 | 2024-04-12 20:00 | Spring | TRUE | nonsummer
2024-04-12 20:00 | 2024-04-12 21:00 | Spring | TRUE | nonsummer
2024-04-12 21:00 | 2024-04-12 22:00 | Spring | TRUE | nonsummer
2024-04-12 22:00 | 2024-04-12 23:00 | Spring | FALSE | nonsummer
2024-04-12 23:00 | 2024-04-13 | Spring | FALSE | nonsummer
2024-04-13 | 2024-04-13 01:00 | Spring | FALSE | nonsummer
2024-04-13 01:00 | 2024-04-13 02:00 | Spring | FALSE | nonsummer
2024-04-13 02:00 | 2024-04-13 03:00 | Spring | FALSE | nonsummer
2024-04-13 03:00 | 2024-04-13 04:00 | Spring | FALSE | nonsummer
2024-04-13 04:00 | 2024-04-13 05:00 | Spring | FALSE | nonsummer
2024-04-13 05:00 | 2024-04-13 06:00 | Spring | FALSE | nonsummer
2024-04-13 06:00 | 2024-04-13 07:00 | Spring | FALSE | nonsummer
2024-04-13 07:00 | 2024-04-13 08:00 | Spring | FALSE | nonsummer
2024-04-13 08:00 | 2024-04-13 09:00 | Spring | FALSE | nonsummer
2024-04-13 09:00 | 2024-04-13 10:00 | Spring | FALSE | nonsummer
2024-04-13 10:00 | 2024-04-13 11:00 | Spring | FALSE | nonsummer
2024-04-13 11:00 | 2024-04-13 12:00 | Spring | FALSE | nonsummer
2024-04-13 12:00 | 2024-04-13 13:00 | Spring | FALSE | nonsummer
2024-04-13 13:00 | 2024-04-13 14:00 | Spring | FALSE | nonsummer
2024-04-13 14:00 | 2024-04-13 15:00 | Spring | FALSE | nonsummer
2024-04-13 15:00 | 2024-04-13 16:00 | Spring | FALSE | nonsummer
2024-04-13 16:00 | 2024-04-13 17:00 | Spring | FALSE | nonsummer
2024-04-13 17:00 | 2024-04-13 18:00 | Spring | TRUE | nonsummer
2024-04-13 18:00 | 2024-04-13 19:00 | Spring | TRUE | nonsummer
2024-04-13 19:00 | 2024-04-13 20:00 | Spring | TRUE | nonsummer
2024-04-13 20:00 | 2024-04-13 21:00 | Spring | TRUE | nonsummer
2024-04-13 21:00 | 2024-04-13 22:00 | Spring | TRUE | nonsummer
2024-04-13 22:00 | 2024-04-13 23:00 | Spring | FALSE | nonsummer
2024-04-13 23:00 | 2024-04-14 | Spring | FALSE | nonsummer
2024-04-14 | 2024-04-14 01:00 | Spring | FALSE | nonsummer
2024-04-14 01:00 | 2024-04-14 02:00 | Spring | FALSE | nonsummer
2024-04-14 02:00 | 2024-04-14 03:00 | Spring | FALSE | nonsummer
2024-04-14 03:00 | 2024-04-14 04:00 | Spring | FALSE | nonsummer
2024-04-14 04:00 | 2024-04-14 05:00 | Spring | FALSE | nonsummer
2024-04-14 05:00 | 2024-04-14 06:00 | Spring | FALSE | nonsummer
2024-04-14 06:00 | 2024-04-14 07:00 | Spring | FALSE | nonsummer
2024-04-14 07:00 | 2024-04-14 08:00 | Spring | FALSE | nonsummer
2024-04-14 08:00 | 2024-04-14 09:00 | Spring | FALSE | nonsummer
2024-04-14 09:00 | 2024-04-14 10:00 | Spring | FALSE | nonsummer
2024-04-14 10:00 | 2024-04-14 11:00 | Spring | FALSE | nonsummer
2024-04-14 11:00 | 2024-04-14 12:00 | Spring | FALSE | nonsummer
2024-04-14 12:00 | 2024-04-14 13:00 | Spring | FALSE | nonsummer
2024-04-14 13:00 | 2024-04-14 14:00 | Spring | FALSE | nonsummer
2024-04-14 14:00 | 2024-04-14 15:00 | Spring | FALSE | nonsummer
2024-04-14 15:00 | 2024-04-14 16:00 | Spring | FALSE | nonsummer
2024-04-14 16:00 | 2024-04-14 17:00 | Spring | FALSE | nonsummer
2024-04-14 17:00 | 2024-04-14 18:00 | Spring | TRUE | nonsummer
2024-04-14 18:00 | 2024-04-14 19:00 | Spring | TRUE | nonsummer
2024-04-14 19:00 | 2024-04-14 20:00 | Spring | TRUE | nonsummer
2024-04-14 20:00 | 2024-04-14 21:00 | Spring | TRUE | nonsummer
2024-04-14 21:00 | 2024-04-14 22:00 | Spring | TRUE | nonsummer
2024-04-14 22:00 | 2024-04-14 23:00 | Spring | FALSE | nonsummer
2024-04-14 23:00 | 2024-04-15 | Spring | FALSE | nonsummer
2024-04-15 | 2024-04-15 01:00 | Spring | FALSE | nonsummer
2024-04-15 01:00 | 2024-04-15 02:00 | Spring | FALSE | nonsummer
2024-04-15 02:00 | 2024-04-15 03:00 | Spring | FALSE | nonsummer
2024-04-15 03:00 | 2024-04-15 04:00 | Spring | FALSE | nonsummer
2024-04-15 04:00 | 2024-04-15 05:00 | Spring | FALSE | nonsummer
2024-04-15 05:00 | 2024-04-15 06:00 | Spring | FALSE | nonsummer
2024-04-15 06:00 | 2024-04-15 07:00 | Spring | FALSE | nonsummer
2024-04-15 07:00 | 2024-04-15 08:00 | Spring | FALSE | nonsummer
2024-04-15 08:00 | 2024-04-15 09:00 | Spring | FALSE | nonsummer
2024-04-15 09:00 | 2024-04-15 10:00 | Spring | FALSE | nonsummer
2024-04-15 10:00 | 2024-04-15 11:00 | Spring | FALSE | nonsummer
2024-04-15 11:00 | 2024-04-15 12:00 | Spring | FALSE | nonsummer
2024-04-15 12:00 | 2024-04-15 13:00 | Spring | FALSE | nonsummer
2024-04-15 13:00 | 2024-04-15 14:00 | Spring | FALSE | nonsummer
2024-04-15 14:00 | 2024-04-15 15:00 | Spring | FALSE | nonsummer
2024-04-15 15:00 | 2024-04-15 16:00 | Spring | FALSE | nonsummer
2024-04-15 16:00 | 2024-04-15 17:00 | Spring | FALSE | nonsummer
2024-04-15 17:00 | 2024-04-15 18:00 | Spring | TRUE | nonsummer
2024-04-15 18:00 | 2024-04-15 19:00 | Spring | TRUE | nonsummer
2024-04-15 19:00 | 2024-04-15 20:00 | Spring | TRUE | nonsummer
2024-04-15 20:00 | 2024-04-15 21:00 | Spring | TRUE | nonsummer
2024-04-15 21:00 | 2024-04-15 22:00 | Spring | TRUE | nonsummer
2024-04-15 22:00 | 2024-04-15 23:00 | Spring | FALSE | nonsummer
2024-04-15 23:00 | 2024-04-16 | Spring | FALSE | nonsummer
2024-04-16 | 2024-04-16 01:00 | Spring | FALSE | nonsummer
2024-04-16 01:00 | 2024-04-16 02:00 | Spring | FALSE | nonsummer
2024-04-16 02:00 | 2024-04-16 03:00 | Spring | FALSE | nonsummer
2024-04-16 03:00 | 2024-04-16 04:00 | Spring | FALSE | nonsummer
2024-04-16 04:00 | 2024-04-16 05:00 | Spring | FALSE | nonsummer
2024-04-16 05:00 | 2024-04-16 06:00 | Spring | FALSE | nonsummer
2024-04-16 06:00 | 2024-04-16 07:00 | Spring | FALSE | nonsummer
2024-04-16 07:00 | 2024-04-16 08:00 | Spring | FALSE | nonsummer
2024-04-16 08:00 | 2024-04-16 09:00 | Spring | FALSE | nonsummer
2024-04-16 09:00 | 2024-04-16 10:00 | Spring | FALSE | nonsummer
2024-04-16 10:00 | 2024-04-16 11:00 | Spring | FALSE | nonsummer
2024-04-16 11:00 | 2024-04-16 12:00 | Spring | FALSE | nonsummer
2024-04-16 12:00 | 2024-04-16 13:00 | Spring | FALSE | nonsummer
2024-04-16 13:00 | 2024-04-16 14:00 | Spring | FALSE | nonsummer
2024-04-16 14:00 | 2024-04-16 15:00 | Spring | FALSE | nonsummer
2024-04-16 15:00 | 2024-04-16 16:00 | Spring | FALSE | nonsummer
2024-04-16 16:00 | 2024-04-16 17:00 | Spring | FALSE | nonsummer
2024-04-16 17:00 | 2024-04-16 18:00 | Spring | TRUE | nonsummer
2024-04-16 18:00 | 2024-04-16 19:00 | Spring | TRUE | nonsummer
2024-04-16 19:00 | 2024-04-16 20:00 | Spring | TRUE | nonsummer
2024-04-16 20:00 | 2024-04-16 21:00 | Spring | TRUE | nonsummer
2024-04-16 21:00 | 2024-04-16 22:00 | Spring | TRUE | nonsummer
2024-04-16 22:00 | 2024-04-16 23:00 | Spring | FALSE | nonsummer
2024-04-16 23:00 | 2024-04-17 | Spring | FALSE | nonsummer
2024-04-17 | 2024-04-17 01:00 | Spring | FALSE | nonsummer
2024-04-17 01:00 | 2024-04-17 02:00 | Spring | FALSE | nonsummer
2024-04-17 02:00 | 2024-04-17 03:00 | Spring | FALSE | nonsummer
2024-04-17 03:00 | 2024-04-17 04:00 | Spring | FALSE | nonsummer
2024-04-17 04:00 | 2024-04-17 05:00 | Spring | FALSE | nonsummer
2024-04-17 05:00 | 2024-04-17 06:00 | Spring | FALSE | nonsummer
2024-04-17 06:00 | 2024-04-17 07:00 | Spring | FALSE | nonsummer
2024-04-17 07:00 | 2024-04-17 08:00 | Spring | FALSE | nonsummer
2024-04-17 08:00 | 2024-04-17 09:00 | Spring | FALSE | nonsummer
2024-04-17 09:00 | 2024-04-17 10:00 | Spring | FALSE | nonsummer
2024-04-17 10:00 | 2024-04-17 11:00 | Spring | FALSE | nonsummer
2024-04-17 11:00 | 2024-04-17 12:00 | Spring | FALSE | nonsummer
2024-04-17 12:00 | 2024-04-17 13:00 | Spring | FALSE | nonsummer
2024-04-17 13:00 | 2024-04-17 14:00 | Spring | FALSE | nonsummer
2024-04-17 14:00 | 2024-04-17 15:00 | Spring | FALSE | nonsummer
2024-04-17 15:00 | 2024-04-17 16:00 | Spring | FALSE | nonsummer
2024-04-17 16:00 | 2024-04-17 17:00 | Spring | FALSE | nonsummer
2024-04-17 17:00 | 2024-04-17 18:00 | Spring | TRUE | nonsummer
2024-04-17 18:00 | 2024-04-17 19:00 | Spring | TRUE | nonsummer
2024-04-17 19:00 | 2024-04-17 20:00 | Spring | TRUE | nonsummer
2024-04-17 20:00 | 2024-04-17 21:00 | Spring | TRUE | nonsummer
2024-04-17 21:00 | 2024-04-17 22:00 | Spring | TRUE | nonsummer
2024-04-17 22:00 | 2024-04-17 23:00 | Spring | FALSE | nonsummer
2024-04-17 23:00 | 2024-04-18 | Spring | FALSE | nonsummer
2024-04-18 | 2024-04-18 01:00 | Spring | FALSE | nonsummer
2024-04-18 01:00 | 2024-04-18 02:00 | Spring | FALSE | nonsummer
2024-04-18 02:00 | 2024-04-18 03:00 | Spring | FALSE | nonsummer
2024-04-18 03:00 | 2024-04-18 04:00 | Spring | FALSE | nonsummer
2024-04-18 04:00 | 2024-04-18 05:00 | Spring | FALSE | nonsummer
2024-04-18 05:00 | 2024-04-18 06:00 | Spring | FALSE | nonsummer
2024-04-18 06:00 | 2024-04-18 07:00 | Spring | FALSE | nonsummer
2024-04-18 07:00 | 2024-04-18 08:00 | Spring | FALSE | nonsummer
2024-04-18 08:00 | 2024-04-18 09:00 | Spring | FALSE | nonsummer
2024-04-18 09:00 | 2024-04-18 10:00 | Spring | FALSE | nonsummer
2024-04-18 10:00 | 2024-04-18 11:00 | Spring | FALSE | nonsummer
2024-04-18 11:00 | 2024-04-18 12:00 | Spring | FALSE | nonsummer
2024-04-18 12:00 | 2024-04-18 13:00 | Spring | FALSE | nonsummer
2024-04-18 13:00 | 2024-04-18 14:00 | Spring | FALSE | nonsummer
2024-04-18 14:00 | 2024-04-18 15:00 | Spring | FALSE | nonsummer
2024-04-18 15:00 | 2024-04-18 16:00 | Spring | FALSE | nonsummer
2024-04-18 16:00 | 2024-04-18 17:00 | Spring | FALSE | nonsummer
2024-04-18 17:00 | 2024-04-18 18:00 | Spring | TRUE | nonsummer
2024-04-18 18:00 | 2024-04-18 19:00 | Spring | TRUE | nonsummer
2024-04-18 19:00 | 2024-04-18 20:00 | Spring | TRUE | nonsummer
2024-04-18 20:00 | 2024-04-18 21:00 | Spring | TRUE | nonsummer
2024-04-18 21:00 | 2024-04-18 22:00 | Spring | TRUE | nonsummer
2024-04-18 22:00 | 2024-04-18 23:00 | Spring | FALSE | nonsummer
2024-04-18 23:00 | 2024-04-19 | Spring | FALSE | nonsummer
2024-04-19 | 2024-04-19 01:00 | Spring | FALSE | nonsummer
2024-04-19 01:00 | 2024-04-19 02:00 | Spring | FALSE | nonsummer
2024-04-19 02:00 | 2024-04-19 03:00 | Spring | FALSE | nonsummer
2024-04-19 03:00 | 2024-04-19 04:00 | Spring | FALSE | nonsummer
2024-04-19 04:00 | 2024-04-19 05:00 | Spring | FALSE | nonsummer
2024-04-19 05:00 | 2024-04-19 06:00 | Spring | FALSE | nonsummer
2024-04-19 06:00 | 2024-04-19 07:00 | Spring | FALSE | nonsummer
2024-04-19 07:00 | 2024-04-19 08:00 | Spring | FALSE | nonsummer
2024-04-19 08:00 | 2024-04-19 09:00 | Spring | FALSE | nonsummer
2024-04-19 09:00 | 2024-04-19 10:00 | Spring | FALSE | nonsummer
2024-04-19 10:00 | 2024-04-19 11:00 | Spring | FALSE | nonsummer
2024-04-19 11:00 | 2024-04-19 12:00 | Spring | FALSE | nonsummer
2024-04-19 12:00 | 2024-04-19 13:00 | Spring | FALSE | nonsummer
2024-04-19 13:00 | 2024-04-19 14:00 | Spring | FALSE | nonsummer
2024-04-19 14:00 | 2024-04-19 15:00 | Spring | FALSE | nonsummer
2024-04-19 15:00 | 2024-04-19 16:00 | Spring | FALSE | nonsummer
2024-04-19 16:00 | 2024-04-19 17:00 | Spring | FALSE | nonsummer
2024-04-19 17:00 | 2024-04-19 18:00 | Spring | TRUE | nonsummer
2024-04-19 18:00 | 2024-04-19 19:00 | Spring | TRUE | nonsummer
2024-04-19 19:00 | 2024-04-19 20:00 | Spring | TRUE | nonsummer
2024-04-19 20:00 | 2024-04-19 21:00 | Spring | TRUE | nonsummer
2024-04-19 21:00 | 2024-04-19 22:00 | Spring | TRUE | nonsummer
2024-04-19 22:00 | 2024-04-19 23:00 | Spring | FALSE | nonsummer
2024-04-19 23:00 | 2024-04-20 | Spring | FALSE | nonsummer
2024-04-20 | 2024-04-20 01:00 | Spring | FALSE | nonsummer
2024-04-20 01:00 | 2024-04-20 02:00 | Spring | FALSE | nonsummer
2024-04-20 02:00 | 2024-04-20 03:00 | Spring | FALSE | nonsummer
2024-04-20 03:00 | 2024-04-20 04:00 | Spring | FALSE | nonsummer
2024-04-20 04:00 | 2024-04-20 05:00 | Spring | FALSE | nonsummer
2024-04-20 05:00 | 2024-04-20 06:00 | Spring | FALSE | nonsummer
2024-04-20 06:00 | 2024-04-20 07:00 | Spring | FALSE | nonsummer
2024-04-20 07:00 | 2024-04-20 08:00 | Spring | FALSE | nonsummer
2024-04-20 08:00 | 2024-04-20 09:00 | Spring | FALSE | nonsummer
2024-04-20 09:00 | 2024-04-20 10:00 | Spring | FALSE | nonsummer
2024-04-20 10:00 | 2024-04-20 11:00 | Spring | FALSE | nonsummer
2024-04-20 11:00 | 2024-04-20 12:00 | Spring | FALSE | nonsummer
2024-04-20 12:00 | 2024-04-20 13:00 | Spring | FALSE | nonsummer
2024-04-20 13:00 | 2024-04-20 14:00 | Spring | FALSE | nonsummer
2024-04-20 14:00 | 2024-04-20 15:00 | Spring | FALSE | nonsummer
2024-04-20 15:00 | 2024-04-20 16:00 | Spring | FALSE | nonsummer
2024-04-20 16:00 | 2024-04-20 17:00 | Spring | FALSE | nonsummer
2024-04-20 17:00 | 2024-04-20 18:00 | Spring | TRUE | nonsummer
2024-04-20 18:00 | 2024-04-20 19:00 | Spring | TRUE | nonsummer
2024-04-20 19:00 | 2024-04-20 20:00 | Spring | TRUE | nonsummer
2024-04-20 20:00 | 2024-04-20 21:00 | Spring | TRUE | nonsummer
2024-04-20 21:00 | 2024-04-20 22:00 | Spring | TRUE | nonsummer
2024-04-20 22:00 | 2024-04-20 23:00 | Spring | FALSE | nonsummer
2024-04-20 23:00 | 2024-04-21 | Spring | FALSE | nonsummer
2024-04-21 | 2024-04-21 01:00 | Spring | FALSE | nonsummer
2024-04-21 01:00 | 2024-04-21 02:00 | Spring | FALSE | nonsummer
2024-04-21 02:00 | 2024-04-21 03:00 | Spring | FALSE | nonsummer
2024-04-21 03:00 | 2024-04-21 04:00 | Spring | FALSE | nonsummer
2024-04-21 04:00 | 2024-04-21 05:00 | Spring | FALSE | nonsummer
2024-04-21 05:00 | 2024-04-21 06:00 | Spring | FALSE | nonsummer
2024-04-21 06:00 | 2024-04-21 07:00 | Spring | FALSE | nonsummer
2024-04-21 07:00 | 2024-04-21 08:00 | Spring | FALSE | nonsummer
2024-04-21 08:00 | 2024-04-21 09:00 | Spring | FALSE | nonsummer
2024-04-21 09:00 | 2024-04-21 10:00 | Spring | FALSE | nonsummer
2024-04-21 10:00 | 2024-04-21 11:00 | Spring | FALSE | nonsummer
2024-04-21 11:00 | 2024-04-21 12:00 | Spring | FALSE | nonsummer
2024-04-21 12:00 | 2024-04-21 13:00 | Spring | FALSE | nonsummer
2024-04-21 13:00 | 2024-04-21 14:00 | Spring | FALSE | nonsummer
2024-04-21 14:00 | 2024-04-21 15:00 | Spring | FALSE | nonsummer
2024-04-21 15:00 | 2024-04-21 16:00 | Spring | FALSE | nonsummer
2024-04-21 16:00 | 2024-04-21 17:00 | Spring | FALSE | nonsummer
2024-04-21 17:00 | 2024-04-21 18:00 | Spring | TRUE | nonsummer
2024-04-21 18:00 | 2024-04-21 19:00 | Spring | TRUE | nonsummer
2024-04-21 19:00 | 2024-04-21 20:00 | Spring | TRUE | nonsummer
2024-04-21 20:00 | 2024-04-21 21:00 | Spring | TRUE | nonsummer
2024-04-21 21:00 | 2024-04-21 22:00 | Spring | TRUE | nonsummer
2024-04-21 22:00 | 2024-04-21 23:00 | Spring | FALSE | nonsummer
2024-04-21 23:00 | 2024-04-22 | Spring | FALSE | nonsummer
2024-04-22 | 2024-04-22 01:00 | Spring | FALSE | nonsummer
2024-04-22 01:00 | 2024-04-22 02:00 | Spring | FALSE | nonsummer
2024-04-22 02:00 | 2024-04-22 03:00 | Spring | FALSE | nonsummer
2024-04-22 03:00 | 2024-04-22 04:00 | Spring | FALSE | nonsummer
2024-04-22 04:00 | 2024-04-22 05:00 | Spring | FALSE | nonsummer
2024-04-22 05:00 | 2024-04-22 06:00 | Spring | FALSE | nonsummer
2024-04-22 06:00 | 2024-04-22 07:00 | Spring | FALSE | nonsummer
2024-04-22 07:00 | 2024-04-22 08:00 | Spring | FALSE | nonsummer
2024-04-22 08:00 | 2024-04-22 09:00 | Spring | FALSE | nonsummer
2024-04-22 09:00 | 2024-04-22 10:00 | Spring | FALSE | nonsummer
2024-04-22 10:00 | 2024-04-22 11:00 | Spring | FALSE | nonsummer
2024-04-22 11:00 | 2024-04-22 12:00 | Spring | FALSE | nonsummer
2024-04-22 12:00 | 2024-04-22 13:00 | Spring | FALSE | nonsummer
2024-04-22 13:00 | 2024-04-22 14:00 | Spring | FALSE | nonsummer
2024-04-22 14:00 | 2024-04-22 15:00 | Spring | FALSE | nonsummer
2024-04-22 15:00 | 2024-04-22 16:00 | Spring | FALSE | nonsummer
2024-04-22 16:00 | 2024-04-22 17:00 | Spring | FALSE | nonsummer
2024-04-22 17:00 | 2024-04-22 18:00 | Spring | TRUE | nonsummer
2024-04-22 18:00 | 2024-04-22 19:00 | Spring | TRUE | nonsummer
2024-04-22 19:00 | 2024-04-22 20:00 | Spring | TRUE | nonsummer
2024-04-22 20:00 | 2024-04-22 21:00 | Spring | TRUE | nonsummer
2024-04-22 21:00 | 2024-04-22 22:00 | Spring | TRUE | nonsummer
2024-04-22 22:00 | 2024-04-22 23:00 | Spring | FALSE | nonsummer
2024-04-22 23:00 | 2024-04-23 | Spring | FALSE | nonsummer
2024-04-23 | 2024-04-23 01:00 | Spring | FALSE | nonsummer
2024-04-23 01:00 | 2024-04-23 02:00 | Spring | FALSE | nonsummer
2024-04-23 02:00 | 2024-04-23 03:00 | Spring | FALSE | nonsummer
2024-04-23 03:00 | 2024-04-23 04:00 | Spring | FALSE | nonsummer
2024-04-23 04:00 | 2024-04-23 05:00 | Spring | FALSE | nonsummer
2024-04-23 05:00 | 2024-04-23 06:00 | Spring | FALSE | nonsummer
2024-04-23 06:00 | 2024-04-23 07:00 | Spring | FALSE | nonsummer
2024-04-23 07:00 | 2024-04-23 08:00 | Spring | FALSE | nonsummer
2024-04-23 08:00 | 2024-04-23 09:00 | Spring | FALSE | nonsummer
2024-04-23 09:00 | 2024-04-23 10:00 | Spring | FALSE | nonsummer
2024-04-23 10:00 | 2024-04-23 11:00 | Spring | FALSE | nonsummer
2024-04-23 11:00 | 2024-04-23 12:00 | Spring | FALSE | nonsummer
2024-04-23 12:00 | 2024-04-23 13:00 | Spring | FALSE | nonsummer
2024-04-23 13:00 | 2024-04-23 14:00 | Spring | FALSE | nonsummer
2024-04-23 14:00 | 2024-04-23 15:00 | Spring | FALSE | nonsummer
2024-04-23 15:00 | 2024-04-23 16:00 | Spring | FALSE | nonsummer
2024-04-23 16:00 | 2024-04-23 17:00 | Spring | FALSE | nonsummer
2024-04-23 17:00 | 2024-04-23 18:00 | Spring | TRUE | nonsummer
2024-04-23 18:00 | 2024-04-23 19:00 | Spring | TRUE | nonsummer
2024-04-23 19:00 | 2024-04-23 20:00 | Spring | TRUE | nonsummer
2024-04-23 20:00 | 2024-04-23 21:00 | Spring | TRUE | nonsummer
2024-04-23 21:00 | 2024-04-23 22:00 | Spring | TRUE | nonsummer
2024-04-23 22:00 | 2024-04-23 23:00 | Spring | FALSE | nonsummer
2024-04-23 23:00 | 2024-04-24 | Spring | FALSE | nonsummer
2024-04-24 | 2024-04-24 01:00 | Spring | FALSE | nonsummer
2024-04-24 01:00 | 2024-04-24 02:00 | Spring | FALSE | nonsummer
2024-04-24 02:00 | 2024-04-24 03:00 | Spring | FALSE | nonsummer
2024-04-24 03:00 | 2024-04-24 04:00 | Spring | FALSE | nonsummer
2024-04-24 04:00 | 2024-04-24 05:00 | Spring | FALSE | nonsummer
2024-04-24 05:00 | 2024-04-24 06:00 | Spring | FALSE | nonsummer
2024-04-24 06:00 | 2024-04-24 07:00 | Spring | FALSE | nonsummer
2024-04-24 07:00 | 2024-04-24 08:00 | Spring | FALSE | nonsummer
2024-04-24 08:00 | 2024-04-24 09:00 | Spring | FALSE | nonsummer
2024-04-24 09:00 | 2024-04-24 10:00 | Spring | FALSE | nonsummer
2024-04-24 10:00 | 2024-04-24 11:00 | Spring | FALSE | nonsummer
2024-04-24 11:00 | 2024-04-24 12:00 | Spring | FALSE | nonsummer
2024-04-24 12:00 | 2024-04-24 13:00 | Spring | FALSE | nonsummer
2024-04-24 13:00 | 2024-04-24 14:00 | Spring | FALSE | nonsummer
2024-04-24 14:00 | 2024-04-24 15:00 | Spring | FALSE | nonsummer
2024-04-24 15:00 | 2024-04-24 16:00 | Spring | FALSE | nonsummer
2024-04-24 16:00 | 2024-04-24 17:00 | Spring | FALSE | nonsummer
2024-04-24 17:00 | 2024-04-24 18:00 | Spring | TRUE | nonsummer
2024-04-24 18:00 | 2024-04-24 19:00 | Spring | TRUE | nonsummer
2024-04-24 19:00 | 2024-04-24 20:00 | Spring | TRUE | nonsummer
2024-04-24 20:00 | 2024-04-24 21:00 | Spring | TRUE | nonsummer
2024-04-24 21:00 | 2024-04-24 22:00 | Spring | TRUE | nonsummer
2024-04-24 22:00 | 2024-04-24 23:00 | Spring | FALSE | nonsummer
2024-04-24 23:00 | 2024-04-25 | Spring | FALSE | nonsummer
2024-04-25 | 2024-04-25 01:00 | Spring | FALSE | nonsummer
2024-04-25 01:00 | 2024-04-25 02:00 | Spring | FALSE | nonsummer
2024-04-25 02:00 | 2024-04-25 03:00 | Spring | FALSE | nonsummer
2024-04-25 03:00 | 2024-04-25 04:00 | Spring | FALSE | nonsummer
2024-04-25 04:00 | 2024-04-25 05:00 | Spring | FALSE | nonsummer
2024-04-25 05:00 | 2024-04-25 06:00 | Spring | FALSE | nonsummer
2024-04-25 06:00 | 2024-04-25 07:00 | Spring | FALSE | nonsummer
2024-04-25 07:00 | 2024-04-25 08:00 | Spring | FALSE | nonsummer
2024-04-25 08:00 | 2024-04-25 09:00 | Spring | FALSE | nonsummer
2024-04-25 09:00 | 2024-04-25 10:00 | Spring | FALSE | nonsummer
2024-04-25 10:00 | 2024-04-25 11:00 | Spring | FALSE | nonsummer
2024-04-25 11:00 | 2024-04-25 12:00 | Spring | FALSE | nonsummer
2024-04-25 12:00 | 2024-04-25 13:00 | Spring | FALSE | nonsummer
2024-04-25 13:00 | 2024-04-25 14:00 | Spring | FALSE | nonsummer
2024-04-25 14:00 | 2024-04-25 15:00 | Spring | FALSE | nonsummer
2024-04-25 15:00 | 2024-04-25 16:00 | Spring | FALSE | nonsummer
2024-04-25 16:00 | 2024-04-25 17:00 | Spring | FALSE | nonsummer
2024-04-25 17:00 | 2024-04-25 18:00 | Spring | TRUE | nonsummer
2024-04-25 18:00 | 2024-04-25 19:00 | Spring | TRUE | nonsummer
2024-04-25 19:00 | 2024-04-25 20:00 | Spring | TRUE | nonsummer
2024-04-25 20:00 | 2024-04-25 21:00 | Spring | TRUE | nonsummer
2024-04-25 21:00 | 2024-04-25 22:00 | Spring | TRUE | nonsummer
2024-04-25 22:00 | 2024-04-25 23:00 | Spring | FALSE | nonsummer
2024-04-25 23:00 | 2024-04-26 | Spring | FALSE | nonsummer
2024-04-26 | 2024-04-26 01:00 | Spring | FALSE | nonsummer
2024-04-26 01:00 | 2024-04-26 02:00 | Spring | FALSE | nonsummer
2024-04-26 02:00 | 2024-04-26 03:00 | Spring | FALSE | nonsummer
2024-04-26 03:00 | 2024-04-26 04:00 | Spring | FALSE | nonsummer
2024-04-26 04:00 | 2024-04-26 05:00 | Spring | FALSE | nonsummer
2024-04-26 05:00 | 2024-04-26 06:00 | Spring | FALSE | nonsummer
2024-04-26 06:00 | 2024-04-26 07:00 | Spring | FALSE | nonsummer
2024-04-26 07:00 | 2024-04-26 08:00 | Spring | FALSE | nonsummer
2024-04-26 08:00 | 2024-04-26 09:00 | Spring | FALSE | nonsummer
2024-04-26 09:00 | 2024-04-26 10:00 | Spring | FALSE | nonsummer
2024-04-26 10:00 | 2024-04-26 11:00 | Spring | FALSE | nonsummer
2024-04-26 11:00 | 2024-04-26 12:00 | Spring | FALSE | nonsummer
2024-04-26 12:00 | 2024-04-26 13:00 | Spring | FALSE | nonsummer
2024-04-26 13:00 | 2024-04-26 14:00 | Spring | FALSE | nonsummer
2024-04-26 14:00 | 2024-04-26 15:00 | Spring | FALSE | nonsummer
2024-04-26 15:00 | 2024-04-26 16:00 | Spring | FALSE | nonsummer
2024-04-26 16:00 | 2024-04-26 17:00 | Spring | FALSE | nonsummer
2024-04-26 17:00 | 2024-04-26 18:00 | Spring | TRUE | nonsummer
2024-04-26 18:00 | 2024-04-26 19:00 | Spring | TRUE | nonsummer
2024-04-26 19:00 | 2024-04-26 20:00 | Spring | TRUE | nonsummer
2024-04-26 20:00 | 2024-04-26 21:00 | Spring | TRUE | nonsummer
2024-04-26 21:00 | 2024-04-26 22:00 | Spring | TRUE | nonsummer
2024-04-26 22:00 | 2024-04-26 23:00 | Spring | FALSE | nonsummer
2024-04-26 23:00 | 2024-04-27 | Spring | FALSE | nonsummer
2024-04-27 | 2024-04-27 01:00 | Spring | FALSE | nonsummer
2024-04-27 01:00 | 2024-04-27 02:00 | Spring | FALSE | nonsummer
2024-04-27 02:00 | 2024-04-27 03:00 | Spring | FALSE | nonsummer
2024-04-27 03:00 | 2024-04-27 04:00 | Spring | FALSE | nonsummer
2024-04-27 04:00 | 2024-04-27 05:00 | Spring | FALSE | nonsummer
2024-04-27 05:00 | 2024-04-27 06:00 | Spring | FALSE | nonsummer
2024-04-27 06:00 | 2024-04-27 07:00 | Spring | FALSE | nonsummer
2024-04-27 07:00 | 2024-04-27 08:00 | Spring | FALSE | nonsummer
2024-04-27 08:00 | 2024-04-27 09:00 | Spring | FALSE | nonsummer
2024-04-27 09:00 | 2024-04-27 10:00 | Spring | FALSE | nonsummer
2024-04-27 10:00 | 2024-04-27 11:00 | Spring | FALSE | nonsummer
2024-04-27 11:00 | 2024-04-27 12:00 | Spring | FALSE | nonsummer
2024-04-27 12:00 | 2024-04-27 13:00 | Spring | FALSE | nonsummer
2024-04-27 13:00 | 2024-04-27 14:00 | Spring | FALSE | nonsummer
2024-04-27 14:00 | 2024-04-27 15:00 | Spring | FALSE | nonsummer
2024-04-27 15:00 | 2024-04-27 16:00 | Spring | FALSE | nonsummer
2024-04-27 16:00 | 2024-04-27 17:00 | Spring | FALSE | nonsummer
2024-04-27 17:00 | 2024-04-27 18:00 | Spring | TRUE | nonsummer
2024-04-27 18:00 | 2024-04-27 19:00 | Spring | TRUE | nonsummer
2024-04-27 19:00 | 2024-04-27 20:00 | Spring | TRUE | nonsummer
2024-04-27 20:00 | 2024-04-27 21:00 | Spring | TRUE | nonsummer
2024-04-27 21:00 | 2024-04-27 22:00 | Spring | TRUE | nonsummer
2024-04-27 22:00 | 2024-04-27 23:00 | Spring | FALSE | nonsummer
2024-04-27 23:00 | 2024-04-28 | Spring | FALSE | nonsummer
2024-04-28 | 2024-04-28 01:00 | Spring | FALSE | nonsummer
2024-04-28 01:00 | 2024-04-28 02:00 | Spring | FALSE | nonsummer
2024-04-28 02:00 | 2024-04-28 03:00 | Spring | FALSE | nonsummer
2024-04-28 03:00 | 2024-04-28 04:00 | Spring | FALSE | nonsummer
2024-04-28 04:00 | 2024-04-28 05:00 | Spring | FALSE | nonsummer
2024-04-28 05:00 | 2024-04-28 06:00 | Spring | FALSE | nonsummer
2024-04-28 06:00 | 2024-04-28 07:00 | Spring | FALSE | nonsummer
2024-04-28 07:00 | 2024-04-28 08:00 | Spring | FALSE | nonsummer
2024-04-28 08:00 | 2024-04-28 09:00 | Spring | FALSE | nonsummer
2024-04-28 09:00 | 2024-04-28 10:00 | Spring | FALSE | nonsummer
2024-04-28 10:00 | 2024-04-28 11:00 | Spring | FALSE | nonsummer
2024-04-28 11:00 | 2024-04-28 12:00 | Spring | FALSE | nonsummer
2024-04-28 12:00 | 2024-04-28 13:00 | Spring | FALSE | nonsummer
2024-04-28 13:00 | 2024-04-28 14:00 | Spring | FALSE | nonsummer
2024-04-28 14:00 | 2024-04-28 15:00 | Spring | FALSE | nonsummer
2024-04-28 15:00 | 2024-04-28 16:00 | Spring | FALSE | nonsummer
2024-04-28 16:00 | 2024-04-28 17:00 | Spring | FALSE | nonsummer
2024-04-28 17:00 | 2024-04-28 18:00 | Spring | TRUE | nonsummer
2024-04-28 18:00 | 2024-04-28 19:00 | Spring | TRUE | nonsummer
2024-04-28 19:00 | 2024-04-28 20:00 | Spring | TRUE | nonsummer
2024-04-28 20:00 | 2024-04-28 21:00 | Spring | TRUE | nonsummer
2024-04-28 21:00 | 2024-04-28 22:00 | Spring | TRUE | nonsummer
2024-04-28 22:00 | 2024-04-28 23:00 | Spring | FALSE | nonsummer
2024-04-28 23:00 | 2024-04-29 | Spring | FALSE | nonsummer
2024-04-29 | 2024-04-29 01:00 | Spring | FALSE | nonsummer
2024-04-29 01:00 | 2024-04-29 02:00 | Spring | FALSE | nonsummer
2024-04-29 02:00 | 2024-04-29 03:00 | Spring | FALSE | nonsummer
2024-04-29 03:00 | 2024-04-29 04:00 | Spring | FALSE | nonsummer
2024-04-29 04:00 | 2024-04-29 05:00 | Spring | FALSE | nonsummer
2024-04-29 05:00 | 2024-04-29 06:00 | Spring | FALSE | nonsummer
2024-04-29 06:00 | 2024-04-29 07:00 | Spring | FALSE | nonsummer
2024-04-29 07:00 | 2024-04-29 08:00 | Spring | FALSE | nonsummer
2024-04-29 08:00 | 2024-04-29 09:00 | Spring | FALSE | nonsummer
2024-04-29 09:00 | 2024-04-29 10:00 | Spring | FALSE | nonsummer
2024-04-29 10:00 | 2024-04-29 11:00 | Spring | FALSE | nonsummer
2024-04-29 11:00 | 2024-04-29 12:00 | Spring | FALSE | nonsummer
2024-04-29 12:00 | 2024-04-29 13:00 | Spring | FALSE | nonsummer
2024-04-29 13:00 | 2024-04-29 14:00 | Spring | FALSE | nonsummer
2024-04-29 14:00 | 2024-04-29 15:00 | Spring | FALSE | nonsummer
2024-04-29 15:00 | 2024-04-29 16:00 | Spring | FALSE | nonsummer
2024-04-29 16:00 | 2024-04-29 17:00 | Spring | FALSE | nonsummer
2024-04-29 17:00 | 2024-04-29 18:00 | Spring | TRUE | nonsummer
2024-04-29 18:00 | 2024-04-29 19:00 | Spring | TRUE | nonsummer
2024-04-29 19:00 | 2024-04-29 20:00 | Spring | TRUE | nonsummer
2024-04-29 20:00 | 2024-04-29 21:00 | Spring | TRUE | nonsummer
2024-04-29 21:00 | 2024-04-29 22:00 | Spring | TRUE | nonsummer
2024-04-29 22:00 | 2024-04-29 23:00 | Spring | FALSE | nonsummer
2024-04-29 23:00 | 2024-04-30 | Spring | FALSE | nonsummer
2024-04-30 | 2024-04-30 01:00 | Spring | FALSE | nonsummer
2024-04-30 01:00 | 2024-04-30 02:00 | Spring | FALSE | nonsummer
2024-04-30 02:00 | 2024-04-30 03:00 | Spring | FALSE | nonsummer
2024-04-30 03:00 | 2024-04-30 04:00 | Spring | FALSE | nonsummer
2024-04-30 04:00 | 2024-04-30 05:00 | Spring | FALSE | nonsummer
2024-04-30 05:00 | 2024-04-30 06:00 | Spring | FALSE | nonsummer
2024-04-30 06:00 | 2024-04-30 07:00 | Spring | FALSE | nonsummer
2024-04-30 07:00 | 2024-04-30 08:00 | Spring | FALSE | nonsummer
2024-04-30 08:00 | 2024-04-30 09:00 | Spring | FALSE | nonsummer
2024-04-30 09:00 | 2024-04-30 10:00 | Spring | FALSE | nonsummer
2024-04-30 10:00 | 2024-04-30 11:00 | Spring | FALSE | nonsummer
2024-04-30 11:00 | 2024-04-30 12:00 | Spring | FALSE | nonsummer
2024-04-30 12:00 | 2024-04-30 13:00 | Spring | FALSE | nonsummer
2024-04-30 13:00 | 2024-04-30 14:00 | Spring | FALSE | nonsummer
2024-04-30 14:00 | 2024-04-30 15:00 | Spring | FALSE | nonsummer
2024-04-30 15:00 | 2024-04-30 16:00 | Spring | FALSE | nonsummer
2024-04-30 16:00 | 2024-04-30 17:00 | Spring | FALSE | nonsummer
2024-04-30 17:00 | 2024-04-30 18:00 | Spring | TRUE | nonsummer
2024-04-30 18:00 | 2024-04-30 19:00 | Spring | TRUE | nonsummer
2024-04-30 19:00 | 2024-04-30 20:00 | Spring | TRUE | nonsummer
2024-04-30 20:00 | 2024-04-30 21:00 | Spring | TRUE | nonsummer
2024-04-30 21:00 | 2024-04-30 22:00 | Spring | TRUE | nonsummer
2024-04-30 22:00 | 2024-04-30 23:00 | Spring | FALSE | nonsummer
2024-04-30 23:00 | 2024-05-01 | Spring | FALSE | nonsummer
2024-05-01 | 2024-05-01 01:00 | Spring | FALSE | nonsummer
2024-05-01 01:00 | 2024-05-01 02:00 | Spring | FALSE | nonsummer
2024-05-01 02:00 | 2024-05-01 03:00 | Spring | FALSE | nonsummer
2024-05-01 03:00 | 2024-05-01 04:00 | Spring | FALSE | nonsummer
2024-05-01 04:00 | 2024-05-01 05:00 | Spring | FALSE | nonsummer
2024-05-01 05:00 | 2024-05-01 06:00 | Spring | FALSE | nonsummer
2024-05-01 06:00 | 2024-05-01 07:00 | Spring | FALSE | nonsummer
2024-05-01 07:00 | 2024-05-01 08:00 | Spring | FALSE | nonsummer
2024-05-01 08:00 | 2024-05-01 09:00 | Spring | FALSE | nonsummer
2024-05-01 09:00 | 2024-05-01 10:00 | Spring | FALSE | nonsummer
2024-05-01 10:00 | 2024-05-01 11:00 | Spring | FALSE | nonsummer
2024-05-01 11:00 | 2024-05-01 12:00 | Spring | FALSE | nonsummer
2024-05-01 12:00 | 2024-05-01 13:00 | Spring | FALSE | nonsummer
2024-05-01 13:00 | 2024-05-01 14:00 | Spring | FALSE | nonsummer
2024-05-01 14:00 | 2024-05-01 15:00 | Spring | FALSE | nonsummer
2024-05-01 15:00 | 2024-05-01 16:00 | Spring | FALSE | nonsummer
2024-05-01 16:00 | 2024-05-01 17:00 | Spring | FALSE | nonsummer
2024-05-01 17:00 | 2024-05-01 18:00 | Spring | TRUE | nonsummer
2024-05-01 18:00 | 2024-05-01 19:00 | Spring | TRUE | nonsummer
2024-05-01 19:00 | 2024-05-01 20:00 | Spring | TRUE | nonsummer
2024-05-01 20:00 | 2024-05-01 21:00 | Spring | TRUE | nonsummer
2024-05-01 21:00 | 2024-05-01 22:00 | Spring | TRUE | nonsummer
2024-05-01 22:00 | 2024-05-01 23:00 | Spring | FALSE | nonsummer
2024-05-01 23:00 | 2024-05-02 | Spring | FALSE | nonsummer
2024-05-02 | 2024-05-02 01:00 | Spring | FALSE | nonsummer
2024-05-02 01:00 | 2024-05-02 02:00 | Spring | FALSE | nonsummer
2024-05-02 02:00 | 2024-05-02 03:00 | Spring | FALSE | nonsummer
2024-05-02 03:00 | 2024-05-02 04:00 | Spring | FALSE | nonsummer
2024-05-02 04:00 | 2024-05-02 05:00 | Spring | FALSE | nonsummer
2024-05-02 05:00 | 2024-05-02 06:00 | Spring | FALSE | nonsummer
2024-05-02 06:00 | 2024-05-02 07:00 | Spring | FALSE | nonsummer
2024-05-02 07:00 | 2024-05-02 08:00 | Spring | FALSE | nonsummer
2024-05-02 08:00 | 2024-05-02 09:00 | Spring | FALSE | nonsummer
2024-05-02 09:00 | 2024-05-02 10:00 | Spring | FALSE | nonsummer
2024-05-02 10:00 | 2024-05-02 11:00 | Spring | FALSE | nonsummer
2024-05-02 11:00 | 2024-05-02 12:00 | Spring | FALSE | nonsummer
2024-05-02 12:00 | 2024-05-02 13:00 | Spring | FALSE | nonsummer
2024-05-02 13:00 | 2024-05-02 14:00 | Spring | FALSE | nonsummer
2024-05-02 14:00 | 2024-05-02 15:00 | Spring | FALSE | nonsummer
2024-05-02 15:00 | 2024-05-02 16:00 | Spring | FALSE | nonsummer
2024-05-02 16:00 | 2024-05-02 17:00 | Spring | FALSE | nonsummer
2024-05-02 17:00 | 2024-05-02 18:00 | Spring | TRUE | nonsummer
2024-05-02 18:00 | 2024-05-02 19:00 | Spring | TRUE | nonsummer
2024-05-02 19:00 | 2024-05-02 20:00 | Spring | TRUE | nonsummer
2024-05-02 20:00 | 2024-05-02 21:00 | Spring | TRUE | nonsummer
2024-05-02 21:00 | 2024-05-02 22:00 | Spring | TRUE | nonsummer
2024-05-02 22:00 | 2024-05-02 23:00 | Spring | FALSE | nonsummer
2024-05-02 23:00 | 2024-05-03 | Spring | FALSE | nonsummer
2024-05-03 | 2024-05-03 01:00 | Spring | FALSE | nonsummer
2024-05-03 01:00 | 2024-05-03 02:00 | Spring | FALSE | nonsummer
2024-05-03 02:00 | 2024-05-03 03:00 | Spring | FALSE | nonsummer
2024-05-03 03:00 | 2024-05-03 04:00 | Spring | FALSE | nonsummer
2024-05-03 04:00 | 2024-05-03 05:00 | Spring | FALSE | nonsummer
2024-05-03 05:00 | 2024-05-03 06:00 | Spring | FALSE | nonsummer
2024-05-03 06:00 | 2024-05-03 07:00 | Spring | FALSE | nonsummer
2024-05-03 07:00 | 2024-05-03 08:00 | Spring | FALSE | nonsummer
2024-05-03 08:00 | 2024-05-03 09:00 | Spring | FALSE | nonsummer
2024-05-03 09:00 | 2024-05-03 10:00 | Spring | FALSE | nonsummer
2024-05-03 10:00 | 2024-05-03 11:00 | Spring | FALSE | nonsummer
2024-05-03 11:00 | 2024-05-03 12:00 | Spring | FALSE | nonsummer
2024-05-03 12:00 | 2024-05-03 13:00 | Spring | FALSE | nonsummer
2024-05-03 13:00 | 2024-05-03 14:00 | Spring | FALSE | nonsummer
2024-05-03 14:00 | 2024-05-03 15:00 | Spring | FALSE | nonsummer
2024-05-03 15:00 | 2024-05-03 16:00 | Spring | FALSE | nonsummer
2024-05-03 16:00 | 2024-05-03 17:00 | Spring | FALSE | nonsummer
2024-05-03 17:00 | 2024-05-03 18:00 | Spring | TRUE | nonsummer
2024-05-03 18:00 | 2024-05-03 19:00 | Spring | TRUE | nonsummer
2024-05-03 19:00 | 2024-05-03 20:00 | Spring | TRUE | nonsummer
2024-05-03 20:00 | 2024-05-03 21:00 | Spring | TRUE | nonsummer
2024-05-03 21:00 | 2024-05-03 22:00 | Spring | TRUE | nonsummer
2024-05-03 22:00 | 2024-05-03 23:00 | Spring | FALSE | nonsummer
2024-05-03 23:00 | 2024-05-04 | Spring | FALSE | nonsummer
2024-05-04 | 2024-05-04 01:00 | Spring | FALSE | nonsummer
2024-05-04 01:00 | 2024-05-04 02:00 | Spring | FALSE | nonsummer
2024-05-04 02:00 | 2024-05-04 03:00 | Spring | FALSE | nonsummer
2024-05-04 03:00 | 2024-05-04 04:00 | Spring | FALSE | nonsummer
2024-05-04 04:00 | 2024-05-04 05:00 | Spring | FALSE | nonsummer
2024-05-04 05:00 | 2024-05-04 06:00 | Spring | FALSE | nonsummer
2024-05-04 06:00 | 2024-05-04 07:00 | Spring | FALSE | nonsummer
2024-05-04 07:00 | 2024-05-04 08:00 | Spring | FALSE | nonsummer
2024-05-04 08:00 | 2024-05-04 09:00 | Spring | FALSE | nonsummer
2024-05-04 09:00 | 2024-05-04 10:00 | Spring | FALSE | nonsummer
2024-05-04 10:00 | 2024-05-04 11:00 | Spring | FALSE | nonsummer
2024-05-04 11:00 | 2024-05-04 12:00 | Spring | FALSE | nonsummer
2024-05-04 12:00 | 2024-05-04 13:00 | Spring | FALSE | nonsummer
2024-05-04 13:00 | 2024-05-04 14:00 | Spring | FALSE | nonsummer
2024-05-04 14:00 | 2024-05-04 15:00 | Spring | FALSE | nonsummer
2024-05-04 15:00 | 2024-05-04 16:00 | Spring | FALSE | nonsummer
2024-05-04 16:00 | 2024-05-04 17:00 | Spring | FALSE | nonsummer
2024-05-04 17:00 | 2024-05-04 18:00 | Spring | TRUE | nonsummer
2024-05-04 18:00 | 2024-05-04 19:00 | Spring | TRUE | nonsummer
2024-05-04 19:00 | 2024-05-04 20:00 | Spring | TRUE | nonsummer
2024-05-04 20:00 | 2024-05-04 21:00 | Spring | TRUE | nonsummer
2024-05-04 21:00 | 2024-05-04 22:00 | Spring | TRUE | nonsummer
2024-05-04 22:00 | 2024-05-04 23:00 | Spring | FALSE | nonsummer
2024-05-04 23:00 | 2024-05-05 | Spring | FALSE | nonsummer
2024-05-05 | 2024-05-05 01:00 | Spring | FALSE | nonsummer
2024-05-05 01:00 | 2024-05-05 02:00 | Spring | FALSE | nonsummer
2024-05-05 02:00 | 2024-05-05 03:00 | Spring | FALSE | nonsummer
2024-05-05 03:00 | 2024-05-05 04:00 | Spring | FALSE | nonsummer
2024-05-05 04:00 | 2024-05-05 05:00 | Spring | FALSE | nonsummer
2024-05-05 05:00 | 2024-05-05 06:00 | Spring | FALSE | nonsummer
2024-05-05 06:00 | 2024-05-05 07:00 | Spring | FALSE | nonsummer
2024-05-05 07:00 | 2024-05-05 08:00 | Spring | FALSE | nonsummer
2024-05-05 08:00 | 2024-05-05 09:00 | Spring | FALSE | nonsummer
2024-05-05 09:00 | 2024-05-05 10:00 | Spring | FALSE | nonsummer
2024-05-05 10:00 | 2024-05-05 11:00 | Spring | FALSE | nonsummer
2024-05-05 11:00 | 2024-05-05 12:00 | Spring | FALSE | nonsummer
2024-05-05 12:00 | 2024-05-05 13:00 | Spring | FALSE | nonsummer
2024-05-05 13:00 | 2024-05-05 14:00 | Spring | FALSE | nonsummer
2024-05-05 14:00 | 2024-05-05 15:00 | Spring | FALSE | nonsummer
2024-05-05 15:00 | 2024-05-05 16:00 | Spring | FALSE | nonsummer
2024-05-05 16:00 | 2024-05-05 17:00 | Spring | FALSE | nonsummer
2024-05-05 17:00 | 2024-05-05 18:00 | Spring | TRUE | nonsummer
2024-05-05 18:00 | 2024-05-05 19:00 | Spring | TRUE | nonsummer
2024-05-05 19:00 | 2024-05-05 20:00 | Spring | TRUE | nonsummer
2024-05-05 20:00 | 2024-05-05 21:00 | Spring | TRUE | nonsummer
2024-05-05 21:00 | 2024-05-05 22:00 | Spring | TRUE | nonsummer
2024-05-05 22:00 | 2024-05-05 23:00 | Spring | FALSE | nonsummer
2024-05-05 23:00 | 2024-05-06 | Spring | FALSE | nonsummer
2024-05-06 | 2024-05-06 01:00 | Spring | FALSE | nonsummer
2024-05-06 01:00 | 2024-05-06 02:00 | Spring | FALSE | nonsummer
2024-05-06 02:00 | 2024-05-06 03:00 | Spring | FALSE | nonsummer
2024-05-06 03:00 | 2024-05-06 04:00 | Spring | FALSE | nonsummer
2024-05-06 04:00 | 2024-05-06 05:00 | Spring | FALSE | nonsummer
2024-05-06 05:00 | 2024-05-06 06:00 | Spring | FALSE | nonsummer
2024-05-06 06:00 | 2024-05-06 07:00 | Spring | FALSE | nonsummer
2024-05-06 07:00 | 2024-05-06 08:00 | Spring | FALSE | nonsummer
2024-05-06 08:00 | 2024-05-06 09:00 | Spring | FALSE | nonsummer
2024-05-06 09:00 | 2024-05-06 10:00 | Spring | FALSE | nonsummer
2024-05-06 10:00 | 2024-05-06 11:00 | Spring | FALSE | nonsummer
2024-05-06 11:00 | 2024-05-06 12:00 | Spring | FALSE | nonsummer
2024-05-06 12:00 | 2024-05-06 13:00 | Spring | FALSE | nonsummer
2024-05-06 13:00 | 2024-05-06 14:00 | Spring | FALSE | nonsummer
2024-05-06 14:00 | 2024-05-06 15:00 | Spring | FALSE | nonsummer
2024-05-06 15:00 | 2024-05-06 16:00 | Spring | FALSE | nonsummer
2024-05-06 16:00 | 2024-05-06 17:00 | Spring | FALSE | nonsummer
2024-05-06 17:00 | 2024-05-06 18:00 | Spring | TRUE | nonsummer
2024-05-06 18:00 | 2024-05-06 19:00 | Spring | TRUE | nonsummer
2024-05-06 19:00 | 2024-05-06 20:00 | Spring | TRUE | nonsummer
2024-05-06 20:00 | 2024-05-06 21:00 | Spring | TRUE | nonsummer
2024-05-06 21:00 | 2024-05-06 22:00 | Spring | TRUE | nonsummer
2024-05-06 22:00 | 2024-05-06 23:00 | Spring | FALSE | nonsummer
2024-05-06 23:00 | 2024-05-07 | Spring | FALSE | nonsummer
2024-05-07 | 2024-05-07 01:00 | Spring | FALSE | nonsummer
2024-05-07 01:00 | 2024-05-07 02:00 | Spring | FALSE | nonsummer
2024-05-07 02:00 | 2024-05-07 03:00 | Spring | FALSE | nonsummer
2024-05-07 03:00 | 2024-05-07 04:00 | Spring | FALSE | nonsummer
2024-05-07 04:00 | 2024-05-07 05:00 | Spring | FALSE | nonsummer
2024-05-07 05:00 | 2024-05-07 06:00 | Spring | FALSE | nonsummer
2024-05-07 06:00 | 2024-05-07 07:00 | Spring | FALSE | nonsummer
2024-05-07 07:00 | 2024-05-07 08:00 | Spring | FALSE | nonsummer
2024-05-07 08:00 | 2024-05-07 09:00 | Spring | FALSE | nonsummer
2024-05-07 09:00 | 2024-05-07 10:00 | Spring | FALSE | nonsummer
2024-05-07 10:00 | 2024-05-07 11:00 | Spring | FALSE | nonsummer
2024-05-07 11:00 | 2024-05-07 12:00 | Spring | FALSE | nonsummer
2024-05-07 12:00 | 2024-05-07 13:00 | Spring | FALSE | nonsummer
2024-05-07 13:00 | 2024-05-07 14:00 | Spring | FALSE | nonsummer
2024-05-07 14:00 | 2024-05-07 15:00 | Spring | FALSE | nonsummer
2024-05-07 15:00 | 2024-05-07 16:00 | Spring | FALSE | nonsummer
2024-05-07 16:00 | 2024-05-07 17:00 | Spring | FALSE | nonsummer
2024-05-07 17:00 | 2024-05-07 18:00 | Spring | TRUE | nonsummer
2024-05-07 18:00 | 2024-05-07 19:00 | Spring | TRUE | nonsummer
2024-05-07 19:00 | 2024-05-07 20:00 | Spring | TRUE | nonsummer
2024-05-07 20:00 | 2024-05-07 21:00 | Spring | TRUE | nonsummer
2024-05-07 21:00 | 2024-05-07 22:00 | Spring | TRUE | nonsummer
2024-05-07 22:00 | 2024-05-07 23:00 | Spring | FALSE | nonsummer
2024-05-07 23:00 | 2024-05-08 | Spring | FALSE | nonsummer
2024-05-08 | 2024-05-08 01:00 | Spring | FALSE | nonsummer
2024-05-08 01:00 | 2024-05-08 02:00 | Spring | FALSE | nonsummer
2024-05-08 02:00 | 2024-05-08 03:00 | Spring | FALSE | nonsummer
2024-05-08 03:00 | 2024-05-08 04:00 | Spring | FALSE | nonsummer
2024-05-08 04:00 | 2024-05-08 05:00 | Spring | FALSE | nonsummer
2024-05-08 05:00 | 2024-05-08 06:00 | Spring | FALSE | nonsummer
2024-05-08 06:00 | 2024-05-08 07:00 | Spring | FALSE | nonsummer
2024-05-08 07:00 | 2024-05-08 08:00 | Spring | FALSE | nonsummer
2024-05-08 08:00 | 2024-05-08 09:00 | Spring | FALSE | nonsummer
2024-05-08 09:00 | 2024-05-08 10:00 | Spring | FALSE | nonsummer
2024-05-08 10:00 | 2024-05-08 11:00 | Spring | FALSE | nonsummer
2024-05-08 11:00 | 2024-05-08 12:00 | Spring | FALSE | nonsummer
2024-05-08 12:00 | 2024-05-08 13:00 | Spring | FALSE | nonsummer
2024-05-08 13:00 | 2024-05-08 14:00 | Spring | FALSE | nonsummer
2024-05-08 14:00 | 2024-05-08 15:00 | Spring | FALSE | nonsummer
2024-05-08 15:00 | 2024-05-08 16:00 | Spring | FALSE | nonsummer
2024-05-08 16:00 | 2024-05-08 17:00 | Spring | FALSE | nonsummer
2024-05-08 17:00 | 2024-05-08 18:00 | Spring | TRUE | nonsummer
2024-05-08 18:00 | 2024-05-08 19:00 | Spring | TRUE | nonsummer
2024-05-08 19:00 | 2024-05-08 20:00 | Spring | TRUE | nonsummer
2024-05-08 20:00 | 2024-05-08 21:00 | Spring | TRUE | nonsummer
2024-05-08 21:00 | 2024-05-08 22:00 | Spring | TRUE | nonsummer
2024-05-08 22:00 | 2024-05-08 23:00 | Spring | FALSE | nonsummer
2024-05-08 23:00 | 2024-05-09 | Spring | FALSE | nonsummer
2024-05-09 | 2024-05-09 01:00 | Spring | FALSE | nonsummer
2024-05-09 01:00 | 2024-05-09 02:00 | Spring | FALSE | nonsummer
2024-05-09 02:00 | 2024-05-09 03:00 | Spring | FALSE | nonsummer
2024-05-09 03:00 | 2024-05-09 04:00 | Spring | FALSE | nonsummer
2024-05-09 04:00 | 2024-05-09 05:00 | Spring | FALSE | nonsummer
2024-05-09 05:00 | 2024-05-09 06:00 | Spring | FALSE | nonsummer
2024-05-09 06:00 | 2024-05-09 07:00 | Spring | FALSE | nonsummer
2024-05-09 07:00 | 2024-05-09 08:00 | Spring | FALSE | nonsummer
2024-05-09 08:00 | 2024-05-09 09:00 | Spring | FALSE | nonsummer
2024-05-09 09:00 | 2024-05-09 10:00 | Spring | FALSE | nonsummer
2024-05-09 10:00 | 2024-05-09 11:00 | Spring | FALSE | nonsummer
2024-05-09 11:00 | 2024-05-09 12:00 | Spring | FALSE | nonsummer
2024-05-09 12:00 | 2024-05-09 13:00 | Spring | FALSE | nonsummer
2024-05-09 13:00 | 2024-05-09 14:00 | Spring | FALSE | nonsummer
2024-05-09 14:00 | 2024-05-09 15:00 | Spring | FALSE | nonsummer
2024-05-09 15:00 | 2024-05-09 16:00 | Spring | FALSE | nonsummer
2024-05-09 16:00 | 2024-05-09 17:00 | Spring | FALSE | nonsummer
2024-05-09 17:00 | 2024-05-09 18:00 | Spring | TRUE | nonsummer
2024-05-09 18:00 | 2024-05-09 19:00 | Spring | TRUE | nonsummer
2024-05-09 19:00 | 2024-05-09 20:00 | Spring | TRUE | nonsummer
2024-05-09 20:00 | 2024-05-09 21:00 | Spring | TRUE | nonsummer
2024-05-09 21:00 | 2024-05-09 22:00 | Spring | TRUE | nonsummer
2024-05-09 22:00 | 2024-05-09 23:00 | Spring | FALSE | nonsummer
2024-05-09 23:00 | 2024-05-10 | Spring | FALSE | nonsummer
2024-05-10 | 2024-05-10 01:00 | Spring | FALSE | nonsummer
2024-05-10 01:00 | 2024-05-10 02:00 | Spring | FALSE | nonsummer
2024-05-10 02:00 | 2024-05-10 03:00 | Spring | FALSE | nonsummer
2024-05-10 03:00 | 2024-05-10 04:00 | Spring | FALSE | nonsummer
2024-05-10 04:00 | 2024-05-10 05:00 | Spring | FALSE | nonsummer
2024-05-10 05:00 | 2024-05-10 06:00 | Spring | FALSE | nonsummer
2024-05-10 06:00 | 2024-05-10 07:00 | Spring | FALSE | nonsummer
2024-05-10 07:00 | 2024-05-10 08:00 | Spring | FALSE | nonsummer
2024-05-10 08:00 | 2024-05-10 09:00 | Spring | FALSE | nonsummer
2024-05-10 09:00 | 2024-05-10 10:00 | Spring | FALSE | nonsummer
2024-05-10 10:00 | 2024-05-10 11:00 | Spring | FALSE | nonsummer
2024-05-10 11:00 | 2024-05-10 12:00 | Spring | FALSE | nonsummer
2024-05-10 12:00 | 2024-05-10 13:00 | Spring | FALSE | nonsummer
2024-05-10 13:00 | 2024-05-10 14:00 | Spring | FALSE | nonsummer
2024-05-10 14:00 | 2024-05-10 15:00 | Spring | FALSE | nonsummer
2024-05-10 15:00 | 2024-05-10 16:00 | Spring | FALSE | nonsummer
2024-05-10 16:00 | 2024-05-10 17:00 | Spring | FALSE | nonsummer
2024-05-10 17:00 | 2024-05-10 18:00 | Spring | TRUE | nonsummer
2024-05-10 18:00 | 2024-05-10 19:00 | Spring | TRUE | nonsummer
2024-05-10 19:00 | 2024-05-10 20:00 | Spring | TRUE | nonsummer
2024-05-10 20:00 | 2024-05-10 21:00 | Spring | TRUE | nonsummer
2024-05-10 21:00 | 2024-05-10 22:00 | Spring | TRUE | nonsummer
2024-05-10 22:00 | 2024-05-10 23:00 | Spring | FALSE | nonsummer
2024-05-10 23:00 | 2024-05-11 | Spring | FALSE | nonsummer
2024-05-11 | 2024-05-11 01:00 | Spring | FALSE | nonsummer
2024-05-11 01:00 | 2024-05-11 02:00 | Spring | FALSE | nonsummer
2024-05-11 02:00 | 2024-05-11 03:00 | Spring | FALSE | nonsummer
2024-05-11 03:00 | 2024-05-11 04:00 | Spring | FALSE | nonsummer
2024-05-11 04:00 | 2024-05-11 05:00 | Spring | FALSE | nonsummer
2024-05-11 05:00 | 2024-05-11 06:00 | Spring | FALSE | nonsummer
2024-05-11 06:00 | 2024-05-11 07:00 | Spring | FALSE | nonsummer
2024-05-11 07:00 | 2024-05-11 08:00 | Spring | FALSE | nonsummer
2024-05-11 08:00 | 2024-05-11 09:00 | Spring | FALSE | nonsummer
2024-05-11 09:00 | 2024-05-11 10:00 | Spring | FALSE | nonsummer
2024-05-11 10:00 | 2024-05-11 11:00 | Spring | FALSE | nonsummer
2024-05-11 11:00 | 2024-05-11 12:00 | Spring | FALSE | nonsummer
2024-05-11 12:00 | 2024-05-11 13:00 | Spring | FALSE | nonsummer
2024-05-11 13:00 | 2024-05-11 14:00 | Spring | FALSE | nonsummer
2024-05-11 14:00 | 2024-05-11 15:00 | Spring | FALSE | nonsummer
2024-05-11 15:00 | 2024-05-11 16:00 | Spring | FALSE | nonsummer
2024-05-11 16:00 | 2024-05-11 17:00 | Spring | FALSE | nonsummer
2024-05-11 17:00 | 2024-05-11 18:00 | Spring | TRUE | nonsummer
2024-05-11 18:00 | 2024-05-11 19:00 | Spring | TRUE | nonsummer
2024-05-11 19:00 | 2024-05-11 20:00 | Spring | TRUE | nonsummer
2024-05-11 20:00 | 2024-05-11 21:00 | Spring | TRUE | nonsummer
2024-05-11 21:00 | 2024-05-11 22:00 | Spring | TRUE | nonsummer
2024-05-11 22:00 | 2024-05-11 23:00 | Spring | FALSE | nonsummer
2024-05-11 23:00 | 2024-05-12 | Spring | FALSE | nonsummer
2024-05-12 | 2024-05-12 01:00 | Spring | FALSE | nonsummer
2024-05-12 01:00 | 2024-05-12 02:00 | Spring | FALSE | nonsummer
2024-05-12 02:00 | 2024-05-12 03:00 | Spring | FALSE | nonsummer
2024-05-12 03:00 | 2024-05-12 04:00 | Spring | FALSE | nonsummer
2024-05-12 04:00 | 2024-05-12 05:00 | Spring | FALSE | nonsummer
2024-05-12 05:00 | 2024-05-12 06:00 | Spring | FALSE | nonsummer
2024-05-12 06:00 | 2024-05-12 07:00 | Spring | FALSE | nonsummer
2024-05-12 07:00 | 2024-05-12 08:00 | Spring | FALSE | nonsummer
2024-05-12 08:00 | 2024-05-12 09:00 | Spring | FALSE | nonsummer
2024-05-12 09:00 | 2024-05-12 10:00 | Spring | FALSE | nonsummer
2024-05-12 10:00 | 2024-05-12 11:00 | Spring | FALSE | nonsummer
2024-05-12 11:00 | 2024-05-12 12:00 | Spring | FALSE | nonsummer
2024-05-12 12:00 | 2024-05-12 13:00 | Spring | FALSE | nonsummer
2024-05-12 13:00 | 2024-05-12 14:00 | Spring | FALSE | nonsummer
2024-05-12 14:00 | 2024-05-12 15:00 | Spring | FALSE | nonsummer
2024-05-12 15:00 | 2024-05-12 16:00 | Spring | FALSE | nonsummer
2024-05-12 16:00 | 2024-05-12 17:00 | Spring | FALSE | nonsummer
2024-05-12 17:00 | 2024-05-12 18:00 | Spring | TRUE | nonsummer
2024-05-12 18:00 | 2024-05-12 19:00 | Spring | TRUE | nonsummer
2024-05-12 19:00 | 2024-05-12 20:00 | Spring | TRUE | nonsummer
2024-05-12 20:00 | 2024-05-12 21:00 | Spring | TRUE | nonsummer
2024-05-12 21:00 | 2024-05-12 22:00 | Spring | TRUE | nonsummer
2024-05-12 22:00 | 2024-05-12 23:00 | Spring | FALSE | nonsummer
2024-05-12 23:00 | 2024-05-13 | Spring | FALSE | nonsummer
2024-05-13 | 2024-05-13 01:00 | Spring | FALSE | nonsummer
2024-05-13 01:00 | 2024-05-13 02:00 | Spring | FALSE | nonsummer
2024-05-13 02:00 | 2024-05-13 03:00 | Spring | FALSE | nonsummer
2024-05-13 03:00 | 2024-05-13 04:00 | Spring | FALSE | nonsummer
2024-05-13 04:00 | 2024-05-13 05:00 | Spring | FALSE | nonsummer
2024-05-13 05:00 | 2024-05-13 06:00 | Spring | FALSE | nonsummer
2024-05-13 06:00 | 2024-05-13 07:00 | Spring | FALSE | nonsummer
2024-05-13 07:00 | 2024-05-13 08:00 | Spring | FALSE | nonsummer
2024-05-13 08:00 | 2024-05-13 09:00 | Spring | FALSE | nonsummer
2024-05-13 09:00 | 2024-05-13 10:00 | Spring | FALSE | nonsummer
2024-05-13 10:00 | 2024-05-13 11:00 | Spring | FALSE | nonsummer
2024-05-13 11:00 | 2024-05-13 12:00 | Spring | FALSE | nonsummer
2024-05-13 12:00 | 2024-05-13 13:00 | Spring | FALSE | nonsummer
2024-05-13 13:00 | 2024-05-13 14:00 | Spring | FALSE | nonsummer
2024-05-13 14:00 | 2024-05-13 15:00 | Spring | FALSE | nonsummer
2024-05-13 15:00 | 2024-05-13 16:00 | Spring | FALSE | nonsummer
2024-05-13 16:00 | 2024-05-13 17:00 | Spring | FALSE | nonsummer
2024-05-13 17:00 | 2024-05-13 18:00 | Spring | TRUE | nonsummer
2024-05-13 18:00 | 2024-05-13 19:00 | Spring | TRUE | nonsummer
2024-05-13 19:00 | 2024-05-13 20:00 | Spring | TRUE | nonsummer
2024-05-13 20:00 | 2024-05-13 21:00 | Spring | TRUE | nonsummer
2024-05-13 21:00 | 2024-05-13 22:00 | Spring | TRUE | nonsummer
2024-05-13 22:00 | 2024-05-13 23:00 | Spring | FALSE | nonsummer
2024-05-13 23:00 | 2024-05-14 | Spring | FALSE | nonsummer
2024-05-14 | 2024-05-14 01:00 | Spring | FALSE | nonsummer
2024-05-14 01:00 | 2024-05-14 02:00 | Spring | FALSE | nonsummer
2024-05-14 02:00 | 2024-05-14 03:00 | Spring | FALSE | nonsummer
2024-05-14 03:00 | 2024-05-14 04:00 | Spring | FALSE | nonsummer
2024-05-14 04:00 | 2024-05-14 05:00 | Spring | FALSE | nonsummer
2024-05-14 05:00 | 2024-05-14 06:00 | Spring | FALSE | nonsummer
2024-05-14 06:00 | 2024-05-14 07:00 | Spring | FALSE | nonsummer
2024-05-14 07:00 | 2024-05-14 08:00 | Spring | FALSE | nonsummer
2024-05-14 08:00 | 2024-05-14 09:00 | Spring | FALSE | nonsummer
2024-05-14 09:00 | 2024-05-14 10:00 | Spring | FALSE | nonsummer
2024-05-14 10:00 | 2024-05-14 11:00 | Spring | FALSE | nonsummer
2024-05-14 11:00 | 2024-05-14 12:00 | Spring | FALSE | nonsummer
2024-05-14 12:00 | 2024-05-14 13:00 | Spring | FALSE | nonsummer
2024-05-14 13:00 | 2024-05-14 14:00 | Spring | FALSE | nonsummer
2024-05-14 14:00 | 2024-05-14 15:00 | Spring | FALSE | nonsummer
2024-05-14 15:00 | 2024-05-14 16:00 | Spring | FALSE | nonsummer
2024-05-14 16:00 | 2024-05-14 17:00 | Spring | FALSE | nonsummer
2024-05-14 17:00 | 2024-05-14 18:00 | Spring | TRUE | nonsummer
2024-05-14 18:00 | 2024-05-14 19:00 | Spring | TRUE | nonsummer
2024-05-14 19:00 | 2024-05-14 20:00 | Spring | TRUE | nonsummer
2024-05-14 20:00 | 2024-05-14 21:00 | Spring | TRUE | nonsummer
2024-05-14 21:00 | 2024-05-14 22:00 | Spring | TRUE | nonsummer
2024-05-14 22:00 | 2024-05-14 23:00 | Spring | FALSE | nonsummer
2024-05-14 23:00 | 2024-05-15 | Spring | FALSE | nonsummer
2024-05-15 | 2024-05-15 01:00 | Spring | FALSE | nonsummer
2024-05-15 01:00 | 2024-05-15 02:00 | Spring | FALSE | nonsummer
2024-05-15 02:00 | 2024-05-15 03:00 | Spring | FALSE | nonsummer
2024-05-15 03:00 | 2024-05-15 04:00 | Spring | FALSE | nonsummer
2024-05-15 04:00 | 2024-05-15 05:00 | Spring | FALSE | nonsummer
2024-05-15 05:00 | 2024-05-15 06:00 | Spring | FALSE | nonsummer
2024-05-15 06:00 | 2024-05-15 07:00 | Spring | FALSE | nonsummer
2024-05-15 07:00 | 2024-05-15 08:00 | Spring | FALSE | nonsummer
2024-05-15 08:00 | 2024-05-15 09:00 | Spring | FALSE | nonsummer
2024-05-15 09:00 | 2024-05-15 10:00 | Spring | FALSE | nonsummer
2024-05-15 10:00 | 2024-05-15 11:00 | Spring | FALSE | nonsummer
2024-05-15 11:00 | 2024-05-15 12:00 | Spring | FALSE | nonsummer
2024-05-15 12:00 | 2024-05-15 13:00 | Spring | FALSE | nonsummer
2024-05-15 13:00 | 2024-05-15 14:00 | Spring | FALSE | nonsummer
2024-05-15 14:00 | 2024-05-15 15:00 | Spring | FALSE | nonsummer
2024-05-15 15:00 | 2024-05-15 16:00 | Spring | FALSE | nonsummer
2024-05-15 16:00 | 2024-05-15 17:00 | Spring | FALSE | nonsummer
2024-05-15 17:00 | 2024-05-15 18:00 | Spring | TRUE | nonsummer
2024-05-15 18:00 | 2024-05-15 19:00 | Spring | TRUE | nonsummer
2024-05-15 19:00 | 2024-05-15 20:00 | Spring | TRUE | nonsummer
2024-05-15 20:00 | 2024-05-15 21:00 | Spring | TRUE | nonsummer
2024-05-15 21:00 | 2024-05-15 22:00 | Spring | TRUE | nonsummer
2024-05-15 22:00 | 2024-05-15 23:00 | Spring | FALSE | nonsummer
2024-05-15 23:00 | 2024-05-16 | Spring | FALSE | nonsummer
2024-05-16 | 2024-05-16 01:00 | Spring | FALSE | nonsummer
2024-05-16 01:00 | 2024-05-16 02:00 | Spring | FALSE | nonsummer
2024-05-16 02:00 | 2024-05-16 03:00 | Spring | FALSE | nonsummer
2024-05-16 03:00 | 2024-05-16 04:00 | Spring | FALSE | nonsummer
2024-05-16 04:00 | 2024-05-16 05:00 | Spring | FALSE | nonsummer
2024-05-16 05:00 | 2024-05-16 06:00 | Spring | FALSE | nonsummer
2024-05-16 06:00 | 2024-05-16 07:00 | Spring | FALSE | nonsummer
2024-05-16 07:00 | 2024-05-16 08:00 | Spring | FALSE | nonsummer
2024-05-16 08:00 | 2024-05-16 09:00 | Spring | FALSE | nonsummer
2024-05-16 09:00 | 2024-05-16 10:00 | Spring | FALSE | nonsummer
2024-05-16 10:00 | 2024-05-16 11:00 | Spring | FALSE | nonsummer
2024-05-16 11:00 | 2024-05-16 12:00 | Spring | FALSE | nonsummer
2024-05-16 12:00 | 2024-05-16 13:00 | Spring | FALSE | nonsummer
2024-05-16 13:00 | 2024-05-16 14:00 | Spring | FALSE | nonsummer
2024-05-16 14:00 | 2024-05-16 15:00 | Spring | FALSE | nonsummer
2024-05-16 15:00 | 2024-05-16 16:00 | Spring | FALSE | nonsummer
2024-05-16 16:00 | 2024-05-16 17:00 | Spring | FALSE | nonsummer
2024-05-16 17:00 | 2024-05-16 18:00 | Spring | TRUE | nonsummer
2024-05-16 18:00 | 2024-05-16 19:00 | Spring | TRUE | nonsummer
2024-05-16 19:00 | 2024-05-16 20:00 | Spring | TRUE | nonsummer
2024-05-16 20:00 | 2024-05-16 21:00 | Spring | TRUE | nonsummer
2024-05-16 21:00 | 2024-05-16 22:00 | Spring | TRUE | nonsummer
2024-05-16 22:00 | 2024-05-16 23:00 | Spring | FALSE | nonsummer
2024-05-16 23:00 | 2024-05-17 | Spring | FALSE | nonsummer
2024-05-17 | 2024-05-17 01:00 | Spring | FALSE | nonsummer
2024-05-17 01:00 | 2024-05-17 02:00 | Spring | FALSE | nonsummer
2024-05-17 02:00 | 2024-05-17 03:00 | Spring | FALSE | nonsummer
2024-05-17 03:00 | 2024-05-17 04:00 | Spring | FALSE | nonsummer
2024-05-17 04:00 | 2024-05-17 05:00 | Spring | FALSE | nonsummer
2024-05-17 05:00 | 2024-05-17 06:00 | Spring | FALSE | nonsummer
2024-05-17 06:00 | 2024-05-17 07:00 | Spring | FALSE | nonsummer
2024-05-17 07:00 | 2024-05-17 08:00 | Spring | FALSE | nonsummer
2024-05-17 08:00 | 2024-05-17 09:00 | Spring | FALSE | nonsummer
2024-05-17 09:00 | 2024-05-17 10:00 | Spring | FALSE | nonsummer
2024-05-17 10:00 | 2024-05-17 11:00 | Spring | FALSE | nonsummer
2024-05-17 11:00 | 2024-05-17 12:00 | Spring | FALSE | nonsummer
2024-05-17 12:00 | 2024-05-17 13:00 | Spring | FALSE | nonsummer
2024-05-17 13:00 | 2024-05-17 14:00 | Spring | FALSE | nonsummer
2024-05-17 14:00 | 2024-05-17 15:00 | Spring | FALSE | nonsummer
2024-05-17 15:00 | 2024-05-17 16:00 | Spring | FALSE | nonsummer
2024-05-17 16:00 | 2024-05-17 17:00 | Spring | FALSE | nonsummer
2024-05-17 17:00 | 2024-05-17 18:00 | Spring | TRUE | nonsummer
2024-05-17 18:00 | 2024-05-17 19:00 | Spring | TRUE | nonsummer
2024-05-17 19:00 | 2024-05-17 20:00 | Spring | TRUE | nonsummer
2024-05-17 20:00 | 2024-05-17 21:00 | Spring | TRUE | nonsummer
2024-05-17 21:00 | 2024-05-17 22:00 | Spring | TRUE | nonsummer
2024-05-17 22:00 | 2024-05-17 23:00 | Spring | FALSE | nonsummer
2024-05-17 23:00 | 2024-05-18 | Spring | FALSE | nonsummer
2024-05-18 | 2024-05-18 01:00 | Spring | FALSE | nonsummer
2024-05-18 01:00 | 2024-05-18 02:00 | Spring | FALSE | nonsummer
2024-05-18 02:00 | 2024-05-18 03:00 | Spring | FALSE | nonsummer
2024-05-18 03:00 | 2024-05-18 04:00 | Spring | FALSE | nonsummer
2024-05-18 04:00 | 2024-05-18 05:00 | Spring | FALSE | nonsummer
2024-05-18 05:00 | 2024-05-18 06:00 | Spring | FALSE | nonsummer
2024-05-18 06:00 | 2024-05-18 07:00 | Spring | FALSE | nonsummer
2024-05-18 07:00 | 2024-05-18 08:00 | Spring | FALSE | nonsummer
2024-05-18 08:00 | 2024-05-18 09:00 | Spring | FALSE | nonsummer
2024-05-18 09:00 | 2024-05-18 10:00 | Spring | FALSE | nonsummer
2024-05-18 10:00 | 2024-05-18 11:00 | Spring | FALSE | nonsummer
2024-05-18 11:00 | 2024-05-18 12:00 | Spring | FALSE | nonsummer
2024-05-18 12:00 | 2024-05-18 13:00 | Spring | FALSE | nonsummer
2024-05-18 13:00 | 2024-05-18 14:00 | Spring | FALSE | nonsummer
2024-05-18 14:00 | 2024-05-18 15:00 | Spring | FALSE | nonsummer
2024-05-18 15:00 | 2024-05-18 16:00 | Spring | FALSE | nonsummer
2024-05-18 16:00 | 2024-05-18 17:00 | Spring | FALSE | nonsummer
2024-05-18 17:00 | 2024-05-18 18:00 | Spring | TRUE | nonsummer
2024-05-18 18:00 | 2024-05-18 19:00 | Spring | TRUE | nonsummer
2024-05-18 19:00 | 2024-05-18 20:00 | Spring | TRUE | nonsummer
2024-05-18 20:00 | 2024-05-18 21:00 | Spring | TRUE | nonsummer
2024-05-18 21:00 | 2024-05-18 22:00 | Spring | TRUE | nonsummer
2024-05-18 22:00 | 2024-05-18 23:00 | Spring | FALSE | nonsummer
2024-05-18 23:00 | 2024-05-19 | Spring | FALSE | nonsummer
2024-05-19 | 2024-05-19 01:00 | Spring | FALSE | nonsummer
2024-05-19 01:00 | 2024-05-19 02:00 | Spring | FALSE | nonsummer
2024-05-19 02:00 | 2024-05-19 03:00 | Spring | FALSE | nonsummer
2024-05-19 03:00 | 2024-05-19 04:00 | Spring | FALSE | nonsummer
2024-05-19 04:00 | 2024-05-19 05:00 | Spring | FALSE | nonsummer
2024-05-19 05:00 | 2024-05-19 06:00 | Spring | FALSE | nonsummer
2024-05-19 06:00 | 2024-05-19 07:00 | Spring | FALSE | nonsummer
2024-05-19 07:00 | 2024-05-19 08:00 | Spring | FALSE | nonsummer
2024-05-19 08:00 | 2024-05-19 09:00 | Spring | FALSE | nonsummer
2024-05-19 09:00 | 2024-05-19 10:00 | Spring | FALSE | nonsummer
2024-05-19 10:00 | 2024-05-19 11:00 | Spring | FALSE | nonsummer
2024-05-19 11:00 | 2024-05-19 12:00 | Spring | FALSE | nonsummer
2024-05-19 12:00 | 2024-05-19 13:00 | Spring | FALSE | nonsummer
2024-05-19 13:00 | 2024-05-19 14:00 | Spring | FALSE | nonsummer
2024-05-19 14:00 | 2024-05-19 15:00 | Spring | FALSE | nonsummer
2024-05-19 15:00 | 2024-05-19 16:00 | Spring | FALSE | nonsummer
2024-05-19 16:00 | 2024-05-19 17:00 | Spring | FALSE | nonsummer
2024-05-19 17:00 | 2024-05-19 18:00 | Spring | TRUE | nonsummer
2024-05-19 18:00 | 2024-05-19 19:00 | Spring | TRUE | nonsummer
2024-05-19 19:00 | 2024-05-19 20:00 | Spring | TRUE | nonsummer
2024-05-19 20:00 | 2024-05-19 21:00 | Spring | TRUE | nonsummer
2024-05-19 21:00 | 2024-05-19 22:00 | Spring | TRUE | nonsummer
2024-05-19 22:00 | 2024-05-19 23:00 | Spring | FALSE | nonsummer
2024-05-19 23:00 | 2024-05-20 | Spring | FALSE | nonsummer
2024-05-20 | 2024-05-20 01:00 | Spring | FALSE | nonsummer
2024-05-20 01:00 | 2024-05-20 02:00 | Spring | FALSE | nonsummer
2024-05-20 02:00 | 2024-05-20 03:00 | Spring | FALSE | nonsummer
2024-05-20 03:00 | 2024-05-20 04:00 | Spring | FALSE | nonsummer
2024-05-20 04:00 | 2024-05-20 05:00 | Spring | FALSE | nonsummer
2024-05-20 05:00 | 2024-05-20 06:00 | Spring | FALSE | nonsummer
2024-05-20 06:00 | 2024-05-20 07:00 | Spring | FALSE | nonsummer
2024-05-20 07:00 | 2024-05-20 08:00 | Spring | FALSE | nonsummer
2024-05-20 08:00 | 2024-05-20 09:00 | Spring | FALSE | nonsummer
2024-05-20 09:00 | 2024-05-20 10:00 | Spring | FALSE | nonsummer
2024-05-20 10:00 | 2024-05-20 11:00 | Spring | FALSE | nonsummer
2024-05-20 11:00 | 2024-05-20 12:00 | Spring | FALSE | nonsummer
2024-05-20 12:00 | 2024-05-20 13:00 | Spring | FALSE | nonsummer
2024-05-20 13:00 | 2024-05-20 14:00 | Spring | FALSE | nonsummer
2024-05-20 14:00 | 2024-05-20 15:00 | Spring | FALSE | nonsummer
2024-05-20 15:00 | 2024-05-20 16:00 | Spring | FALSE | nonsummer
2024-05-20 16:00 | 2024-05-20 17:00 | Spring | FALSE | nonsummer
2024-05-20 17:00 | 2024-05-20 18:00 | Spring | TRUE | nonsummer
2024-05-20 18:00 | 2024-05-20 19:00 | Spring | TRUE | nonsummer
2024-05-20 19:00 | 2024-05-20 20:00 | Spring | TRUE | nonsummer
2024-05-20 20:00 | 2024-05-20 21:00 | Spring | TRUE | nonsummer
2024-05-20 21:00 | 2024-05-20 22:00 | Spring | TRUE | nonsummer
2024-05-20 22:00 | 2024-05-20 23:00 | Spring | FALSE | nonsummer
2024-05-20 23:00 | 2024-05-21 | Spring | FALSE | nonsummer
2024-05-21 | 2024-05-21 01:00 | Spring | FALSE | nonsummer
2024-05-21 01:00 | 2024-05-21 02:00 | Spring | FALSE | nonsummer
2024-05-21 02:00 | 2024-05-21 03:00 | Spring | FALSE | nonsummer
2024-05-21 03:00 | 2024-05-21 04:00 | Spring | FALSE | nonsummer
2024-05-21 04:00 | 2024-05-21 05:00 | Spring | FALSE | nonsummer
2024-05-21 05:00 | 2024-05-21 06:00 | Spring | FALSE | nonsummer
2024-05-21 06:00 | 2024-05-21 07:00 | Spring | FALSE | nonsummer
2024-05-21 07:00 | 2024-05-21 08:00 | Spring | FALSE | nonsummer
2024-05-21 08:00 | 2024-05-21 09:00 | Spring | FALSE | nonsummer
2024-05-21 09:00 | 2024-05-21 10:00 | Spring | FALSE | nonsummer
2024-05-21 10:00 | 2024-05-21 11:00 | Spring | FALSE | nonsummer
2024-05-21 11:00 | 2024-05-21 12:00 | Spring | FALSE | nonsummer
2024-05-21 12:00 | 2024-05-21 13:00 | Spring | FALSE | nonsummer
2024-05-21 13:00 | 2024-05-21 14:00 | Spring | FALSE | nonsummer
2024-05-21 14:00 | 2024-05-21 15:00 | Spring | FALSE | nonsummer
2024-05-21 15:00 | 2024-05-21 16:00 | Spring | FALSE | nonsummer
2024-05-21 16:00 | 2024-05-21 17:00 | Spring | FALSE | nonsummer
2024-05-21 17:00 | 2024-05-21 18:00 | Spring | TRUE | nonsummer
2024-05-21 18:00 | 2024-05-21 19:00 | Spring | TRUE | nonsummer
2024-05-21 19:00 | 2024-05-21 20:00 | Spring | TRUE | nonsummer
2024-05-21 20:00 | 2024-05-21 21:00 | Spring | TRUE | nonsummer
2024-05-21 21:00 | 2024-05-21 22:00 | Spring | TRUE | nonsummer
2024-05-21 22:00 | 2024-05-21 23:00 | Spring | FALSE | nonsummer
2024-05-21 23:00 | 2024-05-22 | Spring | FALSE | nonsummer
2024-05-22 | 2024-05-22 01:00 | Spring | FALSE | nonsummer
2024-05-22 01:00 | 2024-05-22 02:00 | Spring | FALSE | nonsummer
2024-05-22 02:00 | 2024-05-22 03:00 | Spring | FALSE | nonsummer
2024-05-22 03:00 | 2024-05-22 04:00 | Spring | FALSE | nonsummer
2024-05-22 04:00 | 2024-05-22 05:00 | Spring | FALSE | nonsummer
2024-05-22 05:00 | 2024-05-22 06:00 | Spring | FALSE | nonsummer
2024-05-22 06:00 | 2024-05-22 07:00 | Spring | FALSE | nonsummer
2024-05-22 07:00 | 2024-05-22 08:00 | Spring | FALSE | nonsummer
2024-05-22 08:00 | 2024-05-22 09:00 | Spring | FALSE | nonsummer
2024-05-22 09:00 | 2024-05-22 10:00 | Spring | FALSE | nonsummer
2024-05-22 10:00 | 2024-05-22 11:00 | Spring | FALSE | nonsummer
2024-05-22 11:00 | 2024-05-22 12:00 | Spring | FALSE | nonsummer
2024-05-22 12:00 | 2024-05-22 13:00 | Spring | FALSE | nonsummer
2024-05-22 13:00 | 2024-05-22 14:00 | Spring | FALSE | nonsummer
2024-05-22 14:00 | 2024-05-22 15:00 | Spring | FALSE | nonsummer
2024-05-22 15:00 | 2024-05-22 16:00 | Spring | FALSE | nonsummer
2024-05-22 16:00 | 2024-05-22 17:00 | Spring | FALSE | nonsummer
2024-05-22 17:00 | 2024-05-22 18:00 | Spring | TRUE | nonsummer
2024-05-22 18:00 | 2024-05-22 19:00 | Spring | TRUE | nonsummer
2024-05-22 19:00 | 2024-05-22 20:00 | Spring | TRUE | nonsummer
2024-05-22 20:00 | 2024-05-22 21:00 | Spring | TRUE | nonsummer
2024-05-22 21:00 | 2024-05-22 22:00 | Spring | TRUE | nonsummer
2024-05-22 22:00 | 2024-05-22 23:00 | Spring | FALSE | nonsummer
2024-05-22 23:00 | 2024-05-23 | Spring | FALSE | nonsummer
2024-05-23 | 2024-05-23 01:00 | Spring | FALSE | nonsummer
2024-05-23 01:00 | 2024-05-23 02:00 | Spring | FALSE | nonsummer
2024-05-23 02:00 | 2024-05-23 03:00 | Spring | FALSE | nonsummer
2024-05-23 03:00 | 2024-05-23 04:00 | Spring | FALSE | nonsummer
2024-05-23 04:00 | 2024-05-23 05:00 | Spring | FALSE | nonsummer
2024-05-23 05:00 | 2024-05-23 06:00 | Spring | FALSE | nonsummer
2024-05-23 06:00 | 2024-05-23 07:00 | Spring | FALSE | nonsummer
2024-05-23 07:00 | 2024-05-23 08:00 | Spring | FALSE | nonsummer
2024-05-23 08:00 | 2024-05-23 09:00 | Spring | FALSE | nonsummer
2024-05-23 09:00 | 2024-05-23 10:00 | Spring | FALSE | nonsummer
2024-05-23 10:00 | 2024-05-23 11:00 | Spring | FALSE | nonsummer
2024-05-23 11:00 | 2024-05-23 12:00 | Spring | FALSE | nonsummer
2024-05-23 12:00 | 2024-05-23 13:00 | Spring | FALSE | nonsummer
2024-05-23 13:00 | 2024-05-23 14:00 | Spring | FALSE | nonsummer
2024-05-23 14:00 | 2024-05-23 15:00 | Spring | FALSE | nonsummer
2024-05-23 15:00 | 2024-05-23 16:00 | Spring | FALSE | nonsummer
2024-05-23 16:00 | 2024-05-23 17:00 | Spring | FALSE | nonsummer
2024-05-23 17:00 | 2024-05-23 18:00 | Spring | TRUE | nonsummer
2024-05-23 18:00 | 2024-05-23 19:00 | Spring | TRUE | nonsummer
2024-05-23 19:00 | 2024-05-23 20:00 | Spring | TRUE | nonsummer
2024-05-23 20:00 | 2024-05-23 21:00 | Spring | TRUE | nonsummer
2024-05-23 21:00 | 2024-05-23 22:00 | Spring | TRUE | nonsummer
2024-05-23 22:00 | 2024-05-23 23:00 | Spring | FALSE | nonsummer
2024-05-23 23:00 | 2024-05-24 | Spring | FALSE | nonsummer
2024-05-24 | 2024-05-24 01:00 | Spring | FALSE | nonsummer
2024-05-24 01:00 | 2024-05-24 02:00 | Spring | FALSE | nonsummer
2024-05-24 02:00 | 2024-05-24 03:00 | Spring | FALSE | nonsummer
2024-05-24 03:00 | 2024-05-24 04:00 | Spring | FALSE | nonsummer
2024-05-24 04:00 | 2024-05-24 05:00 | Spring | FALSE | nonsummer
2024-05-24 05:00 | 2024-05-24 06:00 | Spring | FALSE | nonsummer
2024-05-24 06:00 | 2024-05-24 07:00 | Spring | FALSE | nonsummer
2024-05-24 07:00 | 2024-05-24 08:00 | Spring | FALSE | nonsummer
2024-05-24 08:00 | 2024-05-24 09:00 | Spring | FALSE | nonsummer
2024-05-24 09:00 | 2024-05-24 10:00 | Spring | FALSE | nonsummer
2024-05-24 10:00 | 2024-05-24 11:00 | Spring | FALSE | nonsummer
2024-05-24 11:00 | 2024-05-24 12:00 | Spring | FALSE | nonsummer
2024-05-24 12:00 | 2024-05-24 13:00 | Spring | FALSE | nonsummer
2024-05-24 13:00 | 2024-05-24 14:00 | Spring | FALSE | nonsummer
2024-05-24 14:00 | 2024-05-24 15:00 | Spring | FALSE | nonsummer
2024-05-24 15:00 | 2024-05-24 16:00 | Spring | FALSE | nonsummer
2024-05-24 16:00 | 2024-05-24 17:00 | Spring | FALSE | nonsummer
2024-05-24 17:00 | 2024-05-24 18:00 | Spring | TRUE | nonsummer
2024-05-24 18:00 | 2024-05-24 19:00 | Spring | TRUE | nonsummer
2024-05-24 19:00 | 2024-05-24 20:00 | Spring | TRUE | nonsummer
2024-05-24 20:00 | 2024-05-24 21:00 | Spring | TRUE | nonsummer
2024-05-24 21:00 | 2024-05-24 22:00 | Spring | TRUE | nonsummer
2024-05-24 22:00 | 2024-05-24 23:00 | Spring | FALSE | nonsummer
2024-05-24 23:00 | 2024-05-25 | Spring | FALSE | nonsummer
2024-05-25 | 2024-05-25 01:00 | Spring | FALSE | nonsummer
2024-05-25 01:00 | 2024-05-25 02:00 | Spring | FALSE | nonsummer
2024-05-25 02:00 | 2024-05-25 03:00 | Spring | FALSE | nonsummer
2024-05-25 03:00 | 2024-05-25 04:00 | Spring | FALSE | nonsummer
2024-05-25 04:00 | 2024-05-25 05:00 | Spring | FALSE | nonsummer
2024-05-25 05:00 | 2024-05-25 06:00 | Spring | FALSE | nonsummer
2024-05-25 06:00 | 2024-05-25 07:00 | Spring | FALSE | nonsummer
2024-05-25 07:00 | 2024-05-25 08:00 | Spring | FALSE | nonsummer
2024-05-25 08:00 | 2024-05-25 09:00 | Spring | FALSE | nonsummer
2024-05-25 09:00 | 2024-05-25 10:00 | Spring | FALSE | nonsummer
2024-05-25 10:00 | 2024-05-25 11:00 | Spring | FALSE | nonsummer
2024-05-25 11:00 | 2024-05-25 12:00 | Spring | FALSE | nonsummer
2024-05-25 12:00 | 2024-05-25 13:00 | Spring | FALSE | nonsummer
2024-05-25 13:00 | 2024-05-25 14:00 | Spring | FALSE | nonsummer
2024-05-25 14:00 | 2024-05-25 15:00 | Spring | FALSE | nonsummer
2024-05-25 15:00 | 2024-05-25 16:00 | Spring | FALSE | nonsummer
2024-05-25 16:00 | 2024-05-25 17:00 | Spring | FALSE | nonsummer
2024-05-25 17:00 | 2024-05-25 18:00 | Spring | TRUE | nonsummer
2024-05-25 18:00 | 2024-05-25 19:00 | Spring | TRUE | nonsummer
2024-05-25 19:00 | 2024-05-25 20:00 | Spring | TRUE | nonsummer
2024-05-25 20:00 | 2024-05-25 21:00 | Spring | TRUE | nonsummer
2024-05-25 21:00 | 2024-05-25 22:00 | Spring | TRUE | nonsummer
2024-05-25 22:00 | 2024-05-25 23:00 | Spring | FALSE | nonsummer
2024-05-25 23:00 | 2024-05-26 | Spring | FALSE | nonsummer
2024-05-26 | 2024-05-26 01:00 | Spring | FALSE | nonsummer
2024-05-26 01:00 | 2024-05-26 02:00 | Spring | FALSE | nonsummer
2024-05-26 02:00 | 2024-05-26 03:00 | Spring | FALSE | nonsummer
2024-05-26 03:00 | 2024-05-26 04:00 | Spring | FALSE | nonsummer
2024-05-26 04:00 | 2024-05-26 05:00 | Spring | FALSE | nonsummer
2024-05-26 05:00 | 2024-05-26 06:00 | Spring | FALSE | nonsummer
2024-05-26 06:00 | 2024-05-26 07:00 | Spring | FALSE | nonsummer
2024-05-26 07:00 | 2024-05-26 08:00 | Spring | FALSE | nonsummer
2024-05-26 08:00 | 2024-05-26 09:00 | Spring | FALSE | nonsummer
2024-05-26 09:00 | 2024-05-26 10:00 | Spring | FALSE | nonsummer
2024-05-26 10:00 | 2024-05-26 11:00 | Spring | FALSE | nonsummer
2024-05-26 11:00 | 2024-05-26 12:00 | Spring | FALSE | nonsummer
2024-05-26 12:00 | 2024-05-26 13:00 | Spring | FALSE | nonsummer
2024-05-26 13:00 | 2024-05-26 14:00 | Spring | FALSE | nonsummer
2024-05-26 14:00 | 2024-05-26 15:00 | Spring | FALSE | nonsummer
2024-05-26 15:00 | 2024-05-26 16:00 | Spring | FALSE | nonsummer
2024-05-26 16:00 | 2024-05-26 17:00 | Spring | FALSE | nonsummer
2024-05-26 17:00 | 2024-05-26 18:00 | Spring | TRUE | nonsummer
2024-05-26 18:00 | 2024-05-26 19:00 | Spring | TRUE | nonsummer
2024-05-26 19:00 | 2024-05-26 20:00 | Spring | TRUE | nonsummer
2024-05-26 20:00 | 2024-05-26 21:00 | Spring | TRUE | nonsummer
2024-05-26 21:00 | 2024-05-26 22:00 | Spring | TRUE | nonsummer
2024-05-26 22:00 | 2024-05-26 23:00 | Spring | FALSE | nonsummer
2024-05-26 23:00 | 2024-05-27 | Spring | FALSE | nonsummer
2024-05-27 | 2024-05-27 01:00 | Spring | FALSE | nonsummer
2024-05-27 01:00 | 2024-05-27 02:00 | Spring | FALSE | nonsummer
2024-05-27 02:00 | 2024-05-27 03:00 | Spring | FALSE | nonsummer
2024-05-27 03:00 | 2024-05-27 04:00 | Spring | FALSE | nonsummer
2024-05-27 04:00 | 2024-05-27 05:00 | Spring | FALSE | nonsummer
2024-05-27 05:00 | 2024-05-27 06:00 | Spring | FALSE | nonsummer
2024-05-27 06:00 | 2024-05-27 07:00 | Spring | FALSE | nonsummer
2024-05-27 07:00 | 2024-05-27 08:00 | Spring | FALSE | nonsummer
2024-05-27 08:00 | 2024-05-27 09:00 | Spring | FALSE | nonsummer
2024-05-27 09:00 | 2024-05-27 10:00 | Spring | FALSE | nonsummer
2024-05-27 10:00 | 2024-05-27 11:00 | Spring | FALSE | nonsummer
2024-05-27 11:00 | 2024-05-27 12:00 | Spring | FALSE | nonsummer
2024-05-27 12:00 | 2024-05-27 13:00 | Spring | FALSE | nonsummer
2024-05-27 13:00 | 2024-05-27 14:00 | Spring | FALSE | nonsummer
2024-05-27 14:00 | 2024-05-27 15:00 | Spring | FALSE | nonsummer
2024-05-27 15:00 | 2024-05-27 16:00 | Spring | FALSE | nonsummer
2024-05-27 16:00 | 2024-05-27 17:00 | Spring | FALSE | nonsummer
2024-05-27 17:00 | 2024-05-27 18:00 | Spring | TRUE | nonsummer
2024-05-27 18:00 | 2024-05-27 19:00 | Spring | TRUE | nonsummer
2024-05-27 19:00 | 2024-05-27 20:00 | Spring | TRUE | nonsummer
2024-05-27 20:00 | 2024-05-27 21:00 | Spring | TRUE | nonsummer
2024-05-27 21:00 | 2024-05-27 22:00 | Spring | TRUE | nonsummer
2024-05-27 22:00 | 2024-05-27 23:00 | Spring | FALSE | nonsummer
2024-05-27 23:00 | 2024-05-28 | Spring | FALSE | nonsummer
2024-05-28 | 2024-05-28 01:00 | Spring | FALSE | nonsummer
2024-05-28 01:00 | 2024-05-28 02:00 | Spring | FALSE | nonsummer
2024-05-28 02:00 | 2024-05-28 03:00 | Spring | FALSE | nonsummer
2024-05-28 03:00 | 2024-05-28 04:00 | Spring | FALSE | nonsummer
2024-05-28 04:00 | 2024-05-28 05:00 | Spring | FALSE | nonsummer
2024-05-28 05:00 | 2024-05-28 06:00 | Spring | FALSE | nonsummer
2024-05-28 06:00 | 2024-05-28 07:00 | Spring | FALSE | nonsummer
2024-05-28 07:00 | 2024-05-28 08:00 | Spring | FALSE | nonsummer
2024-05-28 08:00 | 2024-05-28 09:00 | Spring | FALSE | nonsummer
2024-05-28 09:00 | 2024-05-28 10:00 | Spring | FALSE | nonsummer
2024-05-28 10:00 | 2024-05-28 11:00 | Spring | FALSE | nonsummer
2024-05-28 11:00 | 2024-05-28 12:00 | Spring | FALSE | nonsummer
2024-05-28 12:00 | 2024-05-28 13:00 | Spring | FALSE | nonsummer
2024-05-28 13:00 | 2024-05-28 14:00 | Spring | FALSE | nonsummer
2024-05-28 14:00 | 2024-05-28 15:00 | Spring | FALSE | nonsummer
2024-05-28 15:00 | 2024-05-28 16:00 | Spring | FALSE | nonsummer
2024-05-28 16:00 | 2024-05-28 17:00 | Spring | FALSE | nonsummer
2024-05-28 17:00 | 2024-05-28 18:00 | Spring | TRUE | nonsummer
2024-05-28 18:00 | 2024-05-28 19:00 | Spring | TRUE | nonsummer
2024-05-28 19:00 | 2024-05-28 20:00 | Spring | TRUE | nonsummer
2024-05-28 20:00 | 2024-05-28 21:00 | Spring | TRUE | nonsummer
2024-05-28 21:00 | 2024-05-28 22:00 | Spring | TRUE | nonsummer
2024-05-28 22:00 | 2024-05-28 23:00 | Spring | FALSE | nonsummer
2024-05-28 23:00 | 2024-05-29 | Spring | FALSE | nonsummer
2024-05-29 | 2024-05-29 01:00 | Spring | FALSE | nonsummer
2024-05-29 01:00 | 2024-05-29 02:00 | Spring | FALSE | nonsummer
2024-05-29 02:00 | 2024-05-29 03:00 | Spring | FALSE | nonsummer
2024-05-29 03:00 | 2024-05-29 04:00 | Spring | FALSE | nonsummer
2024-05-29 04:00 | 2024-05-29 05:00 | Spring | FALSE | nonsummer
2024-05-29 05:00 | 2024-05-29 06:00 | Spring | FALSE | nonsummer
2024-05-29 06:00 | 2024-05-29 07:00 | Spring | FALSE | nonsummer
2024-05-29 07:00 | 2024-05-29 08:00 | Spring | FALSE | nonsummer
2024-05-29 08:00 | 2024-05-29 09:00 | Spring | FALSE | nonsummer
2024-05-29 09:00 | 2024-05-29 10:00 | Spring | FALSE | nonsummer
2024-05-29 10:00 | 2024-05-29 11:00 | Spring | FALSE | nonsummer
2024-05-29 11:00 | 2024-05-29 12:00 | Spring | FALSE | nonsummer
2024-05-29 12:00 | 2024-05-29 13:00 | Spring | FALSE | nonsummer
2024-05-29 13:00 | 2024-05-29 14:00 | Spring | FALSE | nonsummer
2024-05-29 14:00 | 2024-05-29 15:00 | Spring | FALSE | nonsummer
2024-05-29 15:00 | 2024-05-29 16:00 | Spring | FALSE | nonsummer
2024-05-29 16:00 | 2024-05-29 17:00 | Spring | FALSE | nonsummer
2024-05-29 17:00 | 2024-05-29 18:00 | Spring | TRUE | nonsummer
2024-05-29 18:00 | 2024-05-29 19:00 | Spring | TRUE | nonsummer
2024-05-29 19:00 | 2024-05-29 20:00 | Spring | TRUE | nonsummer
2024-05-29 20:00 | 2024-05-29 21:00 | Spring | TRUE | nonsummer
2024-05-29 21:00 | 2024-05-29 22:00 | Spring | TRUE | nonsummer
2024-05-29 22:00 | 2024-05-29 23:00 | Spring | FALSE | nonsummer
2024-05-29 23:00 | 2024-05-30 | Spring | FALSE | nonsummer
2024-05-30 | 2024-05-30 01:00 | Spring | FALSE | nonsummer
2024-05-30 01:00 | 2024-05-30 02:00 | Spring | FALSE | nonsummer
2024-05-30 02:00 | 2024-05-30 03:00 | Spring | FALSE | nonsummer
2024-05-30 03:00 | 2024-05-30 04:00 | Spring | FALSE | nonsummer
2024-05-30 04:00 | 2024-05-30 05:00 | Spring | FALSE | nonsummer
2024-05-30 05:00 | 2024-05-30 06:00 | Spring | FALSE | nonsummer
2024-05-30 06:00 | 2024-05-30 07:00 | Spring | FALSE | nonsummer
2024-05-30 07:00 | 2024-05-30 08:00 | Spring | FALSE | nonsummer
2024-05-30 08:00 | 2024-05-30 09:00 | Spring | FALSE | nonsummer
2024-05-30 09:00 | 2024-05-30 10:00 | Spring | FALSE | nonsummer
2024-05-30 10:00 | 2024-05-30 11:00 | Spring | FALSE | nonsummer
2024-05-30 11:00 | 2024-05-30 12:00 | Spring | FALSE | nonsummer
2024-05-30 12:00 | 2024-05-30 13:00 | Spring | FALSE | nonsummer
2024-05-30 13:00 | 2024-05-30 14:00 | Spring | FALSE | nonsummer
2024-05-30 14:00 | 2024-05-30 15:00 | Spring | FALSE | nonsummer
2024-05-30 15:00 | 2024-05-30 16:00 | Spring | FALSE | nonsummer
2024-05-30 16:00 | 2024-05-30 17:00 | Spring | FALSE | nonsummer
2024-05-30 17:00 | 2024-05-30 18:00 | Spring | TRUE | nonsummer
2024-05-30 18:00 | 2024-05-30 19:00 | Spring | TRUE | nonsummer
2024-05-30 19:00 | 2024-05-30 20:00 | Spring | TRUE | nonsummer
2024-05-30 20:00 | 2024-05-30 21:00 | Spring | TRUE | nonsummer
2024-05-30 21:00 | 2024-05-30 22:00 | Spring | TRUE | nonsummer
2024-05-30 22:00 | 2024-05-30 23:00 | Spring | FALSE | nonsummer
2024-05-30 23:00 | 2024-05-31 | Spring | FALSE | nonsummer
2024-05-31 | 2024-05-31 01:00 | Spring | FALSE | nonsummer
2024-05-31 01:00 | 2024-05-31 02:00 | Spring | FALSE | nonsummer
2024-05-31 02:00 | 2024-05-31 03:00 | Spring | FALSE | nonsummer
2024-05-31 03:00 | 2024-05-31 04:00 | Spring | FALSE | nonsummer
2024-05-31 04:00 | 2024-05-31 05:00 | Spring | FALSE | nonsummer
2024-05-31 05:00 | 2024-05-31 06:00 | Spring | FALSE | nonsummer
2024-05-31 06:00 | 2024-05-31 07:00 | Spring | FALSE | nonsummer
2024-05-31 07:00 | 2024-05-31 08:00 | Spring | FALSE | nonsummer
2024-05-31 08:00 | 2024-05-31 09:00 | Spring | FALSE | nonsummer
2024-05-31 09:00 | 2024-05-31 10:00 | Spring | FALSE | nonsummer
2024-05-31 10:00 | 2024-05-31 11:00 | Spring | FALSE | nonsummer
2024-05-31 11:00 | 2024-05-31 12:00 | Spring | FALSE | nonsummer
2024-05-31 12:00 | 2024-05-31 13:00 | Spring | FALSE | nonsummer
2024-05-31 13:00 | 2024-05-31 14:00 | Spring | FALSE | nonsummer
2024-05-31 14:00 | 2024-05-31 15:00 | Spring | FALSE | nonsummer
2024-05-31 15:00 | 2024-05-31 16:00 | Spring | FALSE | nonsummer
2024-05-31 16:00 | 2024-05-31 17:00 | Spring | FALSE | nonsummer
2024-05-31 17:00 | 2024-05-31 18:00 | Spring | TRUE | nonsummer
2024-05-31 18:00 | 2024-05-31 19:00 | Spring | TRUE | nonsummer
2024-05-31 19:00 | 2024-05-31 20:00 | Spring | TRUE | nonsummer
2024-05-31 20:00 | 2024-05-31 21:00 | Spring | TRUE | nonsummer
2024-05-31 21:00 | 2024-05-31 22:00 | Spring | TRUE | nonsummer
2024-05-31 22:00 | 2024-05-31 23:00 | Spring | FALSE | nonsummer
2024-05-31 23:00 | 2024-06-01 | Spring | FALSE | nonsummer
2024-06-01 | 2024-06-01 01:00 | Summer | FALSE | summer
2024-06-01 01:00 | 2024-06-01 02:00 | Summer | FALSE | summer
2024-06-01 02:00 | 2024-06-01 03:00 | Summer | FALSE | summer
2024-06-01 03:00 | 2024-06-01 04:00 | Summer | FALSE | summer
2024-06-01 04:00 | 2024-06-01 05:00 | Summer | FALSE | summer
2024-06-01 05:00 | 2024-06-01 06:00 | Summer | FALSE | summer
2024-06-01 06:00 | 2024-06-01 07:00 | Summer | FALSE | summer
2024-06-01 07:00 | 2024-06-01 08:00 | Summer | FALSE | summer
2024-06-01 08:00 | 2024-06-01 09:00 | Summer | FALSE | summer
2024-06-01 09:00 | 2024-06-01 10:00 | Summer | FALSE | summer
2024-06-01 10:00 | 2024-06-01 11:00 | Summer | FALSE | summer
2024-06-01 11:00 | 2024-06-01 12:00 | Summer | FALSE | summer
2024-06-01 12:00 | 2024-06-01 13:00 | Summer | FALSE | summer
2024-06-01 13:00 | 2024-06-01 14:00 | Summer | FALSE | summer
2024-06-01 14:00 | 2024-06-01 15:00 | Summer | FALSE | summer
2024-06-01 15:00 | 2024-06-01 16:00 | Summer | FALSE | summer
2024-06-01 16:00 | 2024-06-01 17:00 | Summer | TRUE | summer
2024-06-01 17:00 | 2024-06-01 18:00 | Summer | TRUE | summer
2024-06-01 18:00 | 2024-06-01 19:00 | Summer | TRUE | summer
2024-06-01 19:00 | 2024-06-01 20:00 | Summer | TRUE | summer
2024-06-01 20:00 | 2024-06-01 21:00 | Summer | TRUE | summer
2024-06-01 21:00 | 2024-06-01 22:00 | Summer | FALSE | summer
2024-06-01 22:00 | 2024-06-01 23:00 | Summer | FALSE | summer
2024-06-01 23:00 | 2024-06-02 | Summer | FALSE | summer
2024-06-02 | 2024-06-02 01:00 | Summer | FALSE | summer
2024-06-02 01:00 | 2024-06-02 02:00 | Summer | FALSE | summer
2024-06-02 02:00 | 2024-06-02 03:00 | Summer | FALSE | summer
2024-06-02 03:00 | 2024-06-02 04:00 | Summer | FALSE | summer
2024-06-02 04:00 | 2024-06-02 05:00 | Summer | FALSE | summer
2024-06-02 05:00 | 2024-06-02 06:00 | Summer | FALSE | summer
2024-06-02 06:00 | 2024-06-02 07:00 | Summer | FALSE | summer
2024-06-02 07:00 | 2024-06-02 08:00 | Summer | FALSE | summer
2024-06-02 08:00 | 2024-06-02 09:00 | Summer | FALSE | summer
2024-06-02 09:00 | 2024-06-02 10:00 | Summer | FALSE | summer
2024-06-02 10:00 | 2024-06-02 11:00 | Summer | FALSE | summer
2024-06-02 11:00 | 2024-06-02 12:00 | Summer | FALSE | summer
2024-06-02 12:00 | 2024-06-02 13:00 | Summer | FALSE | summer
2024-06-02 13:00 | 2024-06-02 14:00 | Summer | FALSE | summer
2024-06-02 14:00 | 2024-06-02 15:00 | Summer | FALSE | summer
2024-06-02 15:00 | 2024-06-02 16:00 | Summer | FALSE | summer
2024-06-02 16:00 | 2024-06-02 17:00 | Summer | TRUE | summer
2024-06-02 17:00 | 2024-06-02 18:00 | Summer | TRUE | summer
2024-06-02 18:00 | 2024-06-02 19:00 | Summer | TRUE | summer
2024-06-02 19:00 | 2024-06-02 20:00 | Summer | TRUE | summer
2024-06-02 20:00 | 2024-06-02 21:00 | Summer | TRUE | summer
2024-06-02 21:00 | 2024-06-02 22:00 | Summer | FALSE | summer
2024-06-02 22:00 | 2024-06-02 23:00 | Summer | FALSE | summer
2024-06-02 23:00 | 2024-06-03 | Summer | FALSE | summer
2024-06-03 | 2024-06-03 01:00 | Summer | FALSE | summer
2024-06-03 01:00 | 2024-06-03 02:00 | Summer | FALSE | summer
2024-06-03 02:00 | 2024-06-03 03:00 | Summer | FALSE | summer
2024-06-03 03:00 | 2024-06-03 04:00 | Summer | FALSE | summer
2024-06-03 04:00 | 2024-06-03 05:00 | Summer | FALSE | summer
2024-06-03 05:00 | 2024-06-03 06:00 | Summer | FALSE | summer
2024-06-03 06:00 | 2024-06-03 07:00 | Summer | FALSE | summer
2024-06-03 07:00 | 2024-06-03 08:00 | Summer | FALSE | summer
2024-06-03 08:00 | 2024-06-03 09:00 | Summer | FALSE | summer
2024-06-03 09:00 | 2024-06-03 10:00 | Summer | FALSE | summer
2024-06-03 10:00 | 2024-06-03 11:00 | Summer | FALSE | summer
2024-06-03 11:00 | 2024-06-03 12:00 | Summer | FALSE | summer
2024-06-03 12:00 | 2024-06-03 13:00 | Summer | FALSE | summer
2024-06-03 13:00 | 2024-06-03 14:00 | Summer | FALSE | summer
2024-06-03 14:00 | 2024-06-03 15:00 | Summer | FALSE | summer
2024-06-03 15:00 | 2024-06-03 16:00 | Summer | FALSE | summer
2024-06-03 16:00 | 2024-06-03 17:00 | Summer | TRUE | summer
2024-06-03 17:00 | 2024-06-03 18:00 | Summer | TRUE | summer
2024-06-03 18:00 | 2024-06-03 19:00 | Summer | TRUE | summer
2024-06-03 19:00 | 2024-06-03 20:00 | Summer | TRUE | summer
2024-06-03 20:00 | 2024-06-03 21:00 | Summer | TRUE | summer
2024-06-03 21:00 | 2024-06-03 22:00 | Summer | FALSE | summer
2024-06-03 22:00 | 2024-06-03 23:00 | Summer | FALSE | summer
2024-06-03 23:00 | 2024-06-04 | Summer | FALSE | summer
2024-06-04 | 2024-06-04 01:00 | Summer | FALSE | summer
2024-06-04 01:00 | 2024-06-04 02:00 | Summer | FALSE | summer
2024-06-04 02:00 | 2024-06-04 03:00 | Summer | FALSE | summer
2024-06-04 03:00 | 2024-06-04 04:00 | Summer | FALSE | summer
2024-06-04 04:00 | 2024-06-04 05:00 | Summer | FALSE | summer
2024-06-04 05:00 | 2024-06-04 06:00 | Summer | FALSE | summer
2024-06-04 06:00 | 2024-06-04 07:00 | Summer | FALSE | summer
2024-06-04 07:00 | 2024-06-04 08:00 | Summer | FALSE | summer
2024-06-04 08:00 | 2024-06-04 09:00 | Summer | FALSE | summer
2024-06-04 09:00 | 2024-06-04 10:00 | Summer | FALSE | summer
2024-06-04 10:00 | 2024-06-04 11:00 | Summer | FALSE | summer
2024-06-04 11:00 | 2024-06-04 12:00 | Summer | FALSE | summer
2024-06-04 12:00 | 2024-06-04 13:00 | Summer | FALSE | summer
2024-06-04 13:00 | 2024-06-04 14:00 | Summer | FALSE | summer
2024-06-04 14:00 | 2024-06-04 15:00 | Summer | FALSE | summer
2024-06-04 15:00 | 2024-06-04 16:00 | Summer | FALSE | summer
2024-06-04 16:00 | 2024-06-04 17:00 | Summer | TRUE | summer
2024-06-04 17:00 | 2024-06-04 18:00 | Summer | TRUE | summer
2024-06-04 18:00 | 2024-06-04 19:00 | Summer | TRUE | summer
2024-06-04 19:00 | 2024-06-04 20:00 | Summer | TRUE | summer
2024-06-04 20:00 | 2024-06-04 21:00 | Summer | TRUE | summer
2024-06-04 21:00 | 2024-06-04 22:00 | Summer | FALSE | summer
2024-06-04 22:00 | 2024-06-04 23:00 | Summer | FALSE | summer
2024-06-04 23:00 | 2024-06-05 | Summer | FALSE | summer
2024-06-05 | 2024-06-05 01:00 | Summer | FALSE | summer
2024-06-05 01:00 | 2024-06-05 02:00 | Summer | FALSE | summer
2024-06-05 02:00 | 2024-06-05 03:00 | Summer | FALSE | summer
2024-06-05 03:00 | 2024-06-05 04:00 | Summer | FALSE | summer
2024-06-05 04:00 | 2024-06-05 05:00 | Summer | FALSE | summer
2024-06-05 05:00 | 2024-06-05 06:00 | Summer | FALSE | summer
2024-06-05 06:00 | 2024-06-05 07:00 | Summer | FALSE | summer
2024-06-05 07:00 | 2024-06-05 08:00 | Summer | FALSE | summer
2024-06-05 08:00 | 2024-06-05 09:00 | Summer | FALSE | summer
2024-06-05 09:00 | 2024-06-05 10:00 | Summer | FALSE | summer
2024-06-05 10:00 | 2024-06-05 11:00 | Summer | FALSE | summer
2024-06-05 11:00 | 2024-06-05 12:00 | Summer | FALSE | summer
2024-06-05 12:00 | 2024-06-05 13:00 | Summer | FALSE | summer
2024-06-05 13:00 | 2024-06-05 14:00 | Summer | FALSE | summer
2024-06-05 14:00 | 2024-06-05 15:00 | Summer | FALSE | summer
2024-06-05 15:00 | 2024-06-05 16:00 | Summer | FALSE | summer
2024-06-05 16:00 | 2024-06-05 17:00 | Summer | TRUE | summer
2024-06-05 17:00 | 2024-06-05 18:00 | Summer | TRUE | summer
2024-06-05 18:00 | 2024-06-05 19:00 | Summer | TRUE | summer
2024-06-05 19:00 | 2024-06-05 20:00 | Summer | TRUE | summer
2024-06-05 20:00 | 2024-06-05 21:00 | Summer | TRUE | summer
2024-06-05 21:00 | 2024-06-05 22:00 | Summer | FALSE | summer
2024-06-05 22:00 | 2024-06-05 23:00 | Summer | FALSE | summer
2024-06-05 23:00 | 2024-06-06 | Summer | FALSE | summer
2024-06-06 | 2024-06-06 01:00 | Summer | FALSE | summer
2024-06-06 01:00 | 2024-06-06 02:00 | Summer | FALSE | summer
2024-06-06 02:00 | 2024-06-06 03:00 | Summer | FALSE | summer
2024-06-06 03:00 | 2024-06-06 04:00 | Summer | FALSE | summer
2024-06-06 04:00 | 2024-06-06 05:00 | Summer | FALSE | summer
2024-06-06 05:00 | 2024-06-06 06:00 | Summer | FALSE | summer
2024-06-06 06:00 | 2024-06-06 07:00 | Summer | FALSE | summer
2024-06-06 07:00 | 2024-06-06 08:00 | Summer | FALSE | summer
2024-06-06 08:00 | 2024-06-06 09:00 | Summer | FALSE | summer
2024-06-06 09:00 | 2024-06-06 10:00 | Summer | FALSE | summer
2024-06-06 10:00 | 2024-06-06 11:00 | Summer | FALSE | summer
2024-06-06 11:00 | 2024-06-06 12:00 | Summer | FALSE | summer
2024-06-06 12:00 | 2024-06-06 13:00 | Summer | FALSE | summer
2024-06-06 13:00 | 2024-06-06 14:00 | Summer | FALSE | summer
2024-06-06 14:00 | 2024-06-06 15:00 | Summer | FALSE | summer
2024-06-06 15:00 | 2024-06-06 16:00 | Summer | FALSE | summer
2024-06-06 16:00 | 2024-06-06 17:00 | Summer | TRUE | summer
2024-06-06 17:00 | 2024-06-06 18:00 | Summer | TRUE | summer
2024-06-06 18:00 | 2024-06-06 19:00 | Summer | TRUE | summer
2024-06-06 19:00 | 2024-06-06 20:00 | Summer | TRUE | summer
2024-06-06 20:00 | 2024-06-06 21:00 | Summer | TRUE | summer
2024-06-06 21:00 | 2024-06-06 22:00 | Summer | FALSE | summer
2024-06-06 22:00 | 2024-06-06 23:00 | Summer | FALSE | summer
2024-06-06 23:00 | 2024-06-07 | Summer | FALSE | summer
2024-06-07 | 2024-06-07 01:00 | Summer | FALSE | summer
2024-06-07 01:00 | 2024-06-07 02:00 | Summer | FALSE | summer
2024-06-07 02:00 | 2024-06-07 03:00 | Summer | FALSE | summer
2024-06-07 03:00 | 2024-06-07 04:00 | Summer | FALSE | summer
2024-06-07 04:00 | 2024-06-07 05:00 | Summer | FALSE | summer
2024-06-07 05:00 | 2024-06-07 06:00 | Summer | FALSE | summer
2024-06-07 06:00 | 2024-06-07 07:00 | Summer | FALSE | summer
2024-06-07 07:00 | 2024-06-07 08:00 | Summer | FALSE | summer
2024-06-07 08:00 | 2024-06-07 09:00 | Summer | FALSE | summer
2024-06-07 09:00 | 2024-06-07 10:00 | Summer | FALSE | summer
2024-06-07 10:00 | 2024-06-07 11:00 | Summer | FALSE | summer
2024-06-07 11:00 | 2024-06-07 12:00 | Summer | FALSE | summer
2024-06-07 12:00 | 2024-06-07 13:00 | Summer | FALSE | summer
2024-06-07 13:00 | 2024-06-07 14:00 | Summer | FALSE | summer
2024-06-07 14:00 | 2024-06-07 15:00 | Summer | FALSE | summer
2024-06-07 15:00 | 2024-06-07 16:00 | Summer | FALSE | summer
2024-06-07 16:00 | 2024-06-07 17:00 | Summer | TRUE | summer
2024-06-07 17:00 | 2024-06-07 18:00 | Summer | TRUE | summer
2024-06-07 18:00 | 2024-06-07 19:00 | Summer | TRUE | summer
2024-06-07 19:00 | 2024-06-07 20:00 | Summer | TRUE | summer
2024-06-07 20:00 | 2024-06-07 21:00 | Summer | TRUE | summer
2024-06-07 21:00 | 2024-06-07 22:00 | Summer | FALSE | summer
2024-06-07 22:00 | 2024-06-07 23:00 | Summer | FALSE | summer
2024-06-07 23:00 | 2024-06-08 | Summer | FALSE | summer
2024-06-08 | 2024-06-08 01:00 | Summer | FALSE | summer
2024-06-08 01:00 | 2024-06-08 02:00 | Summer | FALSE | summer
2024-06-08 02:00 | 2024-06-08 03:00 | Summer | FALSE | summer
2024-06-08 03:00 | 2024-06-08 04:00 | Summer | FALSE | summer
2024-06-08 04:00 | 2024-06-08 05:00 | Summer | FALSE | summer
2024-06-08 05:00 | 2024-06-08 06:00 | Summer | FALSE | summer
2024-06-08 06:00 | 2024-06-08 07:00 | Summer | FALSE | summer
2024-06-08 07:00 | 2024-06-08 08:00 | Summer | FALSE | summer
2024-06-08 08:00 | 2024-06-08 09:00 | Summer | FALSE | summer
2024-06-08 09:00 | 2024-06-08 10:00 | Summer | FALSE | summer
2024-06-08 10:00 | 2024-06-08 11:00 | Summer | FALSE | summer
2024-06-08 11:00 | 2024-06-08 12:00 | Summer | FALSE | summer
2024-06-08 12:00 | 2024-06-08 13:00 | Summer | FALSE | summer
2024-06-08 13:00 | 2024-06-08 14:00 | Summer | FALSE | summer
2024-06-08 14:00 | 2024-06-08 15:00 | Summer | FALSE | summer
2024-06-08 15:00 | 2024-06-08 16:00 | Summer | FALSE | summer
2024-06-08 16:00 | 2024-06-08 17:00 | Summer | TRUE | summer
2024-06-08 17:00 | 2024-06-08 18:00 | Summer | TRUE | summer
2024-06-08 18:00 | 2024-06-08 19:00 | Summer | TRUE | summer
2024-06-08 19:00 | 2024-06-08 20:00 | Summer | TRUE | summer
2024-06-08 20:00 | 2024-06-08 21:00 | Summer | TRUE | summer
2024-06-08 21:00 | 2024-06-08 22:00 | Summer | FALSE | summer
2024-06-08 22:00 | 2024-06-08 23:00 | Summer | FALSE | summer
2024-06-08 23:00 | 2024-06-09 | Summer | FALSE | summer
2024-06-09 | 2024-06-09 01:00 | Summer | FALSE | summer
2024-06-09 01:00 | 2024-06-09 02:00 | Summer | FALSE | summer
2024-06-09 02:00 | 2024-06-09 03:00 | Summer | FALSE | summer
2024-06-09 03:00 | 2024-06-09 04:00 | Summer | FALSE | summer
2024-06-09 04:00 | 2024-06-09 05:00 | Summer | FALSE | summer
2024-06-09 05:00 | 2024-06-09 06:00 | Summer | FALSE | summer
2024-06-09 06:00 | 2024-06-09 07:00 | Summer | FALSE | summer
2024-06-09 07:00 | 2024-06-09 08:00 | Summer | FALSE | summer
2024-06-09 08:00 | 2024-06-09 09:00 | Summer | FALSE | summer
2024-06-09 09:00 | 2024-06-09 10:00 | Summer | FALSE | summer
2024-06-09 10:00 | 2024-06-09 11:00 | Summer | FALSE | summer
2024-06-09 11:00 | 2024-06-09 12:00 | Summer | FALSE | summer
2024-06-09 12:00 | 2024-06-09 13:00 | Summer | FALSE | summer
2024-06-09 13:00 | 2024-06-09 14:00 | Summer | FALSE | summer
2024-06-09 14:00 | 2024-06-09 15:00 | Summer | FALSE | summer
2024-06-09 15:00 | 2024-06-09 16:00 | Summer | FALSE | summer
2024-06-09 16:00 | 2024-06-09 17:00 | Summer | TRUE | summer
2024-06-09 17:00 | 2024-06-09 18:00 | Summer | TRUE | summer
2024-06-09 18:00 | 2024-06-09 19:00 | Summer | TRUE | summer
2024-06-09 19:00 | 2024-06-09 20:00 | Summer | TRUE | summer
2024-06-09 20:00 | 2024-06-09 21:00 | Summer | TRUE | summer
2024-06-09 21:00 | 2024-06-09 22:00 | Summer | FALSE | summer
2024-06-09 22:00 | 2024-06-09 23:00 | Summer | FALSE | summer
2024-06-09 23:00 | 2024-06-10 | Summer | FALSE | summer
2024-06-10 | 2024-06-10 01:00 | Summer | FALSE | summer
2024-06-10 01:00 | 2024-06-10 02:00 | Summer | FALSE | summer
2024-06-10 02:00 | 2024-06-10 03:00 | Summer | FALSE | summer
2024-06-10 03:00 | 2024-06-10 04:00 | Summer | FALSE | summer
2024-06-10 04:00 | 2024-06-10 05:00 | Summer | FALSE | summer
2024-06-10 05:00 | 2024-06-10 06:00 | Summer | FALSE | summer
2024-06-10 06:00 | 2024-06-10 07:00 | Summer | FALSE | summer
2024-06-10 07:00 | 2024-06-10 08:00 | Summer | FALSE | summer
2024-06-10 08:00 | 2024-06-10 09:00 | Summer | FALSE | summer
2024-06-10 09:00 | 2024-06-10 10:00 | Summer | FALSE | summer
2024-06-10 10:00 | 2024-06-10 11:00 | Summer | FALSE | summer
2024-06-10 11:00 | 2024-06-10 12:00 | Summer | FALSE | summer
2024-06-10 12:00 | 2024-06-10 13:00 | Summer | FALSE | summer
2024-06-10 13:00 | 2024-06-10 14:00 | Summer | FALSE | summer
2024-06-10 14:00 | 2024-06-10 15:00 | Summer | FALSE | summer
2024-06-10 15:00 | 2024-06-10 16:00 | Summer | FALSE | summer
2024-06-10 16:00 | 2024-06-10 17:00 | Summer | TRUE | summer
2024-06-10 17:00 | 2024-06-10 18:00 | Summer | TRUE | summer
2024-06-10 18:00 | 2024-06-10 19:00 | Summer | TRUE | summer
2024-06-10 19:00 | 2024-06-10 20:00 | Summer | TRUE | summer
2024-06-10 20:00 | 2024-06-10 21:00 | Summer | TRUE | summer
2024-06-10 21:00 | 2024-06-10 22:00 | Summer | FALSE | summer
2024-06-10 22:00 | 2024-06-10 23:00 | Summer | FALSE | summer
2024-06-10 23:00 | 2024-06-11 | Summer | FALSE | summer
2024-06-11 | 2024-06-11 01:00 | Summer | FALSE | summer
2024-06-11 01:00 | 2024-06-11 02:00 | Summer | FALSE | summer
2024-06-11 02:00 | 2024-06-11 03:00 | Summer | FALSE | summer
2024-06-11 03:00 | 2024-06-11 04:00 | Summer | FALSE | summer
2024-06-11 04:00 | 2024-06-11 05:00 | Summer | FALSE | summer
2024-06-11 05:00 | 2024-06-11 06:00 | Summer | FALSE | summer
2024-06-11 06:00 | 2024-06-11 07:00 | Summer | FALSE | summer
2024-06-11 07:00 | 2024-06-11 08:00 | Summer | FALSE | summer
2024-06-11 08:00 | 2024-06-11 09:00 | Summer | FALSE | summer
2024-06-11 09:00 | 2024-06-11 10:00 | Summer | FALSE | summer
2024-06-11 10:00 | 2024-06-11 11:00 | Summer | FALSE | summer
2024-06-11 11:00 | 2024-06-11 12:00 | Summer | FALSE | summer
2024-06-11 12:00 | 2024-06-11 13:00 | Summer | FALSE | summer
2024-06-11 13:00 | 2024-06-11 14:00 | Summer | FALSE | summer
2024-06-11 14:00 | 2024-06-11 15:00 | Summer | FALSE | summer
2024-06-11 15:00 | 2024-06-11 16:00 | Summer | FALSE | summer
2024-06-11 16:00 | 2024-06-11 17:00 | Summer | TRUE | summer
2024-06-11 17:00 | 2024-06-11 18:00 | Summer | TRUE | summer
2024-06-11 18:00 | 2024-06-11 19:00 | Summer | TRUE | summer
2024-06-11 19:00 | 2024-06-11 20:00 | Summer | TRUE | summer
2024-06-11 20:00 | 2024-06-11 21:00 | Summer | TRUE | summer
2024-06-11 21:00 | 2024-06-11 22:00 | Summer | FALSE | summer
2024-06-11 22:00 | 2024-06-11 23:00 | Summer | FALSE | summer
2024-06-11 23:00 | 2024-06-12 | Summer | FALSE | summer
2024-06-12 | 2024-06-12 01:00 | Summer | FALSE | summer
2024-06-12 01:00 | 2024-06-12 02:00 | Summer | FALSE | summer
2024-06-12 02:00 | 2024-06-12 03:00 | Summer | FALSE | summer
2024-06-12 03:00 | 2024-06-12 04:00 | Summer | FALSE | summer
2024-06-12 04:00 | 2024-06-12 05:00 | Summer | FALSE | summer
2024-06-12 05:00 | 2024-06-12 06:00 | Summer | FALSE | summer
2024-06-12 06:00 | 2024-06-12 07:00 | Summer | FALSE | summer
2024-06-12 07:00 | 2024-06-12 08:00 | Summer | FALSE | summer
2024-06-12 08:00 | 2024-06-12 09:00 | Summer | FALSE | summer
2024-06-12 09:00 | 2024-06-12 10:00 | Summer | FALSE | summer
2024-06-12 10:00 | 2024-06-12 11:00 | Summer | FALSE | summer
2024-06-12 11:00 | 2024-06-12 12:00 | Summer | FALSE | summer
2024-06-12 12:00 | 2024-06-12 13:00 | Summer | FALSE | summer
2024-06-12 13:00 | 2024-06-12 14:00 | Summer | FALSE | summer
2024-06-12 14:00 | 2024-06-12 15:00 | Summer | FALSE | summer
2024-06-12 15:00 | 2024-06-12 16:00 | Summer | FALSE | summer
2024-06-12 16:00 | 2024-06-12 17:00 | Summer | TRUE | summer
2024-06-12 17:00 | 2024-06-12 18:00 | Summer | TRUE | summer
2024-06-12 18:00 | 2024-06-12 19:00 | Summer | TRUE | summer
2024-06-12 19:00 | 2024-06-12 20:00 | Summer | TRUE | summer
2024-06-12 20:00 | 2024-06-12 21:00 | Summer | TRUE | summer
2024-06-12 21:00 | 2024-06-12 22:00 | Summer | FALSE | summer
2024-06-12 22:00 | 2024-06-12 23:00 | Summer | FALSE | summer
2024-06-12 23:00 | 2024-06-13 | Summer | FALSE | summer
2024-06-13 | 2024-06-13 01:00 | Summer | FALSE | summer
2024-06-13 01:00 | 2024-06-13 02:00 | Summer | FALSE | summer
2024-06-13 02:00 | 2024-06-13 03:00 | Summer | FALSE | summer
2024-06-13 03:00 | 2024-06-13 04:00 | Summer | FALSE | summer
2024-06-13 04:00 | 2024-06-13 05:00 | Summer | FALSE | summer
2024-06-13 05:00 | 2024-06-13 06:00 | Summer | FALSE | summer
2024-06-13 06:00 | 2024-06-13 07:00 | Summer | FALSE | summer
2024-06-13 07:00 | 2024-06-13 08:00 | Summer | FALSE | summer
2024-06-13 08:00 | 2024-06-13 09:00 | Summer | FALSE | summer
2024-06-13 09:00 | 2024-06-13 10:00 | Summer | FALSE | summer
2024-06-13 10:00 | 2024-06-13 11:00 | Summer | FALSE | summer
2024-06-13 11:00 | 2024-06-13 12:00 | Summer | FALSE | summer
2024-06-13 12:00 | 2024-06-13 13:00 | Summer | FALSE | summer
2024-06-13 13:00 | 2024-06-13 14:00 | Summer | FALSE | summer
2024-06-13 14:00 | 2024-06-13 15:00 | Summer | FALSE | summer
2024-06-13 15:00 | 2024-06-13 16:00 | Summer | FALSE | summer
2024-06-13 16:00 | 2024-06-13 17:00 | Summer | TRUE | summer
2024-06-13 17:00 | 2024-06-13 18:00 | Summer | TRUE | summer
2024-06-13 18:00 | 2024-06-13 19:00 | Summer | TRUE | summer
2024-06-13 19:00 | 2024-06-13 20:00 | Summer | TRUE | summer
2024-06-13 20:00 | 2024-06-13 21:00 | Summer | TRUE | summer
2024-06-13 21:00 | 2024-06-13 22:00 | Summer | FALSE | summer
2024-06-13 22:00 | 2024-06-13 23:00 | Summer | FALSE | summer
2024-06-13 23:00 | 2024-06-14 | Summer | FALSE | summer
2024-06-14 | 2024-06-14 01:00 | Summer | FALSE | summer
2024-06-14 01:00 | 2024-06-14 02:00 | Summer | FALSE | summer
2024-06-14 02:00 | 2024-06-14 03:00 | Summer | FALSE | summer
2024-06-14 03:00 | 2024-06-14 04:00 | Summer | FALSE | summer
2024-06-14 04:00 | 2024-06-14 05:00 | Summer | FALSE | summer
2024-06-14 05:00 | 2024-06-14 06:00 | Summer | FALSE | summer
2024-06-14 06:00 | 2024-06-14 07:00 | Summer | FALSE | summer
2024-06-14 07:00 | 2024-06-14 08:00 | Summer | FALSE | summer
2024-06-14 08:00 | 2024-06-14 09:00 | Summer | FALSE | summer
2024-06-14 09:00 | 2024-06-14 10:00 | Summer | FALSE | summer
2024-06-14 10:00 | 2024-06-14 11:00 | Summer | FALSE | summer
2024-06-14 11:00 | 2024-06-14 12:00 | Summer | FALSE | summer
2024-06-14 12:00 | 2024-06-14 13:00 | Summer | FALSE | summer
2024-06-14 13:00 | 2024-06-14 14:00 | Summer | FALSE | summer
2024-06-14 14:00 | 2024-06-14 15:00 | Summer | FALSE | summer
2024-06-14 15:00 | 2024-06-14 16:00 | Summer | FALSE | summer
2024-06-14 16:00 | 2024-06-14 17:00 | Summer | TRUE | summer
2024-06-14 17:00 | 2024-06-14 18:00 | Summer | TRUE | summer
2024-06-14 18:00 | 2024-06-14 19:00 | Summer | TRUE | summer
2024-06-14 19:00 | 2024-06-14 20:00 | Summer | TRUE | summer
2024-06-14 20:00 | 2024-06-14 21:00 | Summer | TRUE | summer
2024-06-14 21:00 | 2024-06-14 22:00 | Summer | FALSE | summer
2024-06-14 22:00 | 2024-06-14 23:00 | Summer | FALSE | summer
2024-06-14 23:00 | 2024-06-15 | Summer | FALSE | summer
2024-06-15 | 2024-06-15 01:00 | Summer | FALSE | summer
2024-06-15 01:00 | 2024-06-15 02:00 | Summer | FALSE | summer
2024-06-15 02:00 | 2024-06-15 03:00 | Summer | FALSE | summer
2024-06-15 03:00 | 2024-06-15 04:00 | Summer | FALSE | summer
2024-06-15 04:00 | 2024-06-15 05:00 | Summer | FALSE | summer
2024-06-15 05:00 | 2024-06-15 06:00 | Summer | FALSE | summer
2024-06-15 06:00 | 2024-06-15 07:00 | Summer | FALSE | summer
2024-06-15 07:00 | 2024-06-15 08:00 | Summer | FALSE | summer
2024-06-15 08:00 | 2024-06-15 09:00 | Summer | FALSE | summer
2024-06-15 09:00 | 2024-06-15 10:00 | Summer | FALSE | summer
2024-06-15 10:00 | 2024-06-15 11:00 | Summer | FALSE | summer
2024-06-15 11:00 | 2024-06-15 12:00 | Summer | FALSE | summer
2024-06-15 12:00 | 2024-06-15 13:00 | Summer | FALSE | summer
2024-06-15 13:00 | 2024-06-15 14:00 | Summer | FALSE | summer
2024-06-15 14:00 | 2024-06-15 15:00 | Summer | FALSE | summer
2024-06-15 15:00 | 2024-06-15 16:00 | Summer | FALSE | summer
2024-06-15 16:00 | 2024-06-15 17:00 | Summer | TRUE | summer
2024-06-15 17:00 | 2024-06-15 18:00 | Summer | TRUE | summer
2024-06-15 18:00 | 2024-06-15 19:00 | Summer | TRUE | summer
2024-06-15 19:00 | 2024-06-15 20:00 | Summer | TRUE | summer
2024-06-15 20:00 | 2024-06-15 21:00 | Summer | TRUE | summer
2024-06-15 21:00 | 2024-06-15 22:00 | Summer | FALSE | summer
2024-06-15 22:00 | 2024-06-15 23:00 | Summer | FALSE | summer
2024-06-15 23:00 | 2024-06-16 | Summer | FALSE | summer
2024-06-16 | 2024-06-16 01:00 | Summer | FALSE | summer
2024-06-16 01:00 | 2024-06-16 02:00 | Summer | FALSE | summer
2024-06-16 02:00 | 2024-06-16 03:00 | Summer | FALSE | summer
2024-06-16 03:00 | 2024-06-16 04:00 | Summer | FALSE | summer
2024-06-16 04:00 | 2024-06-16 05:00 | Summer | FALSE | summer
2024-06-16 05:00 | 2024-06-16 06:00 | Summer | FALSE | summer
2024-06-16 06:00 | 2024-06-16 07:00 | Summer | FALSE | summer
2024-06-16 07:00 | 2024-06-16 08:00 | Summer | FALSE | summer
2024-06-16 08:00 | 2024-06-16 09:00 | Summer | FALSE | summer
2024-06-16 09:00 | 2024-06-16 10:00 | Summer | FALSE | summer
2024-06-16 10:00 | 2024-06-16 11:00 | Summer | FALSE | summer
2024-06-16 11:00 | 2024-06-16 12:00 | Summer | FALSE | summer
2024-06-16 12:00 | 2024-06-16 13:00 | Summer | FALSE | summer
2024-06-16 13:00 | 2024-06-16 14:00 | Summer | FALSE | summer
2024-06-16 14:00 | 2024-06-16 15:00 | Summer | FALSE | summer
2024-06-16 15:00 | 2024-06-16 16:00 | Summer | FALSE | summer
2024-06-16 16:00 | 2024-06-16 17:00 | Summer | TRUE | summer
2024-06-16 17:00 | 2024-06-16 18:00 | Summer | TRUE | summer
2024-06-16 18:00 | 2024-06-16 19:00 | Summer | TRUE | summer
2024-06-16 19:00 | 2024-06-16 20:00 | Summer | TRUE | summer
2024-06-16 20:00 | 2024-06-16 21:00 | Summer | TRUE | summer
2024-06-16 21:00 | 2024-06-16 22:00 | Summer | FALSE | summer
2024-06-16 22:00 | 2024-06-16 23:00 | Summer | FALSE | summer
2024-06-16 23:00 | 2024-06-17 | Summer | FALSE | summer
2024-06-17 | 2024-06-17 01:00 | Summer | FALSE | summer
2024-06-17 01:00 | 2024-06-17 02:00 | Summer | FALSE | summer
2024-06-17 02:00 | 2024-06-17 03:00 | Summer | FALSE | summer
2024-06-17 03:00 | 2024-06-17 04:00 | Summer | FALSE | summer
2024-06-17 04:00 | 2024-06-17 05:00 | Summer | FALSE | summer
2024-06-17 05:00 | 2024-06-17 06:00 | Summer | FALSE | summer
2024-06-17 06:00 | 2024-06-17 07:00 | Summer | FALSE | summer
2024-06-17 07:00 | 2024-06-17 08:00 | Summer | FALSE | summer
2024-06-17 08:00 | 2024-06-17 09:00 | Summer | FALSE | summer
2024-06-17 09:00 | 2024-06-17 10:00 | Summer | FALSE | summer
2024-06-17 10:00 | 2024-06-17 11:00 | Summer | FALSE | summer
2024-06-17 11:00 | 2024-06-17 12:00 | Summer | FALSE | summer
2024-06-17 12:00 | 2024-06-17 13:00 | Summer | FALSE | summer
2024-06-17 13:00 | 2024-06-17 14:00 | Summer | FALSE | summer
2024-06-17 14:00 | 2024-06-17 15:00 | Summer | FALSE | summer
2024-06-17 15:00 | 2024-06-17 16:00 | Summer | FALSE | summer
2024-06-17 16:00 | 2024-06-17 17:00 | Summer | TRUE | summer
2024-06-17 17:00 | 2024-06-17 18:00 | Summer | TRUE | summer
2024-06-17 18:00 | 2024-06-17 19:00 | Summer | TRUE | summer
2024-06-17 19:00 | 2024-06-17 20:00 | Summer | TRUE | summer
2024-06-17 20:00 | 2024-06-17 21:00 | Summer | TRUE | summer
2024-06-17 21:00 | 2024-06-17 22:00 | Summer | FALSE | summer
2024-06-17 22:00 | 2024-06-17 23:00 | Summer | FALSE | summer
2024-06-17 23:00 | 2024-06-18 | Summer | FALSE | summer
2024-06-18 | 2024-06-18 01:00 | Summer | FALSE | summer
2024-06-18 01:00 | 2024-06-18 02:00 | Summer | FALSE | summer
2024-06-18 02:00 | 2024-06-18 03:00 | Summer | FALSE | summer
2024-06-18 03:00 | 2024-06-18 04:00 | Summer | FALSE | summer
2024-06-18 04:00 | 2024-06-18 05:00 | Summer | FALSE | summer
2024-06-18 05:00 | 2024-06-18 06:00 | Summer | FALSE | summer
2024-06-18 06:00 | 2024-06-18 07:00 | Summer | FALSE | summer
2024-06-18 07:00 | 2024-06-18 08:00 | Summer | FALSE | summer
2024-06-18 08:00 | 2024-06-18 09:00 | Summer | FALSE | summer
2024-06-18 09:00 | 2024-06-18 10:00 | Summer | FALSE | summer
2024-06-18 10:00 | 2024-06-18 11:00 | Summer | FALSE | summer
2024-06-18 11:00 | 2024-06-18 12:00 | Summer | FALSE | summer
2024-06-18 12:00 | 2024-06-18 13:00 | Summer | FALSE | summer
2024-06-18 13:00 | 2024-06-18 14:00 | Summer | FALSE | summer
2024-06-18 14:00 | 2024-06-18 15:00 | Summer | FALSE | summer
2024-06-18 15:00 | 2024-06-18 16:00 | Summer | FALSE | summer
2024-06-18 16:00 | 2024-06-18 17:00 | Summer | TRUE | summer
2024-06-18 17:00 | 2024-06-18 18:00 | Summer | TRUE | summer
2024-06-18 18:00 | 2024-06-18 19:00 | Summer | TRUE | summer
2024-06-18 19:00 | 2024-06-18 20:00 | Summer | TRUE | summer
2024-06-18 20:00 | 2024-06-18 21:00 | Summer | TRUE | summer
2024-06-18 21:00 | 2024-06-18 22:00 | Summer | FALSE | summer
2024-06-18 22:00 | 2024-06-18 23:00 | Summer | FALSE | summer
2024-06-18 23:00 | 2024-06-19 | Summer | FALSE | summer
2024-06-19 | 2024-06-19 01:00 | Summer | FALSE | summer
2024-06-19 01:00 | 2024-06-19 02:00 | Summer | FALSE | summer
2024-06-19 02:00 | 2024-06-19 03:00 | Summer | FALSE | summer
2024-06-19 03:00 | 2024-06-19 04:00 | Summer | FALSE | summer
2024-06-19 04:00 | 2024-06-19 05:00 | Summer | FALSE | summer
2024-06-19 05:00 | 2024-06-19 06:00 | Summer | FALSE | summer
2024-06-19 06:00 | 2024-06-19 07:00 | Summer | FALSE | summer
2024-06-19 07:00 | 2024-06-19 08:00 | Summer | FALSE | summer
2024-06-19 08:00 | 2024-06-19 09:00 | Summer | FALSE | summer
2024-06-19 09:00 | 2024-06-19 10:00 | Summer | FALSE | summer
2024-06-19 10:00 | 2024-06-19 11:00 | Summer | FALSE | summer
2024-06-19 11:00 | 2024-06-19 12:00 | Summer | FALSE | summer
2024-06-19 12:00 | 2024-06-19 13:00 | Summer | FALSE | summer
2024-06-19 13:00 | 2024-06-19 14:00 | Summer | FALSE | summer
2024-06-19 14:00 | 2024-06-19 15:00 | Summer | FALSE | summer
2024-06-19 15:00 | 2024-06-19 16:00 | Summer | FALSE | summer
2024-06-19 16:00 | 2024-06-19 17:00 | Summer | TRUE | summer
2024-06-19 17:00 | 2024-06-19 18:00 | Summer | TRUE | summer
2024-06-19 18:00 | 2024-06-19 19:00 | Summer | TRUE | summer
2024-06-19 19:00 | 2024-06-19 20:00 | Summer | TRUE | summer
2024-06-19 20:00 | 2024-06-19 21:00 | Summer | TRUE | summer
2024-06-19 21:00 | 2024-06-19 22:00 | Summer | FALSE | summer
2024-06-19 22:00 | 2024-06-19 23:00 | Summer | FALSE | summer
2024-06-19 23:00 | 2024-06-20 | Summer | FALSE | summer
2024-06-20 | 2024-06-20 01:00 | Summer | FALSE | summer
2024-06-20 01:00 | 2024-06-20 02:00 | Summer | FALSE | summer
2024-06-20 02:00 | 2024-06-20 03:00 | Summer | FALSE | summer
2024-06-20 03:00 | 2024-06-20 04:00 | Summer | FALSE | summer
2024-06-20 04:00 | 2024-06-20 05:00 | Summer | FALSE | summer
2024-06-20 05:00 | 2024-06-20 06:00 | Summer | FALSE | summer
2024-06-20 06:00 | 2024-06-20 07:00 | Summer | FALSE | summer
2024-06-20 07:00 | 2024-06-20 08:00 | Summer | FALSE | summer
2024-06-20 08:00 | 2024-06-20 09:00 | Summer | FALSE | summer
2024-06-20 09:00 | 2024-06-20 10:00 | Summer | FALSE | summer
2024-06-20 10:00 | 2024-06-20 11:00 | Summer | FALSE | summer
2024-06-20 11:00 | 2024-06-20 12:00 | Summer | FALSE | summer
2024-06-20 12:00 | 2024-06-20 13:00 | Summer | FALSE | summer
2024-06-20 13:00 | 2024-06-20 14:00 | Summer | FALSE | summer
2024-06-20 14:00 | 2024-06-20 15:00 | Summer | FALSE | summer
2024-06-20 15:00 | 2024-06-20 16:00 | Summer | FALSE | summer
2024-06-20 16:00 | 2024-06-20 17:00 | Summer | TRUE | summer
2024-06-20 17:00 | 2024-06-20 18:00 | Summer | TRUE | summer
2024-06-20 18:00 | 2024-06-20 19:00 | Summer | TRUE | summer
2024-06-20 19:00 | 2024-06-20 20:00 | Summer | TRUE | summer
2024-06-20 20:00 | 2024-06-20 21:00 | Summer | TRUE | summer
2024-06-20 21:00 | 2024-06-20 22:00 | Summer | FALSE | summer
2024-06-20 22:00 | 2024-06-20 23:00 | Summer | FALSE | summer
2024-06-20 23:00 | 2024-06-21 | Summer | FALSE | summer
2024-06-21 | 2024-06-21 01:00 | Summer | FALSE | summer
2024-06-21 01:00 | 2024-06-21 02:00 | Summer | FALSE | summer
2024-06-21 02:00 | 2024-06-21 03:00 | Summer | FALSE | summer
2024-06-21 03:00 | 2024-06-21 04:00 | Summer | FALSE | summer
2024-06-21 04:00 | 2024-06-21 05:00 | Summer | FALSE | summer
2024-06-21 05:00 | 2024-06-21 06:00 | Summer | FALSE | summer
2024-06-21 06:00 | 2024-06-21 07:00 | Summer | FALSE | summer
2024-06-21 07:00 | 2024-06-21 08:00 | Summer | FALSE | summer
2024-06-21 08:00 | 2024-06-21 09:00 | Summer | FALSE | summer
2024-06-21 09:00 | 2024-06-21 10:00 | Summer | FALSE | summer
2024-06-21 10:00 | 2024-06-21 11:00 | Summer | FALSE | summer
2024-06-21 11:00 | 2024-06-21 12:00 | Summer | FALSE | summer
2024-06-21 12:00 | 2024-06-21 13:00 | Summer | FALSE | summer
2024-06-21 13:00 | 2024-06-21 14:00 | Summer | FALSE | summer
2024-06-21 14:00 | 2024-06-21 15:00 | Summer | FALSE | summer
2024-06-21 15:00 | 2024-06-21 16:00 | Summer | FALSE | summer
2024-06-21 16:00 | 2024-06-21 17:00 | Summer | TRUE | summer
2024-06-21 17:00 | 2024-06-21 18:00 | Summer | TRUE | summer
2024-06-21 18:00 | 2024-06-21 19:00 | Summer | TRUE | summer
2024-06-21 19:00 | 2024-06-21 20:00 | Summer | TRUE | summer
2024-06-21 20:00 | 2024-06-21 21:00 | Summer | TRUE | summer
2024-06-21 21:00 | 2024-06-21 22:00 | Summer | FALSE | summer
2024-06-21 22:00 | 2024-06-21 23:00 | Summer | FALSE | summer
2024-06-21 23:00 | 2024-06-22 | Summer | FALSE | summer
2024-06-22 | 2024-06-22 01:00 | Summer | FALSE | summer
2024-06-22 01:00 | 2024-06-22 02:00 | Summer | FALSE | summer
2024-06-22 02:00 | 2024-06-22 03:00 | Summer | FALSE | summer
2024-06-22 03:00 | 2024-06-22 04:00 | Summer | FALSE | summer
2024-06-22 04:00 | 2024-06-22 05:00 | Summer | FALSE | summer
2024-06-22 05:00 | 2024-06-22 06:00 | Summer | FALSE | summer
2024-06-22 06:00 | 2024-06-22 07:00 | Summer | FALSE | summer
2024-06-22 07:00 | 2024-06-22 08:00 | Summer | FALSE | summer
2024-06-22 08:00 | 2024-06-22 09:00 | Summer | FALSE | summer
2024-06-22 09:00 | 2024-06-22 10:00 | Summer | FALSE | summer
2024-06-22 10:00 | 2024-06-22 11:00 | Summer | FALSE | summer
2024-06-22 11:00 | 2024-06-22 12:00 | Summer | FALSE | summer
2024-06-22 12:00 | 2024-06-22 13:00 | Summer | FALSE | summer
2024-06-22 13:00 | 2024-06-22 14:00 | Summer | FALSE | summer
2024-06-22 14:00 | 2024-06-22 15:00 | Summer | FALSE | summer
2024-06-22 15:00 | 2024-06-22 16:00 | Summer | FALSE | summer
2024-06-22 16:00 | 2024-06-22 17:00 | Summer | TRUE | summer
2024-06-22 17:00 | 2024-06-22 18:00 | Summer | TRUE | summer
2024-06-22 18:00 | 2024-06-22 19:00 | Summer | TRUE | summer
2024-06-22 19:00 | 2024-06-22 20:00 | Summer | TRUE | summer
2024-06-22 20:00 | 2024-06-22 21:00 | Summer | TRUE | summer
2024-06-22 21:00 | 2024-06-22 22:00 | Summer | FALSE | summer
2024-06-22 22:00 | 2024-06-22 23:00 | Summer | FALSE | summer
2024-06-22 23:00 | 2024-06-23 | Summer | FALSE | summer
2024-06-23 | 2024-06-23 01:00 | Summer | FALSE | summer
2024-06-23 01:00 | 2024-06-23 02:00 | Summer | FALSE | summer
2024-06-23 02:00 | 2024-06-23 03:00 | Summer | FALSE | summer
2024-06-23 03:00 | 2024-06-23 04:00 | Summer | FALSE | summer
2024-06-23 04:00 | 2024-06-23 05:00 | Summer | FALSE | summer
2024-06-23 05:00 | 2024-06-23 06:00 | Summer | FALSE | summer
2024-06-23 06:00 | 2024-06-23 07:00 | Summer | FALSE | summer
2024-06-23 07:00 | 2024-06-23 08:00 | Summer | FALSE | summer
2024-06-23 08:00 | 2024-06-23 09:00 | Summer | FALSE | summer
2024-06-23 09:00 | 2024-06-23 10:00 | Summer | FALSE | summer
2024-06-23 10:00 | 2024-06-23 11:00 | Summer | FALSE | summer
2024-06-23 11:00 | 2024-06-23 12:00 | Summer | FALSE | summer
2024-06-23 12:00 | 2024-06-23 13:00 | Summer | FALSE | summer
2024-06-23 13:00 | 2024-06-23 14:00 | Summer | FALSE | summer
2024-06-23 14:00 | 2024-06-23 15:00 | Summer | FALSE | summer
2024-06-23 15:00 | 2024-06-23 16:00 | Summer | FALSE | summer
2024-06-23 16:00 | 2024-06-23 17:00 | Summer | TRUE | summer
2024-06-23 17:00 | 2024-06-23 18:00 | Summer | TRUE | summer
2024-06-23 18:00 | 2024-06-23 19:00 | Summer | TRUE | summer
2024-06-23 19:00 | 2024-06-23 20:00 | Summer | TRUE | summer
2024-06-23 20:00 | 2024-06-23 21:00 | Summer | TRUE | summer
2024-06-23 21:00 | 2024-06-23 22:00 | Summer | FALSE | summer
2024-06-23 22:00 | 2024-06-23 23:00 | Summer | FALSE | summer
2024-06-23 23:00 | 2024-06-24 | Summer | FALSE | summer
2024-06-24 | 2024-06-24 01:00 | Summer | FALSE | summer
2024-06-24 01:00 | 2024-06-24 02:00 | Summer | FALSE | summer
2024-06-24 02:00 | 2024-06-24 03:00 | Summer | FALSE | summer
2024-06-24 03:00 | 2024-06-24 04:00 | Summer | FALSE | summer
2024-06-24 04:00 | 2024-06-24 05:00 | Summer | FALSE | summer
2024-06-24 05:00 | 2024-06-24 06:00 | Summer | FALSE | summer
2024-06-24 06:00 | 2024-06-24 07:00 | Summer | FALSE | summer
2024-06-24 07:00 | 2024-06-24 08:00 | Summer | FALSE | summer
2024-06-24 08:00 | 2024-06-24 09:00 | Summer | FALSE | summer
2024-06-24 09:00 | 2024-06-24 10:00 | Summer | FALSE | summer
2024-06-24 10:00 | 2024-06-24 11:00 | Summer | FALSE | summer
2024-06-24 11:00 | 2024-06-24 12:00 | Summer | FALSE | summer
2024-06-24 12:00 | 2024-06-24 13:00 | Summer | FALSE | summer
2024-06-24 13:00 | 2024-06-24 14:00 | Summer | FALSE | summer
2024-06-24 14:00 | 2024-06-24 15:00 | Summer | FALSE | summer
2024-06-24 15:00 | 2024-06-24 16:00 | Summer | FALSE | summer
2024-06-24 16:00 | 2024-06-24 17:00 | Summer | TRUE | summer
2024-06-24 17:00 | 2024-06-24 18:00 | Summer | TRUE | summer
2024-06-24 18:00 | 2024-06-24 19:00 | Summer | TRUE | summer
2024-06-24 19:00 | 2024-06-24 20:00 | Summer | TRUE | summer
2024-06-24 20:00 | 2024-06-24 21:00 | Summer | TRUE | summer
2024-06-24 21:00 | 2024-06-24 22:00 | Summer | FALSE | summer
2024-06-24 22:00 | 2024-06-24 23:00 | Summer | FALSE | summer
2024-06-24 23:00 | 2024-06-25 | Summer | FALSE | summer
2024-06-25 | 2024-06-25 01:00 | Summer | FALSE | summer
2024-06-25 01:00 | 2024-06-25 02:00 | Summer | FALSE | summer
2024-06-25 02:00 | 2024-06-25 03:00 | Summer | FALSE | summer
2024-06-25 03:00 | 2024-06-25 04:00 | Summer | FALSE | summer
2024-06-25 04:00 | 2024-06-25 05:00 | Summer | FALSE | summer
2024-06-25 05:00 | 2024-06-25 06:00 | Summer | FALSE | summer
2024-06-25 06:00 | 2024-06-25 07:00 | Summer | FALSE | summer
2024-06-25 07:00 | 2024-06-25 08:00 | Summer | FALSE | summer
2024-06-25 08:00 | 2024-06-25 09:00 | Summer | FALSE | summer
2024-06-25 09:00 | 2024-06-25 10:00 | Summer | FALSE | summer
2024-06-25 10:00 | 2024-06-25 11:00 | Summer | FALSE | summer
2024-06-25 11:00 | 2024-06-25 12:00 | Summer | FALSE | summer
2024-06-25 12:00 | 2024-06-25 13:00 | Summer | FALSE | summer
2024-06-25 13:00 | 2024-06-25 14:00 | Summer | FALSE | summer
2024-06-25 14:00 | 2024-06-25 15:00 | Summer | FALSE | summer
2024-06-25 15:00 | 2024-06-25 16:00 | Summer | FALSE | summer
2024-06-25 16:00 | 2024-06-25 17:00 | Summer | TRUE | summer
2024-06-25 17:00 | 2024-06-25 18:00 | Summer | TRUE | summer
2024-06-25 18:00 | 2024-06-25 19:00 | Summer | TRUE | summer
2024-06-25 19:00 | 2024-06-25 20:00 | Summer | TRUE | summer
2024-06-25 20:00 | 2024-06-25 21:00 | Summer | TRUE | summer
2024-06-25 21:00 | 2024-06-25 22:00 | Summer | FALSE | summer
2024-06-25 22:00 | 2024-06-25 23:00 | Summer | FALSE | summer
2024-06-25 23:00 | 2024-06-26 | Summer | FALSE | summer
2024-06-26 | 2024-06-26 01:00 | Summer | FALSE | summer
2024-06-26 01:00 | 2024-06-26 02:00 | Summer | FALSE | summer
2024-06-26 02:00 | 2024-06-26 03:00 | Summer | FALSE | summer
2024-06-26 03:00 | 2024-06-26 04:00 | Summer | FALSE | summer
2024-06-26 04:00 | 2024-06-26 05:00 | Summer | FALSE | summer
2024-06-26 05:00 | 2024-06-26 06:00 | Summer | FALSE | summer
2024-06-26 06:00 | 2024-06-26 07:00 | Summer | FALSE | summer
2024-06-26 07:00 | 2024-06-26 08:00 | Summer | FALSE | summer
2024-06-26 08:00 | 2024-06-26 09:00 | Summer | FALSE | summer
2024-06-26 09:00 | 2024-06-26 10:00 | Summer | FALSE | summer
2024-06-26 10:00 | 2024-06-26 11:00 | Summer | FALSE | summer
2024-06-26 11:00 | 2024-06-26 12:00 | Summer | FALSE | summer
2024-06-26 12:00 | 2024-06-26 13:00 | Summer | FALSE | summer
2024-06-26 13:00 | 2024-06-26 14:00 | Summer | FALSE | summer
2024-06-26 14:00 | 2024-06-26 15:00 | Summer | FALSE | summer
2024-06-26 15:00 | 2024-06-26 16:00 | Summer | FALSE | summer
2024-06-26 16:00 | 2024-06-26 17:00 | Summer | TRUE | summer
2024-06-26 17:00 | 2024-06-26 18:00 | Summer | TRUE | summer
2024-06-26 18:00 | 2024-06-26 19:00 | Summer | TRUE | summer
2024-06-26 19:00 | 2024-06-26 20:00 | Summer | TRUE | summer
2024-06-26 20:00 | 2024-06-26 21:00 | Summer | TRUE | summer
2024-06-26 21:00 | 2024-06-26 22:00 | Summer | FALSE | summer
2024-06-26 22:00 | 2024-06-26 23:00 | Summer | FALSE | summer
2024-06-26 23:00 | 2024-06-27 | Summer | FALSE | summer
2024-06-27 | 2024-06-27 01:00 | Summer | FALSE | summer
2024-06-27 01:00 | 2024-06-27 02:00 | Summer | FALSE | summer
2024-06-27 02:00 | 2024-06-27 03:00 | Summer | FALSE | summer
2024-06-27 03:00 | 2024-06-27 04:00 | Summer | FALSE | summer
2024-06-27 04:00 | 2024-06-27 05:00 | Summer | FALSE | summer
2024-06-27 05:00 | 2024-06-27 06:00 | Summer | FALSE | summer
2024-06-27 06:00 | 2024-06-27 07:00 | Summer | FALSE | summer
2024-06-27 07:00 | 2024-06-27 08:00 | Summer | FALSE | summer
2024-06-27 08:00 | 2024-06-27 09:00 | Summer | FALSE | summer
2024-06-27 09:00 | 2024-06-27 10:00 | Summer | FALSE | summer
2024-06-27 10:00 | 2024-06-27 11:00 | Summer | FALSE | summer
2024-06-27 11:00 | 2024-06-27 12:00 | Summer | FALSE | summer
2024-06-27 12:00 | 2024-06-27 13:00 | Summer | FALSE | summer
2024-06-27 13:00 | 2024-06-27 14:00 | Summer | FALSE | summer
2024-06-27 14:00 | 2024-06-27 15:00 | Summer | FALSE | summer
2024-06-27 15:00 | 2024-06-27 16:00 | Summer | FALSE | summer
2024-06-27 16:00 | 2024-06-27 17:00 | Summer | TRUE | summer
2024-06-27 17:00 | 2024-06-27 18:00 | Summer | TRUE | summer
2024-06-27 18:00 | 2024-06-27 19:00 | Summer | TRUE | summer
2024-06-27 19:00 | 2024-06-27 20:00 | Summer | TRUE | summer
2024-06-27 20:00 | 2024-06-27 21:00 | Summer | TRUE | summer
2024-06-27 21:00 | 2024-06-27 22:00 | Summer | FALSE | summer
2024-06-27 22:00 | 2024-06-27 23:00 | Summer | FALSE | summer
2024-06-27 23:00 | 2024-06-28 | Summer | FALSE | summer
2024-06-28 | 2024-06-28 01:00 | Summer | FALSE | summer
2024-06-28 01:00 | 2024-06-28 02:00 | Summer | FALSE | summer
2024-06-28 02:00 | 2024-06-28 03:00 | Summer | FALSE | summer
2024-06-28 03:00 | 2024-06-28 04:00 | Summer | FALSE | summer
2024-06-28 04:00 | 2024-06-28 05:00 | Summer | FALSE | summer
2024-06-28 05:00 | 2024-06-28 06:00 | Summer | FALSE | summer
2024-06-28 06:00 | 2024-06-28 07:00 | Summer | FALSE | summer
2024-06-28 07:00 | 2024-06-28 08:00 | Summer | FALSE | summer
2024-06-28 08:00 | 2024-06-28 09:00 | Summer | FALSE | summer
2024-06-28 09:00 | 2024-06-28 10:00 | Summer | FALSE | summer
2024-06-28 10:00 | 2024-06-28 11:00 | Summer | FALSE | summer
2024-06-28 11:00 | 2024-06-28 12:00 | Summer | FALSE | summer
2024-06-28 12:00 | 2024-06-28 13:00 | Summer | FALSE | summer
2024-06-28 13:00 | 2024-06-28 14:00 | Summer | FALSE | summer
2024-06-28 14:00 | 2024-06-28 15:00 | Summer | FALSE | summer
2024-06-28 15:00 | 2024-06-28 16:00 | Summer | FALSE | summer
2024-06-28 16:00 | 2024-06-28 17:00 | Summer | TRUE | summer
2024-06-28 17:00 | 2024-06-28 18:00 | Summer | TRUE | summer
2024-06-28 18:00 | 2024-06-28 19:00 | Summer | TRUE | summer
2024-06-28 19:00 | 2024-06-28 20:00 | Summer | TRUE | summer
2024-06-28 20:00 | 2024-06-28 21:00 | Summer | TRUE | summer
2024-06-28 21:00 | 2024-06-28 22:00 | Summer | FALSE | summer
2024-06-28 22:00 | 2024-06-28 23:00 | Summer | FALSE | summer
2024-06-28 23:00 | 2024-06-29 | Summer | FALSE | summer
2024-06-29 | 2024-06-29 01:00 | Summer | FALSE | summer
2024-06-29 01:00 | 2024-06-29 02:00 | Summer | FALSE | summer
2024-06-29 02:00 | 2024-06-29 03:00 | Summer | FALSE | summer
2024-06-29 03:00 | 2024-06-29 04:00 | Summer | FALSE | summer
2024-06-29 04:00 | 2024-06-29 05:00 | Summer | FALSE | summer
2024-06-29 05:00 | 2024-06-29 06:00 | Summer | FALSE | summer
2024-06-29 06:00 | 2024-06-29 07:00 | Summer | FALSE | summer
2024-06-29 07:00 | 2024-06-29 08:00 | Summer | FALSE | summer
2024-06-29 08:00 | 2024-06-29 09:00 | Summer | FALSE | summer
2024-06-29 09:00 | 2024-06-29 10:00 | Summer | FALSE | summer
2024-06-29 10:00 | 2024-06-29 11:00 | Summer | FALSE | summer
2024-06-29 11:00 | 2024-06-29 12:00 | Summer | FALSE | summer
2024-06-29 12:00 | 2024-06-29 13:00 | Summer | FALSE | summer
2024-06-29 13:00 | 2024-06-29 14:00 | Summer | FALSE | summer
2024-06-29 14:00 | 2024-06-29 15:00 | Summer | FALSE | summer
2024-06-29 15:00 | 2024-06-29 16:00 | Summer | FALSE | summer
2024-06-29 16:00 | 2024-06-29 17:00 | Summer | TRUE | summer
2024-06-29 17:00 | 2024-06-29 18:00 | Summer | TRUE | summer
2024-06-29 18:00 | 2024-06-29 19:00 | Summer | TRUE | summer
2024-06-29 19:00 | 2024-06-29 20:00 | Summer | TRUE | summer
2024-06-29 20:00 | 2024-06-29 21:00 | Summer | TRUE | summer
2024-06-29 21:00 | 2024-06-29 22:00 | Summer | FALSE | summer
2024-06-29 22:00 | 2024-06-29 23:00 | Summer | FALSE | summer
2024-06-29 23:00 | 2024-06-30 | Summer | FALSE | summer
2024-06-30 | 2024-06-30 01:00 | Summer | FALSE | summer
2024-06-30 01:00 | 2024-06-30 02:00 | Summer | FALSE | summer
2024-06-30 02:00 | 2024-06-30 03:00 | Summer | FALSE | summer
2024-06-30 03:00 | 2024-06-30 04:00 | Summer | FALSE | summer
2024-06-30 04:00 | 2024-06-30 05:00 | Summer | FALSE | summer
2024-06-30 05:00 | 2024-06-30 06:00 | Summer | FALSE | summer
2024-06-30 06:00 | 2024-06-30 07:00 | Summer | FALSE | summer
2024-06-30 07:00 | 2024-06-30 08:00 | Summer | FALSE | summer
2024-06-30 08:00 | 2024-06-30 09:00 | Summer | FALSE | summer
2024-06-30 09:00 | 2024-06-30 10:00 | Summer | FALSE | summer
2024-06-30 10:00 | 2024-06-30 11:00 | Summer | FALSE | summer
2024-06-30 11:00 | 2024-06-30 12:00 | Summer | FALSE | summer
2024-06-30 12:00 | 2024-06-30 13:00 | Summer | FALSE | summer
2024-06-30 13:00 | 2024-06-30 14:00 | Summer | FALSE | summer
2024-06-30 14:00 | 2024-06-30 15:00 | Summer | FALSE | summer
2024-06-30 15:00 | 2024-06-30 16:00 | Summer | FALSE | summer
2024-06-30 16:00 | 2024-06-30 17:00 | Summer | TRUE | summer
2024-06-30 17:00 | 2024-06-30 18:00 | Summer | TRUE | summer
2024-06-30 18:00 | 2024-06-30 19:00 | Summer | TRUE | summer
2024-06-30 19:00 | 2024-06-30 20:00 | Summer | TRUE | summer
2024-06-30 20:00 | 2024-06-30 21:00 | Summer | TRUE | summer
2024-06-30 21:00 | 2024-06-30 22:00 | Summer | FALSE | summer
2024-06-30 22:00 | 2024-06-30 23:00 | Summer | FALSE | summer
2024-06-30 23:00 | 2024-07-01 | Summer | FALSE | summer
2024-07-01 | 2024-07-01 01:00 | Summer | FALSE | summer
2024-07-01 01:00 | 2024-07-01 02:00 | Summer | FALSE | summer
2024-07-01 02:00 | 2024-07-01 03:00 | Summer | FALSE | summer
2024-07-01 03:00 | 2024-07-01 04:00 | Summer | FALSE | summer
2024-07-01 04:00 | 2024-07-01 05:00 | Summer | FALSE | summer
2024-07-01 05:00 | 2024-07-01 06:00 | Summer | FALSE | summer
2024-07-01 06:00 | 2024-07-01 07:00 | Summer | FALSE | summer
2024-07-01 07:00 | 2024-07-01 08:00 | Summer | FALSE | summer
2024-07-01 08:00 | 2024-07-01 09:00 | Summer | FALSE | summer
2024-07-01 09:00 | 2024-07-01 10:00 | Summer | FALSE | summer
2024-07-01 10:00 | 2024-07-01 11:00 | Summer | FALSE | summer
2024-07-01 11:00 | 2024-07-01 12:00 | Summer | FALSE | summer
2024-07-01 12:00 | 2024-07-01 13:00 | Summer | FALSE | summer
2024-07-01 13:00 | 2024-07-01 14:00 | Summer | FALSE | summer
2024-07-01 14:00 | 2024-07-01 15:00 | Summer | FALSE | summer
2024-07-01 15:00 | 2024-07-01 16:00 | Summer | FALSE | summer
2024-07-01 16:00 | 2024-07-01 17:00 | Summer | TRUE | summer
2024-07-01 17:00 | 2024-07-01 18:00 | Summer | TRUE | summer
2024-07-01 18:00 | 2024-07-01 19:00 | Summer | TRUE | summer
2024-07-01 19:00 | 2024-07-01 20:00 | Summer | TRUE | summer
2024-07-01 20:00 | 2024-07-01 21:00 | Summer | TRUE | summer
2024-07-01 21:00 | 2024-07-01 22:00 | Summer | FALSE | summer
2024-07-01 22:00 | 2024-07-01 23:00 | Summer | FALSE | summer
2024-07-01 23:00 | 2024-07-02 | Summer | FALSE | summer
2024-07-02 | 2024-07-02 01:00 | Summer | FALSE | summer
2024-07-02 01:00 | 2024-07-02 02:00 | Summer | FALSE | summer
2024-07-02 02:00 | 2024-07-02 03:00 | Summer | FALSE | summer
2024-07-02 03:00 | 2024-07-02 04:00 | Summer | FALSE | summer
2024-07-02 04:00 | 2024-07-02 05:00 | Summer | FALSE | summer
2024-07-02 05:00 | 2024-07-02 06:00 | Summer | FALSE | summer
2024-07-02 06:00 | 2024-07-02 07:00 | Summer | FALSE | summer
2024-07-02 07:00 | 2024-07-02 08:00 | Summer | FALSE | summer
2024-07-02 08:00 | 2024-07-02 09:00 | Summer | FALSE | summer
2024-07-02 09:00 | 2024-07-02 10:00 | Summer | FALSE | summer
2024-07-02 10:00 | 2024-07-02 11:00 | Summer | FALSE | summer
2024-07-02 11:00 | 2024-07-02 12:00 | Summer | FALSE | summer
2024-07-02 12:00 | 2024-07-02 13:00 | Summer | FALSE | summer
2024-07-02 13:00 | 2024-07-02 14:00 | Summer | FALSE | summer
2024-07-02 14:00 | 2024-07-02 15:00 | Summer | FALSE | summer
2024-07-02 15:00 | 2024-07-02 16:00 | Summer | FALSE | summer
2024-07-02 16:00 | 2024-07-02 17:00 | Summer | TRUE | summer
2024-07-02 17:00 | 2024-07-02 18:00 | Summer | TRUE | summer
2024-07-02 18:00 | 2024-07-02 19:00 | Summer | TRUE | summer
2024-07-02 19:00 | 2024-07-02 20:00 | Summer | TRUE | summer
2024-07-02 20:00 | 2024-07-02 21:00 | Summer | TRUE | summer
2024-07-02 21:00 | 2024-07-02 22:00 | Summer | FALSE | summer
2024-07-02 22:00 | 2024-07-02 23:00 | Summer | FALSE | summer
2024-07-02 23:00 | 2024-07-03 | Summer | FALSE | summer
2024-07-03 | 2024-07-03 01:00 | Summer | FALSE | summer
2024-07-03 01:00 | 2024-07-03 02:00 | Summer | FALSE | summer
2024-07-03 02:00 | 2024-07-03 03:00 | Summer | FALSE | summer
2024-07-03 03:00 | 2024-07-03 04:00 | Summer | FALSE | summer
2024-07-03 04:00 | 2024-07-03 05:00 | Summer | FALSE | summer
2024-07-03 05:00 | 2024-07-03 06:00 | Summer | FALSE | summer
2024-07-03 06:00 | 2024-07-03 07:00 | Summer | FALSE | summer
2024-07-03 07:00 | 2024-07-03 08:00 | Summer | FALSE | summer
2024-07-03 08:00 | 2024-07-03 09:00 | Summer | FALSE | summer
2024-07-03 09:00 | 2024-07-03 10:00 | Summer | FALSE | summer
2024-07-03 10:00 | 2024-07-03 11:00 | Summer | FALSE | summer
2024-07-03 11:00 | 2024-07-03 12:00 | Summer | FALSE | summer
2024-07-03 12:00 | 2024-07-03 13:00 | Summer | FALSE | summer
2024-07-03 13:00 | 2024-07-03 14:00 | Summer | FALSE | summer
2024-07-03 14:00 | 2024-07-03 15:00 | Summer | FALSE | summer
2024-07-03 15:00 | 2024-07-03 16:00 | Summer | FALSE | summer
2024-07-03 16:00 | 2024-07-03 17:00 | Summer | TRUE | summer
2024-07-03 17:00 | 2024-07-03 18:00 | Summer | TRUE | summer
2024-07-03 18:00 | 2024-07-03 19:00 | Summer | TRUE | summer
2024-07-03 19:00 | 2024-07-03 20:00 | Summer | TRUE | summer
2024-07-03 20:00 | 2024-07-03 21:00 | Summer | TRUE | summer
2024-07-03 21:00 | 2024-07-03 22:00 | Summer | FALSE | summer
2024-07-03 22:00 | 2024-07-03 23:00 | Summer | FALSE | summer
2024-07-03 23:00 | 2024-07-04 | Summer | FALSE | summer
2024-07-04 | 2024-07-04 01:00 | Summer | FALSE | summer
2024-07-04 01:00 | 2024-07-04 02:00 | Summer | FALSE | summer
2024-07-04 02:00 | 2024-07-04 03:00 | Summer | FALSE | summer
2024-07-04 03:00 | 2024-07-04 04:00 | Summer | FALSE | summer
2024-07-04 04:00 | 2024-07-04 05:00 | Summer | FALSE | summer
2024-07-04 05:00 | 2024-07-04 06:00 | Summer | FALSE | summer
2024-07-04 06:00 | 2024-07-04 07:00 | Summer | FALSE | summer
2024-07-04 07:00 | 2024-07-04 08:00 | Summer | FALSE | summer
2024-07-04 08:00 | 2024-07-04 09:00 | Summer | FALSE | summer
2024-07-04 09:00 | 2024-07-04 10:00 | Summer | FALSE | summer
2024-07-04 10:00 | 2024-07-04 11:00 | Summer | FALSE | summer
2024-07-04 11:00 | 2024-07-04 12:00 | Summer | FALSE | summer
2024-07-04 12:00 | 2024-07-04 13:00 | Summer | FALSE | summer
2024-07-04 13:00 | 2024-07-04 14:00 | Summer | FALSE | summer
2024-07-04 14:00 | 2024-07-04 15:00 | Summer | FALSE | summer
2024-07-04 15:00 | 2024-07-04 16:00 | Summer | FALSE | summer
2024-07-04 16:00 | 2024-07-04 17:00 | Summer | TRUE | summer
2024-07-04 17:00 | 2024-07-04 18:00 | Summer | TRUE | summer
2024-07-04 18:00 | 2024-07-04 19:00 | Summer | TRUE | summer
2024-07-04 19:00 | 2024-07-04 20:00 | Summer | TRUE | summer
2024-07-04 20:00 | 2024-07-04 21:00 | Summer | TRUE | summer
2024-07-04 21:00 | 2024-07-04 22:00 | Summer | FALSE | summer
2024-07-04 22:00 | 2024-07-04 23:00 | Summer | FALSE | summer
2024-07-04 23:00 | 2024-07-05 | Summer | FALSE | summer
2024-07-05 | 2024-07-05 01:00 | Summer | FALSE | summer
2024-07-05 01:00 | 2024-07-05 02:00 | Summer | FALSE | summer
2024-07-05 02:00 | 2024-07-05 03:00 | Summer | FALSE | summer
2024-07-05 03:00 | 2024-07-05 04:00 | Summer | FALSE | summer
2024-07-05 04:00 | 2024-07-05 05:00 | Summer | FALSE | summer
2024-07-05 05:00 | 2024-07-05 06:00 | Summer | FALSE | summer
2024-07-05 06:00 | 2024-07-05 07:00 | Summer | FALSE | summer
2024-07-05 07:00 | 2024-07-05 08:00 | Summer | FALSE | summer
2024-07-05 08:00 | 2024-07-05 09:00 | Summer | FALSE | summer
2024-07-05 09:00 | 2024-07-05 10:00 | Summer | FALSE | summer
2024-07-05 10:00 | 2024-07-05 11:00 | Summer | FALSE | summer
2024-07-05 11:00 | 2024-07-05 12:00 | Summer | FALSE | summer
2024-07-05 12:00 | 2024-07-05 13:00 | Summer | FALSE | summer
2024-07-05 13:00 | 2024-07-05 14:00 | Summer | FALSE | summer
2024-07-05 14:00 | 2024-07-05 15:00 | Summer | FALSE | summer
2024-07-05 15:00 | 2024-07-05 16:00 | Summer | FALSE | summer
2024-07-05 16:00 | 2024-07-05 17:00 | Summer | TRUE | summer
2024-07-05 17:00 | 2024-07-05 18:00 | Summer | TRUE | summer
2024-07-05 18:00 | 2024-07-05 19:00 | Summer | TRUE | summer
2024-07-05 19:00 | 2024-07-05 20:00 | Summer | TRUE | summer
2024-07-05 20:00 | 2024-07-05 21:00 | Summer | TRUE | summer
2024-07-05 21:00 | 2024-07-05 22:00 | Summer | FALSE | summer
2024-07-05 22:00 | 2024-07-05 23:00 | Summer | FALSE | summer
2024-07-05 23:00 | 2024-07-06 | Summer | FALSE | summer
2024-07-06 | 2024-07-06 01:00 | Summer | FALSE | summer
2024-07-06 01:00 | 2024-07-06 02:00 | Summer | FALSE | summer
2024-07-06 02:00 | 2024-07-06 03:00 | Summer | FALSE | summer
2024-07-06 03:00 | 2024-07-06 04:00 | Summer | FALSE | summer
2024-07-06 04:00 | 2024-07-06 05:00 | Summer | FALSE | summer
2024-07-06 05:00 | 2024-07-06 06:00 | Summer | FALSE | summer
2024-07-06 06:00 | 2024-07-06 07:00 | Summer | FALSE | summer
2024-07-06 07:00 | 2024-07-06 08:00 | Summer | FALSE | summer
2024-07-06 08:00 | 2024-07-06 09:00 | Summer | FALSE | summer
2024-07-06 09:00 | 2024-07-06 10:00 | Summer | FALSE | summer
2024-07-06 10:00 | 2024-07-06 11:00 | Summer | FALSE | summer
2024-07-06 11:00 | 2024-07-06 12:00 | Summer | FALSE | summer
2024-07-06 12:00 | 2024-07-06 13:00 | Summer | FALSE | summer
2024-07-06 13:00 | 2024-07-06 14:00 | Summer | FALSE | summer
2024-07-06 14:00 | 2024-07-06 15:00 | Summer | FALSE | summer
2024-07-06 15:00 | 2024-07-06 16:00 | Summer | FALSE | summer
2024-07-06 16:00 | 2024-07-06 17:00 | Summer | TRUE | summer
2024-07-06 17:00 | 2024-07-06 18:00 | Summer | TRUE | summer
2024-07-06 18:00 | 2024-07-06 19:00 | Summer | TRUE | summer
2024-07-06 19:00 | 2024-07-06 20:00 | Summer | TRUE | summer
2024-07-06 20:00 | 2024-07-06 21:00 | Summer | TRUE | summer
2024-07-06 21:00 | 2024-07-06 22:00 | Summer | FALSE | summer
2024-07-06 22:00 | 2024-07-06 23:00 | Summer | FALSE | summer
2024-07-06 23:00 | 2024-07-07 | Summer | FALSE | summer
2024-07-07 | 2024-07-07 01:00 | Summer | FALSE | summer
2024-07-07 01:00 | 2024-07-07 02:00 | Summer | FALSE | summer
2024-07-07 02:00 | 2024-07-07 03:00 | Summer | FALSE | summer
2024-07-07 03:00 | 2024-07-07 04:00 | Summer | FALSE | summer
2024-07-07 04:00 | 2024-07-07 05:00 | Summer | FALSE | summer
2024-07-07 05:00 | 2024-07-07 06:00 | Summer | FALSE | summer
2024-07-07 06:00 | 2024-07-07 07:00 | Summer | FALSE | summer
2024-07-07 07:00 | 2024-07-07 08:00 | Summer | FALSE | summer
2024-07-07 08:00 | 2024-07-07 09:00 | Summer | FALSE | summer
2024-07-07 09:00 | 2024-07-07 10:00 | Summer | FALSE | summer
2024-07-07 10:00 | 2024-07-07 11:00 | Summer | FALSE | summer
2024-07-07 11:00 | 2024-07-07 12:00 | Summer | FALSE | summer
2024-07-07 12:00 | 2024-07-07 13:00 | Summer | FALSE | summer
2024-07-07 13:00 | 2024-07-07 14:00 | Summer | FALSE | summer
2024-07-07 14:00 | 2024-07-07 15:00 | Summer | FALSE | summer
2024-07-07 15:00 | 2024-07-07 16:00 | Summer | FALSE | summer
2024-07-07 16:00 | 2024-07-07 17:00 | Summer | TRUE | summer
2024-07-07 17:00 | 2024-07-07 18:00 | Summer | TRUE | summer
2024-07-07 18:00 | 2024-07-07 19:00 | Summer | TRUE | summer
2024-07-07 19:00 | 2024-07-07 20:00 | Summer | TRUE | summer
2024-07-07 20:00 | 2024-07-07 21:00 | Summer | TRUE | summer
2024-07-07 21:00 | 2024-07-07 22:00 | Summer | FALSE | summer
2024-07-07 22:00 | 2024-07-07 23:00 | Summer | FALSE | summer
2024-07-07 23:00 | 2024-07-08 | Summer | FALSE | summer
2024-07-08 | 2024-07-08 01:00 | Summer | FALSE | summer
2024-07-08 01:00 | 2024-07-08 02:00 | Summer | FALSE | summer
2024-07-08 02:00 | 2024-07-08 03:00 | Summer | FALSE | summer
2024-07-08 03:00 | 2024-07-08 04:00 | Summer | FALSE | summer
2024-07-08 04:00 | 2024-07-08 05:00 | Summer | FALSE | summer
2024-07-08 05:00 | 2024-07-08 06:00 | Summer | FALSE | summer
2024-07-08 06:00 | 2024-07-08 07:00 | Summer | FALSE | summer
2024-07-08 07:00 | 2024-07-08 08:00 | Summer | FALSE | summer
2024-07-08 08:00 | 2024-07-08 09:00 | Summer | FALSE | summer
2024-07-08 09:00 | 2024-07-08 10:00 | Summer | FALSE | summer
2024-07-08 10:00 | 2024-07-08 11:00 | Summer | FALSE | summer
2024-07-08 11:00 | 2024-07-08 12:00 | Summer | FALSE | summer
2024-07-08 12:00 | 2024-07-08 13:00 | Summer | FALSE | summer
2024-07-08 13:00 | 2024-07-08 14:00 | Summer | FALSE | summer
2024-07-08 14:00 | 2024-07-08 15:00 | Summer | FALSE | summer
2024-07-08 15:00 | 2024-07-08 16:00 | Summer | FALSE | summer
2024-07-08 16:00 | 2024-07-08 17:00 | Summer | TRUE | summer
2024-07-08 17:00 | 2024-07-08 18:00 | Summer | TRUE | summer
2024-07-08 18:00 | 2024-07-08 19:00 | Summer | TRUE | summer
2024-07-08 19:00 | 2024-07-08 20:00 | Summer | TRUE | summer
2024-07-08 20:00 | 2024-07-08 21:00 | Summer | TRUE | summer
2024-07-08 21:00 | 2024-07-08 22:00 | Summer | FALSE | summer
2024-07-08 22:00 | 2024-07-08 23:00 | Summer | FALSE | summer
2024-07-08 23:00 | 2024-07-09 | Summer | FALSE | summer
2024-07-09 | 2024-07-09 01:00 | Summer | FALSE | summer
2024-07-09 01:00 | 2024-07-09 02:00 | Summer | FALSE | summer
2024-07-09 02:00 | 2024-07-09 03:00 | Summer | FALSE | summer
2024-07-09 03:00 | 2024-07-09 04:00 | Summer | FALSE | summer
2024-07-09 04:00 | 2024-07-09 05:00 | Summer | FALSE | summer
2024-07-09 05:00 | 2024-07-09 06:00 | Summer | FALSE | summer
2024-07-09 06:00 | 2024-07-09 07:00 | Summer | FALSE | summer
2024-07-09 07:00 | 2024-07-09 08:00 | Summer | FALSE | summer
2024-07-09 08:00 | 2024-07-09 09:00 | Summer | FALSE | summer
2024-07-09 09:00 | 2024-07-09 10:00 | Summer | FALSE | summer
2024-07-09 10:00 | 2024-07-09 11:00 | Summer | FALSE | summer
2024-07-09 11:00 | 2024-07-09 12:00 | Summer | FALSE | summer
2024-07-09 12:00 | 2024-07-09 13:00 | Summer | FALSE | summer
2024-07-09 13:00 | 2024-07-09 14:00 | Summer | FALSE | summer
2024-07-09 14:00 | 2024-07-09 15:00 | Summer | FALSE | summer
2024-07-09 15:00 | 2024-07-09 16:00 | Summer | FALSE | summer
2024-07-09 16:00 | 2024-07-09 17:00 | Summer | TRUE | summer
2024-07-09 17:00 | 2024-07-09 18:00 | Summer | TRUE | summer
2024-07-09 18:00 | 2024-07-09 19:00 | Summer | TRUE | summer
2024-07-09 19:00 | 2024-07-09 20:00 | Summer | TRUE | summer
2024-07-09 20:00 | 2024-07-09 21:00 | Summer | TRUE | summer
2024-07-09 21:00 | 2024-07-09 22:00 | Summer | FALSE | summer
2024-07-09 22:00 | 2024-07-09 23:00 | Summer | FALSE | summer
2024-07-09 23:00 | 2024-07-10 | Summer | FALSE | summer
2024-07-10 | 2024-07-10 01:00 | Summer | FALSE | summer
2024-07-10 01:00 | 2024-07-10 02:00 | Summer | FALSE | summer
2024-07-10 02:00 | 2024-07-10 03:00 | Summer | FALSE | summer
2024-07-10 03:00 | 2024-07-10 04:00 | Summer | FALSE | summer
2024-07-10 04:00 | 2024-07-10 05:00 | Summer | FALSE | summer
2024-07-10 05:00 | 2024-07-10 06:00 | Summer | FALSE | summer
2024-07-10 06:00 | 2024-07-10 07:00 | Summer | FALSE | summer
2024-07-10 07:00 | 2024-07-10 08:00 | Summer | FALSE | summer
2024-07-10 08:00 | 2024-07-10 09:00 | Summer | FALSE | summer
2024-07-10 09:00 | 2024-07-10 10:00 | Summer | FALSE | summer
2024-07-10 10:00 | 2024-07-10 11:00 | Summer | FALSE | summer
2024-07-10 11:00 | 2024-07-10 12:00 | Summer | FALSE | summer
2024-07-10 12:00 | 2024-07-10 13:00 | Summer | FALSE | summer
2024-07-10 13:00 | 2024-07-10 14:00 | Summer | FALSE | summer
2024-07-10 14:00 | 2024-07-10 15:00 | Summer | FALSE | summer
2024-07-10 15:00 | 2024-07-10 16:00 | Summer | FALSE | summer
2024-07-10 16:00 | 2024-07-10 17:00 | Summer | TRUE | summer
2024-07-10 17:00 | 2024-07-10 18:00 | Summer | TRUE | summer
2024-07-10 18:00 | 2024-07-10 19:00 | Summer | TRUE | summer
2024-07-10 19:00 | 2024-07-10 20:00 | Summer | TRUE | summer
2024-07-10 20:00 | 2024-07-10 21:00 | Summer | TRUE | summer
2024-07-10 21:00 | 2024-07-10 22:00 | Summer | FALSE | summer
2024-07-10 22:00 | 2024-07-10 23:00 | Summer | FALSE | summer
2024-07-10 23:00 | 2024-07-11 | Summer | FALSE | summer
2024-07-11 | 2024-07-11 01:00 | Summer | FALSE | summer
2024-07-11 01:00 | 2024-07-11 02:00 | Summer | FALSE | summer
2024-07-11 02:00 | 2024-07-11 03:00 | Summer | FALSE | summer
2024-07-11 03:00 | 2024-07-11 04:00 | Summer | FALSE | summer
2024-07-11 04:00 | 2024-07-11 05:00 | Summer | FALSE | summer
2024-07-11 05:00 | 2024-07-11 06:00 | Summer | FALSE | summer
2024-07-11 06:00 | 2024-07-11 07:00 | Summer | FALSE | summer
2024-07-11 07:00 | 2024-07-11 08:00 | Summer | FALSE | summer
2024-07-11 08:00 | 2024-07-11 09:00 | Summer | FALSE | summer
2024-07-11 09:00 | 2024-07-11 10:00 | Summer | FALSE | summer
2024-07-11 10:00 | 2024-07-11 11:00 | Summer | FALSE | summer
2024-07-11 11:00 | 2024-07-11 12:00 | Summer | FALSE | summer
2024-07-11 12:00 | 2024-07-11 13:00 | Summer | FALSE | summer
2024-07-11 13:00 | 2024-07-11 14:00 | Summer | FALSE | summer
2024-07-11 14:00 | 2024-07-11 15:00 | Summer | FALSE | summer
2024-07-11 15:00 | 2024-07-11 16:00 | Summer | FALSE | summer
2024-07-11 16:00 | 2024-07-11 17:00 | Summer | TRUE | summer
2024-07-11 17:00 | 2024-07-11 18:00 | Summer | TRUE | summer
2024-07-11 18:00 | 2024-07-11 19:00 | Summer | TRUE | summer
2024-07-11 19:00 | 2024-07-11 20:00 | Summer | TRUE | summer
2024-07-11 20:00 | 2024-07-11 21:00 | Summer | TRUE | summer
2024-07-11 21:00 | 2024-07-11 22:00 | Summer | FALSE | summer
2024-07-11 22:00 | 2024-07-11 23:00 | Summer | FALSE | summer
2024-07-11 23:00 | 2024-07-12 | Summer | FALSE | summer
2024-07-12 | 2024-07-12 01:00 | Summer | FALSE | summer
2024-07-12 01:00 | 2024-07-12 02:00 | Summer | FALSE | summer
2024-07-12 02:00 | 2024-07-12 03:00 | Summer | FALSE | summer
2024-07-12 03:00 | 2024-07-12 04:00 | Summer | FALSE | summer
2024-07-12 04:00 | 2024-07-12 05:00 | Summer | FALSE | summer
2024-07-12 05:00 | 2024-07-12 06:00 | Summer | FALSE | summer
2024-07-12 06:00 | 2024-07-12 07:00 | Summer | FALSE | summer
2024-07-12 07:00 | 2024-07-12 08:00 | Summer | FALSE | summer
2024-07-12 08:00 | 2024-07-12 09:00 | Summer | FALSE | summer
2024-07-12 09:00 | 2024-07-12 10:00 | Summer | FALSE | summer
2024-07-12 10:00 | 2024-07-12 11:00 | Summer | FALSE | summer
2024-07-12 11:00 | 2024-07-12 12:00 | Summer | FALSE | summer
2024-07-12 12:00 | 2024-07-12 13:00 | Summer | FALSE | summer
2024-07-12 13:00 | 2024-07-12 14:00 | Summer | FALSE | summer
2024-07-12 14:00 | 2024-07-12 15:00 | Summer | FALSE | summer
2024-07-12 15:00 | 2024-07-12 16:00 | Summer | FALSE | summer
2024-07-12 16:00 | 2024-07-12 17:00 | Summer | TRUE | summer
2024-07-12 17:00 | 2024-07-12 18:00 | Summer | TRUE | summer
2024-07-12 18:00 | 2024-07-12 19:00 | Summer | TRUE | summer
2024-07-12 19:00 | 2024-07-12 20:00 | Summer | TRUE | summer
2024-07-12 20:00 | 2024-07-12 21:00 | Summer | TRUE | summer
2024-07-12 21:00 | 2024-07-12 22:00 | Summer | FALSE | summer
2024-07-12 22:00 | 2024-07-12 23:00 | Summer | FALSE | summer
2024-07-12 23:00 | 2024-07-13 | Summer | FALSE | summer
2024-07-13 | 2024-07-13 01:00 | Summer | FALSE | summer
2024-07-13 01:00 | 2024-07-13 02:00 | Summer | FALSE | summer
2024-07-13 02:00 | 2024-07-13 03:00 | Summer | FALSE | summer
2024-07-13 03:00 | 2024-07-13 04:00 | Summer | FALSE | summer
2024-07-13 04:00 | 2024-07-13 05:00 | Summer | FALSE | summer
2024-07-13 05:00 | 2024-07-13 06:00 | Summer | FALSE | summer
2024-07-13 06:00 | 2024-07-13 07:00 | Summer | FALSE | summer
2024-07-13 07:00 | 2024-07-13 08:00 | Summer | FALSE | summer
2024-07-13 08:00 | 2024-07-13 09:00 | Summer | FALSE | summer
2024-07-13 09:00 | 2024-07-13 10:00 | Summer | FALSE | summer
2024-07-13 10:00 | 2024-07-13 11:00 | Summer | FALSE | summer
2024-07-13 11:00 | 2024-07-13 12:00 | Summer | FALSE | summer
2024-07-13 12:00 | 2024-07-13 13:00 | Summer | FALSE | summer
2024-07-13 13:00 | 2024-07-13 14:00 | Summer | FALSE | summer
2024-07-13 14:00 | 2024-07-13 15:00 | Summer | FALSE | summer
2024-07-13 15:00 | 2024-07-13 16:00 | Summer | FALSE | summer
2024-07-13 16:00 | 2024-07-13 17:00 | Summer | TRUE | summer
2024-07-13 17:00 | 2024-07-13 18:00 | Summer | TRUE | summer
2024-07-13 18:00 | 2024-07-13 19:00 | Summer | TRUE | summer
2024-07-13 19:00 | 2024-07-13 20:00 | Summer | TRUE | summer
2024-07-13 20:00 | 2024-07-13 21:00 | Summer | TRUE | summer
2024-07-13 21:00 | 2024-07-13 22:00 | Summer | FALSE | summer
2024-07-13 22:00 | 2024-07-13 23:00 | Summer | FALSE | summer
2024-07-13 23:00 | 2024-07-14 | Summer | FALSE | summer
2024-07-14 | 2024-07-14 01:00 | Summer | FALSE | summer
2024-07-14 01:00 | 2024-07-14 02:00 | Summer | FALSE | summer
2024-07-14 02:00 | 2024-07-14 03:00 | Summer | FALSE | summer
2024-07-14 03:00 | 2024-07-14 04:00 | Summer | FALSE | summer
2024-07-14 04:00 | 2024-07-14 05:00 | Summer | FALSE | summer
2024-07-14 05:00 | 2024-07-14 06:00 | Summer | FALSE | summer
2024-07-14 06:00 | 2024-07-14 07:00 | Summer | FALSE | summer
2024-07-14 07:00 | 2024-07-14 08:00 | Summer | FALSE | summer
2024-07-14 08:00 | 2024-07-14 09:00 | Summer | FALSE | summer
2024-07-14 09:00 | 2024-07-14 10:00 | Summer | FALSE | summer
2024-07-14 10:00 | 2024-07-14 11:00 | Summer | FALSE | summer
2024-07-14 11:00 | 2024-07-14 12:00 | Summer | FALSE | summer
2024-07-14 12:00 | 2024-07-14 13:00 | Summer | FALSE | summer
2024-07-14 13:00 | 2024-07-14 14:00 | Summer | FALSE | summer
2024-07-14 14:00 | 2024-07-14 15:00 | Summer | FALSE | summer
2024-07-14 15:00 | 2024-07-14 16:00 | Summer | FALSE | summer
2024-07-14 16:00 | 2024-07-14 17:00 | Summer | TRUE | summer
2024-07-14 17:00 | 2024-07-14 18:00 | Summer | TRUE | summer
2024-07-14 18:00 | 2024-07-14 19:00 | Summer | TRUE | summer
2024-07-14 19:00 | 2024-07-14 20:00 | Summer | TRUE | summer
2024-07-14 20:00 | 2024-07-14 21:00 | Summer | TRUE | summer
2024-07-14 21:00 | 2024-07-14 22:00 | Summer | FALSE | summer
2024-07-14 22:00 | 2024-07-14 23:00 | Summer | FALSE | summer
2024-07-14 23:00 | 2024-07-15 | Summer | FALSE | summer
2024-07-15 | 2024-07-15 01:00 | Summer | FALSE | summer
2024-07-15 01:00 | 2024-07-15 02:00 | Summer | FALSE | summer
2024-07-15 02:00 | 2024-07-15 03:00 | Summer | FALSE | summer
2024-07-15 03:00 | 2024-07-15 04:00 | Summer | FALSE | summer
2024-07-15 04:00 | 2024-07-15 05:00 | Summer | FALSE | summer
2024-07-15 05:00 | 2024-07-15 06:00 | Summer | FALSE | summer
2024-07-15 06:00 | 2024-07-15 07:00 | Summer | FALSE | summer
2024-07-15 07:00 | 2024-07-15 08:00 | Summer | FALSE | summer
2024-07-15 08:00 | 2024-07-15 09:00 | Summer | FALSE | summer
2024-07-15 09:00 | 2024-07-15 10:00 | Summer | FALSE | summer
2024-07-15 10:00 | 2024-07-15 11:00 | Summer | FALSE | summer
2024-07-15 11:00 | 2024-07-15 12:00 | Summer | FALSE | summer
2024-07-15 12:00 | 2024-07-15 13:00 | Summer | FALSE | summer
2024-07-15 13:00 | 2024-07-15 14:00 | Summer | FALSE | summer
2024-07-15 14:00 | 2024-07-15 15:00 | Summer | FALSE | summer
2024-07-15 15:00 | 2024-07-15 16:00 | Summer | FALSE | summer
2024-07-15 16:00 | 2024-07-15 17:00 | Summer | TRUE | summer
2024-07-15 17:00 | 2024-07-15 18:00 | Summer | TRUE | summer
2024-07-15 18:00 | 2024-07-15 19:00 | Summer | TRUE | summer
2024-07-15 19:00 | 2024-07-15 20:00 | Summer | TRUE | summer
2024-07-15 20:00 | 2024-07-15 21:00 | Summer | TRUE | summer
2024-07-15 21:00 | 2024-07-15 22:00 | Summer | FALSE | summer
2024-07-15 22:00 | 2024-07-15 23:00 | Summer | FALSE | summer
2024-07-15 23:00 | 2024-07-16 | Summer | FALSE | summer
2024-07-16 | 2024-07-16 01:00 | Summer | FALSE | summer
2024-07-16 01:00 | 2024-07-16 02:00 | Summer | FALSE | summer
2024-07-16 02:00 | 2024-07-16 03:00 | Summer | FALSE | summer
2024-07-16 03:00 | 2024-07-16 04:00 | Summer | FALSE | summer
2024-07-16 04:00 | 2024-07-16 05:00 | Summer | FALSE | summer
2024-07-16 05:00 | 2024-07-16 06:00 | Summer | FALSE | summer
2024-07-16 06:00 | 2024-07-16 07:00 | Summer | FALSE | summer
2024-07-16 07:00 | 2024-07-16 08:00 | Summer | FALSE | summer
2024-07-16 08:00 | 2024-07-16 09:00 | Summer | FALSE | summer
2024-07-16 09:00 | 2024-07-16 10:00 | Summer | FALSE | summer
2024-07-16 10:00 | 2024-07-16 11:00 | Summer | FALSE | summer
2024-07-16 11:00 | 2024-07-16 12:00 | Summer | FALSE | summer
2024-07-16 12:00 | 2024-07-16 13:00 | Summer | FALSE | summer
2024-07-16 13:00 | 2024-07-16 14:00 | Summer | FALSE | summer
2024-07-16 14:00 | 2024-07-16 15:00 | Summer | FALSE | summer
2024-07-16 15:00 | 2024-07-16 16:00 | Summer | FALSE | summer
2024-07-16 16:00 | 2024-07-16 17:00 | Summer | TRUE | summer
2024-07-16 17:00 | 2024-07-16 18:00 | Summer | TRUE | summer
2024-07-16 18:00 | 2024-07-16 19:00 | Summer | TRUE | summer
2024-07-16 19:00 | 2024-07-16 20:00 | Summer | TRUE | summer
2024-07-16 20:00 | 2024-07-16 21:00 | Summer | TRUE | summer
2024-07-16 21:00 | 2024-07-16 22:00 | Summer | FALSE | summer
2024-07-16 22:00 | 2024-07-16 23:00 | Summer | FALSE | summer
2024-07-16 23:00 | 2024-07-17 | Summer | FALSE | summer
2024-07-17 | 2024-07-17 01:00 | Summer | FALSE | summer
2024-07-17 01:00 | 2024-07-17 02:00 | Summer | FALSE | summer
2024-07-17 02:00 | 2024-07-17 03:00 | Summer | FALSE | summer
2024-07-17 03:00 | 2024-07-17 04:00 | Summer | FALSE | summer
2024-07-17 04:00 | 2024-07-17 05:00 | Summer | FALSE | summer
2024-07-17 05:00 | 2024-07-17 06:00 | Summer | FALSE | summer
2024-07-17 06:00 | 2024-07-17 07:00 | Summer | FALSE | summer
2024-07-17 07:00 | 2024-07-17 08:00 | Summer | FALSE | summer
2024-07-17 08:00 | 2024-07-17 09:00 | Summer | FALSE | summer
2024-07-17 09:00 | 2024-07-17 10:00 | Summer | FALSE | summer
2024-07-17 10:00 | 2024-07-17 11:00 | Summer | FALSE | summer
2024-07-17 11:00 | 2024-07-17 12:00 | Summer | FALSE | summer
2024-07-17 12:00 | 2024-07-17 13:00 | Summer | FALSE | summer
2024-07-17 13:00 | 2024-07-17 14:00 | Summer | FALSE | summer
2024-07-17 14:00 | 2024-07-17 15:00 | Summer | FALSE | summer
2024-07-17 15:00 | 2024-07-17 16:00 | Summer | FALSE | summer
2024-07-17 16:00 | 2024-07-17 17:00 | Summer | TRUE | summer
2024-07-17 17:00 | 2024-07-17 18:00 | Summer | TRUE | summer
2024-07-17 18:00 | 2024-07-17 19:00 | Summer | TRUE | summer
2024-07-17 19:00 | 2024-07-17 20:00 | Summer | TRUE | summer
2024-07-17 20:00 | 2024-07-17 21:00 | Summer | TRUE | summer
2024-07-17 21:00 | 2024-07-17 22:00 | Summer | FALSE | summer
2024-07-17 22:00 | 2024-07-17 23:00 | Summer | FALSE | summer
2024-07-17 23:00 | 2024-07-18 | Summer | FALSE | summer
2024-07-18 | 2024-07-18 01:00 | Summer | FALSE | summer
2024-07-18 01:00 | 2024-07-18 02:00 | Summer | FALSE | summer
2024-07-18 02:00 | 2024-07-18 03:00 | Summer | FALSE | summer
2024-07-18 03:00 | 2024-07-18 04:00 | Summer | FALSE | summer
2024-07-18 04:00 | 2024-07-18 05:00 | Summer | FALSE | summer
2024-07-18 05:00 | 2024-07-18 06:00 | Summer | FALSE | summer
2024-07-18 06:00 | 2024-07-18 07:00 | Summer | FALSE | summer
2024-07-18 07:00 | 2024-07-18 08:00 | Summer | FALSE | summer
2024-07-18 08:00 | 2024-07-18 09:00 | Summer | FALSE | summer
2024-07-18 09:00 | 2024-07-18 10:00 | Summer | FALSE | summer
2024-07-18 10:00 | 2024-07-18 11:00 | Summer | FALSE | summer
2024-07-18 11:00 | 2024-07-18 12:00 | Summer | FALSE | summer
2024-07-18 12:00 | 2024-07-18 13:00 | Summer | FALSE | summer
2024-07-18 13:00 | 2024-07-18 14:00 | Summer | FALSE | summer
2024-07-18 14:00 | 2024-07-18 15:00 | Summer | FALSE | summer
2024-07-18 15:00 | 2024-07-18 16:00 | Summer | FALSE | summer
2024-07-18 16:00 | 2024-07-18 17:00 | Summer | TRUE | summer
2024-07-18 17:00 | 2024-07-18 18:00 | Summer | TRUE | summer
2024-07-18 18:00 | 2024-07-18 19:00 | Summer | TRUE | summer
2024-07-18 19:00 | 2024-07-18 20:00 | Summer | TRUE | summer
2024-07-18 20:00 | 2024-07-18 21:00 | Summer | TRUE | summer
2024-07-18 21:00 | 2024-07-18 22:00 | Summer | FALSE | summer
2024-07-18 22:00 | 2024-07-18 23:00 | Summer | FALSE | summer
2024-07-18 23:00 | 2024-07-19 | Summer | FALSE | summer
2024-07-19 | 2024-07-19 01:00 | Summer | FALSE | summer
2024-07-19 01:00 | 2024-07-19 02:00 | Summer | FALSE | summer
2024-07-19 02:00 | 2024-07-19 03:00 | Summer | FALSE | summer
2024-07-19 03:00 | 2024-07-19 04:00 | Summer | FALSE | summer
2024-07-19 04:00 | 2024-07-19 05:00 | Summer | FALSE | summer
2024-07-19 05:00 | 2024-07-19 06:00 | Summer | FALSE | summer
2024-07-19 06:00 | 2024-07-19 07:00 | Summer | FALSE | summer
2024-07-19 07:00 | 2024-07-19 08:00 | Summer | FALSE | summer
2024-07-19 08:00 | 2024-07-19 09:00 | Summer | FALSE | summer
2024-07-19 09:00 | 2024-07-19 10:00 | Summer | FALSE | summer
2024-07-19 10:00 | 2024-07-19 11:00 | Summer | FALSE | summer
2024-07-19 11:00 | 2024-07-19 12:00 | Summer | FALSE | summer
2024-07-19 12:00 | 2024-07-19 13:00 | Summer | FALSE | summer
2024-07-19 13:00 | 2024-07-19 14:00 | Summer | FALSE | summer
2024-07-19 14:00 | 2024-07-19 15:00 | Summer | FALSE | summer
2024-07-19 15:00 | 2024-07-19 16:00 | Summer | FALSE | summer
2024-07-19 16:00 | 2024-07-19 17:00 | Summer | TRUE | summer
2024-07-19 17:00 | 2024-07-19 18:00 | Summer | TRUE | summer
2024-07-19 18:00 | 2024-07-19 19:00 | Summer | TRUE | summer
2024-07-19 19:00 | 2024-07-19 20:00 | Summer | TRUE | summer
2024-07-19 20:00 | 2024-07-19 21:00 | Summer | TRUE | summer
2024-07-19 21:00 | 2024-07-19 22:00 | Summer | FALSE | summer
2024-07-19 22:00 | 2024-07-19 23:00 | Summer | FALSE | summer
2024-07-19 23:00 | 2024-07-20 | Summer | FALSE | summer
2024-07-20 | 2024-07-20 01:00 | Summer | FALSE | summer
2024-07-20 01:00 | 2024-07-20 02:00 | Summer | FALSE | summer
2024-07-20 02:00 | 2024-07-20 03:00 | Summer | FALSE | summer
2024-07-20 03:00 | 2024-07-20 04:00 | Summer | FALSE | summer
2024-07-20 04:00 | 2024-07-20 05:00 | Summer | FALSE | summer
2024-07-20 05:00 | 2024-07-20 06:00 | Summer | FALSE | summer
2024-07-20 06:00 | 2024-07-20 07:00 | Summer | FALSE | summer
2024-07-20 07:00 | 2024-07-20 08:00 | Summer | FALSE | summer
2024-07-20 08:00 | 2024-07-20 09:00 | Summer | FALSE | summer
2024-07-20 09:00 | 2024-07-20 10:00 | Summer | FALSE | summer
2024-07-20 10:00 | 2024-07-20 11:00 | Summer | FALSE | summer
2024-07-20 11:00 | 2024-07-20 12:00 | Summer | FALSE | summer
2024-07-20 12:00 | 2024-07-20 13:00 | Summer | FALSE | summer
2024-07-20 13:00 | 2024-07-20 14:00 | Summer | FALSE | summer
2024-07-20 14:00 | 2024-07-20 15:00 | Summer | FALSE | summer
2024-07-20 15:00 | 2024-07-20 16:00 | Summer | FALSE | summer
2024-07-20 16:00 | 2024-07-20 17:00 | Summer | TRUE | summer
2024-07-20 17:00 | 2024-07-20 18:00 | Summer | TRUE | summer
2024-07-20 18:00 | 2024-07-20 19:00 | Summer | TRUE | summer
2024-07-20 19:00 | 2024-07-20 20:00 | Summer | TRUE | summer
2024-07-20 20:00 | 2024-07-20 21:00 | Summer | TRUE | summer
2024-07-20 21:00 | 2024-07-20 22:00 | Summer | FALSE | summer
2024-07-20 22:00 | 2024-07-20 23:00 | Summer | FALSE | summer
2024-07-20 23:00 | 2024-07-21 | Summer | FALSE | summer
2024-07-21 | 2024-07-21 01:00 | Summer | FALSE | summer
2024-07-21 01:00 | 2024-07-21 02:00 | Summer | FALSE | summer
2024-07-21 02:00 | 2024-07-21 03:00 | Summer | FALSE | summer
2024-07-21 03:00 | 2024-07-21 04:00 | Summer | FALSE | summer
2024-07-21 04:00 | 2024-07-21 05:00 | Summer | FALSE | summer
2024-07-21 05:00 | 2024-07-21 06:00 | Summer | FALSE | summer
2024-07-21 06:00 | 2024-07-21 07:00 | Summer | FALSE | summer
2024-07-21 07:00 | 2024-07-21 08:00 | Summer | FALSE | summer
2024-07-21 08:00 | 2024-07-21 09:00 | Summer | FALSE | summer
2024-07-21 09:00 | 2024-07-21 10:00 | Summer | FALSE | summer
2024-07-21 10:00 | 2024-07-21 11:00 | Summer | FALSE | summer
2024-07-21 11:00 | 2024-07-21 12:00 | Summer | FALSE | summer
2024-07-21 12:00 | 2024-07-21 13:00 | Summer | FALSE | summer
2024-07-21 13:00 | 2024-07-21 14:00 | Summer | FALSE | summer
2024-07-21 14:00 | 2024-07-21 15:00 | Summer | FALSE | summer
2024-07-21 15:00 | 2024-07-21 16:00 | Summer | FALSE | summer
2024-07-21 16:00 | 2024-07-21 17:00 | Summer | TRUE | summer
2024-07-21 17:00 | 2024-07-21 18:00 | Summer | TRUE | summer
2024-07-21 18:00 | 2024-07-21 19:00 | Summer | TRUE | summer
2024-07-21 19:00 | 2024-07-21 20:00 | Summer | TRUE | summer
2024-07-21 20:00 | 2024-07-21 21:00 | Summer | TRUE | summer
2024-07-21 21:00 | 2024-07-21 22:00 | Summer | FALSE | summer
2024-07-21 22:00 | 2024-07-21 23:00 | Summer | FALSE | summer
2024-07-21 23:00 | 2024-07-22 | Summer | FALSE | summer
2024-07-22 | 2024-07-22 01:00 | Summer | FALSE | summer
2024-07-22 01:00 | 2024-07-22 02:00 | Summer | FALSE | summer
2024-07-22 02:00 | 2024-07-22 03:00 | Summer | FALSE | summer
2024-07-22 03:00 | 2024-07-22 04:00 | Summer | FALSE | summer
2024-07-22 04:00 | 2024-07-22 05:00 | Summer | FALSE | summer
2024-07-22 05:00 | 2024-07-22 06:00 | Summer | FALSE | summer
2024-07-22 06:00 | 2024-07-22 07:00 | Summer | FALSE | summer
2024-07-22 07:00 | 2024-07-22 08:00 | Summer | FALSE | summer
2024-07-22 08:00 | 2024-07-22 09:00 | Summer | FALSE | summer
2024-07-22 09:00 | 2024-07-22 10:00 | Summer | FALSE | summer
2024-07-22 10:00 | 2024-07-22 11:00 | Summer | FALSE | summer
2024-07-22 11:00 | 2024-07-22 12:00 | Summer | FALSE | summer
2024-07-22 12:00 | 2024-07-22 13:00 | Summer | FALSE | summer
2024-07-22 13:00 | 2024-07-22 14:00 | Summer | FALSE | summer
2024-07-22 14:00 | 2024-07-22 15:00 | Summer | FALSE | summer
2024-07-22 15:00 | 2024-07-22 16:00 | Summer | FALSE | summer
2024-07-22 16:00 | 2024-07-22 17:00 | Summer | TRUE | summer
2024-07-22 17:00 | 2024-07-22 18:00 | Summer | TRUE | summer
2024-07-22 18:00 | 2024-07-22 19:00 | Summer | TRUE | summer
2024-07-22 19:00 | 2024-07-22 20:00 | Summer | TRUE | summer
2024-07-22 20:00 | 2024-07-22 21:00 | Summer | TRUE | summer
2024-07-22 21:00 | 2024-07-22 22:00 | Summer | FALSE | summer
2024-07-22 22:00 | 2024-07-22 23:00 | Summer | FALSE | summer
2024-07-22 23:00 | 2024-07-23 | Summer | FALSE | summer
2024-07-23 | 2024-07-23 01:00 | Summer | FALSE | summer
2024-07-23 01:00 | 2024-07-23 02:00 | Summer | FALSE | summer
2024-07-23 02:00 | 2024-07-23 03:00 | Summer | FALSE | summer
2024-07-23 03:00 | 2024-07-23 04:00 | Summer | FALSE | summer
2024-07-23 04:00 | 2024-07-23 05:00 | Summer | FALSE | summer
2024-07-23 05:00 | 2024-07-23 06:00 | Summer | FALSE | summer
2024-07-23 06:00 | 2024-07-23 07:00 | Summer | FALSE | summer
2024-07-23 07:00 | 2024-07-23 08:00 | Summer | FALSE | summer
2024-07-23 08:00 | 2024-07-23 09:00 | Summer | FALSE | summer
2024-07-23 09:00 | 2024-07-23 10:00 | Summer | FALSE | summer
2024-07-23 10:00 | 2024-07-23 11:00 | Summer | FALSE | summer
2024-07-23 11:00 | 2024-07-23 12:00 | Summer | FALSE | summer
2024-07-23 12:00 | 2024-07-23 13:00 | Summer | FALSE | summer
2024-07-23 13:00 | 2024-07-23 14:00 | Summer | FALSE | summer
2024-07-23 14:00 | 2024-07-23 15:00 | Summer | FALSE | summer
2024-07-23 15:00 | 2024-07-23 16:00 | Summer | FALSE | summer
2024-07-23 16:00 | 2024-07-23 17:00 | Summer | TRUE | summer
2024-07-23 17:00 | 2024-07-23 18:00 | Summer | TRUE | summer
2024-07-23 18:00 | 2024-07-23 19:00 | Summer | TRUE | summer
2024-07-23 19:00 | 2024-07-23 20:00 | Summer | TRUE | summer
2024-07-23 20:00 | 2024-07-23 21:00 | Summer | TRUE | summer
2024-07-23 21:00 | 2024-07-23 22:00 | Summer | FALSE | summer
2024-07-23 22:00 | 2024-07-23 23:00 | Summer | FALSE | summer
2024-07-23 23:00 | 2024-07-24 | Summer | FALSE | summer
2024-07-24 | 2024-07-24 01:00 | Summer | FALSE | summer
2024-07-24 01:00 | 2024-07-24 02:00 | Summer | FALSE | summer
2024-07-24 02:00 | 2024-07-24 03:00 | Summer | FALSE | summer
2024-07-24 03:00 | 2024-07-24 04:00 | Summer | FALSE | summer
2024-07-24 04:00 | 2024-07-24 05:00 | Summer | FALSE | summer
2024-07-24 05:00 | 2024-07-24 06:00 | Summer | FALSE | summer
2024-07-24 06:00 | 2024-07-24 07:00 | Summer | FALSE | summer
2024-07-24 07:00 | 2024-07-24 08:00 | Summer | FALSE | summer
2024-07-24 08:00 | 2024-07-24 09:00 | Summer | FALSE | summer
2024-07-24 09:00 | 2024-07-24 10:00 | Summer | FALSE | summer
2024-07-24 10:00 | 2024-07-24 11:00 | Summer | FALSE | summer
2024-07-24 11:00 | 2024-07-24 12:00 | Summer | FALSE | summer
2024-07-24 12:00 | 2024-07-24 13:00 | Summer | FALSE | summer
2024-07-24 13:00 | 2024-07-24 14:00 | Summer | FALSE | summer
2024-07-24 14:00 | 2024-07-24 15:00 | Summer | FALSE | summer
2024-07-24 15:00 | 2024-07-24 16:00 | Summer | FALSE | summer
2024-07-24 16:00 | 2024-07-24 17:00 | Summer | TRUE | summer
2024-07-24 17:00 | 2024-07-24 18:00 | Summer | TRUE | summer
2024-07-24 18:00 | 2024-07-24 19:00 | Summer | TRUE | summer
2024-07-24 19:00 | 2024-07-24 20:00 | Summer | TRUE | summer
2024-07-24 20:00 | 2024-07-24 21:00 | Summer | TRUE | summer
2024-07-24 21:00 | 2024-07-24 22:00 | Summer | FALSE | summer
2024-07-24 22:00 | 2024-07-24 23:00 | Summer | FALSE | summer
2024-07-24 23:00 | 2024-07-25 | Summer | FALSE | summer
2024-07-25 | 2024-07-25 01:00 | Summer | FALSE | summer
2024-07-25 01:00 | 2024-07-25 02:00 | Summer | FALSE | summer
2024-07-25 02:00 | 2024-07-25 03:00 | Summer | FALSE | summer
2024-07-25 03:00 | 2024-07-25 04:00 | Summer | FALSE | summer
2024-07-25 04:00 | 2024-07-25 05:00 | Summer | FALSE | summer
2024-07-25 05:00 | 2024-07-25 06:00 | Summer | FALSE | summer
2024-07-25 06:00 | 2024-07-25 07:00 | Summer | FALSE | summer
2024-07-25 07:00 | 2024-07-25 08:00 | Summer | FALSE | summer
2024-07-25 08:00 | 2024-07-25 09:00 | Summer | FALSE | summer
2024-07-25 09:00 | 2024-07-25 10:00 | Summer | FALSE | summer
2024-07-25 10:00 | 2024-07-25 11:00 | Summer | FALSE | summer
2024-07-25 11:00 | 2024-07-25 12:00 | Summer | FALSE | summer
2024-07-25 12:00 | 2024-07-25 13:00 | Summer | FALSE | summer
2024-07-25 13:00 | 2024-07-25 14:00 | Summer | FALSE | summer
2024-07-25 14:00 | 2024-07-25 15:00 | Summer | FALSE | summer
2024-07-25 15:00 | 2024-07-25 16:00 | Summer | FALSE | summer
2024-07-25 16:00 | 2024-07-25 17:00 | Summer | TRUE | summer
2024-07-25 17:00 | 2024-07-25 18:00 | Summer | TRUE | summer
2024-07-25 18:00 | 2024-07-25 19:00 | Summer | TRUE | summer
2024-07-25 19:00 | 2024-07-25 20:00 | Summer | TRUE | summer
2024-07-25 20:00 | 2024-07-25 21:00 | Summer | TRUE | summer
2024-07-25 21:00 | 2024-07-25 22:00 | Summer | FALSE | summer
2024-07-25 22:00 | 2024-07-25 23:00 | Summer | FALSE | summer
2024-07-25 23:00 | 2024-07-26 | Summer | FALSE | summer
2024-07-26 | 2024-07-26 01:00 | Summer | FALSE | summer
2024-07-26 01:00 | 2024-07-26 02:00 | Summer | FALSE | summer
2024-07-26 02:00 | 2024-07-26 03:00 | Summer | FALSE | summer
2024-07-26 03:00 | 2024-07-26 04:00 | Summer | FALSE | summer
2024-07-26 04:00 | 2024-07-26 05:00 | Summer | FALSE | summer
2024-07-26 05:00 | 2024-07-26 06:00 | Summer | FALSE | summer
2024-07-26 06:00 | 2024-07-26 07:00 | Summer | FALSE | summer
2024-07-26 07:00 | 2024-07-26 08:00 | Summer | FALSE | summer
2024-07-26 08:00 | 2024-07-26 09:00 | Summer | FALSE | summer
2024-07-26 09:00 | 2024-07-26 10:00 | Summer | FALSE | summer
2024-07-26 10:00 | 2024-07-26 11:00 | Summer | FALSE | summer
2024-07-26 11:00 | 2024-07-26 12:00 | Summer | FALSE | summer
2024-07-26 12:00 | 2024-07-26 13:00 | Summer | FALSE | summer
2024-07-26 13:00 | 2024-07-26 14:00 | Summer | FALSE | summer
2024-07-26 14:00 | 2024-07-26 15:00 | Summer | FALSE | summer
2024-07-26 15:00 | 2024-07-26 16:00 | Summer | FALSE | summer
2024-07-26 16:00 | 2024-07-26 17:00 | Summer | TRUE | summer
2024-07-26 17:00 | 2024-07-26 18:00 | Summer | TRUE | summer
2024-07-26 18:00 | 2024-07-26 19:00 | Summer | TRUE | summer
2024-07-26 19:00 | 2024-07-26 20:00 | Summer | TRUE | summer
2024-07-26 20:00 | 2024-07-26 21:00 | Summer | TRUE | summer
2024-07-26 21:00 | 2024-07-26 22:00 | Summer | FALSE | summer
2024-07-26 22:00 | 2024-07-26 23:00 | Summer | FALSE | summer
2024-07-26 23:00 | 2024-07-27 | Summer | FALSE | summer
2024-07-27 | 2024-07-27 01:00 | Summer | FALSE | summer
2024-07-27 01:00 | 2024-07-27 02:00 | Summer | FALSE | summer
2024-07-27 02:00 | 2024-07-27 03:00 | Summer | FALSE | summer
2024-07-27 03:00 | 2024-07-27 04:00 | Summer | FALSE | summer
2024-07-27 04:00 | 2024-07-27 05:00 | Summer | FALSE | summer
2024-07-27 05:00 | 2024-07-27 06:00 | Summer | FALSE | summer
2024-07-27 06:00 | 2024-07-27 07:00 | Summer | FALSE | summer
2024-07-27 07:00 | 2024-07-27 08:00 | Summer | FALSE | summer
2024-07-27 08:00 | 2024-07-27 09:00 | Summer | FALSE | summer
2024-07-27 09:00 | 2024-07-27 10:00 | Summer | FALSE | summer
2024-07-27 10:00 | 2024-07-27 11:00 | Summer | FALSE | summer
2024-07-27 11:00 | 2024-07-27 12:00 | Summer | FALSE | summer
2024-07-27 12:00 | 2024-07-27 13:00 | Summer | FALSE | summer
2024-07-27 13:00 | 2024-07-27 14:00 | Summer | FALSE | summer
2024-07-27 14:00 | 2024-07-27 15:00 | Summer | FALSE | summer
2024-07-27 15:00 | 2024-07-27 16:00 | Summer | FALSE | summer
2024-07-27 16:00 | 2024-07-27 17:00 | Summer | TRUE | summer
2024-07-27 17:00 | 2024-07-27 18:00 | Summer | TRUE | summer
2024-07-27 18:00 | 2024-07-27 19:00 | Summer | TRUE | summer
2024-07-27 19:00 | 2024-07-27 20:00 | Summer | TRUE | summer
2024-07-27 20:00 | 2024-07-27 21:00 | Summer | TRUE | summer
2024-07-27 21:00 | 2024-07-27 22:00 | Summer | FALSE | summer
2024-07-27 22:00 | 2024-07-27 23:00 | Summer | FALSE | summer
2024-07-27 23:00 | 2024-07-28 | Summer | FALSE | summer
2024-07-28 | 2024-07-28 01:00 | Summer | FALSE | summer
2024-07-28 01:00 | 2024-07-28 02:00 | Summer | FALSE | summer
2024-07-28 02:00 | 2024-07-28 03:00 | Summer | FALSE | summer
2024-07-28 03:00 | 2024-07-28 04:00 | Summer | FALSE | summer
2024-07-28 04:00 | 2024-07-28 05:00 | Summer | FALSE | summer
2024-07-28 05:00 | 2024-07-28 06:00 | Summer | FALSE | summer
2024-07-28 06:00 | 2024-07-28 07:00 | Summer | FALSE | summer
2024-07-28 07:00 | 2024-07-28 08:00 | Summer | FALSE | summer
2024-07-28 08:00 | 2024-07-28 09:00 | Summer | FALSE | summer
2024-07-28 09:00 | 2024-07-28 10:00 | Summer | FALSE | summer
2024-07-28 10:00 | 2024-07-28 11:00 | Summer | FALSE | summer
2024-07-28 11:00 | 2024-07-28 12:00 | Summer | FALSE | summer
2024-07-28 12:00 | 2024-07-28 13:00 | Summer | FALSE | summer
2024-07-28 13:00 | 2024-07-28 14:00 | Summer | FALSE | summer
2024-07-28 14:00 | 2024-07-28 15:00 | Summer | FALSE | summer
2024-07-28 15:00 | 2024-07-28 16:00 | Summer | FALSE | summer
2024-07-28 16:00 | 2024-07-28 17:00 | Summer | TRUE | summer
2024-07-28 17:00 | 2024-07-28 18:00 | Summer | TRUE | summer
2024-07-28 18:00 | 2024-07-28 19:00 | Summer | TRUE | summer
2024-07-28 19:00 | 2024-07-28 20:00 | Summer | TRUE | summer
2024-07-28 20:00 | 2024-07-28 21:00 | Summer | TRUE | summer
2024-07-28 21:00 | 2024-07-28 22:00 | Summer | FALSE | summer
2024-07-28 22:00 | 2024-07-28 23:00 | Summer | FALSE | summer
2024-07-28 23:00 | 2024-07-29 | Summer | FALSE | summer
2024-07-29 | 2024-07-29 01:00 | Summer | FALSE | summer
2024-07-29 01:00 | 2024-07-29 02:00 | Summer | FALSE | summer
2024-07-29 02:00 | 2024-07-29 03:00 | Summer | FALSE | summer
2024-07-29 03:00 | 2024-07-29 04:00 | Summer | FALSE | summer
2024-07-29 04:00 | 2024-07-29 05:00 | Summer | FALSE | summer
2024-07-29 05:00 | 2024-07-29 06:00 | Summer | FALSE | summer
2024-07-29 06:00 | 2024-07-29 07:00 | Summer | FALSE | summer
2024-07-29 07:00 | 2024-07-29 08:00 | Summer | FALSE | summer
2024-07-29 08:00 | 2024-07-29 09:00 | Summer | FALSE | summer
2024-07-29 09:00 | 2024-07-29 10:00 | Summer | FALSE | summer
2024-07-29 10:00 | 2024-07-29 11:00 | Summer | FALSE | summer
2024-07-29 11:00 | 2024-07-29 12:00 | Summer | FALSE | summer
2024-07-29 12:00 | 2024-07-29 13:00 | Summer | FALSE | summer
2024-07-29 13:00 | 2024-07-29 14:00 | Summer | FALSE | summer
2024-07-29 14:00 | 2024-07-29 15:00 | Summer | FALSE | summer
2024-07-29 15:00 | 2024-07-29 16:00 | Summer | FALSE | summer
2024-07-29 16:00 | 2024-07-29 17:00 | Summer | TRUE | summer
2024-07-29 17:00 | 2024-07-29 18:00 | Summer | TRUE | summer
2024-07-29 18:00 | 2024-07-29 19:00 | Summer | TRUE | summer
2024-07-29 19:00 | 2024-07-29 20:00 | Summer | TRUE | summer
2024-07-29 20:00 | 2024-07-29 21:00 | Summer | TRUE | summer
2024-07-29 21:00 | 2024-07-29 22:00 | Summer | FALSE | summer
2024-07-29 22:00 | 2024-07-29 23:00 | Summer | FALSE | summer
2024-07-29 23:00 | 2024-07-30 | Summer | FALSE | summer
2024-07-30 | 2024-07-30 01:00 | Summer | FALSE | summer
2024-07-30 01:00 | 2024-07-30 02:00 | Summer | FALSE | summer
2024-07-30 02:00 | 2024-07-30 03:00 | Summer | FALSE | summer
2024-07-30 03:00 | 2024-07-30 04:00 | Summer | FALSE | summer
2024-07-30 04:00 | 2024-07-30 05:00 | Summer | FALSE | summer
2024-07-30 05:00 | 2024-07-30 06:00 | Summer | FALSE | summer
2024-07-30 06:00 | 2024-07-30 07:00 | Summer | FALSE | summer
2024-07-30 07:00 | 2024-07-30 08:00 | Summer | FALSE | summer
2024-07-30 08:00 | 2024-07-30 09:00 | Summer | FALSE | summer
2024-07-30 09:00 | 2024-07-30 10:00 | Summer | FALSE | summer
2024-07-30 10:00 | 2024-07-30 11:00 | Summer | FALSE | summer
2024-07-30 11:00 | 2024-07-30 12:00 | Summer | FALSE | summer
2024-07-30 12:00 | 2024-07-30 13:00 | Summer | FALSE | summer
2024-07-30 13:00 | 2024-07-30 14:00 | Summer | FALSE | summer
2024-07-30 14:00 | 2024-07-30 15:00 | Summer | FALSE | summer
2024-07-30 15:00 | 2024-07-30 16:00 | Summer | FALSE | summer
2024-07-30 16:00 | 2024-07-30 17:00 | Summer | TRUE | summer
2024-07-30 17:00 | 2024-07-30 18:00 | Summer | TRUE | summer
2024-07-30 18:00 | 2024-07-30 19:00 | Summer | TRUE | summer
2024-07-30 19:00 | 2024-07-30 20:00 | Summer | TRUE | summer
2024-07-30 20:00 | 2024-07-30 21:00 | Summer | TRUE | summer
2024-07-30 21:00 | 2024-07-30 22:00 | Summer | FALSE | summer
2024-07-30 22:00 | 2024-07-30 23:00 | Summer | FALSE | summer
2024-07-30 23:00 | 2024-07-31 | Summer | FALSE | summer
2024-07-31 | 2024-07-31 01:00 | Summer | FALSE | summer
2024-07-31 01:00 | 2024-07-31 02:00 | Summer | FALSE | summer
2024-07-31 02:00 | 2024-07-31 03:00 | Summer | FALSE | summer
2024-07-31 03:00 | 2024-07-31 04:00 | Summer | FALSE | summer
2024-07-31 04:00 | 2024-07-31 05:00 | Summer | FALSE | summer
2024-07-31 05:00 | 2024-07-31 06:00 | Summer | FALSE | summer
2024-07-31 06:00 | 2024-07-31 07:00 | Summer | FALSE | summer
2024-07-31 07:00 | 2024-07-31 08:00 | Summer | FALSE | summer
2024-07-31 08:00 | 2024-07-31 09:00 | Summer | FALSE | summer
2024-07-31 09:00 | 2024-07-31 10:00 | Summer | FALSE | summer
2024-07-31 10:00 | 2024-07-31 11:00 | Summer | FALSE | summer
2024-07-31 11:00 | 2024-07-31 12:00 | Summer | FALSE | summer
2024-07-31 12:00 | 2024-07-31 13:00 | Summer | FALSE | summer
2024-07-31 13:00 | 2024-07-31 14:00 | Summer | FALSE | summer
2024-07-31 14:00 | 2024-07-31 15:00 | Summer | FALSE | summer
2024-07-31 15:00 | 2024-07-31 16:00 | Summer | FALSE | summer
2024-07-31 16:00 | 2024-07-31 17:00 | Summer | TRUE | summer
2024-07-31 17:00 | 2024-07-31 18:00 | Summer | TRUE | summer
2024-07-31 18:00 | 2024-07-31 19:00 | Summer | TRUE | summer
2024-07-31 19:00 | 2024-07-31 20:00 | Summer | TRUE | summer
2024-07-31 20:00 | 2024-07-31 21:00 | Summer | TRUE | summer
2024-07-31 21:00 | 2024-07-31 22:00 | Summer | FALSE | summer
2024-07-31 22:00 | 2024-07-31 23:00 | Summer | FALSE | summer
2024-07-31 23:00 | 2024-08-01 | Summer | FALSE | summer
2024-08-01 | 2024-08-01 01:00 | Summer | FALSE | summer
2024-08-01 01:00 | 2024-08-01 02:00 | Summer | FALSE | summer
2024-08-01 02:00 | 2024-08-01 03:00 | Summer | FALSE | summer
2024-08-01 03:00 | 2024-08-01 04:00 | Summer | FALSE | summer
2024-08-01 04:00 | 2024-08-01 05:00 | Summer | FALSE | summer
2024-08-01 05:00 | 2024-08-01 06:00 | Summer | FALSE | summer
2024-08-01 06:00 | 2024-08-01 07:00 | Summer | FALSE | summer
2024-08-01 07:00 | 2024-08-01 08:00 | Summer | FALSE | summer
2024-08-01 08:00 | 2024-08-01 09:00 | Summer | FALSE | summer
2024-08-01 09:00 | 2024-08-01 10:00 | Summer | FALSE | summer
2024-08-01 10:00 | 2024-08-01 11:00 | Summer | FALSE | summer
2024-08-01 11:00 | 2024-08-01 12:00 | Summer | FALSE | summer
2024-08-01 12:00 | 2024-08-01 13:00 | Summer | FALSE | summer
2024-08-01 13:00 | 2024-08-01 14:00 | Summer | FALSE | summer
2024-08-01 14:00 | 2024-08-01 15:00 | Summer | FALSE | summer
2024-08-01 15:00 | 2024-08-01 16:00 | Summer | FALSE | summer
2024-08-01 16:00 | 2024-08-01 17:00 | Summer | TRUE | summer
2024-08-01 17:00 | 2024-08-01 18:00 | Summer | TRUE | summer
2024-08-01 18:00 | 2024-08-01 19:00 | Summer | TRUE | summer
2024-08-01 19:00 | 2024-08-01 20:00 | Summer | TRUE | summer
2024-08-01 20:00 | 2024-08-01 21:00 | Summer | TRUE | summer
2024-08-01 21:00 | 2024-08-01 22:00 | Summer | FALSE | summer
2024-08-01 22:00 | 2024-08-01 23:00 | Summer | FALSE | summer
2024-08-01 23:00 | 2024-08-02 | Summer | FALSE | summer
2024-08-02 | 2024-08-02 01:00 | Summer | FALSE | summer
2024-08-02 01:00 | 2024-08-02 02:00 | Summer | FALSE | summer
2024-08-02 02:00 | 2024-08-02 03:00 | Summer | FALSE | summer
2024-08-02 03:00 | 2024-08-02 04:00 | Summer | FALSE | summer
2024-08-02 04:00 | 2024-08-02 05:00 | Summer | FALSE | summer
2024-08-02 05:00 | 2024-08-02 06:00 | Summer | FALSE | summer
2024-08-02 06:00 | 2024-08-02 07:00 | Summer | FALSE | summer
2024-08-02 07:00 | 2024-08-02 08:00 | Summer | FALSE | summer
2024-08-02 08:00 | 2024-08-02 09:00 | Summer | FALSE | summer
2024-08-02 09:00 | 2024-08-02 10:00 | Summer | FALSE | summer
2024-08-02 10:00 | 2024-08-02 11:00 | Summer | FALSE | summer
2024-08-02 11:00 | 2024-08-02 12:00 | Summer | FALSE | summer
2024-08-02 12:00 | 2024-08-02 13:00 | Summer | FALSE | summer
2024-08-02 13:00 | 2024-08-02 14:00 | Summer | FALSE | summer
2024-08-02 14:00 | 2024-08-02 15:00 | Summer | FALSE | summer
2024-08-02 15:00 | 2024-08-02 16:00 | Summer | FALSE | summer
2024-08-02 16:00 | 2024-08-02 17:00 | Summer | TRUE | summer
2024-08-02 17:00 | 2024-08-02 18:00 | Summer | TRUE | summer
2024-08-02 18:00 | 2024-08-02 19:00 | Summer | TRUE | summer
2024-08-02 19:00 | 2024-08-02 20:00 | Summer | TRUE | summer
2024-08-02 20:00 | 2024-08-02 21:00 | Summer | TRUE | summer
2024-08-02 21:00 | 2024-08-02 22:00 | Summer | FALSE | summer
2024-08-02 22:00 | 2024-08-02 23:00 | Summer | FALSE | summer
2024-08-02 23:00 | 2024-08-03 | Summer | FALSE | summer
2024-08-03 | 2024-08-03 01:00 | Summer | FALSE | summer
2024-08-03 01:00 | 2024-08-03 02:00 | Summer | FALSE | summer
2024-08-03 02:00 | 2024-08-03 03:00 | Summer | FALSE | summer
2024-08-03 03:00 | 2024-08-03 04:00 | Summer | FALSE | summer
2024-08-03 04:00 | 2024-08-03 05:00 | Summer | FALSE | summer
2024-08-03 05:00 | 2024-08-03 06:00 | Summer | FALSE | summer
2024-08-03 06:00 | 2024-08-03 07:00 | Summer | FALSE | summer
2024-08-03 07:00 | 2024-08-03 08:00 | Summer | FALSE | summer
2024-08-03 08:00 | 2024-08-03 09:00 | Summer | FALSE | summer
2024-08-03 09:00 | 2024-08-03 10:00 | Summer | FALSE | summer
2024-08-03 10:00 | 2024-08-03 11:00 | Summer | FALSE | summer
2024-08-03 11:00 | 2024-08-03 12:00 | Summer | FALSE | summer
2024-08-03 12:00 | 2024-08-03 13:00 | Summer | FALSE | summer
2024-08-03 13:00 | 2024-08-03 14:00 | Summer | FALSE | summer
2024-08-03 14:00 | 2024-08-03 15:00 | Summer | FALSE | summer
2024-08-03 15:00 | 2024-08-03 16:00 | Summer | FALSE | summer
2024-08-03 16:00 | 2024-08-03 17:00 | Summer | TRUE | summer
2024-08-03 17:00 | 2024-08-03 18:00 | Summer | TRUE | summer
2024-08-03 18:00 | 2024-08-03 19:00 | Summer | TRUE | summer
2024-08-03 19:00 | 2024-08-03 20:00 | Summer | TRUE | summer
2024-08-03 20:00 | 2024-08-03 21:00 | Summer | TRUE | summer
2024-08-03 21:00 | 2024-08-03 22:00 | Summer | FALSE | summer
2024-08-03 22:00 | 2024-08-03 23:00 | Summer | FALSE | summer
2024-08-03 23:00 | 2024-08-04 | Summer | FALSE | summer
2024-08-04 | 2024-08-04 01:00 | Summer | FALSE | summer
2024-08-04 01:00 | 2024-08-04 02:00 | Summer | FALSE | summer
2024-08-04 02:00 | 2024-08-04 03:00 | Summer | FALSE | summer
2024-08-04 03:00 | 2024-08-04 04:00 | Summer | FALSE | summer
2024-08-04 04:00 | 2024-08-04 05:00 | Summer | FALSE | summer
2024-08-04 05:00 | 2024-08-04 06:00 | Summer | FALSE | summer
2024-08-04 06:00 | 2024-08-04 07:00 | Summer | FALSE | summer
2024-08-04 07:00 | 2024-08-04 08:00 | Summer | FALSE | summer
2024-08-04 08:00 | 2024-08-04 09:00 | Summer | FALSE | summer
2024-08-04 09:00 | 2024-08-04 10:00 | Summer | FALSE | summer
2024-08-04 10:00 | 2024-08-04 11:00 | Summer | FALSE | summer
2024-08-04 11:00 | 2024-08-04 12:00 | Summer | FALSE | summer
2024-08-04 12:00 | 2024-08-04 13:00 | Summer | FALSE | summer
2024-08-04 13:00 | 2024-08-04 14:00 | Summer | FALSE | summer
2024-08-04 14:00 | 2024-08-04 15:00 | Summer | FALSE | summer
2024-08-04 15:00 | 2024-08-04 16:00 | Summer | FALSE | summer
2024-08-04 16:00 | 2024-08-04 17:00 | Summer | TRUE | summer
2024-08-04 17:00 | 2024-08-04 18:00 | Summer | TRUE | summer
2024-08-04 18:00 | 2024-08-04 19:00 | Summer | TRUE | summer
2024-08-04 19:00 | 2024-08-04 20:00 | Summer | TRUE | summer
2024-08-04 20:00 | 2024-08-04 21:00 | Summer | TRUE | summer
2024-08-04 21:00 | 2024-08-04 22:00 | Summer | FALSE | summer
2024-08-04 22:00 | 2024-08-04 23:00 | Summer | FALSE | summer
2024-08-04 23:00 | 2024-08-05 | Summer | FALSE | summer
2024-08-05 | 2024-08-05 01:00 | Summer | FALSE | summer
2024-08-05 01:00 | 2024-08-05 02:00 | Summer | FALSE | summer
2024-08-05 02:00 | 2024-08-05 03:00 | Summer | FALSE | summer
2024-08-05 03:00 | 2024-08-05 04:00 | Summer | FALSE | summer
2024-08-05 04:00 | 2024-08-05 05:00 | Summer | FALSE | summer
2024-08-05 05:00 | 2024-08-05 06:00 | Summer | FALSE | summer
2024-08-05 06:00 | 2024-08-05 07:00 | Summer | FALSE | summer
2024-08-05 07:00 | 2024-08-05 08:00 | Summer | FALSE | summer
2024-08-05 08:00 | 2024-08-05 09:00 | Summer | FALSE | summer
2024-08-05 09:00 | 2024-08-05 10:00 | Summer | FALSE | summer
2024-08-05 10:00 | 2024-08-05 11:00 | Summer | FALSE | summer
2024-08-05 11:00 | 2024-08-05 12:00 | Summer | FALSE | summer
2024-08-05 12:00 | 2024-08-05 13:00 | Summer | FALSE | summer
2024-08-05 13:00 | 2024-08-05 14:00 | Summer | FALSE | summer
2024-08-05 14:00 | 2024-08-05 15:00 | Summer | FALSE | summer
2024-08-05 15:00 | 2024-08-05 16:00 | Summer | FALSE | summer
2024-08-05 16:00 | 2024-08-05 17:00 | Summer | TRUE | summer
2024-08-05 17:00 | 2024-08-05 18:00 | Summer | TRUE | summer
2024-08-05 18:00 | 2024-08-05 19:00 | Summer | TRUE | summer
2024-08-05 19:00 | 2024-08-05 20:00 | Summer | TRUE | summer
2024-08-05 20:00 | 2024-08-05 21:00 | Summer | TRUE | summer
2024-08-05 21:00 | 2024-08-05 22:00 | Summer | FALSE | summer
2024-08-05 22:00 | 2024-08-05 23:00 | Summer | FALSE | summer
2024-08-05 23:00 | 2024-08-06 | Summer | FALSE | summer
2024-08-06 | 2024-08-06 01:00 | Summer | FALSE | summer
2024-08-06 01:00 | 2024-08-06 02:00 | Summer | FALSE | summer
2024-08-06 02:00 | 2024-08-06 03:00 | Summer | FALSE | summer
2024-08-06 03:00 | 2024-08-06 04:00 | Summer | FALSE | summer
2024-08-06 04:00 | 2024-08-06 05:00 | Summer | FALSE | summer
2024-08-06 05:00 | 2024-08-06 06:00 | Summer | FALSE | summer
2024-08-06 06:00 | 2024-08-06 07:00 | Summer | FALSE | summer
2024-08-06 07:00 | 2024-08-06 08:00 | Summer | FALSE | summer
2024-08-06 08:00 | 2024-08-06 09:00 | Summer | FALSE | summer
2024-08-06 09:00 | 2024-08-06 10:00 | Summer | FALSE | summer
2024-08-06 10:00 | 2024-08-06 11:00 | Summer | FALSE | summer
2024-08-06 11:00 | 2024-08-06 12:00 | Summer | FALSE | summer
2024-08-06 12:00 | 2024-08-06 13:00 | Summer | FALSE | summer
2024-08-06 13:00 | 2024-08-06 14:00 | Summer | FALSE | summer
2024-08-06 14:00 | 2024-08-06 15:00 | Summer | FALSE | summer
2024-08-06 15:00 | 2024-08-06 16:00 | Summer | FALSE | summer
2024-08-06 16:00 | 2024-08-06 17:00 | Summer | TRUE | summer
2024-08-06 17:00 | 2024-08-06 18:00 | Summer | TRUE | summer
2024-08-06 18:00 | 2024-08-06 19:00 | Summer | TRUE | summer
2024-08-06 19:00 | 2024-08-06 20:00 | Summer | TRUE | summer
2024-08-06 20:00 | 2024-08-06 21:00 | Summer | TRUE | summer
2024-08-06 21:00 | 2024-08-06 22:00 | Summer | FALSE | summer
2024-08-06 22:00 | 2024-08-06 23:00 | Summer | FALSE | summer
2024-08-06 23:00 | 2024-08-07 | Summer | FALSE | summer
2024-08-07 | 2024-08-07 01:00 | Summer | FALSE | summer
2024-08-07 01:00 | 2024-08-07 02:00 | Summer | FALSE | summer
2024-08-07 02:00 | 2024-08-07 03:00 | Summer | FALSE | summer
2024-08-07 03:00 | 2024-08-07 04:00 | Summer | FALSE | summer
2024-08-07 04:00 | 2024-08-07 05:00 | Summer | FALSE | summer
2024-08-07 05:00 | 2024-08-07 06:00 | Summer | FALSE | summer
2024-08-07 06:00 | 2024-08-07 07:00 | Summer | FALSE | summer
2024-08-07 07:00 | 2024-08-07 08:00 | Summer | FALSE | summer
2024-08-07 08:00 | 2024-08-07 09:00 | Summer | FALSE | summer
2024-08-07 09:00 | 2024-08-07 10:00 | Summer | FALSE | summer
2024-08-07 10:00 | 2024-08-07 11:00 | Summer | FALSE | summer
2024-08-07 11:00 | 2024-08-07 12:00 | Summer | FALSE | summer
2024-08-07 12:00 | 2024-08-07 13:00 | Summer | FALSE | summer
2024-08-07 13:00 | 2024-08-07 14:00 | Summer | FALSE | summer
2024-08-07 14:00 | 2024-08-07 15:00 | Summer | FALSE | summer
2024-08-07 15:00 | 2024-08-07 16:00 | Summer | FALSE | summer
2024-08-07 16:00 | 2024-08-07 17:00 | Summer | TRUE | summer
2024-08-07 17:00 | 2024-08-07 18:00 | Summer | TRUE | summer
2024-08-07 18:00 | 2024-08-07 19:00 | Summer | TRUE | summer
2024-08-07 19:00 | 2024-08-07 20:00 | Summer | TRUE | summer
2024-08-07 20:00 | 2024-08-07 21:00 | Summer | TRUE | summer
2024-08-07 21:00 | 2024-08-07 22:00 | Summer | FALSE | summer
2024-08-07 22:00 | 2024-08-07 23:00 | Summer | FALSE | summer
2024-08-07 23:00 | 2024-08-08 | Summer | FALSE | summer
2024-08-08 | 2024-08-08 01:00 | Summer | FALSE | summer
2024-08-08 01:00 | 2024-08-08 02:00 | Summer | FALSE | summer
2024-08-08 02:00 | 2024-08-08 03:00 | Summer | FALSE | summer
2024-08-08 03:00 | 2024-08-08 04:00 | Summer | FALSE | summer
2024-08-08 04:00 | 2024-08-08 05:00 | Summer | FALSE | summer
2024-08-08 05:00 | 2024-08-08 06:00 | Summer | FALSE | summer
2024-08-08 06:00 | 2024-08-08 07:00 | Summer | FALSE | summer
2024-08-08 07:00 | 2024-08-08 08:00 | Summer | FALSE | summer
2024-08-08 08:00 | 2024-08-08 09:00 | Summer | FALSE | summer
2024-08-08 09:00 | 2024-08-08 10:00 | Summer | FALSE | summer
2024-08-08 10:00 | 2024-08-08 11:00 | Summer | FALSE | summer
2024-08-08 11:00 | 2024-08-08 12:00 | Summer | FALSE | summer
2024-08-08 12:00 | 2024-08-08 13:00 | Summer | FALSE | summer
2024-08-08 13:00 | 2024-08-08 14:00 | Summer | FALSE | summer
2024-08-08 14:00 | 2024-08-08 15:00 | Summer | FALSE | summer
2024-08-08 15:00 | 2024-08-08 16:00 | Summer | FALSE | summer
2024-08-08 16:00 | 2024-08-08 17:00 | Summer | TRUE | summer
2024-08-08 17:00 | 2024-08-08 18:00 | Summer | TRUE | summer
2024-08-08 18:00 | 2024-08-08 19:00 | Summer | TRUE | summer
2024-08-08 19:00 | 2024-08-08 20:00 | Summer | TRUE | summer
2024-08-08 20:00 | 2024-08-08 21:00 | Summer | TRUE | summer
2024-08-08 21:00 | 2024-08-08 22:00 | Summer | FALSE | summer
2024-08-08 22:00 | 2024-08-08 23:00 | Summer | FALSE | summer
2024-08-08 23:00 | 2024-08-09 | Summer | FALSE | summer
2024-08-09 | 2024-08-09 01:00 | Summer | FALSE | summer
2024-08-09 01:00 | 2024-08-09 02:00 | Summer | FALSE | summer
2024-08-09 02:00 | 2024-08-09 03:00 | Summer | FALSE | summer
2024-08-09 03:00 | 2024-08-09 04:00 | Summer | FALSE | summer
2024-08-09 04:00 | 2024-08-09 05:00 | Summer | FALSE | summer
2024-08-09 05:00 | 2024-08-09 06:00 | Summer | FALSE | summer
2024-08-09 06:00 | 2024-08-09 07:00 | Summer | FALSE | summer
2024-08-09 07:00 | 2024-08-09 08:00 | Summer | FALSE | summer
2024-08-09 08:00 | 2024-08-09 09:00 | Summer | FALSE | summer
2024-08-09 09:00 | 2024-08-09 10:00 | Summer | FALSE | summer
2024-08-09 10:00 | 2024-08-09 11:00 | Summer | FALSE | summer
2024-08-09 11:00 | 2024-08-09 12:00 | Summer | FALSE | summer
2024-08-09 12:00 | 2024-08-09 13:00 | Summer | FALSE | summer
2024-08-09 13:00 | 2024-08-09 14:00 | Summer | FALSE | summer
2024-08-09 14:00 | 2024-08-09 15:00 | Summer | FALSE | summer
2024-08-09 15:00 | 2024-08-09 16:00 | Summer | FALSE | summer
2024-08-09 16:00 | 2024-08-09 17:00 | Summer | TRUE | summer
2024-08-09 17:00 | 2024-08-09 18:00 | Summer | TRUE | summer
2024-08-09 18:00 | 2024-08-09 19:00 | Summer | TRUE | summer
2024-08-09 19:00 | 2024-08-09 20:00 | Summer | TRUE | summer
2024-08-09 20:00 | 2024-08-09 21:00 | Summer | TRUE | summer
2024-08-09 21:00 | 2024-08-09 22:00 | Summer | FALSE | summer
2024-08-09 22:00 | 2024-08-09 23:00 | Summer | FALSE | summer
2024-08-09 23:00 | 2024-08-10 | Summer | FALSE | summer
2024-08-10 | 2024-08-10 01:00 | Summer | FALSE | summer
2024-08-10 01:00 | 2024-08-10 02:00 | Summer | FALSE | summer
2024-08-10 02:00 | 2024-08-10 03:00 | Summer | FALSE | summer
2024-08-10 03:00 | 2024-08-10 04:00 | Summer | FALSE | summer
2024-08-10 04:00 | 2024-08-10 05:00 | Summer | FALSE | summer
2024-08-10 05:00 | 2024-08-10 06:00 | Summer | FALSE | summer
2024-08-10 06:00 | 2024-08-10 07:00 | Summer | FALSE | summer
2024-08-10 07:00 | 2024-08-10 08:00 | Summer | FALSE | summer
2024-08-10 08:00 | 2024-08-10 09:00 | Summer | FALSE | summer
2024-08-10 09:00 | 2024-08-10 10:00 | Summer | FALSE | summer
2024-08-10 10:00 | 2024-08-10 11:00 | Summer | FALSE | summer
2024-08-10 11:00 | 2024-08-10 12:00 | Summer | FALSE | summer
2024-08-10 12:00 | 2024-08-10 13:00 | Summer | FALSE | summer
2024-08-10 13:00 | 2024-08-10 14:00 | Summer | FALSE | summer
2024-08-10 14:00 | 2024-08-10 15:00 | Summer | FALSE | summer
2024-08-10 15:00 | 2024-08-10 16:00 | Summer | FALSE | summer
2024-08-10 16:00 | 2024-08-10 17:00 | Summer | TRUE | summer
2024-08-10 17:00 | 2024-08-10 18:00 | Summer | TRUE | summer
2024-08-10 18:00 | 2024-08-10 19:00 | Summer | TRUE | summer
2024-08-10 19:00 | 2024-08-10 20:00 | Summer | TRUE | summer
2024-08-10 20:00 | 2024-08-10 21:00 | Summer | TRUE | summer
2024-08-10 21:00 | 2024-08-10 22:00 | Summer | FALSE | summer
2024-08-10 22:00 | 2024-08-10 23:00 | Summer | FALSE | summer
2024-08-10 23:00 | 2024-08-11 | Summer | FALSE | summer
2024-08-11 | 2024-08-11 01:00 | Summer | FALSE | summer
2024-08-11 01:00 | 2024-08-11 02:00 | Summer | FALSE | summer
2024-08-11 02:00 | 2024-08-11 03:00 | Summer | FALSE | summer
2024-08-11 03:00 | 2024-08-11 04:00 | Summer | FALSE | summer
2024-08-11 04:00 | 2024-08-11 05:00 | Summer | FALSE | summer
2024-08-11 05:00 | 2024-08-11 06:00 | Summer | FALSE | summer
2024-08-11 06:00 | 2024-08-11 07:00 | Summer | FALSE | summer
2024-08-11 07:00 | 2024-08-11 08:00 | Summer | FALSE | summer
2024-08-11 08:00 | 2024-08-11 09:00 | Summer | FALSE | summer
2024-08-11 09:00 | 2024-08-11 10:00 | Summer | FALSE | summer
2024-08-11 10:00 | 2024-08-11 11:00 | Summer | FALSE | summer
2024-08-11 11:00 | 2024-08-11 12:00 | Summer | FALSE | summer
2024-08-11 12:00 | 2024-08-11 13:00 | Summer | FALSE | summer
2024-08-11 13:00 | 2024-08-11 14:00 | Summer | FALSE | summer
2024-08-11 14:00 | 2024-08-11 15:00 | Summer | FALSE | summer
2024-08-11 15:00 | 2024-08-11 16:00 | Summer | FALSE | summer
2024-08-11 16:00 | 2024-08-11 17:00 | Summer | TRUE | summer
2024-08-11 17:00 | 2024-08-11 18:00 | Summer | TRUE | summer
2024-08-11 18:00 | 2024-08-11 19:00 | Summer | TRUE | summer
2024-08-11 19:00 | 2024-08-11 20:00 | Summer | TRUE | summer
2024-08-11 20:00 | 2024-08-11 21:00 | Summer | TRUE | summer
2024-08-11 21:00 | 2024-08-11 22:00 | Summer | FALSE | summer
2024-08-11 22:00 | 2024-08-11 23:00 | Summer | FALSE | summer
2024-08-11 23:00 | 2024-08-12 | Summer | FALSE | summer
2024-08-12 | 2024-08-12 01:00 | Summer | FALSE | summer
2024-08-12 01:00 | 2024-08-12 02:00 | Summer | FALSE | summer
2024-08-12 02:00 | 2024-08-12 03:00 | Summer | FALSE | summer
2024-08-12 03:00 | 2024-08-12 04:00 | Summer | FALSE | summer
2024-08-12 04:00 | 2024-08-12 05:00 | Summer | FALSE | summer
2024-08-12 05:00 | 2024-08-12 06:00 | Summer | FALSE | summer
2024-08-12 06:00 | 2024-08-12 07:00 | Summer | FALSE | summer
2024-08-12 07:00 | 2024-08-12 08:00 | Summer | FALSE | summer
2024-08-12 08:00 | 2024-08-12 09:00 | Summer | FALSE | summer
2024-08-12 09:00 | 2024-08-12 10:00 | Summer | FALSE | summer
2024-08-12 10:00 | 2024-08-12 11:00 | Summer | FALSE | summer
2024-08-12 11:00 | 2024-08-12 12:00 | Summer | FALSE | summer
2024-08-12 12:00 | 2024-08-12 13:00 | Summer | FALSE | summer
2024-08-12 13:00 | 2024-08-12 14:00 | Summer | FALSE | summer
2024-08-12 14:00 | 2024-08-12 15:00 | Summer | FALSE | summer
2024-08-12 15:00 | 2024-08-12 16:00 | Summer | FALSE | summer
2024-08-12 16:00 | 2024-08-12 17:00 | Summer | TRUE | summer
2024-08-12 17:00 | 2024-08-12 18:00 | Summer | TRUE | summer
2024-08-12 18:00 | 2024-08-12 19:00 | Summer | TRUE | summer
2024-08-12 19:00 | 2024-08-12 20:00 | Summer | TRUE | summer
2024-08-12 20:00 | 2024-08-12 21:00 | Summer | TRUE | summer
2024-08-12 21:00 | 2024-08-12 22:00 | Summer | FALSE | summer
2024-08-12 22:00 | 2024-08-12 23:00 | Summer | FALSE | summer
2024-08-12 23:00 | 2024-08-13 | Summer | FALSE | summer
2024-08-13 | 2024-08-13 01:00 | Summer | FALSE | summer
2024-08-13 01:00 | 2024-08-13 02:00 | Summer | FALSE | summer
2024-08-13 02:00 | 2024-08-13 03:00 | Summer | FALSE | summer
2024-08-13 03:00 | 2024-08-13 04:00 | Summer | FALSE | summer
2024-08-13 04:00 | 2024-08-13 05:00 | Summer | FALSE | summer
2024-08-13 05:00 | 2024-08-13 06:00 | Summer | FALSE | summer
2024-08-13 06:00 | 2024-08-13 07:00 | Summer | FALSE | summer
2024-08-13 07:00 | 2024-08-13 08:00 | Summer | FALSE | summer
2024-08-13 08:00 | 2024-08-13 09:00 | Summer | FALSE | summer
2024-08-13 09:00 | 2024-08-13 10:00 | Summer | FALSE | summer
2024-08-13 10:00 | 2024-08-13 11:00 | Summer | FALSE | summer
2024-08-13 11:00 | 2024-08-13 12:00 | Summer | FALSE | summer
2024-08-13 12:00 | 2024-08-13 13:00 | Summer | FALSE | summer
2024-08-13 13:00 | 2024-08-13 14:00 | Summer | FALSE | summer
2024-08-13 14:00 | 2024-08-13 15:00 | Summer | FALSE | summer
2024-08-13 15:00 | 2024-08-13 16:00 | Summer | FALSE | summer
2024-08-13 16:00 | 2024-08-13 17:00 | Summer | TRUE | summer
2024-08-13 17:00 | 2024-08-13 18:00 | Summer | TRUE | summer
2024-08-13 18:00 | 2024-08-13 19:00 | Summer | TRUE | summer
2024-08-13 19:00 | 2024-08-13 20:00 | Summer | TRUE | summer
2024-08-13 20:00 | 2024-08-13 21:00 | Summer | TRUE | summer
2024-08-13 21:00 | 2024-08-13 22:00 | Summer | FALSE | summer
2024-08-13 22:00 | 2024-08-13 23:00 | Summer | FALSE | summer
2024-08-13 23:00 | 2024-08-14 | Summer | FALSE | summer
2024-08-14 | 2024-08-14 01:00 | Summer | FALSE | summer
2024-08-14 01:00 | 2024-08-14 02:00 | Summer | FALSE | summer
2024-08-14 02:00 | 2024-08-14 03:00 | Summer | FALSE | summer
2024-08-14 03:00 | 2024-08-14 04:00 | Summer | FALSE | summer
2024-08-14 04:00 | 2024-08-14 05:00 | Summer | FALSE | summer
2024-08-14 05:00 | 2024-08-14 06:00 | Summer | FALSE | summer
2024-08-14 06:00 | 2024-08-14 07:00 | Summer | FALSE | summer
2024-08-14 07:00 | 2024-08-14 08:00 | Summer | FALSE | summer
2024-08-14 08:00 | 2024-08-14 09:00 | Summer | FALSE | summer
2024-08-14 09:00 | 2024-08-14 10:00 | Summer | FALSE | summer
2024-08-14 10:00 | 2024-08-14 11:00 | Summer | FALSE | summer
2024-08-14 11:00 | 2024-08-14 12:00 | Summer | FALSE | summer
2024-08-14 12:00 | 2024-08-14 13:00 | Summer | FALSE | summer
2024-08-14 13:00 | 2024-08-14 14:00 | Summer | FALSE | summer
2024-08-14 14:00 | 2024-08-14 15:00 | Summer | FALSE | summer
2024-08-14 15:00 | 2024-08-14 16:00 | Summer | FALSE | summer
2024-08-14 16:00 | 2024-08-14 17:00 | Summer | TRUE | summer
2024-08-14 17:00 | 2024-08-14 18:00 | Summer | TRUE | summer
2024-08-14 18:00 | 2024-08-14 19:00 | Summer | TRUE | summer
2024-08-14 19:00 | 2024-08-14 20:00 | Summer | TRUE | summer
2024-08-14 20:00 | 2024-08-14 21:00 | Summer | TRUE | summer
2024-08-14 21:00 | 2024-08-14 22:00 | Summer | FALSE | summer
2024-08-14 22:00 | 2024-08-14 23:00 | Summer | FALSE | summer
2024-08-14 23:00 | 2024-08-15 | Summer | FALSE | summer
2024-08-15 | 2024-08-15 01:00 | Summer | FALSE | summer
2024-08-15 01:00 | 2024-08-15 02:00 | Summer | FALSE | summer
2024-08-15 02:00 | 2024-08-15 03:00 | Summer | FALSE | summer
2024-08-15 03:00 | 2024-08-15 04:00 | Summer | FALSE | summer
2024-08-15 04:00 | 2024-08-15 05:00 | Summer | FALSE | summer
2024-08-15 05:00 | 2024-08-15 06:00 | Summer | FALSE | summer
2024-08-15 06:00 | 2024-08-15 07:00 | Summer | FALSE | summer
2024-08-15 07:00 | 2024-08-15 08:00 | Summer | FALSE | summer
2024-08-15 08:00 | 2024-08-15 09:00 | Summer | FALSE | summer
2024-08-15 09:00 | 2024-08-15 10:00 | Summer | FALSE | summer
2024-08-15 10:00 | 2024-08-15 11:00 | Summer | FALSE | summer
2024-08-15 11:00 | 2024-08-15 12:00 | Summer | FALSE | summer
2024-08-15 12:00 | 2024-08-15 13:00 | Summer | FALSE | summer
2024-08-15 13:00 | 2024-08-15 14:00 | Summer | FALSE | summer
2024-08-15 14:00 | 2024-08-15 15:00 | Summer | FALSE | summer
2024-08-15 15:00 | 2024-08-15 16:00 | Summer | FALSE | summer
2024-08-15 16:00 | 2024-08-15 17:00 | Summer | TRUE | summer
2024-08-15 17:00 | 2024-08-15 18:00 | Summer | TRUE | summer
2024-08-15 18:00 | 2024-08-15 19:00 | Summer | TRUE | summer
2024-08-15 19:00 | 2024-08-15 20:00 | Summer | TRUE | summer
2024-08-15 20:00 | 2024-08-15 21:00 | Summer | TRUE | summer
2024-08-15 21:00 | 2024-08-15 22:00 | Summer | FALSE | summer
2024-08-15 22:00 | 2024-08-15 23:00 | Summer | FALSE | summer
2024-08-15 23:00 | 2024-08-16 | Summer | FALSE | summer
2024-08-16 | 2024-08-16 01:00 | Summer | FALSE | summer
2024-08-16 01:00 | 2024-08-16 02:00 | Summer | FALSE | summer
2024-08-16 02:00 | 2024-08-16 03:00 | Summer | FALSE | summer
2024-08-16 03:00 | 2024-08-16 04:00 | Summer | FALSE | summer
2024-08-16 04:00 | 2024-08-16 05:00 | Summer | FALSE | summer
2024-08-16 05:00 | 2024-08-16 06:00 | Summer | FALSE | summer
2024-08-16 06:00 | 2024-08-16 07:00 | Summer | FALSE | summer
2024-08-16 07:00 | 2024-08-16 08:00 | Summer | FALSE | summer
2024-08-16 08:00 | 2024-08-16 09:00 | Summer | FALSE | summer
2024-08-16 09:00 | 2024-08-16 10:00 | Summer | FALSE | summer
2024-08-16 10:00 | 2024-08-16 11:00 | Summer | FALSE | summer
2024-08-16 11:00 | 2024-08-16 12:00 | Summer | FALSE | summer
2024-08-16 12:00 | 2024-08-16 13:00 | Summer | FALSE | summer
2024-08-16 13:00 | 2024-08-16 14:00 | Summer | FALSE | summer
2024-08-16 14:00 | 2024-08-16 15:00 | Summer | FALSE | summer
2024-08-16 15:00 | 2024-08-16 16:00 | Summer | FALSE | summer
2024-08-16 16:00 | 2024-08-16 17:00 | Summer | TRUE | summer
2024-08-16 17:00 | 2024-08-16 18:00 | Summer | TRUE | summer
2024-08-16 18:00 | 2024-08-16 19:00 | Summer | TRUE | summer
2024-08-16 19:00 | 2024-08-16 20:00 | Summer | TRUE | summer
2024-08-16 20:00 | 2024-08-16 21:00 | Summer | TRUE | summer
2024-08-16 21:00 | 2024-08-16 22:00 | Summer | FALSE | summer
2024-08-16 22:00 | 2024-08-16 23:00 | Summer | FALSE | summer
2024-08-16 23:00 | 2024-08-17 | Summer | FALSE | summer
2024-08-17 | 2024-08-17 01:00 | Summer | FALSE | summer
2024-08-17 01:00 | 2024-08-17 02:00 | Summer | FALSE | summer
2024-08-17 02:00 | 2024-08-17 03:00 | Summer | FALSE | summer
2024-08-17 03:00 | 2024-08-17 04:00 | Summer | FALSE | summer
2024-08-17 04:00 | 2024-08-17 05:00 | Summer | FALSE | summer
2024-08-17 05:00 | 2024-08-17 06:00 | Summer | FALSE | summer
2024-08-17 06:00 | 2024-08-17 07:00 | Summer | FALSE | summer
2024-08-17 07:00 | 2024-08-17 08:00 | Summer | FALSE | summer
2024-08-17 08:00 | 2024-08-17 09:00 | Summer | FALSE | summer
2024-08-17 09:00 | 2024-08-17 10:00 | Summer | FALSE | summer
2024-08-17 10:00 | 2024-08-17 11:00 | Summer | FALSE | summer
2024-08-17 11:00 | 2024-08-17 12:00 | Summer | FALSE | summer
2024-08-17 12:00 | 2024-08-17 13:00 | Summer | FALSE | summer
2024-08-17 13:00 | 2024-08-17 14:00 | Summer | FALSE | summer
2024-08-17 14:00 | 2024-08-17 15:00 | Summer | FALSE | summer
2024-08-17 15:00 | 2024-08-17 16:00 | Summer | FALSE | summer
2024-08-17 16:00 | 2024-08-17 17:00 | Summer | TRUE | summer
2024-08-17 17:00 | 2024-08-17 18:00 | Summer | TRUE | summer
2024-08-17 18:00 | 2024-08-17 19:00 | Summer | TRUE | summer
2024-08-17 19:00 | 2024-08-17 20:00 | Summer | TRUE | summer
2024-08-17 20:00 | 2024-08-17 21:00 | Summer | TRUE | summer
2024-08-17 21:00 | 2024-08-17 22:00 | Summer | FALSE | summer
2024-08-17 22:00 | 2024-08-17 23:00 | Summer | FALSE | summer
2024-08-17 23:00 | 2024-08-18 | Summer | FALSE | summer
2024-08-18 | 2024-08-18 01:00 | Summer | FALSE | summer
2024-08-18 01:00 | 2024-08-18 02:00 | Summer | FALSE | summer
2024-08-18 02:00 | 2024-08-18 03:00 | Summer | FALSE | summer
2024-08-18 03:00 | 2024-08-18 04:00 | Summer | FALSE | summer
2024-08-18 04:00 | 2024-08-18 05:00 | Summer | FALSE | summer
2024-08-18 05:00 | 2024-08-18 06:00 | Summer | FALSE | summer
2024-08-18 06:00 | 2024-08-18 07:00 | Summer | FALSE | summer
2024-08-18 07:00 | 2024-08-18 08:00 | Summer | FALSE | summer
2024-08-18 08:00 | 2024-08-18 09:00 | Summer | FALSE | summer
2024-08-18 09:00 | 2024-08-18 10:00 | Summer | FALSE | summer
2024-08-18 10:00 | 2024-08-18 11:00 | Summer | FALSE | summer
2024-08-18 11:00 | 2024-08-18 12:00 | Summer | FALSE | summer
2024-08-18 12:00 | 2024-08-18 13:00 | Summer | FALSE | summer
2024-08-18 13:00 | 2024-08-18 14:00 | Summer | FALSE | summer
2024-08-18 14:00 | 2024-08-18 15:00 | Summer | FALSE | summer
2024-08-18 15:00 | 2024-08-18 16:00 | Summer | FALSE | summer
2024-08-18 16:00 | 2024-08-18 17:00 | Summer | TRUE | summer
2024-08-18 17:00 | 2024-08-18 18:00 | Summer | TRUE | summer
2024-08-18 18:00 | 2024-08-18 19:00 | Summer | TRUE | summer
2024-08-18 19:00 | 2024-08-18 20:00 | Summer | TRUE | summer
2024-08-18 20:00 | 2024-08-18 21:00 | Summer | TRUE | summer
2024-08-18 21:00 | 2024-08-18 22:00 | Summer | FALSE | summer
2024-08-18 22:00 | 2024-08-18 23:00 | Summer | FALSE | summer
2024-08-18 23:00 | 2024-08-19 | Summer | FALSE | summer
2024-08-19 | 2024-08-19 01:00 | Summer | FALSE | summer
2024-08-19 01:00 | 2024-08-19 02:00 | Summer | FALSE | summer
2024-08-19 02:00 | 2024-08-19 03:00 | Summer | FALSE | summer
2024-08-19 03:00 | 2024-08-19 04:00 | Summer | FALSE | summer
2024-08-19 04:00 | 2024-08-19 05:00 | Summer | FALSE | summer
2024-08-19 05:00 | 2024-08-19 06:00 | Summer | FALSE | summer
2024-08-19 06:00 | 2024-08-19 07:00 | Summer | FALSE | summer
2024-08-19 07:00 | 2024-08-19 08:00 | Summer | FALSE | summer
2024-08-19 08:00 | 2024-08-19 09:00 | Summer | FALSE | summer
2024-08-19 09:00 | 2024-08-19 10:00 | Summer | FALSE | summer
2024-08-19 10:00 | 2024-08-19 11:00 | Summer | FALSE | summer
2024-08-19 11:00 | 2024-08-19 12:00 | Summer | FALSE | summer
2024-08-19 12:00 | 2024-08-19 13:00 | Summer | FALSE | summer
2024-08-19 13:00 | 2024-08-19 14:00 | Summer | FALSE | summer
2024-08-19 14:00 | 2024-08-19 15:00 | Summer | FALSE | summer
2024-08-19 15:00 | 2024-08-19 16:00 | Summer | FALSE | summer
2024-08-19 16:00 | 2024-08-19 17:00 | Summer | TRUE | summer
2024-08-19 17:00 | 2024-08-19 18:00 | Summer | TRUE | summer
2024-08-19 18:00 | 2024-08-19 19:00 | Summer | TRUE | summer
2024-08-19 19:00 | 2024-08-19 20:00 | Summer | TRUE | summer
2024-08-19 20:00 | 2024-08-19 21:00 | Summer | TRUE | summer
2024-08-19 21:00 | 2024-08-19 22:00 | Summer | FALSE | summer
2024-08-19 22:00 | 2024-08-19 23:00 | Summer | FALSE | summer
2024-08-19 23:00 | 2024-08-20 | Summer | FALSE | summer
2024-08-20 | 2024-08-20 01:00 | Summer | FALSE | summer
2024-08-20 01:00 | 2024-08-20 02:00 | Summer | FALSE | summer
2024-08-20 02:00 | 2024-08-20 03:00 | Summer | FALSE | summer
2024-08-20 03:00 | 2024-08-20 04:00 | Summer | FALSE | summer
2024-08-20 04:00 | 2024-08-20 05:00 | Summer | FALSE | summer
2024-08-20 05:00 | 2024-08-20 06:00 | Summer | FALSE | summer
2024-08-20 06:00 | 2024-08-20 07:00 | Summer | FALSE | summer
2024-08-20 07:00 | 2024-08-20 08:00 | Summer | FALSE | summer
2024-08-20 08:00 | 2024-08-20 09:00 | Summer | FALSE | summer
2024-08-20 09:00 | 2024-08-20 10:00 | Summer | FALSE | summer
2024-08-20 10:00 | 2024-08-20 11:00 | Summer | FALSE | summer
2024-08-20 11:00 | 2024-08-20 12:00 | Summer | FALSE | summer
2024-08-20 12:00 | 2024-08-20 13:00 | Summer | FALSE | summer
2024-08-20 13:00 | 2024-08-20 14:00 | Summer | FALSE | summer
2024-08-20 14:00 | 2024-08-20 15:00 | Summer | FALSE | summer
2024-08-20 15:00 | 2024-08-20 16:00 | Summer | FALSE | summer
2024-08-20 16:00 | 2024-08-20 17:00 | Summer | TRUE | summer
2024-08-20 17:00 | 2024-08-20 18:00 | Summer | TRUE | summer
2024-08-20 18:00 | 2024-08-20 19:00 | Summer | TRUE | summer
2024-08-20 19:00 | 2024-08-20 20:00 | Summer | TRUE | summer
2024-08-20 20:00 | 2024-08-20 21:00 | Summer | TRUE | summer
2024-08-20 21:00 | 2024-08-20 22:00 | Summer | FALSE | summer
2024-08-20 22:00 | 2024-08-20 23:00 | Summer | FALSE | summer
2024-08-20 23:00 | 2024-08-21 | Summer | FALSE | summer
2024-08-21 | 2024-08-21 01:00 | Summer | FALSE | summer
2024-08-21 01:00 | 2024-08-21 02:00 | Summer | FALSE | summer
2024-08-21 02:00 | 2024-08-21 03:00 | Summer | FALSE | summer
2024-08-21 03:00 | 2024-08-21 04:00 | Summer | FALSE | summer
2024-08-21 04:00 | 2024-08-21 05:00 | Summer | FALSE | summer
2024-08-21 05:00 | 2024-08-21 06:00 | Summer | FALSE | summer
2024-08-21 06:00 | 2024-08-21 07:00 | Summer | FALSE | summer
2024-08-21 07:00 | 2024-08-21 08:00 | Summer | FALSE | summer
2024-08-21 08:00 | 2024-08-21 09:00 | Summer | FALSE | summer
2024-08-21 09:00 | 2024-08-21 10:00 | Summer | FALSE | summer
2024-08-21 10:00 | 2024-08-21 11:00 | Summer | FALSE | summer
2024-08-21 11:00 | 2024-08-21 12:00 | Summer | FALSE | summer
2024-08-21 12:00 | 2024-08-21 13:00 | Summer | FALSE | summer
2024-08-21 13:00 | 2024-08-21 14:00 | Summer | FALSE | summer
2024-08-21 14:00 | 2024-08-21 15:00 | Summer | FALSE | summer
2024-08-21 15:00 | 2024-08-21 16:00 | Summer | FALSE | summer
2024-08-21 16:00 | 2024-08-21 17:00 | Summer | TRUE | summer
2024-08-21 17:00 | 2024-08-21 18:00 | Summer | TRUE | summer
2024-08-21 18:00 | 2024-08-21 19:00 | Summer | TRUE | summer
2024-08-21 19:00 | 2024-08-21 20:00 | Summer | TRUE | summer
2024-08-21 20:00 | 2024-08-21 21:00 | Summer | TRUE | summer
2024-08-21 21:00 | 2024-08-21 22:00 | Summer | FALSE | summer
2024-08-21 22:00 | 2024-08-21 23:00 | Summer | FALSE | summer
2024-08-21 23:00 | 2024-08-22 | Summer | FALSE | summer
2024-08-22 | 2024-08-22 01:00 | Summer | FALSE | summer
2024-08-22 01:00 | 2024-08-22 02:00 | Summer | FALSE | summer
2024-08-22 02:00 | 2024-08-22 03:00 | Summer | FALSE | summer
2024-08-22 03:00 | 2024-08-22 04:00 | Summer | FALSE | summer
2024-08-22 04:00 | 2024-08-22 05:00 | Summer | FALSE | summer
2024-08-22 05:00 | 2024-08-22 06:00 | Summer | FALSE | summer
2024-08-22 06:00 | 2024-08-22 07:00 | Summer | FALSE | summer
2024-08-22 07:00 | 2024-08-22 08:00 | Summer | FALSE | summer
2024-08-22 08:00 | 2024-08-22 09:00 | Summer | FALSE | summer
2024-08-22 09:00 | 2024-08-22 10:00 | Summer | FALSE | summer
2024-08-22 10:00 | 2024-08-22 11:00 | Summer | FALSE | summer
2024-08-22 11:00 | 2024-08-22 12:00 | Summer | FALSE | summer
2024-08-22 12:00 | 2024-08-22 13:00 | Summer | FALSE | summer
2024-08-22 13:00 | 2024-08-22 14:00 | Summer | FALSE | summer
2024-08-22 14:00 | 2024-08-22 15:00 | Summer | FALSE | summer
2024-08-22 15:00 | 2024-08-22 16:00 | Summer | FALSE | summer
2024-08-22 16:00 | 2024-08-22 17:00 | Summer | TRUE | summer
2024-08-22 17:00 | 2024-08-22 18:00 | Summer | TRUE | summer
2024-08-22 18:00 | 2024-08-22 19:00 | Summer | TRUE | summer
2024-08-22 19:00 | 2024-08-22 20:00 | Summer | TRUE | summer
2024-08-22 20:00 | 2024-08-22 21:00 | Summer | TRUE | summer
2024-08-22 21:00 | 2024-08-22 22:00 | Summer | FALSE | summer
2024-08-22 22:00 | 2024-08-22 23:00 | Summer | FALSE | summer
2024-08-22 23:00 | 2024-08-23 | Summer | FALSE | summer
2024-08-23 | 2024-08-23 01:00 | Summer | FALSE | summer
2024-08-23 01:00 | 2024-08-23 02:00 | Summer | FALSE | summer
2024-08-23 02:00 | 2024-08-23 03:00 | Summer | FALSE | summer
2024-08-23 03:00 | 2024-08-23 04:00 | Summer | FALSE | summer
2024-08-23 04:00 | 2024-08-23 05:00 | Summer | FALSE | summer
2024-08-23 05:00 | 2024-08-23 06:00 | Summer | FALSE | summer
2024-08-23 06:00 | 2024-08-23 07:00 | Summer | FALSE | summer
2024-08-23 07:00 | 2024-08-23 08:00 | Summer | FALSE | summer
2024-08-23 08:00 | 2024-08-23 09:00 | Summer | FALSE | summer
2024-08-23 09:00 | 2024-08-23 10:00 | Summer | FALSE | summer
2024-08-23 10:00 | 2024-08-23 11:00 | Summer | FALSE | summer
2024-08-23 11:00 | 2024-08-23 12:00 | Summer | FALSE | summer
2024-08-23 12:00 | 2024-08-23 13:00 | Summer | FALSE | summer
2024-08-23 13:00 | 2024-08-23 14:00 | Summer | FALSE | summer
2024-08-23 14:00 | 2024-08-23 15:00 | Summer | FALSE | summer
2024-08-23 15:00 | 2024-08-23 16:00 | Summer | FALSE | summer
2024-08-23 16:00 | 2024-08-23 17:00 | Summer | TRUE | summer
2024-08-23 17:00 | 2024-08-23 18:00 | Summer | TRUE | summer
2024-08-23 18:00 | 2024-08-23 19:00 | Summer | TRUE | summer
2024-08-23 19:00 | 2024-08-23 20:00 | Summer | TRUE | summer
2024-08-23 20:00 | 2024-08-23 21:00 | Summer | TRUE | summer
2024-08-23 21:00 | 2024-08-23 22:00 | Summer | FALSE | summer
2024-08-23 22:00 | 2024-08-23 23:00 | Summer | FALSE | summer
2024-08-23 23:00 | 2024-08-24 | Summer | FALSE | summer
2024-08-24 | 2024-08-24 01:00 | Summer | FALSE | summer
2024-08-24 01:00 | 2024-08-24 02:00 | Summer | FALSE | summer
2024-08-24 02:00 | 2024-08-24 03:00 | Summer | FALSE | summer
2024-08-24 03:00 | 2024-08-24 04:00 | Summer | FALSE | summer
2024-08-24 04:00 | 2024-08-24 05:00 | Summer | FALSE | summer
2024-08-24 05:00 | 2024-08-24 06:00 | Summer | FALSE | summer
2024-08-24 06:00 | 2024-08-24 07:00 | Summer | FALSE | summer
2024-08-24 07:00 | 2024-08-24 08:00 | Summer | FALSE | summer
2024-08-24 08:00 | 2024-08-24 09:00 | Summer | FALSE | summer
2024-08-24 09:00 | 2024-08-24 10:00 | Summer | FALSE | summer
2024-08-24 10:00 | 2024-08-24 11:00 | Summer | FALSE | summer
2024-08-24 11:00 | 2024-08-24 12:00 | Summer | FALSE | summer
2024-08-24 12:00 | 2024-08-24 13:00 | Summer | FALSE | summer
2024-08-24 13:00 | 2024-08-24 14:00 | Summer | FALSE | summer
2024-08-24 14:00 | 2024-08-24 15:00 | Summer | FALSE | summer
2024-08-24 15:00 | 2024-08-24 16:00 | Summer | FALSE | summer
2024-08-24 16:00 | 2024-08-24 17:00 | Summer | TRUE | summer
2024-08-24 17:00 | 2024-08-24 18:00 | Summer | TRUE | summer
2024-08-24 18:00 | 2024-08-24 19:00 | Summer | TRUE | summer
2024-08-24 19:00 | 2024-08-24 20:00 | Summer | TRUE | summer
2024-08-24 20:00 | 2024-08-24 21:00 | Summer | TRUE | summer
2024-08-24 21:00 | 2024-08-24 22:00 | Summer | FALSE | summer
2024-08-24 22:00 | 2024-08-24 23:00 | Summer | FALSE | summer
2024-08-24 23:00 | 2024-08-25 | Summer | FALSE | summer
2024-08-25 | 2024-08-25 01:00 | Summer | FALSE | summer
2024-08-25 01:00 | 2024-08-25 02:00 | Summer | FALSE | summer
2024-08-25 02:00 | 2024-08-25 03:00 | Summer | FALSE | summer
2024-08-25 03:00 | 2024-08-25 04:00 | Summer | FALSE | summer
2024-08-25 04:00 | 2024-08-25 05:00 | Summer | FALSE | summer
2024-08-25 05:00 | 2024-08-25 06:00 | Summer | FALSE | summer
2024-08-25 06:00 | 2024-08-25 07:00 | Summer | FALSE | summer
2024-08-25 07:00 | 2024-08-25 08:00 | Summer | FALSE | summer
2024-08-25 08:00 | 2024-08-25 09:00 | Summer | FALSE | summer
2024-08-25 09:00 | 2024-08-25 10:00 | Summer | FALSE | summer
2024-08-25 10:00 | 2024-08-25 11:00 | Summer | FALSE | summer
2024-08-25 11:00 | 2024-08-25 12:00 | Summer | FALSE | summer
2024-08-25 12:00 | 2024-08-25 13:00 | Summer | FALSE | summer
2024-08-25 13:00 | 2024-08-25 14:00 | Summer | FALSE | summer
2024-08-25 14:00 | 2024-08-25 15:00 | Summer | FALSE | summer
2024-08-25 15:00 | 2024-08-25 16:00 | Summer | FALSE | summer
2024-08-25 16:00 | 2024-08-25 17:00 | Summer | TRUE | summer
2024-08-25 17:00 | 2024-08-25 18:00 | Summer | TRUE | summer
2024-08-25 18:00 | 2024-08-25 19:00 | Summer | TRUE | summer
2024-08-25 19:00 | 2024-08-25 20:00 | Summer | TRUE | summer
2024-08-25 20:00 | 2024-08-25 21:00 | Summer | TRUE | summer
2024-08-25 21:00 | 2024-08-25 22:00 | Summer | FALSE | summer
2024-08-25 22:00 | 2024-08-25 23:00 | Summer | FALSE | summer
2024-08-25 23:00 | 2024-08-26 | Summer | FALSE | summer
2024-08-26 | 2024-08-26 01:00 | Summer | FALSE | summer
2024-08-26 01:00 | 2024-08-26 02:00 | Summer | FALSE | summer
2024-08-26 02:00 | 2024-08-26 03:00 | Summer | FALSE | summer
2024-08-26 03:00 | 2024-08-26 04:00 | Summer | FALSE | summer
2024-08-26 04:00 | 2024-08-26 05:00 | Summer | FALSE | summer
2024-08-26 05:00 | 2024-08-26 06:00 | Summer | FALSE | summer
2024-08-26 06:00 | 2024-08-26 07:00 | Summer | FALSE | summer
2024-08-26 07:00 | 2024-08-26 08:00 | Summer | FALSE | summer
2024-08-26 08:00 | 2024-08-26 09:00 | Summer | FALSE | summer
2024-08-26 09:00 | 2024-08-26 10:00 | Summer | FALSE | summer
2024-08-26 10:00 | 2024-08-26 11:00 | Summer | FALSE | summer
2024-08-26 11:00 | 2024-08-26 12:00 | Summer | FALSE | summer
2024-08-26 12:00 | 2024-08-26 13:00 | Summer | FALSE | summer
2024-08-26 13:00 | 2024-08-26 14:00 | Summer | FALSE | summer
2024-08-26 14:00 | 2024-08-26 15:00 | Summer | FALSE | summer
2024-08-26 15:00 | 2024-08-26 16:00 | Summer | FALSE | summer
2024-08-26 16:00 | 2024-08-26 17:00 | Summer | TRUE | summer
2024-08-26 17:00 | 2024-08-26 18:00 | Summer | TRUE | summer
2024-08-26 18:00 | 2024-08-26 19:00 | Summer | TRUE | summer
2024-08-26 19:00 | 2024-08-26 20:00 | Summer | TRUE | summer
2024-08-26 20:00 | 2024-08-26 21:00 | Summer | TRUE | summer
2024-08-26 21:00 | 2024-08-26 22:00 | Summer | FALSE | summer
2024-08-26 22:00 | 2024-08-26 23:00 | Summer | FALSE | summer
2024-08-26 23:00 | 2024-08-27 | Summer | FALSE | summer
2024-08-27 | 2024-08-27 01:00 | Summer | FALSE | summer
2024-08-27 01:00 | 2024-08-27 02:00 | Summer | FALSE | summer
2024-08-27 02:00 | 2024-08-27 03:00 | Summer | FALSE | summer
2024-08-27 03:00 | 2024-08-27 04:00 | Summer | FALSE | summer
2024-08-27 04:00 | 2024-08-27 05:00 | Summer | FALSE | summer
2024-08-27 05:00 | 2024-08-27 06:00 | Summer | FALSE | summer
2024-08-27 06:00 | 2024-08-27 07:00 | Summer | FALSE | summer
2024-08-27 07:00 | 2024-08-27 08:00 | Summer | FALSE | summer
2024-08-27 08:00 | 2024-08-27 09:00 | Summer | FALSE | summer
2024-08-27 09:00 | 2024-08-27 10:00 | Summer | FALSE | summer
2024-08-27 10:00 | 2024-08-27 11:00 | Summer | FALSE | summer
2024-08-27 11:00 | 2024-08-27 12:00 | Summer | FALSE | summer
2024-08-27 12:00 | 2024-08-27 13:00 | Summer | FALSE | summer
2024-08-27 13:00 | 2024-08-27 14:00 | Summer | FALSE | summer
2024-08-27 14:00 | 2024-08-27 15:00 | Summer | FALSE | summer
2024-08-27 15:00 | 2024-08-27 16:00 | Summer | FALSE | summer
2024-08-27 16:00 | 2024-08-27 17:00 | Summer | TRUE | summer
2024-08-27 17:00 | 2024-08-27 18:00 | Summer | TRUE | summer
2024-08-27 18:00 | 2024-08-27 19:00 | Summer | TRUE | summer
2024-08-27 19:00 | 2024-08-27 20:00 | Summer | TRUE | summer
2024-08-27 20:00 | 2024-08-27 21:00 | Summer | TRUE | summer
2024-08-27 21:00 | 2024-08-27 22:00 | Summer | FALSE | summer
2024-08-27 22:00 | 2024-08-27 23:00 | Summer | FALSE | summer
2024-08-27 23:00 | 2024-08-28 | Summer | FALSE | summer
2024-08-28 | 2024-08-28 01:00 | Summer | FALSE | summer
2024-08-28 01:00 | 2024-08-28 02:00 | Summer | FALSE | summer
2024-08-28 02:00 | 2024-08-28 03:00 | Summer | FALSE | summer
2024-08-28 03:00 | 2024-08-28 04:00 | Summer | FALSE | summer
2024-08-28 04:00 | 2024-08-28 05:00 | Summer | FALSE | summer
2024-08-28 05:00 | 2024-08-28 06:00 | Summer | FALSE | summer
2024-08-28 06:00 | 2024-08-28 07:00 | Summer | FALSE | summer
2024-08-28 07:00 | 2024-08-28 08:00 | Summer | FALSE | summer
2024-08-28 08:00 | 2024-08-28 09:00 | Summer | FALSE | summer
2024-08-28 09:00 | 2024-08-28 10:00 | Summer | FALSE | summer
2024-08-28 10:00 | 2024-08-28 11:00 | Summer | FALSE | summer
2024-08-28 11:00 | 2024-08-28 12:00 | Summer | FALSE | summer
2024-08-28 12:00 | 2024-08-28 13:00 | Summer | FALSE | summer
2024-08-28 13:00 | 2024-08-28 14:00 | Summer | FALSE | summer
2024-08-28 14:00 | 2024-08-28 15:00 | Summer | FALSE | summer
2024-08-28 15:00 | 2024-08-28 16:00 | Summer | FALSE | summer
2024-08-28 16:00 | 2024-08-28 17:00 | Summer | TRUE | summer
2024-08-28 17:00 | 2024-08-28 18:00 | Summer | TRUE | summer
2024-08-28 18:00 | 2024-08-28 19:00 | Summer | TRUE | summer
2024-08-28 19:00 | 2024-08-28 20:00 | Summer | TRUE | summer
2024-08-28 20:00 | 2024-08-28 21:00 | Summer | TRUE | summer
2024-08-28 21:00 | 2024-08-28 22:00 | Summer | FALSE | summer
2024-08-28 22:00 | 2024-08-28 23:00 | Summer | FALSE | summer
2024-08-28 23:00 | 2024-08-29 | Summer | FALSE | summer
2024-08-29 | 2024-08-29 01:00 | Summer | FALSE | summer
2024-08-29 01:00 | 2024-08-29 02:00 | Summer | FALSE | summer
2024-08-29 02:00 | 2024-08-29 03:00 | Summer | FALSE | summer
2024-08-29 03:00 | 2024-08-29 04:00 | Summer | FALSE | summer
2024-08-29 04:00 | 2024-08-29 05:00 | Summer | FALSE | summer
2024-08-29 05:00 | 2024-08-29 06:00 | Summer | FALSE | summer
2024-08-29 06:00 | 2024-08-29 07:00 | Summer | FALSE | summer
2024-08-29 07:00 | 2024-08-29 08:00 | Summer | FALSE | summer
2024-08-29 08:00 | 2024-08-29 09:00 | Summer | FALSE | summer
2024-08-29 09:00 | 2024-08-29 10:00 | Summer | FALSE | summer
2024-08-29 10:00 | 2024-08-29 11:00 | Summer | FALSE | summer
2024-08-29 11:00 | 2024-08-29 12:00 | Summer | FALSE | summer
2024-08-29 12:00 | 2024-08-29 13:00 | Summer | FALSE | summer
2024-08-29 13:00 | 2024-08-29 14:00 | Summer | FALSE | summer
2024-08-29 14:00 | 2024-08-29 15:00 | Summer | FALSE | summer
2024-08-29 15:00 | 2024-08-29 16:00 | Summer | FALSE | summer
2024-08-29 16:00 | 2024-08-29 17:00 | Summer | TRUE | summer
2024-08-29 17:00 | 2024-08-29 18:00 | Summer | TRUE | summer
2024-08-29 18:00 | 2024-08-29 19:00 | Summer | TRUE | summer
2024-08-29 19:00 | 2024-08-29 20:00 | Summer | TRUE | summer
2024-08-29 20:00 | 2024-08-29 21:00 | Summer | TRUE | summer
2024-08-29 21:00 | 2024-08-29 22:00 | Summer | FALSE | summer
2024-08-29 22:00 | 2024-08-29 23:00 | Summer | FALSE | summer
2024-08-29 23:00 | 2024-08-30 | Summer | FALSE | summer
2024-08-30 | 2024-08-30 01:00 | Summer | FALSE | summer
2024-08-30 01:00 | 2024-08-30 02:00 | Summer | FALSE | summer
2024-08-30 02:00 | 2024-08-30 03:00 | Summer | FALSE | summer
2024-08-30 03:00 | 2024-08-30 04:00 | Summer | FALSE | summer
2024-08-30 04:00 | 2024-08-30 05:00 | Summer | FALSE | summer
2024-08-30 05:00 | 2024-08-30 06:00 | Summer | FALSE | summer
2024-08-30 06:00 | 2024-08-30 07:00 | Summer | FALSE | summer
2024-08-30 07:00 | 2024-08-30 08:00 | Summer | FALSE | summer
2024-08-30 08:00 | 2024-08-30 09:00 | Summer | FALSE | summer
2024-08-30 09:00 | 2024-08-30 10:00 | Summer | FALSE | summer
2024-08-30 10:00 | 2024-08-30 11:00 | Summer | FALSE | summer
2024-08-30 11:00 | 2024-08-30 12:00 | Summer | FALSE | summer
2024-08-30 12:00 | 2024-08-30 13:00 | Summer | FALSE | summer
2024-08-30 13:00 | 2024-08-30 14:00 | Summer | FALSE | summer
2024-08-30 14:00 | 2024-08-30 15:00 | Summer | FALSE | summer
2024-08-30 15:00 | 2024-08-30 16:00 | Summer | FALSE | summer
2024-08-30 16:00 | 2024-08-30 17:00 | Summer | TRUE | summer
2024-08-30 17:00 | 2024-08-30 18:00 | Summer | TRUE | summer
2024-08-30 18:00 | 2024-08-30 19:00 | Summer | TRUE | summer
2024-08-30 19:00 | 2024-08-30 20:00 | Summer | TRUE | summer
2024-08-30 20:00 | 2024-08-30 21:00 | Summer | TRUE | summer
2024-08-30 21:00 | 2024-08-30 22:00 | Summer | FALSE | summer
2024-08-30 22:00 | 2024-08-30 23:00 | Summer | FALSE | summer
2024-08-30 23:00 | 2024-08-31 | Summer | FALSE | summer
2024-08-31 | 2024-08-31 01:00 | Summer | FALSE | summer
2024-08-31 01:00 | 2024-08-31 02:00 | Summer | FALSE | summer
2024-08-31 02:00 | 2024-08-31 03:00 | Summer | FALSE | summer
2024-08-31 03:00 | 2024-08-31 04:00 | Summer | FALSE | summer
2024-08-31 04:00 | 2024-08-31 05:00 | Summer | FALSE | summer
2024-08-31 05:00 | 2024-08-31 06:00 | Summer | FALSE | summer
2024-08-31 06:00 | 2024-08-31 07:00 | Summer | FALSE | summer
2024-08-31 07:00 | 2024-08-31 08:00 | Summer | FALSE | summer
2024-08-31 08:00 | 2024-08-31 09:00 | Summer | FALSE | summer
2024-08-31 09:00 | 2024-08-31 10:00 | Summer | FALSE | summer
2024-08-31 10:00 | 2024-08-31 11:00 | Summer | FALSE | summer
2024-08-31 11:00 | 2024-08-31 12:00 | Summer | FALSE | summer
2024-08-31 12:00 | 2024-08-31 13:00 | Summer | FALSE | summer
2024-08-31 13:00 | 2024-08-31 14:00 | Summer | FALSE | summer
2024-08-31 14:00 | 2024-08-31 15:00 | Summer | FALSE | summer
2024-08-31 15:00 | 2024-08-31 16:00 | Summer | FALSE | summer
2024-08-31 16:00 | 2024-08-31 17:00 | Summer | TRUE | summer
2024-08-31 17:00 | 2024-08-31 18:00 | Summer | TRUE | summer
2024-08-31 18:00 | 2024-08-31 19:00 | Summer | TRUE | summer
2024-08-31 19:00 | 2024-08-31 20:00 | Summer | TRUE | summer
2024-08-31 20:00 | 2024-08-31 21:00 | Summer | TRUE | summer
2024-08-31 21:00 | 2024-08-31 22:00 | Summer | FALSE | summer
2024-08-31 22:00 | 2024-08-31 23:00 | Summer | FALSE | summer
2024-08-31 23:00 | 2024-09-01 | Summer | FALSE | summer
2024-09-01 | 2024-09-01 01:00 | Summer | FALSE | summer
2024-09-01 01:00 | 2024-09-01 02:00 | Summer | FALSE | summer
2024-09-01 02:00 | 2024-09-01 03:00 | Summer | FALSE | summer
2024-09-01 03:00 | 2024-09-01 04:00 | Summer | FALSE | summer
2024-09-01 04:00 | 2024-09-01 05:00 | Summer | FALSE | summer
2024-09-01 05:00 | 2024-09-01 06:00 | Summer | FALSE | summer
2024-09-01 06:00 | 2024-09-01 07:00 | Summer | FALSE | summer
2024-09-01 07:00 | 2024-09-01 08:00 | Summer | FALSE | summer
2024-09-01 08:00 | 2024-09-01 09:00 | Summer | FALSE | summer
2024-09-01 09:00 | 2024-09-01 10:00 | Summer | FALSE | summer
2024-09-01 10:00 | 2024-09-01 11:00 | Summer | FALSE | summer
2024-09-01 11:00 | 2024-09-01 12:00 | Summer | FALSE | summer
2024-09-01 12:00 | 2024-09-01 13:00 | Summer | FALSE | summer
2024-09-01 13:00 | 2024-09-01 14:00 | Summer | FALSE | summer
2024-09-01 14:00 | 2024-09-01 15:00 | Summer | FALSE | summer
2024-09-01 15:00 | 2024-09-01 16:00 | Summer | FALSE | summer
2024-09-01 16:00 | 2024-09-01 17:00 | Summer | TRUE | summer
2024-09-01 17:00 | 2024-09-01 18:00 | Summer | TRUE | summer
2024-09-01 18:00 | 2024-09-01 19:00 | Summer | TRUE | summer
2024-09-01 19:00 | 2024-09-01 20:00 | Summer | TRUE | summer
2024-09-01 20:00 | 2024-09-01 21:00 | Summer | TRUE | summer
2024-09-01 21:00 | 2024-09-01 22:00 | Summer | FALSE | summer
2024-09-01 22:00 | 2024-09-01 23:00 | Summer | FALSE | summer
2024-09-01 23:00 | 2024-09-02 | Summer | FALSE | summer
2024-09-02 | 2024-09-02 01:00 | Summer | FALSE | summer
2024-09-02 01:00 | 2024-09-02 02:00 | Summer | FALSE | summer
2024-09-02 02:00 | 2024-09-02 03:00 | Summer | FALSE | summer
2024-09-02 03:00 | 2024-09-02 04:00 | Summer | FALSE | summer
2024-09-02 04:00 | 2024-09-02 05:00 | Summer | FALSE | summer
2024-09-02 05:00 | 2024-09-02 06:00 | Summer | FALSE | summer
2024-09-02 06:00 | 2024-09-02 07:00 | Summer | FALSE | summer
2024-09-02 07:00 | 2024-09-02 08:00 | Summer | FALSE | summer
2024-09-02 08:00 | 2024-09-02 09:00 | Summer | FALSE | summer
2024-09-02 09:00 | 2024-09-02 10:00 | Summer | FALSE | summer
2024-09-02 10:00 | 2024-09-02 11:00 | Summer | FALSE | summer
2024-09-02 11:00 | 2024-09-02 12:00 | Summer | FALSE | summer
2024-09-02 12:00 | 2024-09-02 13:00 | Summer | FALSE | summer
2024-09-02 13:00 | 2024-09-02 14:00 | Summer | FALSE | summer
2024-09-02 14:00 | 2024-09-02 15:00 | Summer | FALSE | summer
2024-09-02 15:00 | 2024-09-02 16:00 | Summer | FALSE | summer
2024-09-02 16:00 | 2024-09-02 17:00 | Summer | TRUE | summer
2024-09-02 17:00 | 2024-09-02 18:00 | Summer | TRUE | summer
2024-09-02 18:00 | 2024-09-02 19:00 | Summer | TRUE | summer
2024-09-02 19:00 | 2024-09-02 20:00 | Summer | TRUE | summer
2024-09-02 20:00 | 2024-09-02 21:00 | Summer | TRUE | summer
2024-09-02 21:00 | 2024-09-02 22:00 | Summer | FALSE | summer
2024-09-02 22:00 | 2024-09-02 23:00 | Summer | FALSE | summer
2024-09-02 23:00 | 2024-09-03 | Summer | FALSE | summer
2024-09-03 | 2024-09-03 01:00 | Summer | FALSE | summer
2024-09-03 01:00 | 2024-09-03 02:00 | Summer | FALSE | summer
2024-09-03 02:00 | 2024-09-03 03:00 | Summer | FALSE | summer
2024-09-03 03:00 | 2024-09-03 04:00 | Summer | FALSE | summer
2024-09-03 04:00 | 2024-09-03 05:00 | Summer | FALSE | summer
2024-09-03 05:00 | 2024-09-03 06:00 | Summer | FALSE | summer
2024-09-03 06:00 | 2024-09-03 07:00 | Summer | FALSE | summer
2024-09-03 07:00 | 2024-09-03 08:00 | Summer | FALSE | summer
2024-09-03 08:00 | 2024-09-03 09:00 | Summer | FALSE | summer
2024-09-03 09:00 | 2024-09-03 10:00 | Summer | FALSE | summer
2024-09-03 10:00 | 2024-09-03 11:00 | Summer | FALSE | summer
2024-09-03 11:00 | 2024-09-03 12:00 | Summer | FALSE | summer
2024-09-03 12:00 | 2024-09-03 13:00 | Summer | FALSE | summer
2024-09-03 13:00 | 2024-09-03 14:00 | Summer | FALSE | summer
2024-09-03 14:00 | 2024-09-03 15:00 | Summer | FALSE | summer
2024-09-03 15:00 | 2024-09-03 16:00 | Summer | FALSE | summer
2024-09-03 16:00 | 2024-09-03 17:00 | Summer | TRUE | summer
2024-09-03 17:00 | 2024-09-03 18:00 | Summer | TRUE | summer
2024-09-03 18:00 | 2024-09-03 19:00 | Summer | TRUE | summer
2024-09-03 19:00 | 2024-09-03 20:00 | Summer | TRUE | summer
2024-09-03 20:00 | 2024-09-03 21:00 | Summer | TRUE | summer
2024-09-03 21:00 | 2024-09-03 22:00 | Summer | FALSE | summer
2024-09-03 22:00 | 2024-09-03 23:00 | Summer | FALSE | summer
2024-09-03 23:00 | 2024-09-04 | Summer | FALSE | summer
2024-09-04 | 2024-09-04 01:00 | Summer | FALSE | summer
2024-09-04 01:00 | 2024-09-04 02:00 | Summer | FALSE | summer
2024-09-04 02:00 | 2024-09-04 03:00 | Summer | FALSE | summer
2024-09-04 03:00 | 2024-09-04 04:00 | Summer | FALSE | summer
2024-09-04 04:00 | 2024-09-04 05:00 | Summer | FALSE | summer
2024-09-04 05:00 | 2024-09-04 06:00 | Summer | FALSE | summer
2024-09-04 06:00 | 2024-09-04 07:00 | Summer | FALSE | summer
2024-09-04 07:00 | 2024-09-04 08:00 | Summer | FALSE | summer
2024-09-04 08:00 | 2024-09-04 09:00 | Summer | FALSE | summer
2024-09-04 09:00 | 2024-09-04 10:00 | Summer | FALSE | summer
2024-09-04 10:00 | 2024-09-04 11:00 | Summer | FALSE | summer
2024-09-04 11:00 | 2024-09-04 12:00 | Summer | FALSE | summer
2024-09-04 12:00 | 2024-09-04 13:00 | Summer | FALSE | summer
2024-09-04 13:00 | 2024-09-04 14:00 | Summer | FALSE | summer
2024-09-04 14:00 | 2024-09-04 15:00 | Summer | FALSE | summer
2024-09-04 15:00 | 2024-09-04 16:00 | Summer | FALSE | summer
2024-09-04 16:00 | 2024-09-04 17:00 | Summer | TRUE | summer
2024-09-04 17:00 | 2024-09-04 18:00 | Summer | TRUE | summer
2024-09-04 18:00 | 2024-09-04 19:00 | Summer | TRUE | summer
2024-09-04 19:00 | 2024-09-04 20:00 | Summer | TRUE | summer
2024-09-04 20:00 | 2024-09-04 21:00 | Summer | TRUE | summer
2024-09-04 21:00 | 2024-09-04 22:00 | Summer | FALSE | summer
2024-09-04 22:00 | 2024-09-04 23:00 | Summer | FALSE | summer
2024-09-04 23:00 | 2024-09-05 | Summer | FALSE | summer
2024-09-05 | 2024-09-05 01:00 | Summer | FALSE | summer
2024-09-05 01:00 | 2024-09-05 02:00 | Summer | FALSE | summer
2024-09-05 02:00 | 2024-09-05 03:00 | Summer | FALSE | summer
2024-09-05 03:00 | 2024-09-05 04:00 | Summer | FALSE | summer
2024-09-05 04:00 | 2024-09-05 05:00 | Summer | FALSE | summer
2024-09-05 05:00 | 2024-09-05 06:00 | Summer | FALSE | summer
2024-09-05 06:00 | 2024-09-05 07:00 | Summer | FALSE | summer
2024-09-05 07:00 | 2024-09-05 08:00 | Summer | FALSE | summer
2024-09-05 08:00 | 2024-09-05 09:00 | Summer | FALSE | summer
2024-09-05 09:00 | 2024-09-05 10:00 | Summer | FALSE | summer
2024-09-05 10:00 | 2024-09-05 11:00 | Summer | FALSE | summer
2024-09-05 11:00 | 2024-09-05 12:00 | Summer | FALSE | summer
2024-09-05 12:00 | 2024-09-05 13:00 | Summer | FALSE | summer
2024-09-05 13:00 | 2024-09-05 14:00 | Summer | FALSE | summer
2024-09-05 14:00 | 2024-09-05 15:00 | Summer | FALSE | summer
2024-09-05 15:00 | 2024-09-05 16:00 | Summer | FALSE | summer
2024-09-05 16:00 | 2024-09-05 17:00 | Summer | TRUE | summer
2024-09-05 17:00 | 2024-09-05 18:00 | Summer | TRUE | summer
2024-09-05 18:00 | 2024-09-05 19:00 | Summer | TRUE | summer
2024-09-05 19:00 | 2024-09-05 20:00 | Summer | TRUE | summer
2024-09-05 20:00 | 2024-09-05 21:00 | Summer | TRUE | summer
2024-09-05 21:00 | 2024-09-05 22:00 | Summer | FALSE | summer
2024-09-05 22:00 | 2024-09-05 23:00 | Summer | FALSE | summer
2024-09-05 23:00 | 2024-09-06 | Summer | FALSE | summer
2024-09-06 | 2024-09-06 01:00 | Summer | FALSE | summer
2024-09-06 01:00 | 2024-09-06 02:00 | Summer | FALSE | summer
2024-09-06 02:00 | 2024-09-06 03:00 | Summer | FALSE | summer
2024-09-06 03:00 | 2024-09-06 04:00 | Summer | FALSE | summer
2024-09-06 04:00 | 2024-09-06 05:00 | Summer | FALSE | summer
2024-09-06 05:00 | 2024-09-06 06:00 | Summer | FALSE | summer
2024-09-06 06:00 | 2024-09-06 07:00 | Summer | FALSE | summer
2024-09-06 07:00 | 2024-09-06 08:00 | Summer | FALSE | summer
2024-09-06 08:00 | 2024-09-06 09:00 | Summer | FALSE | summer
2024-09-06 09:00 | 2024-09-06 10:00 | Summer | FALSE | summer
2024-09-06 10:00 | 2024-09-06 11:00 | Summer | FALSE | summer
2024-09-06 11:00 | 2024-09-06 12:00 | Summer | FALSE | summer
2024-09-06 12:00 | 2024-09-06 13:00 | Summer | FALSE | summer
2024-09-06 13:00 | 2024-09-06 14:00 | Summer | FALSE | summer
2024-09-06 14:00 | 2024-09-06 15:00 | Summer | FALSE | summer
2024-09-06 15:00 | 2024-09-06 16:00 | Summer | FALSE | summer
2024-09-06 16:00 | 2024-09-06 17:00 | Summer | TRUE | summer
2024-09-06 17:00 | 2024-09-06 18:00 | Summer | TRUE | summer
2024-09-06 18:00 | 2024-09-06 19:00 | Summer | TRUE | summer
2024-09-06 19:00 | 2024-09-06 20:00 | Summer | TRUE | summer
2024-09-06 20:00 | 2024-09-06 21:00 | Summer | TRUE | summer
2024-09-06 21:00 | 2024-09-06 22:00 | Summer | FALSE | summer
2024-09-06 22:00 | 2024-09-06 23:00 | Summer | FALSE | summer
2024-09-06 23:00 | 2024-09-07 | Summer | FALSE | summer
2024-09-07 | 2024-09-07 01:00 | Summer | FALSE | summer
2024-09-07 01:00 | 2024-09-07 02:00 | Summer | FALSE | summer
2024-09-07 02:00 | 2024-09-07 03:00 | Summer | FALSE | summer
2024-09-07 03:00 | 2024-09-07 04:00 | Summer | FALSE | summer
2024-09-07 04:00 | 2024-09-07 05:00 | Summer | FALSE | summer
2024-09-07 05:00 | 2024-09-07 06:00 | Summer | FALSE | summer
2024-09-07 06:00 | 2024-09-07 07:00 | Summer | FALSE | summer
2024-09-07 07:00 | 2024-09-07 08:00 | Summer | FALSE | summer
2024-09-07 08:00 | 2024-09-07 09:00 | Summer | FALSE | summer
2024-09-07 09:00 | 2024-09-07 10:00 | Summer | FALSE | summer
2024-09-07 10:00 | 2024-09-07 11:00 | Summer | FALSE | summer
2024-09-07 11:00 | 2024-09-07 12:00 | Summer | FALSE | summer
2024-09-07 12:00 | 2024-09-07 13:00 | Summer | FALSE | summer
2024-09-07 13:00 | 2024-09-07 14:00 | Summer | FALSE | summer
2024-09-07 14:00 | 2024-09-07 15:00 | Summer | FALSE | summer
2024-09-07 15:00 | 2024-09-07 16:00 | Summer | FALSE | summer
2024-09-07 16:00 | 2024-09-07 17:00 | Summer | TRUE | summer
2024-09-07 17:00 | 2024-09-07 18:00 | Summer | TRUE | summer
2024-09-07 18:00 | 2024-09-07 19:00 | Summer | TRUE | summer
2024-09-07 19:00 | 2024-09-07 20:00 | Summer | TRUE | summer
2024-09-07 20:00 | 2024-09-07 21:00 | Summer | TRUE | summer
2024-09-07 21:00 | 2024-09-07 22:00 | Summer | FALSE | summer
2024-09-07 22:00 | 2024-09-07 23:00 | Summer | FALSE | summer
2024-09-07 23:00 | 2024-09-08 | Summer | FALSE | summer
2024-09-08 | 2024-09-08 01:00 | Summer | FALSE | summer
2024-09-08 01:00 | 2024-09-08 02:00 | Summer | FALSE | summer
2024-09-08 02:00 | 2024-09-08 03:00 | Summer | FALSE | summer
2024-09-08 03:00 | 2024-09-08 04:00 | Summer | FALSE | summer
2024-09-08 04:00 | 2024-09-08 05:00 | Summer | FALSE | summer
2024-09-08 05:00 | 2024-09-08 06:00 | Summer | FALSE | summer
2024-09-08 06:00 | 2024-09-08 07:00 | Summer | FALSE | summer
2024-09-08 07:00 | 2024-09-08 08:00 | Summer | FALSE | summer
2024-09-08 08:00 | 2024-09-08 09:00 | Summer | FALSE | summer
2024-09-08 09:00 | 2024-09-08 10:00 | Summer | FALSE | summer
2024-09-08 10:00 | 2024-09-08 11:00 | Summer | FALSE | summer
2024-09-08 11:00 | 2024-09-08 12:00 | Summer | FALSE | summer
2024-09-08 12:00 | 2024-09-08 13:00 | Summer | FALSE | summer
2024-09-08 13:00 | 2024-09-08 14:00 | Summer | FALSE | summer
2024-09-08 14:00 | 2024-09-08 15:00 | Summer | FALSE | summer
2024-09-08 15:00 | 2024-09-08 16:00 | Summer | FALSE | summer
2024-09-08 16:00 | 2024-09-08 17:00 | Summer | TRUE | summer
2024-09-08 17:00 | 2024-09-08 18:00 | Summer | TRUE | summer
2024-09-08 18:00 | 2024-09-08 19:00 | Summer | TRUE | summer
2024-09-08 19:00 | 2024-09-08 20:00 | Summer | TRUE | summer
2024-09-08 20:00 | 2024-09-08 21:00 | Summer | TRUE | summer
2024-09-08 21:00 | 2024-09-08 22:00 | Summer | FALSE | summer
2024-09-08 22:00 | 2024-09-08 23:00 | Summer | FALSE | summer
2024-09-08 23:00 | 2024-09-09 | Summer | FALSE | summer
2024-09-09 | 2024-09-09 01:00 | Summer | FALSE | summer
2024-09-09 01:00 | 2024-09-09 02:00 | Summer | FALSE | summer
2024-09-09 02:00 | 2024-09-09 03:00 | Summer | FALSE | summer
2024-09-09 03:00 | 2024-09-09 04:00 | Summer | FALSE | summer
2024-09-09 04:00 | 2024-09-09 05:00 | Summer | FALSE | summer
2024-09-09 05:00 | 2024-09-09 06:00 | Summer | FALSE | summer
2024-09-09 06:00 | 2024-09-09 07:00 | Summer | FALSE | summer
2024-09-09 07:00 | 2024-09-09 08:00 | Summer | FALSE | summer
2024-09-09 08:00 | 2024-09-09 09:00 | Summer | FALSE | summer
2024-09-09 09:00 | 2024-09-09 10:00 | Summer | FALSE | summer
2024-09-09 10:00 | 2024-09-09 11:00 | Summer | FALSE | summer
2024-09-09 11:00 | 2024-09-09 12:00 | Summer | FALSE | summer
2024-09-09 12:00 | 2024-09-09 13:00 | Summer | FALSE | summer
2024-09-09 13:00 | 2024-09-09 14:00 | Summer | FALSE | summer
2024-09-09 14:00 | 2024-09-09 15:00 | Summer | FALSE | summer
2024-09-09 15:00 | 2024-09-09 16:00 | Summer | FALSE | summer
2024-09-09 16:00 | 2024-09-09 17:00 | Summer | TRUE | summer
2024-09-09 17:00 | 2024-09-09 18:00 | Summer | TRUE | summer
2024-09-09 18:00 | 2024-09-09 19:00 | Summer | TRUE | summer
2024-09-09 19:00 | 2024-09-09 20:00 | Summer | TRUE | summer
2024-09-09 20:00 | 2024-09-09 21:00 | Summer | TRUE | summer
2024-09-09 21:00 | 2024-09-09 22:00 | Summer | FALSE | summer
2024-09-09 22:00 | 2024-09-09 23:00 | Summer | FALSE | summer
2024-09-09 23:00 | 2024-09-10 | Summer | FALSE | summer
2024-09-10 | 2024-09-10 01:00 | Summer | FALSE | summer
2024-09-10 01:00 | 2024-09-10 02:00 | Summer | FALSE | summer
2024-09-10 02:00 | 2024-09-10 03:00 | Summer | FALSE | summer
2024-09-10 03:00 | 2024-09-10 04:00 | Summer | FALSE | summer
2024-09-10 04:00 | 2024-09-10 05:00 | Summer | FALSE | summer
2024-09-10 05:00 | 2024-09-10 06:00 | Summer | FALSE | summer
2024-09-10 06:00 | 2024-09-10 07:00 | Summer | FALSE | summer
2024-09-10 07:00 | 2024-09-10 08:00 | Summer | FALSE | summer
2024-09-10 08:00 | 2024-09-10 09:00 | Summer | FALSE | summer
2024-09-10 09:00 | 2024-09-10 10:00 | Summer | FALSE | summer
2024-09-10 10:00 | 2024-09-10 11:00 | Summer | FALSE | summer
2024-09-10 11:00 | 2024-09-10 12:00 | Summer | FALSE | summer
2024-09-10 12:00 | 2024-09-10 13:00 | Summer | FALSE | summer
2024-09-10 13:00 | 2024-09-10 14:00 | Summer | FALSE | summer
2024-09-10 14:00 | 2024-09-10 15:00 | Summer | FALSE | summer
2024-09-10 15:00 | 2024-09-10 16:00 | Summer | FALSE | summer
2024-09-10 16:00 | 2024-09-10 17:00 | Summer | TRUE | summer
2024-09-10 17:00 | 2024-09-10 18:00 | Summer | TRUE | summer
2024-09-10 18:00 | 2024-09-10 19:00 | Summer | TRUE | summer
2024-09-10 19:00 | 2024-09-10 20:00 | Summer | TRUE | summer
2024-09-10 20:00 | 2024-09-10 21:00 | Summer | TRUE | summer
2024-09-10 21:00 | 2024-09-10 22:00 | Summer | FALSE | summer
2024-09-10 22:00 | 2024-09-10 23:00 | Summer | FALSE | summer
2024-09-10 23:00 | 2024-09-11 | Summer | FALSE | summer
2024-09-11 | 2024-09-11 01:00 | Summer | FALSE | summer
2024-09-11 01:00 | 2024-09-11 02:00 | Summer | FALSE | summer
2024-09-11 02:00 | 2024-09-11 03:00 | Summer | FALSE | summer
2024-09-11 03:00 | 2024-09-11 04:00 | Summer | FALSE | summer
2024-09-11 04:00 | 2024-09-11 05:00 | Summer | FALSE | summer
2024-09-11 05:00 | 2024-09-11 06:00 | Summer | FALSE | summer
2024-09-11 06:00 | 2024-09-11 07:00 | Summer | FALSE | summer
2024-09-11 07:00 | 2024-09-11 08:00 | Summer | FALSE | summer
2024-09-11 08:00 | 2024-09-11 09:00 | Summer | FALSE | summer
2024-09-11 09:00 | 2024-09-11 10:00 | Summer | FALSE | summer
2024-09-11 10:00 | 2024-09-11 11:00 | Summer | FALSE | summer
2024-09-11 11:00 | 2024-09-11 12:00 | Summer | FALSE | summer
2024-09-11 12:00 | 2024-09-11 13:00 | Summer | FALSE | summer
2024-09-11 13:00 | 2024-09-11 14:00 | Summer | FALSE | summer
2024-09-11 14:00 | 2024-09-11 15:00 | Summer | FALSE | summer
2024-09-11 15:00 | 2024-09-11 16:00 | Summer | FALSE | summer
2024-09-11 16:00 | 2024-09-11 17:00 | Summer | TRUE | summer
2024-09-11 17:00 | 2024-09-11 18:00 | Summer | TRUE | summer
2024-09-11 18:00 | 2024-09-11 19:00 | Summer | TRUE | summer
2024-09-11 19:00 | 2024-09-11 20:00 | Summer | TRUE | summer
2024-09-11 20:00 | 2024-09-11 21:00 | Summer | TRUE | summer
2024-09-11 21:00 | 2024-09-11 22:00 | Summer | FALSE | summer
2024-09-11 22:00 | 2024-09-11 23:00 | Summer | FALSE | summer
2024-09-11 23:00 | 2024-09-12 | Summer | FALSE | summer
2024-09-12 | 2024-09-12 01:00 | Summer | FALSE | summer
2024-09-12 01:00 | 2024-09-12 02:00 | Summer | FALSE | summer
2024-09-12 02:00 | 2024-09-12 03:00 | Summer | FALSE | summer
2024-09-12 03:00 | 2024-09-12 04:00 | Summer | FALSE | summer
2024-09-12 04:00 | 2024-09-12 05:00 | Summer | FALSE | summer
2024-09-12 05:00 | 2024-09-12 06:00 | Summer | FALSE | summer
2024-09-12 06:00 | 2024-09-12 07:00 | Summer | FALSE | summer
2024-09-12 07:00 | 2024-09-12 08:00 | Summer | FALSE | summer
2024-09-12 08:00 | 2024-09-12 09:00 | Summer | FALSE | summer
2024-09-12 09:00 | 2024-09-12 10:00 | Summer | FALSE | summer
2024-09-12 10:00 | 2024-09-12 11:00 | Summer | FALSE | summer
2024-09-12 11:00 | 2024-09-12 12:00 | Summer | FALSE | summer
2024-09-12 12:00 | 2024-09-12 13:00 | Summer | FALSE | summer
2024-09-12 13:00 | 2024-09-12 14:00 | Summer | FALSE | summer
2024-09-12 14:00 | 2024-09-12 15:00 | Summer | FALSE | summer
2024-09-12 15:00 | 2024-09-12 16:00 | Summer | FALSE | summer
2024-09-12 16:00 | 2024-09-12 17:00 | Summer | TRUE | summer
2024-09-12 17:00 | 2024-09-12 18:00 | Summer | TRUE | summer
2024-09-12 18:00 | 2024-09-12 19:00 | Summer | TRUE | summer
2024-09-12 19:00 | 2024-09-12 20:00 | Summer | TRUE | summer
2024-09-12 20:00 | 2024-09-12 21:00 | Summer | TRUE | summer
2024-09-12 21:00 | 2024-09-12 22:00 | Summer | FALSE | summer
2024-09-12 22:00 | 2024-09-12 23:00 | Summer | FALSE | summer
2024-09-12 23:00 | 2024-09-13 | Summer | FALSE | summer
2024-09-13 | 2024-09-13 01:00 | Summer | FALSE | summer
2024-09-13 01:00 | 2024-09-13 02:00 | Summer | FALSE | summer
2024-09-13 02:00 | 2024-09-13 03:00 | Summer | FALSE | summer
2024-09-13 03:00 | 2024-09-13 04:00 | Summer | FALSE | summer
2024-09-13 04:00 | 2024-09-13 05:00 | Summer | FALSE | summer
2024-09-13 05:00 | 2024-09-13 06:00 | Summer | FALSE | summer
2024-09-13 06:00 | 2024-09-13 07:00 | Summer | FALSE | summer
2024-09-13 07:00 | 2024-09-13 08:00 | Summer | FALSE | summer
2024-09-13 08:00 | 2024-09-13 09:00 | Summer | FALSE | summer
2024-09-13 09:00 | 2024-09-13 10:00 | Summer | FALSE | summer
2024-09-13 10:00 | 2024-09-13 11:00 | Summer | FALSE | summer
2024-09-13 11:00 | 2024-09-13 12:00 | Summer | FALSE | summer
2024-09-13 12:00 | 2024-09-13 13:00 | Summer | FALSE | summer
2024-09-13 13:00 | 2024-09-13 14:00 | Summer | FALSE | summer
2024-09-13 14:00 | 2024-09-13 15:00 | Summer | FALSE | summer
2024-09-13 15:00 | 2024-09-13 16:00 | Summer | FALSE | summer
2024-09-13 16:00 | 2024-09-13 17:00 | Summer | TRUE | summer
2024-09-13 17:00 | 2024-09-13 18:00 | Summer | TRUE | summer
2024-09-13 18:00 | 2024-09-13 19:00 | Summer | TRUE | summer
2024-09-13 19:00 | 2024-09-13 20:00 | Summer | TRUE | summer
2024-09-13 20:00 | 2024-09-13 21:00 | Summer | TRUE | summer
2024-09-13 21:00 | 2024-09-13 22:00 | Summer | FALSE | summer
2024-09-13 22:00 | 2024-09-13 23:00 | Summer | FALSE | summer
2024-09-13 23:00 | 2024-09-14 | Summer | FALSE | summer
2024-09-14 | 2024-09-14 01:00 | Summer | FALSE | summer
2024-09-14 01:00 | 2024-09-14 02:00 | Summer | FALSE | summer
2024-09-14 02:00 | 2024-09-14 03:00 | Summer | FALSE | summer
2024-09-14 03:00 | 2024-09-14 04:00 | Summer | FALSE | summer
2024-09-14 04:00 | 2024-09-14 05:00 | Summer | FALSE | summer
2024-09-14 05:00 | 2024-09-14 06:00 | Summer | FALSE | summer
2024-09-14 06:00 | 2024-09-14 07:00 | Summer | FALSE | summer
2024-09-14 07:00 | 2024-09-14 08:00 | Summer | FALSE | summer
2024-09-14 08:00 | 2024-09-14 09:00 | Summer | FALSE | summer
2024-09-14 09:00 | 2024-09-14 10:00 | Summer | FALSE | summer
2024-09-14 10:00 | 2024-09-14 11:00 | Summer | FALSE | summer
2024-09-14 11:00 | 2024-09-14 12:00 | Summer | FALSE | summer
2024-09-14 12:00 | 2024-09-14 13:00 | Summer | FALSE | summer
2024-09-14 13:00 | 2024-09-14 14:00 | Summer | FALSE | summer
2024-09-14 14:00 | 2024-09-14 15:00 | Summer | FALSE | summer
2024-09-14 15:00 | 2024-09-14 16:00 | Summer | FALSE | summer
2024-09-14 16:00 | 2024-09-14 17:00 | Summer | TRUE | summer
2024-09-14 17:00 | 2024-09-14 18:00 | Summer | TRUE | summer
2024-09-14 18:00 | 2024-09-14 19:00 | Summer | TRUE | summer
2024-09-14 19:00 | 2024-09-14 20:00 | Summer | TRUE | summer
2024-09-14 20:00 | 2024-09-14 21:00 | Summer | TRUE | summer
2024-09-14 21:00 | 2024-09-14 22:00 | Summer | FALSE | summer
2024-09-14 22:00 | 2024-09-14 23:00 | Summer | FALSE | summer
2024-09-14 23:00 | 2024-09-15 | Summer | FALSE | summer
2024-09-15 | 2024-09-15 01:00 | Summer | FALSE | summer
2024-09-15 01:00 | 2024-09-15 02:00 | Summer | FALSE | summer
2024-09-15 02:00 | 2024-09-15 03:00 | Summer | FALSE | summer
2024-09-15 03:00 | 2024-09-15 04:00 | Summer | FALSE | summer
2024-09-15 04:00 | 2024-09-15 05:00 | Summer | FALSE | summer
2024-09-15 05:00 | 2024-09-15 06:00 | Summer | FALSE | summer
2024-09-15 06:00 | 2024-09-15 07:00 | Summer | FALSE | summer
2024-09-15 07:00 | 2024-09-15 08:00 | Summer | FALSE | summer
2024-09-15 08:00 | 2024-09-15 09:00 | Summer | FALSE | summer
2024-09-15 09:00 | 2024-09-15 10:00 | Summer | FALSE | summer
2024-09-15 10:00 | 2024-09-15 11:00 | Summer | FALSE | summer
2024-09-15 11:00 | 2024-09-15 12:00 | Summer | FALSE | summer
2024-09-15 12:00 | 2024-09-15 13:00 | Summer | FALSE | summer
2024-09-15 13:00 | 2024-09-15 14:00 | Summer | FALSE | summer
2024-09-15 14:00 | 2024-09-15 15:00 | Summer | FALSE | summer
2024-09-15 15:00 | 2024-09-15 16:00 | Summer | FALSE | summer
2024-09-15 16:00 | 2024-09-15 17:00 | Summer | TRUE | summer
2024-09-15 17:00 | 2024-09-15 18:00 | Summer | TRUE | summer
2024-09-15 18:00 | 2024-09-15 19:00 | Summer | TRUE | summer
2024-09-15 19:00 | 2024-09-15 20:00 | Summer | TRUE | summer
2024-09-15 20:00 | 2024-09-15 21:00 | Summer | TRUE | summer
2024-09-15 21:00 | 2024-09-15 22:00 | Summer | FALSE | summer
2024-09-15 22:00 | 2024-09-15 23:00 | Summer | FALSE | summer
2024-09-15 23:00 | 2024-09-16 | Summer | FALSE | summer
2024-09-16 | 2024-09-16 01:00 | Summer | FALSE | summer
2024-09-16 01:00 | 2024-09-16 02:00 | Summer | FALSE | summer
2024-09-16 02:00 | 2024-09-16 03:00 | Summer | FALSE | summer
2024-09-16 03:00 | 2024-09-16 04:00 | Summer | FALSE | summer
2024-09-16 04:00 | 2024-09-16 05:00 | Summer | FALSE | summer
2024-09-16 05:00 | 2024-09-16 06:00 | Summer | FALSE | summer
2024-09-16 06:00 | 2024-09-16 07:00 | Summer | FALSE | summer
2024-09-16 07:00 | 2024-09-16 08:00 | Summer | FALSE | summer
2024-09-16 08:00 | 2024-09-16 09:00 | Summer | FALSE | summer
2024-09-16 09:00 | 2024-09-16 10:00 | Summer | FALSE | summer
2024-09-16 10:00 | 2024-09-16 11:00 | Summer | FALSE | summer
2024-09-16 11:00 | 2024-09-16 12:00 | Summer | FALSE | summer
2024-09-16 12:00 | 2024-09-16 13:00 | Summer | FALSE | summer
2024-09-16 13:00 | 2024-09-16 14:00 | Summer | FALSE | summer
2024-09-16 14:00 | 2024-09-16 15:00 | Summer | FALSE | summer
2024-09-16 15:00 | 2024-09-16 16:00 | Summer | FALSE | summer
2024-09-16 16:00 | 2024-09-16 17:00 | Summer | TRUE | summer
2024-09-16 17:00 | 2024-09-16 18:00 | Summer | TRUE | summer
2024-09-16 18:00 | 2024-09-16 19:00 | Summer | TRUE | summer
2024-09-16 19:00 | 2024-09-16 20:00 | Summer | TRUE | summer
2024-09-16 20:00 | 2024-09-16 21:00 | Summer | TRUE | summer
2024-09-16 21:00 | 2024-09-16 22:00 | Summer | FALSE | summer
2024-09-16 22:00 | 2024-09-16 23:00 | Summer | FALSE | summer
2024-09-16 23:00 | 2024-09-17 | Summer | FALSE | summer
2024-09-17 | 2024-09-17 01:00 | Summer | FALSE | summer
2024-09-17 01:00 | 2024-09-17 02:00 | Summer | FALSE | summer
2024-09-17 02:00 | 2024-09-17 03:00 | Summer | FALSE | summer
2024-09-17 03:00 | 2024-09-17 04:00 | Summer | FALSE | summer
2024-09-17 04:00 | 2024-09-17 05:00 | Summer | FALSE | summer
2024-09-17 05:00 | 2024-09-17 06:00 | Summer | FALSE | summer
2024-09-17 06:00 | 2024-09-17 07:00 | Summer | FALSE | summer
2024-09-17 07:00 | 2024-09-17 08:00 | Summer | FALSE | summer
2024-09-17 08:00 | 2024-09-17 09:00 | Summer | FALSE | summer
2024-09-17 09:00 | 2024-09-17 10:00 | Summer | FALSE | summer
2024-09-17 10:00 | 2024-09-17 11:00 | Summer | FALSE | summer
2024-09-17 11:00 | 2024-09-17 12:00 | Summer | FALSE | summer
2024-09-17 12:00 | 2024-09-17 13:00 | Summer | FALSE | summer
2024-09-17 13:00 | 2024-09-17 14:00 | Summer | FALSE | summer
2024-09-17 14:00 | 2024-09-17 15:00 | Summer | FALSE | summer
2024-09-17 15:00 | 2024-09-17 16:00 | Summer | FALSE | summer
2024-09-17 16:00 | 2024-09-17 17:00 | Summer | TRUE | summer
2024-09-17 17:00 | 2024-09-17 18:00 | Summer | TRUE | summer
2024-09-17 18:00 | 2024-09-17 19:00 | Summer | TRUE | summer
2024-09-17 19:00 | 2024-09-17 20:00 | Summer | TRUE | summer
2024-09-17 20:00 | 2024-09-17 21:00 | Summer | TRUE | summer
2024-09-17 21:00 | 2024-09-17 22:00 | Summer | FALSE | summer
2024-09-17 22:00 | 2024-09-17 23:00 | Summer | FALSE | summer
2024-09-17 23:00 | 2024-09-18 | Summer | FALSE | summer
2024-09-18 | 2024-09-18 01:00 | Summer | FALSE | summer
2024-09-18 01:00 | 2024-09-18 02:00 | Summer | FALSE | summer
2024-09-18 02:00 | 2024-09-18 03:00 | Summer | FALSE | summer
2024-09-18 03:00 | 2024-09-18 04:00 | Summer | FALSE | summer
2024-09-18 04:00 | 2024-09-18 05:00 | Summer | FALSE | summer
2024-09-18 05:00 | 2024-09-18 06:00 | Summer | FALSE | summer
2024-09-18 06:00 | 2024-09-18 07:00 | Summer | FALSE | summer
2024-09-18 07:00 | 2024-09-18 08:00 | Summer | FALSE | summer
2024-09-18 08:00 | 2024-09-18 09:00 | Summer | FALSE | summer
2024-09-18 09:00 | 2024-09-18 10:00 | Summer | FALSE | summer
2024-09-18 10:00 | 2024-09-18 11:00 | Summer | FALSE | summer
2024-09-18 11:00 | 2024-09-18 12:00 | Summer | FALSE | summer
2024-09-18 12:00 | 2024-09-18 13:00 | Summer | FALSE | summer
2024-09-18 13:00 | 2024-09-18 14:00 | Summer | FALSE | summer
2024-09-18 14:00 | 2024-09-18 15:00 | Summer | FALSE | summer
2024-09-18 15:00 | 2024-09-18 16:00 | Summer | FALSE | summer
2024-09-18 16:00 | 2024-09-18 17:00 | Summer | TRUE | summer
2024-09-18 17:00 | 2024-09-18 18:00 | Summer | TRUE | summer
2024-09-18 18:00 | 2024-09-18 19:00 | Summer | TRUE | summer
2024-09-18 19:00 | 2024-09-18 20:00 | Summer | TRUE | summer
2024-09-18 20:00 | 2024-09-18 21:00 | Summer | TRUE | summer
2024-09-18 21:00 | 2024-09-18 22:00 | Summer | FALSE | summer
2024-09-18 22:00 | 2024-09-18 23:00 | Summer | FALSE | summer
2024-09-18 23:00 | 2024-09-19 | Summer | FALSE | summer
2024-09-19 | 2024-09-19 01:00 | Summer | FALSE | summer
2024-09-19 01:00 | 2024-09-19 02:00 | Summer | FALSE | summer
2024-09-19 02:00 | 2024-09-19 03:00 | Summer | FALSE | summer
2024-09-19 03:00 | 2024-09-19 04:00 | Summer | FALSE | summer
2024-09-19 04:00 | 2024-09-19 05:00 | Summer | FALSE | summer
2024-09-19 05:00 | 2024-09-19 06:00 | Summer | FALSE | summer
2024-09-19 06:00 | 2024-09-19 07:00 | Summer | FALSE | summer
2024-09-19 07:00 | 2024-09-19 08:00 | Summer | FALSE | summer
2024-09-19 08:00 | 2024-09-19 09:00 | Summer | FALSE | summer
2024-09-19 09:00 | 2024-09-19 10:00 | Summer | FALSE | summer
2024-09-19 10:00 | 2024-09-19 11:00 | Summer | FALSE | summer
2024-09-19 11:00 | 2024-09-19 12:00 | Summer | FALSE | summer
2024-09-19 12:00 | 2024-09-19 13:00 | Summer | FALSE | summer
2024-09-19 13:00 | 2024-09-19 14:00 | Summer | FALSE | summer
2024-09-19 14:00 | 2024-09-19 15:00 | Summer | FALSE | summer
2024-09-19 15:00 | 2024-09-19 16:00 | Summer | FALSE | summer
2024-09-19 16:00 | 2024-09-19 17:00 | Summer | TRUE | summer
2024-09-19 17:00 | 2024-09-19 18:00 | Summer | TRUE | summer
2024-09-19 18:00 | 2024-09-19 19:00 | Summer | TRUE | summer
2024-09-19 19:00 | 2024-09-19 20:00 | Summer | TRUE | summer
2024-09-19 20:00 | 2024-09-19 21:00 | Summer | TRUE | summer
2024-09-19 21:00 | 2024-09-19 22:00 | Summer | FALSE | summer
2024-09-19 22:00 | 2024-09-19 23:00 | Summer | FALSE | summer
2024-09-19 23:00 | 2024-09-20 | Summer | FALSE | summer
2024-09-20 | 2024-09-20 01:00 | Summer | FALSE | summer
2024-09-20 01:00 | 2024-09-20 02:00 | Summer | FALSE | summer
2024-09-20 02:00 | 2024-09-20 03:00 | Summer | FALSE | summer
2024-09-20 03:00 | 2024-09-20 04:00 | Summer | FALSE | summer
2024-09-20 04:00 | 2024-09-20 05:00 | Summer | FALSE | summer
2024-09-20 05:00 | 2024-09-20 06:00 | Summer | FALSE | summer
2024-09-20 06:00 | 2024-09-20 07:00 | Summer | FALSE | summer
2024-09-20 07:00 | 2024-09-20 08:00 | Summer | FALSE | summer
2024-09-20 08:00 | 2024-09-20 09:00 | Summer | FALSE | summer
2024-09-20 09:00 | 2024-09-20 10:00 | Summer | FALSE | summer
2024-09-20 10:00 | 2024-09-20 11:00 | Summer | FALSE | summer
2024-09-20 11:00 | 2024-09-20 12:00 | Summer | FALSE | summer
2024-09-20 12:00 | 2024-09-20 13:00 | Summer | FALSE | summer
2024-09-20 13:00 | 2024-09-20 14:00 | Summer | FALSE | summer
2024-09-20 14:00 | 2024-09-20 15:00 | Summer | FALSE | summer
2024-09-20 15:00 | 2024-09-20 16:00 | Summer | FALSE | summer
2024-09-20 16:00 | 2024-09-20 17:00 | Summer | TRUE | summer
2024-09-20 17:00 | 2024-09-20 18:00 | Summer | TRUE | summer
2024-09-20 18:00 | 2024-09-20 19:00 | Summer | TRUE | summer
2024-09-20 19:00 | 2024-09-20 20:00 | Summer | TRUE | summer
2024-09-20 20:00 | 2024-09-20 21:00 | Summer | TRUE | summer
2024-09-20 21:00 | 2024-09-20 22:00 | Summer | FALSE | summer
2024-09-20 22:00 | 2024-09-20 23:00 | Summer | FALSE | summer
2024-09-20 23:00 | 2024-09-21 | Summer | FALSE | summer
2024-09-21 | 2024-09-21 01:00 | Summer | FALSE | summer
2024-09-21 01:00 | 2024-09-21 02:00 | Summer | FALSE | summer
2024-09-21 02:00 | 2024-09-21 03:00 | Summer | FALSE | summer
2024-09-21 03:00 | 2024-09-21 04:00 | Summer | FALSE | summer
2024-09-21 04:00 | 2024-09-21 05:00 | Summer | FALSE | summer
2024-09-21 05:00 | 2024-09-21 06:00 | Summer | FALSE | summer
2024-09-21 06:00 | 2024-09-21 07:00 | Summer | FALSE | summer
2024-09-21 07:00 | 2024-09-21 08:00 | Summer | FALSE | summer
2024-09-21 08:00 | 2024-09-21 09:00 | Summer | FALSE | summer
2024-09-21 09:00 | 2024-09-21 10:00 | Summer | FALSE | summer
2024-09-21 10:00 | 2024-09-21 11:00 | Summer | FALSE | summer
2024-09-21 11:00 | 2024-09-21 12:00 | Summer | FALSE | summer
2024-09-21 12:00 | 2024-09-21 13:00 | Summer | FALSE | summer
2024-09-21 13:00 | 2024-09-21 14:00 | Summer | FALSE | summer
2024-09-21 14:00 | 2024-09-21 15:00 | Summer | FALSE | summer
2024-09-21 15:00 | 2024-09-21 16:00 | Summer | FALSE | summer
2024-09-21 16:00 | 2024-09-21 17:00 | Summer | TRUE | summer
2024-09-21 17:00 | 2024-09-21 18:00 | Summer | TRUE | summer
2024-09-21 18:00 | 2024-09-21 19:00 | Summer | TRUE | summer
2024-09-21 19:00 | 2024-09-21 20:00 | Summer | TRUE | summer
2024-09-21 20:00 | 2024-09-21 21:00 | Summer | TRUE | summer
2024-09-21 21:00 | 2024-09-21 22:00 | Summer | FALSE | summer
2024-09-21 22:00 | 2024-09-21 23:00 | Summer | FALSE | summer
2024-09-21 23:00 | 2024-09-22 | Summer | FALSE | summer
2024-09-22 | 2024-09-22 01:00 | Summer | FALSE | summer
2024-09-22 01:00 | 2024-09-22 02:00 | Summer | FALSE | summer
2024-09-22 02:00 | 2024-09-22 03:00 | Summer | FALSE | summer
2024-09-22 03:00 | 2024-09-22 04:00 | Summer | FALSE | summer
2024-09-22 04:00 | 2024-09-22 05:00 | Summer | FALSE | summer
2024-09-22 05:00 | 2024-09-22 06:00 | Summer | FALSE | summer
2024-09-22 06:00 | 2024-09-22 07:00 | Summer | FALSE | summer
2024-09-22 07:00 | 2024-09-22 08:00 | Summer | FALSE | summer
2024-09-22 08:00 | 2024-09-22 09:00 | Summer | FALSE | summer
2024-09-22 09:00 | 2024-09-22 10:00 | Summer | FALSE | summer
2024-09-22 10:00 | 2024-09-22 11:00 | Summer | FALSE | summer
2024-09-22 11:00 | 2024-09-22 12:00 | Summer | FALSE | summer
2024-09-22 12:00 | 2024-09-22 13:00 | Summer | FALSE | summer
2024-09-22 13:00 | 2024-09-22 14:00 | Summer | FALSE | summer
2024-09-22 14:00 | 2024-09-22 15:00 | Summer | FALSE | summer
2024-09-22 15:00 | 2024-09-22 16:00 | Summer | FALSE | summer
2024-09-22 16:00 | 2024-09-22 17:00 | Summer | TRUE | summer
2024-09-22 17:00 | 2024-09-22 18:00 | Summer | TRUE | summer
2024-09-22 18:00 | 2024-09-22 19:00 | Summer | TRUE | summer
2024-09-22 19:00 | 2024-09-22 20:00 | Summer | TRUE | summer
2024-09-22 20:00 | 2024-09-22 21:00 | Summer | TRUE | summer
2024-09-22 21:00 | 2024-09-22 22:00 | Summer | FALSE | summer
2024-09-22 22:00 | 2024-09-22 23:00 | Summer | FALSE | summer
2024-09-22 23:00 | 2024-09-23 | Summer | FALSE | summer
2024-09-23 | 2024-09-23 01:00 | Summer | FALSE | summer
2024-09-23 01:00 | 2024-09-23 02:00 | Summer | FALSE | summer
2024-09-23 02:00 | 2024-09-23 03:00 | Summer | FALSE | summer
2024-09-23 03:00 | 2024-09-23 04:00 | Summer | FALSE | summer
2024-09-23 04:00 | 2024-09-23 05:00 | Summer | FALSE | summer
2024-09-23 05:00 | 2024-09-23 06:00 | Summer | FALSE | summer
2024-09-23 06:00 | 2024-09-23 07:00 | Summer | FALSE | summer
2024-09-23 07:00 | 2024-09-23 08:00 | Summer | FALSE | summer
2024-09-23 08:00 | 2024-09-23 09:00 | Summer | FALSE | summer
2024-09-23 09:00 | 2024-09-23 10:00 | Summer | FALSE | summer
2024-09-23 10:00 | 2024-09-23 11:00 | Summer | FALSE | summer
2024-09-23 11:00 | 2024-09-23 12:00 | Summer | FALSE | summer
2024-09-23 12:00 | 2024-09-23 13:00 | Summer | FALSE | summer
2024-09-23 13:00 | 2024-09-23 14:00 | Summer | FALSE | summer
2024-09-23 14:00 | 2024-09-23 15:00 | Summer | FALSE | summer
2024-09-23 15:00 | 2024-09-23 16:00 | Summer | FALSE | summer
2024-09-23 16:00 | 2024-09-23 17:00 | Summer | TRUE | summer
2024-09-23 17:00 | 2024-09-23 18:00 | Summer | TRUE | summer
2024-09-23 18:00 | 2024-09-23 19:00 | Summer | TRUE | summer
2024-09-23 19:00 | 2024-09-23 20:00 | Summer | TRUE | summer
2024-09-23 20:00 | 2024-09-23 21:00 | Summer | TRUE | summer
2024-09-23 21:00 | 2024-09-23 22:00 | Summer | FALSE | summer
2024-09-23 22:00 | 2024-09-23 23:00 | Summer | FALSE | summer
2024-09-23 23:00 | 2024-09-24 | Summer | FALSE | summer
2024-09-24 | 2024-09-24 01:00 | Summer | FALSE | summer
2024-09-24 01:00 | 2024-09-24 02:00 | Summer | FALSE | summer
2024-09-24 02:00 | 2024-09-24 03:00 | Summer | FALSE | summer
2024-09-24 03:00 | 2024-09-24 04:00 | Summer | FALSE | summer
2024-09-24 04:00 | 2024-09-24 05:00 | Summer | FALSE | summer
2024-09-24 05:00 | 2024-09-24 06:00 | Summer | FALSE | summer
2024-09-24 06:00 | 2024-09-24 07:00 | Summer | FALSE | summer
2024-09-24 07:00 | 2024-09-24 08:00 | Summer | FALSE | summer
2024-09-24 08:00 | 2024-09-24 09:00 | Summer | FALSE | summer
2024-09-24 09:00 | 2024-09-24 10:00 | Summer | FALSE | summer
2024-09-24 10:00 | 2024-09-24 11:00 | Summer | FALSE | summer
2024-09-24 11:00 | 2024-09-24 12:00 | Summer | FALSE | summer
2024-09-24 12:00 | 2024-09-24 13:00 | Summer | FALSE | summer
2024-09-24 13:00 | 2024-09-24 14:00 | Summer | FALSE | summer
2024-09-24 14:00 | 2024-09-24 15:00 | Summer | FALSE | summer
2024-09-24 15:00 | 2024-09-24 16:00 | Summer | FALSE | summer
2024-09-24 16:00 | 2024-09-24 17:00 | Summer | TRUE | summer
2024-09-24 17:00 | 2024-09-24 18:00 | Summer | TRUE | summer
2024-09-24 18:00 | 2024-09-24 19:00 | Summer | TRUE | summer
2024-09-24 19:00 | 2024-09-24 20:00 | Summer | TRUE | summer
2024-09-24 20:00 | 2024-09-24 21:00 | Summer | TRUE | summer
2024-09-24 21:00 | 2024-09-24 22:00 | Summer | FALSE | summer
2024-09-24 22:00 | 2024-09-24 23:00 | Summer | FALSE | summer
2024-09-24 23:00 | 2024-09-25 | Summer | FALSE | summer
2024-09-25 | 2024-09-25 01:00 | Summer | FALSE | summer
2024-09-25 01:00 | 2024-09-25 02:00 | Summer | FALSE | summer
2024-09-25 02:00 | 2024-09-25 03:00 | Summer | FALSE | summer
2024-09-25 03:00 | 2024-09-25 04:00 | Summer | FALSE | summer
2024-09-25 04:00 | 2024-09-25 05:00 | Summer | FALSE | summer
2024-09-25 05:00 | 2024-09-25 06:00 | Summer | FALSE | summer
2024-09-25 06:00 | 2024-09-25 07:00 | Summer | FALSE | summer
2024-09-25 07:00 | 2024-09-25 08:00 | Summer | FALSE | summer
2024-09-25 08:00 | 2024-09-25 09:00 | Summer | FALSE | summer
2024-09-25 09:00 | 2024-09-25 10:00 | Summer | FALSE | summer
2024-09-25 10:00 | 2024-09-25 11:00 | Summer | FALSE | summer
2024-09-25 11:00 | 2024-09-25 12:00 | Summer | FALSE | summer
2024-09-25 12:00 | 2024-09-25 13:00 | Summer | FALSE | summer
2024-09-25 13:00 | 2024-09-25 14:00 | Summer | FALSE | summer
2024-09-25 14:00 | 2024-09-25 15:00 | Summer | FALSE | summer
2024-09-25 15:00 | 2024-09-25 16:00 | Summer | FALSE | summer
2024-09-25 16:00 | 2024-09-25 17:00 | Summer | TRUE | summer
2024-09-25 17:00 | 2024-09-25 18:00 | Summer | TRUE | summer
2024-09-25 18:00 | 2024-09-25 19:00 | Summer | TRUE | summer
2024-09-25 19:00 | 2024-09-25 20:00 | Summer | TRUE | summer
2024-09-25 20:00 | 2024-09-25 21:00 | Summer | TRUE | summer
2024-09-25 21:00 | 2024-09-25 22:00 | Summer | FALSE | summer
2024-09-25 22:00 | 2024-09-25 23:00 | Summer | FALSE | summer
2024-09-25 23:00 | 2024-09-26 | Summer | FALSE | summer
2024-09-26 | 2024-09-26 01:00 | Summer | FALSE | summer
2024-09-26 01:00 | 2024-09-26 02:00 | Summer | FALSE | summer
2024-09-26 02:00 | 2024-09-26 03:00 | Summer | FALSE | summer
2024-09-26 03:00 | 2024-09-26 04:00 | Summer | FALSE | summer
2024-09-26 04:00 | 2024-09-26 05:00 | Summer | FALSE | summer
2024-09-26 05:00 | 2024-09-26 06:00 | Summer | FALSE | summer
2024-09-26 06:00 | 2024-09-26 07:00 | Summer | FALSE | summer
2024-09-26 07:00 | 2024-09-26 08:00 | Summer | FALSE | summer
2024-09-26 08:00 | 2024-09-26 09:00 | Summer | FALSE | summer
2024-09-26 09:00 | 2024-09-26 10:00 | Summer | FALSE | summer
2024-09-26 10:00 | 2024-09-26 11:00 | Summer | FALSE | summer
2024-09-26 11:00 | 2024-09-26 12:00 | Summer | FALSE | summer
2024-09-26 12:00 | 2024-09-26 13:00 | Summer | FALSE | summer
2024-09-26 13:00 | 2024-09-26 14:00 | Summer | FALSE | summer
2024-09-26 14:00 | 2024-09-26 15:00 | Summer | FALSE | summer
2024-09-26 15:00 | 2024-09-26 16:00 | Summer | FALSE | summer
2024-09-26 16:00 | 2024-09-26 17:00 | Summer | TRUE | summer
2024-09-26 17:00 | 2024-09-26 18:00 | Summer | TRUE | summer
2024-09-26 18:00 | 2024-09-26 19:00 | Summer | TRUE | summer
2024-09-26 19:00 | 2024-09-26 20:00 | Summer | TRUE | summer
2024-09-26 20:00 | 2024-09-26 21:00 | Summer | TRUE | summer
2024-09-26 21:00 | 2024-09-26 22:00 | Summer | FALSE | summer
2024-09-26 22:00 | 2024-09-26 23:00 | Summer | FALSE | summer
2024-09-26 23:00 | 2024-09-27 | Summer | FALSE | summer
2024-09-27 | 2024-09-27 01:00 | Summer | FALSE | summer
2024-09-27 01:00 | 2024-09-27 02:00 | Summer | FALSE | summer
2024-09-27 02:00 | 2024-09-27 03:00 | Summer | FALSE | summer
2024-09-27 03:00 | 2024-09-27 04:00 | Summer | FALSE | summer
2024-09-27 04:00 | 2024-09-27 05:00 | Summer | FALSE | summer
2024-09-27 05:00 | 2024-09-27 06:00 | Summer | FALSE | summer
2024-09-27 06:00 | 2024-09-27 07:00 | Summer | FALSE | summer
2024-09-27 07:00 | 2024-09-27 08:00 | Summer | FALSE | summer
2024-09-27 08:00 | 2024-09-27 09:00 | Summer | FALSE | summer
2024-09-27 09:00 | 2024-09-27 10:00 | Summer | FALSE | summer
2024-09-27 10:00 | 2024-09-27 11:00 | Summer | FALSE | summer
2024-09-27 11:00 | 2024-09-27 12:00 | Summer | FALSE | summer
2024-09-27 12:00 | 2024-09-27 13:00 | Summer | FALSE | summer
2024-09-27 13:00 | 2024-09-27 14:00 | Summer | FALSE | summer
2024-09-27 14:00 | 2024-09-27 15:00 | Summer | FALSE | summer
2024-09-27 15:00 | 2024-09-27 16:00 | Summer | FALSE | summer
2024-09-27 16:00 | 2024-09-27 17:00 | Summer | TRUE | summer
2024-09-27 17:00 | 2024-09-27 18:00 | Summer | TRUE | summer
2024-09-27 18:00 | 2024-09-27 19:00 | Summer | TRUE | summer
2024-09-27 19:00 | 2024-09-27 20:00 | Summer | TRUE | summer
2024-09-27 20:00 | 2024-09-27 21:00 | Summer | TRUE | summer
2024-09-27 21:00 | 2024-09-27 22:00 | Summer | FALSE | summer
2024-09-27 22:00 | 2024-09-27 23:00 | Summer | FALSE | summer
2024-09-27 23:00 | 2024-09-28 | Summer | FALSE | summer
2024-09-28 | 2024-09-28 01:00 | Summer | FALSE | summer
2024-09-28 01:00 | 2024-09-28 02:00 | Summer | FALSE | summer
2024-09-28 02:00 | 2024-09-28 03:00 | Summer | FALSE | summer
2024-09-28 03:00 | 2024-09-28 04:00 | Summer | FALSE | summer
2024-09-28 04:00 | 2024-09-28 05:00 | Summer | FALSE | summer
2024-09-28 05:00 | 2024-09-28 06:00 | Summer | FALSE | summer
2024-09-28 06:00 | 2024-09-28 07:00 | Summer | FALSE | summer
2024-09-28 07:00 | 2024-09-28 08:00 | Summer | FALSE | summer
2024-09-28 08:00 | 2024-09-28 09:00 | Summer | FALSE | summer
2024-09-28 09:00 | 2024-09-28 10:00 | Summer | FALSE | summer
2024-09-28 10:00 | 2024-09-28 11:00 | Summer | FALSE | summer
2024-09-28 11:00 | 2024-09-28 12:00 | Summer | FALSE | summer
2024-09-28 12:00 | 2024-09-28 13:00 | Summer | FALSE | summer
2024-09-28 13:00 | 2024-09-28 14:00 | Summer | FALSE | summer
2024-09-28 14:00 | 2024-09-28 15:00 | Summer | FALSE | summer
2024-09-28 15:00 | 2024-09-28 16:00 | Summer | FALSE | summer
2024-09-28 16:00 | 2024-09-28 17:00 | Summer | TRUE | summer
2024-09-28 17:00 | 2024-09-28 18:00 | Summer | TRUE | summer
2024-09-28 18:00 | 2024-09-28 19:00 | Summer | TRUE | summer
2024-09-28 19:00 | 2024-09-28 20:00 | Summer | TRUE | summer
2024-09-28 20:00 | 2024-09-28 21:00 | Summer | TRUE | summer
2024-09-28 21:00 | 2024-09-28 22:00 | Summer | FALSE | summer
2024-09-28 22:00 | 2024-09-28 23:00 | Summer | FALSE | summer
2024-09-28 23:00 | 2024-09-29 | Summer | FALSE | summer
2024-09-29 | 2024-09-29 01:00 | Summer | FALSE | summer
2024-09-29 01:00 | 2024-09-29 02:00 | Summer | FALSE | summer
2024-09-29 02:00 | 2024-09-29 03:00 | Summer | FALSE | summer
2024-09-29 03:00 | 2024-09-29 04:00 | Summer | FALSE | summer
2024-09-29 04:00 | 2024-09-29 05:00 | Summer | FALSE | summer
2024-09-29 05:00 | 2024-09-29 06:00 | Summer | FALSE | summer
2024-09-29 06:00 | 2024-09-29 07:00 | Summer | FALSE | summer
2024-09-29 07:00 | 2024-09-29 08:00 | Summer | FALSE | summer
2024-09-29 08:00 | 2024-09-29 09:00 | Summer | FALSE | summer
2024-09-29 09:00 | 2024-09-29 10:00 | Summer | FALSE | summer
2024-09-29 10:00 | 2024-09-29 11:00 | Summer | FALSE | summer
2024-09-29 11:00 | 2024-09-29 12:00 | Summer | FALSE | summer
2024-09-29 12:00 | 2024-09-29 13:00 | Summer | FALSE | summer
2024-09-29 13:00 | 2024-09-29 14:00 | Summer | FALSE | summer
2024-09-29 14:00 | 2024-09-29 15:00 | Summer | FALSE | summer
2024-09-29 15:00 | 2024-09-29 16:00 | Summer | FALSE | summer
2024-09-29 16:00 | 2024-09-29 17:00 | Summer | TRUE | summer
2024-09-29 17:00 | 2024-09-29 18:00 | Summer | TRUE | summer
2024-09-29 18:00 | 2024-09-29 19:00 | Summer | TRUE | summer
2024-09-29 19:00 | 2024-09-29 20:00 | Summer | TRUE | summer
2024-09-29 20:00 | 2024-09-29 21:00 | Summer | TRUE | summer
2024-09-29 21:00 | 2024-09-29 22:00 | Summer | FALSE | summer
2024-09-29 22:00 | 2024-09-29 23:00 | Summer | FALSE | summer
2024-09-29 23:00 | 2024-09-30 | Summer | FALSE | summer
2024-09-30 | 2024-09-30 01:00 | Summer | FALSE | summer
2024-09-30 01:00 | 2024-09-30 02:00 | Summer | FALSE | summer
2024-09-30 02:00 | 2024-09-30 03:00 | Summer | FALSE | summer
2024-09-30 03:00 | 2024-09-30 04:00 | Summer | FALSE | summer
2024-09-30 04:00 | 2024-09-30 05:00 | Summer | FALSE | summer
2024-09-30 05:00 | 2024-09-30 06:00 | Summer | FALSE | summer
2024-09-30 06:00 | 2024-09-30 07:00 | Summer | FALSE | summer
2024-09-30 07:00 | 2024-09-30 08:00 | Summer | FALSE | summer
2024-09-30 08:00 | 2024-09-30 09:00 | Summer | FALSE | summer
2024-09-30 09:00 | 2024-09-30 10:00 | Summer | FALSE | summer
2024-09-30 10:00 | 2024-09-30 11:00 | Summer | FALSE | summer
2024-09-30 11:00 | 2024-09-30 12:00 | Summer | FALSE | summer
2024-09-30 12:00 | 2024-09-30 13:00 | Summer | FALSE | summer
2024-09-30 13:00 | 2024-09-30 14:00 | Summer | FALSE | summer
2024-09-30 14:00 | 2024-09-30 15:00 | Summer | FALSE | summer
2024-09-30 15:00 | 2024-09-30 16:00 | Summer | FALSE | summer
2024-09-30 16:00 | 2024-09-30 17:00 | Summer | TRUE | summer
2024-09-30 17:00 | 2024-09-30 18:00 | Summer | TRUE | summer
2024-09-30 18:00 | 2024-09-30 19:00 | Summer | TRUE | summer
2024-09-30 19:00 | 2024-09-30 20:00 | Summer | TRUE | summer
2024-09-30 20:00 | 2024-09-30 21:00 | Summer | TRUE | summer
2024-09-30 21:00 | 2024-09-30 22:00 | Summer | FALSE | summer
2024-09-30 22:00 | 2024-09-30 23:00 | Summer | FALSE | summer
2024-09-30 23:00 | 2024-10-01 | Summer | FALSE | summer
2024-10-01 | 2024-10-01 01:00 | Winter | FALSE | summer
2024-10-01 01:00 | 2024-10-01 02:00 | Winter | FALSE | summer
2024-10-01 02:00 | 2024-10-01 03:00 | Winter | FALSE | summer
2024-10-01 03:00 | 2024-10-01 04:00 | Winter | FALSE | summer
2024-10-01 04:00 | 2024-10-01 05:00 | Winter | FALSE | summer
2024-10-01 05:00 | 2024-10-01 06:00 | Winter | FALSE | summer
2024-10-01 06:00 | 2024-10-01 07:00 | Winter | FALSE | summer
2024-10-01 07:00 | 2024-10-01 08:00 | Winter | FALSE | summer
2024-10-01 08:00 | 2024-10-01 09:00 | Winter | FALSE | summer
2024-10-01 09:00 | 2024-10-01 10:00 | Winter | FALSE | summer
2024-10-01 10:00 | 2024-10-01 11:00 | Winter | FALSE | summer
2024-10-01 11:00 | 2024-10-01 12:00 | Winter | FALSE | summer
2024-10-01 12:00 | 2024-10-01 13:00 | Winter | FALSE | summer
2024-10-01 13:00 | 2024-10-01 14:00 | Winter | FALSE | summer
2024-10-01 14:00 | 2024-10-01 15:00 | Winter | FALSE | summer
2024-10-01 15:00 | 2024-10-01 16:00 | Winter | FALSE | summer
2024-10-01 16:00 | 2024-10-01 17:00 | Winter | TRUE | summer
2024-10-01 17:00 | 2024-10-01 18:00 | Winter | TRUE | summer
2024-10-01 18:00 | 2024-10-01 19:00 | Winter | TRUE | summer
2024-10-01 19:00 | 2024-10-01 20:00 | Winter | TRUE | summer
2024-10-01 20:00 | 2024-10-01 21:00 | Winter | TRUE | summer
2024-10-01 21:00 | 2024-10-01 22:00 | Winter | FALSE | summer
2024-10-01 22:00 | 2024-10-01 23:00 | Winter | FALSE | summer
2024-10-01 23:00 | 2024-10-02 | Winter | FALSE | summer
2024-10-02 | 2024-10-02 01:00 | Winter | FALSE | summer
2024-10-02 01:00 | 2024-10-02 02:00 | Winter | FALSE | summer
2024-10-02 02:00 | 2024-10-02 03:00 | Winter | FALSE | summer
2024-10-02 03:00 | 2024-10-02 04:00 | Winter | FALSE | summer
2024-10-02 04:00 | 2024-10-02 05:00 | Winter | FALSE | summer
2024-10-02 05:00 | 2024-10-02 06:00 | Winter | FALSE | summer
2024-10-02 06:00 | 2024-10-02 07:00 | Winter | FALSE | summer
2024-10-02 07:00 | 2024-10-02 08:00 | Winter | FALSE | summer
2024-10-02 08:00 | 2024-10-02 09:00 | Winter | FALSE | summer
2024-10-02 09:00 | 2024-10-02 10:00 | Winter | FALSE | summer
2024-10-02 10:00 | 2024-10-02 11:00 | Winter | FALSE | summer
2024-10-02 11:00 | 2024-10-02 12:00 | Winter | FALSE | summer
2024-10-02 12:00 | 2024-10-02 13:00 | Winter | FALSE | summer
2024-10-02 13:00 | 2024-10-02 14:00 | Winter | FALSE | summer
2024-10-02 14:00 | 2024-10-02 15:00 | Winter | FALSE | summer
2024-10-02 15:00 | 2024-10-02 16:00 | Winter | FALSE | summer
2024-10-02 16:00 | 2024-10-02 17:00 | Winter | TRUE | summer
2024-10-02 17:00 | 2024-10-02 18:00 | Winter | TRUE | summer
2024-10-02 18:00 | 2024-10-02 19:00 | Winter | TRUE | summer
2024-10-02 19:00 | 2024-10-02 20:00 | Winter | TRUE | summer
2024-10-02 20:00 | 2024-10-02 21:00 | Winter | TRUE | summer
2024-10-02 21:00 | 2024-10-02 22:00 | Winter | FALSE | summer
2024-10-02 22:00 | 2024-10-02 23:00 | Winter | FALSE | summer
2024-10-02 23:00 | 2024-10-03 | Winter | FALSE | summer
2024-10-03 | 2024-10-03 01:00 | Winter | FALSE | summer
2024-10-03 01:00 | 2024-10-03 02:00 | Winter | FALSE | summer
2024-10-03 02:00 | 2024-10-03 03:00 | Winter | FALSE | summer
2024-10-03 03:00 | 2024-10-03 04:00 | Winter | FALSE | summer
2024-10-03 04:00 | 2024-10-03 05:00 | Winter | FALSE | summer
2024-10-03 05:00 | 2024-10-03 06:00 | Winter | FALSE | summer
2024-10-03 06:00 | 2024-10-03 07:00 | Winter | FALSE | summer
2024-10-03 07:00 | 2024-10-03 08:00 | Winter | FALSE | summer
2024-10-03 08:00 | 2024-10-03 09:00 | Winter | FALSE | summer
2024-10-03 09:00 | 2024-10-03 10:00 | Winter | FALSE | summer
2024-10-03 10:00 | 2024-10-03 11:00 | Winter | FALSE | summer
2024-10-03 11:00 | 2024-10-03 12:00 | Winter | FALSE | summer
2024-10-03 12:00 | 2024-10-03 13:00 | Winter | FALSE | summer
2024-10-03 13:00 | 2024-10-03 14:00 | Winter | FALSE | summer
2024-10-03 14:00 | 2024-10-03 15:00 | Winter | FALSE | summer
2024-10-03 15:00 | 2024-10-03 16:00 | Winter | FALSE | summer
2024-10-03 16:00 | 2024-10-03 17:00 | Winter | TRUE | summer
2024-10-03 17:00 | 2024-10-03 18:00 | Winter | TRUE | summer
2024-10-03 18:00 | 2024-10-03 19:00 | Winter | TRUE | summer
2024-10-03 19:00 | 2024-10-03 20:00 | Winter | TRUE | summer
2024-10-03 20:00 | 2024-10-03 21:00 | Winter | TRUE | summer
2024-10-03 21:00 | 2024-10-03 22:00 | Winter | FALSE | summer
2024-10-03 22:00 | 2024-10-03 23:00 | Winter | FALSE | summer
2024-10-03 23:00 | 2024-10-04 | Winter | FALSE | summer
2024-10-04 | 2024-10-04 01:00 | Winter | FALSE | summer
2024-10-04 01:00 | 2024-10-04 02:00 | Winter | FALSE | summer
2024-10-04 02:00 | 2024-10-04 03:00 | Winter | FALSE | summer
2024-10-04 03:00 | 2024-10-04 04:00 | Winter | FALSE | summer
2024-10-04 04:00 | 2024-10-04 05:00 | Winter | FALSE | summer
2024-10-04 05:00 | 2024-10-04 06:00 | Winter | FALSE | summer
2024-10-04 06:00 | 2024-10-04 07:00 | Winter | FALSE | summer
2024-10-04 07:00 | 2024-10-04 08:00 | Winter | FALSE | summer
2024-10-04 08:00 | 2024-10-04 09:00 | Winter | FALSE | summer
2024-10-04 09:00 | 2024-10-04 10:00 | Winter | FALSE | summer
2024-10-04 10:00 | 2024-10-04 11:00 | Winter | FALSE | summer
2024-10-04 11:00 | 2024-10-04 12:00 | Winter | FALSE | summer
2024-10-04 12:00 | 2024-10-04 13:00 | Winter | FALSE | summer
2024-10-04 13:00 | 2024-10-04 14:00 | Winter | FALSE | summer
2024-10-04 14:00 | 2024-10-04 15:00 | Winter | FALSE | summer
2024-10-04 15:00 | 2024-10-04 16:00 | Winter | FALSE | summer
2024-10-04 16:00 | 2024-10-04 17:00 | Winter | TRUE | summer
2024-10-04 17:00 | 2024-10-04 18:00 | Winter | TRUE | summer
2024-10-04 18:00 | 2024-10-04 19:00 | Winter | TRUE | summer
2024-10-04 19:00 | 2024-10-04 20:00 | Winter | TRUE | summer
2024-10-04 20:00 | 2024-10-04 21:00 | Winter | TRUE | summer
2024-10-04 21:00 | 2024-10-04 22:00 | Winter | FALSE | summer
2024-10-04 22:00 | 2024-10-04 23:00 | Winter | FALSE | summer
2024-10-04 23:00 | 2024-10-05 | Winter | FALSE | summer
2024-10-05 | 2024-10-05 01:00 | Winter | FALSE | summer
2024-10-05 01:00 | 2024-10-05 02:00 | Winter | FALSE | summer
2024-10-05 02:00 | 2024-10-05 03:00 | Winter | FALSE | summer
2024-10-05 03:00 | 2024-10-05 04:00 | Winter | FALSE | summer
2024-10-05 04:00 | 2024-10-05 05:00 | Winter | FALSE | summer
2024-10-05 05:00 | 2024-10-05 06:00 | Winter | FALSE | summer
2024-10-05 06:00 | 2024-10-05 07:00 | Winter | FALSE | summer
2024-10-05 07:00 | 2024-10-05 08:00 | Winter | FALSE | summer
2024-10-05 08:00 | 2024-10-05 09:00 | Winter | FALSE | summer
2024-10-05 09:00 | 2024-10-05 10:00 | Winter | FALSE | summer
2024-10-05 10:00 | 2024-10-05 11:00 | Winter | FALSE | summer
2024-10-05 11:00 | 2024-10-05 12:00 | Winter | FALSE | summer
2024-10-05 12:00 | 2024-10-05 13:00 | Winter | FALSE | summer
2024-10-05 13:00 | 2024-10-05 14:00 | Winter | FALSE | summer
2024-10-05 14:00 | 2024-10-05 15:00 | Winter | FALSE | summer
2024-10-05 15:00 | 2024-10-05 16:00 | Winter | FALSE | summer
2024-10-05 16:00 | 2024-10-05 17:00 | Winter | TRUE | summer
2024-10-05 17:00 | 2024-10-05 18:00 | Winter | TRUE | summer
2024-10-05 18:00 | 2024-10-05 19:00 | Winter | TRUE | summer
2024-10-05 19:00 | 2024-10-05 20:00 | Winter | TRUE | summer
2024-10-05 20:00 | 2024-10-05 21:00 | Winter | TRUE | summer
2024-10-05 21:00 | 2024-10-05 22:00 | Winter | FALSE | summer
2024-10-05 22:00 | 2024-10-05 23:00 | Winter | FALSE | summer
2024-10-05 23:00 | 2024-10-06 | Winter | FALSE | summer
2024-10-06 | 2024-10-06 01:00 | Winter | FALSE | summer
2024-10-06 01:00 | 2024-10-06 02:00 | Winter | FALSE | summer
2024-10-06 02:00 | 2024-10-06 03:00 | Winter | FALSE | summer
2024-10-06 03:00 | 2024-10-06 04:00 | Winter | FALSE | summer
2024-10-06 04:00 | 2024-10-06 05:00 | Winter | FALSE | summer
2024-10-06 05:00 | 2024-10-06 06:00 | Winter | FALSE | summer
2024-10-06 06:00 | 2024-10-06 07:00 | Winter | FALSE | summer
2024-10-06 07:00 | 2024-10-06 08:00 | Winter | FALSE | summer
2024-10-06 08:00 | 2024-10-06 09:00 | Winter | FALSE | summer
2024-10-06 09:00 | 2024-10-06 10:00 | Winter | FALSE | summer
2024-10-06 10:00 | 2024-10-06 11:00 | Winter | FALSE | summer
2024-10-06 11:00 | 2024-10-06 12:00 | Winter | FALSE | summer
2024-10-06 12:00 | 2024-10-06 13:00 | Winter | FALSE | summer
2024-10-06 13:00 | 2024-10-06 14:00 | Winter | FALSE | summer
2024-10-06 14:00 | 2024-10-06 15:00 | Winter | FALSE | summer
2024-10-06 15:00 | 2024-10-06 16:00 | Winter | FALSE | summer
2024-10-06 16:00 | 2024-10-06 17:00 | Winter | TRUE | summer
2024-10-06 17:00 | 2024-10-06 18:00 | Winter | TRUE | summer
2024-10-06 18:00 | 2024-10-06 19:00 | Winter | TRUE | summer
2024-10-06 19:00 | 2024-10-06 20:00 | Winter | TRUE | summer
2024-10-06 20:00 | 2024-10-06 21:00 | Winter | TRUE | summer
2024-10-06 21:00 | 2024-10-06 22:00 | Winter | FALSE | summer
2024-10-06 22:00 | 2024-10-06 23:00 | Winter | FALSE | summer
2024-10-06 23:00 | 2024-10-07 | Winter | FALSE | summer
2024-10-07 | 2024-10-07 01:00 | Winter | FALSE | summer
2024-10-07 01:00 | 2024-10-07 02:00 | Winter | FALSE | summer
2024-10-07 02:00 | 2024-10-07 03:00 | Winter | FALSE | summer
2024-10-07 03:00 | 2024-10-07 04:00 | Winter | FALSE | summer
2024-10-07 04:00 | 2024-10-07 05:00 | Winter | FALSE | summer
2024-10-07 05:00 | 2024-10-07 06:00 | Winter | FALSE | summer
2024-10-07 06:00 | 2024-10-07 07:00 | Winter | FALSE | summer
2024-10-07 07:00 | 2024-10-07 08:00 | Winter | FALSE | summer
2024-10-07 08:00 | 2024-10-07 09:00 | Winter | FALSE | summer
2024-10-07 09:00 | 2024-10-07 10:00 | Winter | FALSE | summer
2024-10-07 10:00 | 2024-10-07 11:00 | Winter | FALSE | summer
2024-10-07 11:00 | 2024-10-07 12:00 | Winter | FALSE | summer
2024-10-07 12:00 | 2024-10-07 13:00 | Winter | FALSE | summer
2024-10-07 13:00 | 2024-10-07 14:00 | Winter | FALSE | summer
2024-10-07 14:00 | 2024-10-07 15:00 | Winter | FALSE | summer
2024-10-07 15:00 | 2024-10-07 16:00 | Winter | FALSE | summer
2024-10-07 16:00 | 2024-10-07 17:00 | Winter | TRUE | summer
2024-10-07 17:00 | 2024-10-07 18:00 | Winter | TRUE | summer
2024-10-07 18:00 | 2024-10-07 19:00 | Winter | TRUE | summer
2024-10-07 19:00 | 2024-10-07 20:00 | Winter | TRUE | summer
2024-10-07 20:00 | 2024-10-07 21:00 | Winter | TRUE | summer
2024-10-07 21:00 | 2024-10-07 22:00 | Winter | FALSE | summer
2024-10-07 22:00 | 2024-10-07 23:00 | Winter | FALSE | summer
2024-10-07 23:00 | 2024-10-08 | Winter | FALSE | summer
2024-10-08 | 2024-10-08 01:00 | Winter | FALSE | summer
2024-10-08 01:00 | 2024-10-08 02:00 | Winter | FALSE | summer
2024-10-08 02:00 | 2024-10-08 03:00 | Winter | FALSE | summer
2024-10-08 03:00 | 2024-10-08 04:00 | Winter | FALSE | summer
2024-10-08 04:00 | 2024-10-08 05:00 | Winter | FALSE | summer
2024-10-08 05:00 | 2024-10-08 06:00 | Winter | FALSE | summer
2024-10-08 06:00 | 2024-10-08 07:00 | Winter | FALSE | summer
2024-10-08 07:00 | 2024-10-08 08:00 | Winter | FALSE | summer
2024-10-08 08:00 | 2024-10-08 09:00 | Winter | FALSE | summer
2024-10-08 09:00 | 2024-10-08 10:00 | Winter | FALSE | summer
2024-10-08 10:00 | 2024-10-08 11:00 | Winter | FALSE | summer
2024-10-08 11:00 | 2024-10-08 12:00 | Winter | FALSE | summer
2024-10-08 12:00 | 2024-10-08 13:00 | Winter | FALSE | summer
2024-10-08 13:00 | 2024-10-08 14:00 | Winter | FALSE | summer
2024-10-08 14:00 | 2024-10-08 15:00 | Winter | FALSE | summer
2024-10-08 15:00 | 2024-10-08 16:00 | Winter | FALSE | summer
2024-10-08 16:00 | 2024-10-08 17:00 | Winter | TRUE | summer
2024-10-08 17:00 | 2024-10-08 18:00 | Winter | TRUE | summer
2024-10-08 18:00 | 2024-10-08 19:00 | Winter | TRUE | summer
2024-10-08 19:00 | 2024-10-08 20:00 | Winter | TRUE | summer
2024-10-08 20:00 | 2024-10-08 21:00 | Winter | TRUE | summer
2024-10-08 21:00 | 2024-10-08 22:00 | Winter | FALSE | summer
2024-10-08 22:00 | 2024-10-08 23:00 | Winter | FALSE | summer
2024-10-08 23:00 | 2024-10-09 | Winter | FALSE | summer
2024-10-09 | 2024-10-09 01:00 | Winter | FALSE | summer
2024-10-09 01:00 | 2024-10-09 02:00 | Winter | FALSE | summer
2024-10-09 02:00 | 2024-10-09 03:00 | Winter | FALSE | summer
2024-10-09 03:00 | 2024-10-09 04:00 | Winter | FALSE | summer
2024-10-09 04:00 | 2024-10-09 05:00 | Winter | FALSE | summer
2024-10-09 05:00 | 2024-10-09 06:00 | Winter | FALSE | summer
2024-10-09 06:00 | 2024-10-09 07:00 | Winter | FALSE | summer
2024-10-09 07:00 | 2024-10-09 08:00 | Winter | FALSE | summer
2024-10-09 08:00 | 2024-10-09 09:00 | Winter | FALSE | summer
2024-10-09 09:00 | 2024-10-09 10:00 | Winter | FALSE | summer
2024-10-09 10:00 | 2024-10-09 11:00 | Winter | FALSE | summer
2024-10-09 11:00 | 2024-10-09 12:00 | Winter | FALSE | summer
2024-10-09 12:00 | 2024-10-09 13:00 | Winter | FALSE | summer
2024-10-09 13:00 | 2024-10-09 14:00 | Winter | FALSE | summer
2024-10-09 14:00 | 2024-10-09 15:00 | Winter | FALSE | summer
2024-10-09 15:00 | 2024-10-09 16:00 | Winter | FALSE | summer
2024-10-09 16:00 | 2024-10-09 17:00 | Winter | TRUE | summer
2024-10-09 17:00 | 2024-10-09 18:00 | Winter | TRUE | summer
2024-10-09 18:00 | 2024-10-09 19:00 | Winter | TRUE | summer
2024-10-09 19:00 | 2024-10-09 20:00 | Winter | TRUE | summer
2024-10-09 20:00 | 2024-10-09 21:00 | Winter | TRUE | summer
2024-10-09 21:00 | 2024-10-09 22:00 | Winter | FALSE | summer
2024-10-09 22:00 | 2024-10-09 23:00 | Winter | FALSE | summer
2024-10-09 23:00 | 2024-10-10 | Winter | FALSE | summer
2024-10-10 | 2024-10-10 01:00 | Winter | FALSE | summer
2024-10-10 01:00 | 2024-10-10 02:00 | Winter | FALSE | summer
2024-10-10 02:00 | 2024-10-10 03:00 | Winter | FALSE | summer
2024-10-10 03:00 | 2024-10-10 04:00 | Winter | FALSE | summer
2024-10-10 04:00 | 2024-10-10 05:00 | Winter | FALSE | summer
2024-10-10 05:00 | 2024-10-10 06:00 | Winter | FALSE | summer
2024-10-10 06:00 | 2024-10-10 07:00 | Winter | FALSE | summer
2024-10-10 07:00 | 2024-10-10 08:00 | Winter | FALSE | summer
2024-10-10 08:00 | 2024-10-10 09:00 | Winter | FALSE | summer
2024-10-10 09:00 | 2024-10-10 10:00 | Winter | FALSE | summer
2024-10-10 10:00 | 2024-10-10 11:00 | Winter | FALSE | summer
2024-10-10 11:00 | 2024-10-10 12:00 | Winter | FALSE | summer
2024-10-10 12:00 | 2024-10-10 13:00 | Winter | FALSE | summer
2024-10-10 13:00 | 2024-10-10 14:00 | Winter | FALSE | summer
2024-10-10 14:00 | 2024-10-10 15:00 | Winter | FALSE | summer
2024-10-10 15:00 | 2024-10-10 16:00 | Winter | FALSE | summer
2024-10-10 16:00 | 2024-10-10 17:00 | Winter | TRUE | summer
2024-10-10 17:00 | 2024-10-10 18:00 | Winter | TRUE | summer
2024-10-10 18:00 | 2024-10-10 19:00 | Winter | TRUE | summer
2024-10-10 19:00 | 2024-10-10 20:00 | Winter | TRUE | summer
2024-10-10 20:00 | 2024-10-10 21:00 | Winter | TRUE | summer
2024-10-10 21:00 | 2024-10-10 22:00 | Winter | FALSE | summer
2024-10-10 22:00 | 2024-10-10 23:00 | Winter | FALSE | summer
2024-10-10 23:00 | 2024-10-11 | Winter | FALSE | summer
2024-10-11 | 2024-10-11 01:00 | Winter | FALSE | summer
2024-10-11 01:00 | 2024-10-11 02:00 | Winter | FALSE | summer
2024-10-11 02:00 | 2024-10-11 03:00 | Winter | FALSE | summer
2024-10-11 03:00 | 2024-10-11 04:00 | Winter | FALSE | summer
2024-10-11 04:00 | 2024-10-11 05:00 | Winter | FALSE | summer
2024-10-11 05:00 | 2024-10-11 06:00 | Winter | FALSE | summer
2024-10-11 06:00 | 2024-10-11 07:00 | Winter | FALSE | summer
2024-10-11 07:00 | 2024-10-11 08:00 | Winter | FALSE | summer
2024-10-11 08:00 | 2024-10-11 09:00 | Winter | FALSE | summer
2024-10-11 09:00 | 2024-10-11 10:00 | Winter | FALSE | summer
2024-10-11 10:00 | 2024-10-11 11:00 | Winter | FALSE | summer
2024-10-11 11:00 | 2024-10-11 12:00 | Winter | FALSE | summer
2024-10-11 12:00 | 2024-10-11 13:00 | Winter | FALSE | summer
2024-10-11 13:00 | 2024-10-11 14:00 | Winter | FALSE | summer
2024-10-11 14:00 | 2024-10-11 15:00 | Winter | FALSE | summer
2024-10-11 15:00 | 2024-10-11 16:00 | Winter | FALSE | summer
2024-10-11 16:00 | 2024-10-11 17:00 | Winter | TRUE | summer
2024-10-11 17:00 | 2024-10-11 18:00 | Winter | TRUE | summer
2024-10-11 18:00 | 2024-10-11 19:00 | Winter | TRUE | summer
2024-10-11 19:00 | 2024-10-11 20:00 | Winter | TRUE | summer
2024-10-11 20:00 | 2024-10-11 21:00 | Winter | TRUE | summer
2024-10-11 21:00 | 2024-10-11 22:00 | Winter | FALSE | summer
2024-10-11 22:00 | 2024-10-11 23:00 | Winter | FALSE | summer
2024-10-11 23:00 | 2024-10-12 | Winter | FALSE | summer
2024-10-12 | 2024-10-12 01:00 | Winter | FALSE | summer
2024-10-12 01:00 | 2024-10-12 02:00 | Winter | FALSE | summer
2024-10-12 02:00 | 2024-10-12 03:00 | Winter | FALSE | summer
2024-10-12 03:00 | 2024-10-12 04:00 | Winter | FALSE | summer
2024-10-12 04:00 | 2024-10-12 05:00 | Winter | FALSE | summer
2024-10-12 05:00 | 2024-10-12 06:00 | Winter | FALSE | summer
2024-10-12 06:00 | 2024-10-12 07:00 | Winter | FALSE | summer
2024-10-12 07:00 | 2024-10-12 08:00 | Winter | FALSE | summer
2024-10-12 08:00 | 2024-10-12 09:00 | Winter | FALSE | summer
2024-10-12 09:00 | 2024-10-12 10:00 | Winter | FALSE | summer
2024-10-12 10:00 | 2024-10-12 11:00 | Winter | FALSE | summer
2024-10-12 11:00 | 2024-10-12 12:00 | Winter | FALSE | summer
2024-10-12 12:00 | 2024-10-12 13:00 | Winter | FALSE | summer
2024-10-12 13:00 | 2024-10-12 14:00 | Winter | FALSE | summer
2024-10-12 14:00 | 2024-10-12 15:00 | Winter | FALSE | summer
2024-10-12 15:00 | 2024-10-12 16:00 | Winter | FALSE | summer
2024-10-12 16:00 | 2024-10-12 17:00 | Winter | TRUE | summer
2024-10-12 17:00 | 2024-10-12 18:00 | Winter | TRUE | summer
2024-10-12 18:00 | 2024-10-12 19:00 | Winter | TRUE | summer
2024-10-12 19:00 | 2024-10-12 20:00 | Winter | TRUE | summer
2024-10-12 20:00 | 2024-10-12 21:00 | Winter | TRUE | summer
2024-10-12 21:00 | 2024-10-12 22:00 | Winter | FALSE | summer
2024-10-12 22:00 | 2024-10-12 23:00 | Winter | FALSE | summer
2024-10-12 23:00 | 2024-10-13 | Winter | FALSE | summer
2024-10-13 | 2024-10-13 01:00 | Winter | FALSE | summer
2024-10-13 01:00 | 2024-10-13 02:00 | Winter | FALSE | summer
2024-10-13 02:00 | 2024-10-13 03:00 | Winter | FALSE | summer
2024-10-13 03:00 | 2024-10-13 04:00 | Winter | FALSE | summer
2024-10-13 04:00 | 2024-10-13 05:00 | Winter | FALSE | summer
2024-10-13 05:00 | 2024-10-13 06:00 | Winter | FALSE | summer
2024-10-13 06:00 | 2024-10-13 07:00 | Winter | FALSE | summer
2024-10-13 07:00 | 2024-10-13 08:00 | Winter | FALSE | summer
2024-10-13 08:00 | 2024-10-13 09:00 | Winter | FALSE | summer
2024-10-13 09:00 | 2024-10-13 10:00 | Winter | FALSE | summer
2024-10-13 10:00 | 2024-10-13 11:00 | Winter | FALSE | summer
2024-10-13 11:00 | 2024-10-13 12:00 | Winter | FALSE | summer
2024-10-13 12:00 | 2024-10-13 13:00 | Winter | FALSE | summer
2024-10-13 13:00 | 2024-10-13 14:00 | Winter | FALSE | summer
2024-10-13 14:00 | 2024-10-13 15:00 | Winter | FALSE | summer
2024-10-13 15:00 | 2024-10-13 16:00 | Winter | FALSE | summer
2024-10-13 16:00 | 2024-10-13 17:00 | Winter | TRUE | summer
2024-10-13 17:00 | 2024-10-13 18:00 | Winter | TRUE | summer
2024-10-13 18:00 | 2024-10-13 19:00 | Winter | TRUE | summer
2024-10-13 19:00 | 2024-10-13 20:00 | Winter | TRUE | summer
2024-10-13 20:00 | 2024-10-13 21:00 | Winter | TRUE | summer
2024-10-13 21:00 | 2024-10-13 22:00 | Winter | FALSE | summer
2024-10-13 22:00 | 2024-10-13 23:00 | Winter | FALSE | summer
2024-10-13 23:00 | 2024-10-14 | Winter | FALSE | summer
2024-10-14 | 2024-10-14 01:00 | Winter | FALSE | summer
2024-10-14 01:00 | 2024-10-14 02:00 | Winter | FALSE | summer
2024-10-14 02:00 | 2024-10-14 03:00 | Winter | FALSE | summer
2024-10-14 03:00 | 2024-10-14 04:00 | Winter | FALSE | summer
2024-10-14 04:00 | 2024-10-14 05:00 | Winter | FALSE | summer
2024-10-14 05:00 | 2024-10-14 06:00 | Winter | FALSE | summer
2024-10-14 06:00 | 2024-10-14 07:00 | Winter | FALSE | summer
2024-10-14 07:00 | 2024-10-14 08:00 | Winter | FALSE | summer
2024-10-14 08:00 | 2024-10-14 09:00 | Winter | FALSE | summer
2024-10-14 09:00 | 2024-10-14 10:00 | Winter | FALSE | summer
2024-10-14 10:00 | 2024-10-14 11:00 | Winter | FALSE | summer
2024-10-14 11:00 | 2024-10-14 12:00 | Winter | FALSE | summer
2024-10-14 12:00 | 2024-10-14 13:00 | Winter | FALSE | summer
2024-10-14 13:00 | 2024-10-14 14:00 | Winter | FALSE | summer
2024-10-14 14:00 | 2024-10-14 15:00 | Winter | FALSE | summer
2024-10-14 15:00 | 2024-10-14 16:00 | Winter | FALSE | summer
2024-10-14 16:00 | 2024-10-14 17:00 | Winter | TRUE | summer
2024-10-14 17:00 | 2024-10-14 18:00 | Winter | TRUE | summer
2024-10-14 18:00 | 2024-10-14 19:00 | Winter | TRUE | summer
2024-10-14 19:00 | 2024-10-14 20:00 | Winter | TRUE | summer
2024-10-14 20:00 | 2024-10-14 21:00 | Winter | TRUE | summer
2024-10-14 21:00 | 2024-10-14 22:00 | Winter | FALSE | summer
2024-10-14 22:00 | 2024-10-14 23:00 | Winter | FALSE | summer
2024-10-14 23:00 | 2024-10-15 | Winter | FALSE | summer
2024-10-15 | 2024-10-15 01:00 | Winter | FALSE | summer
2024-10-15 01:00 | 2024-10-15 02:00 | Winter | FALSE | summer
2024-10-15 02:00 | 2024-10-15 03:00 | Winter | FALSE | summer
2024-10-15 03:00 | 2024-10-15 04:00 | Winter | FALSE | summer
2024-10-15 04:00 | 2024-10-15 05:00 | Winter | FALSE | summer
2024-10-15 05:00 | 2024-10-15 06:00 | Winter | FALSE | summer
2024-10-15 06:00 | 2024-10-15 07:00 | Winter | FALSE | summer
2024-10-15 07:00 | 2024-10-15 08:00 | Winter | FALSE | summer
2024-10-15 08:00 | 2024-10-15 09:00 | Winter | FALSE | summer
2024-10-15 09:00 | 2024-10-15 10:00 | Winter | FALSE | summer
2024-10-15 10:00 | 2024-10-15 11:00 | Winter | FALSE | summer
2024-10-15 11:00 | 2024-10-15 12:00 | Winter | FALSE | summer
2024-10-15 12:00 | 2024-10-15 13:00 | Winter | FALSE | summer
2024-10-15 13:00 | 2024-10-15 14:00 | Winter | FALSE | summer
2024-10-15 14:00 | 2024-10-15 15:00 | Winter | FALSE | summer
2024-10-15 15:00 | 2024-10-15 16:00 | Winter | FALSE | summer
2024-10-15 16:00 | 2024-10-15 17:00 | Winter | TRUE | summer
2024-10-15 17:00 | 2024-10-15 18:00 | Winter | TRUE | summer
2024-10-15 18:00 | 2024-10-15 19:00 | Winter | TRUE | summer
2024-10-15 19:00 | 2024-10-15 20:00 | Winter | TRUE | summer
2024-10-15 20:00 | 2024-10-15 21:00 | Winter | TRUE | summer
2024-10-15 21:00 | 2024-10-15 22:00 | Winter | FALSE | summer
2024-10-15 22:00 | 2024-10-15 23:00 | Winter | FALSE | summer
2024-10-15 23:00 | 2024-10-16 | Winter | FALSE | summer
2024-10-16 | 2024-10-16 01:00 | Winter | FALSE | summer
2024-10-16 01:00 | 2024-10-16 02:00 | Winter | FALSE | summer
2024-10-16 02:00 | 2024-10-16 03:00 | Winter | FALSE | summer
2024-10-16 03:00 | 2024-10-16 04:00 | Winter | FALSE | summer
2024-10-16 04:00 | 2024-10-16 05:00 | Winter | FALSE | summer
2024-10-16 05:00 | 2024-10-16 06:00 | Winter | FALSE | summer
2024-10-16 06:00 | 2024-10-16 07:00 | Winter | FALSE | summer
2024-10-16 07:00 | 2024-10-16 08:00 | Winter | FALSE | summer
2024-10-16 08:00 | 2024-10-16 09:00 | Winter | FALSE | summer
2024-10-16 09:00 | 2024-10-16 10:00 | Winter | FALSE | summer
2024-10-16 10:00 | 2024-10-16 11:00 | Winter | FALSE | summer
2024-10-16 11:00 | 2024-10-16 12:00 | Winter | FALSE | summer
2024-10-16 12:00 | 2024-10-16 13:00 | Winter | FALSE | summer
2024-10-16 13:00 | 2024-10-16 14:00 | Winter | FALSE | summer
2024-10-16 14:00 | 2024-10-16 15:00 | Winter | FALSE | summer
2024-10-16 15:00 | 2024-10-16 16:00 | Winter | FALSE | summer
2024-10-16 16:00 | 2024-10-16 17:00 | Winter | TRUE | summer
2024-10-16 17:00 | 2024-10-16 18:00 | Winter | TRUE | summer
2024-10-16 18:00 | 2024-10-16 19:00 | Winter | TRUE | summer
2024-10-16 19:00 | 2024-10-16 20:00 | Winter | TRUE | summer
2024-10-16 20:00 | 2024-10-16 21:00 | Winter | TRUE | summer
2024-10-16 21:00 | 2024-10-16 22:00 | Winter | FALSE | summer
2024-10-16 22:00 | 2024-10-16 23:00 | Winter | FALSE | summer
2024-10-16 23:00 | 2024-10-17 | Winter | FALSE | summer
2024-10-17 | 2024-10-17 01:00 | Winter | FALSE | summer
2024-10-17 01:00 | 2024-10-17 02:00 | Winter | FALSE | summer
2024-10-17 02:00 | 2024-10-17 03:00 | Winter | FALSE | summer
2024-10-17 03:00 | 2024-10-17 04:00 | Winter | FALSE | summer
2024-10-17 04:00 | 2024-10-17 05:00 | Winter | FALSE | summer
2024-10-17 05:00 | 2024-10-17 06:00 | Winter | FALSE | summer
2024-10-17 06:00 | 2024-10-17 07:00 | Winter | FALSE | summer
2024-10-17 07:00 | 2024-10-17 08:00 | Winter | FALSE | summer
2024-10-17 08:00 | 2024-10-17 09:00 | Winter | FALSE | summer
2024-10-17 09:00 | 2024-10-17 10:00 | Winter | FALSE | summer
2024-10-17 10:00 | 2024-10-17 11:00 | Winter | FALSE | summer
2024-10-17 11:00 | 2024-10-17 12:00 | Winter | FALSE | summer
2024-10-17 12:00 | 2024-10-17 13:00 | Winter | FALSE | summer
2024-10-17 13:00 | 2024-10-17 14:00 | Winter | FALSE | summer
2024-10-17 14:00 | 2024-10-17 15:00 | Winter | FALSE | summer
2024-10-17 15:00 | 2024-10-17 16:00 | Winter | FALSE | summer
2024-10-17 16:00 | 2024-10-17 17:00 | Winter | TRUE | summer
2024-10-17 17:00 | 2024-10-17 18:00 | Winter | TRUE | summer
2024-10-17 18:00 | 2024-10-17 19:00 | Winter | TRUE | summer
2024-10-17 19:00 | 2024-10-17 20:00 | Winter | TRUE | summer
2024-10-17 20:00 | 2024-10-17 21:00 | Winter | TRUE | summer
2024-10-17 21:00 | 2024-10-17 22:00 | Winter | FALSE | summer
2024-10-17 22:00 | 2024-10-17 23:00 | Winter | FALSE | summer
2024-10-17 23:00 | 2024-10-18 | Winter | FALSE | summer
2024-10-18 | 2024-10-18 01:00 | Winter | FALSE | summer
2024-10-18 01:00 | 2024-10-18 02:00 | Winter | FALSE | summer
2024-10-18 02:00 | 2024-10-18 03:00 | Winter | FALSE | summer
2024-10-18 03:00 | 2024-10-18 04:00 | Winter | FALSE | summer
2024-10-18 04:00 | 2024-10-18 05:00 | Winter | FALSE | summer
2024-10-18 05:00 | 2024-10-18 06:00 | Winter | FALSE | summer
2024-10-18 06:00 | 2024-10-18 07:00 | Winter | FALSE | summer
2024-10-18 07:00 | 2024-10-18 08:00 | Winter | FALSE | summer
2024-10-18 08:00 | 2024-10-18 09:00 | Winter | FALSE | summer
2024-10-18 09:00 | 2024-10-18 10:00 | Winter | FALSE | summer
2024-10-18 10:00 | 2024-10-18 11:00 | Winter | FALSE | summer
2024-10-18 11:00 | 2024-10-18 12:00 | Winter | FALSE | summer
2024-10-18 12:00 | 2024-10-18 13:00 | Winter | FALSE | summer
2024-10-18 13:00 | 2024-10-18 14:00 | Winter | FALSE | summer
2024-10-18 14:00 | 2024-10-18 15:00 | Winter | FALSE | summer
2024-10-18 15:00 | 2024-10-18 16:00 | Winter | FALSE | summer
2024-10-18 16:00 | 2024-10-18 17:00 | Winter | TRUE | summer
2024-10-18 17:00 | 2024-10-18 18:00 | Winter | TRUE | summer
2024-10-18 18:00 | 2024-10-18 19:00 | Winter | TRUE | summer
2024-10-18 19:00 | 2024-10-18 20:00 | Winter | TRUE | summer
2024-10-18 20:00 | 2024-10-18 21:00 | Winter | TRUE | summer
2024-10-18 21:00 | 2024-10-18 22:00 | Winter | FALSE | summer
2024-10-18 22:00 | 2024-10-18 23:00 | Winter | FALSE | summer
2024-10-18 23:00 | 2024-10-19 | Winter | FALSE | summer
2024-10-19 | 2024-10-19 01:00 | Winter | FALSE | summer
2024-10-19 01:00 | 2024-10-19 02:00 | Winter | FALSE | summer
2024-10-19 02:00 | 2024-10-19 03:00 | Winter | FALSE | summer
2024-10-19 03:00 | 2024-10-19 04:00 | Winter | FALSE | summer
2024-10-19 04:00 | 2024-10-19 05:00 | Winter | FALSE | summer
2024-10-19 05:00 | 2024-10-19 06:00 | Winter | FALSE | summer
2024-10-19 06:00 | 2024-10-19 07:00 | Winter | FALSE | summer
2024-10-19 07:00 | 2024-10-19 08:00 | Winter | FALSE | summer
2024-10-19 08:00 | 2024-10-19 09:00 | Winter | FALSE | summer
2024-10-19 09:00 | 2024-10-19 10:00 | Winter | FALSE | summer
2024-10-19 10:00 | 2024-10-19 11:00 | Winter | FALSE | summer
2024-10-19 11:00 | 2024-10-19 12:00 | Winter | FALSE | summer
2024-10-19 12:00 | 2024-10-19 13:00 | Winter | FALSE | summer
2024-10-19 13:00 | 2024-10-19 14:00 | Winter | FALSE | summer
2024-10-19 14:00 | 2024-10-19 15:00 | Winter | FALSE | summer
2024-10-19 15:00 | 2024-10-19 16:00 | Winter | FALSE | summer
2024-10-19 16:00 | 2024-10-19 17:00 | Winter | TRUE | summer
2024-10-19 17:00 | 2024-10-19 18:00 | Winter | TRUE | summer
2024-10-19 18:00 | 2024-10-19 19:00 | Winter | TRUE | summer
2024-10-19 19:00 | 2024-10-19 20:00 | Winter | TRUE | summer
2024-10-19 20:00 | 2024-10-19 21:00 | Winter | TRUE | summer
2024-10-19 21:00 | 2024-10-19 22:00 | Winter | FALSE | summer
2024-10-19 22:00 | 2024-10-19 23:00 | Winter | FALSE | summer
2024-10-19 23:00 | 2024-10-20 | Winter | FALSE | summer
2024-10-20 | 2024-10-20 01:00 | Winter | FALSE | summer
2024-10-20 01:00 | 2024-10-20 02:00 | Winter | FALSE | summer
2024-10-20 02:00 | 2024-10-20 03:00 | Winter | FALSE | summer
2024-10-20 03:00 | 2024-10-20 04:00 | Winter | FALSE | summer
2024-10-20 04:00 | 2024-10-20 05:00 | Winter | FALSE | summer
2024-10-20 05:00 | 2024-10-20 06:00 | Winter | FALSE | summer
2024-10-20 06:00 | 2024-10-20 07:00 | Winter | FALSE | summer
2024-10-20 07:00 | 2024-10-20 08:00 | Winter | FALSE | summer
2024-10-20 08:00 | 2024-10-20 09:00 | Winter | FALSE | summer
2024-10-20 09:00 | 2024-10-20 10:00 | Winter | FALSE | summer
2024-10-20 10:00 | 2024-10-20 11:00 | Winter | FALSE | summer
2024-10-20 11:00 | 2024-10-20 12:00 | Winter | FALSE | summer
2024-10-20 12:00 | 2024-10-20 13:00 | Winter | FALSE | summer
2024-10-20 13:00 | 2024-10-20 14:00 | Winter | FALSE | summer
2024-10-20 14:00 | 2024-10-20 15:00 | Winter | FALSE | summer
2024-10-20 15:00 | 2024-10-20 16:00 | Winter | FALSE | summer
2024-10-20 16:00 | 2024-10-20 17:00 | Winter | TRUE | summer
2024-10-20 17:00 | 2024-10-20 18:00 | Winter | TRUE | summer
2024-10-20 18:00 | 2024-10-20 19:00 | Winter | TRUE | summer
2024-10-20 19:00 | 2024-10-20 20:00 | Winter | TRUE | summer
2024-10-20 20:00 | 2024-10-20 21:00 | Winter | TRUE | summer
2024-10-20 21:00 | 2024-10-20 22:00 | Winter | FALSE | summer
2024-10-20 22:00 | 2024-10-20 23:00 | Winter | FALSE | summer
2024-10-20 23:00 | 2024-10-21 | Winter | FALSE | summer
2024-10-21 | 2024-10-21 01:00 | Winter | FALSE | summer
2024-10-21 01:00 | 2024-10-21 02:00 | Winter | FALSE | summer
2024-10-21 02:00 | 2024-10-21 03:00 | Winter | FALSE | summer
2024-10-21 03:00 | 2024-10-21 04:00 | Winter | FALSE | summer
2024-10-21 04:00 | 2024-10-21 05:00 | Winter | FALSE | summer
2024-10-21 05:00 | 2024-10-21 06:00 | Winter | FALSE | summer
2024-10-21 06:00 | 2024-10-21 07:00 | Winter | FALSE | summer
2024-10-21 07:00 | 2024-10-21 08:00 | Winter | FALSE | summer
2024-10-21 08:00 | 2024-10-21 09:00 | Winter | FALSE | summer
2024-10-21 09:00 | 2024-10-21 10:00 | Winter | FALSE | summer
2024-10-21 10:00 | 2024-10-21 11:00 | Winter | FALSE | summer
2024-10-21 11:00 | 2024-10-21 12:00 | Winter | FALSE | summer
2024-10-21 12:00 | 2024-10-21 13:00 | Winter | FALSE | summer
2024-10-21 13:00 | 2024-10-21 14:00 | Winter | FALSE | summer
2024-10-21 14:00 | 2024-10-21 15:00 | Winter | FALSE | summer
2024-10-21 15:00 | 2024-10-21 16:00 | Winter | FALSE | summer
2024-10-21 16:00 | 2024-10-21 17:00 | Winter | TRUE | summer
2024-10-21 17:00 | 2024-10-21 18:00 | Winter | TRUE | summer
2024-10-21 18:00 | 2024-10-21 19:00 | Winter | TRUE | summer
2024-10-21 19:00 | 2024-10-21 20:00 | Winter | TRUE | summer
2024-10-21 20:00 | 2024-10-21 21:00 | Winter | TRUE | summer
2024-10-21 21:00 | 2024-10-21 22:00 | Winter | FALSE | summer
2024-10-21 22:00 | 2024-10-21 23:00 | Winter | FALSE | summer
2024-10-21 23:00 | 2024-10-22 | Winter | FALSE | summer
2024-10-22 | 2024-10-22 01:00 | Winter | FALSE | summer
2024-10-22 01:00 | 2024-10-22 02:00 | Winter | FALSE | summer
2024-10-22 02:00 | 2024-10-22 03:00 | Winter | FALSE | summer
2024-10-22 03:00 | 2024-10-22 04:00 | Winter | FALSE | summer
2024-10-22 04:00 | 2024-10-22 05:00 | Winter | FALSE | summer
2024-10-22 05:00 | 2024-10-22 06:00 | Winter | FALSE | summer
2024-10-22 06:00 | 2024-10-22 07:00 | Winter | FALSE | summer
2024-10-22 07:00 | 2024-10-22 08:00 | Winter | FALSE | summer
2024-10-22 08:00 | 2024-10-22 09:00 | Winter | FALSE | summer
2024-10-22 09:00 | 2024-10-22 10:00 | Winter | FALSE | summer
2024-10-22 10:00 | 2024-10-22 11:00 | Winter | FALSE | summer
2024-10-22 11:00 | 2024-10-22 12:00 | Winter | FALSE | summer
2024-10-22 12:00 | 2024-10-22 13:00 | Winter | FALSE | summer
2024-10-22 13:00 | 2024-10-22 14:00 | Winter | FALSE | summer
2024-10-22 14:00 | 2024-10-22 15:00 | Winter | FALSE | summer
2024-10-22 15:00 | 2024-10-22 16:00 | Winter | FALSE | summer
2024-10-22 16:00 | 2024-10-22 17:00 | Winter | TRUE | summer
2024-10-22 17:00 | 2024-10-22 18:00 | Winter | TRUE | summer
2024-10-22 18:00 | 2024-10-22 19:00 | Winter | TRUE | summer
2024-10-22 19:00 | 2024-10-22 20:00 | Winter | TRUE | summer
2024-10-22 20:00 | 2024-10-22 21:00 | Winter | TRUE | summer
2024-10-22 21:00 | 2024-10-22 22:00 | Winter | FALSE | summer
2024-10-22 22:00 | 2024-10-22 23:00 | Winter | FALSE | summer
2024-10-22 23:00 | 2024-10-23 | Winter | FALSE | summer
2024-10-23 | 2024-10-23 01:00 | Winter | FALSE | summer
2024-10-23 01:00 | 2024-10-23 02:00 | Winter | FALSE | summer
2024-10-23 02:00 | 2024-10-23 03:00 | Winter | FALSE | summer
2024-10-23 03:00 | 2024-10-23 04:00 | Winter | FALSE | summer
2024-10-23 04:00 | 2024-10-23 05:00 | Winter | FALSE | summer
2024-10-23 05:00 | 2024-10-23 06:00 | Winter | FALSE | summer
2024-10-23 06:00 | 2024-10-23 07:00 | Winter | FALSE | summer
2024-10-23 07:00 | 2024-10-23 08:00 | Winter | FALSE | summer
2024-10-23 08:00 | 2024-10-23 09:00 | Winter | FALSE | summer
2024-10-23 09:00 | 2024-10-23 10:00 | Winter | FALSE | summer
2024-10-23 10:00 | 2024-10-23 11:00 | Winter | FALSE | summer
2024-10-23 11:00 | 2024-10-23 12:00 | Winter | FALSE | summer
2024-10-23 12:00 | 2024-10-23 13:00 | Winter | FALSE | summer
2024-10-23 13:00 | 2024-10-23 14:00 | Winter | FALSE | summer
2024-10-23 14:00 | 2024-10-23 15:00 | Winter | FALSE | summer
2024-10-23 15:00 | 2024-10-23 16:00 | Winter | FALSE | summer
2024-10-23 16:00 | 2024-10-23 17:00 | Winter | TRUE | summer
2024-10-23 17:00 | 2024-10-23 18:00 | Winter | TRUE | summer
2024-10-23 18:00 | 2024-10-23 19:00 | Winter | TRUE | summer
2024-10-23 19:00 | 2024-10-23 20:00 | Winter | TRUE | summer
2024-10-23 20:00 | 2024-10-23 21:00 | Winter | TRUE | summer
2024-10-23 21:00 | 2024-10-23 22:00 | Winter | FALSE | summer
2024-10-23 22:00 | 2024-10-23 23:00 | Winter | FALSE | summer
2024-10-23 23:00 | 2024-10-24 | Winter | FALSE | summer
2024-10-24 | 2024-10-24 01:00 | Winter | FALSE | summer
2024-10-24 01:00 | 2024-10-24 02:00 | Winter | FALSE | summer
2024-10-24 02:00 | 2024-10-24 03:00 | Winter | FALSE | summer
2024-10-24 03:00 | 2024-10-24 04:00 | Winter | FALSE | summer
2024-10-24 04:00 | 2024-10-24 05:00 | Winter | FALSE | summer
2024-10-24 05:00 | 2024-10-24 06:00 | Winter | FALSE | summer
2024-10-24 06:00 | 2024-10-24 07:00 | Winter | FALSE | summer
2024-10-24 07:00 | 2024-10-24 08:00 | Winter | FALSE | summer
2024-10-24 08:00 | 2024-10-24 09:00 | Winter | FALSE | summer
2024-10-24 09:00 | 2024-10-24 10:00 | Winter | FALSE | summer
2024-10-24 10:00 | 2024-10-24 11:00 | Winter | FALSE | summer
2024-10-24 11:00 | 2024-10-24 12:00 | Winter | FALSE | summer
2024-10-24 12:00 | 2024-10-24 13:00 | Winter | FALSE | summer
2024-10-24 13:00 | 2024-10-24 14:00 | Winter | FALSE | summer
2024-10-24 14:00 | 2024-10-24 15:00 | Winter | FALSE | summer
2024-10-24 15:00 | 2024-10-24 16:00 | Winter | FALSE | summer
2024-10-24 16:00 | 2024-10-24 17:00 | Winter | TRUE | summer
2024-10-24 17:00 | 2024-10-24 18:00 | Winter | TRUE | summer
2024-10-24 18:00 | 2024-10-24 19:00 | Winter | TRUE | summer
2024-10-24 19:00 | 2024-10-24 20:00 | Winter | TRUE | summer
2024-10-24 20:00 | 2024-10-24 21:00 | Winter | TRUE | summer
2024-10-24 21:00 | 2024-10-24 22:00 | Winter | FALSE | summer
2024-10-24 22:00 | 2024-10-24 23:00 | Winter | FALSE | summer
2024-10-24 23:00 | 2024-10-25 | Winter | FALSE | summer
2024-10-25 | 2024-10-25 01:00 | Winter | FALSE | summer
2024-10-25 01:00 | 2024-10-25 02:00 | Winter | FALSE | summer
2024-10-25 02:00 | 2024-10-25 03:00 | Winter | FALSE | summer
2024-10-25 03:00 | 2024-10-25 04:00 | Winter | FALSE | summer
2024-10-25 04:00 | 2024-10-25 05:00 | Winter | FALSE | summer
2024-10-25 05:00 | 2024-10-25 06:00 | Winter | FALSE | summer
2024-10-25 06:00 | 2024-10-25 07:00 | Winter | FALSE | summer
2024-10-25 07:00 | 2024-10-25 08:00 | Winter | FALSE | summer
2024-10-25 08:00 | 2024-10-25 09:00 | Winter | FALSE | summer
2024-10-25 09:00 | 2024-10-25 10:00 | Winter | FALSE | summer
2024-10-25 10:00 | 2024-10-25 11:00 | Winter | FALSE | summer
2024-10-25 11:00 | 2024-10-25 12:00 | Winter | FALSE | summer
2024-10-25 12:00 | 2024-10-25 13:00 | Winter | FALSE | summer
2024-10-25 13:00 | 2024-10-25 14:00 | Winter | FALSE | summer
2024-10-25 14:00 | 2024-10-25 15:00 | Winter | FALSE | summer
2024-10-25 15:00 | 2024-10-25 16:00 | Winter | FALSE | summer
2024-10-25 16:00 | 2024-10-25 17:00 | Winter | TRUE | summer
2024-10-25 17:00 | 2024-10-25 18:00 | Winter | TRUE | summer
2024-10-25 18:00 | 2024-10-25 19:00 | Winter | TRUE | summer
2024-10-25 19:00 | 2024-10-25 20:00 | Winter | TRUE | summer
2024-10-25 20:00 | 2024-10-25 21:00 | Winter | TRUE | summer
2024-10-25 21:00 | 2024-10-25 22:00 | Winter | FALSE | summer
2024-10-25 22:00 | 2024-10-25 23:00 | Winter | FALSE | summer
2024-10-25 23:00 | 2024-10-26 | Winter | FALSE | summer
2024-10-26 | 2024-10-26 01:00 | Winter | FALSE | summer
2024-10-26 01:00 | 2024-10-26 02:00 | Winter | FALSE | summer
2024-10-26 02:00 | 2024-10-26 03:00 | Winter | FALSE | summer
2024-10-26 03:00 | 2024-10-26 04:00 | Winter | FALSE | summer
2024-10-26 04:00 | 2024-10-26 05:00 | Winter | FALSE | summer
2024-10-26 05:00 | 2024-10-26 06:00 | Winter | FALSE | summer
2024-10-26 06:00 | 2024-10-26 07:00 | Winter | FALSE | summer
2024-10-26 07:00 | 2024-10-26 08:00 | Winter | FALSE | summer
2024-10-26 08:00 | 2024-10-26 09:00 | Winter | FALSE | summer
2024-10-26 09:00 | 2024-10-26 10:00 | Winter | FALSE | summer
2024-10-26 10:00 | 2024-10-26 11:00 | Winter | FALSE | summer
2024-10-26 11:00 | 2024-10-26 12:00 | Winter | FALSE | summer
2024-10-26 12:00 | 2024-10-26 13:00 | Winter | FALSE | summer
2024-10-26 13:00 | 2024-10-26 14:00 | Winter | FALSE | summer
2024-10-26 14:00 | 2024-10-26 15:00 | Winter | FALSE | summer
2024-10-26 15:00 | 2024-10-26 16:00 | Winter | FALSE | summer
2024-10-26 16:00 | 2024-10-26 17:00 | Winter | TRUE | summer
2024-10-26 17:00 | 2024-10-26 18:00 | Winter | TRUE | summer
2024-10-26 18:00 | 2024-10-26 19:00 | Winter | TRUE | summer
2024-10-26 19:00 | 2024-10-26 20:00 | Winter | TRUE | summer
2024-10-26 20:00 | 2024-10-26 21:00 | Winter | TRUE | summer
2024-10-26 21:00 | 2024-10-26 22:00 | Winter | FALSE | summer
2024-10-26 22:00 | 2024-10-26 23:00 | Winter | FALSE | summer
2024-10-26 23:00 | 2024-10-27 | Winter | FALSE | summer
2024-10-27 | 2024-10-27 01:00 | Winter | FALSE | summer
2024-10-27 01:00 | 2024-10-27 02:00 | Winter | FALSE | summer
2024-10-27 02:00 | 2024-10-27 03:00 | Winter | FALSE | summer
2024-10-27 03:00 | 2024-10-27 04:00 | Winter | FALSE | summer
2024-10-27 04:00 | 2024-10-27 05:00 | Winter | FALSE | summer
2024-10-27 05:00 | 2024-10-27 06:00 | Winter | FALSE | summer
2024-10-27 06:00 | 2024-10-27 07:00 | Winter | FALSE | summer
2024-10-27 07:00 | 2024-10-27 08:00 | Winter | FALSE | summer
2024-10-27 08:00 | 2024-10-27 09:00 | Winter | FALSE | summer
2024-10-27 09:00 | 2024-10-27 10:00 | Winter | FALSE | summer
2024-10-27 10:00 | 2024-10-27 11:00 | Winter | FALSE | summer
2024-10-27 11:00 | 2024-10-27 12:00 | Winter | FALSE | summer
2024-10-27 12:00 | 2024-10-27 13:00 | Winter | FALSE | summer
2024-10-27 13:00 | 2024-10-27 14:00 | Winter | FALSE | summer
2024-10-27 14:00 | 2024-10-27 15:00 | Winter | FALSE | summer
2024-10-27 15:00 | 2024-10-27 16:00 | Winter | FALSE | summer
2024-10-27 16:00 | 2024-10-27 17:00 | Winter | TRUE | summer
2024-10-27 17:00 | 2024-10-27 18:00 | Winter | TRUE | summer
2024-10-27 18:00 | 2024-10-27 19:00 | Winter | TRUE | summer
2024-10-27 19:00 | 2024-10-27 20:00 | Winter | TRUE | summer
2024-10-27 20:00 | 2024-10-27 21:00 | Winter | TRUE | summer
2024-10-27 21:00 | 2024-10-27 22:00 | Winter | FALSE | summer
2024-10-27 22:00 | 2024-10-27 23:00 | Winter | FALSE | summer
2024-10-27 23:00 | 2024-10-28 | Winter | FALSE | summer
2024-10-28 | 2024-10-28 01:00 | Winter | FALSE | summer
2024-10-28 01:00 | 2024-10-28 02:00 | Winter | FALSE | summer
2024-10-28 02:00 | 2024-10-28 03:00 | Winter | FALSE | summer
2024-10-28 03:00 | 2024-10-28 04:00 | Winter | FALSE | summer
2024-10-28 04:00 | 2024-10-28 05:00 | Winter | FALSE | summer
2024-10-28 05:00 | 2024-10-28 06:00 | Winter | FALSE | summer
2024-10-28 06:00 | 2024-10-28 07:00 | Winter | FALSE | summer
2024-10-28 07:00 | 2024-10-28 08:00 | Winter | FALSE | summer
2024-10-28 08:00 | 2024-10-28 09:00 | Winter | FALSE | summer
2024-10-28 09:00 | 2024-10-28 10:00 | Winter | FALSE | summer
2024-10-28 10:00 | 2024-10-28 11:00 | Winter | FALSE | summer
2024-10-28 11:00 | 2024-10-28 12:00 | Winter | FALSE | summer
2024-10-28 12:00 | 2024-10-28 13:00 | Winter | FALSE | summer
2024-10-28 13:00 | 2024-10-28 14:00 | Winter | FALSE | summer
2024-10-28 14:00 | 2024-10-28 15:00 | Winter | FALSE | summer
2024-10-28 15:00 | 2024-10-28 16:00 | Winter | FALSE | summer
2024-10-28 16:00 | 2024-10-28 17:00 | Winter | TRUE | summer
2024-10-28 17:00 | 2024-10-28 18:00 | Winter | TRUE | summer
2024-10-28 18:00 | 2024-10-28 19:00 | Winter | TRUE | summer
2024-10-28 19:00 | 2024-10-28 20:00 | Winter | TRUE | summer
2024-10-28 20:00 | 2024-10-28 21:00 | Winter | TRUE | summer
2024-10-28 21:00 | 2024-10-28 22:00 | Winter | FALSE | summer
2024-10-28 22:00 | 2024-10-28 23:00 | Winter | FALSE | summer
2024-10-28 23:00 | 2024-10-29 | Winter | FALSE | summer
2024-10-29 | 2024-10-29 01:00 | Winter | FALSE | summer
2024-10-29 01:00 | 2024-10-29 02:00 | Winter | FALSE | summer
2024-10-29 02:00 | 2024-10-29 03:00 | Winter | FALSE | summer
2024-10-29 03:00 | 2024-10-29 04:00 | Winter | FALSE | summer
2024-10-29 04:00 | 2024-10-29 05:00 | Winter | FALSE | summer
2024-10-29 05:00 | 2024-10-29 06:00 | Winter | FALSE | summer
2024-10-29 06:00 | 2024-10-29 07:00 | Winter | FALSE | summer
2024-10-29 07:00 | 2024-10-29 08:00 | Winter | FALSE | summer
2024-10-29 08:00 | 2024-10-29 09:00 | Winter | FALSE | summer
2024-10-29 09:00 | 2024-10-29 10:00 | Winter | FALSE | summer
2024-10-29 10:00 | 2024-10-29 11:00 | Winter | FALSE | summer
2024-10-29 11:00 | 2024-10-29 12:00 | Winter | FALSE | summer
2024-10-29 12:00 | 2024-10-29 13:00 | Winter | FALSE | summer
2024-10-29 13:00 | 2024-10-29 14:00 | Winter | FALSE | summer
2024-10-29 14:00 | 2024-10-29 15:00 | Winter | FALSE | summer
2024-10-29 15:00 | 2024-10-29 16:00 | Winter | FALSE | summer
2024-10-29 16:00 | 2024-10-29 17:00 | Winter | TRUE | summer
2024-10-29 17:00 | 2024-10-29 18:00 | Winter | TRUE | summer
2024-10-29 18:00 | 2024-10-29 19:00 | Winter | TRUE | summer
2024-10-29 19:00 | 2024-10-29 20:00 | Winter | TRUE | summer
2024-10-29 20:00 | 2024-10-29 21:00 | Winter | TRUE | summer
2024-10-29 21:00 | 2024-10-29 22:00 | Winter | FALSE | summer
2024-10-29 22:00 | 2024-10-29 23:00 | Winter | FALSE | summer
2024-10-29 23:00 | 2024-10-30 | Winter | FALSE | summer
2024-10-30 | 2024-10-30 01:00 | Winter | FALSE | summer
2024-10-30 01:00 | 2024-10-30 02:00 | Winter | FALSE | summer
2024-10-30 02:00 | 2024-10-30 03:00 | Winter | FALSE | summer
2024-10-30 03:00 | 2024-10-30 04:00 | Winter | FALSE | summer
2024-10-30 04:00 | 2024-10-30 05:00 | Winter | FALSE | summer
2024-10-30 05:00 | 2024-10-30 06:00 | Winter | FALSE | summer
2024-10-30 06:00 | 2024-10-30 07:00 | Winter | FALSE | summer
2024-10-30 07:00 | 2024-10-30 08:00 | Winter | FALSE | summer
2024-10-30 08:00 | 2024-10-30 09:00 | Winter | FALSE | summer
2024-10-30 09:00 | 2024-10-30 10:00 | Winter | FALSE | summer
2024-10-30 10:00 | 2024-10-30 11:00 | Winter | FALSE | summer
2024-10-30 11:00 | 2024-10-30 12:00 | Winter | FALSE | summer
2024-10-30 12:00 | 2024-10-30 13:00 | Winter | FALSE | summer
2024-10-30 13:00 | 2024-10-30 14:00 | Winter | FALSE | summer
2024-10-30 14:00 | 2024-10-30 15:00 | Winter | FALSE | summer
2024-10-30 15:00 | 2024-10-30 16:00 | Winter | FALSE | summer
2024-10-30 16:00 | 2024-10-30 17:00 | Winter | TRUE | summer
2024-10-30 17:00 | 2024-10-30 18:00 | Winter | TRUE | summer
2024-10-30 18:00 | 2024-10-30 19:00 | Winter | TRUE | summer
2024-10-30 19:00 | 2024-10-30 20:00 | Winter | TRUE | summer
2024-10-30 20:00 | 2024-10-30 21:00 | Winter | TRUE | summer
2024-10-30 21:00 | 2024-10-30 22:00 | Winter | FALSE | summer
2024-10-30 22:00 | 2024-10-30 23:00 | Winter | FALSE | summer
2024-10-30 23:00 | 2024-10-31 | Winter | FALSE | summer
2024-10-31 | 2024-10-31 01:00 | Winter | FALSE | summer
2024-10-31 01:00 | 2024-10-31 02:00 | Winter | FALSE | summer
2024-10-31 02:00 | 2024-10-31 03:00 | Winter | FALSE | summer
2024-10-31 03:00 | 2024-10-31 04:00 | Winter | FALSE | summer
2024-10-31 04:00 | 2024-10-31 05:00 | Winter | FALSE | summer
2024-10-31 05:00 | 2024-10-31 06:00 | Winter | FALSE | summer
2024-10-31 06:00 | 2024-10-31 07:00 | Winter | FALSE | summer
2024-10-31 07:00 | 2024-10-31 08:00 | Winter | FALSE | summer
2024-10-31 08:00 | 2024-10-31 09:00 | Winter | FALSE | summer
2024-10-31 09:00 | 2024-10-31 10:00 | Winter | FALSE | summer
2024-10-31 10:00 | 2024-10-31 11:00 | Winter | FALSE | summer
2024-10-31 11:00 | 2024-10-31 12:00 | Winter | FALSE | summer
2024-10-31 12:00 | 2024-10-31 13:00 | Winter | FALSE | summer
2024-10-31 13:00 | 2024-10-31 14:00 | Winter | FALSE | summer
2024-10-31 14:00 | 2024-10-31 15:00 | Winter | FALSE | summer
2024-10-31 15:00 | 2024-10-31 16:00 | Winter | FALSE | summer
2024-10-31 16:00 | 2024-10-31 17:00 | Winter | TRUE | summer
2024-10-31 17:00 | 2024-10-31 18:00 | Winter | TRUE | summer
2024-10-31 18:00 | 2024-10-31 19:00 | Winter | TRUE | summer
2024-10-31 19:00 | 2024-10-31 20:00 | Winter | TRUE | summer
2024-10-31 20:00 | 2024-10-31 21:00 | Winter | TRUE | summer
2024-10-31 21:00 | 2024-10-31 22:00 | Winter | FALSE | summer
2024-10-31 22:00 | 2024-10-31 23:00 | Winter | FALSE | summer
2024-10-31 23:00 | 2024-11-01 | Winter | FALSE | summer
2024-11-01 | 2024-11-01 01:00 | Winter | FALSE | nonsummer
2024-11-01 01:00 | 2024-11-01 02:00 | Winter | FALSE | nonsummer
2024-11-01 02:00 | 2024-11-01 03:00 | Winter | FALSE | nonsummer
2024-11-01 03:00 | 2024-11-01 04:00 | Winter | FALSE | nonsummer
2024-11-01 04:00 | 2024-11-01 05:00 | Winter | FALSE | nonsummer
2024-11-01 05:00 | 2024-11-01 06:00 | Winter | FALSE | nonsummer
2024-11-01 06:00 | 2024-11-01 07:00 | Winter | FALSE | nonsummer
2024-11-01 07:00 | 2024-11-01 08:00 | Winter | FALSE | nonsummer
2024-11-01 08:00 | 2024-11-01 09:00 | Winter | FALSE | nonsummer
2024-11-01 09:00 | 2024-11-01 10:00 | Winter | FALSE | nonsummer
2024-11-01 10:00 | 2024-11-01 11:00 | Winter | FALSE | nonsummer
2024-11-01 11:00 | 2024-11-01 12:00 | Winter | FALSE | nonsummer
2024-11-01 12:00 | 2024-11-01 13:00 | Winter | FALSE | nonsummer
2024-11-01 13:00 | 2024-11-01 14:00 | Winter | FALSE | nonsummer
2024-11-01 14:00 | 2024-11-01 15:00 | Winter | FALSE | nonsummer
2024-11-01 15:00 | 2024-11-01 16:00 | Winter | FALSE | nonsummer
2024-11-01 16:00 | 2024-11-01 17:00 | Winter | TRUE | nonsummer
2024-11-01 17:00 | 2024-11-01 18:00 | Winter | TRUE | nonsummer
2024-11-01 18:00 | 2024-11-01 19:00 | Winter | TRUE | nonsummer
2024-11-01 19:00 | 2024-11-01 20:00 | Winter | TRUE | nonsummer
2024-11-01 20:00 | 2024-11-01 21:00 | Winter | TRUE | nonsummer
2024-11-01 21:00 | 2024-11-01 22:00 | Winter | FALSE | nonsummer
2024-11-01 22:00 | 2024-11-01 23:00 | Winter | FALSE | nonsummer
2024-11-01 23:00 | 2024-11-02 | Winter | FALSE | nonsummer
2024-11-02 | 2024-11-02 01:00 | Winter | FALSE | nonsummer
2024-11-02 01:00 | 2024-11-02 02:00 | Winter | FALSE | nonsummer
2024-11-02 02:00 | 2024-11-02 03:00 | Winter | FALSE | nonsummer
2024-11-02 03:00 | 2024-11-02 04:00 | Winter | FALSE | nonsummer
2024-11-02 04:00 | 2024-11-02 05:00 | Winter | FALSE | nonsummer
2024-11-02 05:00 | 2024-11-02 06:00 | Winter | FALSE | nonsummer
2024-11-02 06:00 | 2024-11-02 07:00 | Winter | FALSE | nonsummer
2024-11-02 07:00 | 2024-11-02 08:00 | Winter | FALSE | nonsummer
2024-11-02 08:00 | 2024-11-02 09:00 | Winter | FALSE | nonsummer
2024-11-02 09:00 | 2024-11-02 10:00 | Winter | FALSE | nonsummer
2024-11-02 10:00 | 2024-11-02 11:00 | Winter | FALSE | nonsummer
2024-11-02 11:00 | 2024-11-02 12:00 | Winter | FALSE | nonsummer
2024-11-02 12:00 | 2024-11-02 13:00 | Winter | FALSE | nonsummer
2024-11-02 13:00 | 2024-11-02 14:00 | Winter | FALSE | nonsummer
2024-11-02 14:00 | 2024-11-02 15:00 | Winter | FALSE | nonsummer
2024-11-02 15:00 | 2024-11-02 16:00 | Winter | FALSE | nonsummer
2024-11-02 16:00 | 2024-11-02 17:00 | Winter | TRUE | nonsummer
2024-11-02 17:00 | 2024-11-02 18:00 | Winter | TRUE | nonsummer
2024-11-02 18:00 | 2024-11-02 19:00 | Winter | TRUE | nonsummer
2024-11-02 19:00 | 2024-11-02 20:00 | Winter | TRUE | nonsummer
2024-11-02 20:00 | 2024-11-02 21:00 | Winter | TRUE | nonsummer
2024-11-02 21:00 | 2024-11-02 22:00 | Winter | FALSE | nonsummer
2024-11-02 22:00 | 2024-11-02 23:00 | Winter | FALSE | nonsummer
2024-11-02 23:00 | 2024-11-03 | Winter | FALSE | nonsummer
2024-11-03 | 2024-11-03 01:00 | Winter | FALSE | nonsummer
2024-11-03 01:00 | 2024-11-03 02:00 | Winter | FALSE | nonsummer
2024-11-03 02:00 | 2024-11-03 03:00 | Winter | FALSE | nonsummer
2024-11-03 03:00 | 2024-11-03 04:00 | Winter | FALSE | nonsummer
2024-11-03 04:00 | 2024-11-03 05:00 | Winter | FALSE | nonsummer
2024-11-03 05:00 | 2024-11-03 06:00 | Winter | FALSE | nonsummer
2024-11-03 06:00 | 2024-11-03 07:00 | Winter | FALSE | nonsummer
2024-11-03 07:00 | 2024-11-03 08:00 | Winter | FALSE | nonsummer
2024-11-03 08:00 | 2024-11-03 09:00 | Winter | FALSE | nonsummer
2024-11-03 09:00 | 2024-11-03 10:00 | Winter | FALSE | nonsummer
2024-11-03 10:00 | 2024-11-03 11:00 | Winter | FALSE | nonsummer
2024-11-03 11:00 | 2024-11-03 12:00 | Winter | FALSE | nonsummer
2024-11-03 12:00 | 2024-11-03 13:00 | Winter | FALSE | nonsummer
2024-11-03 13:00 | 2024-11-03 14:00 | Winter | FALSE | nonsummer
2024-11-03 14:00 | 2024-11-03 15:00 | Winter | FALSE | nonsummer
2024-11-03 15:00 | 2024-11-03 16:00 | Winter | FALSE | nonsummer
2024-11-03 16:00 | 2024-11-03 17:00 | Winter | TRUE | nonsummer
2024-11-03 17:00 | 2024-11-03 18:00 | Winter | TRUE | nonsummer
2024-11-03 18:00 | 2024-11-03 19:00 | Winter | TRUE | nonsummer
2024-11-03 19:00 | 2024-11-03 20:00 | Winter | TRUE | nonsummer
2024-11-03 20:00 | 2024-11-03 21:00 | Winter | TRUE | nonsummer
2024-11-03 21:00 | 2024-11-03 22:00 | Winter | FALSE | nonsummer
2024-11-03 22:00 | 2024-11-03 23:00 | Winter | FALSE | nonsummer
2024-11-03 23:00 | 2024-11-04 | Winter | FALSE | nonsummer
2024-11-04 | 2024-11-04 01:00 | Winter | FALSE | nonsummer
2024-11-04 01:00 | 2024-11-04 02:00 | Winter | FALSE | nonsummer
2024-11-04 02:00 | 2024-11-04 03:00 | Winter | FALSE | nonsummer
2024-11-04 03:00 | 2024-11-04 04:00 | Winter | FALSE | nonsummer
2024-11-04 04:00 | 2024-11-04 05:00 | Winter | FALSE | nonsummer
2024-11-04 05:00 | 2024-11-04 06:00 | Winter | FALSE | nonsummer
2024-11-04 06:00 | 2024-11-04 07:00 | Winter | FALSE | nonsummer
2024-11-04 07:00 | 2024-11-04 08:00 | Winter | FALSE | nonsummer
2024-11-04 08:00 | 2024-11-04 09:00 | Winter | FALSE | nonsummer
2024-11-04 09:00 | 2024-11-04 10:00 | Winter | FALSE | nonsummer
2024-11-04 10:00 | 2024-11-04 11:00 | Winter | FALSE | nonsummer
2024-11-04 11:00 | 2024-11-04 12:00 | Winter | FALSE | nonsummer
2024-11-04 12:00 | 2024-11-04 13:00 | Winter | FALSE | nonsummer
2024-11-04 13:00 | 2024-11-04 14:00 | Winter | FALSE | nonsummer
2024-11-04 14:00 | 2024-11-04 15:00 | Winter | FALSE | nonsummer
2024-11-04 15:00 | 2024-11-04 16:00 | Winter | FALSE | nonsummer
2024-11-04 16:00 | 2024-11-04 17:00 | Winter | TRUE | nonsummer
2024-11-04 17:00 | 2024-11-04 18:00 | Winter | TRUE | nonsummer
2024-11-04 18:00 | 2024-11-04 19:00 | Winter | TRUE | nonsummer
2024-11-04 19:00 | 2024-11-04 20:00 | Winter | TRUE | nonsummer
2024-11-04 20:00 | 2024-11-04 21:00 | Winter | TRUE | nonsummer
2024-11-04 21:00 | 2024-11-04 22:00 | Winter | FALSE | nonsummer
2024-11-04 22:00 | 2024-11-04 23:00 | Winter | FALSE | nonsummer
2024-11-04 23:00 | 2024-11-05 | Winter | FALSE | nonsummer
2024-11-05 | 2024-11-05 01:00 | Winter | FALSE | nonsummer
2024-11-05 01:00 | 2024-11-05 02:00 | Winter | FALSE | nonsummer
2024-11-05 02:00 | 2024-11-05 03:00 | Winter | FALSE | nonsummer
2024-11-05 03:00 | 2024-11-05 04:00 | Winter | FALSE | nonsummer
2024-11-05 04:00 | 2024-11-05 05:00 | Winter | FALSE | nonsummer
2024-11-05 05:00 | 2024-11-05 06:00 | Winter | FALSE | nonsummer
2024-11-05 06:00 | 2024-11-05 07:00 | Winter | FALSE | nonsummer
2024-11-05 07:00 | 2024-11-05 08:00 | Winter | FALSE | nonsummer
2024-11-05 08:00 | 2024-11-05 09:00 | Winter | FALSE | nonsummer
2024-11-05 09:00 | 2024-11-05 10:00 | Winter | FALSE | nonsummer
2024-11-05 10:00 | 2024-11-05 11:00 | Winter | FALSE | nonsummer
2024-11-05 11:00 | 2024-11-05 12:00 | Winter | FALSE | nonsummer
2024-11-05 12:00 | 2024-11-05 13:00 | Winter | FALSE | nonsummer
2024-11-05 13:00 | 2024-11-05 14:00 | Winter | FALSE | nonsummer
2024-11-05 14:00 | 2024-11-05 15:00 | Winter | FALSE | nonsummer
2024-11-05 15:00 | 2024-11-05 16:00 | Winter | FALSE | nonsummer
2024-11-05 16:00 | 2024-11-05 17:00 | Winter | TRUE | nonsummer
2024-11-05 17:00 | 2024-11-05 18:00 | Winter | TRUE | nonsummer
2024-11-05 18:00 | 2024-11-05 19:00 | Winter | TRUE | nonsummer
2024-11-05 19:00 | 2024-11-05 20:00 | Winter | TRUE | nonsummer
2024-11-05 20:00 | 2024-11-05 21:00 | Winter | TRUE | nonsummer
2024-11-05 21:00 | 2024-11-05 22:00 | Winter | FALSE | nonsummer
2024-11-05 22:00 | 2024-11-05 23:00 | Winter | FALSE | nonsummer
2024-11-05 23:00 | 2024-11-06 | Winter | FALSE | nonsummer
2024-11-06 | 2024-11-06 01:00 | Winter | FALSE | nonsummer
2024-11-06 01:00 | 2024-11-06 02:00 | Winter | FALSE | nonsummer
2024-11-06 02:00 | 2024-11-06 03:00 | Winter | FALSE | nonsummer
2024-11-06 03:00 | 2024-11-06 04:00 | Winter | FALSE | nonsummer
2024-11-06 04:00 | 2024-11-06 05:00 | Winter | FALSE | nonsummer
2024-11-06 05:00 | 2024-11-06 06:00 | Winter | FALSE | nonsummer
2024-11-06 06:00 | 2024-11-06 07:00 | Winter | FALSE | nonsummer
2024-11-06 07:00 | 2024-11-06 08:00 | Winter | FALSE | nonsummer
2024-11-06 08:00 | 2024-11-06 09:00 | Winter | FALSE | nonsummer
2024-11-06 09:00 | 2024-11-06 10:00 | Winter | FALSE | nonsummer
2024-11-06 10:00 | 2024-11-06 11:00 | Winter | FALSE | nonsummer
2024-11-06 11:00 | 2024-11-06 12:00 | Winter | FALSE | nonsummer
2024-11-06 12:00 | 2024-11-06 13:00 | Winter | FALSE | nonsummer
2024-11-06 13:00 | 2024-11-06 14:00 | Winter | FALSE | nonsummer
2024-11-06 14:00 | 2024-11-06 15:00 | Winter | FALSE | nonsummer
2024-11-06 15:00 | 2024-11-06 16:00 | Winter | FALSE | nonsummer
2024-11-06 16:00 | 2024-11-06 17:00 | Winter | TRUE | nonsummer
2024-11-06 17:00 | 2024-11-06 18:00 | Winter | TRUE | nonsummer
2024-11-06 18:00 | 2024-11-06 19:00 | Winter | TRUE | nonsummer
2024-11-06 19:00 | 2024-11-06 20:00 | Winter | TRUE | nonsummer
2024-11-06 20:00 | 2024-11-06 21:00 | Winter | TRUE | nonsummer
2024-11-06 21:00 | 2024-11-06 22:00 | Winter | FALSE | nonsummer
2024-11-06 22:00 | 2024-11-06 23:00 | Winter | FALSE | nonsummer
2024-11-06 23:00 | 2024-11-07 | Winter | FALSE | nonsummer
2024-11-07 | 2024-11-07 01:00 | Winter | FALSE | nonsummer
2024-11-07 01:00 | 2024-11-07 02:00 | Winter | FALSE | nonsummer
2024-11-07 02:00 | 2024-11-07 03:00 | Winter | FALSE | nonsummer
2024-11-07 03:00 | 2024-11-07 04:00 | Winter | FALSE | nonsummer
2024-11-07 04:00 | 2024-11-07 05:00 | Winter | FALSE | nonsummer
2024-11-07 05:00 | 2024-11-07 06:00 | Winter | FALSE | nonsummer
2024-11-07 06:00 | 2024-11-07 07:00 | Winter | FALSE | nonsummer
2024-11-07 07:00 | 2024-11-07 08:00 | Winter | FALSE | nonsummer
2024-11-07 08:00 | 2024-11-07 09:00 | Winter | FALSE | nonsummer
2024-11-07 09:00 | 2024-11-07 10:00 | Winter | FALSE | nonsummer
2024-11-07 10:00 | 2024-11-07 11:00 | Winter | FALSE | nonsummer
2024-11-07 11:00 | 2024-11-07 12:00 | Winter | FALSE | nonsummer
2024-11-07 12:00 | 2024-11-07 13:00 | Winter | FALSE | nonsummer
2024-11-07 13:00 | 2024-11-07 14:00 | Winter | FALSE | nonsummer
2024-11-07 14:00 | 2024-11-07 15:00 | Winter | FALSE | nonsummer
2024-11-07 15:00 | 2024-11-07 16:00 | Winter | FALSE | nonsummer
2024-11-07 16:00 | 2024-11-07 17:00 | Winter | TRUE | nonsummer
2024-11-07 17:00 | 2024-11-07 18:00 | Winter | TRUE | nonsummer
2024-11-07 18:00 | 2024-11-07 19:00 | Winter | TRUE | nonsummer
2024-11-07 19:00 | 2024-11-07 20:00 | Winter | TRUE | nonsummer
2024-11-07 20:00 | 2024-11-07 21:00 | Winter | TRUE | nonsummer
2024-11-07 21:00 | 2024-11-07 22:00 | Winter | FALSE | nonsummer
2024-11-07 22:00 | 2024-11-07 23:00 | Winter | FALSE | nonsummer
2024-11-07 23:00 | 2024-11-08 | Winter | FALSE | nonsummer
2024-11-08 | 2024-11-08 01:00 | Winter | FALSE | nonsummer
2024-11-08 01:00 | 2024-11-08 02:00 | Winter | FALSE | nonsummer
2024-11-08 02:00 | 2024-11-08 03:00 | Winter | FALSE | nonsummer
2024-11-08 03:00 | 2024-11-08 04:00 | Winter | FALSE | nonsummer
2024-11-08 04:00 | 2024-11-08 05:00 | Winter | FALSE | nonsummer
2024-11-08 05:00 | 2024-11-08 06:00 | Winter | FALSE | nonsummer
2024-11-08 06:00 | 2024-11-08 07:00 | Winter | FALSE | nonsummer
2024-11-08 07:00 | 2024-11-08 08:00 | Winter | FALSE | nonsummer
2024-11-08 08:00 | 2024-11-08 09:00 | Winter | FALSE | nonsummer
2024-11-08 09:00 | 2024-11-08 10:00 | Winter | FALSE | nonsummer
2024-11-08 10:00 | 2024-11-08 11:00 | Winter | FALSE | nonsummer
2024-11-08 11:00 | 2024-11-08 12:00 | Winter | FALSE | nonsummer
2024-11-08 12:00 | 2024-11-08 13:00 | Winter | FALSE | nonsummer
2024-11-08 13:00 | 2024-11-08 14:00 | Winter | FALSE | nonsummer
2024-11-08 14:00 | 2024-11-08 15:00 | Winter | FALSE | nonsummer
2024-11-08 15:00 | 2024-11-08 16:00 | Winter | FALSE | nonsummer
2024-11-08 16:00 | 2024-11-08 17:00 | Winter | TRUE | nonsummer
2024-11-08 17:00 | 2024-11-08 18:00 | Winter | TRUE | nonsummer
2024-11-08 18:00 | 2024-11-08 19:00 | Winter | TRUE | nonsummer
2024-11-08 19:00 | 2024-11-08 20:00 | Winter | TRUE | nonsummer
2024-11-08 20:00 | 2024-11-08 21:00 | Winter | TRUE | nonsummer
2024-11-08 21:00 | 2024-11-08 22:00 | Winter | FALSE | nonsummer
2024-11-08 22:00 | 2024-11-08 23:00 | Winter | FALSE | nonsummer
2024-11-08 23:00 | 2024-11-09 | Winter | FALSE | nonsummer
2024-11-09 | 2024-11-09 01:00 | Winter | FALSE | nonsummer
2024-11-09 01:00 | 2024-11-09 02:00 | Winter | FALSE | nonsummer
2024-11-09 02:00 | 2024-11-09 03:00 | Winter | FALSE | nonsummer
2024-11-09 03:00 | 2024-11-09 04:00 | Winter | FALSE | nonsummer
2024-11-09 04:00 | 2024-11-09 05:00 | Winter | FALSE | nonsummer
2024-11-09 05:00 | 2024-11-09 06:00 | Winter | FALSE | nonsummer
2024-11-09 06:00 | 2024-11-09 07:00 | Winter | FALSE | nonsummer
2024-11-09 07:00 | 2024-11-09 08:00 | Winter | FALSE | nonsummer
2024-11-09 08:00 | 2024-11-09 09:00 | Winter | FALSE | nonsummer
2024-11-09 09:00 | 2024-11-09 10:00 | Winter | FALSE | nonsummer
2024-11-09 10:00 | 2024-11-09 11:00 | Winter | FALSE | nonsummer
2024-11-09 11:00 | 2024-11-09 12:00 | Winter | FALSE | nonsummer
2024-11-09 12:00 | 2024-11-09 13:00 | Winter | FALSE | nonsummer
2024-11-09 13:00 | 2024-11-09 14:00 | Winter | FALSE | nonsummer
2024-11-09 14:00 | 2024-11-09 15:00 | Winter | FALSE | nonsummer
2024-11-09 15:00 | 2024-11-09 16:00 | Winter | FALSE | nonsummer
2024-11-09 16:00 | 2024-11-09 17:00 | Winter | TRUE | nonsummer
2024-11-09 17:00 | 2024-11-09 18:00 | Winter | TRUE | nonsummer
2024-11-09 18:00 | 2024-11-09 19:00 | Winter | TRUE | nonsummer
2024-11-09 19:00 | 2024-11-09 20:00 | Winter | TRUE | nonsummer
2024-11-09 20:00 | 2024-11-09 21:00 | Winter | TRUE | nonsummer
2024-11-09 21:00 | 2024-11-09 22:00 | Winter | FALSE | nonsummer
2024-11-09 22:00 | 2024-11-09 23:00 | Winter | FALSE | nonsummer
2024-11-09 23:00 | 2024-11-10 | Winter | FALSE | nonsummer
2024-11-10 | 2024-11-10 01:00 | Winter | FALSE | nonsummer
2024-11-10 01:00 | 2024-11-10 02:00 | Winter | FALSE | nonsummer
2024-11-10 02:00 | 2024-11-10 03:00 | Winter | FALSE | nonsummer
2024-11-10 03:00 | 2024-11-10 04:00 | Winter | FALSE | nonsummer
2024-11-10 04:00 | 2024-11-10 05:00 | Winter | FALSE | nonsummer
2024-11-10 05:00 | 2024-11-10 06:00 | Winter | FALSE | nonsummer
2024-11-10 06:00 | 2024-11-10 07:00 | Winter | FALSE | nonsummer
2024-11-10 07:00 | 2024-11-10 08:00 | Winter | FALSE | nonsummer
2024-11-10 08:00 | 2024-11-10 09:00 | Winter | FALSE | nonsummer
2024-11-10 09:00 | 2024-11-10 10:00 | Winter | FALSE | nonsummer
2024-11-10 10:00 | 2024-11-10 11:00 | Winter | FALSE | nonsummer
2024-11-10 11:00 | 2024-11-10 12:00 | Winter | FALSE | nonsummer
2024-11-10 12:00 | 2024-11-10 13:00 | Winter | FALSE | nonsummer
2024-11-10 13:00 | 2024-11-10 14:00 | Winter | FALSE | nonsummer
2024-11-10 14:00 | 2024-11-10 15:00 | Winter | FALSE | nonsummer
2024-11-10 15:00 | 2024-11-10 16:00 | Winter | FALSE | nonsummer
2024-11-10 16:00 | 2024-11-10 17:00 | Winter | TRUE | nonsummer
2024-11-10 17:00 | 2024-11-10 18:00 | Winter | TRUE | nonsummer
2024-11-10 18:00 | 2024-11-10 19:00 | Winter | TRUE | nonsummer
2024-11-10 19:00 | 2024-11-10 20:00 | Winter | TRUE | nonsummer
2024-11-10 20:00 | 2024-11-10 21:00 | Winter | TRUE | nonsummer
2024-11-10 21:00 | 2024-11-10 22:00 | Winter | FALSE | nonsummer
2024-11-10 22:00 | 2024-11-10 23:00 | Winter | FALSE | nonsummer
2024-11-10 23:00 | 2024-11-11 | Winter | FALSE | nonsummer
2024-11-11 | 2024-11-11 01:00 | Winter | FALSE | nonsummer
2024-11-11 01:00 | 2024-11-11 02:00 | Winter | FALSE | nonsummer
2024-11-11 02:00 | 2024-11-11 03:00 | Winter | FALSE | nonsummer
2024-11-11 03:00 | 2024-11-11 04:00 | Winter | FALSE | nonsummer
2024-11-11 04:00 | 2024-11-11 05:00 | Winter | FALSE | nonsummer
2024-11-11 05:00 | 2024-11-11 06:00 | Winter | FALSE | nonsummer
2024-11-11 06:00 | 2024-11-11 07:00 | Winter | FALSE | nonsummer
2024-11-11 07:00 | 2024-11-11 08:00 | Winter | FALSE | nonsummer
2024-11-11 08:00 | 2024-11-11 09:00 | Winter | FALSE | nonsummer
2024-11-11 09:00 | 2024-11-11 10:00 | Winter | FALSE | nonsummer
2024-11-11 10:00 | 2024-11-11 11:00 | Winter | FALSE | nonsummer
2024-11-11 11:00 | 2024-11-11 12:00 | Winter | FALSE | nonsummer
2024-11-11 12:00 | 2024-11-11 13:00 | Winter | FALSE | nonsummer
2024-11-11 13:00 | 2024-11-11 14:00 | Winter | FALSE | nonsummer
2024-11-11 14:00 | 2024-11-11 15:00 | Winter | FALSE | nonsummer
2024-11-11 15:00 | 2024-11-11 16:00 | Winter | FALSE | nonsummer
2024-11-11 16:00 | 2024-11-11 17:00 | Winter | TRUE | nonsummer
2024-11-11 17:00 | 2024-11-11 18:00 | Winter | TRUE | nonsummer
2024-11-11 18:00 | 2024-11-11 19:00 | Winter | TRUE | nonsummer
2024-11-11 19:00 | 2024-11-11 20:00 | Winter | TRUE | nonsummer
2024-11-11 20:00 | 2024-11-11 21:00 | Winter | TRUE | nonsummer
2024-11-11 21:00 | 2024-11-11 22:00 | Winter | FALSE | nonsummer
2024-11-11 22:00 | 2024-11-11 23:00 | Winter | FALSE | nonsummer
2024-11-11 23:00 | 2024-11-12 | Winter | FALSE | nonsummer
2024-11-12 | 2024-11-12 01:00 | Winter | FALSE | nonsummer
2024-11-12 01:00 | 2024-11-12 02:00 | Winter | FALSE | nonsummer
2024-11-12 02:00 | 2024-11-12 03:00 | Winter | FALSE | nonsummer
2024-11-12 03:00 | 2024-11-12 04:00 | Winter | FALSE | nonsummer
2024-11-12 04:00 | 2024-11-12 05:00 | Winter | FALSE | nonsummer
2024-11-12 05:00 | 2024-11-12 06:00 | Winter | FALSE | nonsummer
2024-11-12 06:00 | 2024-11-12 07:00 | Winter | FALSE | nonsummer
2024-11-12 07:00 | 2024-11-12 08:00 | Winter | FALSE | nonsummer
2024-11-12 08:00 | 2024-11-12 09:00 | Winter | FALSE | nonsummer
2024-11-12 09:00 | 2024-11-12 10:00 | Winter | FALSE | nonsummer
2024-11-12 10:00 | 2024-11-12 11:00 | Winter | FALSE | nonsummer
2024-11-12 11:00 | 2024-11-12 12:00 | Winter | FALSE | nonsummer
2024-11-12 12:00 | 2024-11-12 13:00 | Winter | FALSE | nonsummer
2024-11-12 13:00 | 2024-11-12 14:00 | Winter | FALSE | nonsummer
2024-11-12 14:00 | 2024-11-12 15:00 | Winter | FALSE | nonsummer
2024-11-12 15:00 | 2024-11-12 16:00 | Winter | FALSE | nonsummer
2024-11-12 16:00 | 2024-11-12 17:00 | Winter | TRUE | nonsummer
2024-11-12 17:00 | 2024-11-12 18:00 | Winter | TRUE | nonsummer
2024-11-12 18:00 | 2024-11-12 19:00 | Winter | TRUE | nonsummer
2024-11-12 19:00 | 2024-11-12 20:00 | Winter | TRUE | nonsummer
2024-11-12 20:00 | 2024-11-12 21:00 | Winter | TRUE | nonsummer
2024-11-12 21:00 | 2024-11-12 22:00 | Winter | FALSE | nonsummer
2024-11-12 22:00 | 2024-11-12 23:00 | Winter | FALSE | nonsummer
2024-11-12 23:00 | 2024-11-13 | Winter | FALSE | nonsummer
2024-11-13 | 2024-11-13 01:00 | Winter | FALSE | nonsummer
2024-11-13 01:00 | 2024-11-13 02:00 | Winter | FALSE | nonsummer
2024-11-13 02:00 | 2024-11-13 03:00 | Winter | FALSE | nonsummer
2024-11-13 03:00 | 2024-11-13 04:00 | Winter | FALSE | nonsummer
2024-11-13 04:00 | 2024-11-13 05:00 | Winter | FALSE | nonsummer
2024-11-13 05:00 | 2024-11-13 06:00 | Winter | FALSE | nonsummer
2024-11-13 06:00 | 2024-11-13 07:00 | Winter | FALSE | nonsummer
2024-11-13 07:00 | 2024-11-13 08:00 | Winter | FALSE | nonsummer
2024-11-13 08:00 | 2024-11-13 09:00 | Winter | FALSE | nonsummer
2024-11-13 09:00 | 2024-11-13 10:00 | Winter | FALSE | nonsummer
2024-11-13 10:00 | 2024-11-13 11:00 | Winter | FALSE | nonsummer
2024-11-13 11:00 | 2024-11-13 12:00 | Winter | FALSE | nonsummer
2024-11-13 12:00 | 2024-11-13 13:00 | Winter | FALSE | nonsummer
2024-11-13 13:00 | 2024-11-13 14:00 | Winter | FALSE | nonsummer
2024-11-13 14:00 | 2024-11-13 15:00 | Winter | FALSE | nonsummer
2024-11-13 15:00 | 2024-11-13 16:00 | Winter | FALSE | nonsummer
2024-11-13 16:00 | 2024-11-13 17:00 | Winter | TRUE | nonsummer
2024-11-13 17:00 | 2024-11-13 18:00 | Winter | TRUE | nonsummer
2024-11-13 18:00 | 2024-11-13 19:00 | Winter | TRUE | nonsummer
2024-11-13 19:00 | 2024-11-13 20:00 | Winter | TRUE | nonsummer
2024-11-13 20:00 | 2024-11-13 21:00 | Winter | TRUE | nonsummer
2024-11-13 21:00 | 2024-11-13 22:00 | Winter | FALSE | nonsummer
2024-11-13 22:00 | 2024-11-13 23:00 | Winter | FALSE | nonsummer
2024-11-13 23:00 | 2024-11-14 | Winter | FALSE | nonsummer
2024-11-14 | 2024-11-14 01:00 | Winter | FALSE | nonsummer
2024-11-14 01:00 | 2024-11-14 02:00 | Winter | FALSE | nonsummer
2024-11-14 02:00 | 2024-11-14 03:00 | Winter | FALSE | nonsummer
2024-11-14 03:00 | 2024-11-14 04:00 | Winter | FALSE | nonsummer
2024-11-14 04:00 | 2024-11-14 05:00 | Winter | FALSE | nonsummer
2024-11-14 05:00 | 2024-11-14 06:00 | Winter | FALSE | nonsummer
2024-11-14 06:00 | 2024-11-14 07:00 | Winter | FALSE | nonsummer
2024-11-14 07:00 | 2024-11-14 08:00 | Winter | FALSE | nonsummer
2024-11-14 08:00 | 2024-11-14 09:00 | Winter | FALSE | nonsummer
2024-11-14 09:00 | 2024-11-14 10:00 | Winter | FALSE | nonsummer
2024-11-14 10:00 | 2024-11-14 11:00 | Winter | FALSE | nonsummer
2024-11-14 11:00 | 2024-11-14 12:00 | Winter | FALSE | nonsummer
2024-11-14 12:00 | 2024-11-14 13:00 | Winter | FALSE | nonsummer
2024-11-14 13:00 | 2024-11-14 14:00 | Winter | FALSE | nonsummer
2024-11-14 14:00 | 2024-11-14 15:00 | Winter | FALSE | nonsummer
2024-11-14 15:00 | 2024-11-14 16:00 | Winter | FALSE | nonsummer
2024-11-14 16:00 | 2024-11-14 17:00 | Winter | TRUE | nonsummer
2024-11-14 17:00 | 2024-11-14 18:00 | Winter | TRUE | nonsummer
2024-11-14 18:00 | 2024-11-14 19:00 | Winter | TRUE | nonsummer
2024-11-14 19:00 | 2024-11-14 20:00 | Winter | TRUE | nonsummer
2024-11-14 20:00 | 2024-11-14 21:00 | Winter | TRUE | nonsummer
2024-11-14 21:00 | 2024-11-14 22:00 | Winter | FALSE | nonsummer
2024-11-14 22:00 | 2024-11-14 23:00 | Winter | FALSE | nonsummer
2024-11-14 23:00 | 2024-11-15 | Winter | FALSE | nonsummer
2024-11-15 | 2024-11-15 01:00 | Winter | FALSE | nonsummer
2024-11-15 01:00 | 2024-11-15 02:00 | Winter | FALSE | nonsummer
2024-11-15 02:00 | 2024-11-15 03:00 | Winter | FALSE | nonsummer
2024-11-15 03:00 | 2024-11-15 04:00 | Winter | FALSE | nonsummer
2024-11-15 04:00 | 2024-11-15 05:00 | Winter | FALSE | nonsummer
2024-11-15 05:00 | 2024-11-15 06:00 | Winter | FALSE | nonsummer
2024-11-15 06:00 | 2024-11-15 07:00 | Winter | FALSE | nonsummer
2024-11-15 07:00 | 2024-11-15 08:00 | Winter | FALSE | nonsummer
2024-11-15 08:00 | 2024-11-15 09:00 | Winter | FALSE | nonsummer
2024-11-15 09:00 | 2024-11-15 10:00 | Winter | FALSE | nonsummer
2024-11-15 10:00 | 2024-11-15 11:00 | Winter | FALSE | nonsummer
2024-11-15 11:00 | 2024-11-15 12:00 | Winter | FALSE | nonsummer
2024-11-15 12:00 | 2024-11-15 13:00 | Winter | FALSE | nonsummer
2024-11-15 13:00 | 2024-11-15 14:00 | Winter | FALSE | nonsummer
2024-11-15 14:00 | 2024-11-15 15:00 | Winter | FALSE | nonsummer
2024-11-15 15:00 | 2024-11-15 16:00 | Winter | FALSE | nonsummer
2024-11-15 16:00 | 2024-11-15 17:00 | Winter | TRUE | nonsummer
2024-11-15 17:00 | 2024-11-15 18:00 | Winter | TRUE | nonsummer
2024-11-15 18:00 | 2024-11-15 19:00 | Winter | TRUE | nonsummer
2024-11-15 19:00 | 2024-11-15 20:00 | Winter | TRUE | nonsummer
2024-11-15 20:00 | 2024-11-15 21:00 | Winter | TRUE | nonsummer
2024-11-15 21:00 | 2024-11-15 22:00 | Winter | FALSE | nonsummer
2024-11-15 22:00 | 2024-11-15 23:00 | Winter | FALSE | nonsummer
2024-11-15 23:00 | 2024-11-16 | Winter | FALSE | nonsummer
2024-11-16 | 2024-11-16 01:00 | Winter | FALSE | nonsummer
2024-11-16 01:00 | 2024-11-16 02:00 | Winter | FALSE | nonsummer
2024-11-16 02:00 | 2024-11-16 03:00 | Winter | FALSE | nonsummer
2024-11-16 03:00 | 2024-11-16 04:00 | Winter | FALSE | nonsummer
2024-11-16 04:00 | 2024-11-16 05:00 | Winter | FALSE | nonsummer
2024-11-16 05:00 | 2024-11-16 06:00 | Winter | FALSE | nonsummer
2024-11-16 06:00 | 2024-11-16 07:00 | Winter | FALSE | nonsummer
2024-11-16 07:00 | 2024-11-16 08:00 | Winter | FALSE | nonsummer
2024-11-16 08:00 | 2024-11-16 09:00 | Winter | FALSE | nonsummer
2024-11-16 09:00 | 2024-11-16 10:00 | Winter | FALSE | nonsummer
2024-11-16 10:00 | 2024-11-16 11:00 | Winter | FALSE | nonsummer
2024-11-16 11:00 | 2024-11-16 12:00 | Winter | FALSE | nonsummer
2024-11-16 12:00 | 2024-11-16 13:00 | Winter | FALSE | nonsummer
2024-11-16 13:00 | 2024-11-16 14:00 | Winter | FALSE | nonsummer
2024-11-16 14:00 | 2024-11-16 15:00 | Winter | FALSE | nonsummer
2024-11-16 15:00 | 2024-11-16 16:00 | Winter | FALSE | nonsummer
2024-11-16 16:00 | 2024-11-16 17:00 | Winter | TRUE | nonsummer
2024-11-16 17:00 | 2024-11-16 18:00 | Winter | TRUE | nonsummer
2024-11-16 18:00 | 2024-11-16 19:00 | Winter | TRUE | nonsummer
2024-11-16 19:00 | 2024-11-16 20:00 | Winter | TRUE | nonsummer
2024-11-16 20:00 | 2024-11-16 21:00 | Winter | TRUE | nonsummer
2024-11-16 21:00 | 2024-11-16 22:00 | Winter | FALSE | nonsummer
2024-11-16 22:00 | 2024-11-16 23:00 | Winter | FALSE | nonsummer
2024-11-16 23:00 | 2024-11-17 | Winter | FALSE | nonsummer
2024-11-17 | 2024-11-17 01:00 | Winter | FALSE | nonsummer
2024-11-17 01:00 | 2024-11-17 02:00 | Winter | FALSE | nonsummer
2024-11-17 02:00 | 2024-11-17 03:00 | Winter | FALSE | nonsummer
2024-11-17 03:00 | 2024-11-17 04:00 | Winter | FALSE | nonsummer
2024-11-17 04:00 | 2024-11-17 05:00 | Winter | FALSE | nonsummer
2024-11-17 05:00 | 2024-11-17 06:00 | Winter | FALSE | nonsummer
2024-11-17 06:00 | 2024-11-17 07:00 | Winter | FALSE | nonsummer
2024-11-17 07:00 | 2024-11-17 08:00 | Winter | FALSE | nonsummer
2024-11-17 08:00 | 2024-11-17 09:00 | Winter | FALSE | nonsummer
2024-11-17 09:00 | 2024-11-17 10:00 | Winter | FALSE | nonsummer
2024-11-17 10:00 | 2024-11-17 11:00 | Winter | FALSE | nonsummer
2024-11-17 11:00 | 2024-11-17 12:00 | Winter | FALSE | nonsummer
2024-11-17 12:00 | 2024-11-17 13:00 | Winter | FALSE | nonsummer
2024-11-17 13:00 | 2024-11-17 14:00 | Winter | FALSE | nonsummer
2024-11-17 14:00 | 2024-11-17 15:00 | Winter | FALSE | nonsummer
2024-11-17 15:00 | 2024-11-17 16:00 | Winter | FALSE | nonsummer
2024-11-17 16:00 | 2024-11-17 17:00 | Winter | TRUE | nonsummer
2024-11-17 17:00 | 2024-11-17 18:00 | Winter | TRUE | nonsummer
2024-11-17 18:00 | 2024-11-17 19:00 | Winter | TRUE | nonsummer
2024-11-17 19:00 | 2024-11-17 20:00 | Winter | TRUE | nonsummer
2024-11-17 20:00 | 2024-11-17 21:00 | Winter | TRUE | nonsummer
2024-11-17 21:00 | 2024-11-17 22:00 | Winter | FALSE | nonsummer
2024-11-17 22:00 | 2024-11-17 23:00 | Winter | FALSE | nonsummer
2024-11-17 23:00 | 2024-11-18 | Winter | FALSE | nonsummer
2024-11-18 | 2024-11-18 01:00 | Winter | FALSE | nonsummer
2024-11-18 01:00 | 2024-11-18 02:00 | Winter | FALSE | nonsummer
2024-11-18 02:00 | 2024-11-18 03:00 | Winter | FALSE | nonsummer
2024-11-18 03:00 | 2024-11-18 04:00 | Winter | FALSE | nonsummer
2024-11-18 04:00 | 2024-11-18 05:00 | Winter | FALSE | nonsummer
2024-11-18 05:00 | 2024-11-18 06:00 | Winter | FALSE | nonsummer
2024-11-18 06:00 | 2024-11-18 07:00 | Winter | FALSE | nonsummer
2024-11-18 07:00 | 2024-11-18 08:00 | Winter | FALSE | nonsummer
2024-11-18 08:00 | 2024-11-18 09:00 | Winter | FALSE | nonsummer
2024-11-18 09:00 | 2024-11-18 10:00 | Winter | FALSE | nonsummer
2024-11-18 10:00 | 2024-11-18 11:00 | Winter | FALSE | nonsummer
2024-11-18 11:00 | 2024-11-18 12:00 | Winter | FALSE | nonsummer
2024-11-18 12:00 | 2024-11-18 13:00 | Winter | FALSE | nonsummer
2024-11-18 13:00 | 2024-11-18 14:00 | Winter | FALSE | nonsummer
2024-11-18 14:00 | 2024-11-18 15:00 | Winter | FALSE | nonsummer
2024-11-18 15:00 | 2024-11-18 16:00 | Winter | FALSE | nonsummer
2024-11-18 16:00 | 2024-11-18 17:00 | Winter | TRUE | nonsummer
2024-11-18 17:00 | 2024-11-18 18:00 | Winter | TRUE | nonsummer
2024-11-18 18:00 | 2024-11-18 19:00 | Winter | TRUE | nonsummer
2024-11-18 19:00 | 2024-11-18 20:00 | Winter | TRUE | nonsummer
2024-11-18 20:00 | 2024-11-18 21:00 | Winter | TRUE | nonsummer
2024-11-18 21:00 | 2024-11-18 22:00 | Winter | FALSE | nonsummer
2024-11-18 22:00 | 2024-11-18 23:00 | Winter | FALSE | nonsummer
2024-11-18 23:00 | 2024-11-19 | Winter | FALSE | nonsummer
2024-11-19 | 2024-11-19 01:00 | Winter | FALSE | nonsummer
2024-11-19 01:00 | 2024-11-19 02:00 | Winter | FALSE | nonsummer
2024-11-19 02:00 | 2024-11-19 03:00 | Winter | FALSE | nonsummer
2024-11-19 03:00 | 2024-11-19 04:00 | Winter | FALSE | nonsummer
2024-11-19 04:00 | 2024-11-19 05:00 | Winter | FALSE | nonsummer
2024-11-19 05:00 | 2024-11-19 06:00 | Winter | FALSE | nonsummer
2024-11-19 06:00 | 2024-11-19 07:00 | Winter | FALSE | nonsummer
2024-11-19 07:00 | 2024-11-19 08:00 | Winter | FALSE | nonsummer
2024-11-19 08:00 | 2024-11-19 09:00 | Winter | FALSE | nonsummer
2024-11-19 09:00 | 2024-11-19 10:00 | Winter | FALSE | nonsummer
2024-11-19 10:00 | 2024-11-19 11:00 | Winter | FALSE | nonsummer
2024-11-19 11:00 | 2024-11-19 12:00 | Winter | FALSE | nonsummer
2024-11-19 12:00 | 2024-11-19 13:00 | Winter | FALSE | nonsummer
2024-11-19 13:00 | 2024-11-19 14:00 | Winter | FALSE | nonsummer
2024-11-19 14:00 | 2024-11-19 15:00 | Winter | FALSE | nonsummer
2024-11-19 15:00 | 2024-11-19 16:00 | Winter | FALSE | nonsummer
2024-11-19 16:00 | 2024-11-19 17:00 | Winter | TRUE | nonsummer
2024-11-19 17:00 | 2024-11-19 18:00 | Winter | TRUE | nonsummer
2024-11-19 18:00 | 2024-11-19 19:00 | Winter | TRUE | nonsummer
2024-11-19 19:00 | 2024-11-19 20:00 | Winter | TRUE | nonsummer
2024-11-19 20:00 | 2024-11-19 21:00 | Winter | TRUE | nonsummer
2024-11-19 21:00 | 2024-11-19 22:00 | Winter | FALSE | nonsummer
2024-11-19 22:00 | 2024-11-19 23:00 | Winter | FALSE | nonsummer
2024-11-19 23:00 | 2024-11-20 | Winter | FALSE | nonsummer
2024-11-20 | 2024-11-20 01:00 | Winter | FALSE | nonsummer
2024-11-20 01:00 | 2024-11-20 02:00 | Winter | FALSE | nonsummer
2024-11-20 02:00 | 2024-11-20 03:00 | Winter | FALSE | nonsummer
2024-11-20 03:00 | 2024-11-20 04:00 | Winter | FALSE | nonsummer
2024-11-20 04:00 | 2024-11-20 05:00 | Winter | FALSE | nonsummer
2024-11-20 05:00 | 2024-11-20 06:00 | Winter | FALSE | nonsummer
2024-11-20 06:00 | 2024-11-20 07:00 | Winter | FALSE | nonsummer
2024-11-20 07:00 | 2024-11-20 08:00 | Winter | FALSE | nonsummer
2024-11-20 08:00 | 2024-11-20 09:00 | Winter | FALSE | nonsummer
2024-11-20 09:00 | 2024-11-20 10:00 | Winter | FALSE | nonsummer
2024-11-20 10:00 | 2024-11-20 11:00 | Winter | FALSE | nonsummer
2024-11-20 11:00 | 2024-11-20 12:00 | Winter | FALSE | nonsummer
2024-11-20 12:00 | 2024-11-20 13:00 | Winter | FALSE | nonsummer
2024-11-20 13:00 | 2024-11-20 14:00 | Winter | FALSE | nonsummer
2024-11-20 14:00 | 2024-11-20 15:00 | Winter | FALSE | nonsummer
2024-11-20 15:00 | 2024-11-20 16:00 | Winter | FALSE | nonsummer
2024-11-20 16:00 | 2024-11-20 17:00 | Winter | TRUE | nonsummer
2024-11-20 17:00 | 2024-11-20 18:00 | Winter | TRUE | nonsummer
2024-11-20 18:00 | 2024-11-20 19:00 | Winter | TRUE | nonsummer
2024-11-20 19:00 | 2024-11-20 20:00 | Winter | TRUE | nonsummer
2024-11-20 20:00 | 2024-11-20 21:00 | Winter | TRUE | nonsummer
2024-11-20 21:00 | 2024-11-20 22:00 | Winter | FALSE | nonsummer
2024-11-20 22:00 | 2024-11-20 23:00 | Winter | FALSE | nonsummer
2024-11-20 23:00 | 2024-11-21 | Winter | FALSE | nonsummer
2024-11-21 | 2024-11-21 01:00 | Winter | FALSE | nonsummer
2024-11-21 01:00 | 2024-11-21 02:00 | Winter | FALSE | nonsummer
2024-11-21 02:00 | 2024-11-21 03:00 | Winter | FALSE | nonsummer
2024-11-21 03:00 | 2024-11-21 04:00 | Winter | FALSE | nonsummer
2024-11-21 04:00 | 2024-11-21 05:00 | Winter | FALSE | nonsummer
2024-11-21 05:00 | 2024-11-21 06:00 | Winter | FALSE | nonsummer
2024-11-21 06:00 | 2024-11-21 07:00 | Winter | FALSE | nonsummer
2024-11-21 07:00 | 2024-11-21 08:00 | Winter | FALSE | nonsummer
2024-11-21 08:00 | 2024-11-21 09:00 | Winter | FALSE | nonsummer
2024-11-21 09:00 | 2024-11-21 10:00 | Winter | FALSE | nonsummer
2024-11-21 10:00 | 2024-11-21 11:00 | Winter | FALSE | nonsummer
2024-11-21 11:00 | 2024-11-21 12:00 | Winter | FALSE | nonsummer
2024-11-21 12:00 | 2024-11-21 13:00 | Winter | FALSE | nonsummer
2024-11-21 13:00 | 2024-11-21 14:00 | Winter | FALSE | nonsummer
2024-11-21 14:00 | 2024-11-21 15:00 | Winter | FALSE | nonsummer
2024-11-21 15:00 | 2024-11-21 16:00 | Winter | FALSE | nonsummer
2024-11-21 16:00 | 2024-11-21 17:00 | Winter | TRUE | nonsummer
2024-11-21 17:00 | 2024-11-21 18:00 | Winter | TRUE | nonsummer
2024-11-21 18:00 | 2024-11-21 19:00 | Winter | TRUE | nonsummer
2024-11-21 19:00 | 2024-11-21 20:00 | Winter | TRUE | nonsummer
2024-11-21 20:00 | 2024-11-21 21:00 | Winter | TRUE | nonsummer
2024-11-21 21:00 | 2024-11-21 22:00 | Winter | FALSE | nonsummer
2024-11-21 22:00 | 2024-11-21 23:00 | Winter | FALSE | nonsummer
2024-11-21 23:00 | 2024-11-22 | Winter | FALSE | nonsummer
2024-11-22 | 2024-11-22 01:00 | Winter | FALSE | nonsummer
2024-11-22 01:00 | 2024-11-22 02:00 | Winter | FALSE | nonsummer
2024-11-22 02:00 | 2024-11-22 03:00 | Winter | FALSE | nonsummer
2024-11-22 03:00 | 2024-11-22 04:00 | Winter | FALSE | nonsummer
2024-11-22 04:00 | 2024-11-22 05:00 | Winter | FALSE | nonsummer
2024-11-22 05:00 | 2024-11-22 06:00 | Winter | FALSE | nonsummer
2024-11-22 06:00 | 2024-11-22 07:00 | Winter | FALSE | nonsummer
2024-11-22 07:00 | 2024-11-22 08:00 | Winter | FALSE | nonsummer
2024-11-22 08:00 | 2024-11-22 09:00 | Winter | FALSE | nonsummer
2024-11-22 09:00 | 2024-11-22 10:00 | Winter | FALSE | nonsummer
2024-11-22 10:00 | 2024-11-22 11:00 | Winter | FALSE | nonsummer
2024-11-22 11:00 | 2024-11-22 12:00 | Winter | FALSE | nonsummer
2024-11-22 12:00 | 2024-11-22 13:00 | Winter | FALSE | nonsummer
2024-11-22 13:00 | 2024-11-22 14:00 | Winter | FALSE | nonsummer
2024-11-22 14:00 | 2024-11-22 15:00 | Winter | FALSE | nonsummer
2024-11-22 15:00 | 2024-11-22 16:00 | Winter | FALSE | nonsummer
2024-11-22 16:00 | 2024-11-22 17:00 | Winter | TRUE | nonsummer
2024-11-22 17:00 | 2024-11-22 18:00 | Winter | TRUE | nonsummer
2024-11-22 18:00 | 2024-11-22 19:00 | Winter | TRUE | nonsummer
2024-11-22 19:00 | 2024-11-22 20:00 | Winter | TRUE | nonsummer
2024-11-22 20:00 | 2024-11-22 21:00 | Winter | TRUE | nonsummer
2024-11-22 21:00 | 2024-11-22 22:00 | Winter | FALSE | nonsummer
2024-11-22 22:00 | 2024-11-22 23:00 | Winter | FALSE | nonsummer
2024-11-22 23:00 | 2024-11-23 | Winter | FALSE | nonsummer
2024-11-23 | 2024-11-23 01:00 | Winter | FALSE | nonsummer
2024-11-23 01:00 | 2024-11-23 02:00 | Winter | FALSE | nonsummer
2024-11-23 02:00 | 2024-11-23 03:00 | Winter | FALSE | nonsummer
2024-11-23 03:00 | 2024-11-23 04:00 | Winter | FALSE | nonsummer
2024-11-23 04:00 | 2024-11-23 05:00 | Winter | FALSE | nonsummer
2024-11-23 05:00 | 2024-11-23 06:00 | Winter | FALSE | nonsummer
2024-11-23 06:00 | 2024-11-23 07:00 | Winter | FALSE | nonsummer
2024-11-23 07:00 | 2024-11-23 08:00 | Winter | FALSE | nonsummer
2024-11-23 08:00 | 2024-11-23 09:00 | Winter | FALSE | nonsummer
2024-11-23 09:00 | 2024-11-23 10:00 | Winter | FALSE | nonsummer
2024-11-23 10:00 | 2024-11-23 11:00 | Winter | FALSE | nonsummer
2024-11-23 11:00 | 2024-11-23 12:00 | Winter | FALSE | nonsummer
2024-11-23 12:00 | 2024-11-23 13:00 | Winter | FALSE | nonsummer
2024-11-23 13:00 | 2024-11-23 14:00 | Winter | FALSE | nonsummer
2024-11-23 14:00 | 2024-11-23 15:00 | Winter | FALSE | nonsummer
2024-11-23 15:00 | 2024-11-23 16:00 | Winter | FALSE | nonsummer
2024-11-23 16:00 | 2024-11-23 17:00 | Winter | TRUE | nonsummer
2024-11-23 17:00 | 2024-11-23 18:00 | Winter | TRUE | nonsummer
2024-11-23 18:00 | 2024-11-23 19:00 | Winter | TRUE | nonsummer
2024-11-23 19:00 | 2024-11-23 20:00 | Winter | TRUE | nonsummer
2024-11-23 20:00 | 2024-11-23 21:00 | Winter | TRUE | nonsummer
2024-11-23 21:00 | 2024-11-23 22:00 | Winter | FALSE | nonsummer
2024-11-23 22:00 | 2024-11-23 23:00 | Winter | FALSE | nonsummer
2024-11-23 23:00 | 2024-11-24 | Winter | FALSE | nonsummer
2024-11-24 | 2024-11-24 01:00 | Winter | FALSE | nonsummer
2024-11-24 01:00 | 2024-11-24 02:00 | Winter | FALSE | nonsummer
2024-11-24 02:00 | 2024-11-24 03:00 | Winter | FALSE | nonsummer
2024-11-24 03:00 | 2024-11-24 04:00 | Winter | FALSE | nonsummer
2024-11-24 04:00 | 2024-11-24 05:00 | Winter | FALSE | nonsummer
2024-11-24 05:00 | 2024-11-24 06:00 | Winter | FALSE | nonsummer
2024-11-24 06:00 | 2024-11-24 07:00 | Winter | FALSE | nonsummer
2024-11-24 07:00 | 2024-11-24 08:00 | Winter | FALSE | nonsummer
2024-11-24 08:00 | 2024-11-24 09:00 | Winter | FALSE | nonsummer
2024-11-24 09:00 | 2024-11-24 10:00 | Winter | FALSE | nonsummer
2024-11-24 10:00 | 2024-11-24 11:00 | Winter | FALSE | nonsummer
2024-11-24 11:00 | 2024-11-24 12:00 | Winter | FALSE | nonsummer
2024-11-24 12:00 | 2024-11-24 13:00 | Winter | FALSE | nonsummer
2024-11-24 13:00 | 2024-11-24 14:00 | Winter | FALSE | nonsummer
2024-11-24 14:00 | 2024-11-24 15:00 | Winter | FALSE | nonsummer
2024-11-24 15:00 | 2024-11-24 16:00 | Winter | FALSE | nonsummer
2024-11-24 16:00 | 2024-11-24 17:00 | Winter | TRUE | nonsummer
2024-11-24 17:00 | 2024-11-24 18:00 | Winter | TRUE | nonsummer
2024-11-24 18:00 | 2024-11-24 19:00 | Winter | TRUE | nonsummer
2024-11-24 19:00 | 2024-11-24 20:00 | Winter | TRUE | nonsummer
2024-11-24 20:00 | 2024-11-24 21:00 | Winter | TRUE | nonsummer
2024-11-24 21:00 | 2024-11-24 22:00 | Winter | FALSE | nonsummer
2024-11-24 22:00 | 2024-11-24 23:00 | Winter | FALSE | nonsummer
2024-11-24 23:00 | 2024-11-25 | Winter | FALSE | nonsummer
2024-11-25 | 2024-11-25 01:00 | Winter | FALSE | nonsummer
2024-11-25 01:00 | 2024-11-25 02:00 | Winter | FALSE | nonsummer
2024-11-25 02:00 | 2024-11-25 03:00 | Winter | FALSE | nonsummer
2024-11-25 03:00 | 2024-11-25 04:00 | Winter | FALSE | nonsummer
2024-11-25 04:00 | 2024-11-25 05:00 | Winter | FALSE | nonsummer
2024-11-25 05:00 | 2024-11-25 06:00 | Winter | FALSE | nonsummer
2024-11-25 06:00 | 2024-11-25 07:00 | Winter | FALSE | nonsummer
2024-11-25 07:00 | 2024-11-25 08:00 | Winter | FALSE | nonsummer
2024-11-25 08:00 | 2024-11-25 09:00 | Winter | FALSE | nonsummer
2024-11-25 09:00 | 2024-11-25 10:00 | Winter | FALSE | nonsummer
2024-11-25 10:00 | 2024-11-25 11:00 | Winter | FALSE | nonsummer
2024-11-25 11:00 | 2024-11-25 12:00 | Winter | FALSE | nonsummer
2024-11-25 12:00 | 2024-11-25 13:00 | Winter | FALSE | nonsummer
2024-11-25 13:00 | 2024-11-25 14:00 | Winter | FALSE | nonsummer
2024-11-25 14:00 | 2024-11-25 15:00 | Winter | FALSE | nonsummer
2024-11-25 15:00 | 2024-11-25 16:00 | Winter | FALSE | nonsummer
2024-11-25 16:00 | 2024-11-25 17:00 | Winter | TRUE | nonsummer
2024-11-25 17:00 | 2024-11-25 18:00 | Winter | TRUE | nonsummer
2024-11-25 18:00 | 2024-11-25 19:00 | Winter | TRUE | nonsummer
2024-11-25 19:00 | 2024-11-25 20:00 | Winter | TRUE | nonsummer
2024-11-25 20:00 | 2024-11-25 21:00 | Winter | TRUE | nonsummer
2024-11-25 21:00 | 2024-11-25 22:00 | Winter | FALSE | nonsummer
2024-11-25 22:00 | 2024-11-25 23:00 | Winter | FALSE | nonsummer
2024-11-25 23:00 | 2024-11-26 | Winter | FALSE | nonsummer
2024-11-26 | 2024-11-26 01:00 | Winter | FALSE | nonsummer
2024-11-26 01:00 | 2024-11-26 02:00 | Winter | FALSE | nonsummer
2024-11-26 02:00 | 2024-11-26 03:00 | Winter | FALSE | nonsummer
2024-11-26 03:00 | 2024-11-26 04:00 | Winter | FALSE | nonsummer
2024-11-26 04:00 | 2024-11-26 05:00 | Winter | FALSE | nonsummer
2024-11-26 05:00 | 2024-11-26 06:00 | Winter | FALSE | nonsummer
2024-11-26 06:00 | 2024-11-26 07:00 | Winter | FALSE | nonsummer
2024-11-26 07:00 | 2024-11-26 08:00 | Winter | FALSE | nonsummer
2024-11-26 08:00 | 2024-11-26 09:00 | Winter | FALSE | nonsummer
2024-11-26 09:00 | 2024-11-26 10:00 | Winter | FALSE | nonsummer
2024-11-26 10:00 | 2024-11-26 11:00 | Winter | FALSE | nonsummer
2024-11-26 11:00 | 2024-11-26 12:00 | Winter | FALSE | nonsummer
2024-11-26 12:00 | 2024-11-26 13:00 | Winter | FALSE | nonsummer
2024-11-26 13:00 | 2024-11-26 14:00 | Winter | FALSE | nonsummer
2024-11-26 14:00 | 2024-11-26 15:00 | Winter | FALSE | nonsummer
2024-11-26 15:00 | 2024-11-26 16:00 | Winter | FALSE | nonsummer
2024-11-26 16:00 | 2024-11-26 17:00 | Winter | TRUE | nonsummer
2024-11-26 17:00 | 2024-11-26 18:00 | Winter | TRUE | nonsummer
2024-11-26 18:00 | 2024-11-26 19:00 | Winter | TRUE | nonsummer
2024-11-26 19:00 | 2024-11-26 20:00 | Winter | TRUE | nonsummer
2024-11-26 20:00 | 2024-11-26 21:00 | Winter | TRUE | nonsummer
2024-11-26 21:00 | 2024-11-26 22:00 | Winter | FALSE | nonsummer
2024-11-26 22:00 | 2024-11-26 23:00 | Winter | FALSE | nonsummer
2024-11-26 23:00 | 2024-11-27 | Winter | FALSE | nonsummer
2024-11-27 | 2024-11-27 01:00 | Winter | FALSE | nonsummer
2024-11-27 01:00 | 2024-11-27 02:00 | Winter | FALSE | nonsummer
2024-11-27 02:00 | 2024-11-27 03:00 | Winter | FALSE | nonsummer
2024-11-27 03:00 | 2024-11-27 04:00 | Winter | FALSE | nonsummer
2024-11-27 04:00 | 2024-11-27 05:00 | Winter | FALSE | nonsummer
2024-11-27 05:00 | 2024-11-27 06:00 | Winter | FALSE | nonsummer
2024-11-27 06:00 | 2024-11-27 07:00 | Winter | FALSE | nonsummer
2024-11-27 07:00 | 2024-11-27 08:00 | Winter | FALSE | nonsummer
2024-11-27 08:00 | 2024-11-27 09:00 | Winter | FALSE | nonsummer
2024-11-27 09:00 | 2024-11-27 10:00 | Winter | FALSE | nonsummer
2024-11-27 10:00 | 2024-11-27 11:00 | Winter | FALSE | nonsummer
2024-11-27 11:00 | 2024-11-27 12:00 | Winter | FALSE | nonsummer
2024-11-27 12:00 | 2024-11-27 13:00 | Winter | FALSE | nonsummer
2024-11-27 13:00 | 2024-11-27 14:00 | Winter | FALSE | nonsummer
2024-11-27 14:00 | 2024-11-27 15:00 | Winter | FALSE | nonsummer
2024-11-27 15:00 | 2024-11-27 16:00 | Winter | FALSE | nonsummer
2024-11-27 16:00 | 2024-11-27 17:00 | Winter | TRUE | nonsummer
2024-11-27 17:00 | 2024-11-27 18:00 | Winter | TRUE | nonsummer
2024-11-27 18:00 | 2024-11-27 19:00 | Winter | TRUE | nonsummer
2024-11-27 19:00 | 2024-11-27 20:00 | Winter | TRUE | nonsummer
2024-11-27 20:00 | 2024-11-27 21:00 | Winter | TRUE | nonsummer
2024-11-27 21:00 | 2024-11-27 22:00 | Winter | FALSE | nonsummer
2024-11-27 22:00 | 2024-11-27 23:00 | Winter | FALSE | nonsummer
2024-11-27 23:00 | 2024-11-28 | Winter | FALSE | nonsummer
2024-11-28 | 2024-11-28 01:00 | Winter | FALSE | nonsummer
2024-11-28 01:00 | 2024-11-28 02:00 | Winter | FALSE | nonsummer
2024-11-28 02:00 | 2024-11-28 03:00 | Winter | FALSE | nonsummer
2024-11-28 03:00 | 2024-11-28 04:00 | Winter | FALSE | nonsummer
2024-11-28 04:00 | 2024-11-28 05:00 | Winter | FALSE | nonsummer
2024-11-28 05:00 | 2024-11-28 06:00 | Winter | FALSE | nonsummer
2024-11-28 06:00 | 2024-11-28 07:00 | Winter | FALSE | nonsummer
2024-11-28 07:00 | 2024-11-28 08:00 | Winter | FALSE | nonsummer
2024-11-28 08:00 | 2024-11-28 09:00 | Winter | FALSE | nonsummer
2024-11-28 09:00 | 2024-11-28 10:00 | Winter | FALSE | nonsummer
2024-11-28 10:00 | 2024-11-28 11:00 | Winter | FALSE | nonsummer
2024-11-28 11:00 | 2024-11-28 12:00 | Winter | FALSE | nonsummer
2024-11-28 12:00 | 2024-11-28 13:00 | Winter | FALSE | nonsummer
2024-11-28 13:00 | 2024-11-28 14:00 | Winter | FALSE | nonsummer
2024-11-28 14:00 | 2024-11-28 15:00 | Winter | FALSE | nonsummer
2024-11-28 15:00 | 2024-11-28 16:00 | Winter | FALSE | nonsummer
2024-11-28 16:00 | 2024-11-28 17:00 | Winter | TRUE | nonsummer
2024-11-28 17:00 | 2024-11-28 18:00 | Winter | TRUE | nonsummer
2024-11-28 18:00 | 2024-11-28 19:00 | Winter | TRUE | nonsummer
2024-11-28 19:00 | 2024-11-28 20:00 | Winter | TRUE | nonsummer
2024-11-28 20:00 | 2024-11-28 21:00 | Winter | TRUE | nonsummer
2024-11-28 21:00 | 2024-11-28 22:00 | Winter | FALSE | nonsummer
2024-11-28 22:00 | 2024-11-28 23:00 | Winter | FALSE | nonsummer
2024-11-28 23:00 | 2024-11-29 | Winter | FALSE | nonsummer
2024-11-29 | 2024-11-29 01:00 | Winter | FALSE | nonsummer
2024-11-29 01:00 | 2024-11-29 02:00 | Winter | FALSE | nonsummer
2024-11-29 02:00 | 2024-11-29 03:00 | Winter | FALSE | nonsummer
2024-11-29 03:00 | 2024-11-29 04:00 | Winter | FALSE | nonsummer
2024-11-29 04:00 | 2024-11-29 05:00 | Winter | FALSE | nonsummer
2024-11-29 05:00 | 2024-11-29 06:00 | Winter | FALSE | nonsummer
2024-11-29 06:00 | 2024-11-29 07:00 | Winter | FALSE | nonsummer
2024-11-29 07:00 | 2024-11-29 08:00 | Winter | FALSE | nonsummer
2024-11-29 08:00 | 2024-11-29 09:00 | Winter | FALSE | nonsummer
2024-11-29 09:00 | 2024-11-29 10:00 | Winter | FALSE | nonsummer
2024-11-29 10:00 | 2024-11-29 11:00 | Winter | FALSE | nonsummer
2024-11-29 11:00 | 2024-11-29 12:00 | Winter | FALSE | nonsummer
2024-11-29 12:00 | 2024-11-29 13:00 | Winter | FALSE | nonsummer
2024-11-29 13:00 | 2024-11-29 14:00 | Winter | FALSE | nonsummer
2024-11-29 14:00 | 2024-11-29 15:00 | Winter | FALSE | nonsummer
2024-11-29 15:00 | 2024-11-29 16:00 | Winter | FALSE | nonsummer
2024-11-29 16:00 | 2024-11-29 17:00 | Winter | TRUE | nonsummer
2024-11-29 17:00 | 2024-11-29 18:00 | Winter | TRUE | nonsummer
2024-11-29 18:00 | 2024-11-29 19:00 | Winter | TRUE | nonsummer
2024-11-29 19:00 | 2024-11-29 20:00 | Winter | TRUE | nonsummer
2024-11-29 20:00 | 2024-11-29 21:00 | Winter | TRUE | nonsummer
2024-11-29 21:00 | 2024-11-29 22:00 | Winter | FALSE | nonsummer
2024-11-29 22:00 | 2024-11-29 23:00 | Winter | FALSE | nonsummer
2024-11-29 23:00 | 2024-11-30 | Winter | FALSE | nonsummer
2024-11-30 | 2024-11-30 01:00 | Winter | FALSE | nonsummer
2024-11-30 01:00 | 2024-11-30 02:00 | Winter | FALSE | nonsummer
2024-11-30 02:00 | 2024-11-30 03:00 | Winter | FALSE | nonsummer
2024-11-30 03:00 | 2024-11-30 04:00 | Winter | FALSE | nonsummer
2024-11-30 04:00 | 2024-11-30 05:00 | Winter | FALSE | nonsummer
2024-11-30 05:00 | 2024-11-30 06:00 | Winter | FALSE | nonsummer
2024-11-30 06:00 | 2024-11-30 07:00 | Winter | FALSE | nonsummer
2024-11-30 07:00 | 2024-11-30 08:00 | Winter | FALSE | nonsummer
2024-11-30 08:00 | 2024-11-30 09:00 | Winter | FALSE | nonsummer
2024-11-30 09:00 | 2024-11-30 10:00 | Winter | FALSE | nonsummer
2024-11-30 10:00 | 2024-11-30 11:00 | Winter | FALSE | nonsummer
2024-11-30 11:00 | 2024-11-30 12:00 | Winter | FALSE | nonsummer
2024-11-30 12:00 | 2024-11-30 13:00 | Winter | FALSE | nonsummer
2024-11-30 13:00 | 2024-11-30 14:00 | Winter | FALSE | nonsummer
2024-11-30 14:00 | 2024-11-30 15:00 | Winter | FALSE | nonsummer
2024-11-30 15:00 | 2024-11-30 16:00 | Winter | FALSE | nonsummer
2024-11-30 16:00 | 2024-11-30 17:00 | Winter | TRUE | nonsummer
2024-11-30 17:00 | 2024-11-30 18:00 | Winter | TRUE | nonsummer
2024-11-30 18:00 | 2024-11-30 19:00 | Winter | TRUE | nonsummer
2024-11-30 19:00 | 2024-11-30 20:00 | Winter | TRUE | nonsummer
2024-11-30 20:00 | 2024-11-30 21:00 | Winter | TRUE | nonsummer
2024-11-30 21:00 | 2024-11-30 22:00 | Winter | FALSE | nonsummer
2024-11-30 22:00 | 2024-11-30 23:00 | Winter | FALSE | nonsummer
2024-11-30 23:00 | 2024-12-01 | Winter | FALSE | nonsummer
2024-12-01 | 2024-12-01 01:00 | Winter | FALSE | nonsummer
2024-12-01 01:00 | 2024-12-01 02:00 | Winter | FALSE | nonsummer
2024-12-01 02:00 | 2024-12-01 03:00 | Winter | FALSE | nonsummer
2024-12-01 03:00 | 2024-12-01 04:00 | Winter | FALSE | nonsummer
2024-12-01 04:00 | 2024-12-01 05:00 | Winter | FALSE | nonsummer
2024-12-01 05:00 | 2024-12-01 06:00 | Winter | FALSE | nonsummer
2024-12-01 06:00 | 2024-12-01 07:00 | Winter | FALSE | nonsummer
2024-12-01 07:00 | 2024-12-01 08:00 | Winter | FALSE | nonsummer
2024-12-01 08:00 | 2024-12-01 09:00 | Winter | FALSE | nonsummer
2024-12-01 09:00 | 2024-12-01 10:00 | Winter | FALSE | nonsummer
2024-12-01 10:00 | 2024-12-01 11:00 | Winter | FALSE | nonsummer
2024-12-01 11:00 | 2024-12-01 12:00 | Winter | FALSE | nonsummer
2024-12-01 12:00 | 2024-12-01 13:00 | Winter | FALSE | nonsummer
2024-12-01 13:00 | 2024-12-01 14:00 | Winter | FALSE | nonsummer
2024-12-01 14:00 | 2024-12-01 15:00 | Winter | FALSE | nonsummer
2024-12-01 15:00 | 2024-12-01 16:00 | Winter | FALSE | nonsummer
2024-12-01 16:00 | 2024-12-01 17:00 | Winter | TRUE | nonsummer
2024-12-01 17:00 | 2024-12-01 18:00 | Winter | TRUE | nonsummer
2024-12-01 18:00 | 2024-12-01 19:00 | Winter | TRUE | nonsummer
2024-12-01 19:00 | 2024-12-01 20:00 | Winter | TRUE | nonsummer
2024-12-01 20:00 | 2024-12-01 21:00 | Winter | TRUE | nonsummer
2024-12-01 21:00 | 2024-12-01 22:00 | Winter | FALSE | nonsummer
2024-12-01 22:00 | 2024-12-01 23:00 | Winter | FALSE | nonsummer
2024-12-01 23:00 | 2024-12-02 | Winter | FALSE | nonsummer
2024-12-02 | 2024-12-02 01:00 | Winter | FALSE | nonsummer
2024-12-02 01:00 | 2024-12-02 02:00 | Winter | FALSE | nonsummer
2024-12-02 02:00 | 2024-12-02 03:00 | Winter | FALSE | nonsummer
2024-12-02 03:00 | 2024-12-02 04:00 | Winter | FALSE | nonsummer
2024-12-02 04:00 | 2024-12-02 05:00 | Winter | FALSE | nonsummer
2024-12-02 05:00 | 2024-12-02 06:00 | Winter | FALSE | nonsummer
2024-12-02 06:00 | 2024-12-02 07:00 | Winter | FALSE | nonsummer
2024-12-02 07:00 | 2024-12-02 08:00 | Winter | FALSE | nonsummer
2024-12-02 08:00 | 2024-12-02 09:00 | Winter | FALSE | nonsummer
2024-12-02 09:00 | 2024-12-02 10:00 | Winter | FALSE | nonsummer
2024-12-02 10:00 | 2024-12-02 11:00 | Winter | FALSE | nonsummer
2024-12-02 11:00 | 2024-12-02 12:00 | Winter | FALSE | nonsummer
2024-12-02 12:00 | 2024-12-02 13:00 | Winter | FALSE | nonsummer
2024-12-02 13:00 | 2024-12-02 14:00 | Winter | FALSE | nonsummer
2024-12-02 14:00 | 2024-12-02 15:00 | Winter | FALSE | nonsummer
2024-12-02 15:00 | 2024-12-02 16:00 | Winter | FALSE | nonsummer
2024-12-02 16:00 | 2024-12-02 17:00 | Winter | TRUE | nonsummer
2024-12-02 17:00 | 2024-12-02 18:00 | Winter | TRUE | nonsummer
2024-12-02 18:00 | 2024-12-02 19:00 | Winter | TRUE | nonsummer
2024-12-02 19:00 | 2024-12-02 20:00 | Winter | TRUE | nonsummer
2024-12-02 20:00 | 2024-12-02 21:00 | Winter | TRUE | nonsummer
2024-12-02 21:00 | 2024-12-02 22:00 | Winter | FALSE | nonsummer
2024-12-02 22:00 | 2024-12-02 23:00 | Winter | FALSE | nonsummer
2024-12-02 23:00 | 2024-12-03 | Winter | FALSE | nonsummer
2024-12-03 | 2024-12-03 01:00 | Winter | FALSE | nonsummer
2024-12-03 01:00 | 2024-12-03 02:00 | Winter | FALSE | nonsummer
2024-12-03 02:00 | 2024-12-03 03:00 | Winter | FALSE | nonsummer
2024-12-03 03:00 | 2024-12-03 04:00 | Winter | FALSE | nonsummer
2024-12-03 04:00 | 2024-12-03 05:00 | Winter | FALSE | nonsummer
2024-12-03 05:00 | 2024-12-03 06:00 | Winter | FALSE | nonsummer
2024-12-03 06:00 | 2024-12-03 07:00 | Winter | FALSE | nonsummer
2024-12-03 07:00 | 2024-12-03 08:00 | Winter | FALSE | nonsummer
2024-12-03 08:00 | 2024-12-03 09:00 | Winter | FALSE | nonsummer
2024-12-03 09:00 | 2024-12-03 10:00 | Winter | FALSE | nonsummer
2024-12-03 10:00 | 2024-12-03 11:00 | Winter | FALSE | nonsummer
2024-12-03 11:00 | 2024-12-03 12:00 | Winter | FALSE | nonsummer
2024-12-03 12:00 | 2024-12-03 13:00 | Winter | FALSE | nonsummer
2024-12-03 13:00 | 2024-12-03 14:00 | Winter | FALSE | nonsummer
2024-12-03 14:00 | 2024-12-03 15:00 | Winter | FALSE | nonsummer
2024-12-03 15:00 | 2024-12-03 16:00 | Winter | FALSE | nonsummer
2024-12-03 16:00 | 2024-12-03 17:00 | Winter | TRUE | nonsummer
2024-12-03 17:00 | 2024-12-03 18:00 | Winter | TRUE | nonsummer
2024-12-03 18:00 | 2024-12-03 19:00 | Winter | TRUE | nonsummer
2024-12-03 19:00 | 2024-12-03 20:00 | Winter | TRUE | nonsummer
2024-12-03 20:00 | 2024-12-03 21:00 | Winter | TRUE | nonsummer
2024-12-03 21:00 | 2024-12-03 22:00 | Winter | FALSE | nonsummer
2024-12-03 22:00 | 2024-12-03 23:00 | Winter | FALSE | nonsummer
2024-12-03 23:00 | 2024-12-04 | Winter | FALSE | nonsummer
2024-12-04 | 2024-12-04 01:00 | Winter | FALSE | nonsummer
2024-12-04 01:00 | 2024-12-04 02:00 | Winter | FALSE | nonsummer
2024-12-04 02:00 | 2024-12-04 03:00 | Winter | FALSE | nonsummer
2024-12-04 03:00 | 2024-12-04 04:00 | Winter | FALSE | nonsummer
2024-12-04 04:00 | 2024-12-04 05:00 | Winter | FALSE | nonsummer
2024-12-04 05:00 | 2024-12-04 06:00 | Winter | FALSE | nonsummer
2024-12-04 06:00 | 2024-12-04 07:00 | Winter | FALSE | nonsummer
2024-12-04 07:00 | 2024-12-04 08:00 | Winter | FALSE | nonsummer
2024-12-04 08:00 | 2024-12-04 09:00 | Winter | FALSE | nonsummer
2024-12-04 09:00 | 2024-12-04 10:00 | Winter | FALSE | nonsummer
2024-12-04 10:00 | 2024-12-04 11:00 | Winter | FALSE | nonsummer
2024-12-04 11:00 | 2024-12-04 12:00 | Winter | FALSE | nonsummer
2024-12-04 12:00 | 2024-12-04 13:00 | Winter | FALSE | nonsummer
2024-12-04 13:00 | 2024-12-04 14:00 | Winter | FALSE | nonsummer
2024-12-04 14:00 | 2024-12-04 15:00 | Winter | FALSE | nonsummer
2024-12-04 15:00 | 2024-12-04 16:00 | Winter | FALSE | nonsummer
2024-12-04 16:00 | 2024-12-04 17:00 | Winter | TRUE | nonsummer
2024-12-04 17:00 | 2024-12-04 18:00 | Winter | TRUE | nonsummer
2024-12-04 18:00 | 2024-12-04 19:00 | Winter | TRUE | nonsummer
2024-12-04 19:00 | 2024-12-04 20:00 | Winter | TRUE | nonsummer
2024-12-04 20:00 | 2024-12-04 21:00 | Winter | TRUE | nonsummer
2024-12-04 21:00 | 2024-12-04 22:00 | Winter | FALSE | nonsummer
2024-12-04 22:00 | 2024-12-04 23:00 | Winter | FALSE | nonsummer
2024-12-04 23:00 | 2024-12-05 | Winter | FALSE | nonsummer
2024-12-05 | 2024-12-05 01:00 | Winter | FALSE | nonsummer
2024-12-05 01:00 | 2024-12-05 02:00 | Winter | FALSE | nonsummer
2024-12-05 02:00 | 2024-12-05 03:00 | Winter | FALSE | nonsummer
2024-12-05 03:00 | 2024-12-05 04:00 | Winter | FALSE | nonsummer
2024-12-05 04:00 | 2024-12-05 05:00 | Winter | FALSE | nonsummer
2024-12-05 05:00 | 2024-12-05 06:00 | Winter | FALSE | nonsummer
2024-12-05 06:00 | 2024-12-05 07:00 | Winter | FALSE | nonsummer
2024-12-05 07:00 | 2024-12-05 08:00 | Winter | FALSE | nonsummer
2024-12-05 08:00 | 2024-12-05 09:00 | Winter | FALSE | nonsummer
2024-12-05 09:00 | 2024-12-05 10:00 | Winter | FALSE | nonsummer
2024-12-05 10:00 | 2024-12-05 11:00 | Winter | FALSE | nonsummer
2024-12-05 11:00 | 2024-12-05 12:00 | Winter | FALSE | nonsummer
2024-12-05 12:00 | 2024-12-05 13:00 | Winter | FALSE | nonsummer
2024-12-05 13:00 | 2024-12-05 14:00 | Winter | FALSE | nonsummer
2024-12-05 14:00 | 2024-12-05 15:00 | Winter | FALSE | nonsummer
2024-12-05 15:00 | 2024-12-05 16:00 | Winter | FALSE | nonsummer
2024-12-05 16:00 | 2024-12-05 17:00 | Winter | TRUE | nonsummer
2024-12-05 17:00 | 2024-12-05 18:00 | Winter | TRUE | nonsummer
2024-12-05 18:00 | 2024-12-05 19:00 | Winter | TRUE | nonsummer
2024-12-05 19:00 | 2024-12-05 20:00 | Winter | TRUE | nonsummer
2024-12-05 20:00 | 2024-12-05 21:00 | Winter | TRUE | nonsummer
2024-12-05 21:00 | 2024-12-05 22:00 | Winter | FALSE | nonsummer
2024-12-05 22:00 | 2024-12-05 23:00 | Winter | FALSE | nonsummer
2024-12-05 23:00 | 2024-12-06 | Winter | FALSE | nonsummer
2024-12-06 | 2024-12-06 01:00 | Winter | FALSE | nonsummer
2024-12-06 01:00 | 2024-12-06 02:00 | Winter | FALSE | nonsummer
2024-12-06 02:00 | 2024-12-06 03:00 | Winter | FALSE | nonsummer
2024-12-06 03:00 | 2024-12-06 04:00 | Winter | FALSE | nonsummer
2024-12-06 04:00 | 2024-12-06 05:00 | Winter | FALSE | nonsummer
2024-12-06 05:00 | 2024-12-06 06:00 | Winter | FALSE | nonsummer
2024-12-06 06:00 | 2024-12-06 07:00 | Winter | FALSE | nonsummer
2024-12-06 07:00 | 2024-12-06 08:00 | Winter | FALSE | nonsummer
2024-12-06 08:00 | 2024-12-06 09:00 | Winter | FALSE | nonsummer
2024-12-06 09:00 | 2024-12-06 10:00 | Winter | FALSE | nonsummer
2024-12-06 10:00 | 2024-12-06 11:00 | Winter | FALSE | nonsummer
2024-12-06 11:00 | 2024-12-06 12:00 | Winter | FALSE | nonsummer
2024-12-06 12:00 | 2024-12-06 13:00 | Winter | FALSE | nonsummer
2024-12-06 13:00 | 2024-12-06 14:00 | Winter | FALSE | nonsummer
2024-12-06 14:00 | 2024-12-06 15:00 | Winter | FALSE | nonsummer
2024-12-06 15:00 | 2024-12-06 16:00 | Winter | FALSE | nonsummer
2024-12-06 16:00 | 2024-12-06 17:00 | Winter | TRUE | nonsummer
2024-12-06 17:00 | 2024-12-06 18:00 | Winter | TRUE | nonsummer
2024-12-06 18:00 | 2024-12-06 19:00 | Winter | TRUE | nonsummer
2024-12-06 19:00 | 2024-12-06 20:00 | Winter | TRUE | nonsummer
2024-12-06 20:00 | 2024-12-06 21:00 | Winter | TRUE | nonsummer
2024-12-06 21:00 | 2024-12-06 22:00 | Winter | FALSE | nonsummer
2024-12-06 22:00 | 2024-12-06 23:00 | Winter | FALSE | nonsummer
2024-12-06 23:00 | 2024-12-07 | Winter | FALSE | nonsummer
2024-12-07 | 2024-12-07 01:00 | Winter | FALSE | nonsummer
2024-12-07 01:00 | 2024-12-07 02:00 | Winter | FALSE | nonsummer
2024-12-07 02:00 | 2024-12-07 03:00 | Winter | FALSE | nonsummer
2024-12-07 03:00 | 2024-12-07 04:00 | Winter | FALSE | nonsummer
2024-12-07 04:00 | 2024-12-07 05:00 | Winter | FALSE | nonsummer
2024-12-07 05:00 | 2024-12-07 06:00 | Winter | FALSE | nonsummer
2024-12-07 06:00 | 2024-12-07 07:00 | Winter | FALSE | nonsummer
2024-12-07 07:00 | 2024-12-07 08:00 | Winter | FALSE | nonsummer
2024-12-07 08:00 | 2024-12-07 09:00 | Winter | FALSE | nonsummer
2024-12-07 09:00 | 2024-12-07 10:00 | Winter | FALSE | nonsummer
2024-12-07 10:00 | 2024-12-07 11:00 | Winter | FALSE | nonsummer
2024-12-07 11:00 | 2024-12-07 12:00 | Winter | FALSE | nonsummer
2024-12-07 12:00 | 2024-12-07 13:00 | Winter | FALSE | nonsummer
2024-12-07 13:00 | 2024-12-07 14:00 | Winter | FALSE | nonsummer
2024-12-07 14:00 | 2024-12-07 15:00 | Winter | FALSE | nonsummer
2024-12-07 15:00 | 2024-12-07 16:00 | Winter | FALSE | nonsummer
2024-12-07 16:00 | 2024-12-07 17:00 | Winter | TRUE | nonsummer
2024-12-07 17:00 | 2024-12-07 18:00 | Winter | TRUE | nonsummer
2024-12-07 18:00 | 2024-12-07 19:00 | Winter | TRUE | nonsummer
2024-12-07 19:00 | 2024-12-07 20:00 | Winter | TRUE | nonsummer
2024-12-07 20:00 | 2024-12-07 21:00 | Winter | TRUE | nonsummer
2024-12-07 21:00 | 2024-12-07 22:00 | Winter | FALSE | nonsummer
2024-12-07 22:00 | 2024-12-07 23:00 | Winter | FALSE | nonsummer
2024-12-07 23:00 | 2024-12-08 | Winter | FALSE | nonsummer
2024-12-08 | 2024-12-08 01:00 | Winter | FALSE | nonsummer
2024-12-08 01:00 | 2024-12-08 02:00 | Winter | FALSE | nonsummer
2024-12-08 02:00 | 2024-12-08 03:00 | Winter | FALSE | nonsummer
2024-12-08 03:00 | 2024-12-08 04:00 | Winter | FALSE | nonsummer
2024-12-08 04:00 | 2024-12-08 05:00 | Winter | FALSE | nonsummer
2024-12-08 05:00 | 2024-12-08 06:00 | Winter | FALSE | nonsummer
2024-12-08 06:00 | 2024-12-08 07:00 | Winter | FALSE | nonsummer
2024-12-08 07:00 | 2024-12-08 08:00 | Winter | FALSE | nonsummer
2024-12-08 08:00 | 2024-12-08 09:00 | Winter | FALSE | nonsummer
2024-12-08 09:00 | 2024-12-08 10:00 | Winter | FALSE | nonsummer
2024-12-08 10:00 | 2024-12-08 11:00 | Winter | FALSE | nonsummer
2024-12-08 11:00 | 2024-12-08 12:00 | Winter | FALSE | nonsummer
2024-12-08 12:00 | 2024-12-08 13:00 | Winter | FALSE | nonsummer
2024-12-08 13:00 | 2024-12-08 14:00 | Winter | FALSE | nonsummer
2024-12-08 14:00 | 2024-12-08 15:00 | Winter | FALSE | nonsummer
2024-12-08 15:00 | 2024-12-08 16:00 | Winter | FALSE | nonsummer
2024-12-08 16:00 | 2024-12-08 17:00 | Winter | TRUE | nonsummer
2024-12-08 17:00 | 2024-12-08 18:00 | Winter | TRUE | nonsummer
2024-12-08 18:00 | 2024-12-08 19:00 | Winter | TRUE | nonsummer
2024-12-08 19:00 | 2024-12-08 20:00 | Winter | TRUE | nonsummer
2024-12-08 20:00 | 2024-12-08 21:00 | Winter | TRUE | nonsummer
2024-12-08 21:00 | 2024-12-08 22:00 | Winter | FALSE | nonsummer
2024-12-08 22:00 | 2024-12-08 23:00 | Winter | FALSE | nonsummer
2024-12-08 23:00 | 2024-12-09 | Winter | FALSE | nonsummer
2024-12-09 | 2024-12-09 01:00 | Winter | FALSE | nonsummer
2024-12-09 01:00 | 2024-12-09 02:00 | Winter | FALSE | nonsummer
2024-12-09 02:00 | 2024-12-09 03:00 | Winter | FALSE | nonsummer
2024-12-09 03:00 | 2024-12-09 04:00 | Winter | FALSE | nonsummer
2024-12-09 04:00 | 2024-12-09 05:00 | Winter | FALSE | nonsummer
2024-12-09 05:00 | 2024-12-09 06:00 | Winter | FALSE | nonsummer
2024-12-09 06:00 | 2024-12-09 07:00 | Winter | FALSE | nonsummer
2024-12-09 07:00 | 2024-12-09 08:00 | Winter | FALSE | nonsummer
2024-12-09 08:00 | 2024-12-09 09:00 | Winter | FALSE | nonsummer
2024-12-09 09:00 | 2024-12-09 10:00 | Winter | FALSE | nonsummer
2024-12-09 10:00 | 2024-12-09 11:00 | Winter | FALSE | nonsummer
2024-12-09 11:00 | 2024-12-09 12:00 | Winter | FALSE | nonsummer
2024-12-09 12:00 | 2024-12-09 13:00 | Winter | FALSE | nonsummer
2024-12-09 13:00 | 2024-12-09 14:00 | Winter | FALSE | nonsummer
2024-12-09 14:00 | 2024-12-09 15:00 | Winter | FALSE | nonsummer
2024-12-09 15:00 | 2024-12-09 16:00 | Winter | FALSE | nonsummer
2024-12-09 16:00 | 2024-12-09 17:00 | Winter | TRUE | nonsummer
2024-12-09 17:00 | 2024-12-09 18:00 | Winter | TRUE | nonsummer
2024-12-09 18:00 | 2024-12-09 19:00 | Winter | TRUE | nonsummer
2024-12-09 19:00 | 2024-12-09 20:00 | Winter | TRUE | nonsummer
2024-12-09 20:00 | 2024-12-09 21:00 | Winter | TRUE | nonsummer
2024-12-09 21:00 | 2024-12-09 22:00 | Winter | FALSE | nonsummer
2024-12-09 22:00 | 2024-12-09 23:00 | Winter | FALSE | nonsummer
2024-12-09 23:00 | 2024-12-10 | Winter | FALSE | nonsummer
2024-12-10 | 2024-12-10 01:00 | Winter | FALSE | nonsummer
2024-12-10 01:00 | 2024-12-10 02:00 | Winter | FALSE | nonsummer
2024-12-10 02:00 | 2024-12-10 03:00 | Winter | FALSE | nonsummer
2024-12-10 03:00 | 2024-12-10 04:00 | Winter | FALSE | nonsummer
2024-12-10 04:00 | 2024-12-10 05:00 | Winter | FALSE | nonsummer
2024-12-10 05:00 | 2024-12-10 06:00 | Winter | FALSE | nonsummer
2024-12-10 06:00 | 2024-12-10 07:00 | Winter | FALSE | nonsummer
2024-12-10 07:00 | 2024-12-10 08:00 | Winter | FALSE | nonsummer
2024-12-10 08:00 | 2024-12-10 09:00 | Winter | FALSE | nonsummer
2024-12-10 09:00 | 2024-12-10 10:00 | Winter | FALSE | nonsummer
2024-12-10 10:00 | 2024-12-10 11:00 | Winter | FALSE | nonsummer
2024-12-10 11:00 | 2024-12-10 12:00 | Winter | FALSE | nonsummer
2024-12-10 12:00 | 2024-12-10 13:00 | Winter | FALSE | nonsummer
2024-12-10 13:00 | 2024-12-10 14:00 | Winter | FALSE | nonsummer
2024-12-10 14:00 | 2024-12-10 15:00 | Winter | FALSE | nonsummer
2024-12-10 15:00 | 2024-12-10 16:00 | Winter | FALSE | nonsummer
2024-12-10 16:00 | 2024-12-10 17:00 | Winter | TRUE | nonsummer
2024-12-10 17:00 | 2024-12-10 18:00 | Winter | TRUE | nonsummer
2024-12-10 18:00 | 2024-12-10 19:00 | Winter | TRUE | nonsummer
2024-12-10 19:00 | 2024-12-10 20:00 | Winter | TRUE | nonsummer
2024-12-10 20:00 | 2024-12-10 21:00 | Winter | TRUE | nonsummer
2024-12-10 21:00 | 2024-12-10 22:00 | Winter | FALSE | nonsummer
2024-12-10 22:00 | 2024-12-10 23:00 | Winter | FALSE | nonsummer
2024-12-10 23:00 | 2024-12-11 | Winter | FALSE | nonsummer
2024-12-11 | 2024-12-11 01:00 | Winter | FALSE | nonsummer
2024-12-11 01:00 | 2024-12-11 02:00 | Winter | FALSE | nonsummer
2024-12-11 02:00 | 2024-12-11 03:00 | Winter | FALSE | nonsummer
2024-12-11 03:00 | 2024-12-11 04:00 | Winter | FALSE | nonsummer
2024-12-11 04:00 | 2024-12-11 05:00 | Winter | FALSE | nonsummer
2024-12-11 05:00 | 2024-12-11 06:00 | Winter | FALSE | nonsummer
2024-12-11 06:00 | 2024-12-11 07:00 | Winter | FALSE | nonsummer
2024-12-11 07:00 | 2024-12-11 08:00 | Winter | FALSE | nonsummer
2024-12-11 08:00 | 2024-12-11 09:00 | Winter | FALSE | nonsummer
2024-12-11 09:00 | 2024-12-11 10:00 | Winter | FALSE | nonsummer
2024-12-11 10:00 | 2024-12-11 11:00 | Winter | FALSE | nonsummer
2024-12-11 11:00 | 2024-12-11 12:00 | Winter | FALSE | nonsummer
2024-12-11 12:00 | 2024-12-11 13:00 | Winter | FALSE | nonsummer
2024-12-11 13:00 | 2024-12-11 14:00 | Winter | FALSE | nonsummer
2024-12-11 14:00 | 2024-12-11 15:00 | Winter | FALSE | nonsummer
2024-12-11 15:00 | 2024-12-11 16:00 | Winter | FALSE | nonsummer
2024-12-11 16:00 | 2024-12-11 17:00 | Winter | TRUE | nonsummer
2024-12-11 17:00 | 2024-12-11 18:00 | Winter | TRUE | nonsummer
2024-12-11 18:00 | 2024-12-11 19:00 | Winter | TRUE | nonsummer
2024-12-11 19:00 | 2024-12-11 20:00 | Winter | TRUE | nonsummer
2024-12-11 20:00 | 2024-12-11 21:00 | Winter | TRUE | nonsummer
2024-12-11 21:00 | 2024-12-11 22:00 | Winter | FALSE | nonsummer
2024-12-11 22:00 | 2024-12-11 23:00 | Winter | FALSE | nonsummer
2024-12-11 23:00 | 2024-12-12 | Winter | FALSE | nonsummer
2024-12-12 | 2024-12-12 01:00 | Winter | FALSE | nonsummer
2024-12-12 01:00 | 2024-12-12 02:00 | Winter | FALSE | nonsummer
2024-12-12 02:00 | 2024-12-12 03:00 | Winter | FALSE | nonsummer
2024-12-12 03:00 | 2024-12-12 04:00 | Winter | FALSE | nonsummer
2024-12-12 04:00 | 2024-12-12 05:00 | Winter | FALSE | nonsummer
2024-12-12 05:00 | 2024-12-12 06:00 | Winter | FALSE | nonsummer
2024-12-12 06:00 | 2024-12-12 07:00 | Winter | FALSE | nonsummer
2024-12-12 07:00 | 2024-12-12 08:00 | Winter | FALSE | nonsummer
2024-12-12 08:00 | 2024-12-12 09:00 | Winter | FALSE | nonsummer
2024-12-12 09:00 | 2024-12-12 10:00 | Winter | FALSE | nonsummer
2024-12-12 10:00 | 2024-12-12 11:00 | Winter | FALSE | nonsummer
2024-12-12 11:00 | 2024-12-12 12:00 | Winter | FALSE | nonsummer
2024-12-12 12:00 | 2024-12-12 13:00 | Winter | FALSE | nonsummer
2024-12-12 13:00 | 2024-12-12 14:00 | Winter | FALSE | nonsummer
2024-12-12 14:00 | 2024-12-12 15:00 | Winter | FALSE | nonsummer
2024-12-12 15:00 | 2024-12-12 16:00 | Winter | FALSE | nonsummer
2024-12-12 16:00 | 2024-12-12 17:00 | Winter | TRUE | nonsummer
2024-12-12 17:00 | 2024-12-12 18:00 | Winter | TRUE | nonsummer
2024-12-12 18:00 | 2024-12-12 19:00 | Winter | TRUE | nonsummer
2024-12-12 19:00 | 2024-12-12 20:00 | Winter | TRUE | nonsummer
2024-12-12 20:00 | 2024-12-12 21:00 | Winter | TRUE | nonsummer
2024-12-12 21:00 | 2024-12-12 22:00 | Winter | FALSE | nonsummer
2024-12-12 22:00 | 2024-12-12 23:00 | Winter | FALSE | nonsummer
2024-12-12 23:00 | 2024-12-13 | Winter | FALSE | nonsummer
2024-12-13 | 2024-12-13 01:00 | Winter | FALSE | nonsummer
2024-12-13 01:00 | 2024-12-13 02:00 | Winter | FALSE | nonsummer
2024-12-13 02:00 | 2024-12-13 03:00 | Winter | FALSE | nonsummer
2024-12-13 03:00 | 2024-12-13 04:00 | Winter | FALSE | nonsummer
2024-12-13 04:00 | 2024-12-13 05:00 | Winter | FALSE | nonsummer
2024-12-13 05:00 | 2024-12-13 06:00 | Winter | FALSE | nonsummer
2024-12-13 06:00 | 2024-12-13 07:00 | Winter | FALSE | nonsummer
2024-12-13 07:00 | 2024-12-13 08:00 | Winter | FALSE | nonsummer
2024-12-13 08:00 | 2024-12-13 09:00 | Winter | FALSE | nonsummer
2024-12-13 09:00 | 2024-12-13 10:00 | Winter | FALSE | nonsummer
2024-12-13 10:00 | 2024-12-13 11:00 | Winter | FALSE | nonsummer
2024-12-13 11:00 | 2024-12-13 12:00 | Winter | FALSE | nonsummer
2024-12-13 12:00 | 2024-12-13 13:00 | Winter | FALSE | nonsummer
2024-12-13 13:00 | 2024-12-13 14:00 | Winter | FALSE | nonsummer
2024-12-13 14:00 | 2024-12-13 15:00 | Winter | FALSE | nonsummer
2024-12-13 15:00 | 2024-12-13 16:00 | Winter | FALSE | nonsummer
2024-12-13 16:00 | 2024-12-13 17:00 | Winter | TRUE | nonsummer
2024-12-13 17:00 | 2024-12-13 18:00 | Winter | TRUE | nonsummer
2024-12-13 18:00 | 2024-12-13 19:00 | Winter | TRUE | nonsummer
2024-12-13 19:00 | 2024-12-13 20:00 | Winter | TRUE | nonsummer
2024-12-13 20:00 | 2024-12-13 21:00 | Winter | TRUE | nonsummer
2024-12-13 21:00 | 2024-12-13 22:00 | Winter | FALSE | nonsummer
2024-12-13 22:00 | 2024-12-13 23:00 | Winter | FALSE | nonsummer
2024-12-13 23:00 | 2024-12-14 | Winter | FALSE | nonsummer
2024-12-14 | 2024-12-14 01:00 | Winter | FALSE | nonsummer
2024-12-14 01:00 | 2024-12-14 02:00 | Winter | FALSE | nonsummer
2024-12-14 02:00 | 2024-12-14 03:00 | Winter | FALSE | nonsummer
2024-12-14 03:00 | 2024-12-14 04:00 | Winter | FALSE | nonsummer
2024-12-14 04:00 | 2024-12-14 05:00 | Winter | FALSE | nonsummer
2024-12-14 05:00 | 2024-12-14 06:00 | Winter | FALSE | nonsummer
2024-12-14 06:00 | 2024-12-14 07:00 | Winter | FALSE | nonsummer
2024-12-14 07:00 | 2024-12-14 08:00 | Winter | FALSE | nonsummer
2024-12-14 08:00 | 2024-12-14 09:00 | Winter | FALSE | nonsummer
2024-12-14 09:00 | 2024-12-14 10:00 | Winter | FALSE | nonsummer
2024-12-14 10:00 | 2024-12-14 11:00 | Winter | FALSE | nonsummer
2024-12-14 11:00 | 2024-12-14 12:00 | Winter | FALSE | nonsummer
2024-12-14 12:00 | 2024-12-14 13:00 | Winter | FALSE | nonsummer
2024-12-14 13:00 | 2024-12-14 14:00 | Winter | FALSE | nonsummer
2024-12-14 14:00 | 2024-12-14 15:00 | Winter | FALSE | nonsummer
2024-12-14 15:00 | 2024-12-14 16:00 | Winter | FALSE | nonsummer
2024-12-14 16:00 | 2024-12-14 17:00 | Winter | TRUE | nonsummer
2024-12-14 17:00 | 2024-12-14 18:00 | Winter | TRUE | nonsummer
2024-12-14 18:00 | 2024-12-14 19:00 | Winter | TRUE | nonsummer
2024-12-14 19:00 | 2024-12-14 20:00 | Winter | TRUE | nonsummer
2024-12-14 20:00 | 2024-12-14 21:00 | Winter | TRUE | nonsummer
2024-12-14 21:00 | 2024-12-14 22:00 | Winter | FALSE | nonsummer
2024-12-14 22:00 | 2024-12-14 23:00 | Winter | FALSE | nonsummer
2024-12-14 23:00 | 2024-12-15 | Winter | FALSE | nonsummer
2024-12-15 | 2024-12-15 01:00 | Winter | FALSE | nonsummer
2024-12-15 01:00 | 2024-12-15 02:00 | Winter | FALSE | nonsummer
2024-12-15 02:00 | 2024-12-15 03:00 | Winter | FALSE | nonsummer
2024-12-15 03:00 | 2024-12-15 04:00 | Winter | FALSE | nonsummer
2024-12-15 04:00 | 2024-12-15 05:00 | Winter | FALSE | nonsummer
2024-12-15 05:00 | 2024-12-15 06:00 | Winter | FALSE | nonsummer
2024-12-15 06:00 | 2024-12-15 07:00 | Winter | FALSE | nonsummer
2024-12-15 07:00 | 2024-12-15 08:00 | Winter | FALSE | nonsummer
2024-12-15 08:00 | 2024-12-15 09:00 | Winter | FALSE | nonsummer
2024-12-15 09:00 | 2024-12-15 10:00 | Winter | FALSE | nonsummer
2024-12-15 10:00 | 2024-12-15 11:00 | Winter | FALSE | nonsummer
2024-12-15 11:00 | 2024-12-15 12:00 | Winter | FALSE | nonsummer
2024-12-15 12:00 | 2024-12-15 13:00 | Winter | FALSE | nonsummer
2024-12-15 13:00 | 2024-12-15 14:00 | Winter | FALSE | nonsummer
2024-12-15 14:00 | 2024-12-15 15:00 | Winter | FALSE | nonsummer
2024-12-15 15:00 | 2024-12-15 16:00 | Winter | FALSE | nonsummer
2024-12-15 16:00 | 2024-12-15 17:00 | Winter | TRUE | nonsummer
2024-12-15 17:00 | 2024-12-15 18:00 | Winter | TRUE | nonsummer
2024-12-15 18:00 | 2024-12-15 19:00 | Winter | TRUE | nonsummer
2024-12-15 19:00 | 2024-12-15 20:00 | Winter | TRUE | nonsummer
2024-12-15 20:00 | 2024-12-15 21:00 | Winter | TRUE | nonsummer
2024-12-15 21:00 | 2024-12-15 22:00 | Winter | FALSE | nonsummer
2024-12-15 22:00 | 2024-12-15 23:00 | Winter | FALSE | nonsummer
2024-12-15 23:00 | 2024-12-16 | Winter | FALSE | nonsummer
2024-12-16 | 2024-12-16 01:00 | Winter | FALSE | nonsummer
2024-12-16 01:00 | 2024-12-16 02:00 | Winter | FALSE | nonsummer
2024-12-16 02:00 | 2024-12-16 03:00 | Winter | FALSE | nonsummer
2024-12-16 03:00 | 2024-12-16 04:00 | Winter | FALSE | nonsummer
2024-12-16 04:00 | 2024-12-16 05:00 | Winter | FALSE | nonsummer
2024-12-16 05:00 | 2024-12-16 06:00 | Winter | FALSE | nonsummer
2024-12-16 06:00 | 2024-12-16 07:00 | Winter | FALSE | nonsummer
2024-12-16 07:00 | 2024-12-16 08:00 | Winter | FALSE | nonsummer
2024-12-16 08:00 | 2024-12-16 09:00 | Winter | FALSE | nonsummer
2024-12-16 09:00 | 2024-12-16 10:00 | Winter | FALSE | nonsummer
2024-12-16 10:00 | 2024-12-16 11:00 | Winter | FALSE | nonsummer
2024-12-16 11:00 | 2024-12-16 12:00 | Winter | FALSE | nonsummer
2024-12-16 12:00 | 2024-12-16 13:00 | Winter | FALSE | nonsummer
2024-12-16 13:00 | 2024-12-16 14:00 | Winter | FALSE | nonsummer
2024-12-16 14:00 | 2024-12-16 15:00 | Winter | FALSE | nonsummer
2024-12-16 15:00 | 2024-12-16 16:00 | Winter | FALSE | nonsummer
2024-12-16 16:00 | 2024-12-16 17:00 | Winter | TRUE | nonsummer
2024-12-16 17:00 | 2024-12-16 18:00 | Winter | TRUE | nonsummer
2024-12-16 18:00 | 2024-12-16 19:00 | Winter | TRUE | nonsummer
2024-12-16 19:00 | 2024-12-16 20:00 | Winter | TRUE | nonsummer
2024-12-16 20:00 | 2024-12-16 21:00 | Winter | TRUE | nonsummer
2024-12-16 21:00 | 2024-12-16 22:00 | Winter | FALSE | nonsummer
2024-12-16 22:00 | 2024-12-16 23:00 | Winter | FALSE | nonsummer
2024-12-16 23:00 | 2024-12-17 | Winter | FALSE | nonsummer
2024-12-17 | 2024-12-17 01:00 | Winter | FALSE | nonsummer
2024-12-17 01:00 | 2024-12-17 02:00 | Winter | FALSE | nonsummer
2024-12-17 02:00 | 2024-12-17 03:00 | Winter | FALSE | nonsummer
2024-12-17 03:00 | 2024-12-17 04:00 | Winter | FALSE | nonsummer
2024-12-17 04:00 | 2024-12-17 05:00 | Winter | FALSE | nonsummer
2024-12-17 05:00 | 2024-12-17 06:00 | Winter | FALSE | nonsummer
2024-12-17 06:00 | 2024-12-17 07:00 | Winter | FALSE | nonsummer
2024-12-17 07:00 | 2024-12-17 08:00 | Winter | FALSE | nonsummer
2024-12-17 08:00 | 2024-12-17 09:00 | Winter | FALSE | nonsummer
2024-12-17 09:00 | 2024-12-17 10:00 | Winter | FALSE | nonsummer
2024-12-17 10:00 | 2024-12-17 11:00 | Winter | FALSE | nonsummer
2024-12-17 11:00 | 2024-12-17 12:00 | Winter | FALSE | nonsummer
2024-12-17 12:00 | 2024-12-17 13:00 | Winter | FALSE | nonsummer
2024-12-17 13:00 | 2024-12-17 14:00 | Winter | FALSE | nonsummer
2024-12-17 14:00 | 2024-12-17 15:00 | Winter | FALSE | nonsummer
2024-12-17 15:00 | 2024-12-17 16:00 | Winter | FALSE | nonsummer
2024-12-17 16:00 | 2024-12-17 17:00 | Winter | TRUE | nonsummer
2024-12-17 17:00 | 2024-12-17 18:00 | Winter | TRUE | nonsummer
2024-12-17 18:00 | 2024-12-17 19:00 | Winter | TRUE | nonsummer
2024-12-17 19:00 | 2024-12-17 20:00 | Winter | TRUE | nonsummer
2024-12-17 20:00 | 2024-12-17 21:00 | Winter | TRUE | nonsummer
2024-12-17 21:00 | 2024-12-17 22:00 | Winter | FALSE | nonsummer
2024-12-17 22:00 | 2024-12-17 23:00 | Winter | FALSE | nonsummer
2024-12-17 23:00 | 2024-12-18 | Winter | FALSE | nonsummer
2024-12-18 | 2024-12-18 01:00 | Winter | FALSE | nonsummer
2024-12-18 01:00 | 2024-12-18 02:00 | Winter | FALSE | nonsummer
2024-12-18 02:00 | 2024-12-18 03:00 | Winter | FALSE | nonsummer
2024-12-18 03:00 | 2024-12-18 04:00 | Winter | FALSE | nonsummer
2024-12-18 04:00 | 2024-12-18 05:00 | Winter | FALSE | nonsummer
2024-12-18 05:00 | 2024-12-18 06:00 | Winter | FALSE | nonsummer
2024-12-18 06:00 | 2024-12-18 07:00 | Winter | FALSE | nonsummer
2024-12-18 07:00 | 2024-12-18 08:00 | Winter | FALSE | nonsummer
2024-12-18 08:00 | 2024-12-18 09:00 | Winter | FALSE | nonsummer
2024-12-18 09:00 | 2024-12-18 10:00 | Winter | FALSE | nonsummer
2024-12-18 10:00 | 2024-12-18 11:00 | Winter | FALSE | nonsummer
2024-12-18 11:00 | 2024-12-18 12:00 | Winter | FALSE | nonsummer
2024-12-18 12:00 | 2024-12-18 13:00 | Winter | FALSE | nonsummer
2024-12-18 13:00 | 2024-12-18 14:00 | Winter | FALSE | nonsummer
2024-12-18 14:00 | 2024-12-18 15:00 | Winter | FALSE | nonsummer
2024-12-18 15:00 | 2024-12-18 16:00 | Winter | FALSE | nonsummer
2024-12-18 16:00 | 2024-12-18 17:00 | Winter | TRUE | nonsummer
2024-12-18 17:00 | 2024-12-18 18:00 | Winter | TRUE | nonsummer
2024-12-18 18:00 | 2024-12-18 19:00 | Winter | TRUE | nonsummer
2024-12-18 19:00 | 2024-12-18 20:00 | Winter | TRUE | nonsummer
2024-12-18 20:00 | 2024-12-18 21:00 | Winter | TRUE | nonsummer
2024-12-18 21:00 | 2024-12-18 22:00 | Winter | FALSE | nonsummer
2024-12-18 22:00 | 2024-12-18 23:00 | Winter | FALSE | nonsummer
2024-12-18 23:00 | 2024-12-19 | Winter | FALSE | nonsummer
2024-12-19 | 2024-12-19 01:00 | Winter | FALSE | nonsummer
2024-12-19 01:00 | 2024-12-19 02:00 | Winter | FALSE | nonsummer
2024-12-19 02:00 | 2024-12-19 03:00 | Winter | FALSE | nonsummer
2024-12-19 03:00 | 2024-12-19 04:00 | Winter | FALSE | nonsummer
2024-12-19 04:00 | 2024-12-19 05:00 | Winter | FALSE | nonsummer
2024-12-19 05:00 | 2024-12-19 06:00 | Winter | FALSE | nonsummer
2024-12-19 06:00 | 2024-12-19 07:00 | Winter | FALSE | nonsummer
2024-12-19 07:00 | 2024-12-19 08:00 | Winter | FALSE | nonsummer
2024-12-19 08:00 | 2024-12-19 09:00 | Winter | FALSE | nonsummer
2024-12-19 09:00 | 2024-12-19 10:00 | Winter | FALSE | nonsummer
2024-12-19 10:00 | 2024-12-19 11:00 | Winter | FALSE | nonsummer
2024-12-19 11:00 | 2024-12-19 12:00 | Winter | FALSE | nonsummer
2024-12-19 12:00 | 2024-12-19 13:00 | Winter | FALSE | nonsummer
2024-12-19 13:00 | 2024-12-19 14:00 | Winter | FALSE | nonsummer
2024-12-19 14:00 | 2024-12-19 15:00 | Winter | FALSE | nonsummer
2024-12-19 15:00 | 2024-12-19 16:00 | Winter | FALSE | nonsummer
2024-12-19 16:00 | 2024-12-19 17:00 | Winter | TRUE | nonsummer
2024-12-19 17:00 | 2024-12-19 18:00 | Winter | TRUE | nonsummer
2024-12-19 18:00 | 2024-12-19 19:00 | Winter | TRUE | nonsummer
2024-12-19 19:00 | 2024-12-19 20:00 | Winter | TRUE | nonsummer
2024-12-19 20:00 | 2024-12-19 21:00 | Winter | TRUE | nonsummer
2024-12-19 21:00 | 2024-12-19 22:00 | Winter | FALSE | nonsummer
2024-12-19 22:00 | 2024-12-19 23:00 | Winter | FALSE | nonsummer
2024-12-19 23:00 | 2024-12-20 | Winter | FALSE | nonsummer
2024-12-20 | 2024-12-20 01:00 | Winter | FALSE | nonsummer
2024-12-20 01:00 | 2024-12-20 02:00 | Winter | FALSE | nonsummer
2024-12-20 02:00 | 2024-12-20 03:00 | Winter | FALSE | nonsummer
2024-12-20 03:00 | 2024-12-20 04:00 | Winter | FALSE | nonsummer
2024-12-20 04:00 | 2024-12-20 05:00 | Winter | FALSE | nonsummer
2024-12-20 05:00 | 2024-12-20 06:00 | Winter | FALSE | nonsummer
2024-12-20 06:00 | 2024-12-20 07:00 | Winter | FALSE | nonsummer
2024-12-20 07:00 | 2024-12-20 08:00 | Winter | FALSE | nonsummer
2024-12-20 08:00 | 2024-12-20 09:00 | Winter | FALSE | nonsummer
2024-12-20 09:00 | 2024-12-20 10:00 | Winter | FALSE | nonsummer
2024-12-20 10:00 | 2024-12-20 11:00 | Winter | FALSE | nonsummer
2024-12-20 11:00 | 2024-12-20 12:00 | Winter | FALSE | nonsummer
2024-12-20 12:00 | 2024-12-20 13:00 | Winter | FALSE | nonsummer
2024-12-20 13:00 | 2024-12-20 14:00 | Winter | FALSE | nonsummer
2024-12-20 14:00 | 2024-12-20 15:00 | Winter | FALSE | nonsummer
2024-12-20 15:00 | 2024-12-20 16:00 | Winter | FALSE | nonsummer
2024-12-20 16:00 | 2024-12-20 17:00 | Winter | TRUE | nonsummer
2024-12-20 17:00 | 2024-12-20 18:00 | Winter | TRUE | nonsummer
2024-12-20 18:00 | 2024-12-20 19:00 | Winter | TRUE | nonsummer
2024-12-20 19:00 | 2024-12-20 20:00 | Winter | TRUE | nonsummer
2024-12-20 20:00 | 2024-12-20 21:00 | Winter | TRUE | nonsummer
2024-12-20 21:00 | 2024-12-20 22:00 | Winter | FALSE | nonsummer
2024-12-20 22:00 | 2024-12-20 23:00 | Winter | FALSE | nonsummer
2024-12-20 23:00 | 2024-12-21 | Winter | FALSE | nonsummer
2024-12-21 | 2024-12-21 01:00 | Winter | FALSE | nonsummer
2024-12-21 01:00 | 2024-12-21 02:00 | Winter | FALSE | nonsummer
2024-12-21 02:00 | 2024-12-21 03:00 | Winter | FALSE | nonsummer
2024-12-21 03:00 | 2024-12-21 04:00 | Winter | FALSE | nonsummer
2024-12-21 04:00 | 2024-12-21 05:00 | Winter | FALSE | nonsummer
2024-12-21 05:00 | 2024-12-21 06:00 | Winter | FALSE | nonsummer
2024-12-21 06:00 | 2024-12-21 07:00 | Winter | FALSE | nonsummer
2024-12-21 07:00 | 2024-12-21 08:00 | Winter | FALSE | nonsummer
2024-12-21 08:00 | 2024-12-21 09:00 | Winter | FALSE | nonsummer
2024-12-21 09:00 | 2024-12-21 10:00 | Winter | FALSE | nonsummer
2024-12-21 10:00 | 2024-12-21 11:00 | Winter | FALSE | nonsummer
2024-12-21 11:00 | 2024-12-21 12:00 | Winter | FALSE | nonsummer
2024-12-21 12:00 | 2024-12-21 13:00 | Winter | FALSE | nonsummer
2024-12-21 13:00 | 2024-12-21 14:00 | Winter | FALSE | nonsummer
2024-12-21 14:00 | 2024-12-21 15:00 | Winter | FALSE | nonsummer
2024-12-21 15:00 | 2024-12-21 16:00 | Winter | FALSE | nonsummer
2024-12-21 16:00 | 2024-12-21 17:00 | Winter | TRUE | nonsummer
2024-12-21 17:00 | 2024-12-21 18:00 | Winter | TRUE | nonsummer
2024-12-21 18:00 | 2024-12-21 19:00 | Winter | TRUE | nonsummer
2024-12-21 19:00 | 2024-12-21 20:00 | Winter | TRUE | nonsummer
2024-12-21 20:00 | 2024-12-21 21:00 | Winter | TRUE | nonsummer
2024-12-21 21:00 | 2024-12-21 22:00 | Winter | FALSE | nonsummer
2024-12-21 22:00 | 2024-12-21 23:00 | Winter | FALSE | nonsummer
2024-12-21 23:00 | 2024-12-22 | Winter | FALSE | nonsummer
2024-12-22 | 2024-12-22 01:00 | Winter | FALSE | nonsummer
2024-12-22 01:00 | 2024-12-22 02:00 | Winter | FALSE | nonsummer
2024-12-22 02:00 | 2024-12-22 03:00 | Winter | FALSE | nonsummer
2024-12-22 03:00 | 2024-12-22 04:00 | Winter | FALSE | nonsummer
2024-12-22 04:00 | 2024-12-22 05:00 | Winter | FALSE | nonsummer
2024-12-22 05:00 | 2024-12-22 06:00 | Winter | FALSE | nonsummer
2024-12-22 06:00 | 2024-12-22 07:00 | Winter | FALSE | nonsummer
2024-12-22 07:00 | 2024-12-22 08:00 | Winter | FALSE | nonsummer
2024-12-22 08:00 | 2024-12-22 09:00 | Winter | FALSE | nonsummer
2024-12-22 09:00 | 2024-12-22 10:00 | Winter | FALSE | nonsummer
2024-12-22 10:00 | 2024-12-22 11:00 | Winter | FALSE | nonsummer
2024-12-22 11:00 | 2024-12-22 12:00 | Winter | FALSE | nonsummer
2024-12-22 12:00 | 2024-12-22 13:00 | Winter | FALSE | nonsummer
2024-12-22 13:00 | 2024-12-22 14:00 | Winter | FALSE | nonsummer
2024-12-22 14:00 | 2024-12-22 15:00 | Winter | FALSE | nonsummer
2024-12-22 15:00 | 2024-12-22 16:00 | Winter | FALSE | nonsummer
2024-12-22 16:00 | 2024-12-22 17:00 | Winter | TRUE | nonsummer
2024-12-22 17:00 | 2024-12-22 18:00 | Winter | TRUE | nonsummer
2024-12-22 18:00 | 2024-12-22 19:00 | Winter | TRUE | nonsummer
2024-12-22 19:00 | 2024-12-22 20:00 | Winter | TRUE | nonsummer
2024-12-22 20:00 | 2024-12-22 21:00 | Winter | TRUE | nonsummer
2024-12-22 21:00 | 2024-12-22 22:00 | Winter | FALSE | nonsummer
2024-12-22 22:00 | 2024-12-22 23:00 | Winter | FALSE | nonsummer
2024-12-22 23:00 | 2024-12-23 | Winter | FALSE | nonsummer
2024-12-23 | 2024-12-23 01:00 | Winter | FALSE | nonsummer
2024-12-23 01:00 | 2024-12-23 02:00 | Winter | FALSE | nonsummer
2024-12-23 02:00 | 2024-12-23 03:00 | Winter | FALSE | nonsummer
2024-12-23 03:00 | 2024-12-23 04:00 | Winter | FALSE | nonsummer
2024-12-23 04:00 | 2024-12-23 05:00 | Winter | FALSE | nonsummer
2024-12-23 05:00 | 2024-12-23 06:00 | Winter | FALSE | nonsummer
2024-12-23 06:00 | 2024-12-23 07:00 | Winter | FALSE | nonsummer
2024-12-23 07:00 | 2024-12-23 08:00 | Winter | FALSE | nonsummer
2024-12-23 08:00 | 2024-12-23 09:00 | Winter | FALSE | nonsummer
2024-12-23 09:00 | 2024-12-23 10:00 | Winter | FALSE | nonsummer
2024-12-23 10:00 | 2024-12-23 11:00 | Winter | FALSE | nonsummer
2024-12-23 11:00 | 2024-12-23 12:00 | Winter | FALSE | nonsummer
2024-12-23 12:00 | 2024-12-23 13:00 | Winter | FALSE | nonsummer
2024-12-23 13:00 | 2024-12-23 14:00 | Winter | FALSE | nonsummer
2024-12-23 14:00 | 2024-12-23 15:00 | Winter | FALSE | nonsummer
2024-12-23 15:00 | 2024-12-23 16:00 | Winter | FALSE | nonsummer
2024-12-23 16:00 | 2024-12-23 17:00 | Winter | TRUE | nonsummer
2024-12-23 17:00 | 2024-12-23 18:00 | Winter | TRUE | nonsummer
2024-12-23 18:00 | 2024-12-23 19:00 | Winter | TRUE | nonsummer
2024-12-23 19:00 | 2024-12-23 20:00 | Winter | TRUE | nonsummer
2024-12-23 20:00 | 2024-12-23 21:00 | Winter | TRUE | nonsummer
2024-12-23 21:00 | 2024-12-23 22:00 | Winter | FALSE | nonsummer
2024-12-23 22:00 | 2024-12-23 23:00 | Winter | FALSE | nonsummer
2024-12-23 23:00 | 2024-12-24 | Winter | FALSE | nonsummer
2024-12-24 | 2024-12-24 01:00 | Winter | FALSE | nonsummer
2024-12-24 01:00 | 2024-12-24 02:00 | Winter | FALSE | nonsummer
2024-12-24 02:00 | 2024-12-24 03:00 | Winter | FALSE | nonsummer
2024-12-24 03:00 | 2024-12-24 04:00 | Winter | FALSE | nonsummer
2024-12-24 04:00 | 2024-12-24 05:00 | Winter | FALSE | nonsummer
2024-12-24 05:00 | 2024-12-24 06:00 | Winter | FALSE | nonsummer
2024-12-24 06:00 | 2024-12-24 07:00 | Winter | FALSE | nonsummer
2024-12-24 07:00 | 2024-12-24 08:00 | Winter | FALSE | nonsummer
2024-12-24 08:00 | 2024-12-24 09:00 | Winter | FALSE | nonsummer
2024-12-24 09:00 | 2024-12-24 10:00 | Winter | FALSE | nonsummer
2024-12-24 10:00 | 2024-12-24 11:00 | Winter | FALSE | nonsummer
2024-12-24 11:00 | 2024-12-24 12:00 | Winter | FALSE | nonsummer
2024-12-24 12:00 | 2024-12-24 13:00 | Winter | FALSE | nonsummer
2024-12-24 13:00 | 2024-12-24 14:00 | Winter | FALSE | nonsummer
2024-12-24 14:00 | 2024-12-24 15:00 | Winter | FALSE | nonsummer
2024-12-24 15:00 | 2024-12-24 16:00 | Winter | FALSE | nonsummer
2024-12-24 16:00 | 2024-12-24 17:00 | Winter | TRUE | nonsummer
2024-12-24 17:00 | 2024-12-24 18:00 | Winter | TRUE | nonsummer
2024-12-24 18:00 | 2024-12-24 19:00 | Winter | TRUE | nonsummer
2024-12-24 19:00 | 2024-12-24 20:00 | Winter | TRUE | nonsummer
2024-12-24 20:00 | 2024-12-24 21:00 | Winter | TRUE | nonsummer
2024-12-24 21:00 | 2024-12-24 22:00 | Winter | FALSE | nonsummer
2024-12-24 22:00 | 2024-12-24 23:00 | Winter | FALSE | nonsummer
2024-12-24 23:00 | 2024-12-25 | Winter | FALSE | nonsummer
2024-12-25 | 2024-12-25 01:00 | Winter | FALSE | nonsummer
2024-12-25 01:00 | 2024-12-25 02:00 | Winter | FALSE | nonsummer
2024-12-25 02:00 | 2024-12-25 03:00 | Winter | FALSE | nonsummer
2024-12-25 03:00 | 2024-12-25 04:00 | Winter | FALSE | nonsummer
2024-12-25 04:00 | 2024-12-25 05:00 | Winter | FALSE | nonsummer
2024-12-25 05:00 | 2024-12-25 06:00 | Winter | FALSE | nonsummer
2024-12-25 06:00 | 2024-12-25 07:00 | Winter | FALSE | nonsummer
2024-12-25 07:00 | 2024-12-25 08:00 | Winter | FALSE | nonsummer
2024-12-25 08:00 | 2024-12-25 09:00 | Winter | FALSE | nonsummer
2024-12-25 09:00 | 2024-12-25 10:00 | Winter | FALSE | nonsummer
2024-12-25 10:00 | 2024-12-25 11:00 | Winter | FALSE | nonsummer
2024-12-25 11:00 | 2024-12-25 12:00 | Winter | FALSE | nonsummer
2024-12-25 12:00 | 2024-12-25 13:00 | Winter | FALSE | nonsummer
2024-12-25 13:00 | 2024-12-25 14:00 | Winter | FALSE | nonsummer
2024-12-25 14:00 | 2024-12-25 15:00 | Winter | FALSE | nonsummer
2024-12-25 15:00 | 2024-12-25 16:00 | Winter | FALSE | nonsummer
2024-12-25 16:00 | 2024-12-25 17:00 | Winter | TRUE | nonsummer
2024-12-25 17:00 | 2024-12-25 18:00 | Winter | TRUE | nonsummer
2024-12-25 18:00 | 2024-12-25 19:00 | Winter | TRUE | nonsummer
2024-12-25 19:00 | 2024-12-25 20:00 | Winter | TRUE | nonsummer
2024-12-25 20:00 | 2024-12-25 21:00 | Winter | TRUE | nonsummer
2024-12-25 21:00 | 2024-12-25 22:00 | Winter | FALSE | nonsummer
2024-12-25 22:00 | 2024-12-25 23:00 | Winter | FALSE | nonsummer
2024-12-25 23:00 | 2024-12-26 | Winter | FALSE | nonsummer
2024-12-26 | 2024-12-26 01:00 | Winter | FALSE | nonsummer
2024-12-26 01:00 | 2024-12-26 02:00 | Winter | FALSE | nonsummer
2024-12-26 02:00 | 2024-12-26 03:00 | Winter | FALSE | nonsummer
2024-12-26 03:00 | 2024-12-26 04:00 | Winter | FALSE | nonsummer
2024-12-26 04:00 | 2024-12-26 05:00 | Winter | FALSE | nonsummer
2024-12-26 05:00 | 2024-12-26 06:00 | Winter | FALSE | nonsummer
2024-12-26 06:00 | 2024-12-26 07:00 | Winter | FALSE | nonsummer
2024-12-26 07:00 | 2024-12-26 08:00 | Winter | FALSE | nonsummer
2024-12-26 08:00 | 2024-12-26 09:00 | Winter | FALSE | nonsummer
2024-12-26 09:00 | 2024-12-26 10:00 | Winter | FALSE | nonsummer
2024-12-26 10:00 | 2024-12-26 11:00 | Winter | FALSE | nonsummer
2024-12-26 11:00 | 2024-12-26 12:00 | Winter | FALSE | nonsummer
2024-12-26 12:00 | 2024-12-26 13:00 | Winter | FALSE | nonsummer
2024-12-26 13:00 | 2024-12-26 14:00 | Winter | FALSE | nonsummer
2024-12-26 14:00 | 2024-12-26 15:00 | Winter | FALSE | nonsummer
2024-12-26 15:00 | 2024-12-26 16:00 | Winter | FALSE | nonsummer
2024-12-26 16:00 | 2024-12-26 17:00 | Winter | TRUE | nonsummer
2024-12-26 17:00 | 2024-12-26 18:00 | Winter | TRUE | nonsummer
2024-12-26 18:00 | 2024-12-26 19:00 | Winter | TRUE | nonsummer
2024-12-26 19:00 | 2024-12-26 20:00 | Winter | TRUE | nonsummer
2024-12-26 20:00 | 2024-12-26 21:00 | Winter | TRUE | nonsummer
2024-12-26 21:00 | 2024-12-26 22:00 | Winter | FALSE | nonsummer
2024-12-26 22:00 | 2024-12-26 23:00 | Winter | FALSE | nonsummer
2024-12-26 23:00 | 2024-12-27 | Winter | FALSE | nonsummer
2024-12-27 | 2024-12-27 01:00 | Winter | FALSE | nonsummer
2024-12-27 01:00 | 2024-12-27 02:00 | Winter | FALSE | nonsummer
2024-12-27 02:00 | 2024-12-27 03:00 | Winter | FALSE | nonsummer
2024-12-27 03:00 | 2024-12-27 04:00 | Winter | FALSE | nonsummer
2024-12-27 04:00 | 2024-12-27 05:00 | Winter | FALSE | nonsummer
2024-12-27 05:00 | 2024-12-27 06:00 | Winter | FALSE | nonsummer
2024-12-27 06:00 | 2024-12-27 07:00 | Winter | FALSE | nonsummer
2024-12-27 07:00 | 2024-12-27 08:00 | Winter | FALSE | nonsummer
2024-12-27 08:00 | 2024-12-27 09:00 | Winter | FALSE | nonsummer
2024-12-27 09:00 | 2024-12-27 10:00 | Winter | FALSE | nonsummer
2024-12-27 10:00 | 2024-12-27 11:00 | Winter | FALSE | nonsummer
2024-12-27 11:00 | 2024-12-27 12:00 | Winter | FALSE | nonsummer
2024-12-27 12:00 | 2024-12-27 13:00 | Winter | FALSE | nonsummer
2024-12-27 13:00 | 2024-12-27 14:00 | Winter | FALSE | nonsummer
2024-12-27 14:00 | 2024-12-27 15:00 | Winter | FALSE | nonsummer
2024-12-27 15:00 | 2024-12-27 16:00 | Winter | FALSE | nonsummer
2024-12-27 16:00 | 2024-12-27 17:00 | Winter | TRUE | nonsummer
2024-12-27 17:00 | 2024-12-27 18:00 | Winter | TRUE | nonsummer
2024-12-27 18:00 | 2024-12-27 19:00 | Winter | TRUE | nonsummer
2024-12-27 19:00 | 2024-12-27 20:00 | Winter | TRUE | nonsummer
2024-12-27 20:00 | 2024-12-27 21:00 | Winter | TRUE | nonsummer
2024-12-27 21:00 | 2024-12-27 22:00 | Winter | FALSE | nonsummer
2024-12-27 22:00 | 2024-12-27 23:00 | Winter | FALSE | nonsummer
2024-12-27 23:00 | 2024-12-28 | Winter | FALSE | nonsummer
2024-12-28 | 2024-12-28 01:00 | Winter | FALSE | nonsummer
2024-12-28 01:00 | 2024-12-28 02:00 | Winter | FALSE | nonsummer
2024-12-28 02:00 | 2024-12-28 03:00 | Winter | FALSE | nonsummer
2024-12-28 03:00 | 2024-12-28 04:00 | Winter | FALSE | nonsummer
2024-12-28 04:00 | 2024-12-28 05:00 | Winter | FALSE | nonsummer
2024-12-28 05:00 | 2024-12-28 06:00 | Winter | FALSE | nonsummer
2024-12-28 06:00 | 2024-12-28 07:00 | Winter | FALSE | nonsummer
2024-12-28 07:00 | 2024-12-28 08:00 | Winter | FALSE | nonsummer
2024-12-28 08:00 | 2024-12-28 09:00 | Winter | FALSE | nonsummer
2024-12-28 09:00 | 2024-12-28 10:00 | Winter | FALSE | nonsummer
2024-12-28 10:00 | 2024-12-28 11:00 | Winter | FALSE | nonsummer
2024-12-28 11:00 | 2024-12-28 12:00 | Winter | FALSE | nonsummer
2024-12-28 12:00 | 2024-12-28 13:00 | Winter | FALSE | nonsummer
2024-12-28 13:00 | 2024-12-28 14:00 | Winter | FALSE | nonsummer
2024-12-28 14:00 | 2024-12-28 15:00 | Winter | FALSE | nonsummer
2024-12-28 15:00 | 2024-12-28 16:00 | Winter | FALSE | nonsummer
2024-12-28 16:00 | 2024-12-28 17:00 | Winter | TRUE | nonsummer
2024-12-28 17:00 | 2024-12-28 18:00 | Winter | TRUE | nonsummer
2024-12-28 18:00 | 2024-12-28 19:00 | Winter | TRUE | nonsummer
2024-12-28 19:00 | 2024-12-28 20:00 | Winter | TRUE | nonsummer
2024-12-28 20:00 | 2024-12-28 21:00 | Winter | TRUE | nonsummer
2024-12-28 21:00 | 2024-12-28 22:00 | Winter | FALSE | nonsummer
2024-12-28 22:00 | 2024-12-28 23:00 | Winter | FALSE | nonsummer
2024-12-28 23:00 | 2024-12-29 | Winter | FALSE | nonsummer
2024-12-29 | 2024-12-29 01:00 | Winter | FALSE | nonsummer
2024-12-29 01:00 | 2024-12-29 02:00 | Winter | FALSE | nonsummer
2024-12-29 02:00 | 2024-12-29 03:00 | Winter | FALSE | nonsummer
2024-12-29 03:00 | 2024-12-29 04:00 | Winter | FALSE | nonsummer
2024-12-29 04:00 | 2024-12-29 05:00 | Winter | FALSE | nonsummer
2024-12-29 05:00 | 2024-12-29 06:00 | Winter | FALSE | nonsummer
2024-12-29 06:00 | 2024-12-29 07:00 | Winter | FALSE | nonsummer
2024-12-29 07:00 | 2024-12-29 08:00 | Winter | FALSE | nonsummer
2024-12-29 08:00 | 2024-12-29 09:00 | Winter | FALSE | nonsummer
2024-12-29 09:00 | 2024-12-29 10:00 | Winter | FALSE | nonsummer
2024-12-29 10:00 | 2024-12-29 11:00 | Winter | FALSE | nonsummer
2024-12-29 11:00 | 2024-12-29 12:00 | Winter | FALSE | nonsummer
2024-12-29 12:00 | 2024-12-29 13:00 | Winter | FALSE | nonsummer
2024-12-29 13:00 | 2024-12-29 14:00 | Winter | FALSE | nonsummer
2024-12-29 14:00 | 2024-12-29 15:00 | Winter | FALSE | nonsummer
2024-12-29 15:00 | 2024-12-29 16:00 | Winter | FALSE | nonsummer
2024-12-29 16:00 | 2024-12-29 17:00 | Winter | TRUE | nonsummer
2024-12-29 17:00 | 2024-12-29 18:00 | Winter | TRUE | nonsummer
2024-12-29 18:00 | 2024-12-29 19:00 | Winter | TRUE | nonsummer
2024-12-29 19:00 | 2024-12-29 20:00 | Winter | TRUE | nonsummer
2024-12-29 20:00 | 2024-12-29 21:00 | Winter | TRUE | nonsummer
2024-12-29 21:00 | 2024-12-29 22:00 | Winter | FALSE | nonsummer
2024-12-29 22:00 | 2024-12-29 23:00 | Winter | FALSE | nonsummer
2024-12-29 23:00 | 2024-12-30 | Winter | FALSE | nonsummer
2024-12-30 | 2024-12-30 01:00 | Winter | FALSE | nonsummer
2024-12-30 01:00 | 2024-12-30 02:00 | Winter | FALSE | nonsummer
2024-12-30 02:00 | 2024-12-30 03:00 | Winter | FALSE | nonsummer
2024-12-30 03:00 | 2024-12-30 04:00 | Winter | FALSE | nonsummer
2024-12-30 04:00 | 2024-12-30 05:00 | Winter | FALSE | nonsummer
2024-12-30 05:00 | 2024-12-30 06:00 | Winter | FALSE | nonsummer
2024-12-30 06:00 | 2024-12-30 07:00 | Winter | FALSE | nonsummer
2024-12-30 07:00 | 2024-12-30 08:00 | Winter | FALSE | nonsummer
2024-12-30 08:00 | 2024-12-30 09:00 | Winter | FALSE | nonsummer
2024-12-30 09:00 | 2024-12-30 10:00 | Winter | FALSE | nonsummer
2024-12-30 10:00 | 2024-12-30 11:00 | Winter | FALSE | nonsummer
2024-12-30 11:00 | 2024-12-30 12:00 | Winter | FALSE | nonsummer
2024-12-30 12:00 | 2024-12-30 13:00 | Winter | FALSE | nonsummer
2024-12-30 13:00 | 2024-12-30 14:00 | Winter | FALSE | nonsummer
2024-12-30 14:00 | 2024-12-30 15:00 | Winter | FALSE | nonsummer
2024-12-30 15:00 | 2024-12-30 16:00 | Winter | FALSE | nonsummer
2024-12-30 16:00 | 2024-12-30 17:00 | Winter | TRUE | nonsummer
2024-12-30 17:00 | 2024-12-30 18:00 | Winter | TRUE | nonsummer
2024-12-30 18:00 | 2024-12-30 19:00 | Winter | TRUE | nonsummer
2024-12-30 19:00 | 2024-12-30 20:00 | Winter | TRUE | nonsummer
2024-12-30 20:00 | 2024-12-30 21:00 | Winter | TRUE | nonsummer
2024-12-30 21:00 | 2024-12-30 22:00 | Winter | FALSE | nonsummer
2024-12-30 22:00 | 2024-12-30 23:00 | Winter | FALSE | nonsummer
2024-12-30 23:00 | 2024-12-31 | Winter | FALSE | nonsummer
2024-12-31 | 2024-12-31 01:00 | Winter | FALSE | nonsummer
2024-12-31 01:00 | 2024-12-31 02:00 | Winter | FALSE | nonsummer
2024-12-31 02:00 | 2024-12-31 03:00 | Winter | FALSE | nonsummer
2024-12-31 03:00 | 2024-12-31 04:00 | Winter | FALSE | nonsummer
2024-12-31 04:00 | 2024-12-31 05:00 | Winter | FALSE | nonsummer
2024-12-31 05:00 | 2024-12-31 06:00 | Winter | FALSE | nonsummer
2024-12-31 06:00 | 2024-12-31 07:00 | Winter | FALSE | nonsummer
2024-12-31 07:00 | 2024-12-31 08:00 | Winter | FALSE | nonsummer
2024-12-31 08:00 | 2024-12-31 09:00 | Winter | FALSE | nonsummer
2024-12-31 09:00 | 2024-12-31 10:00 | Winter | FALSE | nonsummer
2024-12-31 10:00 | 2024-12-31 11:00 | Winter | FALSE | nonsummer
2024-12-31 11:00 | 2024-12-31 12:00 | Winter | FALSE | nonsummer
2024-12-31 12:00 | 2024-12-31 13:00 | Winter | FALSE | nonsummer
2024-12-31 13:00 | 2024-12-31 14:00 | Winter | FALSE | nonsummer
2024-12-31 14:00 | 2024-12-31 15:00 | Winter | FALSE | nonsummer
2024-12-31 15:00 | 2024-12-31 16:00 | Winter | FALSE | nonsummer
2024-12-31 16:00 | 2024-12-31 17:00 | Winter | TRUE | nonsummer
2024-12-31 17:00 | 2024-12-31 18:00 | Winter | TRUE | nonsummer
2024-12-31 18:00 | 2024-12-31 19:00 | Winter | TRUE | nonsummer
2024-12-31 19:00 | 2024-12-31 20:00 | Winter | TRUE | nonsummer
2024-12-31 20:00 | 2024-12-31 21:00 | Winter | TRUE | nonsummer
2024-12-31 21:00 | 2024-12-31 22:00 | Winter | FALSE | nonsummer
2024-12-31 22:00 | 2024-12-31 23:00 | Winter | FALSE | nonsummer
2024-12-31 23:00 | 2025-01-01 | Winter | FALSE | nonsummer
Formulas:
END DATETIME = [START DATETIME]+1/24

## Resource Database
RESOURCE ID | RESOURCE TYPE | TECHNOLOGY | FUEL | DISPATCHABLE | PMAX OR NDC (MW)
7STDRD_1_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
ACACIA_6_SOLAR | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 20
ADERA_1_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
ADLIN_1_UNITS | Geothermal | STEAM | GEOTHERMAL | TRUE | 22
ADMEST_6_SOLAR | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 19
ADOBEE_1_SOLAR | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
AGRICO_6_PL3N5 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 22.69
AGRICO_7_UNIT | CCGT | OTHER | NATURAL GAS | TRUE | 59.97
AGUCAL_5_SOLAR1 | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 290
AKINGS_6_AMESR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 123
ALAMIT_2_AESBT2 | Battery Storage | OTHER | LESR | TRUE | 82
ALAMIT_2_PL1X3 | CCGT | COMBINED CYCLE | NATURAL GAS | TRUE | 674.7
ALAMIT_7_ES1 | Battery Storage | OTHER | LESR | TRUE | 100.45
ALAMO_6_UNIT | Hydro | HYDRO | WATER | TRUE | 17
ALLGNY_6_HYDRO1 | Hydro | HYDRO | WATER | FALSE | 0.52
ALMASL_2_AL6BT6 | Paired_BattStorage | OTHER | LESR | TRUE | 50
ALMASL_2_GS1SR1 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 125
ALMASL_2_GS4SR4 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 100
ALMASL_2_GS6SR6 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 100
ALMASL_2_GS7SR7 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 132
ALMEGT_1_UNIT 1 | Peaker | FTUR | NATURAL GAS | TRUE | 25
ALMEGT_1_UNIT 2 | Peaker | FTUR | NATURAL GAS | TRUE | 25
ALPAUG_1_TUDSR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 3
ALPSLR_1_NTHSLR | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 20
ALPSLR_1_SPSSLR | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 50
ALT6DN_2_WIND7 | Wind | WIND | WIND | FALSE | 164.31
ALT6DS_2_WIND9 | Wind | WIND | WIND | FALSE | 132
ALTA3A_2_CPCE4 | Wind | WIND | WIND | FALSE | 102
ALTA3A_2_CPCE5 | Wind | WIND | WIND | FALSE | 168
ALTA3A_2_CPCE8 | Wind | WIND | WIND | FALSE | 150
ALTA4A_2_CPCW1 | Wind | WIND | WIND | FALSE | 150
ALTA4B_2_CPCW2 | Wind | WIND | WIND | FALSE | 150
ALTA4B_2_CPCW3 | Wind | WIND | WIND | FALSE | 150
ALTA4B_2_CPCW6 | Wind | WIND | WIND | FALSE | 150
ALTA6B_2_WIND11 | Wind | WIND | WIND | FALSE | 88.15
ALTA6E_2_WIND10 | Wind | WIND | WIND | FALSE | 134.84
ALTWD_2_AT3WD3 | Wind | WIND | WIND | FALSE | 9.8
ALTWD_2_COAWD1 | Wind | WIND | WIND | FALSE | 50.4
ANAHM_2_CANYN1 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 49.21
ANAHM_2_CANYN2 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 48.04
ANAHM_2_CANYN3 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 46.49
ANAHM_2_CANYN4 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 49.8
APLHIL_1_SFKHY1 | Hydro | HYDRO | WATER | TRUE | 2.68
AQUAWS_2_AQWSR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 250
ARBWD_6_QF | Wind | WIND | WIND | FALSE | 19.95
ARCOGN_2_UNITS | CHP | COMBINED CYCLE | NATURAL GAS | TRUE | 245
ARLNTN_2_AR1SR1 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 100
ARLNTN_2_ASUSR1 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 131
ARVINN_6_ORION1 | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 12
ARVINN_6_ORION2 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 8
ASTORA_2_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 100
ASTORA_2_SOLAR2 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 75
ATHOS_5_AP1X2 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 250
ATHOS_5_AP2X2 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 200
ATWEL2_1_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
ATWELL_1_SOLAR | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 20
AVENAL_6_AVPARK | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 6
AVENAL_6_AVSLR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 7.9
AVENAL_6_AVSLR2 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 7.9
AVENAL_6_SANDDG | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 19
AVENAL_6_SUNCTY | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 20
AVSOLR_2_SOLAR | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 241.5
BAHIA_2_LKHSR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 5
BALCHS_7_UNIT 1 | Hydro | HYDRO | WATER | TRUE | 31
BALCHS_7_UNIT 2 | Hydro | HYDRO | WATER | TRUE | 52.5
BALCHS_7_UNIT 3 | Hydro | HYDRO | WATER | TRUE | 54.6
BANKPP_2_NSPIN | Pump | PUMP | WATER | TRUE | 270
BARRE_2_ALASB1 | Hybrid_BattStorage | OTHER | HYBD | TRUE | 5
BARRE_2_ALASB1_SUN | Hybrid_Solar_1Axis | OTHER | HYBD | TRUE | 10
BARRE_2_QF | CHP | OTHER | OTHER | FALSE | 0.2
BARRE_6_PEAKER | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 49
BASICE_2_UNITS | Peaker | COMBINED CYCLE | NATURAL GAS | TRUE | 120
BDGRCK_1_UNITS | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 48.08
BEARDS_7_UNIT 1 | Hydro | HYDRO | WATER | TRUE | 11.5
BEARMT_1_UNIT | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 49.21
BELDEN_7_UNIT 1 | Hydro | HYDRO | WATER | TRUE | 119
BERCYN_2_BCEBT1 | Battery Storage | OTHER | LESR | TRUE | 13
BGROCK_2_BRFBX2 | Battery Storage | OTHER | LESR | TRUE | 200
BGSKYN_2_AS2SR1 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 105
BGSKYN_2_ASPSR2 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 100
BGSKYN_2_ASSR1B | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 17
BGSKYN_2_ASSR3A | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 15
BGSKYN_2_ASSR3B | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 5
BGSKYN_2_BS3SR3 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
BIGCRK_2_EXESWD | Hydro | HYDRO | WATER | TRUE | 820
BIGCRK_7_DAM7 | Hydro | HYDRO | WATER | FALSE | 0.3
BIGCRK_7_MAMRES | Hydro | HYDRO | WATER | FALSE | 1.25
BIGSKY_2_AS2BT1 | Paired_BattStorage | OTHER | LESR | TRUE | 127
BIGSKY_2_ASLBT2 | Paired_BattStorage | OTHER | LESR | TRUE | 100
BIGSKY_2_BSKSR6 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
BIGSKY_2_BSKSR7 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
BIGSKY_2_BSKSR8 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
BIGSKY_2_SOLAR1 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
BIGSKY_2_SOLAR2 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 40
BIGSKY_2_SOLAR3 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
BIGSKY_2_SOLAR4 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
BIGSKY_2_SOLAR5 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 5
BIGSKY_2_SOLAR6 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 85
BIGSKY_2_SOLAR7 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 50
BIOMAS_1_UNIT 1 | Biomass/Wood | STEAM | BIOMASS | FALSE | 25.5
BISHOP_1_ALAMO | Hydro | HYDRO | WATER | FALSE | 13.4
BISHOP_1_UNITS | Hydro | HYDRO | WATER | FALSE | 15.8
BKRFLD_2_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 1.38
BLACK_7_UNIT 1 | Hydro | HYDRO | WATER | TRUE | 85
BLACK_7_UNIT 2 | Hydro | HYDRO | WATER | TRUE | 84.1
BLAST_1_WIND | Wind | WIND | WIND | FALSE | 49
BLCKBT_2_STONEY | Hydro | HYDRO | WATER | TRUE | 6.2
BLCKWL_6_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 12
BLKCRK_2_GMCBT1 | Paired_BattStorage | OTHER | LESR | TRUE | 230
BLKCRK_2_SOLAR1 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 250
BLKDIA_2_BDEBT1 | Battery Storage | OTHER | LESR | TRUE | 200
BLM W_2_COSBT1 | Paired_BattStorage | OTHER | LESR | TRUE | 60
BLM W_2_MDRBT1 | Battery Storage | OTHER | LESR | TRUE | 20
BLM_2_UNITS | Geothermal | STEAM | GEOTHERMAL | TRUE | 35
BLVRDE_6_BLVBT1 | Battery Storage | OTHER | LESR | TRUE | 10
BLYTHE_1_SOLAR1 | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 21
BLYTHE_1_SOLAR2 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
BNNIEN_7_ALTAPH | Hydro | HYDRO | WATER | FALSE | 1
BOGUE_1_UNITA1 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 48.69
BORDER_6_UNITA1 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 51.25
BOWMN_6_HYDRO | Hydro | HYDRO | WATER | FALSE | 3.6
BRDGVL_7_BAKER | Hydro | HYDRO | WATER | FALSE | 1.49
BRDSLD_2_HIWIND | Wind | WIND | WIND | FALSE | 162
BRDSLD_2_MTZUM2 | Wind | WIND | WIND | FALSE | 78.2
BRDSLD_2_MTZUMA | Wind | WIND | WIND | FALSE | 36.8
BRDSLD_2_SHILO1 | Wind | WIND | WIND | FALSE | 150
BRDSLD_2_SHILO2 | Wind | WIND | WIND | FALSE | 150
BRDSLD_2_SHLO3A | Wind | WIND | WIND | FALSE | 102.5
BRDSLD_2_SHLO3B | Wind | WIND | WIND | FALSE | 100
BREGGO_6_DEGRSL | Solar_2Axis | PHOTO VOLTAIC | SUN | FALSE | 6.3
BREGGO_6_SOLAR | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 26
BRODIE_2_WIND | Wind | WIND | WIND | FALSE | 102
BUCKBL_2_PL1X3 | CCGT | COMBINED CYCLE | NATURAL GAS | TRUE | 493.63
BUCKCK_2_HYDRO | Hydro | HYDRO | WATER | FALSE | 0.99
BUCKCK_7_OAKFLT | Hydro | HYDRO | WATER | FALSE | 1.3
BUCKCK_7_PL1X2 | Hydro | HYDRO | WATER | TRUE | 57.25
BUCKWD_1_NPALM1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 2.4
BUCKWD_1_QF | Wind | WIND | WIND | FALSE | 16.5
BURNYF_2_UNIT 1 | Biomass/Wood | STEAM | BIOMASS | FALSE | 29
BUTTVL_7_UNIT 1 | Hydro | HYDRO | WATER | TRUE | 39.5
CABALO_2_M2BSR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 50
CABALO_2_M2WSR2 | Solar_1Axis | PHOTO VOLTAIC | SUN | TRUE | 100
CABLRO_2_CBSBT1 | Battery Storage | OTHER | LESR | TRUE | 99.7
CABZON_1_WINDA1 | Wind | WIND | WIND | FALSE | 41
CALFTN_2_CFSBT1 | Paired_BattStorage | OTHER | LESR | TRUE | 60
CALFTN_2_SOLAR | Paired_Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 130
CALFTS_2_CFSSR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 150
CALGEN_1_MDRBT1 | Battery Storage | OTHER | LESR | TRUE | 25
CALGEN_1_UNITS | Geothermal | STEAM | GEOTHERMAL | TRUE | 55
CALPIN_1_AGNEW | CCGT | COMBUSTION TURBINE | NATURAL GAS | TRUE | 28.56
CAMCHE_1_PL1X3 | Hydro | HYDRO | WATER | FALSE | 9.99
CAMERN_6_BSPSR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 0.84
CAMLOT_2_SOLAR1 | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 45
CAMLOT_2_SOLAR2 | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 15
CAMPFW_7_FARWST | Hydro | HYDRO | WATER | TRUE | 6.8
CANTUA_1_SOLAR | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 20
CAPWD_1_QF | Wind | WIND | WIND | FALSE | 19.55
CARBOU_7_PL2X3 | Hydro | HYDRO | WATER | TRUE | 49
CARBOU_7_PL4X5 | Hydro | HYDRO | WATER | TRUE | 120
CARBOU_7_UNIT 1 | Hydro | HYDRO | WATER | TRUE | 24
CARLS1_2_CARCT1 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 422
CARLS2_1_CARCT1 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 105.5
CASADB_1_CD4GT1 | Geothermal | STEAM | GEOTHERMAL | TRUE | 40.7
CASCES_6_CESBT1 | Battery Storage | OTHER | LESR | TRUE | 25
CASCES_6_CESBT2 | Battery Storage | OTHER | LESR | TRUE | 20
CATLNA_2_SOLAR | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 110
CATLNA_2_SOLAR2 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 18
CAVLSR_2_BSOLAR | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 40
CAVLSR_2_RSOLAR | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 210
CAYTNO_2_VASCO | Biogas | RECIPROCATING ENGINE | BIOGAS | FALSE | 4.3
CDWR07_2_GEN | Reciprocating Engine | PUMP | WATER | TRUE | 415.3
CEDRCK_6_UNIT | Hydro | HYDRO | WATER | FALSE | 0.98
CEDUCR_2_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
CEDUCR_2_SOLAR2 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
CEDUCR_2_SOLAR3 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 15
CEDUCR_2_SOLAR4 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
CENT40_1_C40SR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 40
CENTER_2_RHONDO | Hydro | HYDRO | WATER | TRUE | 1.91
CENTER_2_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 0.9
CENTER_6_PEAKER | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 47.3
CENTPD_2_BMSSX2 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 223.6
CENTPD_2_BMSX2 | Paired_BattStorage | OTHER | LESR | TRUE | 112
CENTRY_6_PL1X4 | Peaker | FTUR | NATURAL GAS | TRUE | 41.4
CHALK_1_UNIT | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 48.67
CHARCA_1_NGLSR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 4.62
CHARMN_2_PGONG1 | CHP | FTUR | NATURAL GAS | FALSE | 19.87
CHESTN_2_CHWBX2 | Paired_BattStorage | OTHER | LESR | TRUE | 135
CHESTN_2_CHWSX2 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 150
CHEVCD_6_UNIT | CHP | COMBUSTION TURBINE | NATURAL GAS | FALSE | 11.5
CHEVCO_6_UNIT 1 | CHP | COMBUSTION TURBINE | NATURAL GAS | FALSE | 16.5
CHEVCO_6_UNIT 2 | CHP | FTUR | NATURAL GAS | FALSE | 8.5
CHEVCY_1_UNIT | CHP | COMBUSTION TURBINE | NATURAL GAS | FALSE | 24.3
CHEVMN_2_UNITS | CHP |  | OTHER | FALSE | 124.87
CHICPK_7_UNIT 1 | Hydro | HYDRO | WATER | TRUE | 42
CHILLS_1_SYCENG | Biogas | COMBUSTION TURBINE | BIOGAS | FALSE | 1.5
CHILLS_7_UNITA1 | Biogas |  | BIOGAS | TRUE | 2.25
CHINO_2_APEBT1 | Battery Storage | OTHER | LESR | TRUE | 20
CHINO_2_JURUPA | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 1.5
CHINO_2_PESBT1 | Battery Storage | OTHER | LESR | TRUE | 20
CHINO_2_QF | CHP | OTHER | OTHER | FALSE | 0.19
CHINO_2_SASOLR | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 1.5
CHINO_2_SOLAR2 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 1.49
CHINO_6_CIMGEN | CHP | COMBINED CYCLE | NATURAL GAS | TRUE | 26
CHWCHL_1_AVSSR1 | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 2.56
CHWCHL_1_AVSSR2 | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 5
CHWCHL_1_UNIT | Reciprocating Engine | RECIPROCATING ENGINE | NATURAL GAS | TRUE | 48.6
CLOVDL_1_SOLAR | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 1.5
CLOVER_2_UNIT | Hydro | HYDRO | WATER | FALSE | 0.99
CLRMNT_6_CLEBT1 | Battery Storage | OTHER | LESR | TRUE | 9
CLRMTK_1_QF | CHP | FTUR | NATURAL GAS | FALSE | 1.25
CMBLND_2_DS2BT1 | Paired_BattStorage | OTHER | LESR | TRUE | 52
CMBLND_2_DS2BT2 | Paired_BattStorage | OTHER | LESR | TRUE | 33
CMBLND_2_DS2BT3 | Paired_BattStorage | OTHER | LESR | TRUE | 46
CMBLND_2_DS2SR1 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 65
CMBLND_2_DS2SR2 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 65
CMBLND_2_DS2SR3 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 52
CNTNLA_2_SOLAR1 | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 125
CNTNLA_2_SOLAR2 | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 45.6
COCOPP_2_CTG1 | Peaker | FTUR | NATURAL GAS | TRUE | 204.2
COCOPP_2_CTG2 | Peaker | FTUR | NATURAL GAS | TRUE | 202.7
COCOPP_2_CTG3 | Peaker | FTUR | NATURAL GAS | TRUE | 208.96
COCOPP_2_CTG4 | Peaker | FTUR | NATURAL GAS | TRUE | 204.29
COCOSB_6_SOLAR | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 1.5
COGNAT_1_UNIT | Biomass/Wood | STEAM | BIOMASS | FALSE | 45
COLEMN_2_UNIT | Hydro | HYDRO | WATER | FALSE | 13
COLGAT_7_UNIT 1 | Hydro | HYDRO | WATER | TRUE | 176.72
COLGAT_7_UNIT 2 | Hydro | HYDRO | WATER | TRUE | 175.67
COLPIN_6_COLLNS | Biomass/Wood | STEAM | BIOMASS | FALSE | 3.3
COLTON_6_AGUAM1 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 43
COLUSA_2_PL1X3 | CCGT | COMBINED CYCLE | NATURAL GAS | TRUE | 641
COLVIL_7_PL1X2 | Hydro | HYDRO | WATER | TRUE | 246.86
CONDOR_2_CDRBT1 | Battery Storage | OTHER | LESR | TRUE | 200
CONTRL_1_CASAD1 | Geothermal | OTHER | GEOTHERMAL | FALSE | 7.2
CONTRL_1_CASAD2 | Geothermal | OTHER | GEOTHERMAL | TRUE | 10.5
CONTRL_1_CASAD3 | Geothermal | OTHER | GEOTHERMAL | FALSE | 14
CONTRL_1_LUNDY | Hydro | HYDRO | WATER | FALSE | 3
CONTRL_1_OXBOW | Geothermal | STEAM | GEOTHERMAL | FALSE | 60
CONTRL_1_POOLE | Hydro | HYDRO | WATER | TRUE | 11.07
CONTRL_1_QF | CHP | OTHER | OTHER | FALSE | 1.05
CONTRL_1_RUSHCK | Hydro | HYDRO | WATER | TRUE | 12.19
COPMT2_2_SOLAR2 | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 155
COPMT4_2_SOLAR4 | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 92
COPMTN_2_CM10 | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 10
COPMTN_2_SOLAR1 | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 48
CORCAN_1_SOLAR1 | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 20
CORCAN_1_SOLAR2 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 11
CORONS_2_SOLAR | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 0.99
CORONS_6_CLRWTR | CCGT | COMBINED CYCLE | NATURAL GAS | TRUE | 28
CORRAL_6_SJOAQN | Biogas | RECIPROCATING ENGINE | BIOGAS | FALSE | 4.3
COTTLE_2_FRNKNH | Hydro | HYDRO | WATER | FALSE | 5.3
COVERD_2_HCKHY1 | Hydro | HYDRO | WATER | FALSE | 6.89
COVERD_2_MCKHY1 | Hydro | HYDRO | WATER | FALSE | 2.8
COVERD_2_QFUNTS | Hydro | HYDRO | WATER | TRUE | 5.5
COVERD_2_RCKHY1 | Hydro | HYDRO | WATER | FALSE | 2
COWCRK_2_UNIT | Hydro | HYDRO | WATER | FALSE | 2
CPVERD_2_SOLAR | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 139
CRELMN_6_RAMON1 | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 2
CRELMN_6_RAMON2 | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 5
CRELMN_6_RAMSR3 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 4.32
CRESSY_1_PARKER | Hydro | HYDRO | WATER | FALSE | 2.83
CRESTA_7_PL1X2 | Hydro | HYDRO | WATER | TRUE | 70.4
CRIMSN_2_CRMBT1 | Battery Storage | OTHER | LESR | TRUE | 200
CRIMSN_2_CRMBT2 | Battery Storage | OTHER | LESR | TRUE | 150
CRNEVL_6_CRNVA | Hydro | HYDRO | WATER | FALSE | 0.9
CRNEVL_6_SJQN 2 | Hydro | HYDRO | WATER | FALSE | 3.2
CROKET_7_UNIT | CHP | COMBINED CYCLE | NATURAL GAS | FALSE | 240
CRSTWD_6_KUMYAY | Wind | WIND | WIND | FALSE | 50
CRWCKS_1_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
CSCGNR_1_UNIT 1 | Peaker | FTUR | NATURAL GAS | TRUE | 24.75
CSCGNR_1_UNIT 2 | Peaker | FTUR | NATURAL GAS | TRUE | 24.75
CSLR4S_2_SOLAR | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 130
CSTRVL_7_PL1X2 | Biogas | RECIPROCATING ENGINE | OTHER | TRUE | 4.53
CSTRVL_7_QFUNTS | CHP | OTHER | OTHER | FALSE | 2
CTNWDP_1_QF | Hydro | HYDRO | WATER | FALSE | 0.5
CUMBIA_1_SOLAR | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 19
CUMMNG_6_SUNCT1 | CHP | RECIPROCATING ENGINE | NATURAL GAS | TRUE | 4
CURTIS_1_CANLCK | Hydro | HYDRO | WATER | FALSE | 0.9
CURTIS_1_FARFLD | Hydro | HYDRO | WATER | FALSE | 0.9
CUYAMA_6_SB3SB1 | Hybrid_BattStorage | OTHER | HYBD | TRUE | 3
CUYAMA_6_SB3SB1_SUN | Hybrid_Solar_1Axis | OTHER | HYBD | TRUE | 3
CUYAMS_6_CUYSR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 40
DAIRLD_1_MD1SL1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 1.5
DAIRLD_1_MD2BM1 | Biogas | RECIPROCATING ENGINE | BIOGAS | FALSE | 0.8
DAVIS_1_SOLAR1 | Solar_2Axis | PHOTO VOLTAIC | SUN | FALSE | 1
DAVIS_1_SOLAR2 | Solar_2Axis | PHOTO VOLTAIC | SUN | FALSE | 1
DAVIS_7_MNMETH | Biogas | RECIPROCATING ENGINE | BIOGAS | FALSE | 4
DEADCK_1_UNIT | Hydro | HYDRO | WATER | FALSE | 1.96
DEERCR_6_UNIT 1 | Hydro | HYDRO | WATER | FALSE | 7
DELAMO_2_ALASB2 | Hybrid_BattStorage | OTHER | HYBD | TRUE | 5
DELAMO_2_ALASB2_SUN | Hybrid_Solar_1Axis | OTHER | HYBD | TRUE | 10
DELAMO_2_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 1.5
DELAMO_2_SOLAR2 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 1.75
DELAMO_2_SOLAR3 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 1.25
DELAMO_2_SOLAR4 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 1.3
DELAMO_2_SOLAR5 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 1
DELAMO_2_SOLAR6 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 2
DELAMO_2_SOLRC1 | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 1.16
DELAMO_2_SOLRD | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 1.25
DELSUR_6_BSOLAR | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 3
DELSUR_6_CREST | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 8.5
DELSUR_6_DRYFRB | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 5
DELSUR_6_HORSR1 |  | PHOTO VOLTAIC | SUN | FALSE | 1.5
DELSUR_6_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 6.5
DELSUR_6_SOLAR4 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 1.5
DELSUR_6_SOLAR5 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 1.5
DELTA_2_PL1X4 | CCGT | COMBINED CYCLE | NATURAL GAS | TRUE | 880
DEVERS_1_SEPV05 | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 2
DEVERS_1_SOLAR | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 18.5
DEVERS_1_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 12
DEVERS_1_SOLAR2 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 9
DEVERS_2_CS2SR4 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 0.91
DEVERS_2_DHSPG2 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 1.4
DEXZEL_1_UNIT | CHP | COMBUSTION TURBINE | NATURAL GAS | TRUE | 20
DIABLO_7_UNIT 1 | Nuclear | STEAM | URANIUM | FALSE | 1150
DIABLO_7_UNIT 2 | Nuclear | STEAM | URANIUM | FALSE | 1150
DISCOV_1_CHEVRN | CHP | FTUR | NATURAL GAS | FALSE | 48.8
DIXNLD_1_LNDFL | Biomass/Wood | RECIPROCATING ENGINE | BIOMASS | FALSE | 1.6
DMDVLY_1_UNITS | Hydro | PUMPED STORAGE | WATER | FALSE | 15.6
DONNLS_7_UNIT | Hydro | HYDRO | WATER | TRUE | 72
DOSMGO_2_NSPIN | Pump | PUMP | WATER | TRUE | 159
DOUBLC_1_UNITS | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 52.23
DRACKR_2_D4SR4B | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 62.5
DRACKR_2_DS3SR3 | Paired_Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 125
DRACKR_2_DS4SR4 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 62.5
DRACKR_2_DSUBT1 | Paired_BattStorage | OTHER | LESR | TRUE | 63
DRACKR_2_DSUBT2 | Paired_BattStorage | OTHER | LESR | TRUE | 115
DRACKR_2_DSUBT3 | Paired_BattStorage | OTHER | LESR | TRUE | 115
DRACKR_2_DSUBT4 | Paired_BattStorage | OTHER | LESR | TRUE | 47
DRACKR_2_SOLAR1 | Paired_Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 110
DRACKR_2_SOLAR2 | Paired_Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 125
DREWS_6_PL1X4 | Peaker | FTUR | NATURAL GAS | TRUE | 41.4
DREWSR_2_BHSSR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 100
DRUM_7_PL1X2 | Hydro | HYDRO | WATER | TRUE | 26
DRUM_7_PL3X4 | Hydro | HYDRO | WATER | TRUE | 28.9
DRUM_7_UNIT 5 | Hydro | HYDRO | WATER | TRUE | 50
DSABLA_7_UNIT | Hydro | HYDRO | WATER | FALSE | 18.5
DSFLWR_2_W9CSB1 | Hybrid_BattStorage | OTHER | HYBD | TRUE | 52
DSFLWR_2_W9CSB1_SUN | Hybrid_Solar_1Axis | OTHER | HYBD | TRUE | 102
DSFLWR_2_W9CSB2 | Hybrid_BattStorage | OTHER | HYBD | TRUE | 36
DSFLWR_2_W9CSB2_SUN | Hybrid_Solar_1Axis | OTHER | HYBD | TRUE | 72
DSFLWR_2_WS2SR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 100
DSRTHV_2_DH1SR1 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 80
DSRTHV_2_DH2BT1 | Paired_BattStorage | OTHER | LESR | TRUE | 35
DSRTHV_2_DH2SR2 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 70
DSRTSL_2_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 296.19
DSRTSN_2_DS2BX2 | Paired_BattStorage | OTHER | LESR | TRUE | 230
DSRTSN_2_DS2X2 | Paired_BattStorage | OTHER | LESR | TRUE | 230
DSRTSN_2_SOLAR1 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 300
DSRTSN_2_SOLAR2 | Paired_Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 250
DTCHWD_2_BT3WND | Wind | WIND | WIND | FALSE | 4.5
DUANE_1_PL1X3 | CCGT | COMBINED CYCLE | NATURAL GAS | TRUE | 147.8
DUTCH1_7_UNIT 1 | Hydro | HYDRO | WATER | TRUE | 22
DUTCH2_7_UNIT 1 | Hydro | HYDRO | WATER | TRUE | 26
DVLCYN_1_UNITS | Hydro | HYDRO | WATER | TRUE | 235
DYERSM_6_DSWWD1 | Wind | WIND | WIND | FALSE | 44.8
DYLAN_2_BMTBT1 | Battery Storage | OTHER | LESR | TRUE | 100
EASTWD_7_UNIT | Pumped Hydro | PUMPED STORAGE | WATER | TRUE | 200
EDMONS_2_NSPIN | Pump | PUMP | WATER | TRUE | 775.8
EDWARD_2_E21SB1 | Hybrid_BattStorage | OTHER | HYBD | TRUE | 71
EDWARD_2_E21SB1_SUN | Hybrid_Solar_1Axis | OTHER | HYBD | TRUE | 130
EDWARD_2_E23SB1 | Hybrid_BattStorage | OTHER | HYBD | TRUE | 6
EDWARD_2_E23SB1_SUN | Hybrid_Solar_1Axis | OTHER | HYBD | TRUE | 24
EDWARD_2_ES2BT3 | Hybrid_BattStorage | OTHER | HYBD | TRUE | 66
EDWARD_2_ES2BT3_SUN | Hybrid_Solar_1Axis | OTHER | HYBD | TRUE | 118
EDWARD_2_ESSSB1 | Hybrid_BattStorage | OTHER | HYBD | TRUE | 47
EDWARD_2_ESSSB1_SUN | Hybrid_Solar_1Axis | OTHER | HYBD | TRUE | 68
EDWARD_2_ESSSB2 | Hybrid_BattStorage | OTHER | HYBD | TRUE | 21.5
EDWARD_2_ESSSB2_SUN | Hybrid_Solar_1Axis | OTHER | HYBD | TRUE | 132
EEKTMN_6_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
ELCAJN_6_EB1BT1 | Battery Storage | OTHER | LESR | TRUE | 7.5
ELCAJN_6_LM6K | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 48.1
ELCAJN_6_UNITA1 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 45.42
ELCAP_1_SOLAR | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 1.5
ELDORO_7_UNIT 1 | Hydro | HYDRO | WATER | FALSE | 11
ELDORO_7_UNIT 2 | Hydro | HYDRO | WATER | FALSE | 11
ELECTR_7_PL1X3 | Hydro | HYDRO | WATER | TRUE | 93
ELKCRK_6_STONYG | Hydro | HYDRO | WATER | TRUE | 4.9
ELKHIL_2_PL1X3 | CCGT | COMBINED CYCLE | NATURAL GAS | TRUE | 551.7
ELKHRN_1_EESX3 | Battery Storage | OTHER | LESR | TRUE | 182.5
ELLIOT_6_ELIBT1 | Battery Storage | OTHER | LESR | TRUE | 10
ELLIS_2_QF | CHP | OTHER | OTHER | FALSE | 12
ELNIDO_1_ECRSR1 | Solar_Fixed | PHOTO VOLTAIC | SUN | TRUE | 3
ELSEGN_2_UN1011 | CCGT | COMBINED CYCLE | NATURAL GAS | TRUE | 274.31
ELSEGN_2_UN2021 | CCGT | COMBINED CYCLE | NATURAL GAS | TRUE | 271.74
ENERSJ_2_WIND | Wind | WIND | WIND | FALSE | 151
ENERSJ_5_ESJWD2 | Wind | WIND | WIND | FALSE | 105
ENWIND_2_WIND1 | Wind | WIND | WIND | FALSE | 47.1
ENWIND_2_WIND2 | Wind | WIND | WIND | FALSE | 38.24
ESCNDO_6_EB1BT1 | Battery Storage | OTHER | LESR | TRUE | 10
ESCNDO_6_EB2BT2 | Battery Storage | OTHER | LESR | TRUE | 10
ESCNDO_6_EB3BT3 | Battery Storage | OTHER | LESR | TRUE | 10
ESCNDO_6_PL1X2 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 48.71
ESCNDO_6_UNITB1 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 50.96
ESCO_6_GLMQF | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 49.9
ESNHWR_2_CS1BT3 | Battery Storage | OTHER | LESR | TRUE | 10
ESNHWR_2_HDSBT2 | Battery Storage | OTHER | LESR | TRUE | 10
ESNHWR_2_WC1BT1 | Battery Storage | OTHER | LESR | TRUE | 3
ESQUON_6_LNDFIL | Biogas | RECIPROCATING ENGINE | BIOGAS | FALSE | 2.1
ESTWND_2_OPPWD1 | Wind | WIND | WIND | FALSE | 57.14
ETIWND_2_CHMPNE | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 1
ETIWND_2_FONTNA | Hydro | HYDRO | WATER | FALSE | 2.56
ETIWND_2_SEPBT1 | Battery Storage | OTHER | LESR | TRUE | 100
ETIWND_2_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 1
ETIWND_2_SOLAR2 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 1
ETIWND_2_SOLAR5 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 2
ETIWND_2_UNIT1 | Peaker | FTUR | NATURAL GAS | TRUE | 33.6
ETIWND_6_GRPLND | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 45.64
ETIWND_6_INEBT1 | Battery Storage | OTHER | LESR | TRUE | 70
ETIWND_6_MWDETI | Hydro | HYDRO | WATER | FALSE | 24
EXCHEC_7_UNIT 1 | Hydro | HYDRO | WATER | TRUE | 94.5
EXCLSG_1_SOLAR | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 60
FALBRK_6_FESBT1 | Battery Storage | OTHER | LESR | TRUE | 40
FELLOW_7_QFUNTS | CHP | FTUR | NATURAL GAS | FALSE | 6.2
FIFTHS_2_FSSBT | Paired_BattStorage | OTHER | LESR | TRUE | 137
FIFTHS_2_FSSR1 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 150
FILIPPI_2_QZSBTX | Paired_BattStorage | OTHER | LESR | TRUE | 150
FILIPPI_2_QZSSRX | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 300
FLOWD_2_RT2WD2 | Wind | WIND | WIND | FALSE | 27.39
FLOWD_2_WIND1 | Wind | WIND | WIND | FALSE | 11.9
FLOWD2_2_FPLWND | Wind | WIND | WIND | FALSE | 18
FMEADO_6_HELLHL | Hydro | HYDRO | WATER | FALSE | 0.6
FMEADO_7_UNIT | Hydro | HYDRO | WATER | TRUE | 16
FORBST_7_UNIT 1 | Hydro | HYDRO | WATER | TRUE | 37.5
FORKBU_6_UNIT | Hydro | HYDRO | WATER | FALSE | 14.4
FRESHW_1_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
FRIANT_6_UNITS | Hydro | HYDRO | WATER | FALSE | 25
FRNTBW_6_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
FROGTN_1_UTICAA | Hydro | HYDRO | WATER | FALSE | 1.4
FROGTN_1_UTICAM | Hydro | HYDRO | WATER | FALSE | 3.6
FTSWRD_6_TRFORK | Hydro | HYDRO | WATER | FALSE | 1.63
FTSWRD_7_QFUNTS | Hydro | HYDRO | WATER | FALSE | 1.6
FULTON_1_QF | Hydro | HYDRO | WATER | FALSE | 1
GALE_1_SR3SR3 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 13.8
GANSO_1_WSTBM1 | Biogas | RECIPROCATING ENGINE | BIOGAS | FALSE | 1
GARLND_2_GARBT1 | Paired_BattStorage | OTHER | LESR | TRUE | 88
GARLND_2_GASLR | Paired_Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 180
GARLND_2_GASLRA | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
GARNET_1_SOLAR | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 4
GARNET_1_SOLAR2 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 4
GARNET_1_WIND | Wind | WIND | WIND | FALSE | 6.5
GARNET_1_WINDS | Wind | WIND | WIND | FALSE | 22.5
GARNET_1_WT3WND | Wind | WIND | WIND | FALSE | 6
GARNET_2_COAWD2 | Wind | WIND | WIND | FALSE | 10.8
GARNET_2_HYDRO | Hydro | HYDRO | WATER | FALSE | 1
GARNET_2_WIND1 | Wind | WIND | WIND | FALSE | 11.2
GARNET_2_WIND2 | Wind | WIND | WIND | FALSE | 11.7
GARNET_2_WIND3 | Wind | WIND | WIND | FALSE | 12.6
GARNET_2_WIND4 | Wind | WIND | WIND | FALSE | 9.8
GARNET_2_WIND5 | Wind | WIND | WIND | FALSE | 3
GASKW1_2_GW1SR1 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
GASKW1_2_GW2BT1 | Paired_BattStorage | OTHER | LESR | TRUE | 20
GASKW1_2_GW2SR1 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 16
GASKW1_2_GW2SR2 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 29
GASKW1_2_GW3SR1 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
GASKW1_2_GW4SR1 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
GASKW1_2_GW5SR1 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
GATES_2_SOLAR | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 20
GATES_2_WSOLAR | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 10
GATEWY_2_GESBT1 | Battery Storage | OTHER | LESR | TRUE | 250
GATWAY_2_PL1X3 | CCGT | COMBINED CYCLE | NATURAL GAS | TRUE | 585
GENESI_2_STG | Paired_Solar_Thermal | STEAM | SUN | FALSE | 250
GEYS11_7_UNIT11 | Geothermal | STEAM | GEOTHERMAL | TRUE | 86.8
GEYS12_7_UNIT12 | Geothermal | STEAM | GEOTHERMAL | TRUE | 57
GEYS13_7_UNIT13 | Geothermal | STEAM | GEOTHERMAL | TRUE | 73
GEYS14_7_UNIT14 | Geothermal | STEAM | GEOTHERMAL | TRUE | 70
GEYS16_7_UNIT16 | Geothermal | STEAM | GEOTHERMAL | TRUE | 63
GEYS17_7_UNIT17 | Geothermal | STEAM | GEOTHERMAL | TRUE | 75.5
GEYS18_7_UNIT18 | Geothermal | STEAM | GEOTHERMAL | TRUE | 72
GEYS20_7_UNIT20 | Geothermal | STEAM | GEOTHERMAL | TRUE | 50
GIFENS_6_BUGSL1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
GIFFEN_6_SOLAR | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 10
GIFFEN_6_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 9
GILROY_1_UNIT | CCGT | COMBINED CYCLE | NATURAL GAS | TRUE | 120
GILRPP_1_PL1X2 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 95.2
GILRPP_1_PL3X4 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 46.2
GLDFGR_6_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
GLDFGR_6_SOLAR2 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 11.4
GLDTWN_6_COLUM3 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 10
GLDTWN_6_SOLAR | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 5
GLNARM_2_UNIT 5 | CCGT | COMBINED CYCLE | NATURAL GAS | TRUE | 65.81
GLNARM_7_UNIT 1 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 22.13
GLNARM_7_UNIT 2 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 22.38
GLNARM_7_UNIT 3 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 44.83
GLNARM_7_UNIT 4 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 42.42
GLOW_6_SOLAR | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
GOLETA_2_GE2BT3 | Battery Storage | OTHER | LESR | TRUE | 60
GOLETA_2_VALBT1 | Battery Storage | OTHER | LESR | TRUE | 10
GOLETA_6_ELLWOD | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 54
GOLETA_6_EXGEN | CHP |  | OTHER | FALSE | 48.2
GONZLS_6_UNIT | Biogas | RECIPROCATING ENGINE | BIOGAS | FALSE | 1.42
GOOSLK_1_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 12
GRIDLY_6_SOLAR | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 2.5
GRIZLY_1_UNIT 1 | Hydro | HYDRO | WATER | TRUE | 20
GRNLF2_1_UNIT | CHP | COMBUSTION TURBINE | NATURAL GAS | TRUE | 49.2
GRNVLY_7_SCLAND | Biogas | RECIPROCATING ENGINE | BIOGAS | FALSE | 3.04
GRSCRK_6_BGCKWW | Hydro | HYDRO | WATER | FALSE | 5
GRZZLY_1_BERKLY | CCGT | COMBINED CYCLE | NATURAL GAS | FALSE | 26.35
GUERNS_6_HD3BM3 | Biogas | RECIPROCATING ENGINE | BIOGAS | TRUE | 1
GUERNS_6_SOLAR | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
GUERNS_6_VH2BM1 | Biogas | RECIPROCATING ENGINE | BIOGAS | TRUE | 1
GWFPWR_1_UNITS | Peaker | COMBUSTION TURBINE | NATURAL GAS |  | 98.46
GYS5X6_7_UNITS | Geothermal | STEAM | GEOTHERMAL | TRUE | 98.43
GYS7X8_7_UNITS | Geothermal | STEAM | GEOTHERMAL | TRUE | 95.8
GYSRVL_7_WSPRNG | Hydro | HYDRO | WATER | FALSE | 3.75
HAASPH_7_PL1X2 | Hydro | HYDRO | WATER | TRUE | 144
HALSEY_6_UNIT | Hydro | HYDRO | WATER | TRUE | 13.5
HAMLIN_1_BLDSB1 | Hybrid_BattStorage | PHOTO VOLTAIC | HYBD | TRUE | 75
HAMLIN_1_BLDSB1_SUN | Hybrid_Solar_1Axis | PHOTO VOLTAIC | HYBD | TRUE | 150
HAMLIN_1_BMSBT2 | Hybrid_BattStorage | PHOTO VOLTAIC | HYBD | TRUE | 25
HAMLIN_1_BMSBT2_SUN | Hybrid_Solar_1Axis | PHOTO VOLTAIC | HYBD | TRUE | 50
HARBGN_7_UNITS | CCGT | COMBINED CYCLE | NATURAL GAS | TRUE | 109.01
HARDWK_6_STWBM1 | Biogas | RECIPROCATING ENGINE | BIOGAS | TRUE | 1
HATCR1_7_UNIT | Hydro | HYDRO | WATER | FALSE | 8.5
HATCR2_7_UNIT | Hydro | HYDRO | WATER | FALSE | 8.5
HATLOS_6_BWDHY1 | Hydro | HYDRO | WATER | FALSE | 2
HATLOS_6_LSCRK | Hydro | HYDRO | WATER | FALSE | 1.7
HATRDG_2_WIND | Wind | WIND | WIND | FALSE | 102
HAYPRS_6_HAYHD1 | Hydro | HYDRO | WATER | FALSE | 5.8
HAYPRS_6_HAYHD2 | Hydro | HYDRO | WATER | FALSE | 6.7
HELMPG_7_UNIT 1 | Pumped Hydro | PUMPED STORAGE | WATER | TRUE | 407
HELMPG_7_UNIT 2 | Pumped Hydro | PUMPED STORAGE | WATER | TRUE | 407
HELMPG_7_UNIT 3 | Pumped Hydro | PUMPED STORAGE | WATER | TRUE | 404
HENRTA_6_ACDSR3 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 3
HENRTA_6_ELCTG1 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 50
HENRTA_6_ELCTG2 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 50
HENRTA_6_HDEBT1 | Battery Storage | OTHER | LESR | TRUE | 10
HENRTA_6_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 1.5
HENRTA_6_SOLAR2 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 2
HENRTS_1_SOLAR | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 100
HERDLN_6_BYHSR1 | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 5
HIDSRT_2_UNITS | CCGT | COMBINED CYCLE | NATURAL GAS | TRUE | 850
HIGGNS_1_COMBIE | Hydro | HYDRO | WATER | FALSE | 1.5
HIGHDS_2_H5SBT1 | Paired_BattStorage | OTHER | LESR | TRUE | 50
HIGHDS_2_H5SSR1 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 100
HILAND_7_YOLOWD | Hydro | HYDRO | WATER | FALSE | 3.75
HINSON_6_LBECH1 | Peaker | FTUR | NATURAL GAS | TRUE | 63
HINSON_6_LBECH2 | Peaker | FTUR | NATURAL GAS | TRUE | 63
HINSON_6_LBECH3 | Peaker | FTUR | NATURAL GAS | TRUE | 63
HINSON_6_LBECH4 | Peaker | FTUR | NATURAL GAS | TRUE | 63
HNTGBH_2_PL1X3 | CCGT | COMBINED CYCLE | NATURAL GAS | TRUE | 673.8
HOLGAT_1_BORAX | CHP |  | OTHER | FALSE | 48.2
HOLSTR_1_SOLAR | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 1.5
HOLSTR_1_SOLAR2 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 1.5
HUMBPP_1_UNITS3 | Reciprocating Engine | RECIPROCATING ENGINE | NATURAL GAS | TRUE | 65.08
HUMBPP_6_UNITS | Reciprocating Engine | RECIPROCATING ENGINE | NATURAL GAS | TRUE | 97.62
HURON_6_SOLAR | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 20
HYTTHM_2_UNITS | Hydro | HYDRO | WATER | TRUE | 933.1
IGNACO_1_QF | CHP | OTHER | OTHER | FALSE | 0.5
INDIGO_1_UNIT 1 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 45.3
INDIGO_1_UNIT 2 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 45.3
INDIGO_1_UNIT 3 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 45.3
INDVLY_1_UNITS | Hydro | HYDRO | WATER | FALSE | 3.01
INTKEP_2_UNITS | Hydro | HYDRO | WATER | TRUE | 405
IVANPA_1_UNIT1 | Solar_Thermal | STEAM | SUN | FALSE | 126
IVANPA_1_UNIT2 | Solar_Thermal | STEAM | SUN | FALSE | 133
IVANPA_1_UNIT3 | Solar_Thermal | STEAM | SUN | FALSE | 133
IVSLR2_2_SM2SR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 150
IVSLRP_2_SOLAR1 | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 200
IVWEST_2_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 150
JACMSR_1_JACSR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
JAVASR_1_JAVSR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 13.5
JAWBNE_2_NSRWND | Wind | WIND | WIND | FALSE | 160
JAWBNE_2_SRWND | Wind | WIND | WIND | FALSE | 30
JAWBNE_2_SRWWD2 | Wind | WIND | WIND | FALSE | 30.2
JAYNE_6_WLSLR | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 18
JOANEC_2_ST3BT3 | Battery Storage | OTHER | LESR | TRUE | 40
JOANEC_2_STABT1 | Battery Storage | OTHER | LESR | TRUE | 20
JOANEC_2_STABT2 | Battery Storage | OTHER | LESR | TRUE | 20
JOHANN_2_JOSBT1 | Battery Storage | OTHER | LESR | TRUE | 10
JOHANN_2_JOSBT2 | Battery Storage | OTHER | LESR | TRUE | 10
JOHANN_2_OCEBT2 | Battery Storage | OTHER | LESR | TRUE | 9
JOHANN_2_OCEBT3 | Battery Storage | OTHER | LESR | TRUE | 6
KANSAS_6_SOLAR | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 20
KEARNY_6_NESBT1 | Battery Storage | OTHER | LESR | TRUE | 10
KEARNY_6_SESBT2 | Battery Storage | OTHER | LESR | TRUE | 10
KEKAWK_6_UNIT | Hydro | HYDRO | WATER | FALSE | 5.5
KELSO_2_UNITS | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 198.03
KELYRG_6_UNIT | Hydro | HYDRO | WATER | TRUE | 11
KERKH2_7_UNIT 1 | Hydro | HYDRO | WATER | TRUE | 153.9
KERMAN_6_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 1.5
KERMAN_6_SOLAR2 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 1.5
KERNEY_6_FCSSR1 |  | PHOTO VOLTAIC | SUN | FALSE | 10
KERNFT_1_UNITS | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 52.4
KERNRG_1_UNITS | Peaker | COMBUSTION TURBINE | NATURAL GAS | FALSE | 55.2
KERRGN_1_UNIT 1 | Hydro | HYDRO | WATER | FALSE | 25.6
KINGCO_1_KINGBR | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 34.5
KINGRV_7_UNIT 1 | Hydro | HYDRO | WATER | TRUE | 51.2
KIRKER_7_KELCYN | Biogas | RECIPROCATING ENGINE | BIOGAS | FALSE | 3.56
KNGBRD_2_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
KNGBRD_2_SOLAR2 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
KNGBRG_1_KBSLR1 | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 1.5
KNGBRG_1_KBSLR2 | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 1.5
KNGCTY_6_UNITA1 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 44.6
KNTSTH_6_SOLAR | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 20
KNTSTH_6_WALSR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 19.88
KRAMER_1_R1BX3 | Paired_BattStorage | OTHER | LESR | TRUE | 75
KRAMER_1_R1PX3 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 90
KRAMER_1_R2BX2 | Paired_BattStorage | OTHER | LESR | TRUE | 40
KRAMER_1_R2PX2 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 48
KRNCNY_6_UNIT | Hydro | HYDRO | WATER | FALSE | 10.6
KYCORA_6_KMSBT1 | Battery Storage | OTHER | LESR | TRUE | 1
LACIEN_2_VENICE | Hydro | HYDRO | WATER | FALSE | 9.95
LAGBEL_2_CBPBT1 | Battery Storage | OTHER | LESR | TRUE | 100
LAMONT_1_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 60
LAMONT_1_SOLAR2 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
LAMONT_1_SOLAR3 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 14.99
LAMONT_1_SOLAR4 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 26.66
LAMONT_1_SOLAR5 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 16.66
LAPLMA_2_UNIT 1 | CCGT | COMBINED CYCLE | NATURAL GAS | TRUE | 267
LAPLMA_2_UNIT 2 | CCGT | COMBINED CYCLE | NATURAL GAS | TRUE | 266
LAPLMA_2_UNIT 3 | CCGT | COMBINED CYCLE | NATURAL GAS | TRUE | 266
LAPLMA_2_UNIT 4 | CCGT | COMBINED CYCLE | NATURAL GAS | TRUE | 267
LARKSP_6_UNIT 1 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 49
LARKSP_6_UNIT 2 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 49
LAROA2_2_UNITA1 | CCGT | COMBINED CYCLE | NATURAL GAS | TRUE | 322
LASSEN_6_UNITS | Biomass/Wood | STEAM | BIOMASS | TRUE | 30
LAWRNC_7_SUNYVL | Biogas | RECIPROCATING ENGINE | BIOGAS | FALSE | 0.3
LCKHT1_2_LH1BT1 | Battery Storage | OTHER | LESR | TRUE | 45
LCKHT1_2_LH1SR1 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 85
LCKHT1_2_LH1SR2 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 75
LEBECS_2_UNITS | CCGT | COMBINED CYCLE | NATURAL GAS | TRUE | 799.47
LECEF_1_UNITS | CCGT | COMBINED CYCLE | NATURAL GAS | TRUE | 309.84
LECONT_2_LESBT1 | Battery Storage | OTHER | LESR | TRUE | 125
LEPRFD_1_KANSAS | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 20
LGHTHP_6_ICEGEN | CCGT | COMBINED CYCLE | NATURAL GAS | TRUE | 48
LHILLS_6_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
LILIAC_6_SOLAR | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 3
LITLRK_6_GBCSR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 3
LITLRK_6_SEPV01 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 2
LITLRK_6_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 5
LITLRK_6_SOLAR2 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 2
LITLRK_6_SOLAR3 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 2
LITLRK_6_SOLAR4 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 3
LIVEOK_6_SOLAR | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 1.25
LIVOAK_1_UNIT 1 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 49.7
LMBEPK_2_UNITA1 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 47.5
LMBEPK_2_UNITA2 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 47.6
LMBEPK_2_UNITA3 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 47.75
LMEC_1_PL1X3 | CCGT | COMBINED CYCLE | NATURAL GAS | TRUE | 580
LNCSTR_6_CREST | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 5.5
LNCSTR_6_SOLAR2 | Hybrid_BattStorage | OTHER | HYBD | TRUE | 7
LNCSTR_6_SOLAR2_SUN | Hybrid_Solar_1Axis | OTHER | HYBD | TRUE | 3
LOCKFD_1_BEARCK | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 1.5
LOCKFD_1_KSOLAR | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 1
LODI25_2_UNIT 1 | Peaker | FTUR | NATURAL GAS | TRUE | 25
LODIEC_2_PL1X2 | CCGT | COMBINED CYCLE | NATURAL GAS | TRUE | 302.58
LOTUS_6_LSFSR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 50
LOWGAP_1_SUPHR | Hydro | HYDRO | WATER | FALSE | 0.99
LOWGAP_7_QFUNTS | Hydro | HYDRO | WATER | FALSE | 1.35
LTBEAR_1_LB3SR3 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
LTBEAR_1_LB4SR4 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 50
LTBEAR_1_LB4SR5 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 50
LTBERA_1_LB1SR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 40
MAGUND_1_BKISR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 1
MAGUND_1_BKSSR2 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 5.25
MALAGA_1_AUCTG1 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 55.3
MALAGA_1_AUCTG2 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 55.3
MALCHQ_7_UNIT 1 | Hydro | HYDRO | WATER | FALSE | 32.5
MANTEC_1_ML1SR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 1
MANZNA_2_CAMSR1 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 44
MANZNA_2_WIND | Wind | WIND | WIND | FALSE | 189
MARCPW_6_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
MARTIN_1_SUNSET | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 4.5
MARVEL_2_MARBT3 | Battery Storage | OTHER | LESR | TRUE | 74.94
MARVEL_2_MARBX2 | Battery Storage | OTHER | LESR | TRUE | 325
MCARTH_6_FRIVRB | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 1.5
MCCALL_1_QF | Hydro | HYDRO | WATER | FALSE | 0.52
MCFLND_5_MBSBX2 | Hybrid_BattStorage | OTHER | HYBD | TRUE | 150
MCFLND_5_MBSBX2_SUN | Hybrid_Solar_1Axis | OTHER | HYBD | TRUE | 300
MCFLND_5_MFSBT1 | Paired_BattStorage | OTHER | LESR | TRUE | 100
MCFLND_5_MFSSR1 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 200
MCFLND_5_MSCBT1 | Paired_BattStorage | OTHER | LESR | TRUE | 185
MCSWAN_6_UNITS | Hydro | HYDRO | WATER | TRUE | 9
MDFKRL_2_PROJCT | Hydro | HYDRO | WATER | TRUE | 210
MELRSE_6_MELBT1 | Battery Storage | OTHER | LESR | TRUE | 10
MELRSE_6_MELBT2 | Battery Storage | OTHER | LESR | TRUE | 10
MENBIO_6_RENEW1 | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 5
MERCED_1_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 1.5
MERCED_1_SOLAR2 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 1.5
MERCFL_6_UNIT | Hydro | HYDRO | WATER | TRUE | 3.5
MESAP_1_QF | CHP | OTHER | OTHER | FALSE | 1
METEC_2_PL1X3 | CCGT | COMBINED CYCLE | NATURAL GAS | TRUE | 597.05
MIDWD_2_WIND2 | Wind | WIND | WIND | FALSE | 3
MIDWD_7_CORAMB | Wind | WIND | WIND | FALSE | 7.5
MIRLOM_2_CORONA | Hydro | HYDRO | WATER | FALSE | 2.85
MIRLOM_2_CREST | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 1.5
MIRLOM_2_LNDFL | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 3
MIRLOM_2_MLBBTA | Battery Storage | OTHER | LESR | TRUE | 10
MIRLOM_2_MLBBTB | Battery Storage | OTHER | LESR | TRUE | 10
MIRLOM_2_TEMESC | Hydro | HYDRO | WATER | FALSE | 2.85
MIRLOM_6_PEAKER | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 47.18
MIRLOM_7_MWDLKM | Hydro | HYDRO | WATER | TRUE | 5
MISSIX_1_QF | CHP | FTUR | NATURAL GAS | FALSE | 1
MKTRCK_1_UNIT 1 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 47.72
MLPTAS_7_QFUNTS | CHP | OTHER | OTHER | FALSE | 1
MNDALY_6_MCGRTH | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 48.56
MNDOTA_1_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 60
MNDOTA_1_SOLAR2 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 5
MOJAVE_1_SIPHON | Hydro | HYDRO | WATER | TRUE | 14.36
MOJAVW_2_SOLAR | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
MONTPH_7_UNITS | Hydro | HYDRO | WATER | FALSE | 12.5
MOORPK_2_ACOBT1 | Battery Storage | OTHER | LESR | TRUE | 1.95
MOORPK_2_CALABS | Biogas | COMBUSTION TURBINE | BIOGAS | FALSE | 6.96
MOORPK_6_QF | CHP | OTHER | OTHER | FALSE | 0.8
MORWD_6_QF | Wind | WIND | WIND | FALSE | 38.16
MOSSLD_2_PSP1 | CCGT | COMBINED CYCLE | NATURAL GAS | TRUE | 510
MOSSLD_2_PSP2 | CCGT | COMBINED CYCLE | NATURAL GAS | TRUE | 510
MRCHNT_2_PL1X3 | CCGT | COMBINED CYCLE | NATURAL GAS | TRUE | 494.58
MRGT_6_MEF2 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 44
MRGT_6_MMAREF | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 45
MRGT_6_TGEBT1 | Battery Storage | OTHER | LESR | TRUE | 30
MRLSDS_6_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 15
MSHGTS_6_MMARLF | Biogas | RECIPROCATING ENGINE | BIOGAS | FALSE | 5
MSOLAR_2_MS4BT1 | Battery Storage | OTHER | LESR | TRUE | 10
MSOLAR_2_MS4SR4 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 52.5
MSOLAR_2_SOLAR1 | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 165
MSOLAR_2_SOLAR2 | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 100.81
MSOLAR_2_SOLAR3 | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 152
MSSION_2_QF | CHP |  | OTHER | FALSE | 2
MSTANG_2_MTGBT1 | Paired_BattStorage | OTHER | LESR | TRUE | 75
MSTANG_2_SOLAR | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 30
MSTANG_2_SOLAR3 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 40
MSTANG_2_SOLAR4 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 30
MTNPOS_1_UNIT | Biomass/Wood | STEAM | BIOMASS | FALSE | 46.64
MTWIND_1_MVPWD1 | Wind | WIND | WIND | FALSE | 66.6
MTWIND_1_UNIT 3 | Wind | WIND | WIND | FALSE | 22.44
MURRAY_6_UNIT | CHP | FTUR | NATURAL GAS | FALSE | 4.12
NAROW1_2_UNIT | Hydro | HYDRO | WATER | TRUE | 12
NAROW2_2_UNIT | Hydro | HYDRO | WATER | TRUE | 55
NAVYII_2_UNITS | Geothermal | STEAM | GEOTHERMAL | TRUE | 47
NCPA_7_GP1UN1 | Geothermal | STEAM | GEOTHERMAL | TRUE | 38.85
NCPA_7_GP1UN2 | Geothermal | STEAM | GEOTHERMAL | TRUE | 50
NCPA_7_GP2UN3 | Geothermal | STEAM | GEOTHERMAL | TRUE | 42.42
NCPA_7_GP2UN4 | Geothermal | STEAM | GEOTHERMAL | TRUE | 52.73
NEENCH_6_SOLAR | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 66
NEWARK_1_QF | CHP | OTHER | OTHER | FALSE | 0.1
NHOGAN_6_UNITS | Hydro | HYDRO | WATER | FALSE | 4
NOAKS_2_PESBT1 | Battery Storage | OTHER | LESR | TRUE | 80
NORCNV_1_NCVBT1 | Battery Storage | OTHER | LESR | TRUE | 132
NORORC_2_NOSBX2 | Hybrid_BattStorage | OTHER | HYBD | TRUE | 92
NORORC_2_NOSBX2_SUN | Hybrid_Solar_1Axis | OTHER | HYBD | TRUE | 150
NOVATO_6_LNDFL | Biogas | RECIPROCATING ENGINE | BIOGAS | FALSE | 3.9
NWCSTL_7_UNIT 1 | Hydro | HYDRO | WATER | FALSE | 12
NZWIND_2_WDSTR5 | Wind | WIND | WIND | FALSE | 6.31
NZWIND_6_CALWND | Wind | WIND | WIND | FALSE | 9
NZWIND_6_WDSTR | Wind | WIND | WIND | FALSE | 4.8
NZWIND_6_WDSTR2 | Wind | WIND | WIND | FALSE | 5.72
NZWIND_6_WDSTR3 | Wind | WIND | WIND | FALSE | 6
NZWIND_6_WDSTR4 | Wind | WIND | WIND | FALSE | 5.91
OAK C_1_EBMUD | Biogas | RECIPROCATING ENGINE | BIOGAS | FALSE | 6.9
OAK C_7_UNIT 1 | Peaker | COMBUSTION TURBINE | DISTILLATE | TRUE | 55
OAK C_7_UNIT 3 | Peaker | COMBUSTION TURBINE | DISTILLATE | TRUE | 55
OAK L_1_GTG1 | Biogas | COMBUSTION TURBINE | BIOGAS | FALSE | 4.6
OAKWD_6_QF | Wind | WIND | WIND | FALSE | 27.87
OAKWD_6_ZEPHWD | Wind | WIND | WIND | FALSE | 3.5
OASIS_6_AR4SR3 |  | PHOTO VOLTAIC | SUN | FALSE | 1.5
OASIS_6_GBDSR4 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 3
OASIS_6_SOLAR1 | Solar_2Axis | PHOTO VOLTAIC | SUN | FALSE | 1.5
OASIS_6_SOLAR2 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
OASIS_6_SOLAR3 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 3
OBERON_5_O1BBX2 | Paired_BattStorage | OTHER | LESR | TRUE | 125
OBERON_5_O1SSR3 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 100
OBERON_5_O1SSX2 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 150
OBERON_5_O2BBX2 | Paired_BattStorage | OTHER | LESR | TRUE | 125
OBERON_5_O2SSR4 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 125
OBERON_5_O2SSR5 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 125
OCTILO_5_WIND | Wind | WIND | WIND | FALSE | 265
OGROVE_6_PL1X2 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 96
OILFLD_7_QFUNTS | Hydro | HYDRO | WATER | FALSE | 3.8
OLDRIV_6_BIOGAS | Biogas | RECIPROCATING ENGINE | BIOGAS | FALSE | 2
OLDRIV_6_CESDBM | Biogas | RECIPROCATING ENGINE | BIOGAS | FALSE | 1
OLDRIV_6_LKVBM1 | Biogas | RECIPROCATING ENGINE | BIOGAS | FALSE | 1
OLDRV1_6_SOLAR | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 20
OLINDA_2_COYCRK | Hydro | HYDRO | WATER | TRUE | 3.13
OLINDA_2_LNDFL2 | Biogas | COMBINED CYCLE | BIOGAS | FALSE | 28.1
OLINDA_7_BLKSND | Biomass/Wood | COMBUSTION TURBINE | WASTE TO POWER | FALSE | 5.6
OLIVEP_1_SOLAR | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 20
OLIVEP_1_SOLAR2 | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 19.75
OLSEN_2_UNIT | Hydro | HYDRO | WATER | FALSE | 5.5
OMAR_2_UNIT 1 | Peaker | FTUR | NATURAL GAS | TRUE | 75
OMAR_2_UNIT 2 | Peaker | FTUR | NATURAL GAS | TRUE | 75
OMAR_2_UNIT 3 | Peaker | FTUR | NATURAL GAS | TRUE | 75
OMAR_2_UNIT 4 | CHP | FTUR | NATURAL GAS | TRUE | 75
ONLLPP_6_UNITS | Pump |  | WATER | FALSE | 25.2
ORLND_6_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 1.5
OROLOM_1_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 10
OROLOM_1_SOLAR2 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 10
OROVIL_6_UNIT | CHP | RECIPROCATING ENGINE | NATURAL GAS | TRUE | 7.5
ORTGA_6_ME1SL1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 3
OSO_6_NSPIN | Pump | PUMP | WATER | TRUE | 70
OTAY_6_PL1X2 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 39.57
OTMESA_2_PL1X3 | CCGT | COMBINED CYCLE | NATURAL GAS | TRUE | 603.68
OXBOW_6_DRUM | Hydro | HYDRO | WATER | FALSE | 5.8
OXMTN_6_LNDFIL | Biogas | RECIPROCATING ENGINE | BIOGAS | FALSE | 10.62
PACLUM_6_UNIT | Biomass/Wood | STEAM | BIOMASS | FALSE | 28.8
PADUA_2_ONTARO | Hydro | HYDRO | WATER | FALSE | 1.92
PADUA_2_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 1.75
PADUA_6_MWDSDM | Hydro | HYDRO | WATER | TRUE | 9.9
PADUA_6_QF | Hydro | OTHER | OTHER | FALSE | 0.87
PADUA_7_SDIMAS | Hydro | HYDRO | WATER | TRUE | 1.05
PAIGES_6_SOLAR | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
PALA_6_PGCBT1 | Battery Storage | OTHER | LESR | TRUE | 10
PALOMR_2_PL1X3 | CCGT | COMBINED CYCLE | NATURAL GAS | TRUE | 588.21
PALSEL_6_PLSBT1 | Paired_BattStorage | OTHER | LESR | TRUE | 15
PALSEL_6_PLSSR1 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | TRUE | 20
PANERO_2_MWPWD1 | Wind | WIND | WIND | FALSE | 30
PARDEB_6_UNITS | Hydro | HYDRO | WATER | TRUE | 30
PARDSE_6_PESBT1 | Battery Storage | OTHER | LESR | TRUE | 10
PBLOSM_2_SOLAR | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 9.5
PEABDY_2_LNDFIL | Biogas | RECIPROCATING ENGINE | BIOGAS | FALSE | 1.6
PEABDY_2_LNDFL1 | Biogas | RECIPROCATING ENGINE | BIOGAS | FALSE | 8
PEARBL_2_NSPIN | Pump | PUMP | WATER | TRUE | 118
PEASE_1_TBEBT1 | Battery Storage | OTHER | LESR | TRUE | 5
PEORIA_1_SOLAR | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 1.5
PERGRN_2_PRSBT1 | Battery Storage | OTHER | LESR | TRUE | 200
PHOENX_1_UNIT | Hydro | HYDRO | WATER | FALSE | 2
PINFLT_7_UNITS | Hydro | HYDRO | WATER | TRUE | 198.51
PIOPIC_2_CTG1 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 111.3
PIOPIC_2_CTG2 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 112.7
PIOPIC_2_CTG3 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 112
PIT1_6_FRIVRA | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 1.5
PIT1_7_UNIT 1 | Hydro | HYDRO | WATER | TRUE | 32
PIT1_7_UNIT 2 | Hydro | HYDRO | WATER | TRUE | 32
PIT3_7_PL1X3 | Hydro | HYDRO | WATER | TRUE | 70.6
PIT4_7_PL1X2 | Hydro | HYDRO | WATER | TRUE | 95
PIT5_7_PL1X2 | Hydro | HYDRO | WATER | TRUE | 82
PIT5_7_PL3X4 | Hydro | HYDRO | WATER | TRUE | 82
PIT5_7_QFUNTS | Hydro | HYDRO | WATER | FALSE | 1.1
PIT6_7_UNIT 1 | Hydro | HYDRO | WATER | TRUE | 39
PIT6_7_UNIT 2 | Hydro | HYDRO | WATER | TRUE | 40
PIT7_7_UNIT 1 | Hydro | HYDRO | WATER | TRUE | 55.7
PIT7_7_UNIT 2 | Hydro | HYDRO | WATER | TRUE | 54.6
PIUTE_6_GNBSR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 3
PLACVL_1_CHILIB | Hydro | HYDRO | WATER | FALSE | 8.34
PLACVL_1_RCKCRE | Hydro | HYDRO | WATER | FALSE | 5
PLAINV_6_BSOLAR | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 20
PLAINV_6_DSOLAR | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 10
PLAINV_6_NLRSR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
PLAINV_6_SOLAR3 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
PLAINV_6_SOLARC | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
PLMSSR_6_HISIER | CHP | RECIPROCATING ENGINE | NATURAL GAS | TRUE | 6
PLSNTG_7_LNCLND | Biogas | RECIPROCATING ENGINE | BIOGAS | FALSE | 4.98
PMDLET_6_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 10
PMPJCK_1_RB2SLR | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
PMPJCK_1_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
PMPJCK_1_SOLAR2 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
PNCHEG_2_PL1X4 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 417
PNCHPP_1_PL1X2 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 119.91
PNCHVS_2_SOLAR | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 140
PNOCHE_1_PL1X2 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 49.97
PNOCHE_1_UNITA1 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 52.3
POEPH_7_UNIT 1 | Hydro | HYDRO | WATER | TRUE | 68
POEPH_7_UNIT 2 | Hydro | HYDRO | WATER | TRUE | 68.5
POLRIS_2_ASEBT1 | Paired_BattStorage | OTHER | LESR | TRUE | 28
POLRIS_2_ASESR1 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 56
POLRIS_2_ASRBT1 | Paired_BattStorage | OTHER | LESR | TRUE | 80
POLRIS_2_ASRSR1 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 125
PRCTVY_1_MIGBT1 | Battery Storage | OTHER | LESR | FALSE | 2
PRIMM_2_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 250
PRIMM_2_SSSBT1 | Paired_BattStorage | OTHER | LESR | TRUE | 200
PROXSR_2_PROSR1 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 120
PROXSR_2_PS1BT1 | Paired_BattStorage | OTHER | LESR | TRUE | 40
PROXSR_2_PS1BT2 | Paired_BattStorage | OTHER | LESR | TRUE | 32
PROXSR_2_PS1SR2 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 69.74
PROXSR_2_PS2BT3 | Paired_BattStorage | OTHER | LESR | TRUE | 90
PSWEET_1_STCRUZ | Biogas | RECIPROCATING ENGINE | BIOGAS | TRUE | 1.6
PUTHCR_1_PCNSB1 | Hybrid_BattStorage | OTHER | HYBD | TRUE | 3
PUTHCR_1_PCNSB1_SUN | Hybrid_Solar_1Axis | OTHER | HYBD | TRUE | 3
PUTHCR_1_SOLAR1 | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 1.98
PWEST_1_UNIT | Wind | WIND | WIND | FALSE | 2.1
RATSKE_2_NROSR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 150
RATSKE_2_RBSSB1 | Hybrid_BattStorage | OTHER | HYBD | TRUE | 7.5
RATSKE_2_RBSSB1_SUN | Hybrid_Solar_1Axis | OTHER | HYBD | TRUE | 60
RATSKE_2_RBSSB2 | Hybrid_BattStorage | OTHER | HYBD | TRUE | 5
RATSKE_2_RBSSB2_SUN | Hybrid_Solar_1Axis | OTHER | HYBD | TRUE | 40
RATSKE_2_WAVBT1 | Battery Storage | OTHER | LESR | TRUE | 125.96
RCKCRK_7_UNIT 1 | Hydro | HYDRO | WATER | TRUE | 57
RCKCRK_7_UNIT 2 | Hydro | HYDRO | WATER | TRUE | 56.9
RDWAY_1_CREST | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 4.5
RDWAY_1_SCKSR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 3
RDWAY_1_WA2SR3 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 0.5
RECTOR_2_CREST | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 10.5
RECTOR_2_IVANPV | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 3.5
RECTOR_2_KAWEAH | Hydro | HYDRO | WATER | FALSE | 6.55
RECTOR_2_KAWH 1 | Hydro | HYDRO | WATER | FALSE | 2.25
RECTOR_2_QF | Hydro | HYDRO | WATER | TRUE | 20.09
RECTOR_2_TFDBM1 | Biogas | RECIPROCATING ENGINE | BIOGAS | FALSE | 0.8
RECTOR_2_VISSR1 |  | PHOTO VOLTAIC | SUN | FALSE | 3
RECTOR_7_TULARE | Biomass/Wood | RECIPROCATING ENGINE | BIOMASS | FALSE | 1.5
REDBLF_6_UNIT | Reciprocating Engine | RECIPROCATING ENGINE | NATURAL GAS | TRUE | 44
REDMAN_2_SOLAR | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 3.75
REDMAN_6_AVSSR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 3
REEDLY_6_SOLAR | Solar_2Axis | PHOTO VOLTAIC | SUN | FALSE | 1.23
RENWD_1_QF | Wind | WIND | WIND | FALSE | 10.5
REXFRD_2_RSFBX2 | Paired_BattStorage | OTHER | LESR | TRUE | 240
REXFRD_2_RSFSX2 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 300
RICHMN_1_CHVSR2 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 8.5
RICHMN_1_SOLAR | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 2
RICHMN_7_BAYENV | Biogas | RECIPROCATING ENGINE | BIOGAS | FALSE | 2.5
RIOBRV_6_UNIT 1 | Hydro | HYDRO | WATER | FALSE | 14
RIOOSO_1_QF | Hydro | HYDRO | WATER | FALSE | 1.11
RNDMTN_2_SLSPHY1 | Hydro | HYDRO | WATER | FALSE | 0.6
RNDSBG_1_HZASR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 2.99
ROLLIN_6_UNIT | Hydro | HYDRO | WATER | TRUE | 13.5
ROMOLA_5_MPBBT1 | Battery Storage | OTHER | LESR | TRUE | 230
ROMOLA_5_MPBBT2 | Battery Storage | OTHER | LESR | TRUE | 230
ROMOLA_5_MPBBT3 | Battery Storage | OTHER | LESR | TRUE | 50
ROMOLA_5_MPBBT4 | Battery Storage | OTHER | LESR | TRUE | 110
ROSMDW_2_WIND1 | Wind | WIND | WIND | FALSE | 140
ROSMND_6_SOLAR | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 3
RSMSLR_6_SOLAR1 | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 20
RSMSLR_6_SOLAR2 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
RTEDDY_2_RWSBT1 | Paired_BattStorage | OTHER | LESR | TRUE | 30
RTEDDY_2_RWSBT2 | Paired_BattStorage | OTHER | LESR | TRUE | 30
RTEDDY_2_RWSBT3 | Paired_BattStorage | OTHER | LESR | TRUE | 45
RTEDDY_2_RWSBT4 | Paired_BattStorage | OTHER | LESR | TRUE | 30
RTEDDY_2_RWSBT5 | Paired_BattStorage | OTHER | LESR | TRUE | 12
RTEDDY_2_SC1SR3 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 40
RTEDDY_2_SEBSR3 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 56
RTEDDY_2_SEBSR4 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 56
RTEDDY_2_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 54
RTEDDY_2_SOLAR2 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 54
RTEDDY_2_SPASR4 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 26
RTEDDY_2_SRXSR4 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 13.6
RTREE_2_WIND1 | Wind | WIND | WIND | FALSE | 79.2
RTREE_2_WIND2 | Wind | WIND | WIND | FALSE | 19.8
RTREE_2_WIND3 | Wind | WIND | WIND | FALSE | 99
RUSCTY_2_UNITS | CCGT | COMBINED CYCLE | NATURAL GAS | TRUE | 615.18
RUSSELL_2_SOLANO1 | Wind | WIND | WIND | FALSE | 229.98
RVRVEW_1_UNITA1 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 48.7
RVSIDE_2_RERCU3 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 49
RVSIDE_2_RERCU4 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 49
RVSIDE_6_RERCU1 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 48.35
RVSIDE_6_RERCU2 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 48.5
RVSIDE_6_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 7.5
RVSIDE_6_SPRING | Peaker | FTUR | NATURAL GAS | TRUE | 36
S_RITA_6_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 1.5
SALIRV_2_UNIT | CHP | FTUR | NATURAL GAS | TRUE | 39
SALTSP_7_UNITS | Hydro | HYDRO | WATER | TRUE | 46
SANBRN_2_EESSB2 | Hybrid_BattStorage | OTHER | HYBD | TRUE | 85
SANBRN_2_EESSB2_SUN | Hybrid_Solar_1Axis | OTHER | HYBD | TRUE | 130
SANBRN_2_ES1BT3 | Hybrid_BattStorage | OTHER | HYBD | TRUE | 22
SANBRN_2_ES1BT3_SUN | Hybrid_Solar_1Axis | OTHER | HYBD | TRUE | 40
SANBRN_2_ES2SB3 | Hybrid_BattStorage | OTHER | HYBD | TRUE | 18
SANBRN_2_ES2SB3_SUN | Hybrid_Solar_1Axis | OTHER | HYBD | TRUE | 33
SANBRN_2_ESABT1 | Battery Storage | OTHER | LESR | TRUE | 100
SANBRN_2_ESBBT1 | Battery Storage | OTHER | LESR | TRUE | 100
SANBRN_2_SS2BT3 | Battery Storage | OTHER | LESR | TRUE | 169
SANBRN_2_SS2BT4 | Battery Storage | OTHER | LESR | TRUE | 47
SANBRN_2_SS2SB4 | Hybrid_BattStorage | OTHER | HYBD | TRUE | 18
SANBRN_2_SS2SB4_SUN | Hybrid_Solar_1Axis | OTHER | HYBD | TRUE | 36
SANDLT_2_SUNITS | Solar_Thermal | STEAM | SUN | FALSE | 275
SANDRN_2_SS1SR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 100
SANDRN_2_SS2SR2 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 200
SANITR_6_UNITS | CCGT | COMBINED CYCLE | NATURAL GAS | FALSE | 8
SANLOB_1_LNDFIL | Biogas | RECIPROCATING ENGINE | BIOGAS | FALSE | 1.5
SANLOB_1_OSFBM1 | Biogas | RECIPROCATING ENGINE | BIOGAS | TRUE | 0.85
SANTFG_7_UNITS | Geothermal | STEAM | GEOTHERMAL | TRUE | 72
SANTGO_2_LNDFL1 | Biogas | RECIPROCATING ENGINE | BIOGAS | FALSE | 19.6
SANWD_1_QF | Wind | WIND | WIND | FALSE | 31
SAUGUS_2_SPESBT1 | Battery Storage | OTHER | LESR | TRUE | 30
SAUGUS_6_CREST | Hydro | HYDRO | WATER | FALSE | 1
SAUGUS_6_MWDFTH | Hydro | HYDRO | WATER | TRUE | 9.1
SAUGUS_6_QF | CHP | OTHER | OTHER | FALSE | 2.19
SAUGUS_7_CHIQCN | Biogas | COMBUSTION TURBINE | BIOGAS | FALSE | 8
SBERDO_2_PSP3 | CCGT | COMBINED CYCLE | NATURAL GAS | TRUE | 555
SBERDO_2_PSP4 | CCGT | COMBINED CYCLE | NATURAL GAS | TRUE | 555
SBERDO_2_SNTANA | Hydro | HYDRO | WATER | FALSE | 6.95
SBERDO_6_MILLCK | Hydro | HYDRO | WATER | FALSE | 3.93
SCARLT_2_SS2BT1 | Paired_BattStorage | OTHER | LESR | TRUE | 150
SCARLT_2_SS2SR1 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 200
SCARLT_2_SSABT1 | Paired_BattStorage | OTHER | LESR | TRUE | 10
SCARLT_2_SSASR1 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 100
SCARLT_2_SSBBT1 | Paired_BattStorage | OTHER | LESR | TRUE | 30
SCARLT_2_SSBSR1 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 100
SCHLTE_1_PL1X3 | CCGT | COMBINED CYCLE | NATURAL GAS | TRUE | 336.04
SCHNDR_1_FIVPTS | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 15
SCHNDR_1_WSTSDE | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 15
SEARLS_1_TS3SR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 2
SEARLS_7_ARGUS | CHP |  | OTHER | FALSE | 19
SEAWND_2_AMWWD1 | Wind | WIND | WIND | FALSE | 27
SEGS_1_SR2SL2 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
SENTNL_2_CTG1 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 107.68
SENTNL_2_CTG2 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 104.19
SENTNL_2_CTG3 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 105.69
SENTNL_2_CTG4 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 106.55
SENTNL_2_CTG5 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 107.52
SENTNL_2_CTG6 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 105
SENTNL_2_CTG7 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 106.73
SENTNL_2_CTG8 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 106.85
SGREGY_6_SANGER | CCGT | COMBINED CYCLE | NATURAL GAS | TRUE | 48.3
SHAFTR_1_HWYSR1 | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 2.25
SHELRF_1_UNITS | CCGT | COMBINED CYCLE | NATURAL GAS | FALSE | 100
SHUTLE_6_RUISR1 |  | PHOTO VOLTAIC | SUN | FALSE | 1.5
SIERRA_1_UNITS | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 52.43
SISPRG_2_DS3BT1 | Paired_BattStorage | OTHER | LESR | TRUE | 61.5
SISPRG_2_DS3BT2 | Paired_BattStorage | OTHER | LESR | TRUE | 60
SISPRG_2_DS3BT3 | Paired_BattStorage | OTHER | LESR | TRUE | 12.5
SISPRG_2_DS3BT4 | Paired_BattStorage | OTHER | LESR | TRUE | 15
SISPRG_2_DS3SR1 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 123
SISPRG_2_DS3SR2 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 110
SISPRG_2_DS3SR3 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 50
SISPRG_2_DS3SR4 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 17
SISQUC_1_SMARIA | Biogas | RECIPROCATING ENGINE | BIOGAS | FALSE | 1.42
SKERN_6_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
SKERN_6_SOLAR2 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 10
SLATE_2_SLASR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 50.5
SLATE_2_SLASR2 | Hybrid_BattStorage | OTHER | HYBD | TRUE | 46.5
SLATE_2_SLASR2_SUN | Hybrid_Solar_1Axis | OTHER | HYBD | TRUE | 93
SLATE_2_SLASR3 | Hybrid_BattStorage | OTHER | HYBD | TRUE | 33.75
SLATE_2_SLASR3_SUN | Hybrid_Solar_Fixed | OTHER | HYBD | TRUE | 67.5
SLATE_2_SLASR4 | Hybrid_BattStorage | OTHER | HYBD | TRUE | 50
SLATE_2_SLASR4_SUN | Hybrid_Solar_1Axis | OTHER | HYBD | TRUE | 63
SLATE_2_SLASR5 | Hybrid_BattStorage | OTHER | HYBD | TRUE | 10
SLATE_2_SLASR5_SUN | Hybrid_Solar_1Axis | OTHER | HYBD | TRUE | 26
SLRMS3_2_SRMSR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 250
SLST13_2_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 107.6
SLSTR1_2_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 310
SLSTR2_2_SOLAR2 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 276
SLUISP_2_UNITS | Pump | PUMPED STORAGE | WATER | FALSE | 374.43
SLYCRK_1_UNIT 1 | Hydro | HYDRO | WATER | TRUE | 13
SMPRIP_1_SMPSON | CHP | COMBUSTION TURBINE | NATURAL GAS | TRUE | 46.05
SMRCOS_6_LNDFIL | Biogas | RECIPROCATING ENGINE | BIOGAS | FALSE | 1.5
SMUDGO_7_UNIT 1 | Geothermal | STEAM | GEOTHERMAL | TRUE | 64.8
SMYRNA_1_DL1SR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 1
SNCLRA_2_HOWLNG | CHP | RECIPROCATING ENGINE | NATURAL GAS | FALSE | 12.71
SNCLRA_2_SILBT1 | Battery Storage | OTHER | LESR | TRUE | 11
SNCLRA_2_SPRHYD | Hydro | HYDRO | WATER | FALSE | 1
SNCLRA_2_UNIT | CHP | COMBINED CYCLE | NATURAL GAS | TRUE | 27.5
SNCLRA_2_UNIT1 | CHP | FTUR | NATURAL GAS | TRUE | 27.8
SNCLRA_2_VESBT1 | Battery Storage | OTHER | LESR | TRUE | 100
SNCLRA_6_OXGEN | CHP | COMBUSTION TURBINE | NATURAL GAS | TRUE | 47.7
SNCLRA_6_PROCGN | CHP | FTUR | NATURAL GAS | FALSE | 47.9
SNCLRA_6_QF | CHP | OTHER | OTHER | FALSE | 1.65
SNDBAR_7_UNIT 1 | Hydro | HYDRO | WATER | FALSE | 16.2
SNMALF_6_UNITS | Biogas | RECIPROCATING ENGINE | BIOGAS | FALSE | 5
SOLBLU_2_WSBBX2 | Paired_BattStorage | OTHER | LESR | TRUE | 225
SOLBLU_2_WSBSX2 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 250
SOUTH_2_UNIT | Hydro | HYDRO | WATER | FALSE | 7.1
SPAULD_6_UNIT 3 | Hydro | HYDRO | WATER | FALSE | 6.5
SPAULD_6_UNIT12 | Hydro | HYDRO | WATER | TRUE | 11.4
SPBURN_2_UNIT 1 | Biomass/Wood | STEAM | BIOMASS | FALSE | 22
SPBURN_7_SNOWMT | Hydro | HYDRO | WATER | FALSE | 3
SPI LI_2_UNIT 1 | Biomass/Wood | STEAM | BIOMASS | FALSE | 17.2
SPIAND_1_ANDSN2 | Biomass/Wood | STEAM | BIOMASS | FALSE | 27.15
SPICER_1_UNITS | Hydro | HYDRO | WATER | TRUE | 6
SPIFBD_1_PL1X2 | Biomass/Wood | STEAM | BIOMASS | FALSE | 7.5
SPQUIN_6_SRPCQU | Biomass/Wood | STEAM | BIOMASS | FALSE | 24
SPRGAP_1_UNIT 1 | Hydro | HYDRO | WATER | FALSE | 7
SPRGVL_2_CREST | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 3
SPRGVL_2_EXETPV | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 3.5
SPRGVL_2_LINDPV | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 4
SPRGVL_2_PORTPV | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 3.5
SPRGVL_2_SUCCES | Hydro | HYDRO | WATER | TRUE | 1.4
SPRGVL_2_TULESC | Hydro | HYDRO | WATER | FALSE | 2.5
SRINTL_6_UNIT | CHP | COMBUSTION TURBINE | NATURAL GAS | FALSE | 6.9
STANIS_7_UNIT 1 | Hydro | HYDRO | WATER | TRUE | 91
STANTN_2_SBEBX2 | Battery Storage | OTHER | LESR | TRUE | 68.8
STANTN_2_STAGT1 | Peaker | OTHER | NATURAL GAS | TRUE | 49.65
STANTN_2_STAGT2 | Peaker | OTHER | NATURAL GAS | TRUE | 49.65
STIGCT_2_LODI | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 49.9
STOILS_1_UNITS | CHP | COMBINED CYCLE | NATURAL GAS | FALSE | 56.2
STOREY_2_MDRCH2 | Hydro | HYDRO | WATER | FALSE | 0.56
STOREY_2_MDRCH3 | Hydro | HYDRO | WATER | FALSE | 0.42
STOREY_2_MDRCH4 | Hydro | HYDRO | WATER | FALSE | 0.92
STOREY_7_MDRCHW | Hydro | HYDRO | WATER | FALSE | 1.84
STRAUS_1_STRWD1 | Wind | WIND | WIND | FALSE | 95.25
STROUD_6_SOLAR | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 20
STROUD_6_WWHSR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 1.5
SUMWHT_6_SWSSR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 18.5
SUNCAT_2_A1ABT1 | Paired_BattStorage | OTHER | LESR | TRUE | 47
SUNCAT_2_A1BBT1 | Paired_BattStorage | OTHER | LESR | TRUE | 63
SUNCAT_2_A2ABT2 | Paired_BattStorage | OTHER | LESR | TRUE | 132
SUNCAT_2_A2BSR2 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 133
SUNRIS_2_PL1X3 | CCGT | COMBINED CYCLE | NATURAL GAS | TRUE | 586.02
SUNSET_2_UNITS | CHP | FTUR | NATURAL GAS | TRUE | 248
SUNSHN_2_LNDFL | Biogas | COMBUSTION TURBINE | BIOGAS | FALSE | 20
SUNSLR_1_SSVSR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 100
SUNSPT_2_WNASR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
SUNST2_5_SS2SR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 150
SYCAMR_2_UNIT 1 | CHP | FTUR | NATURAL GAS | TRUE | 74
SYCAMR_2_UNIT 2 | Peaker | FTUR | NATURAL GAS | TRUE | 76
SYCAMR_2_UNIT 3 | CHP | FTUR | NATURAL GAS | TRUE | 74
SYCAMR_2_UNIT 4 | Peaker | FTUR | NATURAL GAS | TRUE | 76
TAHOE_2_THOBT1 | Battery Storage | OTHER | LESR | TRUE | 60.04
TAHOE_2_THOBT2 | Battery Storage | OTHER | LESR | TRUE | 109.06
TAHOE_2_THOBT3 | Battery Storage | OTHER | LESR | TRUE | 110.1
TANHIL_6_SOLART | CHP | FTUR | NATURAL GAS | FALSE | 17
TBLMTN_6_QF | Hydro | HYDRO | WATER | FALSE | 1.7
TEHAPI_2_PW1WD1 | Wind | WIND | WIND | FALSE | 47.49
TEHAPI_2_PW2WD2 | Wind | WIND | WIND | FALSE | 14.4
TEHAPI_2_WIND1 | Wind | WIND | WIND | FALSE | 19.85
TEHAPI_2_WIND2 | Wind | WIND | WIND | FALSE | 23.66
TENGEN_2_PL1X2 | CHP | COMBUSTION TURBINE | NATURAL GAS | TRUE | 37.7
TERMEX_2_PL1X3 | CCGT | COMBINED CYCLE | NATURAL GAS | TRUE | 625
TESLA_1_QF | CHP | OTHER | OTHER | FALSE | 2
TIDWTR_2_UNITS | CHP | FTUR | NATURAL GAS | FALSE | 114.8
TIFFNY_1_DILLON | Wind | WIND | WIND | FALSE | 45
TIGRCK_7_UNITS | Hydro | HYDRO | WATER | TRUE | 62
TKOPWR_6_HYDRO | Hydro | HYDRO | WATER | FALSE | 2.83
TMPLTN_2_SOLAR | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 1.5
TOADTW_6_UNIT | Hydro | HYDRO | WATER | FALSE | 1.5
TOPAZ_2_SOLAR | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 550
TORTLA_1_SOLAR | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
TRNQL8_2_AMASR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
TRNQL8_2_AZUSR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
TRNQL8_2_ROJSR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 100
TRNQL8_2_VERSR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 60
TRNQLT_2_RETBT1 | Paired_BattStorage | OTHER | LESR | TRUE | 72
TRNQLT_2_SOLAR | Paired_Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 200
TRNSWD_1_QF | Wind | WIND | WIND | FALSE | 38.97
TULARE_2_TULBM1 | Biogas | OTHER | BIOGAS | FALSE | 2.8
TULEWD_1_TULWD1 | Wind | WIND | WIND | FALSE | 130.5
TULLCK_7_UNITS | Hydro |  | WATER | FALSE | 25.9
TUMBWD_2_WISBT3 | Battery Storage | OTHER | LESR | TRUE | 50
TUMBWD_2_WISBT4 | Battery Storage | OTHER | LESR | TRUE | 74.97
TUPMAN_1_BIOGAS | Biogas | RECIPROCATING ENGINE | BIOGAS | FALSE | 0.6
TVYVLY_6_KRSHY1 | Hydro | HYDRO | WATER | TRUE | 1.3
TWISSL_6_SOLAR | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 1.5
TWISSL_6_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
TX-ELK_6_ECKSR2 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 3
TX-ELK_6_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 1.5
TXMCKT_6_UNIT | CHP | FTUR | NATURAL GAS | FALSE | 11.2
UKIAH_7_LAKEMN | Hydro | HYDRO | WATER | TRUE | 3.5
ULTPCH_1_UNIT 1 | Biomass/Wood | STEAM | BIOMASS | FALSE | 18
ULTPFR_1_UNIT 1 | Biomass/Wood | STEAM | BIOMASS | FALSE | 24.3
ULTRCK_2_UNIT | Biomass/Wood | STEAM | BIOMASS | FALSE | 24.4
UNOCAL_1_UNITS | CHP | FTUR | NATURAL GAS | FALSE | 49.85
UNVRSY_1_UNIT 1 | CHP | FTUR | NATURAL GAS | FALSE | 38
USWND2_1_WIND1 | Wind | WIND | WIND | FALSE | 42.96
USWND2_1_WIND2 | Wind | WIND | WIND | FALSE | 42.96
USWND2_1_WIND3 | Wind | WIND | WIND | FALSE | 46
USWND4_2_UNIT2 | Biogas | COMBUSTION TURBINE | BIOGAS | TRUE | 7.4
USWNDR_2_LABWD1 | Wind | WIND | WIND | FALSE | 9
USWPFK_6_FRICK | Wind | WIND | WIND | FALSE | 10
USWPJR_2_UNITS | Wind | WIND | WIND | FALSE | 78.2
VACADX_1_SOLAR | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 2.5
VACADX_1_UNITA1 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 51.91
VALLEY_5_PERRIS | Hydro | HYDRO | WATER | TRUE | 7.94
VALLEY_5_REDMTN | Hydro | HYDRO | WATER | FALSE | 5.9
VALLEY_5_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 1.49
VALLEY_5_SOLAR2 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
VALTNE_2_AVASR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 100
VEAVST_1_SOLAR | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 14.4
VEDDER_1_SEKERN | CHP | FTUR | NATURAL GAS | FALSE | 34.47
VEGA_6_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
VENWD_1_WIND3 | Wind | WIND | WIND | FALSE | 44.53
VERNON_6_GONZL1 | Peaker | FTUR | NATURAL GAS | TRUE | 5.75
VERNON_6_GONZL2 | Peaker | FTUR | NATURAL GAS | TRUE | 5.75
VERNON_6_MALBRG | CCGT | COMBINED CYCLE | NATURAL GAS | TRUE | 139
VESTAL_2_BTNBT1 | Battery Storage | OTHER | LESR | TRUE | 80
VESTAL_2_KERN | Hydro | HYDRO | WATER | FALSE | 36.8
VESTAL_2_RTS042 | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 5
VESTAL_2_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
VESTAL_2_SOLAR2 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 14
VESTAL_2_TS5SR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 55.83
VESTAL_2_UNIT1 | CHP | FTUR | NATURAL GAS | FALSE | 5
VESTAL_2_WELLHD | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 49
VESTAL_6_QF | Hydro | HYDRO | WATER | FALSE | 11.95
VICPAS_2_SLOBT1 | Paired_BattStorage | OTHER | LESR | TRUE | 15
VICPAS_2_SLOSR1 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 49.5
VICPAS_2_SOCBT1 | Paired_BattStorage | OTHER | LESR | TRUE | 50
VICPAS_2_SOCBT2 | Paired_BattStorage | OTHER | LESR | TRUE | 71
VICPAS_2_SOCSR1 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 100
VICPAS_2_SOCSR2 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 93.5
VICPAS_2_SOCSR3 |  | PHOTO VOLTAIC | SUN | FALSE | 20
VICPAS_2_VPSBT1 | Paired_BattStorage | OTHER | LESR | TRUE | 50
VICPAS_2_VPSSR1 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 200
VICTOR_1_CREST | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 11.99
VICTOR_1_EXSLRA | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 2
VICTOR_1_EXSLRB | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 2
VICTOR_1_LVSLR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 10
VICTOR_1_LVSLR2 | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 20
VICTOR_1_SLRHES | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 1.5
VICTOR_1_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 17.5
VICTOR_1_SOLAR2 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
VICTOR_1_SOLAR3 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 7
VICTOR_1_SOLAR4 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
VICTOR_1_VDRYFA | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 5
VICTOR_1_VDRYFB | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 5
VILLPK_2_VALLYV | Hydro | HYDRO | WATER | TRUE | 4.1
VILLPK_6_MWDYOR | Hydro | HYDRO | WATER | TRUE | 5.1
VISTA_6_QF | CHP | OTHER | OTHER | FALSE | 0.18
VISTRA_5_DALBT1 | Battery Storage | OTHER | LESR | TRUE | 100
VISTRA_5_DALBT2 | Battery Storage | OTHER | LESR | TRUE | 100
VISTRA_5_DALBT3 | Battery Storage | OTHER | LESR | TRUE | 100
VISTRA_5_DALBT4 | Battery Storage | OTHER | LESR | TRUE | 100
VISTRA_5_PLABT1 | Battery Storage | OTHER | LESR | TRUE | 100.4
VISTRA_5_PLABT2 | Battery Storage | OTHER | LESR | TRUE | 100.4
VISTRA_5_PLABT3 | Battery Storage | OTHER | LESR | TRUE | 74.6
VISTRA_5_PLABT4 | Battery Storage | OTHER | LESR | TRUE | 74.6
VLCNTR_6_VCEBT1 | Paired_BattStorage | OTHER | LESR | TRUE | 54
VLCNTR_6_VCEBT2 | Paired_BattStorage | OTHER | LESR | TRUE | 85
VLCNTR_6_VCSLR | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 2.33
VLCNTR_6_VCSLR1 | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 2.5
VLCNTR_6_VCSLR2 | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 5
VLYHOM_7_SSJID | Hydro | HYDRO | WATER | FALSE | 3
VOLTA_2_UNIT 1 | Hydro | HYDRO | WATER | FALSE | 9.1
VOLTA_2_UNIT 2 | Hydro | HYDRO | WATER | FALSE | 1
VOLTA_6_BAILCK | Hydro | HYDRO | WATER | FALSE | 0.63
VOLTA_7_PONHY1 | Hydro | HYDRO | WATER | FALSE | 1.25
VOLTA_7_QFUNTS | Hydro | HYDRO | WATER | FALSE | 0.15
VOYAGR_2_VOAWD5 | Wind | WIND | WIND | FALSE | 13.98
VOYAGR_2_VOYWD1 | Wind | WIND | WIND | FALSE | 128.91
VOYAGR_2_VOYWD2 | Wind | WIND | WIND | FALSE | 126.35
VOYAGR_2_VOYWD3 | Wind | WIND | WIND | FALSE | 42.45
VOYAGR_2_VOYWD4 | Wind | WIND | WIND | FALSE | 21.01
VSTAES_6_VESBT1 | Battery Storage | OTHER | LESR | TRUE | 32
WADHAM_6_UNIT | Biomass/Wood | STEAM | WASTE TO POWER | FALSE | 29.07
WALCRK_2_CTG1 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 100.1
WALCRK_2_CTG2 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 100.1
WALCRK_2_CTG3 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 100.1
WALCRK_2_CTG4 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 100.1
WALCRK_2_CTG5 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 100.1
WALNUT_2_SOLAR | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 1.5
WALNUT_6_HILLGEN | Biogas | OTHER | BIOGAS | FALSE | 47
WALNUT_7_WCOVST | Biogas | STEAM | BIOGAS | FALSE | 6.5
WARNE_2_UNIT | Hydro | HYDRO | WATER | TRUE | 76
WASCO_6_TERSR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 4.62
WAUKNA_1_SOLAR | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 20
WAUKNA_1_SOLAR2 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 19.75
WDFRDF_2_WFFBT1 | Battery Storage | OTHER | LESR | TRUE | 25
WDLEAF_7_UNIT 1 | Hydro | HYDRO | WATER | TRUE | 60
WEBER_6_FORWRD | Biogas | RECIPROCATING ENGINE | BIOGAS | FALSE | 4.2
WEEDPC_6_KNSSR1 | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 2.37
WESCAN_2_BDSBT1 | Battery Storage | OTHER | LESR | TRUE | 131
WESCN2_2_BDSBT1 | Battery Storage | OTHER | LESR | TRUE | 119
WESTPT_2_UNIT | Hydro | HYDRO | WATER | TRUE | 14
WFRESN_1_SOLAR | Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 1.5
WHEATL_6_LNDFIL | Biogas | RECIPROCATING ENGINE | BIOGAS | FALSE | 3.55
WHITNY_6_SOLAR | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
WHTWTR_1_WINDA1 | Wind | WIND | WIND | FALSE | 57
WILLMS_6_ARBBM1 |  | OTHER | BIOMASS | FALSE | 3
WISE_1_UNIT 1 | Hydro | HYDRO | WATER | TRUE | 14.5
WISE_1_UNIT 2 | Hydro | HYDRO | WATER | TRUE | 3.2
WISHON_6_UNITS | Hydro | HYDRO | WATER | TRUE | 18.4
WISTRA_2_WRSSR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 100
WLDWD_1_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 20
WLDWD_1_SOLAR2 | Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 15
WNDMAS_2_UNIT 1 | Wind | WIND | WIND | FALSE | 38
WNDSTR_2_WIND | Wind | WIND | WIND | FALSE | 120
WOLFSK_1_UNITA1 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 48.68
WOODWR_1_HYDRO | Hydro | HYDRO | WATER | FALSE | 7.3
WRGTSR_2_WSFSR1 | Hybrid_Solar_Fixed | PHOTO VOLTAIC | SUN | FALSE | 200
WSENGY_1_UNIT 1 | Biomass/Wood | STEAM | BIOMASS | FALSE | 50
WSTWND_2_M89BT2 | Paired_BattStorage | OTHER | LESR | TRUE | 70.6
WSTWND_2_M89WD2 | Wind | WIND | WIND | FALSE | 58.3
WSTWND_2_M90WD2 | Wind | WIND | WIND | FALSE | 64.82
WSTWND_2_SBSBT1 | Battery Storage | OTHER | LESR | TRUE | 80
WSTWND_2_SBSBT2 | Battery Storage | OTHER | LESR | TRUE | 40
WSTWND_2_SBSBT3 | Battery Storage | OTHER | LESR | TRUE | 59
YELPIN_2_YP2BT1 | Paired_BattStorage | OTHER | LESR | TRUE | 65
YELPIN_2_YP2BT2 | Paired_BattStorage | OTHER | LESR | TRUE | 28
YELPIN_2_YP2BT3 | Paired_BattStorage | OTHER | LESR | TRUE | 32
YELPIN_2_YP2SR1 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 125
YELPIN_2_YP2SR2 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 60
YELPIN_2_YP2SR3 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 65
YUBACT_1_SUNSWT | CHP | COMBUSTION TURBINE | NATURAL GAS | TRUE | 49.97
YUBACT_6_UNITA1 | Peaker | COMBUSTION TURBINE | NATURAL GAS | TRUE | 47.16
ZOND_6_UNIT | Wind | WIND | WIND | FALSE | 17.1
ALHMBR_1_ALHSLR | Solar_1Axis | PHOTO VOLTAIC | SUN |  | 50
ANZA_6_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN |  | 20
ARKANS_1_ARKSLR | Solar_1Axis | PHOTO VOLTAIC | SUN |  | 50
ARLINT_5_SCEDYN | CCGT | COMBINED CYCLE | NATURAL GAS |  | 565
ARLVAL_5_SOLAR | Solar_Fixed | PHOTO VOLTAIC | SUN |  | 127
BCTSYS_5_PWXDYN | Hydro |  | WATER |  | 428
BEJNLS_5_BV2SCEDYN | Wind | WIND | WIND |  | 167
BEKWJS_5_BV1SCEDYN | Wind | WIND | WIND |  | 130
CALPSS_6_SOLAR1 | Solar_1Axis | PHOTO VOLTAIC | SUN |  | 19.9
CLINESCO_3_PVDYN | Wind | WIND | WIND |  | 129.94
CLINESCO_3_WBDYN | Wind | WIND | WIND |  | 194.28
COLGNS_2_CNSSR1 | Solar_1Axis | PHOTO VOLTAIC | SUN |  | 74.8
DLN_5_HARQSCEDYN | Solar_1Axis | PHOTO VOLTAIC | SUN |  | 150
DURNMESA_3_WBDYN | Wind | WIND | WIND |  | 105.08
ELCABO_5_ECWSCEDYN | Wind | WIND | WIND |  | 298
GRADYW_5_GDYWD1 | Wind | WIND | WIND |  | 200
GRIFFI_2_LSPDYN | CCGT | COMBINED CYCLE | NATURAL GAS |  | 570
HOOV_2_ANAPT | Hydro | HYDRO | WATER |  | 40.39
HOOVER_2_MWDPT | Hydro | HYDRO | WATER |  | 249
HOOVER_2_SCEPT | Hydro | HYDRO | WATER |  | 287
HOOVER_2_VEAPT | Hydro | HYDRO | WATER |  | 16
INTMNT_3_ANAHEIM | Coal | STEAM | COAL |  | 234
INTMNT_3_PASADENA | Coal | STEAM | COAL |  | 107
INTMNT_3_RIVERSIDE | Coal | STEAM | COAL |  | 135
MAGNLA_6_ANAHEIM | CCGT | COMBINED CYCLE | NATURAL GAS |  | 115
MAGNLA_6_CERRITOS | CCGT | COMBINED CYCLE | NATURAL GAS |  | 12
MAGNLA_6_COLTON | CCGT | COMBINED CYCLE | NATURAL GAS |  | 12
MAGNLA_6_PASADENA | CCGT | COMBINED CYCLE | NATURAL GAS |  | 18
MALIN_5_BPADYN | Hydro |  | WATER |  | 700
MALIN_5_GCPDDYN | Hydro | HYDRO | WATER |  | 125
MALIN_5_HERMDYN | CCGT | COMBINED CYCLE | NATURAL GAS |  | 308
MALIN_5_IBERDR | Wind | WIND | WIND |  | 100
MALIN_5_INHRED | Wind | WIND | WIND |  | 50
MALIN_5_INHRPG | Wind | WIND | WIND |  | 50
MIDWY3_2_MDSSR1 | Solar_Fixed | PHOTO VOLTAIC | SUN |  | 20
MIDWYS_2_MIDSL1 | Solar_Fixed | PHOTO VOLTAIC | SUN |  | 49.9
MILFRD_7_PASADENA | Wind | WIND | WIND |  | 5
MSQUIT_5_SERDYN | CCGT | COMBINED CYCLE | NATURAL GAS |  | 625
NGILAA_5_SDGDYN | CCGT | COMBINED CYCLE | NATURAL GAS |  | 55
PVERDE_5_SCEDYN | Nuclear |  | URANIUM |  | 635
RAMON_2_SCEDYN | Geothermal | OTHER | GEOTHERMAL |  | 106.18
RANCHO_2_SMUDSYSDYN | CCGT | OTHER | OTHER |  | 124
SIGHEB_6_HE2SCEDYN | Geothermal | COMBUSTION TURBINE | GEOTHERMAL |  | 28
SIGHEB_6_MIRDYN | Geothermal | COMBUSTION TURBINE | GEOTHERMAL |  | 17
SNORA_2_SNRSLR | Solar_1Axis | PHOTO VOLTAIC | SUN |  | 50
SUNSTR_5_SS1SCEDYN | Solar_1Axis | PHOTO VOLTAIC | SUN |  | 150
SUTTER_2_CISO | CCGT | COMBINED CYCLE | NATURAL GAS |  | 275
TECOLOTE_3_WBDYN | Wind | WIND | WIND |  | 271.68
TITANS_2_TTSSR1 | Solar_1Axis | PHOTO VOLTAIC | SUN |  | 70
VIKING_2_VCSSR1 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN |  | 132.1
VIKING_2_VCBBT1 | Paired_BattStorage | OTHER | LESR |  | 149.88
WHITEH_2_MEADDYN1 | Wind | WIND | WIND |  | 50
WHITEH_2_MEADDYN2 | Wind | WIND | WIND |  | 300
WISTER_2_WISSR1 | Solar_1Axis | PHOTO VOLTAIC | SUN |  | 20
WSNR_2_CVPDYN | Hydro | HYDRO | WATER |  | 10
WSNR_2_TESLADYN | Hydro | HYDRO | WATER |  | 10
WSNR_5_TRCYDYN | Hydro | HYDRO | WATER |  | 10
TOWNSITE_2_MEADDYN | Hybrid_BattStorage | OTHER | HYBD |  | 90
TOWNSITE_2_MEADDYN_SUN | Hybrid_Solar_1Axis | OTHER | HYBD |  | 180
OCOTLO_6_OCWSB1 | Hybrid_BattStorage | OTHER | HYBD |  | 49.89
OCOTLO_6_OCWSB1_SUN | Hybrid_Solar_1Axis | OTHER | HYBD |  | 50
GWFPWR_1_LDCTG1 | CCGT | COMBUSTION TURBINE | NATURAL GAS | TRUE | 55.3
GWFPWR_1_LDCTG2 | CCGT | COMBUSTION TURBINE | NATURAL GAS | TRUE | 55.3
KOLA_2_KLBBT1 | Battery Storage | OTHER | LESR | TRUE | 275
KOLA_2_KLBBT2 | Battery Storage | OTHER | LESR | TRUE | 125
RSMNDS_2_CSRBT1 | Paired_BattStorage | OTHER | LESR | TRUE | 15
RSMNDS_2_CSRBT2 | Paired_BattStorage | OTHER | LESR | TRUE | 10
RSMNDS_2_CSRSR1 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 30
RSMNDS_2_CSRSR2 |  | PHOTO VOLTAIC | SUN | FALSE | 10
VALLEY_5_ORTBT1 | Battery Storage | OTHER | LESR | TRUE | 20
VALTNE_2_TSASR1 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 58
VALTNE_2_TSASR2 | Paired_Solar_1Axis | PHOTO VOLTAIC | SUN | FALSE | 70
VALTNE_2_TSBBT1 | Paired_BattStorage | OTHER | LESR | TRUE | 18
VALTNE_2_TSBBT2 | Paired_BattStorage | OTHER | LESR | TRUE | 22

## Commercial Operation Dates
CLASSIFICATION | RESOURCE ID | COMMERCIAL OPERATION DATE
Participating Unit | 7STDRD_1_SOLAR1 | 2015-06-04
Participating Unit | ACACIA_6_SOLAR | 2014-11-13
Participating Unit | ADERA_1_SOLAR1 | 2015-12-23
Participating Unit | ADLIN_1_UNITS | 2008-07-28
Participating Unit | ADMEST_6_SOLAR | 2014-12-13
Participating Unit | ADOBEE_1_SOLAR | 2014-05-21
Non-Participating | AGRICO_6_FEGBT1
Participating Unit | AGRICO_6_PL3N5 | 2006-08-30
Non-Participating | AGRICO_6_UNIT 3
Participating Unit | AGRICO_7_UNIT | 2023-03-14
Non-Participating | AGRICO_7_UNIT 4
Participating Unit | AGUCAL_5_SOLAR1 | 2014-06-10
Participating Unit | AKINGS_6_AMESR1 | 2020-12-05
Participating Unit | ALAMIT_2_AESBT2 | 2024-11-14
Participating Unit | ALAMIT_2_PL1X3 | 2020-02-06
Non-Participating | ALAMIT_7_CTG1A
Non-Participating | ALAMIT_7_CTG1B
Participating Unit | ALAMIT_7_ES1 | 2020-12-04
Non-Participating | ALAMIT_7_STG1S
Participating Unit | ALAMIT_7_UNIT 3 | 1961-01-01
Participating Unit | ALAMIT_7_UNIT 4 | 1962-01-01
Participating Unit | ALAMIT_7_UNIT 5 | 1999-01-01
Participating Unit | ALAMO_6_UNIT | 1986-01-01
Participating Unit | ALHMBR_1_ALHSLR | 2015-08-29
Participating Unit | ALLGNY_6_HYDRO1 | 2014-12-03
Participating Unit | ALMASL_2_AL6BT6 | 2022-06-27
Participating Unit | ALMASL_2_GS1SR1 | 2020-12-11
Participating Unit | ALMASL_2_GS4SR4 | 2020-12-11
Participating Unit | ALMASL_2_GS6SR6 | 2021-10-22
Participating Unit | ALMASL_2_GS7SR7 | 2021-12-22
Participating Unit | ALMEGT_1_UNIT 1 | 1986-01-01
Participating Unit | ALMEGT_1_UNIT 2 | 1986-01-01
Participating Unit | ALPAUG_1_TUDSR1 | 2024-10-28
Participating Unit | ALPSLR_1_NTHSLR | 2013-03-08
Participating Unit | ALPSLR_1_SPSSLR | 2013-03-08
Participating Unit | ALT6DN_2_WIND7 | 2013-01-01
Participating Unit | ALT6DS_2_WIND9 | 2013-01-01
Participating Unit | ALTA3A_2_CPCE4 | 2011-03-12
Participating Unit | ALTA3A_2_CPCE5 | 2011-04-21
Participating Unit | ALTA3A_2_CPCE8 | 2012-02-01
Participating Unit | ALTA4A_2_CPCW1 | 2010-12-29
Participating Unit | ALTA4B_2_CPCW2 | 2010-12-29
Participating Unit | ALTA4B_2_CPCW3 | 2011-02-12
Participating Unit | ALTA4B_2_CPCW6 | 2012-05-09
Participating Unit | ALTA6B_2_WIND11 | 2014-03-13
Participating Unit | ALTA6E_2_WIND10 | 2014-03-13
Participating Unit | ALTWD_2_AT3WD3 | 2021-06-24
Participating Unit | ALTWD_2_COAWD1 | 2021-04-13
Participating Unit | ANAHM_2_CANYN1 | 2011-09-16
Participating Unit | ANAHM_2_CANYN2 | 2011-09-16
Participating Unit | ANAHM_2_CANYN3 | 2011-07-30
Participating Unit | ANAHM_2_CANYN4 | 2011-07-30
Participating Unit | ANZA_6_SOLAR1 | 2015-12-30
Participating Unit | APLHIL_1_SFKHY1 | 2020-12-04
Participating Unit | AQUAWS_2_AQWSR1 | 2021-12-08
Non-Participating | AQUAWS_2_AQWSU1
Non-Participating | AQUAWS_2_AQWSU2
Participating Unit | ARBWD_6_QF | 2013-05-17
Participating Unit | ARCATA_6_FCPSB1
Participating Unit | ARCATA_6_FCPSB2
Participating Unit | ARCOGN_2_UNITS | 1987-12-04
Participating Unit | ARKANS_1_ARKSLR | 2015-08-29
Participating Unit | ARLEAF_2_NBSSB1
Participating Unit | ARLINT_5_SCEDYN | 2016-11-02
Participating Unit | ARLNTN_2_AR1SR1 | 2022-03-21
Participating Unit | ARLNTN_2_ASUSR1 | 2022-08-01
Participating Unit | ARLVAL_5_SOLAR | 2013-10-28
Participating Unit | ARVINN_6_ORION1 | 2014-06-26
Participating Unit | ARVINN_6_ORION2 | 2014-06-26
Participating Unit | ASTORA_2_SOLAR1 | 2016-10-18
Participating Unit | ASTORA_2_SOLAR2 | 2016-10-31
Non-Participating | ATHOS_5_AP1SR1
Non-Participating | ATHOS_5_AP1SR2
Participating Unit | ATHOS_5_AP1X2 | 2022-05-13
Non-Participating | ATHOS_5_AP2SR3
Non-Participating | ATHOS_5_AP2SR4
Participating Unit | ATHOS_5_AP2X2 | 2021-12-16
Participating Unit | ATLASC_5_ACAUXL
Participating Unit | ATLASC_5_ACBBT2
Participating Unit | ATLASC_5_ACBBT3
Participating Unit | ATLASC_5_ACBBT6
Participating Unit | ATWEL2_1_SOLAR1 | 2015-06-11
Participating Unit | ATWELL_1_SOLAR | 2013-03-08
Participating Unit | AVENAL_6_AVPARK | 2011-08-05
Participating Unit | AVENAL_6_AVSLR1 | 2017-01-28
Participating Unit | AVENAL_6_AVSLR2 | 2017-01-28
Participating Unit | AVENAL_6_SANDDG | 2011-08-05
Participating Unit | AVENAL_6_SUNCTY | 2011-08-05
Participating Unit | AVSOLR_2_SOLAR | 2014-06-19
Participating Unit | AZALEA_6_AZABT1
Participating Unit | AZALEA_6_AZASR1
Participating Unit | BAHIA_2_LKHSR1 | 2021-09-23
Participating Unit | BALCHS_7_UNIT 1 | 1927-01-01
Participating Unit | BALCHS_7_UNIT 2 | 1958-01-01
Participating Unit | BALCHS_7_UNIT 3 | 1958-01-01
Participating Unit | BANKPP_2_NSPIN | 2009-03-31
Participating Unit | BARRE_2_ALASB1 | 2023-11-10
Participating Unit | BARRE_2_QF | 1994-01-01
Participating Unit | BARRE_2_SBBBT1
Participating Unit | BARRE_2_SBBSR1
Participating Unit | BARRE_6_PEAKER | 2007-09-20
Participating Unit | BASICE_2_UNITS | 1989-03-14
Participating Unit | BCTSYS_5_PWXDYN | 2009-03-31
Participating Unit | BDGRCK_1_UNITS | 1991-04-01
Participating Unit | BEARDS_7_UNIT 1 | 1957-01-01
Participating Unit | BEARMT_1_UNIT | 1995-04-03
Participating Unit | BEJNLS_5_BV2SCEDYN | 2017-01-27
Participating Unit | BEKWJS_5_BV1SCEDYN | 2017-01-27
Participating Unit | BELDEN_7_UNIT 1 | 1969-01-01
Non-Participating | BELLEF_2_BSFBT1
Non-Participating | BELLEF_2_BSFBT2
Non-Participating | BELLEF_2_BSFBT3
Participating Unit | BELLEF_2_BSFBX3
Non-Participating | BELLEF_2_BSFSR1
Non-Participating | BELLEF_2_BSFSR2
Non-Participating | BELLEF_2_BSFSR3
Participating Unit | BELLEF_2_BSFSX3
Participating Unit | BERCYN_2_BCEBT1 | 2024-07-24
Non-Participating | BGCRK1_7_PORTAL
Non-Participating | BGCRK1_7_UNIT 1
Non-Participating | BGCRK1_7_UNIT 2
Non-Participating | BGCRK1_7_UNIT 3
Non-Participating | BGCRK1_7_UNIT 4
Non-Participating | BGCRK2_7_UNIT 1
Non-Participating | BGCRK2_7_UNIT 2
Non-Participating | BGCRK2_7_UNIT 3
Non-Participating | BGCRK2_7_UNIT 4
Non-Participating | BGCRK2_7_UNIT 5
Non-Participating | BGCRK2_7_UNIT 6
Non-Participating | BGCRK3_7_UNIT 1
Non-Participating | BGCRK3_7_UNIT 2
Non-Participating | BGCRK3_7_UNIT 3
Non-Participating | BGCRK3_7_UNIT 4
Non-Participating | BGCRK3_7_UNIT 5
Non-Participating | BGCRK4_7_UNIT 1
Non-Participating | BGCRK4_7_UNIT 2
Non-Participating | BGCRK8_7_UNIT 1
Non-Participating | BGCRK8_7_UNIT 2
Non-Participating | BGROCK_2_BRFBT1
Non-Participating | BGROCK_2_BRFBT2
Participating Unit | BGROCK_2_BRFBX2 | 2025-05-28
Participating Unit | BGSKYN_2_AS2SR1 | 2018-12-18
Participating Unit | BGSKYN_2_ASPSR2 | 2019-08-03
Participating Unit | BGSKYN_2_ASSR1B | 2022-11-23
Participating Unit | BGSKYN_2_ASSR3A | 2021-06-22
Participating Unit | BGSKYN_2_ASSR3B | 2021-06-22
Participating Unit | BGSKYN_2_BS3SR3 | 2019-09-14
Participating Unit | BIGCRK_2_EXESWD | 1913-01-01
Participating Unit | BIGCRK_7_DAM7 | 1986-01-01
Participating Unit | BIGCRK_7_MAMRES | 2009-03-31
Participating Unit | BIGSKY_2_AS2BT1 | 2022-09-02
Participating Unit | BIGSKY_2_ASLBT2 | 2022-07-30
Participating Unit | BIGSKY_2_BSKSR6 | 2017-12-08
Participating Unit | BIGSKY_2_BSKSR7 | 2017-12-08
Participating Unit | BIGSKY_2_BSKSR8 | 2017-12-08
Participating Unit | BIGSKY_2_SOLAR1 | 2016-08-19
Participating Unit | BIGSKY_2_SOLAR2 | 2016-12-03
Participating Unit | BIGSKY_2_SOLAR3 | 2016-07-25
Participating Unit | BIGSKY_2_SOLAR4 | 2016-12-03
Participating Unit | BIGSKY_2_SOLAR5 | 2016-11-30
Participating Unit | BIGSKY_2_SOLAR6 | 2016-12-17
Participating Unit | BIGSKY_2_SOLAR7 | 2016-12-15
Participating Unit | BIOMAS_1_UNIT 1 | 1989-08-31
Participating Unit | BISHOP_1_ALAMO | 1908-01-01
Participating Unit | BISHOP_1_UNITS | 1905-01-01
Participating Unit | BKRFLD_2_SOLAR1 | 2015-07-28
Participating Unit | BLACK_7_UNIT 1 | 1966-01-01
Participating Unit | BLACK_7_UNIT 2 | 1965-01-01
Participating Unit | BLAST_1_WIND | 2012-02-23
Participating Unit | BLCKBT_2_STONEY | 1988-01-01
Participating Unit | BLCKWL_6_BTFBT1
Participating Unit | BLCKWL_6_SOLAR1 | 2015-04-16
Non-Participating | BLKCRK_2_GMBT1A
Non-Participating | BLKCRK_2_GMBT1B
Participating Unit | BLKCRK_2_GMCBT1 | 2021-06-30
Participating Unit | BLKCRK_2_SOLAR1 | 2016-06-14
Non-Participating | BLKCRK_2_SOLR1A
Non-Participating | BLKCRK_2_SOLR1B
Participating Unit | BLKDIA_2_BDEBT1 | 2022-03-17
Non-Participating | BLM E_2_UNIT 7
Non-Participating | BLM E_2_UNIT 8
Participating Unit | BLM W_2_COSBT1 | 2022-02-28
Participating Unit | BLM W_2_MDRBT1 | 2025-04-29
Non-Participating | BLM W_2_UNIT 9
Participating Unit | BLM_2_UNITS | 1988-12-05
Participating Unit | BLVRDE_6_BLVBT1 | 2024-05-21
Participating Unit | BLYTHE_1_SOLAR1 | 2009-12-18
Participating Unit | BLYTHE_1_SOLAR2 | 2017-04-05
Participating Unit | BNNIEN_7_ALTAPH | 1902-01-01
Participating Unit | BOGUE_1_UNITA1 | 2002-12-23
Participating Unit | BORDER_6_LTMBT1
Participating Unit | BORDER_6_LTMCT1
Participating Unit | BORDER_6_UNITA1 | 2001-10-26
Participating Unit | BOWMN_6_HYDRO | 2016-12-20
Participating Unit | BRDGVL_7_BAKER | 1987-12-10
Participating Unit | BRDSLD_2_HIWIND | 2003-12-23
Participating Unit | BRDSLD_2_MTZUM2 | 2012-02-01
Participating Unit | BRDSLD_2_MTZUMA | 2011-01-25
Participating Unit | BRDSLD_2_SHILO1 | 2006-03-30
Participating Unit | BRDSLD_2_SHILO2 | 2009-01-27
Participating Unit | BRDSLD_2_SHLO3A | 2011-12-22
Participating Unit | BRDSLD_2_SHLO3B | 2012-12-07
Participating Unit | BREGGO_6_DEGRSL | 2013-02-13
Participating Unit | BREGGO_6_DSEBT1 | 2025-08-12
Participating Unit | BREGGO_6_SOLAR | 2013-02-12
Participating Unit | BRODIE_2_WIND | 2012-03-29
Non-Participating | BRODIE_2_WIND1
Non-Participating | BRODIE_2_WIND2
Non-Participating | BUCKBL_2_CTG11
Non-Participating | BUCKBL_2_CTG12
Participating Unit | BUCKBL_2_PL1X3 | 2010-07-31
Non-Participating | BUCKBL_2_STG10
Participating Unit | BUCKCK_2_HYDRO | 2016-06-13
Participating Unit | BUCKCK_7_OAKFLT | 1985-01-01
Participating Unit | BUCKCK_7_PL1X2 | 1928-01-01
Non-Participating | BUCKCK_7_UNIT 1
Non-Participating | BUCKCK_7_UNIT 2
Participating Unit | BUCKWD_1_NPALM1 | 2012-04-02
Participating Unit | BUCKWD_1_QF | 1984-12-13
Non-Participating | BUENVS_2_NSPIN
Participating Unit | BURNEY_6_HCCTG1 | 2025-06-30
Participating Unit | BURNYF_2_UNIT 1 | 2018-08-17
Participating Unit | BUTTVL_7_UNIT 1 | 1958-01-01
Participating Unit | CABALO_2_M2BSR1 | 2020-11-18
Participating Unit | CABALO_2_M2WSR2 | 2020-11-11
Participating Unit | CABLRO_2_CBSBT1 | 2025-02-05
Participating Unit | CABZON_1_WINDA1 | 2002-08-31
Participating Unit | CALFTN_2_CFSBT1 | 2021-08-31
Participating Unit | CALFTN_2_SOLAR | 2017-11-29
Participating Unit | CALFTS_2_CFSSR1 | 2019-03-05
Participating Unit | CALGEN_1_MDRBT1 | 2025-04-29
Non-Participating | CALGEN_1_UNIT 1
Non-Participating | CALGEN_1_UNIT 2
Non-Participating | CALGEN_1_UNIT 3
Participating Unit | CALGEN_1_UNITS | 1987-07-13
Participating Unit | CALPIN_1_AGNEW | 1990-10-19
Participating Unit | CALPSS_6_SOLAR1 | 2016-02-12
Participating Unit | CAMCHE_1_PL1X3 | 1983-01-01
Non-Participating | CAMCHE_1_UNIT 1
Non-Participating | CAMCHE_1_UNIT 2
Non-Participating | CAMCHE_1_UNIT 3
Participating Unit | CAMDEN_6_RDDBM1 | 2024-04-24
Participating Unit | CAMERN_6_BSPBT1
Participating Unit | CAMERN_6_BSPSR1 | 2024-01-29
Participating Unit | CAMLOT_2_SOLAR1 | 2014-12-11
Participating Unit | CAMLOT_2_SOLAR2 | 2014-12-10
Participating Unit | CAMPFW_7_FARWST | 1985-01-01
Participating Unit | CANTUA_1_SOLAR | 2012-07-25
Participating Unit | CAPWD_1_QF | 2015-10-19
Participating Unit | CARBOU_7_PL2X3 | 1921-01-01
Participating Unit | CARBOU_7_PL4X5 | 1958-01-01
Participating Unit | CARBOU_7_UNIT 1 | 1921-01-01
Non-Participating | CARBOU_7_UNIT 2
Non-Participating | CARBOU_7_UNIT 3
Non-Participating | CARBOU_7_UNIT 4
Non-Participating | CARBOU_7_UNIT 5
Participating Unit | CARLS1_2_CARCT1 | 2018-11-19
Non-Participating | CARLS1_2_CTG6
Non-Participating | CARLS1_2_CTG7
Non-Participating | CARLS1_2_CTG8
Non-Participating | CARLS1_2_CTG9
Participating Unit | CARLS2_1_CARCT1 | 2018-11-20
Participating Unit | CASADB_1_CD4GT1 | 2024-04-16
Participating Unit | CASCES_6_CESBT1 | 2023-12-14
Participating Unit | CASCES_6_CESBT2 | 2025-03-15
Participating Unit | CATLNA_2_SOLAR | 2013-02-15
Participating Unit | CATLNA_2_SOLAR2 | 2015-07-22
Participating Unit | CAVLSR_2_BSOLAR | 2013-01-01
Participating Unit | CAVLSR_2_RSOLAR | 2013-11-01
Participating Unit | CAYTNO_2_VASCO | 2014-02-05
Participating Unit | CDWR07_2_GEN | 2009-03-31
Participating Unit | CEDRCK_6_UNIT | 1984-03-22
Participating Unit | CEDUCR_2_SOLAR1 | 2016-12-23
Participating Unit | CEDUCR_2_SOLAR2 | 2016-12-23
Participating Unit | CEDUCR_2_SOLAR3 | 2016-12-23
Participating Unit | CEDUCR_2_SOLAR4 | 2016-12-23
Participating Unit | CENT40_1_C40SR1 | 2021-02-23
Participating Unit | CENTER_2_RHONDO | 1984-01-01
Participating Unit | CENTER_2_SOLAR1 | 2015-11-20
Participating Unit | CENTER_6_PEAKER | 2007-09-20
Non-Participating | CENTPD_2_BMSBT1
Non-Participating | CENTPD_2_BMSBT2
Non-Participating | CENTPD_2_BMSSR1
Non-Participating | CENTPD_2_BMSSR2
Participating Unit | CENTPD_2_BMSSX2 | 2022-12-21
Participating Unit | CENTPD_2_BMSX2 | 2022-12-21
Non-Participating | CENTRY_6_GEN 1
Non-Participating | CENTRY_6_GEN 2
Non-Participating | CENTRY_6_GEN 3
Non-Participating | CENTRY_6_GEN 4
Participating Unit | CENTRY_6_PL1X4 | 2001-09-17
Participating Unit | CHALK_1_UNIT | 1990-03-20
Participating Unit | CHARCA_1_NGLSR1 | 2025-01-31
Participating Unit | CHARMN_2_PGONG1 | 2020-08-01
Non-Participating | CHESTN_2_CHWBT1
Non-Participating | CHESTN_2_CHWBT2
Participating Unit | CHESTN_2_CHWBX2 | 2023-12-14
Non-Participating | CHESTN_2_CHWSR1
Non-Participating | CHESTN_2_CHWSR2
Participating Unit | CHESTN_2_CHWSX2 | 2023-12-14
Participating Unit | CHEVCD_6_UNIT | 1982-07-26
Participating Unit | CHEVCO_6_UNIT 1 | 1986-01-17
Participating Unit | CHEVCO_6_UNIT 2 | 1988-06-03
Participating Unit | CHEVCY_1_UNIT | 1982-10-15
Participating Unit | CHEVMN_2_UNITS | 1987-12-29
Participating Unit | CHICPK_7_UNIT 1 | 1965-01-01
Participating Unit | CHILLS_1_SYCENG | 2011-05-19
Participating Unit | CHILLS_7_UNITA1 | 2004-07-14
Participating Unit | CHINO_2_APEBT1 | 2016-12-31
Participating Unit | CHINO_2_JURUPA | 2013-12-20
Participating Unit | CHINO_2_PESBT1 | 2023-07-08
Participating Unit | CHINO_2_QF | 1987-01-01
Participating Unit | CHINO_2_SASOLR | 2013-12-20
Participating Unit | CHINO_2_SOLAR2 | 2015-04-13
Participating Unit | CHINO_6_CIMGEN | 2018-06-27
Participating Unit | CHWCHL_1_AVSSR1 | 2024-11-08
Participating Unit | CHWCHL_1_AVSSR2 | 2024-11-08
Participating Unit | CHWCHL_1_UNIT | 2001-06-13
Participating Unit | CLINESCO_3_PVDYN | 2021-12-01
Participating Unit | CLINESCO_3_WBDYN | 2021-12-01
Participating Unit | CLOVDL_1_SOLAR | 2014-06-26
Participating Unit | CLOVER_2_UNIT | 2016-05-06
Participating Unit | CLRMNT_6_CLEBT1 | 2024-03-27
Participating Unit | CLRMTK_1_QF | 1983-12-05
Participating Unit | CMBLND_2_DS2BT1 | 2023-11-22
Participating Unit | CMBLND_2_DS2BT2 | 2023-11-22
Participating Unit | CMBLND_2_DS2BT3 | 2023-12-01
Participating Unit | CMBLND_2_DS2SR1 | 2023-11-22
Participating Unit | CMBLND_2_DS2SR2 | 2023-11-17
Participating Unit | CMBLND_2_DS2SR3 | 2023-12-01
Participating Unit | CMRRON_2_CMNWD1
Participating Unit | CNTNLA_2_SOLAR1 | 2013-10-16
Participating Unit | CNTNLA_2_SOLAR2 | 2014-08-15
Participating Unit | COCOPP_2_CTG1 | 2013-05-01
Participating Unit | COCOPP_2_CTG2 | 2013-05-01
Participating Unit | COCOPP_2_CTG3 | 2013-05-01
Participating Unit | COCOPP_2_CTG4 | 2013-05-01
Participating Unit | COCOSB_6_SOLAR | 2013-06-12
Participating Unit | COGNAT_1_UNIT | 2014-02-12
Participating Unit | COLEMN_2_UNIT | 1979-01-01
Participating Unit | COLGAT_7_UNIT 1 | 1969-01-01
Participating Unit | COLGAT_7_UNIT 2 | 1969-01-01
Participating Unit | COLGNS_2_CNSSR1 | 2018-12-31
Participating Unit | COLPIN_6_COLLNS | 2021-11-19
Participating Unit | COLTON_6_AGUAM1 | 2003-06-27
Non-Participating | COLUSA_2_CTG1
Non-Participating | COLUSA_2_CTG2
Participating Unit | COLUSA_2_PL1X3 | 2010-12-22
Non-Participating | COLUSA_2_STG
Participating Unit | COLVIL_7_PL1X2 | 1989-12-31
Non-Participating | COLVIL_7_UNIT 1
Non-Participating | COLVIL_7_UNIT 2
Participating Unit | CONDOR_2_CDRBT1 | 2024-05-21
Participating Unit | CONTRL_1_CASAD1 | 1984-11-26
Participating Unit | CONTRL_1_CASAD2 | 2020-12-08
Participating Unit | CONTRL_1_CASAD3 | 2013-04-01
Participating Unit | CONTRL_1_LUNDY | 1911-01-01
Participating Unit | CONTRL_1_OXBOW | 2018-07-05
Participating Unit | CONTRL_1_POOLE | 1924-01-01
Participating Unit | CONTRL_1_QF | 1982-01-01
Participating Unit | CONTRL_1_RUSHCK | 1916-01-01
Participating Unit | COPMT2_2_SOLAR2 | 2012-06-27
Participating Unit | COPMT4_2_SOLAR4 | 2016-12-02
Participating Unit | COPMTN_2_CM10 | 2011-10-03
Participating Unit | COPMTN_2_SOLAR1 | 2010-06-15
Participating Unit | CORCAN_1_SOLAR1 | 2015-01-09
Participating Unit | CORCAN_1_SOLAR2 | 2015-05-23
Participating Unit | CORONS_2_SOLAR | 2013-04-24
Non-Participating | CORONS_6_CLRCTG
Non-Participating | CORONS_6_CLRSTG
Participating Unit | CORONS_6_CLRWTR | 2005-02-28
Participating Unit | CORRAL_6_SJOAQN | 2014-04-24
Participating Unit | COTTLE_2_FRNKNH | 2013-04-01
Participating Unit | COVERD_2_HCKHY1 | 2017-06-01
Participating Unit | COVERD_2_MCKHY1 | 2017-08-01
Participating Unit | COVERD_2_QFUNTS | 1987-01-05
Participating Unit | COVERD_2_RCKHY1 | 2017-06-01
Participating Unit | COWCRK_2_UNIT | 1907-01-01
Participating Unit | CPVERD_2_SOLAR | 2013-10-22
Participating Unit | CRELMN_6_AABBT1 | 2023-08-15
Participating Unit | CRELMN_6_RAMON1 | 2013-12-31
Participating Unit | CRELMN_6_RAMON2 | 2013-12-31
Participating Unit | CRELMN_6_RAMSR3 | 2018-02-03
Participating Unit | CRESSY_1_PARKER | 1981-09-23
Participating Unit | CRESTA_7_PL1X2 | 1949-01-01
Non-Participating | CRESTA_7_UNIT 1
Non-Participating | CRESTA_7_UNIT 2
Participating Unit | CRIMSN_2_CRMBT1 | 2022-09-16
Participating Unit | CRIMSN_2_CRMBT2 | 2022-10-28
Participating Unit | CRNEVL_6_CRNVA | 1919-01-01
Participating Unit | CRNEVL_6_SJQN 2 | 1917-01-01
Participating Unit | CROKET_7_UNIT | 1995-12-20
Participating Unit | CRSTWD_6_KUMYAY | 2005-12-21
Participating Unit | CRWCKS_1_SOLAR1 | 2016-06-30
Participating Unit | CSCGNR_1_UNIT 1 | 1987-01-01
Participating Unit | CSCGNR_1_UNIT 2 | 1986-01-01
Participating Unit | CSLR4S_2_SOLAR | 2013-10-11
Participating Unit | CSTRVL_7_PL1X2 | 2007-09-01
Participating Unit | CSTRVL_7_QFUNTS | 2006-06-01
Participating Unit | CTNWDP_1_QF | 1982-01-01
Participating Unit | CUMBIA_1_SOLAR | 2015-10-21
Participating Unit | CUMMNG_6_SUNCT1 | 2018-05-31
Participating Unit | CURTIS_1_CANLCK | 1983-01-01
Participating Unit | CURTIS_1_FARFLD | 1983-08-02
Participating Unit | CUYAMA_6_SB3SB1 | 2024-01-02
Participating Unit | CUYAMS_6_CUYSR1 | 2017-11-30
Participating Unit | CWATER_1_DS1BT1 | 2025-09-09
Participating Unit | DAIRLD_1_CR1BM1 | 2021-10-01
Participating Unit | DAIRLD_1_MD1SL1 | 2017-12-29
Participating Unit | DAIRLD_1_MD2BM1 | 2019-01-11
Participating Unit | DAVIS_1_SOLAR1 | 2013-07-01
Participating Unit | DAVIS_1_SOLAR2 | 2013-08-05
Participating Unit | DAVIS_7_MNMETH | 1997-01-01
Participating Unit | DEADCK_1_UNIT | 1990-01-29
Participating Unit | DEERCR_6_UNIT 1 | 1908-01-01
Participating Unit | DELAMO_2_ALASB2 | 2023-11-10
Participating Unit | DELAMO_2_SOLAR1 | 2015-04-22
Participating Unit | DELAMO_2_SOLAR2 | 2015-04-01
Participating Unit | DELAMO_2_SOLAR3 | 2017-02-24
Participating Unit | DELAMO_2_SOLAR4 | 2017-02-24
Participating Unit | DELAMO_2_SOLAR5 | 2017-02-24
Participating Unit | DELAMO_2_SOLAR6 | 2017-01-25
Participating Unit | DELAMO_2_SOLRC1 | 2012-02-10
Participating Unit | DELAMO_2_SOLRD | 2012-04-02
Participating Unit | DELSUR_6_BSOLAR | 2017-09-29
Participating Unit | DELSUR_6_CREST | 2016-04-05
Non-Participating | DELSUR_6_CREST1
Participating Unit | DELSUR_6_DRYFRB | 2014-11-21
Participating Unit | DELSUR_6_HORSR1 | 2023-08-22
Participating Unit | DELSUR_6_SOLAR1 | 2015-06-03
Participating Unit | DELSUR_6_SOLAR4 | 2018-12-31
Participating Unit | DELSUR_6_SOLAR5 | 2018-12-31
Non-Participating | DELTA_2_CTG1
Non-Participating | DELTA_2_CTG2
Non-Participating | DELTA_2_CTG3
Participating Unit | DELTA_2_PL1X4 | 2002-06-17
Non-Participating | DELTA_2_STG
Participating Unit | DEVERS_1_SEPV05 | 2012-05-10
Participating Unit | DEVERS_1_SOLAR | 2013-11-30
Participating Unit | DEVERS_1_SOLAR1 | 2013-06-01
Participating Unit | DEVERS_1_SOLAR2 | 2013-06-01
Participating Unit | DEVERS_2_CS2SR4 | 2018-05-18
Participating Unit | DEVERS_2_DHSPG2 | 2013-12-31
Participating Unit | DEXZEL_1_UNIT | 1989-11-30
Participating Unit | DIABLO_7_UNIT 1 | 1985-01-01
Participating Unit | DIABLO_7_UNIT 2 | 1986-01-01
Participating Unit | DISCOV_1_CHEVRN | 1988-06-13
Participating Unit | DIXNLD_1_LNDFL | 2015-11-13
Participating Unit | DLN_5_HARQSCEDYN | 2025-04-19
Non-Participating | DMDVLY_1_GEN 1
Non-Participating | DMDVLY_1_GEN 10
Non-Participating | DMDVLY_1_GEN 11
Non-Participating | DMDVLY_1_GEN 12
Non-Participating | DMDVLY_1_GEN 2
Non-Participating | DMDVLY_1_GEN 3
Non-Participating | DMDVLY_1_GEN 4
Non-Participating | DMDVLY_1_GEN 5
Non-Participating | DMDVLY_1_GEN 6
Non-Participating | DMDVLY_1_GEN 7
Non-Participating | DMDVLY_1_GEN 8
Non-Participating | DMDVLY_1_GEN 9
Participating Unit | DMDVLY_1_UNITS | 2001-01-01
Participating Unit | DONNLS_7_UNIT | 1957-01-01
Participating Unit | DOSMGO_2_NSPIN | 2009-03-31
Participating Unit | DOSPAL_1_DPSSR1 | 2025-03-13
Participating Unit | DOUBLC_1_UNITS | 1989-03-14
Participating Unit | DRACKR_2_D4SR4B | 2020-11-10
Participating Unit | DRACKR_2_DS3SR3 | 2020-05-19
Participating Unit | DRACKR_2_DS4SR4 | 2020-08-24
Participating Unit | DRACKR_2_DSUBT1 | 2021-08-12
Participating Unit | DRACKR_2_DSUBT2 | 2021-04-08
Participating Unit | DRACKR_2_DSUBT3 | 2021-07-23
Participating Unit | DRACKR_2_DSUBT4 | 2022-09-28
Participating Unit | DRACKR_2_SOLAR1 | 2016-03-07
Participating Unit | DRACKR_2_SOLAR2 | 2016-09-30
Non-Participating | DREWS_6_GEN 1
Non-Participating | DREWS_6_GEN 2
Non-Participating | DREWS_6_GEN 3
Non-Participating | DREWS_6_GEN 4
Participating Unit | DREWS_6_PL1X4 | 2001-08-14
Participating Unit | DREWSR_2_BHSSR1 | 2022-11-04
Participating Unit | DRUM_7_PL1X2 | 1913-01-01
Participating Unit | DRUM_7_PL3X4 | 1922-01-01
Non-Participating | DRUM_7_UNIT 1
Non-Participating | DRUM_7_UNIT 2
Non-Participating | DRUM_7_UNIT 3
Non-Participating | DRUM_7_UNIT 4
Participating Unit | DRUM_7_UNIT 5 | 1965-01-01
Participating Unit | DSABLA_7_UNIT | 1963-01-01
Participating Unit | DSFLWR_2_W9CSB1 | 2025-05-08
Participating Unit | DSFLWR_2_W9CSB2 | 2025-05-08
Participating Unit | DSFLWR_2_WS2SR1 | 2019-01-29
Participating Unit | DSRTHV_2_DH1SR1 | 2020-12-11
Participating Unit | DSRTHV_2_DH2BT1 | 2021-06-10
Participating Unit | DSRTHV_2_DH2SR2 | 2020-12-11
Participating Unit | DSRTSL_2_SOLAR1 | 2016-08-30
Non-Participating | DSRTSL_2_SOLR1A
Non-Participating | DSRTSL_2_SOLR1B
Non-Participating | DSRTSN_2_DS2BT1
Non-Participating | DSRTSN_2_DS2BT2
Non-Participating | DSRTSN_2_DS2BT3
Non-Participating | DSRTSN_2_DS2BT4
Participating Unit | DSRTSN_2_DS2BX2 | 2024-04-09
Participating Unit | DSRTSN_2_DS2X2 | 2022-08-28
Participating Unit | DSRTSN_2_SOLAR1 | 2013-10-22
Participating Unit | DSRTSN_2_SOLAR2 | 2013-10-12
Non-Participating | DSRTSN_2_SOLR1A
Non-Participating | DSRTSN_2_SOLR1B
Non-Participating | DSRTSN_2_SOLR2A
Non-Participating | DSRTSN_2_SOLR2B
Participating Unit | DTCHWD_2_BT3WND | 2016-04-22
Participating Unit | DUANE_1_PL1X3 | 2005-03-24
Non-Participating | DUANE_7_CTG1
Non-Participating | DUANE_7_CTG2
Non-Participating | DUANE_7_STG3
Participating Unit | DURNMESA_3_WBDYN | 2021-12-02
Participating Unit | DUTCH1_7_UNIT 1 | 1943-01-01
Participating Unit | DUTCH2_7_UNIT 1 | 1965-01-01
Non-Participating | DVLCYN_1_UNIT 1
Non-Participating | DVLCYN_1_UNIT 2
Non-Participating | DVLCYN_1_UNIT 3
Non-Participating | DVLCYN_1_UNIT 4
Participating Unit | DVLCYN_1_UNITS | 1972-01-01
Participating Unit | DYERSM_6_DSWWD1 | 2022-04-05
Participating Unit | DYLAN_2_BMTBT1 | 2024-08-27
Participating Unit | EASTWD_7_UNIT | 1987-01-01
Participating Unit | ECASCO_2_SJGBT1
Participating Unit | EDMONS_2_NSPIN | 2009-03-31
Participating Unit | EDWARD_2_E21SB1 | 2022-08-27
Participating Unit | EDWARD_2_E23SB1 | 2021-12-30
Participating Unit | EDWARD_2_ES2BT3 | 2022-04-02
Participating Unit | EDWARD_2_ESSSB1 | 2025-01-07
Participating Unit | EDWARD_2_ESSSB2 | 2023-11-14
Participating Unit | EEKTMN_6_SOLAR1 | 2015-08-12
Participating Unit | ELCABO_5_ECWSCEDYN | 2017-06-02
Participating Unit | ELCAJN_6_EB1BT1 | 2017-02-18
Participating Unit | ELCAJN_6_LM6K | 2010-06-16
Participating Unit | ELCAJN_6_UNITA1 | 2002-05-29
Participating Unit | ELCAP_1_SOLAR | 2015-05-01
Participating Unit | ELDORO_7_UNIT 1 | 2005-05-21
Participating Unit | ELDORO_7_UNIT 2 | 2005-05-21
Participating Unit | ELECTR_7_PL1X3 | 1948-01-01
Non-Participating | ELECTR_7_UNIT 1
Non-Participating | ELECTR_7_UNIT 2
Non-Participating | ELECTR_7_UNIT 3
Participating Unit | ELKCRK_6_STONYG | 1986-01-01
Participating Unit | ELKHIL_2_PL1X3 | 2003-07-24
Non-Participating | ELKHIL_7_CTG1
Non-Participating | ELKHIL_7_CTG2
Non-Participating | ELKHIL_7_STG
Non-Participating | ELKHRN_1_EESBT1
Non-Participating | ELKHRN_1_EESBT2
Non-Participating | ELKHRN_1_EESBT3
Participating Unit | ELKHRN_1_EESX3 | 2022-04-07
Participating Unit | ELLIOT_6_ELIBT1 | 2024-04-10
Participating Unit | ELLIS_2_QF | 1993-01-01
Participating Unit | ELNIDO_1_ECRSR1 | 2025-02-25
Participating Unit | ELSEGN_2_UN1011 | 2013-06-29
Participating Unit | ELSEGN_2_UN2021 | 2013-06-29
Non-Participating | ELSEGN_2_UNIT10
Non-Participating | ELSEGN_2_UNIT11
Non-Participating | ELSEGN_2_UNIT20
Non-Participating | ELSEGN_2_UNIT21
Participating Unit | ENERSJ_2_WIND | 2022-01-13
Participating Unit | ENERSJ_5_ESJWD2 | 2022-01-13
Participating Unit | ENWIND_2_WIND1 | 2014-12-10
Participating Unit | ENWIND_2_WIND2 | 2015-03-23
Participating Unit | ESCNDO_6_EB1BT1 | 2017-03-06
Participating Unit | ESCNDO_6_EB2BT2 | 2017-03-06
Participating Unit | ESCNDO_6_EB3BT3 | 2017-03-06
Participating Unit | ESCNDO_6_PL1X2 | 2014-01-25
Participating Unit | ESCNDO_6_UNITB1 | 2001-10-23
Participating Unit | ESCO_6_GLMQF | 1994-01-01
Participating Unit | ESNHWR_2_CS1BT3 | 2025-05-13
Participating Unit | ESNHWR_2_HDSBT2 | 2025-05-16
Participating Unit | ESNHWR_2_WC1BT1 | 2021-10-13
Participating Unit | ESQUON_6_LNDFIL | 2012-09-27
Participating Unit | ESTWND_2_OPPWD1 | 2021-10-12
Participating Unit | ETIWND_2_CHMPNE | 2013-12-20
Participating Unit | ETIWND_2_FONTNA | 1904-01-01
Participating Unit | ETIWND_2_SEPBT1 | 2024-09-24
Participating Unit | ETIWND_2_SOLAR1 | 2016-03-23
Participating Unit | ETIWND_2_SOLAR2 | 2016-09-06
Participating Unit | ETIWND_2_SOLAR5 | 2016-11-17
Participating Unit | ETIWND_2_UNIT1 | 2016-01-01
Participating Unit | ETIWND_6_GRPLND | 2007-09-20
Participating Unit | ETIWND_6_INEBT1 | 2024-10-09
Participating Unit | ETIWND_6_MWDETI | 1994-01-01
Participating Unit | EXCHEC_7_UNIT 1 | 1967-01-01
Participating Unit | EXCLSG_1_SOLAR | 2016-10-06
Participating Unit | FALBRK_6_FESBT1 | 2023-05-03
Participating Unit | FELLOW_7_QFUNTS | 2006-06-01
Participating Unit | FIFTHS_2_FSSBT | 2023-09-15
Participating Unit | FIFTHS_2_FSSR1 | 2023-09-29
Non-Participating | FILIPPI_2_QZSBT1
Non-Participating | FILIPPI_2_QZSBT2
Participating Unit | FILIPPI_2_QZSBTX | 2024-12-17
Non-Participating | FILIPPI_2_QZSSR1
Non-Participating | FILIPPI_2_QZSSR2
Participating Unit | FILIPPI_2_QZSSRX | 2024-12-17
Participating Unit | FLOWD_2_RT2WD2 | 2018-10-12
Participating Unit | FLOWD_2_WIND1 | 2016-01-15
Participating Unit | FLOWD2_2_FPLWND | 2005-05-01
Participating Unit | FMEADO_6_HELLHL | 1983-04-30
Participating Unit | FMEADO_7_UNIT | 1966-01-01
Participating Unit | FORBST_7_UNIT 1 | 1963-01-01
Participating Unit | FORKBU_6_UNIT | 2023-02-06
Participating Unit | FRESHW_1_SOLAR1 | 2016-03-04
Participating Unit | FRIANT_6_UNITS | 2016-03-01
Participating Unit | FRNTBW_6_SOLAR1 | 2019-02-05
Participating Unit | FROGTN_1_UTICAA | 2017-08-22
Participating Unit | FROGTN_1_UTICAM | 2017-08-22
Participating Unit | FTSWRD_6_TRFORK | 2011-11-01
Participating Unit | FTSWRD_7_QFUNTS | 2009-03-31
Participating Unit | FULTON_1_QF | 1983-01-01
Participating Unit | GALE_1_SR3SR3 | 2017-06-29
Participating Unit | GANSO_1_WSTBM1 | 2018-02-02
Participating Unit | GARLND_2_GARBT1 | 2022-01-31
Participating Unit | GARLND_2_GASLR | 2016-10-27
Participating Unit | GARLND_2_GASLRA | 2016-09-23
Participating Unit | GARNET_1_SOLAR | 2012-11-02
Participating Unit | GARNET_1_SOLAR2 | 2014-12-23
Participating Unit | GARNET_1_WIND | 2009-06-02
Participating Unit | GARNET_1_WINDS | 2011-02-21
Participating Unit | GARNET_1_WT3WND | 2012-12-24
Participating Unit | GARNET_2_COAWD2 | 2021-04-26
Participating Unit | GARNET_2_HYDRO | 2016-07-08
Participating Unit | GARNET_2_WIND1 | 2015-01-26
Participating Unit | GARNET_2_WIND2 | 2015-08-05
Participating Unit | GARNET_2_WIND3 | 2016-02-05
Participating Unit | GARNET_2_WIND4 | 2015-12-10
Participating Unit | GARNET_2_WIND5 | 2016-03-01
Participating Unit | GASKW1_2_GW1SR1 | 2018-03-06
Participating Unit | GASKW1_2_GW2BT1 | 2023-05-05
Participating Unit | GASKW1_2_GW2SR1 | 2023-05-05
Participating Unit | GASKW1_2_GW2SR2 | 2023-05-05
Participating Unit | GASKW1_2_GW3SR1 | 2023-05-05
Participating Unit | GASKW1_2_GW4SR1 | 2023-05-05
Participating Unit | GASKW1_2_GW5SR1 | 2023-05-05
Participating Unit | GATES_2_SOLAR | 2013-06-24
Participating Unit | GATES_2_WSOLAR | 2013-06-24
Participating Unit | GATEWY_2_GESBT1 | 2025-04-22
Non-Participating | GATWAY_2_CTGA
Non-Participating | GATWAY_2_CTGB
Participating Unit | GATWAY_2_PL1X3 | 2009-01-06
Non-Participating | GATWAY_2_STGC
Participating Unit | GENESI_2_STG | 2013-11-27
Non-Participating | GENESI_2_STG1
Non-Participating | GENESI_2_STG2
Participating Unit | GEYS11_7_UNIT11 | 1975-01-01
Participating Unit | GEYS12_7_UNIT12 | 1979-01-01
Participating Unit | GEYS13_7_UNIT13 | 1980-01-01
Participating Unit | GEYS14_7_UNIT14 | 1980-01-01
Participating Unit | GEYS16_7_UNIT16 | 1985-01-01
Participating Unit | GEYS17_7_UNIT17 | 1982-01-01
Participating Unit | GEYS18_7_UNIT18 | 1983-01-01
Participating Unit | GEYS20_7_UNIT20 | 1985-01-01
Participating Unit | GIFENS_6_BUGSL1 | 2017-06-16
Participating Unit | GIFFEN_6_SOLAR | 2012-07-25
Participating Unit | GIFFEN_6_SOLAR1 | 2017-09-15
Non-Participating | GILROY_1_CT1
Non-Participating | GILROY_1_ST2
Participating Unit | GILROY_1_UNIT | 1987-01-01
Participating Unit | GILRPP_1_PL1X2 | 2002-01-29
Participating Unit | GILRPP_1_PL3X4 | 2002-02-28
Non-Participating | GILRPP_1_UNIT 1
Non-Participating | GILRPP_1_UNIT 2
Participating Unit | GLDFGR_6_SOLAR1 | 2017-02-15
Participating Unit | GLDFGR_6_SOLAR2 | 2017-02-14
Participating Unit | GLDTWN_6_COLUM3 | 2013-12-10
Participating Unit | GLDTWN_6_SOLAR | 2013-11-18
Participating Unit | GLNARM_2_UNIT 5 | 2016-12-20
Participating Unit | GLNARM_7_UNIT 1 | 1976-01-01
Participating Unit | GLNARM_7_UNIT 2 | 1976-01-01
Participating Unit | GLNARM_7_UNIT 3 | 2004-01-08
Participating Unit | GLNARM_7_UNIT 4 | 2004-01-08
Participating Unit | GLOW_6_SOLAR | 2013-03-25
Participating Unit | GOLETA_2_GE2BT3 | 2024-01-06
Participating Unit | GOLETA_2_PAIBT2
Participating Unit | GOLETA_2_VALBT1 | 2021-02-04
Participating Unit | GOLETA_6_ELLWOD | 1998-04-29
Participating Unit | GOLETA_6_EXGEN | 1993-08-19
Participating Unit | GOLETA_6_TR2BM2 | 2022-06-24
Participating Unit | GONZLS_6_UNIT | 2013-07-08
Participating Unit | GOOSLK_1_SOLAR1 | 2015-05-23
Participating Unit | GRADYW_5_GDYWD1 | 2019-08-01
Participating Unit | GRDISL_1_RVSSR1 | 2025-03-26
Participating Unit | GRIDLY_6_SOLAR | 2013-04-01
Participating Unit | GRIFFI_2_LSPDYN | 2015-01-24
Participating Unit | GRIZLY_1_UNIT 1 | 1993-01-01
Participating Unit | GRNITE_6_ESCBT1
Participating Unit | GRNLF1_1_PL1X2 | 2022-06-24
Non-Participating | GRNLF1_1_UNITA
Non-Participating | GRNLF1_1_UNITB
Participating Unit | GRNLF2_1_UNIT | 2020-06-01
Participating Unit | GRNVLY_7_SCLAND | 2006-02-02
Participating Unit | GRSCRK_6_BGCKWW | 1987-01-01
Participating Unit | GRZZLY_1_BERKLY | 2018-02-20
Participating Unit | GUERNS_6_HD3BM3 | 2019-07-01
Participating Unit | GUERNS_6_SOLAR | 2013-09-18
Participating Unit | GUERNS_6_VH2BM1 | 2019-07-01
Non-Participating | GWFPWR_1_CT 1
Non-Participating | GWFPWR_1_CT 2
Participating Unit | GWFPWR_1_HPPBT1 | 2025-08-20
Participating Unit | GWFPWR_1_LDCTG1 | 2025-07-25
Participating Unit | GWFPWR_1_LDCTG2 | 2025-07-25
Participating Unit | GWFPWR_1_LEDBT1 | 2025-08-20
Participating Unit | GWFPWR_1_UNITS | 2001-08-27
Non-Participating | GYS5X6_7_UNIT 5
Non-Participating | GYS5X6_7_UNIT 6
Participating Unit | GYS5X6_7_UNITS | 1971-01-01
Non-Participating | GYS7X8_7_UNIT 7
Non-Participating | GYS7X8_7_UNIT 8
Participating Unit | GYS7X8_7_UNITS | 1972-01-01
Participating Unit | GYSRVL_7_WSPRNG | 1988-12-22
Participating Unit | HAASPH_7_PL1X2 | 1958-01-01
Non-Participating | HAASPH_7_UNIT 1
Non-Participating | HAASPH_7_UNIT 2
Participating Unit | HALSEY_6_UNIT | 1916-01-01
Participating Unit | HAMLIN_1_BLDSB1 | 2024-04-30
Participating Unit | HAMLIN_1_BMSBT2 | 2024-12-12
Non-Participating | HARBGN_7_UNIT 1
Non-Participating | HARBGN_7_UNIT 2
Non-Participating | HARBGN_7_UNIT 3
Participating Unit | HARBGN_7_UNITS | 2001-06-14
Participating Unit | HARDWK_6_STWBM1 | 2020-05-26
Participating Unit | HATCR1_7_UNIT | 1921-01-01
Participating Unit | HATCR2_7_UNIT | 1921-01-01
Participating Unit | HATLOS_6_BWDHY1 | 2017-06-29
Participating Unit | HATLOS_6_LSCRK | 1989-06-15
Participating Unit | HATRDG_2_WIND | 2010-11-19
Participating Unit | HAYPRS_6_HAYHD1 | 2021-03-03
Participating Unit | HAYPRS_6_HAYHD2 | 2021-04-08
Participating Unit | HELMPG_7_UNIT 1 | 1984-01-01
Participating Unit | HELMPG_7_UNIT 2 | 1984-01-01
Participating Unit | HELMPG_7_UNIT 3 | 1984-01-01
Participating Unit | HENRTA_6_ACDSR3 | 2025-04-04
Non-Participating | HENRTA_6_ELCBT1
Non-Participating | HENRTA_6_ELCBT2
Participating Unit | HENRTA_6_ELCBX2 | 2025-05-20
Participating Unit | HENRTA_6_ELCTG1 | 2025-01-03
Participating Unit | HENRTA_6_ELCTG2 | 2025-01-03
Participating Unit | HENRTA_6_HDEBT1 | 2021-11-04
Participating Unit | HENRTA_6_SOLAR1 | 2016-01-29
Participating Unit | HENRTA_6_SOLAR2 | 2016-05-07
Participating Unit | HENRTS_1_SOLAR | 2016-08-19
Participating Unit | HERDLN_6_BYHSR1 | 2022-11-23
Participating Unit | HIDSRT_2_UNITS | 2003-04-21
Non-Participating | HIDSRT_7_CTG1
Non-Participating | HIDSRT_7_CTG2
Non-Participating | HIDSRT_7_CTG3
Non-Participating | HIDSRT_7_STG
Participating Unit | HIGGNS_1_COMBIE | 2020-05-05
Participating Unit | HIGHDS_2_H5SBT1 | 2021-12-08
Participating Unit | HIGHDS_2_H5SSR1 | 2021-08-09
Participating Unit | HILAND_7_YOLOWD | 1985-09-07
Participating Unit | HINSON_2_CTCSR1
Participating Unit | HINSON_2_W2CSR2 | 2025-08-14
Participating Unit | HINSON_2_WI1SR1
Participating Unit | HINSON_6_LBECH1 | 2007-08-01
Participating Unit | HINSON_6_LBECH2 | 2007-08-01
Participating Unit | HINSON_6_LBECH3 | 2007-08-01
Participating Unit | HINSON_6_LBECH4 | 2007-08-01
Participating Unit | HNTGBH_2_PL1X3 | 2020-02-04
Non-Participating | HNTGBH_7_CTG1A
Non-Participating | HNTGBH_7_CTG1B
Non-Participating | HNTGBH_7_STG1S
Participating Unit | HNTGBH_7_UNIT 2 | 1998-05-05
Participating Unit | HOLGAT_1_BORAX | 1984-06-01
Participating Unit | HOLSTR_1_SOLAR | 2014-06-16
Participating Unit | HOLSTR_1_SOLAR2 | 2015-04-17
Participating Unit | HOOV_2_ANAPT | 2022-12-15
Participating Unit | HOOVER_2_MWDPT | 2023-01-25
Participating Unit | HOOVER_2_SCEPT | 2023-01-25
Participating Unit | HOOVER_2_VEAPT | 2023-01-25
Participating Unit | HUMBPP_1_UNITS3 | 2010-09-29
Participating Unit | HUMBPP_6_UNITS | 2010-09-29
Non-Participating | HUMBPP_6_UNITS1
Non-Participating | HUMBPP_6_UNITS2
Participating Unit | HUMBRD_1_HMBBT1
Participating Unit | HURON_6_SOLAR | 2012-08-30
Non-Participating | HYATT_2_UNIT 1
Non-Participating | HYATT_2_UNIT 2
Non-Participating | HYATT_2_UNIT 3
Non-Participating | HYATT_2_UNIT 4
Non-Participating | HYATT_2_UNIT 5
Non-Participating | HYATT_2_UNIT 6
Participating Unit | HYTTHM_2_UNITS | 1968-01-01
Participating Unit | IGNACO_1_QF | 1985-01-01
Participating Unit | INDIGO_1_UNIT 1 | 2001-09-19
Participating Unit | INDIGO_1_UNIT 2 | 2001-09-19
Participating Unit | INDIGO_1_UNIT 3 | 2001-09-19
Participating Unit | INDVLY_1_UNITS | 1983-09-15
Non-Participating | INTKEP_2_HOLM 1
Non-Participating | INTKEP_2_HOLM 2
Non-Participating | INTKEP_2_KIRKW1
Non-Participating | INTKEP_2_KIRKW2
Non-Participating | INTKEP_2_KIRKW3
Participating Unit | INTKEP_2_UNITS | 2006-07-01
Participating Unit | INTMNT_3_ANAHEIM | 2014-10-01
Participating Unit | INTMNT_3_CC_3_ANAHEIM
Participating Unit | INTMNT_3_CC_3_PASADENA
Participating Unit | INTMNT_3_CC_3_RIVERSIDE
Participating Unit | INTMNT_3_CC_4_ANAHEIM
Participating Unit | INTMNT_3_CC_4_PASADENA
Participating Unit | INTMNT_3_CC_4_RIVERSIDE
Participating Unit | INTMNT_3_PASADENA | 2015-06-01
Participating Unit | INTMNT_3_RIVERSIDE | 2015-04-01
Participating Unit | INYOKN_1_IKSSR1 | 2024-12-31
Participating Unit | INYOKN_1_IKSSR2 | 2024-12-31
Participating Unit | IVANPA_1_UNIT1 | 2013-11-17
Participating Unit | IVANPA_1_UNIT2 | 2013-12-30
Participating Unit | IVANPA_1_UNIT3 | 2013-12-26
Participating Unit | IVSLR2_2_SM2SR1 | 2019-12-06
Participating Unit | IVSLRP_2_SOLAR1 | 2013-10-28
Participating Unit | IVWEST_2_SOLAR1 | 2015-09-30
Non-Participating | IVWEST_2_SOLR1A
Non-Participating | IVWEST_2_SOLR1B
Participating Unit | JACMSR_1_JACSR1 | 2017-07-25
Participating Unit | JANCRK_6_RCABT1 | 2021-12-22
Participating Unit | JAVASR_1_JAVSR1 | 2022-11-18
Participating Unit | JAWBNE_2_NSRWND | 2012-12-08
Participating Unit | JAWBNE_2_SRWND | 2021-09-01
Participating Unit | JAWBNE_2_SRWWD2 | 2021-09-17
Participating Unit | JAYNE_6_WLSLR | 2014-02-14
Participating Unit | JOANEC_2_ST3BT3 | 2023-06-02
Participating Unit | JOANEC_2_STABT1 | 2021-06-11
Participating Unit | JOANEC_2_STABT2 | 2022-06-06
Participating Unit | JOHANN_2_JOSBT1 | 2021-10-29
Participating Unit | JOHANN_2_JOSBT2 | 2021-10-29
Participating Unit | JOHANN_2_OCEBT2 | 2021-12-07
Participating Unit | JOHANN_2_OCEBT3 | 2021-12-07
Participating Unit | JOHANN_2_T1BBT1
Participating Unit | KANSAS_6_SOLAR | 2013-06-06
Participating Unit | KEARNY_6_NESBT1 | 2022-03-10
Participating Unit | KEARNY_6_SESBT2 | 2022-03-10
Participating Unit | KEKAWK_6_UNIT | 1989-12-27
Non-Participating | KELSO_2_GTG6
Non-Participating | KELSO_2_GTG7
Participating Unit | KELSO_2_UNITS | 2012-10-01
Non-Participating | KELSO_3_GTG8
Non-Participating | KELSO_3_GTG9
Participating Unit | KELYRG_6_UNIT | 1963-01-01
Participating Unit | KERKH2_7_UNIT 1 | 1983-01-01
Participating Unit | KERMAN_6_SOLAR1 | 2015-10-21
Participating Unit | KERMAN_6_SOLAR2 | 2015-10-20
Participating Unit | KERNEY_6_FCSSR1 | 2024-07-29
Participating Unit | KERNFT_1_UNITS | 1989-01-07
Participating Unit | KERNRG_1_UNITS | 1985-01-01
Participating Unit | KERRGN_1_UNIT 1 | 1907-01-01
Participating Unit | KINGCO_1_KINGBR | 1990-12-05
Participating Unit | KINGRV_7_UNIT 1 | 1962-01-01
Participating Unit | KIRKER_1_PBSSR1
Participating Unit | KIRKER_7_KELCYN | 2009-08-01
Participating Unit | KNGBRD_2_SOLAR1 | 2016-04-30
Participating Unit | KNGBRD_2_SOLAR2 | 2016-04-30
Participating Unit | KNGBRG_1_KBSLR1 | 2013-12-06
Participating Unit | KNGBRG_1_KBSLR2 | 2013-12-06
Participating Unit | KNGCTY_6_UNITA1 | 2002-01-14
Participating Unit | KNTSTH_6_SOLAR | 2014-12-24
Participating Unit | KNTSTH_6_WALSR1 | 2023-09-26
Participating Unit | KOLA_2_KLBBT1 | 2025-08-01
Participating Unit | KOLA_2_KLBBT2 | 2025-08-01
Non-Participating | KOLA_2_KLBT1A
Non-Participating | KOLA_2_KLBT1B
Non-Participating | KRAMER_1_R1BBT1
Non-Participating | KRAMER_1_R1BBT2
Non-Participating | KRAMER_1_R1BBT3
Participating Unit | KRAMER_1_R1BX3 | 2023-07-01
Non-Participating | KRAMER_1_R1PSR1
Non-Participating | KRAMER_1_R1PSR2
Non-Participating | KRAMER_1_R1PSR3
Participating Unit | KRAMER_1_R1PX3 | 2023-08-02
Non-Participating | KRAMER_1_R2BBT1
Non-Participating | KRAMER_1_R2BBT2
Participating Unit | KRAMER_1_R2BX2 | 2023-08-30
Non-Participating | KRAMER_1_R2PSR1
Non-Participating | KRAMER_1_R2PSR2
Participating Unit | KRAMER_1_R2PX2 | 2023-09-14
Participating Unit | KRNCNY_6_UNIT | 2021-06-09
Participating Unit | KYCORA_6_KMSBT1 | 2020-02-13
Participating Unit | LACIEN_2_VENICE | 1982-01-01
Participating Unit | LAFRES_2_ESHSR1 | 2025-07-24
Participating Unit | LAGBEL_2_CBPBT1 | 2024-07-02
Participating Unit | LAGBEL_2_CDCSR1
Participating Unit | LAGBEL_2_EDCSR1
Participating Unit | LAGBEL_2_EDCSR2
Participating Unit | LAKEVW_6_AFTBT1 | 2025-05-06
Participating Unit | LALPAG_1_LALBT1
Participating Unit | LAMONT_1_SOLAR1 | 2014-09-02
Participating Unit | LAMONT_1_SOLAR2 | 2018-01-06
Participating Unit | LAMONT_1_SOLAR3 | 2015-12-23
Participating Unit | LAMONT_1_SOLAR4 | 2015-12-23
Participating Unit | LAMONT_1_SOLAR5 | 2015-10-30
Participating Unit | LAPLMA_2_UNIT 1 | 2003-01-10
Participating Unit | LAPLMA_2_UNIT 2 | 2003-03-05
Participating Unit | LAPLMA_2_UNIT 3 | 2003-01-13
Participating Unit | LAPLMA_2_UNIT 4 | 2003-03-05
Participating Unit | LARKSP_6_UNIT 1 | 2001-09-13
Participating Unit | LARKSP_6_UNIT 2 | 2001-09-13
Non-Participating | LAROA2_2_CTG 2S
Non-Participating | LAROA2_2_STG 2C
Participating Unit | LAROA2_2_UNITA1 | 2003-07-22
Participating Unit | LASSEN_6_UNITS | 2017-06-27
Participating Unit | LAWRNC_7_SUNYVL | 1999-01-01
Participating Unit | LCKHT1_2_LH1BT1 | 2024-07-08
Participating Unit | LCKHT1_2_LH1SR1 | 2023-07-18
Participating Unit | LCKHT1_2_LH1SR2 | 2023-07-26
Participating Unit | LCKHT1_2_LSCBT1
Participating Unit | LCKHT1_2_LSCBT2
Participating Unit | LEBECS_2_UNITS | 2005-05-04
Non-Participating | LEBECS_7_CTG1
Non-Participating | LEBECS_7_CTG2
Non-Participating | LEBECS_7_CTG4
Non-Participating | LEBECS_7_STG3
Non-Participating | LEBECS_7_STG5
Non-Participating | LECEF_1_CGT 1
Non-Participating | LECEF_1_CGT 2
Non-Participating | LECEF_1_CGT 3
Non-Participating | LECEF_1_CGT 4
Non-Participating | LECEF_1_STG1
Participating Unit | LECEF_1_UNITS | 2013-07-31
Participating Unit | LECONT_2_LESBT1 | 2022-09-01
Participating Unit | LEPRFD_1_KANSAS | 2014-12-18
Participating Unit | LGHTHP_2_DOCSR1 | 2025-08-04
Participating Unit | LGHTHP_2_SBDSR1
Participating Unit | LGHTHP_2_SBDSR2
Participating Unit | LGHTHP_6_ICEGEN | 1989-12-22
Participating Unit | LHILLS_6_SOLAR1 | 2015-04-10
Participating Unit | LILIAC_6_SOLAR | 2016-09-17
Participating Unit | LITLRK_6_GBCSR1 | 2018-08-18
Participating Unit | LITLRK_6_SEPV01 | 2012-05-08
Participating Unit | LITLRK_6_SOLAR1 | 2015-01-17
Participating Unit | LITLRK_6_SOLAR2 | 2016-01-13
Participating Unit | LITLRK_6_SOLAR3 | 2017-09-30
Participating Unit | LITLRK_6_SOLAR4 | 2016-03-22
Participating Unit | LIVEOK_6_SOLAR | 2014-11-27
Participating Unit | LIVOAK_1_UNIT 1 | 1991-03-16
Participating Unit | LMBEPK_2_UNITA1 | 2003-01-06
Participating Unit | LMBEPK_2_UNITA2 | 2003-01-06
Participating Unit | LMBEPK_2_UNITA3 | 2003-01-06
Non-Participating | LMEC_1_CTG1
Non-Participating | LMEC_1_CTG2
Participating Unit | LMEC_1_PL1X3 | 2001-06-09
Non-Participating | LMEC_1_STG
Participating Unit | LNCSTR_6_CREST | 2017-06-23
Participating Unit | LNCSTR_6_SOLAR2 | 2021-12-22
Participating Unit | LOCKFD_1_BEARCK | 2014-02-05
Participating Unit | LOCKFD_1_KSOLAR | 2014-03-14
Participating Unit | LODI25_2_UNIT 1 | 1986-01-01
Participating Unit | LODI25_6_ERKNG1 | 2024-11-22
Non-Participating | LODIEC_2_CTG
Participating Unit | LODIEC_2_PL1X2 | 2012-11-27
Non-Participating | LODIEC_2_STG
Participating Unit | LOTUS_6_LSFSR1 | 2020-05-30
Participating Unit | LOWGAP_1_SUPHR | 1988-02-23
Participating Unit | LOWGAP_7_QFUNTS | 2017-05-10
Participating Unit | LTBEAR_1_LB3SR3 | 2020-12-03
Participating Unit | LTBEAR_1_LB4SR4 | 2020-12-03
Participating Unit | LTBEAR_1_LB4SR5 | 2020-12-03
Participating Unit | LTBERA_1_LB1SR1 | 2020-12-03
Participating Unit | LUNAVL_2_LVSSR1 | 2025-08-22
Participating Unit | LUNAVL_2_LVSSR2 | 2025-08-22
Participating Unit | LUNAVL_2_LVSSR3 | 2025-08-22
Participating Unit | LVNGST_1_WTASR1 | 2024-11-08
Participating Unit | MAGNLA_6_ANAHEIM | 2020-01-15
Participating Unit | MAGNLA_6_CERRITOS | 2020-01-15
Participating Unit | MAGNLA_6_COLTON | 2020-01-15
Participating Unit | MAGNLA_6_PASADENA | 2020-01-15
Participating Unit | MAGUND_1_BKISR1 | 2017-12-27
Participating Unit | MAGUND_1_BKSSR2 | 2017-12-26
Non-Participating | MALAGA_1_ACDBT1
Non-Participating | MALAGA_1_ACDBT2
Participating Unit | MALAGA_1_ACDBX2 | 2025-03-14
Participating Unit | MALAGA_1_AUCTG1 | 2024-11-18
Participating Unit | MALAGA_1_AUCTG2 | 2024-11-18
Participating Unit | MALCHQ_7_UNIT 1 | 1988-12-07
Participating Unit | MALIN_5_BPADYN | 2009-03-31
Participating Unit | MALIN_5_GCPDDYN | 2018-02-09
Participating Unit | MALIN_5_HERMDYN | 2021-04-13
Participating Unit | MALIN_5_IBERDR | 2015-02-01
Participating Unit | MALIN_5_INHRED | 2011-10-01
Participating Unit | MALIN_5_INHRPG | 2011-10-01
Non-Participating | MAMMTH_7_UNIT 1
Non-Participating | MAMMTH_7_UNIT 2
Participating Unit | MANTEC_1_ML1SR1 | 2017-12-28
Participating Unit | MANZNA_2_CAMSR1 | 2025-04-03
Non-Participating | MANZNA_2_MANWD1
Non-Participating | MANZNA_2_MANWD2
Participating Unit | MANZNA_2_WIND | 2012-12-20
Participating Unit | MARCPW_6_SOLAR1 | 2015-12-12
Participating Unit | MARTIN_1_SUNSET | 2010-10-29
Non-Participating | MARVEL_2_MARBT1
Non-Participating | MARVEL_2_MARBT2
Participating Unit | MARVEL_2_MARBT3 | 2024-04-25
Participating Unit | MARVEL_2_MARBX2 | 2024-04-25
Participating Unit | MCARTH_6_FRIVRB | 2014-03-05
Participating Unit | MCCALL_1_QF | 1990-01-01
Participating Unit | MCFLND_5_MBSBX2 | 2024-09-26
Participating Unit | MCFLND_5_MFAUXL1
Participating Unit | MCFLND_5_MFSBT1 | 2023-12-22
Participating Unit | MCFLND_5_MFSSR1 | 2023-12-22
Non-Participating | MCFLND_5_MSBSB1
Non-Participating | MCFLND_5_MSBSB2
Participating Unit | MCFLND_5_MSCBT1 | 2025-04-09
Participating Unit | MCSWAN_6_UNITS | 1967-01-01
Participating Unit | MDFKRL_2_PROJCT | 1966-01-01
Participating Unit | MELRSE_6_MELBT1 | 2024-03-15
Participating Unit | MELRSE_6_MELBT2 | 2024-03-15
Participating Unit | MENBIO_6_RENEW1 | 2010-04-30
Participating Unit | MERCED_1_SOLAR1 | 2015-05-23
Participating Unit | MERCED_1_SOLAR2 | 2015-05-12
Participating Unit | MERCFL_6_UNIT | 1930-01-01
Participating Unit | MESAP_1_QF | 2009-03-31
Participating Unit | MESAS_2_CADBT1
Participating Unit | MESAS_2_YORBT1
Participating Unit | METEC_2_PL1X3 | 2005-05-27
Non-Participating | METEC_7_CTG1
Non-Participating | METEC_7_CTG2
Non-Participating | METEC_7_STG3
Non-Participating | MIDFRK_7_UNIT 1
Non-Participating | MIDFRK_7_UNIT 2
Non-Participating | MIDSUN_1_CT5A
Non-Participating | MIDSUN_1_CT5B
Participating Unit | MIDSUN_1_PL1X2 | 2022-03-17
Participating Unit | MIDWD_2_WIND2 | 2015-12-23
Participating Unit | MIDWD_7_CORAMB | 1983-12-01
Participating Unit | MIDWY3_2_MDSSR1 | 2018-09-06
Participating Unit | MIDWYS_2_MIDSL1 | 2018-01-13
Participating Unit | MILFRD_7_PASADENA | 2016-03-01
Participating Unit | MIRLOM_2_CORONA | 1987-01-01
Participating Unit | MIRLOM_2_CREST | 2020-03-25
Participating Unit | MIRLOM_2_LNDFL | 2017-06-23
Participating Unit | MIRLOM_2_MLBBTA | 2016-12-30
Participating Unit | MIRLOM_2_MLBBTB | 2016-12-30
Participating Unit | MIRLOM_2_TEMESC | 1987-01-01
Participating Unit | MIRLOM_6_PEAKER | 2007-09-20
Participating Unit | MIRLOM_7_MWDLKM | 1980-01-01
Participating Unit | MISSIX_1_QF | 1987-01-01
Participating Unit | MKTRCK_1_UNIT 1 | 1991-10-16
Participating Unit | MLPTAS_7_QFUNTS | 2009-03-31
Participating Unit | MNDALY_6_MCGRTH | 2012-11-01
Participating Unit | MNDOTA_1_SOLAR1 | 2015-06-20
Participating Unit | MNDOTA_1_SOLAR2 | 2015-12-11
Non-Participating | MOCCPH_7_UNIT 1
Non-Participating | MOCCPH_7_UNIT 2
Participating Unit | MOJAVE_1_SIPHON | 1996-01-01
Participating Unit | MOJAVW_2_SOLAR | 2016-06-15
Non-Participating | MONTPH_7_UNIT 1
Non-Participating | MONTPH_7_UNIT 2
Non-Participating | MONTPH_7_UNIT 3
Participating Unit | MONTPH_7_UNITS | 1974-01-01
Participating Unit | MOORPK_2_ACOBT1 | 2021-03-31
Participating Unit | MOORPK_2_CALABS | 2010-09-20
Participating Unit | MOORPK_6_QF | 1976-01-01
Participating Unit | MORWD_6_QF | 2017-01-17
Participating Unit | MOSSLD_2_PSP1 | 2002-07-01
Non-Participating | MOSSLD_2_PSP1G1
Non-Participating | MOSSLD_2_PSP1G2
Non-Participating | MOSSLD_2_PSP1G3
Participating Unit | MOSSLD_2_PSP2 | 2002-07-11
Non-Participating | MOSSLD_2_PSP2G1
Non-Participating | MOSSLD_2_PSP2G2
Non-Participating | MOSSLD_2_PSP2G3
Non-Participating | MRCHNT_2_CTG1
Non-Participating | MRCHNT_2_CTG2
Participating Unit | MRCHNT_2_PL1X3 | 2012-06-18
Non-Participating | MRCHNT_2_STG
Participating Unit | MRGT_6_MEF2 | 2009-08-07
Participating Unit | MRGT_6_MMAREF | 2005-07-27
Participating Unit | MRGT_6_TGEBT1 | 2021-06-30
Participating Unit | MRLSDS_6_SOLAR1 | 2015-11-25
Participating Unit | MSHGTS_6_MMARLF | 2003-05-21
Participating Unit | MSOLAR_2_MS4BT1 | 2024-01-26
Participating Unit | MSOLAR_2_MS4SR4 | 2024-01-18
Participating Unit | MSOLAR_2_SOLAR1 | 2014-01-01
Participating Unit | MSOLAR_2_SOLAR2 | 2017-10-12
Participating Unit | MSOLAR_2_SOLAR3 | 2016-12-06
Participating Unit | MSQUIT_5_SERDYN | 2009-03-31
Participating Unit | MSSION_2_QF | 1980-01-01
Participating Unit | MSTANG_2_MTGBT1 | 2021-11-01
Participating Unit | MSTANG_2_SOLAR | 2016-07-12
Participating Unit | MSTANG_2_SOLAR3 | 2016-05-03
Participating Unit | MSTANG_2_SOLAR4 | 2016-06-09
Participating Unit | MTNPOS_1_UNIT | 1989-04-01
Participating Unit | MTWIND_1_MVPWD1 | 2022-07-26
Participating Unit | MTWIND_1_UNIT 3 | 2003-12-15
Participating Unit | MURRAY_6_UNIT | 2016-12-16
Participating Unit | NAROW1_2_UNIT | 2020-09-21
Participating Unit | NAROW2_2_UNIT | 1969-01-01
Non-Participating | NAVYII_2_UNIT 4
Non-Participating | NAVYII_2_UNIT 5
Non-Participating | NAVYII_2_UNIT 6
Participating Unit | NAVYII_2_UNITS | 1989-12-23
Participating Unit | NCPA_7_GP1UN1 | 1983-01-01
Participating Unit | NCPA_7_GP1UN2 | 1983-01-01
Participating Unit | NCPA_7_GP2UN3 | 1985-01-01
Participating Unit | NCPA_7_GP2UN4 | 1986-01-01
Participating Unit | NEENCH_6_SOLAR | 2013-01-18
Participating Unit | NEWARK_1_QF | 2009-03-31
Participating Unit | NGILAA_5_SDGDYN | 2009-03-31
Non-Participating | NHOGAN_6_UNIT 1
Non-Participating | NHOGAN_6_UNIT 2
Participating Unit | NHOGAN_6_UNITS | 1986-04-15
Participating Unit | NIMTG_6_NICOGN | 1989-01-01
Participating Unit | NITHWK_1_NHSBT1
Participating Unit | NOAKS_2_PESBT1 | 2024-11-14
Participating Unit | NORCNV_1_NCVBT1 | 2023-08-30
Participating Unit | NORORC_2_NOSBX2 | 2025-04-22
Non-Participating | NORORC_2_NOSSB1
Non-Participating | NORORC_2_NOSSB2
Participating Unit | NOVATO_6_LNDFL | 2017-09-16
Participating Unit | NWCSTL_7_UNIT 1 | 1986-01-01
Participating Unit | NZWIND_2_WDSTR5 | 2016-03-08
Participating Unit | NZWIND_6_CALWND | 2012-03-24
Participating Unit | NZWIND_6_WDSTR | 1984-02-01
Participating Unit | NZWIND_6_WDSTR2 | 2014-11-30
Participating Unit | NZWIND_6_WDSTR3 | 2014-11-30
Participating Unit | NZWIND_6_WDSTR4 | 2015-12-11
Participating Unit | OAK C_1_EBMUD | 2012-11-01
Participating Unit | OAK C_7_UNIT 1 | 1978-01-01
Participating Unit | OAK C_7_UNIT 3 | 1978-01-01
Participating Unit | OAK L_1_GTG1 | 1991-10-21
Participating Unit | OAKWD_6_QF | 2017-12-12
Participating Unit | OAKWD_6_ZEPHWD | 2014-02-07
Participating Unit | OASIS_6_AR4SR1 | 2024-05-20
Participating Unit | OASIS_6_AR4SR2 | 2023-12-22
Participating Unit | OASIS_6_AR4SR3 | 2023-12-08
Participating Unit | OASIS_6_AR8SR1 | 2023-06-28
Participating Unit | OASIS_6_AR8SR2 | 2023-06-28
Participating Unit | OASIS_6_AR8SR3 | 2024-06-18
Participating Unit | OASIS_6_GBDSR4 | 2018-08-25
Participating Unit | OASIS_6_LPPSR1 | 2022-07-25
Participating Unit | OASIS_6_MA4SR1 | 2024-05-20
Participating Unit | OASIS_6_SOLAR1 | 2015-12-09
Participating Unit | OASIS_6_SOLAR2 | 2016-01-19
Participating Unit | OASIS_6_SOLAR3 | 2017-08-11
Participating Unit | OASIS_6_VINSR1 | 2023-10-30
Non-Participating | OBERON_5_O1BBT1
Non-Participating | OBERON_5_O1BBT2
Participating Unit | OBERON_5_O1BBX2 | 2023-11-03
Non-Participating | OBERON_5_O1SSR1
Non-Participating | OBERON_5_O1SSR2
Participating Unit | OBERON_5_O1SSR3 | 2023-11-03
Participating Unit | OBERON_5_O1SSX2 | 2023-11-03
Non-Participating | OBERON_5_O2BBT3
Non-Participating | OBERON_5_O2BBT4
Participating Unit | OBERON_5_O2BBX2 | 2023-11-03
Participating Unit | OBERON_5_O2SSR4 | 2023-11-08
Participating Unit | OBERON_5_O2SSR5 | 2023-11-08
Participating Unit | OCOTLO_6_OCWSB1 | 2023-09-01
Participating Unit | OCTILO_5_WIND | 2013-07-30
Non-Participating | OGROVE_6_CTG1
Non-Participating | OGROVE_6_CTG2
Participating Unit | OGROVE_6_PL1X2 | 2010-06-16
Participating Unit | OILFLD_7_QFUNTS | 2013-09-16
Participating Unit | OLDRIV_6_BIOGAS | 2014-03-10
Participating Unit | OLDRIV_6_CESDBM | 2018-02-02
Participating Unit | OLDRIV_6_LKVBM1 | 2018-02-02
Participating Unit | OLDRV1_6_SOLAR | 2014-12-30
Participating Unit | OLINDA_2_COYCRK | 1979-02-21
Participating Unit | OLINDA_2_LNDFL2 | 2012-11-01
Participating Unit | OLINDA_7_BLKSND | 2000-06-01
Participating Unit | OLIVEP_1_SOLAR | 2013-06-22
Participating Unit | OLIVEP_1_SOLAR2 | 2014-10-01
Participating Unit | OLSEN_2_UNIT | 1990-01-03
Participating Unit | OMAR_2_UNIT 1 | 1985-05-01
Participating Unit | OMAR_2_UNIT 2 | 1985-05-01
Participating Unit | OMAR_2_UNIT 3 | 1985-05-01
Participating Unit | OMAR_2_UNIT 4 | 1985-05-01
Non-Participating | ONLLPP_6_UNIT 1
Non-Participating | ONLLPP_6_UNIT 2
Non-Participating | ONLLPP_6_UNIT 3
Non-Participating | ONLLPP_6_UNIT 4
Non-Participating | ONLLPP_6_UNIT 5
Non-Participating | ONLLPP_6_UNIT 6
Participating Unit | ONLLPP_6_UNITS | 2017-11-30
Participating Unit | ORLND_6_SOLAR1 | 2016-03-23
Participating Unit | ORMOND_7_UNIT 1 | 1971-01-01
Participating Unit | ORMOND_7_UNIT 2 | 1971-01-01
Participating Unit | OROLOM_1_SOLAR1 | 2017-01-28
Participating Unit | OROLOM_1_SOLAR2 | 2017-01-28
Participating Unit | OROVIL_6_UNIT | 1989-12-18
Participating Unit | ORTGA_6_LSLSB1
Participating Unit | ORTGA_6_MCDBT1
Participating Unit | ORTGA_6_ME1SL1 | 2018-04-12
Participating Unit | OSO_6_NSPIN | 2009-03-31
Participating Unit | OTAY_6_ECVBT1 | 2024-10-29
Participating Unit | OTAY_6_ECVBT2 | 2024-12-09
Participating Unit | OTAY_6_PL1X2 | 2006-06-08
Non-Participating | OTMESA_2_CTG1
Non-Participating | OTMESA_2_CTG2
Participating Unit | OTMESA_2_PL1X3 | 2009-10-02
Non-Participating | OTMESA_2_STG3
Participating Unit | OXBOW_6_DRUM | 1966-01-01
Participating Unit | OXMTN_6_LNDFIL | 2009-04-01
Participating Unit | PACLUM_6_UNIT | 2017-06-01
Participating Unit | PADUA_2_ONTARO | 1902-01-01
Participating Unit | PADUA_2_SOLAR1 | 2015-06-02
Participating Unit | PADUA_6_MWDSDM | 1981-01-01
Participating Unit | PADUA_6_QF | 1984-01-01
Participating Unit | PADUA_7_SDIMAS | 1986-01-28
Participating Unit | PAIGES_6_SOLAR | 2017-03-09
Participating Unit | PALA_6_PGCBT1 | 2024-03-14
Participating Unit | PALOMR_2_PL1X3 | 2005-10-14
Non-Participating | PALOMR_7_CTG1
Non-Participating | PALOMR_7_CTG2
Non-Participating | PALOMR_7_STG3
Participating Unit | PALSEL_6_PLSBT1 | 2024-06-20
Participating Unit | PALSEL_6_PLSSR1 | 2024-06-20
Participating Unit | PANERO_2_MWPWD1 | 2024-06-19
Non-Participating | PARDEB_2_UNIT 1
Non-Participating | PARDEB_2_UNIT 2
Non-Participating | PARDEB_2_UNIT 3
Participating Unit | PARDEB_6_UNITS | 1930-01-01
Participating Unit | PARDSE_6_PESBT1 | 2024-05-21
Participating Unit | PASTSR_2_PSESR1
Participating Unit | PBLOSM_2_SOLAR | 2016-12-29
Participating Unit | PEABDY_2_LNDFIL | 2013-07-09
Participating Unit | PEABDY_2_LNDFL1 | 2016-04-07
Participating Unit | PEARBL_2_NSPIN | 2009-03-31
Participating Unit | PEASE_1_TBEBT1 | 2022-06-01
Participating Unit | PEORIA_1_SOLAR | 2013-12-23
Participating Unit | PERGRN_2_PRSBT1 | 2025-04-09
Participating Unit | PGCC_1_PDRP100
Participating Unit | PGEB_2_PDRP100
Participating Unit | PGEB_2_PDRP101
Participating Unit | PGEB_2_PDRP102
Participating Unit | PGEB_2_PDRP103
Participating Unit | PGEB_2_PDRP104
Participating Unit | PGEB_2_PDRP105
Participating Unit | PGEB_2_PDRP107
Participating Unit | PGEB_2_PDRP111
Participating Unit | PGEB_2_PDRP112
Participating Unit | PGEB_2_PDRP113
Participating Unit | PGF1_2_PDRP104
Participating Unit | PGF1_2_PDRP105
Participating Unit | PGF1_2_PDRP106
Participating Unit | PGF1_2_PDRP107
Participating Unit | PGF1_2_PDRP108
Participating Unit | PGF1_2_PDRP109
Participating Unit | PGF1_2_PDRP110
Participating Unit | PGF1_2_PDRP111
Participating Unit | PGF1_2_PDRP116
Participating Unit | PGF1_2_PDRP120
Participating Unit | PGF1_2_PDRP127
Participating Unit | PGNB_2_PDRP101
Participating Unit | PGP2_2_PDRP101
Participating Unit | PGSB_1_PDRP101
Participating Unit | PGSB_1_PDRP102
Participating Unit | PGSB_1_PDRP103
Participating Unit | PGSB_1_PDRP104
Participating Unit | PGSB_1_PDRP106
Participating Unit | PGSB_1_PDRP111
Participating Unit | PGSB_1_PDRPCON01
Participating Unit | PGSB_1_PDRPCUR01
Participating Unit | PGSF_2_PDRP100
Participating Unit | PGSI_1_PDRP100
Participating Unit | PGSI_1_PDRP101
Participating Unit | PHOENX_1_UNIT | 1940-01-01
Non-Participating | PINFLT_7_UNIT 1
Non-Participating | PINFLT_7_UNIT 2
Non-Participating | PINFLT_7_UNIT 3
Participating Unit | PINFLT_7_UNITS | 1984-01-01
Participating Unit | PIOPIC_2_CTG1 | 2016-11-03
Participating Unit | PIOPIC_2_CTG2 | 2016-11-03
Participating Unit | PIOPIC_2_CTG3 | 2016-11-03
Participating Unit | PIT1_6_FRIVRA | 2014-03-05
Participating Unit | PIT1_7_UNIT 1 | 1922-01-01
Participating Unit | PIT1_7_UNIT 2 | 1922-01-01
Participating Unit | PIT3_7_PL1X3 | 1925-01-01
Non-Participating | PIT3_7_UNIT 1
Non-Participating | PIT3_7_UNIT 2
Non-Participating | PIT3_7_UNIT 3
Participating Unit | PIT4_7_PL1X2 | 1955-01-01
Non-Participating | PIT4_7_UNIT 1
Non-Participating | PIT4_7_UNIT 2
Participating Unit | PIT5_7_PL1X2 | 1944-01-01
Participating Unit | PIT5_7_PL3X4 | 1944-01-01
Participating Unit | PIT5_7_QFUNTS | 1987-08-15
Non-Participating | PIT5_7_UNIT 1
Non-Participating | PIT5_7_UNIT 2
Non-Participating | PIT5_7_UNIT 3
Non-Participating | PIT5_7_UNIT 4
Participating Unit | PIT6_7_UNIT 1 | 1965-01-01
Participating Unit | PIT6_7_UNIT 2 | 1965-01-01
Participating Unit | PIT7_7_UNIT 1 | 1965-01-01
Participating Unit | PIT7_7_UNIT 2 | 1965-01-01
Participating Unit | PIUTE_6_GNBSR1 | 2018-12-28
Participating Unit | PLACVL_1_CHILIB | 1965-01-01
Participating Unit | PLACVL_1_RCKCRE | 2017-03-29
Participating Unit | PLAINV_6_BSOLAR | 2014-11-07
Participating Unit | PLAINV_6_DSOLAR | 2016-12-01
Participating Unit | PLAINV_6_NLRSR1 | 2016-12-31
Participating Unit | PLAINV_6_SOLAR3 | 2015-11-30
Participating Unit | PLAINV_6_SOLARC | 2016-05-06
Participating Unit | PLMSSR_6_HISIER | 2010-04-22
Participating Unit | PLSNTG_7_LNCLND | 1985-01-01
Participating Unit | PMDLET_6_SOLAR1 | 2015-07-31
Participating Unit | PMPJCK_1_RB2SLR | 2016-12-29
Participating Unit | PMPJCK_1_SOLAR1 | 2015-01-27
Participating Unit | PMPJCK_1_SOLAR2 | 2016-12-21
Non-Participating | PNCHEG_2_CTG1
Non-Participating | PNCHEG_2_CTG2
Non-Participating | PNCHEG_2_CTG3
Non-Participating | PNCHEG_2_CTG4
Participating Unit | PNCHEG_2_PL1X4 | 2009-05-27
Non-Participating | PNCHPP_1_CTG1
Non-Participating | PNCHPP_1_CTG2
Participating Unit | PNCHPP_1_PL1X2 | 2009-05-03
Participating Unit | PNCHVS_2_SOLAR | 2018-11-26
Non-Participating | PNCHVS_2_SOLARA
Non-Participating | PNCHVS_2_SOLARB
Participating Unit | PNOCHE_1_PL1X2 | 2005-06-14
Participating Unit | PNOCHE_1_UNITA1 | 2001-12-27
Non-Participating | PNOCHE_7_CTG1
Non-Participating | PNOCHE_7_ICE2
Participating Unit | POEPH_7_UNIT 1 | 1958-01-01
Participating Unit | POEPH_7_UNIT 2 | 1958-01-01
Participating Unit | POLRIS_2_ASEBT1 | 2023-12-29
Participating Unit | POLRIS_2_ASESR1 | 2023-12-29
Participating Unit | POLRIS_2_ASRBT1 | 2024-03-27
Participating Unit | POLRIS_2_ASRSR1 | 2024-03-27
Participating Unit | POME_6_POMBT1
Participating Unit | PRCTVY_1_MIGBT1 | 2018-12-12
Participating Unit | PRIMM_2_SOLAR1 | 2016-08-23
Non-Participating | PRIMM_2_SOLRA1
Non-Participating | PRIMM_2_SOLRB1
Participating Unit | PRIMM_2_SSSBT1 | 2025-04-01
Participating Unit | PROXSR_2_PROSR1 | 2024-06-11
Participating Unit | PROXSR_2_PS1BT1 | 2024-04-08
Participating Unit | PROXSR_2_PS1BT2 | 2024-05-07
Participating Unit | PROXSR_2_PS1SR2 | 2024-05-07
Participating Unit | PROXSR_2_PS2BT3 | 2024-04-11
Participating Unit | PSWEET_1_STCRUZ | 2010-02-06
Participating Unit | PUTHCR_1_PCNSB1 | 2022-10-15
Participating Unit | PUTHCR_1_SOLAR1 | 2014-12-19
Participating Unit | PVERDE_5_SCEDYN | 2009-03-31
Participating Unit | PWEST_1_UNIT | 2009-03-31
Non-Participating | RALSTN_7_UNIT 1
Participating Unit | RAMON_2_SCEDYN | 2014-10-31
Participating Unit | RANCHO_2_SMUDSYSDYN | 2017-03-01
Participating Unit | RATSKE_2_NROSR1 | 2019-06-11
Participating Unit | RATSKE_2_RBSSB1 | 2022-10-18
Participating Unit | RATSKE_2_RBSSB2 | 2022-10-18
Participating Unit | RATSKE_2_WAVBT1 | 2025-04-16
Participating Unit | RCKCRK_7_UNIT 1 | 1950-01-01
Participating Unit | RCKCRK_7_UNIT 2 | 1950-01-01
Participating Unit | RDWAY_1_CREST | 2016-09-14
Participating Unit | RDWAY_1_SCKSR1 | 2023-07-28
Participating Unit | RDWAY_1_WA2SR3 | 2024-01-15
Participating Unit | RDWAY_1_WAISR2 | 2024-05-28
Participating Unit | RECTOR_2_CREST | 2016-12-23
Participating Unit | RECTOR_2_IVANPV | 2022-01-28
Participating Unit | RECTOR_2_KAWEAH | 1913-01-01
Participating Unit | RECTOR_2_KAWH 1 | 1929-01-01
Participating Unit | RECTOR_2_QF | 2020-05-18
Participating Unit | RECTOR_2_TFDBM1 | 2019-01-07
Participating Unit | RECTOR_2_VISSR1 | 2024-04-03
Participating Unit | RECTOR_7_TULARE | 1998-05-08
Participating Unit | REDBLF_6_UNIT | 2001-08-11
Participating Unit | REDMAN_2_SOLAR | 2017-08-25
Participating Unit | REDMAN_6_AVSSR1 | 2019-02-04
Participating Unit | REEDLY_6_SOLAR | 2014-06-17
Participating Unit | RENWD_1_QF | 2013-01-08
Participating Unit | RETAKE_2_SS2SR5
Participating Unit | RETAKE_2_SS2SR6
Non-Participating | REXFRD_2_RSFBT1
Non-Participating | REXFRD_2_RSFBT2
Participating Unit | REXFRD_2_RSFBX2 | 2025-02-21
Non-Participating | REXFRD_2_RSFSR1
Non-Participating | REXFRD_2_RSFSR2
Participating Unit | REXFRD_2_RSFSX2 | 2025-02-21
Participating Unit | RICHMN_1_CHVSR2 | 2017-12-21
Participating Unit | RICHMN_1_SOLAR | 2017-12-21
Participating Unit | RICHMN_7_BAYENV | 1985-01-01
Participating Unit | RIOBRV_6_UNIT 1 | 1989-05-18
Participating Unit | RIOOSO_1_QF | 1984-01-01
Participating Unit | RNDMTN_2_SLSPHY1 | 2017-08-10
Participating Unit | RNDSBG_1_HZASR1 | 2019-11-11
Participating Unit | ROLLIN_6_UNIT | 1980-01-01
Participating Unit | ROMOLA_5_MPBBT1 | 2024-09-20
Participating Unit | ROMOLA_5_MPBBT2 | 2024-09-20
Participating Unit | ROMOLA_5_MPBBT3 | 2024-09-20
Participating Unit | ROMOLA_5_MPBBT4 | 2024-09-20
Participating Unit | ROMOLA_5_MPBBT5 | 2025-06-30
Participating Unit | ROSMDW_2_WIND1 | 2012-07-20
Participating Unit | ROSMND_6_SOLAR | 2017-04-22
Participating Unit | RSMNDS_2_CSRBT1 | 2025-08-01
Participating Unit | RSMNDS_2_CSRBT2 | 2025-08-01
Participating Unit | RSMNDS_2_CSRSR1 | 2025-08-01
Participating Unit | RSMNDS_2_CSRSR2 | 2025-07-25
Participating Unit | RSMNDS_2_RSEBT1 | 2025-08-06
Participating Unit | RSMNDS_2_RSESR1 | 2025-08-12
Participating Unit | RSMSLR_6_SOLAR1 | 2013-12-20
Participating Unit | RSMSLR_6_SOLAR2 | 2013-12-20
Participating Unit | RTEDDY_2_RWSBT1 | 2024-05-02
Participating Unit | RTEDDY_2_RWSBT2 | 2024-05-02
Participating Unit | RTEDDY_2_RWSBT3 | 2024-05-09
Participating Unit | RTEDDY_2_RWSBT4 | 2024-05-02
Participating Unit | RTEDDY_2_RWSBT5 | 2024-05-03
Participating Unit | RTEDDY_2_SC1SR3 | 2020-12-21
Participating Unit | RTEDDY_2_SEBSR3 | 2020-12-21
Participating Unit | RTEDDY_2_SEBSR4 | 2020-12-21
Participating Unit | RTEDDY_2_SOLAR1 | 2016-12-22
Participating Unit | RTEDDY_2_SOLAR2 | 2016-12-22
Participating Unit | RTEDDY_2_SPASR4 | 2020-12-21
Participating Unit | RTEDDY_2_SRXSR4 | 2020-12-21
Participating Unit | RTREE_2_WIND1 | 2015-01-12
Participating Unit | RTREE_2_WIND2 | 2015-01-12
Participating Unit | RTREE_2_WIND3 | 2015-06-25
Non-Participating | RUSCTY_2_CTG1
Non-Participating | RUSCTY_2_CTG2
Non-Participating | RUSCTY_2_STG
Participating Unit | RUSCTY_2_UNITS | 2013-08-08
Participating Unit | RUSSELL_2_SOLANO1 | 2024-02-06
Non-Participating | RUSSLL_2_SMUD
Non-Participating | RUSSLL_2_SMUD2
Participating Unit | RVRVEW_1_UNITA1 | 2003-05-02
Participating Unit | RVSIDE_2_RERCU3 | 2011-04-01
Participating Unit | RVSIDE_2_RERCU4 | 2011-04-01
Participating Unit | RVSIDE_6_RERCU1 | 2006-06-01
Participating Unit | RVSIDE_6_RERCU2 | 2006-06-01
Participating Unit | RVSIDE_6_SOLAR1 | 2015-09-09
Participating Unit | RVSIDE_6_SPRING | 2002-06-13
Non-Participating | RVSIDE_7_SPRGU1
Non-Participating | RVSIDE_7_SPRGU2
Non-Participating | RVSIDE_7_SPRGU3
Non-Participating | RVSIDE_7_SPRGU4
Participating Unit | S_RITA_6_SOLAR1 | 2015-05-28
Participating Unit | SALIRV_2_UNIT | 1991-10-11
Non-Participating | SALTSP_7_UNIT 1
Non-Participating | SALTSP_7_UNIT 2
Participating Unit | SALTSP_7_UNITS | 1931-01-01
Participating Unit | SAMPSN_6_KELCO1 | 2014-03-05
Participating Unit | SANBRN_2_EESSB2 | 2023-11-09
Participating Unit | SANBRN_2_ES1BT3 | 2022-04-13
Participating Unit | SANBRN_2_ES2SB3 | 2022-04-13
Participating Unit | SANBRN_2_ESABT1 | 2021-11-19
Participating Unit | SANBRN_2_ESBBT1 | 2021-11-01
Participating Unit | SANBRN_2_SS2BT3 | 2023-10-11
Participating Unit | SANBRN_2_SS2BT4 | 2023-11-16
Participating Unit | SANBRN_2_SS2SB4 | 2023-07-11
Non-Participating | SANDLT_2_STGA
Non-Participating | SANDLT_2_STGB
Participating Unit | SANDLT_2_SUNITS | 2014-12-04
Participating Unit | SANDRN_2_SS1SR1 | 2024-12-11
Participating Unit | SANDRN_2_SS2SR2 | 2024-11-05
Non-Participating | SANITR_6_CTG1
Non-Participating | SANITR_6_CTG2
Non-Participating | SANITR_6_CTG3
Non-Participating | SANITR_6_STG4
Participating Unit | SANITR_6_UNITS | 2009-03-31
Participating Unit | SANLOB_1_LNDFIL | 2013-07-18
Participating Unit | SANLOB_1_OSFBM1 | 2019-07-11
Participating Unit | SANTEE_1_SABBT1
Non-Participating | SANTFG_7_UNIT 1
Non-Participating | SANTFG_7_UNIT 2
Participating Unit | SANTFG_7_UNITS | 1984-03-14
Participating Unit | SANTGO_2_LNDFL1 | 2016-04-12
Participating Unit | SANWD_1_QF | 1983-03-01
Participating Unit | SAUGUS_2_SPESBT1 | 2024-03-16
Participating Unit | SAUGUS_6_CREST | 2017-10-11
Participating Unit | SAUGUS_6_MWDFTH | 1981-01-01
Participating Unit | SAUGUS_6_QF | 1987-01-01
Participating Unit | SAUGUS_7_CHIQCN | 2010-11-23
Participating Unit | SBERDO_2_PSP3 | 2005-12-10
Participating Unit | SBERDO_2_PSP4 | 2006-01-19
Participating Unit | SBERDO_2_SNTANA | 2009-03-31
Participating Unit | SBERDO_6_MILLCK | 2009-03-31
Non-Participating | SBERDO_7_CT3A
Non-Participating | SBERDO_7_CT3B
Non-Participating | SBERDO_7_CT4A
Non-Participating | SBERDO_7_CT4B
Non-Participating | SBERDO_7_STG3
Non-Participating | SBERDO_7_STG4
Participating Unit | SCARLT_2_SS2BT1 | 2024-12-11
Participating Unit | SCARLT_2_SS2SR1 | 2024-12-21
Participating Unit | SCARLT_2_SSABT1 | 2024-05-03
Participating Unit | SCARLT_2_SSASR1 | 2024-05-03
Participating Unit | SCARLT_2_SSBBT1 | 2024-05-03
Participating Unit | SCARLT_2_SSBSR1 | 2024-05-02
Participating Unit | SCEC_1_DERP01 | 2025-02-21
Participating Unit | SCEC_1_PDRP100
Participating Unit | SCEC_1_PDRP101
Participating Unit | SCEC_1_PDRP102
Participating Unit | SCEC_1_PDRP103
Participating Unit | SCEC_1_PDRP104
Participating Unit | SCEC_1_PDRP105
Participating Unit | SCEC_1_PDRP106
Participating Unit | SCEC_1_PDRP107
Participating Unit | SCEC_1_PDRP108
Participating Unit | SCEC_1_PDRP109
Participating Unit | SCEC_1_PDRP110
Participating Unit | SCEC_1_PDRP111
Participating Unit | SCEC_1_PDRP113
Participating Unit | SCEC_1_PDRP114
Participating Unit | SCEC_1_PDRP115
Participating Unit | SCEC_1_PDRP116
Participating Unit | SCEC_1_PDRP117
Participating Unit | SCEC_1_PDRP118
Participating Unit | SCEC_1_PDRP119
Participating Unit | SCEC_1_PDRP120
Participating Unit | SCEC_1_PDRP121
Participating Unit | SCEC_1_PDRP122
Participating Unit | SCEC_1_PDRP124
Participating Unit | SCEC_1_PDRP125
Participating Unit | SCEC_1_PDRP126
Participating Unit | SCEC_1_PDRP127
Participating Unit | SCEC_1_PDRP128
Participating Unit | SCEC_1_PDRP129
Participating Unit | SCEC_1_PDRP130
Participating Unit | SCEC_1_PDRP131
Participating Unit | SCEC_1_PDRP132
Participating Unit | SCEC_1_PDRP133
Participating Unit | SCEC_1_PDRP134
Participating Unit | SCEC_1_PDRP135
Participating Unit | SCEC_1_PDRP136
Participating Unit | SCEC_1_PDRP137
Participating Unit | SCEC_1_PDRP138
Participating Unit | SCEC_1_PDRP139
Participating Unit | SCEC_1_PDRP140
Participating Unit | SCEC_1_PDRP141
Participating Unit | SCEC_1_PDRP142
Participating Unit | SCEC_1_PDRP143
Participating Unit | SCEC_1_PDRP144
Participating Unit | SCEC_1_PDRP145
Participating Unit | SCEC_1_PDRP146
Participating Unit | SCEC_1_PDRP147
Participating Unit | SCEC_1_PDRP148
Participating Unit | SCEC_1_PDRP149
Participating Unit | SCEC_1_PDRP150
Participating Unit | SCEC_1_PDRP151
Participating Unit | SCEC_1_PDRP152
Participating Unit | SCEC_1_PDRP153
Participating Unit | SCEC_1_PDRP154
Participating Unit | SCEC_1_PDRP155
Participating Unit | SCEC_1_PDRP156
Participating Unit | SCEC_1_PDRP157
Participating Unit | SCEC_1_PDRP158
Participating Unit | SCEC_1_PDRP159
Participating Unit | SCEC_1_PDRP160
Participating Unit | SCEC_1_PDRP161
Participating Unit | SCEC_1_PDRP162
Participating Unit | SCEC_1_PDRP163
Participating Unit | SCEC_1_PDRP171
Participating Unit | SCEC_1_PDRP173
Participating Unit | SCEC_1_PDRP175
Participating Unit | SCEC_1_PDRP178
Participating Unit | SCEC_1_PDRP179
Participating Unit | SCEC_1_PDRP181
Participating Unit | SCEC_1_PDRP183
Participating Unit | SCEC_1_PDRP193
Participating Unit | SCEC_1_PDRP195
Participating Unit | SCEC_1_PDRP199
Participating Unit | SCEN_6_PDRP101
Participating Unit | SCEN_6_PDRP102
Participating Unit | SCEN_6_PDRP104
Participating Unit | SCEN_6_PDRP105
Participating Unit | SCEN_6_PDRP106
Participating Unit | SCEN_6_PDRP109
Participating Unit | SCEN_6_PDRP113
Participating Unit | SCEW_2_PDRP100
Participating Unit | SCEW_2_PDRP101
Participating Unit | SCEW_2_PDRP102
Participating Unit | SCEW_2_PDRP103
Participating Unit | SCEW_2_PDRP104
Participating Unit | SCEW_2_PDRP105
Participating Unit | SCEW_2_PDRP106
Participating Unit | SCEW_2_PDRP107
Participating Unit | SCEW_2_PDRP108
Participating Unit | SCEW_2_PDRP109
Participating Unit | SCEW_2_PDRP110
Participating Unit | SCEW_2_PDRP111
Participating Unit | SCEW_2_PDRP112
Participating Unit | SCEW_2_PDRP114
Participating Unit | SCEW_2_PDRP116
Participating Unit | SCEW_2_PDRP117
Participating Unit | SCEW_2_PDRP118
Participating Unit | SCEW_2_PDRP119
Participating Unit | SCEW_2_PDRP120
Participating Unit | SCEW_2_PDRP121
Participating Unit | SCEW_2_PDRP122
Participating Unit | SCEW_2_PDRP123
Participating Unit | SCEW_2_PDRP124
Participating Unit | SCEW_2_PDRP125
Participating Unit | SCEW_2_PDRP130
Participating Unit | SCEW_2_PDRP131
Participating Unit | SCEW_2_PDRP133
Participating Unit | SCEW_2_PDRP141
Participating Unit | SCEW_2_PDRP159
Participating Unit | SCEW_2_PDRP160
Participating Unit | SCEW_2_PDRP163
Participating Unit | SCEW_2_PDRP167
Participating Unit | SCEW_2_PDRP168
Participating Unit | SCEW_2_PDRP171
Participating Unit | SCEW_2_PDRP172
Participating Unit | SCEW_2_PDRP173
Participating Unit | SCEW_2_PDRP174
Participating Unit | SCEW_2_PDRP175
Participating Unit | SCEW_2_PDRP179
Participating Unit | SCEW_2_PDRP183
Participating Unit | SCEW_2_PDRP186
Participating Unit | SCEW_2_PDRP190
Participating Unit | SCEW_2_PDRP234
Participating Unit | SCHLTE_1_PL1X3 | 2012-10-31
Non-Participating | SCHLTE_1_UNITA1
Non-Participating | SCHLTE_1_UNITA2
Non-Participating | SCHLTE_1_UNITA3
Participating Unit | SCHNDR_1_FIVPTS | 2011-10-07
Participating Unit | SCHNDR_1_WSTSDE | 2011-09-13
Participating Unit | SDG1_1_PDRP100
Participating Unit | SDG1_1_PDRP101
Participating Unit | SDG1_1_PDRP102
Participating Unit | SDG1_1_PDRP103
Participating Unit | SDG1_1_PDRP104
Participating Unit | SDG1_1_PDRP105
Participating Unit | SDG1_1_PDRP106
Participating Unit | SDG1_1_PDRP111
Participating Unit | SDG1_1_PDRP113
Participating Unit | SDG1_1_PDRP114
Participating Unit | SDG1_1_PDRP117
Participating Unit | SDG1_1_PDRP118
Participating Unit | SDG1_1_PDRP119
Participating Unit | SDG1_1_PDRP120
Participating Unit | SDG1_1_PDRP121
Participating Unit | SDG1_1_PDRP122
Participating Unit | SDG1_1_PDRP123
Participating Unit | SEARLS_1_TS3SR1 | 2023-04-13
Participating Unit | SEARLS_7_ARGUS | 2013-11-15
Participating Unit | SEAWND_2_AMWWD1 | 2025-03-14
Participating Unit | SEGS_1_SR2SL2 | 2017-06-02
Participating Unit | SENTNL_2_CTG1 | 2013-05-06
Participating Unit | SENTNL_2_CTG2 | 2013-05-06
Participating Unit | SENTNL_2_CTG3 | 2013-05-06
Participating Unit | SENTNL_2_CTG4 | 2013-05-06
Participating Unit | SENTNL_2_CTG5 | 2013-05-06
Participating Unit | SENTNL_2_CTG6 | 2013-05-06
Participating Unit | SENTNL_2_CTG7 | 2013-05-06
Participating Unit | SENTNL_2_CTG8 | 2013-05-06
Participating Unit | SGREGY_6_SANGER | 2017-06-01
Participating Unit | SHAFTR_1_HWYSR1 | 2025-01-07
Participating Unit | SHANDN_2_SBBBM1 | 2023-06-30
Participating Unit | SHELRF_1_UNITS | 1995-01-01
Non-Participating | SHELRF_7_UNIT 1
Non-Participating | SHELRF_7_UNIT 2
Non-Participating | SHELRF_7_UNIT 3
Participating Unit | SHUTLE_6_RUISR1 | 2024-04-29
Participating Unit | SHUTLE_6_RUISR2 | 2024-04-29
Participating Unit | SHUTLE_6_RUISR3 | 2024-04-29
Participating Unit | SIERRA_1_UNITS | 1989-02-24
Participating Unit | SIGHEB_6_HE2SCEDYN | 2022-12-20
Participating Unit | SIGHEB_6_MIRDYN | 2021-12-29
Participating Unit | SISPRG_2_DS3BT1 | 2023-11-15
Participating Unit | SISPRG_2_DS3BT2 | 2023-08-24
Participating Unit | SISPRG_2_DS3BT3 | 2023-09-05
Participating Unit | SISPRG_2_DS3BT4 | 2023-08-24
Participating Unit | SISPRG_2_DS3SR1 | 2023-10-24
Participating Unit | SISPRG_2_DS3SR2 | 2023-08-24
Participating Unit | SISPRG_2_DS3SR3 | 2023-09-05
Participating Unit | SISPRG_2_DS3SR4 | 2023-07-14
Participating Unit | SISQUC_1_SMARIA | 2010-09-27
Participating Unit | SJOAQN_6_NFCBM1
Participating Unit | SKERN_6_SOLAR1 | 2015-04-07
Participating Unit | SKERN_6_SOLAR2 | 2017-01-05
Participating Unit | SLATE_2_SLASR1 | 2021-11-12
Participating Unit | SLATE_2_SLASR2 | 2022-03-15
Participating Unit | SLATE_2_SLASR3 | 2022-03-15
Participating Unit | SLATE_2_SLASR4 | 2022-03-15
Participating Unit | SLATE_2_SLASR5 | 2022-03-15
Participating Unit | SLRMS3_2_SRMSR1 | 2019-12-06
Participating Unit | SLST13_2_SOLAR1 | 2015-11-30
Participating Unit | SLSTR1_2_SOLAR1 | 2014-10-22
Non-Participating | SLSTR1_2_SOLR1A
Non-Participating | SLSTR1_2_SOLR1B
Participating Unit | SLSTR2_2_SOLAR2 | 2014-07-31
Non-Participating | SLSTR2_2_SOLR2A
Non-Participating | SLSTR2_2_SOLR2B
Non-Participating | SLUISP_2_UNIT 1
Non-Participating | SLUISP_2_UNIT 2
Non-Participating | SLUISP_2_UNIT 3
Non-Participating | SLUISP_2_UNIT 4
Non-Participating | SLUISP_2_UNIT 5
Non-Participating | SLUISP_2_UNIT 6
Non-Participating | SLUISP_2_UNIT 7
Non-Participating | SLUISP_2_UNIT 8
Participating Unit | SLUISP_2_UNITS | 1967-01-01
Participating Unit | SLYCRK_1_UNIT 1 | 1983-01-01
Participating Unit | SMPRIP_1_SMPSON | 1988-04-19
Participating Unit | SMRCOS_6_LNDFIL | 2011-05-20
Participating Unit | SMUDGO_7_UNIT 1 | 1983-01-01
Participating Unit | SMYRNA_1_DL1SR1 | 2017-12-28
Participating Unit | SNCLRA_2_BWEBT1
Participating Unit | SNCLRA_2_HOWLNG | 2013-06-14
Participating Unit | SNCLRA_2_SILBT1 | 2021-04-01
Participating Unit | SNCLRA_2_SPRHYD | 2016-04-19
Participating Unit | SNCLRA_2_UNIT | 2018-04-26
Participating Unit | SNCLRA_2_UNIT1 | 2016-04-15
Participating Unit | SNCLRA_2_VESBT1 | 2021-04-20
Participating Unit | SNCLRA_6_OXGEN | 2020-06-01
Participating Unit | SNCLRA_6_PROCGN | 1998-11-17
Participating Unit | SNCLRA_6_QF | 1987-01-01
Participating Unit | SNDBAR_7_UNIT 1 | 2017-01-01
Participating Unit | SNMALF_6_UNITS | 1993-04-30
Participating Unit | SNORA_2_SNRSLR | 2015-08-29
Non-Participating | SOLBLU_2_WSBBT1
Non-Participating | SOLBLU_2_WSBBT2
Participating Unit | SOLBLU_2_WSBBX2 | 2023-12-13
Non-Participating | SOLBLU_2_WSBSR1
Non-Participating | SOLBLU_2_WSBSR2
Participating Unit | SOLBLU_2_WSBSX2 | 2023-12-13
Participating Unit | SOUTH_2_UNIT | 1979-01-01
Non-Participating | SPAULD_6_UNIT 1
Non-Participating | SPAULD_6_UNIT 2
Participating Unit | SPAULD_6_UNIT 3 | 1928-01-01
Participating Unit | SPAULD_6_UNIT12 | 1929-01-01
Participating Unit | SPBURN_2_UNIT 1 | 1986-01-01
Participating Unit | SPBURN_7_SNOWMT | 1990-03-28
Participating Unit | SPI LI_2_UNIT 1 | 1986-06-03
Participating Unit | SPIAND_1_ANDSN2 | 2015-09-09
Non-Participating | SPICER_1_UNIT 1
Non-Participating | SPICER_1_UNIT 2
Non-Participating | SPICER_1_UNIT 3
Participating Unit | SPICER_1_UNITS | 1990-01-01
Participating Unit | SPIFBD_1_PL1X2 | 2018-04-12
Participating Unit | SPQUIN_6_SRPCQU | 2018-05-17
Participating Unit | SPRGAP_1_UNIT 1 | 1921-01-01
Participating Unit | SPRGVL_2_CREST | 2017-01-05
Participating Unit | SPRGVL_2_EXETPV | 2022-01-28
Participating Unit | SPRGVL_2_LINDPV | 2022-01-28
Participating Unit | SPRGVL_2_PORTPV | 2022-02-03
Participating Unit | SPRGVL_2_SUCCES | 2024-08-19
Participating Unit | SPRGVL_2_TULE | 2025-02-12
Participating Unit | SPRGVL_2_TULESC | 1909-01-01
Participating Unit | SRAPTA_5_DEAUXL1
Participating Unit | SRAPTA_5_DECBT1
Participating Unit | SRINTL_6_UNIT | 1987-03-10
Participating Unit | STANIS_7_UNIT 1 | 1963-01-01
Non-Participating | STANTN_2_SBEBT3
Non-Participating | STANTN_2_SBEBT4
Participating Unit | STANTN_2_SBEBX2 | 2023-07-19
Participating Unit | STANTN_2_STAGT1 | 2020-05-20
Participating Unit | STANTN_2_STAGT2 | 2020-05-20
Participating Unit | STIGCT_2_LODI | 1996-01-01
Non-Participating | STOILS_1_UNIT 1
Non-Participating | STOILS_1_UNIT 2
Participating Unit | STOILS_1_UNITS | 1992-08-31
Participating Unit | STOREY_2_MDRCH2 | 2016-08-01
Participating Unit | STOREY_2_MDRCH3 | 2016-08-01
Participating Unit | STOREY_2_MDRCH4 | 2016-07-19
Participating Unit | STOREY_7_MDRCHW | 1985-02-02
Participating Unit | STRAUS_1_STRWD1 | 2023-12-20
Participating Unit | STROUD_6_SOLAR | 2011-10-04
Participating Unit | STROUD_6_WWHSR1 | 2019-05-11
Participating Unit | SUMWHT_6_SWSSR1 | 2018-10-11
Participating Unit | SUNCAT_2_A1ABT1 | 2022-08-01
Participating Unit | SUNCAT_2_A1BBT1 | 2022-08-01
Participating Unit | SUNCAT_2_A2ABT2 | 2022-08-16
Participating Unit | SUNCAT_2_A2BSR2 | 2023-10-20
Participating Unit | SUNPND_5_SPSBT1
Participating Unit | SUNPND_5_SPSBT2
Participating Unit | SUNPND_5_SPSSR1
Participating Unit | SUNPND_5_SPSSR2
Participating Unit | SUNRIS_2_PL1X3 | 2001-06-07
Non-Participating | SUNRIS_2_UNIT 1
Non-Participating | SUNRIS_2_UNIT 2
Non-Participating | SUNRIS_2_UNIT 3
Participating Unit | SUNSET_2_UNITS | 1989-12-18
Participating Unit | SUNSHN_2_LNDFL | 2014-09-01
Non-Participating | SUNSHN_2_LNDFL1
Non-Participating | SUNSHN_2_LNDFL2
Non-Participating | SUNSHN_2_LNDFL3
Non-Participating | SUNSHN_2_LNDFL4
Non-Participating | SUNSHN_2_LNDFL5
Participating Unit | SUNSLR_1_SSVSR1 | 2019-12-18
Participating Unit | SUNSPT_2_WNASR1 | 2019-12-18
Participating Unit | SUNST2_5_SS2SR1 | 2021-06-25
Participating Unit | SUNSTR_5_SS1SCEDYN | 2019-11-19
Participating Unit | SUTTER_2_CISO | 2020-07-10
Participating Unit | SYCAMR_2_UNIT 1 | 1987-01-01
Participating Unit | SYCAMR_2_UNIT 2 | 1987-01-01
Participating Unit | SYCAMR_2_UNIT 3 | 1987-01-01
Participating Unit | SYCAMR_2_UNIT 4 | 1987-01-01
Participating Unit | SZWDN_3_SZWX6
Participating Unit | SZWDS_3_SZWX14
Participating Unit | TAHOE_2_THOBT1 | 2025-06-05
Participating Unit | TAHOE_2_THOBT2 | 2025-06-02
Participating Unit | TAHOE_2_THOBT3 | 2025-06-02
Participating Unit | TAHOE_5_THAUXL
Participating Unit | TANHIL_6_SOLART | 1986-01-01
Participating Unit | TBLMTN_6_QF | 1983-01-01
Participating Unit | TECOLOTE_3_WBDYN | 2021-12-01
Participating Unit | TEHAPI_2_PW1WD1 | 2021-03-30
Participating Unit | TEHAPI_2_PW2WD2 | 2021-04-20
Participating Unit | TEHAPI_2_WIND1 | 2021-03-30
Participating Unit | TEHAPI_2_WIND2 | 2021-03-30
Participating Unit | TENGEN_2_PL1X2 | 1990-03-06
Non-Participating | TENGEN_6_UNIT 1
Non-Participating | TENGEN_6_UNIT 2
Non-Participating | TERMEX_2_GTG1
Non-Participating | TERMEX_2_GTG2
Participating Unit | TERMEX_2_PL1X3 | 2003-07-30
Non-Participating | TERMEX_2_STG
Participating Unit | TESLA_1_QF | 1982-01-01
Non-Participating | THERMA_2_UNIT 1
Non-Participating | THERMA_2_UNIT 2
Non-Participating | THERMA_2_UNIT 3
Non-Participating | THERMA_2_UNIT 4
Participating Unit | TIDWTR_2_UNITS | 1987-02-23
Participating Unit | TIFFNY_1_DILLON | 2008-04-18
Non-Participating | TIGRCK_7_UNIT 1
Non-Participating | TIGRCK_7_UNIT 2
Participating Unit | TIGRCK_7_UNITS | 1931-01-01
Participating Unit | TITANS_2_TTSSR1 | 2020-12-17
Participating Unit | TKOPWR_6_HYDRO | 2016-04-27
Participating Unit | TMPLTN_2_SOLAR | 2014-03-05
Participating Unit | TOADTW_6_UNIT | 1986-01-01
Participating Unit | TOPAZ_2_SOLAR | 2014-10-27
Participating Unit | TORTLA_1_SOLAR | 2016-12-16
Participating Unit | TOWNSITE_2_MEADDYN | 2021-12-17
Participating Unit | TRNQL8_2_AMASR1 | 2017-12-26
Participating Unit | TRNQL8_2_AZUSR1 | 2017-12-26
Participating Unit | TRNQL8_2_ROJSR1 | 2018-04-14
Participating Unit | TRNQL8_2_VERSR1 | 2018-04-17
Participating Unit | TRNQLT_2_RETBT1 | 2022-03-16
Participating Unit | TRNQLT_2_SOLAR | 2016-07-28
Participating Unit | TRNSWD_1_QF | 2014-12-22
Participating Unit | TULARE_2_TFCBM1 | 2023-10-27
Participating Unit | TULARE_2_TULBM1 | 2019-12-20
Participating Unit | TULEWD_1_TULWD1 | 2018-01-05
Non-Participating | TULLCK_7_UNIT 1
Non-Participating | TULLCK_7_UNIT 2
Non-Participating | TULLCK_7_UNIT 3
Participating Unit | TULLCK_7_UNITS | 1958-01-01
Participating Unit | TULRLK_6_UTASR1 | 2025-08-27
Participating Unit | TUMBWD_2_WISBT3 | 2024-07-16
Participating Unit | TUMBWD_2_WISBT4 | 2024-08-14
Participating Unit | TUPMAN_1_BIOGAS | 2013-03-20
Participating Unit | TVYVLY_6_KRSHY1 | 2021-09-15
Non-Participating | TWINKL_2_ASCBT1
Non-Participating | TWINKL_2_ASCBT2
Participating Unit | TWINKL_2_ASCBTA
Participating Unit | TWINKL_2_ASCBTB
Non-Participating | TWINKL_2_ASCSR1
Non-Participating | TWINKL_2_ASCSR2
Participating Unit | TWINKL_2_ASCSRA
Participating Unit | TWINKL_2_ASCSRB
Participating Unit | TWISSL_6_PRDSR1
Participating Unit | TWISSL_6_SOLAR | 2012-11-27
Participating Unit | TWISSL_6_SOLAR1 | 2015-05-15
Participating Unit | TX-ELK_6_ECKSR2 | 2019-12-21
Participating Unit | TX-ELK_6_SOLAR1 | 2016-04-02
Participating Unit | TXMCKT_6_UNIT | 1994-10-01
Participating Unit | UKIAH_7_LAKEMN | 2007-07-02
Participating Unit | ULTPCH_1_UCSBT1 | 2025-08-29
Participating Unit | ULTPCH_1_UNIT 1 | 2017-03-01
Participating Unit | ULTPFR_1_UNIT 1 | 2017-09-07
Participating Unit | ULTRCK_2_UNIT | 2017-09-07
Participating Unit | UNOCAL_1_UNITS | 1987-05-21
Participating Unit | UNVRSY_1_UNIT 1 | 1986-01-01
Participating Unit | USWND2_1_WIND1 | 2015-12-18
Participating Unit | USWND2_1_WIND2 | 2015-12-23
Participating Unit | USWND2_1_WIND3 | 2017-11-09
Participating Unit | USWND4_2_UNIT2 | 2018-02-01
Participating Unit | USWNDR_2_LABWD1 | 2019-06-28
Participating Unit | USWPFK_6_FRICK | 2021-07-02
Participating Unit | USWPJR_2_UNITS | 1988-01-01
Participating Unit | VACADX_1_SOLAR | 2013-09-06
Participating Unit | VACADX_1_UNITA1 | 2002-06-21
Participating Unit | VALLEY_5_ORTBT1 | 2025-06-16
Participating Unit | VALLEY_5_PERRIS | 1983-01-01
Participating Unit | VALLEY_5_REDMTN | 1985-01-01
Participating Unit | VALLEY_5_SOLAR1 | 2015-04-13
Participating Unit | VALLEY_5_SOLAR2 | 2015-08-11
Participating Unit | VALTNE_2_AVASR1 | 2019-11-09
Participating Unit | VALTNE_2_TBBBT1 | 2022-12-27
Participating Unit | VALTNE_2_TRSBT1 | 2022-12-27
Participating Unit | VALTNE_2_TSASR1 | 2025-07-02
Participating Unit | VALTNE_2_TSASR2 | 2025-07-02
Participating Unit | VALTNE_2_TSBBT1 | 2025-07-02
Participating Unit | VALTNE_2_TSBBT2 | 2025-07-02
Participating Unit | VEAVST_1_SOLAR | 2017-02-10
Participating Unit | VEDDER_1_SEKERN | 1989-01-31
Participating Unit | VEGA_6_SOLAR1 | 2015-03-23
Participating Unit | VENTSO_6_VENBT1
Participating Unit | VENWD_1_WIND3 | 2021-04-14
Participating Unit | VERNON_6_GONZL1 | 2013-06-13
Participating Unit | VERNON_6_GONZL2 | 2013-06-13
Participating Unit | VERNON_6_MALBRG | 2005-10-17
Non-Participating | VERNON_7_CTG1
Non-Participating | VERNON_7_CTG2
Non-Participating | VERNON_7_STG3
Participating Unit | VESTAL_2_BTNBT1 | 2024-10-19
Participating Unit | VESTAL_2_KERN | 1907-01-01
Participating Unit | VESTAL_2_RTS042 | 2012-11-24
Participating Unit | VESTAL_2_SOLAR1 | 2016-09-15
Participating Unit | VESTAL_2_SOLAR2 | 2016-09-14
Participating Unit | VESTAL_2_TS5SR1 | 2022-04-29
Participating Unit | VESTAL_2_UNIT1 | 2016-06-30
Participating Unit | VESTAL_2_WELLHD | 2013-01-16
Non-Participating | VESTAL_6_KERNU1
Non-Participating | VESTAL_6_KERNU2
Participating Unit | VESTAL_6_QF | 2021-02-05
Participating Unit | VICPAS_2_SLOBT1 | 2024-03-26
Participating Unit | VICPAS_2_SLOSR1 | 2024-03-26
Participating Unit | VICPAS_2_SOCBT1 | 2024-03-26
Participating Unit | VICPAS_2_SOCBT2 | 2024-03-26
Participating Unit | VICPAS_2_SOCSR1 | 2024-03-26
Participating Unit | VICPAS_2_SOCSR2 | 2024-04-02
Participating Unit | VICPAS_2_SOCSR3 | 2024-03-26
Participating Unit | VICPAS_2_VPSBT1 | 2024-03-27
Participating Unit | VICPAS_2_VPSSR1 | 2024-03-26
Participating Unit | VICTOR_1_CREST | 2017-09-13
Participating Unit | VICTOR_1_EXSLRA | 2014-05-07
Participating Unit | VICTOR_1_EXSLRB | 2014-05-07
Participating Unit | VICTOR_1_LMASR1 | 2024-06-25
Participating Unit | VICTOR_1_LMISR2 | 2024-05-28
Participating Unit | VICTOR_1_LRUSR3 | 2024-06-25
Participating Unit | VICTOR_1_LVSLR1 | 2014-11-19
Participating Unit | VICTOR_1_LVSLR2 | 2014-11-22
Participating Unit | VICTOR_1_NUNSR4 | 2024-06-25
Participating Unit | VICTOR_1_SDRSR1 | 2025-07-15
Participating Unit | VICTOR_1_SDRSR2 | 2025-07-15
Participating Unit | VICTOR_1_SLRHES | 2014-08-08
Participating Unit | VICTOR_1_SOLAR1 | 2013-11-18
Participating Unit | VICTOR_1_SOLAR2 | 2015-05-15
Participating Unit | VICTOR_1_SOLAR3 | 2015-07-01
Participating Unit | VICTOR_1_SOLAR4 | 2015-09-03
Participating Unit | VICTOR_1_SWRSR1 | 2025-07-15
Participating Unit | VICTOR_1_SWRSR2 | 2025-07-15
Participating Unit | VICTOR_1_SWRSR3 | 2025-07-15
Participating Unit | VICTOR_1_VDRYFA | 2015-06-12
Participating Unit | VICTOR_1_VDRYFB | 2015-06-12
Participating Unit | VIKING_2_VCBBT1 | 2024-11-11
Participating Unit | VIKING_2_VCSSR1 | 2024-11-11
Participating Unit | VIKING_2_VSHSB1 | 2024-06-08
Participating Unit | VILLPK_2_VALLYV | 1985-01-01
Participating Unit | VILLPK_6_MWDYOR | 1981-01-01
Participating Unit | VISTA_6_QF | 1983-01-01
Participating Unit | VISTRA_5_DALBT1 | 2021-03-23
Participating Unit | VISTRA_5_DALBT2 | 2021-03-23
Participating Unit | VISTRA_5_DALBT3 | 2021-04-06
Participating Unit | VISTRA_5_DALBT4 | 2021-07-28
Participating Unit | VISTRA_5_PLABT1 | 2023-05-13
Participating Unit | VISTRA_5_PLABT2 | 2023-06-01
Participating Unit | VISTRA_5_PLABT3 | 2023-05-16
Participating Unit | VISTRA_5_PLABT4 | 2023-06-02
Participating Unit | VLCNTR_6_VCEBT1 | 2021-11-29
Participating Unit | VLCNTR_6_VCEBT2 | 2021-12-16
Participating Unit | VLCNTR_6_VCSLR | 2016-12-07
Participating Unit | VLCNTR_6_VCSLR1 | 2013-12-31
Participating Unit | VLCNTR_6_VCSLR2 | 2013-12-31
Participating Unit | VLYHOM_7_SSJID | 2013-04-01
Participating Unit | VOLTA_2_UNIT 1 | 1980-01-01
Participating Unit | VOLTA_2_UNIT 2 | 1981-01-01
Participating Unit | VOLTA_6_BAILCK | 1982-05-26
Participating Unit | VOLTA_6_DIGHYD | 2014-07-02
Participating Unit | VOLTA_7_PONHY1 | 2020-03-20
Participating Unit | VOLTA_7_QFUNTS | 2007-03-01
Participating Unit | VOYAGR_2_VOAWD5 | 2021-04-26
Participating Unit | VOYAGR_2_VOYWD1 | 2019-12-30
Participating Unit | VOYAGR_2_VOYWD2 | 2018-12-19
Participating Unit | VOYAGR_2_VOYWD3 | 2018-12-29
Participating Unit | VOYAGR_2_VOYWD4 | 2018-12-29
Participating Unit | VSTAES_6_VESBT1 | 2018-06-26
Participating Unit | WADHAM_6_UNIT | 1989-03-24
Participating Unit | WALCRK_2_CTG1 | 2013-03-21
Participating Unit | WALCRK_2_CTG2 | 2013-03-21
Participating Unit | WALCRK_2_CTG3 | 2013-03-21
Participating Unit | WALCRK_2_CTG4 | 2013-03-29
Participating Unit | WALCRK_2_CTG5 | 2013-04-30
Participating Unit | WALNUT_2_SOLAR | 2012-04-03
Participating Unit | WALNUT_6_HILLGEN | 2017-06-01
Participating Unit | WALNUT_7_WCOVST | 1996-10-05
Participating Unit | WARNE_2_UNIT | 1982-01-01
Non-Participating | WARNE_2_UNIT 1
Non-Participating | WARNE_2_UNIT 2
Participating Unit | WASCO_6_TERSR1 | 2025-01-31
Participating Unit | WAUKNA_1_SOLAR | 2013-08-14
Participating Unit | WAUKNA_1_SOLAR2 | 2015-05-05
Participating Unit | WDFRDF_2_WFFBT1 | 2024-07-25
Participating Unit | WDLEAF_7_UNIT 1 | 1963-01-01
Participating Unit | WEBER_6_FORWRD | 2014-02-05
Participating Unit | WEEDPC_6_KNSSR1 | 2025-01-14
Participating Unit | WESCAN_2_BDSBT1 | 2023-06-23
Participating Unit | WESCN2_2_BDSBT1 | 2024-12-31
Participating Unit | WESCN2_2_BDSBT2 | 2025-07-01
Participating Unit | WESTPT_2_UNIT | 1948-01-01
Participating Unit | WFRESN_1_SOLAR | 2012-12-21
Participating Unit | WHEATL_6_LNDFIL | 2013-09-01
Non-Participating | WHELPP_2_NSPIN
Participating Unit | WHITEH_2_MEADDYN1 | 2020-12-16
Participating Unit | WHITEH_2_MEADDYN2 | 2020-12-16
Participating Unit | WHITEW_5_WWAUXL1
Participating Unit | WHITEW_5_WWRSR1 | 2024-10-23
Participating Unit | WHITNY_6_SOLAR | 2017-04-15
Participating Unit | WHTWTR_1_WINDA1 | 2002-08-31
Participating Unit | WILLMS_6_ARBBM1 | 2022-07-26
Participating Unit | WISE_1_UNIT 1 | 1917-01-01
Participating Unit | WISE_1_UNIT 2 | 1986-01-01
Non-Participating | WISHON_6_UNIT 1
Non-Participating | WISHON_6_UNIT 2
Non-Participating | WISHON_6_UNIT 3
Non-Participating | WISHON_6_UNIT 4
Participating Unit | WISHON_6_UNITS | 1910-01-01
Participating Unit | WISTER_2_WISSR1 | 2022-07-12
Participating Unit | WISTRA_2_WRSSR1 | 2018-11-06
Participating Unit | WLDWD_1_SOLAR1 | 2015-02-19
Participating Unit | WLDWD_1_SOLAR2 | 2017-01-11
Non-Participating | WNDGPP_2_NSPIN
Participating Unit | WNDMAS_2_UNIT 1 | 1983-12-24
Participating Unit | WNDSTR_2_WIND | 2012-01-28
Non-Participating | WNDSTR_2_WIND1
Non-Participating | WNDSTR_2_WIND2
Participating Unit | WOLFSK_1_UNITA1 | 2003-03-22
Participating Unit | WOODWR_1_HYDRO | 2017-06-14
Participating Unit | WRGTSR_2_WSFSR1 | 2019-12-31
Participating Unit | WSENGY_1_UNIT 1 | 2017-12-01
Participating Unit | WSNR_2_CVPDYN | 2017-07-26
Participating Unit | WSNR_2_TESLADYN | 2017-12-13
Participating Unit | WSNR_5_TRCYDYN | 2017-12-13
Participating Unit | WSTWND_2_M89BT2 | 2023-05-25
Participating Unit | WSTWND_2_M89WD2 | 2023-05-25
Participating Unit | WSTWND_2_M90WD2 | 2020-06-02
Participating Unit | WSTWND_2_SBSBT1 | 2023-05-23
Participating Unit | WSTWND_2_SBSBT2 | 2024-09-16
Participating Unit | WSTWND_2_SBSBT3 | 2024-08-13
Participating Unit | YELPIN_2_YP2BT1 | 2023-07-26
Participating Unit | YELPIN_2_YP2BT2 | 2024-05-24
Participating Unit | YELPIN_2_YP2BT3 | 2024-06-04
Participating Unit | YELPIN_2_YP2SR1 | 2023-07-26
Participating Unit | YELPIN_2_YP2SR2 | 2024-06-14
Participating Unit | YELPIN_2_YP2SR3 | 2024-06-27
Participating Unit | YUBACT_1_SUNSWT | 1990-12-27
Participating Unit | YUBACT_6_UNITA1 | 2002-07-26
Participating Unit | ZOND_6_UNIT | 1985-12-30