## Slide 1
RTAC
Relay
Option 1
Schedule
Stored inside the RTAC Registers
Reprogramming required for a new 1-year setting
RTAC
Relay
Option 2
Monitor PCC
Schedule
Send from CSIP G/W to RTAC
Monitor PCC
RTAC
Relay
Option 3
Schedule
Stored inside the RTAC Registers
Reprogramming required for a new 1-year setting
Change Setting Group Command to Relay. Limited by # of setting group Support. 2-6 Second delay for a new setting group to be active (Copy new setting group into Active Setting Group and re-start the logic).
Limited by # of setting groups.
Divide 1 Day into 6 or 12 or 24 blocks as per Relay Support and set active settings group from RTAC based on schedule
RTAC
Relay
Option 4
Change Setting Group Command to Relay. Limited by # of setting group Support. 2-6 Second delay for a new setting group to be active (Copy new setting group into Active Setting Group and re-start the logic).
Limited by # of setting groups.
Divide 1 Day into 6 or 12 or 24 blocks as per Relay Support and set active settings group from RTAC based on schedule
Schedule
Send from CSIP G/W to RTAC
X% Transducer
Error tolerance
X% Transducer
Error tolerance
Monitor PCC
X% Transducer
Error tolerance
X% Transducer
Error tolerance
Monitor PCC
IEC 61850 GOOSE
4 ms Trip Command
OR Mirrored Bits
< 100 ms Logic Loop
IEC 61850 GOOSE
4 ms Trip Command
OR Mirrored Bits
IEC 61850 Setting Group
Command Or Mirrored Bits
IEC 61850 Setting Group
Command Or Mirrored Bits