## Slide 1
Interconnection Process Common Deficiencies and Best Practices
December 7, 2017

## Slide 2: Presenters
PG&E
Rob Chan, Expanded & Standard NEM Programs
Phuoc Tran, Distribution Planning
Dan Brouillard, Service Planning & Design
Tracy Mello, Service Planning & Design
SCE
Rene Valencia, Net Energy Metering Programs
Luis Aguilar, Distribution Engineering
Eduyng Castano, Grid Interconnection
Roger Salas, Tariff Support
SDG&E
Ken Parks, Customer Generation

## Slide 3: Rule 21 Tariff
Approved and enforceable by CPUC, the Rule 21 Tariff describes the Interconnection, Operating, and Metering requirements for those Generating Facilities to be connected to Distribution Provider’s Distribution System and Transmission System over which the California Public Utilities Commission (Commission) has jurisdiction.
The Rule specifies the necessary studies, payments, agreements, and other requirements for interconnection. It contains provisions to ensure non-discriminatory treatment for all customers in the interconnection process.

## Slide 4: Rule 21 Interconnection Process Overview
Planning/Studies
(15-115 BD)
Tender Contract
(15 BD - 30 CD)
Implementation1
(30-200 CD)2
Inspection/Close
(15 CD)2
Review Application
(10 Business Days)
Initial Review
(15 Business Days)
Supplemental Review
(20 Business Days)
Electrical Independence Test
Fail Screen Q -> WDT Cluster
Fail Screen R -> R21 DGSP
Pass Screens Q and R -> System Impact Study
(20 Business Days)
System Impact Study
(60 Business Days)
Interconnection Agreement
(15 Business Days)
Special Facilities Agreement
Engineering Advance
Design and Estimate
Project Construction
Pre Parallel Inspection
(No compliance Timeline)
Issue Permission to Operate
(5 Business Days)
Kickoff
Distribution Group Study Process
2 Windows per Year
March and September
Interconnection Agreement
(30 Calendar Days)
Application1
(10 BD)
1 Customer timeline concerns
2 PG&E Cycle times, not Rule 21 compliance timelines
3 PG&E NEM <=1MW $145 Interconnection Fee; NEM >1MW Fast Track $800, Supplemental $2,500, Detail Study Deposit $10,000, Facilities Study Deposit $10,000 (if requested)
Fast Track3
Independent Study3

## Slide 5: Automated NEM Interconnection Application Process
1) Create MyPartners Account
2) Submit NEM Application in DIIS
3) Sign & Submit Interconnection Agreement
4) City / County Inspection
**Automated Electrical Releases
5) SDG&E Inspection
6) Permission to Operate (PTO) Issued
SDG&E’s automated process has eliminated many of the administrative type application deficiencies that existed prior to its implementation
SDG&E’s <30 kW customers use Fast Track
Customer responsibility
Distribution Interconnection Information System (DIIS)
Process Overview

## Slide 6: Application Phase
Common Deficiency | Best Practice
Discrepancies with Customer information | Use Customer information from the most recent utility bill
Make and model of AC Disconnect, Inverter(s), and/or PV modules not listed or differs from application or single-line diagram | Ensure that single-line and application information match, including make, model, and quantity of equipment
Existing system is not identified or missing complete information | Identify the make and model of the existing system on the application and single-line diagram
Inverter is not on CEC approved Smart Inverter List | Always refer to the current and latest CEC Certified inverter List
Point of interconnection selected not shown or incorrectly labeled on single-line diagram | Clearly identify point of interconnection in relation to main breaker
Single Line Diagram depiction of Line Side Tap shown in utility section | Provide photos of customer panel with proposed Point of Interconnection and wire routing Point of Interconnection and wires cannot be in utility sealed section
Submit interconnection fee payment with application number* | Submit required interconnection payment with invoice and application number
*This deficiency is unique to PG&E.
Application1
(10 BD)
Planning/Studies
(15-115 BD)
Tender Contract
(15 BD - 30 CD)
Implementation1
(30-200 CD)2
Inspection/Close
(15 CD)2

## Slide 7: Application Phase
Program | Common Deficiency (Most Typical) | Best Practice
All | The customer listed in the interconnection request does not have an active registration with the secretary of state website, which causes delays during the interconnection agreement phase. | Customer shall provide evidence of active registration with the secretary of state.
 | The customer name in the application does not match with the customer of record in SCE’s customer database. (NEM & Rule 21 Non-Export) | Customer needs to ensure the account holder name matches what is provided in the application. This can be accomplished by either having SCE’s database updated, or by updating their Interconnection Request.
 | Existing generation is not properly identified on the Interconnection Request (IR) | Customer shall submit a completed Interconnection Request
Rule 21 Export | Site exclusivity documentation does not match the Interconnection Request (IR). For example, the legal entity and project location must match the IR. If a lease or option are provided, the term must extend through the commercial operation date as listed in the IR. | Customer shall review site exclusivity requirements as posted on our website: Site Exclusivity Guidelines.

## Slide 8: Application Phase - NEM
Program | Common Deficiency (Most Typical) | Best Practice
NEM Standard and Expanded | For NEM > 1 MW, site exclusivity documentation does not match the address or legal entity listed in the Interconnection Request | Customer shall review site exclusivity requirements as posted on our website: Site Exclusivity Guidelines.
 | Incorrect application type is selected. For example, an expansion to an existing project and it is the wrong program type selected. | Review program types and FAQ document on www.sce.com/nem and refer to help text on application.
 | Incorrect customer information such as service account, meter, email address, address and/or customer name. | Refer to the current customer or record’s bill to provide accurate information on NEM application.
 | System size justification – system is oversized per the usage or the incorrect form is submitted to clear the deficiency. | Request the most current 12 month usage from the SCE Customer of Record prior to design and submitting NEM application.
 | Final Inspection from AHJ – wrong system size is listed, missing final sign off, missing the AHJ seal or letterhead, wrong or missing job site address | Ensure the information listed on the Final Inspection is consistent with what is listed in PCI on the NEM application.
 | Electrical connection method is not consistent between application and SLD. | Refer to the NEM Interconnection Handbook for explanation of line side and load side connections. Select the correct method in the dropdown on PCI using the help text.
 | Net Generation Output Meter (NGOM) is required/requested for standard solar projects. | NGOMS are not applicable for standard solar applications. SCE NGOMS are not the same as 3rd party production meters.

## Slide 9: Common Deficiencies
Common Deficiencies | How to Avoid
Existing Generation is not listed on the application | Make sure ALL existing and new generation is included on the application
Electrical connection method listed on application is not consistent with the single-line diagram (SLD) | Double check to ensure consistency
Net Generation Output Meter (NGOM), when required, is not included on the SLD | When an NGOM is required, it must be included on the SLD with a visible, lockable disconnect
A visible, lockable AC Disconnect not included on the SLD | When required, a visible, lockable disconnect must be included on the SLD
Incorrect or missing information on export, non-export, or inadvertent export status | Select the appropriate interconnection agreement for the requested operating conditions
Line side tap shown on utility pull section or meter section | Become familiar with SDG&E’s Service Standards
Required engineer drawing for line side tap not included with application | An engineer drawing with PE stamp must be submitted for a line side tap

## Slide 10: Common Deficiencies cont.
Common Deficiencies | How to Avoid
Interconnection Agreement not signed by SDG&E’s customer of record | Agreements must be signed by the individual/entity whose name appears on the SDG&E electric bill
Pages from the terms and conditions and/or required customer account information is missing | A completed set of terms and conditions/ interconnection agreement must be submitted before permission to operate can be provided
When required, a visible, lockable AC disconnect has not been installed | A visible, lockable AC disconnect is required for all non-inverter based generators and all inverter based generators equipped with a current transformer rated meter

## Slide 11: Some Key Steps to Ensuring Timely Processing
Submit application early
If you have questions, call the Customer Generation Team
Become familiar with SDG&E’s Service Standards prior to project design
Contact SDG&E early to obtain switchgear approval
For natural gas fired technologies – Contact SDG&E early to discuss gas requirements
Line-side taps
  Provide engineering drawing with PE stamp
  Provide the date and time/length of required outage

## Slide 12: Planning / Studies Phase
Program | Common Deficiency | Best Practice
All | Inaccurate nameplate information | Ensure correct nameplate information is provided
 | Missing documentation required to complete studies | Customer needs to provide information asked for as documented in the initial review
 | Missing data required to complete supplemental review | Customer needs to provide SLD Impedance data per F2x ii and per the study
 | Incorrect impedance information provided | Customer needs to provide correct impedance information
Non-Export and other Large Projects | Incorrect non-export option selected during application phase | Customer needs to provide correct non-export information
 | Customer specified inverter is not certified | Ensure specified inverter is UL certified
Application1
(10 BD)
Planning/Studies
(15-115 BD)
Tender Contract
(15 BD - 30 CD)
Implementation1
(30-200 CD)2
Inspection/Close
(15 CD)2

## Slide 13: Planning /Study Phase
Program | Common Deficiency (Most Typical) | Best Practice
All | AC disconnect not included as required Rule 21 Section H.1.d | Customer provides a visible, lockable disconnect shown on the single line diagram and plot plan as required in Rule 21 Section H.1.d
 | Point of interconnection selected not shown or incorrectly labeled | Customer provides the correct point of interconnection
 | Line side tap letter not provided | Submit line side tap letter method for proper acceptance as detailed in the NEM handbook
 | Inverter is not on the CEC-approved Smart Inverter List | Always refer to the current and latest CEC Certified Inverter List
 | The number of inverters in the application does not match the single line diagram | Ensure customer provides matching and correct number of inverters on both the application and single line diagram
Rule 21 Non Export | Incorrect Non Export option is chosen by the customer | Customer chooses the correct non export option as described in Rule 21 Section G.1.and submits proper method for complying with the non export requirements.
Rule 21 Export | Missing Inverter Test Data | Customer shall provide the accurate nameplate data
NEM | Make and model of Inverter(s) do not match the application and the single line diagram. | Customer provides matching inverter information for the application and single line diagram
 | PE Stamp required for Line Side tap connection | Ensure PE stamp is on the single line diagram
 | Line Side Tap shown on utility pull section or meter sections | Customers should not tap in the utility sections as described by the Electrical Service Requirements

## Slide 14: Tender Contract Phase
Common Deficiency | Best Practice
Customer information discrepancies | Use Customer information from the most recent utility bill
Interconnection Agreement (IA) signed by someone other than the PG&E Customer of Record (i.e., IA signatory allowed must be someone whose name appears in the generating facility’s electric service account) | Ensure IA is signed by Customer of Record
New Customer signature and date missing when there are changes made to a previously signed Interconnection Agreement | Provide a new Customer signature and date to show that the Interconnection Customer has reviewed and agreed to the changes made
Application1
(10 BD)
Planning/Studies
(15-115 BD)
Tender Contract
(15 BD - 30 CD)
Implementation1
(30-200 CD)2
Inspection/Close
(15 CD)2

## Slide 15: Tender Contract Phase
Program | Common Deficiency (Most Typical) | Best Practice
All | Customer does not execute the agreement within the 90 calendar day window (Rule 21 section F.2.e., or F.3.e ii) | Customer to execute interconnection agreement or request an extension within the 90 calendar day negotiation window
 | Customer does not make their Initial Financial Security posting within the tariff timeline. | Customer to review the terms of their interconnection agreement and meet project milestones
 | Project payments or initial milestones are not met as outlined in the Interconnection Agreement. (ITCC, Project Payment, Written Authorization to Proceed, Initial Specifications, O&M) | Customer to review the terms of their interconnection agreement and meet the milestones.
Rule 21 Export | For Rule 21 Export projects requesting the Renewable Energy Self-Generation Bill Credit Transfer program RESBCT – Benefitting accounts forms not completed, or customer not under applicable rate schedule | Customer to submit benefitting account forms
NEM Standard and Expanded | The Interconnection Agreement (IA) is not signed by the current SCE Customer of Record or spouse. | Ensure the correct person is signing the IA with their full name as shown on the SCE bill.
 | Invalid version of Interconnection Agreement is submitted. (outdated form version or inconsistent pages or the form version and date is missing from the document. | Refer to www.sce.com/nem for the most current version of Interconnection Agreements.
 | All pages of the Interconnection Agreement are not submitted or are missing required customer account information. | View the customer’s current bill to ensure the correct information is populated on the Interconnection Agreement.
 | The benefitting accounts form for NEM Aggregation and Fuel Cell NEM are not properly completed. | Customer to complete and submit benefitting account forms

## Slide 16: Implementation Phase
Common Deficiency | Best Practice
Missing pictures of generator/project site | Provide pictures of panel, service wire and distribution points, accurate loads of PV equipment
Incomplete Single Line Diagrams | Provide detailed Single Line Diagrams for panel connections
Missing/incorrect information | Work with assigned Service Planning Representative on requested information
Application1
(10 BD)
Planning/Studies
(15-115 BD)
Tender Contract
(15 BD - 30 CD)
Implementation1
(30-200 CD)2
Inspection/Close
(15 CD)2

## Slide 17: Inspection / Close Phase
Common Deficiency | Best Practice
Final Signed-Off Building Permit is missing information | Ensure that signing jurisdiction, project address, scope of work, final sign-off date and signature or initial of inspector is included
Equipment is different from what was originally indicated in the submitted application that was reviewed | Provide updated information if changes are made New application is required if inverter nameplate increases
System is connected to meter not listed on application | Ensure application and point of interconnection references the same meter
Site not ready for final inspection (i.e., site contact for customer did not show up, customer is still finalizing some installation-related issues, etc.) | Ensure generating facility is ready for PG&E’s final inspection to avoid delay and need for revisit. Do not submit the Final Signed-Off permit (typically the last component required) to avoid scheduling the site for final inspection
Generating system has point of interconnection and/or wires in the utility’s sealed section | The point of interconnection and wires cannot be in the utility’s sealed section
Application1
(10 BD)
Planning/Studies
(15-115 BD)
Tender Contract
(15 BD - 30 CD)
Implementation1
(30-200 CD)2
Inspection/Close
(15 CD)2

## Slide 18: Inspection/ Close Phase
Program | Common Deficiency (Most Typical) | Best Practice
All | Project not ready for commissioning due to construction issues or delays | Verify that all work has been completed as required prior to commissioning test
 | Inverter or battery system not performing per design witch requires a revisit and causes delays | Customer should perform a test on the system for functionality.
Rule 21 Non Export | Relay non-export control settings not provided | Customer shall provide non export settings as required in the Rule 21 non export options
 | Relay test report not provided | Customer shall provide test report prior to scheduling commissioning test
Rule 21 Export | Implementation of generation ramp rate not implemented by installer due to lack inverter control programming knowledge | Ramp rate requirements need to be programed by customers pre tested for proper functionality
NEM | Visible lockable disconnect switch not lockable or visible | Customer shall install a visible lockable disconnect switch when required by the Rule 21 guidelines
 | Failed commissioning test due to equipment not working | Customer should test system for functionality to avoid delays and re visits
Other delays
Easements not provided by customers causes interconnection facilities construction delays