## Readme
This is the workbook for translating a Loss of Load study to the Slice of Day framework. Here's a step-by-step description of the process: 1. Input 1-2 managed load. 2. Obtain the storage values from SERVM. In the storage tab, calculate the energy using this formula: nameplate MW * duration = 8035.54 * 4 = 32,138 MWh. 3. The Jul_profiles tab has the NQC values by unit category and the profile for each resource type, with solar and wind profiles based on the exceedance values. The PSH and DR shapes and counting are based on RA rules. The import is capped at 4000MW across 24 hours. 4. The final output tab calculates the MW by hour based on the profiles by unit category. 5. The Dashboard tab reflects the MW values of each unit category as well as managed load and supply with and without storage. 6. The PRM_setting tab calculates the PRM using a solver by looking for the minimum PRM across 24 hours without storage, then optimizing by adding storage to this lowest PRM while not allocating more than 8035.54 MW in a given hour and ensuring the total allocation does not exceed 32,138 MWh, also making sure there is enough energy to charge the batteries.

## PRM_Setting
Hour | Load | Supply No batteries (MW) | Excess Capacity | Cumlative Excess | Battery Allocation | Battery SOC Day 1 (MWh) | Battery SOC Day 2 (MWh) | Adjusted Supply | adjusted PRM | Mean PRM - PRM | Min PRM | battery Limits
1 | 28700 | 46858.46 | 11579.9917 | 11579.9917 | 0 | 32138.16 | 6829.359 | 46858.46 | 63.27% | -0.089829 | 29.27% | 32138.16
2 | 27163 | 46694.46 | 12541.7429 | 24121.7346 | 0 | 32138.16 | 13658.718 | 46694.46 | 71.9% | -0.17618 |  | 8034.54 | MW (Total)
3 | 26262 | 46491.46 | 12230.2321 | 36351.9667 | 0 | 32138.16 | 20488.077 | 46491.46 | 77.03% | -0.22742 | Objective
4 | 26233 | 46142.46 | 10748.3847 | 47100.3514 | 0 | 32138.16 | 27317.436 | 46142.46 | 75.89% | -0.21608 | 0.77444
5 | 27107 | 45790.46 | 8919.0085 | 56019.3599 | 0 | 32138.16 | 32138.16 | 45790.46 | 68.92% | -0.14638
6 | 28321 | 45530.46 | 7883.1156 | 63902.4755 | 0 | 32138.16 | 32138.16 | 45530.46 | 60.77% | -0.064787
7 | 29629 | 46185.46 | 11774.6516 | 75677.1271 | 0 | 32138.16 | 32138.16 | 46185.46 | 55.88% | -0.015922
8 | 30143 | 50741.46 | 14929.4547 | 90606.5818 | 0 | 32138.16 | 32138.16 | 50741.46 | 68.34% | -0.14049
9 | 30680 | 54590.46 | 15627.9511 | 106234.5329 | 0 | 32138.16 | 32138.16 | 54590.46 | 77.94% | -0.23648
10 | 31505 | 56355.46 | 15127.6125 | 121362.1454 | 0 | 32138.16 | 32138.16 | 56355.46 | 78.88% | -0.24591
11 | 32449 | 57075.46 | 13796.9396 | 135159.0851 | 0 | 32138.16 | 32138.16 | 57075.46 | 75.89% | -0.21606
12 | 33746 | 57421.46 | 10800.8003 | 145959.8854 | 0 | 32138.16 | 32138.16 | 57421.46 | 70.16% | -0.15871
13 | 36107 | 57477.46 | 7700.7789 | 153660.6643 | 0 | 32138.16 | 32138.16 | 57477.46 | 59.19% | -0.048995
14 | 38553 | 57539.46 | 3585.8904 | 157246.5547 | 0 | 32138.16 | 32138.16 | 57539.46 | 49.25% | 0.050393
15 | 41774 | 57588.46 | 908.0814 | 158154.6361 | 0 | 32138.16 | 32138.16 | 57588.46 | 37.86% | 0.1643
16 | 43864 | 57612.46 | 463.4592 | 158618.0953 | 855.5269 | 31282.6331 | 31282.6331 | 58467.9869 | 33.29% | 0.20993
17 | 45622 | 59440.46 | -989.262 | 156622.331 | 921.7908 | 30360.8423 | 30360.8423 | 60362.2508 | 32.31% | 0.21977
18 | 45908 | 58357.46 | -4214.4797 | 151323.3916 | 2630.3105 | 27730.5318 | 27730.5318 | 60987.7705 | 32.85% | 0.21439
19 | 45369 | 54435.46 | -8034.54 | 140194.3687 | 5270.4496 | 22460.0822 | 22460.0822 | 59705.9096 | 31.6% | 0.22686
20 | 44604 | 49626.46 | -7001.4877 | 126992.352 | 8034.54 | 14425.5422 | 14425.5422 | 57661 | 29.27% | 0.25014
21 | 43029 | 48623.46 | -2851.7143 | 114688.2377 | 8034.5394 | 6391.0029 | 6391.0029 | 56657.9994 | 31.67% | 0.22613
22 | 38664 | 47130.46 | 1780.8071 | 107016.6455 | 5203.9695 | 1187.0334 | 1187.0334 | 52334.4295 | 35.36% | 0.1893
23 | 34966 | 46982.46 | 5833.2535 | 106727.5819 | 1187.0334 | 2.7285e-12 | 2.7285e-12 | 48169.4934 | 37.76% | 0.16526
24 | 31808 | 46952.46 | 0 | 105331.0721 | 0 | 2.7285e-12 | 2.7285e-12 | 46952.46 | 47.61% | 0.066749
|  |  |  | Min: | 0 | 2.7285e-12
|  |  |  | Max: | 8034.54 | 32138.16
|  |  |  | Sum: | 32138.16 | 1171561.0858
|  |  |  | Cumulative Check: | 73192.9121

## Dashboard
| Resource Portfolio | Resource Portfolio | [10 empty] | Hour
|  |  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
|  | Biogas | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
|  | Biomass/Wood | 549 | 549 | 549 | 549 | 549 | 549 | 549 | 549 | 549 | 549 | 549 | 549 | 549 | 549 | 549 | 549 | 549 | 549 | 549 | 549 | 549 | 549 | 549 | 549
|  | CC | 16712 | 16712 | 16712 | 16712 | 16712 | 16712 | 16712 | 16712 | 16712 | 16712 | 16712 | 16712 | 16712 | 16712 | 16712 | 16712 | 16712 | 16712 | 16712 | 16712 | 16712 | 16712 | 16712 | 16712
|  | Coal | 477 | 477 | 477 | 477 | 477 | 477 | 477 | 477 | 477 | 477 | 477 | 477 | 477 | 477 | 477 | 477 | 477 | 477 | 477 | 477 | 477 | 477 | 477 | 477
|  | Cogen | 1656 | 1656 | 1656 | 1656 | 1656 | 1656 | 1656 | 1656 | 1656 | 1656 | 1656 | 1656 | 1656 | 1656 | 1656 | 1656 | 1656 | 1656 | 1656 | 1656 | 1656 | 1656 | 1656 | 1656
|  | CT | 8560 | 8560 | 8560 | 8560 | 8560 | 8560 | 8560 | 8560 | 8560 | 8560 | 8560 | 8560 | 8560 | 8560 | 8560 | 8560 | 8560 | 8560 | 8560 | 8560 | 8560 | 8560 | 8560 | 8560
|  | DR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2016 | 2176 | 2088 | 1977 | 1753 | 168 | 0 | 0
|  | ICE | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255
|  | Geothermal | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272
Legend |  | Hydro | 5621 | 5621 | 5621 | 5621 | 5621 | 5621 | 5621 | 5621 | 5621 | 5621 | 5621 | 5621 | 5621 | 5621 | 5621 | 5621 | 5621 | 5621 | 5621 | 5621 | 5621 | 5621 | 5621 | 5621
User Input |  | Interchange | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000
Imputed Input |  | Nuclear | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280
Obj Function Elements |  | PSH | 1901 | 1901 | 1901 | 1901 | 1901 | 1901 | 1901 | 1901 | 1901 | 1901 | 1901 | 1901 | 1901 | 1901 | 1901 | 1901 | 1901 | 1901 | 1901 | 1901 | 1901 | 1901 | 1901 | 1901
Decision Variable |  | Storage | 8035 | 8035 | 8035 | 8035 | 8035 | 8035 | 8035 | 8035 | 8035 | 8035 | 8035 | 8035 | 8035 | 8035 | 8035 | 8035 | 8035 | 8035 | 8035 | 8035 | 8035 | 8035 | 8035 | 8035
Constraint |  | Solar Fixed_Norcal | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 592 | 1123 | 1434 | 1599 | 1683 | 1712 | 1697 | 1660 | 1578 | 1423 | 1155 | 694 | 152 | 1 | 0 | 0 | 0
|  | Solar Fixed_Socal | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 746 | 1377 | 1772 | 2035 | 2168 | 2212 | 2194 | 2095 | 1960 | 1697 | 1276 | 580 | 66 | 0 | 0 | 0 | 0
|  | Solar Thermal_Norcal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Solar Thermal_Socal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 309 | 500 | 568 | 587 | 597 | 569 | 555 | 521 | 502 | 409 | 301 | 96 | 0 | 0 | 0 | 0
|  | Solar Tracking_Norcal | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 1217 | 2009 | 2219 | 2252 | 2259 | 2242 | 2242 | 2206 | 2204 | 2125 | 1965 | 1363 | 315 | 2 | 0 | 0 | 0
|  | Solar Tracking_Socal | 0 | 0 | 0 | 0 | 0 | 0 | 659 | 3487 | 5590 | 6427 | 6770 | 6903 | 6839 | 6759 | 6701 | 6539 | 6205 | 5366 | 3077 | 460 | 0 | 0 | 0 | 0
|  | Wind_Norcal | 1150 | 1122 | 1039 | 927 | 875 | 819 | 698 | 582 | 414 | 336 | 214 | 152 | 138 | 213 | 252 | 368 | 602 | 759 | 803 | 841 | 963 | 998 | 1096 | 1153
|  | Wind_Socal | 2245 | 2109 | 1989 | 1752 | 1452 | 1248 | 928 | 599 | 305 | 204 | 174 | 206 | 274 | 402 | 656 | 979 | 1407 | 1788 | 2066 | 2256 | 2441 | 2501 | 2423 | 2336
|  | Total Supply With Storage (MW) | 54893 | 54729 | 54526 | 54177 | 53825 | 53565 | 54220 | 58776 | 62625 | 64390 | 65110 | 65456 | 65512 | 65574 | 65623 | 65647 | 67475 | 66392 | 62470 | 57661 | 56658 | 55165 | 55017 | 54987
|  | Total Supply Without Storage (MW) | 46858.46 | 46694.46 | 46491.46 | 46142.46 | 45790.46 | 45530.46 | 46185.46 | 50741.46 | 54590.46 | 56355.46 | 57075.46 | 57421.46 | 57477.46 | 57539.46 | 57588.46 | 57612.46 | 59440.46 | 58357.46 | 54435.46 | 49626.46 | 48623.46 | 47130.46 | 46982.46 | 46952.46
|  | Load | 28700 | 27163 | 26262 | 26233 | 27107 | 28321 | 29629 | 30143 | 30680 | 31505 | 32449 | 33746 | 36107 | 38553 | 41774 | 43864 | 45622 | 45908 | 45369 | 44604 | 43029 | 38664 | 34966 | 31808

## Final_Output
Hour Ending | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
Biogas | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180 | 180
Biomass/Wood | 549 | 549 | 549 | 549 | 549 | 549 | 549 | 549 | 549 | 549 | 549 | 549 | 549 | 549 | 549 | 549 | 549 | 549 | 549 | 549 | 549 | 549 | 549 | 549
CC | 16712 | 16712 | 16712 | 16712 | 16712 | 16712 | 16712 | 16712 | 16712 | 16712 | 16712 | 16712 | 16712 | 16712 | 16712 | 16712 | 16712 | 16712 | 16712 | 16712 | 16712 | 16712 | 16712 | 16712
Coal | 477 | 477 | 477 | 477 | 477 | 477 | 477 | 477 | 477 | 477 | 477 | 477 | 477 | 477 | 477 | 477 | 477 | 477 | 477 | 477 | 477 | 477 | 477 | 477
Cogen | 1656 | 1656 | 1656 | 1656 | 1656 | 1656 | 1656 | 1656 | 1656 | 1656 | 1656 | 1656 | 1656 | 1656 | 1656 | 1656 | 1656 | 1656 | 1656 | 1656 | 1656 | 1656 | 1656 | 1656
CT | 8560 | 8560 | 8560 | 8560 | 8560 | 8560 | 8560 | 8560 | 8560 | 8560 | 8560 | 8560 | 8560 | 8560 | 8560 | 8560 | 8560 | 8560 | 8560 | 8560 | 8560 | 8560 | 8560 | 8560
DR | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2016 | 2176 | 2088 | 1977 | 1753 | 168 | 0 | 0
ICE | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255 | 255
Geothermal | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272 | 1272
Hydro | 5621 | 5621 | 5621 | 5621 | 5621 | 5621 | 5621 | 5621 | 5621 | 5621 | 5621 | 5621 | 5621 | 5621 | 5621 | 5621 | 5621 | 5621 | 5621 | 5621 | 5621 | 5621 | 5621 | 5621
Interchange | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000 | 4000
Nuclear | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280 | 2280
PSH | 1901 | 1901 | 1901 | 1901 | 1901 | 1901 | 1901 | 1901 | 1901 | 1901 | 1901 | 1901 | 1901 | 1901 | 1901 | 1901 | 1901 | 1901 | 1901 | 1901 | 1901 | 1901 | 1901 | 1901
Storage | 8035 | 8035 | 8035 | 8035 | 8035 | 8035 | 8035 | 8035 | 8035 | 8035 | 8035 | 8035 | 8035 | 8035 | 8035 | 8035 | 8035 | 8035 | 8035 | 8035 | 8035 | 8035 | 8035 | 8035
Solar Fixed_Norcal | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 592 | 1123 | 1434 | 1599 | 1683 | 1712 | 1697 | 1660 | 1578 | 1423 | 1155 | 694 | 152 | 1 | 0 | 0 | 0
Solar Fixed_Socal | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 746 | 1377 | 1772 | 2035 | 2168 | 2212 | 2194 | 2095 | 1960 | 1697 | 1276 | 580 | 66 | 0 | 0 | 0 | 0
Solar Thermal_Socal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Solar Thermal_Socal | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 309 | 500 | 568 | 587 | 597 | 569 | 555 | 521 | 502 | 409 | 301 | 96 | 0 | 0 | 0 | 0
Solar Tracking_Norcal | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 1217 | 2009 | 2219 | 2252 | 2259 | 2242 | 2242 | 2206 | 2204 | 2125 | 1965 | 1363 | 315 | 2 | 0 | 0 | 0
Solar Tracking_Socal | 0 | 0 | 0 | 0 | 0 | 0 | 659 | 3487 | 5590 | 6427 | 6770 | 6903 | 6839 | 6759 | 6701 | 6539 | 6205 | 5366 | 3077 | 460 | 0 | 0 | 0 | 0
Wind_Norcal | 1150 | 1122 | 1039 | 927 | 875 | 819 | 698 | 582 | 414 | 336 | 214 | 152 | 138 | 213 | 252 | 368 | 602 | 759 | 803 | 841 | 963 | 998 | 1096 | 1153
Wind_Socal | 2245 | 2109 | 1989 | 1752 | 1452 | 1248 | 928 | 599 | 305 | 204 | 174 | 206 | 274 | 402 | 656 | 979 | 1407 | 1788 | 2066 | 2256 | 2441 | 2501 | 2423 | 2336

## Output
Hour Ending | Biogas | Biomass/Wood | CC | Coal | Cogen | CT | DR | ICE | Geothermal | Hydro | Interchange | Nuclear | PSH | Storage | Solar Fixed_Norcal | Solar Fixed_Socal | Solar Thermal_Norcal | Solar Thermal_Socal | Solar Tracking_Norcal | Solar Tracking_Socal | Wind_Norcal | Wind_Socal
1 | 179.94 | 548.5362 | 16711.88 | 477 | 1656.0907 | 8559.5 | 0 | 254.7 | 1271.7011 | 5620.748 | 4000 | 2280 | 1901.48 | 8034.63 | 0 | 0.013911 | 0 | 0 | 0 | 0 | 1150.0163 | 2244.7974 | 54891.0336
2 | 179.94 | 548.5362 | 16711.88 | 477 | 1656.0907 | 8559.5 | 0 | 254.7 | 1271.7011 | 5620.748 | 4000 | 2280 | 1901.48 | 8034.63 | 0 | 0.0099903 | 0 | 0 | 0 | 0 | 1121.7081 | 2109.0931 | 54727.0173
3 | 179.94 | 548.5362 | 16711.88 | 477 | 1656.0907 | 8559.5 | 0 | 254.7 | 1271.7011 | 5620.748 | 4000 | 2280 | 1901.48 | 8034.63 | 0 | 0.0063483 | 0 | 0 | 0 | 0 | 1038.8472 | 1988.9374 | 54523.997
4 | 179.94 | 548.5362 | 16711.88 | 477 | 1656.0907 | 8559.5 | 0 | 254.7 | 1271.7011 | 5620.748 | 4000 | 2280 | 1901.48 | 8034.63 | 0 | 0.0037432 | 0 | 0 | 0 | 0 | 927.0746 | 1751.8245 | 54175.109
5 | 179.94 | 548.5362 | 16711.88 | 477 | 1656.0907 | 8559.5 | 0 | 254.7 | 1271.7011 | 5620.748 | 4000 | 2280 | 1901.48 | 8034.63 | 0 | 0.0020132 | 0 | 0 | 0 | 0 | 874.9118 | 1451.688 | 53822.808
6 | 179.94 | 548.5362 | 16711.88 | 477 | 1656.0907 | 8559.5 | 0 | 254.7 | 1271.7011 | 5620.748 | 4000 | 2280 | 1901.48 | 8034.63 | 9.6258e-05 | 0.41506 | 0 | 0 | 0.015373 | 0.39306 | 819.0482 | 1247.9641 | 53564.042
7 | 179.94 | 548.5362 | 16711.88 | 477 | 1656.0907 | 8559.5 | 0 | 254.7 | 1271.7011 | 5620.748 | 4000 | 2280 | 1901.48 | 8034.63 | 82.1396 | 170.5503 | 0 | 0 | 183.6935 | 658.7096 | 698.0218 | 927.5894 | 54216.9101
8 | 179.94 | 548.5362 | 16711.88 | 477 | 1656.0907 | 8559.5 | 0 | 254.7 | 1271.7011 | 5620.748 | 4000 | 2280 | 1901.48 | 8034.63 | 592.3775 | 745.6915 | 0 | 55.4352 | 1216.6411 | 3487.3856 | 581.9622 | 599.4122 | 58775.1112
9 | 179.94 | 548.5362 | 16711.88 | 477 | 1656.0907 | 8559.5 | 0 | 254.7 | 1271.7011 | 5620.748 | 4000 | 2280 | 1901.48 | 8034.63 | 1122.9065 | 1377.0447 | 0 | 309.0303 | 2009.3255 | 5589.8935 | 414.0525 | 305.3309 | 62623.7901
10 | 179.94 | 548.5362 | 16711.88 | 477 | 1656.0907 | 8559.5 | 0 | 254.7 | 1271.7011 | 5620.748 | 4000 | 2280 | 1901.48 | 8034.63 | 1434.2185 | 1771.794 | 0 | 500.3814 | 2218.8074 | 6427.3894 | 336.0461 | 203.7718 | 64388.6146
11 | 179.94 | 548.5362 | 16711.88 | 477 | 1656.0907 | 8559.5 | 0 | 254.7 | 1271.7011 | 5620.748 | 4000 | 2280 | 1901.48 | 8034.63 | 1599.3263 | 2034.6517 | 0 | 568.2162 | 2252.4297 | 6770.1322 | 213.7649 | 174.2814 | 65109.0084
12 | 179.94 | 548.5362 | 16711.88 | 477 | 1656.0907 | 8559.5 | 0 | 254.7 | 1271.7011 | 5620.748 | 4000 | 2280 | 1901.48 | 8034.63 | 1683.4503 | 2168.4027 | 0 | 587.0589 | 2258.8598 | 6902.7396 | 152.4352 | 205.8214 | 65454.974
13 | 179.94 | 548.5362 | 16711.88 | 477 | 1656.0907 | 8559.5 | 0 | 254.7 | 1271.7011 | 5620.748 | 4000 | 2280 | 1901.48 | 8034.63 | 1711.8926 | 2211.9557 | 0 | 596.8907 | 2242.0855 | 6839.117 | 138.2577 | 273.9831 | 65510.3884
14 | 179.94 | 548.5362 | 16711.88 | 477 | 1656.0907 | 8559.5 | 0 | 254.7 | 1271.7011 | 5620.748 | 4000 | 2280 | 1901.48 | 8034.63 | 1696.7172 | 2194.1228 | 0 | 569.2441 | 2241.6776 | 6759.4294 | 212.7691 | 401.5763 | 65571.7426
15 | 179.94 | 548.5362 | 16711.88 | 477 | 1656.0907 | 8559.5 | 0 | 254.7 | 1271.7011 | 5620.748 | 4000 | 2280 | 1901.48 | 8034.63 | 1659.8125 | 2095.4269 | 0 | 554.571 | 2206.2199 | 6700.8257 | 251.5211 | 656.2664 | 65620.8496
16 | 179.94 | 548.5362 | 16711.88 | 477 | 1656.0907 | 8559.5 | 0 | 254.7 | 1271.7011 | 5620.748 | 4000 | 2280 | 1901.48 | 8034.63 | 1577.8741 | 1960.2111 | 0 | 520.6147 | 2204.4252 | 6539.1565 | 367.5885 | 978.6167 | 65644.6929
17 | 179.94 | 548.5362 | 16711.88 | 477 | 1656.0907 | 8559.5 | 2015.9277 | 254.7 | 1271.7011 | 5620.748 | 4000 | 2280 | 1901.48 | 8034.63 | 1423.3089 | 1696.9447 | 0 | 502.0519 | 2124.8872 | 6204.5631 | 601.9009 | 1406.5742 | 67472.3647
18 | 179.94 | 548.5362 | 16711.88 | 477 | 1656.0907 | 8559.5 | 2176.0634 | 254.7 | 1271.7011 | 5620.748 | 4000 | 2280 | 1901.48 | 8034.63 | 1155.0425 | 1276.3276 | 0 | 409.2411 | 1965.3668 | 5365.6557 | 759.1752 | 1787.831 | 66390.9095
19 | 179.94 | 548.5362 | 16711.88 | 477 | 1656.0907 | 8559.5 | 2088.3354 | 254.7 | 1271.7011 | 5620.748 | 4000 | 2280 | 1901.48 | 8034.63 | 694.2656 | 580.4918 | 0 | 301.1352 | 1363.2989 | 3076.7998 | 803.3923 | 2066.3816 | 62470.3066
20 | 179.94 | 548.5362 | 16711.88 | 477 | 1656.0907 | 8559.5 | 1977.0587 | 254.7 | 1271.7011 | 5620.748 | 4000 | 2280 | 1901.48 | 8034.63 | 151.6982 | 66.1969 | 0 | 95.9995 | 314.7149 | 460.1888 | 840.5544 | 2255.5576 | 57658.1751
21 | 179.94 | 548.5362 | 16711.88 | 477 | 1656.0907 | 8559.5 | 1752.6708 | 254.7 | 1271.7011 | 5620.748 | 4000 | 2280 | 1901.48 | 8034.63 | 0.83658 | 0.08144 | 0 | 0 | 1.6536 | 0.11091 | 963.4847 | 2441.3999 | 56656.444
22 | 179.94 | 548.5362 | 16711.88 | 477 | 1656.0907 | 8559.5 | 168.3315 | 254.7 | 1271.7011 | 5620.748 | 4000 | 2280 | 1901.48 | 8034.63 | 0 | 0.037685 | 0 | 0 | 0 | 0 | 998.4142 | 2501.2603 | 55164.2498
23 | 179.94 | 548.5362 | 16711.88 | 477 | 1656.0907 | 8559.5 | 0 | 254.7 | 1271.7011 | 5620.748 | 4000 | 2280 | 1901.48 | 8034.63 | 0 | 0.028833 | 0 | 0 | 0 | 0 | 1096.1871 | 2422.5876 | 55015.0096
24 | 179.94 | 548.5362 | 16711.88 | 477 | 1656.0907 | 8559.5 | 0 | 254.7 | 1271.7011 | 5620.748 | 4000 | 2280 | 1901.48 | 8034.63 | 0 | 0.019348 | 0 | 0 | 0 | 0 | 1153.2687 | 2335.8805 | 54985.3746

## Jul_Profiles
Hour Ending | Biogas | Biomass/Wood | CC | Coal | Cogen | CT | DR | ICE | Geothermal | Hydro | Interchange | Nuclear | PSH | Storage | Solar Fixed_Norcal | Solar Fixed_Socal | Solar Thermal_Norcal | Solar Thermal_Socal | Solar Tracking_Norcal | Solar Tracking_Socal | Wind_Norcal | Wind_Socal | Unit Category | NQC
1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 5.5e-06 | 0 | 0 | 0 | 0 | 0.59659 | 0.4184 | Biogas | 179.94
2 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 3.95e-06 | 0 | 0 | 0 | 0 | 0.5819 | 0.3931 | Biomass/Wood | 548.5362
3 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 2.51e-06 | 0 | 0 | 0 | 0 | 0.53892 | 0.37071 | CC | 16711.88
4 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1.48e-06 | 0 | 0 | 0 | 0 | 0.48093 | 0.32651 | Coal | 477
5 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 7.96e-07 | 0 | 0 | 0 | 0 | 0.45387 | 0.27057 | Cogen | 1656.0907
6 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 5.03e-08 | 0.00016411 | 0 | 0 | 5.84e-06 | 4.82e-05 | 0.42489 | 0.2326 | CT | 8559.5
7 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.042922 | 0.067433 | 0 | 0 | 0.069784 | 0.080776 | 0.36211 | 0.17289 | DR | 2066.23
8 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.30955 | 0.29483 | 0 | 0.055602 | 0.4622 | 0.42765 | 0.3019 | 0.11172 | ICE | 254.7
9 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.58678 | 0.54446 | 0 | 0.30996 | 0.76333 | 0.68547 | 0.2148 | 0.056909 | Geothermal | 1271.7011
10 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.74946 | 0.70054 | 0 | 0.50189 | 0.84292 | 0.78817 | 0.17433 | 0.03798 | Hydro | 5620.748
11 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.83573 | 0.80447 | 0 | 0.56993 | 0.85569 | 0.8302 | 0.11089 | 0.032483 | Interchange | 4000
12 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.87969 | 0.85735 | 0 | 0.58883 | 0.85813 | 0.84646 | 0.079078 | 0.038362 | Nuclear | 2280
13 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.89456 | 0.87457 | 0 | 0.59869 | 0.85176 | 0.83866 | 0.071723 | 0.051066 | PSH | 1901.48
14 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.88663 | 0.86752 | 0 | 0.57096 | 0.8516 | 0.82889 | 0.11038 | 0.074848 | Storage | 8034.63
15 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.86734 | 0.8285 | 0 | 0.55624 | 0.83813 | 0.8217 | 0.13048 | 0.12232 | Solar Fixed_Norcal | 1913.68
16 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.82452 | 0.77504 | 0 | 0.52218 | 0.83745 | 0.80188 | 0.19069 | 0.1824 | Solar Fixed_Socal | 2529.19
17 | 1 | 1 | 1 | 1 | 1 | 1 | 0.97566 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.74375 | 0.67094 | 0 | 0.50356 | 0.80724 | 0.76085 | 0.31224 | 0.26216 | Solar Thermal_Norcal | 0
18 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0532 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.60357 | 0.50464 | 0 | 0.41047 | 0.74663 | 0.65797 | 0.39383 | 0.33322 | Solar Thermal_Socal | 997
19 | 1 | 1 | 1 | 1 | 1 | 1 | 1.0107 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.36279 | 0.22952 | 0 | 0.30204 | 0.51791 | 0.3773 | 0.41677 | 0.38514 | Solar Tracking_Norcal | 2632.3
20 | 1 | 1 | 1 | 1 | 1 | 1 | 0.95684 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.07927 | 0.026173 | 0 | 0.096288 | 0.11956 | 0.056432 | 0.43605 | 0.4204 | Solar Tracking_Socal | 8154.81
21 | 1 | 1 | 1 | 1 | 1 | 1 | 0.84825 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0.00043716 | 3.22e-05 | 0 | 0 | 0.00062821 | 1.36e-05 | 0.49982 | 0.45504 | Wind_Norcal | 1927.66
22 | 1 | 1 | 1 | 1 | 1 | 1 | 0.081468 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1.49e-05 | 0 | 0 | 0 | 0 | 0.51794 | 0.4662 | Wind_Socal | 5365.25
23 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1.14e-05 | 0 | 0 | 0 | 0 | 0.56866 | 0.45153 | Total | 77082.3261
24 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 7.65e-06 | 0 | 0 | 0 | 0 | 0.59827 | 0.43537

## Storage
Pndcap | Total Energy
32138.16 | 32138.16

## Managed_load
HOUR | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24
MANAGED_NET_LOAD | 28700 | 27163 | 26262 | 26233 | 27107 | 28321 | 29629 | 30143 | 30680 | 31505 | 32449 | 33746 | 36107 | 38553 | 41774 | 43864 | 45622 | 45908 | 45369 | 44604 | 43029 | 38664 | 34966 | 31808