## Dictionary
Column | Description
Outages | Unique event identification number
County | County
Circuit | Overhead Distribution Circuit Name
CPZ | Circuit Protection Zone
Cause | Outage Suspected Initiating Cause
3rd | Third Party
AN | Animal
CI | Company Initiated
EF | Equipment Failure
ENV | Environmental
UNK | Unknown
VEG | Vegetation
FNL | "First No Light"; Outage Start Day & Time
Week | Reporting Week by FNL
End_Date | Outage End Day & Time
CAIDI | Customer Average Interruption Duration Index, in minutes
EPSS_Outage_Type | FTS, HLT or T-EPSS
FTS | "Fast Trip Setting"; Post-Optimized Circuit Settings
HLT | "Hot Line Tag"; Pre-Optimized Circuit Settings
T-EPSS | "Transmission"-EPSS; EPSS outages on transmission lines
C/OUT | “Reclosing Cut Out (Reclose Blocking Enabled)”; device will not reclose when fault occurs
CESO | Count of Customers Experiencing Sustained Outages
Medical_Baseline | Count of Medical Baseline customer service points
Life_Support | Count of Life Support customer service points
Critical_Customer | Count of Critical Customer service points
Schools | Count of School customer service points
Hospitals | Count of Hospital customer service points
Well_Water_Dependent | Count of Well Water Depended customer service points
Customer_Minutes | Sum of total outage customer minutes
Restoration_Time_Minutes | Amount of time between the FNL and End Date, in minutes

## Summary
2025 YTD Summary
Category | Count
Medical Baseline | 98575
Life Support | 71872
Critical Customers | 29967
Hospitals | 216
Schools | 4196
Overall CAIDI | 136.7726
Restored <60 Mins | 501
Total Outages | 2405
Total Customers Experiencing Outages | 1821243
Unique Customers Experiencing Outages | 838925
November 2025 Summary
Category | Count
Medical Baseline | 337
Life Support | 255
Critical Customers | 151
Hospitals | 0
Schools | 16
Overall CAIDI | 124.0809
Restored <60 Mins | 3
Total Outages | 10
Total Customers Experiencing Outages | 6948
Unique Customers Experiencing Outages | 6696
* As of 12/10/25

## Pivot (hidden)
Column Labels
Values | Jan | Feb | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Grand Total
Sum of Medical_Baseline | 545 | 48 | 472 | 10863 | 18416 | 17937 | 21296 | 22219 | 6442 | 337 | 98575
Sum of Life_Support | 396 | 38 | 353 | 7890 | 13251 | 13072 | 15702 | 16324 | 4591 | 255 | 71872
Sum of Critical_Customer | 193 | 26 | 109 | 3694 | 5610 | 5250 | 6329 | 6644 | 1961 | 151 | 29967
Sum of Hospitals | 0 | 0 | 4 | 17 | 37 | 27 | 31 | 89 | 11 | 0 | 216
Sum of Schools | 20 | 1 | 24 | 505 | 694 | 717 | 933 | 974 | 312 | 16 | 4196
Sum of caidi_calc | 146.5152 | 100.9682 | 59.0631 | 166.3122 | 126.2184 | 140.227 | 125.1911 | 150.1633 | 95.7841 | 124.0809 | 136.7726
Count of Outages | 24 | 5 | 2 | 279 | 464 | 415 | 479 | 550 | 177 | 10 | 2405
Sum of CESO | 11203 | 1669 | 6278 | 214756 | 349273 | 346629 | 383058 | 398333 | 103096 | 6948 | 1821243
2025 YTD Summary
Category | Column Labels Jan: Count
Medical Baseline | Column Labels Jan: 98575
Life Support | Column Labels Jan: 71872
Critical Customers | Column Labels Jan: 29967
Hospitals | Column Labels Jan: 216
Schools | Column Labels Jan: 4196
Overall CAIDI | Column Labels Jan: 136.7726
Restored <60 Mins | Column Labels Jan: 501
Total Outages | Column Labels Jan: 2405
Total Customers Experiencing Outages | Column Labels Jan: 1821243
Unique Customers Experiencing Outages | Column Labels Jan: 838925
Nov 2025 Summary
Category | Column Labels Jan: Count
Medical Baseline | Column Labels Jan: 337
Life Support | Column Labels Jan: 255
Critical Customers | Column Labels Jan: 151
Hospitals | Column Labels Jan: 0
Schools | Column Labels Jan: 16
Overall CAIDI | Column Labels Jan: 124.0809
Restored <60 Mins | Column Labels Jan: 3
Total Outages | Column Labels Jan: 10
Total Customers Experiencing Outages | Column Labels Jan: 6948
Unique Customers Experiencing Outages | Column Labels Jan: 6696
* As of 12/10/25

## YTD Outages 010125_113025
Outages | County | Circuit | CPZ | Cause | FNL | FNL_tz | Week | End_Date | End_Date_tz | CAIDI | EPSS_Outage_Type | Customer_Minutes | CESO | Medical_Baseline | Life_Support | Critical_Customer | Schools | Hospitals | Well_Water_Dependent | Restoration_Time_Minutes
25-0006180 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113A08 | Equipment Failure/Involved | 2025-01-07 06:50 | -08:00 | 01/07 - 01/13 | 2025-01-07 19:31 | -08:00 | 47.4307 | FTS | 44158 | 931 | 56 | 44 | 19 | 0 | 0 | 22 | 761
25-0007295 | Sonoma | GEYSERVILLE 1102 | GEYSERVILLE 110289714 | Equipment Failure/Involved | 2025-01-09 09:22 | -08:00 | 01/07 - 01/13 | 2025-01-09 09:29 | -08:00 | 7 | FTS | 4011 | 573 | 8 | 2 | 11 | 1 | 0 | 3 | 7
25-0007607 | Napa | CALISTOGA 1101 | CALISTOGA 1101257964 | Unknown Cause | 2025-01-09 20:54 | -08:00 | 01/07 - 01/13 | 2025-01-10 11:12 | -08:00 | 858 | FTS | 312312 | 364 | 3 | 3 | 4 | 0 | 0 | 1 | 858
25-0007847 | Sonoma | CALISTOGA 1101 | CALISTOGA 1101242919 | Company Initiated | 2025-01-10 11:43 | -08:00 | 01/07 - 01/13 | 2025-01-10 13:45 | -08:00 | 122 | FTS | 3294 | 27 | 0 | 0 | 1 | 0 | 0 | 0 | 122
25-0008134 | Lake | MIDDLETOWN 1101 | MIDDLETOWN 11014646 | Vegetation | 2025-01-11 11:04 | -08:00 | 01/07 - 01/13 | 2025-01-11 14:18 | -08:00 | 33.5527 | FTS | 10502 | 313 | 16 | 14 | 3 | 0 | 0 | 0 | 194
25-0008178 | Sonoma | CALISTOGA 1101 | CALISTOGA 1101242919 | Unknown Cause | 2025-01-11 13:56 | -08:00 | 01/07 - 01/13 | 2025-01-11 17:20 | -08:00 | 124.7059 | FTS | 6360 | 51 | 0 | 0 | 1 | 0 | 0 | 0 | 204
25-0008232 | Santa Barbara | SISQUOC 1102 | SISQUOC 1102M26 | Unknown Cause | 2025-01-11 20:34 | -08:00 | 01/07 - 01/13 | 2025-01-11 22:44 | -08:00 | 100.24 | FTS | 25060 | 250 | 3 | 2 | 2 | 0 | 0 | 0 | 130
25-0008253 | Napa | CALISTOGA 1101 | CALISTOGA 1101257964 | Unknown Cause | 2025-01-12 04:33 | -08:00 | 01/07 - 01/13 | 2025-01-12 09:13 | -08:00 | 280 | FTS | 101920 | 364 | 3 | 3 | 4 | 0 | 0 | 1 | 280
25-0008312 | Solano | VACAVILLE 1108 | VACAVILLE 110847860 | Company Initiated | 2025-01-12 16:29 | -08:00 | 01/07 - 01/13 | 2025-01-12 18:00 | -08:00 | 91 | FTS | 139685 | 1535 | 121 | 91 | 29 | 4 | 0 | 5 | 91
25-0008647 | Sonoma | CALISTOGA 1101 | CALISTOGA 1101242919 | Company Initiated | 2025-01-13 13:31 | -08:00 | 01/07 - 01/13 | 2025-01-13 16:44 | -08:00 | 193 | FTS | 5211 | 27 | 0 | 0 | 1 | 0 | 0 | 0 | 193
25-0008513 | Napa | CALISTOGA 1101 | CALISTOGA 1101257964 | Equipment Failure/Involved | 2025-01-13 10:35 | -08:00 | 01/14 - 01/20 | 2025-01-14 01:20 | -08:00 | 157.1374 | FTS | 57198 | 364 | 3 | 3 | 4 | 0 | 0 | 1 | 885
25-0009268 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113641367 | Unknown Cause | 2025-01-14 21:19 | -08:00 | 01/14 - 01/20 | 2025-01-15 02:27 | -08:00 | 308 | FTS | 91784 | 298 | 11 | 5 | 3 | 0 | 0 | 11 | 308
25-0009330 | Butte | CLARK ROAD 1102 | CLARK ROAD 110281296 | Unknown Cause | 2025-01-15 07:55 | -08:00 | 01/14 - 01/20 | 2025-01-15 12:45 | -08:00 | 216.0388 | FTS | 211502 | 979 | 72 | 52 | 19 | 3 | 0 | 4 | 290
25-0009715 | San Luis Obispo | ATASCADERO 1103 | ATASCADERO 1103A06 | Unknown Cause | 2025-01-15 16:06 | -08:00 | 01/14 - 01/20 | 2025-01-15 16:58 | -08:00 | 52 | FTS | 32812 | 631 | 32 | 21 | 19 | 2 | 0 | 16 | 52
25-0010356 | Solano | VACAVILLE 1108 | VACAVILLE 110847860 | Unknown Cause | 2025-01-17 10:56 | -08:00 | 01/14 - 01/20 | 2025-01-17 13:14 | -08:00 | 115.3518 | FTS | 177065 | 1535 | 121 | 91 | 29 | 4 | 0 | 5 | 138
25-0010654 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113641367 | Unknown Cause | 2025-01-18 09:31 | -08:00 | 01/14 - 01/20 | 2025-01-18 12:16 | -08:00 | 165 | FTS | 49170 | 298 | 11 | 5 | 3 | 0 | 0 | 11 | 165
25-0011887 | Butte | CLARK ROAD 1102 | CLARK ROAD 11022068 | Equipment Failure/Involved | 2025-01-23 00:09 | -08:00 | 01/21 - 01/27 | 2025-01-23 03:31 | -08:00 | 169.2845 | FTS | 39274 | 232 | 19 | 12 | 4 | 1 | 0 | 2 | 202
25-0012367 | Santa Barbara | PALMER 1101 | PALMER 1101M84 | Animal | 2025-01-24 01:51 | -08:00 | 01/21 - 01/27 | 2025-01-24 03:59 | -08:00 | 128 | FTS | 116608 | 911 | 23 | 20 | 8 | 1 | 0 | 0 | 128
25-0012421 | Sonoma | GEYSERVILLE 1102 | GEYSERVILLE 1102484 | Company Initiated | 2025-01-24 08:03 | -08:00 | 01/21 - 01/27 | 2025-01-24 08:26 | -08:00 | 23 | FTS | 8441 | 367 | 3 | 1 | 10 | 1 | 0 | 3 | 23
25-0012843 | Shasta | CEDAR CREEK 1101 | CEDAR CREEK 11011664 | Unknown Cause | 2025-01-25 04:58 | -08:00 | 01/21 - 01/27 | 2025-01-25 08:04 | -08:00 | 156.9814 | FTS | 75822 | 483 | 32 | 22 | 11 | 1 | 0 | 1 | 186
25-0012935 | Shasta | CEDAR CREEK 1101 | CEDAR CREEK 1101451856 | Company Initiated | 2025-01-25 12:30 | -08:00 | 01/21 - 01/27 | 2025-01-25 12:42 | -08:00 | 12 | FTS | 36 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 12
25-0013007 | Santa Barbara | SANTA YNEZ 1104 | SANTA YNEZ 110477098 | Equipment Failure/Involved | 2025-01-26 02:10 | -08:00 | 01/21 - 01/27 | 2025-01-26 04:45 | -08:00 | 155 | FTS | 21855 | 141 | 1 | 1 | 0 | 0 | 0 | 0 | 155
25-0012934 | Santa Barbara | SISQUOC 1102 | SISQUOC 1102M52 | Unknown Cause | 2025-01-25 12:28 | -08:00 | 01/21 - 01/27 | 2025-01-26 07:33 | -08:00 | 1145 | FTS | 84730 | 74 | 3 | 2 | 1 | 0 | 0 | 0 | 1145
25-0013025 | Santa Barbara | SANTA YNEZ 1104 | SANTA YNEZ 1104Y04 | Unknown Cause | 2025-01-26 08:35 | -08:00 | 01/21 - 01/27 | 2025-01-26 09:25 | -08:00 | 50 | FTS | 22600 | 452 | 4 | 2 | 7 | 2 | 0 | 0 | 50
25-0025491 | Santa Barbara | SISQUOC 1103 | SISQUOC 1102M52 | Company Initiated | 2025-02-26 14:43 | -08:00 | 02/25 - 03/03 | 2025-02-26 15:12 | -08:00 | 29 | FTS | 58 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 29
25-0025780 | Santa Barbara | CABRILLO 1103 | CABRILLO 1103Y10 | Equipment Failure/Involved | 2025-02-27 10:03 | -08:00 | 02/25 - 03/03 | 2025-02-27 14:34 | -08:00 | 91.0167 | FTS | 108856 | 1196 | 38 | 29 | 12 | 1 | 0 | 0 | 271
25-0025993 | Santa Barbara | BUELLTON 1101 | BUELLTON 1101Y06 | Unknown Cause | 2025-02-27 14:53 | -08:00 | 02/25 - 03/03 | 2025-02-27 16:36 | -08:00 | 103 | FTS | 35638 | 346 | 8 | 7 | 9 | 0 | 0 | 0 | 103
25-0025909 | Santa Barbara | CABRILLO 1104 | CABRILLO 1104Y24 | Equipment Failure/Involved | 2025-02-27 13:03 | -08:00 | 02/25 - 03/03 | 2025-02-28 12:20 | -08:00 | 195.9167 | FTS | 14106 | 72 | 2 | 2 | 1 | 0 | 0 | 0 | 1397
25-0026436 | San Luis Obispo | CUYAMA 1103 | CUYAMA 1103622728 | Unknown Cause | 2025-02-28 14:57 | -08:00 | 02/25 - 03/03 | 2025-02-28 18:03 | -08:00 | 186 | FTS | 9858 | 53 | 0 | 0 | 4 | 0 | 0 | 0 | 186
25-0045325 | Tehama | TYLER SUB | N/A | 3rd Party | 2025-04-19 21:10 | -07:00 | 04/15 - 04/21 | 2025-04-19 23:01 | -07:00 | 94.3235 | T-EPSS | 353053 | 3743 | 306 | 230 | 72 | 10 | 4 | 5 | 111
25-0045324 | Tehama | RAWSON SUB | N/A | 3rd Party | 2025-04-19 21:10 | -07:00 | 04/15 - 04/21 | 2025-04-19 23:06 | -07:00 | 7 | T-EPSS | 17745 | 2535 | 166 | 123 | 37 | 14 | 0 | 0 | 116
25-0049492 | Kern | ANTELOPE 1102 | N/A | Equipment Failure/Involved | 2025-05-02 03:39 | -07:00 | 04/29 - 05/05 | 2025-05-02 09:49 | -07:00 | 370 | T-EPSS | 80290 | 217 | 0 | 0 | 12 | 0 | 0 | 0 | 370
25-0049495 | Kern | BERRENDA A 1101 | N/A | Equipment Failure/Involved | 2025-05-02 03:39 | -07:00 | 04/29 - 05/05 | 2025-05-02 10:53 | -07:00 | 434 | T-EPSS | 434 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 434
25-0049494 | Kern | BERRENDA C 0401 | N/A | Equipment Failure/Involved | 2025-05-02 03:39 | -07:00 | 04/29 - 05/05 | 2025-05-02 10:54 | -07:00 | 435 | T-EPSS | 435 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 435
25-0049493 | San Luis Obispo | CHOLAME 1101, CHOLAME 2102 | N/A | Equipment Failure/Involved | 2025-05-02 03:39 | -07:00 | 04/29 - 05/05 | 2025-05-02 16:54 | -07:00 | 533.1973 | T-EPSS | 840319 | 1576 | 39 | 27 | 39 | 6 | 0 | 0 | 795
25-0049496 | Kern | DEVILS DEN 1101, DEVILS DEN 1102 | N/A | Company Initiated | 2025-05-02 03:39 | -07:00 | 04/29 - 05/05 | 2025-05-02 19:24 | -07:00 | 243.192 | T-EPSS | 30399 | 125 | 0 | 0 | 11 | 0 | 0 | 0 | 945
25-0049909 | Glenn | ELK CREEK 1101 | ELK CREEK 11012002 | Company Initiated | 2025-05-03 05:05 | -07:00 | 04/29 - 05/05 | 2025-05-03 09:37 | -07:00 | 233.0515 | FTS | 131208 | 563 | 28 | 19 | 26 | 3 | 0 | 0 | 272
25-0050012 | Glenn | ELK CREEK 1101 | ELK CREEK 11012002 | Company Initiated | 2025-05-03 20:09 | -07:00 | 04/29 - 05/05 | 2025-05-03 22:35 | -07:00 | 143.0844 | FTS | 81415 | 569 | 28 | 19 | 26 | 3 | 0 | 0 | 146
25-0050134 | Monterey | BORONDA 1101, BORONDA 1102 | N/A | Unknown Cause | 2025-05-05 03:09 | -07:00 | 04/29 - 05/05 | 2025-05-05 04:20 | -07:00 | 70.8561 | T-EPSS | 57606 | 813 | 37 | 28 | 13 | 2 | 0 | 0 | 71
25-0050314 | Sonoma | FULTON 1102 | FULTON 1102885254 | Unknown Cause | 2025-05-05 10:35 | -07:00 | 04/29 - 05/05 | 2025-05-05 12:37 | -07:00 | 57.6042 | FTS | 16302 | 283 | 6 | 4 | 3 | 1 | 0 | 1 | 122
25-0050268 | Lake | MIDDLETOWN 1102 | MIDDLETOWN 1102CB | Equipment Failure/Involved | 2025-05-05 09:24 | -07:00 | 04/29 - 05/05 | 2025-05-05 13:13 | -07:00 | 227.7089 | FTS | 588172 | 2583 | 187 | 139 | 37 | 3 | 0 | 2 | 229
25-0050340 | Napa | CALISTOGA 1102 | CALISTOGA 1102706 | Unknown Cause | 2025-05-05 10:56 | -07:00 | 04/29 - 05/05 | 2025-05-05 13:39 | -07:00 | 163 | FTS | 218420 | 1340 | 31 | 19 | 20 | 5 | 0 | 1 | 163
25-0050227 | Solano | VACAVILLE 1103 | VACAVILLE 1103CB | Equipment Failure/Involved | 2025-05-05 08:47 | -07:00 | 04/29 - 05/05 | 2025-05-05 14:25 | -07:00 | 92.6249 | FTS | 218780 | 2362 | 131 | 93 | 32 | 11 | 0 | 0 | 338
25-0050404 | Napa | BASALT 1106 | BASALT 1106657038 | Equipment Failure/Involved | 2025-05-05 12:35 | -07:00 | 04/29 - 05/05 | 2025-05-05 17:28 | -07:00 | 111.6829 | FTS | 13737 | 123 | 0 | 0 | 7 | 0 | 0 | 0 | 293
25-0050346 | Napa | SILVERADO 2102 | SILVERADO 210258626 | Animal | 2025-05-05 11:14 | -07:00 | 04/29 - 05/05 | 2025-05-05 17:53 | -07:00 | 399 | FTS | 122892 | 308 | 4 | 2 | 5 | 0 | 0 | 4 | 399
25-0050527 | Napa | CALISTOGA 1102 | CALISTOGA 1102706 | Unknown Cause | 2025-05-05 15:10 | -07:00 | 04/29 - 05/05 | 2025-05-05 18:03 | -07:00 | 145.1045 | FTS | 194440 | 1340 | 31 | 19 | 20 | 5 | 0 | 1 | 173
25-0050471 | Napa | PUEBLO 2104 | PUEBLO 210438686 | Unknown Cause | 2025-05-05 14:03 | -07:00 | 04/29 - 05/05 | 2025-05-05 18:28 | -07:00 | 258.0639 | FTS | 238193 | 923 | 26 | 15 | 15 | 0 | 0 | 0 | 265
25-0050228 | Solano | VACAVILLE 1108 | VACAVILLE 11088762 | Unknown Cause | 2025-05-05 08:53 | -07:00 | 04/29 - 05/05 | 2025-05-05 18:31 | -07:00 | 269.3366 | FTS | 110428 | 410 | 27 | 22 | 15 | 1 | 0 | 5 | 578
25-0050519 | Contra Costa | BRENTWOOD 2105 | BRENTWOOD 210519062 | Unknown Cause | 2025-05-05 14:58 | -07:00 | 04/29 - 05/05 | 2025-05-05 19:19 | -07:00 | 195.2573 | FTS | 113835 | 583 | 24 | 16 | 25 | 4 | 0 | 0 | 261
25-0050628 | Shasta | STILLWATER 1102 | STILLWATER 110248952 | Animal | 2025-05-05 20:01 | -07:00 | 04/29 - 05/05 | 2025-05-05 22:45 | -07:00 | 115.1111 | FTS | 24864 | 216 | 19 | 14 | 0 | 0 | 0 | 0 | 164
25-0050634 | Sonoma | MONTE RIO 1112 | MONTE RIO 1112CB | Vegetation | 2025-05-05 20:46 | -07:00 | 04/29 - 05/05 | 2025-05-05 23:02 | -07:00 | 126.3528 | FTS | 145053 | 1148 | 45 | 35 | 19 | 0 | 0 | 0 | 136
25-0050637 | Sonoma | DUNBAR 1103 | DUNBAR 1103596218 | Company Initiated | 2025-05-05 20:07 | -07:00 | 05/06 - 05/12 | 2025-05-06 00:22 | -07:00 | 119.25 | FTS | 954 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 255
25-0050651 | Butte | PARADISE 1104 | PARADISE 1104CB | Unknown Cause | 2025-05-06 00:41 | -07:00 | 05/06 - 05/12 | 2025-05-06 02:40 | -07:00 | 86.6675 | FTS | 212682 | 2454 | 165 | 114 | 32 | 2 | 0 | 3 | 119
25-0050661 | Sonoma | DUNBAR 1103 | DUNBAR 1103596218 | Company Initiated | 2025-05-06 06:05 | -07:00 | 05/06 - 05/12 | 2025-05-06 07:07 | -07:00 | 62 | FTS | 310 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 62
25-0050672 | Kern | ANTELOPE 1102 | ANTELOPE 1102CB | Equipment Failure/Involved | 2025-05-06 06:29 | -07:00 | 05/06 - 05/12 | 2025-05-06 07:26 | -07:00 | 57 | T-EPSS | 12369 | 217 | 0 | 0 | 12 | 0 | 0 | 0 | 57
25-0050680 | Contra Costa | ROSSMOOR 1101 | ROSSMOOR 110181770 | Animal | 2025-05-06 06:43 | -07:00 | 05/06 - 05/12 | 2025-05-06 08:03 | -07:00 | 70.3003 | FTS | 24816 | 353 | 28 | 19 | 5 | 0 | 0 | 0 | 80
25-0050663 | Santa Cruz | CAMP EVERS 2105 | CAMP EVERS 2105370732 | Animal | 2025-05-06 06:11 | -07:00 | 05/06 - 05/12 | 2025-05-06 08:09 | -07:00 | 94.1725 | FTS | 40400 | 429 | 15 | 15 | 3 | 1 | 0 | 0 | 118
25-0050596 | Alameda | SAN RAMON 2107 | SAN RAMON 2107MR284 | Company Initiated | 2025-05-05 17:12 | -07:00 | 05/06 - 05/12 | 2025-05-06 08:22 | -07:00 | 910 | FTS | 1128400 | 1240 | 55 | 48 | 18 | 1 | 0 | 2 | 910
25-0050737 | Sonoma | FITCH MOUNTAIN 1113 | FITCH MOUNTAIN 1113154 | Unknown Cause | 2025-05-06 08:21 | -07:00 | 05/06 - 05/12 | 2025-05-06 09:34 | -07:00 | 46.1487 | FTS | 17998 | 390 | 12 | 8 | 10 | 0 | 0 | 8 | 73
25-0050669 | San Luis Obispo | CHOLAME 1101, CHOLAME 2102 | N/A | Animal | 2025-05-06 06:29 | -07:00 | 05/06 - 05/12 | 2025-05-06 10:04 | -07:00 | 180.7497 | T-EPSS | 285223 | 1578 | 39 | 27 | 39 | 6 | 0 | 0 | 215
25-0050385 | Napa | SILVERADO 2102 | SILVERADO 21023010 | Unknown Cause | 2025-05-05 12:14 | -07:00 | 05/06 - 05/12 | 2025-05-06 10:45 | -07:00 | 914.8504 | FTS | 501338 | 548 | 3 | 2 | 12 | 0 | 0 | 1 | 1351
25-0050687 | Kern | DEVILS DEN 1101, DEVILS DEN 1102 | N/A | Equipment Failure/Involved | 2025-05-06 06:29 | -07:00 | 05/06 - 05/12 | 2025-05-06 11:13 | -07:00 | 158.264 | T-EPSS | 19783 | 125 | 0 | 0 | 11 | 0 | 0 | 0 | 284
25-0050933 | Marin | NOVATO 1104 | NOVATO 110438242 | Unknown Cause | 2025-05-06 12:54 | -07:00 | 05/06 - 05/12 | 2025-05-06 15:49 | -07:00 | 174.0714 | FTS | 2437 | 14 | 0 | 0 | 5 | 0 | 0 | 0 | 175
25-0051118 | Contra Costa | MORAGA 1104 | MORAGA 1104CB | Vegetation | 2025-05-06 20:50 | -07:00 | 05/06 - 05/12 | 2025-05-06 22:28 | -07:00 | 98 | FTS | 173166 | 1767 | 94 | 74 | 29 | 5 | 0 | 0 | 98
25-0050655 | Contra Costa | WILLOW PASS 2108 | WILLOW PASS 2108328308 | 3rd Party | 2025-05-06 01:29 | -07:00 | 05/06 - 05/12 | 2025-05-06 23:13 | -07:00 | 90.1178 | FTS | 97958 | 1087 | 60 | 35 | 15 | 0 | 0 | 0 | 1304
25-0050595 | Contra Costa | SAN RAMON 2108 | SAN RAMON 2108CB | Equipment Failure/Involved | 2025-05-05 17:11 | -07:00 | 05/06 - 05/12 | 2025-05-07 03:41 | -07:00 | 301.7181 | FTS | 3383165 | 11213 | 385 | 270 | 125 | 24 | 0 | 1 | 2070
25-0051112 | Contra Costa | LONE TREE 2105 | LONE TREE 2105708440 | Unknown Cause | 2025-05-06 20:32 | -07:00 | 05/06 - 05/12 | 2025-05-07 06:47 | -07:00 | 615 | FTS | 46125 | 75 | 1 | 1 | 2 | 0 | 0 | 0 | 615
25-0051111 | Mendocino | HOPLAND 1101 | HOPLAND 1101865263 | Unknown Cause | 2025-05-06 20:35 | -07:00 | 05/06 - 05/12 | 2025-05-07 07:28 | -07:00 | 547.3662 | FTS | 77726 | 142 | 6 | 4 | 4 | 0 | 0 | 0 | 653
25-0051325 | Glenn | LOGAN CREEK 2101 | LOGAN CREEK 21022428 | Company Initiated | 2025-05-07 10:46 | -07:00 | 05/06 - 05/12 | 2025-05-07 13:59 | -07:00 | 193 | FTS | 28371 | 147 | 1 | 1 | 0 | 0 | 0 | 0 | 193
25-0051408 | Napa | CALISTOGA 1102 | CALISTOGA 1102706 | Equipment Failure/Involved | 2025-05-07 12:57 | -07:00 | 05/06 - 05/12 | 2025-05-08 01:15 | -07:00 | 87.7731 | FTS | 117616 | 1340 | 31 | 19 | 20 | 5 | 0 | 1 | 738
25-0051596 | Santa Barbara | CUYAMA 1103, CUYAMA 1104, CUYAMA 2101, CUYAMA 2102 | N/A | Animal | 2025-05-07 23:18 | -07:00 | 05/06 - 05/12 | 2025-05-08 04:20 | -07:00 | 258.0753 | T-EPSS | 216009 | 837 | 18 | 13 | 15 | 1 | 0 | 0 | 302
25-0051615 | Sonoma | BELLEVUE 2101 | BELLEVUE 2101411782 | Unknown Cause | 2025-05-08 06:17 | -07:00 | 05/06 - 05/12 | 2025-05-08 08:54 | -07:00 | 102.184 | FTS | 119964 | 1174 | 60 | 50 | 25 | 0 | 0 | 31 | 157
25-0051690 | Contra Costa | CLAYTON 2212 | CLAYTON 221296224 | Vegetation | 2025-05-08 08:54 | -07:00 | 05/06 - 05/12 | 2025-05-08 10:44 | -07:00 | 89.2812 | FTS | 22856 | 256 | 18 | 12 | 3 | 0 | 0 | 9 | 110
25-0052020 | Sonoma | MONTE RIO 1112 | MONTE RIO 1112547 | Company Initiated | 2025-05-08 16:20 | -07:00 | 05/06 - 05/12 | 2025-05-08 17:38 | -07:00 | 78 | FTS | 15210 | 195 | 10 | 9 | 5 | 0 | 0 | 0 | 78
25-0052093 | Solano | VACAVILLE 1109 | VACAVILLE 1109592742 | Animal | 2025-05-09 05:46 | -07:00 | 05/06 - 05/12 | 2025-05-09 09:33 | -07:00 | 227 | FTS | 454 | 2 | 0 | 0 | 1 | 1 | 0 | 0 | 227
25-0052080 | Santa Cruz | CAMP EVERS 2105 | CAMP EVERS 2105370732 | Vegetation | 2025-05-09 01:09 | -07:00 | 05/06 - 05/12 | 2025-05-09 13:37 | -07:00 | 341.4615 | FTS | 146487 | 429 | 15 | 15 | 3 | 1 | 0 | 0 | 748
25-0052441 | Glenn | ELK CREEK 1101 | ELK CREEK 11012002 | Company Initiated | 2025-05-09 16:01 | -07:00 | 05/06 - 05/12 | 2025-05-09 19:15 | -07:00 | 194 | FTS | 109222 | 563 | 28 | 19 | 26 | 3 | 0 | 0 | 194
25-0052448 | Santa Cruz | BEN LOMOND 1101 | BEN LOMOND 1101BL 1101 | 3rd Party | 2025-05-09 16:26 | -07:00 | 05/06 - 05/12 | 2025-05-09 23:08 | -07:00 | 121.7162 | FTS | 90922 | 747 | 51 | 48 | 10 | 0 | 0 | 2 | 402
25-0052477 | Santa Cruz | CAMP EVERS 2107 | CAMP EVERS 210511004 | Equipment Failure/Involved | 2025-05-09 19:29 | -07:00 | 05/06 - 05/12 | 2025-05-10 03:02 | -07:00 | 82.563 | FTS | 54409 | 659 | 78 | 64 | 5 | 0 | 0 | 0 | 453
25-0052499 | Plumas | BIG MEADOWS 2101 | BIG MEADOWS 21012056 | Animal | 2025-05-10 03:20 | -07:00 | 05/06 - 05/12 | 2025-05-10 05:47 | -07:00 | 106.6618 | FTS | 80423 | 754 | 37 | 28 | 16 | 3 | 1 | 2 | 147
25-0052507 | Mendocino | HOPLAND 1101 | HOPLAND 1101CB | Animal | 2025-05-10 05:47 | -07:00 | 05/06 - 05/12 | 2025-05-10 06:46 | -07:00 | 57.0401 | FTS | 75350 | 1321 | 61 | 40 | 37 | 16 | 0 | 4 | 59
25-0052573 | Placer | LINCOLN 1101 | LINCOLN 1101210168 | Animal | 2025-05-10 15:38 | -07:00 | 05/06 - 05/12 | 2025-05-10 18:52 | -07:00 | 194 | FTS | 22504 | 116 | 4 | 3 | 0 | 0 | 0 | 6 | 194
25-0052589 | Butte | WYANDOTTE 1107 | WYANDOTTE 11071026 | Animal | 2025-05-10 18:14 | -07:00 | 05/06 - 05/12 | 2025-05-10 19:33 | -07:00 | 57.8082 | FTS | 16880 | 292 | 20 | 16 | 3 | 0 | 0 | 3 | 79
25-0052547 | El Dorado | PLACERVILLE 2106 | PLACERVILLE 210611132 | Company Initiated | 2025-05-10 10:50 | -07:00 | 05/06 - 05/12 | 2025-05-11 10:30 | -07:00 | 709.4546 | FTS | 2173769 | 3064 | 232 | 180 | 67 | 15 | 0 | 17 | 1420
25-0052633 | Sonoma | DUNBAR 1101 | DUNBAR 1101725292 | Vegetation | 2025-05-11 11:50 | -07:00 | 05/06 - 05/12 | 2025-05-11 13:03 | -07:00 | 73 | FTS | 6862 | 94 | 6 | 4 | 2 | 0 | 0 | 0 | 73
25-0052655 | Shasta | BURNEY 1101 | BURNEY 11011322 | 3rd Party | 2025-05-11 14:44 | -07:00 | 05/06 - 05/12 | 2025-05-11 15:56 | -07:00 | 72 | FTS | 4896 | 68 | 3 | 3 | 0 | 0 | 0 | 0 | 72
25-0052666 | Shasta | BURNEY 1101 | BURNEY 11011322 | 3rd Party | 2025-05-11 16:06 | -07:00 | 05/06 - 05/12 | 2025-05-11 16:48 | -07:00 | 42 | FTS | 2856 | 68 | 3 | 3 | 0 | 0 | 0 | 0 | 42
25-0052677 | Amador | PINE GROVE 1101 | PINE GROVE 1101580912 | Animal | 2025-05-11 17:07 | -07:00 | 05/06 - 05/12 | 2025-05-11 18:30 | -07:00 | 55.1577 | FTS | 38114 | 691 | 49 | 35 | 14 | 0 | 0 | 7 | 83
25-0052672 | Shasta | FRENCH GULCH 1101 | FRENCH GULCH 11011464 | Unknown Cause | 2025-05-11 16:39 | -07:00 | 05/06 - 05/12 | 2025-05-11 19:58 | -07:00 | 199 | FTS | 14925 | 75 | 4 | 4 | 1 | 0 | 0 | 0 | 199
25-0052689 | Alameda | VASCO 1102 | VASCO 1102546328 | Vegetation | 2025-05-11 19:16 | -07:00 | 05/06 - 05/12 | 2025-05-12 06:19 | -07:00 | 614.3363 | FTS | 138840 | 226 | 15 | 11 | 7 | 0 | 0 | 2 | 663
25-0052648 | Plumas | CHESTER 1101, CHESTER 1102 | N/A | Vegetation | 2025-05-11 13:56 | -07:00 | 05/06 - 05/12 | 2025-05-12 07:57 | -07:00 | 1080.4032 | T-EPSS | 1803193 | 1669 | 67 | 54 | 44 | 11 | 6 | 0 | 1081
25-0052769 | Shasta | VOLTA 1102 | VOLTA 11029742 | Unknown Cause | 2025-05-12 08:30 | -07:00 | 05/06 - 05/12 | 2025-05-12 08:40 | -07:00 | 10 | FTS | 4850 | 485 | 49 | 40 | 3 | 0 | 0 | 0 | 10
25-0052669 | Shasta | PIT NO 5 1101 | PIT NO 5 11011658 | Unknown Cause | 2025-05-11 16:15 | -07:00 | 05/06 - 05/12 | 2025-05-12 09:54 | -07:00 | 550.6991 | FTS | 62229 | 113 | 2 | 1 | 9 | 2 | 0 | 0 | 1059
25-0052874 | Shasta | BURNEY 1101 | BURNEY 1101355340 | 3rd Party | 2025-05-12 10:43 | -07:00 | 05/06 - 05/12 | 2025-05-12 10:57 | -07:00 | 14 | FTS | 14 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 14
25-0053086 | Glenn | GLENN 1101 | GLENN 110137496 | 3rd Party | 2025-05-12 16:30 | -07:00 | 05/06 - 05/12 | 2025-05-12 17:29 | -07:00 | 28.6456 | FTS | 4526 | 158 | 2 | 0 | 12 | 0 | 0 | 0 | 59
25-0054076 | Colusa | WILLIAMS 1102 | WILLIAMS 110230232 | Animal | 2025-05-14 18:05 | -07:00 | 05/13 - 05/19 | 2025-05-14 20:11 | -07:00 | 126 | FTS | 17766 | 141 | 2 | 0 | 1 | 0 | 0 | 0 | 126
25-0054081 | Monterey | SAN MIGUEL 1106 | SAN MIGUEL 1106605393 | Unknown Cause | 2025-05-14 19:46 | -07:00 | 05/13 - 05/19 | 2025-05-14 22:59 | -07:00 | 193 | FTS | 17370 | 90 | 2 | 1 | 1 | 0 | 0 | 1 | 193
25-0054148 | San Luis Obispo | PERRY 1101, PERRY 1104 | N/A | Equipment Failure/Involved | 2025-05-15 07:43 | -07:00 | 05/13 - 05/19 | 2025-05-15 07:51 | -07:00 | 8 | T-EPSS | 41576 | 5197 | 152 | 117 | 75 | 6 | 3 | 12 | 8
25-0054463 | San Luis Obispo | CHOLAME 1101 | CHOLAME 1101X18 | Animal | 2025-05-15 14:46 | -07:00 | 05/13 - 05/19 | 2025-05-15 17:35 | -07:00 | 169 | FTS | 1352 | 8 | 0 | 0 | 4 | 0 | 0 | 0 | 169
25-0054747 | Napa | CALISTOGA 1102 | CALISTOGA 1102270153 | Company Initiated | 2025-05-16 10:30 | -07:00 | 05/13 - 05/19 | 2025-05-16 10:45 | -07:00 | 8.525 | FTS | 341 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 15
25-0054874 | Sonoma | CLOVERDALE 1102 | CLOVERDALE 1102672 | Company Initiated | 2025-05-16 13:33 | -07:00 | 05/13 - 05/19 | 2025-05-16 13:44 | -07:00 | 11 | FTS | 506 | 46 | 6 | 3 | 1 | 0 | 0 | 0 | 11
25-0055025 | Lake | REDBUD 1102 | REDBUD 1102432 | Unknown Cause | 2025-05-16 18:58 | -07:00 | 05/13 - 05/19 | 2025-05-16 20:42 | -07:00 | 52.9618 | FTS | 108042 | 2040 | 141 | 91 | 22 | 1 | 0 | 0 | 104
25-0055032 | Sonoma | DUNBAR 1103 | DUNBAR 1103596218 | Company Initiated | 2025-05-16 20:19 | -07:00 | 05/13 - 05/19 | 2025-05-16 21:15 | -07:00 | 56 | FTS | 280 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 56
25-0055036 | Monterey | CAMPHORA 1101 | CAMPHORA 110122412 | 3rd Party | 2025-05-16 20:49 | -07:00 | 05/13 - 05/19 | 2025-05-16 22:52 | -07:00 | 123 | FTS | 15498 | 126 | 0 | 0 | 0 | 0 | 0 | 0 | 123
25-0055031 | Santa Clara | SARATOGA 1106 | SARATOGA 1106340986 | Unknown Cause | 2025-05-16 19:55 | -07:00 | 05/13 - 05/19 | 2025-05-16 23:07 | -07:00 | 184.4181 | FTS | 105856 | 574 | 24 | 12 | 5 | 0 | 0 | 0 | 192
25-0055048 | Sonoma | LAKEVILLE 1102 | LAKEVILLE 1102367100 | Unknown Cause | 2025-05-16 23:43 | -07:00 | 05/13 - 05/19 | 2025-05-17 00:39 | -07:00 | 56 | FTS | 504 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 56
25-0055060 | Santa Barbara | CABRILLO 1104 | CABRILLO 1104838078 | Equipment Failure/Involved | 2025-05-17 04:38 | -07:00 | 05/13 - 05/19 | 2025-05-17 08:11 | -07:00 | 213 | FTS | 53037 | 249 | 2 | 1 | 5 | 0 | 0 | 0 | 213
25-0055066 | Alameda | BERKELEY F 1103 | BERKELEY F 1103162952 | Unknown Cause | 2025-05-17 06:05 | -07:00 | 05/13 - 05/19 | 2025-05-17 08:37 | -07:00 | 81.8641 | FTS | 25296 | 309 | 2 | 2 | 6 | 1 | 0 | 0 | 152
25-0055065 | Fresno | SHEPHERD 2111 | SHEPHERD 2111707358 | Unknown Cause | 2025-05-17 06:08 | -07:00 | 05/13 - 05/19 | 2025-05-17 10:24 | -07:00 | 126.4937 | FTS | 50218 | 397 | 25 | 22 | 5 | 0 | 0 | 3 | 256
25-0055113 | Marin | ALTO 1124 | ALTO 1124870444 | Vegetation | 2025-05-17 09:25 | -07:00 | 05/13 - 05/19 | 2025-05-17 10:49 | -07:00 | 84 | FTS | 17724 | 211 | 4 | 1 | 2 | 0 | 0 | 0 | 84
25-0055116 | San Joaquin | HERDLYN 1102 | HERDLYN 1102608254 | Unknown Cause | 2025-05-17 09:21 | -07:00 | 05/13 - 05/19 | 2025-05-17 11:21 | -07:00 | 120 | FTS | 63600 | 530 | 38 | 21 | 20 | 3 | 0 | 0 | 120
25-0055082 | Merced | GUSTINE 1102 | GUSTINE 11026926 | Animal | 2025-05-17 07:56 | -07:00 | 05/13 - 05/19 | 2025-05-17 12:11 | -07:00 | 255 | FTS | 51765 | 203 | 3 | 3 | 2 | 0 | 0 | 0 | 255
25-0055151 | Madera | COARSEGOLD 2104 | COARSEGOLD 210410400 | Animal | 2025-05-17 10:57 | -07:00 | 05/13 - 05/19 | 2025-05-17 12:57 | -07:00 | 79.5739 | FTS | 119520 | 1502 | 127 | 93 | 38 | 2 | 0 | 1 | 120
25-0055178 | Placer | BONNIE NOOK 1102 | BONNIE NOOK 1102542186 | 3rd Party | 2025-05-17 12:55 | -07:00 | 05/13 - 05/19 | 2025-05-17 13:47 | -07:00 | 52 | FTS | 4784 | 92 | 6 | 4 | 1 | 0 | 0 | 2 | 52
25-0055117 | Calaveras | CORRAL 1103 | CORRAL 110314716 | Unknown Cause | 2025-05-17 09:32 | -07:00 | 05/13 - 05/19 | 2025-05-17 13:49 | -07:00 | 257 | FTS | 12336 | 48 | 1 | 0 | 3 | 0 | 0 | 0 | 257
25-0055073 | Monterey | SAN ARDO 1102 | SAN ARDO 11027030 | Unknown Cause | 2025-05-17 07:19 | -07:00 | 05/13 - 05/19 | 2025-05-17 15:13 | -07:00 | 474 | FTS | 49770 | 105 | 1 | 1 | 8 | 0 | 0 | 0 | 474
25-0055188 | Marin | ALTO 1124 | ALTO 1124432 | Vegetation | 2025-05-17 14:13 | -07:00 | 05/13 - 05/19 | 2025-05-17 15:16 | -07:00 | 63 | FTS | 43029 | 683 | 21 | 14 | 7 | 0 | 0 | 0 | 63
25-0055216 | San Luis Obispo | CHOLAME 1101 | CHOLAME 1101CB | Unknown Cause | 2025-05-17 16:00 | -07:00 | 05/13 - 05/19 | 2025-05-17 18:14 | -07:00 | 134 | FTS | 169376 | 1264 | 36 | 25 | 26 | 6 | 0 | 0 | 134
25-0055170 | Santa Cruz | CAMP EVERS 2107 | CAMP EVERS 210711006 | Vegetation | 2025-05-17 12:07 | -07:00 | 05/13 - 05/19 | 2025-05-17 18:42 | -07:00 | 87.4777 | FTS | 196475 | 2246 | 166 | 132 | 39 | 1 | 0 | 2 | 395
25-0047435 | Tuolumne | PEORIA 1705 | PEORIA 170590374 | Company Initiated | 2025-05-17 17:54 | -07:00 | 05/13 - 05/19 | 2025-05-17 18:47 | -07:00 | 53 | FTS | 61533 | 1161 | 91 | 75 | 6 | 0 | 0 | 8 | 53
25-0055242 | Marin | SAN RAFAEL 1108 | SAN RAFAEL 1108583502 | Vegetation | 2025-05-17 18:30 | -07:00 | 05/13 - 05/19 | 2025-05-17 19:04 | -07:00 | 28.037 | FTS | 86494 | 3085 | 105 | 68 | 24 | 1 | 0 | 1 | 34
25-0055248 | San Luis Obispo | BAYWOOD 1101 | BAYWOOD 1101V102 | Vegetation | 2025-05-17 19:23 | -07:00 | 05/13 - 05/19 | 2025-05-17 20:05 | -07:00 | 42 | FTS | 252 | 6 | 0 | 0 | 1 | 2 | 0 | 0 | 42
25-0055254 | San Luis Obispo | BAYWOOD 1101 | BAYWOOD 1101V102 | Vegetation | 2025-05-17 20:21 | -07:00 | 05/13 - 05/19 | 2025-05-17 21:09 | -07:00 | 48 | FTS | 288 | 6 | 0 | 0 | 1 | 2 | 0 | 0 | 48
25-0055228 | Contra Costa | SOBRANTE 1103 | SOBRANTE 1103LA401R | Vegetation | 2025-05-17 16:44 | -07:00 | 05/13 - 05/19 | 2025-05-17 21:46 | -07:00 | 113.9907 | FTS | 48902 | 429 | 24 | 18 | 4 | 0 | 0 | 0 | 302
25-0055177 | San Mateo | RALSTON 1101 | RALSTON 110148936 | Equipment Failure/Involved | 2025-05-17 12:58 | -07:00 | 05/13 - 05/19 | 2025-05-17 22:04 | -07:00 | 103.0527 | FTS | 168182 | 1632 | 50 | 35 | 30 | 2 | 0 | 0 | 546
25-0055189 | Placer | BELL 1107 | BELL 11072400 | 3rd Party | 2025-05-17 14:10 | -07:00 | 05/13 - 05/19 | 2025-05-17 23:36 | -07:00 | 257.2502 | FTS | 404140 | 1571 | 89 | 64 | 34 | 2 | 0 | 17 | 566
25-0055259 | Santa Barbara | CABRILLO 1104 | CABRILLO 1104838078 | Equipment Failure/Involved | 2025-05-17 21:34 | -07:00 | 05/13 - 05/19 | 2025-05-18 01:27 | -07:00 | 233 | FTS | 58017 | 249 | 2 | 1 | 5 | 0 | 0 | 0 | 233
25-0055231 | Santa Clara | LOS GATOS 1106 | LOS GATOS 1106648186 | Vegetation | 2025-05-17 16:52 | -07:00 | 05/13 - 05/19 | 2025-05-18 01:47 | -07:00 | 236.0409 | FTS | 375305 | 1590 | 128 | 104 | 26 | 3 | 0 | 20 | 535
25-0055240 | Solano | JAMESON 1105 | JAMESON 1105CB | 3rd Party | 2025-05-17 18:03 | -07:00 | 05/13 - 05/19 | 2025-05-18 02:37 | -07:00 | 76.7684 | FTS | 203897 | 2656 | 83 | 64 | 33 | 10 | 1 | 4 | 514
25-0055217 | Santa Cruz | ROB ROY 2104 | ROB ROY 210467520 | Vegetation | 2025-05-17 16:01 | -07:00 | 05/13 - 05/19 | 2025-05-18 03:12 | -07:00 | 78.4644 | FTS | 214757 | 2737 | 149 | 120 | 41 | 7 | 0 | 0 | 671
25-0055244 | Madera | OAKHURST 1103 | OAKHURST 1103CB | Company Initiated | 2025-05-17 18:56 | -07:00 | 05/13 - 05/19 | 2025-05-18 07:39 | -07:00 | 622.8386 | FTS | 2300143 | 3693 | 181 | 134 | 88 | 20 | 0 | 4 | 763
25-0055276 | Nevada | NARROWS 2102 | NARROWS 210248484 | Animal | 2025-05-18 06:24 | -07:00 | 05/13 - 05/19 | 2025-05-18 08:32 | -07:00 | 73.1047 | FTS | 65648 | 898 | 48 | 28 | 18 | 5 | 0 | 26 | 128
25-0055282 | Napa | PUEBLO 1105 | PUEBLO 1105348368 | Unknown Cause | 2025-05-18 07:33 | -07:00 | 05/13 - 05/19 | 2025-05-18 08:57 | -07:00 | 84 | FTS | 16968 | 202 | 13 | 7 | 1 | 0 | 0 | 5 | 84
25-0055294 | Napa | SILVERADO 2102 | SILVERADO 2102942170 | Unknown Cause | 2025-05-18 09:14 | -07:00 | 05/13 - 05/19 | 2025-05-18 10:17 | -07:00 | 63 | FTS | 12726 | 202 | 1 | 0 | 3 | 0 | 0 | 1 | 63
25-0055280 | Stanislaus | COTTLE 1701 | COTTLE 170178452 | Unknown Cause | 2025-05-18 07:18 | -07:00 | 05/13 - 05/19 | 2025-05-18 11:11 | -07:00 | 149.3639 | FTS | 52128 | 349 | 21 | 16 | 10 | 1 | 0 | 0 | 233
25-0055302 | Marin | COTATI 1105 | COTATI 1105616 | Equipment Failure/Involved | 2025-05-18 10:06 | -07:00 | 05/13 - 05/19 | 2025-05-18 12:11 | -07:00 | 116.5348 | FTS | 26803 | 230 | 5 | 4 | 6 | 0 | 0 | 1 | 125
25-0055291 | San Joaquin | VALLEY HOME 1703 | VALLEY HOME 17031558 | Unknown Cause | 2025-05-18 08:49 | -07:00 | 05/13 - 05/19 | 2025-05-18 12:43 | -07:00 | 216.0994 | FTS | 39114 | 181 | 3 | 1 | 6 | 0 | 0 | 0 | 234
25-0055272 | El Dorado | SHINGLE SPRINGS 1104 | SHINGLE SPRINGS 1104556218 | 3rd Party | 2025-05-18 03:31 | -07:00 | 05/13 - 05/19 | 2025-05-18 13:37 | -07:00 | 114.8356 | FTS | 74758 | 651 | 54 | 42 | 4 | 0 | 0 | 26 | 606
25-0055312 | Placer | HORSESHOE 1101 | HORSESHOE 110151538 | Unknown Cause | 2025-05-18 10:14 | -07:00 | 05/13 - 05/19 | 2025-05-18 14:21 | -07:00 | 172.2108 | FTS | 63718 | 370 | 17 | 9 | 8 | 0 | 0 | 0 | 247
25-0055342 | Monterey | JOLON 1103 | JOLON 1103549180 | 3rd Party | 2025-05-18 14:45 | -07:00 | 05/13 - 05/19 | 2025-05-18 14:58 | -07:00 | 13 | FTS | 117 | 9 | 0 | 0 | 6 | 0 | 0 | 0 | 13
25-0055317 | Monterey | KING CITY 1103 | KING CITY 11037038 | Company Initiated | 2025-05-18 11:17 | -07:00 | 05/13 - 05/19 | 2025-05-18 15:02 | -07:00 | 89.5232 | FTS | 71350 | 797 | 45 | 36 | 15 | 0 | 0 | 0 | 225
25-0055304 | Sonoma | FITCH MOUNTAIN 1113 | FITCH MOUNTAIN 1113775992 | Equipment Failure/Involved | 2025-05-18 10:20 | -07:00 | 05/13 - 05/19 | 2025-05-18 18:50 | -07:00 | 172.7703 | FTS | 61679 | 357 | 7 | 4 | 1 | 0 | 0 | 4 | 510
25-0055370 | Calaveras | Valley Springs 1101 | Valley Springs 1101207256 | Unknown Cause | 2025-05-18 20:39 | -07:00 | 05/13 - 05/19 | 2025-05-18 21:30 | -07:00 | 44.826 | FTS | 72663 | 1621 | 111 | 82 | 38 | 5 | 1 | 0 | 51
25-0055372 | Shasta | PIT NO 5 1101 | PIT NO 5 1101884224 | Equipment Failure/Involved | 2025-05-18 21:22 | -07:00 | 05/13 - 05/19 | 2025-05-18 21:38 | -07:00 | 16 | FTS | 784 | 49 | 0 | 0 | 1 | 0 | 0 | 0 | 16
25-0055335 | Sonoma | GEYSERVILLE 1102 | GEYSERVILLE 1102429530 | Vegetation | 2025-05-18 14:07 | -07:00 | 05/13 - 05/19 | 2025-05-19 00:58 | -07:00 | 135.6661 | FTS | 77194 | 569 | 6 | 1 | 11 | 1 | 0 | 3 | 651
25-0055384 | Sonoma | WINDSOR 1103 | WINDSOR 11035060 | Unknown Cause | 2025-05-19 01:40 | -07:00 | 05/13 - 05/19 | 2025-05-19 02:48 | -07:00 | 64.525 | FTS | 36134 | 560 | 25 | 17 | 10 | 1 | 0 | 2 | 68
25-0055394 | Mendocino | HOPLAND 1101 | HOPLAND 1101154790 | Animal | 2025-05-19 05:41 | -07:00 | 05/13 - 05/19 | 2025-05-19 07:10 | -07:00 | 89 | FTS | 40762 | 458 | 61 | 40 | 37 | 16 | 0 | 4 | 89
25-0055398 | Santa Cruz | BIG BASIN 1101 | BIG BASIN 1101393582 | Unknown Cause | 2025-05-19 06:34 | -07:00 | 05/13 - 05/19 | 2025-05-19 07:52 | -07:00 | 46.3491 | FTS | 29478 | 636 | 42 | 36 | 10 | 0 | 0 | 2 | 78
25-0055376 | Calaveras | STANISLAUS 1701 | STANISLAUS 170179826 | Company Initiated | 2025-05-18 22:00 | -07:00 | 05/13 - 05/19 | 2025-05-19 09:06 | -07:00 | 666 | FTS | 93240 | 140 | 7 | 6 | 3 | 0 | 0 | 0 | 666
25-0055521 | Lake | KONOCTI 1102 | KONOCTI 1102716 | Unknown Cause | 2025-05-19 10:47 | -07:00 | 05/13 - 05/19 | 2025-05-19 13:17 | -07:00 | 84.2532 | FTS | 65886 | 782 | 39 | 24 | 14 | 0 | 0 | 0 | 150
25-0055620 | Madera | SAN JOAQUIN #3 1103 | SAN JOAQUIN #3 1103403515 | Company Initiated | 2025-05-19 12:43 | -07:00 | 05/13 - 05/19 | 2025-05-19 13:22 | -07:00 | 39 | FTS | 5148 | 132 | 8 | 5 | 2 | 0 | 0 | 0 | 39
25-0055361 | San Mateo | WOODSIDE 1101 | WOODSIDE 11018522 | Unknown Cause | 2025-05-18 17:21 | -07:00 | 05/13 - 05/19 | 2025-05-19 13:32 | -07:00 | 783.5108 | FTS | 1632053 | 2083 | 69 | 51 | 65 | 19 | 0 | 3 | 1211
25-0055407 | Santa Cruz | ROB ROY 2104 | ROB ROY 210410714 | Equipment Failure/Involved | 2025-05-19 07:01 | -07:00 | 05/13 - 05/19 | 2025-05-19 13:50 | -07:00 | 93.974 | FTS | 541760 | 5765 | 289 | 239 | 101 | 15 | 0 | 4 | 409
25-0055766 | Sonoma | MOLINO 1101 | MOLINO 1101338 | Vegetation | 2025-05-19 17:26 | -07:00 | 05/13 - 05/19 | 2025-05-19 18:28 | -07:00 | 62 | FTS | 22816 | 368 | 13 | 6 | 8 | 3 | 0 | 8 | 62
25-0055700 | El Dorado | APPLE HILL 2102 | APPLE HILL 2102836878 | Company Initiated | 2025-05-19 15:01 | -07:00 | 05/13 - 05/19 | 2025-05-19 18:56 | -07:00 | 201.7473 | FTS | 1004500 | 4979 | 393 | 293 | 65 | 12 | 0 | 63 | 235
25-0055603 | San Mateo | WOODSIDE 1101 | WOODSIDE 11018884 | Unknown Cause | 2025-05-19 12:46 | -07:00 | 05/13 - 05/19 | 2025-05-19 19:32 | -07:00 | 402.3721 | FTS | 138416 | 344 | 15 | 9 | 28 | 1 | 0 | 0 | 406
25-0055772 | Marin | SAN RAFAEL 1105 | SAN RAFAEL 1105194366 | Animal | 2025-05-19 18:31 | -07:00 | 05/13 - 05/19 | 2025-05-19 19:34 | -07:00 | 6.4682 | FTS | 12600 | 1948 | 77 | 43 | 35 | 5 | 0 | 1 | 63
25-0055744 | Butte | OROVILLE 1103 | OROVILLE 110313028 | Unknown Cause | 2025-05-19 16:11 | -07:00 | 05/13 - 05/19 | 2025-05-19 19:41 | -07:00 | 118.6243 | HLT | 106406 | 897 | 61 | 44 | 27 | 7 | 0 | 0 | 210
25-0055778 | Merced | WRIGHT 1110 | WRIGHT 111084280 | Equipment Failure/Involved | 2025-05-19 19:15 | -07:00 | 05/13 - 05/19 | 2025-05-19 19:55 | -07:00 | 40 | FTS | 68800 | 1720 | 53 | 37 | 14 | 1 | 0 | 0 | 40
25-0055404 | Sonoma | FITCH MOUNTAIN 1113 | FITCH MOUNTAIN 1113356 | Vegetation | 2025-05-19 06:47 | -07:00 | 05/13 - 05/19 | 2025-05-19 20:45 | -07:00 | 109.5458 | FTS | 33521 | 306 | 7 | 5 | 4 | 0 | 0 | 2 | 838
25-0055760 | Butte | OROVILLE 1104 | OROVILLE 1104CB | 3rd Party | 2025-05-19 16:58 | -07:00 | 05/20 - 05/26 | 2025-05-20 04:14 | -07:00 | 152.2241 | FTS | 292118 | 1919 | 159 | 113 | 21 | 5 | 3 | 1 | 676
25-0055806 | San Benito | HOLLISTER 2105 | HOLLISTER 21054018 | Unknown Cause | 2025-05-20 02:38 | -07:00 | 05/20 - 05/26 | 2025-05-20 05:12 | -07:00 | 88.8792 | FTS | 21331 | 240 | 3 | 1 | 5 | 1 | 0 | 0 | 154
25-0055807 | San Luis Obispo | TEMPLETON 2111 | TEMPLETON 2111A66 | Vegetation | 2025-05-20 04:04 | -07:00 | 05/20 - 05/26 | 2025-05-20 06:39 | -07:00 | 121.88 | FTS | 280324 | 2300 | 138 | 83 | 33 | 8 | 0 | 9 | 155
25-0055845 | Lake | CLEAR LAKE 1101 | CLEAR LAKE 1101872376 | Animal | 2025-05-20 07:38 | -07:00 | 05/20 - 05/26 | 2025-05-20 08:58 | -07:00 | 80 | FTS | 26000 | 325 | 16 | 13 | 2 | 0 | 0 | 0 | 80
25-0055839 | San Luis Obispo | CHOLAME 1101 | CHOLAME 1101X12 | Animal | 2025-05-20 07:35 | -07:00 | 05/20 - 05/26 | 2025-05-20 09:53 | -07:00 | 138 | FTS | 7176 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 138
25-0055790 | Mendocino | UKIAH 1114 | UKIAH 1114408 | Unknown Cause | 2025-05-19 21:18 | -07:00 | 05/20 - 05/26 | 2025-05-20 09:55 | -07:00 | 422.9074 | FTS | 137022 | 324 | 15 | 9 | 8 | 1 | 0 | 0 | 757
25-0055911 | Monterey | GABILAN 1102 | GABILAN 1101566352 | Company Initiated | 2025-05-20 09:27 | -07:00 | 05/20 - 05/26 | 2025-05-20 10:06 | -07:00 | 39 | FTS | 195 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 39
25-0055993 | Alameda | SAN RAMON 2106 | SAN RAMON 2106MR285 | Unknown Cause | 2025-05-20 11:14 | -07:00 | 05/20 - 05/26 | 2025-05-20 12:21 | -07:00 | 67 | FTS | 58625 | 875 | 31 | 21 | 12 | 2 | 0 | 0 | 67
25-0055871 | Monterey | GABILAN 1102 | GABILAN 11013034 | Equipment Failure/Involved | 2025-05-20 08:17 | -07:00 | 05/20 - 05/26 | 2025-05-20 13:04 | -07:00 | 69.256 | FTS | 37606 | 543 | 23 | 19 | 11 | 0 | 0 | 0 | 287
25-0056033 | Marin | SAN RAFAEL 1101 | SAN RAFAEL 1101CB | 3rd Party | 2025-05-20 11:47 | -07:00 | 05/20 - 05/26 | 2025-05-20 13:19 | -07:00 | 86.6106 | FTS | 317168 | 3662 | 76 | 50 | 75 | 33 | 0 | 3 | 92
25-0056132 | Sonoma | MIRABEL 1102 | MIRABEL 110238514 | Company Initiated | 2025-05-20 13:32 | -07:00 | 05/20 - 05/26 | 2025-05-20 13:44 | -07:00 | 12 | FTS | 792 | 66 | 3 | 1 | 2 | 0 | 0 | 0 | 12
25-0056168 | Sonoma | MIRABEL 1102 | MIRABEL 110238514 | Company Initiated | 2025-05-20 13:42 | -07:00 | 05/20 - 05/26 | 2025-05-20 14:54 | -07:00 | 72 | FTS | 4320 | 60 | 4 | 3 | 0 | 0 | 0 | 0 | 72
25-0056144 | Santa Clara | MC KEE 1103 | MC KEE 1103333750 | Animal | 2025-05-20 13:55 | -07:00 | 05/20 - 05/26 | 2025-05-20 15:00 | -07:00 | 65 | FTS | 5005 | 77 | 3 | 0 | 2 | 0 | 0 | 0 | 65
25-0056270 | Sonoma | SONOMA 1102 | SONOMA 1102441730 | Company Initiated | 2025-05-20 16:26 | -07:00 | 05/20 - 05/26 | 2025-05-20 16:38 | -07:00 | 12 | FTS | 252 | 21 | 0 | 0 | 3 | 0 | 0 | 0 | 12
25-0056228 | Glenn | LOGAN CREEK 2102 | LOGAN CREEK 21022428 | Company Initiated | 2025-05-20 15:35 | -07:00 | 05/20 - 05/26 | 2025-05-20 19:21 | -07:00 | 226 | FTS | 33222 | 147 | 1 | 1 | 0 | 0 | 0 | 0 | 226
25-0056260 | Amador | TIGER CREEK 0201 | TIGER CREEK 0201320746 | Unknown Cause | 2025-05-20 16:23 | -07:00 | 05/20 - 05/26 | 2025-05-20 19:27 | -07:00 | 184 | FTS | 552 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 184
25-0055804 | Fresno | TIVY VALLEY 1107 | TIVY VALLEY 11077380 | Unknown Cause | 2025-05-20 01:32 | -07:00 | 05/20 - 05/26 | 2025-05-20 20:36 | -07:00 | 105.1505 | FTS | 117348 | 1116 | 63 | 48 | 19 | 0 | 0 | 2 | 1144
25-0056199 | Monterey | SOLEDAD 2101 | SOLEDAD 2101107872 | Unknown Cause | 2025-05-20 14:56 | -07:00 | 05/20 - 05/26 | 2025-05-20 21:22 | -07:00 | 386 | FTS | 12738 | 33 | 1 | 1 | 0 | 0 | 0 | 0 | 386
25-0055793 | Fresno | TIVY VALLEY 1107 | TIVY VALLEY 1107248306 | Animal | 2025-05-19 22:24 | -07:00 | 05/20 - 05/26 | 2025-05-21 03:04 | -07:00 | 748.1389 | FTS | 26933 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 1720
25-0056428 | Amador | OLETA 1101 | OLETA 110163500 | Company Initiated | 2025-05-21 08:19 | -07:00 | 05/20 - 05/26 | 2025-05-21 08:33 | -07:00 | 14 | FTS | 9114 | 651 | 29 | 18 | 10 | 2 | 0 | 2 | 14
25-0056327 | Marin | NOVATO 1104 | NOVATO 110438242 | Unknown Cause | 2025-05-20 20:41 | -07:00 | 05/20 - 05/26 | 2025-05-21 09:00 | -07:00 | 141.9286 | FTS | 1987 | 14 | 0 | 0 | 5 | 0 | 0 | 0 | 739
25-0056407 | Contra Costa | MORAGA 1105 | MORAGA 1105CB | Unknown Cause | 2025-05-21 07:55 | -07:00 | 05/20 - 05/26 | 2025-05-21 09:52 | -07:00 | 94.6009 | FTS | 179458 | 1897 | 82 | 62 | 17 | 6 | 0 | 1 | 117
25-0056509 | Butte | WYANDOTTE 1103 | WYANDOTTE 1103716082 | 3rd Party | 2025-05-21 10:18 | -07:00 | 05/20 - 05/26 | 2025-05-21 11:39 | -07:00 | 77.6647 | FTS | 103061 | 1327 | 103 | 82 | 20 | 1 | 0 | 3 | 81
25-0056559 | San Mateo | SNEATH LANE 1101 | SNEATH LANE 11016525 | Unknown Cause | 2025-05-21 12:17 | -07:00 | 05/20 - 05/26 | 2025-05-21 13:55 | -07:00 | 98 | FTS | 81928 | 836 | 60 | 47 | 6 | 1 | 0 | 0 | 98
25-0056739 | Butte | BIG BEND 1102 | BIG BEND 1102CB | Unknown Cause | 2025-05-21 15:59 | -07:00 | 05/20 - 05/26 | 2025-05-21 18:11 | -07:00 | 132 | FTS | 43956 | 333 | 11 | 8 | 10 | 0 | 0 | 0 | 132
25-0056535 | Sonoma | GEYSERVILLE 1102 | GEYSERVILLE 1102785626 | Equipment Failure/Involved | 2025-05-21 11:02 | -07:00 | 05/20 - 05/26 | 2025-05-21 20:25 | -07:00 | 116.5439 | FTS | 41140 | 353 | 3 | 1 | 8 | 0 | 0 | 3 | 563
25-0056821 | Sonoma | MONTE RIO 1113 | MONTE RIO 11135024 | Unknown Cause | 2025-05-21 19:55 | -07:00 | 05/20 - 05/26 | 2025-05-21 21:05 | -07:00 | 70 | FTS | 27860 | 398 | 26 | 16 | 4 | 1 | 0 | 0 | 70
25-0056651 | Alameda | CASTRO VALLEY 1110 | CASTRO VALLEY 1110MR273 | 3rd Party | 2025-05-21 14:30 | -07:00 | 05/20 - 05/26 | 2025-05-21 22:30 | -07:00 | 227.524 | FTS | 47325 | 208 | 14 | 11 | 1 | 1 | 0 | 3 | 480
25-0056217 | Tulare | DUNLAP 1102 | DUNLAP 11027050 | Equipment Failure/Involved | 2025-05-20 15:25 | -07:00 | 05/20 - 05/26 | 2025-05-21 22:53 | -07:00 | 627.193 | FTS | 35750 | 57 | 0 | 0 | 5 | 0 | 0 | 0 | 1888
25-0056800 | Merced | WILSON 1103 | WILSON 11039080 | Unknown Cause | 2025-05-21 18:20 | -07:00 | 05/20 - 05/26 | 2025-05-21 23:58 | -07:00 | 115.1489 | FTS | 363410 | 3156 | 55 | 31 | 16 | 6 | 0 | 0 | 338
25-0056839 | Alameda | CAYETANO 2111 | CAYETANO 2111MR444 | Equipment Failure/Involved | 2025-05-22 00:31 | -07:00 | 05/20 - 05/26 | 2025-05-22 03:56 | -07:00 | 205 | FTS | 615 | 3 | 0 | 0 | 3 | 3 | 0 | 0 | 205
25-0056837 | San Mateo | WOODSIDE 1101 | WOODSIDE 11018972 | Vegetation | 2025-05-22 00:29 | -07:00 | 05/20 - 05/26 | 2025-05-22 04:47 | -07:00 | 258 | FTS | 17286 | 67 | 5 | 4 | 1 | 1 | 0 | 0 | 258
25-0056852 | Sonoma | COTATI 1102 | COTATI 110259258 | Unknown Cause | 2025-05-22 04:12 | -07:00 | 05/20 - 05/26 | 2025-05-22 05:42 | -07:00 | 90 | FTS | 22950 | 255 | 14 | 12 | 4 | 0 | 0 | 1 | 90
25-0056825 | San Benito | SAN JUSTO 1101 | SAN JUSTO 110136902 | Unknown Cause | 2025-05-21 20:47 | -07:00 | 05/20 - 05/26 | 2025-05-22 06:32 | -07:00 | 431.009 | FTS | 96115 | 223 | 11 | 9 | 5 | 1 | 0 | 0 | 585
25-0056857 | Calaveras | CORRAL 1103 | CORRAL 110336680 | 3rd Party | 2025-05-22 05:45 | -07:00 | 05/20 - 05/26 | 2025-05-22 06:55 | -07:00 | 70 | FTS | 50470 | 721 | 68 | 42 | 10 | 0 | 0 | 0 | 70
25-0056854 | San Luis Obispo | CHOLAME 1101 | CHOLAME 1101R22 | Animal | 2025-05-22 05:26 | -07:00 | 05/20 - 05/26 | 2025-05-22 07:09 | -07:00 | 91.0719 | FTS | 15209 | 167 | 4 | 2 | 2 | 0 | 0 | 0 | 103
25-0056870 | Merced | GUSTINE 1102 | GUSTINE 1102562202 | Unknown Cause | 2025-05-22 06:45 | -07:00 | 05/20 - 05/26 | 2025-05-22 09:06 | -07:00 | 141 | FTS | 93201 | 661 | 18 | 13 | 12 | 0 | 0 | 0 | 141
25-0056838 | Mariposa | MARIPOSA 2102 | MARIPOSA 21021960 | Unknown Cause | 2025-05-22 00:25 | -07:00 | 05/20 - 05/26 | 2025-05-22 09:26 | -07:00 | 137.6171 | FTS | 132250 | 961 | 41 | 29 | 18 | 5 | 0 | 2 | 541
25-0056860 | Kern | LAKEVIEW 1103 | LAKEVIEW 11034488 | Animal | 2025-05-22 06:14 | -07:00 | 05/20 - 05/26 | 2025-05-22 09:53 | -07:00 | 219 | FTS | 12483 | 57 | 0 | 0 | 2 | 0 | 0 | 0 | 219
25-0056888 | San Joaquin | HERDLYN 1102 | HERDLYN 1102608254 | 3rd Party | 2025-05-22 07:39 | -07:00 | 05/20 - 05/26 | 2025-05-22 14:16 | -07:00 | 119.6503 | FTS | 63295 | 529 | 38 | 21 | 20 | 3 | 0 | 0 | 397
25-0057193 | El Dorado | SHINGLE SPRINGS 2108 | SHINGLE SPRINGS 2108449638 | Equipment Failure/Involved | 2025-05-22 14:26 | -07:00 | 05/20 - 05/26 | 2025-05-22 15:16 | -07:00 | 50 | FTS | 100 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 50
25-0057173 | Monterey | JOLON 1103 | JOLON 1103549180 | 3rd Party | 2025-05-22 13:56 | -07:00 | 05/20 - 05/26 | 2025-05-22 15:23 | -07:00 | 87 | FTS | 783 | 9 | 0 | 0 | 6 | 0 | 0 | 0 | 87
25-0057037 | Contra Costa | SOBRANTE 1101 | SOBRANTE 110142914 | Animal | 2025-05-22 10:32 | -07:00 | 05/20 - 05/26 | 2025-05-22 16:22 | -07:00 | 78.5175 | FTS | 22456 | 286 | 15 | 10 | 2 | 0 | 0 | 0 | 350
25-0057200 | Merced | GUSTINE 1102 | GUSTINE 1102562202 | Unknown Cause | 2025-05-22 14:41 | -07:00 | 05/20 - 05/26 | 2025-05-22 16:49 | -07:00 | 128 | FTS | 84608 | 661 | 18 | 13 | 12 | 0 | 0 | 0 | 128
25-0057284 | El Dorado | PLACERVILLE 2106 | PLACERVILLE 21062224 | Equipment Failure/Involved | 2025-05-22 17:08 | -07:00 | 05/20 - 05/26 | 2025-05-22 18:26 | -07:00 | 48.5946 | FTS | 50101 | 1031 | 73 | 59 | 42 | 10 | 0 | 7 | 78
25-0057309 | Kern | MAGUNDEN 1108 | MAGUNDEN 1108468940 | 3rd Party | 2025-05-22 19:27 | -07:00 | 05/20 - 05/26 | 2025-05-22 20:11 | -07:00 | 44 | FTS | 1848 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 44
25-0057315 | Lake | HIGHLANDS 1103 | HIGHLANDS 1103520 | Vegetation | 2025-05-22 19:27 | -07:00 | 05/20 - 05/26 | 2025-05-22 20:42 | -07:00 | 75 | FTS | 2475 | 33 | 2 | 1 | 0 | 0 | 0 | 0 | 75
25-0057288 | Madera | COARSEGOLD 2103 | COARSEGOLD 210310300 | 3rd Party | 2025-05-22 17:22 | -07:00 | 05/20 - 05/26 | 2025-05-22 20:44 | -07:00 | 107.9522 | FTS | 22562 | 209 | 13 | 10 | 33 | 4 | 0 | 1 | 202
25-0057316 | Kern | MAGUNDEN 1108 | MAGUNDEN 1108468940 | 3rd Party | 2025-05-22 20:31 | -07:00 | 05/20 - 05/26 | 2025-05-22 21:06 | -07:00 | 35 | FTS | 1470 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 35
25-0057334 | Merced | WILSON 1103 | WILSON 11039080 | Equipment Failure/Involved | 2025-05-23 01:01 | -07:00 | 05/20 - 05/26 | 2025-05-23 03:03 | -07:00 | 82.6673 | FTS | 130449 | 1578 | 55 | 31 | 16 | 6 | 0 | 0 | 122
25-0057194 | Santa Cruz | BEN LOMOND 0401 | BEN LOMOND 04015144 | Vegetation | 2025-05-22 14:27 | -07:00 | 05/20 - 05/26 | 2025-05-23 05:28 | -07:00 | 382.6703 | FTS | 34823 | 91 | 3 | 3 | 5 | 0 | 0 | 0 | 901
25-0057335 | Santa Clara | HICKS 2103 | HICKS 2103CB | Equipment Failure/Involved | 2025-05-23 01:17 | -07:00 | 05/20 - 05/26 | 2025-05-23 05:32 | -07:00 | 164.0297 | FTS | 729440 | 4447 | 191 | 126 | 43 | 4 | 0 | 1 | 255
25-0057342 | Calaveras | FROGTOWN 1702 | FROGTOWN 170275252 | Unknown Cause | 2025-05-23 05:24 | -07:00 | 05/20 - 05/26 | 2025-05-23 07:03 | -07:00 | 38.6522 | FTS | 32004 | 828 | 34 | 25 | 28 | 2 | 0 | 3 | 99
25-0056948 | Fresno | AUBERRY 1101 | AUBERRY 1101378194 | Equipment Failure/Involved | 2025-05-22 08:55 | -07:00 | 05/20 - 05/26 | 2025-05-23 09:08 | -07:00 | 230.6701 | FTS | 202067 | 876 | 38 | 32 | 23 | 3 | 0 | 3 | 1453
25-0057373 | Lake | HIGHLANDS 1102 | HIGHLANDS 1102623120 | Unknown Cause | 2025-05-23 07:33 | -07:00 | 05/20 - 05/26 | 2025-05-23 09:16 | -07:00 | 94.8752 | FTS | 58538 | 617 | 49 | 31 | 11 | 0 | 0 | 6 | 103
25-0057459 | Monterey | LOS OSITOS 2101 | LOS OSITOS 21011132 | Company Initiated | 2025-05-23 09:45 | -07:00 | 05/20 - 05/26 | 2025-05-23 09:51 | -07:00 | 6 | FTS | 342 | 57 | 1 | 1 | 2 | 1 | 0 | 0 | 6
25-0057387 | El Dorado | PLACERVILLE 2106 | PLACERVILLE 210619552 | Animal | 2025-05-23 08:00 | -07:00 | 05/20 - 05/26 | 2025-05-23 10:07 | -07:00 | 127 | FTS | 65913 | 519 | 45 | 33 | 5 | 0 | 0 | 5 | 127
25-0057391 | Nevada | BRUNSWICK 1105 | BRUNSWICK 11052204 | Unknown Cause | 2025-05-23 08:10 | -07:00 | 05/20 - 05/26 | 2025-05-23 11:02 | -07:00 | 124.5774 | FTS | 119096 | 956 | 53 | 38 | 14 | 0 | 0 | 24 | 172
25-0057442 | Placer | PENRYN 1103 | PENRYN 110351658 | Animal | 2025-05-23 09:23 | -07:00 | 05/20 - 05/26 | 2025-05-23 11:47 | -07:00 | 144 | FTS | 99072 | 688 | 48 | 36 | 9 | 0 | 0 | 20 | 144
25-0057415 | Napa | SILVERADO 2102 | SILVERADO 210234959 | Unknown Cause | 2025-05-23 08:33 | -07:00 | 05/20 - 05/26 | 2025-05-23 12:21 | -07:00 | 228 | FTS | 40812 | 179 | 1 | 1 | 4 | 0 | 0 | 1 | 228
25-0057510 | Butte | BUTTE 1105 | BUTTE 1105612016 | Equipment Failure/Involved | 2025-05-23 10:53 | -07:00 | 05/20 - 05/26 | 2025-05-23 14:13 | -07:00 | 162.1854 | FTS | 33248 | 205 | 13 | 5 | 2 | 1 | 0 | 6 | 200
25-0057603 | Napa | MONTICELLO 1101 | MONTICELLO 1101256640 | Unknown Cause | 2025-05-23 12:48 | -07:00 | 05/20 - 05/26 | 2025-05-23 15:16 | -07:00 | 148 | FTS | 5772 | 39 | 0 | 0 | 4 | 0 | 0 | 0 | 148
25-0057726 | Sonoma | GEYSERVILLE 1102 | GEYSERVILLE 1102785626 | Unknown Cause | 2025-05-23 15:22 | -07:00 | 05/20 - 05/26 | 2025-05-23 16:50 | -07:00 | 88 | FTS | 31064 | 353 | 3 | 1 | 8 | 0 | 0 | 3 | 88
25-0057742 | Shasta | KESWICK 1101 | KESWICK 1101CB | Animal | 2025-05-23 16:06 | -07:00 | 05/20 - 05/26 | 2025-05-23 18:11 | -07:00 | 108.7205 | FTS | 59905 | 551 | 28 | 19 | 27 | 1 | 0 | 1 | 125
25-0057732 | Calaveras | FROGTOWN 1702 | FROGTOWN 170211212 | Unknown Cause | 2025-05-23 15:38 | -07:00 | 05/20 - 05/26 | 2025-05-23 19:44 | -07:00 | 246 | FTS | 31242 | 127 | 12 | 6 | 7 | 0 | 0 | 0 | 246
25-0057807 | San Luis Obispo | SAN MIGUEL 1107 | SAN MIGUEL 1107608338 | Unknown Cause | 2025-05-24 07:33 | -07:00 | 05/20 - 05/26 | 2025-05-24 09:27 | -07:00 | 114 | FTS | 20178 | 177 | 5 | 5 | 2 | 0 | 0 | 1 | 114
25-0057832 | Fresno | DUNLAP 1103 | DUNLAP 11037170 | Company Initiated | 2025-05-24 09:27 | -07:00 | 05/20 - 05/26 | 2025-05-24 10:41 | -07:00 | 74 | FTS | 26492 | 358 | 13 | 13 | 5 | 0 | 0 | 0 | 74
25-0057784 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113R82 | Animal | 2025-05-23 21:07 | -07:00 | 05/20 - 05/26 | 2025-05-24 11:55 | -07:00 | 197.6966 | FTS | 178520 | 903 | 28 | 17 | 12 | 2 | 0 | 16 | 888
25-0057854 | Fresno | DUNLAP 1103 | DUNLAP 11037170 | Company Initiated | 2025-05-24 11:07 | -07:00 | 05/20 - 05/26 | 2025-05-24 14:01 | -07:00 | 67.5 | FTS | 48330 | 716 | 13 | 13 | 5 | 0 | 0 | 0 | 174
25-0057875 | Sonoma | GEYSERVILLE 1102 | GEYSERVILLE 1102522 | Unknown Cause | 2025-05-24 14:45 | -07:00 | 05/20 - 05/26 | 2025-05-24 17:45 | -07:00 | 180 | FTS | 28260 | 157 | 3 | 3 | 2 | 0 | 0 | 3 | 180
25-0057881 | Fresno | DUNLAP 1103 | DUNLAP 11037080 | Company Initiated | 2025-05-24 15:29 | -07:00 | 05/20 - 05/26 | 2025-05-24 17:58 | -07:00 | 149 | FTS | 41720 | 280 | 12 | 12 | 2 | 0 | 0 | 0 | 149
25-0057869 | Colusa | ARBUCKLE 1101 | ARBUCKLE 11013068 | Unknown Cause | 2025-05-24 14:11 | -07:00 | 05/20 - 05/26 | 2025-05-24 19:20 | -07:00 | 309 | FTS | 25029 | 81 | 0 | 0 | 1 | 0 | 0 | 0 | 309
25-0057885 | Lake | HARTLEY 1101 | HARTLEY 1101743866 | Unknown Cause | 2025-05-24 17:04 | -07:00 | 05/20 - 05/26 | 2025-05-24 19:29 | -07:00 | 71.5842 | FTS | 27202 | 380 | 21 | 12 | 3 | 0 | 0 | 3 | 145
25-0057863 | Yolo | PUTAH CREEK 1105 | PUTAH CREEK 110546162 | Equipment Failure/Involved | 2025-05-24 12:33 | -07:00 | 05/20 - 05/26 | 2025-05-24 20:09 | -07:00 | 456 | FTS | 16416 | 36 | 3 | 1 | 0 | 0 | 0 | 3 | 456
25-0057907 | Colusa | ARBUCKLE 1101 | ARBUCKLE 11013068 | Unknown Cause | 2025-05-25 04:04 | -07:00 | 05/20 - 05/26 | 2025-05-25 07:53 | -07:00 | 158.2963 | FTS | 12822 | 81 | 0 | 0 | 1 | 0 | 0 | 0 | 229
25-0057904 | Monterey | LAURELES 1111 | LAURELES 1111432 | Unknown Cause | 2025-05-25 04:39 | -07:00 | 05/20 - 05/26 | 2025-05-25 08:21 | -07:00 | 222 | FTS | 71928 | 324 | 8 | 8 | 7 | 0 | 0 | 0 | 222
25-0057908 | Tuolumne | CURTIS 1702 | CURTIS 1702961393 | Unknown Cause | 2025-05-25 05:27 | -07:00 | 05/20 - 05/26 | 2025-05-25 08:56 | -07:00 | 209 | FTS | 4807 | 23 | 1 | 1 | 1 | 0 | 0 | 0 | 209
25-0057915 | Santa Clara | MORGAN HILL 2111 | MORGAN HILL 2111XR398 | Animal | 2025-05-25 07:32 | -07:00 | 05/20 - 05/26 | 2025-05-25 10:28 | -07:00 | 176 | FTS | 70576 | 401 | 20 | 17 | 10 | 0 | 0 | 2 | 176
25-0057894 | Santa Clara | MORGAN HILL 2111 | MORGAN HILL 2111997000 | 3rd Party | 2025-05-24 21:29 | -07:00 | 05/20 - 05/26 | 2025-05-25 14:30 | -07:00 | 78.4134 | FTS | 31679 | 404 | 19 | 8 | 4 | 0 | 0 | 0 | 1021
25-0057956 | Glenn | ELK CREEK 1101 | ELK CREEK 11012002 | Company Initiated | 2025-05-25 16:36 | -07:00 | 05/20 - 05/26 | 2025-05-25 16:58 | -07:00 | 22 | FTS | 12474 | 567 | 28 | 19 | 26 | 3 | 0 | 0 | 22
25-0057965 | Yolo | MADISON 2101 | MADISON 2101484892 | Animal | 2025-05-25 19:20 | -07:00 | 05/20 - 05/26 | 2025-05-25 20:51 | -07:00 | 91 | FTS | 10647 | 117 | 3 | 1 | 0 | 0 | 0 | 0 | 91
25-0057967 | Sonoma | SANTA ROSA A 1111 | SANTA ROSA A 1111907192 | Unknown Cause | 2025-05-25 20:02 | -07:00 | 05/20 - 05/26 | 2025-05-26 07:38 | -07:00 | 107.814 | FTS | 109539 | 1016 | 55 | 44 | 15 | 1 | 0 | 2 | 696
25-0057978 | Placer | WISE 1102 | WISE 11022234 | Unknown Cause | 2025-05-26 04:10 | -07:00 | 05/20 - 05/26 | 2025-05-26 09:38 | -07:00 | 328 | FTS | 89544 | 273 | 17 | 11 | 0 | 0 | 0 | 4 | 328
25-0057995 | San Benito | HOLLISTER 2105 | HOLLISTER 2105480430 | 3rd Party | 2025-05-26 07:31 | -07:00 | 05/20 - 05/26 | 2025-05-26 09:39 | -07:00 | 128 | FTS | 4224 | 33 | 0 | 0 | 1 | 0 | 0 | 0 | 128
25-0058012 | Shasta | BURNEY 1101 | BURNEY 11011322 | 3rd Party | 2025-05-26 09:03 | -07:00 | 05/20 - 05/26 | 2025-05-26 10:01 | -07:00 | 33.3676 | FTS | 2269 | 68 | 3 | 3 | 0 | 0 | 0 | 0 | 58
25-0058098 | Sonoma | MIRABEL 1101 | MIRABEL 1101310814 | Vegetation | 2025-05-26 16:49 | -07:00 | 05/20 - 05/26 | 2025-05-26 18:32 | -07:00 | 103 | FTS | 4635 | 45 | 4 | 4 | 0 | 0 | 0 | 0 | 103
25-0058100 | Mariposa | MERCED FALLS 1102 | MERCED FALLS 110285002 | Animal | 2025-05-26 17:45 | -07:00 | 05/20 - 05/26 | 2025-05-26 22:23 | -07:00 | 109.304 | FTS | 60773 | 556 | 39 | 26 | 15 | 2 | 0 | 0 | 278
25-0058114 | Santa Barbara | CABRILLO 1104 | CABRILLO 1104838078 | Equipment Failure/Involved | 2025-05-26 22:48 | -07:00 | 05/27 - 06/02 | 2025-05-27 00:21 | -07:00 | 93 | FTS | 23157 | 249 | 2 | 1 | 5 | 0 | 0 | 0 | 93
25-0058108 | Nevada | COLUMBIA HILL 1101 | COLUMBIA HILL 110135424 | Vegetation | 2025-05-26 20:42 | -07:00 | 05/27 - 06/02 | 2025-05-27 02:49 | -07:00 | 110.3689 | FTS | 26930 | 244 | 16 | 10 | 9 | 3 | 0 | 3 | 367
25-0058127 | Fresno | DUNLAP 1103 | DUNLAP 11037170 | Company Initiated | 2025-05-27 06:25 | -07:00 | 05/27 - 06/02 | 2025-05-27 06:41 | -07:00 | 16 | FTS | 5728 | 358 | 13 | 13 | 5 | 0 | 0 | 0 | 16
25-0058172 | Sonoma | CLOVERDALE 1101 | CLOVERDALE 1101112 | Company Initiated | 2025-05-27 08:29 | -07:00 | 05/27 - 06/02 | 2025-05-27 08:40 | -07:00 | 11 | FTS | 253 | 23 | 2 | 2 | 1 | 0 | 0 | 0 | 11
25-0058200 | Monterey | LOS OSITOS 2103 | LOS OSITOS 2103695270 | Company Initiated | 2025-05-27 09:00 | -07:00 | 05/27 - 06/02 | 2025-05-27 09:15 | -07:00 | 15 | FTS | 6570 | 438 | 10 | 4 | 4 | 0 | 0 | 0 | 15
25-0058205 | Shasta | MC ARTHUR 1101 | MC ARTHUR 1101648698 | Unknown Cause | 2025-05-27 09:15 | -07:00 | 05/27 - 06/02 | 2025-05-27 11:00 | -07:00 | 45.3745 | FTS | 11026 | 243 | 16 | 14 | 3 | 0 | 0 | 0 | 105
25-0058153 | Butte | CLARK ROAD 1102 | CLARK ROAD 11022044 | Unknown Cause | 2025-05-27 07:47 | -07:00 | 05/27 - 06/02 | 2025-05-27 11:14 | -07:00 | 207 | FTS | 14076 | 68 | 4 | 3 | 1 | 0 | 0 | 0 | 207
25-0058255 | Amador | OLETA 1102 | OLETA 11021228 | 3rd Party | 2025-05-27 10:36 | -07:00 | 05/27 - 06/02 | 2025-05-27 12:07 | -07:00 | 91 | FTS | 75985 | 835 | 21 | 16 | 12 | 0 | 0 | 9 | 91
25-0058297 | Napa | PUEBLO 2103 | PUEBLO 2103CB | Animal | 2025-05-27 11:52 | -07:00 | 05/27 - 06/02 | 2025-05-27 14:18 | -07:00 | 78.8756 | FTS | 192693 | 2443 | 231 | 169 | 36 | 5 | 0 | 6 | 146
25-0058362 | El Dorado | DIAMOND SPRINGS 1106 | DIAMOND SPRINGS 110699658 | Vegetation | 2025-05-27 13:37 | -07:00 | 05/27 - 06/02 | 2025-05-27 14:29 | -07:00 | 52 | FTS | 8632 | 166 | 20 | 16 | 0 | 0 | 0 | 0 | 52
25-0058276 | San Luis Obispo | ATASCADERO 1103 | ATASCADERO 1103A18 | Company Initiated | 2025-05-27 11:09 | -07:00 | 05/27 - 06/02 | 2025-05-27 17:57 | -07:00 | 308.8167 | FTS | 518812 | 1680 | 63 | 46 | 21 | 2 | 0 | 5 | 408
25-0058425 | Shasta | MC ARTHUR 1101 | MC ARTHUR 110138998 | Unknown Cause | 2025-05-27 15:11 | -07:00 | 05/27 - 06/02 | 2025-05-27 19:11 | -07:00 | 180.8419 | FTS | 113207 | 626 | 24 | 17 | 22 | 3 | 0 | 0 | 240
25-0058436 | Alameda | VINEYARD 2108 | VINEYARD 2108609690 | Unknown Cause | 2025-05-27 15:28 | -07:00 | 05/27 - 06/02 | 2025-05-28 02:58 | -07:00 | 165.2641 | FTS | 304747 | 1844 | 112 | 85 | 24 | 2 | 0 | 1 | 690
25-0058245 | Santa Clara | MORGAN HILL 2105 | MORGAN HILL 2105XR152 | Equipment Failure/Involved | 2025-05-27 10:00 | -07:00 | 05/27 - 06/02 | 2025-05-28 06:39 | -07:00 | 137.5636 | FTS | 45396 | 330 | 21 | 19 | 1 | 0 | 0 | 1 | 1239
25-0058577 | Sonoma | GEYSERVILLE 1101 | GEYSERVILLE 1101482 | Company Initiated | 2025-05-28 08:05 | -07:00 | 05/27 - 06/02 | 2025-05-28 08:12 | -07:00 | 7 | FTS | 980 | 140 | 1 | 1 | 3 | 0 | 0 | 1 | 7
25-0058515 | Lake | MIDDLETOWN 1101 | MIDDLETOWN 1101614 | Unknown Cause | 2025-05-28 06:08 | -07:00 | 05/27 - 06/02 | 2025-05-28 09:48 | -07:00 | 179.25 | FTS | 74568 | 416 | 19 | 15 | 5 | 0 | 0 | 0 | 220
25-0058639 | Marin | NOVATO 1104 | NOVATO 110438242 | Unknown Cause | 2025-05-28 10:37 | -07:00 | 05/27 - 06/02 | 2025-05-28 12:26 | -07:00 | 41.2143 | FTS | 577 | 14 | 0 | 0 | 5 | 0 | 0 | 0 | 109
25-0058457 | Shasta | OREGON TRAIL 1103 | OREGON TRAIL 11031500 | Unknown Cause | 2025-05-27 16:05 | -07:00 | 05/27 - 06/02 | 2025-05-28 13:41 | -07:00 | 534.6143 | FTS | 694464 | 1299 | 50 | 38 | 4 | 0 | 0 | 1 | 1296
25-0058751 | San Luis Obispo | SAN MIGUEL 1107 | SAN MIGUEL 1107608338 | Unknown Cause | 2025-05-28 13:16 | -07:00 | 05/27 - 06/02 | 2025-05-28 14:50 | -07:00 | 94 | FTS | 16638 | 177 | 5 | 5 | 2 | 0 | 0 | 1 | 94
25-0029758 | El Dorado | APPLE HILL 2102 | APPLE HILL 2102CB | Company Initiated | 2025-05-28 14:55 | -07:00 | 05/27 - 06/02 | 2025-05-28 15:04 | -07:00 | 9 | FTS | 44964 | 4996 | 396 | 296 | 65 | 12 | 0 | 63 | 9
25-0058637 | El Dorado | PLACERVILLE 2106 | PLACERVILLE 2106CB | Unknown Cause | 2025-05-28 10:31 | -07:00 | 05/27 - 06/02 | 2025-05-28 15:54 | -07:00 | 128.5226 | FTS | 687853 | 5352 | 375 | 275 | 92 | 18 | 1 | 33 | 323
25-0058888 | Sonoma | SANTA ROSA A 1104 | SANTA ROSA A 1104991788 | Unknown Cause | 2025-05-28 16:17 | -07:00 | 05/27 - 06/02 | 2025-05-28 17:18 | -07:00 | 61 | FTS | 23058 | 378 | 21 | 17 | 2 | 0 | 0 | 0 | 61
25-0058846 | Santa Cruz | BEN LOMOND 0401 | BEN LOMOND 04015144 | Vegetation | 2025-05-28 15:05 | -07:00 | 05/27 - 06/02 | 2025-05-28 17:44 | -07:00 | 159 | FTS | 23691 | 149 | 8 | 7 | 5 | 0 | 0 | 0 | 159
25-0058715 | Merced | GUSTINE 1102 | GUSTINE 1102562202 | Equipment Failure/Involved | 2025-05-28 12:29 | -07:00 | 05/27 - 06/02 | 2025-05-28 17:52 | -07:00 | 323 | FTS | 213503 | 661 | 18 | 13 | 12 | 0 | 0 | 0 | 323
25-0058900 | Placer | SHADY GLEN 1101 | SHADY GLEN 1101941844 | Unknown Cause | 2025-05-28 16:36 | -07:00 | 05/27 - 06/02 | 2025-05-28 17:55 | -07:00 | 17.8932 | FTS | 10718 | 599 | 36 | 27 | 7 | 0 | 0 | 4 | 79
25-0058828 | Calaveras | CALAVERAS CEMENT 1101 | CALAVERAS CEMENT 1101544800 | Unknown Cause | 2025-05-28 14:43 | -07:00 | 05/27 - 06/02 | 2025-05-28 18:22 | -07:00 | 219 | FTS | 28689 | 131 | 8 | 7 | 4 | 0 | 0 | 0 | 219
25-0058707 | Humboldt | HOOPA 1101 | HOOPA 110182542 | Vegetation | 2025-05-28 12:13 | -07:00 | 05/27 - 06/02 | 2025-05-28 19:37 | -07:00 | 220.6942 | FTS | 53408 | 242 | 11 | 9 | 8 | 0 | 0 | 0 | 444
25-0058958 | Madera | COARSEGOLD 2104 | COARSEGOLD 2104369777 | Animal | 2025-05-28 21:03 | -07:00 | 05/27 - 06/02 | 2025-05-29 00:26 | -07:00 | 203 | FTS | 49126 | 242 | 19 | 16 | 1 | 0 | 0 | 0 | 203
25-0058800 | Marin | ALTO 1124 | ALTO 1124430 | Vegetation | 2025-05-28 14:15 | -07:00 | 05/27 - 06/02 | 2025-05-29 02:24 | -07:00 | 101.1357 | FTS | 99113 | 980 | 24 | 18 | 8 | 2 | 0 | 0 | 729
25-0058925 | Amador | PINE GROVE 1102 | PINE GROVE 11023172 | 3rd Party | 2025-05-28 18:29 | -07:00 | 05/27 - 06/02 | 2025-05-29 05:23 | -07:00 | 78.3697 | FTS | 230642 | 2943 | 231 | 169 | 52 | 5 | 0 | 6 | 654
25-0058941 | Tuolumne | PEORIA 1704 | PEORIA 17048040 | Unknown Cause | 2025-05-28 19:49 | -07:00 | 05/27 - 06/02 | 2025-05-29 09:38 | -07:00 | 715.7939 | FTS | 93769 | 131 | 2 | 2 | 7 | 0 | 0 | 1 | 829
25-0059161 | Lake | HIGHLANDS 1103 | HIGHLANDS 1103726580 | Company Initiated | 2025-05-29 11:43 | -07:00 | 05/27 - 06/02 | 2025-05-29 12:16 | -07:00 | 33 | FTS | 1782 | 54 | 1 | 0 | 2 | 0 | 0 | 0 | 33
25-0058970 | Contra Costa | TASSAJARA 2104 | TASSAJARA 2104967234 | Equipment Failure/Involved | 2025-05-29 02:04 | -07:00 | 05/27 - 06/02 | 2025-05-29 16:45 | -07:00 | 189.0144 | FTS | 26273 | 139 | 8 | 1 | 3 | 0 | 0 | 6 | 881
25-0059274 | Alameda | VINEYARD 2108 | VINEYARD 2108MR172 | Company Initiated | 2025-05-29 15:00 | -07:00 | 05/27 - 06/02 | 2025-05-29 16:57 | -07:00 | 117 | FTS | 351 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 117
25-0059345 | Sonoma | MOLINO 1101 | MOLINO 1101338 | Equipment Failure/Involved | 2025-05-29 17:45 | -07:00 | 05/27 - 06/02 | 2025-05-29 21:24 | -07:00 | 137.2228 | FTS | 50498 | 368 | 13 | 6 | 8 | 3 | 0 | 8 | 219
25-0059285 | Yuba | CHALLENGE 1102 | CHALLENGE 11021064 | Vegetation | 2025-05-29 15:30 | -07:00 | 05/27 - 06/02 | 2025-05-29 23:41 | -07:00 | 313.505 | FTS | 62701 | 200 | 12 | 8 | 0 | 0 | 0 | 0 | 491
25-0059379 | Mariposa | MERCED FALLS 1102 | MERCED FALLS 11029470 | Unknown Cause | 2025-05-29 22:43 | -07:00 | 05/27 - 06/02 | 2025-05-30 00:50 | -07:00 | 127 | FTS | 83820 | 660 | 44 | 29 | 9 | 3 | 0 | 0 | 127
25-0059388 | San Luis Obispo | PERRY 1104 | PERRY 1104175422 | Equipment Failure/Involved | 2025-05-30 03:11 | -07:00 | 05/27 - 06/02 | 2025-05-30 07:33 | -07:00 | 211.8182 | FTS | 13980 | 66 | 0 | 0 | 4 | 0 | 0 | 0 | 262
25-0059438 | Mendocino | CALPELLA 1101 | CALPELLA 1101908688 | Company Initiated | 2025-05-30 08:06 | -07:00 | 05/27 - 06/02 | 2025-05-30 09:20 | -07:00 | 74 | FTS | 40848 | 552 | 33 | 23 | 9 | 1 | 0 | 3 | 74
25-0059478 | Madera | SAN JOAQUIN #3 1101 | SAN JOAQUIN #3 1101CB | Company Initiated | 2025-05-30 09:19 | -07:00 | 05/27 - 06/02 | 2025-05-30 09:44 | -07:00 | 24.8182 | FTS | 16926 | 682 | 32 | 23 | 22 | 0 | 0 | 2 | 25
25-0059393 | San Mateo | SAN CARLOS 1103 | SAN CARLOS 1103586832 | Unknown Cause | 2025-05-30 05:36 | -07:00 | 05/27 - 06/02 | 2025-05-30 10:43 | -07:00 | 271.7761 | FTS | 122571 | 451 | 15 | 12 | 12 | 0 | 0 | 0 | 307
25-0059572 | Nevada | BRUNSWICK 1105 | BRUNSWICK 11052140 | Company Initiated | 2025-05-30 11:54 | -07:00 | 05/27 - 06/02 | 2025-05-30 12:41 | -07:00 | 47 | FTS | 2209 | 47 | 1 | 1 | 0 | 0 | 0 | 2 | 47
25-0059625 | Lake | HIGHLANDS 1104 | HIGHLANDS 110487040 | Vegetation | 2025-05-30 13:40 | -07:00 | 05/27 - 06/02 | 2025-05-30 16:22 | -07:00 | 50.5714 | FTS | 56640 | 1120 | 83 | 55 | 20 | 0 | 1 | 0 | 162
25-0059718 | Shasta | GIRVAN 1102 | GIRVAN 110280726 | Equipment Failure/Involved | 2025-05-30 16:26 | -07:00 | 05/27 - 06/02 | 2025-05-30 17:31 | -07:00 | 65 | FTS | 35815 | 551 | 18 | 12 | 8 | 0 | 0 | 1 | 65
25-0059746 | Calaveras | CORRAL 1103 | CORRAL 1103CB | Equipment Failure/Involved | 2025-05-30 17:58 | -07:00 | 05/27 - 06/02 | 2025-05-30 18:45 | -07:00 | 46.3986 | FTS | 193018 | 4160 | 313 | 219 | 57 | 0 | 0 | 9 | 47
25-0059738 | Santa Cruz | BIG BASIN 1101 | BIG BASIN 110110720 | Vegetation | 2025-05-30 17:38 | -07:00 | 05/27 - 06/02 | 2025-05-30 19:11 | -07:00 | 64.1151 | FTS | 142079 | 2216 | 148 | 119 | 31 | 3 | 0 | 2 | 93
25-0059745 | Sonoma | FITCH MOUNTAIN 1113 | FITCH MOUNTAIN 111324550 | Unknown Cause | 2025-05-30 17:52 | -07:00 | 05/27 - 06/02 | 2025-05-30 20:27 | -07:00 | 141.3891 | FTS | 31247 | 221 | 4 | 2 | 6 | 0 | 0 | 2 | 155
25-0059711 | Tuolumne | CURTIS 1705 | CURTIS 170510590 | Equipment Failure/Involved | 2025-05-30 16:12 | -07:00 | 05/27 - 06/02 | 2025-05-30 20:42 | -07:00 | 206.2242 | FTS | 117754 | 571 | 40 | 29 | 11 | 0 | 0 | 0 | 270
25-0059765 | Fresno | TIVY VALLEY 1107 | TIVY VALLEY 1107599142 | Animal | 2025-05-30 18:46 | -07:00 | 05/27 - 06/02 | 2025-05-30 21:22 | -07:00 | 156 | FTS | 3120 | 20 | 1 | 0 | 0 | 0 | 0 | 0 | 156
25-0053062 | Solano | CORDELIA 1112 | CORDELIA 11128832 | Equipment Failure/Involved | 2025-05-30 18:42 | -07:00 | 05/27 - 06/02 | 2025-05-30 22:18 | -07:00 | 81.8946 | FTS | 367543 | 4488 | 154 | 116 | 36 | 1 | 0 | 0 | 216
25-0059780 | Mariposa | MERCED FALLS 1102 | MERCED FALLS 110285002 | Equipment Failure/Involved | 2025-05-30 21:15 | -07:00 | 05/27 - 06/02 | 2025-05-31 01:09 | -07:00 | 111.2212 | FTS | 61839 | 556 | 39 | 26 | 15 | 2 | 0 | 0 | 234
25-0059695 | Mendocino | LAYTONVILLE 1101 | LAYTONVILLE 1101364398 | Vegetation | 2025-05-30 15:31 | -07:00 | 05/27 - 06/02 | 2025-05-31 01:46 | -07:00 | 176.166 | FTS | 46684 | 265 | 9 | 7 | 8 | 3 | 0 | 0 | 615
25-0059751 | Santa Barbara | SISQUOC 1102 | SISQUOC 1102M26 | 3rd Party | 2025-05-30 18:10 | -07:00 | 05/27 - 06/02 | 2025-05-31 05:38 | -07:00 | 102.6561 | FTS | 25972 | 253 | 3 | 2 | 2 | 0 | 0 | 0 | 688
25-0059816 | Fresno | HAMMONDS 1102 | HAMMONDS 1102CB | Unknown Cause | 2025-05-31 07:48 | -07:00 | 05/27 - 06/02 | 2025-05-31 12:24 | -07:00 | 276 | FTS | 73416 | 266 | 0 | 0 | 11 | 0 | 0 | 0 | 276
25-0059721 | San Mateo | WOODSIDE 1101 | WOODSIDE 110147872 | Equipment Failure/Involved | 2025-05-30 16:34 | -07:00 | 05/27 - 06/02 | 2025-05-31 13:06 | -07:00 | 181.6935 | FTS | 45060 | 248 | 13 | 8 | 14 | 1 | 0 | 0 | 1232
25-0059895 | Humboldt | GARBERVILLE 1102 | GARBERVILLE 11026084 | Vegetation | 2025-05-31 13:42 | -07:00 | 05/27 - 06/02 | 2025-05-31 15:58 | -07:00 | 99.1692 | FTS | 12892 | 130 | 6 | 5 | 5 | 1 | 0 | 0 | 136
25-0059799 | Lake | HIGHLANDS 1102 | HIGHLANDS 1102623120 | Vegetation | 2025-05-31 03:01 | -07:00 | 05/27 - 06/02 | 2025-05-31 18:29 | -07:00 | 341.9887 | FTS | 211007 | 617 | 50 | 32 | 11 | 0 | 0 | 6 | 928
25-0059907 | Humboldt | FRUITLAND 1141 | FRUITLAND 1141CB | Vegetation | 2025-05-31 15:21 | -07:00 | 05/27 - 06/02 | 2025-05-31 19:47 | -07:00 | 258.2089 | FTS | 98894 | 383 | 9 | 9 | 12 | 1 | 0 | 0 | 266
25-0059949 | Calaveras | CORRAL 1103 | CORRAL 1103CB | Equipment Failure/Involved | 2025-05-31 18:23 | -07:00 | 05/27 - 06/02 | 2025-05-31 20:45 | -07:00 | 36.2853 | FTS | 150947 | 4160 | 313 | 219 | 57 | 0 | 0 | 9 | 142
25-0059933 | San Luis Obispo | CHOLAME 2102 | CHOLAME 2102X10 | Animal | 2025-05-31 17:07 | -07:00 | 05/27 - 06/02 | 2025-05-31 20:53 | -07:00 | 125.9905 | FTS | 13229 | 105 | 0 | 0 | 4 | 0 | 0 | 0 | 226
25-0059968 | Marin | SAN RAFAEL 1108 | SAN RAFAEL 11081262 | Unknown Cause | 2025-05-31 21:04 | -07:00 | 05/27 - 06/02 | 2025-05-31 22:45 | -07:00 | 101 | FTS | 78881 | 781 | 23 | 12 | 6 | 3 | 0 | 1 | 101
25-0059928 | Tuolumne | CURTIS 1702 | CURTIS 170247488 | Equipment Failure/Involved | 2025-05-31 16:48 | -07:00 | 05/27 - 06/02 | 2025-05-31 22:47 | -07:00 | 123.2288 | FTS | 72705 | 590 | 46 | 40 | 7 | 8 | 0 | 2 | 359
25-0059911 | Santa Barbara | CABRILLO 1103 | CABRILLO 1103460184 | Equipment Failure/Involved | 2025-05-31 15:32 | -07:00 | 05/27 - 06/02 | 2025-05-31 23:16 | -07:00 | 62.2769 | FTS | 8096 | 130 | 4 | 4 | 1 | 0 | 0 | 1 | 464
25-0059990 | Tuolumne | SPRING GAP 1702 | SPRING GAP 17029690 | Vegetation | 2025-06-01 03:12 | -07:00 | 05/27 - 06/02 | 2025-06-01 08:32 | -07:00 | 320 | FTS | 220160 | 688 | 14 | 9 | 8 | 0 | 0 | 0 | 320
25-0059997 | Tehama | VOLTA 1101 | VOLTA 110153118 | Animal | 2025-06-01 05:49 | -07:00 | 05/27 - 06/02 | 2025-06-01 09:23 | -07:00 | 188.0721 | FTS | 177352 | 943 | 46 | 34 | 31 | 3 | 0 | 0 | 214
25-0059956 | El Dorado | EL DORADO PH 2102 | EL DORADO PH 2102CB | Equipment Failure/Involved | 2025-05-31 19:20 | -07:00 | 05/27 - 06/02 | 2025-06-01 10:40 | -07:00 | 133.5839 | FTS | 219612 | 1644 | 116 | 84 | 21 | 7 | 0 | 0 | 920
25-0060029 | Kings | AVENAL 2101 | AVENAL 21019070 | Animal | 2025-06-01 09:58 | -07:00 | 05/27 - 06/02 | 2025-06-01 13:11 | -07:00 | 193 | FTS | 13317 | 69 | 0 | 0 | 8 | 0 | 0 | 0 | 193
25-0060046 | Nevada | BRUNSWICK 1106 | BRUNSWICK 11062392 | Vegetation | 2025-06-01 13:03 | -07:00 | 05/27 - 06/02 | 2025-06-01 14:29 | -07:00 | 46.4348 | FTS | 25632 | 552 | 29 | 21 | 9 | 2 | 0 | 6 | 86
25-0059961 | Kern | TEJON 1103 | TEJON 1103145334 | Equipment Failure/Involved | 2025-05-31 20:27 | -07:00 | 05/27 - 06/02 | 2025-06-01 15:31 | -07:00 | 370.9344 | FTS | 22627 | 61 | 0 | 0 | 1 | 0 | 0 | 0 | 1144
25-0060053 | Kern | FELLOWS 2103 | FELLOWS 2103CB | Animal | 2025-06-01 14:11 | -07:00 | 05/27 - 06/02 | 2025-06-01 16:05 | -07:00 | 114 | FTS | 21318 | 187 | 6 | 4 | 3 | 0 | 0 | 0 | 114
25-0060067 | Sutter | MERIDIAN 1101 | MERIDIAN 1101CB | Unknown Cause | 2025-06-01 15:41 | -07:00 | 05/27 - 06/02 | 2025-06-01 18:04 | -07:00 | 115.3733 | FTS | 51918 | 450 | 10 | 6 | 5 | 2 | 0 | 0 | 143
25-0059973 | Nevada | GRASS VALLEY 1103 | GRASS VALLEY 11032110 | Vegetation | 2025-05-31 22:19 | -07:00 | 05/27 - 06/02 | 2025-06-01 18:37 | -07:00 | 121.5648 | FTS | 104181 | 857 | 69 | 47 | 20 | 4 | 0 | 17 | 1218
25-0060049 | Contra Costa | SOBRANTE 1103 | SOBRANTE 1103LA401R | Vegetation | 2025-06-01 12:59 | -07:00 | 05/27 - 06/02 | 2025-06-01 19:53 | -07:00 | 125.4266 | FTS | 53808 | 429 | 24 | 18 | 4 | 0 | 0 | 0 | 414
25-0060082 | Sonoma | SONOMA 1105 | SONOMA 1105138 | Animal | 2025-06-01 20:03 | -07:00 | 05/27 - 06/02 | 2025-06-01 21:18 | -07:00 | 75 | FTS | 52725 | 703 | 26 | 18 | 7 | 0 | 0 | 15 | 75
25-0060084 | Contra Costa | VALLEY VIEW 1106 | VALLEY VIEW 1106CB | Unknown Cause | 2025-06-01 20:47 | -07:00 | 05/27 - 06/02 | 2025-06-01 21:34 | -07:00 | 47 | FTS | 213521 | 4543 | 289 | 194 | 59 | 6 | 0 | 2 | 47
25-0060095 | Mendocino | PHILO 1101 | PHILO 1101CB | 3rd Party | 2025-06-01 22:09 | -07:00 | 05/27 - 06/02 | 2025-06-02 00:07 | -07:00 | 90.4207 | FTS | 104888 | 1160 | 28 | 23 | 30 | 9 | 0 | 2 | 118
25-0060000 | Alameda | VINEYARD 2108 | VINEYARD 2108MR172 | Equipment Failure/Involved | 2025-06-01 07:11 | -07:00 | 05/27 - 06/02 | 2025-06-02 02:19 | -07:00 | 156.1217 | FTS | 514577 | 3296 | 151 | 111 | 36 | 2 | 0 | 1 | 1148
25-0060098 | Kings | KETTLEMAN HILLS 2104 | KETTLEMAN HILLS 21049020 | Unknown Cause | 2025-06-01 22:35 | -07:00 | 05/27 - 06/02 | 2025-06-02 06:52 | -07:00 | 473.2857 | FTS | 26504 | 56 | 2 | 0 | 0 | 0 | 0 | 0 | 497
25-0060181 | Napa | SILVERADO 2102 | SILVERADO 2102942170 | Animal | 2025-06-02 08:49 | -07:00 | 05/27 - 06/02 | 2025-06-02 10:09 | -07:00 | 49.4356 | FTS | 9986 | 202 | 1 | 0 | 3 | 0 | 0 | 1 | 80
25-0060146 | Calaveras | FROGTOWN 1702 | FROGTOWN 170232556 | Unknown Cause | 2025-06-02 07:53 | -07:00 | 05/27 - 06/02 | 2025-06-02 10:16 | -07:00 | 59.4627 | FTS | 230537 | 3877 | 216 | 159 | 123 | 16 | 1 | 6 | 143
25-0060294 | Napa | SILVERADO 2104 | SILVERADO 2104959428 | Company Initiated | 2025-06-02 12:09 | -07:00 | 05/27 - 06/02 | 2025-06-02 12:24 | -07:00 | 15 | FTS | 6060 | 404 | 19 | 11 | 3 | 0 | 0 | 3 | 15
25-0052765 | El Dorado | EL DORADO PH 2101 | EL DORADO PH 210119752 | Company Initiated | 2025-06-02 12:21 | -07:00 | 05/27 - 06/02 | 2025-06-02 12:27 | -07:00 | 6 | FTS | 6564 | 1094 | 91 | 71 | 13 | 3 | 0 | 2 | 6
25-0060299 | Madera | OAKHURST 1103 | OAKHURST 1103121108 | Company Initiated | 2025-06-02 12:08 | -07:00 | 05/27 - 06/02 | 2025-06-02 12:35 | -07:00 | 27 | FTS | 3726 | 138 | 5 | 3 | 3 | 0 | 0 | 0 | 27
25-0060253 | Yolo | MADISON 2101 | MADISON 21017702 | 3rd Party | 2025-06-02 10:50 | -07:00 | 05/27 - 06/02 | 2025-06-02 12:46 | -07:00 | 91.0271 | FTS | 84109 | 924 | 19 | 11 | 17 | 14 | 0 | 4 | 116
25-0060194 | Santa Barbara | CUYAMA 1103, CUYAMA 1104, CUYAMA 2102 | N/A | Unknown Cause | 2025-06-02 09:04 | -07:00 | 05/27 - 06/02 | 2025-06-02 13:01 | -07:00 | 218.6122 | T-EPSS | 117832 | 539 | 10 | 7 | 13 | 1 | 0 | 0 | 237
25-0060288 | Kern | FELLOWS 2104 | FELLOWS 210442100 | 3rd Party | 2025-06-02 11:56 | -07:00 | 05/27 - 06/02 | 2025-06-02 14:02 | -07:00 | 126 | FTS | 2646 | 21 | 0 | 0 | 7 | 0 | 0 | 0 | 126
25-0060330 | Glenn | LOGAN CREEK 2102 | LOGAN CREEK 21022428 | Company Initiated | 2025-06-02 12:39 | -07:00 | 05/27 - 06/02 | 2025-06-02 16:26 | -07:00 | 227 | FTS | 33369 | 147 | 1 | 1 | 0 | 0 | 0 | 0 | 227
25-0060414 | Humboldt | TRINIDAD 1101 | N/A | Vegetation | 2025-06-02 15:00 | -07:00 | 05/27 - 06/02 | 2025-06-02 17:24 | -07:00 | 144 | T-EPSS | 211536 | 1469 | 88 | 71 | 43 | 3 | 0 | 17 | 144
25-0060441 | Butte | ANITA 1106 | ANITA 11062418 | Equipment Failure/Involved | 2025-06-02 16:06 | -07:00 | 05/27 - 06/02 | 2025-06-02 17:33 | -07:00 | 87 | FTS | 20097 | 231 | 15 | 7 | 1 | 0 | 0 | 0 | 87
25-0060503 | Lake | HIGHLANDS 1103 | HIGHLANDS 1103726580 | Company Initiated | 2025-06-02 17:52 | -07:00 | 05/27 - 06/02 | 2025-06-02 18:17 | -07:00 | 25 | FTS | 325 | 13 | 1 | 0 | 0 | 0 | 0 | 0 | 25
25-0060416 | Humboldt | BIG LAGOON 1101 | N/A | Vegetation | 2025-06-02 15:00 | -07:00 | 05/27 - 06/02 | 2025-06-02 18:42 | -07:00 | 222 | T-EPSS | 32634 | 147 | 9 | 7 | 3 | 1 | 0 | 0 | 222
25-0060479 | Napa | MONTICELLO 1101 | MONTICELLO 110137384 | Unknown Cause | 2025-06-02 17:00 | -07:00 | 05/27 - 06/02 | 2025-06-02 19:23 | -07:00 | 143 | FTS | 72215 | 505 | 20 | 14 | 11 | 0 | 0 | 3 | 143
25-0060413 | Humboldt | ORICK 1102 | N/A | Vegetation | 2025-06-02 15:00 | -07:00 | 05/27 - 06/02 | 2025-06-02 22:26 | -07:00 | 427.0117 | T-EPSS | 145611 | 341 | 12 | 8 | 8 | 1 | 0 | 1 | 446
25-0060538 | Monterey | BORONDA 1101, BORONDA 1102 | N/A | Unknown Cause | 2025-06-03 04:57 | -07:00 | 06/03 - 06/09 | 2025-06-03 06:37 | -07:00 | 74.3173 | T-EPSS | 60420 | 813 | 35 | 27 | 13 | 2 | 0 | 0 | 100
25-0060539 | Lake | HIGHLANDS 1104 | HIGHLANDS 110448262 | Animal | 2025-06-03 05:29 | -07:00 | 06/03 - 06/09 | 2025-06-03 06:49 | -07:00 | 63.0259 | FTS | 36492 | 579 | 54 | 36 | 2 | 0 | 0 | 0 | 80
25-0060544 | Santa Clara | LOYOLA 1102 | LOYOLA 1102550291 | Animal | 2025-06-03 05:55 | -07:00 | 06/03 - 06/09 | 2025-06-03 08:32 | -07:00 | 157 | FTS | 25434 | 162 | 3 | 3 | 3 | 0 | 0 | 0 | 157
25-0060715 | Santa Clara | MC KEE 1107 | MC KEE 1107827486 | Animal | 2025-06-03 11:21 | -07:00 | 06/03 - 06/09 | 2025-06-03 12:06 | -07:00 | 45 | FTS | 1890 | 42 | 1 | 0 | 0 | 0 | 0 | 1 | 45
25-0060598 | Sonoma | FITCH MOUNTAIN 1113 | FITCH MOUNTAIN 1113356 | Unknown Cause | 2025-06-03 08:09 | -07:00 | 06/03 - 06/09 | 2025-06-03 12:12 | -07:00 | 243 | FTS | 74358 | 306 | 8 | 5 | 4 | 0 | 0 | 2 | 243
25-0060529 | Santa Clara | MORGAN HILL 2111 | MORGAN HILL 2111XR398 | Vegetation | 2025-06-03 00:38 | -07:00 | 06/03 - 06/09 | 2025-06-03 12:50 | -07:00 | 184.6175 | FTS | 73847 | 400 | 20 | 17 | 10 | 0 | 0 | 2 | 732
25-0060802 | Marin | NOVATO 1104 | NOVATO 1104889406 | Company Initiated | 2025-06-03 13:28 | -07:00 | 06/03 - 06/09 | 2025-06-03 14:18 | -07:00 | 50 | FTS | 150 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 50
25-0060851 | San Luis Obispo | ATASCADERO 1103 | ATASCADERO 1103440856 | Company Initiated | 2025-06-03 10:47 | -07:00 | 06/03 - 06/09 | 2025-06-03 14:52 | -07:00 | 245 | FTS | 12005 | 49 | 2 | 1 | 0 | 0 | 0 | 7 | 245
25-0060830 | Sonoma | SONOMA 1104 | SONOMA 1104914376 | Company Initiated | 2025-06-03 14:04 | -07:00 | 06/03 - 06/09 | 2025-06-03 15:03 | -07:00 | 57.4192 | FTS | 43696 | 761 | 32 | 22 | 11 | 1 | 0 | 13 | 59
25-0060730 | Placer | AUBURN 1102 | AUBURN 1102251946 | Vegetation | 2025-06-03 11:32 | -07:00 | 06/03 - 06/09 | 2025-06-03 17:46 | -07:00 | 113.7784 | FTS | 112982 | 993 | 45 | 28 | 11 | 2 | 0 | 0 | 374
25-0060563 | Glenn | ELK CREEK 1101 | ELK CREEK 11012004 | Equipment Failure/Involved | 2025-06-03 06:53 | -07:00 | 06/03 - 06/09 | 2025-06-03 18:46 | -07:00 | 252.6919 | FTS | 43463 | 172 | 11 | 8 | 3 | 0 | 0 | 0 | 713
25-0060962 | Sonoma | DUNBAR 1101 | DUNBAR 1101137736 | 3rd Party | 2025-06-03 17:39 | -07:00 | 06/03 - 06/09 | 2025-06-03 21:56 | -07:00 | 128.1456 | FTS | 216566 | 1690 | 81 | 55 | 28 | 5 | 0 | 1 | 257
25-0060975 | Nevada | NARROWS 2102 | NARROWS 210242584 | Vegetation | 2025-06-03 18:35 | -07:00 | 06/03 - 06/09 | 2025-06-04 05:21 | -07:00 | 160.9508 | FTS | 81763 | 508 | 36 | 29 | 4 | 0 | 0 | 1 | 646
25-0061076 | Calaveras | STANISLAUS 1702 | STANISLAUS 17021850 | Unknown Cause | 2025-06-04 08:37 | -07:00 | 06/03 - 06/09 | 2025-06-04 10:41 | -07:00 | 87.79 | FTS | 214032 | 2438 | 80 | 63 | 27 | 3 | 2 | 0 | 124
25-0061148 | Santa Clara | HICKS 1116 | HICKS 1116LB16 | 3rd Party | 2025-06-04 10:12 | -07:00 | 06/03 - 06/09 | 2025-06-04 11:37 | -07:00 | 55.937 | FTS | 67460 | 1206 | 35 | 27 | 19 | 1 | 1 | 2 | 85
25-0061078 | Calaveras | STANISLAUS 1701 | STANISLAUS 170179826 | Company Initiated | 2025-06-04 08:37 | -07:00 | 06/03 - 06/09 | 2025-06-04 12:24 | -07:00 | 227 | FTS | 31780 | 140 | 7 | 6 | 3 | 0 | 0 | 0 | 227
25-0061284 | Nevada | NARROWS 2105 | NARROWS 21052426 | Animal | 2025-06-04 13:09 | -07:00 | 06/03 - 06/09 | 2025-06-04 13:46 | -07:00 | 37 | FTS | 78440 | 2120 | 149 | 88 | 21 | 4 | 0 | 39 | 37
25-0061311 | Glenn | LOGAN CREEK 2102 | LOGAN CREEK 21022428 | Company Initiated | 2025-06-04 13:41 | -07:00 | 06/03 - 06/09 | 2025-06-04 17:22 | -07:00 | 122.9728 | FTS | 18077 | 147 | 1 | 1 | 0 | 0 | 0 | 0 | 221
25-0061190 | Tuolumne | SPRING GAP 1702 | SPRING GAP 170210720 | Equipment Failure/Involved | 2025-06-04 11:02 | -07:00 | 06/03 - 06/09 | 2025-06-04 17:34 | -07:00 | 226.1871 | FTS | 35059 | 155 | 3 | 3 | 3 | 0 | 0 | 0 | 392
25-0061520 | Contra Costa | CLAYTON 2212 | CLAYTON 2212204416 | Unknown Cause | 2025-06-05 05:14 | -07:00 | 06/03 - 06/09 | 2025-06-05 07:50 | -07:00 | 103.0078 | FTS | 26370 | 256 | 18 | 12 | 3 | 0 | 0 | 9 | 156
25-0061493 | Sonoma | CLOVERDALE 1102 | CLOVERDALE 1102262 | Unknown Cause | 2025-06-04 20:08 | -07:00 | 06/03 - 06/09 | 2025-06-05 09:06 | -07:00 | 778 | FTS | 281636 | 362 | 13 | 13 | 11 | 0 | 0 | 6 | 778
25-0061624 | Amador | CLAY 1101 | CLAY 110113450 | Animal | 2025-06-05 09:47 | -07:00 | 06/03 - 06/09 | 2025-06-05 10:48 | -07:00 | 61 | FTS | 27206 | 446 | 37 | 26 | 5 | 0 | 0 | 0 | 61
25-0061567 | Tehama | VINA 1101 | VINA 11011570 | Animal | 2025-06-05 07:58 | -07:00 | 06/03 - 06/09 | 2025-06-05 11:25 | -07:00 | 181.7843 | FTS | 55626 | 306 | 15 | 12 | 0 | 0 | 0 | 1 | 207
25-0061594 | El Dorado | SHINGLE SPRINGS 2109 | SHINGLE SPRINGS 210913322 | Unknown Cause | 2025-06-05 09:01 | -07:00 | 06/03 - 06/09 | 2025-06-05 12:15 | -07:00 | 181.5484 | FTS | 118188 | 651 | 57 | 40 | 4 | 0 | 0 | 10 | 194
25-0061731 | Napa | CALISTOGA 1102 | CALISTOGA 1102131531 | Company Initiated | 2025-06-05 12:20 | -07:00 | 06/03 - 06/09 | 2025-06-05 12:26 | -07:00 | 6 | FTS | 312 | 52 | 1 | 1 | 1 | 0 | 0 | 0 | 6
25-0061775 | Placer | PENRYN 1103 | PENRYN 1103604 | 3rd Party | 2025-06-05 13:13 | -07:00 | 06/03 - 06/09 | 2025-06-05 14:18 | -07:00 | 65 | FTS | 22230 | 342 | 22 | 14 | 3 | 0 | 0 | 8 | 65
25-0061930 | Sonoma | GEYSERVILLE 1101 | GEYSERVILLE 1101480 | Vegetation | 2025-06-05 16:28 | -07:00 | 06/03 - 06/09 | 2025-06-05 18:26 | -07:00 | 118 | FTS | 17464 | 148 | 2 | 2 | 1 | 0 | 0 | 1 | 118
25-0061960 | El Dorado | EL DORADO PH 2101 | EL DORADO PH 21016852 | Company Initiated | 2025-06-05 18:16 | -07:00 | 06/03 - 06/09 | 2025-06-05 18:51 | -07:00 | 32.6024 | FTS | 66411 | 2037 | 170 | 130 | 34 | 4 | 0 | 2 | 35
25-0061977 | Napa | NAPA 1112 | NAPA 1112315244 | 3rd Party | 2025-06-05 19:53 | -07:00 | 06/03 - 06/09 | 2025-06-05 20:48 | -07:00 | 55 | FTS | 7040 | 128 | 6 | 4 | 1 | 0 | 0 | 5 | 55
25-0061982 | Fresno | CANTUA 1103 | CANTUA 11039900 | Unknown Cause | 2025-06-05 21:46 | -07:00 | 06/03 - 06/09 | 2025-06-06 02:55 | -07:00 | 309 | FTS | 5253 | 17 | 0 | 0 | 1 | 0 | 0 | 0 | 309
25-0062003 | Placer | PENRYN 1103 | PENRYN 1103660 | Animal | 2025-06-06 03:48 | -07:00 | 06/03 - 06/09 | 2025-06-06 06:15 | -07:00 | 147 | FTS | 67179 | 457 | 31 | 21 | 3 | 0 | 0 | 8 | 147
25-0062036 | Calaveras | FROGTOWN 1702 | FROGTOWN 170232556 | Animal | 2025-06-06 07:31 | -07:00 | 06/03 - 06/09 | 2025-06-06 10:09 | -07:00 | 83.2427 | FTS | 295262 | 3547 | 200 | 145 | 95 | 14 | 1 | 6 | 158
25-0061957 | Santa Clara | STELLING 1110 | STELLING 111060094 | Animal | 2025-06-05 18:08 | -07:00 | 06/03 - 06/09 | 2025-06-06 10:35 | -07:00 | 277.1882 | FTS | 75118 | 271 | 15 | 12 | 7 | 0 | 0 | 13 | 987
25-0062118 | El Dorado | MOUNTAIN QUARRIES 2101 | MOUNTAIN QUARRIES 21011102 | Unknown Cause | 2025-06-06 09:29 | -07:00 | 06/03 - 06/09 | 2025-06-06 12:14 | -07:00 | 165 | FTS | 132990 | 806 | 82 | 59 | 10 | 0 | 0 | 26 | 165
25-0062142 | Sonoma | GEYSERVILLE 1101 | GEYSERVILLE 1101166 | Vegetation | 2025-06-06 09:57 | -07:00 | 06/03 - 06/09 | 2025-06-06 13:16 | -07:00 | 141.2989 | FTS | 91703 | 649 | 14 | 12 | 8 | 0 | 0 | 6 | 199
25-0062290 | Glenn | LOGAN CREEK 2102 | LOGAN CREEK 21022428 | Company Initiated | 2025-06-06 13:37 | -07:00 | 06/03 - 06/09 | 2025-06-06 16:19 | -07:00 | 117.4422 | FTS | 17264 | 147 | 1 | 1 | 0 | 0 | 0 | 0 | 162
25-0062389 | Napa | CALISTOGA 1101 | CALISTOGA 1101894220 | Unknown Cause | 2025-06-06 17:45 | -07:00 | 06/03 - 06/09 | 2025-06-06 19:45 | -07:00 | 120 | FTS | 11040 | 92 | 1 | 1 | 7 | 0 | 0 | 1 | 120
25-0062392 | Tehama | CORNING 1101 | CORNING 1101972454 | Animal | 2025-06-06 18:24 | -07:00 | 06/03 - 06/09 | 2025-06-06 19:48 | -07:00 | 84 | FTS | 76692 | 913 | 81 | 59 | 16 | 2 | 0 | 0 | 84
25-0062414 | Contra Costa | FAIRVIEW 2207 | FAIRVIEW 2207P302 | Company Initiated | 2025-06-07 02:00 | -07:00 | 06/03 - 06/09 | 2025-06-07 02:57 | -07:00 | 57 | FTS | 57 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 57
25-0062412 | Humboldt | GARBERVILLE 1101 | GARBERVILLE 11011750 | Unknown Cause | 2025-06-07 00:14 | -07:00 | 06/03 - 06/09 | 2025-06-07 03:54 | -07:00 | 220 | FTS | 20020 | 91 | 3 | 1 | 2 | 0 | 0 | 0 | 220
25-0062418 | Santa Clara | EDENVALE 2105 | EDENVALE 2105739448 | Animal | 2025-06-07 05:35 | -07:00 | 06/03 - 06/09 | 2025-06-07 05:58 | -07:00 | 23 | FTS | 115 | 5 | 0 | 0 | 2 | 0 | 0 | 0 | 23
25-0062472 | Shasta | OREGON TRAIL 1104 | OREGON TRAIL 11041574 | Unknown Cause | 2025-06-07 10:34 | -07:00 | 06/03 - 06/09 | 2025-06-07 13:32 | -07:00 | 175.3711 | FTS | 68044 | 388 | 32 | 21 | 4 | 0 | 0 | 0 | 178
25-0062510 | Sonoma | WINDSOR 1103 | WINDSOR 11035060 | Equipment Failure/Involved | 2025-06-07 14:33 | -07:00 | 06/03 - 06/09 | 2025-06-07 15:53 | -07:00 | 38.35 | FTS | 21476 | 560 | 24 | 16 | 10 | 1 | 0 | 2 | 80
25-0062496 | Tuolumne | MIWUK 1702 | MIWUK 17028130 | Equipment Failure/Involved | 2025-06-07 12:55 | -07:00 | 06/03 - 06/09 | 2025-06-07 16:18 | -07:00 | 203 | FTS | 89117 | 439 | 28 | 18 | 2 | 1 | 0 | 0 | 203
25-0062519 | Contra Costa | CLAYTON 2215 | CLAYTON 2215CB | Animal | 2025-06-07 15:53 | -07:00 | 06/03 - 06/09 | 2025-06-07 16:59 | -07:00 | 62.3479 | FTS | 281937 | 4522 | 314 | 240 | 65 | 6 | 0 | 0 | 66
25-0062529 | Contra Costa | FAIRVIEW 2207 | FAIRVIEW 2207M501R | Animal | 2025-06-07 18:20 | -07:00 | 06/03 - 06/09 | 2025-06-07 19:43 | -07:00 | 83 | FTS | 84245 | 1015 | 40 | 25 | 6 | 0 | 0 | 0 | 83
25-0062538 | Lake | HARTLEY 1101 | HARTLEY 1101738 | Vegetation | 2025-06-07 19:46 | -07:00 | 06/03 - 06/09 | 2025-06-07 21:30 | -07:00 | 104 | FTS | 98176 | 944 | 71 | 52 | 9 | 4 | 0 | 0 | 104
25-0062499 | Placer | PENRYN 1105 | PENRYN 110551676 | 3rd Party | 2025-06-07 13:17 | -07:00 | 06/03 - 06/09 | 2025-06-07 22:35 | -07:00 | 163.576 | FTS | 173227 | 1059 | 58 | 38 | 23 | 8 | 0 | 25 | 558
25-0062547 | Sonoma | GEYSERVILLE 1102 | GEYSERVILLE 1102350 | Unknown Cause | 2025-06-07 22:14 | -07:00 | 06/03 - 06/09 | 2025-06-07 23:50 | -07:00 | 77.608 | FTS | 37019 | 477 | 6 | 1 | 8 | 1 | 0 | 3 | 96
25-0062564 | Placer | PENRYN 1107 | PENRYN 11072704 | Animal | 2025-06-08 05:37 | -07:00 | 06/03 - 06/09 | 2025-06-08 06:28 | -07:00 | 51 | FTS | 9027 | 177 | 9 | 6 | 1 | 0 | 0 | 1 | 51
25-0062562 | Mendocino | HOPLAND 1101 | HOPLAND 1101768 | Unknown Cause | 2025-06-08 05:27 | -07:00 | 06/03 - 06/09 | 2025-06-08 06:49 | -07:00 | 62.47 | FTS | 6247 | 100 | 5 | 5 | 1 | 0 | 0 | 0 | 82
25-0062568 | Mendocino | CALPELLA 1101 | MENDOCINO 1101856020 | Animal | 2025-06-08 06:46 | -07:00 | 06/03 - 06/09 | 2025-06-08 08:09 | -07:00 | 83 | FTS | 62250 | 750 | 37 | 25 | 10 | 1 | 0 | 1 | 83
25-0062573 | Santa Clara | LOS GATOS 1108 | LOS GATOS 1108590544 | Animal | 2025-06-08 06:35 | -07:00 | 06/03 - 06/09 | 2025-06-08 08:24 | -07:00 | 109 | FTS | 82404 | 756 | 19 | 14 | 4 | 2 | 0 | 0 | 109
25-0062559 | Madera | COARSEGOLD 2104 | COARSEGOLD 210410400 | Unknown Cause | 2025-06-08 04:22 | -07:00 | 06/03 - 06/09 | 2025-06-08 09:34 | -07:00 | 83.024 | FTS | 124619 | 1501 | 123 | 89 | 38 | 2 | 0 | 1 | 312
25-0062543 | Monterey | JOLON 1102 | JOLON 11027070 | Unknown Cause | 2025-06-07 22:03 | -07:00 | 06/03 - 06/09 | 2025-06-08 12:42 | -07:00 | 340.6641 | FTS | 88232 | 259 | 4 | 4 | 19 | 0 | 0 | 4 | 879
25-0062553 | Calaveras | CORRAL 1101 | CORRAL 110112606 | 3rd Party | 2025-06-07 23:57 | -07:00 | 06/03 - 06/09 | 2025-06-08 13:37 | -07:00 | 302.2188 | FTS | 96710 | 320 | 19 | 15 | 7 | 0 | 0 | 0 | 820
25-0062530 | Tuolumne | CURTIS 1702 | CURTIS 1702873788 | Equipment Failure/Involved | 2025-06-07 18:40 | -07:00 | 06/03 - 06/09 | 2025-06-08 14:06 | -07:00 | 205.7931 | FTS | 5968 | 29 | 1 | 1 | 0 | 0 | 0 | 0 | 1166
25-0062566 | Santa Clara | LOYOLA 1102 | LOYOLA 110260128 | Animal | 2025-06-08 06:07 | -07:00 | 06/03 - 06/09 | 2025-06-08 16:59 | -07:00 | 117.6078 | FTS | 95968 | 816 | 30 | 21 | 22 | 3 | 0 | 0 | 652
25-0062630 | Santa Clara | MORGAN HILL 2111 | MORGAN HILL 2111XR398 | Unknown Cause | 2025-06-08 15:57 | -07:00 | 06/03 - 06/09 | 2025-06-08 19:06 | -07:00 | 103.575 | FTS | 41430 | 400 | 20 | 17 | 10 | 0 | 0 | 2 | 189
25-0062633 | Nevada | NARROWS 2105 | NARROWS 21052228 | Environmental/External | 2025-06-08 16:58 | -07:00 | 06/03 - 06/09 | 2025-06-08 19:11 | -07:00 | 72.4487 | FTS | 19054 | 263 | 9 | 6 | 5 | 0 | 0 | 4 | 133
25-0062640 | Tulare | STONE CORRAL 1110 | STONE CORRAL 1110975698 | 3rd Party | 2025-06-08 18:14 | -07:00 | 06/03 - 06/09 | 2025-06-08 19:47 | -07:00 | 93 | FTS | 4836 | 52 | 1 | 1 | 1 | 0 | 0 | 0 | 93
25-0062651 | Butte | WYANDOTTE 1107 | WYANDOTTE 1107CB | Unknown Cause | 2025-06-08 19:52 | -07:00 | 06/03 - 06/09 | 2025-06-08 21:56 | -07:00 | 124 | FTS | 10416 | 84 | 11 | 9 | 0 | 0 | 0 | 0 | 124
25-0062656 | Kern | ARVIN 1101 | ARVIN 110194892 | 3rd Party | 2025-06-08 21:02 | -07:00 | 06/03 - 06/09 | 2025-06-08 23:09 | -07:00 | 126.5014 | HLT | 45667 | 361 | 7 | 5 | 3 | 0 | 0 | 0 | 127
25-0062567 | Mendocino | UKIAH 1114 | UKIAH 1114380432 | Vegetation | 2025-06-08 06:13 | -07:00 | 06/03 - 06/09 | 2025-06-08 23:22 | -07:00 | 231.25 | FTS | 29600 | 128 | 2 | 1 | 7 | 0 | 0 | 0 | 1029
25-0062666 | Santa Cruz | BURNS 2101 | BURNS 210110912 | Unknown Cause | 2025-06-08 23:43 | -07:00 | 06/03 - 06/09 | 2025-06-09 02:51 | -07:00 | 182.4502 | FTS | 300678 | 1648 | 116 | 103 | 26 | 3 | 0 | 3 | 188
25-0062679 | Kings | DEVILS DEN 1101 | DEVILS DEN 1101CB | Animal | 2025-06-09 04:15 | -07:00 | 06/03 - 06/09 | 2025-06-09 06:41 | -07:00 | 146 | FTS | 11096 | 76 | 0 | 0 | 8 | 0 | 0 | 0 | 146
25-0062772 | Nevada | BRUNSWICK 1106 | BRUNSWICK 11062790 | Company Initiated | 2025-06-09 09:15 | -07:00 | 06/03 - 06/09 | 2025-06-09 10:08 | -07:00 | 53 | FTS | 2120 | 40 | 2 | 2 | 0 | 0 | 0 | 0 | 53
25-0062704 | Butte | CLARK ROAD 1102 | CLARK ROAD 11022068 | Animal | 2025-06-09 07:37 | -07:00 | 06/03 - 06/09 | 2025-06-09 10:50 | -07:00 | 193 | FTS | 44197 | 229 | 17 | 10 | 2 | 1 | 0 | 2 | 193
25-0062571 | Nevada | NARROWS 2105 | NARROWS 21052216 | Equipment Failure/Involved | 2025-06-08 07:28 | -07:00 | 06/03 - 06/09 | 2025-06-09 11:55 | -07:00 | 155.4913 | FTS | 161400 | 1038 | 68 | 43 | 8 | 0 | 0 | 29 | 1707
25-0062667 | Monterey | LAURELES 1111 | LAURELES 11112020 | Unknown Cause | 2025-06-09 | -07:00 | 06/03 - 06/09 | 2025-06-09 14:27 | -07:00 | 867 | FTS | 725679 | 837 | 20 | 17 | 26 | 0 | 0 | 3 | 867
25-0062647 | Contra Costa | LAKEWOOD 2107 | LAKEWOOD 210738404 | Equipment Failure/Involved | 2025-06-08 19:41 | -07:00 | 06/03 - 06/09 | 2025-06-09 14:55 | -07:00 | 129.4769 | FTS | 50496 | 390 | 18 | 11 | 4 | 0 | 0 | 0 | 1154
25-0062734 | Mendocino | WILLITS 1103 | WILLITS 110391948 | Vegetation | 2025-06-09 08:30 | -07:00 | 06/03 - 06/09 | 2025-06-09 17:14 | -07:00 | 100.8468 | FTS | 11194 | 111 | 8 | 6 | 2 | 0 | 0 | 0 | 524
25-0062867 | Nevada | BRUNSWICK 1105 | BRUNSWICK 11052204 | Vegetation | 2025-06-09 11:57 | -07:00 | 06/10 - 06/16 | 2025-06-10 03:12 | -07:00 | 126.6266 | FTS | 121055 | 956 | 53 | 38 | 14 | 0 | 0 | 24 | 915
25-0063088 | Nevada | BRUNSWICK 1105 | BRUNSWICK 11052140 | Company Initiated | 2025-06-10 03:12 | -07:00 | 06/10 - 06/16 | 2025-06-10 05:11 | -07:00 | 119 | FTS | 5593 | 47 | 1 | 1 | 0 | 0 | 0 | 2 | 119
25-0063091 | Butte | WYANDOTTE 1103 | WYANDOTTE 1103640652 | Unknown Cause | 2025-06-10 05:39 | -07:00 | 06/10 - 06/16 | 2025-06-10 07:29 | -07:00 | 110 | FTS | 50380 | 458 | 26 | 18 | 6 | 1 | 0 | 0 | 110
25-0063101 | Santa Barbara | CABRILLO 1104 | CABRILLO 1104838078 | Equipment Failure/Involved | 2025-06-10 07:06 | -07:00 | 06/10 - 06/16 | 2025-06-10 08:19 | -07:00 | 73 | FTS | 18177 | 249 | 2 | 1 | 5 | 0 | 0 | 0 | 73
25-0063056 | Lassen | BOGARD 1101 | N/A | Unknown Cause | 2025-06-09 18:27 | -07:00 | 06/10 - 06/16 | 2025-06-10 10:57 | -07:00 | 990 | T-EPSS | 8910 | 9 | 0 | 0 | 1 | 0 | 0 | 0 | 990
25-0063085 | Amador | WEST POINT 1102 | WEST POINT 110112256 | Vegetation | 2025-06-10 01:37 | -07:00 | 06/10 - 06/16 | 2025-06-10 11:21 | -07:00 | 72.9513 | FTS | 130218 | 1785 | 133 | 101 | 15 | 0 | 0 | 4 | 584
25-0063090 | Contra Costa | TASSAJARA 2108 | TASSAJARA 2108846900 | Equipment Failure/Involved | 2025-06-10 04:47 | -07:00 | 06/10 - 06/16 | 2025-06-10 13:35 | -07:00 | 118.879 | FTS | 37328 | 314 | 13 | 8 | 2 | 0 | 0 | 1 | 528
25-0063251 | El Dorado | APPLE HILL 1104 | APPLE HILL 110412832 | Vegetation | 2025-06-10 10:54 | -07:00 | 06/10 - 06/16 | 2025-06-10 13:41 | -07:00 | 146.656 | FTS | 114245 | 779 | 58 | 41 | 7 | 0 | 0 | 16 | 167
25-0063074 | Santa Clara | HICKS 2103 | HICKS 2103LB50 | Vegetation | 2025-06-09 22:11 | -07:00 | 06/10 - 06/16 | 2025-06-10 17:06 | -07:00 | 366.2958 | FTS | 26007 | 71 | 1 | 0 | 2 | 0 | 0 | 1 | 1135
25-0063447 | Mendocino | LAYTONVILLE 1102 | LAYTONVILLE 1102CB | Company Initiated | 2025-06-10 13:49 | -07:00 | 06/10 - 06/16 | 2025-06-10 17:56 | -07:00 | 247 | FTS | 2470 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 247
25-0063415 | Santa Barbara | SANTA YNEZ 1102 | SANTA YNEZ 11026149 | Unknown Cause | 2025-06-10 14:56 | -07:00 | 06/10 - 06/16 | 2025-06-10 18:52 | -07:00 | 236 | FTS | 5900 | 25 | 0 | 0 | 1 | 0 | 0 | 0 | 236
25-0063418 | Napa | CALISTOGA 1102 | CALISTOGA 1102640833 | Equipment Failure/Involved | 2025-06-10 15:59 | -07:00 | 06/10 - 06/16 | 2025-06-10 19:08 | -07:00 | 189 | FTS | 1512 | 8 | 1 | 1 | 0 | 0 | 0 | 0 | 189
25-0063381 | Monterey | GONZALES 1101 | GONZALES 11013094 | Equipment Failure/Involved | 2025-06-10 15:10 | -07:00 | 06/10 - 06/16 | 2025-06-10 22:39 | -07:00 | 86.4118 | FTS | 5876 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 449
25-0063494 | Santa Clara | MORGAN HILL 2106 | MORGAN HILL 210653992 | Equipment Failure/Involved | 2025-06-10 22:57 | -07:00 | 06/10 - 06/16 | 2025-06-11 02:01 | -07:00 | 181.2352 | FTS | 113272 | 625 | 42 | 32 | 5 | 1 | 0 | 0 | 184
25-0063504 | San Joaquin | HERDLYN 1102 | HERDLYN 1102608254 | Unknown Cause | 2025-06-11 00:03 | -07:00 | 06/10 - 06/16 | 2025-06-11 04:53 | -07:00 | 250.0964 | FTS | 132301 | 529 | 38 | 21 | 20 | 3 | 0 | 0 | 290
25-0063516 | Santa Barbara | CABRILLO 1104 | CABRILLO 1104838078 | Equipment Failure/Involved | 2025-06-11 05:41 | -07:00 | 06/10 - 06/16 | 2025-06-11 06:51 | -07:00 | 70 | FTS | 17430 | 249 | 2 | 1 | 5 | 0 | 0 | 0 | 70
25-0063530 | Shasta | ANDERSON 1101 | ANDERSON 11011390 | Animal | 2025-06-11 06:57 | -07:00 | 06/10 - 06/16 | 2025-06-11 07:39 | -07:00 | 42 | FTS | 9618 | 229 | 24 | 18 | 1 | 1 | 0 | 0 | 42
25-0063544 | Santa Cruz | BEN LOMOND 0401 | BEN LOMOND 0401698634 | Unknown Cause | 2025-06-11 07:41 | -07:00 | 06/10 - 06/16 | 2025-06-11 09:25 | -07:00 | 104 | FTS | 12792 | 123 | 10 | 8 | 2 | 0 | 0 | 1 | 104
25-0063574 | Nevada | NARROWS 2102 | NARROWS 21022728 | Company Initiated | 2025-06-11 08:47 | -07:00 | 06/10 - 06/16 | 2025-06-11 12:01 | -07:00 | 83.6137 | FTS | 189385 | 2265 | 158 | 110 | 37 | 5 | 0 | 30 | 194
25-0063708 | Calaveras | FROGTOWN 1701 | FROGTOWN 1701914602 | Company Initiated | 2025-06-11 13:02 | -07:00 | 06/10 - 06/16 | 2025-06-11 13:09 | -07:00 | 7 | FTS | 4214 | 602 | 31 | 22 | 11 | 0 | 0 | 0 | 7
25-0059243 | Napa | SILVERADO 2104 | SILVERADO 2104324994 | Company Initiated | 2025-06-11 08:36 | -07:00 | 06/10 - 06/16 | 2025-06-11 14:47 | -07:00 | 20.9774 | FTS | 21313 | 1016 | 37 | 19 | 23 | 8 | 0 | 6 | 371
25-0063755 | El Dorado | ECHO SUMMIT 1101 | ECHO SUMMIT 1101927328 | Company Initiated | 2025-06-11 14:12 | -07:00 | 06/10 - 06/16 | 2025-06-11 15:36 | -07:00 | 84 | FTS | 117432 | 1398 | 40 | 30 | 78 | 1 | 0 | 2 | 84
25-0063802 | Sonoma | MIRABEL 1102 | MIRABEL 1102206 | Unknown Cause | 2025-06-11 14:43 | -07:00 | 06/10 - 06/16 | 2025-06-11 16:11 | -07:00 | 69.1628 | FTS | 17844 | 258 | 12 | 9 | 7 | 0 | 0 | 0 | 88
25-0063537 | San Luis Obispo | PASO ROBLES 1103 | PASO ROBLES 1103N54 | Equipment Failure/Involved | 2025-06-11 07:25 | -07:00 | 06/10 - 06/16 | 2025-06-11 19:44 | -07:00 | 299.7821 | FTS | 394813 | 1317 | 71 | 51 | 20 | 0 | 0 | 16 | 739
25-0063912 | Plumas | HAMILTON BRANCH 1101 | HAMILTON BRANCH 1101161872 | Unknown Cause | 2025-06-11 18:29 | -07:00 | 06/10 - 06/16 | 2025-06-11 21:27 | -07:00 | 178 | FTS | 2670 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 178
25-0063921 | Sonoma | WINDSOR 1103 | WINDSOR 11035060 | Equipment Failure/Involved | 2025-06-11 20:15 | -07:00 | 06/10 - 06/16 | 2025-06-11 21:31 | -07:00 | 76 | FTS | 42560 | 560 | 24 | 16 | 10 | 1 | 0 | 2 | 76
25-0063926 | Napa | CALISTOGA 1102 | CALISTOGA 1102306462 | Animal | 2025-06-11 20:53 | -07:00 | 06/10 - 06/16 | 2025-06-11 22:08 | -07:00 | 40.9567 | FTS | 91825 | 2242 | 51 | 36 | 27 | 5 | 0 | 2 | 75
25-0063932 | San Luis Obispo | ATASCADERO 1102 | ATASCADERO 1102A88 | Company Initiated | 2025-06-11 21:48 | -07:00 | 06/10 - 06/16 | 2025-06-11 23:29 | -07:00 | 101 | FTS | 165236 | 1636 | 41 | 28 | 8 | 2 | 0 | 0 | 101
25-0063949 | Yolo | MADISON 2101 | MADISON 2101760730 | Animal | 2025-06-12 00:03 | -07:00 | 06/10 - 06/16 | 2025-06-12 02:05 | -07:00 | 122 | FTS | 1952 | 16 | 0 | 0 | 1 | 0 | 0 | 0 | 122
25-0063950 | Sonoma | DUNBAR 1101 | DUNBAR 1101725292 | Unknown Cause | 2025-06-12 00:53 | -07:00 | 06/10 - 06/16 | 2025-06-12 02:16 | -07:00 | 83 | FTS | 7802 | 94 | 6 | 4 | 2 | 0 | 0 | 0 | 83
25-0063895 | Marin | STAFFORD 1102 | STAFFORD 11021202 | 3rd Party | 2025-06-11 17:26 | -07:00 | 06/10 - 06/16 | 2025-06-12 02:29 | -07:00 | 149.1935 | FTS | 18500 | 124 | 4 | 4 | 7 | 2 | 0 | 0 | 543
25-0063959 | Humboldt | GARBERVILLE 1102 | GARBERVILLE 1102939030 | Unknown Cause | 2025-06-12 05:37 | -07:00 | 06/10 - 06/16 | 2025-06-12 07:03 | -07:00 | 37.3836 | FTS | 2729 | 73 | 0 | 0 | 3 | 0 | 0 | 0 | 86
25-0064080 | El Dorado | APPLE HILL 1104 | APPLE HILL 110497086 | Company Initiated | 2025-06-12 09:20 | -07:00 | 06/10 - 06/16 | 2025-06-12 09:37 | -07:00 | 17 | FTS | 7769 | 457 | 38 | 26 | 5 | 0 | 0 | 13 | 17
25-0063988 | Yolo | MADISON 2101 | MADISON 2101760730 | Animal | 2025-06-12 07:30 | -07:00 | 06/10 - 06/16 | 2025-06-12 10:48 | -07:00 | 81.5091 | FTS | 76537 | 939 | 19 | 11 | 18 | 14 | 0 | 4 | 198
25-0064087 | Alpine | ALPINE 1101 | ALPINE 1101CB | Animal | 2025-06-12 10:01 | -07:00 | 06/10 - 06/16 | 2025-06-12 11:18 | -07:00 | 77 | FTS | 21714 | 282 | 4 | 3 | 2 | 1 | 0 | 0 | 77
25-0063937 | Monterey | SAN ARDO 1102 | SAN ARDO 11027030 | Unknown Cause | 2025-06-11 22:29 | -07:00 | 06/10 - 06/16 | 2025-06-12 11:57 | -07:00 | 808 | FTS | 86456 | 107 | 1 | 1 | 8 | 0 | 0 | 0 | 808
25-0064123 | San Luis Obispo | ATASCADERO 1102 | ATASCADERO 1102A88 | Company Initiated | 2025-06-12 10:53 | -07:00 | 06/10 - 06/16 | 2025-06-12 12:36 | -07:00 | 103 | FTS | 168508 | 1636 | 41 | 28 | 8 | 2 | 0 | 0 | 103
25-0064097 | Fresno | HAMMONDS 1102 | HAMMONDS 1102CB | Animal | 2025-06-12 10:19 | -07:00 | 06/10 - 06/16 | 2025-06-12 12:56 | -07:00 | 87.234 | FTS | 23117 | 265 | 0 | 0 | 11 | 0 | 0 | 0 | 157
25-0064073 | Kern | POSO MOUNTAIN 2101 | POSO MOUNTAIN 2101535138 | 3rd Party | 2025-06-12 09:38 | -07:00 | 06/10 - 06/16 | 2025-06-12 14:42 | -07:00 | 304 | FTS | 304 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 304
25-0064207 | El Dorado | MOUNTAIN QUARRIES 2101 | MOUNTAIN QUARRIES 21012422 | 3rd Party | 2025-06-12 12:46 | -07:00 | 06/10 - 06/16 | 2025-06-12 14:49 | -07:00 | 66.6248 | FTS | 38709 | 581 | 49 | 38 | 7 | 1 | 0 | 5 | 123
25-0064274 | Nevada | TAMARACK 1101 | TAMARACK 1101291312 | Unknown Cause | 2025-06-12 14:54 | -07:00 | 06/10 - 06/16 | 2025-06-12 16:16 | -07:00 | 82 | FTS | 9840 | 120 | 4 | 4 | 1 | 0 | 0 | 0 | 82
25-0064321 | Butte | WYANDOTTE 1109 | WYANDOTTE 1109759354 | Unknown Cause | 2025-06-12 16:00 | -07:00 | 06/10 - 06/16 | 2025-06-12 18:37 | -07:00 | 138.9304 | FTS | 199504 | 1436 | 125 | 98 | 16 | 5 | 0 | 5 | 157
25-0064390 | Calaveras | WEST POINT 1102 | WEST POINT 1102CB | 3rd Party | 2025-06-12 18:57 | -07:00 | 06/10 - 06/16 | 2025-06-12 20:08 | -07:00 | 71 | FTS | 6887 | 97 | 6 | 3 | 1 | 0 | 0 | 0 | 71
25-0064281 | Napa | SILVERADO 2104 | SILVERADO 2104940 | Company Initiated | 2025-06-12 22:39 | -07:00 | 06/10 - 06/16 | 2025-06-12 22:45 | -07:00 | 23.3404 | FTS | 22967 | 984 | 28 | 16 | 7 | 2 | 0 | 0 | 6
25-0063955 | San Mateo | WOODSIDE 1104 | WOODSIDE 11049032 | Vegetation | 2025-06-12 04:20 | -07:00 | 06/10 - 06/16 | 2025-06-13 02:12 | -07:00 | 181.715 | FTS | 76502 | 421 | 10 | 4 | 11 | 1 | 0 | 0 | 1312
25-0064400 | Lake | REDBUD 1102 | REDBUD 1102922 | Unknown Cause | 2025-06-12 21:44 | -07:00 | 06/10 - 06/16 | 2025-06-13 08:10 | -07:00 | 626 | FTS | 210336 | 336 | 17 | 12 | 5 | 0 | 1 | 2 | 626
25-0064481 | Lake | HIGHLANDS 1104 | HIGHLANDS 1104CB | Animal | 2025-06-13 08:35 | -07:00 | 06/10 - 06/16 | 2025-06-13 09:14 | -07:00 | 39 | FTS | 119028 | 3052 | 265 | 192 | 45 | 5 | 2 | 0 | 39
25-0064488 | San Joaquin | CORRAL 1101 | CORRAL 1101173174 | 3rd Party | 2025-06-13 08:51 | -07:00 | 06/10 - 06/16 | 2025-06-13 09:51 | -07:00 | 60 | FTS | 60 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 60
25-0064409 | Kern | POSO MOUNTAIN 2101 | POSO MOUNTAIN 2101CB | Unknown Cause | 2025-06-13 04:08 | -07:00 | 06/10 - 06/16 | 2025-06-13 09:54 | -07:00 | 202.4966 | FTS | 30172 | 149 | 4 | 4 | 4 | 0 | 0 | 0 | 346
25-0064490 | Lake | REDBUD 1102 | REDBUD 1102432 | Unknown Cause | 2025-06-13 08:41 | -07:00 | 06/10 - 06/16 | 2025-06-13 10:42 | -07:00 | 121 | FTS | 246961 | 2041 | 142 | 91 | 22 | 1 | 0 | 0 | 121
25-0064349 | San Joaquin | HERDLYN 1102 | HERDLYN 1102608254 | Unknown Cause | 2025-06-12 17:24 | -07:00 | 06/10 - 06/16 | 2025-06-13 10:47 | -07:00 | 244.5123 | FTS | 129347 | 529 | 38 | 21 | 20 | 3 | 0 | 0 | 1043
25-0064369 | Alameda | HERDLYN 1102 | HERDLYN 1102608254 | Unknown Cause | 2025-06-12 17:24 | -07:00 | 06/10 - 06/16 | 2025-06-13 10:47 | -07:00 | 250.0175 | FTS | 28502 | 114 | 3 | 2 | 8 | 0 | 0 | 0 | 1043
25-0064634 | El Dorado | SHINGLE SPRINGS 2109 | SHINGLE SPRINGS 210961892 | Unknown Cause | 2025-06-13 12:05 | -07:00 | 06/10 - 06/16 | 2025-06-13 14:33 | -07:00 | 90.5278 | FTS | 37388 | 413 | 43 | 34 | 2 | 0 | 0 | 12 | 148
25-0064636 | Santa Clara | LLAGAS 2106 | LLAGAS 2106338878 | Animal | 2025-06-13 12:23 | -07:00 | 06/10 - 06/16 | 2025-06-13 15:04 | -07:00 | 161 | FTS | 3542 | 22 | 4 | 3 | 0 | 0 | 0 | 0 | 161
25-0064704 | Tuolumne | BEAR VALLEY 2105 | BEAR VALLEY 210538882 | Company Initiated | 2025-06-13 11:45 | -07:00 | 06/10 - 06/16 | 2025-06-13 15:46 | -07:00 | 241 | FTS | 3374 | 14 | 2 | 2 | 0 | 0 | 0 | 0 | 241
25-0064656 | El Dorado | PLACERVILLE 2106 | PLACERVILLE 21062224 | Unknown Cause | 2025-06-13 13:06 | -07:00 | 06/10 - 06/16 | 2025-06-13 15:50 | -07:00 | 164 | FTS | 169084 | 1031 | 73 | 59 | 42 | 10 | 0 | 7 | 164
25-0064495 | Butte | ORO FINO 1102 | ORO FINO 11022090 | Vegetation | 2025-06-13 09:01 | -07:00 | 06/10 - 06/16 | 2025-06-13 16:58 | -07:00 | 160.9437 | FTS | 91416 | 568 | 65 | 44 | 4 | 0 | 0 | 1 | 477
25-0064738 | Santa Clara | LOS GATOS 1107 | LOS GATOS 110760092 | Unknown Cause | 2025-06-13 15:22 | -07:00 | 06/10 - 06/16 | 2025-06-13 18:48 | -07:00 | 206 | FTS | 4944 | 24 | 1 | 1 | 4 | 0 | 0 | 0 | 206
25-0064796 | Sonoma | DUNBAR 1103 | DUNBAR 1103596218 | Company Initiated | 2025-06-13 20:32 | -07:00 | 06/10 - 06/16 | 2025-06-13 22:11 | -07:00 | 99 | FTS | 396 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 99
25-0064811 | Yolo | MADISON 2101 | MADISON 2101168918 | Unknown Cause | 2025-06-14 03:35 | -07:00 | 06/10 - 06/16 | 2025-06-14 05:45 | -07:00 | 130 | FTS | 1690 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 130
25-0064807 | Sonoma | DUNBAR 1103 | DUNBAR 1103596218 | Company Initiated | 2025-06-14 01:13 | -07:00 | 06/10 - 06/16 | 2025-06-14 05:57 | -07:00 | 284 | FTS | 1136 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 284
25-0064805 | Butte | WYANDOTTE 1107 | WYANDOTTE 110777578 | Vegetation | 2025-06-14 00:19 | -07:00 | 06/10 - 06/16 | 2025-06-14 10:06 | -07:00 | 106.767 | FTS | 163140 | 1528 | 135 | 99 | 23 | 2 | 0 | 5 | 587
25-0064856 | Yuba | PIKE CITY 1101 | PIKE CITY 11011730 | 3rd Party | 2025-06-14 08:46 | -07:00 | 06/10 - 06/16 | 2025-06-14 10:59 | -07:00 | 133 | FTS | 18221 | 137 | 23 | 3 | 2 | 0 | 0 | 1 | 133
25-0064817 | El Dorado | PLACERVILLE 2106 | PLACERVILLE 210611132 | Unknown Cause | 2025-06-14 05:48 | -07:00 | 06/10 - 06/16 | 2025-06-14 13:03 | -07:00 | 62.0406 | FTS | 189596 | 3056 | 228 | 177 | 67 | 15 | 0 | 18 | 435
25-0064827 | Fresno | AUBERRY 1101 | AUBERRY 1101R2579 | Unknown Cause | 2025-06-14 07:15 | -07:00 | 06/10 - 06/16 | 2025-06-14 13:36 | -07:00 | 354.67 | FTS | 106401 | 300 | 13 | 9 | 5 | 0 | 0 | 1 | 381
25-0064828 | Marin | SAN RAFAEL 1108 | SAN RAFAEL 1108516 | Animal | 2025-06-14 07:20 | -07:00 | 06/10 - 06/16 | 2025-06-14 14:11 | -07:00 | 41.0168 | FTS | 63658 | 1552 | 53 | 37 | 17 | 1 | 0 | 0 | 411
25-0064899 | Sonoma | WINDSOR 1103 | WINDSOR 11035060 | Equipment Failure/Involved | 2025-06-14 12:52 | -07:00 | 06/10 - 06/16 | 2025-06-14 14:13 | -07:00 | 81 | FTS | 45360 | 560 | 24 | 16 | 10 | 1 | 0 | 2 | 81
25-0064910 | Santa Clara | SARATOGA 1106 | SARATOGA 1106408318 | 3rd Party | 2025-06-14 14:01 | -07:00 | 06/10 - 06/16 | 2025-06-14 15:06 | -07:00 | 64.2147 | FTS | 64600 | 1006 | 43 | 26 | 17 | 1 | 0 | 0 | 65
25-0064826 | Santa Cruz | LOS GATOS 1107 | LOS GATOS 1107781232 | Animal | 2025-06-14 07:18 | -07:00 | 06/10 - 06/16 | 2025-06-14 18:13 | -07:00 | 384.4537 | FTS | 78813 | 205 | 10 | 9 | 2 | 0 | 0 | 7 | 655
25-0064930 | Placer | BELL 1108 | BELL 1108467470 | Animal | 2025-06-14 18:38 | -07:00 | 06/10 - 06/16 | 2025-06-14 21:01 | -07:00 | 91.9747 | FTS | 152770 | 1661 | 110 | 87 | 17 | 0 | 0 | 31 | 143
25-0064932 | San Luis Obispo | SAN LUIS OBISPO 1104 | SAN LUIS OBISPO 1104V40 | Unknown Cause | 2025-06-14 19:19 | -07:00 | 06/10 - 06/16 | 2025-06-14 21:03 | -07:00 | 104 | FTS | 45552 | 438 | 11 | 11 | 11 | 0 | 0 | 8 | 104
25-0064952 | Calaveras | FROGTOWN 1702 | FROGTOWN 1702423550 | Equipment Failure/Involved | 2025-06-15 01:03 | -07:00 | 06/10 - 06/16 | 2025-06-15 07:54 | -07:00 | 276.1343 | FTS | 37002 | 134 | 6 | 5 | 3 | 0 | 0 | 1 | 411
25-0064970 | Kern | ARVIN 1101 | ARVIN 110194892 | Unknown Cause | 2025-06-15 06:40 | -07:00 | 06/10 - 06/16 | 2025-06-15 08:15 | -07:00 | 83.9307 | HLT | 30299 | 361 | 7 | 5 | 3 | 0 | 0 | 0 | 95
25-0064958 | Nevada | BRUNSWICK 1106 | BRUNSWICK 1106CB | Unknown Cause | 2025-06-15 05:49 | -07:00 | 06/10 - 06/16 | 2025-06-15 08:45 | -07:00 | 87.7249 | FTS | 347566 | 3962 | 303 | 213 | 37 | 4 | 0 | 48 | 176
25-0064962 | Placer | WEIMAR 1101, WEIMAR 1102 | N/A | Company Initiated | 2025-06-15 07:07 | -07:00 | 06/10 - 06/16 | 2025-06-15 10:15 | -07:00 | 164.0037 | T-EPSS | 351952 | 2146 | 146 | 104 | 42 | 28 | 0 | 15 | 188
25-0064965 | Placer | FORESTHILL 1102 | FORESTHILL 11022106 | Company Initiated | 2025-06-15 07:16 | -07:00 | 06/10 - 06/16 | 2025-06-15 10:16 | -07:00 | 179.0276 | T-EPSS | 486060 | 2715 | 222 | 158 | 36 | 6 | 0 | 4 | 180
25-0064673 | Kern | POSO MOUNTAIN 2101 | POSO MOUNTAIN 2101720132 | Animal | 2025-06-13 13:38 | -07:00 | 06/10 - 06/16 | 2025-06-15 10:30 | -07:00 | 1911.7545 | FTS | 319263 | 167 | 5 | 5 | 4 | 0 | 0 | 0 | 2692
25-0064981 | Tehama | RED BLUFF 1104 | RED BLUFF 110451238 | Unknown Cause | 2025-06-15 09:43 | -07:00 | 06/10 - 06/16 | 2025-06-15 11:40 | -07:00 | 117 | FTS | 11583 | 99 | 10 | 7 | 4 | 0 | 0 | 0 | 117
25-0064971 | Placer | SHADY GLEN 1101, SHADY GLEN 1102 | N/A | Company Initiated | 2025-06-15 07:07 | -07:00 | 06/10 - 06/16 | 2025-06-15 11:45 | -07:00 | 261.3547 | T-EPSS | 708010 | 2709 | 185 | 132 | 60 | 5 | 0 | 16 | 278
25-0064963 | Placer | BONNIE NOOK 1102 | BONNIE NOOK 1102542186 | Unknown Cause | 2025-06-15 07:07 | -07:00 | 06/10 - 06/16 | 2025-06-15 12:58 | -07:00 | 314.1759 | T-EPSS | 282130 | 898 | 56 | 40 | 24 | 2 | 0 | 2 | 351
25-0064987 | Mendocino | WILLITS 1103 | WILLITS 110391810 | Unknown Cause | 2025-06-15 10:56 | -07:00 | 06/10 - 06/16 | 2025-06-15 14:44 | -07:00 | 75.5617 | FTS | 65512 | 867 | 42 | 28 | 19 | 0 | 0 | 1 | 228
25-0064964 | Santa Cruz | CAMP EVERS 2105 | CAMP EVERS 2105370732 | Equipment Failure/Involved | 2025-06-15 07:17 | -07:00 | 06/10 - 06/16 | 2025-06-15 16:15 | -07:00 | 106.0233 | FTS | 45484 | 429 | 15 | 15 | 3 | 1 | 0 | 0 | 538
25-0065010 | Calaveras | CORRAL 1103 | CORRAL 110359770 | Animal | 2025-06-15 17:44 | -07:00 | 06/10 - 06/16 | 2025-06-15 19:39 | -07:00 | 115 | FTS | 27830 | 242 | 20 | 16 | 2 | 0 | 0 | 0 | 115
25-0065032 | Santa Barbara | BUELLTON 1101 | BUELLTON 1101Y06 | Animal | 2025-06-15 21:23 | -07:00 | 06/10 - 06/16 | 2025-06-15 22:53 | -07:00 | 46.0983 | FTS | 15950 | 346 | 8 | 7 | 9 | 0 | 0 | 0 | 90
25-0065028 | Mendocino | LAYTONVILLE 1101 | LAYTONVILLE 1101448108 | Unknown Cause | 2025-06-15 20:50 | -07:00 | 06/10 - 06/16 | 2025-06-15 23:20 | -07:00 | 150 | FTS | 7200 | 48 | 3 | 3 | 0 | 0 | 0 | 0 | 150
25-0065034 | Napa | PUEBLO 2104 | PUEBLO 2104741958 | Equipment Failure/Involved | 2025-06-15 22:48 | -07:00 | 06/10 - 06/16 | 2025-06-16 04:05 | -07:00 | 260.2769 | FTS | 236852 | 910 | 26 | 15 | 15 | 0 | 0 | 0 | 317
25-0065046 | Monterey | JOLON 1103 | JOLON 1103549180 | Unknown Cause | 2025-06-16 05:29 | -07:00 | 06/10 - 06/16 | 2025-06-16 07:17 | -07:00 | 108 | FTS | 972 | 9 | 0 | 0 | 6 | 0 | 0 | 0 | 108
25-0065057 | Mariposa | MARIPOSA 2102 | MARIPOSA 210237282 | Animal | 2025-06-16 06:59 | -07:00 | 06/10 - 06/16 | 2025-06-16 08:12 | -07:00 | 51.3257 | FTS | 109529 | 2134 | 101 | 70 | 34 | 6 | 0 | 7 | 73
25-0065056 | San Luis Obispo | PASO ROBLES 1108 | PASO ROBLES 1108P10 | 3rd Party | 2025-06-16 06:54 | -07:00 | 06/10 - 06/16 | 2025-06-16 08:32 | -07:00 | 98 | FTS | 9702 | 99 | 0 | 0 | 8 | 0 | 0 | 0 | 98
25-0065119 | Monterey | LOS OSITOS 2102 | LOS OSITOS 21027592 | Company Initiated | 2025-06-16 09:10 | -07:00 | 06/10 - 06/16 | 2025-06-16 09:18 | -07:00 | 8 | FTS | 736 | 92 | 1 | 1 | 5 | 0 | 0 | 0 | 8
25-0065066 | San Luis Obispo | TEMPLETON 2109 | TEMPLETON 2109R92 | Equipment Failure/Involved | 2025-06-16 07:39 | -07:00 | 06/10 - 06/16 | 2025-06-16 10:59 | -07:00 | 75.608 | FTS | 73869 | 977 | 35 | 24 | 6 | 0 | 0 | 2 | 200
25-0065016 | Monterey | LAURELES 1111 | LAURELES 1111432 | Unknown Cause | 2025-06-15 18:19 | -07:00 | 06/10 - 06/16 | 2025-06-16 13:57 | -07:00 | 870.4768 | FTS | 281164 | 323 | 9 | 9 | 7 | 0 | 0 | 0 | 1178
25-0065296 | Santa Cruz | CAMP EVERS 2106 | CAMP EVERS 210637210 | Company Initiated | 2025-06-16 13:59 | -07:00 | 06/10 - 06/16 | 2025-06-16 14:24 | -07:00 | 25 | FTS | 2100 | 84 | 9 | 7 | 1 | 0 | 0 | 1 | 25
25-0064998 | Tulare | DUNLAP 1102 | DUNLAP 11027050 | Equipment Failure/Involved | 2025-06-15 14:30 | -07:00 | 06/10 - 06/16 | 2025-06-16 16:36 | -07:00 | 904.8909 | FTS | 49769 | 55 | 0 | 0 | 5 | 0 | 0 | 0 | 1566
25-0065345 | San Luis Obispo | PASO ROBLES 1108 | PASO ROBLES 1108P10 | 3rd Party | 2025-06-16 15:59 | -07:00 | 06/10 - 06/16 | 2025-06-16 16:45 | -07:00 | 46 | FTS | 4554 | 99 | 0 | 0 | 8 | 0 | 0 | 0 | 46
25-0065331 | Fresno | AUBERRY 1102 | AUBERRY 1102R1013 | Unknown Cause | 2025-06-16 15:14 | -07:00 | 06/10 - 06/16 | 2025-06-16 18:26 | -07:00 | 192 | FTS | 33792 | 176 | 20 | 14 | 3 | 0 | 0 | 5 | 192
25-0065246 | Placer | PENRYN 1107 | PENRYN 11072708 | 3rd Party | 2025-06-16 12:51 | -07:00 | 06/10 - 06/16 | 2025-06-16 18:52 | -07:00 | 222.2519 | FTS | 85567 | 385 | 29 | 21 | 6 | 0 | 0 | 4 | 361
25-0065387 | Monterey | OILFIELDS 1103 | OILFIELDS 1103N48 | Company Initiated | 2025-06-16 17:50 | -07:00 | 06/10 - 06/16 | 2025-06-16 20:30 | -07:00 | 30.6812 | FTS | 36572 | 1192 | 33 | 20 | 24 | 1 | 0 | 13 | 160
25-0065036 | Alameda | VINEYARD 2107 | VINEYARD 2107CB | Equipment Failure/Involved | 2025-06-15 22:45 | -07:00 | 06/17 - 06/23 | 2025-06-17 04:26 | -07:00 | 579.4167 | FTS | 3380317 | 5834 | 249 | 177 | 67 | 4 | 0 | 0 | 1781
25-0065420 | Placer | LINCOLN 1104 | LINCOLN 11042070 | Unknown Cause | 2025-06-17 00:52 | -07:00 | 06/17 - 06/23 | 2025-06-17 05:57 | -07:00 | 242.3129 | FTS | 78994 | 326 | 19 | 16 | 2 | 0 | 0 | 9 | 305
25-0065468 | Tuolumne | PEORIA 1705 | PEORIA 170570198 | Company Initiated | 2025-06-17 07:31 | -07:00 | 06/17 - 06/23 | 2025-06-17 08:11 | -07:00 | 38.6069 | FTS | 11196 | 290 | 21 | 12 | 4 | 0 | 0 | 2 | 40
25-0065469 | Santa Cruz | PAUL SWEET 2105 | PAUL SWEET 2105CB | Company Initiated | 2025-06-17 07:34 | -07:00 | 06/17 - 06/23 | 2025-06-17 08:20 | -07:00 | 46 | HLT | 195454 | 4249 | 186 | 151 | 46 | 5 | 1 | 1 | 46
25-0065495 | Napa | TULUCAY 1101 | TULUCAY 1101504524 | Company Initiated | 2025-06-17 08:06 | -07:00 | 06/17 - 06/23 | 2025-06-17 08:42 | -07:00 | 36 | FTS | 432 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 36
25-0065439 | Mariposa | MARIPOSA 2102 | MARIPOSA 21021960 | Equipment Failure/Involved | 2025-06-17 06:16 | -07:00 | 06/17 - 06/23 | 2025-06-17 08:49 | -07:00 | 153 | FTS | 146880 | 960 | 41 | 28 | 18 | 5 | 0 | 2 | 153
25-0065422 | Monterey | LOS OSITOS 2101 | LOS OSITOS 21011132 | Unknown Cause | 2025-06-17 01:41 | -07:00 | 06/17 - 06/23 | 2025-06-17 11:16 | -07:00 | 575 | FTS | 59225 | 103 | 3 | 3 | 4 | 1 | 0 | 0 | 575
25-0065584 | Mariposa | MARIPOSA 2101 | MARIPOSA 2101310816 | Company Initiated | 2025-06-17 10:11 | -07:00 | 06/17 - 06/23 | 2025-06-17 12:47 | -07:00 | 156 | FTS | 31512 | 202 | 12 | 7 | 8 | 0 | 0 | 0 | 156
25-0065682 | Placer | BONNIE NOOK 1102 | BONNIE NOOK 1102542186 | Company Initiated | 2025-06-17 13:45 | -07:00 | 06/17 - 06/23 | 2025-06-17 14:14 | -07:00 | 29 | FTS | 2581 | 89 | 6 | 6 | 0 | 0 | 0 | 2 | 29
25-0065688 | Sonoma | GEYSERVILLE 1101 | GEYSERVILLE 110137454 | Company Initiated | 2025-06-17 14:17 | -07:00 | 06/17 - 06/23 | 2025-06-17 14:29 | -07:00 | 12 | FTS | 780 | 65 | 1 | 1 | 1 | 0 | 0 | 0 | 12
25-0065691 | Calaveras | WEST POINT 1102 | WEST POINT 1102CB | Company Initiated | 2025-06-17 14:29 | -07:00 | 06/17 - 06/23 | 2025-06-17 15:40 | -07:00 | 71 | FTS | 1278 | 18 | 5 | 3 | 0 | 0 | 0 | 0 | 71
25-0065459 | Napa | SILVERADO 2102 | SILVERADO 2102CB | 3rd Party | 2025-06-17 07:10 | -07:00 | 06/17 - 06/23 | 2025-06-17 18:34 | -07:00 | 168.758 | FTS | 221748 | 1314 | 11 | 7 | 25 | 0 | 0 | 6 | 684
25-0065812 | Santa Cruz | BURNS 2101 | BURNS 210136516 | 3rd Party | 2025-06-17 23:40 | -07:00 | 06/17 - 06/23 | 2025-06-18 02:07 | -07:00 | 141.4772 | FTS | 55742 | 394 | 27 | 20 | 9 | 0 | 0 | 11 | 147
25-0065736 | Tehama | COTTONWOOD 1101 | COTTONWOOD 11011610 | 3rd Party | 2025-06-17 15:46 | -07:00 | 06/17 - 06/23 | 2025-06-18 03:00 | -07:00 | 61.2373 | FTS | 28904 | 472 | 44 | 29 | 5 | 1 | 0 | 2 | 674
25-0065857 | Santa Barbara | CABRILLO 1104 | CABRILLO 1104838078 | Equipment Failure/Involved | 2025-06-18 07:38 | -07:00 | 06/17 - 06/23 | 2025-06-18 09:11 | -07:00 | 80.6265 | FTS | 20076 | 249 | 2 | 1 | 5 | 0 | 0 | 0 | 93
25-0065899 | Napa | CALISTOGA 1102 | CALISTOGA 1102306462 | Company Initiated | 2025-06-18 08:50 | -07:00 | 06/17 - 06/23 | 2025-06-18 09:12 | -07:00 | 14.6759 | FTS | 32155 | 2191 | 51 | 36 | 25 | 5 | 0 | 2 | 22
25-0065796 | Monterey | SOLEDAD 2102 | SOLEDAD 2102858388 | Unknown Cause | 2025-06-17 20:43 | -07:00 | 06/17 - 06/23 | 2025-06-18 09:35 | -07:00 | 187.4914 | FTS | 21749 | 116 | 1 | 1 | 0 | 1 | 0 | 0 | 772
25-0065963 | San Joaquin | LAMMERS 1101 | LAMMERS 1101932641 | Unknown Cause | 2025-06-18 10:54 | -07:00 | 06/17 - 06/23 | 2025-06-18 12:41 | -07:00 | 94.3333 | FTS | 3679 | 39 | 0 | 0 | 4 | 0 | 0 | 0 | 107
25-0065973 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113175566 | Company Initiated | 2025-06-18 11:16 | -07:00 | 06/17 - 06/23 | 2025-06-18 13:20 | -07:00 | 124 | FTS | 183520 | 1480 | 66 | 51 | 24 | 0 | 1 | 24 | 124
25-0065931 | Tehama | CORNING 1102 | CORNING 11021900 | Equipment Failure/Involved | 2025-06-18 09:57 | -07:00 | 06/17 - 06/23 | 2025-06-18 13:59 | -07:00 | 189.6576 | FTS | 69794 | 368 | 18 | 13 | 10 | 3 | 0 | 1 | 242
25-0065951 | San Luis Obispo | TEMPLETON 2111 | TEMPLETON 2111514592 | Unknown Cause | 2025-06-18 10:24 | -07:00 | 06/17 - 06/23 | 2025-06-18 14:11 | -07:00 | 93.9319 | FTS | 246853 | 2628 | 148 | 91 | 37 | 8 | 0 | 16 | 227
25-0066096 | Plumas | HAMILTON BRANCH 1101 | HAMILTON BRANCH 11012046 | 3rd Party | 2025-06-18 14:01 | -07:00 | 06/17 - 06/23 | 2025-06-18 14:37 | -07:00 | 36 | FTS | 7380 | 205 | 11 | 8 | 6 | 0 | 0 | 0 | 36
25-0065980 | Santa Clara | EDENVALE 2105 | EDENVALE 2105469810 | 3rd Party | 2025-06-18 09:42 | -07:00 | 06/17 - 06/23 | 2025-06-18 14:40 | -07:00 | 297.0588 | FTS | 5050 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 298
25-0065944 | San Luis Obispo | OCEANO 1104 | OCEANO 1104V38 | Equipment Failure/Involved | 2025-06-18 10:22 | -07:00 | 06/17 - 06/23 | 2025-06-18 15:25 | -07:00 | 39.0671 | FTS | 58796 | 1505 | 60 | 50 | 15 | 3 | 0 | 32 | 303
25-0066073 | Tehama | COTTONWOOD 1103 | COTTONWOOD 11031348 | 3rd Party | 2025-06-18 13:30 | -07:00 | 06/17 - 06/23 | 2025-06-18 15:41 | -07:00 | 115.9213 | FTS | 110473 | 953 | 71 | 56 | 10 | 1 | 0 | 1 | 131
25-0066061 | Marin | WOODACRE 1101 | WOODACRE 110191900 | Unknown Cause | 2025-06-18 13:11 | -07:00 | 06/17 - 06/23 | 2025-06-18 16:48 | -07:00 | 203.1947 | FTS | 22961 | 113 | 2 | 1 | 3 | 2 | 0 | 2 | 217
25-0066043 | Napa | SILVERADO 2104 | SILVERADO 2104106272 | Unknown Cause | 2025-06-18 12:49 | -07:00 | 06/17 - 06/23 | 2025-06-18 17:39 | -07:00 | 290 | FTS | 51040 | 176 | 1 | 0 | 2 | 0 | 0 | 0 | 290
25-0066131 | Napa | SILVERADO 2104 | SILVERADO 210437632 | Unknown Cause | 2025-06-18 14:53 | -07:00 | 06/17 - 06/23 | 2025-06-18 19:38 | -07:00 | 207.9231 | FTS | 316251 | 1521 | 65 | 38 | 37 | 6 | 16 | 6 | 285
25-0066255 | Marin | SAN RAFAEL 1105 | SAN RAFAEL 1105194366 | Animal | 2025-06-18 19:29 | -07:00 | 06/17 - 06/23 | 2025-06-18 20:52 | -07:00 | 81.0164 | FTS | 157739 | 1947 | 74 | 40 | 35 | 5 | 0 | 1 | 83
25-0066247 | Tuolumne | CURTIS 1704 | CURTIS 1704895006 | Unknown Cause | 2025-06-18 18:51 | -07:00 | 06/17 - 06/23 | 2025-06-18 22:52 | -07:00 | 222.2461 | FTS | 99344 | 447 | 30 | 21 | 7 | 2 | 0 | 1 | 241
25-0066138 | Monterey | OTTER 1102 | OTTER 11022012 | Equipment Failure/Involved | 2025-06-18 15:06 | -07:00 | 06/17 - 06/23 | 2025-06-19 04:36 | -07:00 | 810 | FTS | 403380 | 498 | 4 | 3 | 19 | 2 | 1 | 0 | 810
25-0066310 | Santa Clara | MORGAN HILL 2104 | MORGAN HILL 2104152774 | Unknown Cause | 2025-06-19 06:03 | -07:00 | 06/17 - 06/23 | 2025-06-19 08:43 | -07:00 | 160 | FTS | 88480 | 553 | 38 | 26 | 12 | 0 | 0 | 0 | 160
25-0066331 | Mendocino | POTTER VALLEY P H 1105 | POTTER VALLEY P H 110595878 | Unknown Cause | 2025-06-19 07:46 | -07:00 | 06/17 - 06/23 | 2025-06-19 09:15 | -07:00 | 89 | FTS | 27234 | 306 | 10 | 6 | 3 | 0 | 0 | 0 | 89
25-0066317 | Yolo | MADISON 2101 | MADISON 21011606 | Unknown Cause | 2025-06-19 06:41 | -07:00 | 06/17 - 06/23 | 2025-06-19 09:24 | -07:00 | 92.2734 | FTS | 48259 | 523 | 10 | 3 | 6 | 0 | 0 | 2 | 163
25-0066358 | San Luis Obispo | TEMPLETON 2109 | TEMPLETON 2109R78 | Animal | 2025-06-19 09:00 | -07:00 | 06/17 - 06/23 | 2025-06-19 09:58 | -07:00 | 46.7311 | FTS | 80284 | 1718 | 83 | 54 | 17 | 0 | 0 | 0 | 58
25-0066367 | El Dorado | SHINGLE SPRINGS 2110 | SHINGLE SPRINGS 2110634118 | Animal | 2025-06-19 08:23 | -07:00 | 06/17 - 06/23 | 2025-06-19 10:06 | -07:00 | 103 | FTS | 74572 | 724 | 64 | 49 | 4 | 0 | 0 | 12 | 103
25-0066323 | Tehama | CORNING 1102 | CORNING 11021900 | Equipment Failure/Involved | 2025-06-19 07:13 | -07:00 | 06/17 - 06/23 | 2025-06-19 11:21 | -07:00 | 241.3052 | FTS | 88559 | 367 | 18 | 13 | 10 | 3 | 0 | 1 | 248
25-0066340 | Sutter | LIVE OAK 1104 | LIVE OAK 1104309742 | Unknown Cause | 2025-06-19 08:02 | -07:00 | 06/17 - 06/23 | 2025-06-19 13:07 | -07:00 | 248.4614 | FTS | 151313 | 609 | 15 | 9 | 3 | 0 | 0 | 0 | 305
25-0066312 | San Joaquin | LOCKEFORD 2102 | LOCKEFORD 210212468 | Animal | 2025-06-19 06:23 | -07:00 | 06/17 - 06/23 | 2025-06-19 13:25 | -07:00 | 422 | FTS | 276832 | 656 | 26 | 17 | 24 | 0 | 0 | 0 | 422
25-0066433 | San Mateo | HALF MOON BAY 1103 | HALF MOON BAY 1103869420 | Equipment Failure/Involved | 2025-06-19 11:46 | -07:00 | 06/17 - 06/23 | 2025-06-19 13:36 | -07:00 | 110 | FTS | 5940 | 54 | 3 | 2 | 0 | 0 | 0 | 0 | 110
25-0066451 | Marin | OLEMA 1101 | OLEMA 11011318 | Vegetation | 2025-06-19 12:42 | -07:00 | 06/17 - 06/23 | 2025-06-19 14:15 | -07:00 | 75.1038 | FTS | 91176 | 1214 | 40 | 34 | 40 | 1 | 0 | 4 | 93
25-0066302 | Santa Barbara | ZACA 1102 | ZACA 1102Y48 | Equipment Failure/Involved | 2025-06-19 03:17 | -07:00 | 06/17 - 06/23 | 2025-06-19 15:29 | -07:00 | 211.5151 | FTS | 175346 | 829 | 27 | 16 | 15 | 15 | 0 | 5 | 732
25-0066475 | Shasta | COTTONWOOD 1102 | COTTONWOOD 1102544790 | Unknown Cause | 2025-06-19 13:18 | -07:00 | 06/17 - 06/23 | 2025-06-19 17:21 | -07:00 | 178.8901 | FTS | 177459 | 992 | 87 | 66 | 10 | 3 | 0 | 5 | 243
25-0066285 | Contra Costa | LONE TREE 2105 | LONE TREE 2105CB | Unknown Cause | 2025-06-18 22:59 | -07:00 | 06/17 - 06/23 | 2025-06-19 18:22 | -07:00 | 161.6751 | FTS | 426499 | 2638 | 152 | 113 | 43 | 5 | 1 | 0 | 1163
25-0066574 | Merced | WRIGHT 1110 | WRIGHT 1110CB | Unknown Cause | 2025-06-19 19:00 | -07:00 | 06/17 - 06/23 | 2025-06-19 20:21 | -07:00 | 81 | FTS | 58239 | 719 | 18 | 7 | 15 | 5 | 0 | 0 | 81
25-0066565 | San Luis Obispo | MESA 1101 | MESA 1101M86 | 3rd Party | 2025-06-19 17:32 | -07:00 | 06/17 - 06/23 | 2025-06-19 21:27 | -07:00 | 104.3824 | FTS | 79435 | 761 | 32 | 19 | 14 | 3 | 0 | 22 | 235
25-0066495 | Kings | KETTLEMAN HILLS 2104 | KETTLEMAN HILLS 2104CB | Environmental/External | 2025-06-19 14:09 | -07:00 | 06/17 - 06/23 | 2025-06-19 23:56 | -07:00 | 159.5333 | FTS | 9572 | 60 | 2 | 0 | 1 | 1 | 0 | 0 | 587
25-0066513 | Sonoma | SALMON CREEK 1101 | SALMON CREEK 1101196 | Equipment Failure/Involved | 2025-06-19 13:42 | -07:00 | 06/17 - 06/23 | 2025-06-20 01:27 | -07:00 | 267.9072 | FTS | 51974 | 194 | 8 | 6 | 11 | 0 | 0 | 2 | 705
25-0066479 | Yolo | MADISON 2101 | MADISON 2101CB | 3rd Party | 2025-06-19 13:34 | -07:00 | 06/17 - 06/23 | 2025-06-20 02:43 | -07:00 | 215.9047 | FTS | 473479 | 2193 | 82 | 59 | 48 | 26 | 0 | 5 | 789
25-0066575 | Contra Costa | BRENTWOOD 2105 | BRENTWOOD 2105502672 | Equipment Failure/Involved | 2025-06-19 19:11 | -07:00 | 06/17 - 06/23 | 2025-06-20 02:50 | -07:00 | 278.5443 | FTS | 22005 | 79 | 1 | 1 | 5 | 0 | 0 | 0 | 459
25-0066603 | Solano | BAHIA 1102 | BAHIA 1102946 | Animal | 2025-06-20 01:26 | -07:00 | 06/17 - 06/23 | 2025-06-20 04:22 | -07:00 | 175.339 | HLT | 41380 | 236 | 2 | 1 | 18 | 0 | 0 | 1 | 176
25-0066621 | Merced | GUSTINE 1102 | GUSTINE 1102562202 | Unknown Cause | 2025-06-20 07:25 | -07:00 | 06/17 - 06/23 | 2025-06-20 09:28 | -07:00 | 123 | FTS | 77859 | 633 | 19 | 14 | 12 | 0 | 0 | 0 | 123
25-0066713 | Napa | CALISTOGA 1102 | CALISTOGA 1102131531 | Company Initiated | 2025-06-20 09:34 | -07:00 | 06/17 - 06/23 | 2025-06-20 10:02 | -07:00 | 28 | FTS | 924 | 33 | 1 | 1 | 2 | 0 | 0 | 0 | 28
25-0066697 | Lake | REDBUD 1102 | REDBUD 1102432 | Equipment Failure/Involved | 2025-06-20 09:32 | -07:00 | 06/17 - 06/23 | 2025-06-20 10:16 | -07:00 | 44 | FTS | 89804 | 2041 | 142 | 91 | 22 | 1 | 0 | 0 | 44
25-0066605 | Placer | BELL 1107 | BELL 11072400 | Vegetation | 2025-06-20 05:03 | -07:00 | 06/17 - 06/23 | 2025-06-20 10:31 | -07:00 | 117.2519 | FTS | 61440 | 524 | 34 | 25 | 2 | 1 | 0 | 11 | 328
25-0066655 | Monterey | CAMPHORA 1101 | CAMPHORA 110122412 | Unknown Cause | 2025-06-20 08:34 | -07:00 | 06/17 - 06/23 | 2025-06-20 10:41 | -07:00 | 127 | FTS | 16002 | 126 | 0 | 0 | 0 | 0 | 0 | 0 | 127
25-0066754 | Sonoma | FULTON 1102 | FULTON 1102258281 | Company Initiated | 2025-06-20 10:42 | -07:00 | 06/17 - 06/23 | 2025-06-20 10:52 | -07:00 | 10 | FTS | 250 | 25 | 0 | 0 | 1 | 0 | 0 | 0 | 10
25-0066661 | Plumas | BIG MEADOWS 2101 | BIG MEADOWS 21012562 | Animal | 2025-06-20 08:50 | -07:00 | 06/17 - 06/23 | 2025-06-20 10:59 | -07:00 | 49.3721 | FTS | 10615 | 215 | 12 | 8 | 2 | 0 | 0 | 1 | 129
25-0066718 | Sonoma | SONOMA 1103 | SONOMA 11033052 | Unknown Cause | 2025-06-20 10:08 | -07:00 | 06/17 - 06/23 | 2025-06-20 11:47 | -07:00 | 81.9293 | FTS | 24333 | 297 | 9 | 4 | 1 | 0 | 0 | 6 | 99
25-0066768 | Sonoma | IGNACIO 1104 | IGNACIO 1104469764 | Unknown Cause | 2025-06-20 11:06 | -07:00 | 06/17 - 06/23 | 2025-06-20 13:15 | -07:00 | 77.9654 | FTS | 69779 | 895 | 28 | 20 | 35 | 0 | 0 | 0 | 129
25-0066869 | Mendocino | GUALALA 1112 | GUALALA 1112662 | Unknown Cause | 2025-06-20 13:08 | -07:00 | 06/17 - 06/23 | 2025-06-20 15:29 | -07:00 | 141 | FTS | 142128 | 1008 | 35 | 29 | 13 | 0 | 0 | 0 | 141
25-0066857 | Sonoma | FULTON 1102 | FULTON 11024994 | Company Initiated | 2025-06-20 12:57 | -07:00 | 06/17 - 06/23 | 2025-06-20 15:36 | -07:00 | 156.1162 | FTS | 81961 | 525 | 11 | 9 | 6 | 1 | 0 | 5 | 159
25-0066925 | Mariposa | BEAR VALLEY 2105 | BEAR VALLEY 21054629 | Company Initiated | 2025-06-20 14:26 | -07:00 | 06/17 - 06/23 | 2025-06-20 15:49 | -07:00 | 83 | FTS | 4731 | 57 | 6 | 5 | 2 | 0 | 0 | 2 | 83
25-0066963 | Butte | KANAKA 1101 | KANAKA 1101713674 | Unknown Cause | 2025-06-20 15:15 | -07:00 | 06/17 - 06/23 | 2025-06-20 16:21 | -07:00 | 66 | FTS | 594 | 9 | 0 | 0 | 5 | 0 | 0 | 0 | 66
25-0066953 | San Mateo | BERESFORD 0403 | BERESFORD 0403855954 | Vegetation | 2025-06-20 16:00 | -07:00 | 06/17 - 06/23 | 2025-06-20 17:07 | -07:00 | 67 | FTS | 22177 | 331 | 9 | 7 | 9 | 2 | 0 | 0 | 67
25-0066740 | Sonoma | SALMON CREEK 1101 | SALMON CREEK 1101196 | Equipment Failure/Involved | 2025-06-20 10:20 | -07:00 | 06/17 - 06/23 | 2025-06-20 18:00 | -07:00 | 423.1959 | FTS | 82100 | 194 | 8 | 6 | 11 | 0 | 0 | 2 | 460
25-0066962 | San Luis Obispo | FOOTHILL 1102 | FOOTHILL 110299432 | Company Initiated | 2025-06-20 16:18 | -07:00 | 06/17 - 06/23 | 2025-06-20 18:07 | -07:00 | 109 | FTS | 184646 | 1694 | 36 | 27 | 14 | 3 | 0 | 0 | 109
25-0066919 | Santa Barbara | CABRILLO 1104 | CABRILLO 1104838078 | Equipment Failure/Involved | 2025-06-20 14:44 | -07:00 | 06/17 - 06/23 | 2025-06-20 18:18 | -07:00 | 78.9076 | FTS | 19648 | 249 | 2 | 1 | 5 | 0 | 0 | 0 | 214
25-0066977 | Sonoma | RINCON 1104 | RINCON 1104CB | Equipment Failure/Involved | 2025-06-20 17:06 | -07:00 | 06/17 - 06/23 | 2025-06-20 19:01 | -07:00 | 99.9961 | FTS | 332987 | 3330 | 178 | 129 | 23 | 2 | 0 | 0 | 115
25-0066996 | Marin | NOVATO 1104 | NOVATO 110438242 | Unknown Cause | 2025-06-20 18:12 | -07:00 | 06/17 - 06/23 | 2025-06-20 19:20 | -07:00 | 40.1448 | FTS | 100884 | 2513 | 98 | 69 | 59 | 4 | 1 | 0 | 68
25-0067001 | Santa Cruz | CAMP EVERS 2107 | CAMP EVERS 2107543858 | Vegetation | 2025-06-20 18:32 | -07:00 | 06/17 - 06/23 | 2025-06-20 19:50 | -07:00 | 56.2785 | FTS | 8892 | 158 | 10 | 9 | 2 | 0 | 0 | 0 | 78
25-0066972 | Marin | OLEMA 1101 | OLEMA 1101359772 | Vegetation | 2025-06-20 16:51 | -07:00 | 06/17 - 06/23 | 2025-06-20 20:24 | -07:00 | 213 | FTS | 38553 | 181 | 5 | 4 | 7 | 0 | 0 | 1 | 213
25-0067015 | Butte | CLARK ROAD 1102 | CLARK ROAD 1102212118 | Unknown Cause | 2025-06-20 20:06 | -07:00 | 06/17 - 06/23 | 2025-06-20 21:10 | -07:00 | 64 | FTS | 4288 | 67 | 7 | 6 | 4 | 1 | 0 | 0 | 64
25-0067036 | Marin | ALTO 1120 | ALTO 112088190 | Vegetation | 2025-06-20 22:34 | -07:00 | 06/17 - 06/23 | 2025-06-20 23:26 | -07:00 | 52 | FTS | 86008 | 1654 | 46 | 34 | 18 | 2 | 0 | 0 | 52
25-0066923 | Santa Cruz | CAMP EVERS 2105 | CAMP EVERS 210584166 | Vegetation | 2025-06-20 14:45 | -07:00 | 06/17 - 06/23 | 2025-06-21 00:02 | -07:00 | 113.1277 | FTS | 382598 | 3382 | 266 | 219 | 48 | 4 | 0 | 13 | 557
25-0067043 | San Mateo | HALF MOON BAY 1101 | HALF MOON BAY 11018940 | Vegetation | 2025-06-20 23:27 | -07:00 | 06/17 - 06/23 | 2025-06-21 01:04 | -07:00 | 50.4682 | FTS | 72220 | 1431 | 32 | 29 | 30 | 4 | 0 | 1 | 97
25-0067027 | Santa Clara | HICKS 2101 | HICKS 2101257172 | Unknown Cause | 2025-06-20 21:43 | -07:00 | 06/17 - 06/23 | 2025-06-21 03:02 | -07:00 | 319 | FTS | 167156 | 524 | 26 | 18 | 10 | 1 | 0 | 0 | 319
25-0066887 | Sonoma | GEYSERVILLE 1102 | GEYSERVILLE 1102429530 | Vegetation | 2025-06-20 13:37 | -07:00 | 06/17 - 06/23 | 2025-06-21 05:35 | -07:00 | 268.5945 | FTS | 127851 | 476 | 6 | 1 | 8 | 1 | 0 | 3 | 958
25-0067051 | Madera | STOREY 1109 | STOREY 1109272650 | Unknown Cause | 2025-06-21 03:16 | -07:00 | 06/17 - 06/23 | 2025-06-21 06:13 | -07:00 | 177 | FTS | 26550 | 150 | 8 | 5 | 6 | 0 | 0 | 0 | 177
25-0066984 | Marin | SAN RAFAEL 1105 | SAN RAFAEL 1105194366 | Company Initiated | 2025-06-20 17:28 | -07:00 | 06/17 - 06/23 | 2025-06-21 08:48 | -07:00 | 36.322 | FTS | 70719 | 1947 | 74 | 40 | 35 | 5 | 0 | 1 | 920
25-0067049 | Mendocino | POTTER VALLEY P H 1105 | POTTER VALLEY P H 110576498 | Unknown Cause | 2025-06-21 02:52 | -07:00 | 06/17 - 06/23 | 2025-06-21 09:17 | -07:00 | 385 | FTS | 51205 | 133 | 5 | 2 | 2 | 0 | 0 | 0 | 385
25-0067055 | El Dorado | DIAMOND SPRINGS 1106 | DIAMOND SPRINGS 1106803034 | Unknown Cause | 2025-06-21 06:35 | -07:00 | 06/17 - 06/23 | 2025-06-21 09:21 | -07:00 | 103.3955 | FTS | 123661 | 1196 | 103 | 73 | 12 | 0 | 0 | 31 | 166
25-0067079 | San Luis Obispo | OCEANO 1104 | OCEANO 1104V36 | Animal | 2025-06-21 08:44 | -07:00 | 06/17 - 06/23 | 2025-06-21 10:27 | -07:00 | 71.7362 | FTS | 107963 | 1505 | 60 | 50 | 15 | 3 | 0 | 32 | 103
25-0067071 | San Luis Obispo | FOOTHILL 1101 | FOOTHILL 1101CB | Unknown Cause | 2025-06-21 08:23 | -07:00 | 06/17 - 06/23 | 2025-06-21 10:40 | -07:00 | 137 | FTS | 51923 | 379 | 12 | 9 | 6 | 1 | 0 | 1 | 137
25-0067105 | Sonoma | FITCH MOUNTAIN 1113 | FITCH MOUNTAIN 11134566 | Vegetation | 2025-06-20 18:37 | -07:00 | 06/17 - 06/23 | 2025-06-21 10:47 | -07:00 | 71.2392 | FTS | 21443 | 301 | 7 | 4 | 1 | 0 | 0 | 3 | 970
25-0066961 | San Luis Obispo | FOOTHILL 1101 | FOOTHILL 1101CB | Equipment Failure/Involved | 2025-06-20 16:18 | -07:00 | 06/17 - 06/23 | 2025-06-21 10:58 | -07:00 | 188.6178 | FTS | 72052 | 382 | 12 | 9 | 6 | 1 | 0 | 1 | 1120
25-0067006 | Tulare | DUNLAP 1102 | DUNLAP 11027050 | Equipment Failure/Involved | 2025-06-20 19:02 | -07:00 | 06/17 - 06/23 | 2025-06-21 11:27 | -07:00 | 800.614 | FTS | 45635 | 57 | 0 | 0 | 5 | 0 | 0 | 0 | 985
25-0066934 | Santa Cruz | BIG BASIN 1102 | BIG BASIN 1102CB | Unknown Cause | 2025-06-20 15:14 | -07:00 | 06/17 - 06/23 | 2025-06-21 11:40 | -07:00 | 338.8057 | FTS | 571904 | 1688 | 102 | 78 | 26 | 1 | 0 | 5 | 1226
25-0067123 | Tulare | DUNLAP 1102 | DUNLAP 11027050 | Company Initiated | 2025-06-21 11:34 | -07:00 | 06/17 - 06/23 | 2025-06-21 11:40 | -07:00 | 6 | FTS | 342 | 57 | 0 | 0 | 5 | 0 | 0 | 0 | 6
25-0067057 | Placer | SHADY GLEN 1101 | SHADY GLEN 110151696 | 3rd Party | 2025-06-21 06:48 | -07:00 | 06/17 - 06/23 | 2025-06-21 12:30 | -07:00 | 59.9394 | FTS | 59340 | 990 | 57 | 43 | 12 | 1 | 0 | 4 | 342
25-0067093 | Placer | PENRYN 1107 | PENRYN 1107378926 | 3rd Party | 2025-06-21 09:15 | -07:00 | 06/17 - 06/23 | 2025-06-21 12:43 | -07:00 | 46.8198 | FTS | 46258 | 988 | 58 | 37 | 12 | 0 | 0 | 10 | 208
25-0067125 | Tehama | CORNING 1101 | CORNING 11011440 | Unknown Cause | 2025-06-21 11:37 | -07:00 | 06/17 - 06/23 | 2025-06-21 13:45 | -07:00 | 85.2598 | HLT | 39049 | 458 | 17 | 12 | 4 | 0 | 0 | 0 | 128
25-0067155 | Contra Costa | BRENTWOOD 2105 | BRENTWOOD 210519062 | Animal | 2025-06-21 13:41 | -07:00 | 06/17 - 06/23 | 2025-06-21 16:11 | -07:00 | 124.1887 | FTS | 72402 | 583 | 24 | 16 | 25 | 4 | 0 | 0 | 150
25-0067045 | Monterey | OTTER 1102 | OTTER 11022166 | Vegetation | 2025-06-21 01:21 | -07:00 | 06/17 - 06/23 | 2025-06-21 16:27 | -07:00 | 127.6751 | FTS | 60518 | 474 | 4 | 3 | 14 | 2 | 1 | 0 | 906
25-0067047 | Nevada | GRASS VALLEY 1103 | GRASS VALLEY 11032180 | Equipment Failure/Involved | 2025-06-21 01:50 | -07:00 | 06/17 - 06/23 | 2025-06-21 16:29 | -07:00 | 406.9027 | FTS | 213217 | 524 | 41 | 27 | 14 | 4 | 0 | 12 | 879
25-0067178 | Calaveras | FROGTOWN 1701 | FROGTOWN 170113412 | Animal | 2025-06-21 16:01 | -07:00 | 06/17 - 06/23 | 2025-06-21 17:20 | -07:00 | 30.1879 | FTS | 55908 | 1852 | 108 | 79 | 26 | 4 | 0 | 3 | 79
25-0067184 | San Mateo | HALF MOON BAY 1101 | HALF MOON BAY 11011741 | Company Initiated | 2025-06-21 16:37 | -07:00 | 06/17 - 06/23 | 2025-06-21 17:34 | -07:00 | 57 | FTS | 285 | 5 | 0 | 0 | 1 | 1 | 0 | 0 | 57
25-0067149 | Sonoma | MOLINO 1104 | MOLINO 1104368158 | Equipment Failure/Involved | 2025-06-21 13:23 | -07:00 | 06/17 - 06/23 | 2025-06-21 19:12 | -07:00 | 188.485 | FTS | 43917 | 233 | 10 | 6 | 4 | 0 | 0 | 3 | 349
25-0067188 | Butte | NOTRE DAME 1104 | NOTRE DAME 1104CB | Equipment Failure/Involved | 2025-06-21 16:47 | -07:00 | 06/17 - 06/23 | 2025-06-21 19:35 | -07:00 | 49.7453 | FTS | 177541 | 3569 | 221 | 156 | 36 | 2 | 0 | 5 | 168
25-0067168 | Solano | CORDELIA 1104 | CORDELIA 110448536 | Unknown Cause | 2025-06-21 14:21 | -07:00 | 06/17 - 06/23 | 2025-06-21 19:41 | -07:00 | 320 | HLT | 21440 | 67 | 0 | 0 | 2 | 0 | 0 | 0 | 320
25-0067195 | Madera | COARSEGOLD 2104 | COARSEGOLD 210490356 | Unknown Cause | 2025-06-21 17:32 | -07:00 | 06/17 - 06/23 | 2025-06-21 19:57 | -07:00 | 108.9655 | FTS | 22120 | 203 | 14 | 12 | 8 | 6 | 0 | 0 | 145
25-0067208 | Kings | AVENAL 2101 | AVENAL 210144778 | 3rd Party | 2025-06-21 18:28 | -07:00 | 06/17 - 06/23 | 2025-06-21 22:46 | -07:00 | 78.4773 | HLT | 86482 | 1102 | 34 | 26 | 12 | 5 | 0 | 0 | 258
25-0067204 | Monterey | CAMPHORA 1101 | CAMPHORA 110177978 | Unknown Cause | 2025-06-21 18:50 | -07:00 | 06/17 - 06/23 | 2025-06-21 22:47 | -07:00 | 237 | FTS | 58776 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 237
25-0067215 | Santa Barbara | CUYAMA 2101 | CUYAMA 2101952122 | Unknown Cause | 2025-06-21 20:55 | -07:00 | 06/17 - 06/23 | 2025-06-21 23:24 | -07:00 | 97.7027 | FTS | 7230 | 74 | 4 | 2 | 1 | 0 | 0 | 0 | 149
25-0067223 | Nevada | BRUNSWICK 1104 | BRUNSWICK 11041020 | Vegetation | 2025-06-21 23:22 | -07:00 | 06/17 - 06/23 | 2025-06-22 01:27 | -07:00 | 125 | FTS | 61000 | 488 | 22 | 15 | 4 | 0 | 0 | 16 | 125
25-0067228 | Kern | COPUS 1102 | COPUS 11022399 | Animal | 2025-06-22 01:34 | -07:00 | 06/17 - 06/23 | 2025-06-22 06:18 | -07:00 | 284 | HLT | 9372 | 33 | 0 | 0 | 1 | 0 | 0 | 0 | 284
25-0067235 | Madera | STOREY 1109 | STOREY 1109272650 | Unknown Cause | 2025-06-22 04:09 | -07:00 | 06/17 - 06/23 | 2025-06-22 07:25 | -07:00 | 196 | FTS | 29400 | 150 | 8 | 5 | 6 | 0 | 0 | 0 | 196
25-0067236 | Madera | STOREY 1109 | STOREY 11095200 | Company Initiated | 2025-06-22 04:09 | -07:00 | 06/17 - 06/23 | 2025-06-22 07:57 | -07:00 | 228 | HLT | 228 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 228
25-0067191 | Butte | ORO FINO 1102 | ORO FINO 11022236 | Vegetation | 2025-06-21 17:10 | -07:00 | 06/17 - 06/23 | 2025-06-22 08:16 | -07:00 | 575.5841 | FTS | 622782 | 1082 | 84 | 53 | 12 | 1 | 0 | 3 | 906
25-0067242 | San Luis Obispo | TEMPLETON 2108 | TEMPLETON 2108A64 | Animal | 2025-06-22 06:53 | -07:00 | 06/17 - 06/23 | 2025-06-22 08:37 | -07:00 | 56.9595 | FTS | 166094 | 2916 | 84 | 60 | 45 | 18 | 1 | 0 | 104
25-0067247 | Solano | VACAVILLE 1103 | VACAVILLE 1103CB | Unknown Cause | 2025-06-22 07:22 | -07:00 | 06/17 - 06/23 | 2025-06-22 09:09 | -07:00 | 107 | FTS | 252627 | 2361 | 128 | 90 | 32 | 11 | 0 | 0 | 107
25-0067257 | El Dorado | APPLE HILL 1104 | APPLE HILL 110412832 | Animal | 2025-06-22 08:08 | -07:00 | 06/17 - 06/23 | 2025-06-22 09:17 | -07:00 | 69 | FTS | 53820 | 780 | 58 | 41 | 7 | 0 | 0 | 16 | 69
25-0067255 | Kern | TEJON 1106 | TEJON 1106382086 | Unknown Cause | 2025-06-22 07:58 | -07:00 | 06/17 - 06/23 | 2025-06-22 09:28 | -07:00 | 88.1538 | HLT | 1146 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 90
25-0067250 | Fresno | WAHTOKE 1108 | WAHTOKE 11087570 | Unknown Cause | 2025-06-22 07:42 | -07:00 | 06/17 - 06/23 | 2025-06-22 10:27 | -07:00 | 144.0933 | HLT | 32421 | 225 | 8 | 5 | 2 | 0 | 0 | 0 | 165
25-0067206 | Fresno | TIVY VALLEY 1106 | TIVY VALLEY 11067150 | Vegetation | 2025-06-21 19:01 | -07:00 | 06/17 - 06/23 | 2025-06-22 10:49 | -07:00 | 306.2637 | FTS | 55740 | 182 | 3 | 3 | 4 | 0 | 0 | 0 | 948
25-0067251 | San Luis Obispo | MORRO BAY 1102 | MORRO BAY 1102V84 | Unknown Cause | 2025-06-22 07:43 | -07:00 | 06/17 - 06/23 | 2025-06-22 11:16 | -07:00 | 47.8519 | FTS | 116280 | 2430 | 76 | 60 | 17 | 4 | 0 | 1 | 213
25-0067279 | San Benito | HOLLISTER 2105 | HOLLISTER 21054048 | Unknown Cause | 2025-06-22 09:57 | -07:00 | 06/17 - 06/23 | 2025-06-22 11:30 | -07:00 | 72.504 | FTS | 9063 | 125 | 2 | 2 | 2 | 2 | 0 | 0 | 93
25-0067286 | San Luis Obispo | OCEANO 1104 | OCEANO 1104V38 | Animal | 2025-06-22 10:39 | -07:00 | 06/17 - 06/23 | 2025-06-22 12:26 | -07:00 | 84.9774 | FTS | 127891 | 1505 | 60 | 50 | 15 | 3 | 0 | 32 | 107
25-0067245 | Placer | HALSEY 1101 | HALSEY 1101173478 | Equipment Failure/Involved | 2025-06-22 07:04 | -07:00 | 06/17 - 06/23 | 2025-06-22 14:40 | -07:00 | 167.5287 | FTS | 55452 | 331 | 32 | 24 | 2 | 0 | 0 | 2 | 456
25-0067233 | Kern | TAFT 1103 | TAFT 11033068 | 3rd Party | 2025-06-22 02:49 | -07:00 | 06/17 - 06/23 | 2025-06-22 16:48 | -07:00 | 312.7647 | HLT | 10634 | 34 | 0 | 0 | 7 | 1 | 0 | 0 | 839
25-0067308 | Mariposa | MARIPOSA 2101 | MARIPOSA 2101310816 | Company Initiated | 2025-06-22 14:38 | -07:00 | 06/17 - 06/23 | 2025-06-22 16:57 | -07:00 | 139 | FTS | 22379 | 161 | 8 | 5 | 8 | 0 | 0 | 0 | 139
25-0067315 | Santa Clara | LOS GATOS 1108 | LOS GATOS 1108590544 | Animal | 2025-06-22 16:34 | -07:00 | 06/17 - 06/23 | 2025-06-22 17:43 | -07:00 | 69 | FTS | 53751 | 779 | 20 | 14 | 4 | 2 | 0 | 0 | 69
25-0067319 | Santa Barbara | CUYAMA 2101 | CUYAMA 2101952122 | Animal | 2025-06-22 17:04 | -07:00 | 06/17 - 06/23 | 2025-06-22 18:29 | -07:00 | 85 | FTS | 6290 | 74 | 8 | 6 | 2 | 0 | 0 | 0 | 85
25-0067318 | Tehama | VOLTA 1101 | VOLTA 1101914816 | 3rd Party | 2025-06-22 17:00 | -07:00 | 06/17 - 06/23 | 2025-06-22 19:02 | -07:00 | 122 | FTS | 26230 | 215 | 10 | 9 | 7 | 0 | 0 | 0 | 122
25-0067226 | Solano | JAMESON 1102 | JAMESON 1102CB | Equipment Failure/Involved | 2025-06-22 00:34 | -07:00 | 06/17 - 06/23 | 2025-06-22 19:15 | -07:00 | 451.2836 | FTS | 1034342 | 2292 | 156 | 112 | 33 | 1 | 0 | 4 | 1121
25-0067303 | San Luis Obispo | OCEANO 1104 | OCEANO 1104Q08 | Vegetation | 2025-06-22 14:00 | -07:00 | 06/17 - 06/23 | 2025-06-22 19:28 | -07:00 | 54.4745 | FTS | 20319 | 373 | 11 | 10 | 0 | 1 | 0 | 25 | 328
25-0067339 | Sonoma | COTATI 1105 | COTATI 1105844060 | Unknown Cause | 2025-06-22 19:10 | -07:00 | 06/17 - 06/23 | 2025-06-22 20:04 | -07:00 | 54 | FTS | 702 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 54
25-0067344 | San Luis Obispo | TEMPLETON 2111 | TEMPLETON 2111461692 | Vegetation | 2025-06-22 20:35 | -07:00 | 06/17 - 06/23 | 2025-06-22 23:24 | -07:00 | 73.0731 | FTS | 96018 | 1314 | 70 | 41 | 13 | 4 | 0 | 7 | 169
25-0067346 | Napa | CALISTOGA 1101 | CALISTOGA 1101959538 | Unknown Cause | 2025-06-22 20:42 | -07:00 | 06/17 - 06/23 | 2025-06-22 23:28 | -07:00 | 75.753 | FTS | 127871 | 1688 | 46 | 38 | 22 | 0 | 0 | 12 | 166
25-0067354 | San Luis Obispo | PERRY 1101 | PERRY 1101618168 | Unknown Cause | 2025-06-22 23:00 | -07:00 | 06/17 - 06/23 | 2025-06-23 01:20 | -07:00 | 140 | FTS | 21280 | 152 | 8 | 6 | 1 | 0 | 0 | 0 | 140
25-0067300 | Santa Cruz | ROB ROY 2104 | ROB ROY 210458988 | Equipment Failure/Involved | 2025-06-22 12:39 | -07:00 | 06/17 - 06/23 | 2025-06-23 01:52 | -07:00 | 74.3738 | FTS | 15916 | 214 | 22 | 21 | 3 | 0 | 0 | 2 | 793
25-0067353 | San Joaquin | LINDEN 1104 | LINDEN 11042456 | Equipment Failure/Involved | 2025-06-22 21:44 | -07:00 | 06/17 - 06/23 | 2025-06-23 03:51 | -07:00 | 116.6913 | HLT | 52161 | 447 | 16 | 6 | 2 | 0 | 0 | 0 | 367
25-0067355 | Amador | CLAY 1101 | CLAY 110113442 | Vegetation | 2025-06-22 23:13 | -07:00 | 06/17 - 06/23 | 2025-06-23 06:33 | -07:00 | 87.6077 | FTS | 68334 | 780 | 57 | 40 | 8 | 0 | 0 | 5 | 440
25-0067363 | Shasta | JESSUP 1101 | JESSUP 11019002 | Equipment Failure/Involved | 2025-06-23 05:30 | -07:00 | 06/17 - 06/23 | 2025-06-23 06:52 | -07:00 | 68.4941 | FTS | 121714 | 1777 | 170 | 132 | 19 | 3 | 0 | 1 | 82
25-0067362 | Yolo | MADISON 2101 | MADISON 21011606 | Animal | 2025-06-23 05:19 | -07:00 | 06/17 - 06/23 | 2025-06-23 07:09 | -07:00 | 103.7176 | FTS | 54348 | 524 | 10 | 3 | 6 | 0 | 0 | 2 | 110
25-0067377 | Marin | STAFFORD 1101 | STAFFORD 1101902998 | Unknown Cause | 2025-06-23 06:46 | -07:00 | 06/17 - 06/23 | 2025-06-23 07:29 | -07:00 | 43 | FTS | 39259 | 913 | 35 | 25 | 5 | 1 | 0 | 0 | 43
25-0067374 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113A24 | Unknown Cause | 2025-06-23 06:39 | -07:00 | 06/17 - 06/23 | 2025-06-23 07:47 | -07:00 | 49.4058 | FTS | 63190 | 1279 | 58 | 45 | 23 | 0 | 1 | 22 | 68
25-0067381 | El Dorado | SHINGLE SPRINGS 2110 | SHINGLE SPRINGS 211051790 | Animal | 2025-06-23 06:59 | -07:00 | 06/17 - 06/23 | 2025-06-23 08:02 | -07:00 | 63 | FTS | 12474 | 198 | 12 | 9 | 7 | 0 | 0 | 2 | 63
25-0067392 | Fresno | SANGER 1108 | SANGER 1108R544 | Equipment Failure/Involved | 2025-06-23 07:16 | -07:00 | 06/17 - 06/23 | 2025-06-23 08:06 | -07:00 | 50 | HLT | 41600 | 832 | 73 | 49 | 10 | 1 | 0 | 0 | 50
25-0067384 | Monterey | DOLAN ROAD 1101 | DOLAN ROAD 1101491190 | Vegetation | 2025-06-23 07:22 | -07:00 | 06/17 - 06/23 | 2025-06-23 08:14 | -07:00 | 52 | FTS | 42068 | 809 | 28 | 21 | 3 | 0 | 0 | 0 | 52
25-0067366 | San Mateo | EMERALD LAKE 0401 | EMERALD LAKE 0401843236 | Vegetation | 2025-06-23 05:49 | -07:00 | 06/17 - 06/23 | 2025-06-23 09:39 | -07:00 | 230 | FTS | 6210 | 27 | 0 | 0 | 6 | 0 | 0 | 0 | 230
25-0067387 | Contra Costa | TIDEWATER 2106 | TIDEWATER 210657926 | Unknown Cause | 2025-06-23 07:28 | -07:00 | 06/17 - 06/23 | 2025-06-23 10:19 | -07:00 | 67.2416 | FTS | 231042 | 3436 | 185 | 131 | 88 | 6 | 0 | 0 | 171
25-0067438 | Santa Clara | LOYOLA 1102 | LOYOLA 1102550291 | Animal | 2025-06-23 08:45 | -07:00 | 06/17 - 06/23 | 2025-06-23 10:31 | -07:00 | 104.9655 | FTS | 21308 | 203 | 5 | 4 | 4 | 0 | 0 | 0 | 106
25-0067407 | Santa Clara | MILPITAS 1109 | MILPITAS 1109903328 | Equipment Failure/Involved | 2025-06-23 08:13 | -07:00 | 06/17 - 06/23 | 2025-06-23 10:42 | -07:00 | 132.7086 | FTS | 43263 | 326 | 15 | 9 | 18 | 1 | 0 | 0 | 149
25-0067639 | Merced | LE GRAND 1112 | LE GRAND 111212020 | 3rd Party | 2025-06-23 11:45 | -07:00 | 06/17 - 06/23 | 2025-06-23 12:51 | -07:00 | 63.5742 | HLT | 26574 | 418 | 9 | 8 | 4 | 2 | 0 | 0 | 66
25-0067559 | Santa Cruz | LOS GATOS 1106 | LOS GATOS 1106848782 | Animal | 2025-06-23 10:22 | -07:00 | 06/17 - 06/23 | 2025-06-23 13:03 | -07:00 | 161 | FTS | 14973 | 93 | 3 | 1 | 1 | 0 | 0 | 1 | 161
25-0067645 | Alameda | CASTRO VALLEY 1110 | CASTRO VALLEY 1110MR243 | Equipment Failure/Involved | 2025-06-23 11:38 | -07:00 | 06/17 - 06/23 | 2025-06-23 13:18 | -07:00 | 100 | FTS | 39200 | 392 | 26 | 14 | 12 | 0 | 0 | 2 | 100
25-0067713 | Yuba | EAST MARYSVILLE 1108 | EAST MARYSVILLE 1108900690 | 3rd Party | 2025-06-23 13:57 | -07:00 | 06/17 - 06/23 | 2025-06-23 14:34 | -07:00 | 37 | FTS | 14356 | 388 | 18 | 12 | 3 | 0 | 0 | 1 | 37
25-0067698 | Monterey | DOLAN ROAD 1101 | DOLAN ROAD 1101491190 | Equipment Failure/Involved | 2025-06-23 13:39 | -07:00 | 06/17 - 06/23 | 2025-06-23 15:28 | -07:00 | 109 | FTS | 88181 | 809 | 28 | 21 | 3 | 0 | 0 | 0 | 109
25-0067486 | Santa Barbara | SISQUOC 1102 | SISQUOC 1102M26 | Equipment Failure/Involved | 2025-06-23 09:28 | -07:00 | 06/17 - 06/23 | 2025-06-23 15:59 | -07:00 | 199.3004 | FTS | 50423 | 253 | 3 | 2 | 2 | 0 | 0 | 0 | 391
25-0067806 | Napa | TULUCAY 1101 | TULUCAY 1101504524 | Unknown Cause | 2025-06-23 16:24 | -07:00 | 06/17 - 06/23 | 2025-06-23 17:10 | -07:00 | 46 | FTS | 552 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 46
25-0067770 | Santa Barbara | PALMER 1101 | PALMER 1101M88 | Unknown Cause | 2025-06-23 15:06 | -07:00 | 06/17 - 06/23 | 2025-06-23 17:14 | -07:00 | 70.4062 | FTS | 11265 | 160 | 0 | 0 | 5 | 0 | 0 | 0 | 128
25-0067812 | Fresno | SANGER 1108 | SANGER 110864662 | Unknown Cause | 2025-06-23 16:30 | -07:00 | 06/17 - 06/23 | 2025-06-23 17:49 | -07:00 | 79 | HLT | 30415 | 385 | 37 | 24 | 10 | 0 | 0 | 0 | 79
25-0067466 | Butte | WYANDOTTE 1107 | WYANDOTTE 1107CB | Animal | 2025-06-23 09:09 | -07:00 | 06/17 - 06/23 | 2025-06-23 18:42 | -07:00 | 137.2913 | FTS | 417640 | 3042 | 281 | 210 | 81 | 2 | 0 | 10 | 573
25-0067745 | Fresno | AUBERRY 1101 | AUBERRY 1101R314 | 3rd Party | 2025-06-23 14:36 | -07:00 | 06/17 - 06/23 | 2025-06-23 20:22 | -07:00 | 78.6794 | FTS | 104801 | 1332 | 101 | 70 | 17 | 4 | 0 | 14 | 346
25-0067873 | Alameda | CASTRO VALLEY 1110 | CASTRO VALLEY 1110MR243 | Equipment Failure/Involved | 2025-06-23 19:04 | -07:00 | 06/17 - 06/23 | 2025-06-23 20:32 | -07:00 | 88 | FTS | 34496 | 392 | 26 | 14 | 12 | 0 | 0 | 2 | 88
25-0067907 | Tuolumne | CURTIS 1705 | CURTIS 1705CB | Animal | 2025-06-24 00:27 | -07:00 | 06/24 - 06/30 | 2025-06-24 02:31 | -07:00 | 90.6296 | FTS | 256935 | 2835 | 206 | 157 | 43 | 20 | 0 | 2 | 124
25-0067909 | Santa Clara | MORGAN HILL 2111 | MORGAN HILL 2111997000 | Unknown Cause | 2025-06-24 01:25 | -07:00 | 06/24 - 06/30 | 2025-06-24 04:03 | -07:00 | 134.4851 | FTS | 54332 | 404 | 19 | 8 | 4 | 0 | 0 | 0 | 158
25-0067919 | Contra Costa | CLAYTON 2215 | CLAYTON 2215W531R | Animal | 2025-06-24 03:27 | -07:00 | 06/24 - 06/30 | 2025-06-24 05:08 | -07:00 | 39.8886 | FTS | 28281 | 709 | 50 | 38 | 11 | 0 | 0 | 0 | 101
25-0067913 | Merced | GUSTINE 1102 | GUSTINE 1102562202 | Animal | 2025-06-24 02:05 | -07:00 | 06/24 - 06/30 | 2025-06-24 07:48 | -07:00 | 151.2918 | FTS | 99550 | 658 | 19 | 14 | 12 | 0 | 0 | 0 | 343
25-0067901 | Marin | BOLINAS 1101 | BOLINAS 1101528 | Equipment Failure/Involved | 2025-06-23 22:55 | -07:00 | 06/24 - 06/30 | 2025-06-24 08:06 | -07:00 | 549 | FTS | 427671 | 779 | 10 | 7 | 6 | 0 | 0 | 0 | 551
25-0067940 | Placer | BELL 1107 | BELL 110750172 | Animal | 2025-06-24 07:00 | -07:00 | 06/24 - 06/30 | 2025-06-24 08:18 | -07:00 | 78 | FTS | 26832 | 344 | 24 | 18 | 4 | 0 | 0 | 6 | 78
25-0067926 | Glenn | ELK CREEK 1101 | ELK CREEK 11012004 | Unknown Cause | 2025-06-24 05:06 | -07:00 | 06/24 - 06/30 | 2025-06-24 09:00 | -07:00 | 234 | FTS | 40014 | 171 | 11 | 8 | 3 | 0 | 0 | 0 | 234
25-0067941 | Placer | WISE 1102 | WISE 1102697216 | Animal | 2025-06-24 07:03 | -07:00 | 06/24 - 06/30 | 2025-06-24 09:29 | -07:00 | 146 | FTS | 32412 | 222 | 12 | 9 | 0 | 0 | 0 | 8 | 146
25-0067979 | Merced | MERCED FALLS 1102 | MERCED FALLS 11024000 | Unknown Cause | 2025-06-24 08:26 | -07:00 | 06/24 - 06/30 | 2025-06-24 09:35 | -07:00 | 69 | FTS | 10005 | 145 | 3 | 2 | 1 | 0 | 0 | 0 | 69
25-0067898 | Fresno | DUNLAP 1103 | DUNLAP 11037080 | 3rd Party | 2025-06-23 22:32 | -07:00 | 06/24 - 06/30 | 2025-06-24 09:41 | -07:00 | 669 | FTS | 187320 | 280 | 12 | 12 | 2 | 0 | 0 | 0 | 669
25-0067928 | Napa | SILVERADO 2103 | SILVERADO 2103617828 | Unknown Cause | 2025-06-24 05:45 | -07:00 | 06/24 - 06/30 | 2025-06-24 10:27 | -07:00 | 282 | FTS | 9588 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 282
25-0068028 | San Mateo | CAROLANDS 0404 | CAROLANDS 04049024 | Company Initiated | 2025-06-24 09:20 | -07:00 | 06/24 - 06/30 | 2025-06-24 11:09 | -07:00 | 109 | FTS | 40657 | 373 | 22 | 14 | 4 | 0 | 0 | 0 | 109
25-0067925 | Contra Costa | CLAYTON 2212 | CLAYTON 2212CB | Equipment Failure/Involved | 2025-06-24 04:34 | -07:00 | 06/24 - 06/30 | 2025-06-24 11:19 | -07:00 | 89.3982 | FTS | 303060 | 3390 | 240 | 173 | 77 | 8 | 0 | 15 | 405
25-0067983 | Kern | CARNERAS 1103 | CARNERAS 1103430670 | Unknown Cause | 2025-06-24 08:30 | -07:00 | 06/24 - 06/30 | 2025-06-24 11:39 | -07:00 | 189 | FTS | 2646 | 14 | 0 | 0 | 1 | 0 | 0 | 0 | 189
25-0067915 | Sonoma | GEYSERVILLE 1102 | GEYSERVILLE 110289714 | Vegetation | 2025-06-24 01:40 | -07:00 | 06/24 - 06/30 | 2025-06-24 12:48 | -07:00 | 668 | FTS | 15364 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 668
25-0068153 | Contra Costa | MORAGA 1101 | MORAGA 1101121620 | Unknown Cause | 2025-06-24 11:33 | -07:00 | 06/24 - 06/30 | 2025-06-24 13:00 | -07:00 | 87 | FTS | 34017 | 391 | 19 | 17 | 5 | 0 | 0 | 1 | 87
25-0068086 | Placer | BONNIE NOOK 1102 | BONNIE NOOK 1102542186 | Company Initiated | 2025-06-24 10:25 | -07:00 | 06/24 - 06/30 | 2025-06-24 13:08 | -07:00 | 163 | FTS | 14996 | 92 | 6 | 6 | 1 | 0 | 0 | 2 | 163
25-0068194 | Santa Clara | LOS GATOS 1101 | LOS GATOS 1101865012 | Company Initiated | 2025-06-24 12:23 | -07:00 | 06/24 - 06/30 | 2025-06-24 13:15 | -07:00 | 52 | FTS | 4160 | 80 | 1 | 1 | 1 | 0 | 0 | 0 | 52
25-0068188 | Alameda | CASTRO VALLEY 1110 | CASTRO VALLEY 1110MR243 | Equipment Failure/Involved | 2025-06-24 12:33 | -07:00 | 06/24 - 06/30 | 2025-06-24 13:32 | -07:00 | 59 | FTS | 23128 | 392 | 26 | 14 | 12 | 0 | 0 | 2 | 59
25-0068284 | Alameda | CASTRO VALLEY 1110 | CASTRO VALLEY 1110MR243 | Equipment Failure/Involved | 2025-06-24 14:18 | -07:00 | 06/24 - 06/30 | 2025-06-24 14:50 | -07:00 | 32 | FTS | 12544 | 392 | 26 | 14 | 12 | 0 | 0 | 2 | 32
25-0068267 | Mariposa | MARIPOSA 2101 | MARIPOSA 2101310816 | Company Initiated | 2025-06-24 13:45 | -07:00 | 06/24 - 06/30 | 2025-06-24 15:32 | -07:00 | 107 | FTS | 20437 | 191 | 11 | 6 | 8 | 0 | 0 | 0 | 107
25-0068254 | Butte | BIG BEND 1102 | BIG BEND 1102CB | Unknown Cause | 2025-06-24 13:40 | -07:00 | 06/24 - 06/30 | 2025-06-24 15:36 | -07:00 | 116 | FTS | 38744 | 334 | 11 | 8 | 10 | 0 | 0 | 0 | 116
25-0068215 | San Luis Obispo | TEMPLETON 2110 | TEMPLETON 2110R94 | Equipment Failure/Involved | 2025-06-24 13:01 | -07:00 | 06/24 - 06/30 | 2025-06-24 16:06 | -07:00 | 185 | FTS | 34225 | 185 | 5 | 5 | 0 | 0 | 0 | 2 | 185
25-0068374 | Marin | SAN RAFAEL 1108 | SAN RAFAEL 1108516 | Vegetation | 2025-06-24 16:15 | -07:00 | 06/24 - 06/30 | 2025-06-24 17:34 | -07:00 | 32.9678 | FTS | 51166 | 1552 | 53 | 37 | 17 | 1 | 0 | 0 | 79
25-0068182 | San Mateo | CAROLANDS 0404 | CAROLANDS 04049024 | Company Initiated | 2025-06-24 12:22 | -07:00 | 06/24 - 06/30 | 2025-06-24 18:46 | -07:00 | 72.2976 | FTS | 26967 | 373 | 22 | 14 | 4 | 0 | 0 | 0 | 384
25-0068315 | Sonoma | PETALUMA C 1108 | PETALUMA C 1108618 | Equipment Failure/Involved | 2025-06-24 14:51 | -07:00 | 06/24 - 06/30 | 2025-06-24 21:06 | -07:00 | 101.7751 | FTS | 71955 | 707 | 31 | 25 | 10 | 4 | 0 | 3 | 375
25-0068033 | San Mateo | CAROLANDS 0404 | CAROLANDS 04049026 | Company Initiated | 2025-06-24 09:20 | -07:00 | 06/24 - 06/30 | 2025-06-24 21:16 | -07:00 | 332.4688 | FTS | 175876 | 529 | 17 | 10 | 10 | 0 | 0 | 0 | 716
25-0068375 | Butte | PARADISE 1105 | PARADISE 1105CB | Equipment Failure/Involved | 2025-06-24 16:45 | -07:00 | 06/24 - 06/30 | 2025-06-25 04:11 | -07:00 | 150.8989 | FTS | 323980 | 2147 | 168 | 123 | 41 | 1 | 0 | 0 | 686
25-0068462 | Placer | PENRYN 1103 | PENRYN 110351658 | Animal | 2025-06-25 03:08 | -07:00 | 06/24 - 06/30 | 2025-06-25 06:46 | -07:00 | 182.186 | FTS | 125344 | 688 | 46 | 34 | 9 | 0 | 0 | 20 | 218
25-0068463 | Nevada | GRASS VALLEY 1103 | GRASS VALLEY 11032180 | Animal | 2025-06-25 03:32 | -07:00 | 06/24 - 06/30 | 2025-06-25 07:37 | -07:00 | 245 | FTS | 128380 | 524 | 41 | 27 | 14 | 4 | 0 | 12 | 245
25-0068458 | San Mateo | SNEATH LANE 1106 | SNEATH LANE 1106CB | Unknown Cause | 2025-06-25 00:58 | -07:00 | 06/24 - 06/30 | 2025-06-25 07:43 | -07:00 | 105.1669 | FTS | 431605 | 4104 | 138 | 102 | 32 | 5 | 0 | 0 | 405
25-0068523 | Nevada | GRASS VALLEY 1101 | GRASS VALLEY 11012208 | 3rd Party | 2025-06-25 08:07 | -07:00 | 06/24 - 06/30 | 2025-06-25 09:09 | -07:00 | 62 | FTS | 25048 | 404 | 43 | 33 | 6 | 0 | 0 | 3 | 62
25-0068565 | Santa Cruz | PAUL SWEET 2106 | PAUL SWEET 2106607772 | Animal | 2025-06-25 08:56 | -07:00 | 06/24 - 06/30 | 2025-06-25 09:44 | -07:00 | 25.9107 | FTS | 135720 | 5238 | 257 | 214 | 62 | 14 | 2 | 15 | 48
25-0068464 | Sonoma | COTATI 1105 | COTATI 1105104502 | Vegetation | 2025-06-25 03:44 | -07:00 | 06/24 - 06/30 | 2025-06-25 10:55 | -07:00 | 100.5341 | FTS | 100333 | 998 | 55 | 39 | 11 | 1 | 0 | 9 | 431
25-0068540 | Santa Clara | MILPITAS 1109 | MILPITAS 1109903328 | Unknown Cause | 2025-06-25 08:30 | -07:00 | 06/24 - 06/30 | 2025-06-25 11:10 | -07:00 | 160 | FTS | 34080 | 213 | 10 | 7 | 1 | 0 | 0 | 0 | 160
25-0068595 | Napa | SILVERADO 2105 | SILVERADO 2105167360 | Unknown Cause | 2025-06-25 09:25 | -07:00 | 06/24 - 06/30 | 2025-06-25 12:15 | -07:00 | 170 | FTS | 16830 | 99 | 1 | 0 | 1 | 0 | 0 | 0 | 170
25-0068448 | Marin | BOLINAS 1101 | BOLINAS 1101504 | Equipment Failure/Involved | 2025-06-24 23:12 | -07:00 | 06/24 - 06/30 | 2025-06-25 12:36 | -07:00 | 326.4776 | FTS | 277506 | 850 | 13 | 7 | 11 | 1 | 0 | 0 | 804
25-0068690 | Napa | SILVERADO 2105 | SILVERADO 210234959 | Company Initiated | 2025-06-25 12:23 | -07:00 | 06/24 - 06/30 | 2025-06-25 12:42 | -07:00 | 19 | FTS | 190 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 19
25-0068607 | San Luis Obispo | ATASCADERO 1103 | ATASCADERO 1103440856 | Unknown Cause | 2025-06-25 09:59 | -07:00 | 06/24 - 06/30 | 2025-06-25 13:28 | -07:00 | 189.5543 | FTS | 120367 | 635 | 31 | 20 | 19 | 2 | 0 | 18 | 209
25-0061604 | Tuolumne | CURTIS 1704 | CURTIS 17048140 | Company Initiated | 2025-06-25 12:02 | -07:00 | 06/24 - 06/30 | 2025-06-25 16:56 | -07:00 | 294 | FTS | 8232 | 28 | 2 | 2 | 0 | 0 | 0 | 0 | 294
25-0068777 | Sonoma | GEYSERVILLE 1102 | GEYSERVILLE 1102429530 | Unknown Cause | 2025-06-25 14:33 | -07:00 | 06/24 - 06/30 | 2025-06-25 16:57 | -07:00 | 65.2887 | FTS | 31208 | 478 | 6 | 1 | 8 | 1 | 0 | 3 | 144
25-0068769 | Sonoma | BELLEVUE 2101 | BELLEVUE 2101270638 | Unknown Cause | 2025-06-25 14:12 | -07:00 | 06/24 - 06/30 | 2025-06-25 17:03 | -07:00 | 100.698 | FTS | 118018 | 1172 | 60 | 50 | 25 | 0 | 0 | 31 | 171
25-0068285 | Lake | HIGHLANDS 1102 | HIGHLANDS 1102623120 | Environmental/External | 2025-06-24 14:03 | -07:00 | 06/24 - 06/30 | 2025-06-25 17:20 | -07:00 | 138.1232 | FTS | 85222 | 617 | 48 | 31 | 11 | 0 | 0 | 6 | 1637
25-0068841 | Colusa | MAXWELL 1102 | MAXWELL 11023306 | Unknown Cause | 2025-06-25 16:18 | -07:00 | 06/24 - 06/30 | 2025-06-25 19:10 | -07:00 | 162.6918 | FTS | 25868 | 159 | 5 | 2 | 2 | 0 | 0 | 0 | 172
25-0068905 | Amador | CLAY 1101 | CLAY 1101CB | Animal | 2025-06-25 19:36 | -07:00 | 06/24 - 06/30 | 2025-06-25 20:15 | -07:00 | 27.5688 | FTS | 47253 | 1714 | 110 | 74 | 25 | 3 | 0 | 5 | 39
25-0068896 | Lake | UPPER LAKE 1101 | UPPER LAKE 1101861806 | Unknown Cause | 2025-06-25 18:35 | -07:00 | 06/24 - 06/30 | 2025-06-25 20:45 | -07:00 | 62.3285 | FTS | 25804 | 414 | 17 | 11 | 3 | 2 | 0 | 2 | 130
25-0068904 | Marin | COTATI 1103 | COTATI 1103310 | Unknown Cause | 2025-06-25 19:14 | -07:00 | 06/24 - 06/30 | 2025-06-25 20:49 | -07:00 | 57.3838 | FTS | 28405 | 495 | 17 | 14 | 17 | 0 | 0 | 0 | 95
25-0068847 | Napa | CALISTOGA 1102 | CALISTOGA 1102892348 | Equipment Failure/Involved | 2025-06-25 16:27 | -07:00 | 06/24 - 06/30 | 2025-06-26 00:30 | -07:00 | 162.0625 | FTS | 2593 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 483
25-0068733 | San Mateo | RALSTON 1102 | RALSTON 11022028 | Equipment Failure/Involved | 2025-06-25 13:17 | -07:00 | 06/24 - 06/30 | 2025-06-26 03:14 | -07:00 | 45.43 | FTS | 59377 | 1307 | 60 | 51 | 19 | 0 | 0 | 0 | 837
25-0068948 | Contra Costa | CLAYTON 2212 | CLAYTON 2212158138 | Unknown Cause | 2025-06-26 04:05 | -07:00 | 06/24 - 06/30 | 2025-06-26 05:33 | -07:00 | 88 | FTS | 1056 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 88
25-0068955 | Placer | PENRYN 1103 | PENRYN 1103604 | Animal | 2025-06-26 05:49 | -07:00 | 06/24 - 06/30 | 2025-06-26 07:05 | -07:00 | 76 | FTS | 25992 | 342 | 22 | 14 | 3 | 0 | 0 | 8 | 76
25-0068985 | Shasta | GIRVAN 1102 | GIRVAN 1102296428 | Unknown Cause | 2025-06-26 06:58 | -07:00 | 06/24 - 06/30 | 2025-06-26 09:29 | -07:00 | 117.3322 | FTS | 68522 | 584 | 45 | 30 | 7 | 0 | 0 | 0 | 151
25-0069000 | Santa Clara | MILPITAS 1108 | MILPITAS 1108342498 | Unknown Cause | 2025-06-26 07:45 | -07:00 | 06/24 - 06/30 | 2025-06-26 09:57 | -07:00 | 132 | FTS | 792 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 132
25-0069093 | Santa Barbara | SISQUOC 1102 | SISQUOC 1102M26 | 3rd Party | 2025-06-26 10:04 | -07:00 | 06/24 - 06/30 | 2025-06-26 11:17 | -07:00 | 73 | FTS | 18469 | 253 | 3 | 2 | 2 | 0 | 0 | 0 | 73
25-0069117 | Lake | LUCERNE 1103 | LUCERNE 110327932 | 3rd Party | 2025-06-26 10:42 | -07:00 | 06/24 - 06/30 | 2025-06-26 11:44 | -07:00 | 62 | FTS | 992 | 16 | 0 | 0 | 7 | 0 | 0 | 0 | 62
25-0068939 | Monterey | LAURELES 1111 | LAURELES 1111432 | Animal | 2025-06-26 00:22 | -07:00 | 06/24 - 06/30 | 2025-06-26 12:09 | -07:00 | 528.0774 | FTS | 170569 | 323 | 9 | 9 | 7 | 0 | 0 | 0 | 707
25-0069196 | El Dorado | DIAMOND SPRINGS 1105 | DIAMOND SPRINGS 11057722 | 3rd Party | 2025-06-26 11:07 | -07:00 | 06/24 - 06/30 | 2025-06-26 14:33 | -07:00 | 206 | FTS | 1442 | 7 | 1 | 1 | 0 | 0 | 0 | 0 | 206
25-0069137 | El Dorado | DIAMOND SPRINGS 1105 | DIAMOND SPRINGS 11057722 | 3rd Party | 2025-06-26 11:07 | -07:00 | 06/24 - 06/30 | 2025-06-26 17:08 | -07:00 | 197.1671 | FTS | 231277 | 1173 | 93 | 68 | 18 | 0 | 0 | 10 | 361
25-0069013 | Nevada | COLUMBIA HILL 1101 | COLUMBIA HILL 1101764 | Animal | 2025-06-26 07:33 | -07:00 | 06/24 - 06/30 | 2025-06-26 18:59 | -07:00 | 140.9468 | FTS | 37069 | 263 | 11 | 7 | 3 | 2 | 0 | 8 | 686
25-0069090 | Placer | LINCOLN 1104 | LINCOLN 1104693294 | Equipment Failure/Involved | 2025-06-26 10:06 | -07:00 | 06/24 - 06/30 | 2025-06-26 20:45 | -07:00 | 96.6392 | FTS | 30538 | 316 | 11 | 3 | 0 | 0 | 0 | 0 | 639
25-0069034 | Santa Cruz | BIG BASIN 1102 | BIG BASIN 110276752 | Equipment Failure/Involved | 2025-06-26 08:48 | -07:00 | 06/24 - 06/30 | 2025-06-27 01:10 | -07:00 | 75.1818 | FTS | 14059 | 187 | 17 | 14 | 3 | 0 | 0 | 0 | 982
25-0069470 | Placer | PENRYN 1105 | PENRYN 110550548 | Animal | 2025-06-27 05:44 | -07:00 | 06/24 - 06/30 | 2025-06-27 06:54 | -07:00 | 70 | FTS | 17080 | 244 | 16 | 12 | 0 | 0 | 0 | 3 | 70
25-0069521 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113CB | Unknown Cause | 2025-06-27 08:03 | -07:00 | 06/24 - 06/30 | 2025-06-27 09:55 | -07:00 | 112 | FTS | 60032 | 536 | 27 | 16 | 8 | 0 | 0 | 0 | 112
25-0069483 | San Luis Obispo | ATASCADERO 1103 | ATASCADERO 1103A18 | Unknown Cause | 2025-06-27 06:52 | -07:00 | 06/24 - 06/30 | 2025-06-27 14:27 | -07:00 | 385.0596 | FTS | 633423 | 1645 | 185 | 129 | 54 | 7 | 0 | 5 | 455
25-0069434 | Shasta | PIT NO 5 1101 | PIT NO 5 11011658 | Equipment Failure/Involved | 2025-06-26 20:28 | -07:00 | 06/24 - 06/30 | 2025-06-27 20:33 | -07:00 | 344.8125 | FTS | 38619 | 112 | 2 | 1 | 9 | 2 | 0 | 0 | 1445
25-0069767 | Tuolumne | CURTIS 1703 | CURTIS 17039240 | Vegetation | 2025-06-27 13:57 | -07:00 | 06/24 - 06/30 | 2025-06-27 23:06 | -07:00 | 63.7521 | FTS | 130373 | 2045 | 103 | 77 | 25 | 1 | 0 | 1 | 549
25-0069926 | El Dorado | MOUNTAIN QUARRIES 2101 | MOUNTAIN QUARRIES 2101117452 | Animal | 2025-06-27 23:42 | -07:00 | 06/24 - 06/30 | 2025-06-28 03:21 | -07:00 | 199.0687 | FTS | 52156 | 262 | 38 | 30 | 1 | 0 | 0 | 9 | 219
25-0069929 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113175566 | Company Initiated | 2025-06-28 03:29 | -07:00 | 06/24 - 06/30 | 2025-06-28 03:50 | -07:00 | 20.6968 | FTS | 30714 | 1484 | 66 | 51 | 24 | 0 | 1 | 24 | 21
25-0069905 | El Dorado | SHINGLE SPRINGS 2105 | SHINGLE SPRINGS 210551738 | Equipment Failure/Involved | 2025-06-27 19:16 | -07:00 | 06/24 - 06/30 | 2025-06-28 04:35 | -07:00 | 68.7723 | FTS | 152193 | 2213 | 148 | 113 | 22 | 0 | 0 | 9 | 559
25-0069906 | Sonoma | MIRABEL 1102 | MIRABEL 1102CB | Vegetation | 2025-06-27 19:21 | -07:00 | 06/24 - 06/30 | 2025-06-28 08:05 | -07:00 | 174.3278 | FTS | 423268 | 2428 | 107 | 79 | 49 | 4 | 0 | 1 | 764
25-0069933 | San Luis Obispo | PERRY 1101 | PERRY 1101925053 | Unknown Cause | 2025-06-28 05:56 | -07:00 | 06/24 - 06/30 | 2025-06-28 08:27 | -07:00 | 44.4909 | FTS | 143661 | 3229 | 107 | 81 | 35 | 3 | 0 | 0 | 151
25-0069932 | Glenn | GLENN 1101 | GLENN 110137496 | Unknown Cause | 2025-06-28 05:06 | -07:00 | 06/24 - 06/30 | 2025-06-28 08:30 | -07:00 | 202.6282 | FTS | 31610 | 156 | 2 | 0 | 12 | 0 | 0 | 0 | 204
25-0069938 | El Dorado | SHINGLE SPRINGS 1103 | SHINGLE SPRINGS 11038752 | Animal | 2025-06-28 07:26 | -07:00 | 06/24 - 06/30 | 2025-06-28 08:35 | -07:00 | 69 | FTS | 26496 | 384 | 20 | 16 | 2 | 0 | 0 | 0 | 69
25-0069969 | Santa Clara | LOS GATOS 1102 | LOS GATOS 1102526868 | Equipment Failure/Involved | 2025-06-28 10:18 | -07:00 | 06/24 - 06/30 | 2025-06-28 11:58 | -07:00 | 51.0169 | FTS | 30100 | 590 | 16 | 12 | 1 | 0 | 0 | 0 | 100
25-0070011 | Tuolumne | MIWUK 1702 | MIWUK 170238218 | Company Initiated | 2025-06-28 13:11 | -07:00 | 06/24 - 06/30 | 2025-06-28 13:44 | -07:00 | 33 | FTS | 4092 | 124 | 8 | 6 | 0 | 0 | 0 | 0 | 33
25-0070013 | Santa Barbara | SANTA YNEZ 1104 | SANTA YNEZ 1104Y04 | Company Initiated | 2025-06-28 13:33 | -07:00 | 06/24 - 06/30 | 2025-06-28 14:10 | -07:00 | 36.7143 | FTS | 23130 | 630 | 8 | 5 | 8 | 2 | 0 | 0 | 37
25-0069927 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113A70 | Animal | 2025-06-28 00:15 | -07:00 | 06/24 - 06/30 | 2025-06-28 14:42 | -07:00 | 137.2561 | FTS | 235806 | 1718 | 71 | 55 | 19 | 2 | 0 | 34 | 867
25-0070045 | El Dorado | SHINGLE SPRINGS 2110 | SHINGLE SPRINGS 2110CB | Company Initiated | 2025-06-28 20:59 | -07:00 | 06/24 - 06/30 | 2025-06-28 21:58 | -07:00 | 59 | FTS | 76759 | 1301 | 97 | 72 | 20 | 8 | 0 | 14 | 59
25-0070052 | Tuolumne | CURTIS 1704 | CURTIS 17048140 | Unknown Cause | 2025-06-28 21:18 | -07:00 | 06/24 - 06/30 | 2025-06-28 23:20 | -07:00 | 122 | FTS | 3416 | 28 | 1 | 1 | 0 | 0 | 0 | 0 | 122
25-0070058 | Plumas | CHESTER 1102 | CHESTER 1102385846 | Equipment Failure/Involved | 2025-06-29 00:16 | -07:00 | 06/24 - 06/30 | 2025-06-29 02:46 | -07:00 | 134.5147 | FTS | 9147 | 68 | 3 | 3 | 8 | 0 | 0 | 0 | 150
25-0070061 | Sonoma | GEYSERVILLE 1101 | GEYSERVILLE 1101166 | Vegetation | 2025-06-29 02:48 | -07:00 | 06/24 - 06/30 | 2025-06-29 04:39 | -07:00 | 111 | FTS | 71928 | 648 | 14 | 12 | 8 | 0 | 0 | 6 | 111
25-0070070 | Shasta | FRENCH GULCH 1102 | FRENCH GULCH 11021462 | Animal | 2025-06-29 05:15 | -07:00 | 06/24 - 06/30 | 2025-06-29 08:15 | -07:00 | 180 | FTS | 4860 | 27 | 1 | 1 | 5 | 0 | 0 | 0 | 180
25-0070068 | Alameda | JARVIS 1101 | JARVIS 1101467034 | Equipment Failure/Involved | 2025-06-29 05:50 | -07:00 | 06/24 - 06/30 | 2025-06-29 09:21 | -07:00 | 140.1513 | FTS | 570696 | 4072 | 160 | 115 | 35 | 6 | 0 | 0 | 211
25-0070075 | San Luis Obispo | PASO ROBLES 1108 | PASO ROBLES 1108P10 | Unknown Cause | 2025-06-29 07:36 | -07:00 | 06/24 - 06/30 | 2025-06-29 09:43 | -07:00 | 127 | FTS | 12573 | 99 | 0 | 0 | 8 | 0 | 0 | 0 | 127
25-0070085 | Sonoma | BELLEVUE 2101 | BELLEVUE 2101411782 | Unknown Cause | 2025-06-29 08:05 | -07:00 | 06/24 - 06/30 | 2025-06-29 09:45 | -07:00 | 78.3524 | FTS | 91829 | 1172 | 60 | 50 | 25 | 0 | 0 | 31 | 100
25-0070050 | Trinity | LOW GAP 1101 | LOW GAP 1101750090 | Vegetation | 2025-06-28 22:52 | -07:00 | 06/24 - 06/30 | 2025-06-29 10:26 | -07:00 | 693.2305 | FTS | 204503 | 295 | 12 | 7 | 6 | 3 | 0 | 0 | 694
25-0070080 | El Dorado | PLACERVILLE 2106 | PLACERVILLE 2106654798 | Animal | 2025-06-29 08:00 | -07:00 | 06/24 - 06/30 | 2025-06-29 11:52 | -07:00 | 232 | FTS | 54288 | 234 | 14 | 13 | 5 | 0 | 0 | 0 | 232
25-0070067 | Santa Clara | SWIFT 2110 | SWIFT 2110XR366 | Company Initiated | 2025-06-29 05:31 | -07:00 | 06/24 - 06/30 | 2025-06-29 12:00 | -07:00 | 307.8917 | FTS | 122233 | 397 | 16 | 10 | 20 | 0 | 0 | 2 | 389
25-0070112 | Nevada | BRUNSWICK 1105 | BRUNSWICK 11052204 | Vegetation | 2025-06-29 13:23 | -07:00 | 06/24 - 06/30 | 2025-06-29 14:12 | -07:00 | 27.6182 | FTS | 26403 | 956 | 53 | 38 | 14 | 0 | 0 | 24 | 49
25-0070137 | Contra Costa | CLAYTON 2212 | CLAYTON 221296224 | Animal | 2025-06-29 18:01 | -07:00 | 06/24 - 06/30 | 2025-06-29 18:59 | -07:00 | 58 | FTS | 14848 | 256 | 18 | 12 | 3 | 0 | 0 | 9 | 58
25-0070132 | Santa Clara | MORGAN HILL 2111 | MORGAN HILL 2111997000 | Vegetation | 2025-06-29 16:58 | -07:00 | 06/24 - 06/30 | 2025-06-29 20:02 | -07:00 | 164.198 | FTS | 66336 | 404 | 19 | 8 | 4 | 0 | 0 | 0 | 184
25-0070141 | Contra Costa | CLAYTON 2215 | CLAYTON 2215CB | Animal | 2025-06-29 18:09 | -07:00 | 06/24 - 06/30 | 2025-06-29 20:25 | -07:00 | 90.7824 | FTS | 408430 | 4499 | 314 | 240 | 65 | 6 | 0 | 0 | 136
25-0070144 | Nevada | NARROWS 2105 | NARROWS 21052426 | Unknown Cause | 2025-06-29 18:41 | -07:00 | 06/24 - 06/30 | 2025-06-29 21:14 | -07:00 | 99.445 | FTS | 257463 | 2589 | 188 | 116 | 23 | 4 | 0 | 40 | 153
25-0070076 | Yolo | PUTAH CREEK 1105 | PUTAH CREEK 11058812 | Vegetation | 2025-06-29 07:39 | -07:00 | 06/24 - 06/30 | 2025-06-30 02:21 | -07:00 | 93.3026 | FTS | 36388 | 390 | 4 | 1 | 6 | 2 | 0 | 1 | 1122
25-0070122 | Mendocino | WILLITS 1103 | WILLITS 1103966 | Equipment Failure/Involved | 2025-06-29 14:32 | -07:00 | 06/24 - 06/30 | 2025-06-30 07:30 | -07:00 | 89.5169 | FTS | 98200 | 1097 | 46 | 32 | 36 | 12 | 0 | 1 | 1018
25-0070300 | Placer | PENRYN 1105 | PENRYN 1105196418 | Company Initiated | 2025-06-30 09:46 | -07:00 | 06/24 - 06/30 | 2025-06-30 10:01 | -07:00 | 15 | FTS | 1065 | 71 | 6 | 3 | 1 | 0 | 0 | 4 | 15
25-0070185 | Placer | SHADY GLEN 1102 | SHADY GLEN 11022232 | Unknown Cause | 2025-06-30 02:27 | -07:00 | 06/24 - 06/30 | 2025-06-30 10:47 | -07:00 | 500 | FTS | 177500 | 355 | 27 | 18 | 15 | 0 | 0 | 4 | 500
25-0070333 | San Mateo | WOODSIDE 1104 | WOODSIDE 11049116 | Equipment Failure/Involved | 2025-06-30 09:48 | -07:00 | 06/24 - 06/30 | 2025-06-30 11:00 | -07:00 | 68.8584 | FTS | 79256 | 1151 | 36 | 31 | 23 | 5 | 0 | 0 | 72
25-0070299 | Sonoma | GEYSERVILLE 1102 | GEYSERVILLE 1102429530 | 3rd Party | 2025-06-30 09:40 | -07:00 | 06/24 - 06/30 | 2025-06-30 11:09 | -07:00 | 24.9498 | FTS | 11926 | 478 | 6 | 1 | 8 | 1 | 0 | 3 | 89
25-0070179 | Butte | ORO FINO 1102 | ORO FINO 11022090 | Vegetation | 2025-06-29 23:46 | -07:00 | 06/24 - 06/30 | 2025-06-30 11:22 | -07:00 | 176.3662 | FTS | 100176 | 568 | 65 | 44 | 4 | 0 | 0 | 1 | 696
25-0070349 | Mendocino | PHILO 1102 | PHILO 1102CB | Company Initiated | 2025-06-30 10:50 | -07:00 | 06/24 - 06/30 | 2025-06-30 12:13 | -07:00 | 17.4551 | FTS | 18485 | 1059 | 22 | 17 | 20 | 4 | 0 | 3 | 83
25-0070193 | Nevada | NARROWS 2105 | NARROWS 21052216 | Vegetation | 2025-06-30 05:10 | -07:00 | 06/24 - 06/30 | 2025-06-30 14:00 | -07:00 | 78.8709 | FTS | 81868 | 1038 | 68 | 43 | 8 | 0 | 0 | 29 | 530
25-0070433 | Shasta | COTTONWOOD 1102 | COTTONWOOD 11021578 | Animal | 2025-06-30 13:23 | -07:00 | 06/24 - 06/30 | 2025-06-30 15:25 | -07:00 | 122 | FTS | 32086 | 263 | 28 | 22 | 2 | 0 | 0 | 1 | 122
25-0070521 | El Dorado | PLACERVILLE 2106 | PLACERVILLE 21067522 | Unknown Cause | 2025-06-30 15:37 | -07:00 | 06/24 - 06/30 | 2025-06-30 18:39 | -07:00 | 179.2905 | FTS | 187000 | 1043 | 81 | 64 | 18 | 5 | 0 | 3 | 182
25-0070379 | Calaveras | STANISLAUS 1702 | STANISLAUS 17021850 | Vegetation | 2025-06-30 11:28 | -07:00 | 06/24 - 06/30 | 2025-06-30 20:18 | -07:00 | 72.1354 | FTS | 175866 | 2438 | 80 | 63 | 27 | 3 | 2 | 0 | 530
25-0070601 | Lake | KONOCTI 1108 | KONOCTI 1108950 | Animal | 2025-06-30 20:13 | -07:00 | 06/24 - 06/30 | 2025-06-30 21:19 | -07:00 | 66 | FTS | 68442 | 1037 | 104 | 70 | 12 | 1 | 0 | 0 | 66
25-0070288 | Sonoma | RINCON 1103 | RINCON 1103198 | 3rd Party | 2025-06-30 09:23 | -07:00 | 06/24 - 06/30 | 2025-06-30 23:30 | -07:00 | 222.8025 | FTS | 88007 | 395 | 14 | 10 | 4 | 0 | 0 | 3 | 847
25-0070609 | Santa Cruz | BIG BASIN 1101 | BIG BASIN 110165444 | Vegetation | 2025-06-30 21:12 | -07:00 | 06/24 - 06/30 | 2025-06-30 23:46 | -07:00 | 41.2015 | FTS | 32714 | 794 | 61 | 46 | 4 | 0 | 0 | 0 | 154
25-0070615 | Napa | MONTICELLO 1101 | MONTICELLO 1101720 | Equipment Failure/Involved | 2025-07-01 00:05 | -07:00 | 07/01 - 07/07 | 2025-07-01 01:31 | -07:00 | 86 | FTS | 6364 | 74 | 6 | 4 | 0 | 0 | 0 | 0 | 86
25-0070568 | Tuolumne | PEORIA 1705 | PEORIA 170567898 | 3rd Party | 2025-06-30 17:32 | -07:00 | 07/01 - 07/07 | 2025-07-01 03:07 | -07:00 | 161.8098 | FTS | 248378 | 1535 | 141 | 109 | 15 | 0 | 0 | 2 | 575
25-0070591 | Placer | BELL 1107 | BELL 11072400 | Environmental/External | 2025-06-30 19:05 | -07:00 | 07/01 - 07/07 | 2025-07-01 04:04 | -07:00 | 394.7462 | FTS | 206847 | 524 | 34 | 25 | 2 | 1 | 0 | 10 | 539
25-0070719 | Mendocino | COVELO 1101 | COVELO 1101430286 | Environmental/External | 2025-07-01 08:47 | -07:00 | 07/01 - 07/07 | 2025-07-01 11:05 | -07:00 | 138 | FTS | 552 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 138
25-0070722 | Fresno | TIVY VALLEY 1107 | TIVY VALLEY 1107822606 | Unknown Cause | 2025-07-01 08:50 | -07:00 | 07/01 - 07/07 | 2025-07-01 11:44 | -07:00 | 174 | FTS | 51678 | 297 | 15 | 12 | 2 | 0 | 0 | 0 | 174
25-0070586 | Santa Clara | LOS GATOS 1106 | LOS GATOS 1106648186 | Vegetation | 2025-06-30 18:18 | -07:00 | 07/01 - 07/07 | 2025-07-01 13:06 | -07:00 | 112.767 | FTS | 242449 | 2150 | 156 | 124 | 54 | 8 | 0 | 25 | 1128
25-0070902 | Santa Clara | MORGAN HILL 2111 | MORGAN HILL 2111997000 | Unknown Cause | 2025-07-01 13:02 | -07:00 | 07/01 - 07/07 | 2025-07-01 14:41 | -07:00 | 83.6782 | FTS | 33806 | 404 | 19 | 8 | 4 | 0 | 0 | 0 | 99
25-0070923 | Santa Clara | LLAGAS 2101 | LLAGAS 2101XR586 | Equipment Failure/Involved | 2025-07-01 13:27 | -07:00 | 07/01 - 07/07 | 2025-07-01 16:23 | -07:00 | 176 | FTS | 10032 | 57 | 1 | 1 | 3 | 0 | 0 | 2 | 176
25-0070734 | Humboldt | GARBERVILLE 1101 | GARBERVILLE 11016014 | Environmental/External | 2025-07-01 09:00 | -07:00 | 07/01 - 07/07 | 2025-07-01 17:01 | -07:00 | 352.5461 | FTS | 49709 | 141 | 2 | 0 | 9 | 3 | 0 | 0 | 481
25-0071065 | Nevada | BRUNSWICK 1106 | BRUNSWICK 110651486 | Company Initiated | 2025-07-01 17:19 | -07:00 | 07/01 - 07/07 | 2025-07-01 17:42 | -07:00 | 23 | FTS | 1104 | 48 | 3 | 1 | 0 | 0 | 0 | 0 | 23
25-0071088 | Contra Costa | TASSAJARA 2112 | TASSAJARA 2112925966 | Animal | 2025-07-01 18:34 | -07:00 | 07/01 - 07/07 | 2025-07-01 21:31 | -07:00 | 177 | FTS | 83544 | 472 | 30 | 23 | 7 | 4 | 0 | 0 | 177
25-0071081 | Contra Costa | TASSAJARA 2108 | TASSAJARA 2108846900 | Company Initiated | 2025-07-01 18:32 | -07:00 | 07/01 - 07/07 | 2025-07-01 22:51 | -07:00 | 259 | FTS | 81067 | 313 | 13 | 8 | 2 | 0 | 0 | 1 | 259
25-0071058 | Shasta | PIT NO 1 1101 | PIT NO 1 11011552 | Environmental/External | 2025-07-01 16:46 | -07:00 | 07/01 - 07/07 | 2025-07-02 01:38 | -07:00 | 56.9087 | FTS | 13715 | 241 | 17 | 14 | 3 | 0 | 0 | 0 | 532
25-0070901 | Mendocino | WILLITS 1103 | WILLITS 1103409216 | 3rd Party | 2025-07-01 13:02 | -07:00 | 07/01 - 07/07 | 2025-07-02 01:57 | -07:00 | 510.5669 | FTS | 129684 | 254 | 13 | 7 | 7 | 0 | 0 | 1 | 775
25-0071009 | Butte | WYANDOTTE 1107 | WYANDOTTE 11071026 | 3rd Party | 2025-07-01 15:13 | -07:00 | 07/01 - 07/07 | 2025-07-02 02:53 | -07:00 | 80.7308 | FTS | 31485 | 390 | 20 | 16 | 3 | 0 | 0 | 3 | 700
25-0071135 | Sutter | LIVE OAK 1104 | LIVE OAK 11041300 | Unknown Cause | 2025-07-01 21:54 | -07:00 | 07/01 - 07/07 | 2025-07-02 07:51 | -07:00 | 255.3404 | FTS | 60005 | 235 | 3 | 1 | 2 | 0 | 0 | 0 | 597
25-0071172 | Monterey | LOS OSITOS 2103 | LOS OSITOS 21037062 | Unknown Cause | 2025-07-02 05:49 | -07:00 | 07/01 - 07/07 | 2025-07-02 08:36 | -07:00 | 167 | FTS | 8517 | 51 | 0 | 0 | 1 | 0 | 0 | 0 | 167
25-0071181 | Monterey | OILFIELDS 1103 | OILFIELDS 1103N48 | Unknown Cause | 2025-07-02 06:34 | -07:00 | 07/01 - 07/07 | 2025-07-02 08:57 | -07:00 | 44.1328 | FTS | 52518 | 1190 | 33 | 20 | 24 | 1 | 0 | 13 | 143
25-0071221 | Madera | SAN JOAQUIN #3 1103 | SAN JOAQUIN #3 1103403515 | Animal | 2025-07-02 07:40 | -07:00 | 07/01 - 07/07 | 2025-07-02 09:22 | -07:00 | 102 | FTS | 15300 | 150 | 10 | 6 | 3 | 0 | 0 | 0 | 102
25-0071141 | Santa Clara | EDENVALE 1102 | EDENVALE 1102319134 | 3rd Party | 2025-07-01 22:31 | -07:00 | 07/01 - 07/07 | 2025-07-02 09:36 | -07:00 | 106.0575 | FTS | 86755 | 818 | 36 | 25 | 15 | 4 | 0 | 0 | 665
25-0071002 | El Dorado | CLARKSVILLE 2109 | CLARKSVILLE 21096502 | Vegetation | 2025-07-01 14:58 | -07:00 | 07/01 - 07/07 | 2025-07-02 09:41 | -07:00 | 140.8707 | FTS | 239621 | 1701 | 96 | 66 | 35 | 3 | 0 | 1 | 1123
25-0071112 | Marin | SAN RAFAEL 1109 | SAN RAFAEL 1109418 | Equipment Failure/Involved | 2025-07-01 19:43 | -07:00 | 07/01 - 07/07 | 2025-07-02 09:49 | -07:00 | 238.7215 | FTS | 343759 | 1440 | 83 | 44 | 32 | 4 | 0 | 0 | 846
25-0071089 | Shasta | PIT NO 5 1101 | PIT NO 5 11011658 | Environmental/External | 2025-07-01 18:29 | -07:00 | 07/01 - 07/07 | 2025-07-02 11:16 | -07:00 | 254.5893 | FTS | 28514 | 112 | 2 | 1 | 9 | 2 | 0 | 0 | 1007
25-0071174 | Solano | JAMESON 1103 | JAMESON 1103118944 | Unknown Cause | 2025-07-02 06:13 | -07:00 | 07/01 - 07/07 | 2025-07-02 12:04 | -07:00 | 351 | FTS | 28431 | 81 | 4 | 4 | 5 | 0 | 0 | 2 | 351
25-0071344 | Butte | CLARK ROAD 1102 | CLARK ROAD 11022068 | Company Initiated | 2025-07-02 10:26 | -07:00 | 07/01 - 07/07 | 2025-07-02 12:53 | -07:00 | 132.0259 | FTS | 30630 | 232 | 18 | 10 | 2 | 1 | 0 | 2 | 147
25-0071607 | Solano | PEABODY 2105 | PEABODY 2105CB | Company Initiated | 2025-07-02 14:38 | -07:00 | 07/01 - 07/07 | 2025-07-02 15:53 | -07:00 | 75 | FTS | 406575 | 5421 | 299 | 234 | 36 | 0 | 0 | 0 | 75
25-0071629 | Monterey | LOS OSITOS 2103 | LOS OSITOS 2103258688 | Unknown Cause | 2025-07-02 16:53 | -07:00 | 07/01 - 07/07 | 2025-07-02 18:14 | -07:00 | 81 | FTS | 1053 | 13 | 15 | 8 | 9 | 0 | 0 | 0 | 81
25-0071563 | Amador | WEST POINT 1102 | WEST POINT 110113444 | Equipment Failure/Involved | 2025-07-02 15:26 | -07:00 | 07/01 - 07/07 | 2025-07-02 19:58 | -07:00 | 210.7959 | FTS | 143552 | 681 | 49 | 41 | 2 | 0 | 0 | 3 | 272
25-0071608 | Yolo | PUTAH CREEK 1105 | PUTAH CREEK 110546162 | Unknown Cause | 2025-07-02 16:17 | -07:00 | 07/01 - 07/07 | 2025-07-02 20:20 | -07:00 | 73.52 | FTS | 3676 | 50 | 3 | 1 | 0 | 0 | 0 | 3 | 243
25-0071092 | Shasta | CEDAR CREEK 1101 | CEDAR CREEK 11011664 | Environmental/External | 2025-07-01 18:27 | -07:00 | 07/01 - 07/07 | 2025-07-02 23:51 | -07:00 | 789.3216 | FTS | 380453 | 482 | 29 | 20 | 11 | 1 | 0 | 1 | 1764
25-0071248 | Humboldt | HOOPA 1101 | HOOPA 11013174 | Vegetation | 2025-07-02 08:35 | -07:00 | 07/01 - 07/07 | 2025-07-03 06:08 | -07:00 | 388.7695 | FTS | 259698 | 668 | 17 | 13 | 24 | 5 | 0 | 0 | 1293
25-0071655 | Fresno | TIVY VALLEY 1107 | TIVY VALLEY 1107869946 | Vegetation | 2025-07-02 18:01 | -07:00 | 07/01 - 07/07 | 2025-07-03 09:47 | -07:00 | 526.9486 | FTS | 307738 | 584 | 47 | 34 | 5 | 0 | 0 | 0 | 946
25-0071747 | Sonoma | MONTE RIO 1113 | MONTE RIO 1113CB | Unknown Cause | 2025-07-03 07:39 | -07:00 | 07/01 - 07/07 | 2025-07-03 09:49 | -07:00 | 127.3862 | FTS | 499736 | 3923 | 203 | 141 | 68 | 7 | 0 | 2 | 130
25-0071712 | Monterey | RESERVATION ROAD 1101 | RESERVATION ROAD 110123818 | Unknown Cause | 2025-07-03 01:45 | -07:00 | 07/01 - 07/07 | 2025-07-03 12:30 | -07:00 | 629 | FTS | 13209 | 21 | 0 | 0 | 5 | 0 | 0 | 0 | 645
25-0071140 | Shasta | ANTLER 1101 | ANTLER 11011378 | Vegetation | 2025-07-01 19:43 | -07:00 | 07/01 - 07/07 | 2025-07-03 13:51 | -07:00 | 1058.1295 | FTS | 408438 | 386 | 23 | 14 | 8 | 0 | 0 | 1 | 2528
25-0071708 | Sonoma | MOLINO 1104 | MOLINO 1102178 | Environmental/External | 2025-07-03 00:42 | -07:00 | 07/01 - 07/07 | 2025-07-03 14:11 | -07:00 | 463.4121 | FTS | 1099677 | 2373 | 143 | 110 | 30 | 1 | 1 | 61 | 809
25-0071986 | El Dorado | CLARKSVILLE 2109 | CLARKSVILLE 210951742 | Animal | 2025-07-03 12:50 | -07:00 | 07/01 - 07/07 | 2025-07-03 14:52 | -07:00 | 27.3621 | FTS | 34531 | 1262 | 65 | 46 | 29 | 3 | 0 | 0 | 122
25-0071996 | Butte | CLARK ROAD 1102 | CLARK ROAD 11022044 | 3rd Party | 2025-07-03 13:01 | -07:00 | 07/01 - 07/07 | 2025-07-03 16:12 | -07:00 | 191 | FTS | 7831 | 41 | 1 | 0 | 1 | 0 | 0 | 0 | 191
25-0071713 | Lake | HIGHLANDS 1102 | HIGHLANDS 110265650 | Equipment Failure/Involved | 2025-07-03 02:32 | -07:00 | 07/01 - 07/07 | 2025-07-03 16:17 | -07:00 | 86.7797 | FTS | 192217 | 2215 | 183 | 124 | 23 | 8 | 0 | 0 | 825
25-0072080 | Humboldt | HOOPA 1101 | HOOPA 110137202 | Vegetation | 2025-07-03 12:12 | -07:00 | 07/01 - 07/07 | 2025-07-03 16:24 | -07:00 | 252 | FTS | 29484 | 117 | 2 | 2 | 9 | 1 | 0 | 0 | 252
25-0072123 | Lake | HARTLEY 1101 | HARTLEY 1101738 | Unknown Cause | 2025-07-03 17:07 | -07:00 | 07/01 - 07/07 | 2025-07-03 18:17 | -07:00 | 70 | FTS | 66080 | 944 | 72 | 52 | 9 | 4 | 0 | 0 | 70
25-0072144 | Contra Costa | FAIRVIEW 2207 | FAIRVIEW 2207P302 | 3rd Party | 2025-07-03 20:03 | -07:00 | 07/01 - 07/07 | 2025-07-03 20:24 | -07:00 | 21 | FTS | 21 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 21
25-0072146 | Nevada | NARROWS 2105 | NARROWS 21052216 | Equipment Failure/Involved | 2025-07-03 20:45 | -07:00 | 07/01 - 07/07 | 2025-07-04 01:01 | -07:00 | 164.0885 | FTS | 170488 | 1039 | 68 | 43 | 8 | 0 | 0 | 29 | 256
25-0072149 | Santa Clara | LOS GATOS 1101 | LOS GATOS 1101LB40 | Unknown Cause | 2025-07-03 21:18 | -07:00 | 07/01 - 07/07 | 2025-07-04 02:10 | -07:00 | 292 | FTS | 194764 | 667 | 27 | 19 | 9 | 3 | 0 | 0 | 292
25-0072162 | Kern | MAGUNDEN 1108 | MAGUNDEN 1108468940 | Unknown Cause | 2025-07-04 02:05 | -07:00 | 07/01 - 07/07 | 2025-07-04 03:49 | -07:00 | 104 | FTS | 4160 | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 104
25-0072160 | Santa Barbara | PALMER 1101 | PALMER 1101M88 | Unknown Cause | 2025-07-04 01:14 | -07:00 | 07/01 - 07/07 | 2025-07-04 05:20 | -07:00 | 246 | FTS | 39360 | 160 | 0 | 0 | 5 | 0 | 0 | 0 | 246
25-0072163 | Madera | COARSEGOLD 2104 | COARSEGOLD 210490356 | Unknown Cause | 2025-07-04 02:50 | -07:00 | 07/01 - 07/07 | 2025-07-04 05:35 | -07:00 | 165 | FTS | 33495 | 203 | 14 | 12 | 8 | 6 | 0 | 0 | 165
25-0072124 | Fresno | TIVY VALLEY 1107 | TIVY VALLEY 1107822606 | Equipment Failure/Involved | 2025-07-03 17:07 | -07:00 | 07/01 - 07/07 | 2025-07-04 05:44 | -07:00 | 639.4982 | FTS | 531423 | 831 | 56 | 39 | 13 | 0 | 0 | 0 | 757
25-0072167 | El Dorado | PLACERVILLE 2106 | PLACERVILLE 21062224 | Vegetation | 2025-07-04 03:57 | -07:00 | 07/01 - 07/07 | 2025-07-04 06:55 | -07:00 | 111.4239 | FTS | 114878 | 1031 | 74 | 59 | 42 | 10 | 0 | 7 | 178
25-0072166 | Marin | STAFFORD 1102 | STAFFORD 1102361952 | Vegetation | 2025-07-04 03:54 | -07:00 | 07/01 - 07/07 | 2025-07-04 12:12 | -07:00 | 71.5806 | FTS | 8876 | 124 | 4 | 4 | 8 | 2 | 0 | 0 | 498
25-0072244 | Santa Barbara | ZACA 1102 | ZACA 1102Y48 | Unknown Cause | 2025-07-04 17:15 | -07:00 | 07/01 - 07/07 | 2025-07-04 18:44 | -07:00 | 39.041 | FTS | 32365 | 829 | 29 | 17 | 15 | 15 | 0 | 5 | 89
25-0072250 | Placer | PENRYN 1105 | PENRYN 11052406 | Animal | 2025-07-04 18:28 | -07:00 | 07/01 - 07/07 | 2025-07-04 19:12 | -07:00 | 31.6712 | FTS | 28124 | 888 | 55 | 39 | 9 | 1 | 0 | 13 | 44
25-0072248 | Napa | JAMESON 1103 | JAMESON 1103118944 | Unknown Cause | 2025-07-04 17:44 | -07:00 | 07/01 - 07/07 | 2025-07-04 20:04 | -07:00 | 140 | FTS | 11340 | 81 | 4 | 4 | 5 | 0 | 0 | 2 | 140
25-0072219 | Sonoma | PETALUMA C 1108 | PETALUMA C 1108600 | 3rd Party | 2025-07-04 13:17 | -07:00 | 07/01 - 07/07 | 2025-07-04 23:30 | -07:00 | 169.6058 | FTS | 146709 | 865 | 35 | 29 | 17 | 1 | 0 | 2 | 613
25-0072269 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113CB | Vegetation | 2025-07-05 04:21 | -07:00 | 07/01 - 07/07 | 2025-07-05 05:58 | -07:00 | 97 | FTS | 511190 | 5270 | 219 | 159 | 77 | 10 | 1 | 61 | 97
25-0072274 | Santa Clara | HICKS 1116 | HICKS 1116LB16 | Unknown Cause | 2025-07-05 07:17 | -07:00 | 07/01 - 07/07 | 2025-07-05 08:18 | -07:00 | 61 | FTS | 4270 | 70 | 3 | 3 | 0 | 0 | 0 | 0 | 61
25-0072267 | Placer | FORESTHILL 1101 | FORESTHILL 11011802 | Animal | 2025-07-05 04:04 | -07:00 | 07/01 - 07/07 | 2025-07-05 10:40 | -07:00 | 198.2373 | FTS | 330858 | 1669 | 157 | 110 | 12 | 2 | 0 | 0 | 396
25-0072292 | El Dorado | MOUNTAIN QUARRIES 2101 | MOUNTAIN QUARRIES 2101117452 | Unknown Cause | 2025-07-05 09:17 | -07:00 | 07/01 - 07/07 | 2025-07-05 10:49 | -07:00 | 41.7443 | FTS | 10937 | 262 | 38 | 30 | 1 | 0 | 0 | 9 | 92
25-0072314 | Placer | WISE 1102 | WISE 11022054 | Animal | 2025-07-05 12:14 | -07:00 | 07/01 - 07/07 | 2025-07-05 15:08 | -07:00 | 124.2262 | FTS | 27454 | 221 | 20 | 14 | 2 | 0 | 0 | 12 | 174
25-0072351 | Shasta | ANDERSON 1101 | ANDERSON 1101CB | Unknown Cause | 2025-07-06 01:28 | -07:00 | 07/01 - 07/07 | 2025-07-06 06:45 | -07:00 | 39.0453 | FTS | 69774 | 1787 | 163 | 125 | 32 | 12 | 0 | 0 | 317
25-0072363 | Placer | PENRYN 1105 | PENRYN 1105680290 | Animal | 2025-07-06 08:20 | -07:00 | 07/01 - 07/07 | 2025-07-06 09:45 | -07:00 | 85 | FTS | 33065 | 389 | 23 | 11 | 3 | 0 | 0 | 7 | 85
25-0072384 | Santa Barbara | CUYAMA 2101 | CUYAMA 21013542 | Animal | 2025-07-06 12:21 | -07:00 | 07/01 - 07/07 | 2025-07-06 14:23 | -07:00 | 122 | FTS | 15128 | 124 | 4 | 4 | 1 | 0 | 0 | 0 | 122
25-0072386 | Lake | LUCERNE 1103 | LUCERNE 1103630 | Animal | 2025-07-06 12:46 | -07:00 | 07/01 - 07/07 | 2025-07-06 14:42 | -07:00 | 54.0686 | FTS | 80400 | 1487 | 101 | 67 | 22 | 2 | 0 | 2 | 116
25-0072392 | Mariposa | MERCED FALLS 1102 | MERCED FALLS 110285002 | Equipment Failure/Involved | 2025-07-06 13:46 | -07:00 | 07/01 - 07/07 | 2025-07-06 19:07 | -07:00 | 86.4234 | FTS | 47965 | 555 | 38 | 24 | 15 | 2 | 0 | 0 | 321
25-0072420 | San Luis Obispo | TEMPLETON 2108 | TEMPLETON 2108A64 | Animal | 2025-07-06 18:04 | -07:00 | 07/01 - 07/07 | 2025-07-06 19:26 | -07:00 | 69.5529 | FTS | 203929 | 2932 | 86 | 61 | 45 | 18 | 1 | 0 | 82
25-0072427 | Lake | MIDDLETOWN 1102 | MIDDLETOWN 1102998 | 3rd Party | 2025-07-06 19:07 | -07:00 | 07/01 - 07/07 | 2025-07-07 03:07 | -07:00 | 97.0257 | FTS | 60350 | 622 | 44 | 35 | 11 | 1 | 0 | 2 | 480
25-0072443 | Mendocino | WILLITS 1103 | WILLITS 1103826 | Vegetation | 2025-07-07 01:01 | -07:00 | 07/01 - 07/07 | 2025-07-07 06:21 | -07:00 | 63.7463 | FTS | 55268 | 867 | 43 | 28 | 19 | 0 | 0 | 1 | 320
25-0072455 | El Dorado | APPLE HILL 1104 | APPLE HILL 110413512 | Animal | 2025-07-07 06:20 | -07:00 | 07/01 - 07/07 | 2025-07-07 07:46 | -07:00 | 86 | FTS | 80410 | 935 | 54 | 36 | 11 | 1 | 0 | 3 | 86
25-0072461 | Amador | PINE GROVE 1102 | PINE GROVE 11021222 | Unknown Cause | 2025-07-07 06:44 | -07:00 | 07/01 - 07/07 | 2025-07-07 08:25 | -07:00 | 83.8064 | FTS | 110373 | 1317 | 104 | 77 | 25 | 0 | 0 | 1 | 101
25-0072453 | El Dorado | SHINGLE SPRINGS 2109 | SHINGLE SPRINGS 210981390 | Unknown Cause | 2025-07-07 06:01 | -07:00 | 07/01 - 07/07 | 2025-07-07 09:57 | -07:00 | 236 | FTS | 80004 | 339 | 23 | 22 | 4 | 1 | 0 | 13 | 236
25-0072547 | Sonoma | MOLINO 1103 | MOLINO 1102384 | Animal | 2025-07-07 09:43 | -07:00 | 07/01 - 07/07 | 2025-07-07 10:36 | -07:00 | 50.7873 | HLT | 30320 | 597 | 28 | 22 | 9 | 0 | 0 | 3 | 53
25-0072656 | El Dorado | APPLE HILL 1104 | APPLE HILL 110413512 | Company Initiated | 2025-07-07 12:39 | -07:00 | 07/01 - 07/07 | 2025-07-07 13:12 | -07:00 | 33 | FTS | 6963 | 211 | 8 | 5 | 1 | 0 | 0 | 0 | 33
25-0072524 | Humboldt | GARBERVILLE 1102 | GARBERVILLE 11028652 | Unknown Cause | 2025-07-07 09:11 | -07:00 | 07/01 - 07/07 | 2025-07-07 13:50 | -07:00 | 279 | FTS | 70029 | 251 | 8 | 6 | 7 | 1 | 0 | 0 | 279
25-0072564 | Plumas | HAMILTON BRANCH 1101 | HAMILTON BRANCH 110190334 | Equipment Failure/Involved | 2025-07-07 10:02 | -07:00 | 07/01 - 07/07 | 2025-07-07 14:29 | -07:00 | 41.1262 | FTS | 4236 | 103 | 6 | 4 | 4 | 0 | 0 | 0 | 267
25-0072583 | Calaveras | FROGTOWN 1701 | FROGTOWN 1701914602 | Unknown Cause | 2025-07-07 10:40 | -07:00 | 07/01 - 07/07 | 2025-07-07 14:57 | -07:00 | 148.0078 | FTS | 94873 | 641 | 37 | 26 | 11 | 0 | 0 | 0 | 257
25-0072618 | Santa Barbara | SANTA YNEZ 1102 | SANTA YNEZ 1102320270 | Equipment Failure/Involved | 2025-07-07 11:45 | -07:00 | 07/01 - 07/07 | 2025-07-07 17:23 | -07:00 | 97.413 | FTS | 22405 | 230 | 2 | 2 | 8 | 0 | 0 | 0 | 338
25-0072445 | Santa Clara | MORGAN HILL 2111 | MORGAN HILL 2111XR398 | Equipment Failure/Involved | 2025-07-07 03:43 | -07:00 | 07/01 - 07/07 | 2025-07-07 17:40 | -07:00 | 251.425 | FTS | 100570 | 400 | 20 | 17 | 10 | 0 | 0 | 2 | 837
25-0072653 | San Luis Obispo | SANTA MARIA 1108 | SANTA MARIA 1108M80 | Unknown Cause | 2025-07-07 12:38 | -07:00 | 07/01 - 07/07 | 2025-07-07 17:40 | -07:00 | 302 | FTS | 117176 | 388 | 15 | 15 | 4 | 0 | 0 | 20 | 302
25-0072432 | Solano | VACAVILLE 1108 | VACAVILLE 1108341974 | Animal | 2025-07-06 19:59 | -07:00 | 07/01 - 07/07 | 2025-07-07 19:58 | -07:00 | 246.4073 | HLT | 222013 | 901 | 81 | 61 | 19 | 1 | 0 | 5 | 1439
25-0072821 | Kings | AVENAL 2101 | AVENAL 21019070 | Animal | 2025-07-07 19:27 | -07:00 | 07/01 - 07/07 | 2025-07-07 21:51 | -07:00 | 144 | FTS | 9936 | 69 | 0 | 0 | 8 | 0 | 0 | 0 | 144
25-0072844 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113A24 | Equipment Failure/Involved | 2025-07-08 01:39 | -07:00 | 07/08 - 07/14 | 2025-07-08 03:35 | -07:00 | 116 | FTS | 28420 | 245 | 9 | 3 | 4 | 0 | 1 | 0 | 116
25-0072855 | Napa | PUEBLO 2103 | PUEBLO 2103694 | Unknown Cause | 2025-07-08 05:29 | -07:00 | 07/08 - 07/14 | 2025-07-08 06:32 | -07:00 | 63 | FTS | 1638 | 26 | 2 | 1 | 0 | 0 | 0 | 1 | 63
25-0072851 | Monterey | LAURELES 1111 | LAURELES 1111CB | Animal | 2025-07-08 06:11 | -07:00 | 07/08 - 07/14 | 2025-07-08 08:09 | -07:00 | 114.2044 | FTS | 402799 | 3527 | 126 | 96 | 79 | 3 | 0 | 8 | 118
25-0072856 | El Dorado | EL DORADO PH 2102 | EL DORADO PH 2102927014 | Animal | 2025-07-08 06:27 | -07:00 | 07/08 - 07/14 | 2025-07-08 08:52 | -07:00 | 145 | FTS | 44660 | 308 | 22 | 16 | 3 | 0 | 0 | 0 | 145
25-0072794 | Kern | POSO MOUNTAIN 2101 | POSO MOUNTAIN 21012181 | 3rd Party | 2025-07-07 17:04 | -07:00 | 07/08 - 07/14 | 2025-07-08 11:17 | -07:00 | 1092.6471 | FTS | 55725 | 51 | 0 | 0 | 1 | 0 | 0 | 0 | 1093
25-0072988 | Santa Clara | EDENVALE 2105 | EDENVALE 2105469810 | 3rd Party | 2025-07-08 10:20 | -07:00 | 07/08 - 07/14 | 2025-07-08 13:45 | -07:00 | 205 | FTS | 3485 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 205
25-0072925 | Madera | COARSEGOLD 2104 | COARSEGOLD 2104905960 | Unknown Cause | 2025-07-08 09:02 | -07:00 | 07/08 - 07/14 | 2025-07-08 14:20 | -07:00 | 207.2029 | FTS | 547430 | 2642 | 221 | 163 | 56 | 8 | 0 | 4 | 318
25-0073081 | Contra Costa | ROSSMOOR 1106 | ROSSMOOR 1106L552R | Animal | 2025-07-08 13:57 | -07:00 | 07/08 - 07/14 | 2025-07-08 15:38 | -07:00 | 53.6873 | FTS | 104046 | 1938 | 62 | 42 | 20 | 9 | 0 | 0 | 101
25-0073127 | Mendocino | HOPLAND 1101 | HOPLAND 1101768 | Vegetation | 2025-07-08 14:50 | -07:00 | 07/08 - 07/14 | 2025-07-08 16:19 | -07:00 | 89 | FTS | 8900 | 100 | 5 | 5 | 1 | 0 | 0 | 0 | 89
25-0073083 | Santa Cruz | BIG BASIN 1101 | BIG BASIN 110165444 | 3rd Party | 2025-07-08 14:06 | -07:00 | 07/08 - 07/14 | 2025-07-09 02:07 | -07:00 | 94.9093 | FTS | 75358 | 794 | 71 | 54 | 5 | 0 | 0 | 0 | 721
25-0073244 | Contra Costa | SOBRANTE 1102 | SOBRANTE 1102690098 | Animal | 2025-07-09 02:31 | -07:00 | 07/08 - 07/14 | 2025-07-09 05:44 | -07:00 | 193 | FTS | 112133 | 581 | 24 | 19 | 13 | 2 | 0 | 0 | 193
25-0073186 | Santa Clara | MORGAN HILL 2111 | MORGAN HILL 2111XR398 | 3rd Party | 2025-07-08 16:21 | -07:00 | 07/08 - 07/14 | 2025-07-09 06:10 | -07:00 | 240.2375 | FTS | 96095 | 400 | 20 | 17 | 10 | 0 | 0 | 2 | 829
25-0073324 | San Luis Obispo | CHOLAME 2102 | CHOLAME 2102867686 | Company Initiated | 2025-07-09 08:48 | -07:00 | 07/08 - 07/14 | 2025-07-09 08:58 | -07:00 | 10 | FTS | 560 | 56 | 0 | 0 | 3 | 0 | 0 | 0 | 10
25-0073230 | Yuba | DOBBINS 1101 | DOBBINS 11011808 | Animal | 2025-07-08 22:17 | -07:00 | 07/08 - 07/14 | 2025-07-09 09:32 | -07:00 | 675 | FTS | 114750 | 170 | 11 | 9 | 0 | 0 | 0 | 0 | 675
25-0073340 | Santa Cruz | BIG BASIN 1102 | BIG BASIN 110212758 | Vegetation | 2025-07-09 09:08 | -07:00 | 07/08 - 07/14 | 2025-07-09 10:38 | -07:00 | 90 | FTS | 25290 | 281 | 18 | 15 | 6 | 0 | 0 | 0 | 90
25-0073242 | Tehama | RED BLUFF 1105 | RED BLUFF 11051564 | Equipment Failure/Involved | 2025-07-09 02:56 | -07:00 | 07/08 - 07/14 | 2025-07-09 10:59 | -07:00 | 392.9545 | FTS | 397670 | 1012 | 99 | 67 | 20 | 1 | 0 | 10 | 483
25-0073221 | Contra Costa | CLAYTON 2212 | CLAYTON 221296224 | Vegetation | 2025-07-08 20:07 | -07:00 | 07/08 - 07/14 | 2025-07-09 11:56 | -07:00 | 180.6328 | FTS | 46242 | 256 | 18 | 12 | 3 | 0 | 0 | 9 | 949
25-0073525 | Shasta | BURNEY 1101 | BURNEY 11011358 | Company Initiated | 2025-07-09 13:21 | -07:00 | 07/08 - 07/14 | 2025-07-09 13:32 | -07:00 | 11 | FTS | 1507 | 137 | 8 | 5 | 10 | 0 | 0 | 0 | 11
25-0073225 | Santa Clara | MORGAN HILL 2105 | MORGAN HILL 2105XR176 | Equipment Failure/Involved | 2025-07-08 21:07 | -07:00 | 07/08 - 07/14 | 2025-07-09 13:41 | -07:00 | 178.3457 | FTS | 197072 | 1105 | 52 | 44 | 16 | 3 | 0 | 10 | 994
25-0073514 | Santa Clara | MC KEE 1111 | MC KEE 1111711900 | Company Initiated | 2025-07-09 13:23 | -07:00 | 07/08 - 07/14 | 2025-07-09 14:17 | -07:00 | 54 | FTS | 28890 | 535 | 29 | 17 | 6 | 0 | 0 | 0 | 54
25-0073128 | Santa Cruz | CAMP EVERS 2106 | CAMP EVERS 210694770 | Vegetation | 2025-07-08 14:51 | -07:00 | 07/08 - 07/14 | 2025-07-09 14:38 | -07:00 | 97.3263 | FTS | 175382 | 1802 | 129 | 111 | 36 | 7 | 0 | 22 | 1427
25-0072022 | Santa Barbara | SISQUOC 1102 | SISQUOC 1102M52 | Environmental/External | 2025-07-03 13:42 | -07:00 | 07/08 - 07/14 | 2025-07-09 18:02 | -07:00 | 184.473 | FTS | 13651 | 74 | 3 | 2 | 1 | 0 | 0 | 0 | 8900
25-0073601 | Mendocino | COVELO 1101 | COVELO 1101562360 | Animal | 2025-07-09 15:22 | -07:00 | 07/08 - 07/14 | 2025-07-09 18:08 | -07:00 | 142.9725 | FTS | 72916 | 510 | 16 | 15 | 2 | 3 | 0 | 3 | 166
25-0073544 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113A12 | Equipment Failure/Involved | 2025-07-09 14:10 | -07:00 | 07/08 - 07/14 | 2025-07-09 18:08 | -07:00 | 62.3288 | FTS | 64448 | 1034 | 50 | 43 | 19 | 0 | 0 | 21 | 238
25-0073682 | Sonoma | DUNBAR 1101 | DUNBAR 1101534 | Unknown Cause | 2025-07-10 00:20 | -07:00 | 07/08 - 07/14 | 2025-07-10 01:31 | -07:00 | 70.3023 | FTS | 12092 | 172 | 4 | 3 | 4 | 0 | 0 | 8 | 71
25-0073688 | Calaveras | FROGTOWN 1702 | FROGTOWN 1702902652 | Animal | 2025-07-10 04:58 | -07:00 | 07/08 - 07/14 | 2025-07-10 07:13 | -07:00 | 135 | FTS | 23355 | 173 | 6 | 5 | 4 | 0 | 0 | 0 | 135
25-0073685 | Marin | ALTO 1122 | ALTO 112265474 | Animal | 2025-07-10 02:58 | -07:00 | 07/08 - 07/14 | 2025-07-10 07:47 | -07:00 | 287.8521 | FTS | 970925 | 3373 | 75 | 45 | 38 | 3 | 0 | 0 | 289
25-0073695 | Santa Clara | LLAGAS 2107 | LLAGAS 2107374344 | Animal | 2025-07-10 06:08 | -07:00 | 07/08 - 07/14 | 2025-07-10 07:54 | -07:00 | 106 | FTS | 27772 | 262 | 16 | 11 | 3 | 0 | 0 | 0 | 106
25-0073696 | Yuba | DOBBINS 1101 | DOBBINS 110191464 | Animal | 2025-07-10 06:14 | -07:00 | 07/08 - 07/14 | 2025-07-10 07:55 | -07:00 | 101 | FTS | 11514 | 114 | 7 | 7 | 1 | 1 | 0 | 0 | 101
25-0073751 | Alameda | JARVIS 1110 | JARVIS 1108289662 | Unknown Cause | 2025-07-10 08:24 | -07:00 | 07/08 - 07/14 | 2025-07-10 09:09 | -07:00 | 45 | FTS | 3690 | 82 | 7 | 5 | 1 | 1 | 0 | 0 | 45
25-0073734 | Alameda | LAS POSITAS 2108 | LAS POSITAS 2108794616 | Unknown Cause | 2025-07-10 07:54 | -07:00 | 07/08 - 07/14 | 2025-07-10 10:04 | -07:00 | 40.7947 | FTS | 141476 | 3468 | 163 | 124 | 51 | 2 | 2 | 0 | 130
25-0073833 | Madera | OAKHURST 1103 | OAKHURST 11035726 | Company Initiated | 2025-07-10 10:45 | -07:00 | 07/08 - 07/14 | 2025-07-10 11:14 | -07:00 | 29 | FTS | 5887 | 203 | 11 | 6 | 5 | 0 | 0 | 0 | 29
25-0073878 | Tehama | COTTONWOOD 1103 | COTTONWOOD 11031616 | Company Initiated | 2025-07-10 11:54 | -07:00 | 07/08 - 07/14 | 2025-07-10 12:28 | -07:00 | 34 | FTS | 986 | 29 | 8 | 5 | 0 | 0 | 0 | 0 | 34
25-0073825 | El Dorado | MOUNTAIN QUARRIES 2101 | MOUNTAIN QUARRIES 21012422 | Company Initiated | 2025-07-10 10:41 | -07:00 | 07/08 - 07/14 | 2025-07-10 13:56 | -07:00 | 195 | FTS | 112905 | 579 | 50 | 38 | 7 | 1 | 0 | 5 | 195
25-0073976 | El Dorado | MOUNTAIN QUARRIES 2101 | MOUNTAIN QUARRIES 21012422 | Company Initiated | 2025-07-10 14:16 | -07:00 | 07/08 - 07/14 | 2025-07-10 14:57 | -07:00 | 41 | FTS | 23780 | 580 | 50 | 38 | 7 | 1 | 0 | 5 | 41
25-0073912 | Marin | NOVATO 1104 | NOVATO 11046137 | Unknown Cause | 2025-07-10 12:36 | -07:00 | 07/08 - 07/14 | 2025-07-10 15:06 | -07:00 | 88.2029 | FTS | 6086 | 69 | 0 | 0 | 4 | 0 | 0 | 0 | 150
25-0074057 | Marin | NOVATO 1104 | NOVATO 1104889406 | Company Initiated | 2025-07-10 14:35 | -07:00 | 07/08 - 07/14 | 2025-07-10 16:11 | -07:00 | 96 | FTS | 288 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 96
25-0074048 | Santa Barbara | CABRILLO 1104 | CABRILLO 1104838078 | Unknown Cause | 2025-07-10 15:34 | -07:00 | 07/08 - 07/14 | 2025-07-10 16:53 | -07:00 | 79 | FTS | 19671 | 249 | 2 | 1 | 5 | 0 | 0 | 0 | 79
25-0074098 | Sonoma | DUNBAR 1101 | DUNBAR 1101534 | Company Initiated | 2025-07-10 16:23 | -07:00 | 07/08 - 07/14 | 2025-07-10 17:05 | -07:00 | 42 | FTS | 3528 | 84 | 1 | 0 | 2 | 0 | 0 | 4 | 42
25-0074115 | Amador | ELECTRA 1101 | ELECTRA 1101CB | Company Initiated | 2025-07-10 14:54 | -07:00 | 07/08 - 07/14 | 2025-07-10 17:20 | -07:00 | 146 | FTS | 1168 | 8 | 1 | 1 | 0 | 0 | 0 | 0 | 146
25-0074165 | Shasta | STILLWATER 1102 | STILLWATER 11021466 | Equipment Failure/Involved | 2025-07-10 18:29 | -07:00 | 07/08 - 07/14 | 2025-07-10 21:16 | -07:00 | 119.6178 | FTS | 89833 | 751 | 71 | 54 | 11 | 0 | 0 | 1 | 167
25-0074160 | Santa Clara | MORGAN HILL 2104 | MORGAN HILL 2104152774 | Unknown Cause | 2025-07-10 18:07 | -07:00 | 07/08 - 07/14 | 2025-07-10 21:31 | -07:00 | 201.1359 | FTS | 111027 | 552 | 39 | 26 | 12 | 0 | 0 | 0 | 204
25-0074201 | Calaveras | FROGTOWN 1702 | FROGTOWN 17027108 | Unknown Cause | 2025-07-10 20:33 | -07:00 | 07/08 - 07/14 | 2025-07-10 23:24 | -07:00 | 171 | FTS | 48735 | 285 | 14 | 11 | 5 | 0 | 0 | 0 | 171
25-0074198 | Santa Cruz | BIG BASIN 1102 | BIG BASIN 110296986 | 3rd Party | 2025-07-10 20:15 | -07:00 | 07/08 - 07/14 | 2025-07-11 00:05 | -07:00 | 168.8454 | FTS | 137609 | 815 | 47 | 38 | 14 | 1 | 0 | 5 | 230
25-0074229 | Santa Cruz | BIG BASIN 1101 | BIG BASIN 1101136050 | Company Initiated | 2025-07-10 23:00 | -07:00 | 07/08 - 07/14 | 2025-07-11 01:16 | -07:00 | 136 | FTS | 11288 | 83 | 8 | 6 | 1 | 0 | 0 | 0 | 136
25-0073970 | Monterey | GONZALES 1101 | GONZALES 11013094 | 3rd Party | 2025-07-10 14:13 | -07:00 | 07/08 - 07/14 | 2025-07-11 01:50 | -07:00 | 208.2647 | FTS | 14162 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 697
25-0074095 | Contra Costa | VALLEY VIEW 1105 | VALLEY VIEW 1105305072 | Vegetation | 2025-07-10 16:28 | -07:00 | 07/08 - 07/14 | 2025-07-11 06:07 | -07:00 | 204.5117 | FTS | 61149 | 299 | 12 | 9 | 7 | 0 | 0 | 0 | 819
25-0074246 | Santa Cruz | CAMP EVERS 2105 | CAMP EVERS 2105370732 | Unknown Cause | 2025-07-11 06:04 | -07:00 | 07/08 - 07/14 | 2025-07-11 07:49 | -07:00 | 105 | FTS | 45045 | 429 | 14 | 14 | 3 | 1 | 0 | 0 | 105
25-0074239 | Napa | SILVERADO 2104 | SILVERADO 2104959428 | Animal | 2025-07-11 02:24 | -07:00 | 07/08 - 07/14 | 2025-07-11 09:26 | -07:00 | 422 | FTS | 181882 | 431 | 21 | 12 | 7 | 0 | 0 | 3 | 422
25-0074396 | Napa | SILVERADO 2103 | SILVERADO 2103507513 | Animal | 2025-07-11 10:06 | -07:00 | 07/08 - 07/14 | 2025-07-11 10:40 | -07:00 | 34 | FTS | 5134 | 151 | 2 | 0 | 1 | 0 | 0 | 0 | 34
25-0074258 | Nevada | HIGGINS 1103 | HIGGINS 110332120 | Unknown Cause | 2025-07-11 06:31 | -07:00 | 07/08 - 07/14 | 2025-07-11 11:53 | -07:00 | 286.943 | FTS | 407459 | 1420 | 135 | 98 | 12 | 2 | 0 | 10 | 322
25-0074490 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113205874 | Company Initiated | 2025-07-11 11:54 | -07:00 | 07/08 - 07/14 | 2025-07-11 12:03 | -07:00 | 9 | FTS | 1818 | 202 | 10 | 10 | 3 | 0 | 0 | 10 | 9
25-0074491 | El Dorado | CLARKSVILLE 2104 | CLARKSVILLE 210413352 | Company Initiated | 2025-07-11 11:21 | -07:00 | 07/08 - 07/14 | 2025-07-11 12:13 | -07:00 | 52 | FTS | 104 | 2 | 1 | 1 | 0 | 0 | 0 | 0 | 52
25-0074563 | Sonoma | MOLINO 1102 | MOLINO 1102658 | Company Initiated | 2025-07-11 13:41 | -07:00 | 07/08 - 07/14 | 2025-07-11 14:20 | -07:00 | 39 | FTS | 1404 | 36 | 0 | 0 | 1 | 0 | 0 | 1 | 39
25-0074503 | El Dorado | DIAMOND SPRINGS 1104 | DIAMOND SPRINGS 1104CB | 3rd Party | 2025-07-11 12:12 | -07:00 | 07/08 - 07/14 | 2025-07-11 14:35 | -07:00 | 31.1105 | FTS | 31546 | 1014 | 92 | 65 | 20 | 7 | 0 | 1 | 143
25-0074606 | Sonoma | CALISTOGA 1101 | CALISTOGA 1101843761 | Company Initiated | 2025-07-11 14:38 | -07:00 | 07/08 - 07/14 | 2025-07-11 14:58 | -07:00 | 20 | FTS | 1040 | 52 | 0 | 0 | 1 | 0 | 0 | 0 | 20
25-0074212 | Shasta | STILLWATER 1102 | STILLWATER 1102828624 | Equipment Failure/Involved | 2025-07-10 21:55 | -07:00 | 07/08 - 07/14 | 2025-07-11 15:22 | -07:00 | 427.5231 | FTS | 601525 | 1407 | 132 | 95 | 16 | 0 | 0 | 2 | 1047
25-0074414 | Yuba | NARROWS 2101 | NARROWS 21011202 | Unknown Cause | 2025-07-11 10:23 | -07:00 | 07/08 - 07/14 | 2025-07-11 15:44 | -07:00 | 200.2332 | FTS | 101318 | 506 | 47 | 31 | 2 | 0 | 0 | 9 | 321
25-0074245 | Alameda | EL CERRITO G 1105 | EL CERRITO G 1105BR316 | Vegetation | 2025-07-11 05:35 | -07:00 | 07/08 - 07/14 | 2025-07-11 16:35 | -07:00 | 98.1973 | FTS | 71684 | 730 | 25 | 16 | 6 | 1 | 0 | 0 | 660
25-0074627 | Sonoma | CALISTOGA 1101 | CALISTOGA 1101242919 | Company Initiated | 2025-07-11 15:18 | -07:00 | 07/08 - 07/14 | 2025-07-11 16:59 | -07:00 | 101 | FTS | 2727 | 27 | 0 | 0 | 1 | 0 | 0 | 0 | 101
25-0074695 | Napa | PUEBLO 2103 | PUEBLO 2103489964 | Equipment Failure/Involved | 2025-07-11 19:48 | -07:00 | 07/08 - 07/14 | 2025-07-11 23:29 | -07:00 | 221 | FTS | 165308 | 748 | 44 | 31 | 8 | 1 | 0 | 0 | 221
25-0074692 | Calaveras | FROGTOWN 1702 | FROGTOWN 170274648 | Unknown Cause | 2025-07-11 19:44 | -07:00 | 07/08 - 07/14 | 2025-07-12 03:10 | -07:00 | 304.2587 | FTS | 332859 | 1094 | 74 | 54 | 16 | 6 | 0 | 0 | 446
25-0074719 | Monterey | BORONDA 1101, BORONDA 1102 | BORONDA 1101CB | Unknown Cause | 2025-07-12 00:16 | -07:00 | 07/08 - 07/14 | 2025-07-12 06:54 | -07:00 | 150.2857 | T-EPSS | 122032 | 812 | 38 | 27 | 13 | 2 | 0 | 0 | 398
25-0074744 | Solano | PEABODY 2106 | PEABODY 2106CB | Company Initiated | 2025-07-12 07:15 | -07:00 | 07/08 - 07/14 | 2025-07-12 08:08 | -07:00 | 53 | FTS | 186772 | 3524 | 284 | 218 | 25 | 4 | 0 | 0 | 53
25-0074743 | Sonoma | MIRABEL 1101 | MIRABEL 1101116 | Vegetation | 2025-07-12 07:05 | -07:00 | 07/08 - 07/14 | 2025-07-12 08:18 | -07:00 | 57.7823 | FTS | 21495 | 372 | 16 | 13 | 2 | 0 | 0 | 0 | 73
25-0074734 | Monterey | LOS OSITOS 2103 | LOS OSITOS 2103258688 | Unknown Cause | 2025-07-12 06:27 | -07:00 | 07/08 - 07/14 | 2025-07-12 08:54 | -07:00 | 147 | FTS | 1911 | 13 | 15 | 8 | 9 | 0 | 0 | 0 | 147
25-0074740 | Nevada | HIGGINS 1109 | HIGGINS 110950078 | Unknown Cause | 2025-07-12 06:56 | -07:00 | 07/08 - 07/14 | 2025-07-12 10:02 | -07:00 | 80.0217 | FTS | 33129 | 414 | 31 | 23 | 4 | 0 | 0 | 12 | 186
25-0074762 | El Dorado | SHINGLE SPRINGS 2109 | SHINGLE SPRINGS 210913322 | Animal | 2025-07-12 08:54 | -07:00 | 07/08 - 07/14 | 2025-07-12 10:26 | -07:00 | 60.8111 | FTS | 39588 | 651 | 58 | 40 | 4 | 0 | 0 | 10 | 92
25-0074741 | Lake | KONOCTI 1102 | KONOCTI 1102391062 | Animal | 2025-07-12 06:57 | -07:00 | 07/08 - 07/14 | 2025-07-12 12:22 | -07:00 | 134.7772 | HLT | 24799 | 184 | 10 | 5 | 1 | 0 | 0 | 1 | 325
25-0074760 | Solano | VACAVILLE 1108 | VACAVILLE 1108530880 | Unknown Cause | 2025-07-12 08:39 | -07:00 | 07/08 - 07/14 | 2025-07-12 12:29 | -07:00 | 173.4286 | HLT | 38848 | 224 | 12 | 10 | 3 | 0 | 0 | 2 | 230
25-0074713 | Placer | HORSESHOE 1101 | HORSESHOE 110150140 | Equipment Failure/Involved | 2025-07-11 22:00 | -07:00 | 07/08 - 07/14 | 2025-07-12 12:57 | -07:00 | 75.072 | FTS | 36485 | 486 | 32 | 24 | 3 | 0 | 0 | 5 | 897
25-0074705 | San Mateo | BAY MEADOWS 2102 | BAY MEADOWS 210257886 | Vegetation | 2025-07-11 21:18 | -07:00 | 07/08 - 07/14 | 2025-07-12 14:15 | -07:00 | 62.371 | FTS | 72288 | 1159 | 52 | 41 | 25 | 3 | 0 | 0 | 1017
25-0074751 | San Mateo | WOODSIDE 1104 | WOODSIDE 11049116 | Vegetation | 2025-07-12 07:51 | -07:00 | 07/08 - 07/14 | 2025-07-12 14:24 | -07:00 | 127.5334 | FTS | 146791 | 1151 | 35 | 31 | 23 | 5 | 0 | 0 | 393
25-0074746 | Solano | PEABODY 2107 | PEABODY 21079784 | Unknown Cause | 2025-07-12 07:18 | -07:00 | 07/08 - 07/14 | 2025-07-12 16:14 | -07:00 | 535.9965 | HLT | 308198 | 575 | 14 | 12 | 23 | 0 | 0 | 0 | 536
25-0074828 | Mendocino | COVELO 1101 | COVELO 1101664688 | 3rd Party | 2025-07-12 14:25 | -07:00 | 07/08 - 07/14 | 2025-07-12 16:45 | -07:00 | 140 | FTS | 2520 | 18 | 1 | 0 | 0 | 0 | 0 | 0 | 140
25-0074840 | Solano | PEABODY 2105 | PEABODY 2105CB | 3rd Party | 2025-07-12 16:12 | -07:00 | 07/08 - 07/14 | 2025-07-12 17:53 | -07:00 | 57.755 | FTS | 308585 | 5343 | 299 | 234 | 35 | 0 | 0 | 0 | 101
25-0074839 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113A70 | Unknown Cause | 2025-07-12 15:48 | -07:00 | 07/08 - 07/14 | 2025-07-12 18:02 | -07:00 | 34.6135 | FTS | 59466 | 1718 | 71 | 54 | 19 | 2 | 0 | 34 | 134
25-0074745 | Solano | PEABODY 2108 | PEABODY 2108CB | 3rd Party | 2025-07-12 07:15 | -07:00 | 07/08 - 07/14 | 2025-07-12 18:17 | -07:00 | 102.5084 | FTS | 384714 | 3753 | 303 | 222 | 42 | 2 | 0 | 0 | 662
25-0074814 | Sonoma | SONOMA 1107 | SONOMA 1107844168 | Animal | 2025-07-12 13:12 | -07:00 | 07/08 - 07/14 | 2025-07-12 21:13 | -07:00 | 209.192 | FTS | 26149 | 125 | 4 | 4 | 4 | 0 | 0 | 0 | 481
25-0074883 | Lake | HIGHLANDS 1103 | HIGHLANDS 1103568 | Unknown Cause | 2025-07-13 02:13 | -07:00 | 07/08 - 07/14 | 2025-07-13 05:34 | -07:00 | 201 | FTS | 67134 | 334 | 25 | 17 | 4 | 0 | 0 | 0 | 201
25-0074892 | El Dorado | SHINGLE SPRINGS 2109 | SHINGLE SPRINGS 210913322 | Unknown Cause | 2025-07-13 05:25 | -07:00 | 07/08 - 07/14 | 2025-07-13 06:49 | -07:00 | 64.6298 | FTS | 42074 | 651 | 58 | 40 | 4 | 0 | 0 | 10 | 84
25-0074889 | Santa Clara | HICKS 1116 | HICKS 1116983580 | Animal | 2025-07-13 04:41 | -07:00 | 07/08 - 07/14 | 2025-07-13 07:08 | -07:00 | 103.604 | FTS | 15437 | 149 | 4 | 3 | 2 | 0 | 0 | 0 | 147
25-0074900 | Alameda | MT EDEN 1109 | JARVIS 1101467034 | Unknown Cause | 2025-07-13 07:52 | -07:00 | 07/08 - 07/14 | 2025-07-13 09:42 | -07:00 | 110 | FTS | 1430 | 13 | 3 | 1 | 0 | 0 | 0 | 0 | 110
25-0074884 | Fresno | TIVY VALLEY 1107 | TIVY VALLEY 1107822606 | Unknown Cause | 2025-07-13 02:45 | -07:00 | 07/08 - 07/14 | 2025-07-13 10:24 | -07:00 | 411.1661 | FTS | 341679 | 831 | 56 | 39 | 13 | 0 | 0 | 0 | 459
25-0074913 | Fresno | DUNLAP 1103 | DUNLAP 11037080 | Company Initiated | 2025-07-13 10:54 | -07:00 | 07/08 - 07/14 | 2025-07-13 11:02 | -07:00 | 8 | FTS | 16 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 8
25-0074897 | San Mateo | WOODSIDE 1101 | WOODSIDE 11018972 | Unknown Cause | 2025-07-13 07:11 | -07:00 | 07/08 - 07/14 | 2025-07-13 12:05 | -07:00 | 294 | FTS | 19698 | 67 | 5 | 4 | 1 | 1 | 0 | 0 | 294
25-0074881 | Napa | PUEBLO 2102 | PUEBLO 2102279478 | Unknown Cause | 2025-07-13 02:10 | -07:00 | 07/08 - 07/14 | 2025-07-13 12:47 | -07:00 | 637 | FTS | 2548 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 637
25-0074915 | Amador | CLAY 1103 | CLAY 11031230 | 3rd Party | 2025-07-13 11:34 | -07:00 | 07/08 - 07/14 | 2025-07-13 18:40 | -07:00 | 304.7798 | FTS | 33221 | 109 | 3 | 3 | 4 | 0 | 0 | 1 | 426
25-0074944 | Santa Clara | STELLING 1110 | STELLING 1110LL72 | Animal | 2025-07-13 17:33 | -07:00 | 07/08 - 07/14 | 2025-07-13 19:04 | -07:00 | 91 | FTS | 76531 | 841 | 16 | 15 | 13 | 0 | 0 | 0 | 91
25-0074932 | Lake | HARTLEY 1102 | HARTLEY 1102841676 | Vegetation | 2025-07-13 15:07 | -07:00 | 07/08 - 07/14 | 2025-07-13 19:34 | -07:00 | 65.0834 | FTS | 60072 | 923 | 80 | 57 | 10 | 0 | 0 | 0 | 267
25-0074931 | Marin | NOVATO 1104 | NOVATO 1104676060 | Equipment Failure/Involved | 2025-07-13 15:06 | -07:00 | 07/08 - 07/14 | 2025-07-13 19:48 | -07:00 | 232.2363 | FTS | 97307 | 419 | 22 | 16 | 11 | 0 | 0 | 0 | 282
25-0074951 | El Dorado | SHINGLE SPRINGS 2108 | SHINGLE SPRINGS 210819622 | Vegetation | 2025-07-13 19:19 | -07:00 | 07/08 - 07/14 | 2025-07-13 21:50 | -07:00 | 127.0271 | FTS | 309565 | 2437 | 174 | 127 | 20 | 2 | 0 | 2 | 151
25-0074955 | Marin | IGNACIO 1105 | IGNACIO 1105318 | 3rd Party | 2025-07-13 20:29 | -07:00 | 07/08 - 07/14 | 2025-07-13 22:00 | -07:00 | 87.8707 | FTS | 387334 | 4408 | 174 | 117 | 39 | 7 | 2 | 1 | 91
25-0074954 | Solano | PEABODY 2105 | PEABODY 210515812 | Vegetation | 2025-07-13 20:23 | -07:00 | 07/08 - 07/14 | 2025-07-13 22:14 | -07:00 | 111 | HLT | 39294 | 354 | 9 | 8 | 5 | 0 | 0 | 0 | 111
25-0074963 | Monterey | GABILAN 1101 | GABILAN 1101460414 | Equipment Failure/Involved | 2025-07-13 21:02 | -07:00 | 07/08 - 07/14 | 2025-07-13 22:52 | -07:00 | 110 | FTS | 3850 | 35 | 2 | 2 | 0 | 0 | 0 | 0 | 110
25-0074961 | El Dorado | CLARKSVILLE 2104 | CLARKSVILLE 2104CB | Vegetation | 2025-07-13 22:47 | -07:00 | 07/08 - 07/14 | 2025-07-14 00:44 | -07:00 | 108.0335 | FTS | 552267 | 5112 | 352 | 262 | 62 | 5 | 0 | 60 | 117
25-0074887 | Calaveras | STANISLAUS 1701 | STANISLAUS 17017144 | Equipment Failure/Involved | 2025-07-13 04:09 | -07:00 | 07/08 - 07/14 | 2025-07-14 02:23 | -07:00 | 135.6286 | FTS | 121252 | 894 | 53 | 40 | 16 | 0 | 0 | 0 | 1334
25-0074984 | Madera | SAN JOAQUIN #3 1103 | SAN JOAQUIN #3 1103374484 | Unknown Cause | 2025-07-14 06:48 | -07:00 | 07/08 - 07/14 | 2025-07-14 08:25 | -07:00 | 97 | FTS | 97 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 97
25-0074994 | Nevada | BRUNSWICK 1103 | BRUNSWICK 11032200 | 3rd Party | 2025-07-14 07:34 | -07:00 | 07/08 - 07/14 | 2025-07-14 08:31 | -07:00 | 57 | FTS | 6498 | 114 | 5 | 5 | 0 | 0 | 0 | 1 | 57
25-0074983 | Sonoma | MOLINO 1101 | MOLINO 1101338 | Unknown Cause | 2025-07-14 06:54 | -07:00 | 07/08 - 07/14 | 2025-07-14 08:46 | -07:00 | 73.4685 | FTS | 26816 | 365 | 13 | 6 | 8 | 3 | 0 | 8 | 112
25-0074970 | Napa | BASALT 1106 | BASALT 1106657038 | Unknown Cause | 2025-07-14 03:59 | -07:00 | 07/08 - 07/14 | 2025-07-14 08:49 | -07:00 | 290 | FTS | 35670 | 123 | 0 | 0 | 7 | 0 | 0 | 0 | 290
25-0075000 | Sonoma | SONOMA 1103 | SONOMA 11033138 | Animal | 2025-07-14 07:42 | -07:00 | 07/08 - 07/14 | 2025-07-14 09:11 | -07:00 | 89 | FTS | 21004 | 236 | 9 | 7 | 0 | 0 | 0 | 0 | 89
25-0074952 | Placer | HALSEY 1102 | HALSEY 1102CB | 3rd Party | 2025-07-13 19:23 | -07:00 | 07/08 - 07/14 | 2025-07-14 09:40 | -07:00 | 144.241 | FTS | 298002 | 2066 | 123 | 79 | 46 | 11 | 0 | 27 | 857
25-0075044 | Napa | SILVERADO 2102 | SILVERADO 21023010 | Animal | 2025-07-14 09:11 | -07:00 | 07/08 - 07/14 | 2025-07-14 09:59 | -07:00 | 36.5219 | FTS | 20014 | 548 | 3 | 2 | 12 | 0 | 0 | 1 | 48
25-0075026 | Mendocino | POTTER VALLEY P H 1105 | POTTER VALLEY P H 11051904 | Animal | 2025-07-14 08:45 | -07:00 | 07/08 - 07/14 | 2025-07-14 10:03 | -07:00 | 78 | FTS | 9594 | 123 | 9 | 6 | 0 | 0 | 0 | 1 | 78
25-0075090 | Fresno | AUBERRY 1101 | AUBERRY 1101233716 | Equipment Failure/Involved | 2025-07-14 10:24 | -07:00 | 07/08 - 07/14 | 2025-07-14 10:49 | -07:00 | 25 | FTS | 5300 | 212 | 11 | 9 | 5 | 0 | 0 | 0 | 25
25-0075100 | Sonoma | BELLEVUE 2101 | BELLEVUE 2101411782 | Animal | 2025-07-14 10:54 | -07:00 | 07/08 - 07/14 | 2025-07-14 11:43 | -07:00 | 49 | FTS | 4214 | 86 | 3 | 2 | 2 | 0 | 0 | 4 | 49
25-0075074 | San Luis Obispo | PASO ROBLES 1104 | PASO ROBLES 1104R12 | Animal | 2025-07-14 10:09 | -07:00 | 07/08 - 07/14 | 2025-07-14 13:31 | -07:00 | 75.7099 | FTS | 32101 | 424 | 11 | 6 | 9 | 0 | 0 | 15 | 202
25-0075118 | Napa | SILVERADO 2105 | SILVERADO 2105861266 | Company Initiated | 2025-07-14 11:24 | -07:00 | 07/08 - 07/14 | 2025-07-14 13:34 | -07:00 | 130 | FTS | 7150 | 55 | 1 | 1 | 0 | 0 | 0 | 1 | 130
25-0075083 | Contra Costa | ALHAMBRA 1105 | ALHAMBRA 11058302 | Unknown Cause | 2025-07-14 09:50 | -07:00 | 07/08 - 07/14 | 2025-07-14 16:28 | -07:00 | 398 | FTS | 18308 | 46 | 1 | 0 | 4 | 0 | 0 | 1 | 398
25-0075112 | Napa | SILVERADO 2104 | SILVERADO 2104633600 | Unknown Cause | 2025-07-14 11:22 | -07:00 | 07/08 - 07/14 | 2025-07-14 16:39 | -07:00 | 317 | FTS | 109365 | 345 | 18 | 8 | 13 | 3 | 0 | 0 | 317
25-0075300 | Nevada | HIGGINS 1104 | HIGGINS 1104663774 | Vegetation | 2025-07-14 15:48 | -07:00 | 07/08 - 07/14 | 2025-07-14 16:57 | -07:00 | 69 | FTS | 98808 | 1432 | 121 | 81 | 15 | 0 | 0 | 2 | 69
25-0075245 | Mendocino | CALPELLA 1101 | CALPELLA 1101619542 | Equipment Failure/Involved | 2025-07-14 14:52 | -07:00 | 07/08 - 07/14 | 2025-07-14 18:07 | -07:00 | 35.6629 | FTS | 3174 | 89 | 2 | 1 | 5 | 0 | 0 | 1 | 195
25-0075122 | Napa | SILVERADO 2105 | SILVERADO 2105394844 | 3rd Party | 2025-07-14 11:24 | -07:00 | 07/08 - 07/14 | 2025-07-14 19:07 | -07:00 | 183.3495 | FTS | 140079 | 764 | 11 | 9 | 11 | 5 | 0 | 1 | 463
25-0075373 | Tuolumne | CURTIS 1703 | CURTIS 1703258550 | Company Initiated | 2025-07-14 18:19 | -07:00 | 07/08 - 07/14 | 2025-07-14 19:20 | -07:00 | 61 | FTS | 159088 | 2608 | 139 | 102 | 44 | 1 | 0 | 1 | 61
25-0075343 | Contra Costa | ALHAMBRA 1105 | ALHAMBRA 11058302 | Unknown Cause | 2025-07-14 16:41 | -07:00 | 07/08 - 07/14 | 2025-07-14 20:31 | -07:00 | 84.3611 | FTS | 12148 | 144 | 10 | 6 | 6 | 0 | 0 | 6 | 230
25-0075361 | Kings | AVENAL 2101 | AVENAL 2101CB | Equipment Failure/Involved | 2025-07-14 17:28 | -07:00 | 07/08 - 07/14 | 2025-07-14 22:05 | -07:00 | 180.283 | FTS | 554190 | 3074 | 80 | 61 | 33 | 16 | 1 | 0 | 277
25-0075384 | Mendocino | MENDOCINO 1101 | MENDOCINO 1101856020 | Vegetation | 2025-07-14 18:49 | -07:00 | 07/15 - 07/21 | 2025-07-15 00:16 | -07:00 | 66.4278 | FTS | 49688 | 748 | 38 | 25 | 10 | 1 | 0 | 1 | 327
25-0075382 | Placer | WEIMAR 1101 | WEIMAR 11012764 | Vegetation | 2025-07-14 19:07 | -07:00 | 07/15 - 07/21 | 2025-07-15 00:39 | -07:00 | 102.0708 | FTS | 183217 | 1795 | 118 | 81 | 37 | 28 | 0 | 13 | 332
25-0075114 | Contra Costa | SOBRANTE 1103 | SOBRANTE 1103CB | Vegetation | 2025-07-14 11:25 | -07:00 | 07/15 - 07/21 | 2025-07-15 03:04 | -07:00 | 82.9495 | FTS | 72249 | 871 | 42 | 30 | 13 | 1 | 0 | 0 | 939
25-0075443 | Santa Cruz | BURNS 2101 | BURNS 2101CB | Equipment Failure/Involved | 2025-07-15 02:12 | -07:00 | 07/15 - 07/21 | 2025-07-15 06:08 | -07:00 | 235.4134 | FTS | 548984 | 2332 | 165 | 139 | 39 | 3 | 0 | 19 | 236
25-0075463 | Madera | SAN JOAQUIN #3 1103 | SAN JOAQUIN #3 1103374484 | Unknown Cause | 2025-07-15 06:47 | -07:00 | 07/15 - 07/21 | 2025-07-15 07:48 | -07:00 | 61 | FTS | 61 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 61
25-0075519 | Shasta | BURNEY 1101 | BURNEY 1101355340 | 3rd Party | 2025-07-15 08:05 | -07:00 | 07/15 - 07/21 | 2025-07-15 09:09 | -07:00 | 64 | FTS | 64 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 64
25-0075449 | Monterey | JOLON 1102 | JOLON 11027004 | Unknown Cause | 2025-07-15 05:28 | -07:00 | 07/15 - 07/21 | 2025-07-15 09:29 | -07:00 | 241 | FTS | 35909 | 149 | 2 | 2 | 9 | 0 | 0 | 4 | 241
25-0075475 | El Dorado | DIAMOND SPRINGS 1103 | DIAMOND SPRINGS 1103467046 | Unknown Cause | 2025-07-15 07:18 | -07:00 | 07/15 - 07/21 | 2025-07-15 10:09 | -07:00 | 135.8492 | FTS | 237872 | 1751 | 130 | 90 | 29 | 0 | 0 | 3 | 171
25-0075507 | Shasta | RISING RIVER 1101 | RISING RIVER 1101CB | Unknown Cause | 2025-07-15 08:05 | -07:00 | 07/15 - 07/21 | 2025-07-15 10:35 | -07:00 | 134.2931 | FTS | 113612 | 846 | 38 | 32 | 15 | 0 | 0 | 0 | 150
25-0075390 | Glenn | ELK CREEK 1101 | ELK CREEK 11012002 | Unknown Cause | 2025-07-14 19:34 | -07:00 | 07/15 - 07/21 | 2025-07-15 11:22 | -07:00 | 663.2601 | FTS | 591628 | 892 | 47 | 33 | 37 | 8 | 0 | 1 | 948
25-0075594 | Contra Costa | ALHAMBRA 1105 | ALHAMBRA 11058302 | Unknown Cause | 2025-07-15 09:28 | -07:00 | 07/15 - 07/21 | 2025-07-15 12:45 | -07:00 | 105.8056 | FTS | 15236 | 144 | 10 | 6 | 6 | 0 | 0 | 6 | 197
25-0075454 | Placer | PENRYN 1105 | PENRYN 11052406 | Animal | 2025-07-15 05:57 | -07:00 | 07/15 - 07/21 | 2025-07-15 13:01 | -07:00 | 57.214 | FTS | 50806 | 888 | 55 | 39 | 9 | 1 | 0 | 13 | 424
25-0075605 | Tuolumne | PEORIA 1704 | PEORIA 17048040 | Equipment Failure/Involved | 2025-07-15 09:51 | -07:00 | 07/15 - 07/21 | 2025-07-15 13:40 | -07:00 | 209.1053 | FTS | 27811 | 133 | 2 | 2 | 7 | 0 | 0 | 1 | 229
25-0075451 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113A70 | Unknown Cause | 2025-07-15 05:51 | -07:00 | 07/15 - 07/21 | 2025-07-15 13:50 | -07:00 | 98.2305 | FTS | 168760 | 1718 | 71 | 54 | 19 | 2 | 0 | 34 | 479
25-0075798 | Contra Costa | FAIRVIEW 2207 | FAIRVIEW 2207P304 | Company Initiated | 2025-07-15 13:49 | -07:00 | 07/15 - 07/21 | 2025-07-15 14:01 | -07:00 | 12 | FTS | 20520 | 1710 | 77 | 53 | 21 | 3 | 0 | 0 | 12
25-0075686 | Lake | MIDDLETOWN 1102 | MIDDLETOWN 1102CB | Unknown Cause | 2025-07-15 11:38 | -07:00 | 07/15 - 07/21 | 2025-07-15 15:02 | -07:00 | 192.5484 | FTS | 497160 | 2582 | 188 | 139 | 37 | 3 | 0 | 2 | 204
25-0075689 | Santa Clara | HICKS 1116 | HICKS 111660050 | Company Initiated | 2025-07-15 11:42 | -07:00 | 07/15 - 07/21 | 2025-07-15 15:20 | -07:00 | 218 | FTS | 49268 | 226 | 11 | 8 | 11 | 0 | 0 | 2 | 218
25-0075797 | Santa Clara | LOS GATOS 1107 | LOS GATOS 110760092 | Equipment Failure/Involved | 2025-07-15 13:01 | -07:00 | 07/15 - 07/21 | 2025-07-15 16:04 | -07:00 | 183 | FTS | 4392 | 24 | 1 | 1 | 4 | 0 | 0 | 0 | 183
25-0075935 | Santa Clara | LOS GATOS 1107 | LOS GATOS 110760092 | Company Initiated | 2025-07-15 18:26 | -07:00 | 07/15 - 07/21 | 2025-07-15 19:08 | -07:00 | 42 | FTS | 882 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 42
25-0075948 | Contra Costa | CLAYTON 2215 | CLAYTON 22159765 | Animal | 2025-07-15 19:00 | -07:00 | 07/15 - 07/21 | 2025-07-15 20:19 | -07:00 | 67.3571 | FTS | 11316 | 168 | 9 | 7 | 4 | 0 | 0 | 0 | 79
25-0075936 | Yolo | MADISON 2101 | MADISON 21017702 | Unknown Cause | 2025-07-15 18:32 | -07:00 | 07/15 - 07/21 | 2025-07-15 21:51 | -07:00 | 199 | FTS | 187060 | 940 | 18 | 10 | 18 | 14 | 0 | 4 | 199
25-0075940 | Santa Clara | MORGAN HILL 2105 | MORGAN HILL 2105XR176 | Animal | 2025-07-15 19:09 | -07:00 | 07/15 - 07/21 | 2025-07-15 22:23 | -07:00 | 137.1357 | FTS | 151535 | 1105 | 52 | 44 | 16 | 3 | 0 | 10 | 194
25-0075961 | Monterey | LOS OSITOS 2101 | LOS OSITOS 21011132 | Animal | 2025-07-15 22:00 | -07:00 | 07/15 - 07/21 | 2025-07-16 00:56 | -07:00 | 176 | FTS | 28160 | 160 | 3 | 3 | 4 | 1 | 0 | 0 | 176
25-0075955 | Santa Clara | HICKS 2101 | HICKS 2101257172 | Equipment Failure/Involved | 2025-07-15 21:19 | -07:00 | 07/15 - 07/21 | 2025-07-16 01:08 | -07:00 | 131.4293 | FTS | 124595 | 948 | 40 | 27 | 15 | 1 | 0 | 1 | 229
25-0075966 | Contra Costa | OAKLAND K 1102 | OAKLAND K 1102CR014 | Unknown Cause | 2025-07-15 22:49 | -07:00 | 07/15 - 07/21 | 2025-07-16 01:30 | -07:00 | 126.9401 | FTS | 169592 | 1336 | 63 | 46 | 39 | 0 | 0 | 0 | 161
25-0075919 | Sonoma | MIRABEL 1102 | MIRABEL 110238514 | Vegetation | 2025-07-15 17:15 | -07:00 | 07/15 - 07/21 | 2025-07-16 01:38 | -07:00 | 112.3603 | FTS | 61124 | 544 | 22 | 14 | 10 | 0 | 0 | 0 | 503
25-0075943 | Humboldt | GARBERVILLE 1102 | GARBERVILLE 1102939030 | Vegetation | 2025-07-15 19:20 | -07:00 | 07/15 - 07/21 | 2025-07-16 02:24 | -07:00 | 422.1285 | FTS | 344879 | 817 | 23 | 13 | 16 | 4 | 0 | 2 | 424
25-0075950 | Napa | MONTICELLO 1101 | MONTICELLO 11014360 | Animal | 2025-07-15 20:05 | -07:00 | 07/15 - 07/21 | 2025-07-16 03:24 | -07:00 | 142.7391 | FTS | 39396 | 276 | 7 | 5 | 4 | 0 | 0 | 1 | 439
25-0076067 | Tehama | BIG BEND 1102 | BIG BEND 1102CB | Equipment Failure/Involved | 2025-07-16 08:31 | -07:00 | 07/15 - 07/21 | 2025-07-16 09:08 | -07:00 | 37 | FTS | 12358 | 334 | 11 | 8 | 10 | 0 | 0 | 0 | 37
25-0075983 | Shasta | BURNEY 1101 | BURNEY 1101519432 | Unknown Cause | 2025-07-16 01:26 | -07:00 | 07/15 - 07/21 | 2025-07-16 09:46 | -07:00 | 500 | FTS | 10500 | 21 | 0 | 0 | 9 | 0 | 0 | 0 | 500
25-0076078 | Amador | ELECTRA 1101 | ELECTRA 110161816 | Unknown Cause | 2025-07-16 08:51 | -07:00 | 07/15 - 07/21 | 2025-07-16 09:59 | -07:00 | 41.9435 | FTS | 15603 | 372 | 38 | 28 | 3 | 0 | 0 | 13 | 68
25-0076086 | Butte | CLARK ROAD 1102 | CLARK ROAD 11022068 | Equipment Failure/Involved | 2025-07-16 09:01 | -07:00 | 07/15 - 07/21 | 2025-07-16 10:10 | -07:00 | 69 | FTS | 6072 | 88 | 8 | 4 | 1 | 0 | 0 | 2 | 69
25-0075794 | Contra Costa | ALHAMBRA 1105 | ALHAMBRA 11058302 | Equipment Failure/Involved | 2025-07-15 13:49 | -07:00 | 07/15 - 07/21 | 2025-07-16 11:16 | -07:00 | 1287 | FTS | 59202 | 46 | 1 | 0 | 4 | 0 | 0 | 1 | 1287
25-0075965 | El Dorado | APPLE HILL 1103 | APPLE HILL 11038412 | Vegetation | 2025-07-15 22:39 | -07:00 | 07/15 - 07/21 | 2025-07-16 11:33 | -07:00 | 422.55 | FTS | 84510 | 200 | 10 | 8 | 2 | 0 | 0 | 5 | 774
25-0075967 | El Dorado | APPLE HILL 2102 | APPLE HILL 2102124050 | Unknown Cause | 2025-07-15 22:39 | -07:00 | 07/15 - 07/21 | 2025-07-16 12:25 | -07:00 | 424.8545 | FTS | 397239 | 935 | 65 | 46 | 9 | 0 | 0 | 4 | 826
25-0076254 | Nevada | BRUNSWICK 1104 | BRUNSWICK 1104789062 | 3rd Party | 2025-07-16 13:33 | -07:00 | 07/15 - 07/21 | 2025-07-16 15:35 | -07:00 | 122 | FTS | 122 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 122
25-0076224 | Sonoma | FITCH MOUNTAIN 1113 | FITCH MOUNTAIN 1113824468 | Unknown Cause | 2025-07-16 12:49 | -07:00 | 07/15 - 07/21 | 2025-07-16 15:51 | -07:00 | 182 | FTS | 97552 | 536 | 23 | 17 | 4 | 0 | 0 | 8 | 182
25-0076377 | Marin | SAN RAFAEL 1104 | SAN RAFAEL 1104717160 | 3rd Party | 2025-07-16 16:37 | -07:00 | 07/15 - 07/21 | 2025-07-16 17:22 | -07:00 | 42.7356 | FTS | 138378 | 3238 | 109 | 68 | 31 | 9 | 0 | 0 | 45
25-0076013 | Tuolumne | CURTIS 1705 | CURTIS 170565908 | 3rd Party | 2025-07-16 07:22 | -07:00 | 07/15 - 07/21 | 2025-07-16 17:46 | -07:00 | 239.1806 | FTS | 162882 | 681 | 44 | 36 | 7 | 5 | 0 | 0 | 624
25-0076370 | Amador | CLAY 1102 | CLAY 1102CB | 3rd Party | 2025-07-16 16:25 | -07:00 | 07/15 - 07/21 | 2025-07-16 17:56 | -07:00 | 91 | FTS | 273 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 91
25-0076396 | San Luis Obispo | PERRY 1101 | PERRY 1101V88 | Unknown Cause | 2025-07-16 17:45 | -07:00 | 07/15 - 07/21 | 2025-07-16 19:47 | -07:00 | 87.6157 | FTS | 64748 | 739 | 19 | 11 | 15 | 2 | 0 | 0 | 122
25-0076411 | Santa Barbara | ZACA 1102 | ZACA 1102CB | Unknown Cause | 2025-07-16 18:58 | -07:00 | 07/15 - 07/21 | 2025-07-16 20:03 | -07:00 | 65 | FTS | 94250 | 1450 | 35 | 21 | 24 | 16 | 0 | 7 | 65
25-0076428 | Lake | CLEAR LAKE 1101 | CLEAR LAKE 11011302 | Equipment Failure/Involved | 2025-07-16 21:01 | -07:00 | 07/15 - 07/21 | 2025-07-16 22:19 | -07:00 | 78 | FTS | 41028 | 526 | 37 | 24 | 8 | 0 | 0 | 1 | 78
25-0076481 | Tehama | VOLTA 1101 | VOLTA 11011596 | Company Initiated | 2025-07-17 08:03 | -07:00 | 07/15 - 07/21 | 2025-07-17 08:41 | -07:00 | 36.0538 | FTS | 30141 | 836 | 41 | 30 | 27 | 3 | 0 | 0 | 38
25-0076517 | Contra Costa | NORTH DUBLIN 2101 | NORTH DUBLIN 2101CB | Unknown Cause | 2025-07-17 09:18 | -07:00 | 07/15 - 07/21 | 2025-07-17 11:36 | -07:00 | 102.8721 | FTS | 560447 | 5448 | 92 | 70 | 20 | 2 | 0 | 0 | 138
25-0076522 | Tuolumne | PEORIA 1704 | PEORIA 17048040 | Unknown Cause | 2025-07-17 09:23 | -07:00 | 07/15 - 07/21 | 2025-07-17 12:58 | -07:00 | 197.812 | FTS | 26309 | 133 | 2 | 2 | 7 | 0 | 0 | 1 | 215
25-0076546 | Nevada | BRUNSWICK 1105 | BRUNSWICK 11052130 | Vegetation | 2025-07-17 10:26 | -07:00 | 07/15 - 07/21 | 2025-07-17 14:16 | -07:00 | 52.1386 | FTS | 34985 | 671 | 44 | 28 | 19 | 0 | 0 | 12 | 230
25-0076681 | Amador | ELECTRA 1101 | ELECTRA 1101CB | Company Initiated | 2025-07-17 13:48 | -07:00 | 07/15 - 07/21 | 2025-07-17 15:17 | -07:00 | 89 | FTS | 712 | 8 | 1 | 1 | 0 | 0 | 0 | 0 | 89
25-0076646 | Tuolumne | PEORIA 1701 | PEORIA 170190090 | Company Initiated | 2025-07-17 14:07 | -07:00 | 07/15 - 07/21 | 2025-07-17 15:32 | -07:00 | 85 | FTS | 215475 | 2535 | 176 | 131 | 29 | 14 | 0 | 2 | 85
25-0076644 | Shasta | JESSUP 1102 | JESSUP 1102146332 | Unknown Cause | 2025-07-17 13:57 | -07:00 | 07/15 - 07/21 | 2025-07-17 15:35 | -07:00 | 80.2455 | FTS | 31376 | 391 | 36 | 25 | 1 | 0 | 0 | 0 | 98
25-0076668 | Nevada | HIGGINS 1104 | HIGGINS 1104498932 | Unknown Cause | 2025-07-17 14:47 | -07:00 | 07/15 - 07/21 | 2025-07-17 15:52 | -07:00 | 22.8845 | FTS | 42977 | 1878 | 153 | 104 | 18 | 1 | 0 | 9 | 65
25-0076710 | Marin | IGNACIO 1101 | IGNACIO 11011300 | Animal | 2025-07-17 15:34 | -07:00 | 07/15 - 07/21 | 2025-07-17 16:23 | -07:00 | 49 | FTS | 41797 | 853 | 38 | 26 | 8 | 0 | 0 | 0 | 49
25-0076780 | Yolo | MADISON 2101 | MADISON 2101117644 | Unknown Cause | 2025-07-17 19:15 | -07:00 | 07/15 - 07/21 | 2025-07-17 21:16 | -07:00 | 121 | FTS | 1089 | 9 | 0 | 0 | 1 | 0 | 0 | 0 | 121
25-0076739 | Placer | PENRYN 1103 | PENRYN 110351658 | Equipment Failure/Involved | 2025-07-17 16:11 | -07:00 | 07/15 - 07/21 | 2025-07-18 01:49 | -07:00 | 122.9898 | FTS | 84740 | 689 | 46 | 34 | 9 | 0 | 0 | 19 | 578
25-0076807 | Shasta | OREGON TRAIL 1102 | OREGON TRAIL 1102CB | 3rd Party | 2025-07-17 22:45 | -07:00 | 07/15 - 07/21 | 2025-07-18 02:10 | -07:00 | 139.7605 | FTS | 86931 | 622 | 52 | 43 | 9 | 1 | 0 | 0 | 205
25-0076840 | Placer | PENRYN 1105 | PENRYN 1105680290 | Animal | 2025-07-18 07:06 | -07:00 | 07/15 - 07/21 | 2025-07-18 08:47 | -07:00 | 63.3728 | FTS | 24652 | 389 | 23 | 11 | 3 | 0 | 0 | 7 | 101
25-0076819 | Fresno | AUBERRY 1101 | AUBERRY 1101R2579 | Vegetation | 2025-07-18 01:25 | -07:00 | 07/15 - 07/21 | 2025-07-18 09:41 | -07:00 | 496 | FTS | 12400 | 25 | 0 | 0 | 1 | 0 | 0 | 0 | 496
25-0076960 | Mendocino | HOPLAND 1101 | HOPLAND 1101563064 | Company Initiated | 2025-07-18 10:36 | -07:00 | 07/15 - 07/21 | 2025-07-18 10:48 | -07:00 | 12 | FTS | 24 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 12
25-0076816 | San Luis Obispo | ATASCADERO 1103 | ATASCADERO 1103440856 | Vegetation | 2025-07-18 00:47 | -07:00 | 07/15 - 07/21 | 2025-07-18 14:42 | -07:00 | 311.8534 | FTS | 178692 | 573 | 29 | 19 | 13 | 0 | 0 | 18 | 835
25-0077204 | Tuolumne | PEORIA 1701 | CURTIS 17039330 | Company Initiated | 2025-07-18 16:25 | -07:00 | 07/15 - 07/21 | 2025-07-18 18:02 | -07:00 | 97 | FTS | 59170 | 610 | 33 | 23 | 17 | 0 | 0 | 0 | 97
25-0077223 | Contra Costa | ROSSMOOR 1101 | ROSSMOOR 110181770 | Animal | 2025-07-18 17:21 | -07:00 | 07/15 - 07/21 | 2025-07-18 18:05 | -07:00 | 44 | FTS | 10824 | 246 | 28 | 19 | 5 | 0 | 0 | 0 | 44
25-0077206 | Tuolumne | PEORIA 1701 | PEORIA 1701169700 | Company Initiated | 2025-07-18 16:27 | -07:00 | 07/15 - 07/21 | 2025-07-18 18:43 | -07:00 | 110.7458 | FTS | 176418 | 1593 | 97 | 81 | 18 | 1 | 0 | 1 | 136
25-0076873 | Monterey | SPENCE 1102 | SPENCE 1102276712 | Equipment Failure/Involved | 2025-07-18 08:23 | -07:00 | 07/15 - 07/21 | 2025-07-18 20:20 | -07:00 | 151.0909 | FTS | 29916 | 198 | 1 | 0 | 0 | 0 | 0 | 0 | 717
25-0077265 | Nevada | BRUNSWICK 1105 | BRUNSWICK 11052140 | Unknown Cause | 2025-07-19 04:15 | -07:00 | 07/15 - 07/21 | 2025-07-19 06:03 | -07:00 | 56.5374 | FTS | 46078 | 815 | 44 | 33 | 13 | 0 | 0 | 22 | 108
25-0077269 | Marin | PETALUMA C 1101, PETALUMA C 1102, PETALUMA C 1105, PETALUMA C 1106, PETALUMA C 1108, PETALUMA C 1109, PETALUMA C 1110 | PETALUMA C 1108632 | Equipment Failure/Involved | 2025-07-19 04:47 | -07:00 | 07/15 - 07/21 | 2025-07-19 08:01 | -07:00 | 159.0547 | T-EPSS | 3197476 | 20103 | 674 | 496 | 257 | 52 | 3 | 11 | 194
25-0077271 | Glenn | ELK CREEK 1101 | ELK CREEK 1101CB | Animal | 2025-07-19 05:33 | -07:00 | 07/15 - 07/21 | 2025-07-19 08:30 | -07:00 | 133.2643 | FTS | 119005 | 893 | 47 | 33 | 37 | 8 | 0 | 1 | 177
25-0077279 | Shasta | BURNEY 1101 | BURNEY 11011340 | Unknown Cause | 2025-07-19 07:10 | -07:00 | 07/15 - 07/21 | 2025-07-19 08:33 | -07:00 | 83 | FTS | 35192 | 424 | 41 | 29 | 6 | 0 | 0 | 0 | 83
25-0077318 | Calaveras | FROGTOWN 1702 | FROGTOWN 170275252 | Unknown Cause | 2025-07-19 09:31 | -07:00 | 07/15 - 07/21 | 2025-07-19 12:05 | -07:00 | 154 | FTS | 127358 | 827 | 33 | 23 | 28 | 2 | 0 | 3 | 154
25-0077348 | Fresno | DUNLAP 1103 | DUNLAP 1103124724 | Company Initiated | 2025-07-19 08:52 | -07:00 | 07/15 - 07/21 | 2025-07-19 13:12 | -07:00 | 260 | FTS | 70720 | 272 | 11 | 11 | 1 | 0 | 0 | 0 | 260
25-0077334 | Shasta | OREGON TRAIL 1104 | OREGON TRAIL 11041574 | Company Initiated | 2025-07-19 11:00 | -07:00 | 07/15 - 07/21 | 2025-07-19 13:39 | -07:00 | 157.5974 | FTS | 60675 | 385 | 33 | 22 | 4 | 0 | 0 | 0 | 159
25-0077339 | Lake | MIDDLETOWN 1102 | MIDDLETOWN 1102414 | Unknown Cause | 2025-07-19 11:35 | -07:00 | 07/15 - 07/21 | 2025-07-19 13:39 | -07:00 | 124 | FTS | 54808 | 442 | 26 | 20 | 7 | 0 | 0 | 0 | 124
25-0077363 | Mendocino | CALPELLA 1102 | CALPELLA 1102421412 | 3rd Party | 2025-07-19 14:34 | -07:00 | 07/15 - 07/21 | 2025-07-19 15:29 | -07:00 | 55 | FTS | 4840 | 88 | 2 | 2 | 3 | 0 | 0 | 0 | 55
25-0073283 | Shasta | OREGON TRAIL 1102 | OREGON TRAIL 11021584 | Equipment Failure/Involved | 2025-07-19 14:38 | -07:00 | 07/15 - 07/21 | 2025-07-19 15:45 | -07:00 | 67 | FTS | 14874 | 222 | 24 | 22 | 3 | 0 | 0 | 0 | 67
25-0077374 | Mariposa | OAKHURST 1103 | OAKHURST 110377384 | Equipment Failure/Involved | 2025-07-19 17:13 | -07:00 | 07/15 - 07/21 | 2025-07-19 18:20 | -07:00 | 67 | FTS | 31356 | 468 | 20 | 11 | 16 | 0 | 0 | 0 | 67
25-0077376 | Placer | DEL MAR 2109 | DEL MAR 2109CB | Company Initiated | 2025-07-19 17:50 | -07:00 | 07/15 - 07/21 | 2025-07-19 22:33 | -07:00 | 53.6647 | FTS | 446276 | 8316 | 229 | 158 | 40 | 1 | 0 | 1 | 283
25-0077215 | Santa Clara | SWIFT 2109 | SWIFT 2109XR300 | Equipment Failure/Involved | 2025-07-18 17:08 | -07:00 | 07/15 - 07/21 | 2025-07-20 05:15 | -07:00 | 322.6363 | FTS | 659146 | 2043 | 91 | 63 | 25 | 4 | 0 | 0 | 2167
25-0077391 | Humboldt | HOOPA 1101 | HOOPA 110182542 | Vegetation | 2025-07-19 21:46 | -07:00 | 07/15 - 07/21 | 2025-07-20 05:16 | -07:00 | 359.8077 | FTS | 84195 | 234 | 11 | 9 | 8 | 0 | 0 | 0 | 450
25-0077402 | Tuolumne | PEORIA 1701 | PEORIA 170176030 | Animal | 2025-07-20 05:40 | -07:00 | 07/15 - 07/21 | 2025-07-20 07:12 | -07:00 | 69.6193 | FTS | 13715 | 197 | 12 | 10 | 7 | 2 | 0 | 0 | 92
25-0077435 | Santa Cruz | CAMP EVERS 2107 | CAMP EVERS 2107287578 | Unknown Cause | 2025-07-20 10:43 | -07:00 | 07/15 - 07/21 | 2025-07-20 11:59 | -07:00 | 32.2736 | FTS | 6842 | 212 | 20 | 18 | 2 | 0 | 0 | 0 | 76
25-0077450 | Contra Costa | BRENTWOOD 2105 | BRENTWOOD 210596324 | Animal | 2025-07-20 13:10 | -07:00 | 07/15 - 07/21 | 2025-07-20 13:51 | -07:00 | 41 | FTS | 82 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 41
25-0077452 | Contra Costa | BRENTWOOD 2105 | BRENTWOOD 210519062 | Animal | 2025-07-20 13:10 | -07:00 | 07/15 - 07/21 | 2025-07-20 14:01 | -07:00 | 51 | FTS | 29580 | 580 | 25 | 17 | 25 | 4 | 0 | 0 | 51
25-0077446 | San Luis Obispo | TEMPLETON 2110 | TEMPLETON 2110901690 | Unknown Cause | 2025-07-20 12:22 | -07:00 | 07/15 - 07/21 | 2025-07-20 15:29 | -07:00 | 187 | FTS | 53295 | 285 | 4 | 3 | 5 | 0 | 0 | 13 | 187
25-0077473 | Butte | WYANDOTTE 1109 | WYANDOTTE 1109759354 | Animal | 2025-07-20 20:59 | -07:00 | 07/15 - 07/21 | 2025-07-20 23:25 | -07:00 | 56.921 | FTS | 81454 | 1431 | 127 | 99 | 16 | 5 | 0 | 5 | 146
25-0077477 | Madera | COARSEGOLD 2103 | COARSEGOLD 210310300 | Unknown Cause | 2025-07-20 22:07 | -07:00 | 07/15 - 07/21 | 2025-07-21 02:17 | -07:00 | 110.066 | FTS | 23334 | 212 | 13 | 10 | 33 | 4 | 0 | 1 | 250
25-0077490 | Contra Costa | TASSAJARA 2112 | TASSAJARA 2112CB | Animal | 2025-07-21 02:10 | -07:00 | 07/15 - 07/21 | 2025-07-21 02:53 | -07:00 | 39.9781 | FTS | 103903 | 2599 | 123 | 83 | 61 | 16 | 0 | 1 | 43
25-0077494 | Placer | LINCOLN 1104 | LINCOLN 1104693294 | 3rd Party | 2025-07-21 05:29 | -07:00 | 07/15 - 07/21 | 2025-07-21 06:47 | -07:00 | 78 | FTS | 24648 | 316 | 11 | 3 | 0 | 0 | 0 | 0 | 78
25-0077500 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113A70 | Animal | 2025-07-21 06:16 | -07:00 | 07/15 - 07/21 | 2025-07-21 07:14 | -07:00 | 58 | FTS | 99644 | 1718 | 71 | 54 | 19 | 2 | 0 | 34 | 58
25-0077527 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113175566 | Company Initiated | 2025-07-21 08:03 | -07:00 | 07/15 - 07/21 | 2025-07-21 08:23 | -07:00 | 16.3124 | FTS | 23914 | 1466 | 67 | 52 | 23 | 0 | 1 | 23 | 20
25-0077496 | Kern | MARICOPA 1101 | MARICOPA 1101931236 | Unknown Cause | 2025-07-21 05:36 | -07:00 | 07/15 - 07/21 | 2025-07-21 09:39 | -07:00 | 243 | FTS | 19926 | 82 | 1 | 1 | 5 | 0 | 0 | 0 | 243
25-0077771 | Santa Cruz | CAMP EVERS 2107 | CAMP EVERS 210711044 | Unknown Cause | 2025-07-21 14:29 | -07:00 | 07/15 - 07/21 | 2025-07-21 17:07 | -07:00 | 131.6214 | FTS | 295490 | 2245 | 165 | 132 | 39 | 1 | 0 | 2 | 158
25-0077845 | Monterey | SAN MIGUEL 1106 | SAN MIGUEL 1106605393 | Unknown Cause | 2025-07-21 18:26 | -07:00 | 07/15 - 07/21 | 2025-07-21 20:32 | -07:00 | 126 | FTS | 11214 | 89 | 2 | 1 | 1 | 0 | 0 | 1 | 126
25-0077856 | San Luis Obispo | ATASCADERO 1103 | ATASCADERO 1103A06 | Unknown Cause | 2025-07-21 19:34 | -07:00 | 07/15 - 07/21 | 2025-07-21 20:33 | -07:00 | 59 | FTS | 37524 | 636 | 31 | 21 | 18 | 2 | 0 | 18 | 59
25-0077833 | San Luis Obispo | TEMPLETON 2110 | TEMPLETON 2110901690 | Unknown Cause | 2025-07-21 17:34 | -07:00 | 07/15 - 07/21 | 2025-07-21 22:32 | -07:00 | 185.9018 | FTS | 52982 | 285 | 4 | 3 | 5 | 0 | 0 | 13 | 298
25-0077882 | Santa Clara | STELLING 1109 | STELLING 110913228 | Unknown Cause | 2025-07-22 01:08 | -07:00 | 07/22 - 07/28 | 2025-07-22 03:45 | -07:00 | 156.6667 | FTS | 223250 | 1425 | 43 | 33 | 17 | 3 | 0 | 0 | 157
25-0077838 | Butte | WYANDOTTE 1109 | WYANDOTTE 1109758802 | 3rd Party | 2025-07-21 17:54 | -07:00 | 07/22 - 07/28 | 2025-07-22 04:40 | -07:00 | 75.5275 | FTS | 138895 | 1839 | 165 | 126 | 21 | 5 | 0 | 5 | 646
25-0077893 | Lake | CLEAR LAKE 1101 | CLEAR LAKE 11011302 | Animal | 2025-07-22 05:48 | -07:00 | 07/22 - 07/28 | 2025-07-22 06:51 | -07:00 | 63 | FTS | 33138 | 526 | 37 | 24 | 8 | 0 | 0 | 1 | 63
25-0077892 | Santa Clara | MORGAN HILL 2105 | MORGAN HILL 2105XR176 | Unknown Cause | 2025-07-22 05:46 | -07:00 | 07/22 - 07/28 | 2025-07-22 09:11 | -07:00 | 50.552 | FTS | 55860 | 1105 | 52 | 44 | 16 | 3 | 0 | 10 | 205
25-0078050 | El Dorado | DIAMOND SPRINGS 1105 | DIAMOND SPRINGS 1105146980 | Company Initiated | 2025-07-22 10:04 | -07:00 | 07/22 - 07/28 | 2025-07-22 10:17 | -07:00 | 13 | FTS | 689 | 53 | 1 | 0 | 0 | 0 | 0 | 0 | 13
25-0077703 | Santa Clara | PIERCY 2110 | PIERCY 2110799154 | Unknown Cause | 2025-07-21 12:33 | -07:00 | 07/22 - 07/28 | 2025-07-22 10:18 | -07:00 | 102.542 | FTS | 75676 | 738 | 27 | 19 | 12 | 0 | 0 | 0 | 1305
25-0077999 | El Dorado | APPLE HILL 2102 | APPLE HILL 210297982 | Unknown Cause | 2025-07-22 09:11 | -07:00 | 07/22 - 07/28 | 2025-07-22 11:06 | -07:00 | 96.4715 | FTS | 47464 | 492 | 38 | 28 | 2 | 0 | 0 | 0 | 115
25-0078111 | Sonoma | MONTE RIO 1113 | MONTE RIO 1113539938 | 3rd Party | 2025-07-22 11:13 | -07:00 | 07/22 - 07/28 | 2025-07-22 12:32 | -07:00 | 49.619 | FTS | 25653 | 517 | 38 | 26 | 16 | 5 | 0 | 1 | 79
25-0078004 | Tuolumne | RACETRACK 1703 | RACETRACK 170311270 | 3rd Party | 2025-07-22 09:22 | -07:00 | 07/22 - 07/28 | 2025-07-22 12:42 | -07:00 | 200 | FTS | 67600 | 338 | 41 | 28 | 6 | 0 | 0 | 0 | 200
25-0077998 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113175566 | Animal | 2025-07-22 09:10 | -07:00 | 07/22 - 07/28 | 2025-07-22 12:45 | -07:00 | 76.4884 | FTS | 112132 | 1466 | 67 | 52 | 23 | 0 | 1 | 23 | 215
25-0078138 | Sonoma | LAKEVILLE 1102 | LAKEVILLE 1102677880 | Unknown Cause | 2025-07-22 11:59 | -07:00 | 07/22 - 07/28 | 2025-07-22 13:18 | -07:00 | 79 | FTS | 3713 | 47 | 3 | 3 | 4 | 0 | 0 | 0 | 79
25-0078061 | Tuolumne | PEORIA 1704 | PEORIA 17048040 | Unknown Cause | 2025-07-22 10:20 | -07:00 | 07/22 - 07/28 | 2025-07-22 15:46 | -07:00 | 326 | FTS | 43358 | 133 | 2 | 2 | 7 | 0 | 0 | 1 | 326
25-0078183 | Santa Clara | HICKS 2103 | HICKS 2103LB50 | Vegetation | 2025-07-22 13:11 | -07:00 | 07/22 - 07/28 | 2025-07-22 16:19 | -07:00 | 188 | FTS | 12784 | 68 | 1 | 0 | 2 | 0 | 0 | 1 | 188
25-0078239 | Plumas | GANSNER 1101 | GANSNER 110152664 | Animal | 2025-07-22 14:05 | -07:00 | 07/22 - 07/28 | 2025-07-22 16:24 | -07:00 | 115.7944 | FTS | 261927 | 2262 | 82 | 61 | 47 | 18 | 2 | 0 | 139
25-0077879 | Tuolumne | RACETRACK 1703 | RACETRACK 1703CB | Equipment Failure/Involved | 2025-07-21 23:05 | -07:00 | 07/22 - 07/28 | 2025-07-22 16:46 | -07:00 | 88.7328 | FTS | 276314 | 3114 | 263 | 203 | 62 | 16 | 2 | 0 | 1061
25-0078331 | Plumas | BIG MEADOWS 2101 | BIG MEADOWS 21012056 | Animal | 2025-07-22 17:08 | -07:00 | 07/22 - 07/28 | 2025-07-22 18:00 | -07:00 | 35.5846 | FTS | 26724 | 751 | 38 | 29 | 16 | 2 | 1 | 2 | 52
25-0078358 | Santa Cruz | CAMP EVERS 2105 | CAMP EVERS 210510728 | Unknown Cause | 2025-07-22 18:28 | -07:00 | 07/22 - 07/28 | 2025-07-22 19:35 | -07:00 | 59.6531 | FTS | 131535 | 2205 | 175 | 148 | 31 | 4 | 0 | 2 | 67
25-0078340 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113A08 | Animal | 2025-07-22 17:20 | -07:00 | 07/22 - 07/28 | 2025-07-22 20:01 | -07:00 | 85.205 | FTS | 88102 | 1034 | 50 | 43 | 19 | 0 | 0 | 21 | 161
25-0078246 | San Benito | HOLLISTER 2106 | HOLLISTER 2106281712 | Vegetation | 2025-07-22 14:14 | -07:00 | 07/22 - 07/28 | 2025-07-22 20:42 | -07:00 | 225.4912 | FTS | 12853 | 57 | 1 | 0 | 2 | 1 | 0 | 0 | 388
25-0078134 | Santa Cruz | BURNS 2101 | BURNS 210136516 | 3rd Party | 2025-07-22 11:51 | -07:00 | 07/22 - 07/28 | 2025-07-22 23:24 | -07:00 | 158.1548 | FTS | 62313 | 394 | 29 | 22 | 9 | 0 | 0 | 11 | 693
25-0078379 | Humboldt | WILLOW CREEK 1103 | WILLOW CREEK 11037514 | Vegetation | 2025-07-22 20:30 | -07:00 | 07/22 - 07/28 | 2025-07-23 05:11 | -07:00 | 411.6257 | FTS | 535525 | 1301 | 62 | 44 | 14 | 1 | 0 | 2 | 521
25-0078395 | Sonoma | FITCH MOUNTAIN 1113 | FITCH MOUNTAIN 1113154 | Unknown Cause | 2025-07-23 03:24 | -07:00 | 07/22 - 07/28 | 2025-07-23 07:35 | -07:00 | 128.5569 | FTS | 188593 | 1467 | 43 | 30 | 17 | 0 | 0 | 21 | 251
25-0078428 | Contra Costa | BRENTWOOD 2105 | BRENTWOOD 2105822252 | Animal | 2025-07-23 07:06 | -07:00 | 07/22 - 07/28 | 2025-07-23 07:53 | -07:00 | 47 | FTS | 47 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 47
25-0078399 | Kern | POSO MOUNTAIN 2104 | POSO MOUNTAIN 210448268 | Unknown Cause | 2025-07-23 05:15 | -07:00 | 07/22 - 07/28 | 2025-07-23 10:38 | -07:00 | 323 | FTS | 2907 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 323
25-0078400 | Sonoma | FITCH MOUNTAIN 1113 | FITCH MOUNTAIN 1113824468 | Unknown Cause | 2025-07-23 05:47 | -07:00 | 07/22 - 07/28 | 2025-07-23 10:49 | -07:00 | 302 | FTS | 161872 | 536 | 23 | 17 | 4 | 0 | 0 | 8 | 302
25-0078540 | Placer | PENRYN 1105 | PENRYN 1105196418 | Animal | 2025-07-23 09:57 | -07:00 | 07/22 - 07/28 | 2025-07-23 10:55 | -07:00 | 58 | FTS | 4582 | 79 | 7 | 4 | 1 | 0 | 0 | 4 | 58
25-0078559 | Butte | PARADISE 1105 | PARADISE 1105829194 | 3rd Party | 2025-07-23 10:22 | -07:00 | 07/22 - 07/28 | 2025-07-23 11:34 | -07:00 | 44.5447 | FTS | 11448 | 257 | 24 | 16 | 3 | 1 | 0 | 0 | 72
25-0078649 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113A20 | Company Initiated | 2025-07-23 12:26 | -07:00 | 07/22 - 07/28 | 2025-07-23 12:33 | -07:00 | 7 | FTS | 23121 | 3303 | 143 | 112 | 48 | 2 | 1 | 62 | 7
25-0078435 | Madera | COARSEGOLD 2103 | COARSEGOLD 2103731524 | Animal | 2025-07-23 07:27 | -07:00 | 07/22 - 07/28 | 2025-07-23 14:51 | -07:00 | 84.8989 | FTS | 68004 | 801 | 86 | 64 | 20 | 2 | 0 | 1 | 444
25-0078678 | Sonoma | FITCH MOUNTAIN 1113 | FITCH MOUNTAIN 1113824468 | Unknown Cause | 2025-07-23 13:09 | -07:00 | 07/22 - 07/28 | 2025-07-23 16:28 | -07:00 | 199 | FTS | 106863 | 537 | 23 | 17 | 4 | 0 | 0 | 8 | 199
25-0078855 | Mendocino | POTTER VALLEY P H 1105 | POTTER VALLEY P H 11051904 | Unknown Cause | 2025-07-23 16:58 | -07:00 | 07/22 - 07/28 | 2025-07-23 20:16 | -07:00 | 198 | FTS | 8118 | 41 | 1 | 1 | 0 | 0 | 0 | 1 | 198
25-0078884 | San Luis Obispo | TEMPLETON 2110 | TEMPLETON 2110901690 | Unknown Cause | 2025-07-23 18:17 | -07:00 | 07/22 - 07/28 | 2025-07-23 23:04 | -07:00 | 186.9123 | FTS | 53270 | 285 | 4 | 3 | 5 | 0 | 0 | 13 | 287
25-0078416 | Calaveras | PEORIA 1704 | PEORIA 170459596 | Equipment Failure/Involved | 2025-07-23 06:34 | -07:00 | 07/22 - 07/28 | 2025-07-24 02:01 | -07:00 | 314.8485 | FTS | 207800 | 660 | 47 | 33 | 24 | 0 | 0 | 1 | 1167
25-0078954 | Contra Costa | NORTH DUBLIN 2101 | NORTH DUBLIN 2101CB | Unknown Cause | 2025-07-24 02:42 | -07:00 | 07/22 - 07/28 | 2025-07-24 05:53 | -07:00 | 152.0305 | FTS | 828262 | 5448 | 92 | 70 | 20 | 2 | 0 | 0 | 191
25-0078953 | Shasta | COTTONWOOD 1101 | COTTONWOOD 1101384360 | Unknown Cause | 2025-07-24 02:59 | -07:00 | 07/22 - 07/28 | 2025-07-24 07:30 | -07:00 | 180.1786 | FTS | 170449 | 946 | 81 | 56 | 9 | 1 | 0 | 5 | 271
25-0078989 | Monterey | JOLON 1103 | JOLON 1103CB | 3rd Party | 2025-07-24 07:11 | -07:00 | 07/22 - 07/28 | 2025-07-24 08:06 | -07:00 | 55 | FTS | 1100 | 20 | 0 | 0 | 15 | 0 | 0 | 0 | 55
25-0079132 | Mariposa | MARIPOSA 2101 | MARIPOSA 210110215 | Company Initiated | 2025-07-24 10:44 | -07:00 | 07/22 - 07/28 | 2025-07-24 11:34 | -07:00 | 50 | FTS | 3350 | 67 | 8 | 6 | 5 | 0 | 0 | 0 | 50
25-0079152 | San Luis Obispo | TEMPLETON 2110 | TEMPLETON 2110901690 | Unknown Cause | 2025-07-24 11:46 | -07:00 | 07/22 - 07/28 | 2025-07-24 15:30 | -07:00 | 79.7053 | FTS | 22716 | 285 | 4 | 3 | 5 | 0 | 0 | 13 | 224
25-0079390 | Placer | PENRYN 1105 | PENRYN 110550550 | Unknown Cause | 2025-07-24 19:06 | -07:00 | 07/22 - 07/28 | 2025-07-24 21:12 | -07:00 | 126 | FTS | 34272 | 272 | 18 | 12 | 2 | 0 | 0 | 4 | 126
25-0079354 | Mendocino | COVELO 1101 | COVELO 1101562360 | Vegetation | 2025-07-24 16:37 | -07:00 | 07/22 - 07/28 | 2025-07-25 00:10 | -07:00 | 146.7353 | FTS | 74835 | 510 | 16 | 15 | 2 | 3 | 0 | 3 | 453
25-0079326 | Santa Barbara | BUELLTON 1101 | BUELLTON 1101Y06 | 3rd Party | 2025-07-24 15:55 | -07:00 | 07/22 - 07/28 | 2025-07-25 02:26 | -07:00 | 23.2894 | FTS | 60203 | 2585 | 41 | 30 | 50 | 6 | 0 | 3 | 631
25-0079396 | Kern | ANTELOPE 1101, ANTELOPE 1102 | ANTELOPE 1101CB | Equipment Failure/Involved | 2025-07-24 19:37 | -07:00 | 07/22 - 07/28 | 2025-07-25 02:47 | -07:00 | 430 | T-EPSS | 93310 | 217 | 0 | 0 | 12 | 0 | 0 | 0 | 430
25-0079397 | Kern | DEVILS DEN 1101, DEVILS DEN 1102 | DEVILS DEN 1101CB | Equipment Failure/Involved | 2025-07-24 19:37 | -07:00 | 07/22 - 07/28 | 2025-07-25 04:17 | -07:00 | 466.9685 | T-EPSS | 59305 | 127 | 0 | 0 | 11 | 0 | 0 | 0 | 520
25-0079442 | Placer | HALSEY 1102 | HALSEY 1102CB | Environmental/External | 2025-07-24 23:47 | -07:00 | 07/22 - 07/28 | 2025-07-25 04:31 | -07:00 | 284 | FTS | 18176 | 64 | 5 | 2 | 0 | 0 | 0 | 4 | 284
25-0079445 | Placer | BELL 1107 | BELL 110750172 | Animal | 2025-07-25 05:48 | -07:00 | 07/22 - 07/28 | 2025-07-25 07:05 | -07:00 | 77 | FTS | 26488 | 344 | 25 | 19 | 4 | 0 | 0 | 6 | 77
25-0079452 | Monterey | GABILAN 1101 | GABILAN 1101460414 | Animal | 2025-07-25 06:11 | -07:00 | 07/22 - 07/28 | 2025-07-25 07:42 | -07:00 | 91 | FTS | 3185 | 35 | 2 | 2 | 0 | 0 | 0 | 0 | 91
25-0079447 | Nevada | BRUNSWICK 1110 | BRUNSWICK 1110CB | Equipment Failure/Involved | 2025-07-25 05:55 | -07:00 | 07/22 - 07/28 | 2025-07-25 08:16 | -07:00 | 75.698 | FTS | 302565 | 3997 | 241 | 166 | 73 | 20 | 5 | 37 | 141
25-0079446 | San Luis Obispo | TEMPLETON 2111 | TEMPLETON 2111461692 | Animal | 2025-07-25 05:59 | -07:00 | 07/22 - 07/28 | 2025-07-25 08:18 | -07:00 | 70.7962 | FTS | 93097 | 1315 | 71 | 42 | 13 | 4 | 0 | 7 | 139
25-0079402 | Shasta | GIRVAN 1101 | GIRVAN 11011330 | Environmental/External | 2025-07-24 20:40 | -07:00 | 07/22 - 07/28 | 2025-07-25 08:26 | -07:00 | 128.7061 | FTS | 146725 | 1140 | 93 | 62 | 29 | 6 | 0 | 0 | 706
25-0073960 | Napa | SILVERADO 2103 | SILVERADO 2103CB | Equipment Failure/Involved | 2025-07-24 16:16 | -07:00 | 07/22 - 07/28 | 2025-07-25 08:27 | -07:00 | 111.6507 | FTS | 107408 | 962 | 10 | 5 | 13 | 1 | 0 | 2 | 971
25-0079404 | Shasta | JESSUP 1101 | JESSUP 110141356 | Environmental/External | 2025-07-24 20:57 | -07:00 | 07/22 - 07/28 | 2025-07-25 09:03 | -07:00 | 273.6447 | FTS | 95502 | 349 | 26 | 19 | 7 | 2 | 0 | 1 | 726
25-0079393 | Yuba | NARROWS 2101 | NARROWS 21011202 | Environmental/External | 2025-07-24 19:07 | -07:00 | 07/22 - 07/28 | 2025-07-25 09:45 | -07:00 | 530.2154 | FTS | 268289 | 506 | 47 | 31 | 2 | 0 | 0 | 9 | 878
25-0079459 | Nevada | SPAULDING 1101 | SPAULDING 1101578852 | 3rd Party | 2025-07-25 06:23 | -07:00 | 07/22 - 07/28 | 2025-07-25 09:53 | -07:00 | 210 | FTS | 35070 | 167 | 2 | 0 | 18 | 3 | 0 | 0 | 210
25-0079423 | Nevada | HIGGINS 1103 | HIGGINS 110350072 | Environmental/External | 2025-07-24 23:14 | -07:00 | 07/22 - 07/28 | 2025-07-25 10:35 | -07:00 | 481.5278 | FTS | 312030 | 648 | 37 | 26 | 3 | 0 | 0 | 21 | 681
25-0079539 | Placer | PENRYN 1103 | PENRYN 11032198 | Equipment Failure/Involved | 2025-07-25 09:37 | -07:00 | 07/22 - 07/28 | 2025-07-25 11:24 | -07:00 | 107 | FTS | 49220 | 460 | 27 | 17 | 5 | 0 | 0 | 17 | 107
25-0079431 | Placer | PENRYN 1105 | PENRYN 1105680290 | Environmental/External | 2025-07-25 00:16 | -07:00 | 07/22 - 07/28 | 2025-07-25 11:38 | -07:00 | 92.5116 | FTS | 35987 | 389 | 23 | 11 | 3 | 0 | 0 | 7 | 682
25-0079430 | Sonoma | PENNGROVE 1101 | PENNGROVE 1101950828 | Unknown Cause | 2025-07-25 00:17 | -07:00 | 07/22 - 07/28 | 2025-07-25 12:55 | -07:00 | 758 | FTS | 197838 | 261 | 10 | 5 | 3 | 0 | 0 | 9 | 758
25-0079395 | San Luis Obispo | CHOLAME 1101, CHOLAME 2102 | CHOLAME 2102CB | Equipment Failure/Involved | 2025-07-24 19:37 | -07:00 | 07/22 - 07/28 | 2025-07-25 13:00 | -07:00 | 937.8936 | T-EPSS | 1480934 | 1579 | 39 | 27 | 39 | 6 | 0 | 0 | 1043
25-0079605 | Merced | WILSON 1103 | WILSON 1103291366 | 3rd Party | 2025-07-25 11:05 | -07:00 | 07/22 - 07/28 | 2025-07-25 14:40 | -07:00 | 94.7857 | HLT | 7962 | 84 | 1 | 0 | 0 | 0 | 0 | 0 | 215
25-0071957 | Sonoma | MONROE 2103 | MONROE 210392868 | Company Initiated | 2025-07-25 15:08 | -07:00 | 07/22 - 07/28 | 2025-07-25 15:23 | -07:00 | 15 | FTS | 40680 | 2712 | 0 | 0 | 1 | 0 | 0 | 0 | 15
25-0079810 | Butte | ORO FINO 1102 | ORO FINO 110239154 | Environmental/External | 2025-07-25 16:39 | -07:00 | 07/22 - 07/28 | 2025-07-25 18:09 | -07:00 | 90 | FTS | 28350 | 315 | 15 | 10 | 3 | 0 | 0 | 0 | 90
25-0079833 | Shasta | PIT NO 3 2101 | PIT NO 3 21011480 | Environmental/External | 2025-07-25 18:29 | -07:00 | 07/22 - 07/28 | 2025-07-25 19:38 | -07:00 | 68.4453 | FTS | 8761 | 128 | 5 | 5 | 2 | 0 | 0 | 0 | 69
25-0079845 | Shasta | CEDAR CREEK 1101 | CEDAR CREEK 1101CB | Environmental/External | 2025-07-25 20:04 | -07:00 | 07/22 - 07/28 | 2025-07-25 21:10 | -07:00 | 66 | FTS | 2178 | 33 | 3 | 0 | 0 | 0 | 0 | 1 | 66
25-0079760 | San Luis Obispo | TEMPLETON 2110 | TEMPLETON 2110901690 | Vegetation | 2025-07-25 15:10 | -07:00 | 07/22 - 07/28 | 2025-07-25 22:33 | -07:00 | 107.7404 | FTS | 30706 | 285 | 4 | 3 | 5 | 0 | 0 | 13 | 443
25-0079836 | Shasta | BURNEY 1101 | BURNEY 11011322 | Environmental/External | 2025-07-25 18:51 | -07:00 | 07/22 - 07/28 | 2025-07-26 00:59 | -07:00 | 368 | FTS | 25024 | 68 | 4 | 4 | 0 | 0 | 0 | 0 | 368
25-0079841 | Shasta | CEDAR CREEK 1101 | CEDAR CREEK 11011664 | Environmental/External | 2025-07-25 19:34 | -07:00 | 07/22 - 07/28 | 2025-07-26 08:35 | -07:00 | 61.5519 | FTS | 29668 | 482 | 29 | 20 | 11 | 1 | 0 | 1 | 781
25-0079883 | Monterey | OILFIELDS 1103 | OILFIELDS 1103N42 | Unknown Cause | 2025-07-26 07:10 | -07:00 | 07/22 - 07/28 | 2025-07-26 09:18 | -07:00 | 122.8376 | FTS | 285966 | 2328 | 97 | 69 | 43 | 2 | 0 | 16 | 128
25-0074836 | Solano | VACAVILLE 1108 | VACAVILLE 1108530880 | Company Initiated | 2025-07-26 10:00 | -07:00 | 07/22 - 07/28 | 2025-07-26 10:08 | -07:00 | 8 | HLT | 1584 | 198 | 12 | 10 | 3 | 0 | 0 | 2 | 8
25-0079942 | Humboldt | GARBERVILLE 1101 | GARBERVILLE 11011617 | Company Initiated | 2025-07-26 11:12 | -07:00 | 07/22 - 07/28 | 2025-07-26 11:45 | -07:00 | 56.9831 | FTS | 3362 | 59 | 0 | 0 | 1 | 3 | 0 | 0 | 33
25-0079862 | San Luis Obispo | SANTA MARIA 1108 | SANTA MARIA 1108M18 | Unknown Cause | 2025-07-26 04:33 | -07:00 | 07/22 - 07/28 | 2025-07-26 12:17 | -07:00 | 404.3586 | FTS | 181557 | 449 | 16 | 16 | 4 | 0 | 0 | 20 | 464
25-0079931 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113A70 | Unknown Cause | 2025-07-26 09:45 | -07:00 | 07/22 - 07/28 | 2025-07-26 13:38 | -07:00 | 84.1287 | FTS | 144449 | 1717 | 71 | 54 | 19 | 2 | 0 | 34 | 233
25-0079969 | Mariposa | MARIPOSA 2101 | MARIPOSA 210110215 | Company Initiated | 2025-07-26 13:27 | -07:00 | 07/22 - 07/28 | 2025-07-26 13:48 | -07:00 | 21 | FTS | 1722 | 82 | 10 | 8 | 5 | 0 | 0 | 0 | 21
25-0079993 | Lassen | MC ARTHUR 1101 | MC ARTHUR 11011544 | 3rd Party | 2025-07-26 15:58 | -07:00 | 07/22 - 07/28 | 2025-07-26 17:22 | -07:00 | 69.6978 | FTS | 25370 | 364 | 14 | 10 | 20 | 3 | 0 | 0 | 84
25-0080008 | Sonoma | MIRABEL 1101 | MIRABEL 1101254 | Animal | 2025-07-26 19:10 | -07:00 | 07/22 - 07/28 | 2025-07-26 20:29 | -07:00 | 47.348 | FTS | 28030 | 592 | 24 | 22 | 8 | 1 | 0 | 6 | 79
25-0080019 | Amador | OLETA 1101 | OLETA 1101239062 | Unknown Cause | 2025-07-26 20:34 | -07:00 | 07/22 - 07/28 | 2025-07-26 22:57 | -07:00 | 143 | FTS | 10725 | 75 | 6 | 2 | 1 | 0 | 0 | 5 | 143
25-0070412 | Tuolumne | PEORIA 1705 | PEORIA 170567898 | Company Initiated | 2025-07-26 23:49 | -07:00 | 07/22 - 07/28 | 2025-07-27 00:49 | -07:00 | 60 | FTS | 123660 | 2061 | 164 | 132 | 16 | 0 | 0 | 8 | 60
25-0080020 | Napa | PUEBLO 2103 | PUEBLO 210398394 | Equipment Failure/Involved | 2025-07-27 01:17 | -07:00 | 07/22 - 07/28 | 2025-07-27 01:36 | -07:00 | 19 | FTS | 29811 | 1569 | 96 | 70 | 16 | 1 | 0 | 1 | 19
25-0080012 | Amador | OLETA 1101 | OLETA 1101239062 | Unknown Cause | 2025-07-26 20:34 | -07:00 | 07/22 - 07/28 | 2025-07-27 07:26 | -07:00 | 181.6959 | FTS | 31070 | 171 | 7 | 3 | 2 | 0 | 0 | 1 | 652
25-0080025 | Monterey | GABILAN 1101 | GABILAN 1101460414 | Unknown Cause | 2025-07-27 06:03 | -07:00 | 07/22 - 07/28 | 2025-07-27 07:37 | -07:00 | 94 | FTS | 3290 | 35 | 2 | 2 | 0 | 0 | 0 | 0 | 94
25-0079990 | Monterey | RESERVATION ROAD 1101 | RESERVATION ROAD 1101383718 | 3rd Party | 2025-07-26 15:20 | -07:00 | 07/22 - 07/28 | 2025-07-27 07:50 | -07:00 | 331.0732 | FTS | 235062 | 710 | 52 | 37 | 17 | 2 | 0 | 2 | 990
25-0080049 | Santa Clara | HICKS 1116 | HICKS 1116983580 | Equipment Failure/Involved | 2025-07-27 10:21 | -07:00 | 07/22 - 07/28 | 2025-07-27 12:07 | -07:00 | 95.047 | FTS | 14162 | 149 | 4 | 3 | 2 | 0 | 0 | 0 | 106
25-0080054 | Plumas | HAMILTON BRANCH 1101 | HAMILTON BRANCH 110190334 | Animal | 2025-07-27 10:58 | -07:00 | 07/22 - 07/28 | 2025-07-27 13:44 | -07:00 | 66.9709 | FTS | 6898 | 103 | 6 | 4 | 4 | 0 | 0 | 0 | 166
25-0080028 | Calaveras | STANISLAUS 1701 | STANISLAUS 170179826 | Company Initiated | 2025-07-27 07:30 | -07:00 | 07/22 - 07/28 | 2025-07-27 13:56 | -07:00 | 59.3229 | FTS | 13229 | 223 | 12 | 10 | 3 | 0 | 0 | 0 | 386
25-0080061 | Madera | COARSEGOLD 2104 | COARSEGOLD 2104905960 | Animal | 2025-07-27 12:12 | -07:00 | 07/22 - 07/28 | 2025-07-27 15:02 | -07:00 | 134.0644 | FTS | 386910 | 2886 | 221 | 163 | 56 | 8 | 0 | 4 | 170
25-0080032 | Trinity | LOW GAP 1101 | LOW GAP 1101CB | 3rd Party | 2025-07-27 08:39 | -07:00 | 07/22 - 07/28 | 2025-07-27 21:11 | -07:00 | 460.4451 | FTS | 335204 | 728 | 29 | 19 | 12 | 3 | 0 | 0 | 752
25-0080095 | Shasta | JESSUP 1101 | JESSUP 110168362 | 3rd Party | 2025-07-27 21:43 | -07:00 | 07/22 - 07/28 | 2025-07-28 04:51 | -07:00 | 58.3615 | FTS | 89118 | 1527 | 159 | 124 | 17 | 3 | 0 | 1 | 428
25-0080127 | Shasta | VOLTA 1101 | VOLTA 1101519282 | 3rd Party | 2025-07-28 07:27 | -07:00 | 07/22 - 07/28 | 2025-07-28 07:34 | -07:00 | 7 | FTS | 7 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 7
25-0080118 | Sonoma | SANTA ROSA A 1111 | SANTA ROSA A 1111758024 | Unknown Cause | 2025-07-28 06:30 | -07:00 | 07/22 - 07/28 | 2025-07-28 08:44 | -07:00 | 134 | FTS | 12194 | 91 | 7 | 7 | 1 | 0 | 0 | 2 | 134
25-0080151 | Monterey | JOLON 1103 | JOLON 1103549180 | Unknown Cause | 2025-07-28 06:03 | -07:00 | 07/22 - 07/28 | 2025-07-28 09:40 | -07:00 | 217 | FTS | 651 | 3 | 0 | 0 | 2 | 0 | 0 | 0 | 217
25-0080112 | El Dorado | DIAMOND SPRINGS 1106 | DIAMOND SPRINGS 1106803034 | Unknown Cause | 2025-07-28 04:12 | -07:00 | 07/22 - 07/28 | 2025-07-28 13:56 | -07:00 | 441.9324 | FTS | 542251 | 1227 | 101 | 72 | 12 | 0 | 0 | 31 | 584
25-0080120 | Nevada | BRUNSWICK 1105 | BRUNSWICK 11052130 | Animal | 2025-07-28 06:40 | -07:00 | 07/22 - 07/28 | 2025-07-28 14:09 | -07:00 | 77.9904 | FTS | 16222 | 208 | 10 | 7 | 7 | 0 | 0 | 8 | 449
25-0080334 | Napa | PUEBLO 2102 | PUEBLO 2102378860 | 3rd Party | 2025-07-28 12:24 | -07:00 | 07/22 - 07/28 | 2025-07-28 14:34 | -07:00 | 130 | FTS | 23140 | 178 | 3 | 1 | 3 | 1 | 0 | 2 | 130
25-0080366 | Amador | PINE GROVE 1102 | PINE GROVE 11021222 | Equipment Failure/Involved | 2025-07-28 13:19 | -07:00 | 07/22 - 07/28 | 2025-07-28 14:59 | -07:00 | 100 | FTS | 131700 | 1317 | 104 | 77 | 25 | 0 | 0 | 1 | 100
25-0080465 | Fresno | SAND CREEK 1103 | SAND CREEK 1103818064 | Unknown Cause | 2025-07-28 15:30 | -07:00 | 07/22 - 07/28 | 2025-07-28 17:46 | -07:00 | 136 | FTS | 71128 | 523 | 51 | 33 | 5 | 0 | 0 | 1 | 136
25-0080515 | Marin | SAN RAFAEL 1107 | SAN RAFAEL 1107CB | Equipment Failure/Involved | 2025-07-28 17:01 | -07:00 | 07/22 - 07/28 | 2025-07-28 17:58 | -07:00 | 56.6154 | FTS | 263205 | 4649 | 141 | 95 | 58 | 10 | 0 | 4 | 57
25-0080186 | Lake | HIGHLANDS 1104 | HIGHLANDS 110439458 | Equipment Failure/Involved | 2025-07-28 09:22 | -07:00 | 07/22 - 07/28 | 2025-07-28 18:02 | -07:00 | 94.5952 | FTS | 54676 | 578 | 71 | 59 | 8 | 2 | 0 | 0 | 520
25-0080548 | Placer | PLACER 1103 | PLACER 1103284874 | Animal | 2025-07-28 20:46 | -07:00 | 07/22 - 07/28 | 2025-07-28 23:35 | -07:00 | 169 | FTS | 27885 | 165 | 11 | 5 | 3 | 0 | 0 | 0 | 169
25-0080300 | San Mateo | WOODSIDE 1101 | WOODSIDE 110179892 | Vegetation | 2025-07-28 12:09 | -07:00 | 07/29 - 08/04 | 2025-07-29 07:55 | -07:00 | 979.7149 | FTS | 223375 | 228 | 6 | 3 | 4 | 2 | 0 | 0 | 1186
25-0080604 | Napa | TULUCAY 1101 | TULUCAY 1101504524 | Unknown Cause | 2025-07-29 08:12 | -07:00 | 07/29 - 08/04 | 2025-07-29 08:58 | -07:00 | 46 | FTS | 552 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 46
25-0080658 | Santa Clara | MENLO 1103 | MENLO 1103866118 | Company Initiated | 2025-07-29 09:10 | -07:00 | 07/29 - 08/04 | 2025-07-29 10:12 | -07:00 | 59.9259 | FTS | 24270 | 405 | 18 | 14 | 18 | 0 | 0 | 9 | 62
25-0080793 | Trinity | WILDWOOD 1101 | WILDWOOD 11011576 | Unknown Cause | 2025-07-29 12:51 | -07:00 | 07/29 - 08/04 | 2025-07-29 15:43 | -07:00 | 172 | FTS | 14104 | 82 | 3 | 1 | 6 | 1 | 0 | 0 | 172
25-0080992 | Tuolumne | CURTIS 1703 | CURTIS 17031949 | Company Initiated | 2025-07-29 19:25 | -07:00 | 07/29 - 08/04 | 2025-07-29 19:57 | -07:00 | 32 | FTS | 3872 | 121 | 6 | 5 | 1 | 0 | 0 | 0 | 32
25-0081005 | Merced | SANTA NELLA 1104 | SANTA NELLA 11049660 | Unknown Cause | 2025-07-29 21:15 | -07:00 | 07/29 - 08/04 | 2025-07-29 23:35 | -07:00 | 129 | HLT | 9288 | 72 | 1 | 0 | 1 | 0 | 0 | 0 | 140
25-0080807 | Alameda | SUNOL 1101 | SUNOL 1101605520 | Equipment Failure/Involved | 2025-07-29 12:45 | -07:00 | 07/29 - 08/04 | 2025-07-30 03:43 | -07:00 | 317.8298 | FTS | 29876 | 94 | 4 | 1 | 1 | 0 | 0 | 0 | 898
25-0081030 | Calaveras | SALT SPRINGS 2102 | SALT SPRINGS 21023118 | Environmental/External | 2025-07-30 03:59 | -07:00 | 07/29 - 08/04 | 2025-07-30 05:38 | -07:00 | 99 | FTS | 199782 | 2018 | 46 | 34 | 35 | 0 | 0 | 0 | 99
25-0081032 | Calaveras | STANISLAUS 1701 | STANISLAUS 170179826 | Company Initiated | 2025-07-30 04:48 | -07:00 | 07/29 - 08/04 | 2025-07-30 06:07 | -07:00 | 79 | FTS | 11139 | 141 | 7 | 6 | 3 | 0 | 0 | 0 | 79
25-0081028 | Monterey | RESERVATION ROAD 1101 | RESERVATION ROAD 1101383718 | Unknown Cause | 2025-07-30 02:56 | -07:00 | 07/29 - 08/04 | 2025-07-30 06:25 | -07:00 | 82.4471 | FTS | 58455 | 709 | 52 | 37 | 17 | 2 | 0 | 2 | 209
25-0081094 | Sonoma | ANNAPOLIS 1101 | ANNAPOLIS 110176842 | Company Initiated | 2025-07-30 08:15 | -07:00 | 07/29 - 08/04 | 2025-07-30 08:24 | -07:00 | 9 | FTS | 135 | 15 | 0 | 0 | 1 | 0 | 0 | 0 | 9
25-0081042 | Butte | ORO FINO 1102 | ORO FINO 11022236 | Animal | 2025-07-30 06:17 | -07:00 | 07/29 - 08/04 | 2025-07-30 08:52 | -07:00 | 151.0056 | FTS | 163086 | 1080 | 84 | 53 | 10 | 1 | 0 | 3 | 155
25-0080997 | Marin | SAN RAFAEL 1104 | SAN RAFAEL 1104CB | Unknown Cause | 2025-07-29 20:24 | -07:00 | 07/29 - 08/04 | 2025-07-30 09:21 | -07:00 | 399.2785 | FTS | 1797552 | 4502 | 130 | 82 | 39 | 10 | 0 | 0 | 777
25-0081033 | Calaveras | STANISLAUS 1702 | STANISLAUS 17021850 | Environmental/External | 2025-07-30 04:49 | -07:00 | 07/29 - 08/04 | 2025-07-30 10:54 | -07:00 | 175.6313 | FTS | 428189 | 2438 | 80 | 62 | 27 | 3 | 2 | 0 | 365
25-0081029 | Mendocino | PHILO 1101 | PHILO 11013700 | Equipment Failure/Involved | 2025-07-30 03:59 | -07:00 | 07/29 - 08/04 | 2025-07-30 11:41 | -07:00 | 171.2957 | FTS | 134981 | 788 | 23 | 18 | 19 | 4 | 0 | 1 | 462
25-0081399 | Sonoma | ANNAPOLIS 1101 | ANNAPOLIS 1101202158 | Unknown Cause | 2025-07-30 14:48 | -07:00 | 07/29 - 08/04 | 2025-07-30 18:35 | -07:00 | 227 | FTS | 12939 | 57 | 1 | 1 | 8 | 1 | 0 | 0 | 227
25-0081503 | Nevada | NARROWS 2102 | NARROWS 2102960916 | Unknown Cause | 2025-07-30 19:21 | -07:00 | 07/29 - 08/04 | 2025-07-30 21:22 | -07:00 | 86.8686 | FTS | 78008 | 898 | 49 | 29 | 18 | 5 | 0 | 26 | 121
25-0081533 | Butte | SYCAMORE CREEK 1111 | SYCAMORE CREEK 11112602 | 3rd Party | 2025-07-31 05:13 | -07:00 | 07/29 - 08/04 | 2025-07-31 07:46 | -07:00 | 105.125 | FTS | 5046 | 48 | 0 | 0 | 9 | 0 | 0 | 0 | 153
25-0081550 | Sonoma | FITCH MOUNTAIN 1113 | FITCH MOUNTAIN 1113775992 | Unknown Cause | 2025-07-31 06:42 | -07:00 | 07/29 - 08/04 | 2025-07-31 08:22 | -07:00 | 93.7255 | FTS | 33460 | 357 | 7 | 4 | 1 | 0 | 0 | 4 | 100
25-0081585 | San Luis Obispo | SAN LUIS OBISPO 1103 | SAN LUIS OBISPO 1103V82 | Company Initiated | 2025-07-31 08:31 | -07:00 | 07/29 - 08/04 | 2025-07-31 08:44 | -07:00 | 13 | FTS | 14937 | 1149 | 39 | 32 | 23 | 1 | 0 | 15 | 13
25-0081532 | Contra Costa | FRANKLIN 1104 | FRANKLIN 1104P136 | Unknown Cause | 2025-07-31 04:47 | -07:00 | 07/29 - 08/04 | 2025-07-31 09:53 | -07:00 | 306 | FTS | 24786 | 81 | 1 | 1 | 8 | 1 | 0 | 0 | 306
25-0081506 | San Luis Obispo | MESA 1101 | MESA 1101M86 | Unknown Cause | 2025-07-30 19:52 | -07:00 | 07/29 - 08/04 | 2025-07-31 11:10 | -07:00 | 210.4724 | FTS | 160380 | 762 | 31 | 18 | 14 | 3 | 0 | 22 | 918
25-0081662 | Sonoma | ANNAPOLIS 1101 | ANNAPOLIS 1101202158 | Unknown Cause | 2025-07-31 10:09 | -07:00 | 07/29 - 08/04 | 2025-07-31 12:47 | -07:00 | 158 | FTS | 9006 | 57 | 1 | 1 | 8 | 1 | 0 | 0 | 158
25-0081853 | Santa Clara | HICKS 2101 | HICKS 2101257172 | Company Initiated | 2025-07-31 14:14 | -07:00 | 07/29 - 08/04 | 2025-07-31 14:23 | -07:00 | 9 | FTS | 1395 | 155 | 3 | 1 | 3 | 0 | 0 | 0 | 9
25-0081810 | Monterey | KING CITY 1104 | JOLON 11027070 | Company Initiated | 2025-07-31 13:39 | -07:00 | 07/29 - 08/04 | 2025-07-31 14:41 | -07:00 | 62 | FTS | 16058 | 259 | 4 | 4 | 19 | 0 | 0 | 4 | 62
25-0081667 | Santa Clara | MC KEE 1111 | MC KEE 1111711900 | Company Initiated | 2025-07-31 10:11 | -07:00 | 07/29 - 08/04 | 2025-07-31 15:28 | -07:00 | 208.1731 | FTS | 123863 | 595 | 30 | 17 | 7 | 0 | 0 | 0 | 317
25-0081943 | Contra Costa | RESEARCH 2102 | RESEARCH 210263274 | Vegetation | 2025-07-31 16:21 | -07:00 | 07/29 - 08/04 | 2025-07-31 22:42 | -07:00 | 77.75 | FTS | 105118 | 1352 | 66 | 51 | 21 | 7 | 0 | 0 | 381
25-0081990 | Marin | STAFFORD 1102 | STAFFORD 11021202 | Unknown Cause | 2025-07-31 22:04 | -07:00 | 07/29 - 08/04 | 2025-07-31 23:33 | -07:00 | 89 | FTS | 4717 | 53 | 1 | 1 | 1 | 0 | 0 | 0 | 89
25-0081993 | Stanislaus | NEWMAN 1105 | NEWMAN 110590430 | Unknown Cause | 2025-07-31 23:04 | -07:00 | 07/29 - 08/04 | 2025-08-01 03:52 | -07:00 | 288 | FTS | 50688 | 176 | 4 | 3 | 3 | 0 | 0 | 0 | 288
25-0081977 | Fresno | SAND CREEK 1103 | SAND CREEK 11037140 | 3rd Party | 2025-07-31 18:52 | -07:00 | 07/29 - 08/04 | 2025-08-01 06:01 | -07:00 | 471.0044 | FTS | 213836 | 454 | 49 | 35 | 3 | 0 | 0 | 1 | 669
25-0082043 | Santa Cruz | POINT MORETTI 1101 | POINT MORETTI 110135874 | Company Initiated | 2025-08-01 07:43 | -07:00 | 07/29 - 08/04 | 2025-08-01 08:06 | -07:00 | 18.7236 | FTS | 15447 | 825 | 39 | 29 | 43 | 16 | 0 | 20 | 23
25-0082037 | San Luis Obispo | TEMPLETON 2110 | TEMPLETON 2110R94 | Animal | 2025-08-01 07:37 | -07:00 | 07/29 - 08/04 | 2025-08-01 12:54 | -07:00 | 93.2162 | FTS | 17245 | 185 | 5 | 5 | 0 | 0 | 0 | 2 | 317
25-0082257 | Monterey | KING CITY 1104 | JOLON 11027070 | Company Initiated | 2025-08-01 13:52 | -07:00 | 07/29 - 08/04 | 2025-08-01 16:30 | -07:00 | 158 | FTS | 40922 | 259 | 4 | 4 | 19 | 0 | 0 | 4 | 158
25-0082372 | Humboldt | HOOPA 1101 | HOOPA 110193038 | Unknown Cause | 2025-08-01 20:14 | -07:00 | 07/29 - 08/04 | 2025-08-01 22:00 | -07:00 | 106 | FTS | 10494 | 99 | 2 | 2 | 11 | 11 | 0 | 0 | 106
25-0082007 | Contra Costa | RESEARCH 2102 | RESEARCH 210263274 | Equipment Failure/Involved | 2025-08-01 02:08 | -07:00 | 07/29 - 08/04 | 2025-08-02 00:02 | -07:00 | 301.427 | FTS | 421395 | 1398 | 67 | 51 | 21 | 7 | 0 | 0 | 1314
25-0082391 | Sonoma | MONTE RIO 1113 | MONTE RIO 1113524 | Vegetation | 2025-08-02 00:58 | -07:00 | 07/29 - 08/04 | 2025-08-02 08:31 | -07:00 | 99.8248 | FTS | 101422 | 1016 | 50 | 36 | 15 | 0 | 0 | 0 | 453
25-0082397 | Santa Clara | LLAGAS 2101 | LLAGAS 2101XR586 | Unknown Cause | 2025-08-02 02:53 | -07:00 | 07/29 - 08/04 | 2025-08-02 08:47 | -07:00 | 354 | FTS | 20178 | 57 | 1 | 1 | 3 | 0 | 0 | 2 | 354
25-0082268 | Placer | PLACER 1102 | PLACER 1102CB | 3rd Party | 2025-08-01 14:13 | -07:00 | 07/29 - 08/04 | 2025-08-02 09:34 | -07:00 | 191.4617 | FTS | 852196 | 4451 | 294 | 210 | 53 | 5 | 0 | 67 | 1161
25-0082469 | Santa Cruz | POINT MORETTI 1101 | POINT MORETTI 110135874 | Unknown Cause | 2025-08-02 13:38 | -07:00 | 07/29 - 08/04 | 2025-08-02 14:24 | -07:00 | 46 | FTS | 32982 | 717 | 32 | 25 | 41 | 16 | 0 | 18 | 46
25-0082451 | Santa Cruz | POINT MORETTI 1101 | POINT MORETTI 11015078 | Unknown Cause | 2025-08-02 11:53 | -07:00 | 07/29 - 08/04 | 2025-08-02 14:29 | -07:00 | 156 | FTS | 16848 | 108 | 7 | 4 | 2 | 0 | 0 | 2 | 156
25-0082487 | Santa Clara | LLAGAS 2101 | LLAGAS 2101XR244 | 3rd Party | 2025-08-02 15:00 | -07:00 | 07/29 - 08/04 | 2025-08-02 17:21 | -07:00 | 139.0465 | FTS | 140576 | 1011 | 34 | 20 | 16 | 2 | 0 | 8 | 141
25-0082442 | San Luis Obispo | TEMPLETON 2110 | TEMPLETON 2110317796 | Vegetation | 2025-08-02 11:39 | -07:00 | 07/29 - 08/04 | 2025-08-02 17:40 | -07:00 | 117.1664 | FTS | 171766 | 1466 | 43 | 31 | 20 | 0 | 0 | 34 | 361
25-0082364 | Shasta | MC ARTHUR 1101 | MC ARTHUR 110138998 | Vegetation | 2025-08-01 18:21 | -07:00 | 07/29 - 08/04 | 2025-08-02 18:12 | -07:00 | 447.2984 | FTS | 337263 | 754 | 31 | 21 | 23 | 3 | 0 | 0 | 1431
25-0082507 | Solano | JAMESON 1102 | JAMESON 1102865502 | Unknown Cause | 2025-08-02 17:56 | -07:00 | 07/29 - 08/04 | 2025-08-02 18:54 | -07:00 | 58 | FTS | 1566 | 27 | 1 | 1 | 1 | 0 | 0 | 0 | 58
25-0082512 | Humboldt | HOOPA 1101 | HOOPA 110193038 | Unknown Cause | 2025-08-02 19:03 | -07:00 | 07/29 - 08/04 | 2025-08-02 20:30 | -07:00 | 87 | FTS | 8613 | 99 | 2 | 2 | 11 | 11 | 0 | 0 | 87
25-0082514 | Santa Clara | MORGAN HILL 2105 | MORGAN HILL 2105XR176 | 3rd Party | 2025-08-02 19:13 | -07:00 | 07/29 - 08/04 | 2025-08-02 22:22 | -07:00 | 61.2525 | FTS | 67684 | 1105 | 52 | 44 | 16 | 3 | 0 | 10 | 189
25-0082521 | Plumas | BIG MEADOWS 2101 | BIG MEADOWS 21012056 | Unknown Cause | 2025-08-02 21:55 | -07:00 | 07/29 - 08/04 | 2025-08-03 01:36 | -07:00 | 78.9707 | FTS | 59307 | 751 | 39 | 30 | 16 | 2 | 1 | 2 | 221
25-0082528 | Calaveras | CORRAL 1101 | CORRAL 110112612 | Animal | 2025-08-02 22:55 | -07:00 | 07/29 - 08/04 | 2025-08-03 01:46 | -07:00 | 171 | FTS | 56088 | 328 | 16 | 12 | 8 | 0 | 0 | 0 | 171
25-0082530 | Napa | PUEBLO 2104 | PUEBLO 2104741958 | Unknown Cause | 2025-08-02 23:32 | -07:00 | 07/29 - 08/04 | 2025-08-03 02:16 | -07:00 | 164 | FTS | 117096 | 714 | 18 | 10 | 6 | 0 | 0 | 0 | 164
25-0082471 | Shasta | DESCHUTES 1104 | DESCHUTES 1104622260 | Equipment Failure/Involved | 2025-08-02 13:15 | -07:00 | 07/29 - 08/04 | 2025-08-03 04:31 | -07:00 | 142.24 | FTS | 17780 | 125 | 8 | 7 | 1 | 0 | 0 | 0 | 916
25-0082532 | Nevada | BRUNSWICK 1104 | BRUNSWICK 11041020 | Vegetation | 2025-08-02 23:36 | -07:00 | 07/29 - 08/04 | 2025-08-03 06:20 | -07:00 | 264.5738 | FTS | 129112 | 488 | 21 | 15 | 4 | 0 | 0 | 16 | 404
25-0082537 | Tuolumne | CURTIS 1702 | CURTIS 17026008 | Equipment Failure/Involved | 2025-08-03 01:57 | -07:00 | 07/29 - 08/04 | 2025-08-03 06:47 | -07:00 | 270.125 | FTS | 155592 | 576 | 61 | 45 | 3 | 4 | 0 | 5 | 290
25-0082540 | El Dorado | SHINGLE SPRINGS 2109 | SHINGLE SPRINGS 210913322 | Animal | 2025-08-03 05:47 | -07:00 | 07/29 - 08/04 | 2025-08-03 08:17 | -07:00 | 150 | FTS | 97650 | 651 | 58 | 40 | 4 | 0 | 0 | 10 | 150
25-0082552 | San Mateo | SAN CARLOS 1103 | SAN CARLOS 1103586832 | Unknown Cause | 2025-08-03 08:00 | -07:00 | 07/29 - 08/04 | 2025-08-03 09:57 | -07:00 | 117 | FTS | 52767 | 451 | 14 | 11 | 12 | 0 | 0 | 0 | 117
25-0082566 | Nevada | BRUNSWICK 1105 | BRUNSWICK 11052130 | Animal | 2025-08-03 09:26 | -07:00 | 07/29 - 08/04 | 2025-08-03 11:03 | -07:00 | 75.0486 | FTS | 81878 | 1091 | 59 | 40 | 24 | 0 | 0 | 12 | 97
25-0082589 | Napa | SILVERADO 2105 | SILVERADO 2105861266 | Unknown Cause | 2025-08-03 13:15 | -07:00 | 07/29 - 08/04 | 2025-08-03 15:11 | -07:00 | 116 | FTS | 6380 | 55 | 1 | 1 | 0 | 0 | 0 | 1 | 116
25-0082588 | Santa Barbara | SISQUOC 1102 | SISQUOC 1102M26 | 3rd Party | 2025-08-03 13:04 | -07:00 | 07/29 - 08/04 | 2025-08-03 15:35 | -07:00 | 151 | FTS | 38203 | 253 | 3 | 2 | 2 | 0 | 0 | 0 | 151
25-0082593 | Lake | REDBUD 1102 | REDBUD 1102922 | Unknown Cause | 2025-08-03 13:58 | -07:00 | 07/29 - 08/04 | 2025-08-03 16:41 | -07:00 | 163 | FTS | 54768 | 336 | 19 | 13 | 5 | 0 | 1 | 2 | 163
25-0082600 | Fresno | SAND CREEK 1103 | SAND CREEK 11037140 | Animal | 2025-08-03 15:12 | -07:00 | 07/29 - 08/04 | 2025-08-03 18:53 | -07:00 | 194.3392 | FTS | 88230 | 454 | 49 | 35 | 3 | 0 | 0 | 1 | 221
25-0082573 | San Luis Obispo | SAN LUIS OBISPO 1107 | SAN LUIS OBISPO 1107CB | 3rd Party | 2025-08-03 10:20 | -07:00 | 07/29 - 08/04 | 2025-08-03 22:07 | -07:00 | 75.3736 | FTS | 192655 | 2556 | 53 | 44 | 47 | 4 | 0 | 52 | 707
25-0082654 | Mariposa | MARIPOSA 2102 | MARIPOSA 2102851902 | Equipment Failure/Involved | 2025-08-04 06:52 | -07:00 | 07/29 - 08/04 | 2025-08-04 09:19 | -07:00 | 146.2751 | FTS | 395089 | 2701 | 145 | 102 | 40 | 6 | 0 | 8 | 147
25-0082655 | San Mateo | WOODSIDE 1101 | WOODSIDE 110179892 | Animal | 2025-08-04 07:12 | -07:00 | 07/29 - 08/04 | 2025-08-04 09:31 | -07:00 | 139 | FTS | 31692 | 228 | 6 | 3 | 4 | 2 | 0 | 0 | 139
25-0082669 | Shasta | OREGON TRAIL 1102 | OREGON TRAIL 1102CB | Unknown Cause | 2025-08-04 07:53 | -07:00 | 07/29 - 08/04 | 2025-08-04 09:41 | -07:00 | 91.4103 | FTS | 79527 | 870 | 83 | 67 | 12 | 1 | 0 | 0 | 108
25-0082709 | Sonoma | FITCH MOUNTAIN 1113 | FITCH MOUNTAIN 111324550 | Animal | 2025-08-04 08:39 | -07:00 | 07/29 - 08/04 | 2025-08-04 10:17 | -07:00 | 98 | FTS | 21658 | 221 | 4 | 2 | 6 | 0 | 0 | 2 | 98
25-0082648 | Shasta | JESSUP 1101 | JESSUP 110168362 | 3rd Party | 2025-08-04 05:50 | -07:00 | 07/29 - 08/04 | 2025-08-04 12:49 | -07:00 | 81.26 | FTS | 124084 | 1527 | 161 | 125 | 17 | 3 | 0 | 1 | 419
25-0082861 | Santa Barbara | CABRILLO 1103 | CABRILLO 1103Y46 | 3rd Party | 2025-08-04 12:43 | -07:00 | 07/29 - 08/04 | 2025-08-04 15:42 | -07:00 | 118.7391 | FTS | 32772 | 276 | 2 | 2 | 5 | 0 | 0 | 0 | 179
25-0082646 | Monterey | SPENCE 1102 | SPENCE 1102276712 | 3rd Party | 2025-08-04 04:05 | -07:00 | 07/29 - 08/04 | 2025-08-04 15:58 | -07:00 | 158.7576 | FTS | 31434 | 198 | 1 | 0 | 0 | 0 | 0 | 0 | 713
25-0082644 | Mariposa | MARIPOSA 2102 | MARIPOSA 2102CB | Equipment Failure/Involved | 2025-08-04 03:41 | -07:00 | 07/29 - 08/04 | 2025-08-04 16:00 | -07:00 | 114.5741 | FTS | 382563 | 3339 | 162 | 112 | 67 | 22 | 3 | 8 | 739
25-0082947 | Santa Clara | HICKS 2105 | HICKS 2105954008 | Unknown Cause | 2025-08-04 14:47 | -07:00 | 07/29 - 08/04 | 2025-08-04 16:48 | -07:00 | 121 | FTS | 17787 | 147 | 5 | 4 | 7 | 0 | 0 | 0 | 121
25-0082972 | Santa Cruz | CAMP EVERS 2105 | CAMP EVERS 210510214 | Vegetation | 2025-08-04 15:35 | -07:00 | 07/29 - 08/04 | 2025-08-04 16:52 | -07:00 | 40.8447 | FTS | 8945 | 219 | 17 | 15 | 2 | 0 | 0 | 9 | 77
25-0083048 | Tuolumne | PEORIA 1701 | PEORIA 17013186 | Animal | 2025-08-04 18:53 | -07:00 | 07/29 - 08/04 | 2025-08-04 20:56 | -07:00 | 89.4688 | FTS | 113357 | 1267 | 82 | 68 | 14 | 0 | 0 | 0 | 123
25-0083173 | Santa Barbara | ZACA 1102 | ZACA 1102Y54 | Company Initiated | 2025-08-05 08:31 | -07:00 | 08/05 - 08/11 | 2025-08-05 08:44 | -07:00 | 13 | FTS | 1508 | 116 | 3 | 3 | 0 | 0 | 0 | 1 | 13
25-0083274 | Santa Cruz | CAMP EVERS 2106 | CAMP EVERS 210612760 | Company Initiated | 2025-08-05 10:34 | -07:00 | 08/05 - 08/11 | 2025-08-05 10:43 | -07:00 | 9 | FTS | 4869 | 541 | 39 | 35 | 9 | 0 | 0 | 11 | 9
25-0083330 | Amador | MARTELL 1101 | MARTELL 110191216 | Company Initiated | 2025-08-05 11:59 | -07:00 | 08/05 - 08/11 | 2025-08-05 12:19 | -07:00 | 20 | FTS | 700 | 35 | 2 | 1 | 0 | 0 | 0 | 0 | 20
25-0083346 | Marin | ALTO 1122 | ALTO 1122591122 | Unknown Cause | 2025-08-05 12:43 | -07:00 | 08/05 - 08/11 | 2025-08-05 13:43 | -07:00 | 60 | FTS | 4320 | 72 | 1 | 1 | 0 | 0 | 0 | 0 | 60
25-0083286 | Napa | MONTICELLO 1101 | MONTICELLO 110137384 | Unknown Cause | 2025-08-05 10:30 | -07:00 | 08/05 - 08/11 | 2025-08-05 14:42 | -07:00 | 251.0931 | FTS | 126802 | 505 | 21 | 14 | 11 | 0 | 0 | 3 | 252
25-0083095 | Sonoma | DUNBAR 1103 | DUNBAR 1103302 | Vegetation | 2025-08-05 03:45 | -07:00 | 08/05 - 08/11 | 2025-08-05 15:02 | -07:00 | 148.7878 | FTS | 36453 | 245 | 10 | 9 | 3 | 0 | 0 | 13 | 677
25-0083337 | Fresno | SAND CREEK 1103 | SAND CREEK 1103818064 | Unknown Cause | 2025-08-05 12:12 | -07:00 | 08/05 - 08/11 | 2025-08-05 17:39 | -07:00 | 258.3142 | FTS | 134840 | 522 | 51 | 33 | 5 | 0 | 0 | 1 | 327
25-0083503 | San Luis Obispo | MESA 1101 | MESA 1101M86 | Animal | 2025-08-05 17:12 | -07:00 | 08/05 - 08/11 | 2025-08-05 19:08 | -07:00 | 88.3789 | FTS | 67168 | 760 | 31 | 18 | 14 | 3 | 0 | 22 | 116
25-0083504 | Alameda | CAYETANO 2109 | CAYETANO 2109CB | Equipment Failure/Involved | 2025-08-05 17:35 | -07:00 | 08/05 - 08/11 | 2025-08-05 19:20 | -07:00 | 99.1011 | FTS | 311772 | 3146 | 155 | 115 | 46 | 8 | 0 | 3 | 105
25-0083323 | Shasta | OREGON TRAIL 1102 | OREGON TRAIL 1102CB | 3rd Party | 2025-08-05 11:55 | -07:00 | 08/05 - 08/11 | 2025-08-05 19:25 | -07:00 | 89.53 | FTS | 76190 | 851 | 80 | 65 | 12 | 1 | 0 | 0 | 450
25-0083358 | Contra Costa | CLAYTON 2215 | CLAYTON 2215W531R | 3rd Party | 2025-08-05 12:53 | -07:00 | 08/05 - 08/11 | 2025-08-05 19:42 | -07:00 | 66.2054 | FTS | 46741 | 706 | 53 | 41 | 11 | 0 | 0 | 0 | 409
25-0083525 | El Dorado | APPLE HILL 2102 | APPLE HILL 210277546 | Unknown Cause | 2025-08-05 19:09 | -07:00 | 08/05 - 08/11 | 2025-08-05 23:39 | -07:00 | 173.6791 | FTS | 74682 | 430 | 25 | 25 | 8 | 0 | 0 | 9 | 270
25-0083499 | Santa Cruz | LOS GATOS 1106 | LOS GATOS 1106229258 | Vegetation | 2025-08-05 16:42 | -07:00 | 08/05 - 08/11 | 2025-08-06 02:16 | -07:00 | 136.8516 | FTS | 294231 | 2150 | 156 | 124 | 54 | 8 | 0 | 25 | 574
25-0083493 | San Luis Obispo | TEMPLETON 2110 | TEMPLETON 2110941946 | Equipment Failure/Involved | 2025-08-05 16:30 | -07:00 | 08/05 - 08/11 | 2025-08-06 03:11 | -07:00 | 249.781 | FTS | 187086 | 749 | 30 | 20 | 12 | 0 | 0 | 14 | 641
25-0083562 | Madera | COARSEGOLD 2104 | COARSEGOLD 210410110 | Animal | 2025-08-06 05:14 | -07:00 | 08/05 - 08/11 | 2025-08-06 08:55 | -07:00 | 91.121 | FTS | 97864 | 1074 | 77 | 57 | 13 | 0 | 0 | 1 | 221
25-0083606 | Santa Cruz | PAUL SWEET 2107 | PAUL SWEET 2107781810 | Unknown Cause | 2025-08-06 08:01 | -07:00 | 08/05 - 08/11 | 2025-08-06 09:04 | -07:00 | 63 | FTS | 10962 | 174 | 7 | 5 | 15 | 0 | 0 | 1 | 63
25-0083555 | Monterey | HATTON 1101 | HATTON 110175304 | 3rd Party | 2025-08-06 00:12 | -07:00 | 08/05 - 08/11 | 2025-08-06 09:31 | -07:00 | 296.0185 | FTS | 272337 | 920 | 37 | 30 | 23 | 0 | 0 | 2 | 559
25-0083541 | Alameda | SAN RAMON 2103 | SAN RAMON 2103MR279 | Unknown Cause | 2025-08-05 21:35 | -07:00 | 08/05 - 08/11 | 2025-08-06 10:19 | -07:00 | 495.3846 | FTS | 966000 | 1950 | 115 | 87 | 28 | 2 | 0 | 1 | 764
25-0083601 | El Dorado | SHINGLE SPRINGS 1104 | SHINGLE SPRINGS 1104556218 | Animal | 2025-08-06 07:59 | -07:00 | 08/05 - 08/11 | 2025-08-06 10:22 | -07:00 | 35.5337 | FTS | 23168 | 652 | 55 | 42 | 4 | 0 | 0 | 26 | 143
25-0083641 | Solano | JAMESON 1103 | JAMESON 1103118944 | Equipment Failure/Involved | 2025-08-06 08:49 | -07:00 | 08/05 - 08/11 | 2025-08-06 13:44 | -07:00 | 78.2328 | FTS | 200276 | 2560 | 167 | 122 | 25 | 2 | 0 | 2 | 295
25-0083912 | Sonoma | ANNAPOLIS 1101 | ANNAPOLIS 1101528344 | Equipment Failure/Involved | 2025-08-06 14:28 | -07:00 | 08/05 - 08/11 | 2025-08-06 14:34 | -07:00 | 6 | FTS | 912 | 152 | 5 | 4 | 5 | 3 | 0 | 2 | 6
25-0083721 | Napa | SILVERADO 2102 | SILVERADO 2102714 | Unknown Cause | 2025-08-06 10:41 | -07:00 | 08/05 - 08/11 | 2025-08-06 15:25 | -07:00 | 283.1888 | FTS | 304428 | 1075 | 8 | 4 | 19 | 0 | 0 | 6 | 284
25-0083561 | Santa Cruz | STELLING 1110 | STELLING 111060094 | Vegetation | 2025-08-06 04:45 | -07:00 | 08/05 - 08/11 | 2025-08-06 15:27 | -07:00 | 146.1328 | FTS | 39602 | 271 | 15 | 12 | 7 | 0 | 0 | 13 | 642
25-0083706 | Santa Clara | PIERCY 2110 | PIERCY 2110799154 | Unknown Cause | 2025-08-06 10:29 | -07:00 | 08/05 - 08/11 | 2025-08-06 18:41 | -07:00 | 396.5207 | FTS | 153057 | 386 | 11 | 7 | 7 | 0 | 0 | 0 | 492
25-0084046 | Santa Cruz | PAUL SWEET 2106 | PAUL SWEET 21065178 | Company Initiated | 2025-08-06 19:07 | -07:00 | 08/05 - 08/11 | 2025-08-06 20:33 | -07:00 | 86 | FTS | 9460 | 110 | 12 | 9 | 3 | 0 | 0 | 4 | 86
25-0084052 | Monterey | HATTON 1101 | HATTON 1101CB | Unknown Cause | 2025-08-06 21:01 | -07:00 | 08/05 - 08/11 | 2025-08-06 21:45 | -07:00 | 44 | FTS | 156332 | 3553 | 252 | 225 | 81 | 8 | 0 | 3 | 44
25-0084021 | Sonoma | FITCH MOUNTAIN 1113 | FITCH MOUNTAIN 111324550 | Vegetation | 2025-08-06 17:29 | -07:00 | 08/05 - 08/11 | 2025-08-07 05:24 | -07:00 | 269.724 | FTS | 59609 | 221 | 4 | 2 | 6 | 0 | 0 | 2 | 715
25-0084043 | Santa Cruz | BURNS 2101 | BURNS 2101389090 | 3rd Party | 2025-08-06 19:16 | -07:00 | 08/05 - 08/11 | 2025-08-07 05:54 | -07:00 | 216.3887 | FTS | 420876 | 1945 | 125 | 109 | 27 | 3 | 0 | 3 | 638
25-0084088 | Santa Cruz | GREEN VALLEY 2103 | GREEN VALLEY 210310932 | Animal | 2025-08-07 04:31 | -07:00 | 08/05 - 08/11 | 2025-08-07 06:48 | -07:00 | 108.614 | FTS | 690242 | 6355 | 405 | 343 | 104 | 14 | 0 | 7 | 137
25-0084097 | Sonoma | FITCH MOUNTAIN 1113 | FITCH MOUNTAIN 1113154 | Animal | 2025-08-07 06:08 | -07:00 | 08/05 - 08/11 | 2025-08-07 07:38 | -07:00 | 55.9254 | FTS | 21755 | 389 | 11 | 7 | 10 | 0 | 0 | 8 | 90
25-0084194 | Napa | CALISTOGA 1101 | CALISTOGA 1101894 | Company Initiated | 2025-08-07 08:52 | -07:00 | 08/05 - 08/11 | 2025-08-07 09:10 | -07:00 | 18 | FTS | 4734 | 263 | 12 | 8 | 3 | 0 | 0 | 0 | 18
25-0084241 | Calaveras | STANISLAUS 1702 | STANISLAUS 17021850 | Animal | 2025-08-07 09:44 | -07:00 | 08/05 - 08/11 | 2025-08-07 11:18 | -07:00 | 86.7531 | FTS | 211504 | 2438 | 81 | 63 | 27 | 3 | 2 | 0 | 94
25-0084138 | Placer | PLACER 1102 | PLACER 1102CB | Animal | 2025-08-07 07:30 | -07:00 | 08/05 - 08/11 | 2025-08-07 12:21 | -07:00 | 137.4561 | FTS | 309826 | 2254 | 207 | 154 | 38 | 6 | 0 | 61 | 291
25-0084320 | Sonoma | COTATI 1103 | COTATI 1103132 | Unknown Cause | 2025-08-07 11:43 | -07:00 | 08/05 - 08/11 | 2025-08-07 12:32 | -07:00 | 49 | FTS | 50666 | 1034 | 28 | 22 | 32 | 7 | 0 | 4 | 49
25-0084319 | Monterey | RESERVATION ROAD 1101 | RESERVATION ROAD 1101383718 | Unknown Cause | 2025-08-07 11:38 | -07:00 | 08/05 - 08/11 | 2025-08-07 12:53 | -07:00 | 52.0817 | FTS | 36978 | 710 | 55 | 40 | 17 | 2 | 0 | 2 | 75
25-0084239 | Calaveras | STANISLAUS 1701 | STANISLAUS 170179826 | Company Initiated | 2025-08-07 09:44 | -07:00 | 08/05 - 08/11 | 2025-08-07 14:13 | -07:00 | 269 | FTS | 37929 | 141 | 7 | 6 | 3 | 0 | 0 | 0 | 269
25-0084449 | Mendocino | WILLITS 1103 | WILLITS 1103538 | Company Initiated | 2025-08-07 11:51 | -07:00 | 08/05 - 08/11 | 2025-08-07 14:28 | -07:00 | 157 | FTS | 3611 | 23 | 1 | 1 | 0 | 0 | 0 | 0 | 157
25-0084161 | Alameda | SUNOL 1101 | SUNOL 1101904308 | 3rd Party | 2025-08-07 08:17 | -07:00 | 08/05 - 08/11 | 2025-08-07 16:09 | -07:00 | 92.4348 | FTS | 4252 | 46 | 1 | 0 | 5 | 0 | 0 | 0 | 472
25-0084510 | Shasta | ANTLER 1101 | ANTLER 11011378 | Company Initiated | 2025-08-07 15:33 | -07:00 | 08/05 - 08/11 | 2025-08-07 16:23 | -07:00 | 50 | FTS | 1300 | 26 | 6 | 3 | 1 | 0 | 0 | 0 | 50
25-0084466 | Marin | COTATI 1103 | COTATI 110361736 | Unknown Cause | 2025-08-07 14:38 | -07:00 | 08/05 - 08/11 | 2025-08-07 16:47 | -07:00 | 79.246 | FTS | 69261 | 874 | 27 | 22 | 30 | 7 | 0 | 4 | 129
25-0084564 | Tuolumne | CURTIS 1704 | CURTIS 170463502 | Company Initiated | 2025-08-07 17:08 | -07:00 | 08/05 - 08/11 | 2025-08-07 17:48 | -07:00 | 40 | FTS | 1120 | 28 | 1 | 1 | 0 | 0 | 0 | 0 | 40
25-0084266 | Monterey | SAN ARDO 1102 | SAN ARDO 110291894 | 3rd Party | 2025-08-07 10:34 | -07:00 | 08/05 - 08/11 | 2025-08-07 18:29 | -07:00 | 111.4275 | FTS | 29194 | 262 | 1 | 1 | 11 | 4 | 0 | 0 | 475
25-0084542 | Mendocino | GUALALA 1112 | GUALALA 111135562 | Vegetation | 2025-08-07 16:34 | -07:00 | 08/05 - 08/11 | 2025-08-07 20:30 | -07:00 | 101.8341 | FTS | 41752 | 410 | 19 | 14 | 8 | 0 | 0 | 0 | 236
25-0084587 | Alameda | SAN RAMON 2119 | SAN RAMON 2119CB | Equipment Failure/Involved | 2025-08-07 18:28 | -07:00 | 08/05 - 08/11 | 2025-08-07 22:56 | -07:00 | 109.6513 | FTS | 409767 | 3737 | 196 | 121 | 88 | 12 | 0 | 0 | 268
25-0084653 | San Luis Obispo | PERRY 1101 | PERRY 1101200598 | Animal | 2025-08-08 06:07 | -07:00 | 08/05 - 08/11 | 2025-08-08 07:38 | -07:00 | 33.3956 | FTS | 67793 | 2030 | 70 | 54 | 14 | 0 | 0 | 0 | 91
25-0084615 | El Dorado | PLACERVILLE 2106 | PLACERVILLE 21069712 | Unknown Cause | 2025-08-07 17:39 | -07:00 | 08/05 - 08/11 | 2025-08-08 11:59 | -07:00 | 1100 | FTS | 22000 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 1100
25-0084720 | Nevada | BRUNSWICK 1103 | BRUNSWICK 1103851116 | Animal | 2025-08-08 08:25 | -07:00 | 08/05 - 08/11 | 2025-08-08 13:01 | -07:00 | 77.8438 | FTS | 2491 | 32 | 1 | 1 | 2 | 1 | 0 | 0 | 276
25-0084631 | San Mateo | SNEATH LANE 1106 | SNEATH LANE 1106CB | Equipment Failure/Involved | 2025-08-07 23:20 | -07:00 | 08/05 - 08/11 | 2025-08-08 13:15 | -07:00 | 73.4763 | FTS | 301767 | 4107 | 145 | 104 | 33 | 5 | 0 | 0 | 835
25-0084825 | El Dorado | APPLE HILL 2102 | APPLE HILL 2102836878 | Equipment Failure/Involved | 2025-08-08 11:19 | -07:00 | 08/05 - 08/11 | 2025-08-08 13:48 | -07:00 | 149 | FTS | 709985 | 4765 | 379 | 279 | 62 | 12 | 0 | 63 | 149
25-0084912 | Contra Costa | RESEARCH 2102 | RESEARCH 2102644462 | Unknown Cause | 2025-08-08 13:27 | -07:00 | 08/05 - 08/11 | 2025-08-08 14:48 | -07:00 | 81 | FTS | 6804 | 84 | 6 | 3 | 4 | 0 | 0 | 0 | 81
25-0084939 | Monterey | LAURELES 1111 | LAURELES 1111822080 | Company Initiated | 2025-08-08 14:01 | -07:00 | 08/05 - 08/11 | 2025-08-08 16:00 | -07:00 | 119 | FTS | 15351 | 129 | 4 | 2 | 2 | 0 | 0 | 1 | 119
25-0084975 | Humboldt | RIO DELL 1104 | RIO DELL 11041504 | Vegetation | 2025-08-08 15:07 | -07:00 | 08/05 - 08/11 | 2025-08-08 16:38 | -07:00 | 91 | FTS | 23205 | 255 | 10 | 4 | 3 | 0 | 0 | 1 | 91
25-0084988 | Napa | SILVERADO 2103 | SILVERADO 2103507513 | 3rd Party | 2025-08-08 15:24 | -07:00 | 08/05 - 08/11 | 2025-08-08 16:39 | -07:00 | 60.5276 | FTS | 12045 | 199 | 3 | 0 | 1 | 0 | 0 | 0 | 75
25-0084974 | Shasta | PANORAMA 1102 | PANORAMA 1102280170 | Unknown Cause | 2025-08-08 15:01 | -07:00 | 08/05 - 08/11 | 2025-08-08 17:06 | -07:00 | 80.9381 | FTS | 7851 | 97 | 3 | 1 | 2 | 0 | 0 | 0 | 125
25-0084962 | Alameda | VINEYARD 2108 | VINEYARD 2108MR172 | Unknown Cause | 2025-08-08 14:44 | -07:00 | 08/05 - 08/11 | 2025-08-08 17:53 | -07:00 | 77.1484 | FTS | 234994 | 3046 | 158 | 117 | 36 | 2 | 0 | 1 | 189
25-0084626 | San Luis Obispo | SAN LUIS OBISPO 1104 | SAN LUIS OBISPO 1104V46 | Equipment Failure/Involved | 2025-08-07 22:08 | -07:00 | 08/05 - 08/11 | 2025-08-08 20:06 | -07:00 | 376.6514 | FTS | 65914 | 175 | 4 | 4 | 10 | 0 | 0 | 3 | 1318
25-0085034 | Alameda | VINEYARD 2108 | VINEYARD 2108MR172 | Unknown Cause | 2025-08-08 19:23 | -07:00 | 08/05 - 08/11 | 2025-08-08 20:28 | -07:00 | 53.0118 | FTS | 161580 | 3048 | 158 | 117 | 36 | 2 | 0 | 1 | 65
25-0085030 | Kings | AVENAL 2101 | AVENAL 2101CB | 3rd Party | 2025-08-08 18:49 | -07:00 | 08/05 - 08/11 | 2025-08-08 20:45 | -07:00 | 113.001 | FTS | 347365 | 3074 | 86 | 63 | 33 | 16 | 1 | 0 | 116
25-0085043 | San Mateo | SAN CARLOS 1103 | SAN CARLOS 11039148 | Unknown Cause | 2025-08-08 20:35 | -07:00 | 08/05 - 08/11 | 2025-08-08 21:17 | -07:00 | 42 | FTS | 924 | 22 | 1 | 0 | 0 | 0 | 0 | 0 | 42
25-0067813 | El Dorado | PLACERVILLE 1112 | PLACERVILLE 111219712 | Company Initiated | 2025-08-07 20:02 | -07:00 | 08/05 - 08/11 | 2025-08-08 21:31 | -07:00 | 146.2485 | FTS | 49432 | 338 | 4 | 3 | 1 | 0 | 0 | 2 | 1529
25-0084885 | Santa Cruz | BURNS 2101 | BURNS 2101CB | 3rd Party | 2025-08-08 12:48 | -07:00 | 08/05 - 08/11 | 2025-08-09 00:08 | -07:00 | 133.6615 | FTS | 311164 | 2328 | 168 | 141 | 39 | 3 | 0 | 18 | 680
25-0085067 | Placer | PENRYN 1103 | PENRYN 1103604 | Animal | 2025-08-08 23:30 | -07:00 | 08/05 - 08/11 | 2025-08-09 01:26 | -07:00 | 116 | FTS | 39556 | 341 | 23 | 15 | 3 | 0 | 0 | 8 | 116
25-0085031 | Santa Barbara | SISQUOC 1102 | SISQUOC 1102M26 | 3rd Party | 2025-08-08 19:03 | -07:00 | 08/05 - 08/11 | 2025-08-09 04:11 | -07:00 | 94.0531 | FTS | 21256 | 226 | 1 | 1 | 2 | 0 | 0 | 0 | 548
25-0085047 | Stanislaus | WESTLEY 1103 | WESTLEY 1103237522 | Unknown Cause | 2025-08-08 21:16 | -07:00 | 08/05 - 08/11 | 2025-08-09 08:48 | -07:00 | 692 | FTS | 24912 | 36 | 0 | 0 | 11 | 0 | 0 | 0 | 692
25-0085100 | Santa Cruz | PAUL SWEET 2106 | PAUL SWEET 21065178 | Company Initiated | 2025-08-09 08:41 | -07:00 | 08/05 - 08/11 | 2025-08-09 09:45 | -07:00 | 64 | FTS | 7040 | 110 | 12 | 9 | 3 | 0 | 0 | 4 | 64
25-0085044 | El Dorado | CLARKSVILLE 2109 | CLARKSVILLE 2109CB | Equipment Failure/Involved | 2025-08-08 21:00 | -07:00 | 08/05 - 08/11 | 2025-08-09 10:21 | -07:00 | 133.0063 | FTS | 404206 | 3039 | 185 | 120 | 55 | 5 | 0 | 3 | 801
25-0085122 | Santa Cruz | PAUL SWEET 2106 | PAUL SWEET 21065178 | Company Initiated | 2025-08-09 10:38 | -07:00 | 08/05 - 08/11 | 2025-08-09 12:31 | -07:00 | 94.8364 | FTS | 10432 | 110 | 12 | 9 | 3 | 0 | 0 | 4 | 113
25-0085141 | Monterey | LAURELES 1111 | LAURELES 1111822080 | Unknown Cause | 2025-08-09 12:17 | -07:00 | 08/05 - 08/11 | 2025-08-09 14:26 | -07:00 | 129 | FTS | 16641 | 129 | 4 | 2 | 2 | 0 | 0 | 1 | 129
25-0085157 | Mariposa | MARIPOSA 2101 | MARIPOSA 210110240 | Company Initiated | 2025-08-09 13:18 | -07:00 | 08/05 - 08/11 | 2025-08-09 14:31 | -07:00 | 73 | FTS | 30952 | 424 | 20 | 15 | 9 | 0 | 0 | 0 | 73
25-0085169 | Solano | BAHIA 1102 | BAHIA 1102946 | Unknown Cause | 2025-08-09 14:30 | -07:00 | 08/05 - 08/11 | 2025-08-09 15:52 | -07:00 | 82 | HLT | 19434 | 237 | 2 | 1 | 18 | 0 | 0 | 1 | 82
25-0085126 | Tehama | TYLER 1105 | TYLER 11051704 | Animal | 2025-08-09 10:50 | -07:00 | 08/05 - 08/11 | 2025-08-09 17:12 | -07:00 | 102.9868 | FTS | 86097 | 836 | 77 | 55 | 13 | 3 | 0 | 4 | 382
25-0085173 | Lake | HIGHLANDS 1103 | HIGHLANDS 1103520 | Unknown Cause | 2025-08-09 15:18 | -07:00 | 08/05 - 08/11 | 2025-08-09 18:43 | -07:00 | 205 | FTS | 149650 | 730 | 55 | 31 | 5 | 0 | 0 | 7 | 205
25-0085168 | Tuolumne | MIWUK 1701 | MIWUK 1701767890 | Equipment Failure/Involved | 2025-08-09 14:18 | -07:00 | 08/05 - 08/11 | 2025-08-09 20:10 | -07:00 | 131.1782 | FTS | 162661 | 1240 | 61 | 47 | 11 | 2 | 0 | 1 | 352
25-0085179 | Amador | PINE GROVE 1102 | PINE GROVE 11023168 | Equipment Failure/Involved | 2025-08-09 16:46 | -07:00 | 08/05 - 08/11 | 2025-08-09 22:50 | -07:00 | 243.9922 | FTS | 435526 | 1785 | 134 | 96 | 14 | 0 | 0 | 10 | 364
25-0085193 | Contra Costa | TASSAJARA 2104 | TASSAJARA 2104967234 | Unknown Cause | 2025-08-09 20:24 | -07:00 | 08/05 - 08/11 | 2025-08-09 23:10 | -07:00 | 88.0071 | FTS | 173990 | 1977 | 101 | 69 | 19 | 3 | 0 | 6 | 166
25-0085201 | Santa Barbara | SISQUOC 1102 | SISQUOC 1102M26 | 3rd Party | 2025-08-09 22:40 | -07:00 | 08/05 - 08/11 | 2025-08-10 08:32 | -07:00 | 73.0711 | FTS | 18487 | 253 | 3 | 2 | 2 | 0 | 0 | 0 | 592
25-0085219 | Santa Barbara | SANTA YNEZ 1101 | SANTA YNEZ 1101Y52 | Animal | 2025-08-10 06:49 | -07:00 | 08/05 - 08/11 | 2025-08-10 08:43 | -07:00 | 114 | FTS | 21432 | 188 | 0 | 0 | 25 | 0 | 0 | 0 | 114
25-0085223 | Solano | BAHIA 1102 | BAHIA 1102946 | Unknown Cause | 2025-08-10 07:48 | -07:00 | 08/05 - 08/11 | 2025-08-10 09:26 | -07:00 | 86.0759 | HLT | 20400 | 237 | 2 | 1 | 18 | 0 | 0 | 1 | 98
25-0085216 | Sonoma | COTATI 1103 | COTATI 1103CB | Animal | 2025-08-10 05:24 | -07:00 | 08/05 - 08/11 | 2025-08-10 10:27 | -07:00 | 104.4483 | FTS | 155419 | 1488 | 57 | 42 | 41 | 7 | 0 | 15 | 303
25-0085161 | Santa Clara | SARATOGA 1107 | SARATOGA 1107667000 | Vegetation | 2025-08-09 13:41 | -07:00 | 08/05 - 08/11 | 2025-08-10 10:34 | -07:00 | 161.6434 | FTS | 83408 | 516 | 26 | 16 | 13 | 2 | 0 | 7 | 1253
25-0085229 | San Benito | HOLLISTER 2104 | HOLLISTER 2102113634 | Unknown Cause | 2025-08-10 08:46 | -07:00 | 08/05 - 08/11 | 2025-08-10 10:43 | -07:00 | 117 | FTS | 10530 | 90 | 2 | 0 | 3 | 0 | 0 | 0 | 117
25-0085275 | Monterey | LAURELES 1111 | LAURELES 1111822080 | Unknown Cause | 2025-08-10 13:42 | -07:00 | 08/05 - 08/11 | 2025-08-10 15:26 | -07:00 | 104 | FTS | 13416 | 129 | 4 | 2 | 2 | 0 | 0 | 1 | 104
25-0085320 | Solano | GRAND ISLAND 2226 | GRAND ISLAND 2226292892 | Equipment Failure/Involved | 2025-08-10 18:58 | -07:00 | 08/05 - 08/11 | 2025-08-10 20:50 | -07:00 | 112 | HLT | 498400 | 4450 | 450 | 341 | 33 | 2 | 0 | 1 | 112
25-0085303 | Mariposa | BEAR VALLEY 2105 | N/A | Animal | 2025-08-10 17:10 | -07:00 | 08/05 - 08/11 | 2025-08-10 22:24 | -07:00 | 137.4581 | T-EPSS | 608802 | 4429 | 184 | 138 | 77 | 11 | 0 | 12 | 314
25-0085334 | Mendocino | POTTER VALLEY P H 1105 | POTTER VALLEY P H 110537476 | Unknown Cause | 2025-08-10 21:15 | -07:00 | 08/05 - 08/11 | 2025-08-11 00:06 | -07:00 | 171 | FTS | 19323 | 113 | 1 | 1 | 0 | 0 | 0 | 1 | 171
25-0085318 | Santa Cruz | CAMP EVERS 2105 | BEN LOMOND 0401944178 | Equipment Failure/Involved | 2025-08-10 18:43 | -07:00 | 08/05 - 08/11 | 2025-08-11 02:43 | -07:00 | 381.32 | FTS | 2387063 | 6260 | 418 | 338 | 124 | 14 | 0 | 13 | 480
25-0085336 | Nevada | HIGGINS 1103 | HIGGINS 110332120 | Vegetation | 2025-08-10 21:29 | -07:00 | 08/05 - 08/11 | 2025-08-11 04:04 | -07:00 | 124.0521 | FTS | 176154 | 1420 | 140 | 101 | 12 | 2 | 0 | 10 | 395
25-0085350 | Napa | PUEBLO 2102 | PUEBLO 2102698 | Unknown Cause | 2025-08-11 02:20 | -07:00 | 08/05 - 08/11 | 2025-08-11 04:25 | -07:00 | 106.9466 | FTS | 84167 | 787 | 18 | 15 | 9 | 0 | 0 | 0 | 125
25-0085358 | Mendocino | MENDOCINO 1101 | MENDOCINO 1101856020 | Animal | 2025-08-11 05:02 | -07:00 | 08/05 - 08/11 | 2025-08-11 08:22 | -07:00 | 82.1858 | FTS | 61475 | 748 | 40 | 26 | 10 | 1 | 0 | 1 | 200
25-0085364 | Solano | GRAND ISLAND 2226 | GRAND ISLAND 2226292892 | Equipment Failure/Involved | 2025-08-11 06:18 | -07:00 | 08/05 - 08/11 | 2025-08-11 09:06 | -07:00 | 167.9533 | HLT | 747392 | 4450 | 450 | 341 | 33 | 2 | 0 | 1 | 168
25-0085368 | Alameda | CASTRO VALLEY 1108 | CASTRO VALLEY 1108343456 | Unknown Cause | 2025-08-11 06:37 | -07:00 | 08/05 - 08/11 | 2025-08-11 09:35 | -07:00 | 98.8196 | FTS | 183508 | 1857 | 131 | 96 | 28 | 2 | 0 | 1 | 178
25-0085441 | Calaveras | FROGTOWN 1702 | FROGTOWN 170232556 | Company Initiated | 2025-08-11 09:13 | -07:00 | 08/05 - 08/11 | 2025-08-11 09:36 | -07:00 | 23 | FTS | 88872 | 3864 | 221 | 163 | 122 | 16 | 1 | 6 | 23
25-0085343 | Calaveras | FROGTOWN 1701 | FROGTOWN 1701CB | Unknown Cause | 2025-08-10 22:10 | -07:00 | 08/05 - 08/11 | 2025-08-11 10:01 | -07:00 | 483.3168 | FTS | 982583 | 2033 | 121 | 87 | 30 | 4 | 0 | 3 | 711
25-0085507 | Santa Cruz | CAMP EVERS 2106 | CAMP EVERS 210612518 | Company Initiated | 2025-08-11 10:45 | -07:00 | 08/05 - 08/11 | 2025-08-11 11:08 | -07:00 | 23 | FTS | 1403 | 61 | 5 | 4 | 2 | 3 | 0 | 0 | 23
25-0085304 | Mariposa | INDIAN FLAT 1104 | N/A | Animal | 2025-08-10 17:10 | -07:00 | 08/05 - 08/11 | 2025-08-11 11:11 | -07:00 | 1081 | T-EPSS | 665896 | 616 | 8 | 6 | 10 | 2 | 0 | 4 | 1081
25-0085408 | Shasta | PIT NO 3 2101 | PIT NO 3 21011360 | Unknown Cause | 2025-08-11 08:29 | -07:00 | 08/05 - 08/11 | 2025-08-11 11:14 | -07:00 | 165 | FTS | 9405 | 57 | 1 | 1 | 1 | 0 | 0 | 0 | 165
25-0085590 | Santa Cruz | CAMP EVERS 2106 | CAMP EVERS 210612518 | Company Initiated | 2025-08-11 12:31 | -07:00 | 08/05 - 08/11 | 2025-08-11 12:41 | -07:00 | 10 | FTS | 730 | 73 | 5 | 4 | 3 | 3 | 0 | 0 | 10
25-0085568 | Calaveras | FROGTOWN 1701 | FROGTOWN 170113412 | Company Initiated | 2025-08-11 12:10 | -07:00 | 08/05 - 08/11 | 2025-08-11 12:41 | -07:00 | 31 | FTS | 57443 | 1853 | 108 | 78 | 26 | 4 | 0 | 3 | 31
25-0085595 | El Dorado | DIAMOND SPRINGS 1106 | DIAMOND SPRINGS 11062100 | Vegetation | 2025-08-11 10:58 | -07:00 | 08/05 - 08/11 | 2025-08-11 13:45 | -07:00 | 167 | FTS | 10855 | 65 | 7 | 3 | 1 | 0 | 0 | 1 | 167
25-0082394 | San Luis Obispo | CUYAMA 1103 | CUYAMA 1103684566 | Environmental/External | 2025-08-02 01:47 | -07:00 | 08/05 - 08/11 | 2025-08-11 14:51 | -07:00 | 4706 | FTS | 28236 | 6 | 339 | 245 | 193 | 27 | 0 | 0 | 13744
25-0085467 | Monterey | SOLEDAD 2101 | SOLEDAD 2101107872 | Unknown Cause | 2025-08-11 09:47 | -07:00 | 08/05 - 08/11 | 2025-08-11 15:41 | -07:00 | 302.3636 | FTS | 9978 | 33 | 1 | 1 | 0 | 0 | 0 | 0 | 354
25-0085738 | Monterey | LAURELES 1111 | LAURELES 1111822080 | Unknown Cause | 2025-08-11 15:40 | -07:00 | 08/05 - 08/11 | 2025-08-11 16:03 | -07:00 | 23 | FTS | 2967 | 129 | 4 | 2 | 2 | 0 | 0 | 1 | 23
25-0085698 | Santa Barbara | ZACA 1101 | ZACA 1101CB | Unknown Cause | 2025-08-11 15:01 | -07:00 | 08/05 - 08/11 | 2025-08-11 17:24 | -07:00 | 70.1071 | FTS | 11778 | 168 | 0 | 0 | 11 | 13 | 0 | 0 | 143
25-0085389 | Sonoma | IGNACIO 1104 | IGNACIO 1104469764 | Unknown Cause | 2025-08-11 07:44 | -07:00 | 08/05 - 08/11 | 2025-08-11 17:56 | -07:00 | 342.4539 | FTS | 100339 | 293 | 2 | 2 | 14 | 0 | 0 | 0 | 612
25-0085807 | Calaveras | FROGTOWN 1702 | FROGTOWN 1702531640 | Unknown Cause | 2025-08-11 16:58 | -07:00 | 08/05 - 08/11 | 2025-08-11 19:22 | -07:00 | 144 | FTS | 7632 | 53 | 0 | 0 | 10 | 0 | 0 | 0 | 144
25-0085786 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113641367 | Unknown Cause | 2025-08-11 17:16 | -07:00 | 08/05 - 08/11 | 2025-08-11 21:16 | -07:00 | 240 | FTS | 71280 | 297 | 9 | 5 | 3 | 0 | 0 | 11 | 240
25-0085825 | Napa | SILVERADO 2105 | SILVERADO 2105131568 | Unknown Cause | 2025-08-11 21:35 | -07:00 | 08/05 - 08/11 | 2025-08-11 23:51 | -07:00 | 136 | FTS | 15232 | 112 | 3 | 2 | 1 | 0 | 0 | 0 | 136
25-0085819 | Monterey | SAN MIGUEL 1106 | SAN MIGUEL 1106N34 | Animal | 2025-08-11 20:27 | -07:00 | 08/12 - 08/18 | 2025-08-12 00:23 | -07:00 | 231.3608 | FTS | 22442 | 97 | 0 | 0 | 11 | 2 | 0 | 0 | 236
25-0085822 | Alameda | VINEYARD 2107 | VINEYARD 2107MR332 | Equipment Failure/Involved | 2025-08-11 21:00 | -07:00 | 08/12 - 08/18 | 2025-08-12 07:36 | -07:00 | 97.8696 | FTS | 108048 | 1104 | 31 | 21 | 17 | 0 | 0 | 0 | 636
25-0085858 | Placer | PENRYN 1103 | PENRYN 110351658 | Animal | 2025-08-12 06:47 | -07:00 | 08/12 - 08/18 | 2025-08-12 07:46 | -07:00 | 50.3585 | FTS | 34697 | 689 | 45 | 34 | 9 | 0 | 0 | 19 | 59
25-0085831 | Humboldt | HOOPA 1101 | HOOPA 11013304 | Vegetation | 2025-08-11 23:12 | -07:00 | 08/12 - 08/18 | 2025-08-12 12:26 | -07:00 | 173.8096 | FTS | 115931 | 667 | 18 | 14 | 24 | 5 | 0 | 0 | 794
25-0086043 | Santa Cruz | CAMP EVERS 2105 | CAMP EVERS 210612518 | Vegetation | 2025-08-12 09:47 | -07:00 | 08/12 - 08/18 | 2025-08-12 13:13 | -07:00 | 199.0909 | FTS | 4380 | 22 | 1 | 1 | 2 | 2 | 0 | 0 | 206
25-0085832 | Mendocino | POTTER VALLEY P H 1105 | POTTER VALLEY P H 110537476 | Equipment Failure/Involved | 2025-08-11 23:40 | -07:00 | 08/12 - 08/18 | 2025-08-12 15:36 | -07:00 | 221.1327 | FTS | 24988 | 113 | 1 | 1 | 0 | 0 | 0 | 1 | 956
25-0086163 | Santa Cruz | BEN LOMOND 0401 | BEN LOMOND 04015144 | Unknown Cause | 2025-08-12 15:08 | -07:00 | 08/12 - 08/18 | 2025-08-12 18:59 | -07:00 | 231 | FTS | 34419 | 149 | 7 | 6 | 5 | 0 | 0 | 0 | 231
25-0086239 | San Luis Obispo | CHOLAME 1101 | CHOLAME 1101X06 | Unknown Cause | 2025-08-12 19:23 | -07:00 | 08/12 - 08/18 | 2025-08-12 22:44 | -07:00 | 200.8596 | FTS | 34347 | 171 | 2 | 2 | 7 | 2 | 0 | 0 | 201
25-0086267 | Amador | OLETA 1102 | OLETA 11021228 | Animal | 2025-08-12 21:37 | -07:00 | 08/12 - 08/18 | 2025-08-12 23:23 | -07:00 | 106 | FTS | 4240 | 40 | 2 | 2 | 0 | 0 | 0 | 2 | 106
25-0086255 | Amador | OLETA 1102 | OLETA 11021228 | Animal | 2025-08-12 21:36 | -07:00 | 08/12 - 08/18 | 2025-08-12 23:23 | -07:00 | 107 | FTS | 89452 | 836 | 22 | 17 | 12 | 0 | 0 | 9 | 107
25-0086273 | Solano | JAMESON 1103 | JAMESON 1103118944 | Unknown Cause | 2025-08-13 01:47 | -07:00 | 08/12 - 08/18 | 2025-08-13 07:59 | -07:00 | 167.5556 | FTS | 13572 | 81 | 4 | 4 | 5 | 0 | 0 | 2 | 372
25-0086313 | Placer | PENRYN 1105 | PENRYN 11052406 | Animal | 2025-08-13 07:55 | -07:00 | 08/12 - 08/18 | 2025-08-13 08:35 | -07:00 | 31.2973 | FTS | 27792 | 888 | 57 | 41 | 9 | 1 | 0 | 13 | 40
25-0086305 | San Luis Obispo | FOOTHILL 1102 | FOOTHILL 110263550 | Unknown Cause | 2025-08-13 07:39 | -07:00 | 08/12 - 08/18 | 2025-08-13 08:49 | -07:00 | 70 | FTS | 38570 | 551 | 15 | 11 | 1 | 0 | 0 | 0 | 70
25-0086337 | Sonoma | SONOMA 1103 | SONOMA 11033138 | Animal | 2025-08-13 08:32 | -07:00 | 08/12 - 08/18 | 2025-08-13 09:37 | -07:00 | 65 | FTS | 15340 | 236 | 9 | 7 | 0 | 0 | 0 | 0 | 65
25-0086303 | San Joaquin | CARBONA 1101 | CARBONA 1101CB | Unknown Cause | 2025-08-13 07:33 | -07:00 | 08/12 - 08/18 | 2025-08-13 10:12 | -07:00 | 27.2749 | HLT | 77379 | 2837 | 64 | 41 | 20 | 0 | 0 | 0 | 159
25-0086525 | Calaveras | FROGTOWN 1701 | FROGTOWN 1701564780 | Company Initiated | 2025-08-13 11:57 | -07:00 | 08/12 - 08/18 | 2025-08-13 12:54 | -07:00 | 57 | FTS | 16131 | 283 | 24 | 20 | 2 | 0 | 0 | 2 | 57
25-0086510 | Placer | BELL 1107 | BELL 110750172 | Animal | 2025-08-13 12:25 | -07:00 | 08/12 - 08/18 | 2025-08-13 12:58 | -07:00 | 33 | FTS | 11352 | 344 | 25 | 19 | 4 | 0 | 0 | 6 | 33
25-0086443 | Mariposa | INDIAN FLAT 1104 | INDIAN FLAT 1104CB | Unknown Cause | 2025-08-13 11:00 | -07:00 | 08/12 - 08/18 | 2025-08-13 13:27 | -07:00 | 147 | FTS | 88347 | 601 | 8 | 6 | 10 | 2 | 0 | 4 | 147
25-0070104 | San Mateo | MENLO 1102 | MENLO 1102154024 | Company Initiated | 2025-08-13 16:45 | -07:00 | 08/12 - 08/18 | 2025-08-13 18:39 | -07:00 | 114 | FTS | 11400 | 100 | 4 | 3 | 4 | 0 | 0 | 0 | 114
25-0086673 | Nevada | NARROWS 2105 | NARROWS 21052426 | Company Initiated | 2025-08-13 17:28 | -07:00 | 08/12 - 08/18 | 2025-08-13 18:47 | -07:00 | 79 | FTS | 2686 | 34 | 3 | 2 | 0 | 0 | 0 | 0 | 79
25-0086634 | Humboldt | GARBERVILLE 1101 | GARBERVILLE 11011750 | Unknown Cause | 2025-08-13 15:33 | -07:00 | 08/12 - 08/18 | 2025-08-13 19:19 | -07:00 | 224.0889 | FTS | 20168 | 90 | 3 | 1 | 2 | 0 | 0 | 0 | 226
25-0086545 | Nevada | GRASS VALLEY 1101 | GRASS VALLEY 11012208 | 3rd Party | 2025-08-13 13:23 | -07:00 | 08/12 - 08/18 | 2025-08-14 03:25 | -07:00 | 110.1188 | FTS | 44488 | 404 | 45 | 33 | 6 | 0 | 0 | 3 | 842
25-0086713 | Santa Barbara | PALMER 1101 | PALMER 1101M88 | 3rd Party | 2025-08-13 23:48 | -07:00 | 08/12 - 08/18 | 2025-08-14 04:45 | -07:00 | 236.3812 | FTS | 37821 | 160 | 0 | 0 | 5 | 0 | 0 | 0 | 297
25-0086704 | Calaveras | FROGTOWN 1702 | FROGTOWN 1702902652 | Equipment Failure/Involved | 2025-08-13 20:25 | -07:00 | 08/12 - 08/18 | 2025-08-14 05:04 | -07:00 | 364.896 | FTS | 63127 | 173 | 6 | 5 | 4 | 0 | 0 | 0 | 519
25-0086739 | Placer | AUBURN 1102 | AUBURN 1102251946 | Animal | 2025-08-14 07:15 | -07:00 | 08/12 - 08/18 | 2025-08-14 08:48 | -07:00 | 93 | FTS | 92442 | 994 | 47 | 30 | 11 | 2 | 0 | 0 | 93
25-0086723 | San Luis Obispo | PASO ROBLES 1104 | PASO ROBLES 1104R12 | Unknown Cause | 2025-08-14 05:06 | -07:00 | 08/12 - 08/18 | 2025-08-14 11:36 | -07:00 | 318.8803 | FTS | 74618 | 234 | 1 | 1 | 2 | 0 | 0 | 3 | 390
25-0086875 | San Luis Obispo | TEMPLETON 2110 | TEMPLETON 2110307832 | Unknown Cause | 2025-08-14 10:33 | -07:00 | 08/12 - 08/18 | 2025-08-14 13:39 | -07:00 | 104.2845 | FTS | 145894 | 1399 | 42 | 30 | 20 | 0 | 0 | 31 | 186
25-0086938 | Mendocino | HOPLAND 1101 | HOPLAND 110180620 | Unknown Cause | 2025-08-14 12:21 | -07:00 | 08/12 - 08/18 | 2025-08-14 14:02 | -07:00 | 101 | FTS | 7070 | 70 | 3 | 2 | 1 | 0 | 0 | 0 | 101
25-0086988 | Nevada | BRUNSWICK 1105 | BRUNSWICK 11052204 | 3rd Party | 2025-08-14 13:36 | -07:00 | 08/12 - 08/18 | 2025-08-14 15:55 | -07:00 | 129.6883 | FTS | 123982 | 956 | 53 | 38 | 14 | 0 | 0 | 24 | 139
25-0086717 | Contra Costa | ROSSMOOR 1102 | ROSSMOOR 1102457174 | Equipment Failure/Involved | 2025-08-14 01:14 | -07:00 | 08/12 - 08/18 | 2025-08-14 17:02 | -07:00 | 192.3288 | FTS | 1096082 | 5699 | 346 | 237 | 46 | 2 | 1 | 0 | 948
25-0087016 | Mendocino | POINT ARENA 1101 | POINT ARENA 11013702 | Vegetation | 2025-08-14 14:28 | -07:00 | 08/12 - 08/18 | 2025-08-14 17:41 | -07:00 | 183.8264 | FTS | 44486 | 242 | 8 | 7 | 3 | 0 | 0 | 0 | 193
25-0087127 | Madera | OAKHURST 1101 | OAKHURST 11015490 | Unknown Cause | 2025-08-14 19:31 | -07:00 | 08/12 - 08/18 | 2025-08-14 21:23 | -07:00 | 42.8017 | FTS | 66685 | 1558 | 154 | 120 | 29 | 2 | 0 | 0 | 112
25-0087128 | Contra Costa | VALLEY VIEW 1105 | VALLEY VIEW 1105P190 | Equipment Failure/Involved | 2025-08-14 19:32 | -07:00 | 08/12 - 08/18 | 2025-08-14 21:41 | -07:00 | 98.9436 | FTS | 156034 | 1577 | 74 | 48 | 21 | 2 | 0 | 0 | 129
25-0086818 | Calaveras | FROGTOWN 1702 | FROGTOWN 170274648 | Equipment Failure/Involved | 2025-08-14 09:35 | -07:00 | 08/12 - 08/18 | 2025-08-15 00:55 | -07:00 | 68.5768 | FTS | 75023 | 1094 | 75 | 54 | 16 | 6 | 0 | 0 | 920
25-0087148 | Monterey | RESERVATION ROAD 1102 | RESERVATION ROAD 110222136 | 3rd Party | 2025-08-14 22:49 | -07:00 | 08/12 - 08/18 | 2025-08-15 07:09 | -07:00 | 114.3386 | FTS | 21610 | 189 | 6 | 6 | 1 | 0 | 0 | 0 | 500
25-0087169 | El Dorado | SHINGLE SPRINGS 2109 | SHINGLE SPRINGS 210961892 | Equipment Failure/Involved | 2025-08-15 06:05 | -07:00 | 08/12 - 08/18 | 2025-08-15 08:14 | -07:00 | 129 | FTS | 53277 | 413 | 43 | 34 | 2 | 0 | 0 | 12 | 129
25-0087160 | Mendocino | PHILO 1102 | PHILO 1102920 | Vegetation | 2025-08-15 01:54 | -07:00 | 08/12 - 08/18 | 2025-08-15 11:52 | -07:00 | 161.9945 | FTS | 118742 | 733 | 15 | 12 | 13 | 1 | 0 | 2 | 598
25-0087351 | Marin | NOVATO 1104 | NOVATO 1104889406 | 3rd Party | 2025-08-15 11:34 | -07:00 | 08/12 - 08/18 | 2025-08-15 12:31 | -07:00 | 57 | FTS | 171 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 57
25-0087118 | San Mateo | WOODSIDE 1101 | WOODSIDE 11018974 | Company Initiated | 2025-08-14 18:44 | -07:00 | 08/12 - 08/18 | 2025-08-15 13:01 | -07:00 | 1097 | FTS | 341167 | 311 | 6 | 4 | 14 | 2 | 0 | 2 | 1097
25-0087164 | Sonoma | MONTE RIO 1111 | MONTE RIO 111164758 | Equipment Failure/Involved | 2025-08-15 04:52 | -07:00 | 08/12 - 08/18 | 2025-08-15 14:01 | -07:00 | 172.7553 | FTS | 97434 | 564 | 27 | 19 | 16 | 1 | 0 | 0 | 549
25-0087343 | Sonoma | FORT ROSS 1121 | FORT ROSS 1121134 | Unknown Cause | 2025-08-15 11:12 | -07:00 | 08/12 - 08/18 | 2025-08-15 14:41 | -07:00 | 206.3957 | FTS | 48503 | 235 | 5 | 5 | 8 | 0 | 0 | 1 | 209
25-0087474 | Placer | FLINT 1101 | FLINT 1101750 | Unknown Cause | 2025-08-15 14:51 | -07:00 | 08/12 - 08/18 | 2025-08-15 18:17 | -07:00 | 182.1856 | FTS | 159048 | 873 | 63 | 46 | 10 | 0 | 0 | 5 | 206
25-0087544 | Santa Cruz | CAMP EVERS 2107 | CAMP EVERS 2105601610 | Vegetation | 2025-08-15 18:56 | -07:00 | 08/12 - 08/18 | 2025-08-15 21:45 | -07:00 | 169 | FTS | 16731 | 99 | 9 | 8 | 1 | 0 | 0 | 9 | 169
25-0087577 | Contra Costa | CLAYTON 2212 | CLAYTON 221296224 | Animal | 2025-08-16 06:22 | -07:00 | 08/12 - 08/18 | 2025-08-16 07:01 | -07:00 | 34.2188 | FTS | 8760 | 256 | 18 | 12 | 3 | 0 | 0 | 9 | 39
25-0087574 | Placer | WISE 1102 | WISE 11022054 | Unknown Cause | 2025-08-16 06:09 | -07:00 | 08/12 - 08/18 | 2025-08-16 08:11 | -07:00 | 101.8824 | FTS | 22516 | 221 | 20 | 14 | 2 | 0 | 0 | 12 | 122
25-0087580 | Shasta | PIT NO 1 1101 | PIT NO 1 11019702 | Unknown Cause | 2025-08-16 06:39 | -07:00 | 08/12 - 08/18 | 2025-08-16 08:47 | -07:00 | 86.7079 | FTS | 15434 | 178 | 8 | 7 | 16 | 1 | 2 | 0 | 128
25-0087587 | Marin | SAN RAFAEL 1110 | SAN RAFAEL 11011210 | Animal | 2025-08-16 07:26 | -07:00 | 08/12 - 08/18 | 2025-08-16 08:53 | -07:00 | 78.4863 | HLT | 287260 | 3660 | 85 | 58 | 75 | 33 | 0 | 3 | 87
25-0087599 | Sonoma | COTATI 1102 | COTATI 110259258 | Unknown Cause | 2025-08-16 08:25 | -07:00 | 08/12 - 08/18 | 2025-08-16 09:59 | -07:00 | 77.1111 | FTS | 19432 | 252 | 13 | 12 | 4 | 0 | 0 | 1 | 94
25-0087559 | Monterey | GREEN VALLEY 2103 | ROB ROY 2104422016 | Vegetation | 2025-08-15 23:55 | -07:00 | 08/12 - 08/18 | 2025-08-16 11:11 | -07:00 | 54.9054 | FTS | 53423 | 973 | 68 | 60 | 18 | 4 | 0 | 0 | 676
25-0087602 | Nevada | BRUNSWICK 1106 | BRUNSWICK 110651486 | Unknown Cause | 2025-08-16 08:44 | -07:00 | 08/12 - 08/18 | 2025-08-16 11:29 | -07:00 | 165 | FTS | 143385 | 869 | 67 | 50 | 7 | 0 | 0 | 18 | 165
25-0087638 | Mariposa | MARIPOSA 2101 | MARIPOSA 2101151918 | Company Initiated | 2025-08-16 11:44 | -07:00 | 08/12 - 08/18 | 2025-08-16 12:53 | -07:00 | 69 | FTS | 198375 | 2875 | 188 | 132 | 46 | 0 | 0 | 2 | 69
25-0087623 | Santa Cruz | CAMP EVERS 2107 | BURNS 210136516 | Unknown Cause | 2025-08-16 10:14 | -07:00 | 08/12 - 08/18 | 2025-08-16 13:37 | -07:00 | 109.8421 | FTS | 58436 | 532 | 30 | 24 | 17 | 9 | 0 | 23 | 203
25-0087586 | Alameda | CASTRO VALLEY 1108 | CASTRO VALLEY 1108343456 | Equipment Failure/Involved | 2025-08-16 07:25 | -07:00 | 08/12 - 08/18 | 2025-08-16 15:18 | -07:00 | 35.8912 | FTS | 66650 | 1857 | 131 | 96 | 28 | 2 | 0 | 1 | 473
25-0087670 | Monterey | LAURELES 1111 | LAURELES 1111822080 | Unknown Cause | 2025-08-16 14:06 | -07:00 | 08/12 - 08/18 | 2025-08-16 15:42 | -07:00 | 96 | FTS | 12384 | 129 | 4 | 2 | 2 | 0 | 0 | 1 | 96
25-0087695 | Santa Clara | HICKS 1116 | HICKS 1116583284 | Company Initiated | 2025-08-16 16:56 | -07:00 | 08/12 - 08/18 | 2025-08-16 17:45 | -07:00 | 49 | FTS | 784 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 49
25-0087699 | Shasta | BURNEY 1101 | BURNEY 1101355340 | 3rd Party | 2025-08-16 17:42 | -07:00 | 08/12 - 08/18 | 2025-08-16 18:21 | -07:00 | 39 | FTS | 39 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 39
25-0087571 | Alameda | SAN RAMON 2106 | SAN RAMON 2106MR285 | Equipment Failure/Involved | 2025-08-16 05:13 | -07:00 | 08/12 - 08/18 | 2025-08-16 19:14 | -07:00 | 38.5888 | FTS | 33688 | 873 | 31 | 21 | 12 | 2 | 0 | 0 | 841
25-0087702 | Santa Clara | MORGAN HILL 2111 | MORGAN HILL 2111997000 | Unknown Cause | 2025-08-16 18:10 | -07:00 | 08/12 - 08/18 | 2025-08-16 19:59 | -07:00 | 109 | FTS | 44254 | 406 | 18 | 8 | 4 | 0 | 0 | 0 | 109
25-0087710 | Placer | LINCOLN 1104 | LINCOLN 1104818790 | Unknown Cause | 2025-08-16 20:25 | -07:00 | 08/12 - 08/18 | 2025-08-16 22:08 | -07:00 | 103 | FTS | 5974 | 58 | 4 | 4 | 0 | 0 | 0 | 1 | 103
25-0087711 | Santa Clara | SWIFT 2102 | SWIFT 2102889948 | Unknown Cause | 2025-08-16 20:28 | -07:00 | 08/12 - 08/18 | 2025-08-16 22:08 | -07:00 | 100 | FTS | 600 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 100
25-0087728 | Amador | MARTELL 1101 | MARTELL 110111244 | Unknown Cause | 2025-08-17 06:02 | -07:00 | 08/12 - 08/18 | 2025-08-17 11:06 | -07:00 | 77.2688 | FTS | 60656 | 785 | 65 | 46 | 9 | 0 | 0 | 13 | 304
25-0084993 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113A12 | Environmental/External | 2025-08-08 15:33 | -07:00 | 08/12 - 08/18 | 2025-08-17 12:00 | -07:00 | 78.6107 | FTS | 10298 | 131 | 3 | 2 | 4 | 0 | 0 | 3 | 12747
25-0087740 | Napa | PUEBLO 1105 | PUEBLO 1105426584 | Unknown Cause | 2025-08-17 08:34 | -07:00 | 08/12 - 08/18 | 2025-08-17 12:41 | -07:00 | 213.5574 | FTS | 39081 | 183 | 0 | 0 | 1 | 0 | 0 | 2 | 247
25-0087713 | El Dorado | PLACERVILLE 2106 | PLACERVILLE 210611132 | Unknown Cause | 2025-08-16 20:50 | -07:00 | 08/12 - 08/18 | 2025-08-17 16:04 | -07:00 | 163.835 | FTS | 1381784 | 8434 | 380 | 282 | 92 | 19 | 1 | 36 | 1154
25-0087738 | Marin | IGNACIO 1104 | IGNACIO 11041290 | 3rd Party | 2025-08-17 08:10 | -07:00 | 08/12 - 08/18 | 2025-08-17 16:22 | -07:00 | 78.8523 | FTS | 70494 | 894 | 27 | 19 | 35 | 0 | 0 | 0 | 492
25-0087733 | Shasta | PANORAMA 1102 | PANORAMA 1102280170 | Vegetation | 2025-08-17 07:01 | -07:00 | 08/12 - 08/18 | 2025-08-17 17:23 | -07:00 | 91.0722 | FTS | 8834 | 97 | 3 | 1 | 2 | 0 | 0 | 0 | 622
25-0087776 | Butte | WYANDOTTE 1109 | WYANDOTTE 110979932 | Unknown Cause | 2025-08-17 14:56 | -07:00 | 08/12 - 08/18 | 2025-08-17 17:56 | -07:00 | 115.4194 | FTS | 46514 | 403 | 33 | 27 | 1 | 0 | 0 | 2 | 180
25-0087794 | Santa Clara | HICKS 1116 | HICKS 1116583284 | Company Initiated | 2025-08-17 17:34 | -07:00 | 08/12 - 08/18 | 2025-08-17 18:21 | -07:00 | 47 | FTS | 752 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 47
25-0087772 | Placer | BELL 1107 | BELL 11072400 | Unknown Cause | 2025-08-17 13:47 | -07:00 | 08/12 - 08/18 | 2025-08-17 18:41 | -07:00 | 257.1298 | FTS | 134736 | 524 | 34 | 25 | 2 | 1 | 0 | 10 | 294
25-0087804 | Monterey | GONZALES 1101 | GONZALES 11013094 | Unknown Cause | 2025-08-17 18:59 | -07:00 | 08/12 - 08/18 | 2025-08-17 21:52 | -07:00 | 69.6471 | FTS | 4736 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 173
25-0087811 | Sutter | PEASE 1104 | PEASE 11041228 | Unknown Cause | 2025-08-17 21:06 | -07:00 | 08/12 - 08/18 | 2025-08-17 23:30 | -07:00 | 116.1429 | FTS | 13008 | 112 | 2 | 0 | 2 | 0 | 0 | 0 | 144
25-0087797 | San Luis Obispo | TEMPLETON 2111 | TEMPLETON 2111A66 | Vegetation | 2025-08-17 18:18 | -07:00 | 08/12 - 08/18 | 2025-08-18 03:12 | -07:00 | 64.6811 | FTS | 148896 | 2302 | 138 | 82 | 33 | 8 | 0 | 9 | 534
25-0087826 | Marin | IGNACIO 1104 | IGNACIO 11041290 | Unknown Cause | 2025-08-18 00:55 | -07:00 | 08/12 - 08/18 | 2025-08-18 07:43 | -07:00 | 77.1298 | FTS | 68954 | 894 | 27 | 19 | 35 | 0 | 0 | 0 | 408
25-0087862 | San Joaquin | CORRAL 1101 | CORRAL 1101173174 | 3rd Party | 2025-08-18 07:19 | -07:00 | 08/12 - 08/18 | 2025-08-18 07:44 | -07:00 | 25 | FTS | 25 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 25
25-0087830 | Monterey | SOLEDAD 2102 | SOLEDAD 2102304826 | Unknown Cause | 2025-08-18 04:05 | -07:00 | 08/12 - 08/18 | 2025-08-18 07:50 | -07:00 | 225 | FTS | 11025 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 225
25-0087923 | Humboldt | FRUITLAND 1142 | FRUITLAND 11426054 | Company Initiated | 2025-08-18 09:37 | -07:00 | 08/12 - 08/18 | 2025-08-18 09:48 | -07:00 | 11 | FTS | 5302 | 482 | 17 | 10 | 13 | 4 | 0 | 0 | 11
25-0087922 | Placer | LINCOLN 1104 | LINCOLN 1104685276 | Animal | 2025-08-18 09:39 | -07:00 | 08/12 - 08/18 | 2025-08-18 11:24 | -07:00 | 105 | FTS | 28245 | 269 | 20 | 15 | 2 | 0 | 0 | 5 | 105
25-0087906 | Shasta | WILDWOOD 1101 | WILDWOOD 11011454 | Unknown Cause | 2025-08-18 09:07 | -07:00 | 08/12 - 08/18 | 2025-08-18 11:28 | -07:00 | 141 | FTS | 2397 | 17 | 1 | 0 | 3 | 0 | 0 | 0 | 141
25-0083796 | Butte | BANGOR 1101 | BANGOR 11011804 | Company Initiated | 2025-08-18 11:18 | -07:00 | 08/12 - 08/18 | 2025-08-18 12:01 | -07:00 | 43 | FTS | 2967 | 69 | 6 | 5 | 1 | 0 | 0 | 0 | 43
25-0087793 | Monterey | DEL MONTE 2104 | DEL MONTE 21043088 | Equipment Failure/Involved | 2025-08-17 17:26 | -07:00 | 08/12 - 08/18 | 2025-08-18 15:06 | -07:00 | 78.6458 | FTS | 26425 | 336 | 19 | 15 | 3 | 1 | 0 | 1 | 1300
25-0088135 | Napa | SILVERADO 2102 | SILVERADO 2102922022 | Company Initiated | 2025-08-18 14:53 | -07:00 | 08/12 - 08/18 | 2025-08-18 17:47 | -07:00 | 174 | FTS | 7308 | 42 | 1 | 1 | 0 | 0 | 0 | 0 | 174
25-0088160 | Santa Barbara | CABRILLO 1103 | CABRILLO 1103Y46 | Unknown Cause | 2025-08-18 16:01 | -07:00 | 08/12 - 08/18 | 2025-08-18 18:13 | -07:00 | 132 | FTS | 36432 | 276 | 2 | 2 | 5 | 0 | 0 | 0 | 132
25-0087969 | Placer | FORESTHILL 1102 | FORESTHILL 1102CB | Company Initiated | 2025-08-18 10:54 | -07:00 | 08/12 - 08/18 | 2025-08-18 18:41 | -07:00 | 79.2385 | FTS | 34548 | 436 | 38 | 28 | 5 | 0 | 0 | 3 | 467
25-0088199 | Monterey | GABILAN 1101 | GABILAN 1101566352 | Unknown Cause | 2025-08-18 18:29 | -07:00 | 08/12 - 08/18 | 2025-08-18 18:58 | -07:00 | 29 | FTS | 145 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 29
25-0088163 | El Dorado | APPLE HILL 2102 | APPLE HILL 21029722 | Equipment Failure/Involved | 2025-08-18 15:24 | -07:00 | 08/12 - 08/18 | 2025-08-18 19:21 | -07:00 | 237 | FTS | 28203 | 119 | 3 | 2 | 4 | 0 | 0 | 2 | 237
25-0088211 | Tuolumne | PEORIA 1704 | PEORIA 1704CB | Unknown Cause | 2025-08-18 20:11 | -07:00 | 08/12 - 08/18 | 2025-08-18 20:48 | -07:00 | 37 | FTS | 120398 | 3254 | 226 | 158 | 78 | 1 | 4 | 3 | 37
25-0087889 | Marin | SAN RAFAEL 1105 | SAN RAFAEL 1105645362 | Equipment Failure/Involved | 2025-08-18 08:38 | -07:00 | 08/19 - 08/25 | 2025-08-19 01:15 | -07:00 | 173.751 | FTS | 87223 | 502 | 18 | 15 | 5 | 1 | 0 | 0 | 997
25-0088221 | Santa Barbara | SISQUOC 1102 | SISQUOC 1102846970 | Unknown Cause | 2025-08-18 22:11 | -07:00 | 08/19 - 08/25 | 2025-08-19 02:03 | -07:00 | 232 | FTS | 12528 | 54 | 0 | 0 | 1 | 0 | 0 | 0 | 232
25-0088193 | Monterey | GABILAN 1101 | GABILAN 11013034 | Equipment Failure/Involved | 2025-08-18 17:32 | -07:00 | 08/19 - 08/25 | 2025-08-19 02:18 | -07:00 | 53.051 | FTS | 23926 | 451 | 18 | 15 | 7 | 0 | 0 | 0 | 526
25-0088222 | Tuolumne | CURTIS 1702 | CURTIS 170247488 | Animal | 2025-08-18 23:32 | -07:00 | 08/19 - 08/25 | 2025-08-19 07:01 | -07:00 | 148.3898 | FTS | 87550 | 590 | 46 | 40 | 7 | 8 | 0 | 2 | 449
25-0088243 | Mendocino | PHILO 1101 | PHILO 11013700 | Unknown Cause | 2025-08-19 06:19 | -07:00 | 08/19 - 08/25 | 2025-08-19 08:39 | -07:00 | 91.6948 | FTS | 22832 | 249 | 12 | 10 | 11 | 0 | 0 | 0 | 140
25-0088269 | Fresno | AUBERRY 1101 | AUBERRY 1101R2838 | Unknown Cause | 2025-08-19 07:38 | -07:00 | 08/19 - 08/25 | 2025-08-19 11:02 | -07:00 | 204 | FTS | 86496 | 424 | 24 | 18 | 27 | 0 | 0 | 1 | 204
25-0088375 | Santa Barbara | PALMER 1101 | PALMER 1101M88 | 3rd Party | 2025-08-19 10:02 | -07:00 | 08/19 - 08/25 | 2025-08-19 11:07 | -07:00 | 65 | FTS | 10400 | 160 | 0 | 0 | 5 | 0 | 0 | 0 | 65
25-0088210 | Santa Clara | SWIFT 2110 | SWIFT 2110853720 | Unknown Cause | 2025-08-18 19:55 | -07:00 | 08/19 - 08/25 | 2025-08-19 11:27 | -07:00 | 932 | FTS | 61512 | 66 | 1 | 0 | 5 | 0 | 0 | 0 | 932
25-0088237 | Santa Cruz | PAUL SWEET 2109 | ROB ROY 210538430 | Vegetation | 2025-08-19 05:16 | -07:00 | 08/19 - 08/25 | 2025-08-19 12:20 | -07:00 | 70.8043 | FTS | 217086 | 3066 | 180 | 145 | 26 | 3 | 0 | 0 | 424
25-0088558 | Fresno | AUBERRY 1101 | AUBERRY 1101D323 | Company Initiated | 2025-08-19 12:21 | -07:00 | 08/19 - 08/25 | 2025-08-19 14:17 | -07:00 | 116 | FTS | 14848 | 128 | 14 | 11 | 0 | 0 | 0 | 0 | 116
25-0088268 | Nevada | BRUNSWICK 1105 | BRUNSWICK 11052210 | Animal | 2025-08-19 07:37 | -07:00 | 08/19 - 08/25 | 2025-08-19 14:37 | -07:00 | 75.3907 | FTS | 66570 | 883 | 49 | 33 | 17 | 0 | 0 | 4 | 420
25-0088604 | Mariposa | MARIPOSA 2101 | MARIPOSA 210110990 | Company Initiated | 2025-08-19 14:41 | -07:00 | 08/19 - 08/25 | 2025-08-19 14:52 | -07:00 | 11 | FTS | 5280 | 480 | 28 | 23 | 3 | 0 | 0 | 1 | 11
25-0088596 | San Mateo | RALSTON 1102 | RALSTON 11029126 | Unknown Cause | 2025-08-19 14:23 | -07:00 | 08/19 - 08/25 | 2025-08-19 15:55 | -07:00 | 92 | FTS | 47012 | 511 | 21 | 12 | 7 | 2 | 0 | 0 | 92
25-0088678 | Mendocino | WILLITS 1103 | WILLITS 1103409216 | Company Initiated | 2025-08-19 16:53 | -07:00 | 08/19 - 08/25 | 2025-08-19 18:37 | -07:00 | 103.1064 | FTS | 9692 | 94 | 7 | 4 | 4 | 0 | 0 | 0 | 104
25-0088735 | El Dorado | APPLE HILL 1104 | APPLE HILL 1104275024 | Unknown Cause | 2025-08-19 20:26 | -07:00 | 08/19 - 08/25 | 2025-08-20 01:38 | -07:00 | 312 | FTS | 8424 | 27 | 1 | 0 | 0 | 0 | 0 | 1 | 312
25-0088743 | Mendocino | HOPLAND 1101 | HOPLAND 110180620 | Unknown Cause | 2025-08-20 03:00 | -07:00 | 08/19 - 08/25 | 2025-08-20 04:46 | -07:00 | 106 | FTS | 7420 | 70 | 3 | 2 | 1 | 0 | 0 | 0 | 106
25-0088812 | Calaveras | FROGTOWN 1702 | FROGTOWN 170275252 | Unknown Cause | 2025-08-20 06:17 | -07:00 | 08/19 - 08/25 | 2025-08-20 08:05 | -07:00 | 108 | FTS | 4320 | 40 | 0 | 0 | 1 | 0 | 0 | 1 | 108
25-0088724 | Napa | PUEBLO 2104 | PUEBLO 210438686 | Unknown Cause | 2025-08-19 20:20 | -07:00 | 08/19 - 08/25 | 2025-08-20 08:56 | -07:00 | 123.8178 | FTS | 114160 | 922 | 25 | 15 | 15 | 0 | 0 | 0 | 756
25-0088686 | Fresno | DUNLAP 1103 | DUNLAP 11037040 | Unknown Cause | 2025-08-19 17:23 | -07:00 | 08/19 - 08/25 | 2025-08-20 09:13 | -07:00 | 319.6873 | FTS | 128834 | 403 | 16 | 11 | 0 | 0 | 0 | 0 | 950
25-0088948 | Amador | IONE 1101 | IONE 1101510200 | Unknown Cause | 2025-08-20 11:21 | -07:00 | 08/19 - 08/25 | 2025-08-20 14:19 | -07:00 | 178 | FTS | 17978 | 101 | 5 | 3 | 2 | 0 | 0 | 2 | 178
25-0088937 | Plumas | BIG MEADOWS 2101 | BIG MEADOWS 21012056 | Unknown Cause | 2025-08-20 11:02 | -07:00 | 08/19 - 08/25 | 2025-08-20 14:27 | -07:00 | 87.3936 | FTS | 65720 | 752 | 39 | 30 | 16 | 2 | 1 | 2 | 205
25-0089072 | Amador | PINE GROVE 1102 | PINE GROVE 11023172 | Company Initiated | 2025-08-20 14:52 | -07:00 | 08/19 - 08/25 | 2025-08-20 16:26 | -07:00 | 94 | FTS | 2256 | 24 | 3 | 3 | 0 | 0 | 0 | 0 | 94
25-0089009 | Alameda | SAN RAMON 2103 | SAN RAMON 2103MR279 | Unknown Cause | 2025-08-20 12:47 | -07:00 | 08/19 - 08/25 | 2025-08-20 17:52 | -07:00 | 165.0168 | FTS | 353466 | 2142 | 128 | 98 | 30 | 2 | 0 | 1 | 305
25-0089165 | Nevada | GRASS VALLEY 1103 | GRASS VALLEY 11032110 | Vegetation | 2025-08-20 20:19 | -07:00 | 08/19 - 08/25 | 2025-08-21 03:51 | -07:00 | 62.0596 | FTS | 53123 | 856 | 66 | 45 | 20 | 4 | 0 | 17 | 452
25-0089205 | Monterey | GABILAN 1101 | GABILAN 11013034 | 3rd Party | 2025-08-21 06:18 | -07:00 | 08/19 - 08/25 | 2025-08-21 07:12 | -07:00 | 54 | FTS | 1890 | 35 | 2 | 2 | 0 | 0 | 0 | 0 | 54
25-0089140 | Sonoma | FITCH MOUNTAIN 1113 | FITCH MOUNTAIN 1113443164 | Unknown Cause | 2025-08-20 18:24 | -07:00 | 08/19 - 08/25 | 2025-08-21 08:49 | -07:00 | 428.6139 | FTS | 86580 | 202 | 6 | 6 | 7 | 0 | 0 | 6 | 865
25-0089219 | El Dorado | APPLE HILL 2102 | APPLE HILL 21021532 | Animal | 2025-08-21 07:43 | -07:00 | 08/19 - 08/25 | 2025-08-21 08:58 | -07:00 | 75 | FTS | 2400 | 32 | 3 | 1 | 0 | 0 | 0 | 2 | 75
25-0089241 | Santa Cruz | GREEN VALLEY 2101 | GREEN VALLEY 2101454176 | Animal | 2025-08-21 08:26 | -07:00 | 08/19 - 08/25 | 2025-08-21 10:17 | -07:00 | 111 | FTS | 5661 | 51 | 2 | 2 | 0 | 0 | 0 | 0 | 111
25-0089271 | Amador | CLAY 1103 | CLAY 110334338 | Animal | 2025-08-21 09:30 | -07:00 | 08/19 - 08/25 | 2025-08-21 10:50 | -07:00 | 57.027 | FTS | 4220 | 74 | 3 | 2 | 4 | 0 | 0 | 0 | 80
25-0089190 | San Mateo | WOODSIDE 1101 | WOODSIDE 11018974 | Company Initiated | 2025-08-20 23:44 | -07:00 | 08/19 - 08/25 | 2025-08-21 12:54 | -07:00 | 790 | FTS | 245690 | 311 | 6 | 4 | 14 | 2 | 0 | 2 | 790
25-0089324 | Calaveras | STANISLAUS 1702 | STANISLAUS 1702247448 | Unknown Cause | 2025-08-21 11:15 | -07:00 | 08/19 - 08/25 | 2025-08-21 12:57 | -07:00 | 78.5486 | FTS | 13746 | 175 | 4 | 3 | 2 | 0 | 0 | 0 | 102
25-0089299 | Santa Clara | LLAGAS 2101 | LLAGAS 2101XR244 | Equipment Failure/Involved | 2025-08-21 10:29 | -07:00 | 08/19 - 08/25 | 2025-08-21 13:05 | -07:00 | 34.1009 | FTS | 34476 | 1011 | 34 | 20 | 16 | 2 | 0 | 8 | 156
25-0089506 | Alameda | LAS POSITAS 2108 | LAS POSITAS 2108794616 | Equipment Failure/Involved | 2025-08-21 16:13 | -07:00 | 08/19 - 08/25 | 2025-08-21 17:08 | -07:00 | 48.6497 | FTS | 209145 | 4299 | 188 | 141 | 58 | 2 | 2 | 0 | 55
25-0089500 | San Mateo | WOODSIDE 1101 | WOODSIDE 11018974 | Company Initiated | 2025-08-21 16:09 | -07:00 | 08/19 - 08/25 | 2025-08-21 17:54 | -07:00 | 105 | FTS | 32970 | 314 | 6 | 4 | 14 | 2 | 0 | 2 | 105
25-0089492 | Yuba | BANGOR 1101 | BANGOR 11011806 | Animal | 2025-08-21 15:56 | -07:00 | 08/19 - 08/25 | 2025-08-21 18:08 | -07:00 | 81.1407 | FTS | 49009 | 604 | 37 | 24 | 4 | 0 | 0 | 8 | 132
25-0089309 | San Benito | HOLLISTER 2105 | HOLLISTER 2105475946 | 3rd Party | 2025-08-21 10:55 | -07:00 | 08/19 - 08/25 | 2025-08-21 18:28 | -07:00 | 64.672 | FTS | 8084 | 125 | 2 | 2 | 2 | 2 | 0 | 0 | 453
25-0088633 | Santa Clara | MORGAN HILL 2105 | MORGAN HILL 2105XR176 | Equipment Failure/Involved | 2025-08-19 15:22 | -07:00 | 08/19 - 08/25 | 2025-08-21 21:18 | -07:00 | 209.4534 | FTS | 231446 | 1105 | 52 | 44 | 16 | 3 | 0 | 10 | 3236
25-0089568 | San Luis Obispo | CHOLAME 2102 | CHOLAME 2102X10 | Animal | 2025-08-21 20:21 | -07:00 | 08/19 - 08/25 | 2025-08-21 22:33 | -07:00 | 132 | FTS | 13860 | 105 | 0 | 0 | 4 | 0 | 0 | 0 | 132
25-0089603 | Santa Clara | LLAGAS 2101 | LLAGAS 2101XR244 | Unknown Cause | 2025-08-22 00:19 | -07:00 | 08/19 - 08/25 | 2025-08-22 03:43 | -07:00 | 159.4214 | FTS | 161175 | 1011 | 34 | 20 | 16 | 2 | 0 | 8 | 204
25-0081886 | Santa Clara | LOS GATOS 1101 | LOS GATOS 1101CB | Company Initiated | 2025-08-22 04:24 | -07:00 | 08/19 - 08/25 | 2025-08-22 04:44 | -07:00 | 20 | FTS | 420 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 20
25-0089565 | Napa | PUEBLO 2104 | PUEBLO 210375612 | Equipment Failure/Involved | 2025-08-21 19:59 | -07:00 | 08/19 - 08/25 | 2025-08-22 08:10 | -07:00 | 110.2647 | FTS | 7498 | 68 | 5 | 2 | 0 | 0 | 0 | 0 | 731
25-0089556 | San Benito | HOLLISTER 2104 | HOLLISTER 21044782 | Equipment Failure/Involved | 2025-08-21 19:03 | -07:00 | 08/19 - 08/25 | 2025-08-22 08:22 | -07:00 | 65.7437 | FTS | 36685 | 558 | 17 | 12 | 7 | 1 | 0 | 0 | 799
25-0089625 | Santa Cruz | GREEN VALLEY 2103 | ROB ROY 210410298 | Vegetation | 2025-08-22 06:34 | -07:00 | 08/19 - 08/25 | 2025-08-22 08:28 | -07:00 | 114 | FTS | 25650 | 225 | 21 | 20 | 0 | 0 | 0 | 0 | 114
25-0089623 | El Dorado | APPLE HILL 2102 | APPLE HILL 2102836878 | Company Initiated | 2025-08-22 06:30 | -07:00 | 08/19 - 08/25 | 2025-08-22 09:30 | -07:00 | 147.1112 | FTS | 701426 | 4768 | 379 | 279 | 62 | 12 | 0 | 63 | 180
25-0089611 | San Luis Obispo | GOLDTREE 1108 | GOLDTREE 1108961060 | Equipment Failure/Involved | 2025-08-22 05:13 | -07:00 | 08/19 - 08/25 | 2025-08-22 11:00 | -07:00 | 95.7892 | FTS | 348098 | 3634 | 35 | 29 | 30 | 9 | 0 | 0 | 347
25-0089865 | Tuolumne | CURTIS 1704 | CURTIS 1704895006 | Company Initiated | 2025-08-22 13:10 | -07:00 | 08/19 - 08/25 | 2025-08-22 13:46 | -07:00 | 36 | FTS | 16092 | 447 | 29 | 20 | 7 | 2 | 0 | 1 | 36
25-0089622 | Nevada | HIGGINS 1110 | HIGGINS 11102408 | Vegetation | 2025-08-22 06:18 | -07:00 | 08/19 - 08/25 | 2025-08-22 15:41 | -07:00 | 116.7076 | FTS | 52285 | 448 | 38 | 28 | 3 | 0 | 0 | 17 | 563
25-0089942 | Amador | PINE GROVE 1102 | PINE GROVE 1102269286 | Company Initiated | 2025-08-22 15:42 | -07:00 | 08/19 - 08/25 | 2025-08-22 17:04 | -07:00 | 82 | FTS | 6724 | 82 | 4 | 2 | 3 | 2 | 0 | 0 | 82
25-0089840 | Sonoma | FITCH MOUNTAIN 1113 | FITCH MOUNTAIN 1113443164 | Equipment Failure/Involved | 2025-08-22 11:38 | -07:00 | 08/19 - 08/25 | 2025-08-22 17:18 | -07:00 | 18.2178 | FTS | 3680 | 202 | 6 | 6 | 7 | 0 | 0 | 6 | 340
25-0089969 | Butte | WYANDOTTE 1110 | WYANDOTTE 1110747922 | Animal | 2025-08-22 17:37 | -07:00 | 08/19 - 08/25 | 2025-08-22 18:58 | -07:00 | 78.5428 | FTS | 138471 | 1763 | 187 | 133 | 29 | 0 | 0 | 1 | 81
25-0089939 | Monterey | CAMPHORA 1101 | CAMPHORA 110122412 | Animal | 2025-08-22 15:43 | -07:00 | 08/19 - 08/25 | 2025-08-22 19:35 | -07:00 | 136.6111 | FTS | 17213 | 126 | 0 | 0 | 0 | 0 | 0 | 0 | 232
25-0089905 | Placer | AUBURN 1101 | AUBURN 1101173014 | Vegetation | 2025-08-22 14:38 | -07:00 | 08/19 - 08/25 | 2025-08-22 19:47 | -07:00 | 57.7437 | FTS | 52720 | 913 | 31 | 24 | 10 | 1 | 0 | 0 | 309
25-0089981 | Santa Clara | MORGAN HILL 2111 | MORGAN HILL 2111997000 | Animal | 2025-08-22 18:51 | -07:00 | 08/19 - 08/25 | 2025-08-22 21:11 | -07:00 | 139.7488 | FTS | 56738 | 406 | 18 | 8 | 4 | 0 | 0 | 0 | 140
25-0090012 | Sonoma | SONOMA 1105 | SONOMA 1105539450 | Unknown Cause | 2025-08-23 03:28 | -07:00 | 08/19 - 08/25 | 2025-08-23 04:34 | -07:00 | 66 | FTS | 4554 | 69 | 1 | 0 | 0 | 0 | 0 | 1 | 66
25-0090018 | Sonoma | BELLEVUE 2101 | BELLEVUE 2101270638 | Unknown Cause | 2025-08-23 06:10 | -07:00 | 08/19 - 08/25 | 2025-08-23 07:11 | -07:00 | 48.3279 | FTS | 32718 | 677 | 38 | 32 | 14 | 0 | 0 | 16 | 61
25-0090006 | San Luis Obispo | PERRY 1101 | PERRY 1101V88 | Equipment Failure/Involved | 2025-08-23 00:18 | -07:00 | 08/19 - 08/25 | 2025-08-23 08:18 | -07:00 | 249.8539 | FTS | 184642 | 739 | 19 | 11 | 15 | 2 | 0 | 0 | 480
25-0089983 | Colusa | ELK CREEK 1101 | ELK CREEK 11012008 | Unknown Cause | 2025-08-22 19:00 | -07:00 | 08/19 - 08/25 | 2025-08-23 08:58 | -07:00 | 515.6941 | FTS | 288273 | 559 | 31 | 22 | 26 | 3 | 0 | 0 | 838
25-0090017 | Tuolumne | CURTIS 1705 | CURTIS 170539256 | Unknown Cause | 2025-08-23 06:10 | -07:00 | 08/19 - 08/25 | 2025-08-23 09:05 | -07:00 | 80.8046 | FTS | 42180 | 522 | 48 | 31 | 4 | 0 | 0 | 1 | 175
25-0089990 | San Benito | SAN JUSTO 1101 | SAN JUSTO 11014002 | Vegetation | 2025-08-22 20:04 | -07:00 | 08/19 - 08/25 | 2025-08-23 10:05 | -07:00 | 108.2059 | FTS | 18395 | 170 | 12 | 7 | 13 | 0 | 0 | 3 | 841
25-0090038 | Fresno | CANTUA 1101 | CANTUA 1101CB | 3rd Party | 2025-08-23 08:31 | -07:00 | 08/19 - 08/25 | 2025-08-23 10:53 | -07:00 | 142 | FTS | 8520 | 60 | 0 | 0 | 1 | 0 | 0 | 0 | 142
25-0090008 | San Mateo | WOODSIDE 1101 | WOODSIDE 110147872 | Unknown Cause | 2025-08-23 01:18 | -07:00 | 08/19 - 08/25 | 2025-08-23 11:50 | -07:00 | 524.1774 | FTS | 129996 | 248 | 13 | 8 | 14 | 1 | 0 | 0 | 632
25-0090071 | Kern | TEJON 1106 | TEJON 11062436 | Environmental/External | 2025-08-23 10:59 | -07:00 | 08/19 - 08/25 | 2025-08-23 12:51 | -07:00 | 112 | HLT | 11536 | 103 | 0 | 0 | 4 | 0 | 0 | 0 | 112
25-0090031 | Contra Costa | VALLEY VIEW 1105 | VALLEY VIEW 1105305072 | Animal | 2025-08-23 06:41 | -07:00 | 08/19 - 08/25 | 2025-08-23 12:56 | -07:00 | 100.5786 | FTS | 30073 | 299 | 12 | 9 | 7 | 0 | 0 | 0 | 375
25-0090090 | Amador | IONE 1101 | IONE 1101510200 | Unknown Cause | 2025-08-23 11:42 | -07:00 | 08/19 - 08/25 | 2025-08-23 13:57 | -07:00 | 135 | FTS | 13635 | 101 | 5 | 3 | 2 | 0 | 0 | 2 | 135
25-0089994 | Santa Cruz | CAMP EVERS 2106 | CAMP EVERS 210612518 | Equipment Failure/Involved | 2025-08-22 21:27 | -07:00 | 08/19 - 08/25 | 2025-08-23 15:55 | -07:00 | 221.8953 | FTS | 19083 | 86 | 7 | 6 | 4 | 3 | 0 | 1 | 1108
25-0090106 | Tulare | DUNLAP 1102 | DUNLAP 110239190 | Environmental/External | 2025-08-23 13:08 | -07:00 | 08/19 - 08/25 | 2025-08-23 16:51 | -07:00 | 223 | FTS | 3791 | 17 | 3 | 3 | 0 | 0 | 0 | 1 | 223
25-0090039 | Humboldt | WILLOW CREEK 1101 | WILLOW CREEK 11013050 | 3rd Party | 2025-08-23 08:34 | -07:00 | 08/19 - 08/25 | 2025-08-23 17:39 | -07:00 | 504.25 | FTS | 8068 | 16 | 0 | 0 | 5 | 0 | 0 | 0 | 545
25-0090134 | Monterey | GONZALES 1101 | GONZALES 11013094 | 3rd Party | 2025-08-23 15:38 | -07:00 | 08/19 - 08/25 | 2025-08-23 17:52 | -07:00 | 134 | FTS | 9112 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 134
25-0090114 | Fresno | HAAS 2101 | HAAS 2101R2770 | Environmental/External | 2025-08-23 13:40 | -07:00 | 08/19 - 08/25 | 2025-08-23 18:06 | -07:00 | 203.274 | FTS | 14839 | 73 | 0 | 0 | 1 | 0 | 0 | 0 | 266
25-0090101 | Fresno | DUNLAP 1102 | DUNLAP 11027360 | Environmental/External | 2025-08-23 13:07 | -07:00 | 08/19 - 08/25 | 2025-08-23 18:07 | -07:00 | 296.625 | FTS | 18984 | 64 | 4 | 4 | 1 | 0 | 0 | 0 | 300
25-0090179 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113CB | Animal | 2025-08-23 18:58 | -07:00 | 08/19 - 08/25 | 2025-08-23 19:59 | -07:00 | 61 | FTS | 32757 | 537 | 28 | 17 | 8 | 0 | 0 | 0 | 61
25-0090176 | Mendocino | UKIAH 1114 | UKIAH 1114380432 | Unknown Cause | 2025-08-23 18:31 | -07:00 | 08/19 - 08/25 | 2025-08-23 21:28 | -07:00 | 177 | FTS | 22656 | 128 | 2 | 1 | 7 | 0 | 0 | 0 | 177
25-0090100 | Fresno | SAND CREEK 1103 | SAND CREEK 1103818064 | Environmental/External | 2025-08-23 13:06 | -07:00 | 08/19 - 08/25 | 2025-08-23 21:59 | -07:00 | 287.1724 | FTS | 149904 | 522 | 51 | 33 | 5 | 0 | 0 | 1 | 533
25-0090186 | Nevada | HIGGINS 1109 | HIGGINS 1109594 | Unknown Cause | 2025-08-23 20:05 | -07:00 | 08/19 - 08/25 | 2025-08-23 22:32 | -07:00 | 63.8966 | FTS | 33354 | 522 | 38 | 30 | 4 | 0 | 0 | 11 | 147
25-0090188 | Nevada | HIGGINS 1109 | HIGGINS 110950078 | Company Initiated | 2025-08-23 20:06 | -07:00 | 08/19 - 08/25 | 2025-08-24 00:09 | -07:00 | 243 | FTS | 52488 | 216 | 18 | 14 | 3 | 0 | 0 | 3 | 243
25-0090207 | El Dorado | DIAMOND SPRINGS 1103 | DIAMOND SPRINGS 11039432 | Vegetation | 2025-08-24 00:01 | -07:00 | 08/19 - 08/25 | 2025-08-24 02:12 | -07:00 | 131 | FTS | 72574 | 554 | 53 | 37 | 8 | 0 | 0 | 2 | 131
25-0090181 | Sonoma | DUNBAR 1103 | DUNBAR 1103234 | Vegetation | 2025-08-23 19:07 | -07:00 | 08/19 - 08/25 | 2025-08-24 03:05 | -07:00 | 72.8913 | FTS | 179021 | 2456 | 253 | 199 | 19 | 0 | 0 | 23 | 478
25-0090220 | San Luis Obispo | ATASCADERO 1102 | ATASCADERO 1102A26 | Animal | 2025-08-24 06:38 | -07:00 | 08/19 - 08/25 | 2025-08-24 07:35 | -07:00 | 57 | FTS | 163248 | 2864 | 96 | 66 | 24 | 3 | 0 | 0 | 57
25-0090206 | Alameda | CAYETANO 2109 | CAYETANO 2109884904 | Unknown Cause | 2025-08-23 23:44 | -07:00 | 08/19 - 08/25 | 2025-08-24 07:43 | -07:00 | 452.0055 | FTS | 82717 | 183 | 10 | 6 | 10 | 0 | 0 | 3 | 479
25-0090218 | San Luis Obispo | TEMPLETON 2111 | TEMPLETON 2111461692 | Unknown Cause | 2025-08-24 06:11 | -07:00 | 08/19 - 08/25 | 2025-08-24 08:33 | -07:00 | 63.984 | FTS | 84139 | 1315 | 72 | 42 | 13 | 4 | 0 | 7 | 142
25-0090216 | Humboldt | FRUITLAND 1141 | FRUITLAND 1141CB | Vegetation | 2025-08-24 05:23 | -07:00 | 08/19 - 08/25 | 2025-08-24 08:35 | -07:00 | 168.0057 | FTS | 175398 | 1044 | 33 | 23 | 23 | 4 | 0 | 1 | 192
25-0090219 | Sonoma | FITCH MOUNTAIN 1113 | FITCH MOUNTAIN 1113775992 | Unknown Cause | 2025-08-24 06:22 | -07:00 | 08/19 - 08/25 | 2025-08-24 08:47 | -07:00 | 113.8507 | FTS | 40417 | 355 | 7 | 4 | 1 | 0 | 0 | 4 | 145
25-0090112 | Tulare | SAND CREEK 1103 | SAND CREEK 1103416018 | Unknown Cause | 2025-08-23 13:52 | -07:00 | 08/19 - 08/25 | 2025-08-24 09:14 | -07:00 | 439.2623 | FTS | 53590 | 122 | 2 | 2 | 3 | 1 | 0 | 0 | 1162
25-0090097 | Tulare | SAND CREEK 1103 | SAND CREEK 11037110 | Environmental/External | 2025-08-23 12:58 | -07:00 | 08/19 - 08/25 | 2025-08-24 09:17 | -07:00 | 1214.5872 | FTS | 208909 | 172 | 4 | 4 | 7 | 0 | 0 | 0 | 1219
25-0090075 | Kern | POSO MOUNTAIN 2103 | POSO MOUNTAIN 2103CB | Environmental/External | 2025-08-23 11:18 | -07:00 | 08/19 - 08/25 | 2025-08-24 09:33 | -07:00 | 1335 | FTS | 18690 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 1335
25-0090126 | Fresno | KERCKHOFF 1101 | KERCKHOFF 1101R308 | Environmental/External | 2025-08-23 15:05 | -07:00 | 08/19 - 08/25 | 2025-08-24 10:08 | -07:00 | 1143 | FTS | 30861 | 27 | 3 | 2 | 2 | 0 | 0 | 0 | 1143
25-0090236 | Placer | BELL 1107 | BELL 11072400 | Unknown Cause | 2025-08-24 09:30 | -07:00 | 08/19 - 08/25 | 2025-08-24 11:44 | -07:00 | 60.2824 | FTS | 31588 | 524 | 34 | 25 | 2 | 1 | 0 | 10 | 134
25-0090121 | Kings | AVENAL 2101 | AVENAL 21019070 | Environmental/External | 2025-08-23 14:31 | -07:00 | 08/19 - 08/25 | 2025-08-24 11:45 | -07:00 | 757.3768 | FTS | 52259 | 69 | 0 | 0 | 8 | 0 | 0 | 0 | 1274
25-0090254 | Tulare | SAND CREEK 1103 | SAND CREEK 11037992 | Environmental/External | 2025-08-24 10:30 | -07:00 | 08/19 - 08/25 | 2025-08-24 12:13 | -07:00 | 103 | FTS | 2781 | 27 | 2 | 2 | 0 | 0 | 0 | 0 | 103
25-0090199 | Fresno | AUBERRY 1101 | AUBERRY 1101D320 | Environmental/External | 2025-08-23 13:40 | -07:00 | 08/19 - 08/25 | 2025-08-24 13:20 | -07:00 | 1319.5652 | FTS | 30350 | 23 | 2 | 0 | 1 | 0 | 0 | 2 | 1420
25-0090223 | Napa | CALISTOGA 1102 | CALISTOGA 1102634 | Unknown Cause | 2025-08-24 07:19 | -07:00 | 08/19 - 08/25 | 2025-08-24 13:38 | -07:00 | 229.1159 | FTS | 106768 | 466 | 6 | 6 | 6 | 0 | 0 | 1 | 379
25-0090258 | Tehama | RED BLUFF 1101 | RED BLUFF 110185837 | Equipment Failure/Involved | 2025-08-24 12:13 | -07:00 | 08/19 - 08/25 | 2025-08-24 14:55 | -07:00 | 162 | FTS | 28998 | 179 | 13 | 9 | 0 | 0 | 0 | 1 | 162
25-0090262 | Plumas | GANSNER 1101 | GANSNER 1101489276 | Unknown Cause | 2025-08-24 14:03 | -07:00 | 08/19 - 08/25 | 2025-08-24 15:01 | -07:00 | 58 | FTS | 1102 | 19 | 0 | 0 | 3 | 0 | 0 | 0 | 58
25-0090273 | Plumas | HAMILTON BRANCH 1101 | HAMILTON BRANCH 110137534 | Environmental/External | 2025-08-24 16:07 | -07:00 | 08/19 - 08/25 | 2025-08-24 17:25 | -07:00 | 78 | FTS | 110994 | 1423 | 38 | 30 | 18 | 0 | 0 | 0 | 78
25-0090259 | El Dorado | APPLE HILL 2102 | APPLE HILL 21029722 | Equipment Failure/Involved | 2025-08-24 12:42 | -07:00 | 08/19 - 08/25 | 2025-08-24 17:29 | -07:00 | 287 | FTS | 34153 | 119 | 3 | 2 | 4 | 0 | 0 | 2 | 287
25-0090271 | Tuolumne | CURTIS 1702 | CURTIS 17026008 | Equipment Failure/Involved | 2025-08-24 16:03 | -07:00 | 08/19 - 08/25 | 2025-08-24 18:55 | -07:00 | 73.6875 | FTS | 42444 | 576 | 61 | 45 | 3 | 4 | 0 | 5 | 172
25-0090294 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 211318370 | Unknown Cause | 2025-08-24 20:03 | -07:00 | 08/19 - 08/25 | 2025-08-24 21:58 | -07:00 | 115 | FTS | 31165 | 271 | 12 | 10 | 2 | 0 | 0 | 4 | 115
25-0090315 | San Benito | SAN JUSTO 1101 | SAN JUSTO 110136902 | Unknown Cause | 2025-08-25 01:45 | -07:00 | 08/19 - 08/25 | 2025-08-25 03:15 | -07:00 | 90 | FTS | 19890 | 221 | 12 | 10 | 5 | 1 | 0 | 0 | 90
25-0090319 | Calaveras | FROGTOWN 1702 | FROGTOWN 170211212 | Vegetation | 2025-08-25 05:05 | -07:00 | 08/19 - 08/25 | 2025-08-25 07:28 | -07:00 | 143 | FTS | 18304 | 128 | 13 | 7 | 6 | 0 | 0 | 0 | 143
25-0090321 | Tehama | RED BLUFF 1104 | RED BLUFF 11041630 | Unknown Cause | 2025-08-25 06:06 | -07:00 | 08/19 - 08/25 | 2025-08-25 07:58 | -07:00 | 88.3534 | FTS | 30747 | 348 | 27 | 21 | 4 | 2 | 0 | 0 | 112
25-0090345 | Santa Barbara | CABRILLO 1103 | CABRILLO 1103420128 | 3rd Party | 2025-08-25 07:18 | -07:00 | 08/19 - 08/25 | 2025-08-25 10:16 | -07:00 | 178 | FTS | 24742 | 139 | 2 | 2 | 1 | 0 | 0 | 1 | 178
25-0090323 | Santa Clara | LLAGAS 2101 | LLAGAS 2101XR244 | Unknown Cause | 2025-08-25 06:17 | -07:00 | 08/19 - 08/25 | 2025-08-25 10:31 | -07:00 | 87.6746 | FTS | 88639 | 1011 | 34 | 20 | 16 | 2 | 0 | 8 | 254
25-0090542 | Shasta | STILLWATER 1101 | STILLWATER 1101747294 | Unknown Cause | 2025-08-25 10:53 | -07:00 | 08/19 - 08/25 | 2025-08-25 13:14 | -07:00 | 141 | FTS | 4512 | 32 | 0 | 0 | 5 | 0 | 0 | 0 | 141
25-0090553 | Tuolumne | CURTIS 1702 | CURTIS 17026008 | Company Initiated | 2025-08-25 12:03 | -07:00 | 08/19 - 08/25 | 2025-08-25 13:23 | -07:00 | 43.4375 | FTS | 25020 | 576 | 61 | 45 | 3 | 4 | 0 | 5 | 80
25-0090302 | Fresno | HAAS 2101 | HAAS 2101R2770 | Environmental/External | 2025-08-24 17:02 | -07:00 | 08/19 - 08/25 | 2025-08-25 13:53 | -07:00 | 1140.8267 | FTS | 85562 | 75 | 0 | 0 | 1 | 0 | 0 | 0 | 1251
25-0090728 | Mariposa | INDIAN FLAT 1104 | INDIAN FLAT 11045456 | Unknown Cause | 2025-08-25 14:51 | -07:00 | 08/19 - 08/25 | 2025-08-25 18:20 | -07:00 | 196.4554 | FTS | 61687 | 314 | 5 | 4 | 5 | 0 | 0 | 4 | 209
25-0090839 | Solano | JAMESON 1105 | JAMESON 1105466348 | 3rd Party | 2025-08-25 18:57 | -07:00 | 08/19 - 08/25 | 2025-08-25 20:09 | -07:00 | 72 | FTS | 25560 | 355 | 12 | 6 | 7 | 2 | 0 | 2 | 72
25-0090829 | El Dorado | PLACERVILLE 2106 | PLACERVILLE 2106560252 | Animal | 2025-08-25 19:00 | -07:00 | 08/19 - 08/25 | 2025-08-25 20:12 | -07:00 | 30.6491 | FTS | 31967 | 1043 | 83 | 66 | 18 | 5 | 0 | 3 | 72
25-0090825 | Mariposa | INDIAN FLAT 1104 | INDIAN FLAT 11045456 | Unknown Cause | 2025-08-25 18:29 | -07:00 | 08/19 - 08/25 | 2025-08-25 22:26 | -07:00 | 129.0701 | FTS | 40528 | 314 | 5 | 4 | 5 | 0 | 0 | 4 | 237
25-0090834 | Tehama | COTTONWOOD 1103 | COTTONWOOD 11031348 | Environmental/External | 2025-08-25 19:03 | -07:00 | 08/19 - 08/25 | 2025-08-25 22:32 | -07:00 | 85.0073 | FTS | 81012 | 953 | 72 | 57 | 10 | 1 | 0 | 1 | 209
25-0090847 | El Dorado | DIAMOND SPRINGS 1106 | DIAMOND SPRINGS 110676088 | Company Initiated | 2025-08-25 18:40 | -07:00 | 08/19 - 08/25 | 2025-08-25 23:10 | -07:00 | 125 | FTS | 9500 | 76 | 3 | 1 | 0 | 0 | 0 | 1 | 270
25-0090851 | Tehama | COTTONWOOD 1102 | COTTONWOOD 1102544790 | Environmental/External | 2025-08-25 21:02 | -07:00 | 08/19 - 08/25 | 2025-08-25 23:22 | -07:00 | 112.2145 | FTS | 111429 | 993 | 89 | 68 | 10 | 3 | 0 | 5 | 140
25-0090842 | Tehama | CORNING 1101 | CORNING 110185162 | Environmental/External | 2025-08-25 19:56 | -07:00 | 08/19 - 08/25 | 2025-08-25 23:37 | -07:00 | 221 | FTS | 192933 | 873 | 83 | 60 | 15 | 2 | 0 | 0 | 221
25-0090809 | Shasta | BURNEY 1101 | BURNEY 1101355340 | Environmental/External | 2025-08-25 17:25 | -07:00 | 08/26 - 09/01 | 2025-08-26 00:13 | -07:00 | 406.0294 | FTS | 27610 | 68 | 4 | 4 | 0 | 0 | 0 | 0 | 408
25-0090886 | San Luis Obispo | SAN LUIS OBISPO 1107 | SAN LUIS OBISPO 1107V58 | Unknown Cause | 2025-08-26 01:39 | -07:00 | 08/26 - 09/01 | 2025-08-26 02:39 | -07:00 | 56.6824 | FTS | 120110 | 2119 | 52 | 43 | 41 | 3 | 0 | 52 | 60
25-0090833 | Shasta | RISING RIVER 1101 | RISING RIVER 11019032 | Environmental/External | 2025-08-25 18:51 | -07:00 | 08/26 - 09/01 | 2025-08-26 03:13 | -07:00 | 411.2296 | FTS | 130771 | 318 | 10 | 8 | 5 | 0 | 0 | 0 | 502
25-0090895 | Mendocino | CALPELLA 1101 | CALPELLA 11016383 | Unknown Cause | 2025-08-26 01:11 | -07:00 | 08/26 - 09/01 | 2025-08-26 04:54 | -07:00 | 223 | FTS | 30774 | 138 | 8 | 7 | 2 | 0 | 0 | 0 | 223
25-0090888 | Tulare | DUNLAP 1102 | DUNLAP 11027050 | Environmental/External | 2025-08-26 01:54 | -07:00 | 08/26 - 09/01 | 2025-08-26 04:55 | -07:00 | 180.2245 | FTS | 8831 | 49 | 0 | 0 | 4 | 0 | 0 | 0 | 181
25-0090883 | Placer | PENRYN 1105 | PENRYN 1105680290 | Unknown Cause | 2025-08-26 01:00 | -07:00 | 08/26 - 09/01 | 2025-08-26 04:57 | -07:00 | 79.4884 | FTS | 30921 | 389 | 23 | 11 | 3 | 0 | 0 | 7 | 237
25-0090921 | Sonoma | FITCH MOUNTAIN 1113 | FITCH MOUNTAIN 1113824468 | Animal | 2025-08-26 06:35 | -07:00 | 08/26 - 09/01 | 2025-08-26 07:53 | -07:00 | 78 | FTS | 41808 | 536 | 22 | 16 | 4 | 0 | 0 | 8 | 78
25-0090950 | Santa Cruz | CAMP EVERS 2107 | CAMP EVERS 210510214 | Vegetation | 2025-08-26 07:44 | -07:00 | 08/26 - 09/01 | 2025-08-26 08:33 | -07:00 | 49 | FTS | 7595 | 155 | 8 | 6 | 2 | 0 | 0 | 0 | 49
25-0090920 | Fresno | HAAS 2101 | HAAS 2101R2770 | Environmental/External | 2025-08-26 06:24 | -07:00 | 08/26 - 09/01 | 2025-08-26 09:19 | -07:00 | 175 | FTS | 12775 | 73 | 0 | 0 | 1 | 0 | 0 | 0 | 175
25-0090947 | Mariposa | MERCED FALLS 1102 | MERCED FALLS 1102482838 | Animal | 2025-08-26 07:38 | -07:00 | 08/26 - 09/01 | 2025-08-26 09:28 | -07:00 | 110 | FTS | 156090 | 1419 | 92 | 58 | 28 | 5 | 0 | 0 | 110
25-0090902 | Tulare | DUNLAP 1103 | DUNLAP 11037040 | Environmental/External | 2025-08-26 05:22 | -07:00 | 08/26 - 09/01 | 2025-08-26 09:41 | -07:00 | 241.9826 | FTS | 97519 | 403 | 16 | 11 | 0 | 0 | 0 | 0 | 259
25-0090887 | Tuolumne | RACETRACK 1703 | RACETRACK 170310850 | Vegetation | 2025-08-26 01:41 | -07:00 | 08/26 - 09/01 | 2025-08-26 09:45 | -07:00 | 272.9048 | FTS | 126082 | 462 | 16 | 11 | 7 | 0 | 1 | 0 | 484
25-0090899 | Fresno | DUNLAP 1103 | DUNLAP 1103124724 | Environmental/External | 2025-08-26 04:55 | -07:00 | 08/26 - 09/01 | 2025-08-26 10:03 | -07:00 | 308 | FTS | 83468 | 271 | 11 | 11 | 1 | 0 | 0 | 0 | 308
25-0090937 | Yuba | NARROWS 2101 | NARROWS 21011202 | Unknown Cause | 2025-08-26 06:35 | -07:00 | 08/26 - 09/01 | 2025-08-26 10:22 | -07:00 | 227 | FTS | 22246 | 98 | 7 | 6 | 0 | 0 | 0 | 0 | 227
25-0090862 | Butte | BIG BEND 1102 | BIG BEND 1102CB | Unknown Cause | 2025-08-25 22:14 | -07:00 | 08/26 - 09/01 | 2025-08-26 10:46 | -07:00 | 733.7395 | FTS | 245069 | 334 | 11 | 8 | 10 | 0 | 0 | 0 | 752
25-0091118 | Colusa | ARBUCKLE 1101 | ARBUCKLE 11013068 | Unknown Cause | 2025-08-26 10:05 | -07:00 | 08/26 - 09/01 | 2025-08-26 10:56 | -07:00 | 51 | FTS | 5406 | 106 | 0 | 0 | 1 | 0 | 0 | 0 | 51
25-0090957 | Fresno | TIVY VALLEY 1107 | TIVY VALLEY 1107718068 | Environmental/External | 2025-08-26 05:35 | -07:00 | 08/26 - 09/01 | 2025-08-26 11:33 | -07:00 | 358 | FTS | 70884 | 198 | 16 | 11 | 1 | 0 | 0 | 1 | 358
25-0091055 | Fresno | SANGER 1108 | SANGER 110864662 | Environmental/External | 2025-08-26 09:25 | -07:00 | 08/26 - 09/01 | 2025-08-26 11:38 | -07:00 | 133 | HLT | 51072 | 384 | 40 | 25 | 10 | 0 | 0 | 0 | 133
25-0091113 | Mariposa | BEAR VALLEY 2105 | BEAR VALLEY 21059480 | Environmental/External | 2025-08-26 10:27 | -07:00 | 08/26 - 09/01 | 2025-08-26 11:45 | -07:00 | 78 | FTS | 69810 | 895 | 70 | 56 | 18 | 1 | 0 | 0 | 78
25-0091178 | Colusa | ARBUCKLE 1101 | ARBUCKLE 11013068 | Company Initiated | 2025-08-26 11:05 | -07:00 | 08/26 - 09/01 | 2025-08-26 12:18 | -07:00 | 73 | FTS | 7738 | 106 | 0 | 0 | 1 | 0 | 0 | 0 | 73
25-0091201 | El Dorado | DIAMOND SPRINGS 1106 | DIAMOND SPRINGS 110519910 | Equipment Failure/Involved | 2025-08-26 11:05 | -07:00 | 08/26 - 09/01 | 2025-08-26 12:50 | -07:00 | 105 | FTS | 3990 | 38 | 3 | 1 | 0 | 0 | 0 | 1 | 105
25-0091186 | Placer | PLACER 1102 | PLACER 1102CB | Unknown Cause | 2025-08-26 11:30 | -07:00 | 08/26 - 09/01 | 2025-08-26 12:56 | -07:00 | 81.3008 | FTS | 173252 | 2131 | 160 | 127 | 25 | 4 | 0 | 61 | 86
25-0090898 | Tulare | DUNLAP 1102 | DUNLAP 11027360 | Environmental/External | 2025-08-26 04:56 | -07:00 | 08/26 - 09/01 | 2025-08-26 12:57 | -07:00 | 469 | FTS | 30016 | 64 | 4 | 4 | 1 | 0 | 0 | 0 | 481
25-0091203 | Humboldt | HOOPA 1101 | HOOPA 110193038 | Animal | 2025-08-26 11:46 | -07:00 | 08/26 - 09/01 | 2025-08-26 13:11 | -07:00 | 85 | FTS | 8415 | 99 | 2 | 2 | 11 | 11 | 0 | 0 | 85
25-0091192 | Butte | BIG BEND 1101 | BIG BEND 1101180398 | Unknown Cause | 2025-08-26 10:45 | -07:00 | 08/26 - 09/01 | 2025-08-26 13:55 | -07:00 | 190 | FTS | 7220 | 38 | 3 | 2 | 0 | 0 | 0 | 0 | 190
25-0091321 | Santa Cruz | CAMP EVERS 2107 | CAMP EVERS 210711044 | 3rd Party | 2025-08-26 13:47 | -07:00 | 08/26 - 09/01 | 2025-08-26 15:06 | -07:00 | 79 | FTS | 177197 | 2243 | 166 | 132 | 39 | 1 | 0 | 2 | 79
25-0091090 | Tuolumne | PEORIA 1704 | PEORIA 17048040 | Environmental/External | 2025-08-26 09:48 | -07:00 | 08/26 - 09/01 | 2025-08-26 16:13 | -07:00 | 342.8881 | FTS | 45947 | 134 | 2 | 2 | 7 | 0 | 0 | 1 | 385
25-0090840 | Tehama | RED BLUFF 1103 | RED BLUFF 1103CB | Environmental/External | 2025-08-25 19:38 | -07:00 | 08/26 - 09/01 | 2025-08-26 16:53 | -07:00 | 125.787 | FTS | 343650 | 2732 | 189 | 137 | 28 | 9 | 1 | 6 | 1275
25-0091443 | Plumas | GANSNER 1101 | EAST QUINCY 11012452 | Unknown Cause | 2025-08-26 10:41 | -07:00 | 08/26 - 09/01 | 2025-08-26 17:15 | -07:00 | 394 | FTS | 9850 | 25 | 2 | 1 | 0 | 0 | 0 | 0 | 394
25-0091084 | Fresno | SHEPHERD 2111 | SHEPHERD 2111327814 | Environmental/External | 2025-08-26 09:53 | -07:00 | 08/26 - 09/01 | 2025-08-26 17:37 | -07:00 | 269.6053 | FTS | 40980 | 152 | 3 | 2 | 3 | 0 | 0 | 2 | 464
25-0091462 | Fresno | AUBERRY 1101 | AUBERRY 1101D320 | Environmental/External | 2025-08-26 11:06 | -07:00 | 08/26 - 09/01 | 2025-08-26 17:54 | -07:00 | 408 | FTS | 9384 | 23 | 2 | 0 | 1 | 0 | 0 | 2 | 408
25-0091459 | Fresno | AUBERRY 1101 | AUBERRY 1101R324 | Environmental/External | 2025-08-26 11:06 | -07:00 | 08/26 - 09/01 | 2025-08-26 18:26 | -07:00 | 440 | FTS | 18040 | 41 | 0 | 0 | 1 | 0 | 0 | 0 | 440
25-0091115 | Butte | CLARK ROAD 1102 | CLARK ROAD 110290548 | Environmental/External | 2025-08-26 10:29 | -07:00 | 08/26 - 09/01 | 2025-08-26 18:39 | -07:00 | 237.358 | FTS | 38452 | 162 | 11 | 7 | 1 | 1 | 0 | 0 | 490
25-0091409 | Lassen | MC ARTHUR 1101 | MC ARTHUR 11011546 | Environmental/External | 2025-08-26 15:28 | -07:00 | 08/26 - 09/01 | 2025-08-26 19:03 | -07:00 | 215 | FTS | 22790 | 106 | 5 | 3 | 2 | 0 | 0 | 0 | 215
25-0091501 | Plumas | GANSNER 1101 | GANSNER 1101489276 | Company Initiated | 2025-08-26 18:41 | -07:00 | 08/26 - 09/01 | 2025-08-26 19:08 | -07:00 | 27 | FTS | 513 | 19 | 0 | 0 | 3 | 0 | 0 | 0 | 27
25-0091033 | Tulare | DUNLAP 1102 | DUNLAP 11027060 | Environmental/External | 2025-08-26 05:00 | -07:00 | 08/26 - 09/01 | 2025-08-26 19:11 | -07:00 | 595.1429 | FTS | 124980 | 210 | 15 | 10 | 3 | 1 | 0 | 1 | 851
25-0091496 | Plumas | GANSNER 1101 | GANSNER 110199388 | Environmental/External | 2025-08-26 18:41 | -07:00 | 08/26 - 09/01 | 2025-08-26 20:24 | -07:00 | 93.9509 | FTS | 36359 | 387 | 7 | 4 | 10 | 70 | 0 | 3 | 103
25-0091515 | Tehama | RED BLUFF 1104 | RED BLUFF 11041302 | Environmental/External | 2025-08-26 19:36 | -07:00 | 08/26 - 09/01 | 2025-08-26 20:33 | -07:00 | 37.194 | FTS | 33363 | 897 | 68 | 45 | 16 | 2 | 0 | 2 | 57
25-0091510 | Tehama | RED BLUFF 1101 | RED BLUFF 11011556 | Unknown Cause | 2025-08-26 19:24 | -07:00 | 08/26 - 09/01 | 2025-08-26 20:46 | -07:00 | 62.5364 | FTS | 30080 | 481 | 49 | 36 | 3 | 0 | 0 | 2 | 82
25-0091500 | Mendocino | COVELO 1101 | COVELO 110137328 | Unknown Cause | 2025-08-26 18:46 | -07:00 | 08/26 - 09/01 | 2025-08-26 20:57 | -07:00 | 131 | FTS | 145672 | 1112 | 38 | 26 | 22 | 14 | 0 | 6 | 131
25-0091386 | Shasta | MC ARTHUR 1101 | MC ARTHUR 110138998 | Environmental/External | 2025-08-26 14:56 | -07:00 | 08/26 - 09/01 | 2025-08-26 21:05 | -07:00 | 218.4543 | FTS | 136097 | 623 | 26 | 18 | 23 | 3 | 0 | 0 | 369
25-0091512 | Tehama | COTTONWOOD 1103 | COTTONWOOD 11031616 | Environmental/External | 2025-08-26 19:22 | -07:00 | 08/26 - 09/01 | 2025-08-26 21:26 | -07:00 | 114.5494 | FTS | 63804 | 557 | 39 | 26 | 6 | 0 | 0 | 2 | 124
25-0091508 | Tehama | COTTONWOOD 1103 | COTTONWOOD 11039072 | Environmental/External | 2025-08-26 19:13 | -07:00 | 08/26 - 09/01 | 2025-08-26 21:36 | -07:00 | 143 | FTS | 41756 | 292 | 23 | 16 | 3 | 0 | 0 | 0 | 143
25-0091509 | Tehama | RED BLUFF 1103 | RED BLUFF 1103234278 | Environmental/External | 2025-08-26 19:20 | -07:00 | 08/26 - 09/01 | 2025-08-26 22:32 | -07:00 | 70.9559 | FTS | 16107 | 227 | 19 | 16 | 0 | 0 | 0 | 6 | 192
25-0091076 | Tuolumne | PEORIA 1701 | PEORIA 170176030 | Environmental/External | 2025-08-26 09:37 | -07:00 | 08/26 - 09/01 | 2025-08-26 22:37 | -07:00 | 128.1777 | FTS | 25251 | 197 | 12 | 9 | 7 | 2 | 0 | 0 | 780
25-0091502 | Tehama | COTTONWOOD 1101 | COTTONWOOD 110168190 | Environmental/External | 2025-08-26 18:50 | -07:00 | 08/26 - 09/01 | 2025-08-26 23:08 | -07:00 | 122.5751 | FTS | 57978 | 473 | 46 | 30 | 5 | 1 | 0 | 2 | 258
25-0090900 | Fresno | SAND CREEK 1103 | SAND CREEK 1103818064 | Environmental/External | 2025-08-26 05:07 | -07:00 | 08/26 - 09/01 | 2025-08-26 23:30 | -07:00 | 412.6801 | FTS | 215419 | 522 | 51 | 33 | 5 | 0 | 0 | 1 | 1103
25-0091553 | Mariposa | MARIPOSA 2102 | MARIPOSA 2102CB | Animal | 2025-08-26 23:06 | -07:00 | 08/26 - 09/01 | 2025-08-26 23:45 | -07:00 | 38.9871 | FTS | 130178 | 3339 | 162 | 112 | 67 | 22 | 3 | 8 | 39
25-0091286 | Colusa | ARBUCKLE 1101 | ARBUCKLE 11013068 | Environmental/External | 2025-08-26 13:03 | -07:00 | 08/26 - 09/01 | 2025-08-26 23:57 | -07:00 | 92.9151 | FTS | 9849 | 106 | 5 | 4 | 3 | 0 | 0 | 0 | 654
25-0091319 | El Dorado | SHINGLE SPRINGS 2109 | SHINGLE SPRINGS 210912392 | Equipment Failure/Involved | 2025-08-26 13:44 | -07:00 | 08/26 - 09/01 | 2025-08-27 01:47 | -07:00 | 246.708 | FTS | 27878 | 113 | 6 | 4 | 1 | 0 | 0 | 2 | 723
25-0091582 | San Mateo | MENLO 1102 | MENLO 11029110 | Company Initiated | 2025-08-27 03:25 | -07:00 | 08/26 - 09/01 | 2025-08-27 04:09 | -07:00 | 44 | FTS | 53152 | 1208 | 47 | 38 | 31 | 2 | 0 | 3 | 44
25-0091546 | El Dorado | PLACERVILLE 2106 | PLACERVILLE 210611132 | 3rd Party | 2025-08-26 22:27 | -07:00 | 08/26 - 09/01 | 2025-08-27 07:02 | -07:00 | 116.8349 | FTS | 357398 | 3059 | 232 | 181 | 67 | 15 | 0 | 19 | 515
25-0091636 | Sonoma | CLOVERDALE 1102 | CLOVERDALE 1102262 | Company Initiated | 2025-08-27 08:01 | -07:00 | 08/26 - 09/01 | 2025-08-27 08:17 | -07:00 | 15.3549 | FTS | 4975 | 324 | 14 | 14 | 11 | 0 | 0 | 5 | 16
25-0091613 | Humboldt | WILLOW CREEK 1101 | WILLOW CREEK 11015002 | Unknown Cause | 2025-08-27 07:18 | -07:00 | 08/26 - 09/01 | 2025-08-27 09:00 | -07:00 | 102 | FTS | 60894 | 597 | 29 | 22 | 5 | 0 | 1 | 1 | 102
25-0091494 | Shasta | JESSUP 1102 | JESSUP 110262802 | Environmental/External | 2025-08-26 18:39 | -07:00 | 08/26 - 09/01 | 2025-08-27 09:31 | -07:00 | 156.6092 | FTS | 239612 | 1530 | 141 | 106 | 11 | 2 | 0 | 1 | 892
25-0091533 | Shasta | PANORAMA 1102 | PANORAMA 1102508502 | Environmental/External | 2025-08-26 21:03 | -07:00 | 08/26 - 09/01 | 2025-08-27 10:25 | -07:00 | 379.3846 | FTS | 49320 | 130 | 7 | 5 | 0 | 0 | 0 | 1 | 802
25-0091534 | Tehama | VOLTA 1101 | VOLTA 11011516 | Environmental/External | 2025-08-26 21:03 | -07:00 | 08/26 - 09/01 | 2025-08-27 10:57 | -07:00 | 834 | FTS | 109254 | 131 | 5 | 4 | 16 | 2 | 0 | 0 | 834
25-0091538 | Shasta | ANTLER 1101 | ANTLER 1101671078 | Environmental/External | 2025-08-26 21:31 | -07:00 | 08/26 - 09/01 | 2025-08-27 11:48 | -07:00 | 298.8303 | FTS | 65145 | 218 | 15 | 10 | 3 | 0 | 0 | 1 | 857
25-0091665 | Mendocino | COVELO 1101 | COVELO 110137328 | Vegetation | 2025-08-27 08:47 | -07:00 | 08/26 - 09/01 | 2025-08-27 13:08 | -07:00 | 89.6763 | FTS | 99720 | 1112 | 38 | 26 | 22 | 14 | 0 | 6 | 261
25-0091543 | Humboldt | HOOPA 1101 | HOOPA 110137202 | Vegetation | 2025-08-26 21:56 | -07:00 | 08/26 - 09/01 | 2025-08-27 15:11 | -07:00 | 643.5678 | FTS | 75941 | 118 | 2 | 2 | 9 | 1 | 0 | 0 | 1035
25-0092013 | Santa Barbara | SISQUOC 1103 | SISQUOC 1103858898 | Unknown Cause | 2025-08-27 16:41 | -07:00 | 08/26 - 09/01 | 2025-08-27 18:55 | -07:00 | 134 | FTS | 21306 | 159 | 2 | 2 | 5 | 0 | 0 | 5 | 134
25-0091950 | El Dorado | EL DORADO PH 2101 | EL DORADO PH 210113532 | Unknown Cause | 2025-08-27 14:45 | -07:00 | 08/26 - 09/01 | 2025-08-27 19:06 | -07:00 | 143.5846 | FTS | 102663 | 715 | 16 | 13 | 32 | 0 | 0 | 1 | 261
25-0091986 | Mariposa | INDIAN FLAT 1104 | INDIAN FLAT 11045456 | Unknown Cause | 2025-08-27 15:40 | -07:00 | 08/26 - 09/01 | 2025-08-27 19:29 | -07:00 | 214.6847 | FTS | 67411 | 314 | 5 | 4 | 5 | 0 | 0 | 4 | 229
25-0092044 | Mendocino | HOPLAND 1101 | HOPLAND 11014335 | Vegetation | 2025-08-27 16:19 | -07:00 | 08/26 - 09/01 | 2025-08-27 21:49 | -07:00 | 218.9688 | FTS | 7007 | 32 | 0 | 0 | 13 | 13 | 0 | 0 | 330
25-0091634 | El Dorado | PLACERVILLE 2106 | PLACERVILLE 2106935216 | Equipment Failure/Involved | 2025-08-27 18:16 | -07:00 | 08/26 - 09/01 | 2025-08-27 22:24 | -07:00 | 245.1765 | FTS | 4168 | 17 | 1 | 1 | 0 | 0 | 0 | 1 | 248
25-0092087 | Santa Cruz | CAMP EVERS 2103 | CAMP EVERS 210311046 | Vegetation | 2025-08-28 01:14 | -07:00 | 08/26 - 09/01 | 2025-08-28 03:20 | -07:00 | 126 | FTS | 44226 | 351 | 14 | 10 | 8 | 2 | 0 | 5 | 126
25-0092091 | Santa Barbara | SANTA YNEZ 1102 | SANTA YNEZ 1102Y18 | Vegetation | 2025-08-28 02:06 | -07:00 | 08/26 - 09/01 | 2025-08-28 05:18 | -07:00 | 87.6648 | FTS | 47076 | 537 | 10 | 7 | 15 | 0 | 0 | 0 | 192
25-0092122 | San Mateo | RALSTON 1102 | RALSTON 1102CB | Equipment Failure/Involved | 2025-08-28 07:34 | -07:00 | 08/26 - 09/01 | 2025-08-28 08:06 | -07:00 | 32 | FTS | 73184 | 2287 | 94 | 72 | 37 | 6 | 0 | 0 | 32
25-0092130 | Santa Cruz | CAMP EVERS 2105 | CAMP EVERS 210510214 | Unknown Cause | 2025-08-28 07:43 | -07:00 | 08/26 - 09/01 | 2025-08-28 08:49 | -07:00 | 39.2785 | FTS | 8602 | 219 | 17 | 15 | 2 | 0 | 0 | 9 | 66
25-0092083 | El Dorado | SHINGLE SPRINGS 2109 | SHINGLE SPRINGS 210981390 | Vegetation | 2025-08-28 00:50 | -07:00 | 08/26 - 09/01 | 2025-08-28 11:19 | -07:00 | 193.8673 | FTS | 65721 | 339 | 24 | 23 | 4 | 1 | 0 | 13 | 629
25-0087645 | Tuolumne | PEORIA 1704 | PEORIA 1704CB | Company Initiated | 2025-08-27 16:35 | -07:00 | 08/26 - 09/01 | 2025-08-28 11:54 | -07:00 | 17.0219 | FTS | 204910 | 12038 | 413 | 297 | 115 | 17 | 4 | 5 | 1159
25-0092247 | Placer | PENRYN 1105 | PENRYN 11052406 | Unknown Cause | 2025-08-28 10:47 | -07:00 | 08/26 - 09/01 | 2025-08-28 12:40 | -07:00 | 51.3296 | FTS | 45632 | 889 | 57 | 41 | 9 | 1 | 0 | 13 | 113
25-0092388 | Marin | SAN RAFAEL 1109 | SAN RAFAEL 1109692576 | Unknown Cause | 2025-08-28 14:00 | -07:00 | 08/26 - 09/01 | 2025-08-28 16:03 | -07:00 | 114.3333 | FTS | 24696 | 216 | 11 | 8 | 2 | 2 | 0 | 1 | 123
25-0092495 | El Dorado | DIAMOND SPRINGS 1105 | DIAMOND SPRINGS 11057722 | Company Initiated | 2025-08-28 16:02 | -07:00 | 08/26 - 09/01 | 2025-08-28 18:33 | -07:00 | 151 | FTS | 177123 | 1173 | 94 | 69 | 18 | 0 | 0 | 10 | 151
25-0092150 | Monterey | SAN ARDO 1102 | SAN ARDO 1102CB | Equipment Failure/Involved | 2025-08-28 08:13 | -07:00 | 08/26 - 09/01 | 2025-08-28 20:03 | -07:00 | 94.6058 | FTS | 61683 | 652 | 9 | 6 | 25 | 7 | 0 | 0 | 710
25-0092542 | Lake | LUCERNE 1106 | LUCERNE 110676850 | Unknown Cause | 2025-08-28 17:32 | -07:00 | 08/26 - 09/01 | 2025-08-28 20:22 | -07:00 | 67.6811 | FTS | 146868 | 2170 | 165 | 120 | 45 | 4 | 1 | 1 | 170
25-0092573 | El Dorado | DIAMOND SPRINGS 1105 | DIAMOND SPRINGS 11057722 | Unknown Cause | 2025-08-28 19:48 | -07:00 | 08/26 - 09/01 | 2025-08-28 20:38 | -07:00 | 46.5011 | FTS | 43990 | 946 | 77 | 57 | 17 | 0 | 0 | 9 | 50
25-0092541 | Solano | JAMESON 1105 | JAMESON 1105466348 | Equipment Failure/Involved | 2025-08-28 17:26 | -07:00 | 08/26 - 09/01 | 2025-08-28 20:59 | -07:00 | 121.5634 | FTS | 43155 | 355 | 12 | 6 | 7 | 2 | 0 | 2 | 213
25-0092209 | Tehama | CORNING 1101 | CORNING 110185162 | 3rd Party | 2025-08-28 09:56 | -07:00 | 08/26 - 09/01 | 2025-08-28 21:39 | -07:00 | 148.1617 | FTS | 129197 | 872 | 83 | 60 | 15 | 2 | 0 | 0 | 703
25-0092550 | Monterey | KING CITY 1102 | KING CITY 1102728782 | Unknown Cause | 2025-08-28 18:02 | -07:00 | 08/26 - 09/01 | 2025-08-28 21:46 | -07:00 | 224 | FTS | 1120 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 224
25-0092586 | Monterey | RESERVATION ROAD 1101 | RESERVATION ROAD 1101370948 | Unknown Cause | 2025-08-28 21:33 | -07:00 | 08/26 - 09/01 | 2025-08-29 00:43 | -07:00 | 177.1911 | FTS | 127046 | 717 | 56 | 44 | 12 | 0 | 0 | 0 | 190
25-0092626 | Napa | SILVERADO 2103 | SILVERADO 2103CB | Unknown Cause | 2025-08-29 06:14 | -07:00 | 08/26 - 09/01 | 2025-08-29 08:23 | -07:00 | 49.4906 | FTS | 47610 | 962 | 10 | 5 | 13 | 1 | 0 | 2 | 129
25-0092764 | Amador | OLETA 1101 | OLETA 1101CB | Company Initiated | 2025-08-29 08:47 | -07:00 | 08/26 - 09/01 | 2025-08-29 09:36 | -07:00 | 42 | FTS | 4830 | 115 | 8 | 4 | 1 | 0 | 0 | 7 | 49
25-0092617 | Santa Cruz | GREEN VALLEY 2103 | ROB ROY 210410714 | Unknown Cause | 2025-08-29 03:55 | -07:00 | 08/26 - 09/01 | 2025-08-29 12:50 | -07:00 | 420.038 | FTS | 1339081 | 3188 | 177 | 145 | 50 | 7 | 0 | 3 | 535
25-0093071 | Monterey | RESERVATION ROAD 1102 | RESERVATION ROAD 1102741002 | Unknown Cause | 2025-08-29 18:22 | -07:00 | 08/26 - 09/01 | 2025-08-29 19:28 | -07:00 | 66 | FTS | 20328 | 308 | 16 | 10 | 8 | 0 | 0 | 0 | 66
25-0072025 | Amador | OLETA 1101 | OLETA 1101CB | Company Initiated | 2025-08-29 08:47 | -07:00 | 08/26 - 09/01 | 2025-08-29 20:04 | -07:00 | 20.3328 | FTS | 108313 | 5327 | 60 | 41 | 31 | 3 | 0 | 15 | 677
25-0093093 | Sonoma | BELLEVUE 2101 | BELLEVUE 2101270638 | Animal | 2025-08-29 20:52 | -07:00 | 08/26 - 09/01 | 2025-08-29 21:43 | -07:00 | 51 | FTS | 306 | 6 | 1 | 1 | 0 | 0 | 0 | 1 | 51
25-0093094 | Monterey | LAURELES 1111 | LAURELES 11112020 | Company Initiated | 2025-08-29 22:11 | -07:00 | 08/26 - 09/01 | 2025-08-29 22:30 | -07:00 | 19 | FTS | 15808 | 832 | 21 | 18 | 26 | 0 | 0 | 3 | 19
25-0093070 | Nevada | SPAULDING 1101 | SPAULDING 1101578852 | Animal | 2025-08-29 18:22 | -07:00 | 08/26 - 09/01 | 2025-08-29 22:47 | -07:00 | 163.1737 | FTS | 27250 | 167 | 2 | 0 | 18 | 3 | 0 | 0 | 265
25-0092620 | Sonoma | RINCON 1101 | RINCON 1101576 | Equipment Failure/Involved | 2025-08-29 05:24 | -07:00 | 08/26 - 09/01 | 2025-08-30 01:43 | -07:00 | 125.9124 | FTS | 300427 | 2386 | 178 | 137 | 34 | 0 | 0 | 13 | 1219
25-0093074 | Tulare | REEDLEY 1112 | REEDLEY 11127240 | 3rd Party | 2025-08-29 18:36 | -07:00 | 08/26 - 09/01 | 2025-08-30 02:32 | -07:00 | 105.1954 | FTS | 31769 | 302 | 2 | 2 | 1 | 0 | 0 | 0 | 476
25-0093102 | El Dorado | SHINGLE SPRINGS 2109 | SHINGLE SPRINGS 210911092 | Unknown Cause | 2025-08-29 22:58 | -07:00 | 08/26 - 09/01 | 2025-08-30 04:10 | -07:00 | 312 | FTS | 13104 | 42 | 1 | 1 | 0 | 0 | 0 | 2 | 312
25-0093104 | Shasta | OREGON TRAIL 1104 | OREGON TRAIL 11041634 | Animal | 2025-08-30 01:53 | -07:00 | 08/26 - 09/01 | 2025-08-30 05:01 | -07:00 | 147.0857 | FTS | 82368 | 560 | 35 | 23 | 6 | 0 | 0 | 5 | 188
25-0093119 | Santa Clara | MORGAN HILL 2104 | MORGAN HILL 2104152774 | Animal | 2025-08-30 07:01 | -07:00 | 08/26 - 09/01 | 2025-08-30 07:52 | -07:00 | 51 | FTS | 28152 | 552 | 37 | 25 | 12 | 0 | 0 | 0 | 51
25-0093109 | El Dorado | APPLE HILL 2102 | APPLE HILL 2102836878 | Company Initiated | 2025-08-30 05:49 | -07:00 | 08/26 - 09/01 | 2025-08-30 07:54 | -07:00 | 116.9966 | FTS | 557840 | 4768 | 379 | 279 | 62 | 12 | 0 | 63 | 125
25-0093114 | Tuolumne | MIWUK 1702 | MIWUK 1702667248 | Animal | 2025-08-30 06:42 | -07:00 | 08/26 - 09/01 | 2025-08-30 09:04 | -07:00 | 129.0495 | FTS | 372566 | 2887 | 207 | 155 | 26 | 1 | 0 | 1 | 142
25-0093127 | Contra Costa | ROSSMOOR 1108 | ROSSMOOR 1108180088 | Animal | 2025-08-30 07:41 | -07:00 | 08/26 - 09/01 | 2025-08-30 09:10 | -07:00 | 89 | FTS | 94162 | 1058 | 67 | 47 | 11 | 6 | 0 | 0 | 89
25-0093145 | Nevada | BRUNSWICK 1107 | BRUNSWICK 110750010 | Animal | 2025-08-30 08:57 | -07:00 | 08/26 - 09/01 | 2025-08-30 10:03 | -07:00 | 66 | FTS | 83622 | 1267 | 81 | 45 | 13 | 2 | 0 | 0 | 66
25-0093157 | San Mateo | BELMONT 1110 | BELMONT 11109090 | Vegetation | 2025-08-30 09:34 | -07:00 | 08/26 - 09/01 | 2025-08-30 10:33 | -07:00 | 54.8745 | FTS | 124181 | 2263 | 38 | 27 | 21 | 6 | 0 | 0 | 59
25-0093143 | Nevada | BRUNSWICK 1105 | BRUNSWICK 11052130 | Company Initiated | 2025-08-30 08:56 | -07:00 | 08/26 - 09/01 | 2025-08-30 10:39 | -07:00 | 103 | FTS | 21424 | 208 | 10 | 7 | 7 | 0 | 0 | 8 | 103
25-0093101 | Stanislaus | WESTLEY 1103 | WESTLEY 11039010 | 3rd Party | 2025-08-30 00:53 | -07:00 | 08/26 - 09/01 | 2025-08-30 11:06 | -07:00 | 192.9699 | FTS | 57698 | 299 | 1 | 0 | 15 | 0 | 0 | 0 | 613
25-0093136 | El Dorado | PLACERVILLE 2106 | PLACERVILLE 21061104 | Animal | 2025-08-30 08:24 | -07:00 | 08/26 - 09/01 | 2025-08-30 11:17 | -07:00 | 96.5519 | FTS | 150621 | 1560 | 118 | 93 | 45 | 10 | 0 | 10 | 173
25-0093158 | Mendocino | CALPELLA 1101 | CALPELLA 11015659 | Unknown Cause | 2025-08-30 09:08 | -07:00 | 08/26 - 09/01 | 2025-08-30 11:29 | -07:00 | 141 | FTS | 32007 | 227 | 21 | 15 | 1 | 0 | 0 | 0 | 141
25-0093177 | Monterey | FORT ORD 2106 | FORT ORD 21069658 | Unknown Cause | 2025-08-30 11:41 | -07:00 | 08/26 - 09/01 | 2025-08-30 12:03 | -07:00 | 22 | FTS | 25168 | 1144 | 43 | 29 | 6 | 0 | 0 | 0 | 22
25-0093189 | Monterey | FORT ORD 2106 | FORT ORD 21069658 | Unknown Cause | 2025-08-30 12:13 | -07:00 | 08/26 - 09/01 | 2025-08-30 12:53 | -07:00 | 40 | FTS | 45760 | 1144 | 43 | 29 | 6 | 0 | 0 | 0 | 40
25-0093194 | Calaveras | FROGTOWN 1702 | FROGTOWN 1702531640 | Equipment Failure/Involved | 2025-08-30 10:26 | -07:00 | 08/26 - 09/01 | 2025-08-30 12:58 | -07:00 | 145.2642 | FTS | 7699 | 53 | 0 | 0 | 10 | 0 | 0 | 0 | 152
25-0093182 | Nevada | COLUMBIA HILL 1101 | COLUMBIA HILL 1101764 | Vegetation | 2025-08-30 11:45 | -07:00 | 08/26 - 09/01 | 2025-08-30 13:08 | -07:00 | 83 | FTS | 21829 | 263 | 11 | 7 | 3 | 2 | 0 | 8 | 83
25-0093178 | Monterey | SPENCE 1104 | SPENCE 1104965598 | Unknown Cause | 2025-08-30 11:40 | -07:00 | 08/26 - 09/01 | 2025-08-30 14:10 | -07:00 | 150 | FTS | 25050 | 167 | 1 | 0 | 2 | 0 | 0 | 1 | 150
25-0093201 | Santa Clara | MORGAN HILL 2109 | MORGAN HILL 2109XR104 | 3rd Party | 2025-08-30 13:56 | -07:00 | 08/26 - 09/01 | 2025-08-30 16:23 | -07:00 | 147 | FTS | 79968 | 544 | 29 | 22 | 6 | 0 | 0 | 0 | 147
25-0093218 | Contra Costa | TASSAJARA 2108 | TASSAJARA 2108846900 | Unknown Cause | 2025-08-30 16:34 | -07:00 | 08/26 - 09/01 | 2025-08-30 17:40 | -07:00 | 66 | FTS | 20592 | 312 | 13 | 8 | 1 | 0 | 0 | 1 | 66
25-0093230 | Marin | STAFFORD 1101 | STAFFORD 11011082 | Unknown Cause | 2025-08-30 19:27 | -07:00 | 08/26 - 09/01 | 2025-08-30 21:30 | -07:00 | 123 | FTS | 46125 | 375 | 28 | 18 | 2 | 0 | 0 | 0 | 123
25-0093241 | Lake | HARTLEY 1101 | HARTLEY 110186876 | 3rd Party | 2025-08-31 00:04 | -07:00 | 08/26 - 09/01 | 2025-08-31 00:51 | -07:00 | 47 | FTS | 51042 | 1086 | 79 | 49 | 14 | 0 | 0 | 3 | 47
25-0093240 | San Luis Obispo | PERRY 1101 | PERRY 1101W52 | Equipment Failure/Involved | 2025-08-30 23:23 | -07:00 | 08/26 - 09/01 | 2025-08-31 03:55 | -07:00 | 272 | FTS | 110432 | 406 | 19 | 15 | 4 | 0 | 0 | 0 | 272
25-0093223 | Napa | PUEBLO 1105 | PUEBLO 1105348368 | Unknown Cause | 2025-08-30 17:18 | -07:00 | 08/26 - 09/01 | 2025-08-31 08:45 | -07:00 | 927 | FTS | 188181 | 203 | 13 | 7 | 1 | 0 | 0 | 5 | 927
25-0093222 | Mariposa | INDIAN FLAT 1104 | INDIAN FLAT 11045456 | Unknown Cause | 2025-08-30 17:15 | -07:00 | 08/26 - 09/01 | 2025-08-31 09:14 | -07:00 | 546.465 | FTS | 171590 | 314 | 5 | 4 | 5 | 0 | 0 | 4 | 959
25-0093247 | Kern | TEMBLOR 1104 | TEMBLOR 1104284004 | Animal | 2025-08-31 06:41 | -07:00 | 08/26 - 09/01 | 2025-08-31 09:19 | -07:00 | 158 | FTS | 5214 | 33 | 0 | 0 | 2 | 1 | 0 | 0 | 158
25-0093259 | Santa Clara | LOS GATOS 1106 | LOS GATOS 1106CB | Animal | 2025-08-31 08:15 | -07:00 | 08/26 - 09/01 | 2025-08-31 09:51 | -07:00 | 93.4667 | FTS | 210300 | 2250 | 161 | 126 | 56 | 8 | 0 | 25 | 96
25-0093246 | Colusa | MAXWELL 1102 | MAXWELL 11023306 | Unknown Cause | 2025-08-31 05:58 | -07:00 | 08/26 - 09/01 | 2025-08-31 10:05 | -07:00 | 247 | FTS | 39273 | 159 | 5 | 2 | 2 | 0 | 0 | 0 | 247
25-0093268 | Kern | MCKITTRICK 1101 | MCKITTRICK 11011639 | Animal | 2025-08-31 09:30 | -07:00 | 08/26 - 09/01 | 2025-08-31 10:12 | -07:00 | 42 | FTS | 1638 | 39 | 0 | 0 | 11 | 0 | 0 | 0 | 42
25-0093270 | El Dorado | APPLE HILL 2102 | APPLE HILL 2102836878 | Company Initiated | 2025-08-31 09:43 | -07:00 | 08/26 - 09/01 | 2025-08-31 10:33 | -07:00 | 48.6065 | FTS | 231756 | 4768 | 379 | 279 | 62 | 12 | 0 | 63 | 50
25-0093291 | Sonoma | GEYSERVILLE 1101 | GEYSERVILLE 1101166 | Company Initiated | 2025-08-31 13:56 | -07:00 | 08/26 - 09/01 | 2025-08-31 14:57 | -07:00 | 56.7635 | FTS | 36726 | 647 | 13 | 11 | 8 | 0 | 0 | 6 | 61
25-0093257 | Humboldt | HOOPA 1101 | HOOPA 11013174 | Unknown Cause | 2025-08-31 07:58 | -07:00 | 08/26 - 09/01 | 2025-08-31 16:08 | -07:00 | 283.3368 | FTS | 189269 | 668 | 18 | 14 | 24 | 5 | 0 | 0 | 490
25-0093298 | Sonoma | PETALUMA C 1108 | PETALUMA C 1108636 | Unknown Cause | 2025-08-31 15:30 | -07:00 | 08/26 - 09/01 | 2025-08-31 16:46 | -07:00 | 76 | FTS | 10868 | 143 | 2 | 2 | 2 | 0 | 0 | 1 | 76
25-0093242 | Nevada | HIGGINS 1109 | HIGGINS 110950078 | Equipment Failure/Involved | 2025-08-31 00:09 | -07:00 | 08/26 - 09/01 | 2025-08-31 18:08 | -07:00 | 178.9108 | FTS | 74248 | 415 | 32 | 24 | 4 | 0 | 0 | 12 | 1079
25-0093316 | Fresno | DUNLAP 1103 | DUNLAP 11037959F | Unknown Cause | 2025-08-31 16:38 | -07:00 | 08/26 - 09/01 | 2025-08-31 19:32 | -07:00 | 174 | FTS | 10614 | 61 | 3 | 1 | 0 | 0 | 0 | 0 | 174
25-0093289 | San Luis Obispo | TEMPLETON 2110 | TEMPLETON 2110317796 | Vegetation | 2025-08-31 13:33 | -07:00 | 08/26 - 09/01 | 2025-08-31 19:59 | -07:00 | 88.0867 | FTS | 128959 | 1464 | 43 | 31 | 20 | 0 | 0 | 34 | 386
25-0093309 | Alameda | SAN RAMON 2108 | SAN RAMON 2108CB | Unknown Cause | 2025-08-31 17:37 | -07:00 | 08/26 - 09/01 | 2025-08-31 20:05 | -07:00 | 148 | FTS | 14356 | 97 | 7 | 5 | 5 | 0 | 0 | 1 | 148
25-0093330 | Alameda | OAKLAND X 1104 | OAKLAND X 1104438648 | Company Initiated | 2025-08-31 20:48 | -07:00 | 08/26 - 09/01 | 2025-08-31 21:43 | -07:00 | 48.5707 | FTS | 120941 | 2490 | 79 | 53 | 46 | 2 | 0 | 1 | 55
25-0093321 | Placer | PENRYN 1103 | PENRYN 1103660 | 3rd Party | 2025-08-31 20:02 | -07:00 | 08/26 - 09/01 | 2025-08-31 21:44 | -07:00 | 102 | FTS | 46614 | 457 | 32 | 22 | 3 | 0 | 0 | 8 | 102
25-0093322 | San Benito | HOLLISTER 2105 | HOLLISTER 21054042 | Unknown Cause | 2025-08-31 20:03 | -07:00 | 08/26 - 09/01 | 2025-08-31 22:32 | -07:00 | 149 | FTS | 23691 | 159 | 7 | 2 | 1 | 0 | 0 | 0 | 149
25-0093355 | Napa | PUEBLO 2102 | PUEBLO 2102618 | Animal | 2025-09-01 06:43 | -07:00 | 08/26 - 09/01 | 2025-09-01 07:53 | -07:00 | 34.2863 | FTS | 16766 | 489 | 6 | 4 | 7 | 1 | 0 | 3 | 70
25-0093313 | Santa Barbara | BUELLTON 1102 | BUELLTON 1102CB | Equipment Failure/Involved | 2025-08-31 18:34 | -07:00 | 08/26 - 09/01 | 2025-09-01 07:57 | -07:00 | 183.7045 | FTS | 384861 | 2095 | 38 | 31 | 31 | 6 | 0 | 1 | 803
25-0093356 | Placer | WISE 1102 | WISE 11022234 | Animal | 2025-09-01 06:53 | -07:00 | 08/26 - 09/01 | 2025-09-01 08:09 | -07:00 | 76 | FTS | 20672 | 272 | 19 | 14 | 0 | 0 | 0 | 4 | 76
25-0093353 | Santa Cruz | GREEN VALLEY 2101 | GREEN VALLEY 210111054 | Unknown Cause | 2025-09-01 06:46 | -07:00 | 08/26 - 09/01 | 2025-09-01 08:12 | -07:00 | 31.7194 | FTS | 9833 | 310 | 10 | 7 | 10 | 5 | 0 | 1 | 86
25-0093349 | Amador | OLETA 1102 | OLETA 11022642 | Animal | 2025-09-01 06:19 | -07:00 | 08/26 - 09/01 | 2025-09-01 08:44 | -07:00 | 101.8 | FTS | 2036 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 145
25-0093372 | Calaveras | CORRAL 1101 | CORRAL 110136652 | Unknown Cause | 2025-09-01 08:37 | -07:00 | 08/26 - 09/01 | 2025-09-01 10:51 | -07:00 | 121.5869 | FTS | 53863 | 443 | 35 | 25 | 3 | 0 | 0 | 3 | 134
25-0093343 | Calaveras | PEORIA 1704 | PEORIA 170459596 | 3rd Party | 2025-08-31 23:46 | -07:00 | 08/26 - 09/01 | 2025-09-01 11:13 | -07:00 | 400.5939 | FTS | 264392 | 660 | 49 | 33 | 24 | 0 | 0 | 1 | 687
25-0093375 | Contra Costa | SOBRANTE 1101 | SOBRANTE 1101CB | Unknown Cause | 2025-09-01 08:50 | -07:00 | 08/26 - 09/01 | 2025-09-01 11:38 | -07:00 | 155.1044 | FTS | 348985 | 2250 | 74 | 52 | 20 | 5 | 0 | 1 | 168
25-0093357 | San Luis Obispo | TEMPLETON 2110 | TEMPLETON 2110901690 | Unknown Cause | 2025-09-01 07:00 | -07:00 | 08/26 - 09/01 | 2025-09-01 12:29 | -07:00 | 304.407 | FTS | 86756 | 285 | 4 | 3 | 5 | 0 | 0 | 13 | 329
25-0093326 | Napa | SILVERADO 2102 | SILVERADO 2102772792 | Unknown Cause | 2025-08-31 20:01 | -07:00 | 08/26 - 09/01 | 2025-09-01 17:28 | -07:00 | 182.4167 | FTS | 4378 | 24 | 0 | 0 | 2 | 0 | 0 | 0 | 1287
25-0093468 | Santa Clara | SARATOGA 1107 | SARATOGA 11075696 | Company Initiated | 2025-09-01 17:51 | -07:00 | 08/26 - 09/01 | 2025-09-01 20:34 | -07:00 | 160.3744 | FTS | 109215 | 681 | 19 | 14 | 8 | 3 | 0 | 1 | 163
25-0093500 | Santa Clara | SARATOGA 1107 | SARATOGA 11075696 | Company Initiated | 2025-09-01 21:06 | -07:00 | 08/26 - 09/01 | 2025-09-01 21:13 | -07:00 | 7 | FTS | 4767 | 681 | 19 | 14 | 8 | 3 | 0 | 1 | 7
25-0093550 | Marin | ALTO 1124 | ALTO 1124CB | Equipment Failure/Involved | 2025-09-02 05:27 | -07:00 | 09/02 - 09/08 | 2025-09-02 06:35 | -07:00 | 68 | FTS | 204 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 68
25-0093528 | San Luis Obispo | CARRIZO PLAINS 1101 | CARRIZO PLAINS 1101384116 | Animal | 2025-09-02 04:00 | -07:00 | 09/02 - 09/08 | 2025-09-02 06:50 | -07:00 | 134.6545 | FTS | 44436 | 330 | 5 | 3 | 7 | 1 | 3 | 0 | 170
25-0093575 | San Luis Obispo | PERRY 1101 | PERRY 1101200598 | Unknown Cause | 2025-09-02 06:37 | -07:00 | 09/02 - 09/08 | 2025-09-02 08:18 | -07:00 | 87.5517 | FTS | 177730 | 2030 | 72 | 54 | 14 | 0 | 0 | 0 | 101
25-0093593 | Sonoma | MOLINO 1101 | MOLINO 1101152 | Company Initiated | 2025-09-02 07:05 | -07:00 | 09/02 - 09/08 | 2025-09-02 08:42 | -07:00 | 72.4522 | FTS | 56875 | 785 | 254 | 181 | 66 | 13 | 0 | 31 | 97
25-0093603 | Amador | CLAY 1101 | CLAY 110113450 | Unknown Cause | 2025-09-02 07:20 | -07:00 | 09/02 - 09/08 | 2025-09-02 08:45 | -07:00 | 85 | FTS | 37910 | 446 | 38 | 27 | 5 | 0 | 0 | 0 | 85
25-0093590 | Monterey | GABILAN 1101 | GABILAN 1101468770 | Unknown Cause | 2025-09-02 07:00 | -07:00 | 09/02 - 09/08 | 2025-09-02 08:47 | -07:00 | 107 | FTS | 3745 | 35 | 2 | 2 | 0 | 0 | 0 | 0 | 107
25-0093527 | Fresno | CANTUA 1101 | CANTUA 1101CB | Environmental/External | 2025-09-02 03:58 | -07:00 | 09/02 - 09/08 | 2025-09-02 08:48 | -07:00 | 290 | FTS | 17400 | 60 | 0 | 0 | 1 | 0 | 0 | 0 | 290
25-0093542 | Calaveras | FROGTOWN 1702 | FROGTOWN 170275252 | Environmental/External | 2025-09-02 04:59 | -07:00 | 09/02 - 09/08 | 2025-09-02 09:25 | -07:00 | 266 | FTS | 220248 | 828 | 34 | 24 | 28 | 2 | 0 | 3 | 266
25-0093708 | Mendocino | WILLITS 1103 | WILLITS 1103964 | Company Initiated | 2025-09-02 09:14 | -07:00 | 09/02 - 09/08 | 2025-09-02 09:26 | -07:00 | 12 | FTS | 540 | 45 | 0 | 0 | 1 | 0 | 0 | 0 | 12
25-0093638 | Solano | VACAVILLE 1104 | VACAVILLE 1104CB | Unknown Cause | 2025-09-02 07:30 | -07:00 | 09/02 - 09/08 | 2025-09-02 09:27 | -07:00 | 27.3009 | FTS | 34836 | 1276 | 76 | 55 | 14 | 0 | 0 | 2 | 117
25-0093548 | Amador | MARTELL 1103 | MARTELL 11033152 | Environmental/External | 2025-09-02 05:21 | -07:00 | 09/02 - 09/08 | 2025-09-02 09:57 | -07:00 | 276 | FTS | 38916 | 141 | 10 | 8 | 6 | 0 | 0 | 1 | 276
25-0093729 | Amador | ELECTRA 1101 | ELECTRA 11017104 | Environmental/External | 2025-09-02 09:13 | -07:00 | 09/02 - 09/08 | 2025-09-02 09:57 | -07:00 | 44 | FTS | 2992 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 44
25-0093573 | Fresno | COALINGA NO 1 1109 | COALINGA NO 1 1109696152 | Environmental/External | 2025-09-02 05:35 | -07:00 | 09/02 - 09/08 | 2025-09-02 10:23 | -07:00 | 288 | FTS | 2016 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 288
25-0093668 | Shasta | DESCHUTES 1101 | DESCHUTES 1101CB | Unknown Cause | 2025-09-02 08:46 | -07:00 | 09/02 - 09/08 | 2025-09-02 10:27 | -07:00 | 54.2979 | FTS | 65429 | 1205 | 81 | 56 | 19 | 3 | 0 | 8 | 101
25-0093728 | Monterey | LOS OSITOS 2103 | LOS OSITOS 2103606732 | 3rd Party | 2025-09-02 09:44 | -07:00 | 09/02 - 09/08 | 2025-09-02 10:40 | -07:00 | 56 | HLT | 1792 | 32 | 1 | 1 | 0 | 0 | 0 | 0 | 56
25-0093707 | Tuolumne | CURTIS 1705 | CURTIS 170565908 | Environmental/External | 2025-09-02 09:18 | -07:00 | 09/02 - 09/08 | 2025-09-02 10:46 | -07:00 | 88 | FTS | 59752 | 679 | 43 | 35 | 7 | 5 | 0 | 0 | 88
25-0093509 | Napa | SILVERADO 2104 | SILVERADO 2104106272 | Unknown Cause | 2025-09-01 22:23 | -07:00 | 09/02 - 09/08 | 2025-09-02 10:47 | -07:00 | 744 | FTS | 130944 | 176 | 1 | 0 | 2 | 0 | 0 | 0 | 744
25-0093581 | Tuolumne | PEORIA 1704 | PEORIA 17048040 | Environmental/External | 2025-09-02 06:45 | -07:00 | 09/02 - 09/08 | 2025-09-02 11:31 | -07:00 | 257.3083 | FTS | 34222 | 133 | 2 | 2 | 7 | 0 | 0 | 1 | 286
25-0093732 | Tuolumne | CURTIS 1701 | CURTIS 1701CB | Environmental/External | 2025-09-02 09:26 | -07:00 | 09/02 - 09/08 | 2025-09-02 11:57 | -07:00 | 151 | FTS | 397885 | 2635 | 149 | 113 | 35 | 10 | 9 | 0 | 151
25-0093522 | Kern | ANTELOPE 1101, ANTELOPE 1102 | ANTELOPE 1101CB | Unknown Cause | 2025-09-02 02:58 | -07:00 | 09/02 - 09/08 | 2025-09-02 12:10 | -07:00 | 345.8341 | T-EPSS | 75046 | 217 | 0 | 0 | 12 | 0 | 0 | 0 | 552
25-0093693 | Tuolumne | CURTIS 1703 | CURTIS 170384944 | Environmental/External | 2025-09-02 09:10 | -07:00 | 09/02 - 09/08 | 2025-09-02 12:13 | -07:00 | 158.7641 | FTS | 516777 | 3255 | 177 | 134 | 46 | 1 | 0 | 8 | 183
25-0093520 | San Luis Obispo | CHOLAME 1101, CHOLAME 2102 | CHOLAME 2102X08 | Unknown Cause | 2025-09-02 02:57 | -07:00 | 09/02 - 09/08 | 2025-09-02 12:36 | -07:00 | 527.5304 | T-EPSS | 833498 | 1580 | 44 | 29 | 39 | 6 | 0 | 0 | 579
25-0093567 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113A70 | Unknown Cause | 2025-09-02 06:18 | -07:00 | 09/02 - 09/08 | 2025-09-02 13:00 | -07:00 | 152.3589 | FTS | 261905 | 1719 | 74 | 57 | 19 | 2 | 0 | 34 | 402
25-0093686 | Tuolumne | PEORIA 1701 | PEORIA 170190090 | Environmental/External | 2025-09-02 09:05 | -07:00 | 09/02 - 09/08 | 2025-09-02 13:22 | -07:00 | 257 | FTS | 605235 | 2355 | 168 | 125 | 27 | 14 | 0 | 1 | 257
25-0093521 | Kern | DEVILS DEN 1101, DEVILS DEN 1102 | DEVILS DEN 1101CB | Environmental/External | 2025-09-02 02:58 | -07:00 | 09/02 - 09/08 | 2025-09-02 13:56 | -07:00 | 653.9843 | T-EPSS | 83056 | 127 | 0 | 0 | 10 | 0 | 0 | 0 | 658
25-0093563 | Placer | DEL MAR 2109 | DEL MAR 2109CB | Environmental/External | 2025-09-02 06:16 | -07:00 | 09/02 - 09/08 | 2025-09-02 14:04 | -07:00 | 150.6865 | FTS | 757953 | 5030 | 314 | 218 | 45 | 1 | 0 | 1 | 468
25-0093712 | Tuolumne | CURTIS 1702 | CURTIS 1702756888 | Environmental/External | 2025-09-02 09:28 | -07:00 | 09/02 - 09/08 | 2025-09-02 15:17 | -07:00 | 349 | FTS | 45021 | 129 | 16 | 10 | 0 | 0 | 0 | 0 | 349
25-0093666 | Tuolumne | PEORIA 1701 | PEORIA 1701349908 | Environmental/External | 2025-09-02 08:47 | -07:00 | 09/02 - 09/08 | 2025-09-02 15:25 | -07:00 | 398 | FTS | 40994 | 103 | 5 | 4 | 2 | 0 | 0 | 1 | 398
25-0093539 | Calaveras | CALAVERAS CEMENT 1101 | CALAVERAS CEMENT 1101120672 | Environmental/External | 2025-09-02 04:57 | -07:00 | 09/02 - 09/08 | 2025-09-02 16:10 | -07:00 | 435.2436 | FTS | 33949 | 78 | 4 | 4 | 6 | 0 | 0 | 0 | 673
25-0093537 | Alameda | HERDLYN 1102 | HERDLYN 1102609338 | Environmental/External | 2025-09-02 04:46 | -07:00 | 09/02 - 09/08 | 2025-09-02 16:57 | -07:00 | 389 | FTS | 12448 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 731
25-0094134 | El Dorado | SHINGLE SPRINGS 2109 | SHINGLE SPRINGS 210913322 | Company Initiated | 2025-09-02 16:00 | -07:00 | 09/02 - 09/08 | 2025-09-02 17:01 | -07:00 | 61 | FTS | 7808 | 128 | 6 | 6 | 0 | 0 | 0 | 2 | 61
25-0093523 | Fresno | COALINGA NO 2 1107 | COALINGA NO 2 1107CB | Environmental/External | 2025-09-02 03:13 | -07:00 | 09/02 - 09/08 | 2025-09-02 17:56 | -07:00 | 534.5 | HLT | 76968 | 144 | 0 | 0 | 5 | 0 | 0 | 0 | 883
25-0093529 | San Luis Obispo | CUYAMA 1103 | CUYAMA 1103622728 | Equipment Failure/Involved | 2025-09-02 03:53 | -07:00 | 09/02 - 09/08 | 2025-09-02 18:00 | -07:00 | 287.0943 | FTS | 15216 | 53 | 0 | 0 | 4 | 0 | 0 | 0 | 847
25-0093713 | Tuolumne | CURTIS 1702 | CURTIS 170210940 | Environmental/External | 2025-09-02 09:28 | -07:00 | 09/02 - 09/08 | 2025-09-02 18:04 | -07:00 | 269.7671 | FTS | 173730 | 644 | 50 | 39 | 3 | 1 | 0 | 0 | 516
25-0093556 | Fresno | CANTUA 1103 | CANTUA 11039900 | Environmental/External | 2025-09-02 05:50 | -07:00 | 09/02 - 09/08 | 2025-09-02 18:32 | -07:00 | 762 | FTS | 12954 | 17 | 0 | 0 | 1 | 0 | 0 | 0 | 762
25-0094208 | Santa Cruz | LOS GATOS 1106 | LOS GATOS 1106229258 | Unknown Cause | 2025-09-02 17:02 | -07:00 | 09/02 - 09/08 | 2025-09-02 19:02 | -07:00 | 120 | FTS | 18720 | 156 | 10 | 8 | 1 | 0 | 0 | 5 | 120
25-0093716 | Tuolumne | CURTIS 1702 | CURTIS 170247488 | Environmental/External | 2025-09-02 09:23 | -07:00 | 09/02 - 09/08 | 2025-09-02 19:43 | -07:00 | 245.4593 | FTS | 144821 | 590 | 50 | 43 | 7 | 8 | 0 | 2 | 620
25-0094097 | Tuolumne | CURTIS 1704 | CURTIS 1704895006 | Unknown Cause | 2025-09-02 15:52 | -07:00 | 09/02 - 09/08 | 2025-09-02 19:58 | -07:00 | 233.9978 | FTS | 104363 | 446 | 30 | 21 | 7 | 2 | 0 | 1 | 246
25-0094167 | Santa Barbara | CUYAMA 2101 | CUYAMA 21013542 | 3rd Party | 2025-09-02 17:18 | -07:00 | 09/02 - 09/08 | 2025-09-02 20:02 | -07:00 | 164 | FTS | 20336 | 124 | 4 | 4 | 1 | 0 | 0 | 0 | 164
25-0094161 | Butte | WYANDOTTE 1105 | WYANDOTTE 1105329930 | Unknown Cause | 2025-09-02 17:12 | -07:00 | 09/02 - 09/08 | 2025-09-02 20:24 | -07:00 | 192 | FTS | 101376 | 528 | 50 | 33 | 7 | 1 | 0 | 1 | 192
25-0094234 | Yuba | DOBBINS 1101 | DOBBINS 110169722 | Environmental/External | 2025-09-02 19:46 | -07:00 | 09/02 - 09/08 | 2025-09-02 20:48 | -07:00 | 62 | FTS | 43710 | 705 | 58 | 41 | 15 | 2 | 0 | 5 | 62
25-0094222 | Yuba | NARROWS 2101 | NARROWS 21011202 | Environmental/External | 2025-09-02 19:11 | -07:00 | 09/02 - 09/08 | 2025-09-02 21:01 | -07:00 | 110 | FTS | 55770 | 507 | 47 | 31 | 2 | 0 | 0 | 9 | 110
25-0094255 | Nevada | BRUNSWICK 1102 | BRUNSWICK 11021010 | Environmental/External | 2025-09-02 20:31 | -07:00 | 09/02 - 09/08 | 2025-09-02 21:34 | -07:00 | 63 | FTS | 42525 | 675 | 49 | 36 | 3 | 0 | 0 | 15 | 63
25-0094140 | Amador | MARTELL 1103 | MARTELL 11033152 | Equipment Failure/Involved | 2025-09-02 16:42 | -07:00 | 09/02 - 09/08 | 2025-09-02 21:45 | -07:00 | 303 | FTS | 42723 | 141 | 10 | 8 | 6 | 0 | 0 | 1 | 303
25-0094253 | Nevada | BRUNSWICK 1106 | BRUNSWICK 110651486 | Environmental/External | 2025-09-02 20:29 | -07:00 | 09/02 - 09/08 | 2025-09-02 21:52 | -07:00 | 83 | FTS | 72127 | 869 | 68 | 51 | 7 | 0 | 0 | 18 | 83
25-0094261 | Butte | ORO FINO 1102 | ORO FINO 110265932 | Vegetation | 2025-09-02 21:03 | -07:00 | 09/02 - 09/08 | 2025-09-02 22:13 | -07:00 | 66.5428 | FTS | 71600 | 1076 | 87 | 57 | 12 | 1 | 0 | 3 | 70
25-0093525 | San Luis Obispo | SISQUOC 1102 | SISQUOC 1102M52 | Environmental/External | 2025-09-02 03:43 | -07:00 | 09/02 - 09/08 | 2025-09-02 23:51 | -07:00 | 712.7432 | FTS | 52743 | 74 | 3 | 2 | 1 | 0 | 0 | 0 | 1208
25-0094284 | Butte | WYANDOTTE 1107 | WYANDOTTE 11071510 | Environmental/External | 2025-09-02 19:46 | -07:00 | 09/02 - 09/08 | 2025-09-03 00:06 | -07:00 | 260 | FTS | 17420 | 67 | 5 | 4 | 0 | 0 | 0 | 0 | 260
25-0094280 | Shasta | PIT NO 1 1101 | PIT NO 1 1101CB | Equipment Failure/Involved | 2025-09-02 22:50 | -07:00 | 09/02 - 09/08 | 2025-09-03 00:50 | -07:00 | 71.0215 | FTS | 62854 | 885 | 53 | 43 | 33 | 3 | 11 | 0 | 120
25-0094076 | Mendocino | COVELO 1101 | COVELO 110137328 | Vegetation | 2025-09-02 15:31 | -07:00 | 09/02 - 09/08 | 2025-09-03 01:30 | -07:00 | 98.214 | FTS | 109214 | 1112 | 39 | 26 | 22 | 14 | 0 | 5 | 599
25-0094283 | Santa Clara | HICKS 2105 | HICKS 2105954008 | Animal | 2025-09-02 23:22 | -07:00 | 09/02 - 09/08 | 2025-09-03 01:37 | -07:00 | 135 | FTS | 19845 | 147 | 5 | 4 | 7 | 0 | 0 | 0 | 135
25-0093578 | Fresno | COALINGA NO 2 1105 | COALINGA NO 2 110541954 | Environmental/External | 2025-09-02 05:45 | -07:00 | 09/02 - 09/08 | 2025-09-03 02:32 | -07:00 | 998.5583 | FTS | 162765 | 163 | 1 | 1 | 6 | 4 | 0 | 0 | 1247
25-0093935 | Fresno | COALINGA NO 2 1105 | COALINGA NO 2 11059000 | Equipment Failure/Involved | 2025-09-02 12:50 | -07:00 | 09/02 - 09/08 | 2025-09-03 02:40 | -07:00 | 161.625 | FTS | 5172 | 32 | 0 | 0 | 11 | 0 | 0 | 0 | 830
25-0094322 | Santa Clara | SWIFT 2110 | SWIFT 2110XR366 | Animal | 2025-09-03 07:08 | -07:00 | 09/02 - 09/08 | 2025-09-03 08:18 | -07:00 | 69.4232 | FTS | 27561 | 397 | 15 | 10 | 20 | 0 | 0 | 2 | 70
25-0094157 | Mariposa | BEAR VALLEY 2101 | BEAR VALLEY 2101149792 | Environmental/External | 2025-09-02 17:10 | -07:00 | 09/02 - 09/08 | 2025-09-03 08:48 | -07:00 | 95.2326 | FTS | 16380 | 172 | 5 | 4 | 4 | 2 | 0 | 1 | 938
25-0094389 | Butte | BANGOR 1101 | BANGOR 11011804 | Environmental/External | 2025-09-02 19:44 | -07:00 | 09/02 - 09/08 | 2025-09-03 09:23 | -07:00 | 819 | FTS | 89271 | 109 | 6 | 5 | 1 | 0 | 0 | 0 | 819
25-0094305 | El Dorado | APPLE HILL 2102 | APPLE HILL 21029722 | Equipment Failure/Involved | 2025-09-03 03:14 | -07:00 | 09/02 - 09/08 | 2025-09-03 10:07 | -07:00 | 413 | FTS | 49147 | 119 | 3 | 2 | 4 | 0 | 0 | 2 | 413
25-0094216 | Yuba | WHEATLAND 1105 | WHEATLAND 1105248490 | Environmental/External | 2025-09-02 19:07 | -07:00 | 09/02 - 09/08 | 2025-09-03 11:22 | -07:00 | 975 | FTS | 207675 | 213 | 13 | 8 | 3 | 0 | 0 | 5 | 975
25-0094461 | El Dorado | SHINGLE SPRINGS 2110 | SHINGLE SPRINGS 211051800 | Animal | 2025-09-03 10:31 | -07:00 | 09/02 - 09/08 | 2025-09-03 11:39 | -07:00 | 51.5164 | FTS | 51980 | 1009 | 84 | 62 | 12 | 7 | 0 | 12 | 68
25-0094172 | Butte | BUTTE 1105 | BUTTE 1105612016 | Environmental/External | 2025-09-02 17:44 | -07:00 | 09/02 - 09/08 | 2025-09-03 12:10 | -07:00 | 839.0931 | FTS | 171175 | 204 | 13 | 5 | 2 | 1 | 0 | 6 | 1106
25-0094235 | Nevada | NARROWS 2102 | NARROWS 2102960916 | Environmental/External | 2025-09-02 19:39 | -07:00 | 09/02 - 09/08 | 2025-09-03 12:52 | -07:00 | 115.9196 | FTS | 209119 | 1804 | 129 | 88 | 31 | 5 | 0 | 28 | 1033
25-0094160 | Plumas | BIG MEADOWS 2101 | BIG MEADOWS 21012562 | Equipment Failure/Involved | 2025-09-02 17:15 | -07:00 | 09/02 - 09/08 | 2025-09-03 13:32 | -07:00 | 145.0185 | FTS | 31324 | 216 | 13 | 9 | 2 | 0 | 0 | 1 | 1217
25-0094544 | Sonoma | FITCH MOUNTAIN 1113 | FITCH MOUNTAIN 11132955 | Unknown Cause | 2025-09-03 11:31 | -07:00 | 09/02 - 09/08 | 2025-09-03 14:04 | -07:00 | 153 | FTS | 3060 | 20 | 3 | 3 | 0 | 0 | 0 | 0 | 153
25-0094231 | Nevada | GRASS VALLEY 1103 | GRASS VALLEY 11032180 | Environmental/External | 2025-09-02 19:34 | -07:00 | 09/02 - 09/08 | 2025-09-03 14:25 | -07:00 | 828.1603 | FTS | 433956 | 524 | 40 | 26 | 14 | 4 | 0 | 11 | 1131
25-0094269 | Amador | MARTELL 1103 | MARTELL 11033152 | Environmental/External | 2025-09-02 21:57 | -07:00 | 09/02 - 09/08 | 2025-09-03 14:32 | -07:00 | 871.1915 | FTS | 122838 | 141 | 10 | 8 | 6 | 0 | 0 | 1 | 995
25-0094630 | Lake | KONOCTI 1102 | KONOCTI 11021573 | Company Initiated | 2025-09-03 13:12 | -07:00 | 09/02 - 09/08 | 2025-09-03 14:45 | -07:00 | 93 | FTS | 7812 | 84 | 5 | 1 | 0 | 0 | 0 | 1 | 93
25-0093723 | Calaveras | FROGTOWN 1702 | FROGTOWN 1702737236 | Environmental/External | 2025-09-02 09:05 | -07:00 | 09/02 - 09/08 | 2025-09-03 15:24 | -07:00 | 1580.2209 | FTS | 393475 | 249 | 16 | 12 | 0 | 0 | 0 | 2 | 1819
25-0094159 | Mendocino | LAYTONVILLE 1101 | LAYTONVILLE 1101364398 | Vegetation | 2025-09-02 17:13 | -07:00 | 09/02 - 09/08 | 2025-09-03 15:26 | -07:00 | 116.6782 | FTS | 30453 | 261 | 8 | 6 | 8 | 3 | 0 | 0 | 1333
25-0094685 | Butte | KANAKA 1101 | KANAKA 1101713674 | Unknown Cause | 2025-09-03 13:36 | -07:00 | 09/02 - 09/08 | 2025-09-03 15:27 | -07:00 | 111 | FTS | 999 | 9 | 0 | 0 | 5 | 0 | 0 | 0 | 111
25-0094693 | Mariposa | MARIPOSA 2101 | MARIPOSA 21019400 | Company Initiated | 2025-09-03 15:43 | -07:00 | 09/02 - 09/08 | 2025-09-03 15:53 | -07:00 | 10 | FTS | 1380 | 138 | 3 | 2 | 1 | 0 | 0 | 0 | 10
25-0094292 | Shasta | DESCHUTES 1104 | DESCHUTES 1104656708 | Vegetation | 2025-09-03 00:23 | -07:00 | 09/02 - 09/08 | 2025-09-03 15:56 | -07:00 | 338.8939 | FTS | 143691 | 424 | 35 | 24 | 3 | 0 | 0 | 5 | 933
25-0094298 | Lake | HIGHLANDS 1103 | HIGHLANDS 1103520 | Vegetation | 2025-09-03 01:39 | -07:00 | 09/02 - 09/08 | 2025-09-03 16:47 | -07:00 | 502.2123 | FTS | 366615 | 730 | 56 | 32 | 5 | 0 | 0 | 7 | 908
25-0094735 | Tuolumne | CURTIS 1702 | CURTIS 1702873788 | Environmental/External | 2025-09-02 09:26 | -07:00 | 09/02 - 09/08 | 2025-09-03 17:03 | -07:00 | 1897 | FTS | 55013 | 29 | 1 | 1 | 0 | 0 | 0 | 0 | 1897
25-0094194 | Plumas | BIG MEADOWS 2101 | BIG MEADOWS 21012476 | Vegetation | 2025-09-02 18:12 | -07:00 | 09/02 - 09/08 | 2025-09-03 17:06 | -07:00 | 382.9938 | FTS | 621982 | 1624 | 60 | 44 | 20 | 0 | 0 | 1 | 1374
25-0094371 | Placer | LINCOLN 1101 | LINCOLN 1101CB | Animal | 2025-09-03 08:44 | -07:00 | 09/02 - 09/08 | 2025-09-03 18:34 | -07:00 | 133.909 | FTS | 447390 | 3341 | 169 | 130 | 38 | 17 | 0 | 19 | 590
25-0094740 | El Dorado | PLACERVILLE 2106 | PLACERVILLE 21069712 | Vegetation | 2025-09-03 16:49 | -07:00 | 09/02 - 09/08 | 2025-09-03 18:46 | -07:00 | 79.2801 | FTS | 242597 | 3060 | 239 | 185 | 67 | 15 | 0 | 20 | 117
25-0094770 | Nevada | NARROWS 2102 | NARROWS 210248484 | Vegetation | 2025-09-03 21:05 | -07:00 | 09/02 - 09/08 | 2025-09-04 03:02 | -07:00 | 124.8126 | FTS | 77259 | 619 | 39 | 25 | 16 | 4 | 0 | 19 | 357
25-0094659 | Trinity | WILLOW CREEK 1103 | WILLOW CREEK 11032936 | Vegetation | 2025-09-03 15:00 | -07:00 | 09/02 - 09/08 | 2025-09-04 04:38 | -07:00 | 224.6573 | FTS | 128504 | 572 | 30 | 22 | 9 | 1 | 0 | 2 | 818
25-0094812 | Solano | PEABODY 2113 | PEABODY 2113CB | Unknown Cause | 2025-09-04 02:12 | -07:00 | 09/02 - 09/08 | 2025-09-04 04:47 | -07:00 | 155 | FTS | 775 | 5 | 1 | 1 | 0 | 0 | 0 | 0 | 155
25-0094794 | Amador | ELECTRA 1101 | ELECTRA 110136816 | Equipment Failure/Involved | 2025-09-03 23:58 | -07:00 | 09/02 - 09/08 | 2025-09-04 06:38 | -07:00 | 195.1954 | FTS | 16982 | 87 | 8 | 6 | 1 | 0 | 0 | 0 | 400
25-0094929 | Shasta | GIRVAN 1102 | GIRVAN 110280726 | Animal | 2025-09-04 08:42 | -07:00 | 09/02 - 09/08 | 2025-09-04 09:45 | -07:00 | 63 | FTS | 34587 | 549 | 16 | 12 | 8 | 0 | 0 | 1 | 63
25-0095038 | Napa | SILVERADO 2104 | SILVERADO 210478268 | 3rd Party | 2025-09-04 10:01 | -07:00 | 09/02 - 09/08 | 2025-09-04 10:25 | -07:00 | 24 | FTS | 7800 | 325 | 20 | 16 | 11 | 2 | 0 | 5 | 24
25-0095068 | Santa Clara | HOLLISTER 2104 | HOLLISTER 2102676164 | 3rd Party | 2025-09-04 10:43 | -07:00 | 09/02 - 09/08 | 2025-09-04 11:31 | -07:00 | 29.2353 | FTS | 2982 | 102 | 0 | 0 | 13 | 0 | 0 | 0 | 48
25-0095055 | San Luis Obispo | SAN LUIS OBISPO 1107 | SAN LUIS OBISPO 1107V02 | Vegetation | 2025-09-04 10:24 | -07:00 | 09/02 - 09/08 | 2025-09-04 11:41 | -07:00 | 60.9073 | FTS | 132108 | 2169 | 64 | 55 | 43 | 2 | 0 | 51 | 77
25-0095093 | El Dorado | DIAMOND SPRINGS 1106 | DIAMOND SPRINGS 11062100 | Company Initiated | 2025-09-04 11:13 | -07:00 | 09/02 - 09/08 | 2025-09-04 12:08 | -07:00 | 55 | FTS | 1815 | 33 | 3 | 2 | 1 | 0 | 0 | 0 | 55
25-0095158 | Santa Clara | SWIFT 2110 | SWIFT 2110XR366 | Animal | 2025-09-04 12:44 | -07:00 | 09/02 - 09/08 | 2025-09-04 13:34 | -07:00 | 49.4232 | FTS | 19621 | 397 | 15 | 10 | 20 | 0 | 0 | 2 | 50
25-0094824 | Calaveras | STANISLAUS 1701 | STANISLAUS 1701862450 | 3rd Party | 2025-09-04 06:05 | -07:00 | 09/02 - 09/08 | 2025-09-04 13:41 | -07:00 | 171.5866 | FTS | 56452 | 329 | 16 | 14 | 28 | 2 | 0 | 0 | 456
25-0095032 | El Dorado | APPLE HILL 2102 | APPLE HILL 21029722 | Equipment Failure/Involved | 2025-09-04 09:20 | -07:00 | 09/02 - 09/08 | 2025-09-04 13:51 | -07:00 | 271 | FTS | 32249 | 119 | 3 | 2 | 4 | 0 | 0 | 2 | 271
25-0095293 | Calaveras | WEST POINT 1102 | WEST POINT 1102CB | Company Initiated | 2025-09-04 14:25 | -07:00 | 09/02 - 09/08 | 2025-09-04 14:48 | -07:00 | 23 | FTS | 299 | 13 | 2 | 0 | 0 | 0 | 0 | 0 | 23
25-0095380 | Santa Clara | SWIFT 2110 | SWIFT 2110XR366 | Animal | 2025-09-04 16:58 | -07:00 | 09/02 - 09/08 | 2025-09-04 18:44 | -07:00 | 104.8463 | FTS | 41624 | 397 | 15 | 10 | 20 | 0 | 0 | 2 | 106
25-0094199 | Tuolumne | PEORIA 1704 | PEORIA 17048040 | Environmental/External | 2025-09-02 18:19 | -07:00 | 09/02 - 09/08 | 2025-09-04 19:49 | -07:00 | 959.5038 | FTS | 127614 | 133 | 2 | 2 | 7 | 0 | 0 | 1 | 2970
25-0094190 | Calaveras | PEORIA 1704 | PEORIA 170459596 | Environmental/External | 2025-09-02 18:04 | -07:00 | 09/02 - 09/08 | 2025-09-04 19:52 | -07:00 | 5.4924 | FTS | 3625 | 660 | 49 | 33 | 24 | 0 | 0 | 1 | 2988
25-0095296 | Calaveras | FROGTOWN 1702 | FROGTOWN 170211212 | 3rd Party | 2025-09-04 14:36 | -07:00 | 09/02 - 09/08 | 2025-09-04 21:08 | -07:00 | 214.4297 | FTS | 27447 | 128 | 13 | 7 | 6 | 0 | 0 | 0 | 392
25-0095411 | Fresno | AUBERRY 1102 | AUBERRY 1102R309 | Equipment Failure/Involved | 2025-09-04 18:48 | -07:00 | 09/02 - 09/08 | 2025-09-05 01:00 | -07:00 | 244.2479 | FTS | 29554 | 121 | 12 | 8 | 1 | 0 | 0 | 0 | 372
25-0094815 | Shasta | PIT NO 3 2101 | PIT NO 3 21011360 | Environmental/External | 2025-09-04 04:44 | -07:00 | 09/02 - 09/08 | 2025-09-05 01:54 | -07:00 | 386.5614 | FTS | 22034 | 57 | 1 | 1 | 1 | 0 | 0 | 0 | 1270
25-0095382 | Nevada | HIGGINS 1104 | HIGGINS 11041006 | Vegetation | 2025-09-04 16:54 | -07:00 | 09/02 - 09/08 | 2025-09-05 02:58 | -07:00 | 91.7034 | FTS | 172219 | 1878 | 159 | 109 | 18 | 1 | 0 | 9 | 604
25-0094921 | Alameda | CASTRO VALLEY 1102 | CASTRO VALLEY 1102840916 | Equipment Failure/Involved | 2025-09-04 08:40 | -07:00 | 09/02 - 09/08 | 2025-09-05 05:30 | -07:00 | 320.7081 | FTS | 332895 | 1038 | 34 | 23 | 9 | 0 | 0 | 0 | 1250
25-0095504 | Alameda | CAYETANO 2111 | CAYETANO 2111MR444 | 3rd Party | 2025-09-05 07:25 | -07:00 | 09/02 - 09/08 | 2025-09-05 08:06 | -07:00 | 41 | FTS | 123 | 3 | 0 | 0 | 3 | 3 | 0 | 0 | 41
25-0095497 | San Luis Obispo | CHOLAME 2102 | CHOLAME 210249414 | Animal | 2025-09-05 07:02 | -07:00 | 09/02 - 09/08 | 2025-09-05 09:23 | -07:00 | 141 | FTS | 3807 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 141
25-0095422 | Nevada | NARROWS 2105 | NARROWS 21052216 | Unknown Cause | 2025-09-04 19:34 | -07:00 | 09/02 - 09/08 | 2025-09-05 09:25 | -07:00 | 458.8314 | FTS | 476267 | 1038 | 69 | 45 | 8 | 0 | 0 | 29 | 831
25-0095529 | Placer | FORESTHILL 1101, FORESTHILL 1102 | FORESTHILL 1101CB | Unknown Cause | 2025-09-05 07:50 | -07:00 | 09/02 - 09/08 | 2025-09-05 09:30 | -07:00 | 97.4994 | T-EPSS | 255351 | 2619 | 210 | 146 | 36 | 6 | 0 | 4 | 100
25-0095444 | Tulare | STONE CORRAL 1108 | STONE CORRAL 1108CB | 3rd Party | 2025-09-05 00:42 | -07:00 | 09/02 - 09/08 | 2025-09-05 09:33 | -07:00 | 237.7048 | FTS | 214172 | 901 | 13 | 9 | 13 | 4 | 0 | 0 | 531
25-0095520 | Placer | WEIMAR 1101, WEIMAR 1102 | WEIMAR 1101CB | Unknown Cause | 2025-09-05 07:50 | -07:00 | 09/02 - 09/08 | 2025-09-05 09:45 | -07:00 | 87.5487 | T-EPSS | 187967 | 2147 | 155 | 112 | 42 | 28 | 0 | 15 | 115
25-0095595 | Sonoma | MOLINO 1101 | MOLINO 11015042 | Company Initiated | 2025-09-05 09:27 | -07:00 | 09/02 - 09/08 | 2025-09-05 09:47 | -07:00 | 20 | FTS | 320 | 16 | 2 | 1 | 0 | 0 | 0 | 0 | 20
25-0095537 | Placer | BONNIE NOOK 1101, BONNIE NOOK 1102 | BONNIE NOOK 1102CB | Unknown Cause | 2025-09-05 07:50 | -07:00 | 09/02 - 09/08 | 2025-09-05 11:53 | -07:00 | 243 | T-EPSS | 195615 | 805 | 50 | 34 | 23 | 2 | 0 | 1 | 243
25-0095628 | Lake | UPPER LAKE 1101 | UPPER LAKE 110142378 | 3rd Party | 2025-09-05 10:18 | -07:00 | 09/02 - 09/08 | 2025-09-05 11:56 | -07:00 | 52.1529 | FTS | 36507 | 700 | 43 | 28 | 11 | 5 | 0 | 2 | 98
25-0095535 | Placer | SHADY GLEN 1101, SHADY GLEN 1102 | SHADY GLEN 1102CB | Unknown Cause | 2025-09-05 07:50 | -07:00 | 09/02 - 09/08 | 2025-09-05 12:08 | -07:00 | 213.3437 | T-EPSS | 577948 | 2709 | 188 | 132 | 60 | 5 | 0 | 16 | 258
25-0095655 | Nevada | SUMMIT 1102 | SUMMIT 110249484 | Unknown Cause | 2025-09-05 10:39 | -07:00 | 09/02 - 09/08 | 2025-09-05 13:04 | -07:00 | 106.5 | FTS | 10011 | 94 | 1 | 1 | 6 | 0 | 0 | 0 | 145
25-0095450 | El Dorado | APPLE HILL 2102 | APPLE HILL 2102124050 | 3rd Party | 2025-09-05 03:22 | -07:00 | 09/02 - 09/08 | 2025-09-05 13:13 | -07:00 | 216.0373 | FTS | 202643 | 938 | 68 | 47 | 9 | 0 | 0 | 4 | 591
25-0095745 | Solano | VACAVILLE 1109 | VACAVILLE 1109799940 | Animal | 2025-09-05 12:16 | -07:00 | 09/02 - 09/08 | 2025-09-05 13:34 | -07:00 | 78 | FTS | 16068 | 206 | 28 | 19 | 3 | 0 | 0 | 1 | 78
25-0095788 | Lake | HARTLEY 1101 | HARTLEY 110194178 | Animal | 2025-09-05 13:01 | -07:00 | 09/02 - 09/08 | 2025-09-05 13:53 | -07:00 | 52 | FTS | 16224 | 312 | 16 | 9 | 2 | 0 | 0 | 0 | 52
25-0095823 | Monterey | LAURELES 1111 | LAURELES 1111822080 | Company Initiated | 2025-09-05 13:50 | -07:00 | 09/02 - 09/08 | 2025-09-05 14:02 | -07:00 | 12 | FTS | 252 | 21 | 0 | 0 | 1 | 0 | 0 | 1 | 12
25-0095864 | San Luis Obispo | PERRY 1101 | PERRY 1101CB | 3rd Party | 2025-09-05 14:37 | -07:00 | 09/02 - 09/08 | 2025-09-05 15:47 | -07:00 | 68.2154 | FTS | 242574 | 3556 | 119 | 88 | 41 | 6 | 2 | 6 | 70
25-0095515 | Placer | BONNIE NOOK 1102 | BONNIE NOOK 1102542186 | Company Initiated | 2025-09-05 07:50 | -07:00 | 09/02 - 09/08 | 2025-09-05 16:28 | -07:00 | 518 | FTS | 47656 | 92 | 6 | 6 | 1 | 0 | 0 | 2 | 518
25-0094094 | Tuolumne | PEORIA 1701 | PEORIA 170176030 | Environmental/External | 2025-09-02 15:30 | -07:00 | 09/02 - 09/08 | 2025-09-05 21:25 | -07:00 | 23.4914 | FTS | 4111 | 175 | 9 | 7 | 7 | 2 | 0 | 0 | 4675
25-0095964 | Mendocino | WILLITS 1103 | WILLITS 1103826 | Vegetation | 2025-09-05 21:34 | -07:00 | 09/02 - 09/08 | 2025-09-06 00:39 | -07:00 | 154.8002 | FTS | 153407 | 991 | 51 | 34 | 31 | 6 | 0 | 1 | 185
25-0095975 | Yolo | MADISON 2101 | MADISON 2101888814 | Unknown Cause | 2025-09-06 01:38 | -07:00 | 09/02 - 09/08 | 2025-09-06 03:06 | -07:00 | 88 | FTS | 88 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 88
25-0095968 | Mendocino | WILLITS 1103 | WILLITS 110391948 | Unknown Cause | 2025-09-05 21:52 | -07:00 | 09/02 - 09/08 | 2025-09-06 04:01 | -07:00 | 275.9744 | FTS | 32289 | 117 | 8 | 6 | 2 | 0 | 0 | 0 | 369
25-0095980 | Monterey | RESERVATION ROAD 1101 | RESERVATION ROAD 1101383718 | Unknown Cause | 2025-09-06 03:03 | -07:00 | 09/02 - 09/08 | 2025-09-06 04:16 | -07:00 | 26.4775 | FTS | 18799 | 710 | 56 | 40 | 17 | 2 | 0 | 2 | 73
25-0095997 | El Dorado | EL DORADO PH 2102 | EL DORADO PH 210219542 | Unknown Cause | 2025-09-06 07:13 | -07:00 | 09/02 - 09/08 | 2025-09-06 08:15 | -07:00 | 62 | FTS | 38130 | 615 | 45 | 32 | 4 | 0 | 0 | 0 | 62
25-0096039 | Calaveras | WEST POINT 1102 | WEST POINT 11024788 | Company Initiated | 2025-09-06 09:35 | -07:00 | 09/02 - 09/08 | 2025-09-06 09:58 | -07:00 | 23 | FTS | 17112 | 744 | 40 | 29 | 7 | 0 | 0 | 4 | 23
25-0095977 | Placer | SHADY GLEN 1102 | SHADY GLEN 11022232 | Unknown Cause | 2025-09-06 02:26 | -07:00 | 09/02 - 09/08 | 2025-09-06 10:54 | -07:00 | 200.6166 | FTS | 125586 | 626 | 50 | 32 | 22 | 0 | 0 | 5 | 508
25-0096017 | Nevada | NARROWS 2102 | NARROWS 210276952 | Animal | 2025-09-06 08:12 | -07:00 | 09/02 - 09/08 | 2025-09-06 12:16 | -07:00 | 83.5337 | FTS | 75598 | 905 | 79 | 59 | 13 | 0 | 0 | 2 | 244
25-0096024 | Monterey | SOLEDAD 2101 | SOLEDAD 2101107872 | Unknown Cause | 2025-09-06 09:16 | -07:00 | 09/02 - 09/08 | 2025-09-06 12:17 | -07:00 | 174 | FTS | 5742 | 33 | 1 | 1 | 0 | 0 | 0 | 0 | 181
25-0096063 | Calaveras | WEST POINT 1102 | WEST POINT 11024788 | Company Initiated | 2025-09-06 10:42 | -07:00 | 09/02 - 09/08 | 2025-09-06 13:28 | -07:00 | 166 | FTS | 123670 | 745 | 40 | 29 | 7 | 0 | 0 | 4 | 166
25-0096124 | Santa Barbara | SISQUOC 1102 | SISQUOC 1102M52 | Company Initiated | 2025-09-06 15:24 | -07:00 | 09/02 - 09/08 | 2025-09-06 16:20 | -07:00 | 56 | FTS | 112 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 56
25-0096126 | Madera | COARSEGOLD 2102 | COARSEGOLD 21025721 | Company Initiated | 2025-09-06 15:33 | -07:00 | 09/02 - 09/08 | 2025-09-06 16:40 | -07:00 | 67 | FTS | 2814 | 42 | 3 | 2 | 0 | 0 | 0 | 0 | 67
25-0096116 | Santa Clara | LLAGAS 2101 | LLAGAS 2101XR244 | Animal | 2025-09-06 14:28 | -07:00 | 09/02 - 09/08 | 2025-09-06 17:17 | -07:00 | 169 | FTS | 170859 | 1011 | 34 | 20 | 16 | 2 | 0 | 8 | 169
25-0096134 | Contra Costa | TASSAJARA 2112 | TASSAJARA 2112925966 | Unknown Cause | 2025-09-06 16:16 | -07:00 | 09/02 - 09/08 | 2025-09-06 17:32 | -07:00 | 76 | FTS | 35872 | 472 | 30 | 23 | 7 | 4 | 0 | 0 | 76
25-0096151 | Contra Costa | LAKEWOOD 2107 | LAKEWOOD 2107474346 | Unknown Cause | 2025-09-06 18:00 | -07:00 | 09/02 - 09/08 | 2025-09-06 18:56 | -07:00 | 56 | FTS | 4592 | 82 | 9 | 4 | 1 | 0 | 0 | 0 | 56
25-0096147 | Monterey | JOLON 1102 | JOLON 11027004 | Animal | 2025-09-06 17:27 | -07:00 | 09/02 - 09/08 | 2025-09-06 20:04 | -07:00 | 157 | FTS | 23393 | 149 | 2 | 2 | 9 | 0 | 0 | 4 | 157
25-0096145 | Tehama | VOLTA 1101 | VOLTA 1101CB | Animal | 2025-09-06 17:15 | -07:00 | 09/02 - 09/08 | 2025-09-06 20:26 | -07:00 | 186.5157 | FTS | 249185 | 1336 | 69 | 54 | 45 | 3 | 0 | 1 | 191
25-0096072 | San Mateo | WOODSIDE 1101 | WOODSIDE 11018974 | 3rd Party | 2025-09-06 11:16 | -07:00 | 09/02 - 09/08 | 2025-09-06 21:15 | -07:00 | 270.2611 | FTS | 84862 | 314 | 6 | 4 | 14 | 2 | 0 | 2 | 599
25-0096049 | El Dorado | APPLE HILL 2102 | APPLE HILL 21029722 | Equipment Failure/Involved | 2025-09-06 09:03 | -07:00 | 09/02 - 09/08 | 2025-09-06 23:42 | -07:00 | 597.9748 | FTS | 71159 | 119 | 3 | 2 | 4 | 0 | 0 | 2 | 879
25-0096182 | Alameda | SAN RAMON 2107 | SAN RAMON 2107MR441 | Vegetation | 2025-09-07 07:49 | -07:00 | 09/02 - 09/08 | 2025-09-07 10:08 | -07:00 | 139 | FTS | 182924 | 1316 | 56 | 49 | 19 | 2 | 0 | 2 | 139
25-0096176 | Napa | MONTICELLO 1101 | MONTICELLO 11014360 | Unknown Cause | 2025-09-07 06:31 | -07:00 | 09/02 - 09/08 | 2025-09-07 10:25 | -07:00 | 195.0435 | FTS | 53832 | 276 | 7 | 5 | 4 | 0 | 0 | 1 | 234
25-0096208 | Madera | COARSEGOLD 2102 | COARSEGOLD 210210040 | Unknown Cause | 2025-09-07 07:24 | -07:00 | 09/02 - 09/08 | 2025-09-07 11:46 | -07:00 | 262 | FTS | 28558 | 109 | 18 | 11 | 1 | 0 | 0 | 1 | 262
25-0096198 | Napa | PUEBLO 2104 | PUEBLO 210378504 | Unknown Cause | 2025-09-07 10:42 | -07:00 | 09/02 - 09/08 | 2025-09-07 13:40 | -07:00 | 178 | FTS | 23852 | 134 | 11 | 9 | 1 | 0 | 0 | 5 | 178
25-0096199 | Napa | PUEBLO 2104 | PUEBLO 210438686 | Unknown Cause | 2025-09-07 10:44 | -07:00 | 09/02 - 09/08 | 2025-09-07 14:06 | -07:00 | 109.846 | FTS | 101278 | 922 | 25 | 15 | 15 | 0 | 0 | 0 | 202
25-0096237 | Santa Cruz | CAMP EVERS 2103 | CAMP EVERS 2103449218 | Vegetation | 2025-09-07 17:09 | -07:00 | 09/02 - 09/08 | 2025-09-07 19:14 | -07:00 | 125 | FTS | 267875 | 2143 | 139 | 111 | 36 | 1 | 0 | 6 | 125
25-0096161 | Placer | FORESTHILL 1101 | FORESTHILL 11011802 | Equipment Failure/Involved | 2025-09-06 19:16 | -07:00 | 09/02 - 09/08 | 2025-09-07 20:06 | -07:00 | 838.8897 | FTS | 1483157 | 1768 | 154 | 107 | 12 | 2 | 0 | 0 | 1490
25-0096253 | Placer | LINCOLN 1104 | LINCOLN 11042072 | Unknown Cause | 2025-09-07 19:41 | -07:00 | 09/02 - 09/08 | 2025-09-07 21:25 | -07:00 | 104 | FTS | 44304 | 426 | 20 | 8 | 1 | 0 | 0 | 0 | 104
25-0096261 | Santa Clara | MORGAN HILL 2105 | MORGAN HILL 2105CB | Equipment Failure/Involved | 2025-09-08 00:27 | -07:00 | 09/02 - 09/08 | 2025-09-08 04:11 | -07:00 | 210.8753 | FTS | 923212 | 4378 | 256 | 195 | 46 | 9 | 0 | 12 | 224
25-0096288 | Lake | MIDDLETOWN 1101 | MIDDLETOWN 1101548 | Unknown Cause | 2025-09-08 05:00 | -07:00 | 09/02 - 09/08 | 2025-09-08 07:12 | -07:00 | 132 | FTS | 11484 | 87 | 2 | 2 | 0 | 0 | 0 | 0 | 132
25-0096275 | Santa Barbara | CABRILLO 1103 | CABRILLO 1103Y46 | Unknown Cause | 2025-09-08 05:16 | -07:00 | 09/02 - 09/08 | 2025-09-08 07:20 | -07:00 | 107.6232 | FTS | 29704 | 276 | 2 | 2 | 5 | 0 | 0 | 0 | 124
25-0096312 | Placer | BONNIE NOOK 1102 | BONNIE NOOK 1102542186 | Company Initiated | 2025-09-08 08:05 | -07:00 | 09/02 - 09/08 | 2025-09-08 08:18 | -07:00 | 13 | FTS | 1196 | 92 | 6 | 6 | 1 | 0 | 0 | 2 | 13
25-0096292 | Mariposa | MERCED FALLS 1102 | MERCED FALLS 110285002 | Animal | 2025-09-08 07:09 | -07:00 | 09/02 - 09/08 | 2025-09-08 09:14 | -07:00 | 98.0486 | FTS | 54417 | 555 | 39 | 25 | 15 | 2 | 0 | 0 | 125
25-0096300 | Sierra | ALLEGHANY 1101 | ALLEGHANY 1101804 | Unknown Cause | 2025-09-08 07:41 | -07:00 | 09/02 - 09/08 | 2025-09-08 09:52 | -07:00 | 63.7842 | FTS | 38717 | 607 | 26 | 21 | 9 | 0 | 0 | 1 | 131
25-0096443 | Butte | ORO FINO 1102 | ORO FINO 110265932 | Animal | 2025-09-08 11:13 | -07:00 | 09/02 - 09/08 | 2025-09-08 13:13 | -07:00 | 120 | FTS | 127680 | 1064 | 86 | 56 | 12 | 1 | 0 | 3 | 120
25-0096375 | San Luis Obispo | SANTA MARIA 1108 | SANTA MARIA 1108M18 | Equipment Failure/Involved | 2025-09-08 09:31 | -07:00 | 09/02 - 09/08 | 2025-09-08 14:44 | -07:00 | 213.1336 | FTS | 95697 | 449 | 16 | 16 | 4 | 0 | 0 | 20 | 313
25-0096510 | El Dorado | SHINGLE SPRINGS 2109 | SHINGLE SPRINGS 210913322 | Unknown Cause | 2025-09-08 12:48 | -07:00 | 09/02 - 09/08 | 2025-09-08 15:30 | -07:00 | 79.1429 | FTS | 51522 | 651 | 58 | 40 | 4 | 0 | 0 | 10 | 162
25-0096676 | San Luis Obispo | TEMPLETON 2110 | TEMPLETON 21102675 | Unknown Cause | 2025-09-08 15:43 | -07:00 | 09/02 - 09/08 | 2025-09-08 17:21 | -07:00 | 98 | FTS | 11956 | 122 | 3 | 2 | 0 | 0 | 0 | 3 | 98
25-0096366 | Napa | CALISTOGA 1102 | CALISTOGA 1102769230 | Company Initiated | 2025-09-08 19:42 | -07:00 | 09/02 - 09/08 | 2025-09-08 21:42 | -07:00 | 36.1268 | FTS | 25650 | 710 | 7 | 7 | 5 | 0 | 0 | 2 | 120
25-0096693 | Humboldt | GARBERVILLE 1102 | GARBERVILLE 11028652 | Vegetation | 2025-09-08 18:18 | -07:00 | 09/09 - 09/15 | 2025-09-09 03:11 | -07:00 | 181.0956 | FTS | 45455 | 251 | 8 | 6 | 7 | 1 | 0 | 0 | 533
25-0096744 | Lake | HARTLEY 1101 | HARTLEY 110186876 | 3rd Party | 2025-09-09 02:11 | -07:00 | 09/09 - 09/15 | 2025-09-09 04:22 | -07:00 | 131 | FTS | 142135 | 1085 | 78 | 48 | 14 | 0 | 0 | 3 | 131
25-0096774 | Solano | VACAVILLE 1103 | VACAVILLE 1103CB | Animal | 2025-09-09 06:54 | -07:00 | 09/09 - 09/15 | 2025-09-09 07:43 | -07:00 | 49 | FTS | 115640 | 2360 | 132 | 93 | 32 | 11 | 0 | 0 | 49
25-0096777 | Santa Clara | LLAGAS 2107 | LLAGAS 2107374344 | Unknown Cause | 2025-09-09 06:57 | -07:00 | 09/09 - 09/15 | 2025-09-09 08:11 | -07:00 | 74 | FTS | 19536 | 264 | 16 | 11 | 3 | 0 | 0 | 0 | 74
25-0096749 | Tehama | TYLER 1105 | TYLER 11051704 | Unknown Cause | 2025-09-09 03:08 | -07:00 | 09/09 - 09/15 | 2025-09-09 08:35 | -07:00 | 149.4612 | FTS | 125099 | 837 | 75 | 54 | 13 | 3 | 0 | 4 | 327
25-0097124 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 211318370 | Company Initiated | 2025-09-09 14:20 | -07:00 | 09/09 - 09/15 | 2025-09-09 14:36 | -07:00 | 16 | FTS | 3472 | 217 | 10 | 9 | 2 | 0 | 0 | 3 | 16
25-0097074 | San Luis Obispo | CAYUCOS 1102 | CAYUCOS 1102317156 | Unknown Cause | 2025-09-09 13:24 | -07:00 | 09/09 - 09/15 | 2025-09-09 15:14 | -07:00 | 110 | FTS | 5720 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 110
25-0096929 | Amador | PINE GROVE 1102 | PINE GROVE 11023172 | Equipment Failure/Involved | 2025-09-09 10:14 | -07:00 | 09/09 - 09/15 | 2025-09-09 15:27 | -07:00 | 46.6475 | FTS | 145680 | 3123 | 238 | 176 | 52 | 5 | 0 | 5 | 313
25-0097102 | Mendocino | POTTER VALLEY P H 1105 | POTTER VALLEY P H 11051904 | Unknown Cause | 2025-09-09 14:00 | -07:00 | 09/09 - 09/15 | 2025-09-09 15:41 | -07:00 | 101 | FTS | 4141 | 41 | 1 | 1 | 0 | 0 | 0 | 1 | 101
25-0097185 | El Dorado | PLACERVILLE 2106 | PLACERVILLE 21061792 | Company Initiated | 2025-09-09 15:53 | -07:00 | 09/09 - 09/15 | 2025-09-09 16:19 | -07:00 | 9.84 | FTS | 1968 | 200 | 13 | 9 | 8 | 1 | 0 | 1 | 26
25-0097193 | Santa Barbara | CABRILLO 1103 | CABRILLO 1103Y46 | Equipment Failure/Involved | 2025-09-09 16:13 | -07:00 | 09/09 - 09/15 | 2025-09-09 17:38 | -07:00 | 85 | FTS | 23460 | 276 | 2 | 2 | 5 | 0 | 0 | 0 | 85
25-0097190 | Marin | STAFFORD 1102 | STAFFORD 11021258 | Animal | 2025-09-09 16:08 | -07:00 | 09/09 - 09/15 | 2025-09-09 17:55 | -07:00 | 107 | FTS | 128614 | 1202 | 61 | 35 | 6 | 3 | 0 | 1 | 107
25-0097224 | Sutter | MERIDIAN 1102 | MERIDIAN 11023502 | 3rd Party | 2025-09-09 17:05 | -07:00 | 09/09 - 09/15 | 2025-09-09 18:09 | -07:00 | 64 | FTS | 7936 | 124 | 1 | 1 | 2 | 0 | 0 | 0 | 64
25-0097129 | Lake | HARTLEY 1101 | HARTLEY 1101658 | Vegetation | 2025-09-09 14:27 | -07:00 | 09/09 - 09/15 | 2025-09-09 18:12 | -07:00 | 30.9911 | FTS | 97467 | 3145 | 229 | 152 | 36 | 4 | 0 | 8 | 225
25-0097249 | Monterey | SAN ARDO 1102 | SAN ARDO 11027107 | Company Initiated | 2025-09-09 16:14 | -07:00 | 09/09 - 09/15 | 2025-09-09 19:00 | -07:00 | 166 | FTS | 2822 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 166
25-0096909 | Kern | TEMBLOR 1104 | TEMBLOR 1104284004 | Animal | 2025-09-09 09:55 | -07:00 | 09/09 - 09/15 | 2025-09-09 22:30 | -07:00 | 149.9091 | FTS | 4947 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 755
25-0097303 | Mendocino | COVELO 1101 | COVELO 110137328 | Vegetation | 2025-09-10 01:51 | -07:00 | 09/09 - 09/15 | 2025-09-10 04:32 | -07:00 | 122.6097 | FTS | 136342 | 1112 | 39 | 26 | 22 | 14 | 0 | 5 | 161
25-0097302 | Napa | CALISTOGA 1102 | CALISTOGA 1102634 | Unknown Cause | 2025-09-10 00:52 | -07:00 | 09/09 - 09/15 | 2025-09-10 05:37 | -07:00 | 93.6116 | FTS | 43623 | 466 | 7 | 7 | 6 | 0 | 0 | 1 | 285
25-0097358 | Contra Costa | NORTH DUBLIN 2103 | NORTH DUBLIN 2103CB | Company Initiated | 2025-09-10 07:21 | -07:00 | 09/09 - 09/15 | 2025-09-10 07:38 | -07:00 | 17 | FTS | 88842 | 5226 | 175 | 133 | 57 | 7 | 0 | 1 | 17
25-0097310 | Santa Cruz | CAMP EVERS 2107 | CAMP EVERS 210711044 | Vegetation | 2025-09-10 03:54 | -07:00 | 09/09 - 09/15 | 2025-09-10 09:08 | -07:00 | 283.7258 | FTS | 636397 | 2243 | 172 | 136 | 39 | 1 | 0 | 2 | 314
25-0097361 | Contra Costa | NORTH DUBLIN 2103 | NORTH DUBLIN 2103248212 | Unknown Cause | 2025-09-10 07:21 | -07:00 | 09/09 - 09/15 | 2025-09-10 09:20 | -07:00 | 119 | FTS | 6545 | 55 | 5 | 3 | 0 | 0 | 0 | 1 | 119
25-0097227 | Tuolumne | RACETRACK 1704 | RACETRACK 1704787277 | Unknown Cause | 2025-09-09 16:13 | -07:00 | 09/09 - 09/15 | 2025-09-10 09:58 | -07:00 | 505.678 | FTS | 59670 | 118 | 12 | 8 | 4 | 0 | 0 | 0 | 1065
25-0097336 | Santa Clara | LOS GATOS 1106 | LOS GATOS 1106229258 | Unknown Cause | 2025-09-10 07:05 | -07:00 | 09/09 - 09/15 | 2025-09-10 10:23 | -07:00 | 146.4201 | FTS | 116404 | 795 | 60 | 48 | 12 | 3 | 0 | 16 | 198
25-0097254 | Sonoma | FITCH MOUNTAIN 1113 | FITCH MOUNTAIN 111324918 | Vegetation | 2025-09-09 18:06 | -07:00 | 09/09 - 09/15 | 2025-09-10 11:02 | -07:00 | 282.7063 | FTS | 45233 | 160 | 5 | 3 | 4 | 1 | 0 | 0 | 1016
25-0097263 | Fresno | AUBERRY 1101 | AUBERRY 1101D320 | Unknown Cause | 2025-09-09 17:10 | -07:00 | 09/09 - 09/15 | 2025-09-10 11:49 | -07:00 | 1119 | FTS | 25737 | 23 | 2 | 0 | 1 | 0 | 0 | 2 | 1119
25-0097262 | Fresno | AUBERRY 1101 | AUBERRY 1101R324 | Unknown Cause | 2025-09-09 17:10 | -07:00 | 09/09 - 09/15 | 2025-09-10 11:56 | -07:00 | 1126 | FTS | 46166 | 41 | 0 | 0 | 1 | 0 | 0 | 0 | 1126
25-0097534 | Sonoma | MONTE RIO 1113 | MONTE RIO 1113346 | Vegetation | 2025-09-10 10:55 | -07:00 | 09/09 - 09/15 | 2025-09-10 12:16 | -07:00 | 43.8069 | FTS | 22692 | 518 | 39 | 27 | 16 | 5 | 0 | 1 | 81
25-0097500 | Napa | SILVERADO 2102 | SILVERADO 2102914108 | Unknown Cause | 2025-09-10 10:18 | -07:00 | 09/09 - 09/15 | 2025-09-10 13:42 | -07:00 | 204 | FTS | 66096 | 324 | 4 | 2 | 5 | 0 | 0 | 4 | 204
25-0097653 | Lake | MIDDLETOWN 1102 | MIDDLETOWN 1102998 | Environmental/External | 2025-09-10 13:40 | -07:00 | 09/09 - 09/15 | 2025-09-10 14:54 | -07:00 | 74 | FTS | 46028 | 622 | 46 | 36 | 11 | 1 | 0 | 2 | 74
25-0097596 | Sonoma | MOLINO 1102 | MOLINO 1102104 | Vegetation | 2025-09-10 12:32 | -07:00 | 09/09 - 09/15 | 2025-09-10 15:04 | -07:00 | 152 | FTS | 7904 | 52 | 4 | 3 | 0 | 0 | 0 | 2 | 152
25-0097635 | Tehama | RED BLUFF 1101 | RED BLUFF 1101453972 | Animal | 2025-09-10 13:30 | -07:00 | 09/09 - 09/15 | 2025-09-10 15:08 | -07:00 | 98 | FTS | 12642 | 129 | 13 | 7 | 2 | 0 | 0 | 0 | 98
25-0097463 | San Benito | SAN JUSTO 1101 | SAN JUSTO 110136902 | Equipment Failure/Involved | 2025-09-10 09:34 | -07:00 | 09/09 - 09/15 | 2025-09-10 15:43 | -07:00 | 62.3937 | FTS | 13789 | 221 | 12 | 10 | 5 | 1 | 0 | 0 | 369
25-0097673 | Yolo | MADISON 2101 | MADISON 21011606 | Animal | 2025-09-10 14:01 | -07:00 | 09/09 - 09/15 | 2025-09-10 15:46 | -07:00 | 105 | FTS | 54915 | 523 | 8 | 1 | 6 | 0 | 0 | 2 | 105
25-0097714 | Shasta | GIRVAN 1101 | GIRVAN 11011330 | Environmental/External | 2025-09-10 14:50 | -07:00 | 09/09 - 09/15 | 2025-09-10 16:09 | -07:00 | 34.5303 | FTS | 34185 | 990 | 89 | 59 | 24 | 6 | 0 | 0 | 79
25-0097676 | Shasta | DESCHUTES 1101 | DESCHUTES 11019722 | Environmental/External | 2025-09-10 13:57 | -07:00 | 09/09 - 09/15 | 2025-09-10 16:21 | -07:00 | 127.2982 | FTS | 126789 | 996 | 68 | 50 | 17 | 3 | 0 | 8 | 144
25-0097681 | Shasta | GIRVAN 1101 | GIRVAN 1101323094 | Environmental/External | 2025-09-10 14:05 | -07:00 | 09/09 - 09/15 | 2025-09-10 16:21 | -07:00 | 136 | FTS | 20400 | 150 | 9 | 6 | 5 | 0 | 0 | 0 | 136
25-0097775 | Napa | SILVERADO 2102 | SILVERADO 21021607 | Unknown Cause | 2025-09-10 13:47 | -07:00 | 09/09 - 09/15 | 2025-09-10 17:32 | -07:00 | 225 | FTS | 12150 | 54 | 1 | 1 | 1 | 0 | 0 | 0 | 225
25-0097788 | Shasta | WHITMORE 1101 | WHITMORE 11012211 | Environmental/External | 2025-09-10 14:09 | -07:00 | 09/09 - 09/15 | 2025-09-10 17:48 | -07:00 | 219 | FTS | 18177 | 83 | 8 | 2 | 0 | 0 | 0 | 1 | 219
25-0097786 | Tehama | RED BLUFF 1104 | RED BLUFF 11041630 | Environmental/External | 2025-09-10 17:03 | -07:00 | 09/09 - 09/15 | 2025-09-10 18:46 | -07:00 | 103 | FTS | 35844 | 348 | 28 | 22 | 4 | 2 | 0 | 0 | 103
25-0097759 | Tehama | RED BLUFF 1101 | RED BLUFF 11011556 | Environmental/External | 2025-09-10 16:08 | -07:00 | 09/09 - 09/15 | 2025-09-10 19:19 | -07:00 | 191 | FTS | 92062 | 482 | 49 | 36 | 3 | 0 | 0 | 2 | 191
25-0097817 | Santa Clara | EDENVALE 2105 | EDENVALE 2105739448 | Unknown Cause | 2025-09-10 18:44 | -07:00 | 09/09 - 09/15 | 2025-09-10 19:37 | -07:00 | 53 | FTS | 265 | 5 | 0 | 0 | 2 | 0 | 0 | 0 | 53
25-0097769 | Shasta | DESCHUTES 1104 | DESCHUTES 1104421598 | Environmental/External | 2025-09-10 16:18 | -07:00 | 09/09 - 09/15 | 2025-09-10 19:39 | -07:00 | 159.6287 | FTS | 26658 | 167 | 19 | 15 | 1 | 0 | 0 | 1 | 201
25-0097825 | Napa | SILVERADO 2102 | SILVERADO 21021607 | Unknown Cause | 2025-09-10 18:01 | -07:00 | 09/09 - 09/15 | 2025-09-10 19:43 | -07:00 | 102 | FTS | 5508 | 54 | 1 | 1 | 1 | 0 | 0 | 0 | 102
25-0097713 | Shasta | ANTLER 1101 | ANTLER 1101CB | Environmental/External | 2025-09-10 14:49 | -07:00 | 09/09 - 09/15 | 2025-09-10 19:59 | -07:00 | 310 | T-EPSS | 291400 | 940 | 51 | 35 | 27 | 2 | 0 | 1 | 310
25-0097727 | Shasta | KESWICK 1101 | KESWICK 11019712 | Equipment Failure/Involved | 2025-09-10 15:15 | -07:00 | 09/09 - 09/15 | 2025-09-10 20:04 | -07:00 | 142.3474 | FTS | 40569 | 285 | 14 | 9 | 7 | 1 | 0 | 1 | 289
25-0097698 | San Benito | HOLLISTER 2104 | HOLLISTER 21044068 | 3rd Party | 2025-09-10 14:25 | -07:00 | 09/09 - 09/15 | 2025-09-10 20:07 | -07:00 | 43.4138 | FTS | 52140 | 1201 | 44 | 30 | 12 | 2 | 0 | 0 | 342
25-0097704 | Shasta | KESWICK 1101 | KESWICK 11011588 | Environmental/External | 2025-09-10 14:35 | -07:00 | 09/09 - 09/15 | 2025-09-10 22:36 | -07:00 | 162 | FTS | 4860 | 30 | 0 | 0 | 6 | 0 | 0 | 0 | 481
25-0097866 | Fresno | AUBERRY 1102 | AUBERRY 1102CB | Animal | 2025-09-11 00:31 | -07:00 | 09/09 - 09/15 | 2025-09-11 02:08 | -07:00 | 67.2225 | FTS | 114211 | 1699 | 154 | 113 | 24 | 4 | 0 | 11 | 97
25-0097871 | Sutter | PEASE 1104 | PEASE 11041228 | Unknown Cause | 2025-09-11 02:18 | -07:00 | 09/09 - 09/15 | 2025-09-11 03:35 | -07:00 | 77 | FTS | 8624 | 112 | 2 | 0 | 2 | 0 | 0 | 0 | 77
25-0097718 | Santa Clara | MORGAN HILL 2105 | MORGAN HILL 2105XR564 | 3rd Party | 2025-09-10 14:57 | -07:00 | 09/09 - 09/15 | 2025-09-11 04:12 | -07:00 | 100.3333 | FTS | 110768 | 1104 | 52 | 44 | 16 | 3 | 0 | 10 | 795
25-0097862 | San Luis Obispo | OCEANO 1104 | OCEANO 1104Q10 | 3rd Party | 2025-09-10 23:29 | -07:00 | 09/09 - 09/15 | 2025-09-11 07:06 | -07:00 | 243.7484 | FTS | 190855 | 783 | 51 | 40 | 4 | 0 | 0 | 43 | 457
25-0097884 | Tehama | RED BLUFF 1105 | RED BLUFF 11051564 | Unknown Cause | 2025-09-11 05:22 | -07:00 | 09/09 - 09/15 | 2025-09-11 08:02 | -07:00 | 138.3333 | FTS | 78435 | 567 | 50 | 33 | 12 | 1 | 0 | 4 | 160
25-0097878 | Colusa | MAXWELL 1105 | MAXWELL 11053008 | Unknown Cause | 2025-09-11 04:00 | -07:00 | 09/09 - 09/15 | 2025-09-11 08:53 | -07:00 | 293 | FTS | 14357 | 49 | 0 | 0 | 4 | 0 | 0 | 0 | 293
25-0097955 | Fresno | AUBERRY 1101 | AUBERRY 1101R2839 | Company Initiated | 2025-09-11 08:39 | -07:00 | 09/09 - 09/15 | 2025-09-11 09:08 | -07:00 | 29 | FTS | 34336 | 1184 | 104 | 71 | 20 | 6 | 0 | 14 | 29
25-0097631 | Tehama | VOLTA 1101 | VOLTA 110153118 | Environmental/External | 2025-09-10 13:21 | -07:00 | 09/09 - 09/15 | 2025-09-11 10:30 | -07:00 | 301.4487 | FTS | 235130 | 780 | 42 | 31 | 14 | 1 | 0 | 0 | 1269
25-0097809 | Humboldt | GARBERVILLE 1101 | GARBERVILLE 11011617 | Environmental/External | 2025-09-10 17:03 | -07:00 | 09/09 - 09/15 | 2025-09-11 11:17 | -07:00 | 443.6271 | FTS | 26174 | 59 | 0 | 0 | 1 | 3 | 0 | 0 | 1094
25-0097846 | San Mateo | WOODSIDE 1104 | WOODSIDE 1104520832 | Unknown Cause | 2025-09-10 21:06 | -07:00 | 09/09 - 09/15 | 2025-09-11 11:20 | -07:00 | 854 | FTS | 204106 | 239 | 7 | 6 | 9 | 0 | 0 | 0 | 854
25-0098109 | Humboldt | GARBERVILLE 1102 | GARBERVILLE 1102CB | Vegetation | 2025-09-11 12:15 | -07:00 | 09/09 - 09/15 | 2025-09-11 14:10 | -07:00 | 70.1144 | FTS | 128730 | 1836 | 42 | 31 | 54 | 9 | 0 | 0 | 115
25-0098145 | El Dorado | DIAMOND SPRINGS 1106 | DIAMOND SPRINGS 11062100 | Company Initiated | 2025-09-11 13:07 | -07:00 | 09/09 - 09/15 | 2025-09-11 15:00 | -07:00 | 113 | FTS | 3729 | 33 | 3 | 2 | 1 | 0 | 0 | 0 | 113
25-0098148 | Napa | NAPA 1112 | NAPA 1112895680 | Unknown Cause | 2025-09-11 13:16 | -07:00 | 09/09 - 09/15 | 2025-09-11 15:05 | -07:00 | 109 | FTS | 13407 | 123 | 4 | 2 | 0 | 0 | 0 | 3 | 109
25-0098330 | Santa Barbara | CABRILLO 1103 | CABRILLO 1103420128 | Unknown Cause | 2025-09-11 18:20 | -07:00 | 09/09 - 09/15 | 2025-09-11 20:06 | -07:00 | 106 | FTS | 14734 | 139 | 2 | 2 | 1 | 0 | 0 | 1 | 106
25-0098359 | Shasta | VOLTA 1102 | VOLTA 110254932 | Equipment Failure/Involved | 2025-09-11 22:21 | -07:00 | 09/09 - 09/15 | 2025-09-12 00:06 | -07:00 | 105 | FTS | 22365 | 213 | 23 | 18 | 3 | 0 | 0 | 0 | 105
25-0098299 | Placer | WEIMAR 1101 | WEIMAR 11012058 | Unknown Cause | 2025-09-11 16:29 | -07:00 | 09/09 - 09/15 | 2025-09-12 06:39 | -07:00 | 318.2903 | FTS | 189701 | 596 | 30 | 21 | 10 | 0 | 0 | 6 | 850
25-0098386 | San Benito | LOS OSITOS 2101 | LOS OSITOS 21017014 | Unknown Cause | 2025-09-12 06:23 | -07:00 | 09/09 - 09/15 | 2025-09-12 10:22 | -07:00 | 184.85 | FTS | 29576 | 160 | 4 | 4 | 4 | 1 | 0 | 0 | 239
25-0098444 | Madera | OAKHURST 1102 | OAKHURST 1102333062 | Unknown Cause | 2025-09-12 08:31 | -07:00 | 09/09 - 09/15 | 2025-09-12 11:00 | -07:00 | 149 | FTS | 119796 | 804 | 46 | 35 | 37 | 0 | 0 | 0 | 149
25-0098755 | Glenn | LOGAN CREEK 2102 | LOGAN CREEK 210262032 | Unknown Cause | 2025-09-12 14:40 | -07:00 | 09/09 - 09/15 | 2025-09-12 16:36 | -07:00 | 116 | FTS | 9396 | 81 | 1 | 1 | 6 | 0 | 0 | 0 | 116
25-0098760 | Placer | WISE 1101 | WISE 1101CB | Unknown Cause | 2025-09-12 15:37 | -07:00 | 09/09 - 09/15 | 2025-09-12 18:05 | -07:00 | 82.9132 | FTS | 176688 | 2131 | 165 | 131 | 24 | 4 | 0 | 61 | 148
25-0098805 | Placer | SHADY GLEN 1101 | SHADY GLEN 11012768 | Animal | 2025-09-12 18:32 | -07:00 | 09/09 - 09/15 | 2025-09-12 22:24 | -07:00 | 173.413 | FTS | 31908 | 184 | 14 | 11 | 6 | 4 | 0 | 1 | 232
25-0098750 | San Luis Obispo | SAN MIGUEL 1107 | SAN MIGUEL 1107R66 | 3rd Party | 2025-09-12 15:23 | -07:00 | 09/09 - 09/15 | 2025-09-13 02:40 | -07:00 | 95.2708 | FTS | 26390 | 277 | 13 | 8 | 2 | 0 | 0 | 1 | 677
25-0098907 | Tuolumne | CURTIS 1703 | CURTIS 1703956734 | Company Initiated | 2025-09-13 11:26 | -07:00 | 09/09 - 09/15 | 2025-09-13 11:53 | -07:00 | 27 | FTS | 2187 | 81 | 2 | 1 | 0 | 0 | 0 | 4 | 27
25-0098924 | Nevada | COLUMBIA HILL 1101 | COLUMBIA HILL 110190730 | Animal | 2025-09-13 12:38 | -07:00 | 09/09 - 09/15 | 2025-09-13 13:52 | -07:00 | 74 | FTS | 6364 | 86 | 1 | 1 | 1 | 0 | 0 | 3 | 74
25-0098821 | Santa Clara | MORGAN HILL 2111 | MORGAN HILL 2111XR398 | Vegetation | 2025-09-12 23:28 | -07:00 | 09/09 - 09/15 | 2025-09-13 14:04 | -07:00 | 565.2275 | FTS | 226091 | 400 | 20 | 17 | 10 | 0 | 0 | 2 | 876
25-0098900 | Mariposa | MARIPOSA 2101 | MARIPOSA 210110990 | Company Initiated | 2025-09-13 11:06 | -07:00 | 09/09 - 09/15 | 2025-09-13 15:25 | -07:00 | 239.1617 | FTS | 121255 | 507 | 34 | 27 | 4 | 0 | 0 | 1 | 259
25-0098953 | Humboldt | GARBERVILLE 1101 | GARBERVILLE 11011617 | Company Initiated | 2025-09-13 14:15 | -07:00 | 09/09 - 09/15 | 2025-09-13 17:50 | -07:00 | 215 | FTS | 12685 | 59 | 0 | 0 | 1 | 3 | 0 | 0 | 215
25-0098946 | San Benito | PANOCHE 1103 | PANOCHE 11034010 | Animal | 2025-09-13 15:59 | -07:00 | 09/09 - 09/15 | 2025-09-13 19:09 | -07:00 | 184.5023 | FTS | 39668 | 215 | 6 | 6 | 8 | 1 | 0 | 0 | 190
25-0098884 | Shasta | BURNEY 1101 | BURNEY 1101355340 | Company Initiated | 2025-09-13 10:18 | -07:00 | 09/09 - 09/15 | 2025-09-13 21:26 | -07:00 | 668 | FTS | 668 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 668
25-0098952 | Shasta | ANTLER 1101 | ANTLER 1101671078 | Unknown Cause | 2025-09-13 17:01 | -07:00 | 09/09 - 09/15 | 2025-09-13 21:41 | -07:00 | 197.1101 | FTS | 42970 | 218 | 15 | 10 | 3 | 0 | 0 | 1 | 280
25-0098963 | Calaveras | CORRAL 1103 | CORRAL 110359770 | 3rd Party | 2025-09-13 21:48 | -07:00 | 09/09 - 09/15 | 2025-09-13 23:48 | -07:00 | 120 | FTS | 29160 | 243 | 23 | 17 | 2 | 0 | 0 | 0 | 120
25-0098974 | Contra Costa | TIDEWATER 2106 | TIDEWATER 2106C514R | Unknown Cause | 2025-09-14 01:38 | -07:00 | 09/09 - 09/15 | 2025-09-14 05:42 | -07:00 | 244 | FTS | 92720 | 380 | 35 | 24 | 2 | 0 | 0 | 0 | 244
25-0098987 | Mendocino | UKIAH 1114 | UKIAH 1114822 | Vegetation | 2025-09-14 03:24 | -07:00 | 09/09 - 09/15 | 2025-09-14 07:33 | -07:00 | 249 | FTS | 2988 | 12 | 1 | 1 | 0 | 0 | 0 | 0 | 249
25-0098991 | Shasta | BURNEY 1101 | BURNEY 11011322 | Company Initiated | 2025-09-14 07:39 | -07:00 | 09/09 - 09/15 | 2025-09-14 08:44 | -07:00 | 58.1029 | FTS | 3951 | 68 | 4 | 4 | 0 | 0 | 0 | 0 | 65
25-0098990 | Shasta | BURNEY 1101 | BURNEY 11011340 | Animal | 2025-09-14 07:39 | -07:00 | 09/09 - 09/15 | 2025-09-14 09:09 | -07:00 | 73.1061 | FTS | 30997 | 424 | 40 | 28 | 6 | 0 | 0 | 0 | 90
25-0098950 | Santa Clara | PIERCY 2110 | PIERCY 2110799154 | Unknown Cause | 2025-09-13 16:39 | -07:00 | 09/09 - 09/15 | 2025-09-14 10:00 | -07:00 | 237.1554 | FTS | 91542 | 386 | 11 | 7 | 7 | 0 | 0 | 0 | 1041
25-0098962 | Sutter | PEASE 1104 | PEASE 11041228 | Unknown Cause | 2025-09-13 20:29 | -07:00 | 09/09 - 09/15 | 2025-09-14 10:45 | -07:00 | 571.7143 | FTS | 64032 | 112 | 2 | 0 | 2 | 0 | 0 | 0 | 856
25-0098971 | Sonoma | MOLINO 1102 | MOLINO 110266006 | 3rd Party | 2025-09-14 00:07 | -07:00 | 09/09 - 09/15 | 2025-09-14 13:08 | -07:00 | 68.8756 | FTS | 124045 | 1801 | 114 | 88 | 26 | 1 | 0 | 46 | 781
25-0098984 | Mendocino | COVELO 1101 | COVELO 110137328 | Vegetation | 2025-09-14 06:10 | -07:00 | 09/09 - 09/15 | 2025-09-14 15:25 | -07:00 | 138.0865 | FTS | 153276 | 1110 | 39 | 26 | 22 | 14 | 0 | 5 | 555
25-0099045 | Santa Clara | MORGAN HILL 2105 | MORGAN HILL 2105XR176 | Unknown Cause | 2025-09-14 16:04 | -07:00 | 09/09 - 09/15 | 2025-09-14 18:56 | -07:00 | 155.0072 | FTS | 171128 | 1104 | 52 | 44 | 16 | 3 | 0 | 10 | 172
25-0099038 | Sonoma | GEYSERVILLE 1101 | GEYSERVILLE 1101166 | 3rd Party | 2025-09-14 13:56 | -07:00 | 09/09 - 09/15 | 2025-09-14 19:03 | -07:00 | 227.7673 | FTS | 147821 | 649 | 12 | 11 | 8 | 0 | 0 | 6 | 307
25-0098972 | Mendocino | COVELO 1101 | COVELO 1101516510 | Vegetation | 2025-09-14 01:18 | -07:00 | 09/09 - 09/15 | 2025-09-14 19:17 | -07:00 | 1079 | FTS | 64740 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 1079
25-0099050 | Santa Cruz | GREEN VALLEY 2101 | GREEN VALLEY 210111054 | Unknown Cause | 2025-09-14 17:38 | -07:00 | 09/09 - 09/15 | 2025-09-14 19:32 | -07:00 | 69.9161 | FTS | 21674 | 310 | 10 | 7 | 10 | 5 | 0 | 1 | 114
25-0099080 | Lake | MIDDLETOWN 1103 | MIDDLETOWN 1103248100 | Animal | 2025-09-15 05:35 | -07:00 | 09/09 - 09/15 | 2025-09-15 07:38 | -07:00 | 107.2222 | FTS | 16405 | 153 | 6 | 4 | 2 | 0 | 0 | 0 | 123
25-0099085 | Tuolumne | CURTIS 1704 | CURTIS 1704895006 | Unknown Cause | 2025-09-15 06:21 | -07:00 | 09/09 - 09/15 | 2025-09-15 07:45 | -07:00 | 84 | FTS | 37464 | 446 | 30 | 21 | 7 | 2 | 0 | 1 | 84
25-0099064 | San Luis Obispo | BAYWOOD 1101 | BAYWOOD 1101CB | Company Initiated | 2025-09-14 21:42 | -07:00 | 09/09 - 09/15 | 2025-09-15 08:00 | -07:00 | 512.589 | FTS | 149676 | 292 | 7 | 3 | 14 | 19 | 0 | 0 | 618
25-0099106 | Sonoma | COTATI 1102 | COTATI 110259258 | Unknown Cause | 2025-09-15 07:07 | -07:00 | 09/09 - 09/15 | 2025-09-15 08:31 | -07:00 | 74.2222 | FTS | 18704 | 252 | 13 | 12 | 4 | 0 | 0 | 1 | 84
25-0099067 | Napa | SILVERADO 2102 | SILVERADO 21021607 | Unknown Cause | 2025-09-14 22:43 | -07:00 | 09/09 - 09/15 | 2025-09-15 09:48 | -07:00 | 665 | FTS | 35910 | 54 | 1 | 1 | 1 | 0 | 0 | 0 | 665
25-0099136 | Santa Cruz | PAUL SWEET 2106 | PAUL SWEET 2106CB | Unknown Cause | 2025-09-15 07:54 | -07:00 | 09/09 - 09/15 | 2025-09-15 10:05 | -07:00 | 101.3717 | FTS | 325099 | 3207 | 191 | 164 | 39 | 10 | 1 | 16 | 131
25-0068529 | San Luis Obispo | BAYWOOD 1101 | BAYWOOD 1101CB | Company Initiated | 2025-09-15 08:52 | -07:00 | 09/09 - 09/15 | 2025-09-15 10:15 | -07:00 | 75.2805 | FTS | 280721 | 3729 | 95 | 71 | 41 | 21 | 0 | 0 | 83
25-0099183 | Santa Clara | LOYOLA 1102 | LOYOLA 1102550291 | Animal | 2025-09-15 09:12 | -07:00 | 09/09 - 09/15 | 2025-09-15 10:21 | -07:00 | 69 | FTS | 11109 | 161 | 3 | 3 | 3 | 0 | 0 | 0 | 69
25-0099075 | Monterey | LOS OSITOS 2103 | LOS OSITOS 21037086 | Equipment Failure/Involved | 2025-09-15 03:46 | -07:00 | 09/09 - 09/15 | 2025-09-15 16:51 | -07:00 | 199.4179 | HLT | 80166 | 402 | 2 | 1 | 3 | 0 | 0 | 0 | 785
25-0099561 | Tuolumne | CURTIS 1704 | CURTIS 170420771 | Unknown Cause | 2025-09-15 13:57 | -07:00 | 09/09 - 09/15 | 2025-09-15 17:05 | -07:00 | 188 | FTS | 3384 | 18 | 0 | 0 | 0 | 0 | 0 | 1 | 188
25-0091545 | Butte | NOTRE DAME 1104 | NOTRE DAME 1104176446 | Equipment Failure/Involved | 2025-09-15 15:28 | -07:00 | 09/09 - 09/15 | 2025-09-15 19:04 | -07:00 | 23.6891 | FTS | 6325 | 267 | 10 | 7 | 6 | 0 | 0 | 3 | 216
25-0099581 | Mendocino | PHILO 1101 | PHILO 1101431952 | Unknown Cause | 2025-09-15 18:12 | -07:00 | 09/09 - 09/15 | 2025-09-15 19:42 | -07:00 | 90 | FTS | 11340 | 126 | 3 | 3 | 0 | 0 | 0 | 1 | 90
25-0099590 | San Luis Obispo | FOOTHILL 1101 | FOOTHILL 1101549904 | Equipment Failure/Involved | 2025-09-15 19:32 | -07:00 | 09/09 - 09/15 | 2025-09-15 21:30 | -07:00 | 117.6297 | FTS | 819644 | 6968 | 216 | 170 | 77 | 10 | 1 | 8 | 118
25-0099293 | San Luis Obispo | TEMPLETON 2111 | TEMPLETON 2111R86 | 3rd Party | 2025-09-15 11:08 | -07:00 | 09/09 - 09/15 | 2025-09-15 21:30 | -07:00 | 76.0883 | FTS | 21533 | 283 | 13 | 9 | 2 | 0 | 0 | 7 | 622
25-0099139 | El Dorado | SHINGLE SPRINGS 2105 | SHINGLE SPRINGS 210511172 | Equipment Failure/Involved | 2025-09-15 08:01 | -07:00 | 09/09 - 09/15 | 2025-09-15 21:37 | -07:00 | 168.7127 | FTS | 139188 | 825 | 77 | 50 | 7 | 0 | 0 | 0 | 816
25-0099479 | Alameda | FREMONT 1104 | FREMONT 1104645342 | 3rd Party | 2025-09-15 14:58 | -07:00 | 09/16 - 09/22 | 2025-09-16 02:30 | -07:00 | 167.9333 | FTS | 10076 | 60 | 2 | 1 | 6 | 0 | 0 | 0 | 692
25-0099716 | Sonoma | SONOMA 1103 | SONOMA 1103470636 | Company Initiated | 2025-09-16 08:33 | -07:00 | 09/16 - 09/22 | 2025-09-16 09:14 | -07:00 | 40.1851 | FTS | 56018 | 1394 | 43 | 30 | 12 | 1 | 0 | 6 | 41
25-0099638 | El Dorado | MOUNTAIN QUARRIES 2101 | MOUNTAIN QUARRIES 2101117452 | Animal | 2025-09-16 06:28 | -07:00 | 09/16 - 09/22 | 2025-09-16 09:23 | -07:00 | 171.0115 | FTS | 44805 | 262 | 39 | 31 | 1 | 0 | 0 | 9 | 175
25-0099600 | Santa Barbara | CABRILLO 1104 | CABRILLO 1104597930 | Equipment Failure/Involved | 2025-09-15 20:54 | -07:00 | 09/16 - 09/22 | 2025-09-16 09:25 | -07:00 | 741.5097 | FTS | 2418063 | 3261 | 115 | 90 | 31 | 6 | 0 | 0 | 751
25-0099672 | Calaveras | CORRAL 1101 | CORRAL 11012128 | Unknown Cause | 2025-09-16 07:41 | -07:00 | 09/16 - 09/22 | 2025-09-16 10:04 | -07:00 | 103.1189 | FTS | 19077 | 185 | 10 | 7 | 2 | 0 | 0 | 0 | 143
25-0099646 | Nevada | SHADY GLEN 1102 | SHADY GLEN 110248894 | Animal | 2025-09-16 07:01 | -07:00 | 09/16 - 09/22 | 2025-09-16 10:05 | -07:00 | 184 | FTS | 38088 | 207 | 25 | 14 | 4 | 0 | 0 | 1 | 184
25-0099665 | Mendocino | COVELO 1101 | COVELO 1101562360 | Unknown Cause | 2025-09-16 07:35 | -07:00 | 09/16 - 09/22 | 2025-09-16 10:19 | -07:00 | 164 | FTS | 75768 | 462 | 16 | 14 | 1 | 2 | 0 | 3 | 164
25-0099733 | Kern | POSO MOUNTAIN 2101 | POSO MOUNTAIN 2101730862 | 3rd Party | 2025-09-16 08:56 | -07:00 | 09/16 - 09/22 | 2025-09-16 11:08 | -07:00 | 60.7059 | FTS | 3096 | 51 | 0 | 0 | 1 | 0 | 0 | 0 | 132
25-0099708 | Placer | BELL 1107 | BELL 1107CB | Equipment Failure/Involved | 2025-09-16 08:27 | -07:00 | 09/16 - 09/22 | 2025-09-16 12:20 | -07:00 | 79.875 | FTS | 1278 | 16 | 1 | 1 | 0 | 0 | 0 | 0 | 233
25-0099867 | San Luis Obispo | TEMPLETON 2110 | TEMPLETON 2110901690 | Animal | 2025-09-16 11:03 | -07:00 | 09/16 - 09/22 | 2025-09-16 13:09 | -07:00 | 104.3298 | FTS | 29734 | 285 | 4 | 3 | 5 | 0 | 0 | 13 | 126
25-0099898 | San Benito | HOLLISTER 2105 | HOLLISTER 21054018 | Unknown Cause | 2025-09-16 11:31 | -07:00 | 09/16 - 09/22 | 2025-09-16 13:19 | -07:00 | 104.3485 | FTS | 25148 | 241 | 3 | 1 | 5 | 1 | 0 | 0 | 108
25-0099915 | Santa Clara | LOS GATOS 1106 | LOS GATOS 1106229258 | 3rd Party | 2025-09-16 12:02 | -07:00 | 09/16 - 09/22 | 2025-09-16 13:28 | -07:00 | 85.4849 | FTS | 67875 | 794 | 60 | 48 | 12 | 3 | 0 | 16 | 86
25-0099960 | Alameda | FREMONT 1104 | FREMONT 1104MR584 | Unknown Cause | 2025-09-16 11:44 | -07:00 | 09/16 - 09/22 | 2025-09-16 14:09 | -07:00 | 88.8207 | FTS | 111470 | 1255 | 39 | 29 | 20 | 3 | 0 | 0 | 145
25-0099940 | Humboldt | RIO DELL 1102 | RIO DELL 110275970 | Unknown Cause | 2025-09-16 12:23 | -07:00 | 09/16 - 09/22 | 2025-09-16 14:15 | -07:00 | 68.9167 | FTS | 3308 | 48 | 1 | 1 | 10 | 0 | 0 | 0 | 112
25-0099633 | Santa Cruz | POINT MORETTI 1101 | POINT MORETTI 110112122 | Equipment Failure/Involved | 2025-09-16 06:16 | -07:00 | 09/16 - 09/22 | 2025-09-16 14:37 | -07:00 | 172.6875 | FTS | 11052 | 64 | 1 | 1 | 5 | 0 | 0 | 0 | 501
25-0099982 | Butte | BIG BEND 1102 | BIG BEND 1102CB | Company Initiated | 2025-09-16 13:29 | -07:00 | 09/16 - 09/22 | 2025-09-16 14:53 | -07:00 | 59.3323 | FTS | 19817 | 334 | 11 | 8 | 10 | 0 | 0 | 0 | 84
25-0099851 | Napa | SILVERADO 2104 | SILVERADO 2104909390 | Unknown Cause | 2025-09-16 10:21 | -07:00 | 09/16 - 09/22 | 2025-09-16 15:38 | -07:00 | 217.2188 | FTS | 514157 | 2367 | 104 | 70 | 58 | 8 | 24 | 14 | 317
25-0100076 | Mendocino | WILLITS 1103 | WILLITS 1103696 | Vegetation | 2025-09-16 14:30 | -07:00 | 09/16 - 09/22 | 2025-09-16 15:49 | -07:00 | 79 | FTS | 37367 | 473 | 32 | 27 | 9 | 0 | 0 | 1 | 79
25-0100066 | San Benito | PANOCHE 1103 | PANOCHE 11034010 | Unknown Cause | 2025-09-16 14:50 | -07:00 | 09/16 - 09/22 | 2025-09-16 17:10 | -07:00 | 78.7101 | FTS | 16293 | 207 | 6 | 6 | 8 | 1 | 0 | 0 | 140
25-0100166 | Contra Costa | FAIRVIEW 2207 | FAIRVIEW 2207P150 | Animal | 2025-09-16 19:26 | -07:00 | 09/16 - 09/22 | 2025-09-16 20:33 | -07:00 | 67 | FTS | 8844 | 132 | 3 | 2 | 4 | 0 | 0 | 0 | 67
25-0100108 | Santa Cruz | GREEN VALLEY 2103 | ROB ROY 210410714 | Unknown Cause | 2025-09-16 15:56 | -07:00 | 09/16 - 09/22 | 2025-09-16 21:07 | -07:00 | 264.7253 | FTS | 836532 | 3160 | 177 | 145 | 49 | 7 | 0 | 3 | 311
25-0100141 | Fresno | DUNLAP 1103 | DUNLAP 1103124724 | Company Initiated | 2025-09-16 16:41 | -07:00 | 09/16 - 09/22 | 2025-09-16 21:33 | -07:00 | 292 | FTS | 79132 | 271 | 11 | 11 | 1 | 0 | 0 | 0 | 292
25-0099967 | San Joaquin | CORRAL 1101 | CORRAL 110175204 | Equipment Failure/Involved | 2025-09-16 12:58 | -07:00 | 09/16 - 09/22 | 2025-09-17 02:39 | -07:00 | 89.6264 | FTS | 16312 | 182 | 3 | 3 | 4 | 0 | 0 | 0 | 821
25-0100199 | Contra Costa | SAN RAMON 2101 | SAN RAMON 2101CB | Unknown Cause | 2025-09-16 23:28 | -07:00 | 09/16 - 09/22 | 2025-09-17 04:33 | -07:00 | 23.0926 | FTS | 140703 | 6093 | 155 | 116 | 41 | 9 | 0 | 0 | 305
25-0100038 | Napa | SILVERADO 2102 | SILVERADO 2102942170 | Unknown Cause | 2025-09-16 14:05 | -07:00 | 09/16 - 09/22 | 2025-09-17 07:52 | -07:00 | 648.9507 | FTS | 131737 | 203 | 1 | 0 | 3 | 0 | 0 | 1 | 1067
25-0100223 | Calaveras | CORRAL 1102 | CORRAL 110214026 | Unknown Cause | 2025-09-17 06:39 | -07:00 | 09/16 - 09/22 | 2025-09-17 08:01 | -07:00 | 82 | FTS | 10332 | 126 | 9 | 6 | 0 | 0 | 0 | 2 | 82
25-0100225 | Placer | PENRYN 1105 | PENRYN 1105680290 | Unknown Cause | 2025-09-17 06:39 | -07:00 | 09/16 - 09/22 | 2025-09-17 08:41 | -07:00 | 60.7635 | FTS | 23637 | 389 | 24 | 12 | 3 | 0 | 0 | 7 | 122
25-0100214 | Monterey | SOLEDAD 2102 | SOLEDAD 21027008 | Unknown Cause | 2025-09-17 06:20 | -07:00 | 09/16 - 09/22 | 2025-09-17 08:44 | -07:00 | 144 | FTS | 13680 | 95 | 0 | 0 | 3 | 0 | 0 | 0 | 144
25-0100397 | Napa | SILVERADO 2103 | SILVERADO 2103507513 | Company Initiated | 2025-09-17 09:58 | -07:00 | 09/16 - 09/22 | 2025-09-17 10:09 | -07:00 | 11 | FTS | 1122 | 102 | 1 | 0 | 1 | 0 | 0 | 0 | 11
25-0100278 | Marin | WOODACRE 1101 | WOODACRE 110191900 | Equipment Failure/Involved | 2025-09-17 07:58 | -07:00 | 09/16 - 09/22 | 2025-09-17 12:07 | -07:00 | 87.4425 | FTS | 9881 | 113 | 2 | 1 | 3 | 2 | 0 | 2 | 249
25-0100373 | San Luis Obispo | ATASCADERO 1103 | ATASCADERO 1103411671 | Unknown Cause | 2025-09-17 09:36 | -07:00 | 09/16 - 09/22 | 2025-09-17 13:01 | -07:00 | 125.8333 | FTS | 28690 | 228 | 9 | 6 | 2 | 0 | 0 | 4 | 205
25-0100543 | Contra Costa | VALLEY VIEW 1103 | VALLEY VIEW 1103P158 | Unknown Cause | 2025-09-17 12:44 | -07:00 | 09/16 - 09/22 | 2025-09-17 13:41 | -07:00 | 57 | HLT | 43776 | 768 | 55 | 39 | 7 | 2 | 0 | 0 | 57
25-0100423 | Sonoma | CLOVERDALE 1101 | CLOVERDALE 1101112 | Equipment Failure/Involved | 2025-09-17 10:27 | -07:00 | 09/16 - 09/22 | 2025-09-17 13:52 | -07:00 | 98.6254 | FTS | 328817 | 3334 | 83 | 52 | 23 | 6 | 0 | 2 | 205
25-0100492 | Calaveras | FROGTOWN 1702 | FROGTOWN 1702737236 | Unknown Cause | 2025-09-17 11:37 | -07:00 | 09/16 - 09/22 | 2025-09-17 14:25 | -07:00 | 149.7831 | FTS | 37296 | 249 | 16 | 12 | 0 | 0 | 0 | 2 | 168
25-0100405 | Kern | FELLOWS 2104 | FELLOWS 210442100 | Environmental/External | 2025-09-17 10:08 | -07:00 | 09/16 - 09/22 | 2025-09-17 14:28 | -07:00 | 237.1429 | FTS | 4980 | 21 | 0 | 0 | 7 | 0 | 0 | 0 | 260
25-0100630 | Fresno | DUNLAP 1103 | DUNLAP 11037959F | Unknown Cause | 2025-09-17 11:57 | -07:00 | 09/16 - 09/22 | 2025-09-17 14:34 | -07:00 | 157 | FTS | 9577 | 61 | 3 | 1 | 0 | 0 | 0 | 0 | 157
25-0100511 | Fresno | DUNLAP 1103 | DUNLAP 1103124724 | Company Initiated | 2025-09-17 11:55 | -07:00 | 09/16 - 09/22 | 2025-09-17 14:53 | -07:00 | 178 | FTS | 48238 | 271 | 11 | 11 | 1 | 0 | 0 | 0 | 178
25-0100786 | San Luis Obispo | SAN LUIS OBISPO 1104 | SAN LUIS OBISPO 1104777686 | Environmental/External | 2025-09-17 16:56 | -07:00 | 09/16 - 09/22 | 2025-09-17 17:49 | -07:00 | 53 | FTS | 901 | 17 | 0 | 0 | 1 | 0 | 0 | 0 | 53
25-0100751 | Marin | OLEMA 1101 | OLEMA 1101435308 | Vegetation | 2025-09-17 16:11 | -07:00 | 09/16 - 09/22 | 2025-09-17 18:02 | -07:00 | 111 | FTS | 80031 | 721 | 16 | 12 | 19 | 5 | 0 | 0 | 111
25-0100839 | Contra Costa | TASSAJARA 2108 | TASSAJARA 2108846900 | Unknown Cause | 2025-09-17 18:42 | -07:00 | 09/16 - 09/22 | 2025-09-17 19:04 | -07:00 | 22 | FTS | 6864 | 312 | 14 | 8 | 1 | 0 | 0 | 1 | 22
25-0100771 | Santa Barbara | DIVIDE 1103 | PURISIMA 110154728 | Environmental/External | 2025-09-17 16:40 | -07:00 | 09/16 - 09/22 | 2025-09-17 19:26 | -07:00 | 79.9524 | FTS | 3358 | 42 | 0 | 0 | 9 | 0 | 0 | 0 | 166
25-0100844 | Marin | NOVATO 1104 | NOVATO 1104CB | Unknown Cause | 2025-09-17 18:41 | -07:00 | 09/16 - 09/22 | 2025-09-17 20:07 | -07:00 | 64.8351 | FTS | 199757 | 3081 | 112 | 77 | 78 | 2 | 0 | 0 | 86
25-0100271 | Tehama | COTTONWOOD 1103 | COTTONWOOD 11031616 | Equipment Failure/Involved | 2025-09-17 07:53 | -07:00 | 09/16 - 09/22 | 2025-09-17 20:46 | -07:00 | 171.6376 | FTS | 39305 | 229 | 13 | 8 | 1 | 0 | 0 | 1 | 773
25-0100785 | Santa Barbara | PALMER 1101 | PALMER 1101M84 | Environmental/External | 2025-09-17 16:57 | -07:00 | 09/16 - 09/22 | 2025-09-17 21:06 | -07:00 | 248.8721 | FTS | 227718 | 915 | 23 | 20 | 8 | 1 | 0 | 0 | 249
25-0100848 | San Mateo | WOODSIDE 1101 | WOODSIDE 11018522 | Company Initiated | 2025-09-17 19:25 | -07:00 | 09/16 - 09/22 | 2025-09-17 22:48 | -07:00 | 152.2357 | FTS | 316498 | 2079 | 76 | 57 | 65 | 19 | 0 | 3 | 203
25-0100860 | Amador | IONE 1101 | IONE 1101CB | Unknown Cause | 2025-09-17 20:35 | -07:00 | 09/16 - 09/22 | 2025-09-17 23:55 | -07:00 | 200 | FTS | 209000 | 1045 | 64 | 48 | 6 | 0 | 0 | 2 | 200
25-0100878 | El Dorado | DIAMOND SPRINGS 1106 | DIAMOND SPRINGS 110699658 | 3rd Party | 2025-09-17 22:43 | -07:00 | 09/16 - 09/22 | 2025-09-18 00:08 | -07:00 | 42.1996 | FTS | 143521 | 3401 | 257 | 188 | 32 | 5 | 0 | 30 | 85
25-0100881 | Placer | DEL MAR 2109 | DEL MAR 210975802 | Unknown Cause | 2025-09-17 23:25 | -07:00 | 09/16 - 09/22 | 2025-09-18 01:24 | -07:00 | 100.0512 | FTS | 371490 | 3713 | 242 | 166 | 31 | 1 | 0 | 1 | 119
25-0100884 | San Mateo | WOODSIDE 1101 | WOODSIDE 11018522 | Company Initiated | 2025-09-18 00:01 | -07:00 | 09/16 - 09/22 | 2025-09-18 02:28 | -07:00 | 91.4829 | FTS | 190193 | 2079 | 76 | 57 | 65 | 19 | 0 | 3 | 147
25-0100888 | Santa Cruz | BIG BASIN 1102 | BIG BASIN 110212992 | Vegetation | 2025-09-18 00:51 | -07:00 | 09/16 - 09/22 | 2025-09-18 05:41 | -07:00 | 145.5152 | FTS | 100842 | 693 | 43 | 36 | 12 | 1 | 0 | 2 | 290
25-0100949 | Calaveras | WEST POINT 1102 | WEST POINT 11024788 | Company Initiated | 2025-09-18 08:04 | -07:00 | 09/16 - 09/22 | 2025-09-18 08:13 | -07:00 | 9 | FTS | 6525 | 725 | 40 | 29 | 7 | 0 | 0 | 4 | 9
25-0100936 | Sonoma | PETALUMA C 1108 | PETALUMA C 1108208 | Unknown Cause | 2025-09-18 07:16 | -07:00 | 09/16 - 09/22 | 2025-09-18 08:52 | -07:00 | 63.1844 | FTS | 11310 | 179 | 2 | 2 | 6 | 1 | 0 | 1 | 96
25-0100787 | San Luis Obispo | MESA 1101 | MESA 1101CB | Environmental/External | 2025-09-17 16:56 | -07:00 | 09/16 - 09/22 | 2025-09-18 09:01 | -07:00 | 78.3552 | FTS | 164781 | 2103 | 75 | 54 | 35 | 7 | 0 | 22 | 965
25-0101103 | Santa Cruz | BIG BASIN 1101 | BIG BASIN 110169550 | Company Initiated | 2025-09-18 11:47 | -07:00 | 09/16 - 09/22 | 2025-09-18 12:02 | -07:00 | 15 | FTS | 420 | 28 | 1 | 1 | 0 | 0 | 0 | 0 | 15
25-0101116 | Santa Barbara | CUYAMA 2101 | CUYAMA 21013542 | 3rd Party | 2025-09-18 12:21 | -07:00 | 09/16 - 09/22 | 2025-09-18 14:16 | -07:00 | 115 | FTS | 14260 | 124 | 4 | 4 | 1 | 0 | 0 | 0 | 115
25-0100981 | Humboldt | BRIDGEVILLE 1101 | BRIDGEVILLE 110137484 | Unknown Cause | 2025-09-18 08:47 | -07:00 | 09/16 - 09/22 | 2025-09-18 14:43 | -07:00 | 184.2141 | FTS | 141108 | 766 | 30 | 21 | 12 | 3 | 0 | 0 | 356
25-0101221 | Santa Barbara | CUYAMA 2101 | CUYAMA 21013542 | 3rd Party | 2025-09-18 15:01 | -07:00 | 09/16 - 09/22 | 2025-09-18 15:47 | -07:00 | 46 | FTS | 5704 | 124 | 4 | 4 | 1 | 0 | 0 | 0 | 46
25-0101243 | Contra Costa | TASSAJARA 2108 | TASSAJARA 2108846900 | Unknown Cause | 2025-09-18 15:41 | -07:00 | 09/16 - 09/22 | 2025-09-18 16:23 | -07:00 | 42 | FTS | 13104 | 312 | 14 | 8 | 1 | 0 | 0 | 1 | 42
25-0101260 | Kings | DEVILS DEN 1101 | DEVILS DEN 11019470 | Animal | 2025-09-18 15:56 | -07:00 | 09/16 - 09/22 | 2025-09-18 18:02 | -07:00 | 126 | FTS | 882 | 7 | 0 | 0 | 1 | 0 | 0 | 0 | 126
25-0101329 | Monterey | SPENCE 1102 | SPENCE 1102276712 | Equipment Failure/Involved | 2025-09-18 18:22 | -07:00 | 09/16 - 09/22 | 2025-09-18 19:38 | -07:00 | 76 | FTS | 15048 | 198 | 1 | 0 | 0 | 0 | 0 | 0 | 76
25-0097338 | Napa | SILVERADO 2103 | SILVERADO 2103CB | 3rd Party | 2025-09-10 07:07 | -07:00 | 09/16 - 09/22 | 2025-09-18 20:34 | -07:00 | 156.0214 | FTS | 160702 | 1030 | 10 | 5 | 13 | 1 | 0 | 2 | 12327
25-0101349 | Sonoma | MONTE RIO 1113 | MONTE RIO 1113CB | Animal | 2025-09-18 19:52 | -07:00 | 09/16 - 09/22 | 2025-09-18 23:02 | -07:00 | 189.6573 | FTS | 745543 | 3931 | 206 | 140 | 68 | 7 | 0 | 2 | 190
25-0100932 | Santa Cruz | CAMP EVERS 2107 | CAMP EVERS 210746311 | Vegetation | 2025-09-18 07:13 | -07:00 | 09/16 - 09/22 | 2025-09-19 01:30 | -07:00 | 590.2203 | FTS | 139292 | 236 | 22 | 17 | 3 | 0 | 0 | 0 | 1097
25-0101857 | El Dorado | APPLE HILL 2102 | APPLE HILL 2102836878 | Vegetation | 2025-09-18 18:56 | -07:00 | 09/16 - 09/22 | 2025-09-19 01:55 | -07:00 | 419 | FTS | 2095 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 419
25-0101410 | San Luis Obispo | CHOLAME 2102 | CHOLAME 2102X20 | Animal | 2025-09-19 00:02 | -07:00 | 09/16 - 09/22 | 2025-09-19 02:48 | -07:00 | 104.5814 | FTS | 8994 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 166
25-0101193 | Santa Clara | MENLO 1103 | MENLO 1103612726 | 3rd Party | 2025-09-18 14:17 | -07:00 | 09/16 - 09/22 | 2025-09-19 03:16 | -07:00 | 97.6088 | FTS | 57882 | 593 | 22 | 17 | 21 | 0 | 0 | 9 | 779
25-0101393 | Mariposa | MARIPOSA 2101 | MARIPOSA 2101CB | Equipment Failure/Involved | 2025-09-18 22:24 | -07:00 | 09/16 - 09/22 | 2025-09-19 04:07 | -07:00 | 324.5433 | FTS | 1246571 | 3841 | 257 | 181 | 62 | 0 | 10 | 2 | 343
25-0101444 | Tulare | REEDLEY 1112 | REEDLEY 11127240 | Unknown Cause | 2025-09-19 04:20 | -07:00 | 09/16 - 09/22 | 2025-09-19 06:37 | -07:00 | 137 | FTS | 41374 | 302 | 2 | 1 | 1 | 0 | 0 | 0 | 137
25-0101491 | Tuolumne | MIWUK 1702 | MIWUK 170236888 | Unknown Cause | 2025-09-19 07:50 | -07:00 | 09/16 - 09/22 | 2025-09-19 08:09 | -07:00 | 19 | FTS | 5244 | 276 | 12 | 8 | 3 | 0 | 0 | 0 | 19
25-0101440 | Mendocino | COVELO 1101 | COVELO 1101CB | Environmental/External | 2025-09-19 03:49 | -07:00 | 09/16 - 09/22 | 2025-09-19 08:26 | -07:00 | 273.4473 | T-EPSS | 373529 | 1366 | 47 | 31 | 24 | 14 | 0 | 5 | 277
25-0101485 | Tulare | REEDLEY 1112 | REEDLEY 11127240 | Unknown Cause | 2025-09-19 07:01 | -07:00 | 09/16 - 09/22 | 2025-09-19 08:37 | -07:00 | 96 | FTS | 28992 | 302 | 2 | 1 | 1 | 0 | 0 | 0 | 96
25-0101403 | Napa | SILVERADO 2102 | SILVERADO 21021607 | Unknown Cause | 2025-09-18 21:46 | -07:00 | 09/16 - 09/22 | 2025-09-19 08:49 | -07:00 | 663 | FTS | 35802 | 54 | 1 | 1 | 1 | 0 | 0 | 0 | 663
25-0101514 | Placer | BELL 1109 | BELL 110950506 | Company Initiated | 2025-09-19 08:37 | -07:00 | 09/16 - 09/22 | 2025-09-19 09:08 | -07:00 | 31 | FTS | 1302 | 42 | 0 | 0 | 3 | 0 | 0 | 0 | 31
25-0101421 | San Luis Obispo | CHOLAME 2102 | CHOLAME 2102654164 | Animal | 2025-09-19 01:22 | -07:00 | 09/16 - 09/22 | 2025-09-19 10:05 | -07:00 | 523 | FTS | 4184 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 523
25-0101430 | Napa | BASALT 1106 | BASALT 1106657038 | Vegetation | 2025-09-19 02:50 | -07:00 | 09/16 - 09/22 | 2025-09-19 10:09 | -07:00 | 275.4146 | FTS | 33876 | 123 | 0 | 0 | 7 | 0 | 0 | 0 | 439
25-0101495 | Fresno | TIVY VALLEY 1107 | TIVY VALLEY 11077380 | Unknown Cause | 2025-09-19 07:58 | -07:00 | 09/16 - 09/22 | 2025-09-19 10:44 | -07:00 | 165.6935 | FTS | 125430 | 757 | 51 | 34 | 14 | 0 | 0 | 2 | 166
25-0101549 | Santa Cruz | BIG BASIN 1101 | BIG BASIN 110195690 | Unknown Cause | 2025-09-19 09:20 | -07:00 | 09/16 - 09/22 | 2025-09-19 10:54 | -07:00 | 39.4463 | FTS | 83784 | 2124 | 146 | 121 | 29 | 1 | 0 | 2 | 94
25-0100402 | Kern | MARICOPA 1102 | MARICOPA 11023082 | Environmental/External | 2025-09-17 10:06 | -07:00 | 09/16 - 09/22 | 2025-09-19 11:36 | -07:00 | 294.6114 | FTS | 56860 | 193 | 15 | 10 | 5 | 2 | 0 | 0 | 2970
25-0101446 | Tehama | CORNING 1102 | CORNING 11021900 | Unknown Cause | 2025-09-19 04:21 | -07:00 | 09/16 - 09/22 | 2025-09-19 11:44 | -07:00 | 227.3571 | FTS | 82758 | 364 | 18 | 13 | 10 | 3 | 0 | 1 | 443
25-0101640 | Mendocino | GARBERVILLE 1101 | GARBERVILLE 11011770 | Vegetation | 2025-09-19 10:48 | -07:00 | 09/16 - 09/22 | 2025-09-19 11:59 | -07:00 | 53.5153 | FTS | 8723 | 163 | 2 | 2 | 5 | 0 | 0 | 0 | 71
25-0101436 | San Luis Obispo | CHOLAME 2102 | CHOLAME 2102X22 | Equipment Failure/Involved | 2025-09-19 03:19 | -07:00 | 09/16 - 09/22 | 2025-09-19 12:03 | -07:00 | 524 | FTS | 45064 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 524
25-0101353 | Contra Costa | HERDLYN 1102 | HERDLYN 1102B569R | Animal | 2025-09-18 20:21 | -07:00 | 09/16 - 09/22 | 2025-09-19 12:06 | -07:00 | 945 | HLT | 10395 | 11 | 0 | 0 | 4 | 0 | 0 | 0 | 945
25-0101451 | Kings | DEVILS DEN 1101 | DEVILS DEN 1101824190 | Animal | 2025-09-19 03:25 | -07:00 | 09/16 - 09/22 | 2025-09-19 12:29 | -07:00 | 426.16 | FTS | 31962 | 75 | 0 | 0 | 7 | 0 | 0 | 0 | 544
25-0101620 | Santa Cruz | LOS GATOS 1107 | LOS GATOS 110760118 | 3rd Party | 2025-09-19 10:24 | -07:00 | 09/16 - 09/22 | 2025-09-19 13:09 | -07:00 | 65.4473 | FTS | 60866 | 930 | 68 | 53 | 28 | 0 | 0 | 30 | 165
25-0101335 | El Dorado | APPLE HILL 2102 | APPLE HILL 2102836878 | Vegetation | 2025-09-18 18:57 | -07:00 | 09/16 - 09/22 | 2025-09-19 13:17 | -07:00 | 401.9663 | FTS | 1918183 | 4772 | 382 | 281 | 62 | 12 | 0 | 63 | 1100
25-0100907 | Mendocino | POTTER VALLEY P H 1105 | POTTER VALLEY P H 110537476 | Equipment Failure/Involved | 2025-09-18 05:32 | -07:00 | 09/16 - 09/22 | 2025-09-19 13:40 | -07:00 | 172.0619 | FTS | 19443 | 113 | 1 | 1 | 0 | 0 | 0 | 1 | 1928
25-0101448 | San Luis Obispo | CARRIZO PLAINS 1101 | CARRIZO PLAINS 1101384116 | Equipment Failure/Involved | 2025-09-19 04:47 | -07:00 | 09/16 - 09/22 | 2025-09-19 13:56 | -07:00 | 294.7727 | FTS | 97275 | 330 | 5 | 3 | 7 | 1 | 3 | 0 | 549
25-0101435 | Kern | CARNERAS 1103 | CARNERAS 1103CB | Equipment Failure/Involved | 2025-09-19 03:27 | -07:00 | 09/16 - 09/22 | 2025-09-19 15:59 | -07:00 | 247.2821 | HLT | 9644 | 39 | 0 | 0 | 6 | 0 | 0 | 0 | 752
25-0101920 | Nevada | NARROWS 2102 | NARROWS 210276952 | Animal | 2025-09-19 19:10 | -07:00 | 09/16 - 09/22 | 2025-09-19 20:03 | -07:00 | 42.723 | FTS | 129237 | 3025 | 235 | 151 | 34 | 4 | 0 | 41 | 53
25-0101923 | Sonoma | MONTE RIO 1111 | MONTE RIO 111137520 | Unknown Cause | 2025-09-19 19:26 | -07:00 | 09/16 - 09/22 | 2025-09-19 22:29 | -07:00 | 28.9229 | FTS | 20998 | 726 | 32 | 23 | 19 | 1 | 0 | 1 | 183
25-0101931 | Shasta | VOLTA 1102 | VOLTA 110254932 | Equipment Failure/Involved | 2025-09-19 20:57 | -07:00 | 09/16 - 09/22 | 2025-09-19 23:21 | -07:00 | 107.1925 | FTS | 22832 | 213 | 23 | 18 | 3 | 0 | 0 | 0 | 144
25-0101946 | Monterey | OTTER 1101 | OTTER 1101440 | Unknown Cause | 2025-09-20 01:36 | -07:00 | 09/16 - 09/22 | 2025-09-20 03:04 | -07:00 | 76.0215 | FTS | 60133 | 791 | 31 | 24 | 22 | 2 | 0 | 0 | 88
25-0101953 | Contra Costa | LAKEWOOD 2107 | LAKEWOOD 210769586 | Unknown Cause | 2025-09-20 04:02 | -07:00 | 09/16 - 09/22 | 2025-09-20 05:36 | -07:00 | 87.6237 | FTS | 109442 | 1249 | 66 | 50 | 14 | 0 | 0 | 0 | 94
25-0101955 | Glenn | LOGAN CREEK 2102 | LOGAN CREEK 21022226 | Animal | 2025-09-20 05:05 | -07:00 | 09/16 - 09/22 | 2025-09-20 06:59 | -07:00 | 114 | FTS | 7752 | 68 | 1 | 0 | 0 | 0 | 0 | 0 | 114
25-0101958 | Santa Barbara | ZACA 1101 | ZACA 1101Y72 | Unknown Cause | 2025-09-20 05:53 | -07:00 | 09/16 - 09/22 | 2025-09-20 07:47 | -07:00 | 114 | FTS | 7638 | 67 | 0 | 0 | 8 | 14 | 0 | 0 | 114
25-0101951 | Mariposa | MARIPOSA 2101 | MARIPOSA 2101752630 | Unknown Cause | 2025-09-20 03:52 | -07:00 | 09/16 - 09/22 | 2025-09-20 08:13 | -07:00 | 115.4667 | FTS | 51960 | 450 | 14 | 11 | 8 | 0 | 0 | 0 | 261
25-0101950 | Humboldt | HOOPA 1101 | HOOPA 1101CB | Vegetation | 2025-09-20 03:13 | -07:00 | 09/16 - 09/22 | 2025-09-20 13:31 | -07:00 | 92.3613 | FTS | 190172 | 2059 | 90 | 70 | 60 | 17 | 1 | 0 | 618
25-0102017 | Alameda | FREMONT 1104 | FREMONT 1104MR584 | Unknown Cause | 2025-09-20 12:44 | -07:00 | 09/16 - 09/22 | 2025-09-20 14:03 | -07:00 | 33.2948 | FTS | 41785 | 1255 | 39 | 29 | 20 | 3 | 0 | 0 | 79
25-0102014 | Santa Cruz | SAN BENITO 2104 | SAN BENITO 210488772 | Unknown Cause | 2025-09-20 12:39 | -07:00 | 09/16 - 09/22 | 2025-09-20 14:39 | -07:00 | 103.2312 | FTS | 129039 | 1250 | 86 | 72 | 21 | 1 | 0 | 6 | 120
25-0101970 | Nevada | BRUNSWICK 1104 | BRUNSWICK 11042112 | Animal | 2025-09-20 08:39 | -07:00 | 09/16 - 09/22 | 2025-09-20 15:54 | -07:00 | 124.3402 | FTS | 66522 | 535 | 27 | 18 | 4 | 1 | 0 | 21 | 435
25-0102003 | Shasta | PIT NO 1 1101 | PIT NO 1 1101CB | Animal | 2025-09-20 11:22 | -07:00 | 09/16 - 09/22 | 2025-09-20 17:36 | -07:00 | 33.9887 | FTS | 30080 | 885 | 53 | 43 | 33 | 3 | 11 | 0 | 374
25-0102028 | Santa Cruz | GREEN VALLEY 2103 | ROB ROY 210410960 | Unknown Cause | 2025-09-20 14:01 | -07:00 | 09/16 - 09/22 | 2025-09-20 18:07 | -07:00 | 241.863 | FTS | 681570 | 2818 | 409 | 347 | 104 | 14 | 0 | 7 | 246
25-0102033 | Monterey | LAURELES 1111 | LAURELES 1111192764 | Animal | 2025-09-20 14:33 | -07:00 | 09/16 - 09/22 | 2025-09-20 18:20 | -07:00 | 125.0968 | FTS | 3878 | 31 | 0 | 0 | 3 | 0 | 0 | 0 | 227
25-0102065 | Santa Cruz | CAMP EVERS 2104 | CAMP EVERS 210411048 | Equipment Failure/Involved | 2025-09-20 18:32 | -07:00 | 09/16 - 09/22 | 2025-09-20 23:00 | -07:00 | 177.8558 | FTS | 133214 | 749 | 35 | 30 | 6 | 0 | 0 | 5 | 268
25-0102099 | El Dorado | EL DORADO PH 2101 | EL DORADO PH 21016852 | Company Initiated | 2025-09-21 07:40 | -07:00 | 09/16 - 09/22 | 2025-09-21 08:45 | -07:00 | 65 | FTS | 142740 | 2196 | 179 | 140 | 34 | 3 | 0 | 2 | 65
25-0102092 | Santa Cruz | SAN BENITO 2104 | SAN BENITO 210488772 | Unknown Cause | 2025-09-21 07:00 | -07:00 | 09/16 - 09/22 | 2025-09-21 08:46 | -07:00 | 91.4136 | FTS | 114267 | 1250 | 86 | 72 | 21 | 1 | 0 | 6 | 106
25-0102094 | Santa Clara | SWIFT 2107 | SWIFT 2107XR526 | Unknown Cause | 2025-09-21 07:14 | -07:00 | 09/16 - 09/22 | 2025-09-21 09:26 | -07:00 | 132 | FTS | 29700 | 225 | 7 | 6 | 5 | 0 | 0 | 0 | 132
25-0102077 | Yolo | MADISON 2101 | MADISON 2101484892 | Animal | 2025-09-20 23:05 | -07:00 | 09/16 - 09/22 | 2025-09-21 10:02 | -07:00 | 169.2906 | FTS | 19807 | 117 | 3 | 1 | 0 | 0 | 0 | 0 | 657
25-0102040 | Sonoma | GEYSERVILLE 1101 | GEYSERVILLE 1101166 | 3rd Party | 2025-09-20 15:08 | -07:00 | 09/16 - 09/22 | 2025-09-21 10:54 | -07:00 | 233.0231 | FTS | 151232 | 649 | 12 | 11 | 8 | 0 | 0 | 6 | 1186
25-0102071 | Monterey | SAN MIGUEL 1107 | SAN MIGUEL 1107R66 | Unknown Cause | 2025-09-20 21:11 | -07:00 | 09/16 - 09/22 | 2025-09-21 10:57 | -07:00 | 826 | FTS | 33866 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 826
25-0102107 | Napa | SILVERADO 2104 | SILVERADO 2104773670 | Unknown Cause | 2025-09-21 08:35 | -07:00 | 09/16 - 09/22 | 2025-09-21 12:18 | -07:00 | 147.4435 | FTS | 50868 | 345 | 17 | 8 | 13 | 3 | 0 | 0 | 223
25-0102126 | Sonoma | MOLINO 1102 | MOLINO 1102178 | Unknown Cause | 2025-09-21 10:48 | -07:00 | 09/16 - 09/22 | 2025-09-21 12:38 | -07:00 | 79.8761 | FTS | 189546 | 2373 | 150 | 116 | 30 | 1 | 1 | 61 | 110
25-0102123 | Shasta | OREGON TRAIL 1104 | OREGON TRAIL 11041574 | Equipment Failure/Involved | 2025-09-21 10:01 | -07:00 | 09/16 - 09/22 | 2025-09-21 13:04 | -07:00 | 91.2987 | FTS | 70300 | 770 | 40 | 28 | 4 | 0 | 0 | 0 | 183
25-0102141 | Humboldt | GARBERVILLE 1102 | GARBERVILLE 11028652 | Unknown Cause | 2025-09-21 13:38 | -07:00 | 09/16 - 09/22 | 2025-09-21 14:43 | -07:00 | 65 | FTS | 16250 | 250 | 8 | 6 | 7 | 1 | 0 | 0 | 65
25-0102156 | Santa Clara | MC KEE 1111 | MC KEE 1111711900 | Animal | 2025-09-21 15:04 | -07:00 | 09/16 - 09/22 | 2025-09-21 17:07 | -07:00 | 76.64 | FTS | 45984 | 600 | 29 | 17 | 7 | 0 | 0 | 0 | 123
25-0102160 | Santa Cruz | GREEN VALLEY 2103 | GREEN VALLEY 210310932 | Unknown Cause | 2025-09-21 15:24 | -07:00 | 09/16 - 09/22 | 2025-09-21 17:11 | -07:00 | 55.8755 | HLT | 355089 | 6355 | 409 | 347 | 104 | 14 | 0 | 7 | 107
25-0102180 | Santa Cruz | GREEN VALLEY 2103 | ROB ROY 210410954 | Unknown Cause | 2025-09-21 17:03 | -07:00 | 09/16 - 09/22 | 2025-09-21 18:02 | -07:00 | 59 | FTS | 29500 | 500 | 50 | 46 | 10 | 0 | 0 | 2 | 59
25-0102209 | Placer | LINCOLN 1104 | LINCOLN 1104818790 | Unknown Cause | 2025-09-21 19:31 | -07:00 | 09/16 - 09/22 | 2025-09-21 21:06 | -07:00 | 95 | FTS | 5510 | 58 | 4 | 4 | 0 | 0 | 0 | 1 | 95
25-0102133 | Placer | BELL 1107 | BELL 11072400 | 3rd Party | 2025-09-21 11:58 | -07:00 | 09/16 - 09/22 | 2025-09-22 00:45 | -07:00 | 269.7977 | FTS | 141374 | 524 | 34 | 24 | 2 | 1 | 0 | 10 | 767
25-0102166 | Santa Cruz | CAMP EVERS 2104 | CAMP EVERS 210411048 | Equipment Failure/Involved | 2025-09-21 16:35 | -07:00 | 09/16 - 09/22 | 2025-09-22 03:05 | -07:00 | 86.5661 | FTS | 64838 | 749 | 35 | 30 | 6 | 0 | 0 | 5 | 630
25-0102252 | Mendocino | COVELO 1101 | COVELO 1101516510 | Vegetation | 2025-09-22 00:13 | -07:00 | 09/16 - 09/22 | 2025-09-22 03:24 | -07:00 | 191 | FTS | 11460 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 191
25-0102253 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113520924 | Unknown Cause | 2025-09-22 02:38 | -07:00 | 09/16 - 09/22 | 2025-09-22 05:06 | -07:00 | 118.1412 | FTS | 10042 | 85 | 3 | 3 | 1 | 0 | 0 | 0 | 148
25-0102179 | El Dorado | MOUNTAIN QUARRIES 2101 | MOUNTAIN QUARRIES 21011102 | Unknown Cause | 2025-09-21 16:53 | -07:00 | 09/16 - 09/22 | 2025-09-22 09:57 | -07:00 | 607.9318 | FTS | 489993 | 806 | 84 | 61 | 10 | 0 | 0 | 26 | 1024
25-0102242 | Lake | LUCERNE 1106 | LUCERNE 1106CB | 3rd Party | 2025-09-21 23:17 | -07:00 | 09/16 - 09/22 | 2025-09-22 10:03 | -07:00 | 86.9184 | FTS | 279182 | 3212 | 264 | 185 | 52 | 7 | 1 | 1 | 646
25-0102280 | Santa Barbara | SANTA YNEZ 1101 | SANTA YNEZ 1101Y52 | Unknown Cause | 2025-09-22 07:27 | -07:00 | 09/16 - 09/22 | 2025-09-22 10:04 | -07:00 | 157 | FTS | 29673 | 189 | 0 | 0 | 25 | 0 | 0 | 0 | 157
25-0102189 | Santa Clara | SWIFT 2110 | SWIFT 2110XR254 | Unknown Cause | 2025-09-21 17:47 | -07:00 | 09/16 - 09/22 | 2025-09-22 11:04 | -07:00 | 1037 | FTS | 175253 | 169 | 3 | 0 | 14 | 0 | 0 | 2 | 1037
25-0102335 | Calaveras | FROGTOWN 1702 | FROGTOWN 170275252 | Animal | 2025-09-22 09:15 | -07:00 | 09/16 - 09/22 | 2025-09-22 11:27 | -07:00 | 86.0141 | FTS | 304920 | 3545 | 206 | 150 | 94 | 14 | 1 | 6 | 132
25-0102284 | Napa | SILVERADO 2105 | SILVERADO 2105167360 | Unknown Cause | 2025-09-22 07:39 | -07:00 | 09/16 - 09/22 | 2025-09-22 12:52 | -07:00 | 313 | FTS | 3130 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 313
25-0102473 | Tehama | VOLTA 1101 | VOLTA 110153118 | Unknown Cause | 2025-09-22 12:32 | -07:00 | 09/16 - 09/22 | 2025-09-22 14:40 | -07:00 | 127.9179 | FTS | 99776 | 780 | 42 | 31 | 14 | 1 | 0 | 0 | 128
25-0097083 | San Mateo | WOODSIDE 1104 | WOODSIDE 1104520832 | Company Initiated | 2025-09-22 15:26 | -07:00 | 09/16 - 09/22 | 2025-09-22 15:35 | -07:00 | 9 | FTS | 2115 | 235 | 7 | 6 | 9 | 0 | 0 | 0 | 9
25-0102712 | Santa Clara | STELLING 1111 | STELLING 1111LM10 | Animal | 2025-09-22 17:28 | -07:00 | 09/16 - 09/22 | 2025-09-22 18:26 | -07:00 | 58 | FTS | 6670 | 115 | 3 | 3 | 3 | 1 | 0 | 0 | 58
25-0102745 | San Luis Obispo | PERRY 1101 | PERRY 1101W12 | Unknown Cause | 2025-09-22 19:22 | -07:00 | 09/16 - 09/22 | 2025-09-22 21:00 | -07:00 | 68.166 | FTS | 53374 | 783 | 27 | 19 | 4 | 0 | 0 | 0 | 98
25-0102749 | Napa | PUEBLO 2103 | PUEBLO 210398394 | Unknown Cause | 2025-09-22 19:31 | -07:00 | 09/16 - 09/22 | 2025-09-22 21:06 | -07:00 | 88.4939 | FTS | 138847 | 1569 | 97 | 70 | 16 | 1 | 0 | 1 | 95
25-0102598 | Santa Cruz | CAMP EVERS 2105 | CAMP EVERS 210510214 | Vegetation | 2025-09-22 14:54 | -07:00 | 09/16 - 09/22 | 2025-09-22 21:59 | -07:00 | 234.4725 | FTS | 51115 | 218 | 17 | 15 | 2 | 0 | 0 | 9 | 425
25-0102760 | Contra Costa | TASSAJARA 2108 | TASSAJARA 2108846900 | Unknown Cause | 2025-09-22 20:59 | -07:00 | 09/16 - 09/22 | 2025-09-22 22:44 | -07:00 | 105 | FTS | 32760 | 312 | 14 | 8 | 1 | 0 | 0 | 1 | 105
25-0102780 | Tehama | RED BLUFF 1104 | RED BLUFF 11041302 | Company Initiated | 2025-09-22 23:55 | -07:00 | 09/23 - 09/29 | 2025-09-23 00:02 | -07:00 | 7 | FTS | 3941 | 563 | 41 | 24 | 11 | 0 | 0 | 2 | 7
25-0089787 | Monterey | DEL MONTE 2104 | DEL MONTE 21049500 | Company Initiated | 2025-09-22 11:30 | -07:00 | 09/23 - 09/29 | 2025-09-23 01:45 | -07:00 | 26.7833 | FTS | 87019 | 3249 | 244 | 217 | 74 | 4 | 0 | 5 | 855
25-0094336 | Alameda | OAKLAND K 1104 | OAKLAND X 1104CR288 | Company Initiated | 2025-09-23 07:15 | -07:00 | 09/23 - 09/29 | 2025-09-23 07:22 | -07:00 | 7 | FTS | 4781 | 683 | 26 | 18 | 6 | 0 | 0 | 1 | 7
25-0102781 | Butte | BANGOR 1101 | BANGOR 1101CB | Animal | 2025-09-23 01:14 | -07:00 | 09/23 - 09/29 | 2025-09-23 08:24 | -07:00 | 109.0187 | FTS | 17443 | 160 | 9 | 7 | 0 | 0 | 0 | 2 | 430
25-0093044 | Nevada | BRUNSWICK 1103 | BRUNSWICK 11032784 | Company Initiated | 2025-09-23 08:40 | -07:00 | 09/23 - 09/29 | 2025-09-23 09:01 | -07:00 | 21 | FTS | 70560 | 3360 | 203 | 133 | 52 | 2 | 0 | 36 | 21
25-0102963 | Santa Clara | MORGAN HILL 2108 | MORGAN HILL 2108XR328 | 3rd Party | 2025-09-23 10:45 | -07:00 | 09/23 - 09/29 | 2025-09-23 11:43 | -07:00 | 58 | FTS | 28826 | 497 | 33 | 25 | 12 | 5 | 0 | 0 | 58
25-0102761 | Contra Costa | TASSAJARA 2109 | TASSAJARA 2109CB | Equipment Failure/Involved | 2025-09-22 21:00 | -07:00 | 09/23 - 09/29 | 2025-09-23 12:13 | -07:00 | 64.5194 | FTS | 131039 | 2031 | 100 | 70 | 26 | 0 | 0 | 0 | 913
25-0102997 | Sonoma | DUNBAR 1103 | DUNBAR 1103302 | Company Initiated | 2025-09-23 11:43 | -07:00 | 09/23 - 09/29 | 2025-09-23 12:55 | -07:00 | 72 | FTS | 1512 | 21 | 1 | 1 | 0 | 0 | 0 | 0 | 72
25-0104669 | Tehama | RED BLUFF 1104 | RED BLUFF 11044965 | Company Initiated | 2025-09-23 12:26 | -07:00 | 09/23 - 09/29 | 2025-09-23 13:09 | -07:00 | 43 | FTS | 774 | 18 | 1 | 1 | 0 | 0 | 0 | 0 | 43
25-0096135 | Plumas | BUCKS CREEK 1103 | BUCKS CREEK 1103338520 | Company Initiated | 2025-09-23 11:36 | -07:00 | 09/23 - 09/29 | 2025-09-23 14:02 | -07:00 | 44.7089 | FTS | 13055 | 292 | 11 | 10 | 2 | 0 | 0 | 0 | 146
25-0102916 | Shasta | DESCHUTES 1101 | DESCHUTES 11011580 | Animal | 2025-09-23 09:48 | -07:00 | 09/23 - 09/29 | 2025-09-23 14:06 | -07:00 | 56.6847 | FTS | 19953 | 352 | 23 | 21 | 9 | 2 | 0 | 2 | 258
25-0103160 | Santa Cruz | GREEN VALLEY 2101 | GREEN VALLEY 210190860 | Company Initiated | 2025-09-23 14:54 | -07:00 | 09/23 - 09/29 | 2025-09-23 15:02 | -07:00 | 8 | FTS | 440 | 55 | 7 | 6 | 0 | 0 | 0 | 1 | 8
25-0102979 | El Dorado | APPLE HILL 2102 | APPLE HILL 210297982 | Unknown Cause | 2025-09-23 11:12 | -07:00 | 09/23 - 09/29 | 2025-09-23 15:07 | -07:00 | 116.7091 | FTS | 57771 | 495 | 40 | 29 | 2 | 0 | 0 | 0 | 235
25-0103134 | San Benito | HOLLISTER 2104 | HOLLISTER 21044068 | Unknown Cause | 2025-09-23 14:23 | -07:00 | 09/23 - 09/29 | 2025-09-23 15:09 | -07:00 | 46 | FTS | 55292 | 1202 | 44 | 30 | 12 | 2 | 0 | 0 | 46
25-0103063 | Mendocino | UKIAH 1115 | UKIAH 1115899594 | Equipment Failure/Involved | 2025-09-23 13:14 | -07:00 | 09/23 - 09/29 | 2025-09-23 15:37 | -07:00 | 114.5303 | FTS | 115103 | 1005 | 40 | 27 | 14 | 0 | 1 | 0 | 143
25-0103191 | Amador | PINE GROVE 1102 | PINE GROVE 11023172 | Company Initiated | 2025-09-23 14:57 | -07:00 | 09/23 - 09/29 | 2025-09-23 15:59 | -07:00 | 62 | FTS | 868 | 14 | 3 | 3 | 0 | 0 | 0 | 0 | 62
25-0103239 | Santa Cruz | PAUL SWEET 2109 | ROB ROY 210571630 | Unknown Cause | 2025-09-23 17:17 | -07:00 | 09/23 - 09/29 | 2025-09-23 18:04 | -07:00 | 35.3188 | FTS | 21933 | 621 | 35 | 30 | 7 | 2 | 0 | 5 | 47
25-0103234 | Napa | PUEBLO 1105 | PUEBLO 1105348368 | Unknown Cause | 2025-09-23 17:00 | -07:00 | 09/23 - 09/29 | 2025-09-23 18:35 | -07:00 | 95 | FTS | 19285 | 203 | 14 | 8 | 1 | 0 | 0 | 5 | 95
25-0103271 | Monterey | DEL MONTE 2104 | DEL MONTE 21042624 | Animal | 2025-09-23 18:45 | -07:00 | 09/23 - 09/29 | 2025-09-24 00:08 | -07:00 | 274.1976 | FTS | 1157388 | 4221 | 315 | 277 | 121 | 5 | 0 | 7 | 323
25-0103335 | Monterey | GONZALES 1101 | GONZALES 11013094 | Unknown Cause | 2025-09-24 01:04 | -07:00 | 09/23 - 09/29 | 2025-09-24 02:27 | -07:00 | 83 | FTS | 5644 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 83
25-0103334 | Santa Barbara | SISQUOC 1102 | SISQUOC 1102M52 | Environmental/External | 2025-09-24 00:45 | -07:00 | 09/23 - 09/29 | 2025-09-24 02:59 | -07:00 | 134 | FTS | 9916 | 74 | 3 | 2 | 1 | 0 | 0 | 0 | 134
25-0103319 | Santa Barbara | CABRILLO 1103 | CABRILLO 1103Y46 | Environmental/External | 2025-09-23 22:35 | -07:00 | 09/23 - 09/29 | 2025-09-24 04:56 | -07:00 | 381 | FTS | 105156 | 276 | 2 | 2 | 5 | 0 | 0 | 0 | 381
25-0103341 | San Luis Obispo | CHOLAME 2102 | CHOLAME 2102X04 | Unknown Cause | 2025-09-24 02:13 | -07:00 | 09/23 - 09/29 | 2025-09-24 05:27 | -07:00 | 140.5586 | FTS | 128330 | 913 | 37 | 25 | 12 | 4 | 0 | 0 | 194
25-0103339 | San Luis Obispo | CAYUCOS 1102 | CAYUCOS 1102317156 | Environmental/External | 2025-09-24 02:02 | -07:00 | 09/23 - 09/29 | 2025-09-24 06:06 | -07:00 | 244 | FTS | 12688 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 244
25-0103352 | San Luis Obispo | PERRY 1101 | PERRY 1101V88 | Unknown Cause | 2025-09-24 05:06 | -07:00 | 09/23 - 09/29 | 2025-09-24 06:26 | -07:00 | 41.6861 | FTS | 30806 | 739 | 19 | 11 | 15 | 2 | 0 | 0 | 80
25-0103259 | Santa Barbara | SANTA YNEZ 1102 | SANTA YNEZ 1102320270 | Equipment Failure/Involved | 2025-09-23 18:12 | -07:00 | 09/23 - 09/29 | 2025-09-24 07:49 | -07:00 | 125.4632 | FTS | 28982 | 231 | 2 | 2 | 8 | 0 | 0 | 0 | 817
25-0103377 | Monterey | SAN ARDO 1101 | SAN ARDO 11017094 | Unknown Cause | 2025-09-24 06:48 | -07:00 | 09/23 - 09/29 | 2025-09-24 08:18 | -07:00 | 84.1154 | FTS | 4374 | 52 | 0 | 0 | 1 | 0 | 0 | 0 | 90
25-0103349 | San Luis Obispo | PASO ROBLES 1104 | PASO ROBLES 1104R12 | Environmental/External | 2025-09-24 04:37 | -07:00 | 09/23 - 09/29 | 2025-09-24 08:18 | -07:00 | 124.9065 | FTS | 53460 | 428 | 12 | 7 | 9 | 0 | 0 | 15 | 221
25-0103356 | Monterey | OILFIELDS 1103 | OILFIELDS 1103CB | Environmental/External | 2025-09-24 05:51 | -07:00 | 09/23 - 09/29 | 2025-09-24 08:22 | -07:00 | 150.5823 | FTS | 390460 | 2593 | 107 | 73 | 49 | 2 | 0 | 21 | 151
25-0103343 | San Luis Obispo | CARRIZO PLAINS 1101 | CARRIZO PLAINS 1101384116 | Environmental/External | 2025-09-24 02:55 | -07:00 | 09/23 - 09/29 | 2025-09-24 08:38 | -07:00 | 343 | FTS | 113190 | 330 | 5 | 3 | 7 | 1 | 3 | 0 | 343
25-0103344 | Monterey | JOLON 1102 | JOLON 11027040 | Vegetation | 2025-09-24 03:33 | -07:00 | 09/23 - 09/29 | 2025-09-24 09:36 | -07:00 | 84.2903 | FTS | 7839 | 93 | 4 | 3 | 1 | 0 | 0 | 0 | 363
25-0103440 | Lake | REDBUD 1101 | REDBUD 1101CB | Company Initiated | 2025-09-24 08:29 | -07:00 | 09/23 - 09/29 | 2025-09-24 10:20 | -07:00 | 111 | FTS | 231657 | 2087 | 171 | 125 | 33 | 2 | 0 | 0 | 111
25-0103525 | San Benito | SAN BENITO 2101 | SAN BENITO 2101355426 | Animal | 2025-09-24 09:47 | -07:00 | 09/23 - 09/29 | 2025-09-24 10:21 | -07:00 | 34 | FTS | 16150 | 475 | 17 | 12 | 4 | 0 | 0 | 0 | 34
25-0103517 | Merced | GUSTINE 1102 | GUSTINE 1102562202 | Animal | 2025-09-24 09:40 | -07:00 | 09/23 - 09/29 | 2025-09-24 10:31 | -07:00 | 46.0152 | FTS | 30278 | 658 | 18 | 13 | 12 | 0 | 0 | 0 | 51
25-0103420 | Santa Barbara | SISQUOC 1102 | SISQUOC 11022017 | Environmental/External | 2025-09-24 05:41 | -07:00 | 09/23 - 09/29 | 2025-09-24 10:59 | -07:00 | 318 | FTS | 3180 | 10 | 1 | 1 | 0 | 0 | 0 | 0 | 318
25-0103402 | Calaveras | CALAVERAS CEMENT 1101 | CALAVERAS CEMENT 110180930 | Unknown Cause | 2025-09-24 07:38 | -07:00 | 09/23 - 09/29 | 2025-09-24 11:27 | -07:00 | 124.72 | FTS | 87304 | 700 | 41 | 34 | 18 | 0 | 0 | 0 | 229
25-0103515 | Yuba | WHEATLAND 1105 | WHEATLAND 1105248490 | Equipment Failure/Involved | 2025-09-24 09:31 | -07:00 | 09/23 - 09/29 | 2025-09-24 11:28 | -07:00 | 63.9014 | FTS | 13611 | 213 | 13 | 8 | 3 | 0 | 0 | 5 | 117
25-0103524 | Fresno | COALINGA NO 2 1107 | COALINGA NO 2 1107793144 | Environmental/External | 2025-09-24 09:40 | -07:00 | 09/23 - 09/29 | 2025-09-24 11:38 | -07:00 | 118 | FTS | 6018 | 51 | 0 | 0 | 2 | 0 | 0 | 0 | 118
25-0103634 | Tuolumne | CURTIS 1704 | CURTIS 17048140 | Unknown Cause | 2025-09-24 11:06 | -07:00 | 09/23 - 09/29 | 2025-09-24 12:05 | -07:00 | 59 | FTS | 1652 | 28 | 1 | 1 | 0 | 0 | 0 | 0 | 59
25-0103686 | San Luis Obispo | SANTA MARIA 1108 | SANTA MARIA 1108M80 | Environmental/External | 2025-09-24 00:34 | -07:00 | 09/23 - 09/29 | 2025-09-24 13:07 | -07:00 | 513.2474 | FTS | 199140 | 388 | 15 | 15 | 4 | 0 | 0 | 20 | 753
25-0103625 | San Mateo | HALF MOON BAY 1103 | HALF MOON BAY 11036014 | Unknown Cause | 2025-09-24 11:49 | -07:00 | 09/23 - 09/29 | 2025-09-24 13:12 | -07:00 | 82.4224 | FTS | 19122 | 232 | 2 | 1 | 15 | 4 | 0 | 0 | 83
25-0103348 | San Luis Obispo | CHOLAME 2102 | CHOLAME 2102X16 | Environmental/External | 2025-09-24 04:19 | -07:00 | 09/23 - 09/29 | 2025-09-24 14:01 | -07:00 | 280.8706 | FTS | 80329 | 286 | 4 | 2 | 14 | 2 | 0 | 0 | 582
25-0103493 | Monterey | LOS OSITOS 2103 | LOS OSITOS 21037086 | Equipment Failure/Involved | 2025-09-24 09:14 | -07:00 | 09/23 - 09/29 | 2025-09-24 14:31 | -07:00 | 46.0373 | HLT | 6169 | 134 | 2 | 1 | 3 | 0 | 0 | 0 | 317
25-0103684 | San Luis Obispo | CARRIZO PLAINS 1101 | CARRIZO PLAINS 1101384116 | Equipment Failure/Involved | 2025-09-24 12:59 | -07:00 | 09/23 - 09/29 | 2025-09-24 14:57 | -07:00 | 118 | FTS | 38940 | 330 | 5 | 3 | 7 | 1 | 3 | 0 | 118
25-0103575 | Mendocino | ELK 1101 | ELK 11014628 | Vegetation | 2025-09-24 10:52 | -07:00 | 09/23 - 09/29 | 2025-09-24 14:57 | -07:00 | 97.3304 | FTS | 10901 | 112 | 1 | 0 | 2 | 0 | 0 | 0 | 245
25-0103717 | Sonoma | CLOVERDALE 1102 | CLOVERDALE 1102674 | Unknown Cause | 2025-09-24 13:29 | -07:00 | 09/23 - 09/29 | 2025-09-24 15:23 | -07:00 | 114 | FTS | 24624 | 216 | 9 | 5 | 11 | 0 | 0 | 0 | 114
25-0103829 | Merced | GUSTINE 1102 | GUSTINE 11026926 | Animal | 2025-09-24 14:45 | -07:00 | 09/23 - 09/29 | 2025-09-24 15:38 | -07:00 | 53 | FTS | 10759 | 203 | 3 | 3 | 2 | 0 | 0 | 0 | 53
25-0103887 | Mendocino | LAYTONVILLE 1102 | LAYTONVILLE 1102CB | Company Initiated | 2025-09-24 13:54 | -07:00 | 09/23 - 09/29 | 2025-09-24 16:12 | -07:00 | 138 | FTS | 1380 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 138
25-0103323 | Santa Barbara | SANTA YNEZ 1101 | SANTA YNEZ 1101Y52 | Equipment Failure/Involved | 2025-09-23 22:57 | -07:00 | 09/23 - 09/29 | 2025-09-24 17:44 | -07:00 | 1127 | FTS | 213003 | 189 | 0 | 0 | 25 | 0 | 0 | 0 | 1127
25-0103326 | Santa Barbara | CABRILLO 1103 | CABRILLO 1103420128 | Environmental/External | 2025-09-23 23:11 | -07:00 | 09/23 - 09/29 | 2025-09-24 17:47 | -07:00 | 317.6115 | FTS | 44148 | 139 | 2 | 2 | 1 | 0 | 0 | 1 | 1116
25-0103941 | El Dorado | DIAMOND SPRINGS 1106 | DIAMOND SPRINGS 110676088 | Company Initiated | 2025-09-24 16:14 | -07:00 | 09/23 - 09/29 | 2025-09-24 18:45 | -07:00 | 151 | FTS | 2567 | 17 | 2 | 1 | 0 | 0 | 0 | 0 | 151
25-0103649 | Merced | GUSTINE 1102 | GUSTINE 1102999258 | Unknown Cause | 2025-09-24 12:18 | -07:00 | 09/23 - 09/29 | 2025-09-24 19:08 | -07:00 | 115.2 | FTS | 2880 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 410
25-0103720 | San Benito | HOLLISTER 2104 | HOLLISTER 21044068 | Equipment Failure/Involved | 2025-09-24 13:32 | -07:00 | 09/23 - 09/29 | 2025-09-24 20:41 | -07:00 | 57.5674 | FTS | 69196 | 1202 | 56 | 37 | 40 | 3 | 0 | 1 | 429
25-0103976 | Monterey | GABILAN 1101 | GABILAN 1101468770 | Unknown Cause | 2025-09-24 20:51 | -07:00 | 09/23 - 09/29 | 2025-09-24 21:58 | -07:00 | 67 | FTS | 2345 | 35 | 2 | 2 | 0 | 0 | 0 | 0 | 67
25-0103978 | Glenn | HAMILTON A 1101, HAMILTON A 1102 | HAMILTON A 1101CB | Equipment Failure/Involved | 2025-09-24 20:51 | -07:00 | 09/23 - 09/29 | 2025-09-24 22:42 | -07:00 | 110.0824 | T-EPSS | 141566 | 1286 | 49 | 34 | 25 | 9 | 0 | 0 | 111
25-0103977 | Glenn | JACINTO 1101, JACINTO 1102 | JACINTO 1101CB | Equipment Failure/Involved | 2025-09-24 20:51 | -07:00 | 09/23 - 09/29 | 2025-09-24 22:54 | -07:00 | 123 | T-EPSS | 117834 | 958 | 15 | 12 | 11 | 1 | 0 | 0 | 123
25-0103980 | Colusa | RICE 1101, RICE 1102, RICE 1103, RICE 1104 | RICE 1103CB | Company Initiated | 2025-09-24 20:51 | -07:00 | 09/23 - 09/29 | 2025-09-24 22:56 | -07:00 | 118.5778 | T-EPSS | 154744 | 1305 | 21 | 14 | 19 | 6 | 0 | 0 | 125
25-0103995 | Contra Costa | VALLEY VIEW 1103 | VALLEY VIEW 1103P158 | Environmental/External | 2025-09-24 22:34 | -07:00 | 09/23 - 09/29 | 2025-09-24 23:35 | -07:00 | 37.5013 | HLT | 28726 | 766 | 55 | 39 | 7 | 2 | 0 | 0 | 61
25-0103991 | Alameda | CAYETANO 2109 | CAYETANO 2109884904 | Unknown Cause | 2025-09-24 21:51 | -07:00 | 09/23 - 09/29 | 2025-09-24 23:57 | -07:00 | 126 | FTS | 22806 | 181 | 10 | 6 | 10 | 0 | 0 | 3 | 126
25-0104030 | Contra Costa | BALFOUR 1101 | BALFOUR 1101CB | Environmental/External | 2025-09-25 00:04 | -07:00 | 09/23 - 09/29 | 2025-09-25 00:35 | -07:00 | 31 | T-EPSS | 15128 | 488 | 12 | 9 | 18 | 2 | 0 | 0 | 31
25-0103366 | Tuolumne | CURTIS 1704 | CURTIS 17048140 | Equipment Failure/Involved | 2025-09-24 06:20 | -07:00 | 09/23 - 09/29 | 2025-09-25 02:39 | -07:00 | 148.6117 | FTS | 194830 | 1311 | 95 | 74 | 20 | 2 | 0 | 2 | 1219
25-0104046 | Calaveras | Valley Springs 1101 | Valley Springs 1101207256 | Environmental/External | 2025-09-25 01:47 | -07:00 | 09/23 - 09/29 | 2025-09-25 03:16 | -07:00 | 89 | FTS | 144447 | 1623 | 112 | 82 | 38 | 5 | 1 | 0 | 89
25-0104068 | Tuolumne | CURTIS 1704 | CURTIS 17048140 | Environmental/External | 2025-09-25 01:54 | -07:00 | 09/23 - 09/29 | 2025-09-25 05:20 | -07:00 | 206 | FTS | 5768 | 28 | 1 | 1 | 0 | 0 | 0 | 0 | 206
25-0104053 | Tuolumne | MIWUK 1702 | MIWUK 1702823548 | Environmental/External | 2025-09-25 02:08 | -07:00 | 09/23 - 09/29 | 2025-09-25 05:22 | -07:00 | 161.3389 | FTS | 135202 | 838 | 64 | 52 | 11 | 0 | 0 | 0 | 194
25-0104061 | Santa Clara | LLAGAS 2101 | LLAGAS 2101XR244 | Unknown Cause | 2025-09-25 03:59 | -07:00 | 09/23 - 09/29 | 2025-09-25 06:02 | -07:00 | 123 | FTS | 124353 | 1011 | 34 | 20 | 16 | 2 | 0 | 8 | 123
25-0104066 | Santa Clara | MORGAN HILL 2105 | MORGAN HILL 2105XR176 | Environmental/External | 2025-09-25 04:47 | -07:00 | 09/23 - 09/29 | 2025-09-25 06:18 | -07:00 | 70.0798 | FTS | 77298 | 1103 | 52 | 44 | 16 | 3 | 0 | 10 | 91
25-0104062 | Santa Cruz | GREEN VALLEY 2101 | GREEN VALLEY 2101804170 | Vegetation | 2025-09-25 04:02 | -07:00 | 09/23 - 09/29 | 2025-09-25 06:25 | -07:00 | 143 | FTS | 17875 | 125 | 0 | 0 | 10 | 5 | 0 | 1 | 143
25-0104067 | San Benito | TRES PINOS 1111 | TRES PINOS 1111203126 | Environmental/External | 2025-09-25 04:59 | -07:00 | 09/23 - 09/29 | 2025-09-25 06:46 | -07:00 | 107 | FTS | 5029 | 47 | 1 | 0 | 0 | 0 | 0 | 0 | 107
25-0104093 | Sonoma | RINCON 1101 | RINCON 1101576 | Unknown Cause | 2025-09-25 06:56 | -07:00 | 09/23 - 09/29 | 2025-09-25 07:43 | -07:00 | 47 | FTS | 940 | 20 | 1 | 1 | 0 | 0 | 0 | 1 | 47
25-0104096 | Santa Barbara | ZACA 1102 | ZACA 1102CB | Animal | 2025-09-25 07:05 | -07:00 | 09/23 - 09/29 | 2025-09-25 07:47 | -07:00 | 42 | FTS | 60984 | 1452 | 38 | 23 | 24 | 16 | 0 | 7 | 42
25-0104090 | Sonoma | RINCON 1101 | RINCON 1101205854 | Unknown Cause | 2025-09-25 06:50 | -07:00 | 09/23 - 09/29 | 2025-09-25 08:04 | -07:00 | 74 | FTS | 148 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 74
25-0103993 | Contra Costa | TIDEWATER 2106 | FAIRVIEW 2207M500R | Unknown Cause | 2025-09-24 21:53 | -07:00 | 09/23 - 09/29 | 2025-09-25 09:19 | -07:00 | 357.2883 | HLT | 2571404 | 7197 | 293 | 202 | 94 | 9 | 0 | 0 | 686
25-0104248 | Plumas | CHESTER 1102 | CHESTER 1102385846 | Company Initiated | 2025-09-25 10:06 | -07:00 | 09/23 - 09/29 | 2025-09-25 10:59 | -07:00 | 45.8947 | FTS | 3488 | 76 | 3 | 3 | 8 | 0 | 0 | 0 | 53
25-0104034 | Calaveras | CORRAL 1103 | CORRAL 1103CB | Environmental/External | 2025-09-25 00:37 | -07:00 | 09/23 - 09/29 | 2025-09-25 11:20 | -07:00 | 187.4278 | FTS | 399596 | 2132 | 209 | 140 | 29 | 0 | 0 | 0 | 643
25-0104267 | Santa Clara | MORGAN HILL 2108 | MORGAN HILL 2108XR328 | Animal | 2025-09-25 10:26 | -07:00 | 09/23 - 09/29 | 2025-09-25 11:40 | -07:00 | 74 | FTS | 22274 | 301 | 9 | 7 | 6 | 2 | 0 | 0 | 74
25-0104214 | Lake | KONOCTI 1102 | KONOCTI 1102948 | Unknown Cause | 2025-09-25 09:37 | -07:00 | 09/23 - 09/29 | 2025-09-25 11:47 | -07:00 | 130 | FTS | 42900 | 330 | 22 | 15 | 5 | 0 | 0 | 0 | 130
25-0104209 | Lake | MIDDLETOWN 1101 | MIDDLETOWN 1101644756 | Unknown Cause | 2025-09-25 09:31 | -07:00 | 09/23 - 09/29 | 2025-09-25 12:22 | -07:00 | 170.3478 | FTS | 7836 | 46 | 0 | 0 | 1 | 0 | 0 | 2 | 171
25-0104071 | Santa Clara | MORGAN HILL 2108 | MORGAN HILL 2108XR328 | Equipment Failure/Involved | 2025-09-25 05:24 | -07:00 | 09/23 - 09/29 | 2025-09-25 12:24 | -07:00 | 236.9429 | FTS | 116102 | 490 | 33 | 25 | 12 | 5 | 0 | 0 | 420
25-0104051 | Calaveras | STANISLAUS 1702 | STANISLAUS 170237276 | Equipment Failure/Involved | 2025-09-25 02:35 | -07:00 | 09/23 - 09/29 | 2025-09-25 13:00 | -07:00 | 128.1962 | FTS | 101916 | 795 | 22 | 16 | 8 | 0 | 0 | 0 | 625
25-0104040 | Calaveras | CORRAL 1101 | CORRAL 1101220994 | Environmental/External | 2025-09-25 00:45 | -07:00 | 09/23 - 09/29 | 2025-09-25 13:48 | -07:00 | 339.6058 | FTS | 561708 | 1654 | 115 | 83 | 22 | 0 | 0 | 9 | 783
25-0104069 | San Benito | HOLLISTER 2106 | HOLLISTER 21064004 | Environmental/External | 2025-09-25 05:06 | -07:00 | 09/23 - 09/29 | 2025-09-25 14:51 | -07:00 | 103.8654 | FTS | 33964 | 327 | 16 | 9 | 3 | 1 | 0 | 1 | 585
25-0104044 | Stanislaus | VALLEY HOME 1703 | VALLEY HOME 17031532 | Environmental/External | 2025-09-25 00:04 | -07:00 | 09/23 - 09/29 | 2025-09-25 15:08 | -07:00 | 904 | FTS | 188032 | 208 | 2 | 1 | 3 | 0 | 0 | 0 | 904
25-0104077 | Santa Clara | HOLLISTER 2104 | HOLLISTER 2102113634 | Environmental/External | 2025-09-25 06:00 | -07:00 | 09/23 - 09/29 | 2025-09-25 15:36 | -07:00 | 62.2111 | FTS | 5599 | 90 | 2 | 0 | 3 | 0 | 0 | 0 | 576
25-0104287 | Tuolumne | PEORIA 1701 | PEORIA 170190090 | Unknown Cause | 2025-09-25 10:42 | -07:00 | 09/23 - 09/29 | 2025-09-25 16:00 | -07:00 | 318 | FTS | 800088 | 2516 | 221 | 167 | 31 | 14 | 0 | 3 | 318
25-0104033 | Calaveras | FROGTOWN 1702 | FROGTOWN 170232556 | Environmental/External | 2025-09-25 00:23 | -07:00 | 09/23 - 09/29 | 2025-09-25 16:53 | -07:00 | 199.2214 | FTS | 706240 | 3545 | 206 | 150 | 94 | 14 | 1 | 6 | 990
25-0104065 | Tuolumne | CURTIS 1704 | CURTIS 170420771 | Environmental/External | 2025-09-25 01:54 | -07:00 | 09/23 - 09/29 | 2025-09-25 17:14 | -07:00 | 432.3429 | FTS | 15132 | 35 | 1 | 1 | 0 | 0 | 0 | 1 | 920
25-0104501 | San Mateo | BELMONT 1103 | BELMONT 11038958 | Equipment Failure/Involved | 2025-09-25 14:54 | -07:00 | 09/23 - 09/29 | 2025-09-25 19:57 | -07:00 | 110.7141 | FTS | 103407 | 934 | 38 | 31 | 9 | 0 | 0 | 0 | 303
25-0104602 | Butte | WYANDOTTE 1109 | WYANDOTTE 1109759354 | Animal | 2025-09-25 18:14 | -07:00 | 09/23 - 09/29 | 2025-09-25 20:20 | -07:00 | 41.1823 | FTS | 58973 | 1432 | 129 | 100 | 16 | 5 | 0 | 5 | 126
25-0104271 | Monterey | LOS OSITOS 2103 | LOS OSITOS 2103174580 | Environmental/External | 2025-09-25 10:25 | -07:00 | 09/23 - 09/29 | 2025-09-25 20:34 | -07:00 | 30.7537 | FTS | 4121 | 134 | 2 | 1 | 3 | 0 | 0 | 0 | 609
25-0103983 | Contra Costa | LONE TREE 2105 | LONE TREE 2105CB | Equipment Failure/Involved | 2025-09-24 21:04 | -07:00 | 09/23 - 09/29 | 2025-09-25 20:45 | -07:00 | 57.3324 | FTS | 151243 | 2638 | 158 | 114 | 43 | 5 | 1 | 0 | 1421
25-0104142 | Santa Cruz | LOS GATOS 1106 | LOS GATOS 1106648186 | Vegetation | 2025-09-25 08:16 | -07:00 | 09/23 - 09/29 | 2025-09-25 23:15 | -07:00 | 127.45 | FTS | 202773 | 1591 | 129 | 102 | 28 | 3 | 0 | 20 | 899
25-0104657 | Santa Clara | MORGAN HILL 2111 | MORGAN HILL 2111123422 | Vegetation | 2025-09-25 22:24 | -07:00 | 09/23 - 09/29 | 2025-09-26 03:51 | -07:00 | 59.425 | FTS | 23770 | 400 | 20 | 17 | 10 | 0 | 0 | 2 | 327
25-0104634 | Sonoma | MONTE RIO 1113 | MONTE RIO 1113346 | Equipment Failure/Involved | 2025-09-25 20:11 | -07:00 | 09/23 - 09/29 | 2025-09-26 03:53 | -07:00 | 194.1313 | FTS | 100560 | 518 | 39 | 27 | 16 | 5 | 0 | 1 | 462
25-0104694 | Contra Costa | MEADOW LANE 2106 | MEADOW LANE 2106970936 | Animal | 2025-09-26 06:44 | -07:00 | 09/23 - 09/29 | 2025-09-26 09:17 | -07:00 | 153 | FTS | 612 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 153
25-0104731 | Santa Clara | HICKS 2101 | HICKS 1112CB | Animal | 2025-09-26 08:22 | -07:00 | 09/23 - 09/29 | 2025-09-26 09:31 | -07:00 | 69 | FTS | 21459 | 311 | 12 | 8 | 4 | 0 | 0 | 1 | 69
25-0104723 | Kern | CARNERAS 1103 | CARNERAS 1103430670 | 3rd Party | 2025-09-26 08:04 | -07:00 | 09/23 - 09/29 | 2025-09-26 09:50 | -07:00 | 106 | FTS | 1484 | 14 | 0 | 0 | 1 | 0 | 0 | 0 | 106
25-0104787 | Solano | VACAVILLE 1104 | VACAVILLE 1104CB | Animal | 2025-09-26 09:54 | -07:00 | 09/23 - 09/29 | 2025-09-26 10:29 | -07:00 | 35 | FTS | 44660 | 1276 | 76 | 55 | 14 | 0 | 0 | 2 | 35
25-0104758 | Monterey | KING CITY 1103 | KING CITY 11037038 | Equipment Failure/Involved | 2025-09-26 09:10 | -07:00 | 09/23 - 09/29 | 2025-09-26 11:38 | -07:00 | 72.8381 | FTS | 58052 | 797 | 46 | 36 | 15 | 0 | 0 | 0 | 148
25-0104520 | Santa Clara | SARATOGA 1107 | SARATOGA 11075696 | Vegetation | 2025-09-25 15:35 | -07:00 | 09/23 - 09/29 | 2025-09-26 11:43 | -07:00 | 237.9251 | FTS | 162027 | 681 | 19 | 14 | 8 | 3 | 0 | 1 | 1208
25-0104717 | Shasta | VOLTA 1102 | VOLTA 11021650 | Animal | 2025-09-26 08:02 | -07:00 | 09/23 - 09/29 | 2025-09-26 13:04 | -07:00 | 145.0166 | FTS | 34949 | 241 | 15 | 13 | 8 | 0 | 0 | 1 | 302
25-0104842 | Kern | POSO MOUNTAIN 2101 | POSO MOUNTAIN 2101535138 | 3rd Party | 2025-09-26 11:13 | -07:00 | 09/23 - 09/29 | 2025-09-26 14:11 | -07:00 | 31.7188 | FTS | 1015 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 178
25-0104869 | Sutter | PEASE 1103 | PEASE 11031226 | Unknown Cause | 2025-09-26 11:45 | -07:00 | 09/23 - 09/29 | 2025-09-26 14:17 | -07:00 | 42.9079 | FTS | 29821 | 695 | 54 | 33 | 10 | 3 | 0 | 0 | 152
25-0105032 | Contra Costa | SOBRANTE 1102 | SOBRANTE 1102690098 | Equipment Failure/Involved | 2025-09-26 15:14 | -07:00 | 09/23 - 09/29 | 2025-09-26 17:21 | -07:00 | 127 | FTS | 74041 | 583 | 22 | 18 | 13 | 2 | 0 | 0 | 127
25-0105123 | Tuolumne | CURTIS 1703 | CURTIS 1703476872 | Unknown Cause | 2025-09-27 06:34 | -07:00 | 09/23 - 09/29 | 2025-09-27 09:23 | -07:00 | 169 | FTS | 22815 | 135 | 9 | 8 | 0 | 0 | 0 | 0 | 169
25-0105085 | Sonoma | CLOVERDALE 1102 | CLOVERDALE 1102674 | Equipment Failure/Involved | 2025-09-26 17:33 | -07:00 | 09/23 - 09/29 | 2025-09-27 13:03 | -07:00 | 103.9583 | FTS | 22455 | 216 | 9 | 5 | 11 | 0 | 0 | 0 | 1170
25-0105129 | Mendocino | CALPELLA 1101 | CALPELLA 1101908688 | Animal | 2025-09-27 07:32 | -07:00 | 09/23 - 09/29 | 2025-09-27 16:23 | -07:00 | 109.5697 | FTS | 72316 | 660 | 36 | 26 | 18 | 2 | 0 | 3 | 531
25-0105238 | Lake | HIGHLANDS 1102 | HIGHLANDS 1102CB | Unknown Cause | 2025-09-27 16:04 | -07:00 | 09/23 - 09/29 | 2025-09-27 17:59 | -07:00 | 72.0352 | FTS | 263649 | 3660 | 298 | 195 | 44 | 8 | 0 | 6 | 115
25-0102798 | Contra Costa | CLAYTON 2212 | CLAYTON 2212614950 | Equipment Failure/Involved | 2025-09-23 06:48 | -07:00 | 09/23 - 09/29 | 2025-09-27 19:16 | -07:00 | 729.5417 | FTS | 35018 | 48 | 4 | 3 | 0 | 0 | 0 | 0 | 6508
25-0105260 | Placer | FORESTHILL 1101 | FORESTHILL 11011802 | Equipment Failure/Involved | 2025-09-28 02:45 | -07:00 | 09/23 - 09/29 | 2025-09-28 04:34 | -07:00 | 73.5776 | FTS | 122801 | 1669 | 154 | 107 | 12 | 2 | 0 | 0 | 109
25-0105289 | Nevada | NARROWS 2102 | NARROWS 210242584 | Unknown Cause | 2025-09-28 09:51 | -07:00 | 09/23 - 09/29 | 2025-09-28 10:48 | -07:00 | 57 | FTS | 28956 | 508 | 42 | 33 | 4 | 0 | 0 | 1 | 57
25-0105259 | San Mateo | WOODSIDE 1104 | WOODSIDE 1104520832 | Unknown Cause | 2025-09-28 01:37 | -07:00 | 09/23 - 09/29 | 2025-09-28 11:01 | -07:00 | 564 | FTS | 138744 | 246 | 7 | 6 | 9 | 0 | 0 | 0 | 564
25-0105279 | Napa | PUEBLO 2104 | PUEBLO 210438686 | Animal | 2025-09-28 08:51 | -07:00 | 09/23 - 09/29 | 2025-09-28 11:19 | -07:00 | 148 | FTS | 30784 | 208 | 7 | 5 | 9 | 0 | 0 | 0 | 148
25-0105263 | Alameda | MILPITAS 1109 | MILPITAS 1109694832 | Unknown Cause | 2025-09-28 05:06 | -07:00 | 09/23 - 09/29 | 2025-09-28 11:59 | -07:00 | 413 | FTS | 413 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 413
25-0105264 | Santa Clara | MILPITAS 1109 | MILPITAS 1109XR524 | Unknown Cause | 2025-09-28 05:06 | -07:00 | 09/23 - 09/29 | 2025-09-28 11:59 | -07:00 | 413 | FTS | 18998 | 46 | 3 | 1 | 14 | 0 | 0 | 0 | 413
25-0105300 | Napa | PUEBLO 2104 | PUEBLO 2104600010 | Company Initiated | 2025-09-28 11:20 | -07:00 | 09/23 - 09/29 | 2025-09-28 12:26 | -07:00 | 66 | FTS | 924 | 14 | 0 | 0 | 4 | 0 | 0 | 0 | 66
25-0105299 | Yolo | MADISON 2101 | MADISON 21017702 | Unknown Cause | 2025-09-28 12:14 | -07:00 | 09/23 - 09/29 | 2025-09-28 14:19 | -07:00 | 116.5457 | FTS | 109553 | 940 | 17 | 9 | 18 | 14 | 0 | 4 | 125
25-0105290 | Shasta | OREGON TRAIL 1104 | OREGON TRAIL 11041574 | Equipment Failure/Involved | 2025-09-28 11:05 | -07:00 | 09/23 - 09/29 | 2025-09-28 14:56 | -07:00 | 173.6286 | FTS | 66847 | 385 | 40 | 28 | 4 | 0 | 0 | 0 | 231
25-0105320 | El Dorado | SHINGLE SPRINGS 1104 | SHINGLE SPRINGS 1104556218 | Animal | 2025-09-28 16:09 | -07:00 | 09/23 - 09/29 | 2025-09-28 17:16 | -07:00 | 67 | FTS | 43684 | 652 | 52 | 41 | 4 | 0 | 0 | 26 | 67
25-0105323 | El Dorado | DIAMOND SPRINGS 1105 | DIAMOND SPRINGS 110519910 | Unknown Cause | 2025-09-28 14:13 | -07:00 | 09/23 - 09/29 | 2025-09-28 18:05 | -07:00 | 232 | FTS | 98600 | 425 | 30 | 21 | 4 | 0 | 0 | 3 | 232
25-0105345 | Placer | HALSEY 1102 | HALSEY 1102CB | Unknown Cause | 2025-09-28 17:21 | -07:00 | 09/23 - 09/29 | 2025-09-28 19:06 | -07:00 | 105 | FTS | 6720 | 64 | 5 | 2 | 0 | 0 | 0 | 4 | 105
25-0105379 | Shasta | VOLTA 1102 | VOLTA 110254932 | Equipment Failure/Involved | 2025-09-29 03:18 | -07:00 | 09/23 - 09/29 | 2025-09-29 05:22 | -07:00 | 86.2723 | FTS | 18376 | 213 | 23 | 18 | 3 | 0 | 0 | 0 | 124
25-0105380 | Humboldt | HOOPA 1101 | HOOPA 11013304 | Vegetation | 2025-09-29 03:40 | -07:00 | 09/23 - 09/29 | 2025-09-29 05:47 | -07:00 | 126.7194 | FTS | 84902 | 670 | 18 | 14 | 24 | 5 | 0 | 0 | 127
25-0105386 | Contra Costa | TASSAJARA 2104 | TASSAJARA 2109CB | Company Initiated | 2025-09-29 06:13 | -07:00 | 09/23 - 09/29 | 2025-09-29 06:44 | -07:00 | 31 | FTS | 4340 | 140 | 8 | 1 | 3 | 0 | 0 | 6 | 31
25-0105378 | Calaveras | STANISLAUS 1701 | STANISLAUS 170179826 | Unknown Cause | 2025-09-29 01:18 | -07:00 | 09/23 - 09/29 | 2025-09-29 07:55 | -07:00 | 397 | FTS | 55977 | 141 | 7 | 6 | 3 | 0 | 0 | 0 | 397
25-0105410 | Shasta | VOLTA 1102 | VOLTA 110254932 | Equipment Failure/Involved | 2025-09-29 07:45 | -07:00 | 09/23 - 09/29 | 2025-09-29 10:25 | -07:00 | 97.4272 | FTS | 20752 | 213 | 23 | 18 | 3 | 0 | 0 | 0 | 160
25-0105482 | Butte | WYANDOTTE 1102 | WYANDOTTE 110213916 | Unknown Cause | 2025-09-29 09:58 | -07:00 | 09/23 - 09/29 | 2025-09-29 11:24 | -07:00 | 86 | FTS | 182492 | 2122 | 148 | 110 | 29 | 3 | 0 | 1 | 86
25-0105506 | El Dorado | SHINGLE SPRINGS 2105 | SHINGLE SPRINGS 210511172 | Unknown Cause | 2025-09-29 10:17 | -07:00 | 09/23 - 09/29 | 2025-09-29 12:33 | -07:00 | 128.6097 | FTS | 106103 | 825 | 77 | 50 | 7 | 0 | 0 | 0 | 136
25-0105594 | Santa Barbara | CABRILLO 1103 | CABRILLO 11031437 | Equipment Failure/Involved | 2025-09-29 12:18 | -07:00 | 09/23 - 09/29 | 2025-09-29 14:52 | -07:00 | 154 | FTS | 6314 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 154
25-0105549 | Fresno | DUNLAP 1103 | DUNLAP 1103CB | Unknown Cause | 2025-09-29 11:19 | -07:00 | 09/23 - 09/29 | 2025-09-29 17:25 | -07:00 | 174.3879 | FTS | 172644 | 990 | 34 | 30 | 12 | 3 | 0 | 2 | 366
25-0089193 | Marin | SAN RAFAEL 1107 | SAN RAFAEL 11071166 | Equipment Failure/Involved | 2025-08-21 00:58 | -07:00 | 09/23 - 09/29 | 2025-09-29 17:35 | -07:00 | 67.1207 | FTS | 225794 | 3364 | 93 | 62 | 46 | 10 | 0 | 3 | 57157
25-0105775 | Shasta | VOLTA 1102 | VOLTA 110254932 | Equipment Failure/Involved | 2025-09-29 16:34 | -07:00 | 09/23 - 09/29 | 2025-09-29 20:24 | -07:00 | 85.939 | FTS | 18305 | 213 | 23 | 18 | 3 | 0 | 0 | 0 | 230
25-0105826 | Tuolumne | CURTIS 1704 | CURTIS 17041691 | Environmental/External | 2025-09-29 17:48 | -07:00 | 09/23 - 09/29 | 2025-09-29 20:55 | -07:00 | 187 | FTS | 27115 | 145 | 11 | 10 | 4 | 0 | 0 | 0 | 187
25-0105789 | Fresno | AUBERRY 1101 | AUBERRY 1101R2579 | Vegetation | 2025-09-29 17:01 | -07:00 | 09/30 - 10/06 | 2025-09-30 00:54 | -07:00 | 116.588 | FTS | 171501 | 1471 | 116 | 79 | 24 | 6 | 0 | 15 | 473
25-0105846 | Tuolumne | CURTIS 1704 | CURTIS 17041691BP | Environmental/External | 2025-09-29 21:08 | -07:00 | 09/30 - 10/06 | 2025-09-30 02:56 | -07:00 | 123 | FTS | 5658 | 46 | 6 | 6 | 0 | 0 | 0 | 0 | 348
25-0105879 | Contra Costa | TASSAJARA 2112 | TASSAJARA 2112925966 | Unknown Cause | 2025-09-30 06:38 | -07:00 | 09/30 - 10/06 | 2025-09-30 07:47 | -07:00 | 69 | FTS | 32568 | 472 | 30 | 23 | 7 | 4 | 0 | 0 | 69
25-0105777 | Lake | UPPER LAKE 1101 | UPPER LAKE 110175370 | Equipment Failure/Involved | 2025-09-29 16:34 | -07:00 | 09/30 - 10/06 | 2025-09-30 11:40 | -07:00 | 161.4366 | FTS | 22924 | 142 | 7 | 4 | 2 | 0 | 0 | 1 | 1146
25-0106010 | Nevada | HIGGINS 1103 | HIGGINS 110350072 | Unknown Cause | 2025-09-30 09:37 | -07:00 | 09/30 - 10/06 | 2025-09-30 11:44 | -07:00 | 89.5309 | FTS | 58016 | 648 | 39 | 27 | 3 | 0 | 0 | 21 | 127
25-0106195 | Santa Clara | SARATOGA 1107 | SARATOGA 1107899344 | Unknown Cause | 2025-09-30 12:46 | -07:00 | 09/30 - 10/06 | 2025-09-30 13:30 | -07:00 | 40.678 | FTS | 4800 | 118 | 3 | 1 | 1 | 2 | 0 | 5 | 44
25-0106218 | El Dorado | SHINGLE SPRINGS 1104 | SHINGLE SPRINGS 1104556218 | Animal | 2025-09-30 13:25 | -07:00 | 09/30 - 10/06 | 2025-09-30 14:52 | -07:00 | 58.3558 | FTS | 38048 | 652 | 52 | 41 | 4 | 0 | 0 | 26 | 87
25-0106231 | Shasta | PIT NO 1 1101 | PIT NO 1 11011552 | Unknown Cause | 2025-09-30 13:43 | -07:00 | 09/30 - 10/06 | 2025-09-30 15:18 | -07:00 | 80.5685 | FTS | 19417 | 241 | 18 | 15 | 3 | 0 | 0 | 0 | 95
25-0106219 | Santa Clara | MILPITAS 1109 | MILPITAS 1109903328 | Unknown Cause | 2025-09-30 13:22 | -07:00 | 09/30 - 10/06 | 2025-09-30 15:30 | -07:00 | 128 | FTS | 27264 | 213 | 10 | 7 | 1 | 0 | 0 | 0 | 128
25-0106186 | Yuba | WHEATLAND 1105 | WHEATLAND 1105248490 | Equipment Failure/Involved | 2025-09-30 12:54 | -07:00 | 09/30 - 10/06 | 2025-09-30 17:40 | -07:00 | 147.1268 | FTS | 31338 | 213 | 13 | 8 | 3 | 0 | 0 | 5 | 286
25-0097107 | Mariposa | MARIPOSA 2101 | MARIPOSA 2101310816 | Company Initiated | 2025-09-30 08:14 | -07:00 | 09/30 - 10/06 | 2025-09-30 17:45 | -07:00 | 571 | FTS | 3426 | 6 | 13 | 7 | 8 | 0 | 0 | 0 | 571
25-0106394 | Mendocino | COVELO 1101 | COVELO 110137328 | Animal | 2025-09-30 16:53 | -07:00 | 09/30 - 10/06 | 2025-09-30 19:38 | -07:00 | 23.8327 | FTS | 12107 | 508 | 17 | 15 | 2 | 2 | 0 | 3 | 165
25-0106402 | Glenn | LOGAN CREEK 2102 | LOGAN CREEK 210262032 | Unknown Cause | 2025-09-30 19:27 | -07:00 | 09/30 - 10/06 | 2025-09-30 19:44 | -07:00 | 17 | FTS | 1377 | 81 | 1 | 1 | 6 | 0 | 0 | 0 | 17
25-0106451 | Shasta | MC ARTHUR 1101 | MC ARTHUR 1101648698 | Unknown Cause | 2025-10-01 03:18 | -07:00 | 09/30 - 10/06 | 2025-10-01 03:37 | -07:00 | 19 | FTS | 4617 | 243 | 16 | 14 | 3 | 0 | 0 | 0 | 19
25-0106448 | Shasta | GIRVAN 1101 | GIRVAN 11019732 | Equipment Failure/Involved | 2025-10-01 02:36 | -07:00 | 09/30 - 10/06 | 2025-10-01 06:23 | -07:00 | 97.5386 | FTS | 47989 | 492 | 43 | 32 | 12 | 4 | 0 | 0 | 227
25-0106459 | Sonoma | GEYSERVILLE 1101 | GEYSERVILLE 1101166 | 3rd Party | 2025-10-01 05:45 | -07:00 | 09/30 - 10/06 | 2025-10-01 06:55 | -07:00 | 63.8968 | FTS | 41469 | 649 | 13 | 12 | 8 | 0 | 0 | 6 | 70
25-0106473 | Nevada | BRUNSWICK 1103 | BRUNSWICK 11032784 | 3rd Party | 2025-10-01 06:46 | -07:00 | 09/30 - 10/06 | 2025-10-01 07:39 | -07:00 | 41.0841 | FTS | 52752 | 1284 | 76 | 47 | 12 | 2 | 0 | 6 | 53
25-0106367 | Calaveras | FROGTOWN 1701 | FROGTOWN 170113412 | Unknown Cause | 2025-09-30 16:22 | -07:00 | 09/30 - 10/06 | 2025-10-01 08:48 | -07:00 | 174.6375 | FTS | 323778 | 1854 | 120 | 85 | 26 | 4 | 0 | 3 | 986
25-0106644 | Nevada | HIGGINS 1103 | HIGGINS 1104498932 | Unknown Cause | 2025-10-01 10:20 | -07:00 | 09/30 - 10/06 | 2025-10-01 10:29 | -07:00 | 9 | FTS | 1404 | 156 | 8 | 5 | 3 | 1 | 0 | 0 | 9
25-0106575 | Shasta | MC ARTHUR 1101 | MC ARTHUR 1101648698 | Unknown Cause | 2025-10-01 09:14 | -07:00 | 09/30 - 10/06 | 2025-10-01 10:59 | -07:00 | 49.2305 | FTS | 11963 | 243 | 16 | 14 | 3 | 0 | 0 | 0 | 105
25-0106736 | Placer | SHADY GLEN 1101 | SHADY GLEN 1101941844 | Unknown Cause | 2025-10-01 10:41 | -07:00 | 09/30 - 10/06 | 2025-10-01 12:12 | -07:00 | 91 | FTS | 1274 | 14 | 2 | 2 | 0 | 0 | 0 | 0 | 91
25-0106984 | Butte | ANITA 1106 | ANITA 1106552724 | Unknown Cause | 2025-10-01 16:40 | -07:00 | 09/30 - 10/06 | 2025-10-01 16:58 | -07:00 | 18 | FTS | 1224 | 68 | 5 | 0 | 0 | 0 | 0 | 0 | 18
25-0107015 | El Dorado | DIAMOND SPRINGS 1106 | DIAMOND SPRINGS 11062100 | Company Initiated | 2025-10-01 19:06 | -07:00 | 09/30 - 10/06 | 2025-10-01 19:35 | -07:00 | 29 | FTS | 319 | 11 | 1 | 1 | 0 | 0 | 0 | 0 | 29
25-0107020 | Santa Clara | HICKS 2101 | HICKS 2101510890 | Unknown Cause | 2025-10-01 19:58 | -07:00 | 09/30 - 10/06 | 2025-10-01 20:20 | -07:00 | 22 | FTS | 3850 | 175 | 8 | 7 | 9 | 1 | 0 | 0 | 22
25-0107036 | Santa Clara | HICKS 2103 | HICKS 2103XR248 | Vegetation | 2025-10-01 23:56 | -07:00 | 09/30 - 10/06 | 2025-10-02 00:53 | -07:00 | 57 | FTS | 28728 | 504 | 22 | 15 | 5 | 0 | 0 | 0 | 57
25-0107061 | Contra Costa | TASSAJARA 2112 | TASSAJARA 2112925966 | Unknown Cause | 2025-10-02 06:27 | -07:00 | 09/30 - 10/06 | 2025-10-02 07:43 | -07:00 | 76 | FTS | 35872 | 472 | 31 | 24 | 7 | 4 | 0 | 0 | 76
25-0107101 | Contra Costa | BRENTWOOD 2105 | BRENTWOOD 210596324 | 3rd Party | 2025-10-02 07:22 | -07:00 | 09/30 - 10/06 | 2025-10-02 08:31 | -07:00 | 66 | FTS | 132 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 69
25-0107104 | Amador | CLAY 1103 | CLAY 110334338 | Animal | 2025-10-02 07:51 | -07:00 | 09/30 - 10/06 | 2025-10-02 08:42 | -07:00 | 51 | FTS | 3825 | 75 | 3 | 2 | 4 | 0 | 0 | 0 | 51
25-0107327 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 211318370 | Company Initiated | 2025-10-02 12:12 | -07:00 | 09/30 - 10/06 | 2025-10-02 12:24 | -07:00 | 12 | FTS | 2604 | 217 | 10 | 9 | 2 | 0 | 0 | 3 | 12
25-0107361 | Glenn | GLENN 1101 | GLENN 110137496 | Unknown Cause | 2025-10-02 12:56 | -07:00 | 09/30 - 10/06 | 2025-10-02 13:05 | -07:00 | 9 | FTS | 441 | 49 | 2 | 0 | 9 | 0 | 0 | 0 | 9
25-0107323 | Plumas | BIG MEADOWS 2101 | BIG MEADOWS 2101427964 | Equipment Failure/Involved | 2025-10-02 11:53 | -07:00 | 09/30 - 10/06 | 2025-10-02 13:52 | -07:00 | 36.9334 | FTS | 27737 | 751 | 41 | 31 | 16 | 2 | 1 | 2 | 119
25-0107385 | Monterey | KING CITY 1103 | KING CITY 11037038 | Equipment Failure/Involved | 2025-10-02 13:32 | -07:00 | 09/30 - 10/06 | 2025-10-02 15:05 | -07:00 | 51.3626 | FTS | 40936 | 797 | 47 | 37 | 15 | 0 | 0 | 0 | 93
25-0107504 | Nevada | BRUNSWICK 1106 | BRUNSWICK 110651486 | Unknown Cause | 2025-10-02 15:58 | -07:00 | 09/30 - 10/06 | 2025-10-02 16:28 | -07:00 | 30 | FTS | 5160 | 172 | 9 | 7 | 1 | 0 | 0 | 3 | 30
25-0107473 | Tehama | COTTONWOOD 1103 | COTTONWOOD 110331548 | Company Initiated | 2025-10-02 15:12 | -07:00 | 09/30 - 10/06 | 2025-10-02 16:56 | -07:00 | 104 | FTS | 4264 | 41 | 2 | 2 | 3 | 1 | 0 | 0 | 104
25-0107343 | Calaveras | Valley Springs 1102 | Valley Springs 1102606522 | Equipment Failure/Involved | 2025-10-02 12:31 | -07:00 | 09/30 - 10/06 | 2025-10-02 18:15 | -07:00 | 101.3633 | FTS | 110486 | 1090 | 68 | 50 | 33 | 10 | 0 | 1 | 344
25-0107544 | Sonoma | SONOMA 1104 | SONOMA 110478372 | Unknown Cause | 2025-10-02 14:24 | -07:00 | 09/30 - 10/06 | 2025-10-02 18:29 | -07:00 | 245 | FTS | 1225 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 245
25-0107441 | Tehama | VOLTA 1101 | VOLTA 110149742 | Animal | 2025-10-02 14:55 | -07:00 | 09/30 - 10/06 | 2025-10-02 19:34 | -07:00 | 239.6074 | FTS | 225231 | 940 | 51 | 35 | 30 | 3 | 0 | 0 | 279
25-0107463 | Tehama | COTTONWOOD 1103 | COTTONWOOD 11031348 | 3rd Party | 2025-10-02 15:12 | -07:00 | 09/30 - 10/06 | 2025-10-02 22:25 | -07:00 | 157.9846 | FTS | 144082 | 912 | 72 | 56 | 7 | 0 | 0 | 1 | 433
25-0107619 | San Luis Obispo | TEMPLETON 2111 | TEMPLETON 2111461692 | Animal | 2025-10-02 23:23 | -07:00 | 09/30 - 10/06 | 2025-10-03 01:14 | -07:00 | 42.8586 | FTS | 56359 | 1315 | 73 | 42 | 13 | 4 | 0 | 7 | 111
25-0107638 | Colusa | COLUSA 1101, COLUSA 1103, COLUSA 1104, COLUSA 1105 | COLUSA 1101CB | Environmental/External | 2025-10-03 01:23 | -07:00 | 09/30 - 10/06 | 2025-10-03 01:49 | -07:00 | 26 | T-EPSS | 82862 | 3187 | 158 | 100 | 42 | 17 | 5 | 0 | 26
25-0107640 | Shasta | PANORAMA 1101 | PANORAMA 1101CB | Environmental/External | 2025-10-03 01:30 | -07:00 | 09/30 - 10/06 | 2025-10-03 02:06 | -07:00 | 35.3092 | FTS | 53670 | 1520 | 131 | 90 | 15 | 0 | 0 | 1 | 36
25-0107598 | Mariposa | MARIPOSA 2102 | MARIPOSA 210210880 | Environmental/External | 2025-10-02 20:25 | -07:00 | 09/30 - 10/06 | 2025-10-03 02:09 | -07:00 | 59.5901 | FTS | 28782 | 483 | 35 | 25 | 5 | 0 | 0 | 1 | 344
25-0107636 | Shasta | JESSUP 1101 | JESSUP 11019002 | Environmental/External | 2025-10-03 01:15 | -07:00 | 09/30 - 10/06 | 2025-10-03 02:20 | -07:00 | 65 | FTS | 105300 | 1620 | 166 | 126 | 17 | 3 | 0 | 1 | 65
25-0107625 | Shasta | DESCHUTES 1104 | DESCHUTES 1104421598 | Environmental/External | 2025-10-02 23:53 | -07:00 | 09/30 - 10/06 | 2025-10-03 03:06 | -07:00 | 191.521 | FTS | 31984 | 167 | 19 | 15 | 1 | 0 | 0 | 1 | 193
25-0107668 | Placer | LINCOLN 1104 | LINCOLN 1104818790 | Environmental/External | 2025-10-03 03:40 | -07:00 | 09/30 - 10/06 | 2025-10-03 03:56 | -07:00 | 16 | FTS | 864 | 54 | 4 | 4 | 0 | 0 | 0 | 1 | 16
25-0107623 | Shasta | DESCHUTES 1104 | DESCHUTES 1104378894 | Environmental/External | 2025-10-02 23:45 | -07:00 | 09/30 - 10/06 | 2025-10-03 04:04 | -07:00 | 91.4921 | FTS | 5764 | 63 | 8 | 6 | 0 | 0 | 0 | 0 | 259
25-0107682 | Yuba | NARROWS 2101 | NARROWS 21011202 | Environmental/External | 2025-10-03 04:15 | -07:00 | 09/30 - 10/06 | 2025-10-03 04:38 | -07:00 | 23 | FTS | 11684 | 508 | 47 | 31 | 2 | 0 | 0 | 9 | 23
25-0107663 | Colusa | ELK CREEK 1101 | ELK CREEK 11012008 | Environmental/External | 2025-10-03 02:20 | -07:00 | 09/30 - 10/06 | 2025-10-03 04:55 | -07:00 | 155 | T-EPSS | 138415 | 893 | 50 | 36 | 37 | 8 | 0 | 1 | 155
25-0107684 | Nevada | BRUNSWICK 1105 | BRUNSWICK 11051030 | Environmental/External | 2025-10-03 03:48 | -07:00 | 09/30 - 10/06 | 2025-10-03 04:59 | -07:00 | 71 | FTS | 87969 | 1239 | 93 | 57 | 26 | 0 | 0 | 11 | 71
25-0107665 | Butte | ORO FINO 1101 | ORO FINO 11012022 | Environmental/External | 2025-10-03 03:28 | -07:00 | 09/30 - 10/06 | 2025-10-03 05:06 | -07:00 | 98 | FTS | 101724 | 1038 | 126 | 98 | 10 | 1 | 0 | 0 | 98
25-0107586 | Mariposa | MERCED FALLS 1102 | MERCED FALLS 1102482838 | Equipment Failure/Involved | 2025-10-02 19:25 | -07:00 | 09/30 - 10/06 | 2025-10-03 05:42 | -07:00 | 118.7477 | FTS | 168503 | 1419 | 92 | 58 | 28 | 5 | 0 | 0 | 617
25-0107637 | Colusa | MAXWELL 1102, MAXWELL 1105, MAXWELL 1106 | MAXWELL 1102CB | Environmental/External | 2025-10-03 01:23 | -07:00 | 09/30 - 10/06 | 2025-10-03 05:44 | -07:00 | 224.7622 | T-EPSS | 266568 | 1186 | 28 | 17 | 20 | 5 | 0 | 0 | 261
25-0107666 | Butte | BIG BEND 1102 | BIG BEND 1102884340 | Unknown Cause | 2025-10-03 03:29 | -07:00 | 09/30 - 10/06 | 2025-10-03 05:44 | -07:00 | 135 | FTS | 30645 | 227 | 6 | 4 | 3 | 0 | 0 | 0 | 135
25-0107652 | Tehama | GERBER 1101, GERBER 1102 | GERBER 1101CB | Environmental/External | 2025-10-03 02:18 | -07:00 | 09/30 - 10/06 | 2025-10-03 05:48 | -07:00 | 154.0556 | T-EPSS | 227232 | 1475 | 92 | 65 | 24 | 3 | 0 | 1 | 210
25-0107689 | Nevada | HIGGINS 1103 | HIGGINS 1103173744 | Company Initiated | 2025-10-03 03:58 | -07:00 | 09/30 - 10/06 | 2025-10-03 06:08 | -07:00 | 130 | FTS | 16510 | 127 | 16 | 11 | 1 | 0 | 0 | 2 | 130
25-0107695 | Nevada | BRUNSWICK 1105 | BRUNSWICK 11052130 | Company Initiated | 2025-10-03 03:48 | -07:00 | 09/30 - 10/06 | 2025-10-03 06:17 | -07:00 | 144.0481 | FTS | 29962 | 208 | 12 | 9 | 7 | 0 | 0 | 8 | 149
25-0107687 | Placer | WHEATLAND 1104 | WHEATLAND 11041348 | Environmental/External | 2025-10-03 03:48 | -07:00 | 09/30 - 10/06 | 2025-10-03 06:22 | -07:00 | 154 | FTS | 39578 | 257 | 26 | 20 | 1 | 0 | 0 | 3 | 154
25-0107727 | Butte | KANAKA 1101 | KANAKA 110183288 | Environmental/External | 2025-10-03 04:48 | -07:00 | 09/30 - 10/06 | 2025-10-03 07:59 | -07:00 | 191 | FTS | 2483 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 191
25-0107674 | Yuba | SMARTVILLE 1101 | SMARTVILLE 1101CB | Environmental/External | 2025-10-03 03:48 | -07:00 | 09/30 - 10/06 | 2025-10-03 08:19 | -07:00 | 271 | T-EPSS | 74796 | 276 | 24 | 21 | 14 | 0 | 0 | 2 | 271
25-0107670 | Butte | BIG BEND 1101 | BIG BEND 1101641808 | Unknown Cause | 2025-10-03 03:48 | -07:00 | 09/30 - 10/06 | 2025-10-03 09:27 | -07:00 | 339 | FTS | 678 | 2 | 0 | 0 | 1 | 0 | 0 | 0 | 339
25-0107864 | Butte | WYANDOTTE 1109 | WYANDOTTE 110979932 | Unknown Cause | 2025-10-03 10:02 | -07:00 | 09/30 - 10/06 | 2025-10-03 10:21 | -07:00 | 19 | FTS | 7657 | 403 | 32 | 26 | 1 | 0 | 0 | 2 | 19
25-0107678 | Butte | CLARK ROAD 1102 | CLARK ROAD 1102212118 | Environmental/External | 2025-10-03 04:07 | -07:00 | 09/30 - 10/06 | 2025-10-03 13:07 | -07:00 | 96.6418 | FTS | 6475 | 67 | 7 | 6 | 4 | 1 | 0 | 0 | 540
25-0108072 | Mariposa | MARIPOSA 2102 | MARIPOSA 210237288 | Company Initiated | 2025-10-03 13:24 | -07:00 | 09/30 - 10/06 | 2025-10-03 13:35 | -07:00 | 11 | FTS | 7271 | 661 | 29 | 20 | 14 | 5 | 0 | 1 | 11
25-0107696 | Amador | MARTELL 1101 | PINE GROVE 11024088 | Environmental/External | 2025-10-03 06:06 | -07:00 | 09/30 - 10/06 | 2025-10-03 14:03 | -07:00 | 81.2798 | FTS | 19751 | 243 | 9 | 6 | 2 | 0 | 0 | 5 | 477
25-0107728 | Kern | TEJON 1103 | TEJON 1103286542 | Animal | 2025-10-03 07:06 | -07:00 | 09/30 - 10/06 | 2025-10-03 14:22 | -07:00 | 144.8 | FTS | 2172 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 436
25-0108099 | Butte | WYANDOTTE 1107 | WYANDOTTE 110777578 | Animal | 2025-10-03 13:34 | -07:00 | 09/30 - 10/06 | 2025-10-03 14:43 | -07:00 | 69 | FTS | 105018 | 1522 | 141 | 99 | 23 | 2 | 0 | 5 | 69
25-0108150 | Tuolumne | PEORIA 1701 | PEORIA 170190090 | Company Initiated | 2025-10-03 14:53 | -07:00 | 09/30 - 10/06 | 2025-10-03 15:21 | -07:00 | 28 | FTS | 1596 | 57 | 3 | 1 | 0 | 0 | 0 | 0 | 28
25-0108091 | Stanislaus | WESTLEY 1103 | WESTLEY 11039010 | Unknown Cause | 2025-10-03 13:13 | -07:00 | 09/30 - 10/06 | 2025-10-03 17:02 | -07:00 | 129.6054 | FTS | 38752 | 299 | 1 | 0 | 15 | 0 | 0 | 0 | 229
25-0108214 | Alameda | CASTRO VALLEY 1110 | CASTRO VALLEY 1110560528 | Company Initiated | 2025-10-03 17:02 | -07:00 | 09/30 - 10/06 | 2025-10-03 17:11 | -07:00 | 8.1388 | FTS | 15358 | 1887 | 110 | 72 | 28 | 2 | 0 | 3 | 9
25-0108089 | Fresno | AUBERRY 1101 | AUBERRY 1101R324 | Environmental/External | 2025-10-03 13:37 | -07:00 | 09/30 - 10/06 | 2025-10-03 18:02 | -07:00 | 205.0684 | FTS | 53933 | 263 | 9 | 7 | 6 | 0 | 0 | 3 | 265
25-0108122 | Fresno | AUBERRY 1101 | AUBERRY 1101460274 | Environmental/External | 2025-10-03 14:14 | -07:00 | 09/30 - 10/06 | 2025-10-03 20:14 | -07:00 | 226.6294 | FTS | 64816 | 286 | 27 | 14 | 3 | 0 | 0 | 0 | 360
25-0107673 | Nevada | HIGGINS 1103 | HIGGINS 110332120 | Vegetation | 2025-10-03 03:58 | -07:00 | 09/30 - 10/06 | 2025-10-03 20:38 | -07:00 | 214.5525 | FTS | 304450 | 1419 | 141 | 102 | 12 | 2 | 0 | 10 | 1000
25-0108233 | Alameda | JARVIS 1111 | JARVIS 1111907698 | Unknown Cause | 2025-10-03 19:31 | -07:00 | 09/30 - 10/06 | 2025-10-03 20:50 | -07:00 | 79 | FTS | 1106 | 14 | 0 | 0 | 4 | 0 | 0 | 0 | 79
25-0108248 | Contra Costa | SOBRANTE 1102 | SOBRANTE 1102690098 | Animal | 2025-10-03 21:01 | -07:00 | 09/30 - 10/06 | 2025-10-03 22:34 | -07:00 | 93 | FTS | 54219 | 583 | 22 | 18 | 13 | 2 | 0 | 0 | 93
25-0108263 | Butte | WYANDOTTE 1107 | WYANDOTTE 110737472 | Unknown Cause | 2025-10-04 03:51 | -07:00 | 09/30 - 10/06 | 2025-10-04 08:29 | -07:00 | 123.7463 | FTS | 58037 | 469 | 40 | 32 | 5 | 0 | 0 | 5 | 278
25-0108282 | Santa Clara | MORGAN HILL 2105 | MORGAN HILL 2105XR176 | Unknown Cause | 2025-10-04 07:00 | -07:00 | 09/30 - 10/06 | 2025-10-04 09:04 | -07:00 | 26.276 | FTS | 29035 | 1105 | 53 | 45 | 16 | 3 | 0 | 10 | 124
25-0108284 | Tehama | TYLER 1105 | TYLER 1105503690 | Unknown Cause | 2025-10-04 07:04 | -07:00 | 09/30 - 10/06 | 2025-10-04 09:33 | -07:00 | 149 | FTS | 26820 | 180 | 17 | 14 | 5 | 0 | 0 | 0 | 149
25-0108249 | Napa | SILVERADO 2105 | SILVERADO 2105658898 | Unknown Cause | 2025-10-03 21:15 | -07:00 | 09/30 - 10/06 | 2025-10-04 09:59 | -07:00 | 764 | FTS | 99320 | 130 | 0 | 0 | 2 | 0 | 0 | 1 | 764
25-0108220 | San Luis Obispo | PASO ROBLES 1104 | PASO ROBLES 1104R56 | Company Initiated | 2025-10-03 17:58 | -07:00 | 09/30 - 10/06 | 2025-10-04 11:02 | -07:00 | 611.186 | FTS | 262810 | 430 | 51 | 19 | 14 | 1 | 0 | 16 | 1024
25-0108356 | Sonoma | BELLEVUE 2101 | BELLEVUE 2101270638 | Unknown Cause | 2025-10-04 11:52 | -07:00 | 09/30 - 10/06 | 2025-10-04 12:33 | -07:00 | 41 | FTS | 246 | 6 | 1 | 1 | 0 | 0 | 0 | 1 | 41
25-0108372 | Fresno | KERCKHOFF 1101 | AUBERRY 110137536 | Company Initiated | 2025-10-04 14:08 | -07:00 | 09/30 - 10/06 | 2025-10-04 15:00 | -07:00 | 52 | FTS | 33540 | 645 | 76 | 58 | 52 | 3 | 0 | 4 | 52
25-0108324 | Nevada | HIGGINS 1109 | HIGGINS 1109594 | Animal | 2025-10-04 10:09 | -07:00 | 09/30 - 10/06 | 2025-10-04 15:04 | -07:00 | 53.2802 | FTS | 27759 | 521 | 40 | 32 | 4 | 0 | 0 | 11 | 295
25-0108395 | Alameda | VINEYARD 2107 | VINEYARD 2107CB | Unknown Cause | 2025-10-04 15:49 | -07:00 | 09/30 - 10/06 | 2025-10-04 16:54 | -07:00 | 65 | FTS | 2210 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 65
25-0108300 | Sonoma | NOVATO 1104 | IGNACIO 1104450582 | 3rd Party | 2025-10-04 08:24 | -07:00 | 09/30 - 10/06 | 2025-10-04 22:50 | -07:00 | 47.1709 | FTS | 35614 | 755 | 21 | 15 | 28 | 0 | 0 | 0 | 866
25-0108260 | Placer | FORESTHILL 1101 | FORESTHILL 110150486 | Equipment Failure/Involved | 2025-10-04 01:42 | -07:00 | 09/30 - 10/06 | 2025-10-05 00:39 | -07:00 | 172.2069 | FTS | 178923 | 1039 | 95 | 66 | 6 | 0 | 0 | 0 | 1377
25-0108451 | Solano | PEABODY 2113 | PEABODY 2113CB | Company Initiated | 2025-10-05 00:01 | -07:00 | 09/30 - 10/06 | 2025-10-05 01:39 | -07:00 | 98 | HLT | 12348 | 126 | 6 | 5 | 0 | 0 | 0 | 0 | 98
25-0108452 | Solano | PEABODY 2113 | PEABODY 211357908 | Company Initiated | 2025-10-05 00:01 | -07:00 | 09/30 - 10/06 | 2025-10-05 03:38 | -07:00 | 217 | HLT | 129332 | 596 | 38 | 28 | 1 | 0 | 0 | 0 | 217
25-0108399 | Santa Barbara | PURISIMA 1101 | PURISIMA 1101104948 | Equipment Failure/Involved | 2025-10-04 17:37 | -07:00 | 09/30 - 10/06 | 2025-10-05 09:49 | -07:00 | 66.385 | FTS | 12414 | 187 | 0 | 0 | 14 | 0 | 0 | 0 | 972
25-0108490 | Nevada | HIGGINS 1110 | HIGGINS 1110166282 | Unknown Cause | 2025-10-05 10:03 | -07:00 | 09/30 - 10/06 | 2025-10-05 11:47 | -07:00 | 104 | FTS | 34112 | 328 | 28 | 19 | 3 | 0 | 0 | 12 | 104
25-0108444 | Contra Costa | CLAYTON 2212 | CLAYTON 2212681608 | Unknown Cause | 2025-10-04 22:31 | -07:00 | 09/30 - 10/06 | 2025-10-05 12:18 | -07:00 | 827 | FTS | 458985 | 555 | 34 | 25 | 46 | 0 | 0 | 15 | 827
25-0108504 | Shasta | OREGON TRAIL 1104 | OREGON TRAIL 11041574 | Equipment Failure/Involved | 2025-10-05 10:48 | -07:00 | 09/30 - 10/06 | 2025-10-05 14:42 | -07:00 | 222.1351 | FTS | 85522 | 385 | 40 | 28 | 4 | 0 | 0 | 0 | 234
25-0108438 | Shasta | JESSUP 1102 | JESSUP 110262802 | 3rd Party | 2025-10-04 20:57 | -07:00 | 09/30 - 10/06 | 2025-10-05 14:51 | -07:00 | 81.649 | FTS | 124923 | 1530 | 146 | 110 | 11 | 2 | 0 | 1 | 1074
25-0108535 | Contra Costa | MORAGA 1101 | MORAGA 1101108540 | Animal | 2025-10-05 17:32 | -07:00 | 09/30 - 10/06 | 2025-10-05 19:18 | -07:00 | 90.4627 | FTS | 112807 | 1247 | 57 | 41 | 24 | 2 | 0 | 0 | 106
25-0108589 | Sutter | MERIDIAN 1102 | MERIDIAN 11023502 | Unknown Cause | 2025-10-06 06:59 | -07:00 | 09/30 - 10/06 | 2025-10-06 09:18 | -07:00 | 139 | FTS | 17236 | 124 | 1 | 1 | 2 | 0 | 0 | 0 | 139
25-0108672 | Tuolumne | TAR FLAT 0402 | TAR FLAT 0402327672 | Vegetation | 2025-10-06 09:38 | -07:00 | 09/30 - 10/06 | 2025-10-06 10:29 | -07:00 | 50.0301 | FTS | 24965 | 499 | 22 | 18 | 1 | 2 | 0 | 0 | 51
25-0108746 | El Dorado | SHINGLE SPRINGS 1104 | SHINGLE SPRINGS 1104CB | Animal | 2025-10-06 10:57 | -07:00 | 09/30 - 10/06 | 2025-10-06 12:12 | -07:00 | 54.8416 | FTS | 146756 | 2676 | 207 | 152 | 33 | 8 | 0 | 50 | 75
25-0108729 | Lake | HIGHLANDS 1103 | HIGHLANDS 1103CB | Unknown Cause | 2025-10-06 10:43 | -07:00 | 09/30 - 10/06 | 2025-10-06 12:43 | -07:00 | 120 | FTS | 286320 | 2386 | 156 | 90 | 51 | 12 | 2 | 9 | 120
25-0108861 | Santa Cruz | CAMP EVERS 2105 | CAMP EVERS 2105370732 | 3rd Party | 2025-10-06 13:13 | -07:00 | 09/30 - 10/06 | 2025-10-06 14:23 | -07:00 | 59.9535 | FTS | 25780 | 430 | 16 | 15 | 3 | 1 | 0 | 0 | 70
25-0108894 | Madera | COARSEGOLD 2102 | SAN JOAQUIN #3 1103374484 | 3rd Party | 2025-10-06 13:49 | -07:00 | 09/30 - 10/06 | 2025-10-06 14:39 | -07:00 | 50 | FTS | 50 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 50
25-0108938 | El Dorado | PLACERVILLE 2106 | PLACERVILLE 2106654798 | Unknown Cause | 2025-10-06 13:36 | -07:00 | 09/30 - 10/06 | 2025-10-06 14:41 | -07:00 | 65 | FTS | 975 | 15 | 1 | 1 | 0 | 0 | 0 | 0 | 65
25-0108958 | Madera | COARSEGOLD 2104 | COARSEGOLD 2104369777 | Company Initiated | 2025-10-06 14:46 | -07:00 | 09/30 - 10/06 | 2025-10-06 15:13 | -07:00 | 27 | FTS | 5319 | 197 | 20 | 17 | 1 | 0 | 0 | 0 | 27
25-0108719 | Tehama | VOLTA 1101 | VOLTA 1101914816 | Animal | 2025-10-06 10:36 | -07:00 | 09/30 - 10/06 | 2025-10-06 17:50 | -07:00 | 93.3671 | FTS | 7376 | 79 | 4 | 4 | 2 | 0 | 0 | 0 | 434
25-0109044 | Contra Costa | NORTH DUBLIN 2103 | NORTH DUBLIN 2103248212 | Unknown Cause | 2025-10-06 18:29 | -07:00 | 09/30 - 10/06 | 2025-10-06 20:00 | -07:00 | 91 | FTS | 1092 | 12 | 0 | 0 | 0 | 0 | 0 | 1 | 91
25-0108537 | Lake | MIDDLETOWN 1102 | MIDDLETOWN 1102998 | Equipment Failure/Involved | 2025-10-05 17:59 | -07:00 | 09/30 - 10/06 | 2025-10-06 20:27 | -07:00 | 573.9277 | FTS | 356983 | 622 | 48 | 38 | 11 | 1 | 0 | 2 | 1588
25-0109104 | San Benito | SAN BENITO 2104 | SAN BENITO 210488772 | Animal | 2025-10-07 06:53 | -07:00 | 10/07 - 10/13 | 2025-10-07 08:08 | -07:00 | 25.4 | FTS | 31750 | 1250 | 88 | 73 | 21 | 1 | 0 | 6 | 75
25-0109109 | El Dorado | MOUNTAIN QUARRIES 2101 | MOUNTAIN QUARRIES 21011184 | Unknown Cause | 2025-10-07 07:03 | -07:00 | 10/07 - 10/13 | 2025-10-07 11:00 | -07:00 | 67.125 | FTS | 122973 | 1832 | 149 | 113 | 47 | 11 | 0 | 10 | 237
25-0109236 | Napa | SILVERADO 2105 | SILVERADO 2105861266 | Unknown Cause | 2025-10-07 10:25 | -07:00 | 10/07 - 10/13 | 2025-10-07 12:02 | -07:00 | 97 | FTS | 5335 | 55 | 1 | 1 | 0 | 0 | 0 | 1 | 97
25-0109390 | Humboldt | HOOPA 1101 | HOOPA 11013174 | Company Initiated | 2025-10-07 13:51 | -07:00 | 10/07 - 10/13 | 2025-10-07 14:02 | -07:00 | 11 | FTS | 5302 | 482 | 14 | 11 | 12 | 3 | 0 | 0 | 11
25-0109328 | Calaveras | FROGTOWN 1702 | FROGTOWN 1702531640 | Unknown Cause | 2025-10-07 11:56 | -07:00 | 10/07 - 10/13 | 2025-10-07 14:05 | -07:00 | 129 | FTS | 6837 | 53 | 0 | 0 | 10 | 0 | 0 | 0 | 129
25-0109125 | Butte | ORO FINO 1102 | ORO FINO 11022236 | Company Initiated | 2025-10-07 07:53 | -07:00 | 10/07 - 10/13 | 2025-10-07 15:51 | -07:00 | 26.2701 | FTS | 28109 | 1070 | 79 | 54 | 12 | 1 | 0 | 2 | 478
25-0109311 | Humboldt | WILLOW CREEK 1101 | WILLOW CREEK 11014904 | Company Initiated | 2025-10-07 12:27 | -07:00 | 10/07 - 10/13 | 2025-10-07 19:13 | -07:00 | 359.5568 | FTS | 66518 | 185 | 8 | 6 | 8 | 1 | 0 | 1 | 406
25-0109186 | Amador | CLAY 1103 | CLAY 11035386 | Equipment Failure/Involved | 2025-10-07 09:30 | -07:00 | 10/07 - 10/13 | 2025-10-07 19:34 | -07:00 | 222.6842 | FTS | 21155 | 95 | 3 | 3 | 4 | 0 | 0 | 0 | 604
25-0109591 | San Luis Obispo | ATASCADERO 1103 | ATASCADERO 1103A46 | Animal | 2025-10-07 19:58 | -07:00 | 10/07 - 10/13 | 2025-10-07 22:01 | -07:00 | 123 | FTS | 100614 | 818 | 29 | 24 | 10 | 1 | 0 | 4 | 123
25-0109610 | Kern | LAMONT 1104 | LAMONT 11044222 | 3rd Party | 2025-10-07 21:30 | -07:00 | 10/07 - 10/13 | 2025-10-07 22:55 | -07:00 | 76.5281 | FTS | 6811 | 89 | 0 | 0 | 3 | 0 | 0 | 0 | 85
25-0109700 | Solano | PUTAH CREEK 1103 | PUTAH CREEK 11038362 | Equipment Failure/Involved | 2025-10-08 08:43 | -07:00 | 10/07 - 10/13 | 2025-10-08 09:59 | -07:00 | 22.0245 | FTS | 5396 | 245 | 11 | 10 | 3 | 2 | 0 | 6 | 76
25-0109688 | Monterey | KING CITY 1103 | KING CITY 11037038 | Equipment Failure/Involved | 2025-10-08 08:17 | -07:00 | 10/07 - 10/13 | 2025-10-08 10:07 | -07:00 | 23.2748 | FTS | 18550 | 797 | 47 | 37 | 15 | 0 | 0 | 0 | 110
25-0109748 | Madera | COARSEGOLD 2103 | COARSEGOLD 2103CB | Equipment Failure/Involved | 2025-10-08 09:41 | -07:00 | 10/07 - 10/13 | 2025-10-08 10:42 | -07:00 | 60.1599 | FTS | 124892 | 2076 | 232 | 166 | 73 | 6 | 0 | 3 | 61
25-0109835 | Santa Barbara | SANTA YNEZ 1101 | SANTA YNEZ 1101277014 | Company Initiated | 2025-10-08 11:38 | -07:00 | 10/07 - 10/13 | 2025-10-08 11:57 | -07:00 | 19 | FTS | 6878 | 362 | 6 | 4 | 26 | 0 | 0 | 0 | 19
25-0109936 | Shasta | PANORAMA 1102 | PANORAMA 1102280170 | Animal | 2025-10-08 13:42 | -07:00 | 10/07 - 10/13 | 2025-10-08 14:31 | -07:00 | 49 | FTS | 4753 | 97 | 3 | 1 | 2 | 0 | 0 | 0 | 49
25-0110108 | Shasta | RISING RIVER 1101 | RISING RIVER 11019032 | Company Initiated | 2025-10-08 17:42 | -07:00 | 10/07 - 10/13 | 2025-10-08 20:56 | -07:00 | 30.5157 | FTS | 9704 | 318 | 12 | 10 | 5 | 0 | 0 | 0 | 194
25-0110178 | Alameda | SUNOL 1101 | SUNOL 1101298061 | Vegetation | 2025-10-09 03:51 | -07:00 | 10/07 - 10/13 | 2025-10-09 08:27 | -07:00 | 276 | FTS | 55752 | 202 | 15 | 10 | 4 | 0 | 0 | 0 | 276
25-0110268 | Tehama | RED BLUFF 1105 | RED BLUFF 110585632 | Company Initiated | 2025-10-09 08:35 | -07:00 | 10/07 - 10/13 | 2025-10-09 09:17 | -07:00 | 29.0571 | FTS | 28476 | 980 | 97 | 65 | 19 | 1 | 0 | 10 | 42
25-0110223 | Napa | PUEBLO 2104 | PUEBLO 210438686 | Unknown Cause | 2025-10-09 07:21 | -07:00 | 10/07 - 10/13 | 2025-10-09 09:31 | -07:00 | 130 | FTS | 27040 | 208 | 7 | 5 | 9 | 0 | 0 | 0 | 130
25-0110405 | El Dorado | APPLE HILL 1104 | APPLE HILL 110497086 | Company Initiated | 2025-10-09 12:22 | -07:00 | 10/07 - 10/13 | 2025-10-09 12:40 | -07:00 | 18 | FTS | 252 | 14 | 2 | 0 | 0 | 0 | 0 | 0 | 18
25-0110388 | El Dorado | PLACERVILLE 2106 | PLACERVILLE 21067522 | Animal | 2025-10-09 11:47 | -07:00 | 10/07 - 10/13 | 2025-10-09 12:43 | -07:00 | 38.691 | FTS | 40316 | 1042 | 85 | 67 | 18 | 5 | 0 | 3 | 56
25-0110382 | Solano | PUTAH CREEK 1103 | PUTAH CREEK 11038362 | Equipment Failure/Involved | 2025-10-09 11:40 | -07:00 | 10/07 - 10/13 | 2025-10-09 14:05 | -07:00 | 145 | FTS | 35525 | 245 | 11 | 10 | 3 | 2 | 0 | 6 | 145
25-0110505 | San Luis Obispo | TEMPLETON 2113 | TEMPLETON 2113A10 | Company Initiated | 2025-10-09 13:38 | -07:00 | 10/07 - 10/13 | 2025-10-09 14:51 | -07:00 | 73 | FTS | 438 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 73
25-0110471 | Monterey | KING CITY 1103 | KING CITY 11037038 | Equipment Failure/Involved | 2025-10-09 13:54 | -07:00 | 10/07 - 10/13 | 2025-10-09 15:17 | -07:00 | 30.0013 | FTS | 23911 | 797 | 47 | 37 | 15 | 0 | 0 | 0 | 83
25-0110644 | Tehama | TYLER 1105 | TYLER 11051704 | Unknown Cause | 2025-10-09 18:40 | -07:00 | 10/07 - 10/13 | 2025-10-09 22:10 | -07:00 | 102.5856 | FTS | 85659 | 835 | 76 | 55 | 13 | 3 | 0 | 4 | 210
25-0110754 | Shasta | DESCHUTES 1101 | DESCHUTES 11019722 | Company Initiated | 2025-10-10 08:06 | -07:00 | 10/07 - 10/13 | 2025-10-10 08:48 | -07:00 | 38.6969 | FTS | 38426 | 993 | 68 | 50 | 17 | 3 | 0 | 8 | 42
25-0110950 | Nevada | HIGGINS 1103 | HIGGINS 1103173744 | Company Initiated | 2025-10-10 11:42 | -07:00 | 10/07 - 10/13 | 2025-10-10 12:14 | -07:00 | 32 | FTS | 3520 | 110 | 15 | 10 | 1 | 0 | 0 | 2 | 32
25-0110901 | Sonoma | FITCH MOUNTAIN 1113 | FITCH MOUNTAIN 1113154 | Vegetation | 2025-10-10 11:08 | -07:00 | 10/07 - 10/13 | 2025-10-10 12:18 | -07:00 | 29.5722 | FTS | 11474 | 388 | 11 | 7 | 10 | 0 | 0 | 8 | 70
25-0110619 | Monterey | LOS OSITOS 2103 | LOS OSITOS 21037062 | Unknown Cause | 2025-10-09 17:24 | -07:00 | 10/07 - 10/13 | 2025-10-10 12:35 | -07:00 | 598.8235 | FTS | 30540 | 51 | 0 | 0 | 1 | 0 | 0 | 0 | 1151
25-0111037 | Shasta | DESCHUTES 1101 | DESCHUTES 11011380 | Unknown Cause | 2025-10-10 14:16 | -07:00 | 10/07 - 10/13 | 2025-10-10 16:18 | -07:00 | 60.4384 | FTS | 35296 | 584 | 38 | 25 | 8 | 1 | 0 | 6 | 122
25-0111200 | Calaveras | Valley Springs 1102 | Valley Springs 1102748874 | Animal | 2025-10-11 08:35 | -07:00 | 10/07 - 10/13 | 2025-10-11 10:16 | -07:00 | 94.4503 | FTS | 30413 | 322 | 19 | 11 | 15 | 9 | 0 | 1 | 101
25-0111203 | Tuolumne | PEORIA 1705 | PEORIA 1705625728 | Unknown Cause | 2025-10-11 08:42 | -07:00 | 10/07 - 10/13 | 2025-10-11 10:51 | -07:00 | 126.838 | FTS | 22704 | 179 | 16 | 12 | 0 | 0 | 0 | 0 | 129
25-0111265 | Placer | SHADY GLEN 1101 | SHADY GLEN 11012768 | Animal | 2025-10-11 11:12 | -07:00 | 10/07 - 10/13 | 2025-10-11 12:33 | -07:00 | 81 | FTS | 14985 | 185 | 15 | 12 | 6 | 4 | 0 | 1 | 81
25-0111308 | Tehama | COTTONWOOD 1101 | COTTONWOOD 110168190 | Unknown Cause | 2025-10-11 14:50 | -07:00 | 10/07 - 10/13 | 2025-10-11 17:36 | -07:00 | 80.7447 | FTS | 38273 | 474 | 45 | 29 | 5 | 1 | 0 | 2 | 166
25-0111346 | Calaveras | FROGTOWN 1702 | FROGTOWN 1702CB | Unknown Cause | 2025-10-12 00:47 | -07:00 | 10/07 - 10/13 | 2025-10-12 03:34 | -07:00 | 124.1114 | FTS | 483538 | 3896 | 228 | 165 | 101 | 14 | 1 | 6 | 167
25-0111361 | Sonoma | SONOMA 1104 | SONOMA 1104914376 | Unknown Cause | 2025-10-12 07:10 | -07:00 | 10/07 - 10/13 | 2025-10-12 09:20 | -07:00 | 109.4364 | FTS | 84266 | 770 | 39 | 26 | 11 | 1 | 0 | 13 | 130
25-0111342 | Sonoma | FITCH MOUNTAIN 1113 | FITCH MOUNTAIN 1113CB | 3rd Party | 2025-10-11 22:38 | -07:00 | 10/07 - 10/13 | 2025-10-12 10:32 | -07:00 | 28.1116 | FTS | 74046 | 2634 | 76 | 52 | 41 | 5 | 0 | 27 | 714
25-0111307 | Nevada | HIGGINS 1109 | HIGGINS 1109594 | Equipment Failure/Involved | 2025-10-11 14:46 | -07:00 | 10/07 - 10/13 | 2025-10-12 11:25 | -07:00 | 210.8092 | FTS | 219874 | 1043 | 40 | 32 | 4 | 0 | 0 | 11 | 1239
25-0111388 | Napa | PUEBLO 2103 | PUEBLO 210398394 | Unknown Cause | 2025-10-12 11:21 | -07:00 | 10/07 - 10/13 | 2025-10-12 12:12 | -07:00 | 51 | FTS | 80019 | 1569 | 99 | 72 | 16 | 1 | 0 | 1 | 51
25-0111352 | Stanislaus | WESTLEY 1103 | WESTLEY 11039010 | 3rd Party | 2025-10-12 06:10 | -07:00 | 10/07 - 10/13 | 2025-10-12 15:20 | -07:00 | 147.8395 | FTS | 44204 | 299 | 1 | 0 | 15 | 0 | 0 | 0 | 550
25-0111369 | San Luis Obispo | TEMPLETON 2110 | TEMPLETON 2110941946 | Vegetation | 2025-10-12 08:48 | -07:00 | 10/07 - 10/13 | 2025-10-12 17:15 | -07:00 | 136.9268 | FTS | 102832 | 751 | 29 | 20 | 12 | 0 | 0 | 14 | 507
25-0111380 | Nevada | NARROWS 2102 | NARROWS 210248484 | 3rd Party | 2025-10-12 10:08 | -07:00 | 10/07 - 10/13 | 2025-10-12 17:32 | -07:00 | 97.4466 | FTS | 60222 | 618 | 41 | 25 | 14 | 4 | 0 | 20 | 444
25-0111341 | Calaveras | STANISLAUS 1701 | STANISLAUS 1701862450 | Equipment Failure/Involved | 2025-10-11 22:29 | -07:00 | 10/07 - 10/13 | 2025-10-12 17:51 | -07:00 | 524.1884 | FTS | 172458 | 329 | 16 | 14 | 28 | 2 | 0 | 0 | 1162
25-0111433 | Placer | WISE 1102 | WISE 1102307494 | Animal | 2025-10-12 23:32 | -07:00 | 10/07 - 10/13 | 2025-10-13 03:18 | -07:00 | 177.9568 | FTS | 49472 | 278 | 33 | 26 | 3 | 0 | 0 | 9 | 226
25-0111761 | Stanislaus | WESTLEY 1103 | WESTLEY 11039010 | 3rd Party | 2025-10-13 14:26 | -07:00 | 10/07 - 10/13 | 2025-10-13 19:29 | -07:00 | 303 | FTS | 90597 | 299 | 1 | 0 | 15 | 0 | 0 | 0 | 303
25-0112290 | Calaveras | FROGTOWN 1701 | FROGTOWN 1701564780 | Equipment Failure/Involved | 2025-10-14 09:19 | -07:00 | 10/14 - 10/20 | 2025-10-14 10:27 | -07:00 | 68 | FTS | 19244 | 283 | 26 | 20 | 2 | 0 | 0 | 2 | 68
25-0112094 | Kern | POSO MOUNTAIN 2104 | POSO MOUNTAIN 210448268 | 3rd Party | 2025-10-14 04:24 | -07:00 | 10/14 - 10/20 | 2025-10-15 12:32 | -07:00 | 357.3333 | FTS | 3216 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1928
25-0114810 | Butte | CLARK ROAD 1102 | CLARK ROAD 1102212118 | Animal | 2025-10-19 07:41 | -07:00 | 10/14 - 10/20 | 2025-10-19 08:49 | -07:00 | 68 | FTS | 4556 | 67 | 7 | 6 | 4 | 1 | 0 | 0 | 68
25-0114855 | Contra Costa | TASSAJARA 2104 | TASSAJARA 2104967234 | Animal | 2025-10-19 18:04 | -07:00 | 10/14 - 10/20 | 2025-10-19 21:02 | -07:00 | 178 | FTS | 24920 | 140 | 8 | 1 | 3 | 0 | 0 | 6 | 178
25-0114873 | Glenn | LOGAN CREEK 2102 | LOGAN CREEK 21022540 | Equipment Failure/Involved | 2025-10-19 23:10 | -07:00 | 10/14 - 10/20 | 2025-10-20 01:00 | -07:00 | 109.0707 | HLT | 40138 | 368 | 5 | 4 | 11 | 0 | 0 | 0 | 110
25-0114875 | Napa | SILVERADO 2102 | SILVERADO 21021607 | Unknown Cause | 2025-10-19 22:44 | -07:00 | 10/14 - 10/20 | 2025-10-20 08:00 | -07:00 | 553 | FTS | 29862 | 54 | 1 | 1 | 1 | 0 | 0 | 0 | 556
25-0114967 | Butte | CLARK ROAD 1102 | CLARK ROAD 11022582 | Company Initiated | 2025-10-20 08:53 | -07:00 | 10/14 - 10/20 | 2025-10-20 11:33 | -07:00 | 160 | FTS | 30880 | 193 | 20 | 9 | 1 | 0 | 0 | 4 | 160
25-0115141 | El Dorado | DIAMOND SPRINGS 1106 | DIAMOND SPRINGS 1106337536 | Company Initiated | 2025-10-20 13:07 | -07:00 | 10/14 - 10/20 | 2025-10-20 13:19 | -07:00 | 12 | FTS | 1536 | 128 | 6 | 5 | 2 | 0 | 0 | 0 | 12
25-0115294 | Calaveras | WEST POINT 1102 | WEST POINT 110272036 | Company Initiated | 2025-10-20 18:27 | -07:00 | 10/14 - 10/20 | 2025-10-20 18:33 | -07:00 | 6 | FTS | 276 | 46 | 3 | 2 | 1 | 0 | 0 | 0 | 6
25-0115361 | Colusa | MAXWELL 1105 | MAXWELL 1105910362 | Unknown Cause | 2025-10-21 03:02 | -07:00 | 10/21 - 10/27 | 2025-10-21 06:14 | -07:00 | 192 | FTS | 24384 | 127 | 1 | 0 | 1 | 0 | 0 | 0 | 192
25-0115376 | El Dorado | APPLE HILL 2102 | APPLE HILL 21029722 | Company Initiated | 2025-10-20 11:06 | -07:00 | 10/21 - 10/27 | 2025-10-21 06:58 | -07:00 | 1192 | FTS | 1192 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 1192
25-0115383 | Napa | SILVERADO 2104 | SILVERADO 2104324994 | Animal | 2025-10-21 06:54 | -07:00 | 10/21 - 10/27 | 2025-10-21 08:56 | -07:00 | 91.1708 | FTS | 134477 | 1475 | 61 | 37 | 32 | 7 | 0 | 6 | 122
25-0115289 | Shasta | DESCHUTES 1101 | DESCHUTES 11011652 | Unknown Cause | 2025-10-20 18:01 | -07:00 | 10/21 - 10/27 | 2025-10-21 09:24 | -07:00 | 145.4768 | FTS | 46989 | 323 | 25 | 17 | 4 | 0 | 0 | 3 | 923
25-0115827 | Butte | CLARK ROAD 1102 | CLARK ROAD 110292622 | Company Initiated | 2025-10-21 15:46 | -07:00 | 10/21 - 10/27 | 2025-10-21 16:02 | -07:00 | 16 | FTS | 2256 | 141 | 6 | 4 | 2 | 0 | 0 | 0 | 16
25-0115931 | San Mateo | HALF MOON BAY 1103 | HALF MOON BAY 11036115 | Unknown Cause | 2025-10-21 17:10 | -07:00 | 10/21 - 10/27 | 2025-10-21 21:50 | -07:00 | 280 | FTS | 7000 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 280
25-0115804 | Calaveras | FROGTOWN 1701 | FROGTOWN 170113412 | Equipment Failure/Involved | 2025-10-21 15:27 | -07:00 | 10/21 - 10/27 | 2025-10-22 04:05 | -07:00 | 52.2152 | FTS | 96807 | 1854 | 120 | 85 | 26 | 4 | 0 | 3 | 758
25-0116016 | Monterey | LOS OSITOS 2103 | LOS OSITOS 2103606732 | Environmental/External | 2025-10-22 05:13 | -07:00 | 10/21 - 10/27 | 2025-10-22 05:57 | -07:00 | 44 | HLT | 1408 | 32 | 1 | 1 | 0 | 0 | 0 | 0 | 44
25-0115994 | Shasta | PANORAMA 1102 | PANORAMA 1102508502 | Unknown Cause | 2025-10-22 03:30 | -07:00 | 10/21 - 10/27 | 2025-10-22 08:16 | -07:00 | 231.1692 | FTS | 30052 | 130 | 7 | 6 | 0 | 0 | 0 | 1 | 286
25-0116129 | Nevada | BRUNSWICK 1106 | BRUNSWICK 11062416 | Vegetation | 2025-10-22 08:55 | -07:00 | 10/21 - 10/27 | 2025-10-22 09:24 | -07:00 | 29 | FTS | 28449 | 981 | 92 | 63 | 9 | 0 | 0 | 12 | 29
25-0115916 | Yolo | MADISON 2101 | MADISON 2101484892 | Animal | 2025-10-21 18:59 | -07:00 | 10/21 - 10/27 | 2025-10-22 09:49 | -07:00 | 208.0932 | FTS | 24555 | 118 | 3 | 1 | 0 | 0 | 0 | 0 | 890
25-0116242 | Nevada | BRUNSWICK 1106 | BRUNSWICK 110651484 | Company Initiated | 2025-10-22 10:42 | -07:00 | 10/21 - 10/27 | 2025-10-22 11:10 | -07:00 | 28 | FTS | 728 | 26 | 3 | 3 | 0 | 0 | 0 | 1 | 28
25-0116477 | Nevada | HIGGINS 1110 | HIGGINS 11102408 | Animal | 2025-10-22 15:02 | -07:00 | 10/21 - 10/27 | 2025-10-22 16:38 | -07:00 | 78.0536 | FTS | 34968 | 448 | 38 | 28 | 3 | 0 | 0 | 17 | 96
25-0116894 | El Dorado | APPLE HILL 1103 | APPLE HILL 1103CB | 3rd Party | 2025-10-23 11:38 | -07:00 | 10/21 - 10/27 | 2025-10-23 12:20 | -07:00 | 42 | FTS | 52458 | 1249 | 72 | 52 | 24 | 5 | 0 | 6 | 42
25-0116904 | El Dorado | APPLE HILL 1104 | APPLE HILL 110497086 | Company Initiated | 2025-10-23 11:38 | -07:00 | 10/21 - 10/27 | 2025-10-23 12:27 | -07:00 | 49 | FTS | 22393 | 457 | 40 | 27 | 5 | 0 | 0 | 13 | 49
25-0117086 | El Dorado | APPLE HILL 1104 | APPLE HILL 110497086 | Equipment Failure/Involved | 2025-10-23 13:33 | -07:00 | 10/21 - 10/27 | 2025-10-23 20:01 | -07:00 | 142.8077 | FTS | 3713 | 26 | 3 | 1 | 1 | 0 | 0 | 0 | 388
25-0117581 | Santa Barbara | SANTA YNEZ 1102 | SANTA YNEZ 11026149 | 3rd Party | 2025-10-24 11:56 | -07:00 | 10/21 - 10/27 | 2025-10-24 15:05 | -07:00 | 189 | FTS | 4725 | 25 | 0 | 0 | 1 | 0 | 0 | 0 | 189
25-0117825 | Napa | PUEBLO 2103 | PUEBLO 2103489964 | Unknown Cause | 2025-10-25 08:22 | -07:00 | 10/21 - 10/27 | 2025-10-25 08:29 | -07:00 | 7 | FTS | 5236 | 748 | 44 | 31 | 8 | 1 | 0 | 0 | 7
25-0117828 | Napa | PUEBLO 2103 | PUEBLO 21031970 | Equipment Failure/Involved | 2025-10-25 08:30 | -07:00 | 10/21 - 10/27 | 2025-10-25 10:44 | -07:00 | 50.7449 | FTS | 79568 | 1568 | 99 | 72 | 16 | 1 | 0 | 1 | 134
25-0118114 | San Luis Obispo | PERRY 1101, PERRY 1104 | PERRY 1101CB | Unknown Cause | 2025-10-26 07:26 | -07:00 | 10/21 - 10/27 | 2025-10-26 09:03 | -07:00 | 70.4097 | T-EPSS | 365708 | 5194 | 160 | 117 | 75 | 6 | 2 | 12 | 97
25-0118667 | Santa Barbara | SANTA YNEZ 1101 | SANTA YNEZ 1101673618 | Company Initiated | 2025-10-27 17:54 | -07:00 | 10/21 - 10/27 | 2025-10-27 19:00 | -07:00 | 66 | FTS | 924 | 14 | 29 | 18 | 40 | 4 | 0 | 0 | 66
25-0118995 | San Luis Obispo | SAN LUIS OBISPO 1107 | SAN LUIS OBISPO 1107V58 | Company Initiated | 2025-10-28 11:48 | -07:00 | 10/28 - 11/03 | 2025-10-28 12:04 | -07:00 | 16 | FTS | 33024 | 2064 | 51 | 42 | 40 | 3 | 0 | 41 | 16
25-0119285 | San Luis Obispo | BAYWOOD 1101 | BAYWOOD 1101CB | Company Initiated | 2025-10-28 20:22 | -07:00 | 10/28 - 11/03 | 2025-10-28 22:54 | -07:00 | 127.0342 | FTS | 37094 | 292 | 7 | 3 | 14 | 19 | 0 | 0 | 152
25-0119317 | Santa Barbara | SANTA YNEZ 1102 | SANTA YNEZ 11026149 | 3rd Party | 2025-10-29 02:17 | -07:00 | 10/28 - 11/03 | 2025-10-29 10:02 | -07:00 | 465 | FTS | 11625 | 25 | 0 | 0 | 1 | 0 | 0 | 0 | 465
25-0119566 | Santa Cruz | BIG BASIN 1102 | BIG BASIN 1102991420 | Company Initiated | 2025-10-29 12:37 | -07:00 | 10/28 - 11/03 | 2025-10-29 12:54 | -07:00 | 14.3609 | FTS | 1910 | 133 | 7 | 5 | 1 | 0 | 0 | 0 | 17
25-0119529 | Santa Barbara | SANTA YNEZ 1102 | SANTA YNEZ 11026149 | 3rd Party | 2025-10-29 11:00 | -07:00 | 10/28 - 11/03 | 2025-10-29 15:40 | -07:00 | 236.64 | FTS | 5916 | 25 | 0 | 0 | 1 | 0 | 0 | 0 | 280
25-0119562 | San Luis Obispo | BAYWOOD 1101 | BAYWOOD 1101CB | Company Initiated | 2025-10-29 12:21 | -07:00 | 10/28 - 11/03 | 2025-10-29 22:55 | -07:00 | 247.3288 | FTS | 72220 | 292 | 7 | 3 | 14 | 19 | 0 | 0 | 634
25-0119752 | Monterey | GABILAN 1101 | GABILAN 1101460414 | Vegetation | 2025-10-29 17:24 | -07:00 | 10/28 - 11/03 | 2025-10-29 23:46 | -07:00 | 382 | FTS | 15280 | 40 | 2 | 2 | 0 | 0 | 0 | 0 | 382
25-0119904 | Monterey | LAURELES 1111 | LAURELES 1111822080 | Animal | 2025-10-30 08:39 | -07:00 | 10/28 - 11/03 | 2025-10-30 09:59 | -07:00 | 80 | FTS | 10320 | 129 | 4 | 2 | 2 | 0 | 0 | 1 | 80
25-0120004 | San Luis Obispo | BAYWOOD 1101 | BAYWOOD 1101CB | 3rd Party | 2025-10-30 10:46 | -07:00 | 10/28 - 11/03 | 2025-10-30 16:31 | -07:00 | 82.9007 | FTS | 24207 | 292 | 7 | 3 | 14 | 19 | 0 | 0 | 345
25-0120400 | Santa Barbara | ZACA 1101 | ZACA 1101Y72 | Unknown Cause | 2025-10-31 02:51 | -07:00 | 10/28 - 11/03 | 2025-10-31 14:20 | -07:00 | 374.6912 | FTS | 25479 | 68 | 0 | 0 | 8 | 14 | 0 | 0 | 689
25-0120721 | Yuba | NARROWS 2101 | NARROWS 21011202 | Company Initiated | 2025-10-31 14:45 | -07:00 | 10/28 - 11/03 | 2025-10-31 15:17 | -07:00 | 32 | FTS | 1280 | 40 | 4 | 3 | 0 | 0 | 0 | 0 | 32
25-0121180 | Yuba | NARROWS 2101 | NARROWS 2101307774 | Unknown Cause | 2025-11-03 06:18 | -08:00 | 10/28 - 11/03 | 2025-11-03 10:15 | -08:00 | 237 | FTS | 4266 | 18 | 0 | 0 | 9 | 6 | 0 | 0 | 237
25-0121991 | Fresno | COALINGA NO 2 1107 | COALINGA NO 2 1107793144 | Unknown Cause | 2025-11-04 15:48 | -08:00 | 11/04 - 11/10 | 2025-11-04 17:21 | -08:00 | 86.4231 | FTS | 4494 | 52 | 0 | 0 | 2 | 0 | 0 | 0 | 93
25-0121710 | Humboldt | ORICK 1102 | ORICK 1102CB | 3rd Party | 2025-11-04 08:35 | -08:00 | 11/04 - 11/10 | 2025-11-04 18:02 | -08:00 | 174.3153 | T-EPSS | 345493 | 1982 | 109 | 87 | 55 | 5 | 0 | 18 | 567
25-0121670 | Sierra | ALLEGHANY 1101 | ALLEGHANY 1101CB | 3rd Party | 2025-11-04 06:45 | -08:00 | 11/04 - 11/10 | 2025-11-04 21:21 | -08:00 | 90.967 | FTS | 90967 | 1000 | 38 | 28 | 20 | 1 | 0 | 1 | 876
25-0122142 | Napa | PUEBLO 2102 | PUEBLO 2102618 | Unknown Cause | 2025-11-05 06:03 | -08:00 | 11/04 - 11/10 | 2025-11-05 06:14 | -08:00 | 11 | FTS | 1078 | 98 | 1 | 0 | 1 | 0 | 0 | 0 | 11
25-0122344 | Kern | TEJON 1102 | TEJON 11023751 | Company Initiated | 2025-11-05 09:22 | -08:00 | 11/04 - 11/10 | 2025-11-05 09:48 | -08:00 | 26 | FTS | 16068 | 618 | 25 | 19 | 26 | 3 | 0 | 0 | 26
25-0123446 | Santa Barbara | SISQUOC 1102 | SISQUOC 1102M52 | Company Initiated | 2025-11-06 17:16 | -08:00 | 11/04 - 11/10 | 2025-11-06 17:28 | -08:00 | 12 | FTS | 804 | 67 | 2 | 1 | 1 | 0 | 0 | 0 | 12
25-0124840 | Kern | POSO MOUNTAIN 2103 | POSO MOUNTAIN 2103CB | Unknown Cause | 2025-11-12 07:52 | -08:00 | 11/11 - 11/17 | 2025-11-12 12:45 | -08:00 | 293 | FTS | 4102 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 293
25-0125168 | Fresno | COALINGA NO 2 1107 | COALINGA NO 2 1107793144 | Equipment Failure/Involved | 2025-11-12 15:28 | -08:00 | 11/11 - 11/17 | 2025-11-12 22:50 | -08:00 | 233.4231 | FTS | 12138 | 52 | 0 | 0 | 2 | 0 | 0 | 0 | 442
25-0126541 | Alameda | VINEYARD 2108 | VINEYARD 2108MR172 | Animal | 2025-11-15 07:58 | -08:00 | 11/11 - 11/17 | 2025-11-15 10:04 | -08:00 | 125.6003 | FTS | 382704 | 3047 | 162 | 120 | 35 | 1 | 0 | 1 | 126

## Nov Outages 110125_113025
Outages | County | Circuit | CPZ | Cause | FNL | FNL_tz | Week | End_Date | End_Date_tz | CAIDI | EPSS_Outage_Type | Customer_Minutes | CESO | Medical_Baseline | Life_Support | Critical_Customer | Schools | Hospitals | Well_Water_Dependent | Restoration_Time_Minutes
25-0121180 | Yuba | NARROWS 2101 | NARROWS 2101307774 | Unknown Cause | 2025-11-03 06:18 | -08:00 | 10/28 - 11/03 | 2025-11-03 10:15 | -08:00 | 237 | FTS | 4266 | 18 | 0 | 0 | 9 | 6 | 0 | 0 | 237
25-0121991 | Fresno | COALINGA NO 2 1107 | COALINGA NO 2 1107793144 | Unknown Cause | 2025-11-04 15:48 | -08:00 | 11/04 - 11/10 | 2025-11-04 17:21 | -08:00 | 86.4231 | FTS | 4494 | 52 | 0 | 0 | 2 | 0 | 0 | 0 | 93
25-0121710 | Humboldt | ORICK 1102 | ORICK 1102CB | 3rd Party | 2025-11-04 08:35 | -08:00 | 11/04 - 11/10 | 2025-11-04 18:02 | -08:00 | 174.3153 | T-EPSS | 345493 | 1982 | 109 | 87 | 55 | 5 | 0 | 18 | 567
25-0121670 | Sierra | ALLEGHANY 1101 | ALLEGHANY 1101CB | 3rd Party | 2025-11-04 06:45 | -08:00 | 11/04 - 11/10 | 2025-11-04 21:21 | -08:00 | 90.967 | FTS | 90967 | 1000 | 38 | 28 | 20 | 1 | 0 | 1 | 876
25-0122142 | Napa | PUEBLO 2102 | PUEBLO 2102618 | Unknown Cause | 2025-11-05 06:03 | -08:00 | 11/04 - 11/10 | 2025-11-05 06:14 | -08:00 | 11 | C/OUT | 1078 | 98 | 1 | 0 | 1 | 0 | 0 | 0 | 11
25-0122344 | Kern | TEJON 1102 | TEJON 11023751 | Company Initiated | 2025-11-05 09:22 | -08:00 | 11/04 - 11/10 | 2025-11-05 09:48 | -08:00 | 26 | FTS | 16068 | 618 | 25 | 19 | 26 | 3 | 0 | 0 | 26
25-0123446 | Santa Barbara | SISQUOC 1102 | SISQUOC 1102M52 | Company Initiated | 2025-11-06 17:16 | -08:00 | 11/04 - 11/10 | 2025-11-06 17:28 | -08:00 | 12 | FTS | 804 | 67 | 2 | 1 | 1 | 0 | 0 | 0 | 12
25-0124840 | Kern | POSO MOUNTAIN 2103 | POSO MOUNTAIN 2103CB | Unknown Cause | 2025-11-12 07:52 | -08:00 | 11/11 - 11/17 | 2025-11-12 12:45 | -08:00 | 293 | FTS | 4102 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 293
25-0125168 | Fresno | COALINGA NO 2 1107 | COALINGA NO 2 1107793144 | Equipment Failure/Involved | 2025-11-12 15:28 | -08:00 | 11/11 - 11/17 | 2025-11-12 22:50 | -08:00 | 233.4231 | FTS | 12138 | 52 | 0 | 0 | 2 | 0 | 0 | 0 | 442
25-0126541 | Alameda | VINEYARD 2108 | VINEYARD 2108MR172 | Animal | 2025-11-15 07:58 | -08:00 | 11/11 - 11/17 | 2025-11-15 10:04 | -08:00 | 125.6003 | FTS | 382704 | 3047 | 162 | 120 | 35 | 1 | 0 | 1 | 126

## YTD EPSS Outages_Circuit
Circuit | Count of Outages
ALHAMBRA 1105 | 4
ALLEGHANY 1101 | 2
ALPINE 1101 | 1
ALTO 1120 | 1
ALTO 1122 | 2
ALTO 1124 | 4
ANDERSON 1101 | 2
ANITA 1106 | 2
ANNAPOLIS 1101 | 4
ANTELOPE 1101, ANTELOPE 1102 | 2
ANTELOPE 1102 | 2
ANTLER 1101 | 5
APPLE HILL 1103 | 2
APPLE HILL 1104 | 9
APPLE HILL 2102 | 20
ARBUCKLE 1101 | 5
ARVIN 1101 | 2
ATASCADERO 1102 | 3
ATASCADERO 1103 | 9
AUBERRY 1101 | 16
AUBERRY 1102 | 3
AUBURN 1101 | 1
AUBURN 1102 | 2
AVENAL 2101 | 6
BAHIA 1102 | 3
BALFOUR 1101 | 1
BANGOR 1101 | 4
BASALT 1106 | 3
BAY MEADOWS 2102 | 1
BAYWOOD 1101 | 7
BEAR VALLEY 2101 | 1
BEAR VALLEY 2105 | 4
BELL 1107 | 10
BELL 1108 | 1
BELL 1109 | 1
BELLEVUE 2101 | 7
BELMONT 1103 | 1
BELMONT 1110 | 1
BEN LOMOND 0401 | 4
BEN LOMOND 1101 | 1
BERESFORD 0403 | 1
BERKELEY F 1103 | 1
BERRENDA A 1101 | 1
BERRENDA C 0401 | 1
BIG BASIN 1101 | 7
BIG BASIN 1102 | 6
BIG BEND 1101 | 2
BIG BEND 1102 | 6
BIG LAGOON 1101 | 1
BIG MEADOWS 2101 | 8
BOGARD 1101 | 1
BOLINAS 1101 | 2
BONNIE NOOK 1101, BONNIE NOOK 1102 | 1
BONNIE NOOK 1102 | 6
BORONDA 1101, BORONDA 1102 | 3
BRENTWOOD 2105 | 7
BRIDGEVILLE 1101 | 1
BRUNSWICK 1102 | 1
BRUNSWICK 1103 | 4
BRUNSWICK 1104 | 4
BRUNSWICK 1105 | 14
BRUNSWICK 1106 | 9
BRUNSWICK 1107 | 1
BRUNSWICK 1110 | 1
BUCKS CREEK 1103 | 1
BUELLTON 1101 | 3
BUELLTON 1102 | 1
BURNEY 1101 | 14
BURNS 2101 | 6
BUTTE 1105 | 2
CABRILLO 1103 | 11
CABRILLO 1104 | 10
CALAVERAS CEMENT 1101 | 3
CALISTOGA 1101 | 11
CALISTOGA 1102 | 13
CALPELLA 1101 | 6
CALPELLA 1102 | 1
CAMP EVERS 2103 | 2
CAMP EVERS 2104 | 2
CAMP EVERS 2105 | 12
CAMP EVERS 2106 | 6
CAMP EVERS 2107 | 11
CAMPHORA 1101 | 4
CANTUA 1101 | 2
CANTUA 1103 | 2
CARBONA 1101 | 1
CARNERAS 1103 | 3
CAROLANDS 0404 | 3
CARRIZO PLAINS 1101 | 4
CASTRO VALLEY 1102 | 1
CASTRO VALLEY 1108 | 2
CASTRO VALLEY 1110 | 6
CAYETANO 2109 | 3
CAYETANO 2111 | 2
CAYUCOS 1102 | 2
CEDAR CREEK 1101 | 5
CHALLENGE 1102 | 1
CHESTER 1101, CHESTER 1102 | 1
CHESTER 1102 | 2
CHOLAME 1101 | 5
CHOLAME 1101, CHOLAME 2102 | 4
CHOLAME 2102 | 9
CLARK ROAD 1102 | 13
CLARKSVILLE 2104 | 2
CLARKSVILLE 2109 | 3
CLAY 1101 | 4
CLAY 1102 | 1
CLAY 1103 | 4
CLAYTON 2212 | 9
CLAYTON 2215 | 5
CLEAR LAKE 1101 | 3
CLOVERDALE 1101 | 2
CLOVERDALE 1102 | 5
COALINGA NO 1 1109 | 1
COALINGA NO 2 1105 | 2
COALINGA NO 2 1107 | 4
COARSEGOLD 2102 | 3
COARSEGOLD 2103 | 4
COARSEGOLD 2104 | 9
COLUMBIA HILL 1101 | 4
COLUSA 1101, COLUSA 1103, COLUSA 1104, COLUSA 1105 | 1
COPUS 1102 | 1
CORDELIA 1104 | 1
CORDELIA 1112 | 1
CORNING 1101 | 4
CORNING 1102 | 3
CORRAL 1101 | 8
CORRAL 1102 | 1
CORRAL 1103 | 7
COTATI 1102 | 3
COTATI 1103 | 4
COTATI 1105 | 3
COTTLE 1701 | 1
COTTONWOOD 1101 | 4
COTTONWOOD 1102 | 3
COTTONWOOD 1103 | 8
COVELO 1101 | 14
CURTIS 1701 | 1
CURTIS 1702 | 11
CURTIS 1703 | 6
CURTIS 1704 | 14
CURTIS 1705 | 5
CUYAMA 1103 | 3
CUYAMA 1103, CUYAMA 1104, CUYAMA 2101, CUYAMA 2102 | 1
CUYAMA 1103, CUYAMA 1104, CUYAMA 2102 | 1
CUYAMA 2101 | 6
DEL MAR 2109 | 3
DEL MONTE 2104 | 3
DESCHUTES 1101 | 6
DESCHUTES 1104 | 5
DEVILS DEN 1101 | 3
DEVILS DEN 1101, DEVILS DEN 1102 | 4
DIAMOND SPRINGS 1103 | 2
DIAMOND SPRINGS 1104 | 1
DIAMOND SPRINGS 1105 | 6
DIAMOND SPRINGS 1106 | 12
DIVIDE 1103 | 1
DOBBINS 1101 | 3
DOLAN ROAD 1101 | 2
DUNBAR 1101 | 5
DUNBAR 1103 | 8
DUNLAP 1102 | 9
DUNLAP 1103 | 15
EAST MARYSVILLE 1108 | 1
ECHO SUMMIT 1101 | 1
EDENVALE 1102 | 1
EDENVALE 2105 | 4
EL CERRITO G 1105 | 1
EL DORADO PH 2101 | 4
EL DORADO PH 2102 | 3
ELECTRA 1101 | 5
ELK 1101 | 1
ELK CREEK 1101 | 10
EMERALD LAKE 0401 | 1
FAIRVIEW 2207 | 5
FELLOWS 2103 | 1
FELLOWS 2104 | 2
FITCH MOUNTAIN 1113 | 22
FLINT 1101 | 1
FOOTHILL 1101 | 3
FOOTHILL 1102 | 2
FORESTHILL 1101 | 4
FORESTHILL 1101, FORESTHILL 1102 | 1
FORESTHILL 1102 | 2
FORT ORD 2106 | 2
FORT ROSS 1121 | 1
FRANKLIN 1104 | 1
FREMONT 1104 | 3
FRENCH GULCH 1101 | 1
FRENCH GULCH 1102 | 1
FROGTOWN 1701 | 9
FROGTOWN 1702 | 24
FRUITLAND 1141 | 2
FRUITLAND 1142 | 1
FULTON 1102 | 3
GABILAN 1101 | 9
GABILAN 1102 | 2
GANSNER 1101 | 5
GARBERVILLE 1101 | 7
GARBERVILLE 1102 | 7
GERBER 1101, GERBER 1102 | 1
GEYSERVILLE 1101 | 9
GEYSERVILLE 1102 | 11
GIRVAN 1101 | 4
GIRVAN 1102 | 3
GLENN 1101 | 3
GOLDTREE 1108 | 1
GONZALES 1101 | 5
GRAND ISLAND 2226 | 2
GRASS VALLEY 1101 | 2
GRASS VALLEY 1103 | 5
GREEN VALLEY 2101 | 5
GREEN VALLEY 2103 | 8
GUALALA 1112 | 2
GUSTINE 1102 | 9
HAAS 2101 | 3
HALF MOON BAY 1101 | 2
HALF MOON BAY 1103 | 3
HALSEY 1101 | 1
HALSEY 1102 | 3
HAMILTON A 1101, HAMILTON A 1102 | 1
HAMILTON BRANCH 1101 | 5
HAMMONDS 1102 | 2
HARTLEY 1101 | 7
HARTLEY 1102 | 1
HATTON 1101 | 2
HERDLYN 1102 | 7
HICKS 1116 | 7
HICKS 2101 | 5
HICKS 2103 | 4
HICKS 2105 | 2
HIGGINS 1103 | 8
HIGGINS 1104 | 3
HIGGINS 1109 | 6
HIGGINS 1110 | 3
HIGHLANDS 1102 | 5
HIGHLANDS 1103 | 7
HIGHLANDS 1104 | 4
HOLLISTER 2104 | 7
HOLLISTER 2105 | 6
HOLLISTER 2106 | 2
HOOPA 1101 | 13
HOPLAND 1101 | 9
HORSESHOE 1101 | 2
IGNACIO 1101 | 1
IGNACIO 1104 | 4
IGNACIO 1105 | 1
INDIAN FLAT 1104 | 6
IONE 1101 | 3
JACINTO 1101, JACINTO 1102 | 1
JAMESON 1102 | 2
JAMESON 1103 | 4
JAMESON 1105 | 3
JARVIS 1101 | 1
JARVIS 1110 | 1
JARVIS 1111 | 1
JESSUP 1101 | 5
JESSUP 1102 | 3
JOLON 1102 | 4
JOLON 1103 | 5
KANAKA 1101 | 3
KERCKHOFF 1101 | 2
KESWICK 1101 | 3
KETTLEMAN HILLS 2104 | 2
KING CITY 1102 | 1
KING CITY 1103 | 5
KING CITY 1104 | 2
KONOCTI 1102 | 4
KONOCTI 1108 | 1
LAKEVIEW 1103 | 1
LAKEVILLE 1102 | 2
LAKEWOOD 2107 | 3
LAMMERS 1101 | 1
LAMONT 1104 | 1
LAS POSITAS 2108 | 2
LAURELES 1111 | 14
LAYTONVILLE 1101 | 3
LAYTONVILLE 1102 | 2
LE GRAND 1112 | 1
LINCOLN 1101 | 2
LINCOLN 1104 | 8
LINDEN 1104 | 1
LIVE OAK 1104 | 2
LLAGAS 2101 | 8
LLAGAS 2106 | 1
LLAGAS 2107 | 2
LOCKEFORD 2102 | 1
LOGAN CREEK 2101 | 1
LOGAN CREEK 2102 | 8
LONE TREE 2105 | 3
LOS GATOS 1101 | 3
LOS GATOS 1102 | 1
LOS GATOS 1106 | 9
LOS GATOS 1107 | 5
LOS GATOS 1108 | 2
LOS OSITOS 2101 | 4
LOS OSITOS 2102 | 1
LOS OSITOS 2103 | 10
LOW GAP 1101 | 2
LOYOLA 1102 | 4
LUCERNE 1103 | 2
LUCERNE 1106 | 2
MADISON 2101 | 15
MAGUNDEN 1108 | 3
MARICOPA 1101 | 1
MARICOPA 1102 | 1
MARIPOSA 2101 | 13
MARIPOSA 2102 | 8
MARTELL 1101 | 3
MARTELL 1103 | 3
MAXWELL 1102 | 2
MAXWELL 1102, MAXWELL 1105, MAXWELL 1106 | 1
MAXWELL 1105 | 2
MC ARTHUR 1101 | 8
MC KEE 1103 | 1
MC KEE 1107 | 1
MC KEE 1111 | 3
MCKITTRICK 1101 | 1
MEADOW LANE 2106 | 1
MENDOCINO 1101 | 2
MENLO 1102 | 2
MENLO 1103 | 2
MERCED FALLS 1102 | 8
MERIDIAN 1101 | 1
MERIDIAN 1102 | 2
MESA 1101 | 4
MIDDLETOWN 1101 | 4
MIDDLETOWN 1102 | 6
MIDDLETOWN 1103 | 1
MILPITAS 1108 | 1
MILPITAS 1109 | 5
MIRABEL 1101 | 3
MIRABEL 1102 | 5
MIWUK 1701 | 1
MIWUK 1702 | 5
MOLINO 1101 | 5
MOLINO 1102 | 4
MOLINO 1103 | 1
MOLINO 1104 | 2
MONROE 2103 | 1
MONTE RIO 1111 | 2
MONTE RIO 1112 | 2
MONTE RIO 1113 | 7
MONTICELLO 1101 | 6
MORAGA 1101 | 2
MORAGA 1104 | 1
MORAGA 1105 | 1
MORGAN HILL 2104 | 3
MORGAN HILL 2105 | 11
MORGAN HILL 2106 | 1
MORGAN HILL 2108 | 3
MORGAN HILL 2109 | 1
MORGAN HILL 2111 | 13
MORRO BAY 1102 | 1
MOUNTAIN QUARRIES 2101 | 9
MT EDEN 1109 | 1
NAPA 1112 | 2
NARROWS 2101 | 7
NARROWS 2102 | 10
NARROWS 2105 | 8
NEWMAN 1105 | 1
NORTH DUBLIN 2101 | 2
NORTH DUBLIN 2103 | 3
NOTRE DAME 1104 | 2
NOVATO 1104 | 11
OAKHURST 1101 | 1
OAKHURST 1102 | 1
OAKHURST 1103 | 4
OAKLAND K 1102 | 1
OAKLAND K 1104 | 1
OAKLAND X 1104 | 1
OCEANO 1104 | 5
OILFIELDS 1103 | 4
OLEMA 1101 | 3
OLETA 1101 | 5
OLETA 1102 | 4
OREGON TRAIL 1102 | 4
OREGON TRAIL 1103 | 1
OREGON TRAIL 1104 | 6
ORICK 1102 | 2
ORO FINO 1101 | 1
ORO FINO 1102 | 8
OROVILLE 1103 | 1
OROVILLE 1104 | 1
OTTER 1101 | 1
OTTER 1102 | 2
PALMER 1101 | 6
PANOCHE 1103 | 2
PANORAMA 1101 | 1
PANORAMA 1102 | 5
PARADISE 1104 | 1
PARADISE 1105 | 2
PASO ROBLES 1103 | 1
PASO ROBLES 1104 | 4
PASO ROBLES 1108 | 3
PAUL SWEET 2105 | 1
PAUL SWEET 2106 | 5
PAUL SWEET 2107 | 1
PAUL SWEET 2109 | 2
PEABODY 2105 | 3
PEABODY 2106 | 1
PEABODY 2107 | 1
PEABODY 2108 | 1
PEABODY 2113 | 3
PEASE 1103 | 1
PEASE 1104 | 3
PENNGROVE 1101 | 1
PENRYN 1103 | 10
PENRYN 1105 | 14
PENRYN 1107 | 3
PEORIA 1701 | 11
PEORIA 1704 | 12
PEORIA 1705 | 5
PERRY 1101 | 10
PERRY 1101, PERRY 1104 | 2
PERRY 1104 | 1
PETALUMA C 1101, PETALUMA C 1102, PETALUMA C 1105, PETALUMA C 1106, PETALUMA C 1108, PETALUMA C 1109, PETALUMA C 1110 | 1
PETALUMA C 1108 | 4
PHILO 1101 | 4
PHILO 1102 | 2
PIERCY 2110 | 3
PIKE CITY 1101 | 1
PINE GROVE 1101 | 1
PINE GROVE 1102 | 8
PIT NO 1 1101 | 5
PIT NO 3 2101 | 3
PIT NO 5 1101 | 4
PLACER 1102 | 3
PLACER 1103 | 1
PLACERVILLE 1112 | 1
PLACERVILLE 2106 | 19
POINT ARENA 1101 | 1
POINT MORETTI 1101 | 4
POSO MOUNTAIN 2101 | 6
POSO MOUNTAIN 2103 | 2
POSO MOUNTAIN 2104 | 2
POTTER VALLEY P H 1105 | 8
PUEBLO 1105 | 4
PUEBLO 2102 | 5
PUEBLO 2103 | 8
PUEBLO 2104 | 10
PURISIMA 1101 | 1
PUTAH CREEK 1103 | 2
PUTAH CREEK 1105 | 3
RACETRACK 1703 | 3
RACETRACK 1704 | 1
RALSTON 1101 | 1
RALSTON 1102 | 3
RAWSON SUB | 1
RED BLUFF 1101 | 4
RED BLUFF 1103 | 2
RED BLUFF 1104 | 6
RED BLUFF 1105 | 3
REDBUD 1101 | 1
REDBUD 1102 | 5
REEDLEY 1112 | 3
RESEARCH 2102 | 3
RESERVATION ROAD 1101 | 6
RESERVATION ROAD 1102 | 2
RICE 1101, RICE 1102, RICE 1103, RICE 1104 | 1
RINCON 1101 | 3
RINCON 1103 | 1
RINCON 1104 | 1
RIO DELL 1102 | 1
RIO DELL 1104 | 1
RISING RIVER 1101 | 3
ROB ROY 2104 | 3
ROSSMOOR 1101 | 2
ROSSMOOR 1102 | 1
ROSSMOOR 1106 | 1
ROSSMOOR 1108 | 1
SALMON CREEK 1101 | 2
SALT SPRINGS 2102 | 1
SAN ARDO 1101 | 1
SAN ARDO 1102 | 5
SAN BENITO 2101 | 1
SAN BENITO 2104 | 3
SAN CARLOS 1103 | 3
SAN JOAQUIN #3 1101 | 1
SAN JOAQUIN #3 1103 | 4
SAN JUSTO 1101 | 4
SAN LUIS OBISPO 1103 | 1
SAN LUIS OBISPO 1104 | 3
SAN LUIS OBISPO 1107 | 4
SAN MIGUEL 1106 | 3
SAN MIGUEL 1107 | 4
SAN RAFAEL 1101 | 1
SAN RAFAEL 1104 | 2
SAN RAFAEL 1105 | 4
SAN RAFAEL 1107 | 2
SAN RAFAEL 1108 | 4
SAN RAFAEL 1109 | 2
SAN RAFAEL 1110 | 1
SAN RAMON 2101 | 1
SAN RAMON 2103 | 2
SAN RAMON 2106 | 2
SAN RAMON 2107 | 2
SAN RAMON 2108 | 2
SAN RAMON 2119 | 1
SAND CREEK 1103 | 9
SANGER 1108 | 3
SANTA MARIA 1108 | 4
SANTA NELLA 1104 | 1
SANTA ROSA A 1104 | 1
SANTA ROSA A 1111 | 2
SANTA YNEZ 1101 | 5
SANTA YNEZ 1102 | 7
SANTA YNEZ 1104 | 3
SARATOGA 1106 | 2
SARATOGA 1107 | 5
SHADY GLEN 1101 | 5
SHADY GLEN 1101, SHADY GLEN 1102 | 2
SHADY GLEN 1102 | 3
SHEPHERD 2111 | 2
SHINGLE SPRINGS 1103 | 1
SHINGLE SPRINGS 1104 | 5
SHINGLE SPRINGS 2105 | 3
SHINGLE SPRINGS 2108 | 2
SHINGLE SPRINGS 2109 | 12
SHINGLE SPRINGS 2110 | 4
SILVERADO 2102 | 17
SILVERADO 2103 | 7
SILVERADO 2104 | 12
SILVERADO 2105 | 9
SISQUOC 1102 | 15
SISQUOC 1103 | 2
SMARTVILLE 1101 | 1
SNEATH LANE 1101 | 1
SNEATH LANE 1106 | 2
SOBRANTE 1101 | 2
SOBRANTE 1102 | 3
SOBRANTE 1103 | 3
SOLEDAD 2101 | 3
SOLEDAD 2102 | 3
SONOMA 1102 | 1
SONOMA 1103 | 4
SONOMA 1104 | 3
SONOMA 1105 | 2
SONOMA 1107 | 1
SPAULDING 1101 | 2
SPENCE 1102 | 3
SPENCE 1104 | 1
SPRING GAP 1702 | 2
STAFFORD 1101 | 2
STAFFORD 1102 | 4
STANISLAUS 1701 | 9
STANISLAUS 1702 | 6
STELLING 1109 | 1
STELLING 1110 | 3
STELLING 1111 | 1
STILLWATER 1101 | 1
STILLWATER 1102 | 3
STONE CORRAL 1108 | 1
STONE CORRAL 1110 | 1
STOREY 1109 | 3
SUMMIT 1102 | 1
SUNOL 1101 | 3
SWIFT 2102 | 1
SWIFT 2107 | 1
SWIFT 2109 | 1
SWIFT 2110 | 6
SYCAMORE CREEK 1111 | 1
TAFT 1103 | 1
TAMARACK 1101 | 1
TAR FLAT 0402 | 1
TASSAJARA 2104 | 4
TASSAJARA 2108 | 6
TASSAJARA 2109 | 1
TASSAJARA 2112 | 5
TEJON 1102 | 1
TEJON 1103 | 2
TEJON 1106 | 2
TEMBLOR 1104 | 2
TEMPLETON 2108 | 2
TEMPLETON 2109 | 2
TEMPLETON 2110 | 15
TEMPLETON 2111 | 8
TEMPLETON 2113 | 30
TIDEWATER 2106 | 3
TIGER CREEK 0201 | 1
TIVY VALLEY 1106 | 1
TIVY VALLEY 1107 | 9
TRES PINOS 1111 | 1
TRINIDAD 1101 | 1
TULUCAY 1101 | 3
TYLER 1105 | 4
TYLER SUB | 1
UKIAH 1114 | 4
UKIAH 1115 | 1
UPPER LAKE 1101 | 3
VACAVILLE 1103 | 3
VACAVILLE 1104 | 2
VACAVILLE 1108 | 6
VACAVILLE 1109 | 2
VALLEY HOME 1703 | 2
Valley Springs 1101 | 2
Valley Springs 1102 | 2
VALLEY VIEW 1103 | 2
VALLEY VIEW 1105 | 3
VALLEY VIEW 1106 | 1
VASCO 1102 | 1
VINA 1101 | 1
VINEYARD 2107 | 3
VINEYARD 2108 | 6
VOLTA 1101 | 10
VOLTA 1102 | 7
WAHTOKE 1108 | 1
WEIMAR 1101 | 2
WEIMAR 1101, WEIMAR 1102 | 2
WEST POINT 1102 | 9
WESTLEY 1103 | 5
WHEATLAND 1104 | 1
WHEATLAND 1105 | 3
WHITMORE 1101 | 1
WILDWOOD 1101 | 2
WILLIAMS 1102 | 1
WILLITS 1103 | 11
WILLOW CREEK 1101 | 3
WILLOW CREEK 1103 | 2
WILLOW PASS 2108 | 1
WILSON 1103 | 3
WINDSOR 1103 | 4
WISE 1101 | 1
WISE 1102 | 6
WOODACRE 1101 | 2
WOODSIDE 1101 | 14
WOODSIDE 1104 | 6
WRIGHT 1110 | 2
WYANDOTTE 1102 | 1
WYANDOTTE 1103 | 2
WYANDOTTE 1105 | 1
WYANDOTTE 1107 | 8
WYANDOTTE 1109 | 6
WYANDOTTE 1110 | 1
ZACA 1101 | 3
ZACA 1102 | 5
Grand Total | 2405

## YTD EPSS Outages_CAIDI
Circuit | CAIDI
ALHAMBRA 1105 | 276.0368
ALLEGHANY 1101 | 80.6994
ALPINE 1101 | 77
ALTO 1120 | 52
ALTO 1122 | 283.09
ALTO 1124 | 85.2797
ANDERSON 1101 | 39.381
ANITA 1106 | 71.3077
ANNAPOLIS 1101 | 81.8221
ANTELOPE 1101, ANTELOPE 1102 | 387.9171
ANTELOPE 1102 | 213.5
ANTLER 1101 | 452.6023
APPLE HILL 1103 | 94.5259
APPLE HILL 1104 | 80.8435
APPLE HILL 2102 | 163.4662
ARBUCKLE 1101 | 126.7583
ARVIN 1101 | 105.2161
ATASCADERO 1102 | 80.9961
ATASCADERO 1103 | 241.1804
AUBERRY 1101 | 148.3127
AUBERRY 1102 | 88.9564
AUBURN 1101 | 57.7437
AUBURN 1102 | 103.384
AVENAL 2101 | 142.6242
BAHIA 1102 | 114.3859
BALFOUR 1101 | 31
BANGOR 1101 | 168.4607
BASALT 1106 | 225.6992
BAY MEADOWS 2102 | 62.371
BAYWOOD 1101 | 114.9843
BEAR VALLEY 2101 | 95.2326
BEAR VALLEY 2105 | 127.2877
BELL 1107 | 199.6707
BELL 1108 | 91.9747
BELL 1109 | 31
BELLEVUE 2101 | 85.5567
BELMONT 1103 | 110.7141
BELMONT 1110 | 54.8745
BEN LOMOND 0401 | 206.4941
BEN LOMOND 1101 | 121.7162
BERESFORD 0403 | 67
BERKELEY F 1103 | 81.8641
BERRENDA A 1101 | 434
BERRENDA C 0401 | 435
BIG BASIN 1101 | 56.1979
BIG BASIN 1102 | 224.286
BIG BEND 1101 | 197.45
BIG BEND 1102 | 206.0069
BIG LAGOON 1101 | 222
BIG MEADOWS 2101 | 158.8978
BOGARD 1101 | 990
BOLINAS 1101 | 432.8895
BONNIE NOOK 1101, BONNIE NOOK 1102 | 243
BONNIE NOOK 1102 | 260.7697
BORONDA 1101, BORONDA 1102 | 98.4651
BRENTWOOD 2105 | 130.1
BRIDGEVILLE 1101 | 184.2141
BRUNSWICK 1102 | 63
BRUNSWICK 1103 | 27.6203
BRUNSWICK 1104 | 169.8122
BRUNSWICK 1105 | 84.7772
BRUNSWICK 1106 | 83.2918
BRUNSWICK 1107 | 66
BRUNSWICK 1110 | 75.698
BUCKS CREEK 1103 | 44.7089
BUELLTON 1101 | 34.1138
BUELLTON 1102 | 183.7045
BURNEY 1101 | 102.6707
BURNS 2101 | 188.0054
BUTTE 1105 | 499.8117
CABRILLO 1103 | 137.299
CABRILLO 1104 | 499.79
CALAVERAS CEMENT 1101 | 164.9527
CALISTOGA 1101 | 190.9331
CALISTOGA 1102 | 81.6262
CALPELLA 1101 | 99.9044
CALPELLA 1102 | 55
CAMP EVERS 2103 | 125.1407
CAMP EVERS 2104 | 132.2109
CAMP EVERS 2105 | 223.3954
CAMP EVERS 2106 | 76.9048
CAMP EVERS 2107 | 144.8818
CAMPHORA 1101 | 171.7077
CANTUA 1101 | 216
CANTUA 1103 | 535.5
CARBONA 1101 | 27.2749
CARNERAS 1103 | 205.5821
CAROLANDS 0404 | 190.9804
CARRIZO PLAINS 1101 | 222.6068
CASTRO VALLEY 1102 | 320.7081
CASTRO VALLEY 1108 | 67.3554
CASTRO VALLEY 1110 | 46.97
CAYETANO 2109 | 118.8875
CAYETANO 2111 | 123
CAYUCOS 1102 | 177
CEDAR CREEK 1101 | 329.1686
CHALLENGE 1102 | 313.505
CHESTER 1101, CHESTER 1102 | 1080.4032
CHESTER 1102 | 87.7431
CHOLAME 1101 | 136.8592
CHOLAME 1101, CHOLAME 2102 | 544.9032
CHOLAME 2102 | 178.4432
CLARK ROAD 1102 | 171.6637
CLARKSVILLE 2104 | 108.0115
CLARKSVILLE 2109 | 113.022
CLAY 1101 | 53.3677
CLAY 1102 | 91
CLAY 1103 | 176.83
CLAYTON 2212 | 173.5468
CLAYTON 2215 | 73.2464
CLEAR LAKE 1101 | 72.7422
CLOVERDALE 1101 | 98.025
CLOVERDALE 1102 | 287.11
COALINGA NO 1 1109 | 288
COALINGA NO 2 1105 | 861.2154
COALINGA NO 2 1107 | 333.1706
COARSEGOLD 2102 | 206.7237
COARSEGOLD 2103 | 72.4051
COARSEGOLD 2104 | 132.6701
COLUMBIA HILL 1101 | 107.7009
COLUSA 1101, COLUSA 1103, COLUSA 1104, COLUSA 1105 | 26
COPUS 1102 | 284
CORDELIA 1104 | 320
CORDELIA 1112 | 81.8946
CORNING 1101 | 140.5234
CORNING 1102 | 219.3913
CORRAL 1101 | 258.1384
CORRAL 1102 | 82
CORRAL 1103 | 73.7534
COTATI 1102 | 80.4822
COTATI 1103 | 78.065
COTATI 1105 | 103.0121
COTTLE 1701 | 149.3639
COTTONWOOD 1101 | 124.9911
COTTONWOOD 1102 | 142.782
COTTONWOOD 1103 | 122.4614
COVELO 1101 | 147.1567
CURTIS 1701 | 151
CURTIS 1702 | 186.7351
CURTIS 1703 | 101.2871
CURTIS 1704 | 150.4079
CURTIS 1705 | 120.9348
CUYAMA 1103 | 475.9821
CUYAMA 1103, CUYAMA 1104, CUYAMA 2101, CUYAMA 2102 | 258.0753
CUYAMA 1103, CUYAMA 1104, CUYAMA 2102 | 218.6122
CUYAMA 2101 | 107.0621
DEL MAR 2109 | 92.3688
DEL MONTE 2104 | 162.8019
DESCHUTES 1101 | 74.7545
DESCHUTES 1104 | 238.7706
DEVILS DEN 1101 | 278.1013
DEVILS DEN 1101, DEVILS DEN 1102 | 382.0298
DIAMOND SPRINGS 1103 | 134.6837
DIAMOND SPRINGS 1104 | 31.1105
DIAMOND SPRINGS 1105 | 146.4445
DIAMOND SPRINGS 1106 | 133.3713
DIVIDE 1103 | 79.9524
DOBBINS 1101 | 171.8645
DOLAN ROAD 1101 | 80.5
DUNBAR 1101 | 115.6748
DUNBAR 1103 | 80.0808
DUNLAP 1102 | 504.9175
DUNLAP 1103 | 202.1917
EAST MARYSVILLE 1108 | 37
ECHO SUMMIT 1101 | 84
EDENVALE 1102 | 106.0575
EDENVALE 2105 | 202.6136
EL CERRITO G 1105 | 98.1973
EL DORADO PH 2101 | 52.6941
EL DORADO PH 2102 | 117.8037
ELECTRA 1101 | 68.9816
ELK 1101 | 97.3304
ELK CREEK 1101 | 266.196
EMERALD LAKE 0401 | 230
FAIRVIEW 2207 | 39.7646
FELLOWS 2103 | 114
FELLOWS 2104 | 181.5714
FITCH MOUNTAIN 1113 | 116.3227
FLINT 1101 | 182.1856
FOOTHILL 1101 | 122.0881
FOOTHILL 1102 | 99.4281
FORESTHILL 1101 | 344.3025
FORESTHILL 1101, FORESTHILL 1102 | 97.4994
FORESTHILL 1102 | 165.2199
FORT ORD 2106 | 31
FORT ROSS 1121 | 206.3957
FRANKLIN 1104 | 306
FREMONT 1104 | 63.5529
FRENCH GULCH 1101 | 199
FRENCH GULCH 1102 | 180
FROGTOWN 1701 | 146.6887
FROGTOWN 1702 | 125.1592
FRUITLAND 1141 | 192.2158
FRUITLAND 1142 | 11
FULTON 1102 | 118.2629
GABILAN 1101 | 81.6657
GABILAN 1102 | 68.9799
GANSNER 1101 | 114.215
GARBERVILLE 1101 | 212.7508
GARBERVILLE 1102 | 172.1075
GERBER 1101, GERBER 1102 | 154.0556
GEYSERVILLE 1101 | 131.9753
GEYSERVILLE 1102 | 96.0683
GIRVAN 1101 | 89.9347
GIRVAN 1102 | 82.4964
GLENN 1101 | 100.7631
GOLDTREE 1108 | 95.7892
GONZALES 1101 | 116.2647
GRAND ISLAND 2226 | 139.9766
GRASS VALLEY 1101 | 86.0594
GRASS VALLEY 1103 | 283.9747
GREEN VALLEY 2101 | 65.1974
GREEN VALLEY 2103 | 170.1488
GUALALA 1112 | 129.6756
GUSTINE 1102 | 152.2812
HAAS 2101 | 512.1086
HALF MOON BAY 1101 | 50.4909
HALF MOON BAY 1103 | 103.0932
HALSEY 1101 | 167.5287
HALSEY 1102 | 147.1732
HAMILTON A 1101, HAMILTON A 1102 | 110.0824
HAMILTON BRANCH 1101 | 71.4862
HAMMONDS 1102 | 181.7947
HARTLEY 1101 | 63.1112
HARTLEY 1102 | 65.0834
HATTON 1101 | 95.8348
HERDLYN 1102 | 193.4424
HICKS 1116 | 83.042
HICKS 2101 | 150.7123
HICKS 2103 | 156.5735
HICKS 2105 | 128
HIGGINS 1103 | 215.1216
HIGGINS 1104 | 60.5251
HIGGINS 1109 | 140.8023
HIGGINS 1110 | 99.1544
HIGHLANDS 1102 | 104.9227
HIGHLANDS 1103 | 204.2759
HIGHLANDS 1104 | 50.0724
HOLLISTER 2104 | 52.2889
HOLLISTER 2105 | 99.1777
HOLLISTER 2106 | 121.9193
HOOPA 1101 | 179.3353
HOPLAND 1101 | 100.4383
HORSESHOE 1101 | 117.0596
IGNACIO 1101 | 49
IGNACIO 1104 | 104.0208
IGNACIO 1105 | 87.8707
INDIAN FLAT 1104 | 442.9677
IONE 1101 | 192.9535
JACINTO 1101, JACINTO 1102 | 123
JAMESON 1102 | 446.7046
JAMESON 1103 | 90.4813
JAMESON 1105 | 80.9899
JARVIS 1101 | 140.1513
JARVIS 1110 | 45
JARVIS 1111 | 79
JESSUP 1101 | 78.7821
JESSUP 1102 | 114.7236
JOLON 1102 | 239.0354
JOLON 1103 | 72.46
KANAKA 1101 | 131.4839
KERCKHOFF 1101 | 95.8348
KESWICK 1101 | 121.6328
KETTLEMAN HILLS 2104 | 311
KING CITY 1102 | 224
KING CITY 1103 | 53.4
KING CITY 1104 | 110
KONOCTI 1102 | 102.4616
KONOCTI 1108 | 66
LAKEVIEW 1103 | 219
LAKEVILLE 1102 | 75.3036
LAKEWOOD 2107 | 95.6014
LAMMERS 1101 | 94.3333
LAMONT 1104 | 76.5281
LAS POSITAS 2108 | 45.1424
LAURELES 1111 | 249.3072
LAYTONVILLE 1101 | 146.9286
LAYTONVILLE 1102 | 192.5
LE GRAND 1112 | 63.5742
LINCOLN 1101 | 135.9254
LINCOLN 1104 | 120.1739
LINDEN 1104 | 116.6913
LIVE OAK 1104 | 250.3768
LLAGAS 2101 | 121.4058
LLAGAS 2106 | 161
LLAGAS 2107 | 89.9392
LOCKEFORD 2102 | 422
LOGAN CREEK 2101 | 193
LOGAN CREEK 2102 | 135.4089
LONE TREE 2105 | 116.5889
LOS GATOS 1101 | 259.5625
LOS GATOS 1102 | 51.0169
LOS GATOS 1106 | 133.3763
LOS GATOS 1107 | 124.4992
LOS GATOS 1108 | 88.7003
LOS OSITOS 2101 | 244.3812
LOS OSITOS 2102 | 8
LOS OSITOS 2103 | 109.4208
LOW GAP 1101 | 527.5728
LOYOLA 1102 | 114.6192
LUCERNE 1103 | 54.153
LUCERNE 1106 | 79.162
MADISON 2101 | 145.3828
MAGUNDEN 1108 | 60.3065
MARICOPA 1101 | 243
MARICOPA 1102 | 294.6114
MARIPOSA 2101 | 184.4863
MARIPOSA 2102 | 91.4077
MARTELL 1101 | 76.3001
MARTELL 1103 | 483.3972
MAXWELL 1102 | 204.8459
MAXWELL 1102, MAXWELL 1105, MAXWELL 1106 | 224.7622
MAXWELL 1105 | 220.1193
MC ARTHUR 1101 | 206.8498
MC KEE 1103 | 65
MC KEE 1107 | 45
MC KEE 1111 | 114.8769
MCKITTRICK 1101 | 42
MEADOW LANE 2106 | 153
MENDOCINO 1101 | 74.3068
MENLO 1102 | 49.3517
MENLO 1103 | 82.3166
MERCED FALLS 1102 | 109.7037
MERIDIAN 1101 | 115.3733
MERIDIAN 1102 | 101.5
MESA 1101 | 107.5613
MIDDLETOWN 1101 | 121.1021
MIDDLETOWN 1102 | 214.5726
MIDDLETOWN 1103 | 107.2222
MILPITAS 1108 | 132
MILPITAS 1109 | 155.2165
MIRABEL 1101 | 53.6769
MIRABEL 1102 | 151.1764
MIWUK 1701 | 131.1782
MIWUK 1702 | 132.8267
MOLINO 1101 | 82.7156
MOLINO 1102 | 75.7623
MOLINO 1103 | 50.7873
MOLINO 1104 | 438.8312
MONROE 2103 | 15
MONTE RIO 1111 | 91.8078
MONTE RIO 1112 | 119.3321
MONTE RIO 1113 | 140.7879
MONTICELLO 1101 | 181.72
MORAGA 1101 | 89.6361
MORAGA 1104 | 98
MORAGA 1105 | 94.6009
MORGAN HILL 2104 | 137.3923
MORGAN HILL 2105 | 140.6536
MORGAN HILL 2106 | 181.2352
MORGAN HILL 2108 | 129.8152
MORGAN HILL 2109 | 147
MORGAN HILL 2111 | 175.8508
MORRO BAY 1102 | 47.8519
MOUNTAIN QUARRIES 2101 | 172.4034
MT EDEN 1109 | 110
NAPA 1112 | 81.4622
NARROWS 2101 | 212.9423
NARROWS 2102 | 82.6025
NARROWS 2105 | 136.223
NEWMAN 1105 | 288
NORTH DUBLIN 2101 | 127.4513
NORTH DUBLIN 2103 | 18.2277
NOTRE DAME 1104 | 47.9317
NOVATO 1104 | 64.6426
OAKHURST 1101 | 42.8017
OAKHURST 1102 | 149
OAKHURST 1103 | 520.016
OAKLAND K 1102 | 126.9401
OAKLAND K 1104 | 7
OAKLAND X 1104 | 48.5707
OCEANO 1104 | 89.1949
OILFIELDS 1103 | 104.8221
OLEMA 1101 | 99.1304
OLETA 1101 | 25.8798
OLETA 1102 | 99.1987
OREGON TRAIL 1102 | 100.3984
OREGON TRAIL 1103 | 534.6143
OREGON TRAIL 1104 | 150.9767
ORICK 1102 | 211.4094
ORO FINO 1101 | 98
ORO FINO 1102 | 180.7415
OROVILLE 1103 | 118.6243
OROVILLE 1104 | 152.2241
OTTER 1101 | 76.0215
OTTER 1102 | 477.2613
PALMER 1101 | 179.7129
PANOCHE 1103 | 132.609
PANORAMA 1101 | 35.3092
PANORAMA 1102 | 182.9583
PARADISE 1104 | 86.6675
PARADISE 1105 | 139.5291
PASO ROBLES 1103 | 299.7821
PASO ROBLES 1104 | 279.0165
PASO ROBLES 1108 | 90.3333
PAUL SWEET 2105 | 46
PAUL SWEET 2106 | 55.5842
PAUL SWEET 2107 | 63
PAUL SWEET 2109 | 64.8275
PEABODY 2105 | 67.8588
PEABODY 2106 | 53
PEABODY 2107 | 535.9965
PEABODY 2108 | 102.5084
PEABODY 2113 | 195.9491
PEASE 1103 | 42.9079
PEASE 1104 | 254.9524
PENNGROVE 1101 | 758
PENRYN 1103 | 115.3976
PENRYN 1105 | 73.4933
PENRYN 1107 | 90.8723
PEORIA 1701 | 177.1142
PEORIA 1704 | 65.9353
PEORIA 1705 | 89.451
PERRY 1101 | 76.1675
PERRY 1101, PERRY 1104 | 39.1958
PERRY 1104 | 211.8182
PETALUMA C 1101, PETALUMA C 1102, PETALUMA C 1105, PETALUMA C 1106, PETALUMA C 1108, PETALUMA C 1109, PETALUMA C 1110 | 159.0547
PETALUMA C 1108 | 127.1605
PHILO 1101 | 117.9686
PHILO 1102 | 76.5776
PIERCY 2110 | 212.1026
PIKE CITY 1101 | 133
PINE GROVE 1101 | 55.1577
PINE GROVE 1102 | 100.3083
PIT NO 1 1101 | 58.2305
PIT NO 3 2101 | 166.1157
PIT NO 5 1101 | 337.1658
PLACER 1102 | 151.1175
PLACER 1103 | 169
PLACERVILLE 1112 | 146.2485
PLACERVILLE 2106 | 170.2415
POINT ARENA 1101 | 183.8264
POINT MORETTI 1101 | 44.5327
POSO MOUNTAIN 2101 | 908.1486
POSO MOUNTAIN 2103 | 814
POSO MOUNTAIN 2104 | 340.1667
POTTER VALLEY P H 1105 | 166.883
PUEBLO 1105 | 333.1416
PUEBLO 2102 | 82.0688
PUEBLO 2103 | 67.6875
PUEBLO 2104 | 178.7133
PURISIMA 1101 | 66.385
PUTAH CREEK 1103 | 83.5122
PUTAH CREEK 1105 | 118.6555
RACETRACK 1703 | 120.0807
RACETRACK 1704 | 505.678
RALSTON 1101 | 103.0527
RALSTON 1102 | 43.7449
RAWSON SUB | 7
RED BLUFF 1101 | 128.8607
RED BLUFF 1103 | 121.5806
RED BLUFF 1104 | 51.1447
RED BLUFF 1105 | 197.179
REDBUD 1101 | 111
REDBUD 1102 | 104.4909
REEDLEY 1112 | 112.7318
RESEARCH 2102 | 188.1853
RESERVATION ROAD 1101 | 136.8602
RESERVATION ROAD 1102 | 84.3823
RICE 1101, RICE 1102, RICE 1103, RICE 1104 | 118.5778
RINCON 1101 | 125.2139
RINCON 1103 | 222.8025
RINCON 1104 | 99.9961
RIO DELL 1102 | 68.9167
RIO DELL 1104 | 91
RISING RIVER 1101 | 171.4487
ROB ROY 2104 | 88.6224
ROSSMOOR 1101 | 59.4992
ROSSMOOR 1102 | 192.3288
ROSSMOOR 1106 | 53.6873
ROSSMOOR 1108 | 89
SALMON CREEK 1101 | 345.5515
SALT SPRINGS 2102 | 99
SAN ARDO 1101 | 84.1154
SAN ARDO 1102 | 201.1592
SAN BENITO 2101 | 34
SAN BENITO 2104 | 73.3483
SAN CARLOS 1103 | 190.7597
SAN JOAQUIN #3 1101 | 24.8182
SAN JOAQUIN #3 1103 | 72.5563
SAN JUSTO 1101 | 177.4719
SAN LUIS OBISPO 1103 | 13
SAN LUIS OBISPO 1104 | 178.3603
SAN LUIS OBISPO 1107 | 53.6481
SAN MIGUEL 1106 | 184.8768
SAN MIGUEL 1107 | 144.4524
SAN RAFAEL 1101 | 86.6106
SAN RAFAEL 1104 | 250.1202
SAN RAFAEL 1105 | 51.7467
SAN RAFAEL 1107 | 61.0257
SAN RAFAEL 1108 | 40.2007
SAN RAFAEL 1109 | 222.497
SAN RAFAEL 1110 | 78.4863
SAN RAMON 2101 | 23.0926
SAN RAMON 2103 | 322.4501
SAN RAMON 2106 | 52.8106
SAN RAMON 2107 | 513.0376
SAN RAMON 2108 | 300.3997
SAN RAMON 2119 | 109.6513
SAND CREEK 1103 | 343.1697
SANGER 1108 | 76.8813
SANTA MARIA 1108 | 354.5818
SANTA NELLA 1104 | 129
SANTA ROSA A 1104 | 61
SANTA ROSA A 1111 | 109.9666
SANTA YNEZ 1101 | 288.6518
SANTA YNEZ 1102 | 115.327
SANTA YNEZ 1104 | 55.2617
SARATOGA 1106 | 107.8835
SARATOGA 1107 | 136.0542
SHADY GLEN 1101 | 59.9518
SHADY GLEN 1101, SHADY GLEN 1102 | 237.3492
SHADY GLEN 1102 | 287.1835
SHEPHERD 2111 | 166.1166
SHINGLE SPRINGS 1103 | 69
SHINGLE SPRINGS 1104 | 61.7857
SHINGLE SPRINGS 2105 | 102.8952
SHINGLE SPRINGS 2108 | 126.9639
SHINGLE SPRINGS 2109 | 125.7838
SHINGLE SPRINGS 2110 | 66.7652
SILVERADO 2102 | 298.2812
SILVERADO 2103 | 99.8863
SILVERADO 2104 | 161.7485
SILVERADO 2105 | 227.6326
SISQUOC 1102 | 173.0571
SISQUOC 1103 | 132.6957
SMARTVILLE 1101 | 271
SNEATH LANE 1101 | 98
SNEATH LANE 1106 | 89.3158
SOBRANTE 1101 | 146.4673
SOBRANTE 1102 | 137.6033
SOBRANTE 1103 | 101.1909
SOLEDAD 2101 | 287.4545
SOLEDAD 2102 | 178.6692
SONOMA 1102 | 12
SONOMA 1103 | 53.9505
SONOMA 1104 | 84.1061
SONOMA 1105 | 74.1956
SONOMA 1107 | 209.192
SPAULDING 1101 | 186.5868
SPENCE 1102 | 128.6162
SPENCE 1104 | 150
SPRING GAP 1702 | 302.7509
STAFFORD 1101 | 66.2919
STAFFORD 1102 | 106.9242
STANISLAUS 1701 | 239.4899
STANISLAUS 1702 | 106.8134
STELLING 1109 | 156.6667
STELLING 1110 | 138.2871
STELLING 1111 | 58
STILLWATER 1101 | 141
STILLWATER 1102 | 301.6942
STONE CORRAL 1108 | 237.7048
STONE CORRAL 1110 | 93
STOREY 1109 | 186.6379
SUMMIT 1102 | 106.5
SUNOL 1101 | 262.807
SWIFT 2102 | 100
SWIFT 2107 | 132
SWIFT 2109 | 322.6363
SWIFT 2110 | 245.6413
SYCAMORE CREEK 1111 | 105.125
TAFT 1103 | 312.7647
TAMARACK 1101 | 82
TAR FLAT 0402 | 50.0301
TASSAJARA 2104 | 95.7942
TASSAJARA 2108 | 102.248
TASSAJARA 2109 | 64.5194
TASSAJARA 2112 | 65.0232
TEJON 1102 | 26
TEJON 1103 | 326.3026
TEJON 1106 | 109.3276
TEMBLOR 1104 | 153.9545
TEMPLETON 2108 | 63.2734
TEMPLETON 2109 | 57.1996
TEMPLETON 2110 | 135.8131
TEMPLETON 2111 | 80.4274
TEMPLETON 2113 | 80.6751
TIDEWATER 2106 | 262.8862
TIGER CREEK 0201 | 184
TIVY VALLEY 1106 | 306.2637
TIVY VALLEY 1107 | 337.5231
TRES PINOS 1111 | 107
TRINIDAD 1101 | 144
TULUCAY 1101 | 42.6667
TYLER 1105 | 120.4148
TYLER SUB | 94.3235
UKIAH 1114 | 324.7736
UKIAH 1115 | 114.5303
UPPER LAKE 1101 | 67.8623
VACAVILLE 1103 | 82.8811
VACAVILLE 1104 | 31.1505
VACAVILLE 1108 | 143.5817
VACAVILLE 1109 | 79.4327
VALLEY HOME 1703 | 583.9229
Valley Springs 1101 | 66.9266
Valley Springs 1102 | 99.7868
VALLEY VIEW 1103 | 47.2634
VALLEY VIEW 1105 | 113.6809
VALLEY VIEW 1106 | 47
VASCO 1102 | 614.3363
VINA 1101 | 181.7843
VINEYARD 2107 | 500.6562
VINEYARD 2108 | 111.9401
VOLTA 1101 | 191.9685
VOLTA 1102 | 79.5248
WAHTOKE 1108 | 144.0933
WEIMAR 1101 | 155.9674
WEIMAR 1101, WEIMAR 1102 | 125.7673
WEST POINT 1102 | 88.549
WESTLEY 1103 | 207.9245
WHEATLAND 1104 | 154
WHEATLAND 1105 | 395.3427
WHITMORE 1101 | 219
WILDWOOD 1101 | 166.6768
WILLIAMS 1102 | 126
WILLITS 1103 | 120.8269
WILLOW CREEK 1101 | 169.7744
WILLOW CREEK 1103 | 354.527
WILLOW PASS 2108 | 90.1178
WILSON 1103 | 104.1555
WINDSOR 1103 | 64.9688
WISE 1101 | 82.9132
WISE 1102 | 162.7909
WOODACRE 1101 | 145.3186
WOODSIDE 1101 | 386.6109
WOODSIDE 1104 | 188.0668
WRIGHT 1110 | 52.0865
WYANDOTTE 1102 | 86
WYANDOTTE 1103 | 85.9613
WYANDOTTE 1105 | 192
WYANDOTTE 1107 | 110.9056
WYANDOTTE 1109 | 76.7565
WYANDOTTE 1110 | 78.5428
ZACA 1101 | 148.1683
ZACA 1102 | 77.9412
Grand Total | 136.7726

## YTD EPSS Outages_CESO
Circuit | Sum of CESO
ALHAMBRA 1105 | 380
ALLEGHANY 1101 | 1607
ALPINE 1101 | 282
ALTO 1120 | 1654
ALTO 1122 | 3445
ALTO 1124 | 1877
ANDERSON 1101 | 2016
ANITA 1106 | 299
ANNAPOLIS 1101 | 281
ANTELOPE 1101, ANTELOPE 1102 | 434
ANTELOPE 1102 | 434
ANTLER 1101 | 1788
APPLE HILL 1103 | 1449
APPLE HILL 1104 | 3686
APPLE HILL 2102 | 37739
ARBUCKLE 1101 | 480
ARVIN 1101 | 722
ATASCADERO 1102 | 6136
ATASCADERO 1103 | 6895
AUBERRY 1101 | 6652
AUBERRY 1102 | 1996
AUBURN 1101 | 913
AUBURN 1102 | 1987
AVENAL 2101 | 7457
BAHIA 1102 | 710
BALFOUR 1101 | 488
BANGOR 1101 | 942
BASALT 1106 | 369
BAY MEADOWS 2102 | 1159
BAYWOOD 1101 | 4909
BEAR VALLEY 2101 | 172
BEAR VALLEY 2105 | 5395
BELL 1107 | 5239
BELL 1108 | 1661
BELL 1109 | 42
BELLEVUE 2101 | 4293
BELMONT 1103 | 934
BELMONT 1110 | 2263
BEN LOMOND 0401 | 512
BEN LOMOND 1101 | 747
BERESFORD 0403 | 331
BERKELEY F 1103 | 309
BERRENDA A 1101 | 1
BERRENDA C 0401 | 1
BIG BASIN 1101 | 6675
BIG BASIN 1102 | 3797
BIG BEND 1101 | 40
BIG BEND 1102 | 1896
BIG LAGOON 1101 | 147
BIG MEADOWS 2101 | 5814
BOGARD 1101 | 9
BOLINAS 1101 | 1629
BONNIE NOOK 1101, BONNIE NOOK 1102 | 805
BONNIE NOOK 1102 | 1355
BORONDA 1101, BORONDA 1102 | 2438
BRENTWOOD 2105 | 1830
BRIDGEVILLE 1101 | 766
BRUNSWICK 1102 | 675
BRUNSWICK 1103 | 4790
BRUNSWICK 1104 | 1512
BRUNSWICK 1105 | 9241
BRUNSWICK 1106 | 7519
BRUNSWICK 1107 | 1267
BRUNSWICK 1110 | 3997
BUCKS CREEK 1103 | 292
BUELLTON 1101 | 3277
BUELLTON 1102 | 2095
BURNEY 1101 | 1418
BURNS 2101 | 9041
BUTTE 1105 | 409
CABRILLO 1103 | 3164
CABRILLO 1104 | 5325
CALAVERAS CEMENT 1101 | 909
CALISTOGA 1101 | 3319
CALISTOGA 1102 | 10244
CALPELLA 1101 | 2416
CALPELLA 1102 | 88
CAMP EVERS 2103 | 2494
CAMP EVERS 2104 | 1498
CAMP EVERS 2105 | 14671
CAMP EVERS 2106 | 2647
CAMP EVERS 2107 | 11028
CAMPHORA 1101 | 626
CANTUA 1101 | 120
CANTUA 1103 | 34
CARBONA 1101 | 2837
CARNERAS 1103 | 67
CAROLANDS 0404 | 1275
CARRIZO PLAINS 1101 | 1320
CASTRO VALLEY 1102 | 1038
CASTRO VALLEY 1108 | 3714
CASTRO VALLEY 1110 | 3663
CAYETANO 2109 | 3510
CAYETANO 2111 | 6
CAYUCOS 1102 | 104
CEDAR CREEK 1101 | 1483
CHALLENGE 1102 | 200
CHESTER 1101, CHESTER 1102 | 1669
CHESTER 1102 | 144
CHOLAME 1101 | 1662
CHOLAME 1101, CHOLAME 2102 | 6313
CHOLAME 2102 | 1672
CLARK ROAD 1102 | 2566
CLARKSVILLE 2104 | 5114
CLARKSVILLE 2109 | 6002
CLAY 1101 | 3386
CLAY 1102 | 3
CLAY 1103 | 353
CLAYTON 2212 | 5285
CLAYTON 2215 | 10604
CLEAR LAKE 1101 | 1377
CLOVERDALE 1101 | 3357
CLOVERDALE 1102 | 1164
COALINGA NO 1 1109 | 7
COALINGA NO 2 1105 | 195
COALINGA NO 2 1107 | 299
COARSEGOLD 2102 | 152
COARSEGOLD 2103 | 3298
COARSEGOLD 2104 | 10450
COLUMBIA HILL 1101 | 856
COLUSA 1101, COLUSA 1103, COLUSA 1104, COLUSA 1105 | 3187
COPUS 1102 | 33
CORDELIA 1104 | 67
CORDELIA 1112 | 4488
CORNING 1101 | 3116
CORNING 1102 | 1099
CORRAL 1101 | 3114
CORRAL 1102 | 126
CORRAL 1103 | 11706
COTATI 1102 | 759
COTATI 1103 | 3891
COTATI 1105 | 1241
COTTLE 1701 | 349
COTTONWOOD 1101 | 2365
COTTONWOOD 1102 | 2248
COTTONWOOD 1103 | 3966
COVELO 1101 | 9056
CURTIS 1701 | 2635
CURTIS 1702 | 4352
CURTIS 1703 | 8245
CURTIS 1704 | 3481
CURTIS 1705 | 5288
CUYAMA 1103 | 112
CUYAMA 1103, CUYAMA 1104, CUYAMA 2101, CUYAMA 2102 | 837
CUYAMA 1103, CUYAMA 1104, CUYAMA 2102 | 539
CUYAMA 2101 | 644
DEL MAR 2109 | 17059
DEL MONTE 2104 | 7806
DESCHUTES 1101 | 4453
DESCHUTES 1104 | 946
DEVILS DEN 1101 | 158
DEVILS DEN 1101, DEVILS DEN 1102 | 504
DIAMOND SPRINGS 1103 | 2305
DIAMOND SPRINGS 1104 | 1014
DIAMOND SPRINGS 1105 | 3777
DIAMOND SPRINGS 1106 | 6391
DIVIDE 1103 | 42
DOBBINS 1101 | 989
DOLAN ROAD 1101 | 1618
DUNBAR 1101 | 2134
DUNBAR 1103 | 2748
DUNLAP 1102 | 630
DUNLAP 1103 | 4997
EAST MARYSVILLE 1108 | 388
ECHO SUMMIT 1101 | 1398
EDENVALE 1102 | 818
EDENVALE 2105 | 44
EL CERRITO G 1105 | 730
EL DORADO PH 2101 | 6042
EL DORADO PH 2102 | 2567
ELECTRA 1101 | 543
ELK 1101 | 112
ELK CREEK 1101 | 5842
EMERALD LAKE 0401 | 27
FAIRVIEW 2207 | 2859
FELLOWS 2103 | 187
FELLOWS 2104 | 42
FITCH MOUNTAIN 1113 | 10642
FLINT 1101 | 873
FOOTHILL 1101 | 7729
FOOTHILL 1102 | 2245
FORESTHILL 1101 | 6145
FORESTHILL 1101, FORESTHILL 1102 | 2619
FORESTHILL 1102 | 3151
FORT ORD 2106 | 2288
FORT ROSS 1121 | 235
FRANKLIN 1104 | 81
FREMONT 1104 | 2570
FRENCH GULCH 1101 | 75
FRENCH GULCH 1102 | 27
FROGTOWN 1701 | 11255
FROGTOWN 1702 | 28790
FRUITLAND 1141 | 1427
FRUITLAND 1142 | 482
FULTON 1102 | 833
GABILAN 1101 | 706
GABILAN 1102 | 548
GANSNER 1101 | 2712
GARBERVILLE 1101 | 662
GARBERVILLE 1102 | 3608
GERBER 1101, GERBER 1102 | 1475
GEYSERVILLE 1101 | 4244
GEYSERVILLE 1102 | 4304
GIRVAN 1101 | 2772
GIRVAN 1102 | 1684
GLENN 1101 | 363
GOLDTREE 1108 | 3634
GONZALES 1101 | 340
GRAND ISLAND 2226 | 8900
GRASS VALLEY 1101 | 808
GRASS VALLEY 1103 | 3285
GREEN VALLEY 2101 | 851
GREEN VALLEY 2103 | 23574
GUALALA 1112 | 1418
GUSTINE 1102 | 4363
HAAS 2101 | 221
HALF MOON BAY 1101 | 1436
HALF MOON BAY 1103 | 311
HALSEY 1101 | 331
HALSEY 1102 | 2194
HAMILTON A 1101, HAMILTON A 1102 | 1286
HAMILTON BRANCH 1101 | 1849
HAMMONDS 1102 | 531
HARTLEY 1101 | 7896
HARTLEY 1102 | 923
HATTON 1101 | 4473
HERDLYN 1102 | 2274
HICKS 1116 | 1832
HICKS 2101 | 2113
HICKS 2103 | 5090
HICKS 2105 | 294
HIGGINS 1103 | 5948
HIGGINS 1104 | 5188
HIGGINS 1109 | 3131
HIGGINS 1110 | 1224
HIGHLANDS 1102 | 7726
HIGHLANDS 1103 | 4280
HIGHLANDS 1104 | 5329
HOLLISTER 2104 | 4445
HOLLISTER 2105 | 923
HOLLISTER 2106 | 384
HOOPA 1101 | 6222
HOPLAND 1101 | 2295
HORSESHOE 1101 | 856
IGNACIO 1101 | 853
IGNACIO 1104 | 2976
IGNACIO 1105 | 4408
INDIAN FLAT 1104 | 2473
IONE 1101 | 1247
JACINTO 1101, JACINTO 1102 | 958
JAMESON 1102 | 2319
JAMESON 1103 | 2803
JAMESON 1105 | 3366
JARVIS 1101 | 4072
JARVIS 1110 | 82
JARVIS 1111 | 14
JESSUP 1101 | 6800
JESSUP 1102 | 3451
JOLON 1102 | 650
JOLON 1103 | 50
KANAKA 1101 | 31
KERCKHOFF 1101 | 672
KESWICK 1101 | 866
KETTLEMAN HILLS 2104 | 116
KING CITY 1102 | 5
KING CITY 1103 | 3985
KING CITY 1104 | 518
KONOCTI 1102 | 1380
KONOCTI 1108 | 1037
LAKEVIEW 1103 | 57
LAKEVILLE 1102 | 56
LAKEWOOD 2107 | 1721
LAMMERS 1101 | 39
LAMONT 1104 | 89
LAS POSITAS 2108 | 7767
LAURELES 1111 | 6992
LAYTONVILLE 1101 | 574
LAYTONVILLE 1102 | 20
LE GRAND 1112 | 418
LINCOLN 1101 | 3457
LINCOLN 1104 | 1823
LINDEN 1104 | 447
LIVE OAK 1104 | 844
LLAGAS 2101 | 6180
LLAGAS 2106 | 22
LLAGAS 2107 | 526
LOCKEFORD 2102 | 656
LOGAN CREEK 2101 | 147
LOGAN CREEK 2102 | 1186
LONE TREE 2105 | 5351
LOS GATOS 1101 | 768
LOS GATOS 1102 | 590
LOS GATOS 1106 | 11569
LOS GATOS 1107 | 1204
LOS GATOS 1108 | 1535
LOS OSITOS 2101 | 480
LOS OSITOS 2102 | 92
LOS OSITOS 2103 | 1300
LOW GAP 1101 | 1023
LOYOLA 1102 | 1342
LUCERNE 1103 | 1503
LUCERNE 1106 | 5382
MADISON 2101 | 7897
MAGUNDEN 1108 | 124
MARICOPA 1101 | 82
MARICOPA 1102 | 193
MARIPOSA 2101 | 9424
MARIPOSA 2102 | 14578
MARTELL 1101 | 1063
MARTELL 1103 | 423
MAXWELL 1102 | 318
MAXWELL 1102, MAXWELL 1105, MAXWELL 1106 | 1186
MAXWELL 1105 | 176
MC ARTHUR 1101 | 3202
MC KEE 1103 | 77
MC KEE 1107 | 42
MC KEE 1111 | 1730
MCKITTRICK 1101 | 39
MEADOW LANE 2106 | 4
MENDOCINO 1101 | 1496
MENLO 1102 | 1308
MENLO 1103 | 998
MERCED FALLS 1102 | 5865
MERIDIAN 1101 | 450
MERIDIAN 1102 | 248
MESA 1101 | 4386
MIDDLETOWN 1101 | 862
MIDDLETOWN 1102 | 7473
MIDDLETOWN 1103 | 153
MILPITAS 1108 | 6
MILPITAS 1109 | 799
MIRABEL 1101 | 1009
MIRABEL 1102 | 3356
MIWUK 1701 | 1240
MIWUK 1702 | 4564
MOLINO 1101 | 1902
MOLINO 1102 | 4262
MOLINO 1103 | 597
MOLINO 1104 | 2606
MONROE 2103 | 2712
MONTE RIO 1111 | 1290
MONTE RIO 1112 | 1343
MONTE RIO 1113 | 10821
MONTICELLO 1101 | 1675
MORAGA 1101 | 1638
MORAGA 1104 | 1767
MORAGA 1105 | 1897
MORGAN HILL 2104 | 1657
MORGAN HILL 2105 | 14649
MORGAN HILL 2106 | 625
MORGAN HILL 2108 | 1288
MORGAN HILL 2109 | 544
MORGAN HILL 2111 | 5229
MORRO BAY 1102 | 2430
MOUNTAIN QUARRIES 2101 | 5970
MT EDEN 1109 | 13
NAPA 1112 | 251
NARROWS 2101 | 2183
NARROWS 2102 | 12048
NARROWS 2105 | 9159
NEWMAN 1105 | 176
NORTH DUBLIN 2101 | 10896
NORTH DUBLIN 2103 | 5293
NOTRE DAME 1104 | 3836
NOVATO 1104 | 6888
OAKHURST 1101 | 1558
OAKHURST 1102 | 804
OAKHURST 1103 | 4502
OAKLAND K 1102 | 1336
OAKLAND K 1104 | 683
OAKLAND X 1104 | 2490
OCEANO 1104 | 5671
OILFIELDS 1103 | 7303
OLEMA 1101 | 2116
OLETA 1101 | 6339
OLETA 1102 | 1731
OREGON TRAIL 1102 | 2565
OREGON TRAIL 1103 | 1299
OREGON TRAIL 1104 | 2873
ORICK 1102 | 2323
ORO FINO 1101 | 1038
ORO FINO 1102 | 6823
OROVILLE 1103 | 897
OROVILLE 1104 | 1919
OTTER 1101 | 791
OTTER 1102 | 972
PALMER 1101 | 2466
PANOCHE 1103 | 422
PANORAMA 1101 | 1520
PANORAMA 1102 | 551
PARADISE 1104 | 2454
PARADISE 1105 | 2404
PASO ROBLES 1103 | 1317
PASO ROBLES 1104 | 1516
PASO ROBLES 1108 | 297
PAUL SWEET 2105 | 4249
PAUL SWEET 2106 | 8775
PAUL SWEET 2107 | 174
PAUL SWEET 2109 | 3687
PEABODY 2105 | 11118
PEABODY 2106 | 3524
PEABODY 2107 | 575
PEABODY 2108 | 3753
PEABODY 2113 | 727
PEASE 1103 | 695
PEASE 1104 | 336
PENNGROVE 1101 | 261
PENRYN 1103 | 5153
PENRYN 1105 | 7223
PENRYN 1107 | 1550
PEORIA 1701 | 11605
PEORIA 1704 | 18202
PEORIA 1705 | 5226
PERRY 1101 | 14403
PERRY 1101, PERRY 1104 | 10391
PERRY 1104 | 66
PETALUMA C 1101, PETALUMA C 1102, PETALUMA C 1105, PETALUMA C 1106, PETALUMA C 1108, PETALUMA C 1109, PETALUMA C 1110 | 20103
PETALUMA C 1108 | 1894
PHILO 1101 | 2323
PHILO 1102 | 1792
PIERCY 2110 | 1510
PIKE CITY 1101 | 137
PINE GROVE 1101 | 691
PINE GROVE 1102 | 10605
PIT NO 1 1101 | 2430
PIT NO 3 2101 | 242
PIT NO 5 1101 | 386
PLACER 1102 | 8836
PLACER 1103 | 165
PLACERVILLE 1112 | 338
PLACERVILLE 2106 | 34811
POINT ARENA 1101 | 242
POINT MORETTI 1101 | 1714
POSO MOUNTAIN 2101 | 451
POSO MOUNTAIN 2103 | 28
POSO MOUNTAIN 2104 | 18
POTTER VALLEY P H 1105 | 983
PUEBLO 1105 | 791
PUEBLO 2102 | 1556
PUEBLO 2103 | 10240
PUEBLO 2104 | 5023
PURISIMA 1101 | 187
PUTAH CREEK 1103 | 490
PUTAH CREEK 1105 | 476
RACETRACK 1703 | 3914
RACETRACK 1704 | 118
RALSTON 1101 | 1632
RALSTON 1102 | 4105
RAWSON SUB | 2535
RED BLUFF 1101 | 1271
RED BLUFF 1103 | 2959
RED BLUFF 1104 | 2273
RED BLUFF 1105 | 2559
REDBUD 1101 | 2087
REDBUD 1102 | 6794
REEDLEY 1112 | 906
RESEARCH 2102 | 2834
RESERVATION ROAD 1101 | 3577
RESERVATION ROAD 1102 | 497
RICE 1101, RICE 1102, RICE 1103, RICE 1104 | 1305
RINCON 1101 | 2408
RINCON 1103 | 395
RINCON 1104 | 3330
RIO DELL 1102 | 48
RIO DELL 1104 | 255
RISING RIVER 1101 | 1482
ROB ROY 2104 | 8716
ROSSMOOR 1101 | 599
ROSSMOOR 1102 | 5699
ROSSMOOR 1106 | 1938
ROSSMOOR 1108 | 1058
SALMON CREEK 1101 | 388
SALT SPRINGS 2102 | 2018
SAN ARDO 1101 | 52
SAN ARDO 1102 | 1143
SAN BENITO 2101 | 475
SAN BENITO 2104 | 3750
SAN CARLOS 1103 | 924
SAN JOAQUIN #3 1101 | 682
SAN JOAQUIN #3 1103 | 284
SAN JUSTO 1101 | 835
SAN LUIS OBISPO 1103 | 1149
SAN LUIS OBISPO 1104 | 630
SAN LUIS OBISPO 1107 | 8908
SAN MIGUEL 1106 | 276
SAN MIGUEL 1107 | 672
SAN RAFAEL 1101 | 3662
SAN RAFAEL 1104 | 7740
SAN RAFAEL 1105 | 6344
SAN RAFAEL 1107 | 8013
SAN RAFAEL 1108 | 6970
SAN RAFAEL 1109 | 1656
SAN RAFAEL 1110 | 3660
SAN RAMON 2101 | 6093
SAN RAMON 2103 | 4092
SAN RAMON 2106 | 1748
SAN RAMON 2107 | 2556
SAN RAMON 2108 | 11310
SAN RAMON 2119 | 3737
SAND CREEK 1103 | 3318
SANGER 1108 | 1601
SANTA MARIA 1108 | 1674
SANTA NELLA 1104 | 72
SANTA ROSA A 1104 | 378
SANTA ROSA A 1111 | 1107
SANTA YNEZ 1101 | 942
SANTA YNEZ 1102 | 1098
SANTA YNEZ 1104 | 1223
SARATOGA 1106 | 1580
SARATOGA 1107 | 2677
SHADY GLEN 1101 | 1972
SHADY GLEN 1101, SHADY GLEN 1102 | 5418
SHADY GLEN 1102 | 1188
SHEPHERD 2111 | 549
SHINGLE SPRINGS 1103 | 384
SHINGLE SPRINGS 1104 | 5283
SHINGLE SPRINGS 2105 | 3863
SHINGLE SPRINGS 2108 | 2439
SHINGLE SPRINGS 2109 | 5042
SHINGLE SPRINGS 2110 | 3232
SILVERADO 2102 | 5239
SILVERADO 2103 | 3440
SILVERADO 2104 | 9565
SILVERADO 2105 | 1290
SISQUOC 1102 | 2170
SISQUOC 1103 | 161
SMARTVILLE 1101 | 276
SNEATH LANE 1101 | 836
SNEATH LANE 1106 | 8211
SOBRANTE 1101 | 2536
SOBRANTE 1102 | 1747
SOBRANTE 1103 | 1729
SOLEDAD 2101 | 99
SOLEDAD 2102 | 260
SONOMA 1102 | 21
SONOMA 1103 | 2163
SONOMA 1104 | 1536
SONOMA 1105 | 772
SONOMA 1107 | 125
SPAULDING 1101 | 334
SPENCE 1102 | 594
SPENCE 1104 | 167
SPRING GAP 1702 | 843
STAFFORD 1101 | 1288
STAFFORD 1102 | 1503
STANISLAUS 1701 | 2478
STANISLAUS 1702 | 10722
STELLING 1109 | 1425
STELLING 1110 | 1383
STELLING 1111 | 115
STILLWATER 1101 | 32
STILLWATER 1102 | 2374
STONE CORRAL 1108 | 901
STONE CORRAL 1110 | 52
STOREY 1109 | 301
SUMMIT 1102 | 94
SUNOL 1101 | 342
SWIFT 2102 | 6
SWIFT 2107 | 225
SWIFT 2109 | 2043
SWIFT 2110 | 1823
SYCAMORE CREEK 1111 | 48
TAFT 1103 | 34
TAMARACK 1101 | 120
TAR FLAT 0402 | 499
TASSAJARA 2104 | 2396
TASSAJARA 2108 | 1875
TASSAJARA 2109 | 2031
TASSAJARA 2112 | 4487
TEJON 1102 | 618
TEJON 1103 | 76
TEJON 1106 | 116
TEMBLOR 1104 | 66
TEMPLETON 2108 | 5848
TEMPLETON 2109 | 2695
TEMPLETON 2110 | 8316
TEMPLETON 2111 | 12772
TEMPLETON 2113 | 33298
TIDEWATER 2106 | 11013
TIGER CREEK 0201 | 3
TIVY VALLEY 1106 | 182
TIVY VALLEY 1107 | 4670
TRES PINOS 1111 | 47
TRINIDAD 1101 | 1469
TULUCAY 1101 | 36
TYLER 1105 | 2688
TYLER SUB | 3743
UKIAH 1114 | 592
UKIAH 1115 | 1005
UPPER LAKE 1101 | 1256
VACAVILLE 1103 | 7083
VACAVILLE 1104 | 2552
VACAVILLE 1108 | 4803
VACAVILLE 1109 | 208
VALLEY HOME 1703 | 389
Valley Springs 1101 | 3244
Valley Springs 1102 | 1412
VALLEY VIEW 1103 | 1534
VALLEY VIEW 1105 | 2175
VALLEY VIEW 1106 | 4543
VASCO 1102 | 226
VINA 1101 | 306
VINEYARD 2107 | 6972
VINEYARD 2108 | 14284
VOLTA 1101 | 6041
VOLTA 1102 | 1791
WAHTOKE 1108 | 225
WEIMAR 1101 | 2391
WEIMAR 1101, WEIMAR 1102 | 4293
WEST POINT 1102 | 4854
WESTLEY 1103 | 1232
WHEATLAND 1104 | 257
WHEATLAND 1105 | 639
WHITMORE 1101 | 83
WILDWOOD 1101 | 99
WILLIAMS 1102 | 141
WILLITS 1103 | 4939
WILLOW CREEK 1101 | 798
WILLOW CREEK 1103 | 1873
WILLOW PASS 2108 | 1087
WILSON 1103 | 4818
WINDSOR 1103 | 2240
WISE 1101 | 2131
WISE 1102 | 1487
WOODACRE 1101 | 226
WOODSIDE 1101 | 8921
WOODSIDE 1104 | 3443
WRIGHT 1110 | 2439
WYANDOTTE 1102 | 2122
WYANDOTTE 1103 | 1785
WYANDOTTE 1105 | 528
WYANDOTTE 1107 | 7394
WYANDOTTE 1109 | 6944
WYANDOTTE 1110 | 1763
ZACA 1101 | 303
ZACA 1102 | 4676
Grand Total | 1821243

## YTD EPSS Outages_CPZ
CPZ | Count of Outages
ALHAMBRA 11058302 | 4
ALLEGHANY 1101804 | 1
ALLEGHANY 1101CB | 1
ALPINE 1101CB | 1
ALTO 112088190 | 1
ALTO 1122591122 | 1
ALTO 112265474 | 1
ALTO 1124430 | 1
ALTO 1124432 | 1
ALTO 1124870444 | 1
ALTO 1124CB | 1
ANDERSON 11011390 | 1
ANDERSON 1101CB | 1
ANITA 11062418 | 1
ANITA 1106552724 | 1
ANNAPOLIS 1101202158 | 2
ANNAPOLIS 1101528344 | 1
ANNAPOLIS 110176842 | 1
ANTELOPE 1101CB | 2
ANTELOPE 1102CB | 1
ANTLER 11011378 | 2
ANTLER 1101671078 | 2
ANTLER 1101CB | 1
APPLE HILL 11038412 | 1
APPLE HILL 1103CB | 1
APPLE HILL 110412832 | 2
APPLE HILL 110413512 | 2
APPLE HILL 1104275024 | 1
APPLE HILL 110497086 | 4
APPLE HILL 2102124050 | 2
APPLE HILL 21021532 | 1
APPLE HILL 210277546 | 1
APPLE HILL 2102836878 | 7
APPLE HILL 21029722 | 6
APPLE HILL 210297982 | 2
APPLE HILL 2102CB | 1
ARBUCKLE 11013068 | 5
ARVIN 110194892 | 2
ATASCADERO 1102A26 | 1
ATASCADERO 1102A88 | 2
ATASCADERO 1103411671 | 1
ATASCADERO 1103440856 | 3
ATASCADERO 1103A06 | 2
ATASCADERO 1103A18 | 2
ATASCADERO 1103A46 | 1
AUBERRY 1101233716 | 1
AUBERRY 110137536 | 1
AUBERRY 1101378194 | 1
AUBERRY 1101460274 | 1
AUBERRY 1101D320 | 3
AUBERRY 1101D323 | 1
AUBERRY 1101R2579 | 3
AUBERRY 1101R2838 | 1
AUBERRY 1101R2839 | 1
AUBERRY 1101R314 | 1
AUBERRY 1101R324 | 3
AUBERRY 1102CB | 1
AUBERRY 1102R1013 | 1
AUBERRY 1102R309 | 1
AUBURN 1101173014 | 1
AUBURN 1102251946 | 2
AVENAL 210144778 | 1
AVENAL 21019070 | 3
AVENAL 2101CB | 2
BAHIA 1102946 | 3
BALFOUR 1101CB | 1
BANGOR 11011804 | 2
BANGOR 11011806 | 1
BANGOR 1101CB | 1
BASALT 1106657038 | 3
BAY MEADOWS 210257886 | 1
BAYWOOD 1101CB | 5
BAYWOOD 1101V102 | 2
BEAR VALLEY 2101149792 | 1
BEAR VALLEY 210538882 | 1
BEAR VALLEY 21054629 | 1
BEAR VALLEY 21059480 | 1
BELL 11072400 | 6
BELL 110750172 | 3
BELL 1107CB | 1
BELL 1108467470 | 1
BELL 110950506 | 1
BELLEVUE 2101270638 | 4
BELLEVUE 2101411782 | 3
BELMONT 11038958 | 1
BELMONT 11109090 | 1
BEN LOMOND 04015144 | 3
BEN LOMOND 0401698634 | 1
BEN LOMOND 0401944178 | 1
BEN LOMOND 1101BL 1101 | 1
BERESFORD 0403855954 | 1
BERKELEY F 1103162952 | 1
BIG BASIN 110110720 | 1
BIG BASIN 1101136050 | 1
BIG BASIN 1101393582 | 1
BIG BASIN 110165444 | 2
BIG BASIN 110169550 | 1
BIG BASIN 110195690 | 1
BIG BASIN 110212758 | 1
BIG BASIN 110212992 | 1
BIG BASIN 110276752 | 1
BIG BASIN 110296986 | 1
BIG BASIN 1102991420 | 1
BIG BASIN 1102CB | 1
BIG BEND 1101180398 | 1
BIG BEND 1101641808 | 1
BIG BEND 1102884340 | 1
BIG BEND 1102CB | 5
BIG MEADOWS 21012056 | 4
BIG MEADOWS 21012476 | 1
BIG MEADOWS 21012562 | 2
BIG MEADOWS 2101427964 | 1
BOLINAS 1101504 | 1
BOLINAS 1101528 | 1
BONNIE NOOK 1102542186 | 6
BONNIE NOOK 1102CB | 1
BORONDA 1101CB | 1
BRENTWOOD 210519062 | 3
BRENTWOOD 2105502672 | 1
BRENTWOOD 2105822252 | 1
BRENTWOOD 210596324 | 2
BRIDGEVILLE 110137484 | 1
BRUNSWICK 11021010 | 1
BRUNSWICK 11032200 | 1
BRUNSWICK 11032784 | 2
BRUNSWICK 1103851116 | 1
BRUNSWICK 11041020 | 2
BRUNSWICK 11042112 | 1
BRUNSWICK 1104789062 | 1
BRUNSWICK 11051030 | 1
BRUNSWICK 11052130 | 5
BRUNSWICK 11052140 | 3
BRUNSWICK 11052204 | 4
BRUNSWICK 11052210 | 1
BRUNSWICK 11062392 | 1
BRUNSWICK 11062416 | 1
BRUNSWICK 11062790 | 1
BRUNSWICK 110651484 | 1
BRUNSWICK 110651486 | 4
BRUNSWICK 1106CB | 1
BRUNSWICK 110750010 | 1
BRUNSWICK 1110CB | 1
BUCKS CREEK 1103338520 | 1
BUELLTON 1101Y06 | 3
BUELLTON 1102CB | 1
BURNEY 11011322 | 5
BURNEY 11011340 | 2
BURNEY 11011358 | 1
BURNEY 1101355340 | 5
BURNEY 1101519432 | 1
BURNS 210110912 | 1
BURNS 210136516 | 3
BURNS 2101389090 | 1
BURNS 2101CB | 2
BUTTE 1105612016 | 2
CABRILLO 11031437 | 1
CABRILLO 1103420128 | 3
CABRILLO 1103460184 | 1
CABRILLO 1103Y10 | 1
CABRILLO 1103Y46 | 5
CABRILLO 1104597930 | 1
CABRILLO 1104838078 | 8
CABRILLO 1104Y24 | 1
CALAVERAS CEMENT 1101120672 | 1
CALAVERAS CEMENT 1101544800 | 1
CALAVERAS CEMENT 110180930 | 1
CALISTOGA 1101242919 | 4
CALISTOGA 1101257964 | 3
CALISTOGA 1101843761 | 1
CALISTOGA 1101894 | 1
CALISTOGA 1101894220 | 1
CALISTOGA 1101959538 | 1
CALISTOGA 1102131531 | 2
CALISTOGA 1102270153 | 1
CALISTOGA 1102306462 | 2
CALISTOGA 1102634 | 2
CALISTOGA 1102640833 | 1
CALISTOGA 1102706 | 3
CALISTOGA 1102769230 | 1
CALISTOGA 1102892348 | 1
CALPELLA 11015659 | 1
CALPELLA 1101619542 | 1
CALPELLA 11016383 | 1
CALPELLA 1101908688 | 2
CALPELLA 1102421412 | 1
CAMP EVERS 210311046 | 1
CAMP EVERS 2103449218 | 1
CAMP EVERS 210411048 | 2
CAMP EVERS 210510214 | 4
CAMP EVERS 210510728 | 1
CAMP EVERS 210511004 | 1
CAMP EVERS 2105370732 | 5
CAMP EVERS 2105601610 | 1
CAMP EVERS 210584166 | 1
CAMP EVERS 210612518 | 4
CAMP EVERS 210612760 | 1
CAMP EVERS 210637210 | 1
CAMP EVERS 210694770 | 1
CAMP EVERS 210711006 | 1
CAMP EVERS 210711044 | 3
CAMP EVERS 2107287578 | 1
CAMP EVERS 210746311 | 1
CAMP EVERS 2107543858 | 1
CAMPHORA 110122412 | 3
CAMPHORA 110177978 | 1
CANTUA 1101CB | 2
CANTUA 11039900 | 2
CARBONA 1101CB | 1
CARNERAS 1103430670 | 2
CARNERAS 1103CB | 1
CAROLANDS 04049024 | 2
CAROLANDS 04049026 | 1
CARRIZO PLAINS 1101384116 | 4
CASTRO VALLEY 1102840916 | 1
CASTRO VALLEY 1108343456 | 2
CASTRO VALLEY 1110560528 | 1
CASTRO VALLEY 1110MR243 | 4
CASTRO VALLEY 1110MR273 | 1
CAYETANO 2109884904 | 2
CAYETANO 2109CB | 1
CAYETANO 2111MR444 | 2
CAYUCOS 1102317156 | 2
CEDAR CREEK 11011664 | 3
CEDAR CREEK 1101451856 | 1
CEDAR CREEK 1101CB | 1
CHALLENGE 11021064 | 1
CHESTER 1102385846 | 2
CHOLAME 1101CB | 1
CHOLAME 1101R22 | 1
CHOLAME 1101X06 | 1
CHOLAME 1101X12 | 1
CHOLAME 1101X18 | 1
CHOLAME 210249414 | 1
CHOLAME 2102654164 | 1
CHOLAME 2102867686 | 1
CHOLAME 2102CB | 1
CHOLAME 2102X04 | 1
CHOLAME 2102X08 | 1
CHOLAME 2102X10 | 2
CHOLAME 2102X16 | 1
CHOLAME 2102X20 | 1
CHOLAME 2102X22 | 1
CLARK ROAD 11022044 | 2
CLARK ROAD 11022068 | 4
CLARK ROAD 1102212118 | 3
CLARK ROAD 11022582 | 1
CLARK ROAD 110281296 | 1
CLARK ROAD 110290548 | 1
CLARK ROAD 110292622 | 1
CLARKSVILLE 210413352 | 1
CLARKSVILLE 2104CB | 1
CLARKSVILLE 210951742 | 1
CLARKSVILLE 21096502 | 1
CLARKSVILLE 2109CB | 1
CLAY 110113442 | 1
CLAY 110113450 | 2
CLAY 1101CB | 1
CLAY 1102CB | 1
CLAY 11031230 | 1
CLAY 110334338 | 2
CLAY 11035386 | 1
CLAYTON 2212158138 | 1
CLAYTON 2212204416 | 1
CLAYTON 2212614950 | 1
CLAYTON 2212681608 | 1
CLAYTON 221296224 | 4
CLAYTON 2212CB | 1
CLAYTON 22159765 | 1
CLAYTON 2215CB | 2
CLAYTON 2215W531R | 2
CLEAR LAKE 11011302 | 2
CLEAR LAKE 1101872376 | 1
CLOVERDALE 1101112 | 2
CLOVERDALE 1102262 | 2
CLOVERDALE 1102672 | 1
CLOVERDALE 1102674 | 2
COALINGA NO 1 1109696152 | 1
COALINGA NO 2 110541954 | 1
COALINGA NO 2 11059000 | 1
COALINGA NO 2 1107793144 | 3
COALINGA NO 2 1107CB | 1
COARSEGOLD 210210040 | 1
COARSEGOLD 21025721 | 1
COARSEGOLD 210310300 | 2
COARSEGOLD 2103731524 | 1
COARSEGOLD 2103CB | 1
COARSEGOLD 210410110 | 1
COARSEGOLD 210410400 | 2
COARSEGOLD 2104369777 | 2
COARSEGOLD 210490356 | 2
COARSEGOLD 2104905960 | 2
COLUMBIA HILL 110135424 | 1
COLUMBIA HILL 1101764 | 2
COLUMBIA HILL 110190730 | 1
COLUSA 1101CB | 1
COPUS 11022399 | 1
CORDELIA 110448536 | 1
CORDELIA 11128832 | 1
CORNING 11011440 | 1
CORNING 110185162 | 2
CORNING 1101972454 | 1
CORNING 11021900 | 3
CORRAL 110112606 | 1
CORRAL 110112612 | 1
CORRAL 1101173174 | 2
CORRAL 11012128 | 1
CORRAL 1101220994 | 1
CORRAL 110136652 | 1
CORRAL 110175204 | 1
CORRAL 110214026 | 1
CORRAL 110314716 | 1
CORRAL 110336680 | 1
CORRAL 110359770 | 2
CORRAL 1103CB | 3
COTATI 110259258 | 3
COTATI 1103132 | 1
COTATI 1103310 | 1
COTATI 110361736 | 1
COTATI 1103CB | 1
COTATI 1105104502 | 1
COTATI 1105616 | 1
COTATI 1105844060 | 1
COTTLE 170178452 | 1
COTTONWOOD 11011610 | 1
COTTONWOOD 1101384360 | 1
COTTONWOOD 110168190 | 2
COTTONWOOD 11021578 | 1
COTTONWOOD 1102544790 | 2
COTTONWOOD 11031348 | 3
COTTONWOOD 11031616 | 3
COTTONWOOD 110331548 | 1
COTTONWOOD 11039072 | 1
COVELO 110137328 | 6
COVELO 1101430286 | 1
COVELO 1101516510 | 2
COVELO 1101562360 | 3
COVELO 1101664688 | 1
COVELO 1101CB | 1
CURTIS 1701CB | 1
CURTIS 170210940 | 1
CURTIS 170247488 | 3
CURTIS 17026008 | 3
CURTIS 1702756888 | 1
CURTIS 1702873788 | 2
CURTIS 1702961393 | 1
CURTIS 17031949 | 1
CURTIS 1703258550 | 1
CURTIS 1703476872 | 1
CURTIS 170384944 | 1
CURTIS 17039240 | 1
CURTIS 17039330 | 1
CURTIS 1703956734 | 1
CURTIS 17041691 | 1
CURTIS 17041691BP | 1
CURTIS 170420771 | 2
CURTIS 170463502 | 1
CURTIS 17048140 | 5
CURTIS 1704895006 | 4
CURTIS 170510590 | 1
CURTIS 170539256 | 1
CURTIS 170565908 | 2
CURTIS 1705CB | 1
CUYAMA 1103622728 | 2
CUYAMA 1103684566 | 1
CUYAMA 21013542 | 4
CUYAMA 2101952122 | 2
DEL MAR 210975802 | 1
DEL MAR 2109CB | 2
DEL MONTE 21042624 | 1
DEL MONTE 21043088 | 1
DEL MONTE 21049500 | 1
DESCHUTES 11011380 | 1
DESCHUTES 11011580 | 1
DESCHUTES 11011652 | 1
DESCHUTES 11019722 | 2
DESCHUTES 1101CB | 1
DESCHUTES 1104378894 | 1
DESCHUTES 1104421598 | 2
DESCHUTES 1104622260 | 1
DESCHUTES 1104656708 | 1
DEVILS DEN 1101824190 | 1
DEVILS DEN 11019470 | 1
DEVILS DEN 1101CB | 3
DIAMOND SPRINGS 1103467046 | 1
DIAMOND SPRINGS 11039432 | 1
DIAMOND SPRINGS 1104CB | 1
DIAMOND SPRINGS 1105146980 | 1
DIAMOND SPRINGS 110519910 | 2
DIAMOND SPRINGS 11057722 | 4
DIAMOND SPRINGS 11062100 | 4
DIAMOND SPRINGS 1106337536 | 1
DIAMOND SPRINGS 110676088 | 2
DIAMOND SPRINGS 1106803034 | 2
DIAMOND SPRINGS 110699658 | 2
DOBBINS 11011808 | 1
DOBBINS 110169722 | 1
DOBBINS 110191464 | 1
DOLAN ROAD 1101491190 | 2
DUNBAR 1101137736 | 1
DUNBAR 1101534 | 2
DUNBAR 1101725292 | 2
DUNBAR 1103234 | 1
DUNBAR 1103302 | 2
DUNBAR 1103596218 | 5
DUNLAP 110239190 | 1
DUNLAP 11027050 | 5
DUNLAP 11027060 | 1
DUNLAP 11027360 | 2
DUNLAP 1103124724 | 4
DUNLAP 11037040 | 2
DUNLAP 11037080 | 3
DUNLAP 11037170 | 3
DUNLAP 11037959F | 2
DUNLAP 1103CB | 1
EAST MARYSVILLE 1108900690 | 1
EAST QUINCY 11012452 | 1
ECHO SUMMIT 1101927328 | 1
EDENVALE 1102319134 | 1
EDENVALE 2105469810 | 2
EDENVALE 2105739448 | 2
EL CERRITO G 1105BR316 | 1
EL DORADO PH 210113532 | 1
EL DORADO PH 210119752 | 1
EL DORADO PH 21016852 | 2
EL DORADO PH 210219542 | 1
EL DORADO PH 2102927014 | 1
EL DORADO PH 2102CB | 1
ELECTRA 110136816 | 1
ELECTRA 110161816 | 1
ELECTRA 11017104 | 1
ELECTRA 1101CB | 2
ELK 11014628 | 1
ELK CREEK 11012002 | 5
ELK CREEK 11012004 | 2
ELK CREEK 11012008 | 2
ELK CREEK 1101CB | 1
EMERALD LAKE 0401843236 | 1
FAIRVIEW 2207M500R | 1
FAIRVIEW 2207M501R | 1
FAIRVIEW 2207P150 | 1
FAIRVIEW 2207P302 | 2
FAIRVIEW 2207P304 | 1
FELLOWS 2103CB | 1
FELLOWS 210442100 | 2
FITCH MOUNTAIN 1113154 | 4
FITCH MOUNTAIN 111324550 | 3
FITCH MOUNTAIN 111324918 | 1
FITCH MOUNTAIN 11132955 | 1
FITCH MOUNTAIN 1113356 | 2
FITCH MOUNTAIN 1113443164 | 2
FITCH MOUNTAIN 11134566 | 1
FITCH MOUNTAIN 1113775992 | 3
FITCH MOUNTAIN 1113824468 | 4
FITCH MOUNTAIN 1113CB | 1
FLINT 1101750 | 1
FOOTHILL 1101549904 | 1
FOOTHILL 1101CB | 2
FOOTHILL 110263550 | 1
FOOTHILL 110299432 | 1
FORESTHILL 11011802 | 3
FORESTHILL 110150486 | 1
FORESTHILL 1101CB | 1
FORESTHILL 11022106 | 1
FORESTHILL 1102CB | 1
FORT ORD 21069658 | 2
FORT ROSS 1121134 | 1
FRANKLIN 1104P136 | 1
FREMONT 1104645342 | 1
FREMONT 1104MR584 | 2
FRENCH GULCH 11011464 | 1
FRENCH GULCH 11021462 | 1
FROGTOWN 170113412 | 4
FROGTOWN 1701564780 | 2
FROGTOWN 1701914602 | 2
FROGTOWN 1701CB | 1
FROGTOWN 170211212 | 3
FROGTOWN 170232556 | 4
FROGTOWN 1702423550 | 1
FROGTOWN 1702531640 | 3
FROGTOWN 17027108 | 1
FROGTOWN 1702737236 | 2
FROGTOWN 170274648 | 2
FROGTOWN 170275252 | 5
FROGTOWN 1702902652 | 2
FROGTOWN 1702CB | 1
FRUITLAND 1141CB | 2
FRUITLAND 11426054 | 1
FULTON 1102258281 | 1
FULTON 11024994 | 1
FULTON 1102885254 | 1
GABILAN 11013034 | 3
GABILAN 1101460414 | 4
GABILAN 1101468770 | 2
GABILAN 1101566352 | 2
GANSNER 1101489276 | 2
GANSNER 110152664 | 1
GANSNER 110199388 | 1
GARBERVILLE 11011617 | 3
GARBERVILLE 11011750 | 2
GARBERVILLE 11011770 | 1
GARBERVILLE 11016014 | 1
GARBERVILLE 11026084 | 1
GARBERVILLE 11028652 | 3
GARBERVILLE 1102939030 | 2
GARBERVILLE 1102CB | 1
GERBER 1101CB | 1
GEYSERVILLE 1101166 | 6
GEYSERVILLE 110137454 | 1
GEYSERVILLE 1101480 | 1
GEYSERVILLE 1101482 | 1
GEYSERVILLE 1102350 | 1
GEYSERVILLE 1102429530 | 4
GEYSERVILLE 1102484 | 1
GEYSERVILLE 1102522 | 1
GEYSERVILLE 1102785626 | 2
GEYSERVILLE 110289714 | 2
GIRVAN 11011330 | 2
GIRVAN 1101323094 | 1
GIRVAN 11019732 | 1
GIRVAN 1102296428 | 1
GIRVAN 110280726 | 2
GLENN 110137496 | 3
GOLDTREE 1108961060 | 1
GONZALES 11013094 | 5
GRAND ISLAND 2226292892 | 2
GRASS VALLEY 11012208 | 2
GRASS VALLEY 11032110 | 2
GRASS VALLEY 11032180 | 3
GREEN VALLEY 210111054 | 2
GREEN VALLEY 2101454176 | 1
GREEN VALLEY 2101804170 | 1
GREEN VALLEY 210190860 | 1
GREEN VALLEY 210310932 | 2
GUALALA 111135562 | 1
GUALALA 1112662 | 1
GUSTINE 1102562202 | 6
GUSTINE 11026926 | 2
GUSTINE 1102999258 | 1
HAAS 2101R2770 | 3
HALF MOON BAY 11011741 | 1
HALF MOON BAY 11018940 | 1
HALF MOON BAY 11036014 | 1
HALF MOON BAY 11036115 | 1
HALF MOON BAY 1103869420 | 1
HALSEY 1101173478 | 1
HALSEY 1102CB | 3
HAMILTON A 1101CB | 1
HAMILTON BRANCH 1101161872 | 1
HAMILTON BRANCH 11012046 | 1
HAMILTON BRANCH 110137534 | 1
HAMILTON BRANCH 110190334 | 2
HAMMONDS 1102CB | 2
HARTLEY 1101658 | 1
HARTLEY 1101738 | 2
HARTLEY 1101743866 | 1
HARTLEY 110186876 | 2
HARTLEY 110194178 | 1
HARTLEY 1102841676 | 1
HATTON 110175304 | 1
HATTON 1101CB | 1
HERDLYN 1102608254 | 5
HERDLYN 1102609338 | 1
HERDLYN 1102B569R | 1
HICKS 1112CB | 1
HICKS 1116583284 | 2
HICKS 111660050 | 1
HICKS 1116983580 | 2
HICKS 1116LB16 | 2
HICKS 2101257172 | 3
HICKS 2101510890 | 1
HICKS 2103CB | 1
HICKS 2103LB50 | 2
HICKS 2103XR248 | 1
HICKS 2105954008 | 2
HIGGINS 1103173744 | 2
HIGGINS 110332120 | 3
HIGGINS 110350072 | 2
HIGGINS 11041006 | 1
HIGGINS 1104498932 | 2
HIGGINS 1104663774 | 1
HIGGINS 110950078 | 3
HIGGINS 1109594 | 3
HIGGINS 1110166282 | 1
HIGGINS 11102408 | 2
HIGHLANDS 1102623120 | 3
HIGHLANDS 110265650 | 1
HIGHLANDS 1102CB | 1
HIGHLANDS 1103520 | 3
HIGHLANDS 1103568 | 1
HIGHLANDS 1103726580 | 2
HIGHLANDS 1103CB | 1
HIGHLANDS 110439458 | 1
HIGHLANDS 110448262 | 1
HIGHLANDS 110487040 | 1
HIGHLANDS 1104CB | 1
HOLLISTER 2102113634 | 2
HOLLISTER 2102676164 | 1
HOLLISTER 21044068 | 3
HOLLISTER 21044782 | 1
HOLLISTER 21054018 | 2
HOLLISTER 21054042 | 1
HOLLISTER 21054048 | 1
HOLLISTER 2105475946 | 1
HOLLISTER 2105480430 | 1
HOLLISTER 2106281712 | 1
HOLLISTER 21064004 | 1
HOOPA 11013174 | 3
HOOPA 11013304 | 2
HOOPA 110137202 | 2
HOOPA 110182542 | 2
HOOPA 110193038 | 3
HOOPA 1101CB | 1
HOPLAND 1101154790 | 1
HOPLAND 11014335 | 1
HOPLAND 1101563064 | 1
HOPLAND 1101768 | 2
HOPLAND 110180620 | 2
HOPLAND 1101865263 | 1
HOPLAND 1101CB | 1
HORSESHOE 110150140 | 1
HORSESHOE 110151538 | 1
IGNACIO 11011300 | 1
IGNACIO 11041290 | 2
IGNACIO 1104450582 | 1
IGNACIO 1104469764 | 2
IGNACIO 1105318 | 1
INDIAN FLAT 11045456 | 4
INDIAN FLAT 1104CB | 1
IONE 1101510200 | 2
IONE 1101CB | 1
JACINTO 1101CB | 1
JAMESON 1102865502 | 1
JAMESON 1102CB | 1
JAMESON 1103118944 | 4
JAMESON 1105466348 | 2
JAMESON 1105CB | 1
JARVIS 1101467034 | 2
JARVIS 1108289662 | 1
JARVIS 1111907698 | 1
JESSUP 110141356 | 1
JESSUP 110168362 | 2
JESSUP 11019002 | 2
JESSUP 1102146332 | 1
JESSUP 110262802 | 2
JOLON 11027004 | 2
JOLON 11027040 | 1
JOLON 11027070 | 3
JOLON 1103549180 | 4
JOLON 1103CB | 1
KANAKA 1101713674 | 2
KANAKA 110183288 | 1
KERCKHOFF 1101R308 | 1
KESWICK 11011588 | 1
KESWICK 11019712 | 1
KESWICK 1101CB | 1
KETTLEMAN HILLS 21049020 | 1
KETTLEMAN HILLS 2104CB | 1
KING CITY 1102728782 | 1
KING CITY 11037038 | 5
KONOCTI 11021573 | 1
KONOCTI 1102391062 | 1
KONOCTI 1102716 | 1
KONOCTI 1102948 | 1
KONOCTI 1108950 | 1
LAKEVIEW 11034488 | 1
LAKEVILLE 1102367100 | 1
LAKEVILLE 1102677880 | 1
LAKEWOOD 210738404 | 1
LAKEWOOD 2107474346 | 1
LAKEWOOD 210769586 | 1
LAMMERS 1101932641 | 1
LAMONT 11044222 | 1
LAS POSITAS 2108794616 | 2
LAURELES 1111192764 | 1
LAURELES 11112020 | 2
LAURELES 1111432 | 3
LAURELES 1111822080 | 7
LAURELES 1111CB | 1
LAYTONVILLE 1101364398 | 2
LAYTONVILLE 1101448108 | 1
LAYTONVILLE 1102CB | 2
LE GRAND 111212020 | 1
LINCOLN 1101210168 | 1
LINCOLN 1101CB | 1
LINCOLN 11042070 | 1
LINCOLN 11042072 | 1
LINCOLN 1104685276 | 1
LINCOLN 1104693294 | 2
LINCOLN 1104818790 | 3
LINDEN 11042456 | 1
LIVE OAK 11041300 | 1
LIVE OAK 1104309742 | 1
LLAGAS 2101XR244 | 6
LLAGAS 2101XR586 | 2
LLAGAS 2106338878 | 1
LLAGAS 2107374344 | 2
LOCKEFORD 210212468 | 1
LOGAN CREEK 21022226 | 1
LOGAN CREEK 21022428 | 5
LOGAN CREEK 21022540 | 1
LOGAN CREEK 210262032 | 2
LONE TREE 2105708440 | 1
LONE TREE 2105CB | 2
LOS GATOS 1101865012 | 1
LOS GATOS 1101CB | 1
LOS GATOS 1101LB40 | 1
LOS GATOS 1102526868 | 1
LOS GATOS 1106229258 | 4
LOS GATOS 1106648186 | 3
LOS GATOS 1106848782 | 1
LOS GATOS 1106CB | 1
LOS GATOS 110760092 | 3
LOS GATOS 110760118 | 1
LOS GATOS 1107781232 | 1
LOS GATOS 1108590544 | 2
LOS OSITOS 21011132 | 3
LOS OSITOS 21017014 | 1
LOS OSITOS 21027592 | 1
LOS OSITOS 2103174580 | 1
LOS OSITOS 2103258688 | 2
LOS OSITOS 2103606732 | 2
LOS OSITOS 2103695270 | 1
LOS OSITOS 21037062 | 2
LOS OSITOS 21037086 | 2
LOW GAP 1101750090 | 1
LOW GAP 1101CB | 1
LOYOLA 1102550291 | 3
LOYOLA 110260128 | 1
LUCERNE 110327932 | 1
LUCERNE 1103630 | 1
LUCERNE 110676850 | 1
LUCERNE 1106CB | 1
MADISON 2101117644 | 1
MADISON 21011606 | 3
MADISON 2101168918 | 1
MADISON 2101484892 | 3
MADISON 2101760730 | 2
MADISON 21017702 | 3
MADISON 2101888814 | 1
MADISON 2101CB | 1
MAGUNDEN 1108468940 | 3
MARICOPA 1101931236 | 1
MARICOPA 11023082 | 1
MARIPOSA 210110215 | 2
MARIPOSA 210110240 | 1
MARIPOSA 210110990 | 2
MARIPOSA 2101151918 | 1
MARIPOSA 2101310816 | 4
MARIPOSA 2101752630 | 1
MARIPOSA 21019400 | 1
MARIPOSA 2101CB | 1
MARIPOSA 210210880 | 1
MARIPOSA 21021960 | 2
MARIPOSA 210237282 | 1
MARIPOSA 210237288 | 1
MARIPOSA 2102851902 | 1
MARIPOSA 2102CB | 2
MARTELL 110111244 | 1
MARTELL 110191216 | 1
MARTELL 11033152 | 3
MAXWELL 11023306 | 2
MAXWELL 1102CB | 1
MAXWELL 11053008 | 1
MAXWELL 1105910362 | 1
MC ARTHUR 11011544 | 1
MC ARTHUR 11011546 | 1
MC ARTHUR 110138998 | 3
MC ARTHUR 1101648698 | 3
MC KEE 1103333750 | 1
MC KEE 1107827486 | 1
MC KEE 1111711900 | 3
MCKITTRICK 11011639 | 1
MEADOW LANE 2106970936 | 1
MENDOCINO 1101856020 | 3
MENLO 1102154024 | 1
MENLO 11029110 | 1
MENLO 1103612726 | 1
MENLO 1103866118 | 1
MERCED FALLS 11024000 | 1
MERCED FALLS 1102482838 | 2
MERCED FALLS 110285002 | 4
MERCED FALLS 11029470 | 1
MERIDIAN 1101CB | 1
MERIDIAN 11023502 | 2
MESA 1101CB | 1
MESA 1101M86 | 3
MIDDLETOWN 11014646 | 1
MIDDLETOWN 1101548 | 1
MIDDLETOWN 1101614 | 1
MIDDLETOWN 1101644756 | 1
MIDDLETOWN 1102414 | 1
MIDDLETOWN 1102998 | 3
MIDDLETOWN 1102CB | 2
MIDDLETOWN 1103248100 | 1
MILPITAS 1108342498 | 1
MILPITAS 1109694832 | 1
MILPITAS 1109903328 | 3
MILPITAS 1109XR524 | 1
MIRABEL 1101116 | 1
MIRABEL 1101254 | 1
MIRABEL 1101310814 | 1
MIRABEL 1102206 | 1
MIRABEL 110238514 | 3
MIRABEL 1102CB | 1
MIWUK 1701767890 | 1
MIWUK 170236888 | 1
MIWUK 170238218 | 1
MIWUK 1702667248 | 1
MIWUK 17028130 | 1
MIWUK 1702823548 | 1
MOLINO 1101152 | 1
MOLINO 1101338 | 3
MOLINO 11015042 | 1
MOLINO 1102104 | 1
MOLINO 1102178 | 2
MOLINO 1102384 | 1
MOLINO 1102658 | 1
MOLINO 110266006 | 1
MOLINO 1104368158 | 1
MONROE 210392868 | 1
MONTE RIO 111137520 | 1
MONTE RIO 111164758 | 1
MONTE RIO 1112547 | 1
MONTE RIO 1112CB | 1
MONTE RIO 1113346 | 2
MONTE RIO 11135024 | 1
MONTE RIO 1113524 | 1
MONTE RIO 1113539938 | 1
MONTE RIO 1113CB | 2
MONTICELLO 1101256640 | 1
MONTICELLO 110137384 | 2
MONTICELLO 11014360 | 2
MONTICELLO 1101720 | 1
MORAGA 1101108540 | 1
MORAGA 1101121620 | 1
MORAGA 1104CB | 1
MORAGA 1105CB | 1
MORGAN HILL 2104152774 | 3
MORGAN HILL 2105CB | 1
MORGAN HILL 2105XR152 | 1
MORGAN HILL 2105XR176 | 8
MORGAN HILL 2105XR564 | 1
MORGAN HILL 210653992 | 1
MORGAN HILL 2108XR328 | 3
MORGAN HILL 2109XR104 | 1
MORGAN HILL 2111123422 | 1
MORGAN HILL 2111997000 | 6
MORGAN HILL 2111XR398 | 6
MORRO BAY 1102V84 | 1
MOUNTAIN QUARRIES 21011102 | 2
MOUNTAIN QUARRIES 2101117452 | 3
MOUNTAIN QUARRIES 21011184 | 1
MOUNTAIN QUARRIES 21012422 | 3
N/A | 23
NAPA 1112315244 | 1
NAPA 1112895680 | 1
NARROWS 21011202 | 6
NARROWS 2101307774 | 1
NARROWS 21022728 | 1
NARROWS 210242584 | 2
NARROWS 210248484 | 3
NARROWS 210276952 | 2
NARROWS 2102960916 | 2
NARROWS 21052216 | 4
NARROWS 21052228 | 1
NARROWS 21052426 | 3
NEWMAN 110590430 | 1
NORTH DUBLIN 2101CB | 2
NORTH DUBLIN 2103248212 | 2
NORTH DUBLIN 2103CB | 1
NOTRE DAME 1104176446 | 1
NOTRE DAME 1104CB | 1
NOVATO 110438242 | 4
NOVATO 11046137 | 1
NOVATO 1104676060 | 1
NOVATO 1104889406 | 3
NOVATO 1104CB | 1
OAKHURST 11015490 | 1
OAKHURST 1102333062 | 1
OAKHURST 1103121108 | 1
OAKHURST 11035726 | 1
OAKHURST 110377384 | 1
OAKHURST 1103CB | 1
OAKLAND K 1102CR014 | 1
OAKLAND X 1104438648 | 1
OAKLAND X 1104CR288 | 1
OCEANO 1104Q08 | 1
OCEANO 1104Q10 | 1
OCEANO 1104V36 | 1
OCEANO 1104V38 | 2
OILFIELDS 1103CB | 1
OILFIELDS 1103N42 | 1
OILFIELDS 1103N48 | 2
OLEMA 11011318 | 1
OLEMA 1101359772 | 1
OLEMA 1101435308 | 1
OLETA 1101239062 | 2
OLETA 110163500 | 1
OLETA 1101CB | 2
OLETA 11021228 | 3
OLETA 11022642 | 1
OREGON TRAIL 11021584 | 1
OREGON TRAIL 1102CB | 3
OREGON TRAIL 11031500 | 1
OREGON TRAIL 11041574 | 5
OREGON TRAIL 11041634 | 1
ORICK 1102CB | 1
ORO FINO 11012022 | 1
ORO FINO 11022090 | 2
ORO FINO 11022236 | 3
ORO FINO 110239154 | 1
ORO FINO 110265932 | 2
OROVILLE 110313028 | 1
OROVILLE 1104CB | 1
OTTER 1101440 | 1
OTTER 11022012 | 1
OTTER 11022166 | 1
PALMER 1101M84 | 2
PALMER 1101M88 | 4
PANOCHE 11034010 | 2
PANORAMA 1101CB | 1
PANORAMA 1102280170 | 3
PANORAMA 1102508502 | 2
PARADISE 1104CB | 1
PARADISE 1105829194 | 1
PARADISE 1105CB | 1
PASO ROBLES 1103N54 | 1
PASO ROBLES 1104R12 | 3
PASO ROBLES 1104R56 | 1
PASO ROBLES 1108P10 | 3
PAUL SWEET 2105CB | 1
PAUL SWEET 21065178 | 3
PAUL SWEET 2106607772 | 1
PAUL SWEET 2106CB | 1
PAUL SWEET 2107781810 | 1
PEABODY 210515812 | 1
PEABODY 2105CB | 2
PEABODY 2106CB | 1
PEABODY 21079784 | 1
PEABODY 2108CB | 1
PEABODY 211357908 | 1
PEABODY 2113CB | 2
PEASE 11031226 | 1
PEASE 11041228 | 3
PENNGROVE 1101950828 | 1
PENRYN 11032198 | 1
PENRYN 110351658 | 4
PENRYN 1103604 | 3
PENRYN 1103660 | 2
PENRYN 1105196418 | 2
PENRYN 11052406 | 4
PENRYN 110550548 | 1
PENRYN 110550550 | 1
PENRYN 110551676 | 1
PENRYN 1105680290 | 5
PENRYN 11072704 | 1
PENRYN 11072708 | 1
PENRYN 1107378926 | 1
PEORIA 1701169700 | 1
PEORIA 17013186 | 1
PEORIA 1701349908 | 1
PEORIA 170176030 | 3
PEORIA 170190090 | 4
PEORIA 170459596 | 3
PEORIA 17048040 | 7
PEORIA 1704CB | 2
PEORIA 1705625728 | 1
PEORIA 170567898 | 2
PEORIA 170570198 | 1
PEORIA 170590374 | 1
PERRY 1101200598 | 2
PERRY 1101618168 | 1
PERRY 1101925053 | 1
PERRY 1101CB | 2
PERRY 1101V88 | 3
PERRY 1101W12 | 1
PERRY 1101W52 | 1
PERRY 1104175422 | 1
PETALUMA C 1108208 | 1
PETALUMA C 1108600 | 1
PETALUMA C 1108618 | 1
PETALUMA C 1108632 | 1
PETALUMA C 1108636 | 1
PHILO 11013700 | 2
PHILO 1101431952 | 1
PHILO 1101CB | 1
PHILO 1102920 | 1
PHILO 1102CB | 1
PIERCY 2110799154 | 3
PIKE CITY 11011730 | 1
PINE GROVE 1101580912 | 1
PINE GROVE 11021222 | 2
PINE GROVE 1102269286 | 1
PINE GROVE 11023168 | 1
PINE GROVE 11023172 | 4
PINE GROVE 11024088 | 1
PIT NO 1 11011552 | 2
PIT NO 1 11019702 | 1
PIT NO 1 1101CB | 2
PIT NO 3 21011360 | 2
PIT NO 3 21011480 | 1
PIT NO 5 11011658 | 3
PIT NO 5 1101884224 | 1
PLACER 1102CB | 3
PLACER 1103284874 | 1
PLACERVILLE 111219712 | 1
PLACERVILLE 21061104 | 1
PLACERVILLE 210611132 | 4
PLACERVILLE 21061792 | 1
PLACERVILLE 210619552 | 1
PLACERVILLE 21062224 | 3
PLACERVILLE 2106560252 | 1
PLACERVILLE 2106654798 | 2
PLACERVILLE 21067522 | 2
PLACERVILLE 2106935216 | 1
PLACERVILLE 21069712 | 2
PLACERVILLE 2106CB | 1
POINT ARENA 11013702 | 1
POINT MORETTI 110112122 | 1
POINT MORETTI 110135874 | 2
POINT MORETTI 11015078 | 1
POSO MOUNTAIN 21012181 | 1
POSO MOUNTAIN 2101535138 | 2
POSO MOUNTAIN 2101720132 | 1
POSO MOUNTAIN 2101730862 | 1
POSO MOUNTAIN 2101CB | 1
POSO MOUNTAIN 2103CB | 2
POSO MOUNTAIN 210448268 | 2
POTTER VALLEY P H 11051904 | 3
POTTER VALLEY P H 110537476 | 3
POTTER VALLEY P H 110576498 | 1
POTTER VALLEY P H 110595878 | 1
PUEBLO 1105348368 | 3
PUEBLO 1105426584 | 1
PUEBLO 2102279478 | 1
PUEBLO 2102378860 | 1
PUEBLO 2102618 | 2
PUEBLO 2102698 | 1
PUEBLO 21031970 | 1
PUEBLO 2103489964 | 2
PUEBLO 2103694 | 1
PUEBLO 210375612 | 1
PUEBLO 210378504 | 1
PUEBLO 210398394 | 3
PUEBLO 2103CB | 1
PUEBLO 210438686 | 5
PUEBLO 2104600010 | 1
PUEBLO 2104741958 | 2
PURISIMA 1101104948 | 1
PURISIMA 110154728 | 1
PUTAH CREEK 11038362 | 2
PUTAH CREEK 110546162 | 2
PUTAH CREEK 11058812 | 1
RACETRACK 170310850 | 1
RACETRACK 170311270 | 1
RACETRACK 1703CB | 1
RACETRACK 1704787277 | 1
RALSTON 110148936 | 1
RALSTON 11022028 | 1
RALSTON 11029126 | 1
RALSTON 1102CB | 1
RED BLUFF 11011556 | 2
RED BLUFF 1101453972 | 1
RED BLUFF 110185837 | 1
RED BLUFF 1103234278 | 1
RED BLUFF 1103CB | 1
RED BLUFF 11041302 | 2
RED BLUFF 11041630 | 2
RED BLUFF 11044965 | 1
RED BLUFF 110451238 | 1
RED BLUFF 11051564 | 2
RED BLUFF 110585632 | 1
REDBUD 1101CB | 1
REDBUD 1102432 | 3
REDBUD 1102922 | 2
REEDLEY 11127240 | 3
RESEARCH 210263274 | 2
RESEARCH 2102644462 | 1
RESERVATION ROAD 110123818 | 1
RESERVATION ROAD 1101370948 | 1
RESERVATION ROAD 1101383718 | 4
RESERVATION ROAD 110222136 | 1
RESERVATION ROAD 1102741002 | 1
RICE 1103CB | 1
RINCON 1101205854 | 1
RINCON 1101576 | 2
RINCON 1103198 | 1
RINCON 1104CB | 1
RIO DELL 110275970 | 1
RIO DELL 11041504 | 1
RISING RIVER 11019032 | 2
RISING RIVER 1101CB | 1
ROB ROY 210410298 | 1
ROB ROY 210410714 | 3
ROB ROY 210410954 | 1
ROB ROY 210410960 | 1
ROB ROY 2104422016 | 1
ROB ROY 210458988 | 1
ROB ROY 210467520 | 1
ROB ROY 210538430 | 1
ROB ROY 210571630 | 1
ROSSMOOR 110181770 | 2
ROSSMOOR 1102457174 | 1
ROSSMOOR 1106L552R | 1
ROSSMOOR 1108180088 | 1
SALMON CREEK 1101196 | 2
SALT SPRINGS 21023118 | 1
SAN ARDO 11017094 | 1
SAN ARDO 11027030 | 2
SAN ARDO 11027107 | 1
SAN ARDO 110291894 | 1
SAN ARDO 1102CB | 1
SAN BENITO 2101355426 | 1
SAN BENITO 210488772 | 3
SAN CARLOS 1103586832 | 2
SAN CARLOS 11039148 | 1
SAN JOAQUIN #3 1101CB | 1
SAN JOAQUIN #3 1103374484 | 3
SAN JOAQUIN #3 1103403515 | 2
SAN JUSTO 110136902 | 3
SAN JUSTO 11014002 | 1
SAN LUIS OBISPO 1103V82 | 1
SAN LUIS OBISPO 1104777686 | 1
SAN LUIS OBISPO 1104V40 | 1
SAN LUIS OBISPO 1104V46 | 1
SAN LUIS OBISPO 1107CB | 1
SAN LUIS OBISPO 1107V02 | 1
SAN LUIS OBISPO 1107V58 | 2
SAN MIGUEL 1106605393 | 2
SAN MIGUEL 1106N34 | 1
SAN MIGUEL 1107608338 | 2
SAN MIGUEL 1107R66 | 2
SAN RAFAEL 11011210 | 1
SAN RAFAEL 1101CB | 1
SAN RAFAEL 1104717160 | 1
SAN RAFAEL 1104CB | 1
SAN RAFAEL 1105194366 | 3
SAN RAFAEL 1105645362 | 1
SAN RAFAEL 11071166 | 1
SAN RAFAEL 1107CB | 1
SAN RAFAEL 11081262 | 1
SAN RAFAEL 1108516 | 2
SAN RAFAEL 1108583502 | 1
SAN RAFAEL 1109418 | 1
SAN RAFAEL 1109692576 | 1
SAN RAMON 2101CB | 1
SAN RAMON 2103MR279 | 2
SAN RAMON 2106MR285 | 2
SAN RAMON 2107MR284 | 1
SAN RAMON 2107MR441 | 1
SAN RAMON 2108CB | 2
SAN RAMON 2119CB | 1
SAND CREEK 1103416018 | 1
SAND CREEK 11037110 | 1
SAND CREEK 11037140 | 2
SAND CREEK 11037992 | 1
SAND CREEK 1103818064 | 4
SANGER 110864662 | 2
SANGER 1108R544 | 1
SANTA MARIA 1108M18 | 2
SANTA MARIA 1108M80 | 2
SANTA NELLA 11049660 | 1
SANTA ROSA A 1104991788 | 1
SANTA ROSA A 1111758024 | 1
SANTA ROSA A 1111907192 | 1
SANTA YNEZ 1101277014 | 1
SANTA YNEZ 1101673618 | 1
SANTA YNEZ 1101Y52 | 3
SANTA YNEZ 1102320270 | 2
SANTA YNEZ 11026149 | 4
SANTA YNEZ 1102Y18 | 1
SANTA YNEZ 110477098 | 1
SANTA YNEZ 1104Y04 | 2
SARATOGA 1106340986 | 1
SARATOGA 1106408318 | 1
SARATOGA 11075696 | 3
SARATOGA 1107667000 | 1
SARATOGA 1107899344 | 1
SHADY GLEN 11012768 | 2
SHADY GLEN 110151696 | 1
SHADY GLEN 1101941844 | 2
SHADY GLEN 11022232 | 2
SHADY GLEN 110248894 | 1
SHADY GLEN 1102CB | 1
SHEPHERD 2111327814 | 1
SHEPHERD 2111707358 | 1
SHINGLE SPRINGS 11038752 | 1
SHINGLE SPRINGS 1104556218 | 4
SHINGLE SPRINGS 1104CB | 1
SHINGLE SPRINGS 210511172 | 2
SHINGLE SPRINGS 210551738 | 1
SHINGLE SPRINGS 210819622 | 1
SHINGLE SPRINGS 2108449638 | 1
SHINGLE SPRINGS 210911092 | 1
SHINGLE SPRINGS 210912392 | 1
SHINGLE SPRINGS 210913322 | 6
SHINGLE SPRINGS 210961892 | 2
SHINGLE SPRINGS 210981390 | 2
SHINGLE SPRINGS 211051790 | 1
SHINGLE SPRINGS 211051800 | 1
SHINGLE SPRINGS 2110634118 | 1
SHINGLE SPRINGS 2110CB | 1
SILVERADO 21021607 | 5
SILVERADO 21023010 | 2
SILVERADO 210234959 | 2
SILVERADO 210258626 | 1
SILVERADO 2102714 | 1
SILVERADO 2102772792 | 1
SILVERADO 2102914108 | 1
SILVERADO 2102922022 | 1
SILVERADO 2102942170 | 3
SILVERADO 2102CB | 1
SILVERADO 2103507513 | 3
SILVERADO 2103617828 | 1
SILVERADO 2103CB | 3
SILVERADO 2104106272 | 2
SILVERADO 2104324994 | 2
SILVERADO 210437632 | 1
SILVERADO 2104633600 | 1
SILVERADO 2104773670 | 1
SILVERADO 210478268 | 1
SILVERADO 2104909390 | 1
SILVERADO 2104940 | 1
SILVERADO 2104959428 | 2
SILVERADO 2105131568 | 1
SILVERADO 2105167360 | 2
SILVERADO 2105394844 | 1
SILVERADO 2105658898 | 1
SILVERADO 2105861266 | 3
SISQUOC 11022017 | 1
SISQUOC 1102846970 | 1
SISQUOC 1102M26 | 7
SISQUOC 1102M52 | 7
SISQUOC 1103858898 | 1
SMARTVILLE 1101CB | 1
SNEATH LANE 11016525 | 1
SNEATH LANE 1106CB | 2
SOBRANTE 110142914 | 1
SOBRANTE 1101CB | 1
SOBRANTE 1102690098 | 3
SOBRANTE 1103CB | 1
SOBRANTE 1103LA401R | 2
SOLEDAD 2101107872 | 3
SOLEDAD 2102304826 | 1
SOLEDAD 21027008 | 1
SOLEDAD 2102858388 | 1
SONOMA 1102441730 | 1
SONOMA 11033052 | 1
SONOMA 11033138 | 2
SONOMA 1103470636 | 1
SONOMA 110478372 | 1
SONOMA 1104914376 | 2
SONOMA 1105138 | 1
SONOMA 1105539450 | 1
SONOMA 1107844168 | 1
SPAULDING 1101578852 | 2
SPENCE 1102276712 | 3
SPENCE 1104965598 | 1
SPRING GAP 170210720 | 1
SPRING GAP 17029690 | 1
STAFFORD 11011082 | 1
STAFFORD 1101902998 | 1
STAFFORD 11021202 | 2
STAFFORD 11021258 | 1
STAFFORD 1102361952 | 1
STANISLAUS 17017144 | 1
STANISLAUS 170179826 | 6
STANISLAUS 1701862450 | 2
STANISLAUS 17021850 | 4
STANISLAUS 1702247448 | 1
STANISLAUS 170237276 | 1
STELLING 110913228 | 1
STELLING 111060094 | 2
STELLING 1110LL72 | 1
STELLING 1111LM10 | 1
STILLWATER 1101747294 | 1
STILLWATER 11021466 | 1
STILLWATER 110248952 | 1
STILLWATER 1102828624 | 1
STONE CORRAL 1108CB | 1
STONE CORRAL 1110975698 | 1
STOREY 1109272650 | 2
STOREY 11095200 | 1
SUMMIT 110249484 | 1
SUNOL 1101298061 | 1
SUNOL 1101605520 | 1
SUNOL 1101904308 | 1
SWIFT 2102889948 | 1
SWIFT 2107XR526 | 1
SWIFT 2109XR300 | 1
SWIFT 2110853720 | 1
SWIFT 2110XR254 | 1
SWIFT 2110XR366 | 4
SYCAMORE CREEK 11112602 | 1
TAFT 11033068 | 1
TAMARACK 1101291312 | 1
TAR FLAT 0402327672 | 1
TASSAJARA 2104967234 | 3
TASSAJARA 2108846900 | 6
TASSAJARA 2109CB | 2
TASSAJARA 2112925966 | 4
TASSAJARA 2112CB | 1
TEJON 11023751 | 1
TEJON 1103145334 | 1
TEJON 1103286542 | 1
TEJON 11062436 | 1
TEJON 1106382086 | 1
TEMBLOR 1104284004 | 2
TEMPLETON 2108A64 | 2
TEMPLETON 2109R78 | 1
TEMPLETON 2109R92 | 1
TEMPLETON 21102675 | 1
TEMPLETON 2110307832 | 1
TEMPLETON 2110317796 | 2
TEMPLETON 2110901690 | 7
TEMPLETON 2110941946 | 2
TEMPLETON 2110R94 | 2
TEMPLETON 2111461692 | 4
TEMPLETON 2111514592 | 1
TEMPLETON 2111A66 | 2
TEMPLETON 2111R86 | 1
TEMPLETON 2113175566 | 4
TEMPLETON 211318370 | 3
TEMPLETON 2113205874 | 1
TEMPLETON 2113520924 | 1
TEMPLETON 2113641367 | 3
TEMPLETON 2113A08 | 2
TEMPLETON 2113A10 | 1
TEMPLETON 2113A12 | 2
TEMPLETON 2113A20 | 1
TEMPLETON 2113A24 | 2
TEMPLETON 2113A70 | 6
TEMPLETON 2113CB | 3
TEMPLETON 2113R82 | 1
TIDEWATER 210657926 | 1
TIDEWATER 2106C514R | 1
TIGER CREEK 0201320746 | 1
TIVY VALLEY 11067150 | 1
TIVY VALLEY 1107248306 | 1
TIVY VALLEY 1107599142 | 1
TIVY VALLEY 1107718068 | 1
TIVY VALLEY 11077380 | 2
TIVY VALLEY 1107822606 | 3
TIVY VALLEY 1107869946 | 1
TRES PINOS 1111203126 | 1
TULUCAY 1101504524 | 3
TYLER 11051704 | 3
TYLER 1105503690 | 1
UKIAH 1114380432 | 2
UKIAH 1114408 | 1
UKIAH 1114822 | 1
UKIAH 1115899594 | 1
UPPER LAKE 110142378 | 1
UPPER LAKE 110175370 | 1
UPPER LAKE 1101861806 | 1
VACAVILLE 1103CB | 3
VACAVILLE 1104CB | 2
VACAVILLE 1108341974 | 1
VACAVILLE 110847860 | 2
VACAVILLE 1108530880 | 2
VACAVILLE 11088762 | 1
VACAVILLE 1109592742 | 1
VACAVILLE 1109799940 | 1
VALLEY HOME 17031532 | 1
VALLEY HOME 17031558 | 1
Valley Springs 1101207256 | 2
Valley Springs 1102606522 | 1
Valley Springs 1102748874 | 1
VALLEY VIEW 1103P158 | 2
VALLEY VIEW 1105305072 | 2
VALLEY VIEW 1105P190 | 1
VALLEY VIEW 1106CB | 1
VASCO 1102546328 | 1
VINA 11011570 | 1
VINEYARD 2107CB | 2
VINEYARD 2107MR332 | 1
VINEYARD 2108609690 | 1
VINEYARD 2108MR172 | 5
VOLTA 11011516 | 1
VOLTA 11011596 | 1
VOLTA 110149742 | 1
VOLTA 1101519282 | 1
VOLTA 110153118 | 3
VOLTA 1101914816 | 2
VOLTA 1101CB | 1
VOLTA 11021650 | 1
VOLTA 110254932 | 5
VOLTA 11029742 | 1
WAHTOKE 11087570 | 1
WEIMAR 11012058 | 1
WEIMAR 11012764 | 1
WEIMAR 1101CB | 1
WEST POINT 110112256 | 1
WEST POINT 110113444 | 1
WEST POINT 11024788 | 3
WEST POINT 110272036 | 1
WEST POINT 1102CB | 3
WESTLEY 1103237522 | 1
WESTLEY 11039010 | 4
WHEATLAND 11041348 | 1
WHEATLAND 1105248490 | 3
WHITMORE 11012211 | 1
WILDWOOD 11011454 | 1
WILDWOOD 11011576 | 1
WILLIAMS 110230232 | 1
WILLITS 1103409216 | 2
WILLITS 1103538 | 1
WILLITS 1103696 | 1
WILLITS 1103826 | 2
WILLITS 110391810 | 1
WILLITS 110391948 | 2
WILLITS 1103964 | 1
WILLITS 1103966 | 1
WILLOW CREEK 11013050 | 1
WILLOW CREEK 11014904 | 1
WILLOW CREEK 11015002 | 1
WILLOW CREEK 11032936 | 1
WILLOW CREEK 11037514 | 1
WILLOW PASS 2108328308 | 1
WILSON 1103291366 | 1
WILSON 11039080 | 2
WINDSOR 11035060 | 4
WISE 1101CB | 1
WISE 11022054 | 2
WISE 11022234 | 2
WISE 1102307494 | 1
WISE 1102697216 | 1
WOODACRE 110191900 | 2
WOODSIDE 110147872 | 2
WOODSIDE 110179892 | 2
WOODSIDE 11018522 | 3
WOODSIDE 11018884 | 1
WOODSIDE 11018972 | 2
WOODSIDE 11018974 | 4
WOODSIDE 1104520832 | 3
WOODSIDE 11049032 | 1
WOODSIDE 11049116 | 2
WRIGHT 111084280 | 1
WRIGHT 1110CB | 1
WYANDOTTE 110213916 | 1
WYANDOTTE 1103640652 | 1
WYANDOTTE 1103716082 | 1
WYANDOTTE 1105329930 | 1
WYANDOTTE 11071026 | 2
WYANDOTTE 11071510 | 1
WYANDOTTE 110737472 | 1
WYANDOTTE 110777578 | 2
WYANDOTTE 1107CB | 2
WYANDOTTE 1109758802 | 1
WYANDOTTE 1109759354 | 3
WYANDOTTE 110979932 | 2
WYANDOTTE 1110747922 | 1
ZACA 1101CB | 1
ZACA 1101Y72 | 2
ZACA 1102CB | 2
ZACA 1102Y48 | 2
ZACA 1102Y54 | 1
Grand Total | 2405

## CPZs
CPZ | EPSS_Device_Global_ID
AIRWAYS 1107671922 | {699F35EF-CD23-41E8-B6FA-12DF53887A19}
AIRWAYS 1107752346 | {B45EE5FC-838A-44D6-87B3-CB4EE322C116}
AIRWAYS 1107CB | {C0A78F81-F1CA-4A4F-B49A-0AE0914F21F5}
AIRWAYS 1107R1250 | {D2E48662-0010-463C-89AD-F2F63DA51E65}
AIRWAYS 1107R1426 | {9AC710E6-8A8D-4E77-8534-B51181066B47}
ALHAMBRA 1101CB | {8AE2EF2A-3822-4BB8-8505-AA1FB37F605D}
ALHAMBRA 110213333 | {CC913DB3-6A51-493D-BE11-D5EAF399B0A8}
ALHAMBRA 110281034 | {6B94D9C9-A215-4C1F-B682-652037A86205}
ALHAMBRA 1102CB | {CC913DB3-6A51-493D-BE11-D5EAF399B0A8}
ALHAMBRA 1105295792 | {8C6CE5F6-5F2A-4876-BD0D-A2DA021CCAD3}
ALHAMBRA 110581514 | {AC26085C-F280-4A6A-A0D9-361E1E9983F9}
ALHAMBRA 110582622 | {43B3FCFC-E570-42A3-9958-1934EF46169A}
ALHAMBRA 110582622 | {2DD5AD9E-82A0-40E3-9440-AC94C1A7128E}
ALHAMBRA 11058302 | {09B35F29-6F1B-4C76-9517-956EDF4EF867}
ALHAMBRA 11058302 | {EAE1D7B0-E463-4F79-B04B-CDCA7EEEF36C}
ALHAMBRA 110595016 | {9A4542AE-EE8F-4BB7-BE2E-76002D6DCF25}
ALHAMBRA 1105CB | {36DDF29F-B22D-4B8A-AF4A-BB933D5333CF}
ALLEGHANY 1101183068 | {F078E4AC-B64C-461C-A921-5985B3E5BCBB}
ALLEGHANY 1101804 | {FD15787C-9E6A-4119-888E-7A4D03372AC4}
ALLEGHANY 1101806 | {F534F342-21BA-4355-A014-C411F19E4970}
ALLEGHANY 1101808 | {A284EBFC-892C-41D6-A2C0-D7253C0FC922}
ALLEGHANY 1101978 | {3479738B-50FC-4140-94A7-E159A76AE25B}
ALLEGHANY 1101CB | {326E3BAE-F690-4463-8FFC-C774FBAA59CE}
ALLEGHANY 1101DV 1101/2 | {A284EBFC-892C-41D6-A2C0-D7253C0FC922}
ALLEGHANY 1101SC 1101/2 | {FD15787C-9E6A-4119-888E-7A4D03372AC4}
ALLEGHANY 1101VR816 | {A284EBFC-892C-41D6-A2C0-D7253C0FC922}
ALLEGHANY 1102CB | {303E53EF-22EF-468F-BD54-C029D47A56AA}
ALLEGHANY 1102WC 1101/2 | {303E53EF-22EF-468F-BD54-C029D47A56AA}
ALPINE 1101CB | {147B95CE-2512-4395-8036-5E41FB98DF5E}
ALTO 11201214 | {3BFC9BC6-5EFD-4D57-B09B-83E9EA9F84AE}
ALTO 112019262 | {698E995F-28A3-47DF-9838-EFB3793E33D7}
ALTO 1120500 | {E6E93162-4459-4248-A579-2775F57735F8}
ALTO 112087204 | {698E995F-28A3-47DF-9838-EFB3793E33D7}
ALTO 112088190 | {FB7430F5-69AD-42E3-8B5B-42F0E8A7B1F0}
ALTO 1120CB | {D4FBBC03-A778-4C54-9456-3A890F4850F6}
ALTO 1121137664 | {F8ED8086-0E7D-4BB7-85C2-CAA1D3DA55CE}
ALTO 1121508 | {F8ED8086-0E7D-4BB7-85C2-CAA1D3DA55CE}
ALTO 112191428 | {987386B4-3AF7-40EE-94AC-C1508EDFA8F3}
ALTO 1121CB | {AC60738C-EEA0-4867-B6FF-D969AE620995}
ALTO 11221212 | {480E1BDA-E928-4338-A7BA-DDA1B7A106EF}
ALTO 11221260 | {7808A995-1603-4DBC-94EF-C3DF7EAAE7DD}
ALTO 11221260 | {D90E1E5B-095C-40EA-8C33-94BE6207ACAA}
ALTO 11223897 | {9C5DD07F-FD14-472A-A32B-CEF63645989D}
ALTO 1122591122 | {E26D9B6D-6B45-4494-94E9-E5BD7162DD89}
ALTO 112265474 | {C2F314B0-1B7A-4CC5-862B-042BD22A1A33}
ALTO 112278672 | {7DD6C0DE-19A6-4180-A610-1E9856610C4D}
ALTO 1122CB | {F8F75874-EBBE-4BAE-AEB7-B4201B2B809B}
ALTO 11231222 | {52729A7B-7BFA-4980-A850-5BD8CF10E4D2}
ALTO 112332448 | {C469F866-3A91-4B43-94B4-8116C5F6A5C8}
ALTO 1123CB | {727BD7F2-BE7C-4A08-9D75-7C070423C0FA}
ALTO 1123CB | {C4F18DDE-7DF7-43C4-9D20-1B47C5ED6CA4}
ALTO 1124207690 | {863408D9-1A75-4C4A-9595-1FB728D819F1}
ALTO 1124246034 | {7D95830D-A648-4B7C-9FF3-8B171C1CA56A}
ALTO 11243117 | {98215F20-19FF-4047-B9C6-AC6BA0563184}
ALTO 11243121 | {5B9950E9-6C0C-44EE-B414-F2773560C367}
ALTO 11243745 | {5A7E1969-E475-4A2E-A5C6-85EFB5802FE4}
ALTO 1124428 | {27199B13-B86B-4E3B-B3CA-CB9918D6CC38}
ALTO 1124428 | {09C55786-AE16-446A-A4CF-3ACE21BE3C26}
ALTO 1124428 | {16B78F6F-5719-4A1D-9210-ED6B09C6C185}
ALTO 1124428 | {84CE664B-0611-4200-83BA-04B0E42A1B56}
ALTO 1124430 | {5B9950E9-6C0C-44EE-B414-F2773560C367}
ALTO 1124432 | {5A7E1969-E475-4A2E-A5C6-85EFB5802FE4}
ALTO 1124635972 | {09E5B2C8-C5E7-4FCA-92E9-55DF7D2FE60B}
ALTO 1124703432 | {60AD6E98-4C8E-4B03-A21E-57588A85616E}
ALTO 1124810594 | {D958A2D4-CE6E-4B3C-AC0F-6AE22C6D92E7}
ALTO 1124870444 | {856EAD72-BC3F-4C54-B04F-3629A4B87A87}
ALTO 1124CB | {2C543D7C-5902-4DC9-BE9B-719A66315791}
ALTO 1124CB | {B1454119-63A8-48AF-9377-F24B23472EF9}
ALTO 1124CB | {5017D9D5-0257-4525-9036-FC54DCC8E2D0}
ALTO 11251158 | {230CA050-BA1E-4373-AB59-B01CD2906F80}
ALTO 11251158 | {DC93F2BF-1FFD-4AAB-B042-E35ACAAAB3A8}
ALTO 11251226 | {E82C2F97-5C09-4976-BD47-A486EC875FA4}
ALTO 11251256 | {68422AE1-2121-4A4F-B961-26CF0C3DA27B}
ALTO 1125296476 | {0ECD6D03-E99B-4280-9CB5-4AEDBF369158}
ALTO 1125510 | {3D1372A7-8F04-4F4C-824F-7EEDAB15603F}
ALTO 1125530664 | {DA893851-A239-41E8-8E7B-70F066561313}
ALTO 11256405 | {DA893851-A239-41E8-8E7B-70F066561313}
ALTO 1125902 | {A0846B72-320F-48B2-9E0D-A5F9C3A78393}
ALTO 1125902 | {F0017B1D-08AA-44FE-9A3F-CDBC16DA0E27}
ALTO 1125CB | {F6FBF85B-F199-40F3-8A70-868561B74EE6}
ANDERSON 11011390 | {F53F100A-A47D-4F77-AE95-9A2266045C73}
ANDERSON 11011752 | {E71E97E5-7CA9-434D-BB6A-304C5D96B11A}
ANDERSON 1101337668 | {4FF91FEF-C966-4E36-B08B-C812EFC4BE16}
ANDERSON 1101514412 | {4FF91FEF-C966-4E36-B08B-C812EFC4BE16}
ANDERSON 1101583708 | {C1AE4ED5-9E2B-4787-958E-F3CEA46DF77D}
ANDERSON 1101810804 | {5720837F-AF3C-4D19-9FD1-A4D55662D2CC}
ANDERSON 1101909424 | {4FF91FEF-C966-4E36-B08B-C812EFC4BE16}
ANDERSON 1101CB | {4FF91FEF-C966-4E36-B08B-C812EFC4BE16}
ANDERSON 1101CB | {A21FB6E2-C2EE-4D2F-B401-72361201D9F9}
ANDERSON 11029792 | {F240E67E-FE6C-498C-BF9F-54CAA8C204DD}
ANDERSON 110299392 | {82EAFCF1-F1E6-41E8-A0B3-25F73ADE0F7A}
ANDERSON 1102CB | {4CF4EB85-76D9-4518-B772-23773872AF10}
ANDERSON 11031600 | {38F7B678-11EB-498C-AD48-774BD4B8786F}
ANDERSON 1103193378 | {00748604-4E7C-487B-992B-00C51AC005AF}
ANDERSON 1103226050 | {F12B9CD1-046D-40CE-8D1D-9858A5F6226D}
ANDERSON 1103625006 | {2202852F-03C4-41E3-B139-E2377399FC2A}
ANDERSON 1103721690 | {53A9B8B1-BFDE-47C9-97AE-1322DE96BE54}
ANDERSON 1103CB | {87B1630C-320C-4426-9018-625251B99E73}
ANITA 1105110976 | {3EFD1E32-C502-4A40-8351-D4C9EEC84A29}
ANITA 11062074 | {F3D6F39A-52C7-4EF2-B536-42290D3060B9}
ANITA 11062418 | {BF1D640B-1AB6-49FB-AB3D-0A09BCB77224}
ANITA 11062462 | {B21854B4-082A-4DCD-AEF9-3CC73D3BD93D}
ANITA 11062496 | {CA64925E-CB77-4A47-8864-C246E9A1F937}
ANITA 110648098 | {B21854B4-082A-4DCD-AEF9-3CC73D3BD93D}
ANITA 1106552724 | {66BDFA7D-F7B6-403B-BF76-C55BF0419221}
ANITA 1106CB | {89E1C548-ADAA-4B04-80A4-5DCCECCCDB3E}
ANNAPOLIS 1101202158 | {8CD49C37-5159-470E-8F4C-B96EC53C83B1}
ANNAPOLIS 11014577 | {74D97DAC-3757-437C-9FF1-D70630E201C4}
ANNAPOLIS 11014585 | {A6AF7951-6A66-4E7F-8BA2-7E906C001184}
ANNAPOLIS 11014597 | {E1C27A8E-E34E-4807-8D2C-EA452D1B7FBF}
ANNAPOLIS 1101528344 | {7D61C9A3-0A8E-455B-9684-CECD384B35D0}
ANNAPOLIS 1101528344 | {BBF5959F-6ADA-4D26-8318-2B0FB4D319D8}
ANNAPOLIS 11016073 | {33DAB4F4-5EB0-4873-8ABE-9C2FCFBBE565}
ANNAPOLIS 110176842 | {2E3AB06D-E271-44D1-BCDE-8DE501692F34}
ANNAPOLIS 1101CB | {26E5272A-CBC3-4332-B0D6-5C00B9086880}
ANTELOPE 11011631 | {F610032A-F2E0-4366-8F75-D3F075E51CA8}
ANTELOPE 11012656 | {0223D8A4-0FAE-4E90-8B93-4043739FD071}
ANTELOPE 1101318686 | {946AC549-8FBD-4BEB-87DA-8E29BFBBE9D4}
ANTELOPE 11013609 | {F610032A-F2E0-4366-8F75-D3F075E51CA8}
ANTELOPE 1101CB | {71672BA6-4FC5-4F1A-9DC4-9818F13C90C3}
ANTELOPE 1102809584 | {CB97938A-1CC5-47B5-86BD-A8F931D99B70}
ANTELOPE 1102CB | {C3268251-FFC0-4729-94B8-55800124A207}
ANTELOPE 1102CUS5485 | {CB97938A-1CC5-47B5-86BD-A8F931D99B70}
ANTLER 11011376 | {C9530905-CD21-41F4-B554-42FC45B1FB4F}
ANTLER 11011376 | {96A0A843-7251-461B-B57C-57ECCA82B23A}
ANTLER 11011384 | {C5E3EE8D-D562-41BA-8596-EEF5987F2F11}
ANTLER 11011612 | {EAAD5F12-9AE3-4341-A497-B18C1046E2B5}
ANTLER 1101671078 | {06D2F196-2635-44B3-B616-380DADBEF83C}
ANTLER 1101671078 | {F4B3B428-AF10-428A-86EF-E870D3B14484}
ANTLER 1101671078 | {0E4C50F8-B230-44E8-8D9C-7286CD8064DE}
ANTLER 1101671078 | {8E148904-632C-4897-8A4C-68D035CA5B54}
ANTLER 1101718316 | {4413B493-DE83-49E8-BEE8-12AA31A465DE}
ANTLER 1101CB | {5E7DC64A-0B4A-4299-87CB-EE1D39916B3F}
APPLE HILL 110312097 | {B8A75F8D-21E1-43F4-9CA8-4293D8B45C51}
APPLE HILL 11031311 | {1B093AE4-9CE5-4514-9035-2EB6942DD0A2}
APPLE HILL 110313312 | {4D62B52A-6FFC-40E3-9CBB-F053155CEAAC}
APPLE HILL 11038412 | {07722CD6-14E4-4447-AD94-AC55195AC8E1}
APPLE HILL 1103CB | {DD461B3A-397C-4A3A-A4DD-6F0A05715903}
APPLE HILL 110412832 | {1553DCA8-0228-4053-AA0E-5DC75B4B0E18}
APPLE HILL 110412842 | {04FA73EB-B797-476B-86A7-C1CFAD605BCA}
APPLE HILL 110413512 | {A3A7F5CC-9E45-4A1C-ADC2-13C82D28F975}
APPLE HILL 110413512 | {2CED8BE1-6338-42D0-A2DE-4B39ED30BDA5}
APPLE HILL 110413512 | {C961DA87-D3C6-40FA-87BC-1A5AB7DF3FCD}
APPLE HILL 1104236062 | {78CB65A8-D5F1-4141-9775-453719688C2B}
APPLE HILL 1104275024 | {60D1E266-474C-4944-877D-C3B4C2A1D233}
APPLE HILL 1104814656 | {E9B2D551-2CAF-489B-9D1C-4D1BCFDB0559}
APPLE HILL 110497086 | {E9B2D551-2CAF-489B-9D1C-4D1BCFDB0559}
APPLE HILL 110497086 | {7A7E63E4-F688-4EFA-9C2A-128D65F363D3}
APPLE HILL 110497086 | {70A5FDF1-D752-4981-A4F6-51478D7FB5C0}
APPLE HILL 110497086 | {3367D5C5-8359-4C3E-83AD-C940808FEEBA}
APPLE HILL 110497086 | {84B18874-411C-472A-8D15-24AC466796F6}
APPLE HILL 110497086 | {F15F9881-A54B-48D4-824E-69DF9C8D6BAD}
APPLE HILL 110497086 | {2D7A6BD8-8AC9-477E-9801-B1A21ECB84A5}
APPLE HILL 110497086 | {B8655369-329A-44D8-BC3C-EE1BD7F8F1A6}
APPLE HILL 1104CB | {C95685B7-B649-4BB7-AFD8-6C20EE89F893}
APPLE HILL 2102124050 | {679E3FFB-DC7A-4A32-B0F8-8E2206389F5B}
APPLE HILL 21021532 | {9C4905F1-5CAF-4EA3-AEC8-7E33B8AB07B0}
APPLE HILL 21021532 | {4A1B7FA4-9EA2-489A-952B-02F0D69E191E}
APPLE HILL 21021532 | {42888C76-1C24-4534-8952-ACB552DA1F96}
APPLE HILL 2102186912 | {F16EB94A-D353-463E-A791-8C9D54574309}
APPLE HILL 2102186912 | {E5CCD6CB-B684-43B9-9D77-BACF4A9F8791}
APPLE HILL 2102186912 | {91ECE238-710F-4C4F-A561-52ADF6AC65F6}
APPLE HILL 2102186912 | {85D8469B-D450-488F-A1B7-8A871E2BBDDB}
APPLE HILL 2102186912 | {465DB4EC-AD0D-4513-8558-C56336450D1C}
APPLE HILL 2102411690 | {5BDDDBB6-CEEF-4AD4-9BDD-F629132804C2}
APPLE HILL 2102501650 | {4047ABE5-181C-4DB3-9DBB-212375DDD70B}
APPLE HILL 210251792 | {60540539-B6BA-4E80-BC6C-988DA579218B}
APPLE HILL 210277546 | {71852C93-FB23-454D-AA22-159ABBF0F364}
APPLE HILL 210277546 | {0ED6D056-42CA-4070-ABF6-5026D2D9ADD4}
APPLE HILL 2102836878 | {CB359284-0736-45D2-B59D-DFB4E12FD162}
APPLE HILL 21028372 | {02B3726E-2D82-414E-A66D-D9CB526BF564}
APPLE HILL 21028372 | {87934A6A-C9D7-420E-9278-5C4F8DB79DED}
APPLE HILL 21029722 | {6E1E8BC2-4BBC-4030-84A6-7F33037C45AF}
APPLE HILL 21029722 | {679E3FFB-DC7A-4A32-B0F8-8E2206389F5B}
APPLE HILL 21029722 | {3E62C8CC-00AC-4511-BF73-2FA1B4F16739}
APPLE HILL 21029722 | {ABE893A2-F5F5-4D68-80F5-C330AD045D89}
APPLE HILL 21029722 | {9F7208AF-E6F9-4926-932A-80C26A40F5B6}
APPLE HILL 21029722 | {F831EA7F-1C58-4FA3-87D6-400D9A04EDCF}
APPLE HILL 210297982 | {1FCD571D-957E-4FF9-863E-0126FD4A401D}
APPLE HILL 2102CB | {5DC9E720-795B-432E-BA68-667FD0BD630A}
ARBUCKLE 1101107710 | {4EF9BC28-BDED-4FDB-AEF0-17E60D4EB2C0}
ARBUCKLE 110130014 | {16274AA4-E286-41C7-935D-804D0E44A27C}
ARBUCKLE 11013068 | {124AA8B2-E7E1-4C6C-A0AA-A0DC7D438AA7}
ARBUCKLE 1101932352 | {B2E83566-334B-4D06-8145-C26AD63C12BB}
ARBUCKLE 110194064 | {B2E83566-334B-4D06-8145-C26AD63C12BB}
ARBUCKLE 1104969486 | {09231E8B-9807-445C-B8AC-5325493AFFCC}
ARCATA 11211206 | {4C349E36-FC6C-4846-B54D-365EB19746B7}
ARCATA 11216004 | {7105441B-4177-4883-821E-B79840B9E771}
ARCATA 1121716954 | {FF12024C-319B-45A6-9F88-A7BDDD085162}
ARCATA 1121716954 | {6E3AE2B4-F135-43F0-832F-E39BC5035CBC}
ARCATA 1121716954 | {2938B984-F7EB-4FD2-BCCA-0E89F66CB086}
ARCATA 1121CB | {B9FFA3B9-62B6-4B90-9671-6A7AB6EDF708}
ARCATA 11220664 | {7208E20C-4385-4370-9AB9-5E96AF86A832}
ARCATA 1122120516 | {BC947882-27AB-456F-9300-7FB41DC4C028}
ARCATA 1122175610 | {367A2503-D1F3-412A-9C31-B8346F988B1A}
ARCATA 1122175610 | {60C859E8-56F8-475C-9BD0-71756055FB49}
ARCATA 1122328150 | {8FD0CF2A-B76A-4A6B-BC5A-684C3A58EA8B}
ARCATA 112233060 | {2ED8BBD5-6C9A-4FD4-8C9D-6FDEBFB20056}
ARCATA 112233060 | {74B63A88-19CC-40B3-96BB-E8B6366AE354}
ARCATA 112233062 | {56380981-464C-4374-B31B-B60916A64447}
ARCATA 11225384 | {BF59168C-9799-46DA-A7CF-3B05E57A19FB}
ARCATA 112293912 | {C09061FA-DFCA-4DE9-B6C9-B473EDEEC5A7}
ARCATA 1122CB | {4D343D95-65B7-4F09-8335-963B7DE7388B}
ARLINGTON 0401404226 | {B073565E-E5DC-4302-BADE-27F696E6F580}
ARLINGTON 0401CB | {B0F9DF73-E5FE-4D63-9A97-F698C647DBAA}
ARVIN 1101463604 | {E830FDFF-C4A8-4EF0-A197-1F92FDE42347}
ARVIN 110153388 | {B37866BB-1986-4551-BA79-436337F9C94A}
ARVIN 110169618 | {E830FDFF-C4A8-4EF0-A197-1F92FDE42347}
ARVIN 110194892 | {226706D2-A5D5-4ADA-8765-BEC337D79F6B}
ATASCADERO 1101747522 | {9D5F98AC-D692-4AC3-B10F-B55050027580}
ATASCADERO 1101A22 | {1A2AEC20-7798-471E-990E-3BD9D80801FA}
ATASCADERO 1101A50 | {CC1F4643-49D2-4B99-B353-84FF1B6CAA23}
ATASCADERO 1101A50 | {C74334F6-C157-4384-BFB7-ED7E4C2B59D6}
ATASCADERO 1101CB | {98F44516-A7DA-4F88-98E1-7BF277BBBD67}
ATASCADERO 1102A26 | {C057EF7E-9D13-4CEE-8644-90B6E434EFC2}
ATASCADERO 1102A26 | {7EFA95C1-893A-40F2-8270-A822F9E8EEA7}
ATASCADERO 1102A28 | {36829D64-BEC3-4EA2-AAF0-03E28E121283}
ATASCADERO 1102A88 | {553C693F-FB0A-403F-AF7B-DFD04F0B4035}
ATASCADERO 1102CB | {E22A44CE-34F2-45EB-BA42-C88A6CDC3537}
ATASCADERO 1103411671 | {106A13D2-1B29-4364-8FDB-B35DD75DEE06}
ATASCADERO 1103440856 | {278EF629-FBA2-4705-B4A9-1A30E95AD439}
ATASCADERO 1103440856 | {151D8956-D712-470E-962E-BED84A9C436F}
ATASCADERO 1103440856 | {628B6BC0-BA06-497E-B4ED-6B13D69067FB}
ATASCADERO 1103440856 | {CE1B4F1D-0818-4F54-96A6-5CB8D8BF7895}
ATASCADERO 1103492068 | {BDD83B1C-28F8-4B09-B7CE-E948BFB7D564}
ATASCADERO 11035391 | {33E2266E-C59A-4274-8F59-B7C367D641B2}
ATASCADERO 1103635958 | {F5631237-9E9F-4E89-82C9-2C77B3AF73EC}
ATASCADERO 1103823802 | {A603C8C1-E145-42D7-879D-ECA6829DF7E5}
ATASCADERO 1103A06 | {80C03548-09A3-4516-9CD7-A85242729AF9}
ATASCADERO 1103A18 | {1D2DA1C9-B2A9-4713-BA25-DD6CA0F657BB}
ATASCADERO 1103A46 | {614AFF73-1972-445B-AB78-45C825B90AEF}
ATASCADERO 1103A80 | {01E75A4D-5E59-4C31-876B-BB494E0AE408}
ATASCADERO 1103CB | {80C03548-09A3-4516-9CD7-A85242729AF9}
AUBERRY 1101230220 | {6578AE08-8528-42A9-B88B-9F0506EECBA8}
AUBERRY 1101233716 | {8DAF4421-DB43-404E-B3EA-C8130D3598E3}
AUBERRY 1101323028 | {C1CE4AB8-208D-468C-9C9D-4AE66225C482}
AUBERRY 110137536 | {054B3D26-E4A1-4A6E-9629-D6301040C307}
AUBERRY 1101378194 | {9E177A83-2291-4771-8E4C-995A8D03280B}
AUBERRY 1101460274 | {F66DFB2B-82DA-4BE1-8506-259D11CF42F9}
AUBERRY 110149122 | {CF6620C8-D567-44D2-A333-6E23E0B1AECE}
AUBERRY 110149122 | {BA3893C1-711D-4BF6-9767-7C0EC1B0CA4D}
AUBERRY 110149122 | {27512000-168A-47A4-8DFA-AD440ABAD8D8}
AUBERRY 110173626 | {BC876154-7845-44A7-BC55-2B0AE4B68F02}
AUBERRY 1101CB | {50F15232-B267-496F-ACCD-C66670CD5E1D}
AUBERRY 1101D2262 | {0A127AB1-4951-453F-81E5-EB366C1F2903}
AUBERRY 1101D320 | {E656C875-B162-4287-8C4F-66D9D43BC79E}
AUBERRY 1101D323 | {AEA04BC8-FBBB-49BC-827C-3203359CB919}
AUBERRY 1101D4982 | {C1CE4AB8-208D-468C-9C9D-4AE66225C482}
AUBERRY 1101R2579 | {1328D5B4-6BC6-4A19-8B7D-C1E2266894DF}
AUBERRY 1101R2579 | {9BB6BE7C-5772-4C94-8384-8E6EC9DC2BBE}
AUBERRY 1101R2579 | {95ACBB6B-3AD7-4ACE-B4BD-75A89BA08D43}
AUBERRY 1101R2579 | {389DAAB1-8301-4FC3-BCC4-D4FE426D5F9A}
AUBERRY 1101R2579 | {0B36B16E-9EDF-4BA7-8692-E55FFDC053B4}
AUBERRY 1101R2838 | {48B8D134-2217-4EE4-BD7C-3270CBBFB37D}
AUBERRY 1101R2839 | {1D410A42-CC20-42CD-9AF0-41D38F1027D3}
AUBERRY 1101R314 | {4F5EBE36-6D68-4A47-AF49-0D6F0830F1BC}
AUBERRY 1101R324 | {E1E5839C-1351-4866-AD70-89FE7DE5E158}
AUBERRY 1101R324 | {409EAFEB-3764-475B-B7F3-77873A86BB80}
AUBERRY 110237466 | {72B3FD6E-4E00-4CD9-8668-70733AC266B2}
AUBERRY 1102394080 | {761E9CCE-293A-4976-B463-76F9E32A5475}
AUBERRY 1102CB | {004C66A4-EFD9-4F4F-AA71-77719D3D9AC9}
AUBERRY 1102R1013 | {71E8F95F-8504-4520-9C3B-8AB71CD7CDDD}
AUBERRY 1102R2850 | {CFE5622E-640A-4701-B25A-30E645D814D9}
AUBERRY 1102R309 | {6CB8407B-8DEC-4DDB-A06C-70CFC4C2C27B}
AUBERRY 1102R902 | {5ED2B13E-98E4-45F9-A6A0-57DA496030DD}
AUBURN 1101173014 | {ACC7CE4E-E9FD-4F32-956F-F6FB27435C5C}
AUBURN 1101CB | {0654A595-233E-4128-BBD6-123F6D88D1DE}
AUBURN 1102251946 | {F47804CC-754A-4FCA-B217-8CAF682A164E}
AUBURN 11028611 | {F47804CC-754A-4FCA-B217-8CAF682A164E}
AUBURN 1102CB | {8B190E99-2FFD-4283-B3F1-C9A94DD8C8D7}
AVENA 17025494 | {3E1C42BA-A837-4BE0-A8EE-C29428358DD7}
AVENAL 210144778 | {11F90B20-4653-4D7A-8552-7BBFF5CBD8D2}
AVENAL 2101602496 | {8B93F65F-A3CE-4094-B716-57A94689987D}
AVENAL 210181938 | {21D8EC29-B012-4964-A94B-7962FD71A3CF}
AVENAL 21019070 | {DA3E7D61-550F-4F15-867E-0DA2789E9CC5}
AVENAL 21019070 | {BA67822C-2303-4723-983B-9142A9A0088D}
AVENAL 210192528 | {96C1E685-DB65-486D-B437-8350A5CAAD0D}
AVENAL 21019810 | {25E0F7F5-6399-4822-97AD-9B04397D81D8}
AVENAL 2101CB | {EB157AB6-E56D-43C2-BD2F-2465135D5AE1}
BAHIA 1102350336 | {D779E260-A9EB-488D-9C51-276E03633CA6}
BAHIA 110243940 | {DEDF96A5-C41B-4EBC-91B1-8B12D8F8D23A}
BAHIA 11026757 | {D779E260-A9EB-488D-9C51-276E03633CA6}
BAHIA 1102946 | {DB2FC269-3C3E-4BA8-90F2-EC4309787301}
BAHIA 1102CB | {DEDF96A5-C41B-4EBC-91B1-8B12D8F8D23A}
BAHIA 1104624 | {1174208D-2F2B-4ED1-8FDD-04AE48889F27}
BAHIA 110493908 | {3BBA0B55-FB4F-4853-A573-C71E59BF6BC9}
BAHIA 1104997506 | {4003F221-0ED3-4BA8-886E-AA900ED94F65}
BAHIA 1104CB | {D9CE4B2B-90AD-417B-A653-259F334A8D17}
BAHIA 1104CUS8929 | {4003F221-0ED3-4BA8-886E-AA900ED94F65}
BAKERSFIELD 1101CB | {B5412FC5-E78F-497B-B8CB-A43397A714FB}
BALCH NO 1 1101105414 | {AE86CCC0-9A32-4ECB-B70D-2CCE4DDF5F1F}
BALCH NO 1 1101406582 | {F32CC135-97A4-4BFA-A01E-518E8F21967F}
BANCROFT 0401CB | {AB9DBAEE-49BE-4F3F-BA1E-0AF3126C876D}
BANCROFT 0402CB | {A91DA441-EEAC-4573-A6F0-741EAB76EF3B}
BANGOR 11011804 | {AA43926C-4093-46DB-8206-D72B26A57306}
BANGOR 11011804 | {F430F9BA-4822-49EF-972E-D271E55910BA}
BANGOR 11011804 | {A2E5624F-A564-417E-8208-737F78425523}
BANGOR 11011806 | {ABE5C26B-A76B-46B8-A04C-0EC15FF8F909}
BANGOR 11011958 | {4EADDDA4-9026-4CB9-B9C4-03D97B5E8FF0}
BANGOR 11011958 | {11F38EC3-5F35-4498-B01A-5E1A27124E84}
BANGOR 110131502 | {6925CBA3-93E0-44A7-B2DC-50805D93ECF4}
BANGOR 1101417210 | {16EDAC9B-8C49-4185-9FE4-CF4748324FBE}
BANGOR 1101498380 | {B3637D02-5D81-4552-9104-06FFEBB0B445}
BANGOR 1101537672 | {50071A42-1669-4AE7-A593-9FFF3A6A09B5}
BANGOR 1101614048 | {5063F2C6-9AF9-45AF-BA98-1D8C5E52CC95}
BANGOR 1101614048 | {808B9A32-C42D-445B-9979-179B0B7A37BE}
BANGOR 1101626862 | {73DF3F19-FCAA-4424-828D-710D5840063F}
BANGOR 1101626862 | {B9A26858-5BF1-4397-B906-AEAA4C335F21}
BANGOR 11017446 | {37FE066D-28CF-4140-A2D0-4ABC1EA8F8E8}
BANGOR 11017446 | {1FB07492-7817-4281-B458-54D457C1DE65}
BANGOR 110182350 | {61206052-9537-4FFD-A305-D8F681D781BF}
BANGOR 1101870548 | {16EDAC9B-8C49-4185-9FE4-CF4748324FBE}
BANGOR 1101CB | {CB9FA698-E2B3-4923-A1DA-DA7C548C122C}
BANGOR 1101CB | {C9648835-EB5A-442A-856F-5456F572C3DC}
BANGOR 1101CB | {95A6A954-1179-44FA-AE45-DBA914F6C1CE}
BASALT 110138824 | {36CB0205-94DA-45AD-B087-D2736F00D26A}
BASALT 110175886 | {0FAE99A3-272C-4D4D-AE6A-B1955441A366}
BASALT 1101860318 | {36CB0205-94DA-45AD-B087-D2736F00D26A}
BASALT 1101CB | {36CB0205-94DA-45AD-B087-D2736F00D26A}
BASALT 1104CB | {1D69793B-6513-4BDE-BB21-BAE25C357436}
BASALT 1105CB | {6CFDCF11-C002-42A5-AACA-1A265A50033F}
BASALT 11061781 | {230E7534-26E2-46DC-BF08-6106FB749B89}
BASALT 1106267462 | {B44FE367-DC69-440D-96D5-5E7D077FB65E}
BASALT 1106316302 | {4B4F529E-61C9-4763-88C9-BA9E643D6014}
BASALT 110635550 | {59993A18-7188-40F9-AA27-F234DF60E7B5}
BASALT 11065030 | {31C38397-CC97-43EB-A38A-D18D8FE5AEB7}
BASALT 1106657038 | {0C9DEF06-9AAB-4128-9810-85E010FF7C1A}
BASALT 1106724 | {8A4F47EF-D877-4E31-A408-D8738C611CAB}
BASALT 1106783176 | {C1B4D7E0-AEC0-40F6-81FE-1CB70FC2FD8F}
BASALT 1106CB | {230E7534-26E2-46DC-BF08-6106FB749B89}
BASALT 1106CUS167 | {4B4F529E-61C9-4763-88C9-BA9E643D6014}
BAY MEADOWS 110565187 | {4460A2C3-E57A-4228-8E6E-BAA1830E8AC4}
BAY MEADOWS 210248770 | {89242FEE-8748-42BC-8EA8-CDD97EA44EAD}
BAY MEADOWS 210257886 | {D73C61C6-F360-40B2-9388-D54915745260}
BAY MEADOWS 21029062 | {86CF771D-C898-49B6-8034-3BBD63FEE2E4}
BAY MEADOWS 21029162 | {662A3116-C1F1-4DE2-847C-5739AB01C30F}
BAY MEADOWS 2102CB | {7B48B738-B738-4F2B-B0D7-4D191D860D4E}
BAYWOOD 11014757 | {82D72170-020E-4DD7-9C9F-960EDB0862CE}
BAYWOOD 1101CB | {82D72170-020E-4DD7-9C9F-960EDB0862CE}
BAYWOOD 1101V102 | {6A94C75C-2B9D-417A-8946-7997EE49AE89}
BEAR VALLEY 210110000 | {0D159A34-F101-472F-9F8B-631446B0CF4C}
BEAR VALLEY 210110019 | {01E04AB3-4BC7-461C-86D6-3A3D5CD166F9}
BEAR VALLEY 2101149792 | {7F12A0FF-C6CD-40D3-8553-D87925458375}
BEAR VALLEY 2101411778 | {D8905D05-FE0C-4412-824D-0169810EFC53}
BEAR VALLEY 21014160 | {853E569F-DA3D-4A9C-B01E-E103347AC121}
BEAR VALLEY 21014500 | {D468A32E-4500-4D2C-80DA-85F74A9A6EF3}
BEAR VALLEY 210190550 | {CE2E0286-475F-4451-81F2-51329124240C}
BEAR VALLEY 2101CB | {01E04AB3-4BC7-461C-86D6-3A3D5CD166F9}
BEAR VALLEY 210513430 | {905BEAA4-243C-41ED-823A-50DB7B85C9FD}
BEAR VALLEY 210513430 | {F76AEDBB-91E0-4407-A41D-F6794405D1E1}
BEAR VALLEY 210521160 | {9D629412-09DA-443B-9B7B-592362EFA238}
BEAR VALLEY 210521160 | {BAB6581B-1DEF-4E8B-AEF9-096FA24A0638}
BEAR VALLEY 2105293732 | {ABB0CC40-D4C3-4C01-9BEA-4570C6C0972F}
BEAR VALLEY 210538882 | {95D37E71-331C-488B-BF85-EF1162FA998D}
BEAR VALLEY 210538882 | {7E9139D1-4F22-45BD-A941-3C57538462E5}
BEAR VALLEY 210538882 | {C4DA8875-2CAC-4FC9-938E-4AFDA696A7EC}
BEAR VALLEY 21054170 | {ABA71BA3-C71D-490E-AEB5-C37239F168A1}
BEAR VALLEY 2105454432 | {11DB8C84-C8EE-401C-AB12-1A2E81A02CED}
BEAR VALLEY 21054599 | {E128FAC8-5771-4A6B-BBDB-194BBEB3F182}
BEAR VALLEY 21054629 | {93C3CB59-F607-47A8-B6D4-F1D4F739461B}
BEAR VALLEY 21054629 | {7747897D-2130-437A-A837-21C6F7DB3FFB}
BEAR VALLEY 210576694 | {DBF29453-0B03-42AD-A97A-1CA961543977}
BEAR VALLEY 2105916436 | {C5D51BCC-B370-48A3-8349-FB710857EC4B}
BEAR VALLEY 21059480 | {83E15892-C159-48B2-98C7-95188F40B517}
BEAR VALLEY 21059570 | {98A91A9D-C05D-414B-BFBB-E243D651003D}
BEAR VALLEY 2105CB | {3A07F3B8-E9B8-45C5-8744-6792C16A4186}
BELL 11072400 | {6DE1646E-6151-474F-97FF-CEA29373F76D}
BELL 110750172 | {6BF0E854-A546-4347-BF88-873ABBCE7D58}
BELL 1107643778 | {B62CEF1F-B5AF-4B96-9E64-FF58A6B33C79}
BELL 1107CB | {49E80940-99B4-47A0-948C-E1482C4F88F1}
BELL 1107CB | {CD565697-14B6-4AA0-954C-46CA84031737}
BELL 1108127062 | {EA7A922D-E9BD-484D-B6ED-929B9EBF7C80}
BELL 11082202 | {C705CC3B-4CE7-4574-9451-1595DBBA258B}
BELL 11082226 | {FF6B966D-B6C9-448E-9EAD-BA4CD433B469}
BELL 1108339792 | {C5B6945A-DE5A-4681-9AEF-7B6CF23C0D53}
BELL 1108351852 | {50A19D76-23E4-4194-A546-FA4EB9B67EC9}
BELL 1108467470 | {BDA23D69-24A9-4707-9922-D38045FF1C5B}
BELL 110880680 | {3A2A466A-E07F-43BB-BFCA-7454C5908F19}
BELL 1108CB | {35B30399-E588-44B0-B481-56F6CD9688B5}
BELL 110950506 | {085B8A15-383C-4AC7-8C00-A9FA8BED6EBE}
BELL 110950520 | {C66EE736-987A-4FEF-A8AF-F6DA5647068C}
BELL 1109724884 | {C6312B9E-C10C-4771-B9EE-B7179EF46C16}
BELL 1109CB | {4EF25014-B554-454F-9BE5-F3AB9DDDB6E9}
BELL 111050182 | {6B9F0345-026B-4979-BA83-3B077A617109}
BELL 111050522 | {E670C03E-CA4E-48A0-8E3D-40CC604AC7DD}
BELL 111056214 | {451291E3-291B-4A82-B036-A633A631A6D2}
BELL 111056214 | {AAA117DC-6FD5-43B8-AB6A-D4EAC9CEEA32}
BELL 1110CB | {451291E3-291B-4A82-B036-A633A631A6D2}
BELLEVUE 1102136 | {47497F55-F48D-47C7-AAFC-7B07673C8B7F}
BELLEVUE 1102463316 | {D29926DB-AE31-4DF0-BAC8-C7164572C130}
BELLEVUE 110278286 | {E3F3EE76-01DA-4EFD-A1DD-D7EE0921249A}
BELLEVUE 110285324 | {730DE3CC-E804-4522-94AF-60C26239A0C9}
BELLEVUE 1102888582 | {730DE3CC-E804-4522-94AF-60C26239A0C9}
BELLEVUE 2101270638 | {ABF9E8AA-C530-456E-BDAA-8AFA4226EA5F}
BELLEVUE 2101270638 | {C2168EAB-2E5E-4647-A287-4FD5B5CF5938}
BELLEVUE 2101335190 | {91F5D445-CCB5-4AE4-9883-27CF7A3A57E6}
BELLEVUE 2101411782 | {73326473-50A2-4B61-8AE0-45D2B6598A9B}
BELLEVUE 2101411782 | {E4FC579C-7A1E-4479-8137-13D0C4CC48DA}
BELLEVUE 2101552 | {6A4534AC-BAD0-486B-B524-008947385542}
BELLEVUE 2101665958 | {E204770B-40AE-4F36-B5DE-F75D80D964DE}
BELLEVUE 2101695464 | {877EF16D-6256-4A26-B0E1-879E065EF7D7}
BELLEVUE 2101CB | {09987E11-E541-4564-AE03-05F03FAC13CB}
BELLEVUE 2103388 | {018227D6-38CC-4EE9-BD26-7E3FF5AE9B25}
BELLEVUE 210342412 | {870B589F-AE99-44A8-A719-E41C0F6953BE}
BELLEVUE 2103940234 | {018227D6-38CC-4EE9-BD26-7E3FF5AE9B25}
BELLEVUE 2103CB | {D7E9D0AF-E912-4093-ACB1-C01E71ABC496}
BELMONT 110214543 | {8299BD19-90A4-4D64-8B9E-E4A475CD494E}
BELMONT 110268446 | {E797AB19-3600-4F18-89F8-9B9F590AAC2A}
BELMONT 11028918 | {8299BD19-90A4-4D64-8B9E-E4A475CD494E}
BELMONT 110347804 | {84C88409-8465-4D6B-B014-0E4B9C728457}
BELMONT 1103543076 | {569CF394-B2AE-4327-8C56-28F1C3082F97}
BELMONT 11038956 | {1467F520-572F-46EC-93E0-707DAECC5FB0}
BELMONT 11038958 | {B68C4BA8-94F5-4FA3-9062-8EFAD0B4F95D}
BELMONT 1110330790 | {E5D2E9A8-3F25-4DA6-AD92-5C753B714148}
BELMONT 111039182 | {2B049CE5-6DAC-4065-B555-915EF340A6E9}
BELMONT 11103975 | {650AE2A0-8481-4167-A199-68E796B3390A}
BELMONT 11104845 | {D5010A07-EC1F-422A-818C-56120CF28FE6}
BELMONT 11104946 | {D5010A07-EC1F-422A-818C-56120CF28FE6}
BELMONT 1110522372 | {51260AC6-2AC8-4069-B8E3-2060BA0FD12D}
BELMONT 11109088 | {5067650F-CC3C-4E18-8D3F-C80B3D2ACAFD}
BELMONT 11109090 | {650AE2A0-8481-4167-A199-68E796B3390A}
BEN LOMOND 040116010 | {52BA473C-1BA5-4952-86A7-343CF045CF65}
BEN LOMOND 04015144 | {8CE26437-AB3D-4CA1-B3DD-136FBC93120B}
BEN LOMOND 04015400 | {81F477DE-A079-435A-9F55-2410FEC944BA}
BEN LOMOND 0401698634 | {84DC7993-D314-489B-A9D8-96434904B6FE}
BEN LOMOND 0401944178 | {EB10C4EE-4491-4EBB-BF92-473E5065B27C}
BEN LOMOND 1101478943 | {1D042F8C-B79F-4337-A2A7-D1E8EDBAECAB}
BEN LOMOND 110186338 | {57B27573-8DC8-48D4-8AC0-33FCE490B77B}
BEN LOMOND 110196738 | {F1160745-E3B9-41AD-AB6A-9D1012602B97}
BEN LOMOND 1101BL 1101 | {3CDF572E-D09D-4161-963B-79B138C50CEF}
BEN LOMOND 1101BL 1101 | {97243609-0190-4CA4-910D-8656166A7529}
BEN LOMOND 1101BL 1101 | {EE23F1C9-1C16-447D-9AB4-7B3F0FB37912}
BERESFORD 0403435168 | {9E0ECC0E-D080-43C9-A87B-75BDCB2E0E91}
BERESFORD 0403855954 | {D4A9962C-7929-42D6-9791-5B60C706E999}
BERESFORD 04039154 | {59262E1A-A9BD-4C08-8147-3EF20A86F7EA}
BERKELEY F 0402502466 | {5BAFA9F8-CA96-406F-9803-715FC721E178}
BERKELEY F 1103162952 | {0AD46168-2B6E-4761-82AD-462845B00603}
BERKELEY F 1103620294 | {A3A50FD3-D864-4F5A-8B1F-9F554249643F}
BERKELEY F 1103813976 | {8BB0C622-0BA1-48A6-BC5B-DC08A0DC776B}
BERKELEY F 1103BR110 | {C6EF6B66-22B5-4479-8720-12455A79DA2B}
BERKELEY F 1105189500 | {5B19BE61-6886-4FC7-B0FB-4DA13CF3F560}
BERKELEY F 1105BR100 | {1FBD34FB-E63F-478E-B3DC-405EBBA003F8}
BERKELEY F 1105BR100 | {34B1FBA6-E642-41FD-8BD2-ADAC657BB906}
BERKELEY F 1105BR106 | {F0A66D2A-43AE-49AC-B30E-96FA410F3F7E}
BERKELEY F 1105BR166 | {ABB7B77D-2EF2-4B3C-9B77-BF1774A4BD64}
BERKELEY F 1105BR168 | {34B1FBA6-E642-41FD-8BD2-ADAC657BB906}
BERKELEY F 1105CB | {34B1FBA6-E642-41FD-8BD2-ADAC657BB906}
BIG BASIN 110110720 | {1594C1F1-1EBD-4EB0-9A76-086953E0C574}
BIG BASIN 110110720 | {178199BE-5B17-4F6D-8689-35D805AA6B49}
BIG BASIN 110110720 | {B41B9692-ED6C-4FFA-85C6-678BDDD16C3B}
BIG BASIN 110112838 | {CC60F8EB-8583-4463-B38C-D2F869F171F0}
BIG BASIN 1101136050 | {EC6DAEAE-4663-4197-A593-D4839F2AF80A}
BIG BASIN 1101136050 | {D289407A-D347-4D80-AEB6-2C2B754CD8EC}
BIG BASIN 1101166904 | {49F37291-C321-4777-8DA7-573CFC6ADF40}
BIG BASIN 1101391980 | {6AB8FDF6-DF60-4669-94F5-76C04F7F5767}
BIG BASIN 1101393582 | {498E3237-3BEA-4CD5-BBB3-313CDEBA801E}
BIG BASIN 1101492378 | {6354480C-8249-49EA-A1BF-3E1F5053B4FF}
BIG BASIN 1101595388 | {BF396B32-BD22-486B-867E-90456CF37674}
BIG BASIN 1101643012 | {5495FA79-A308-4D02-8FCE-6ADE4C10D9CD}
BIG BASIN 110165444 | {E247FC6E-157B-4272-AEDD-8C777FFAAD92}
BIG BASIN 110169550 | {6AB8FDF6-DF60-4669-94F5-76C04F7F5767}
BIG BASIN 110169550 | {0BA1101B-99F3-4D87-946C-F832D0B52AF5}
BIG BASIN 1101790070 | {1F2C0723-A02D-4717-A9F9-7293B40A8333}
BIG BASIN 1101921168 | {1F2C0723-A02D-4717-A9F9-7293B40A8333}
BIG BASIN 1101921168 | {116286DA-BE13-490C-B676-B1D2E8BDCEE7}
BIG BASIN 110195690 | {0F585841-A965-44FC-98CB-5C72CA920770}
BIG BASIN 1101CB | {94CF54F7-C6CD-4453-B5AE-8C10C6BEE2CA}
BIG BASIN 110210254 | {15D4C8BA-CC0A-4EB2-8B2F-A8AED4A99003}
BIG BASIN 110212124 | {5E67FDC7-6621-4E4B-BC49-469EB29666B6}
BIG BASIN 110212758 | {99A79B5B-089E-4FC6-A0B0-CC4BF6257CED}
BIG BASIN 110212992 | {1695E978-9BD4-42EE-A017-6DD99E4F027F}
BIG BASIN 1102181438 | {7B9330C9-21D3-4FE4-B12F-F901A02287FF}
BIG BASIN 1102234250 | {0446505A-76DD-42E2-9D1A-AEEF551F9135}
BIG BASIN 1102243760 | {F17F7C6C-C6EB-41A5-A036-4078B48FB103}
BIG BASIN 1102307348 | {684496E5-6AA8-4CE0-BD15-F571AD20F865}
BIG BASIN 1102351054 | {B62C3773-D34D-46C7-939C-19D4366AAEC1}
BIG BASIN 110276752 | {7395FFA4-03E8-4D80-A8FA-546880E8DDC7}
BIG BASIN 110296986 | {87B7E394-3606-4372-9564-36FE0E57DA45}
BIG BASIN 1102991420 | {54A733ED-2352-4B50-846E-30C38BF5D8CD}
BIG BASIN 1102991420 | {4B74CFBF-A620-44B0-9E87-B923B8B74082}
BIG BASIN 1102CB | {7DF78B7A-3D58-4011-B365-74BA17A842F7}
BIG BEND 11011725 | {EC8BFB10-4A1A-42A7-A7FC-014E26BA3A62}
BIG BEND 1101180398 | {8A0E1297-B2C6-4E29-9AF9-DF1E115646B0}
BIG BEND 1101641808 | {5A96A91D-9C08-4D36-BEF1-A7C7B5FBE746}
BIG BEND 1101641808 | {A3F84BA5-8D5A-4B0D-AFE9-3E2A03521912}
BIG BEND 1101641808 | {EEF1FB43-EE56-47A9-B5CC-F4202613DE85}
BIG BEND 1101CB | {25C4070D-0704-4FE8-B250-876F6C426225}
BIG BEND 1102884340 | {DF76653F-9A84-406D-B399-26AC3048352B}
BIG BEND 1102CB | {85F75799-861A-4B10-9325-0D2253E0A08E}
BIG BEND 1102CB | {05EF3BA2-F04A-49CF-AF87-10424EDE6926}
BIG MEADOWS 21012016 | {6B2D5F4D-4DFC-49DF-85DE-2AF9D30D36A6}
BIG MEADOWS 21012056 | {BEDEF3DF-E1F0-4BAB-9E81-90CA4240CF80}
BIG MEADOWS 21012232 | {6FD1FEB7-53BB-4905-92FA-6BF228EE659D}
BIG MEADOWS 21012246 | {FF704EC9-7B07-4166-A0E1-5C891877A473}
BIG MEADOWS 21012476 | {A5EA53CA-65A7-43BC-BB3E-43041FB8E51A}
BIG MEADOWS 21012510 | {2FDD93D7-D61D-44CD-93DA-C1ACCE10D2C0}
BIG MEADOWS 21012562 | {50FC30D9-9631-47C1-AB52-87E3C16BC0D9}
BIG MEADOWS 21012586 | {70718D9A-2BF1-4C9C-AEE6-9A1119246050}
BIG MEADOWS 2101359058 | {8DF482B0-5CCB-4CC9-AA8F-1A1962A5C42D}
BIG MEADOWS 2101427964 | {2C94AA17-3708-4386-ABB7-D3EA4530E839}
BIG MEADOWS 210187164 | {474E60B3-EEE4-47A7-A7A1-094D2AD2E873}
BIG MEADOWS 2101919580 | {0A6163FE-AC9E-41E5-8BA8-81682DE0D204}
BIG MEADOWS 2101CB | {48DFC761-81AC-4E6E-A815-DEA2190E6576}
BIG RIVER 11011052 | {774F8E82-5627-4004-BA65-1CFB3311B274}
BIG RIVER 11012183 | {A36BE560-E1CB-4559-8E7E-01132EBA1D0A}
BIG RIVER 1101262924 | {BCC029FE-B790-4D1A-9B12-5D2C7AA3930D}
BIG RIVER 11012989 | {2D8E8FC7-3A5C-40AE-8F67-02A91CEAEC16}
BIG RIVER 110155402 | {2D8E8FC7-3A5C-40AE-8F67-02A91CEAEC16}
BIG RIVER 1101603538 | {622A2921-75E5-472B-9EB3-6D063B9584A0}
BIG RIVER 110169032 | {B18E180C-39A4-4EFB-8DCB-B1B629947F6E}
BIG RIVER 110179628 | {82A21CBC-843C-4ABE-B864-8FD58FD45315}
BIG RIVER 110179628 | {20E18CC8-D4A7-4B74-B6A8-456036AC47A2}
BIG RIVER 1101856308 | {5C7DC8E9-53A7-4585-B5A7-95F547E33181}
BIG RIVER 1101856308 | {D95A7C0C-0AF4-4CEB-8EB2-04C841B078C9}
BIG RIVER 1101952 | {1DB69746-E909-4FD7-90E8-E346F8AB657A}
BIG RIVER 1101954 | {A36BE560-E1CB-4559-8E7E-01132EBA1D0A}
BIG RIVER 1101CB | {BCC029FE-B790-4D1A-9B12-5D2C7AA3930D}
BLACKWELL 11023241 | {C4A4F1FA-941D-4D29-86EA-8608CA25A8E9}
BLACKWELL 11024745 | {C4A4F1FA-941D-4D29-86EA-8608CA25A8E9}
BLACKWELL 1102CB | {C4A4F1FA-941D-4D29-86EA-8608CA25A8E9}
BLACKWELL 21011104 | {0EA73BF2-EBD4-4ED8-92F8-0C06D695F6C7}
BLACKWELL 21013258 | {0EA73BF2-EBD4-4ED8-92F8-0C06D695F6C7}
BLACKWELL 2101894658 | {0EA73BF2-EBD4-4ED8-92F8-0C06D695F6C7}
BLACKWELL 2101991762 | {0EA73BF2-EBD4-4ED8-92F8-0C06D695F6C7}
BLACKWELL 2101CB | {0EA73BF2-EBD4-4ED8-92F8-0C06D695F6C7}
BLACKWELL 2101CUS2577 | {0EA73BF2-EBD4-4ED8-92F8-0C06D695F6C7}
BLUE LAKE 11013578 | {2B080883-3F89-467A-86D3-526324676232}
BLUE LAKE 1101CB | {E31E0DBD-FA9C-4715-8BFA-E451681E5B43}
BLUE LAKE 11021024 | {3C7601AF-6F6C-4334-9C5E-41DFDCEC0722}
BLUE LAKE 11024624 | {24F46A83-ED65-43A8-82C2-D01D5A9977F9}
BLUE LAKE 110256630 | {3C7601AF-6F6C-4334-9C5E-41DFDCEC0722}
BLUE LAKE 110266454 | {85554A90-3141-4763-A606-B31257470C42}
BLUE LAKE 110294240 | {6705332E-2929-4E9F-8E1A-9444B006678B}
BLUE LAKE 1102CB | {DB40B2E8-0171-47DD-8BAC-EDA4F7194556}
BOLINAS 11011064 | {196072E3-9BAD-4649-BDA0-FE3AF88F88C8}
BOLINAS 11011232 | {6FB5348B-5DA9-49B1-98A7-B3620A483016}
BOLINAS 11011236 | {6AEEBA49-CC4B-431B-92AA-34EB4CB9F64F}
BOLINAS 110137034 | {92DF57CB-130C-4B97-B59B-998A6C49E6E1}
BOLINAS 110146152 | {14035AAB-B6A7-4C8F-9B08-2EC08FB0B5E9}
BOLINAS 1101504 | {24FD9F9F-3AE5-44A3-85E5-C29F5C852455}
BOLINAS 1101528 | {E52E3AA8-626F-4DCF-BFEC-F21E6141C71E}
BOLINAS 1101530 | {E368881D-C918-4559-9B53-61F2E5E1FBD8}
BOLINAS 1101806 | {52879B9D-A33B-4D4E-99FA-0487B37405B8}
BOLINAS 1101CB | {86BA3963-96A5-4181-83CD-FA7B5EC47222}
BONNIE NOOK 1101CB | {9FFB5CDC-505F-4B8E-9B6D-E79E68D9EC60}
BONNIE NOOK 1102542186 | {297BF28C-8BC3-41EA-8E65-D92643DE031D}
BONNIE NOOK 1102CB | {3EE03E8E-7174-416B-B7B0-D49DC8F3C48B}
BONNIE NOOK 1103CB | {C90BDB25-C8EE-44ED-88EB-56C4AFDDB087}
BORDEN 110190050 | {8A1141A1-2ABF-41D9-A40D-E53E544995AA}
BRENTWOOD 21051511 | {AD36ABDA-018A-4DCD-9AF6-021D01D9D642}
BRENTWOOD 210519062 | {16A60C80-01C0-4028-B861-91744A19BAF9}
BRENTWOOD 210519062 | {FD4D2903-E29C-42C5-9D7A-9CB3E7F5D51B}
BRENTWOOD 2105219013 | {659CB7C9-DF34-4927-8487-32FE0AC742E7}
BRENTWOOD 2105472766 | {20303ED9-EE8A-40D6-A17F-821F7BF64DB2}
BRENTWOOD 2105500796 | {20554200-5340-4600-A74E-4043866C22E6}
BRENTWOOD 2105502672 | {B557525E-C955-4555-A43D-602C62B6D5B3}
BRENTWOOD 2105561968 | {67A8D291-E2D9-4A33-B191-9D0761D072BE}
BRENTWOOD 21056512 | {DA007DA4-760F-4151-A582-C98D9C468550}
BRENTWOOD 210577560 | {20303ED9-EE8A-40D6-A17F-821F7BF64DB2}
BRENTWOOD 2105822252 | {57758A07-35F4-41B5-94A9-0785D1D22397}
BRENTWOOD 210596324 | {8B109078-C964-45C9-BF00-4904308EBFAE}
BRENTWOOD 2105973026 | {7BB4E553-039C-4D09-8308-DC01500FEC6B}
BRENTWOOD 210598606 | {659CB7C9-DF34-4927-8487-32FE0AC742E7}
BRENTWOOD 2105B504R | {9A8233B7-234B-46CF-8EEF-6B74776F9D38}
BRENTWOOD 2105CUS1379 | {7BB4E553-039C-4D09-8308-DC01500FEC6B}
BRENTWOOD 2105CUS9768 | {67A8D291-E2D9-4A33-B191-9D0761D072BE}
BRENTWOOD 2110CB | {656225FC-E476-48B0-B77B-181188E8D8F8}
BRENTWOOD 211199210 | {E5AF8736-114E-4C01-9F04-EE6BE2C6FDFA}
BRENTWOOD 2111CB | {E5AF8736-114E-4C01-9F04-EE6BE2C6FDFA}
BRIDGEVILLE 1101365380 | {45735E53-2C9A-40EA-8C09-9822459D7915}
BRIDGEVILLE 110137484 | {24C71D6A-46DB-4BB7-8807-9800CAD347CE}
BRIDGEVILLE 110169866 | {3BB5B038-4064-4F43-B944-1BDE53135960}
BRIDGEVILLE 1101CB | {FC8DA5F1-E256-452E-840A-DB2CC55A41C4}
BRIDGEVILLE 1102353222 | {7337F134-7FAF-4975-B99D-C63324850B37}
BRIDGEVILLE 110237486 | {DC0A7D01-2EED-443F-A8C6-2C05CEB2611C}
BRIDGEVILLE 110255612 | {16121076-8F7B-4A07-9991-9C360FE94AC6}
BRIDGEVILLE 1102839652 | {6A116841-A841-40C3-9B48-86C4D5331427}
BRIDGEVILLE 1102CB | {5393CBB1-CE75-4399-B6C7-25EB732D48AF}
BROWNS VALLEY 11011268 | {868A573A-DC6D-45C3-92E0-27ABE99A6BF7}
BROWNS VALLEY 110136622 | {EF947682-77F0-46FF-B597-C974CCFEC84A}
BROWNS VALLEY 110193870 | {77D006A2-E276-4C22-A5B0-EE84D8EA3177}
BROWNS VALLEY 110197188 | {D76845FE-B268-426A-A73C-E770602E73F9}
BROWNS VALLEY 1101CB | {3F3AA0D2-CD3D-432D-9160-6EFA10A51D9D}
BRUNSWICK 11021010 | {CA5C38FD-CE12-4872-96AA-D926F4220C4F}
BRUNSWICK 1102940 | {8A1F3383-8C42-4458-990C-2355B321D3F3}
BRUNSWICK 1102CB | {0BF84A9F-DBEC-4CA7-98FB-695194286708}
BRUNSWICK 1103164092 | {58929914-99C2-4C8E-B85B-CC617974C9CA}
BRUNSWICK 1103173934 | {4D42C841-B88C-453F-8358-63D2C1E45D9F}
BRUNSWICK 1103173934 | {04D37AC0-1325-4EC9-B6FB-C903BA33F6BD}
BRUNSWICK 11032200 | {8832E15C-A8F3-49CE-9AF2-19EADE479033}
BRUNSWICK 1103234378 | {69E159D4-B5BB-47CF-962F-03601F5F22F3}
BRUNSWICK 1103262343 | {8DEE04BC-1F93-42B1-9D32-1482C9BA3DA3}
BRUNSWICK 11032784 | {A034BC39-5C36-44F2-830F-5D5EFC9DEDAA}
BRUNSWICK 110350070 | {DB1F9D2B-D359-4F2E-9F3F-F43B886E9D0B}
BRUNSWICK 1103639148 | {F18B8210-FBEC-4E04-A79C-5C0A5F7DDB09}
BRUNSWICK 110378862 | {B83D09DE-3D47-4840-BFDB-F992D85178B8}
BRUNSWICK 1103851116 | {32013278-E652-4636-8622-02EE3E5AF946}
BRUNSWICK 1103852240 | {D2CFCF41-58C5-4503-B8F1-FDC586F0302A}
BRUNSWICK 11038918 | {D34CE8D2-4E63-4899-B49E-7C6D0FD502F0}
BRUNSWICK 1103904574 | {1762E3E3-DCB4-41D0-A815-060A5A457F0D}
BRUNSWICK 1103956424 | {3FB24E68-4827-4A80-90A1-2EAF2EBC79EB}
BRUNSWICK 1103CB | {D972EC75-3864-4C3E-9FB0-5B538887AB46}
BRUNSWICK 11041020 | {DBDF15C5-1C5A-46A1-9C80-FCF08A12927F}
BRUNSWICK 11042112 | {1C515CF3-FCCE-4095-B61A-ED44FA9AA5B1}
BRUNSWICK 11042112 | {5D7A1019-73A7-4921-AA73-859EBCF0FBCE}
BRUNSWICK 1104285704 | {252458C9-C847-447C-8725-6EE8EF8017F8}
BRUNSWICK 110456468 | {A316ED50-5AA1-4ED8-AC7C-24B23FF6CC3D}
BRUNSWICK 1104761310 | {5D7A1019-73A7-4921-AA73-859EBCF0FBCE}
BRUNSWICK 1104789062 | {9C94BAE7-5392-4BE2-B54A-A9765B78E00E}
BRUNSWICK 1104CB | {4DC4BD40-BC56-400F-B12D-56D1E0B91D5C}
BRUNSWICK 1104CB | {BEA0A501-B4D2-4CC0-BAE4-F7EC8C1D8A1B}
BRUNSWICK 1104CB | {1075F189-27AE-463D-9A6F-C9AFE8205A68}
BRUNSWICK 11051030 | {B6CCA276-60FE-4AA5-8337-7F4B8BC06A51}
BRUNSWICK 11052100 | {EB9602B6-3B78-44B7-9264-163222D3097C}
BRUNSWICK 11052130 | {0D615EE0-F6DA-43C1-B2A5-E4A8F907AA4D}
BRUNSWICK 11052140 | {F48F30DF-84CD-4C48-AE91-CC0DFAC8DA65}
BRUNSWICK 11052140 | {B6A93F55-534E-4C9A-8EB8-6367DF5FB505}
BRUNSWICK 11052140 | {64937DAF-546B-4775-B18A-D5EDC1A6AA5C}
BRUNSWICK 11052204 | {EDC3C6AA-B200-49D0-AFDA-73B9844EB8E4}
BRUNSWICK 11052210 | {061B0891-9632-4691-9CF7-EFB012B2AC41}
BRUNSWICK 1105271012 | {B6CCA276-60FE-4AA5-8337-7F4B8BC06A51}
BRUNSWICK 1105272286 | {8A44AA74-ACDA-4D97-B1DB-12F78C555BFA}
BRUNSWICK 1105297538 | {E1779AD2-4579-4092-9EC8-FEE4F5C13371}
BRUNSWICK 110532536 | {547CB5AE-3FC8-46F0-9836-780E7F4C0AE3}
BRUNSWICK 1105452800 | {E1779AD2-4579-4092-9EC8-FEE4F5C13371}
BRUNSWICK 110584480 | {EB9602B6-3B78-44B7-9264-163222D3097C}
BRUNSWICK 1105875388 | {98D06868-EEDF-4A7F-BF35-3A8029F744C4}
BRUNSWICK 1105963830 | {791B3A7C-E220-4B2B-887F-A916837D4493}
BRUNSWICK 11059997 | {27C5F24D-0F3C-4530-810A-8D4DE3F7977D}
BRUNSWICK 1105CB | {E1779AD2-4579-4092-9EC8-FEE4F5C13371}
BRUNSWICK 1106114670 | {79D77B1C-2CE6-4D9C-82D3-8EC01871EFD8}
BRUNSWICK 11062104 | {BDBA1A41-9235-4F2C-87B2-104E0BB64232}
BRUNSWICK 11062392 | {F0B6C592-2F67-4F88-A13D-794768FAAAF8}
BRUNSWICK 11062416 | {53F5ED11-A466-4CBF-853B-22343DA65E1F}
BRUNSWICK 11062416 | {EDF4431E-F5AF-4806-91E5-400DCB7DFCFA}
BRUNSWICK 11062790 | {796E29D7-A10A-40CC-B6B5-2AFA2E8C7CDC}
BRUNSWICK 11062790 | {C10441DE-4140-4067-AC0A-82D10F063DBA}
BRUNSWICK 11062796 | {EF5B06D7-E629-41B9-B306-6C2CC9919130}
BRUNSWICK 1106458102 | {99ED7682-8D1F-4591-BAB8-0099AD2E7E04}
BRUNSWICK 110651484 | {A8C79078-BC64-48FB-AF0A-D764221046CA}
BRUNSWICK 110651484 | {F211ADF4-31F0-466B-8F59-DF90345ABDCC}
BRUNSWICK 110651484 | {A8552513-CF3E-46F7-AF24-B8EBC87C4A71}
BRUNSWICK 110651486 | {65242D70-6CC2-4910-BBFC-5A7B357B8C04}
BRUNSWICK 110651486 | {B389E6D8-1E85-47BD-BF75-DB3F34F12BB0}
BRUNSWICK 110651486 | {6B871473-104F-4C20-8589-1F02758D0F7A}
BRUNSWICK 110651486 | {20D517CB-EFEF-4E5D-A065-4994CEAE6929}
BRUNSWICK 1106771274 | {5F654CEF-A78C-4321-88E7-EB0EBD690862}
BRUNSWICK 1106CB | {AF57FA57-C475-4337-8BD2-035665A54A70}
BRUNSWICK 1106CB | {05FDE184-0042-4792-8C58-B7C18CC19C9C}
BRUNSWICK 1107357568 | {D067704F-EA17-4E88-B020-8A7104433E44}
BRUNSWICK 110750008 | {779A3152-24AF-4508-86CF-CDD542CFE4FC}
BRUNSWICK 110750010 | {3202AA94-6E44-43EE-96ED-1DD474010CC7}
BRUNSWICK 110756240 | {779A3152-24AF-4508-86CF-CDD542CFE4FC}
BRUNSWICK 110765574 | {22F4E53D-20D9-4A9C-BDCD-9693C219E892}
BRUNSWICK 110767218 | {22F4E53D-20D9-4A9C-BDCD-9693C219E892}
BRUNSWICK 1107969778 | {779A3152-24AF-4508-86CF-CDD542CFE4FC}
BRUNSWICK 1107CB | {22F4E53D-20D9-4A9C-BDCD-9693C219E892}
BRUNSWICK 11102664 | {52CBF115-6640-4F98-9743-613A61123F02}
BRUNSWICK 1110528196 | {91E6440A-FA7C-462D-9F90-13D6AE94C094}
BRUNSWICK 111061602 | {A298B0D8-C9B9-4411-92EE-D00915B8BD24}
BRUNSWICK 111063100 | {F62664EC-2775-4F42-885E-6C5354881CBF}
BRUNSWICK 1110832231 | {4FDE05D2-6E18-49FB-9864-F184CF9B6861}
BRUNSWICK 111094368 | {91E6440A-FA7C-462D-9F90-13D6AE94C094}
BRUNSWICK 111095576 | {AC82A3F6-A35E-40B3-B30F-C23643AC0649}
BRUNSWICK 1110CB | {AC82A3F6-A35E-40B3-B30F-C23643AC0649}
BUCKS CREEK 1103338520 | {E0268E55-B328-47B1-AE66-F18335F2069A}
BUCKS CREEK 1103338520 | {BB387EB0-7BEA-4BDD-8B60-2386CC72E369}
BUCKS CREEK 1103338520 | {788A24F0-B95A-4429-91A6-A78EF0DB40D4}
BUCKS CREEK 1103CB | {2C93052B-CAB6-4039-91C2-ECB9C837F00A}
BUELLTON 1101525952 | {E7520318-B39A-4128-AA65-6D2FC46CE61C}
BUELLTON 1101632102 | {50646AC8-8ED1-4645-B6D1-4F28EA3C2610}
BUELLTON 110163389 | {B215B9B7-F7F3-4553-8BC7-ED531B03358B}
BUELLTON 1101705596 | {68AA8AD6-E474-441A-86E3-E37DEA428CC4}
BUELLTON 1101CB | {3DA79F67-E6AE-44CC-8D0A-A38C65F29240}
BUELLTON 1101Y06 | {B215B9B7-F7F3-4553-8BC7-ED531B03358B}
BUELLTON 1101Y26 | {4514D6A6-77B8-4164-AACC-ADDF4E8C95FD}
BUELLTON 1101Y34 | {9919F67F-7D4E-4CC7-938A-6CB755805F83}
BUELLTON 1101Y36 | {9CBEE47E-1598-4921-97C7-5CC747F89863}
BUELLTON 1102512124 | {25B155BD-8533-40DC-9372-B74526787093}
BUELLTON 1102CB | {2D7A19FE-1388-4016-A42B-7364F42C4D40}
BUELLTON 1102Y20 | {2A274649-29BE-484B-9512-4089BA59299F}
BUELLTON 1102Y50 | {BE22BF5B-77AE-4173-893E-2D7D15CAA658}
BURLINGAME 04049066 | {FEDB38CC-94DB-4131-96EC-01C06ACEAACE}
BURLINGAME 0404CB | {585506C1-ED3B-4FB3-84DA-FABB2641F074}
BURNEY 11011322 | {A45048C4-5E06-4803-9C40-C46808E3753F}
BURNEY 11011340 | {9FEEDD46-3D3C-44E2-AC09-40EF72D10F0B}
BURNEY 11011358 | {2A928B3F-2AFB-4E95-9D5F-1D4611A31405}
BURNEY 11012402 | {2E555E2F-D45B-427A-941D-A906BDE558FE}
BURNEY 1101355340 | {5AE9286D-2A7C-4C73-A9E3-EFFF652994D2}
BURNEY 110145984 | {1877F2B7-68C6-4031-8C15-9D4F18F07556}
BURNEY 1101519432 | {343AC60B-63D0-4E19-ACE7-2943E5C1D0F7}
BURNEY 1101521264 | {9B951220-C3E6-4FEE-B75E-342280FBC977}
BURNEY 11019042 | {76D3EBDD-5C29-47DF-9912-445D8BE3DBA6}
BURNEY 1101CB | {DD5BA261-28C3-4395-8BF5-3D293075C1EE}
BURNEY 1101CUS5486 | {5AE9286D-2A7C-4C73-A9E3-EFFF652994D2}
BURNEY 110237284 | {B2408DFF-DEFE-41B8-ADEE-8F62D90930D1}
BURNEY 110257046 | {2AA24801-8300-4851-B080-261023387F10}
BURNEY 110297318 | {C4DDB13D-8C8F-4D3D-860D-833D982C6826}
BURNEY 1102CB | {36A5A14C-2F20-494D-A5FC-CDF9488C4EA1}
BURNS 210110912 | {62DB6A1E-C643-412E-AD78-478695BE02E4}
BURNS 210136516 | {6763B940-A4FC-4294-830C-EA07CE726C5F}
BURNS 2101389090 | {058B3B74-C76F-4C6B-B6A7-397C17E64FEB}
BURNS 210139126 | {1E00CF74-EEE2-4457-A6AF-F5C49F5CE48D}
BURNS 210190678 | {153A6026-D323-4954-B25F-4B63C2678A6D}
BURNS 210191034 | {B62417A2-05A9-4D8F-8000-7D56F072966D}
BURNS 2101CB | {77124F72-2A10-485B-AF25-5FB9845AECBA}
BUTTE 11032104 | {FB7A2293-9439-48C4-B179-5F6C84D82D44}
BUTTE 11032208 | {CD1DF8F1-73FD-453E-B230-386CF27645DD}
BUTTE 11032422 | {F6CF6B5A-1E51-4A8D-BE96-2DD1B8FF14FE}
BUTTE 1105134600 | {5CCEBBD0-8D8E-4DD0-87AF-C021A43051F6}
BUTTE 11052224 | {7917CC89-A0B7-4415-846C-1F5EBE9DF276}
BUTTE 1105235788 | {E9B89DB3-0831-46EE-9118-671FF72DAA2A}
BUTTE 11052576 | {9A0BA931-124F-4B29-B938-98D870112FD7}
BUTTE 1105398234 | {B2540AD5-03FB-488F-9579-CE16933A52B5}
BUTTE 1105518014 | {EA7C07F2-4273-40BB-B6F5-36B0C70D1D31}
BUTTE 1105612016 | {B2540AD5-03FB-488F-9579-CE16933A52B5}
BUTTE 1105751990 | {5CCEBBD0-8D8E-4DD0-87AF-C021A43051F6}
BUTTE 1105CB | {99D60B56-5961-4789-A3E0-D520C3413381}
CABRILLO 11031437 | {1DCF6444-72BC-4D8E-BA9B-2809A3EB6AC7}
CABRILLO 1103420128 | {7E5D62D0-9F68-41A6-BCDF-AB4845919B9B}
CABRILLO 1103460184 | {E139BDF3-D09C-421F-AF44-12A530393AB3}
CABRILLO 1103CB | {F3B21B24-5FCC-4918-B9AB-A8B8CD51F711}
CABRILLO 1103Y10 | {133D318F-822E-44D3-9638-08188E1B8D58}
CABRILLO 1103Y12 | {723FB00A-7C12-42CB-85FE-70F2D7BE445E}
CABRILLO 1103Y46 | {02264660-E3C6-4806-AC6E-28401EBDA58A}
CABRILLO 1104431976 | {305E578E-95B1-4763-83DE-92B8EEF31599}
CABRILLO 1104497036 | {7F56C5CE-96D2-4940-90A8-E5FBD1C11083}
CABRILLO 1104597930 | {DB4CB1A3-78E1-4EA1-92B3-6161B305FA89}
CABRILLO 1104765792 | {305E578E-95B1-4763-83DE-92B8EEF31599}
CABRILLO 1104838078 | {27DCEC24-FA17-48AC-A20B-BD915C784084}
CABRILLO 1104950258 | {289ECF2F-4604-4567-BB0B-A27BD1E85AF4}
CABRILLO 1104Y08 | {A8C0DCB1-6987-421D-A6ED-00C50AACF3B4}
CABRILLO 1104Y24 | {A2EAD6B1-6208-4216-A913-DC206F2BE25D}
CAL WATER 1102184854 | {B04B3C3D-984F-448F-A624-5DE5D72DBDC8}
CAL WATER 1102329532 | {24A98747-3FED-445B-9217-3A5C8B40D1B5}
CAL WATER 11023428 | {66B5382A-A6B4-4150-9067-49730EEFBF01}
CAL WATER 11023802 | {6AA5677C-0059-432E-BA9C-1357296F1AC8}
CAL WATER 1102690954 | {F35BC96C-F1E1-4513-95B9-90DB5E55FEE2}
CAL WATER 1102920714 | {75FA50A9-2878-4633-B714-48E51CCA6E1E}
CAL WATER 1102CB | {A5C90C7D-4BB3-40A3-8AA7-071C177614C2}
CAL WATER 1103429550 | {110924B4-7F59-475B-B106-57163C412FD0}
CAL WATER 1103604036 | {110924B4-7F59-475B-B106-57163C412FD0}
CAL WATER 1103768902 | {C260EBCD-D5A5-412F-91C3-0E5E44973C82}
CAL WATER 1103CB | {C260EBCD-D5A5-412F-91C3-0E5E44973C82}
CALAVERAS CEMENT 110111236 | {765E2074-110B-4FD6-8019-AD09D7431DAB}
CALAVERAS CEMENT 1101120672 | {1A726743-5C45-4747-8B26-F776276D602C}
CALAVERAS CEMENT 110113424 | {B1720971-4842-488B-929E-F65E96985B19}
CALAVERAS CEMENT 11011393 | {20BF5E63-59BA-4DCB-87D9-63C8D77CF0E7}
CALAVERAS CEMENT 11011419 | {31F34B0C-04AD-46C5-88A1-857D16F62C5A}
CALAVERAS CEMENT 1101174344 | {42941A36-0DA1-40E8-AED6-DBF16FA41113}
CALAVERAS CEMENT 1101174344 | {8149D4C8-32ED-4727-806A-67F10CFB1E1F}
CALAVERAS CEMENT 1101374244 | {5DEDD794-B9EF-4B74-8E2B-8118CA6DAB4D}
CALAVERAS CEMENT 11014786 | {97337433-3515-4873-83F1-570087429B1E}
CALAVERAS CEMENT 11014786 | {889956E6-8651-4B89-8A83-7BDF46B8A02D}
CALAVERAS CEMENT 11014786 | {CF62E6C3-07CA-4DD5-8099-332BF3F2B85C}
CALAVERAS CEMENT 110147968 | {AFAF5A37-E0AD-4142-ABDE-E616F0022060}
CALAVERAS CEMENT 1101502 | {E439BC99-0FF3-4346-9E22-657DA42C4565}
CALAVERAS CEMENT 1101502 | {63928A8D-30CC-4126-8C06-BE43E4C11433}
CALAVERAS CEMENT 1101502 | {6E964224-B327-4B25-BEF9-54920B548AD9}
CALAVERAS CEMENT 1101502 | {16F35289-A6E5-4226-BA73-6AEE45E864D5}
CALAVERAS CEMENT 1101502 | {F147C375-C323-4F63-A5CD-731BE1D08113}
CALAVERAS CEMENT 1101502 | {F0B6EDB2-F177-47DD-9252-89EC915621F7}
CALAVERAS CEMENT 1101544800 | {B4FC0E10-1DBC-4446-A2DE-836BB2DB31D0}
CALAVERAS CEMENT 110180930 | {218A8E8B-5522-44F3-9DD7-A50A226A98E6}
CALAVERAS CEMENT 110180930 | {31F34B0C-04AD-46C5-88A1-857D16F62C5A}
CALAVERAS CEMENT 1101CB | {16B948B9-B372-45A4-B29D-56B8F2A70B74}
CALAVERAS CEMENT 1101L3433 | {F4230456-AE1B-48F7-B66E-A9B084051A07}
CALFLAX 11039560 | {FD495085-1B6B-4EB6-902E-61E28D560BBB}
CALFLAX 1103CUS303 | {FD495085-1B6B-4EB6-902E-61E28D560BBB}
CALISTOGA 1101122350 | {EF1FA2C3-57EE-4BD3-91A2-9186818DE5AD}
CALISTOGA 1101134232 | {C06D7D77-648B-4C10-B65E-6012FCEC9841}
CALISTOGA 1101157668 | {6BBCCA3D-69FC-4060-8327-3D48C3973D5D}
CALISTOGA 1101217982 | {CD3F0C5B-3CFB-463F-84A3-D2D5913DA9C2}
CALISTOGA 1101242919 | {A2E97EA6-1CE8-40C8-917B-02BFB4DB75BC}
CALISTOGA 1101257964 | {0D63E34E-7108-465F-BC13-5DF2F623AD72}
CALISTOGA 1101267806 | {07D5D1F0-E088-492A-95F0-C51ED4C7A4B4}
CALISTOGA 110135588 | {027DEE93-00CD-47B3-9E09-CCA2A54DDEE2}
CALISTOGA 110143924 | {452F0E63-4DD0-460D-9F3F-8DAD64266857}
CALISTOGA 1101537148 | {950B7723-A5B4-41CD-A0A5-13F29B883B0B}
CALISTOGA 11015934 | {39A37840-00F8-46CB-8218-BB0855552677}
CALISTOGA 1101664786 | {E817A6B1-B5A9-480F-BE4E-060F6D3D012F}
CALISTOGA 1101727772 | {15B270FB-A708-4F25-A097-2249C81A7EB5}
CALISTOGA 1101730666 | {DDAD4B33-A9B7-4665-9868-093CCAD563F8}
CALISTOGA 110178734 | {6508E901-1F5A-48C3-8B34-5971800F66D8}
CALISTOGA 1101843761 | {0B54DF53-2082-4B6F-9020-553C5C7EBC03}
CALISTOGA 1101881110 | {0E3098B8-1D79-4775-90EE-1CA04AC01E07}
CALISTOGA 1101886282 | {22798A75-B031-4EAD-AEE6-E26CAD1C77A1}
CALISTOGA 1101890 | {37250BD0-D9D0-484F-9AA1-8C286761C77F}
CALISTOGA 1101894 | {D294E12F-4C7C-4C89-818B-50A112502FCB}
CALISTOGA 1101894220 | {7EC3F9B5-28CF-42D9-B7F8-DA19D0A08EE2}
CALISTOGA 1101959538 | {592CEFBC-9961-4F1D-B002-F87443B77673}
CALISTOGA 1101CB | {07D5D1F0-E088-492A-95F0-C51ED4C7A4B4}
CALISTOGA 1102131531 | {9728A510-4796-446C-AFFA-E71EAF88F06E}
CALISTOGA 1102141073 | {418B82F8-6C32-40A7-BAFC-4E4E4E20312E}
CALISTOGA 1102177784 | {854EA7F2-5906-4478-AEB7-CF15AD49AC3F}
CALISTOGA 1102184814 | {0D3E38EC-4BB1-470D-863A-6F90C01B8B53}
CALISTOGA 1102270153 | {5E03CEC5-E2EB-42D8-9EED-F70D1DF93EB6}
CALISTOGA 1102279135 | {0AB6C849-088B-4982-95AE-9F5B40F2ED13}
CALISTOGA 1102306462 | {03249A53-FC72-4ED0-BDB4-AF9C26BEA8C6}
CALISTOGA 1102447865 | {256C107E-DF69-4B49-8315-E416EEEC567C}
CALISTOGA 1102528622 | {AEB996A6-B3E6-422B-A668-DF66D3A05824}
CALISTOGA 1102634 | {E109FDFB-992F-46AB-911C-190A6187CD9C}
CALISTOGA 1102634 | {1FCE58DF-672D-489A-B6FD-E3E4E442C0A2}
CALISTOGA 1102640833 | {8A508CC4-F811-46AA-A430-C9F69A63B403}
CALISTOGA 110266730 | {2FC93923-0AF8-4A4D-9F96-EF0ED8AF2245}
CALISTOGA 1102706 | {AEB996A6-B3E6-422B-A668-DF66D3A05824}
CALISTOGA 1102714556 | {233F3D08-3CDE-4A75-9C20-C25EF1656D35}
CALISTOGA 1102769230 | {2E19A9CF-57F8-4CF7-B698-92E35CE7A12C}
CALISTOGA 1102892348 | {5967EFD1-F9A6-454F-AA55-1486E49A0BFC}
CALISTOGA 1102929461 | {54FC9C79-A744-48AC-829D-6AD9866F8972}
CALISTOGA 1102960240 | {41CC5656-0DD4-454D-8539-FF84073137C6}
CALISTOGA 1102963232 | {F6B6C2A6-F266-4776-97CA-32630CA07BDE}
CALISTOGA 1102CB | {B6480B23-3B7E-4A3F-9C7B-82F910A25330}
CALPELLA 11013421 | {7335B09E-01E0-44D0-BF6E-76BBD7B6C224}
CALPELLA 1101345230 | {CE47E68B-6431-42EF-95CF-00E7CF465463}
CALPELLA 1101372366 | {94071028-8C5B-457B-A3F8-E4BBBDF8AD63}
CALPELLA 1101542 | {C7347FC3-B613-4AAE-82AC-3F7111D01C04}
CALPELLA 11015659 | {C9B67D65-16AD-4B7D-A1D8-0EB960CC6E37}
CALPELLA 1101619542 | {979C5268-1F54-4BBC-B316-05EF7B718423}
CALPELLA 11016383 | {38F2A96C-79DF-4FBD-80B5-04DE29FDC82B}
CALPELLA 1101668810 | {F7DCF64B-5097-474E-8ED7-A15F65E9941B}
CALPELLA 1101668810 | {9C84A0D0-6931-469A-B0BE-D95A398B38C7}
CALPELLA 1101753000 | {E12D2ABA-05E0-44D9-A574-E03478B74646}
CALPELLA 1101753000 | {081987E7-DF83-4C27-84D1-482701C14CBC}
CALPELLA 1101845240 | {CE689720-9556-4C5E-B674-7DF8555392D5}
CALPELLA 110187784 | {A85B727E-B346-4154-8CE2-B2919F7ECC4A}
CALPELLA 1101908688 | {12A38B89-AFC7-458E-AF14-8B6F24C74831}
CALPELLA 1101931142 | {634C24C9-E71D-4215-AF41-8A5F9990674C}
CALPELLA 1101CB | {C851DF07-17A8-4945-A053-68AC77422563}
CALPELLA 1102421412 | {3A9F2D9A-7433-47D8-8578-46D205BA61B6}
CALPELLA 1102CB | {2993BF9E-90A5-4634-AB04-8D39B8C96792}
CALPELLA 1102CB | {E771C52A-BE31-4D0D-AA3B-7C07C892A3A0}
CAMP EVERS 210311046 | {B353A34F-8932-4DDC-82E9-4F60E2BA52C3}
CAMP EVERS 210312990 | {EA67021F-EC51-4B91-B55C-AC9EF715A21B}
CAMP EVERS 2103172066 | {7171D919-41DE-48AD-8F71-09BC97C4E9B3}
CAMP EVERS 2103449218 | {AD962272-DFC9-4006-90BE-E42CBF343716}
CAMP EVERS 21035402 | {CEB97A6E-057E-4617-8BF5-91D85F0FC1F8}
CAMP EVERS 21035404 | {08861202-71CD-43A7-A4E9-A7647717C791}
CAMP EVERS 210355638 | {4C9A65DC-55B1-4CE2-AD64-FA340511DC8F}
CAMP EVERS 210386048 | {30410242-3A80-46C4-88F5-7381CAFB03C7}
CAMP EVERS 210392582 | {FE8FB0E1-1FAA-49D9-87B9-90771C18AB33}
CAMP EVERS 2103CB | {22D220C5-2768-4212-BADC-DEEFF16BE912}
CAMP EVERS 210410442 | {51C72ADA-5E33-425F-A574-21BEA172A863}
CAMP EVERS 210411048 | {098D976F-684E-43BF-BDED-3FEF6B753DFC}
CAMP EVERS 2104189010 | {CE6EDBCF-B1D7-4C02-8D27-0FDA223000E1}
CAMP EVERS 2104CB | {84EE2558-0006-42C6-8836-08F2D7F2DAA3}
CAMP EVERS 2104CB | {D8B5F10C-1F36-4DDF-ADD9-C8CA172CCAC3}
CAMP EVERS 210510214 | {F835FBEC-BE60-4F27-B7FA-FBF03B1492E9}
CAMP EVERS 210510728 | {61BEE218-5ECD-4073-AA08-F1DB60558A8D}
CAMP EVERS 210510996 | {9C524D92-A5C3-4391-A08F-2E5640BEA3EC}
CAMP EVERS 210511004 | {08294E97-942B-4E2E-BF26-ED1FFEEAC0C1}
CAMP EVERS 210512590 | {9C7B2B92-FC22-48B4-B1A3-9DC57E45ACA3}
CAMP EVERS 210533542 | {AA5C701E-0F96-4151-A44F-2E6809287FB2}
CAMP EVERS 2105370732 | {F3D8BF5C-D197-44D8-98A9-531A4D374A53}
CAMP EVERS 2105384788 | {549C3DE4-1536-4966-BF9C-59298DB9FC95}
CAMP EVERS 2105426822 | {B7A521A6-441C-41FF-9BF3-E1AC07BB086B}
CAMP EVERS 21055188 | {2E032AE3-AAA1-4E0C-B317-C86FD721C0B3}
CAMP EVERS 2105534190 | {AA599654-FFB2-4492-998F-E0F44B671B73}
CAMP EVERS 2105538096 | {9FF05A95-F469-43B4-A412-8145F189B770}
CAMP EVERS 2105601610 | {C60D85EC-3384-4B7F-924F-0F013DD5EB4A}
CAMP EVERS 2105718066 | {C18F23CB-C77B-45AF-AE28-F27A00E5C8FB}
CAMP EVERS 2105740754 | {D3970BD5-F7FC-4C6F-A559-1A1DC9C9809A}
CAMP EVERS 210584166 | {C18F23CB-C77B-45AF-AE28-F27A00E5C8FB}
CAMP EVERS 2105894572 | {63C00E2B-CFDD-4B0D-A40E-E8B775780083}
CAMP EVERS 2105922576 | {113167BA-CCDF-4634-B6F8-AB10EDD459D5}
CAMP EVERS 210595050 | {CA99B367-8DC7-4E82-BCC3-DFC89B2C9160}
CAMP EVERS 2105CB | {EE077F7F-8175-4265-8512-03731CF3E11C}
CAMP EVERS 210612518 | {05F03FD1-1BB1-4BB6-95A1-E80FBA254DAA}
CAMP EVERS 210612518 | {8A35F12A-0761-4DDF-88CA-C8A70AB35338}
CAMP EVERS 210612760 | {11896F5D-08D6-4DB0-AD97-261601AA1945}
CAMP EVERS 210612760 | {77218484-2483-4A3A-8ACC-0336A0ABECA8}
CAMP EVERS 210612840 | {F761DD80-845B-4F29-ADA0-4CE9C4A1F615}
CAMP EVERS 210616000 | {1BABBDF2-DCB6-4552-BE33-67EDAC391159}
CAMP EVERS 2106183880 | {502FF174-EAD6-4A4F-B4D2-169F7D2A0D78}
CAMP EVERS 2106257600 | {A9948C64-0DE8-41DB-BAB3-440E2282849B}
CAMP EVERS 210637210 | {4EC0C5CA-D3E9-47E9-809A-55A51CA9C021}
CAMP EVERS 210637210 | {968E49EC-DA99-4694-8469-77DF22F8452B}
CAMP EVERS 2106478670 | {2A12FE05-29C7-4A7E-ADD1-ADDA9E49ED27}
CAMP EVERS 2106478670 | {F294860C-7C31-40F4-A41B-D8135E8E175E}
CAMP EVERS 21065020 | {D340DCCD-95D6-4317-9003-DD8DEDE9B1C0}
CAMP EVERS 21067603 | {4EC0C5CA-D3E9-47E9-809A-55A51CA9C021}
CAMP EVERS 210694770 | {58DC126F-C9E2-47DB-AFA1-8FE0FF5A0DFD}
CAMP EVERS 2106CB | {F50933AC-5B82-417B-BA6F-799563320ECE}
CAMP EVERS 210711006 | {386E8549-812B-4BD5-AF30-4B8F8F3211D4}
CAMP EVERS 210711044 | {90D97D29-641D-4D44-ABC6-DEB499FDF2DF}
CAMP EVERS 2107130936 | {B2374312-6A96-4C62-9249-47729A4C1D06}
CAMP EVERS 2107255706 | {B9907868-2016-4A65-8566-DE5DBA7654A2}
CAMP EVERS 2107287578 | {8E63B9EB-959B-406C-95DE-C4CA49EAA042}
CAMP EVERS 210746311 | {B304108D-C040-4EBE-BA92-E1140AED5BA0}
CAMP EVERS 21075300 | {30210CF9-C9B7-4E0D-B350-23AD99A7DA9C}
CAMP EVERS 2107543858 | {D583D50F-02EE-4385-9B3E-E046624A43F3}
CAMP EVERS 2107737512 | {38594324-B008-4F93-A718-0D73EA72DED9}
CAMP EVERS 210780820 | {4D40A4E0-2110-4A3E-911D-62C66770AD23}
CAMP EVERS 210780820 | {784A4FF0-C5DB-4C56-8854-EBB481340BB4}
CAMP EVERS 2107CB | {A14DB42B-912E-477D-B41C-7ECE4CFEA3E4}
CAMPHORA 110122412 | {9FC26291-9CED-4A71-A2CE-AB6E8C7B22F0}
CAMPHORA 1101613562 | {C4E21E20-1077-4DDF-9A14-C3E5D8A4A595}
CAMPHORA 110177978 | {31472151-05E0-42A0-B884-E32FC8EACB46}
CANTUA 1101918540 | {0E153826-D478-4D53-9758-C709DD777FA3}
CANTUA 11019880 | {A6F9A9A3-5D53-4719-B0E9-16B5436D2862}
CANTUA 11019890 | {6F887B9C-0786-4A1C-87D5-BFCD7256E812}
CANTUA 1101CB | {B55C2E19-B2B9-47FB-B0FA-5E9F76A070B4}
CANTUA 11029310 | {47A2D34B-B373-4F5E-9E14-A9EF32FD99D4}
CANTUA 1102CB | {593FAF9F-F993-4666-8339-2025B1146F35}
CANTUA 1103585898 | {B585D8B4-1A45-48B1-B4F7-888CD76922E5}
CANTUA 1103792930 | {ADBA8581-1EDE-4FED-96B1-1470CDDF965C}
CANTUA 11039900 | {ADBA8581-1EDE-4FED-96B1-1470CDDF965C}
CANTUA 1103CB | {77E96ADE-449B-4E4F-9A71-36285AE42A93}
CARBONA 110114204 | {2EC5D397-8176-4288-8DB4-84BFFDB565DF}
CARBONA 110145186 | {D5A2A0ED-5854-48FF-9353-DEF3C343CB3C}
CARBONA 1101676198 | {E69359FE-89E4-4F50-AEF9-162E5D779DE2}
CARBONA 1101975330 | {33A7055F-6DBB-40BD-9D42-63496DE4F455}
CARBONA 1101CB | {2EC5D397-8176-4288-8DB4-84BFFDB565DF}
CARLOTTA 112144150 | {47D7E27E-F1F2-4AFA-B2C6-25B11F5B475A}
CARLOTTA 11214914 | {A5C24938-2037-405D-99A3-0ABBFC2B130E}
CARLOTTA 11214914 | {4BBAA0AC-7995-454C-AB3B-BBF0850ECC7D}
CARLOTTA 1121669854 | {EF16DEEE-3B76-4E2B-8361-2A5F1B96B554}
CARLOTTA 1121686774 | {B05654BB-E8D8-4BA7-B923-D4499F5C765C}
CARLOTTA 1121CB | {3CA4A42E-51F1-49B1-95E4-11CB39229D26}
CARNERAS 11023266 | {C41C7194-17C6-4151-B8E2-2BD6F9C8EAEC}
CARNERAS 1102372456 | {60824F07-8DB6-4D03-B960-EDA03FF727A9}
CARNERAS 1102CB | {60824F07-8DB6-4D03-B960-EDA03FF727A9}
CARNERAS 11031584 | {01AEC7BD-16E4-4AFD-978F-FBA233B53DDF}
CARNERAS 1103430670 | {4F63DE1D-7CBF-4AAC-B035-BBB7D4E5B891}
CARNERAS 1103CB | {B861DBCC-FBD6-4E96-83C4-5248989E76A5}
CAROLANDS 04018506 | {41914C65-46E2-4B82-9AFC-5A738FB74209}
CAROLANDS 04018886 | {029D0D55-2BAE-4088-B646-F2DDA198BF80}
CAROLANDS 04018888 | {8A7276CB-0C27-49CE-BD2E-58CE1319B4D3}
CAROLANDS 040197209 | {542C89B5-8855-4F9C-96E0-4B73D5C44BAD}
CAROLANDS 0401CB | {AFAFA564-C801-46B9-B877-3979D8BE4904}
CAROLANDS 0402CB | {6CB7829C-D7F4-4692-906A-EB06183783C1}
CAROLANDS 0403662072 | {67DFE4DD-D106-4874-984D-4AF5F10CD724}
CAROLANDS 04038508 | {4FDA6CDB-0E5F-4B76-BABA-C5F84B9DCB82}
CAROLANDS 040387073 | {4FDA6CDB-0E5F-4B76-BABA-C5F84B9DCB82}
CAROLANDS 040387173 | {4FDA6CDB-0E5F-4B76-BABA-C5F84B9DCB82}
CAROLANDS 04038980 | {4FDA6CDB-0E5F-4B76-BABA-C5F84B9DCB82}
CAROLANDS 0403CB | {4FDA6CDB-0E5F-4B76-BABA-C5F84B9DCB82}
CAROLANDS 040484797 | {F73FE32B-0064-4963-BD0F-96E252B7B701}
CAROLANDS 04049024 | {ADC13D99-F0AF-402E-9F6C-0B91201427B3}
CAROLANDS 04049026 | {EE04BD96-5787-4D66-B00B-BC1201689111}
CAROLANDS 0404CB | {F73FE32B-0064-4963-BD0F-96E252B7B701}
CARRIZO PLAINS 11013527 | {DF118858-83A9-4B97-BE1A-B9801D7678FF}
CARRIZO PLAINS 1101384116 | {6983F117-CF1B-49D2-BCC1-D1CF76202FAE}
CARRIZO PLAINS 1101384116 | {DF118858-83A9-4B97-BE1A-B9801D7678FF}
CARRIZO PLAINS 1101711854 | {412EB69B-2273-4C1E-A820-027827AE03FC}
CASSIDY 21076090 | {052CDEC9-B784-4DBF-834C-E7FA6C02321D}
CASSIDY 2108186620 | {8B1F5CE6-C257-412F-8E44-85F4E3A081D3}
CASSIDY 21086060 | {5B750ACA-14A6-40F8-B701-EBE931C650F3}
CASSIDY 210868818 | {C9676C15-CA45-4CBC-88DA-BADAD16EB7DD}
CASSIDY 21089510 | {C9676C15-CA45-4CBC-88DA-BADAD16EB7DD}
CASSIDY 21089520 | {5B750ACA-14A6-40F8-B701-EBE931C650F3}
CASSIDY 2108CB | {C9676C15-CA45-4CBC-88DA-BADAD16EB7DD}
CASTRO VALLEY 1102837904 | {D1EA05C6-0F55-455A-AD0C-597319479076}
CASTRO VALLEY 1102840916 | {B3742266-0A6B-41B7-BDF6-4E4FF8E74B2F}
CASTRO VALLEY 1102960346 | {2E3992ED-F001-40B5-B77A-1BD22BF80B0A}
CASTRO VALLEY 1102CB | {4C70CAF0-3BFD-4092-B38C-A567700FFBF5}
CASTRO VALLEY 1102MR204 | {B72D11A7-A3E3-4487-9B62-E0B9199739E9}
CASTRO VALLEY 1102MR248 | {30E66223-084D-4B40-9C14-1E91EC3B3A23}
CASTRO VALLEY 1102MR359 | {F23FD02C-15E0-46F5-9C74-B690AB0C4482}
CASTRO VALLEY 1102MR518 | {BF555005-32AC-49E5-8E9E-ED1476EE192C}
CASTRO VALLEY 1105132304 | {DF750B9C-4007-427B-BA49-F0504B484D45}
CASTRO VALLEY 1105634022 | {7DC88504-8437-4262-8C77-15F7F25CD1D4}
CASTRO VALLEY 1105805238 | {9FA4DC7A-6448-41DD-AE90-39B3A5BE7830}
CASTRO VALLEY 1105853216 | {D3473D96-EE5A-4DC3-BCCA-A509A72B1AB7}
CASTRO VALLEY 1105964592 | {9FED133E-FE92-4FFA-BCFF-463F3941ED8F}
CASTRO VALLEY 1105MR201 | {7DC88504-8437-4262-8C77-15F7F25CD1D4}
CASTRO VALLEY 1105MR579 | {7DC88504-8437-4262-8C77-15F7F25CD1D4}
CASTRO VALLEY 1107299128 | {4AB41995-9040-45EF-9F87-1B704EFC09A8}
CASTRO VALLEY 1107425888 | {4AB41995-9040-45EF-9F87-1B704EFC09A8}
CASTRO VALLEY 1107MR235 | {35AEE05C-849F-43E6-A066-12B4CE5002B2}
CASTRO VALLEY 1107MR336 | {AD5F876C-C0A5-47C7-B722-6D39867E5D84}
CASTRO VALLEY 1107MR586 | {AD5F876C-C0A5-47C7-B722-6D39867E5D84}
CASTRO VALLEY 1108305566 | {35F88147-4B50-40D7-9C6E-74760AC2FD85}
CASTRO VALLEY 1108343456 | {FC94D279-1737-41C3-B252-F362937CE45D}
CASTRO VALLEY 1108401060 | {B2D42B03-ACE4-4897-AA57-6053A5805D37}
CASTRO VALLEY 1108622756 | {9CB4F399-E9C8-481A-A773-DACC87BA98EC}
CASTRO VALLEY 1108MR233 | {D8E4C9CA-7EEB-49BA-880B-C873380BC8EB}
CASTRO VALLEY 111010315 | {812DB2D9-B71E-4A4F-9289-9A3531AF9557}
CASTRO VALLEY 111012851 | {CC3DC7E7-30F2-430E-B05D-5397FC73E533}
CASTRO VALLEY 111016330 | {64BEC06F-24A1-44E3-BD06-B44FDAF67990}
CASTRO VALLEY 1110264914 | {FFE0EC6C-F31E-4ACF-B207-C8795D8C3898}
CASTRO VALLEY 1110442664 | {AE3688AC-6024-41C8-B4BC-C9214356323E}
CASTRO VALLEY 1110560528 | {A99DCE6F-B545-4120-B017-A9E82834DFD0}
CASTRO VALLEY 1110610800 | {217855BB-2EFA-4F5A-897E-1A1792604994}
CASTRO VALLEY 1110695103 | {812DB2D9-B71E-4A4F-9289-9A3531AF9557}
CASTRO VALLEY 1110CB | {FFE0EC6C-F31E-4ACF-B207-C8795D8C3898}
CASTRO VALLEY 1110MR243 | {58409F43-908C-4F7B-B13E-65AE96367D27}
CASTRO VALLEY 1110MR379 | {8CF3EAE2-3D5E-46D8-99A9-0040E44D6238}
CASTRO VALLEY 1110MR525 | {DDE57A1E-80D5-431E-961E-F1D86837BDD0}
CASTRO VALLEY 1110MR748 | {AE3688AC-6024-41C8-B4BC-C9214356323E}
CASTRO VALLEY 1111227862 | {24288AD2-A665-4D6B-A149-2AC7913C77E7}
CASTRO VALLEY 1111CB | {75D298E6-3FF1-47B6-9B91-A2291860E391}
CASTRO VALLEY 1111MR334 | {144B3CD2-37D4-4FA9-8973-1F3A9C9CD174}
CASTROVILLE 210436922 | {5DE92B6D-4604-444B-8D65-AB7A469C1FE2}
CAYETANO 2109107664 | {12B1749E-8333-432A-9361-2A3B6886DCEB}
CAYETANO 2109107664 | {12F27C0D-5A90-400E-AE30-47886559E780}
CAYETANO 2109609066 | {64CE1FC3-25BF-4386-8CE0-9A1FA4F6778E}
CAYETANO 2109791914 | {64CE1FC3-25BF-4386-8CE0-9A1FA4F6778E}
CAYETANO 2109884904 | {4B1B4811-B2BF-45DA-954C-55F605B422B6}
CAYETANO 2109884904 | {D6285326-2FFA-4A2D-BFE1-B6ED404A2994}
CAYETANO 2109CB | {6B3AA927-69EC-4F4F-A5CE-660E716543CD}
CAYETANO 2109CB | {CB1F79C6-162B-44E7-BDF1-619119F35335}
CAYETANO 2109MR186 | {96E83343-B1D6-4373-84A9-0E60E5A945BA}
CAYETANO 2109MR774 | {34B1170E-DD05-4114-A2A3-972616378761}
CAYETANO 2111CB | {439ED568-0BDE-4626-B59A-7C48F17E3B78}
CAYETANO 2111CB | {0098F2B1-286E-480D-B861-BA704D93D774}
CAYETANO 2111MR157 | {C40E7CD7-2111-4F6E-9C4C-C85455B7EAD0}
CAYETANO 2111MR157 | {25863AE6-07A1-4FFB-A761-2F9F71C6AB7B}
CAYETANO 2111MR329 | {1F16977C-CF64-491D-9B1C-93E8B1373825}
CAYETANO 2111MR444 | {989DEE6B-7210-45B3-A44F-60353BCD1695}
CAYUCOS 11014701 | {5CFEA468-EAFA-49AC-B046-6E19D81021D8}
CAYUCOS 1101CB | {E8519C3F-CC2F-4A8E-BB1B-BC611BF917C3}
CAYUCOS 1101W14 | {978A144F-73B7-480C-94FC-939745BD7BEE}
CAYUCOS 1101W58 | {5CFEA468-EAFA-49AC-B046-6E19D81021D8}
CAYUCOS 1102143608 | {E67DEA02-1A44-424C-936D-D759BF5FCED4}
CAYUCOS 1102317156 | {BC053071-09B8-414B-AB18-6F0D45277D55}
CAYUCOS 1102613456 | {6A688077-C692-4875-BCC4-AA060549E3B3}
CAYUCOS 1102CB | {80B87962-AD85-4936-A71D-968069A54623}
CAYUCOS 1102W16 | {0CAC8322-2615-4A4F-B632-EB3E5A0867D9}
CAYUCOS 1102W18 | {3F253D0A-A8E6-4C2E-92EB-89E0F265E7C4}
CEDAR CREEK 11011611 | {0418AD5B-C341-4BAF-B8FF-A8765D3AC50B}
CEDAR CREEK 11011664 | {81F58F11-9F6E-4CC2-A527-0CBBB670DE91}
CEDAR CREEK 1101451856 | {1E7F5746-1B26-4A75-989E-3A819FF5E822}
CEDAR CREEK 1101875796 | {A56492F6-CBB4-4F04-B76E-130822FE6244}
CEDAR CREEK 1101875796 | {EA56891F-40B0-435D-ADB3-39CD4358ADD2}
CEDAR CREEK 1101875796 | {5EA4432A-1EF0-43F4-A55B-65976F026C63}
CEDAR CREEK 1101CB | {4A950894-EB8D-4B95-B3B2-200DB270C21B}
CEDAR CREEK 1101CB | {C9CDA609-9CB2-4EAD-95D4-431E1376D17C}
CEDAR CREEK 1101CB | {870D51B3-84BF-4E6C-828B-2BFA04EB5F6D}
CEDAR CREEK 1101CB | {F7168FC2-48DE-401D-AC66-FC654648A9BD}
CELERON 1101CB | {DA90B9DB-1964-4768-8866-8F22EC0A3534}
CHALLENGE 11011955 | {F1D6044D-CC2E-4386-8AB4-1DB7D256DE1A}
CHALLENGE 11015460 | {B23B77B2-F3D5-42C7-AB2B-D58C03818E3A}
CHALLENGE 11015460 | {CC6E361B-CB3E-4B40-BF58-ADB4E431D8DD}
CHALLENGE 11015460 | {F0D31826-5D50-4D47-B81B-BCAAA769528E}
CHALLENGE 1101CB | {6A653745-C5CA-4E78-9C62-82F0E53CCD59}
CHALLENGE 11021064 | {B35DE979-0877-4DCD-A99D-B482E8F19A15}
CHALLENGE 11021064 | {A8BE9978-3573-4952-A661-8D90A51E63A2}
CHALLENGE 11021902 | {1446E22C-05D8-4F82-9637-10F46D2B1E35}
CHALLENGE 11025462 | {9343C558-C255-4E56-87AF-7724333414B9}
CHALLENGE 11025462 | {4D3726CF-6C74-455A-87B0-452D05D9BF39}
CHALLENGE 11025462 | {B40B9BF5-AEEB-45BF-A75E-5FB00E737DDD}
CHALLENGE 1102CB | {C71A58EE-DA31-4CE3-8F9B-4D615671BE3A}
CHESTER 1101656108 | {F5B87947-B1CF-4B32-AB2B-95DA61D92836}
CHESTER 1101922138 | {AC15192F-6D85-4C6F-A091-3F07428B4B1E}
CHESTER 1101CB | {F5B87947-B1CF-4B32-AB2B-95DA61D92836}
CHESTER 11022614 | {1F2FD20C-2DD0-4515-95F2-60329880F6A8}
CHESTER 1102385846 | {1F2FD20C-2DD0-4515-95F2-60329880F6A8}
CHESTER 1102546744 | {655104DB-DE28-4723-9C66-99BF732C7F54}
CHESTER 1102CB | {655104DB-DE28-4723-9C66-99BF732C7F54}
CHOLAME 1101413070 | {76DF57A1-1D71-4B5D-8554-4F7CECAD3660}
CHOLAME 1101468038 | {0B3B6670-1CAC-451F-BC53-8D6FCCBED577}
CHOLAME 1101654164 | {470B1907-B1CB-4483-9DE4-C8447BAC1EF7}
CHOLAME 1101789812 | {AD6BCC6D-9EBE-4E26-9E8F-694A3971F432}
CHOLAME 1101867686 | {97118B4A-2A8C-456A-94EA-FB99937C6D68}
CHOLAME 1101CB | {35294033-F688-4422-9C73-F70641476C8E}
CHOLAME 1101X10 | {DC85B463-1C28-4036-85F0-A9C121ABE158}
CHOLAME 1101X12 | {B37DAD9A-6324-4833-89D5-DCF19FFFD67A}
CHOLAME 2102127926 | {042A33DE-71B1-40FB-B0CF-6D56CCA576B0}
CHOLAME 2102469770 | {DCDC17BE-E1B5-4238-9F74-2FA47A2B0257}
CHOLAME 210249414 | {946E7382-BCE9-4876-B322-206F92E831CA}
CHOLAME 21025597 | {C3648DC1-A8A4-411C-BC09-DF15A6A8CCC0}
CHOLAME 21025939 | {47231439-CE13-4A31-BF86-1A2379821F62}
CHOLAME 2102796386 | {C3648DC1-A8A4-411C-BC09-DF15A6A8CCC0}
CHOLAME 2102CB | {042A33DE-71B1-40FB-B0CF-6D56CCA576B0}
CHOLAME 2102R22 | {7FDC77D6-0D2A-45F5-A1E8-7D8DC458C0F0}
CHOLAME 2102R96 | {0F26305A-B95B-48BC-93DA-531056D0E973}
CHOLAME 2102X04 | {B2BE53B1-E728-42AD-AA07-F412A808DBB0}
CHOLAME 2102X06 | {2CD93861-C1D5-4471-A09B-75955F723957}
CHOLAME 2102X08 | {7DB68BFD-2EE5-4737-904D-3F4AB911B6ED}
CHOLAME 2102X14 | {47231439-CE13-4A31-BF86-1A2379821F62}
CHOLAME 2102X16 | {90DAAFCD-8A40-42C4-A489-C7D86439D101}
CHOLAME 2102X18 | {D9DC2012-D30B-464F-B310-3196684B5ECE}
CHOLAME 2102X20 | {3EDA206D-0CFD-4058-8D33-8D070063612D}
CHOLAME 2102X22 | {8576EB3F-3AE6-4C28-B63E-BF3A9FDC680A}
CHOLAME 2102X24 | {ABA21501-8A25-4A72-8C77-6BC1E75D975D}
CHOWCHILLA 11045980 | {3042AF6D-6219-4BBC-85D9-7CCC6CE2F905}
CHOWCHILLA 110466907 | {3042AF6D-6219-4BBC-85D9-7CCC6CE2F905}
CHOWCHILLA 110483552 | {3042AF6D-6219-4BBC-85D9-7CCC6CE2F905}
CHOWCHILLA 1104856142 | {F0FB904A-2249-4717-AC11-FD12EE47DE5C}
CHOWCHILLA 1106275318 | {B03EE1B6-91C6-4B93-83DE-3440A7AD7AA8}
CHOWCHILLA 110652144 | {BCEA6632-4823-4DD4-9479-E91733D8C5A7}
CLARK ROAD 1101CB | {F673F67C-7B92-4672-819A-41DD2FB01076}
CLARK ROAD 11022044 | {62022298-C96E-4026-AE43-0F12DB277F1C}
CLARK ROAD 11022068 | {31C399B4-B5E1-4797-80CF-566E803A98B5}
CLARK ROAD 1102212118 | {1264D9D2-8375-4858-AD32-A3365D0B100E}
CLARK ROAD 11022582 | {E681E40E-5ECE-4E9E-921D-C13E15C00CCA}
CLARK ROAD 1102274916 | {8AF36E09-4D28-4660-897C-F5ECE008E9D4}
CLARK ROAD 110247006 | {EBE3D588-EDC2-4B91-924B-7B5E1D026A1E}
CLARK ROAD 110281296 | {242A0DDF-2969-4CDF-89E1-CB12AA379A9D}
CLARK ROAD 110281296 | {154C476C-5A31-47D9-B01B-5C020A5462D1}
CLARK ROAD 110290548 | {1DE99E4E-7765-44B0-9832-275F1EB7F7A4}
CLARK ROAD 110292622 | {4AC0D11C-BCBB-44BA-9487-96EC262DE746}
CLARK ROAD 110292622 | {381D7853-5A02-4486-A50E-C31E33DE4E4C}
CLARK ROAD 1102CB | {E6C812B7-52C7-47F0-B595-32AF66AB7A9D}
CLARKSVILLE 210319572 | {AE109701-21ED-44EA-AA47-DDDDD6EEFB68}
CLARKSVILLE 210351564 | {1D188BFE-6402-4FA3-8FCB-922AC5F45D03}
CLARKSVILLE 2103547420 | {9DEE0693-2AD3-4794-A608-F547DC530CB5}
CLARKSVILLE 2103593454 | {1F682AD1-C38A-4DAB-9AB0-5C203E1BC633}
CLARKSVILLE 2103593454 | {7F57523A-6D96-46DD-A031-59531C097C89}
CLARKSVILLE 21036842 | {85AB71C6-0381-47DE-A0EA-E430149236AB}
CLARKSVILLE 2103CB | {582D525E-AEFD-49AD-B483-1141532B60A7}
CLARKSVILLE 210413352 | {76CF34A1-3FD0-4E72-BAFC-6CFED61FA5FB}
CLARKSVILLE 210413352 | {3D2D9C96-4CB1-4214-89A2-5C3F980B327C}
CLARKSVILLE 210419632 | {E10F57CA-31E3-4642-897F-6FA410857C1A}
CLARKSVILLE 210419662 | {A9104265-B4F6-48EE-93C6-57B36F6C317A}
CLARKSVILLE 210419772 | {484A22B9-C40C-4E37-BA87-C46E298525CF}
CLARKSVILLE 2104432966 | {24BA7214-EA0E-4940-8D9A-B12BFFD010BB}
CLARKSVILLE 2104901184 | {62637953-E40C-402C-991C-40D9EA07D110}
CLARKSVILLE 2104CB | {24BA7214-EA0E-4940-8D9A-B12BFFD010BB}
CLARKSVILLE 2105385236 | {760BF466-E4DF-4A5C-B2C4-51F0ABE15277}
CLARKSVILLE 210551478 | {0F59AF2F-5869-40D3-A6B5-13E6D7B47101}
CLARKSVILLE 210575884 | {398A55C4-A233-41E8-986A-9CEE99885341}
CLARKSVILLE 2105CB | {9208AF25-E3F3-4F0D-8CE3-550040B29414}
CLARKSVILLE 210619642 | {6458AB58-DA5E-4D0A-95E1-69BD6C7E0EA2}
CLARKSVILLE 2106CB | {C9DBAC79-A55E-4BD0-B21C-240D7C28DE49}
CLARKSVILLE 210951742 | {678500B4-CC40-4993-94C8-A8D3584C2E9B}
CLARKSVILLE 210951744 | {D119674C-FF38-4F45-A342-82E8B18FF02E}
CLARKSVILLE 210951796 | {4682A97D-092B-40D3-AAD7-69641B1B3CC1}
CLARKSVILLE 210955666 | {58AFEF14-24B5-49DA-AC14-3989473D0CBD}
CLARKSVILLE 21096502 | {B1661BB1-2298-4568-8F99-3AB48F48A478}
CLARKSVILLE 21096502 | {A0936C28-A756-47FA-9C1E-76F4B7CFFF7E}
CLARKSVILLE 2109CB | {7686CD28-0AD3-49A6-802B-4CD3DF814107}
CLARKSVILLE 211011112 | {6508E8D3-0E1A-4D53-A06C-C666BBE3F64E}
CLARKSVILLE 211011142 | {3A0A47C5-9EE4-402A-889E-C298AEE1970F}
CLARKSVILLE 211019692 | {E7EDC231-ACD1-4AD9-A89B-5DAED0E6D6EA}
CLARKSVILLE 21106832 | {C549AB23-FF4D-4476-A6BB-298E3FC3CA01}
CLARKSVILLE 2110CB | {45555E2C-8D80-4EF7-9197-7511D877BC26}
CLAY 110113442 | {31882BA6-5D81-4512-9217-A61120B12235}
CLAY 110113450 | {27131A9E-D142-4A6D-93D0-301DB39F0FC8}
CLAY 110134470 | {7B0202BA-19F1-473A-BFC1-DFF4BE934494}
CLAY 110184572 | {537E07C0-FB8F-462B-87E9-2D8AA468190F}
CLAY 1101CB | {CC3A7F8F-5717-4639-B6A5-ECE8361467E4}
CLAY 11029999 | {D868AF66-93C2-4B3E-8187-2C428023C31E}
CLAY 1102CB | {D868AF66-93C2-4B3E-8187-2C428023C31E}
CLAY 1102CUST | {D868AF66-93C2-4B3E-8187-2C428023C31E}
CLAY 11031230 | {F04A9D2F-E7E7-4E86-8DA7-4CB111C7A3D6}
CLAY 1103142162 | {6EE33790-0FD0-414D-9B0D-F92660B5F1AC}
CLAY 110314674 | {6FB5453C-8E3A-4B58-AB8D-8BEBE74026D5}
CLAY 11031821 | {AE111B59-4073-4BA6-A6F7-C46E4FCA24F4}
CLAY 110334338 | {AE111B59-4073-4BA6-A6F7-C46E4FCA24F4}
CLAY 1103423390 | {0753BBD2-1EA2-4E4F-8F9B-8D8304275754}
CLAY 11035386 | {6E86E44D-E4BB-4FCC-B8C0-43D3EA2779B0}
CLAY 110359714 | {CC378BAE-BD49-4ABE-8599-52019F7E517A}
CLAY 1103636794 | {90124199-1243-4A62-BE12-797EFE6331CC}
CLAY 11037142 | {9E89ADDE-355B-4153-8A3A-140410223CE4}
CLAY 110398680 | {710E8DB6-BDC1-4CFF-BF25-79C21CA3FC16}
CLAY 1103CB | {12C9081C-95BF-4D8B-9422-8F9EBEEF2908}
CLAYTON 2211CB | {6C43A4A0-2BED-42F1-970F-3C9A6C36E609}
CLAYTON 2212158138 | {86E6EBE9-AB18-4CA9-B6B7-D151B1A6516B}
CLAYTON 2212204416 | {D1603D4D-EDBC-4667-A394-6A5E09388F26}
CLAYTON 2212334476 | {463B1668-4DE2-4C88-A747-EE241BC43F5E}
CLAYTON 2212523764 | {F3AF2874-1B26-4F8E-A2D1-24B02ACC6A03}
CLAYTON 2212614950 | {4884B072-CC16-4259-AE22-6A15B8CC59ED}
CLAYTON 2212681608 | {723EB3F4-8F25-4EB8-85CB-92E06EAD1463}
CLAYTON 221296224 | {3D0FC142-36D5-4662-84E1-74BFFF12E068}
CLAYTON 2212CB | {E96A0569-DCDE-4681-A6D1-E506A3CBE6D9}
CLAYTON 2212CB | {2D5D20E5-A0A7-4026-99AD-2AE1DA54D715}
CLAYTON 2213167700 | {C972F264-64D1-4FA4-8935-EB84A5191895}
CLAYTON 2213CB | {9C3B9F47-7C76-4D0E-A6EE-F40396E0D506}
CLAYTON 221442582 | {10733B2C-A5C3-4A9E-8D35-517FAE09EA04}
CLAYTON 221465785 | {10733B2C-A5C3-4A9E-8D35-517FAE09EA04}
CLAYTON 2214CB | {10733B2C-A5C3-4A9E-8D35-517FAE09EA04}
CLAYTON 2215257692 | {7B4DCBC3-18E1-4476-BFE4-2E2AC5317379}
CLAYTON 2215500240 | {6A2904BE-6CF6-42DD-B2C9-F94DF16B8A15}
CLAYTON 2215556215 | {D62CEB8E-E87D-4021-9028-58C41CA4CA60}
CLAYTON 2215738414 | {CF1FEF6D-0FE3-427F-8737-275A3F2A1936}
CLAYTON 2215812394 | {5C22565B-317C-4A78-8439-2CD9CE62BBBD}
CLAYTON 2215854706 | {28B7146E-127F-4EFE-8ACF-33260D39C115}
CLAYTON 2215880066 | {7D32A00C-635A-44F6-950B-F3537B52DE0D}
CLAYTON 2215917736 | {67ED4926-F36E-4F04-ADB2-051BB02280D4}
CLAYTON 22159765 | {67ED4926-F36E-4F04-ADB2-051BB02280D4}
CLAYTON 2215CB | {17D49159-2A99-4FB5-B2DC-0815D2D13280}
CLAYTON 2215CB | {B309937E-0964-40FF-8814-070F4ACC72D8}
CLAYTON 2215W531R | {32128C45-30E5-4BD3-83C6-38B6DDD0B832}
CLAYTON 2215W573R | {C86C14F4-2F7A-4D9D-966F-4FE249C0F52F}
CLAYTON 2216973974 | {5C8E4C32-BE49-44F7-9A24-1083188EB5C9}
CLAYTON 2216C544R | {FB68D9A3-39C1-4B03-AC25-256EB07FCA5D}
CLAYTON 2216CB | {DB6FE7F1-AC75-4C7E-83AC-CE5B6DE225C5}
CLAYTON 221738248 | {2E89F027-67FF-4082-9169-E158A83D0166}
CLAYTON 2217610012 | {2E89F027-67FF-4082-9169-E158A83D0166}
CLAYTON 221798080 | {02D34549-5AC7-4AFF-A057-7824A31FF47B}
CLAYTON 2217C500R | {2E89F027-67FF-4082-9169-E158A83D0166}
CLAYTON 2217CB | {2E89F027-67FF-4082-9169-E158A83D0166}
CLEAR LAKE 11011302 | {4A405FCD-64B2-4AE1-B455-764875D385D0}
CLEAR LAKE 1101444 | {55694D06-24E9-4D6D-8BD5-E5D434DB5805}
CLEAR LAKE 1101463019 | {AEC4E39A-0C5A-4725-BA13-BF05A6D170ED}
CLEAR LAKE 1101486 | {168A101A-B40A-4107-A560-9FF95054D3E7}
CLEAR LAKE 1101529830 | {8781E0D9-6F77-4BEB-91DE-4576788081CC}
CLEAR LAKE 1101699062 | {93794068-C446-4FF0-B0C2-C723FD11D3AC}
CLEAR LAKE 1101740076 | {AF3B7AFC-B2F6-4613-A8C9-551A8B6F40B8}
CLEAR LAKE 110181976 | {4B824BDA-3530-4F86-B304-5BB8EAFD0730}
CLEAR LAKE 1101872376 | {88C4FFE4-36D0-4FDF-B251-5B6E25579BA4}
CLEAR LAKE 1101881362 | {22A23993-BAC9-4CAA-B619-505FC6C27874}
CLEAR LAKE 110192870 | {91E6CF65-65E6-49D9-99AE-7F739C671773}
CLEAR LAKE 1101CB | {4B824BDA-3530-4F86-B304-5BB8EAFD0730}
CLEAR LAKE 11021167 | {21B5F0C5-3885-4C31-AB7F-1F0A40AD14F1}
CLEAR LAKE 1102223792 | {EE43D8DE-EC78-4D51-AA66-FA42E0AD335E}
CLEAR LAKE 110237580 | {2BE21FFC-75C5-4000-AF51-9092A99D4F5A}
CLEAR LAKE 110237582 | {71FD6122-F69C-494A-9394-43B425D2AC38}
CLEAR LAKE 110245252 | {20F1CD1C-92B1-4CFB-8088-D50E75A94B87}
CLEAR LAKE 1102626634 | {8D4D53C7-69F5-4DF7-89C3-CA4E3B7FAF38}
CLEAR LAKE 1102655 | {489F038A-4B72-4F00-B9CE-E13F0B4FAE5A}
CLEAR LAKE 1102697276 | {4E8C02F5-97A1-4413-B4FC-B5FDA16266D7}
CLEAR LAKE 1102697276 | {A2C04B2A-E46B-4144-845F-8FC5D9963BCD}
CLEAR LAKE 1102720 | {71FD6122-F69C-494A-9394-43B425D2AC38}
CLEAR LAKE 1102832686 | {4352C464-74E0-4EAA-9A4D-DC58892F06BA}
CLEAR LAKE 1102904 | {F2BFF36E-7C09-45BB-8051-33603CB60365}
CLEAR LAKE 1102CB | {35CE18CF-0731-4236-B455-551D76E65366}
CLEAR LAKE 1102CB | {F863487A-BF6B-4D3E-93AD-9325B53F05BD}
CLOVERDALE 1101112 | {A3010E82-252F-4B74-842A-7F85E53824BF}
CLOVERDALE 1101112 | {21392700-9E2C-4DF7-B804-2EC4976596B1}
CLOVERDALE 1101112 | {EFFBC73B-5CF0-4391-8D52-00A9D7379A46}
CLOVERDALE 1101112 | {1E501E9A-8949-4278-8D21-F330EF7F0FFB}
CLOVERDALE 1101409224 | {B0E9356B-01BC-40EC-86CF-A93C8EF70CFD}
CLOVERDALE 1101474708 | {70DF189A-0B8F-41F8-947D-2C012503D21C}
CLOVERDALE 110184088 | {58421E59-40D9-4FE6-B6D2-E336A596F8EF}
CLOVERDALE 1101964556 | {C8B8F7FB-319D-436A-B288-8DB11A5DC4AF}
CLOVERDALE 1101964556 | {82D40951-8600-46D0-B24C-ADD5CEAA0C89}
CLOVERDALE 1101CB | {1FD9348C-4D4E-4981-80D7-DF41347DC4BB}
CLOVERDALE 1102156 | {0AFDFC2C-BE93-4295-B473-DFD529280FFF}
CLOVERDALE 110220120 | {D4BDCBBA-B7D7-4BE6-B719-B97CF2ACFA68}
CLOVERDALE 1102262 | {79D04444-8804-48FE-A949-F2CD7D36457D}
CLOVERDALE 1102307342 | {A0D136BC-BED5-4E61-825E-2EC84D15BD33}
CLOVERDALE 1102383183 | {3086B2C7-251B-4A28-B076-620967073FDC}
CLOVERDALE 11024646 | {08D74C7F-8D6E-4EDB-8355-DEA79828121D}
CLOVERDALE 110247214 | {08D74C7F-8D6E-4EDB-8355-DEA79828121D}
CLOVERDALE 1102570 | {32B34880-BC93-4771-BC39-2E887BB96BE8}
CLOVERDALE 1102654084 | {5BCD5375-5195-4DF6-9339-79690A1EF9AB}
CLOVERDALE 1102670 | {40B1E31D-7977-4CD1-A0DB-03E15686CC3E}
CLOVERDALE 1102672 | {B86F1274-5A5C-436E-B792-43E98848CB75}
CLOVERDALE 1102674 | {D3629DD4-F83C-4237-B37C-A36F4F11F0E0}
CLOVERDALE 110276878 | {2F9CFC90-9586-486F-B26D-D17BDCC89525}
CLOVERDALE 110282888 | {B5A8374E-B790-43DB-958F-6C84A7C12E44}
CLOVERDALE 110294476 | {80FED0BE-D166-42DD-AD9D-F9569A62BF53}
CLOVERDALE 1102CB | {A0D136BC-BED5-4E61-825E-2EC84D15BD33}
CLOVIS 110265614 | {B82FA9FD-76F9-4AEF-A9A6-7A2EFF9882E8}
CLOVIS 110285140 | {BF58BE07-BC4A-4C50-9D76-6121EAB3DC85}
CLOVIS 1102CB | {B82FA9FD-76F9-4AEF-A9A6-7A2EFF9882E8}
CLOVIS 1107322332 | {391E76BA-894F-4418-9592-5618A374F89A}
CMC 1101CB | {BCDF55E9-752A-4470-8F8D-971D8F755C6B}
CMC 1102CB | {8AF78B6A-BE16-4226-B393-4AC8AD7FF084}
CMC 1102CUS6960 | {8AF78B6A-BE16-4226-B393-4AC8AD7FF084}
COALINGA NO 1 1107CB | {CAFC6C3B-18ED-40FE-9F55-0436E5310EEA}
COALINGA NO 1 1108722420 | {EE71F2CA-8B22-4516-893E-D39A3D893F22}
COALINGA NO 1 110878186 | {FE0D541A-B7A8-4065-95FA-90BEC263D4F2}
COALINGA NO 1 11089080 | {C2C023AD-0CC1-4E83-AF7F-98D1E04D84AD}
COALINGA NO 1 11089240 | {B19BD356-9072-48E8-A723-5009229A194D}
COALINGA NO 1 11089501F | {36B87616-D679-4742-9439-9BB449E5F7F1}
COALINGA NO 1 11089501F | {AE80C103-54B6-4889-8556-D7A5BEC99C4B}
COALINGA NO 1 11089850 | {F669006F-0523-46A6-B70E-336574BBAF0F}
COALINGA NO 1 11089860 | {382A672C-5BFC-4C8B-930D-3F4093A2C242}
COALINGA NO 1 11089864F | {05FAD7DE-C3C3-47CB-BC8D-16AF839D82E9}
COALINGA NO 1 1108CB | {D0D57548-BFE1-4E51-8167-796FFB6E7A8E}
COALINGA NO 1 1109696152 | {D2837AC8-6682-41DA-9CAE-EF262EB89AC9}
COALINGA NO 1 11099210 | {1B415827-7E73-4327-8D34-697190EF078A}
COALINGA NO 1 11099270 | {FEF9CC74-086D-453B-B63D-D3924FF51CC0}
COALINGA NO 1 11099870 | {FEF9CC74-086D-453B-B63D-D3924FF51CC0}
COALINGA NO 1 1109CB | {FEF9CC74-086D-453B-B63D-D3924FF51CC0}
COALINGA NO 2 1104CB | {A746A1F0-D3DE-4B95-ADE9-A7CBCD9D1F50}
COALINGA NO 2 1105108592 | {D8597270-205B-4E5C-B6F8-6481A227BCEB}
COALINGA NO 2 1105134928 | {9059C27A-D715-4C08-BE52-657FEBC0680B}
COALINGA NO 2 110541882 | {CEE94242-50A6-4818-9FE5-BD8EB00183DB}
COALINGA NO 2 110541954 | {8311BA01-975F-40BD-9A68-D357106FF2E2}
COALINGA NO 2 110541954 | {90AEEBB8-CCE7-458F-AF2F-7D8FEF1C57D6}
COALINGA NO 2 110541954 | {5215DD87-4C4E-4B9C-82FD-42405AA7934A}
COALINGA NO 2 1105897858 | {BB2EB972-0241-4416-BB6F-CD01FA83C53E}
COALINGA NO 2 11059000 | {09F38874-A51D-4724-BABB-AF0D78EDB524}
COALINGA NO 2 1105CB | {17191ABE-2F57-43C1-A179-D9C5A3AD8203}
COALINGA NO 2 110677252 | {A60E3185-D80B-447F-9B0D-05EDACE2420F}
COALINGA NO 2 11069150 | {A68C2CD2-5B38-436A-BF15-89ADDC817323}
COALINGA NO 2 1106CB | {9066DE31-A190-43D2-884C-C4F88C8CE7A3}
COALINGA NO 2 1107129094 | {BFA1A574-4617-443D-8972-34C8CCB23680}
COALINGA NO 2 110770250 | {C9B31884-8FA9-436F-9425-CE594852B802}
COALINGA NO 2 1107793144 | {54AFCD17-4BB7-4BDD-87FC-7E813F8220FC}
COALINGA NO 2 1107CB | {BFA1A574-4617-443D-8972-34C8CCB23680}
COALINGA NO 2 1107CUS6279 | {BFA1A574-4617-443D-8972-34C8CCB23680}
COARSEGOLD 210210040 | {68513B5A-56EB-4D19-97D2-4A9509C9FEBC}
COARSEGOLD 210210040 | {12708C05-8C6A-4DC3-9E2A-9B6F84E84FD7}
COARSEGOLD 210210050 | {246AEE64-BD98-43AF-876E-DF5040419CD3}
COARSEGOLD 210210330 | {FE7641C5-7812-4FD4-8B21-6308923D8DFD}
COARSEGOLD 210210610 | {8FCA88A2-5287-4980-B557-B7704EA7B310}
COARSEGOLD 2102383092 | {F369BA13-9B42-42C0-8490-6E6238248F21}
COARSEGOLD 21025380 | {28AC0DE3-760D-482C-B0A3-0B7999D74D44}
COARSEGOLD 21025721 | {B9D598D0-1E00-48FB-B52F-F61FF97AB941}
COARSEGOLD 21025722 | {28AC0DE3-760D-482C-B0A3-0B7999D74D44}
COARSEGOLD 2102CB | {5FCD3F70-B3EF-41B7-B59A-4AF393BD948D}
COARSEGOLD 210310300 | {D52EB2EB-C85C-45E0-96F5-17449635DB4E}
COARSEGOLD 210310776 | {FFA233AB-FC1E-47C3-8A02-3709DB319511}
COARSEGOLD 2103215516 | {B2E4E1DC-85C2-410D-9F32-E3576DACF3D8}
COARSEGOLD 21035020 | {19623F95-3D51-435E-B42C-17FE4878C880}
COARSEGOLD 21036110 | {04B6E7EF-7D58-4AD6-8C95-F9DC0FD8A439}
COARSEGOLD 2103724496 | {AE2B107B-3AB7-4D9D-BD73-51FE57753B52}
COARSEGOLD 2103731524 | {906462EC-73D3-4A4A-8B59-E052896B0724}
COARSEGOLD 2103988096 | {7584D05F-12B1-4E0E-879F-5BA845EF90AE}
COARSEGOLD 2103CB | {2E4BA31C-6FC8-4D7D-B79B-DB347A05F67C}
COARSEGOLD 210410030 | {A8CB9256-CE86-4125-B378-C2EE50D5BB11}
COARSEGOLD 210410110 | {0324E4A5-AA18-47DE-BE15-56C96BB7C3F8}
COARSEGOLD 210410110 | {D3DB4160-C2D4-42BA-AC1F-E720E9BDC434}
COARSEGOLD 210410160 | {5FAF7A03-8AC9-4665-B0CB-35D3F4BB7385}
COARSEGOLD 210410160 | {A204F83A-3970-43D2-B644-5FB512D6BA91}
COARSEGOLD 210410160 | {39B5E77C-E082-4504-8594-59569A7FC661}
COARSEGOLD 210410160 | {38221EC1-1BBB-45F5-AC2B-A2116A4D8423}
COARSEGOLD 210410400 | {7CAE9E3D-9A6E-4166-92A3-E494C4AA002D}
COARSEGOLD 2104320370 | {F11DC782-1F4C-4436-B59B-6978D4B3AE00}
COARSEGOLD 2104369777 | {12F05A59-1EDC-4386-9A82-0107067D2899}
COARSEGOLD 2104562152 | {53CCCC83-3C44-4BAE-AD69-57D269E535E5}
COARSEGOLD 2104570682 | {9485A7D0-401F-403C-A8F4-B704232548DB}
COARSEGOLD 21046285 | {C79EEAF2-6A1B-4D1B-85A3-D82D59AF94D1}
COARSEGOLD 2104641200 | {DD5F7163-CCAF-4F92-84A5-02E15E5AF6B7}
COARSEGOLD 2104679640 | {459A1C12-55F0-4B6F-B0BA-A3547FB6A27B}
COARSEGOLD 2104791582 | {709102C8-BC3E-47E7-AF09-1C6848A793AA}
COARSEGOLD 2104828842 | {8C9C1F4D-9C24-4A9A-947D-D1CEA924DCBB}
COARSEGOLD 210490356 | {469CEF87-E711-4F83-A7B2-29DFD34E1A44}
COARSEGOLD 2104905960 | {1CD81986-0B0F-405F-918A-03A8DC4F382E}
COARSEGOLD 2104905960 | {D13472F2-B468-44F9-94C6-B98D2DACFC98}
COARSEGOLD 2104CB | {9126AC99-906D-4CEE-8034-3EECC4C90F16}
COLUMBIA HILL 11012212 | {912073EB-9613-41BB-A620-406DBA7A7868}
COLUMBIA HILL 11012212 | {04384579-0651-4BF6-A92C-36154DEBC10E}
COLUMBIA HILL 110135424 | {474A8BDA-95BF-4717-B362-885E409D4F7A}
COLUMBIA HILL 1101764 | {9DC430E4-865B-40A1-B9ED-F689C9145BC5}
COLUMBIA HILL 1101764 | {3151D4D6-E560-46C2-9734-65AECAE37C3A}
COLUMBIA HILL 11019019 | {C6E7737B-9672-443F-A310-F78E46864269}
COLUMBIA HILL 110190730 | {8D36000E-CB6A-4063-B9B3-E1FA6651AB85}
COLUMBIA HILL 1101CB | {033B4911-2D36-4FC4-814B-7A242EEF0004}
COLUMBIA HILL 1101CB | {5FAB0BE8-C348-4680-AAD2-04359C7DB8ED}
COLUMBIA HILL 1101CB | {472D2B95-5CE0-4AF5-93B6-7762ECA68067}
COLUMBIA HILL 1101CB | {ADBD977F-685F-4CA8-8D8E-4BB250559FB0}
COLUMBIA HILL 1101CB | {AFE65AF8-60AD-4B2F-94C0-CF52D73AF5E7}
COLUMBIA HILL 1101CB | {1F2E8865-F4B7-450B-ABE9-98BA0313239B}
COLUMBIA HILL 1101CB | {301371C1-F917-4D83-99A4-9C27E8A52D68}
COLUMBUS 11051767 | {3F8027D2-0389-4022-AA52-2EE0133FB2A5}
COLUMBUS 11054055 | {C2884774-2BB3-482E-835E-A15E46B4CA59}
COLUMBUS 11054059 | {C2884774-2BB3-482E-835E-A15E46B4CA59}
COLUMBUS 1105CB | {679CE7F3-AF0D-465D-B90E-D94D74EFBDDE}
COLUMBUS 11093953 | {4958D282-0BA3-4E65-9734-379E63CFCB91}
COLUMBUS 11094443 | {4958D282-0BA3-4E65-9734-379E63CFCB91}
COLUMBUS 1109CB | {4958D282-0BA3-4E65-9734-379E63CFCB91}
COLUMBUS 1109CUS3980 | {4958D282-0BA3-4E65-9734-379E63CFCB91}
CONTRA COSTA 2108CB | {FBD8C62A-ECAB-4F1E-96CB-B818051971B0}
CONTRA COSTA 211496897 | {E98A5614-0363-4815-B36D-4D8FAB4E4D57}
COPPERMINE 110438474 | {E99FC5E0-5A56-4D2F-900E-4A688BBB4069}
COPPERMINE 1104556430 | {B8BBE87E-B0E7-4F0B-A461-482C2514F445}
COPPERMINE 1104613086 | {3C011A8C-6358-4933-B5ED-50C9AF8F36E1}
COPPERMINE 110496648 | {688691F4-465E-42D5-9D8C-EE4B09B03087}
COPPERMINE 1104CB | {688691F4-465E-42D5-9D8C-EE4B09B03087}
COPPERMINE 1104R3170 | {4532B921-F6B7-42D7-8837-06939F7F1ED4}
COPPERMINE 1104R3200 | {D5328BB7-8D1B-4713-8DFA-263EA71DC9E2}
COPPERMINE 1104R755 | {936C9612-ADD7-4621-B76D-EE018B141219}
COPPERMINE 1106CB | {335BC001-CE71-40A7-9953-1E9872ED486B}
COPPERMINE 1112CB | {390F6795-E424-4A14-B8CA-36C5E71EFA24}
COPPERMINE 2110CB | {5568B2AC-3857-4707-8915-76764205A1B0}
COPUS 1102205562 | {BF32585B-B787-4091-B144-21163D09ED28}
COPUS 11022399 | {A0EF704A-5AE9-46C9-93F7-47C91167EF5B}
COPUS 1102303046 | {2E898B0B-B15A-45F7-86BA-F1749208E3BD}
COPUS 1102CUS2962 | {BF32585B-B787-4091-B144-21163D09ED28}
COPUS 11043551 | {58F9C820-4F76-4357-AC3E-8235F5BDF060}
CORDELIA 110440922 | {83B65017-0E83-4527-8A4F-FF03D1E38C40}
CORDELIA 110448536 | {B19C47CC-F62E-4F48-9076-9FAF34BF321E}
CORNING 11011440 | {9D5A9B31-B8A8-4B57-9A99-1D5479FD613A}
CORNING 11011620 | {6DD0C71B-76D1-4BA7-A46D-8A6279F753E7}
CORNING 110135974 | {1508BCF5-AB97-4CDF-A787-A57A58E9D5A2}
CORNING 110146022 | {96E54BE4-646F-42C8-A68D-ACB997092DF5}
CORNING 110154906 | {1A1AF20D-E504-4C2E-81C6-87E33D50E68E}
CORNING 110164090 | {9C401B14-4A54-4DA8-B9DB-3EDB68F74D1D}
CORNING 110164132 | {9240C96F-E1A7-4EB8-895B-98779A72FDD3}
CORNING 1101773679 | {15290004-331F-45B6-AB86-67F5DC98CB9F}
CORNING 1101799972 | {3037D4DE-B77C-4B55-84CE-869E2F807214}
CORNING 110182846 | {0237A482-F336-4387-BDDB-C855D376A309}
CORNING 110185122 | {83471AED-7A31-4D8C-9060-987B78A1FED5}
CORNING 110185152 | {8A23E27A-2CB7-42F5-83CF-F099215B2762}
CORNING 110185152 | {483043A7-7A4D-4601-B7F1-CAD25B89A5CF}
CORNING 110185152 | {789DE4DB-ACCC-46BB-B059-D9142CE79F75}
CORNING 110185162 | {9C401B14-4A54-4DA8-B9DB-3EDB68F74D1D}
CORNING 110185213 | {BBF640A9-698F-4DA2-8628-DB1BBC7FB9C4}
CORNING 110187304 | {A9C774C3-1428-4B46-A99D-50AD5766C649}
CORNING 110193362 | {1508BCF5-AB97-4CDF-A787-A57A58E9D5A2}
CORNING 1101972454 | {1508BCF5-AB97-4CDF-A787-A57A58E9D5A2}
CORNING 11021622 | {96C223CD-EECE-427E-9B50-0567153A92FD}
CORNING 11021622 | {1E555403-7FC2-464B-BDD6-14FBD4EE8B9D}
CORNING 11021666 | {75BA43D5-036C-4D69-AA67-0F28603F12A6}
CORNING 11021900 | {097280CB-BBAB-443B-A213-61E2653EB02B}
CORNING 11022029 | {D940129E-2F21-4BA3-94CB-49D3F1E7AEE0}
CORNING 1102305332 | {06847180-4D1F-40C8-B7D9-99A63FFBCE91}
CORNING 110237398 | {EACD8289-5D7A-4EFF-8DCC-1E85E9255904}
CORNING 110253184 | {15DF5EF9-6694-4A35-B7F3-919A8A286CFC}
CORNING 1102630712 | {82559D15-D4A8-43B6-85EA-6434E2A32780}
CORNING 1102915324 | {097280CB-BBAB-443B-A213-61E2653EB02B}
CORNING 11031628 | {EC952F54-C300-4DC5-8566-7547D561FE6A}
CORNING 110337546 | {4CCC4243-0BB7-470D-AABB-D9BCC9E3613F}
CORNING 110349740 | {D4FB5B4E-8347-4531-AA48-355E5A6F473F}
CORNING 110366390 | {32045170-E378-4F87-8F1E-4580C2F37475}
CORNING 110368304 | {A98FCDBF-127D-419A-B966-65773B26BEDA}
CORNING 1103922360 | {15BEB41F-CFF0-4E2D-85DD-33D0FFAD5BB9}
CORONA 1101248 | {028C9314-BFED-46A4-8526-CFB499FC78E8}
CORONA 1103176 | {C751DAA9-A68F-4E3E-9A3D-8380575CF487}
CORONA 11034446 | {D1AA7A01-6717-4A8D-8AC5-0F1F18BEAC1F}
CORONA 11034446 | {DC9BD939-EE4C-4BE5-8C2C-6AD7A533B4E4}
CORONA 1103776806 | {02DCFD19-ACE4-4ED7-8974-B818BB682331}
CORRAL 110112304 | {95CAC7AA-1B21-40B1-A176-356923BEEB13}
CORRAL 110112606 | {83EA1908-090F-4204-B568-C4FACFA08477}
CORRAL 110112612 | {30A29F57-3EDB-40DD-A238-DD66DF206CFB}
CORRAL 1101173174 | {488178E5-61FC-444B-88C1-9B8C60F860FF}
CORRAL 11012128 | {B16B71D1-22D0-45E3-8592-F21047B1C034}
CORRAL 1101220994 | {A6323C32-8311-4368-BEEC-212DDF7458C7}
CORRAL 110133616 | {C0EF126A-6BDE-4B56-BFB5-8D9A05C3D2AC}
CORRAL 110136652 | {B537B104-D44A-45F9-BCC9-AE639B2EEDC6}
CORRAL 1101639614 | {6157CE71-7864-4436-AA7C-5C09CBEE33F6}
CORRAL 110175204 | {C6783DDC-8CCC-4EFE-8097-5CE8336375DE}
CORRAL 1101CB | {67B48D0E-E0F7-48F9-B3C0-C31311AFB61B}
CORRAL 1101CUS9215 | {488178E5-61FC-444B-88C1-9B8C60F860FF}
CORRAL 1101D1495 | {B16B71D1-22D0-45E3-8592-F21047B1C034}
CORRAL 110214026 | {9D2DD8C8-FD4B-4B60-ACA0-0CCE69EA2F96}
CORRAL 110214028 | {485BC0B3-AC72-4623-B01D-27E2B69AFA49}
CORRAL 110236666 | {D6BA7AB0-BD1E-4258-B5D5-B64D6E99400B}
CORRAL 110275622 | {C5570B1A-B071-4827-88D1-68633BB92AFE}
CORRAL 1102CB | {A70761E3-E888-44FB-B083-651B5C823F25}
CORRAL 110313474 | {6748E8F4-5236-4133-9E21-482CCE2EC069}
CORRAL 110314716 | {69E7CCAD-089B-4A0D-AFD3-F9DC2B18E72C}
CORRAL 110336680 | {EB467927-3D28-42DC-B202-516334CB2DF4}
CORRAL 110359770 | {A87A01D7-FDFF-4B8F-B41F-FAA11796C3AB}
CORRAL 1103936674 | {6A75A276-6764-44DB-AA5D-741492F8A6AA}
CORRAL 1103CB | {64858239-7E97-43B3-8DF6-6A5627532E97}
CORRAL 1103CB | {03D991AF-6109-4C4F-9E0E-284738E05B02}
CORRAL 1103CB | {4981751E-CE05-4494-A91D-08CCD674D767}
CORRAL 1103CB | {9A391715-6E90-453E-8F9B-52BCEA2804B7}
CORTINA 110130006 | {E3B77E93-BB57-4588-891B-4456F675EF56}
CORTINA 110130016 | {E3B77E93-BB57-4588-891B-4456F675EF56}
CORTINA 110130192 | {E3B77E93-BB57-4588-891B-4456F675EF56}
CORTINA 1101302192 | {C85ADA73-8870-45FD-B010-320E0217B2D6}
CORTINA 1101302192 | {E3B77E93-BB57-4588-891B-4456F675EF56}
CORTINA 110130262 | {E3B77E93-BB57-4588-891B-4456F675EF56}
CORTINA 11013056 | {E3B77E93-BB57-4588-891B-4456F675EF56}
CORTINA 11013058 | {E3B77E93-BB57-4588-891B-4456F675EF56}
CORTINA 110137554 | {E3B77E93-BB57-4588-891B-4456F675EF56}
CORTINA 110149858 | {CE64727D-AFA9-4CB2-B083-0E8C4E6C1F9B}
CORTINA 110189686 | {E3B77E93-BB57-4588-891B-4456F675EF56}
CORTINA 1101CB | {E3B77E93-BB57-4588-891B-4456F675EF56}
COTATI 1102282 | {25F749B3-A74D-4E71-A304-4CB2AAD2E132}
COTATI 1102282 | {307C6E99-F23B-44B2-9403-EE1517D0BB70}
COTATI 1102462 | {752A255C-25AB-486C-849A-6B37BD05DF59}
COTATI 1102464 | {E06C85FF-5B48-4064-AE0D-D34C585D0676}
COTATI 1102468 | {16354696-727C-4984-B8B7-F51CF686C119}
COTATI 11025080 | {16354696-727C-4984-B8B7-F51CF686C119}
COTATI 110257108 | {A14958E1-D297-472D-9215-4ED35B3E001F}
COTATI 110259258 | {94E0088D-6FDA-42A4-A01C-471E05EB28CA}
COTATI 1102825 | {94E0088D-6FDA-42A4-A01C-471E05EB28CA}
COTATI 110283200 | {A14958E1-D297-472D-9215-4ED35B3E001F}
COTATI 1102CB | {991C05ED-971F-4D32-B6E6-51948C4F329B}
COTATI 1103132 | {0BC4DF2E-A149-4CB4-954C-46E1120FDBD8}
COTATI 1103148 | {E6932BC8-83DE-4484-A9F8-B83591D802E2}
COTATI 1103267370 | {A3999210-0621-4637-83D0-49BA6466DB59}
COTATI 1103310 | {40F0C968-F731-4A61-A453-D93A6C5B08AE}
COTATI 1103446 | {181E81CC-8A10-40D6-ABD4-3AD397DDF786}
COTATI 110361736 | {BCD422E2-9AE0-44D1-BF49-26A0E5D7C844}
COTATI 1103621078 | {A2DDF03A-CB1E-4268-A8BB-1D52CCD7F4B7}
COTATI 110379140 | {8B07F2D1-E8C2-46BF-BEB1-6EA256DCFEAC}
COTATI 110387402 | {EEE52A91-AF03-4B18-9CCC-F7F6825D7052}
COTATI 1103CB | {9A3F5ECF-0D58-446E-BB8C-0FCF9D3017A7}
COTATI 1103CB | {181E81CC-8A10-40D6-ABD4-3AD397DDF786}
COTATI 1104232 | {0D1EAD50-F416-4D20-B817-3BDC9FDA64E8}
COTATI 1104426 | {B13BE392-390E-4E3B-A432-5336348FF9E8}
COTATI 110475972 | {A8AFA199-8340-4CFB-8F0F-27828B093B75}
COTATI 110494186 | {2F39A049-2BA5-4A00-94B6-4F8A51F9E4CE}
COTATI 1104CB | {D0082608-F94E-4A4E-A9EF-A114F6AAC5C3}
COTATI 1105103816 | {775E53AE-0A4A-4EB7-B07F-0C65E0B68CCC}
COTATI 1105104502 | {1E254E89-80C2-40C5-86C1-3418E85098A5}
COTATI 11052121 | {554E4D6F-0779-4CD2-B95F-DB489BEA9C8F}
COTATI 1105213984 | {681EF2A3-DED2-470D-950D-0263CA946ECD}
COTATI 1105292326 | {EFC49C22-4FE7-4DE7-9C3A-62D64894324A}
COTATI 1105328 | {711CF875-45FB-4C9E-91F5-632D204CB23D}
COTATI 110536536 | {554E4D6F-0779-4CD2-B95F-DB489BEA9C8F}
COTATI 110536536 | {59C20F9E-941B-4368-AC69-729A9F11D7BD}
COTATI 11055156 | {ACC3FA28-9FAB-4AE9-AABE-1ABF0B659322}
COTATI 1105606190 | {4F20DCB4-F85A-45A4-A57B-B2D116AC5E33}
COTATI 1105616 | {6AC0ECBC-74AD-428D-833B-C292E3BD3458}
COTATI 1105844060 | {8FC5790B-23DE-4032-81D7-65E070CCE3DA}
COTATI 11058459 | {1E254E89-80C2-40C5-86C1-3418E85098A5}
COTATI 110599720 | {711CF875-45FB-4C9E-91F5-632D204CB23D}
COTATI 1105CB | {03190DAD-5324-4E1C-86DE-04D88D55A9A0}
COTTLE 1701246168 | {57CFB929-3B5E-4B4F-A512-0DD7E750CC8F}
COTTLE 170139546 | {15BAA95B-AE18-43EB-909B-A990B51DB78E}
COTTLE 170144183 | {2F67CBBC-F160-4E90-BD4C-A4B9FEA8300D}
COTTLE 170149704 | {F39A2933-94D3-46C0-B046-E562EB078272}
COTTLE 1701498444 | {84E892B0-A5DA-42AB-B054-207DF2B66532}
COTTLE 170178452 | {D07798BA-B7E6-4FB9-A5A9-A05BC7F2FB6F}
COTTLE 170194082 | {03F0CE5B-338A-4FB3-B9BB-CF2EB9F1A657}
COTTLE 1701CB | {F39A2933-94D3-46C0-B046-E562EB078272}
COTTLE 17026318 | {AF187BA4-684B-4BA6-AE38-39C6DA9D0863}
COTTLE 1702704450 | {AF187BA4-684B-4BA6-AE38-39C6DA9D0863}
COTTLE 17033292 | {E8B81995-90FF-4F6D-BD2F-471CABC1BF0A}
COTTLE 170847747 | {9FFC0599-7BDD-4120-9A8C-31EF3E3F7596}
COTTLE 1708728510 | {394CDBEC-A00E-4775-A418-69F3C43E4BC5}
COTTLE 170889662 | {A9C6870F-B02D-4E3D-84FB-7B93865B2BC9}
COTTLE 1708968888 | {9FFC0599-7BDD-4120-9A8C-31EF3E3F7596}
COTTLE 17089860 | {EF760450-32FF-482A-AFAF-6B26A5B571C3}
COTTONWOOD 11011510 | {5015BD4C-1343-44E6-A042-6E4A95169A73}
COTTONWOOD 11011610 | {FD19D23C-6A96-40C9-9542-F7EF9A6AB34E}
COTTONWOOD 11011610 | {5D333E8A-D690-4D85-98EF-024A7D0BF424}
COTTONWOOD 110131500 | {5015BD4C-1343-44E6-A042-6E4A95169A73}
COTTONWOOD 1101384360 | {6E9AA275-95DB-4AA1-8ECE-7A4C85318300}
COTTONWOOD 1101384360 | {A7550642-0D72-41F1-BA6F-2A6F710153F0}
COTTONWOOD 110168190 | {B9D0806A-E952-4DB8-821A-8A74AB16F016}
COTTONWOOD 1101CB | {509EDC5C-5C13-447D-BAA5-6AE957D846E4}
COTTONWOOD 11021578 | {0E682A09-C0D8-404A-8B27-2B967048024C}
COTTONWOOD 1102544790 | {7F934250-B67B-44F2-9547-08902728DC9E}
COTTONWOOD 1102CB | {7F728486-5D30-4578-BA26-525DB688C650}
COTTONWOOD 11031344 | {B1A37D66-F35D-4EB7-8214-339B94F2CF9F}
COTTONWOOD 11031348 | {7B732F61-9830-429D-98CB-A07442DFF2C3}
COTTONWOOD 11031508 | {86195D79-B13D-4A31-9815-45E1A5BFFF0A}
COTTONWOOD 11031616 | {6AAE7F1E-BB91-4B40-919F-7A37BE5E005F}
COTTONWOOD 11031616 | {DB1CB0BF-953F-4047-B280-2F768227CB6A}
COTTONWOOD 11031616 | {C5040B2B-4C8C-4639-95E4-0DB3DBF91F3A}
COTTONWOOD 110331548 | {AD28CBC4-C4F7-4A16-8577-33ED0BB05DAC}
COTTONWOOD 110335470 | {E7F7F25C-AE9C-459D-9EB5-32BCE8602EF6}
COTTONWOOD 1103389928 | {323D98DF-F7C8-439D-8E63-3A2D9C1F2EC2}
COTTONWOOD 110359128 | {7A360B24-DB74-4302-B7FF-A7991F9BEB20}
COTTONWOOD 1103732932 | {B34D6510-4EA4-4D05-870A-2F82DCFA67AE}
COTTONWOOD 110385050 | {7567B55E-AD2E-47FA-B262-240B7B9C7A1E}
COTTONWOOD 11039072 | {CCBE325F-DB08-456F-8920-C4494B0832D2}
COTTONWOOD 1103957942 | {FE2A03BF-2A82-4C60-A029-FE923684D1C7}
COTTONWOOD 1103CB | {7A360B24-DB74-4302-B7FF-A7991F9BEB20}
COVELO 1101112804 | {5A8F3694-A0F4-41C3-88AB-492CAEAEF38E}
COVELO 1101225458 | {A1037E1E-1E0B-4B86-909D-EE36FE670AFC}
COVELO 11012467 | {149E5268-4926-4B7A-B9E2-928EA9B5F83B}
COVELO 110137328 | {D4E144DE-8AEF-45D3-9080-EB1CCEA62B46}
COVELO 1101430286 | {64F3E707-0C89-449C-A14A-0CB9EA1C7E88}
COVELO 110146208 | {1E92B113-D351-4051-A3ED-221149B2FA2D}
COVELO 11014678 | {8CC880C0-D20D-47C4-883B-62E97018E45A}
COVELO 1101516510 | {BF61C71A-A0DD-4587-ACF3-DC551BEE5438}
COVELO 1101516510 | {EADD8CA4-64AF-4618-B2F5-C69C9631D28B}
COVELO 1101536 | {7897A070-7C30-42E9-B1B0-EB5E015E733B}
COVELO 1101562360 | {149E5268-4926-4B7A-B9E2-928EA9B5F83B}
COVELO 1101562360 | {FAE39AD0-CFA0-43A2-BED8-699A9ED56A44}
COVELO 1101664688 | {C8F422B1-D98B-4D4B-B551-2EAF4DF3598A}
COVELO 1101679050 | {E8D43501-2CC4-44EA-8BFB-97C2437C266E}
COVELO 1101694140 | {6A1BD807-05E2-4F2D-97EA-2EA08300A3E6}
COVELO 110196896 | {C93D43A5-1B00-47F7-99CB-5288FDBDDC41}
COVELO 1101CB | {F774F37B-0BFB-4E5C-8B3B-83726F441387}
CRESSEY 2103421930 | {5AB4EA86-7A4C-4D08-8C80-B7F0F2FBC0B5}
CRESSEY 21034350 | {9BABC230-10D6-439D-93FE-FC6E107DEA09}
CRESSEY 2103505894 | {5AB4EA86-7A4C-4D08-8C80-B7F0F2FBC0B5}
CRESSEY 2103593420 | {DE9A9FD1-E640-4A16-B0F1-6A591D0FA13F}
CRESSEY 2103596130 | {9BABC230-10D6-439D-93FE-FC6E107DEA09}
CRESSEY 21039390 | {DE9A9FD1-E640-4A16-B0F1-6A591D0FA13F}
CRESSEY 210453374 | {4680CD9B-1C7A-4FFA-93AE-DE77CE0DFEB9}
CRESSEY 2104551990 | {BD805C25-C4EA-47CD-8376-E7DA2BE0F24B}
CRESSEY 2104947844 | {4680CD9B-1C7A-4FFA-93AE-DE77CE0DFEB9}
CRESTA 1101103126 | {8CC5C28A-D4E3-4E7C-8DC9-1431E561B6CC}
CRESTA 1101546650 | {A1AFFBEB-1EC0-4B98-95D8-379CD77E7C39}
CROWS LANDING 110190600 | {5A5D22BF-24BA-433C-9E32-EE55B80DC70A}
CURTIS 1701407366 | {0A85DFD6-88D4-40ED-975D-794F2BF88AA0}
CURTIS 1701842008 | {11782BED-BAF4-482E-B926-E7AFADCE2119}
CURTIS 170190120 | {B36B99C9-0DE6-45EE-9DB4-F71926B74F59}
CURTIS 1701CB | {74641153-5847-4D3C-B484-25FD29972F96}
CURTIS 170210940 | {16922C05-7DEF-4043-B388-9531C1140314}
CURTIS 1702196950 | {61F405DF-A5CE-4759-B799-2F2573DE63D8}
CURTIS 1702278740 | {3F3B50FA-3E42-4B14-8E0A-7FFA3136F01E}
CURTIS 1702295054 | {C340F85E-29B2-42A2-BE33-BCC9FBC9DF79}
CURTIS 1702295684 | {FDA50671-204B-49A7-913B-C1D4704BA325}
CURTIS 170234426 | {897848FB-F125-46A8-B9E9-7A6CE5229B91}
CURTIS 170247488 | {679E62FD-129F-450C-96FA-1CC9B9454DF8}
CURTIS 170247488 | {A13891AD-BB5A-427E-8F5C-CEB24021177B}
CURTIS 17026008 | {3DCC560A-A4CD-4E56-B3FD-95E4BD898152}
CURTIS 170268380 | {EF2D6CE0-C909-419D-A7AC-B995D6FEEF27}
CURTIS 170268380 | {45D5D58B-80DE-4D2E-89C9-FED8B8DCC26F}
CURTIS 1702756888 | {0EDAFFD7-D6A6-47ED-82C2-1002577B09D4}
CURTIS 1702787480 | {C4F8C293-CBEC-458F-BA61-7DD19B2529A5}
CURTIS 17028000 | {C413BF51-2D4A-4E14-8A5C-AF93355185D2}
CURTIS 1702873788 | {6238CFAC-450A-43EE-9347-C8519B3AFC7D}
CURTIS 1702961393 | {59990925-7789-44EC-9879-24716A265024}
CURTIS 1702CB | {7226EEDE-AAEC-45AB-A41D-23DA3572485A}
CURTIS 17031945 | {6315A27E-8EDD-4A40-A33B-4CE6DD1CE36A}
CURTIS 17031949 | {D86564DD-FB0D-414E-AA5C-462986116445}
CURTIS 17032317 | {538EF88E-B7E1-491C-971A-489D35F27B72}
CURTIS 1703258550 | {E57DD2D7-FAFD-479E-9BAB-621A0696EA30}
CURTIS 170327335 | {57428321-9DE3-463E-A110-291978FFA946}
CURTIS 1703476872 | {65C9BF26-DCEA-4580-BD2C-5DE390077812}
CURTIS 170349746 | {7D0477A1-3B70-4629-B0DA-1E96F8ADF8DC}
CURTIS 170354505 | {31F1F065-CA03-44B3-B0FA-D9152C25D341}
CURTIS 17036064 | {1D6F2813-1DE7-4CF3-9F1D-B6618158D284}
CURTIS 1703680666 | {844C8F02-F5B6-4910-9A6D-2918F0EC9DE4}
CURTIS 1703829620 | {E51694B5-AA1C-4D62-9699-29EE4A9AF914}
CURTIS 170384944 | {46CEA7E9-BB3A-493A-8627-27189E1BD87C}
CURTIS 170390320 | {5F7A2008-1CE2-4B47-8EE7-E42EE270907C}
CURTIS 170390320 | {7CE6E278-AED2-4FB9-9113-6F7B76C12C93}
CURTIS 17039210 | {28A07299-BAB6-4846-84FA-366E13AEFEE9}
CURTIS 17039240 | {11F969DC-9C50-4BBE-BE33-15DB7CEEDE86}
CURTIS 17039330 | {4381CA31-F367-419C-9844-15BF5ABE53D9}
CURTIS 17039330 | {BE967458-9C2E-4DBF-9D1D-857D10B2BFD4}
CURTIS 17039330 | {328271F2-4A84-4162-B82C-FC63663EBC79}
CURTIS 1703956734 | {0AEF3DF1-EA58-4522-8227-A49EA81C8088}
CURTIS 1703956734 | {72C01A75-4F3E-40D9-A832-25340880CE32}
CURTIS 1703CB | {C4B116D3-EE04-4D0A-96A8-6CF57FE78721}
CURTIS 1703L1207 | {918634DC-A751-4646-8E29-9E34F3B1C082}
CURTIS 1703L2287 | {0011ADD1-E1CB-44B9-B7AD-37FC168B38DA}
CURTIS 1704100850 | {156CC3EF-E88A-4B4A-BC9D-90176C05B816}
CURTIS 170411290 | {5B03EFF1-F12F-4656-8D60-84D55FFB9841}
CURTIS 170411300 | {1342493A-4682-4997-B671-32B9B4D877B0}
CURTIS 17041691 | {4F425A5F-9E60-4583-B0E2-03F6FF8A0629}
CURTIS 17041691 | {F277BD33-99CC-49BB-97B8-30A89C53B396}
CURTIS 170420771 | {5444202A-A2BB-45AE-B4C4-6DF69B3381C2}
CURTIS 170420771 | {5F3207D0-1905-4719-A8FC-73CD2FFE0036}
CURTIS 1704232322 | {183E2C68-34E5-48FA-9D61-7632B5D82E71}
CURTIS 1704252818 | {677BC4CE-74C4-4870-9B50-45491FB41EEF}
CURTIS 170463502 | {5266FAB3-7730-4DD4-BFC5-448CE0D44F05}
CURTIS 170463502 | {A5122D22-FC3B-40AD-B1C9-1922AC7D5EB3}
CURTIS 1704754060 | {3C4F3D19-E752-4413-B337-BFBB0047DE5B}
CURTIS 17048140 | {44BC81C9-8540-477A-9326-99FB3CD481E2}
CURTIS 17048140 | {A5C49ECB-AB62-4B88-B0AF-3FADB0483D59}
CURTIS 17048140 | {9D512F80-46CD-467B-92A2-3C55E7E9284D}
CURTIS 1704895006 | {762DB30B-09CF-4C49-AE75-FD0402056B3F}
CURTIS 1704CB | {6CFF4874-9416-4562-8168-A66869F04B91}
CURTIS 170510590 | {646CB9C8-1918-432B-A6E2-6AE09F45C1A8}
CURTIS 170510590 | {EA84943C-5C73-4028-8D85-A074BC119CA8}
CURTIS 170511790 | {82A7B687-8833-4D9D-84AF-D482AF9F7393}
CURTIS 1705303216 | {053232CD-C9FB-4EBC-A723-88D478A20023}
CURTIS 170539256 | {60313232-3855-4646-B9A6-D03E4546E4FB}
CURTIS 170565908 | {2ED0FFD8-DF5F-45A0-8687-5F34F37A5A97}
CURTIS 17058110 | {67888239-14C4-4F58-AE21-095B302530E4}
CURTIS 17058170 | {944E3EC7-4285-4D17-99A0-D6960B77E4D2}
CURTIS 1705CB | {87827028-00DC-43D6-989D-C6C9D1E3E860}
CUYAMA 11031635 | {7338276C-0737-41F2-B421-53D877AA647D}
CUYAMA 11031681 | {050F4AFE-98D0-4DBA-AEE5-12301500CD87}
CUYAMA 1103282557 | {B9AA0189-24D7-4071-9165-3E1FA51856CE}
CUYAMA 1103622728 | {EC646814-C576-4C16-B414-32B05AD6EA11}
CUYAMA 1103684566 | {D1C13827-3D8F-47CF-923A-969F7154F0AA}
CUYAMA 11039040 | {91A9B458-321A-49C3-9021-7195C83B1790}
CUYAMA 1103934590 | {85AC51B2-8F96-41CA-A563-24966A62ABEE}
CUYAMA 1103CB | {086ABE98-CA07-4B5E-94A2-D2E7EF6983E6}
CUYAMA 1104796172 | {BA5325F6-D122-4175-8C85-E48969E254C9}
CUYAMA 1104CB | {C3CB332E-B41D-4DA6-9C37-1357A17FBA81}
CUYAMA 1104CUST | {C3CB332E-B41D-4DA6-9C37-1357A17FBA81}
CUYAMA 2101111544 | {A7BC3A91-18C0-47E6-A9C8-4D7D73EA0E4E}
CUYAMA 21013039 | {AE254590-1F13-4FEF-92B1-1F8EB5A8892D}
CUYAMA 21013533 | {AE254590-1F13-4FEF-92B1-1F8EB5A8892D}
CUYAMA 21013542 | {F9E131D2-E655-4DF9-A7E0-8C8B213A0782}
CUYAMA 2101423828 | {ED38237A-AC0E-4695-8E2D-36EFF3ABDFF7}
CUYAMA 2101952122 | {A7BC3A91-18C0-47E6-A9C8-4D7D73EA0E4E}
CUYAMA 21021000 | {1E4085A9-9FA5-4201-A41B-812EF3A4EB26}
CUYAMA 21021000 | {CF1208A0-A4C0-4DDD-B379-1B6865E1ECD4}
DAIRYVILLE 1101147562 | {CA0AD6F1-1C97-4016-B9E2-C0F9F142B73C}
DAIRYVILLE 11014679 | {7E805BB6-FA35-4404-BBBB-4801C3E98DDD}
DAIRYVILLE 1101CB | {7E805BB6-FA35-4404-BBBB-4801C3E98DDD}
DALY CITY 110442434 | {A5E0E43C-1108-48A2-8321-362EF7E23788}
DALY CITY 110539396 | {E7423657-E776-46D7-95AD-F8D58DE8F127}
DALY CITY 1105611740 | {E7423657-E776-46D7-95AD-F8D58DE8F127}
DALY CITY 110576128 | {E7423657-E776-46D7-95AD-F8D58DE8F127}
DALY CITY 1105CB | {E7423657-E776-46D7-95AD-F8D58DE8F127}
DALY CITY 11061801 | {1BDA3EE1-9B4E-4F38-A7BE-1CC0738E5C02}
DALY CITY 1106CB | {1BDA3EE1-9B4E-4F38-A7BE-1CC0738E5C02}
DEL MAR 11032702 | {FAA4BB2F-A14A-4ACA-9B63-02DFB58C1EE6}
DEL MAR 11032716 | {EF81CA1C-18C9-4299-AF2A-DDBDF91E767C}
DEL MAR 1103624 | {C849372A-DDB7-468F-9EC0-AE7D09002A23}
DEL MAR 1103CB | {8F0FCBB5-348C-4DDA-9D44-60778A054848}
DEL MAR 21051270 | {E6D47C85-E105-4B65-8361-FF40BF24A550}
DEL MAR 210551692 | {E6D47C85-E105-4B65-8361-FF40BF24A550}
DEL MAR 210584138 | {DD87F226-71D9-4417-928F-44802F1E6068}
DEL MAR 21061686 | {1E127AF9-846D-4194-872F-DBA8A5888781}
DEL MAR 210938684 | {D6637242-CFF7-4E25-9BED-9E794623EBCA}
DEL MAR 210975802 | {AAD63AEA-E006-40EA-8F1E-5C283AEC521A}
DEL MAR 2109CB | {A3D1D6B2-C2DB-46A7-9A60-CC55ABB31E62}
DEL MAR 211064434 | {67D76908-7B70-4DAD-A31C-C1F7E75F3357}
DEL MAR 2110CB | {67D76908-7B70-4DAD-A31C-C1F7E75F3357}
DEL MONTE 210138582 | {2F70F4D8-3BA3-4012-9A01-B8B771F3D276}
DEL MONTE 2101670188 | {AC768364-0998-4B6B-9363-88D95B1FF179}
DEL MONTE 2102396158 | {C195EA2E-4577-42D2-B33A-631AD864FAE4}
DEL MONTE 2102615458 | {C195EA2E-4577-42D2-B33A-631AD864FAE4}
DEL MONTE 21032000 | {A7511424-C0A7-4DC4-BAD6-B60505BBA431}
DEL MONTE 21032144 | {9F6F0B77-F96F-45F4-9ED5-EDDD1890DAC3}
DEL MONTE 2103239408 | {BB5BD7AB-D246-4BC4-A40D-7487E300E89C}
DEL MONTE 21032642 | {5254C050-229F-4607-A796-9D51DDA6F333}
DEL MONTE 210332886 | {95BA16F1-C0BE-4BE8-9C3E-AD056E7BB712}
DEL MONTE 210342226 | {9627C1E3-F422-440A-AEBA-EC231A63790D}
DEL MONTE 2103468158 | {6129877C-0FCC-4F26-BBF6-7A6117D5D7AC}
DEL MONTE 2103617344 | {A04AFFEA-C849-4263-A535-5ECE95BFA747}
DEL MONTE 210386496 | {572A903E-D7FD-4349-978F-5FBD205DDA11}
DEL MONTE 21039106 | {900D5BA1-EA68-418C-9CFF-B7A1E9A4FECC}
DEL MONTE 21039452 | {5254C050-229F-4607-A796-9D51DDA6F333}
DEL MONTE 2104181640 | {F5363A17-6294-4FBA-A5E9-297DB437E9E9}
DEL MONTE 21042032 | {C1DCB446-91BC-4976-8E19-E90A61136DD7}
DEL MONTE 21042624 | {F5363A17-6294-4FBA-A5E9-297DB437E9E9}
DEL MONTE 21042762 | {32A9C949-424C-43B5-963D-82C15E14F50A}
DEL MONTE 21043088 | {FB7A8750-C967-4B2F-BC27-F33BBB5DCEFD}
DEL MONTE 210448004 | {738FF9BC-104B-4186-B51C-DAF898F7C078}
DEL MONTE 210477432 | {29D13B0A-64A5-4979-9725-C7E6D900D129}
DEL MONTE 21049096 | {30AEAB14-B5AB-4231-9287-9FE7C85B2C05}
DEL MONTE 2104916780 | {FA9C0962-F593-48CD-A46E-8B69795ED19E}
DEL MONTE 21049500 | {9F487EDE-1254-4232-B1F0-1B8CB4720B05}
DEL MONTE 21052644 | {317B7582-B045-4053-8009-5D848CC65A15}
DELEVAN 1101CB | {A015DEAF-5DA3-41A3-8034-9B950FE760DB}
DELEVAN 1102CB | {DA124654-577F-4E6D-AC06-7BB0A9097578}
DESCHUTES 1101100620 | {08BF9D80-4661-4C00-B319-F768A57A93B2}
DESCHUTES 11011380 | {53F1163A-2879-44DA-A8DC-132948A94C1B}
DESCHUTES 11011580 | {064EA007-8A62-40F7-BDB2-55C9C2572F4C}
DESCHUTES 11011580 | {89362ED0-C2BF-461A-9E75-514DA7E2537F}
DESCHUTES 11011652 | {FDD63F63-31B3-4440-A376-DFAEA489B8E7}
DESCHUTES 11019722 | {2EB378FB-B271-4EC9-A2B7-75CAD47F81DF}
DESCHUTES 1101CB | {FE5A37BD-E086-417E-B0C1-D984D30B636B}
DESCHUTES 1104100170 | {C6E4D1C6-A148-459C-BC88-ACC391E7C0CA}
DESCHUTES 1104116082 | {C4971820-C995-457E-94B8-C11C12DB11A4}
DESCHUTES 11041370 | {7B256BE5-97E8-449E-A46C-21FA2871BA72}
DESCHUTES 11041582 | {1467DC6C-6C30-498B-9696-60E37D99774A}
DESCHUTES 1104269170 | {2ABC92FF-56CD-4099-9E14-FDA9128A7AC4}
DESCHUTES 1104378894 | {BC7A1387-B3D8-4140-98B2-87298F0B6696}
DESCHUTES 1104421598 | {C5BC56B2-92C0-428B-9EBD-2409EE5861AB}
DESCHUTES 1104421598 | {101F2F9F-D72D-4EB8-8A9A-E537C20D5C27}
DESCHUTES 110449024 | {6DDF5542-CAB8-4ED4-9238-C0F4D392F99F}
DESCHUTES 1104589602 | {A660A9BE-07D9-4051-AC7B-0365C697FBAD}
DESCHUTES 1104622260 | {77B43BDD-8E2B-4B03-A902-769AAAC5407C}
DESCHUTES 1104656708 | {105AF226-5705-41BD-B206-D294BEEB8D68}
DESCHUTES 1104656708 | {49CC7AFD-B7BE-4904-85E5-5CD1E848703A}
DESCHUTES 1104715242 | {58F0D5D6-E6BB-4E86-AC03-61DDABB38346}
DESCHUTES 11049718 | {F164BF8B-3484-47A3-8EEF-5FFD77D4911A}
DESCHUTES 1104CB | {2726A95C-76D3-45AF-8DAD-F0D1D6243DBE}
DESCHUTES 1104CB | {969F6F9B-F1AA-4EF5-A1EE-31E0C15FF124}
DESCHUTES 1104CB | {D7FE7EC5-7478-43B3-9A24-52065EFA1755}
DESCHUTES 1104CB | {5D26706C-A4A6-4F70-88DF-BA9D990C37DF}
DEVILS DEN 1101824190 | {6AC8C034-0ED1-40D0-97BB-138938DBB781}
DEVILS DEN 11019470 | {17BFFF76-12CD-4B44-AB51-12EF1D22B1EB}
DEVILS DEN 1101CB | {E637B763-1297-4DA3-B168-C020DBAC2EB8}
DEVILS DEN 1102421480 | {E0599860-AD27-437B-92F6-9FBDCB4E15BA}
DEVILS DEN 1102460850 | {1ABBA2B1-53B5-449A-A275-B6A0999D81FE}
DEVILS DEN 1102CB | {A92A6C8C-B557-4608-A4A1-975F3E0D9109}
DIAMOND SPRINGS 1103467046 | {2A7BBA85-AF71-468C-A351-10A5AC7DB14A}
DIAMOND SPRINGS 1103940676 | {B24EB565-F859-4931-B092-8E6CC9CCD13B}
DIAMOND SPRINGS 11039432 | {A12D2A90-44E6-4ECA-BE2F-8893B2D17E74}
DIAMOND SPRINGS 1103CB | {F21436B1-06B1-4781-A6B4-F2B85E06831B}
DIAMOND SPRINGS 1103CB | {A0F6FAAB-8AD3-4FB6-80FD-2F7C87739A36}
DIAMOND SPRINGS 1103CB | {9212A36D-CBC9-4C2D-979D-8E57F583136A}
DIAMOND SPRINGS 1104147386 | {8D8139BF-D216-4D14-B0AC-67DE21E71989}
DIAMOND SPRINGS 1104705100 | {B2C0084B-109E-44CB-BAED-2939A6DED126}
DIAMOND SPRINGS 1104CB | {6872443C-7FE4-416F-92B9-65D58A293737}
DIAMOND SPRINGS 1105146980 | {47C81E1B-8837-481E-AA75-EC428AEB85F2}
DIAMOND SPRINGS 110518935 | {51B4FBA6-E864-4F62-B988-2A8243E75100}
DIAMOND SPRINGS 110519910 | {B086CF84-D2F5-42B5-8FBA-007201735811}
DIAMOND SPRINGS 11052102 | {51B4FBA6-E864-4F62-B988-2A8243E75100}
DIAMOND SPRINGS 11052102 | {A0B3A835-3CA2-4898-91AB-E29D11CEF787}
DIAMOND SPRINGS 11057722 | {733F22CA-FEC2-4592-8FEA-9D2EAB9A6FBA}
DIAMOND SPRINGS 11057722 | {2B853B38-9B63-41B8-8287-6DC1AF05DC5F}
DIAMOND SPRINGS 11057722 | {9B3053D4-0FCD-415D-AE49-1C1AC44BB827}
DIAMOND SPRINGS 11057722 | {6CC5E5CA-9E7E-4BF4-8ED8-46AE63679A37}
DIAMOND SPRINGS 11057722 | {64B36DA0-B43B-4C7B-BDF0-9C7A8CE740AE}
DIAMOND SPRINGS 1105CB | {76BB324A-98B3-4C58-A6D4-32DC864FAEB9}
DIAMOND SPRINGS 1106176130 | {069FC1F9-26AE-4248-95D3-8B4718D722BC}
DIAMOND SPRINGS 1106279670 | {1FAA72D4-5699-41F5-A2F3-C539D6B6ADA9}
DIAMOND SPRINGS 1106337536 | {4FE0ADB2-8944-4613-9148-3D68B70EC500}
DIAMOND SPRINGS 110650324 | {DCB9D4A3-4396-4AF7-B5A4-4405D20B6E8E}
DIAMOND SPRINGS 110656026 | {95AAF818-10A5-460C-909E-8A1D81C4AEC8}
DIAMOND SPRINGS 110676088 | {11EA4392-1B4D-42CA-BC2B-6189E8B41C5B}
DIAMOND SPRINGS 110676088 | {173699EA-8EA6-482C-B18E-B695B506E673}
DIAMOND SPRINGS 110676088 | {423A8C76-9A51-45A6-B374-FEBC31B925B4}
DIAMOND SPRINGS 110676088 | {ACE99E54-0B5D-4028-ABCC-1BDC876D160C}
DIAMOND SPRINGS 1106762780 | {5E624FA1-8898-49A2-BC33-0C0CCA1E740F}
DIAMOND SPRINGS 1106803034 | {6647B708-EB30-40C8-9FB8-1AD5D9953BA6}
DIAMOND SPRINGS 1106803034 | {16EDBAFD-5173-4127-A0C1-F8B63917692F}
DIAMOND SPRINGS 1106803034 | {33B1FB6F-61B4-4FEA-92A9-9A74CEB96B9D}
DIAMOND SPRINGS 1106803034 | {F2A5D64B-22A8-4AF8-A7DF-A30C3FA56945}
DIAMOND SPRINGS 1106803034 | {FB9AE970-0795-40A3-9446-AC1D8383DEBC}
DIAMOND SPRINGS 1106803034 | {1C6E1452-BEEC-4B8B-8B47-1992A1DB58E4}
DIAMOND SPRINGS 1106930190 | {DCB9D4A3-4396-4AF7-B5A4-4405D20B6E8E}
DIAMOND SPRINGS 110699658 | {AE525890-6C02-4814-857B-4FEF1E7D58A9}
DIAMOND SPRINGS 110699658 | {5F542D36-4FC1-413E-B114-C90AD9930E1C}
DIAMOND SPRINGS 110699658 | {66BEC755-EB33-41C4-BD19-8B49A68F1B0F}
DIAMOND SPRINGS 1106CB | {C99F1365-4BA0-493A-A0A5-5D7F7D14700C}
DIAMOND SPRINGS 1106CB | {21AB04EE-D7E1-4680-98C1-D718C5F41455}
DIAMOND SPRINGS 11071402 | {04F6A01A-981F-4306-9D80-21027E2CEC32}
DIAMOND SPRINGS 110719702 | {635CA5E5-8968-4E76-BA11-3BE643BA9E35}
DIAMOND SPRINGS 1107203504 | {C468F999-9DD1-4480-AEEA-A7CA15687805}
DIAMOND SPRINGS 1107217974 | {EA651BD1-B1BE-4A95-908A-06FA4832B9F5}
DIAMOND SPRINGS 1107301798 | {87CBC4D7-654D-4F94-B8EF-BF8BE88A6CF0}
DIAMOND SPRINGS 1107336076 | {01A8C6BD-323D-44E5-A686-1246351A46F2}
DIAMOND SPRINGS 110777086 | {124D6D8B-14FB-4F2A-A51D-104BDFD91E41}
DIAMOND SPRINGS 1107CB | {01A8C6BD-323D-44E5-A686-1246351A46F2}
DIAMOND SPRINGS 1107CB | {9EEBDB00-7814-4DCA-94A7-A89D1F5F04EB}
DIVIDE 1101CB | {24B4C5D2-9190-403A-BD5D-182F06265073}
DIVIDE 1101M78 | {932BDC94-3FB8-445D-8673-FBC593EFEC6B}
DIVIDE 11021385 | {A0FD2E34-A735-4A8C-A9DC-394B15A3212D}
DIVIDE 110245067 | {EF9A6FA5-0241-4F64-89EA-1575EA9DAF76}
DIVIDE 1102609332 | {B07064C2-2470-4EB2-BB60-A2A3257C8D27}
DIVIDE 110266960 | {945DB13B-5462-41AD-A956-C4E2651389F9}
DIVIDE 1102679356 | {20DEB5EB-1393-4AA6-A72C-1809C63AEE53}
DIVIDE 1102CB | {EF9A6FA5-0241-4F64-89EA-1575EA9DAF76}
DIVIDE 1102M144 | {A0FD2E34-A735-4A8C-A9DC-394B15A3212D}
DIVIDE 1102M46 | {CA16F48A-6A4D-4E2F-9307-EE7712739B5B}
DIVIDE 110323614 | {AB1CE55B-42CF-42B2-8A5C-221DBBC685D8}
DIVIDE 110348160 | {6ECC9377-E065-4FCE-971C-2036CD830EDE}
DIVIDE 1103567884 | {8595AA03-4461-43F0-83E3-96D1A07CC7F4}
DIVIDE 110398166 | {4AF5ECF8-33C4-4E7E-9141-A6CD2D4FF4E6}
DIVIDE 1103CB | {BFA942F4-E00F-4B4B-9BEC-83B4F4C04B73}
DIXON LANDING 2109MR211 | {270CEB57-AF3B-4573-86AD-B73952A8BF6B}
DOBBINS 11011267 | {373D073A-B93D-4FD4-80CB-8FEAD7594C31}
DOBBINS 11011271 | {DCAE4F2E-B523-439D-A13B-B54DC0B640F3}
DOBBINS 11011808 | {E4399593-CC75-4E6C-A098-AD618A358CCA}
DOBBINS 11015202 | {65B27162-E2B7-4CEC-9138-2917B0C9553F}
DOBBINS 11015202 | {765A3ECF-80B9-4E18-8B6F-F5488F049C29}
DOBBINS 11015203 | {6A55AB0A-3F48-44FC-9D3F-A88C9F82F0E9}
DOBBINS 1101625448 | {9A77FF27-1EB8-4534-9759-A18E0385536C}
DOBBINS 110169722 | {DCD6C7A6-BCDE-42A2-9036-021FA6ED047F}
DOBBINS 110183186 | {F41B1B82-AAA2-4875-9D41-FA7459D64A74}
DOBBINS 110183186 | {79296F22-0716-473A-A665-0DFCBF4642CD}
DOBBINS 1101900482 | {EF74781A-DE56-43A8-A96E-CF92872B71C9}
DOBBINS 110191464 | {93C56D43-333C-4331-959E-24C064CB9C39}
DOBBINS 1101CB | {3EEFA179-0D60-4808-A6C9-A2D8F6C0C66D}
DOLAN ROAD 1101156268 | {A6335D58-E606-4A31-A5A5-958C5FE37A92}
DOLAN ROAD 1101173702 | {F06F081F-C9F5-4637-B24B-42F86E64048D}
DOLAN ROAD 11011831 | {95DA73C9-4DB4-4C31-AFD8-C43A5BC36425}
DOLAN ROAD 110122158 | {95DA73C9-4DB4-4C31-AFD8-C43A5BC36425}
DOLAN ROAD 1101257586 | {D2A3503D-1D44-42E3-A6ED-43C563CA7E48}
DOLAN ROAD 11014319 | {8DAD43E1-C0B6-4B91-89E1-55DFB8ABD7AF}
DOLAN ROAD 1101491190 | {601897CD-D608-4456-8A73-B9E82EC75438}
DOLAN ROAD 110157184 | {87CC29A1-7A48-41F1-B98E-3354A3499A6D}
DOLAN ROAD 1101590402 | {B7B666E0-E3B4-4668-B112-954F6AFA2706}
DOLAN ROAD 1101672110 | {18BD8A9E-072B-4ADD-8F74-F890B89581F0}
DOLAN ROAD 110169466 | {8DAD43E1-C0B6-4B91-89E1-55DFB8ABD7AF}
DOLAN ROAD 1101857972 | {EB37E4EB-78C1-4046-AF1B-2299D2328F22}
DOLAN ROAD 1101882610 | {6AB13B35-5C7E-47B3-B58A-5166F0A77CC1}
DRUM 11011602 | {4FA3034C-CC34-47A2-AF7A-8A1D1515E919}
DRUM 1101CB | {4FA3034C-CC34-47A2-AF7A-8A1D1515E919}
DUNBAR 1101137736 | {7EED3CE2-525A-40E2-A0FE-AAB7CF9E89BB}
DUNBAR 1101142052 | {973AD71F-0A48-4C76-99A8-AC94CF8D1012}
DUNBAR 1101440 | {5AA0A9EA-0FB6-4230-B4CC-9462B9350D46}
DUNBAR 1101440 | {6FF82866-EF3C-4AEF-B41F-362F035D5794}
DUNBAR 110149556 | {A38F6B87-9815-4AE5-B53E-BF10B2A51673}
DUNBAR 1101534 | {8CA59690-B3BA-4A2A-90F5-8A9118795C50}
DUNBAR 1101534 | {87B3C20A-D657-4078-8D6A-35BAF0B1250C}
DUNBAR 1101725292 | {86609C6B-F85A-40FF-9C70-59FE9D214477}
DUNBAR 110181584 | {BDFCA591-2F6A-41F8-B3C8-57FDA10FAC4E}
DUNBAR 1101835658 | {E3222172-78EF-43FF-8CE5-0E25731FEA0D}
DUNBAR 110184678 | {053B6290-C448-4801-B1A5-3E9ABB283E0F}
DUNBAR 11018473 | {49873133-4881-4683-BDF9-184EEF7CAEE8}
DUNBAR 1101872066 | {7BA4959A-2F94-4080-BC9D-0C53D9644F4F}
DUNBAR 1101904852 | {EE9E2000-1BCF-4D6D-94B0-B0FE09254374}
DUNBAR 1101CB | {099221CD-5C0A-49E5-8576-2B334B5F477C}
DUNBAR 110211121 | {02DBC2D1-A9F9-4ADA-8050-E324E7170429}
DUNBAR 1102246 | {E5FC257A-973F-414F-A273-EE859A543B23}
DUNBAR 1102246 | {ECF0597E-C523-4664-9DE2-2ED0EC5C00F2}
DUNBAR 1102261774 | {04FFFA70-53BF-428C-99F6-1A2E798AF420}
DUNBAR 1102264 | {8BDDF9F2-4A86-41E7-8ABB-CA8E9473A01E}
DUNBAR 1102386158 | {672F5B11-4A5D-4A77-BAE9-574FB74B1678}
DUNBAR 1102426094 | {FB8DED4F-C1A4-4542-AF21-D3D770C633DF}
DUNBAR 1102426094 | {7C5703DD-38DB-4320-9340-3B87889ADBF6}
DUNBAR 1102448 | {19F00F46-8DF2-4369-8C23-B78BEB3B793E}
DUNBAR 1102694641 | {9330F6B0-760C-4338-A4C1-C3EAEF5F2D51}
DUNBAR 1102861496 | {591157C5-704F-458F-BA92-87D78CA82BDD}
DUNBAR 1102CB | {46D8BBC2-519D-4FA1-BC3E-5FF3581AAFDB}
DUNBAR 110318267 | {BE081CEF-1321-46BF-8EE1-AAAEC935F528}
DUNBAR 1103234 | {E64AC1A3-7B00-44C4-B413-8ED8E1419B88}
DUNBAR 1103234 | {670EEEC7-97F3-49B4-8DF7-BA5F346AE80F}
DUNBAR 1103302 | {6B9EB51B-5FA3-4BC3-9024-69ABFBD94AA6}
DUNBAR 1103302 | {34794EA8-41B0-4C58-A267-88FB7ED2F311}
DUNBAR 1103416 | {BF23F54F-E263-4EE1-9D2E-F9BC52287A4F}
DUNBAR 1103416 | {E1077E4E-022A-4658-906D-61D41C4EF125}
DUNBAR 110347964 | {7261231D-2D38-4D93-8944-3B1E84FC417E}
DUNBAR 11034882 | {2B1CF1D9-BF9E-474F-B027-6D9BAFB42F24}
DUNBAR 1103596218 | {E64AC1A3-7B00-44C4-B413-8ED8E1419B88}
DUNBAR 1103659950 | {FB34E87E-78C2-48AF-AF93-B274D8B5A56D}
DUNBAR 1103681238 | {E1077E4E-022A-4658-906D-61D41C4EF125}
DUNBAR 110379086 | {EDA68B39-7DBD-43E4-954E-1185A3CE9473}
DUNBAR 1103799422 | {587017B7-CF95-40B8-A31E-326EDAB4E012}
DUNBAR 1103831696 | {E0CFF63C-79DD-403F-842B-413C7E8A35ED}
DUNBAR 1103839384 | {587017B7-CF95-40B8-A31E-326EDAB4E012}
DUNBAR 1103839384 | {BDF50AB5-3CEB-497D-9CC1-A6453469223A}
DUNBAR 1103CB | {587017B7-CF95-40B8-A31E-326EDAB4E012}
DUNLAP 110212868 | {539D1C1A-DA20-4E86-B585-05A7466CFDFA}
DUNLAP 110212868 | {FDA74305-DCF3-40EA-A165-1499B44312F3}
DUNLAP 110239190 | {03B91929-B748-41B7-BED2-9D46A08F08B1}
DUNLAP 1102686102 | {B3254CDE-A101-49A4-BFD4-9DE599D942ED}
DUNLAP 11027060 | {1CE889BB-8D39-47CF-B31A-B81CA7117CDD}
DUNLAP 11027060 | {DC0C9AE9-E0EC-4108-AF9E-4DDFE694FC71}
DUNLAP 11027360 | {81D716EF-AF38-46F5-8FD2-48383247DE01}
DUNLAP 1102912874 | {1D97E837-4A47-4DD4-8CC4-BE0501A87156}
DUNLAP 1102CB | {A6D1F5C5-C503-4CFC-844D-2877BC97AA39}
DUNLAP 1103124724 | {F0F8BF7A-36DE-4BF7-A0C2-ACA432CBFC5E}
DUNLAP 1103395208 | {BB46EC8C-C88E-45DD-841E-D23CBA70A0A2}
DUNLAP 11037040 | {C465DFBD-710D-45BE-B470-E6FF6541A1FA}
DUNLAP 11037040 | {B50E0057-39ED-4964-90AB-86F39978479B}
DUNLAP 11037080 | {3474C71F-C417-4DFD-9033-1EBD72D1A9BF}
DUNLAP 11037170 | {733D4902-C475-4A3B-A2B1-E7586C4C7AE4}
DUNLAP 11037220 | {6435FC5F-46A2-430E-986D-1340D0B45DC1}
DUNLAP 11037220 | {5755A55C-8127-474D-99F5-38E2401D21A6}
DUNLAP 11037258F | {D2D3D5F6-5D99-4DCE-9353-4AD4408F5945}
DUNLAP 11037709F | {E8CE8FAB-3899-4E84-84B4-F8D80F9BC055}
DUNLAP 11037959F | {15DD097B-4EA6-43D8-96C5-6F14199506F4}
DUNLAP 1103CB | {2C485712-3D09-43E6-B47A-A2006FA28A66}
DUNLAP 1103CB | {5DF2E0F6-2F6D-4508-9EBD-950E30F367F0}
DUNNIGAN 11024706 | {EB4A4637-7210-458E-BFA3-561528E6F7C9}
DUNNIGAN 1102589936 | {2C09B3F8-9818-4F23-8122-3E56A60AC6D0}
DUNNIGAN 11033048 | {1B9C8A8F-5842-44B4-8525-5B03DDD35104}
DUNNIGAN 110347282 | {44D6ED2F-777A-4FEB-A593-3F9A2FF8D4A7}
DUNNIGAN 1103669720 | {4F1CDC69-EA0B-4135-93B4-1C48EA3748CD}
EAST GRAND 110412701 | {2FE2C718-71DF-4462-89A9-DDA3D06C96CB}
EAST GRAND 11045435 | {F330C2FA-3825-42DF-A05B-7C890E2905DE}
EAST GRAND 1104690146 | {05E0A139-88F6-4074-BDF4-4CA0182EFB05}
EAST GRAND 1116CB | {6A6EA7B3-32BA-426B-8527-8C5EED883D2A}
EAST MARYSVILLE 1108900690 | {D1622BED-440D-498A-AED4-D8C420D1B767}
EAST QUINCY 1101186938 | {627D9E79-9527-4BAE-9B90-33425D67192A}
EAST QUINCY 11012452 | {D7BCD386-8384-4488-96C5-A2E06819036D}
EAST QUINCY 11012452 | {59C78EE7-5933-47F9-84F9-14C071079C84}
EAST QUINCY 11012452 | {59C7C56F-8F8D-453D-B2CA-2A56446D1413}
EAST QUINCY 1101424048 | {13F95C63-620B-4827-AE11-2F38727C8122}
EAST QUINCY 1101951424 | {D3FA1F53-9642-40C0-A05D-D3416EB9964D}
EAST QUINCY 1101951424 | {83723391-EB93-4D6A-A5B4-68EA4AD17B8A}
EAST QUINCY 1101951424 | {181CA5A4-D7E4-4D9E-BABB-349CF307AC6C}
EAST QUINCY 1101CB | {7BDDAA75-E6EC-4597-A704-7B9866E3D480}
ECHO SUMMIT 11012500 | {52018984-7699-4174-8C0E-5E599E3F4F55}
ECHO SUMMIT 1101265728 | {14BBAC88-26D3-4F29-8425-274D619391ED}
ECHO SUMMIT 1101344250 | {501D001C-604C-4CB0-BC61-4A03C3824F33}
ECHO SUMMIT 1101481660 | {3CE51A5B-7612-4EAB-BF43-95EB9AC2B5AB}
ECHO SUMMIT 1101507864 | {501D001C-604C-4CB0-BC61-4A03C3824F33}
ECHO SUMMIT 110155262 | {D6DB5AF9-E5B0-458F-9897-3AC3E052AB08}
ECHO SUMMIT 1101741586 | {52018984-7699-4174-8C0E-5E599E3F4F55}
ECHO SUMMIT 1101889106 | {F991AA46-5F55-4799-A06C-6C07D5355682}
ECHO SUMMIT 11018922 | {3CE51A5B-7612-4EAB-BF43-95EB9AC2B5AB}
ECHO SUMMIT 1101927328 | {14BBAC88-26D3-4F29-8425-274D619391ED}
ECHO SUMMIT 1101927812 | {14BBAC88-26D3-4F29-8425-274D619391ED}
EDENVALE 1102319134 | {CFB4CE48-4FB8-4CC4-B5C6-42BE9D63CB83}
EDENVALE 2105469810 | {8B87811F-B323-4484-BBE4-38B55670D94B}
EDENVALE 2105696340 | {3428AB16-83A3-41CA-A97D-9F45E561A9E9}
EDENVALE 2105739448 | {0DDD3612-D5D8-453A-817C-994BF75B062F}
EDENVALE 210589634 | {3428AB16-83A3-41CA-A97D-9F45E561A9E9}
EDENVALE 2105CB | {F17E89AC-8FEA-42F2-9DD9-35EC50696318}
EDENVALE 2105CB | {151AF940-1BF4-4727-B020-E7A10BD33E51}
EDENVALE 2105CB | {8A7625DF-9660-4682-92E4-DE9581577DA5}
EDENVALE 2105XR336 | {15F04618-5F16-4576-9451-1BBF99F669DC}
EDENVALE 2105XR350 | {67328E6B-5487-40C1-A12E-3EE6D34B5146}
EDENVALE 2105XR392 | {8483E0B5-64AC-44E8-8893-21CFBA8E4B48}
EDES 1112484536 | {D3882565-9819-45B1-A12B-BBD1105FE66C}
EDES 1112CB | {2D451082-1A86-4185-BC9F-55534CD32ABA}
EDES 1112CB | {8BEFF91A-7C09-4291-9AE2-AE9219165D14}
EDES 1112CR100 | {D27A7551-3A39-4FC0-B1B2-BDEDF3C7E8DB}
EDES 1112CR282 | {F0491A07-EB84-48E1-A4FC-240F9B964E65}
EDES 1112CR306 | {1CFCF663-0CF6-44D7-93F9-73671725C761}
EDES 1112CR308 | {D27A7551-3A39-4FC0-B1B2-BDEDF3C7E8DB}
EDES 1112CR312 | {BFA33FCB-E1C5-4ED0-AC2E-104CE6FA2AEF}
EEL RIVER 11021902 | {AD459C08-CBDF-43AA-86A2-CD8C1B5B6101}
EEL RIVER 1102409694 | {FB6BD3A7-81A9-4DC9-861C-0BEFD220DE29}
EEL RIVER 11024396 | {890D4B8A-DB25-4CCA-9D69-562BFAFFB09E}
EEL RIVER 11024600 | {5BECDCB5-20C5-46EC-8F15-C58B62BFE787}
EEL RIVER 11024814 | {CCE91D7C-BCE4-4F01-BD5F-6C83E3A409D2}
EEL RIVER 110249130 | {1527E47A-434D-4693-8754-4E5320E20B87}
EEL RIVER 110249130 | {ADA0B946-8139-4D75-A3D4-894703D1FC57}
EEL RIVER 1102530 | {B0F5DD9B-BA5B-4914-9A80-5D9AD769A95A}
EEL RIVER 1102630456 | {BA4CF323-BCF8-49E7-A1D7-D6A1F53933B5}
EEL RIVER 1102680 | {4D91C2EE-0E70-4830-92FF-2507FF07CCFB}
EEL RIVER 11028416 | {6978B352-246E-461A-9563-C7EBE0EFF7EF}
EEL RIVER 1102CB | {27E2901A-1EBE-4CC0-B5CB-538A633C6C56}
EEL RIVER 1103216324 | {A8C66523-6BAD-4410-B093-1D69B3A4DEED}
EEL RIVER 11033820 | {A8C66523-6BAD-4410-B093-1D69B3A4DEED}
EEL RIVER 11033820 | {FA181DA8-1354-4C84-A9C6-33FBBB81A738}
EEL RIVER 1103CB | {A1A1D221-0393-4995-8057-AA9153B871D9}
EL CAPITAN 1102605060 | {1FB8CF1D-B8D4-494F-A122-DDDCBA73A41F}
EL CAPITAN 110310910 | {C73A3607-EEBF-4680-A80D-EAA18BD94E3D}
EL CAPITAN 110311670 | {BCF947C4-6F66-4253-A6FE-897D9621AEC6}
EL CAPITAN 110311820 | {2233E67D-12E3-4FC5-9E53-75C3C429A8E8}
EL CAPITAN 1103182416 | {CABFFA67-A4B5-4F4F-9CCD-9CB105B36D4E}
EL CAPITAN 110354922 | {C73A3607-EEBF-4680-A80D-EAA18BD94E3D}
EL CAPITAN 110384120 | {C73A3607-EEBF-4680-A80D-EAA18BD94E3D}
EL CAPITAN 11039700 | {C73A3607-EEBF-4680-A80D-EAA18BD94E3D}
EL CAPITAN 1103975920 | {12E2EC58-591F-446C-A03B-F23ACE308468}
EL CAPITAN 1103CB | {C73A3607-EEBF-4680-A80D-EAA18BD94E3D}
EL CERRITO G 1105452366 | {27CF384C-468A-4BD6-8180-083597D0D7F0}
EL CERRITO G 1105978484 | {A06397A2-6E65-4BA1-B08E-782C28C5386E}
EL CERRITO G 1105BR164 | {14BEC098-B04A-4CB2-9AA3-38D63A101CE1}
EL CERRITO G 1105BR304 | {9DF9A52F-32F8-4676-BE5E-F9A3D03712AF}
EL CERRITO G 1105BR316 | {3F882A80-2491-48FC-AFA8-BDC3FFEA4D12}
EL CERRITO G 1105CB | {63FDD22C-1D84-438C-BDD2-97E9627809B3}
EL CERRITO G 1108BR254 | {2AF1BFBB-E94D-4DBD-A7B7-05379A4F71FB}
EL CERRITO G 1108BR346 | {47E84AA2-B51F-4F91-9057-B9557EEB1018}
EL CERRITO G 1108CB | {1BE7584A-89AA-4EFA-BCE7-9E7AC1997D2C}
EL CERRITO G 1110173396 | {DFE6BFCE-280C-433D-BB23-93842B63AE53}
EL CERRITO G 1110BR126 | {DC82074B-02F2-45E5-9AA4-D308CE04252A}
EL CERRITO G 1110BR236 | {DBB65B1C-D816-44BD-B6A7-C95BB0A659FA}
EL CERRITO G 1110BR238 | {DC82074B-02F2-45E5-9AA4-D308CE04252A}
EL CERRITO G 1110BR240 | {DC82074B-02F2-45E5-9AA4-D308CE04252A}
EL CERRITO G 1110CB | {D5C37EEA-D463-430D-8618-04212D08A58F}
EL CERRITO G 1111760530 | {EC819229-CAFA-4A70-A2A2-F76BBD0A5610}
EL CERRITO G 1112418480 | {F4711D50-C892-433D-B1D0-EB1B6E0C6AE7}
EL CERRITO G 111257953 | {908A23EF-FC10-4338-97D4-D163D991549B}
EL CERRITO G 1112649732 | {7A0FE4A4-8FE2-4A7A-9013-EEA423D246F9}
EL CERRITO G 1112664184 | {908A23EF-FC10-4338-97D4-D163D991549B}
EL CERRITO G 1112779030 | {1F8F52CE-D6F8-4FF1-8C8D-BAA757FE8A8B}
EL CERRITO G 1112BR152 | {845D27B3-846A-46D0-A68B-8869856351B8}
EL CERRITO G 1112BR196 | {00AF1949-B9F3-40C7-B655-E7207FF7DB49}
EL CERRITO G 1112CB | {C8CD1F48-28E2-4083-A5C4-229D22866F79}
EL CERRITO G 1113BR120 | {C8899222-544D-48B0-AC50-54347CEE25CC}
EL CERRITO G 1113BR280 | {C8899222-544D-48B0-AC50-54347CEE25CC}
EL CERRITO G 1113BR282 | {C8899222-544D-48B0-AC50-54347CEE25CC}
EL CERRITO G 1113BR320 | {C8899222-544D-48B0-AC50-54347CEE25CC}
EL CERRITO G 1113CB | {F1CD3584-0342-4B1C-AC95-933DCB32DB86}
EL DORADO PH 210113362 | {57E73AB0-1604-40EC-989B-4C2615C4D2B1}
EL DORADO PH 210113532 | {1AECFC8B-BC7B-4454-BB87-FD8F012E171A}
EL DORADO PH 210119612 | {5BE9A1BF-757A-4781-BCE2-C4049CA25F7D}
EL DORADO PH 210119752 | {EA95703C-880D-4BB3-B2BC-E10DAD4E7C96}
EL DORADO PH 210119752 | {68FE35B5-E746-4699-B6E9-9CFC306D8322}
EL DORADO PH 210119752 | {8256574C-8B3C-4A26-BCE0-BA059359AE5F}
EL DORADO PH 2101221877 | {12BA20BC-B79E-402F-A697-67112CBED8F3}
EL DORADO PH 210126000 | {563CD71D-CD80-49B9-9B00-20025334D5E0}
EL DORADO PH 210136764 | {1AECFC8B-BC7B-4454-BB87-FD8F012E171A}
EL DORADO PH 210152456 | {20EA6D57-AE8A-4389-B5E9-F8A1FC109811}
EL DORADO PH 210163464 | {FE51108B-22A5-4F91-8D8C-80182B656BBD}
EL DORADO PH 2101668674 | {BEB260CA-F357-43C4-98B3-E8E440632DBC}
EL DORADO PH 2101668674 | {9026688D-0DDE-43F9-BDC1-1D8B37EA23F4}
EL DORADO PH 21016852 | {550714A4-7303-4842-936D-572C7CE200C4}
EL DORADO PH 2101740738 | {176334C7-212A-44E0-B8CB-5D1B35653938}
EL DORADO PH 2101757474 | {2CD9E52A-6A79-4188-9009-789B4DEB91D6}
EL DORADO PH 2101852836 | {52B1F038-2EF8-414D-9DD4-FFF5BF680B76}
EL DORADO PH 2101852976 | {2CD9E52A-6A79-4188-9009-789B4DEB91D6}
EL DORADO PH 2101887684 | {45EE85CB-8EDF-4EEA-84E0-238BA75D28B0}
EL DORADO PH 2101CB | {39E7EF6F-8B16-4AF2-A2FE-E60F0DC95D0D}
EL DORADO PH 2101CB | {9026688D-0DDE-43F9-BDC1-1D8B37EA23F4}
EL DORADO PH 210219542 | {D823F384-3D02-4716-90A2-5DA25C95DCED}
EL DORADO PH 210219562 | {40FC7F52-2B65-471F-ACDA-BEA2893716D4}
EL DORADO PH 2102542272 | {5B8E36B2-B12B-4F00-8166-D1E50ADA08E5}
EL DORADO PH 2102771208 | {06B529E5-576A-4A82-B77A-D8131F4A0F31}
EL DORADO PH 2102899842 | {5C5307A7-E83D-444B-B19A-4560FBFF053A}
EL DORADO PH 2102927014 | {E3E5615A-B2A3-4BC1-8E71-88BAE49F47C5}
EL DORADO PH 2102CB | {876266AC-37EA-414C-92FC-94A2ACD4EB2D}
ELECTRA 1101105880 | {3B44BEAE-4498-4CF7-B761-D8F28E5D84CB}
ELECTRA 11011238 | {79D3DE13-EDFE-4798-9C48-8D9438D496D5}
ELECTRA 1101175840 | {469B859F-0510-40B4-9350-60E15239ED7D}
ELECTRA 1101175840 | {E00CD82A-5CEC-4EDB-807A-202043F17A48}
ELECTRA 110136816 | {7E08659E-39A5-4373-949B-319BDC171EA7}
ELECTRA 110161816 | {8166BFFD-39A2-433D-8ED2-2366DDF535A5}
ELECTRA 110161816 | {467D6E51-4EB9-458F-952D-00686C463F1F}
ELECTRA 110161816 | {F81CEAAD-C058-42C9-B285-E3027883E9CD}
ELECTRA 11017104 | {21E26CE5-9BFF-45A6-8272-2A9D442E9691}
ELECTRA 11019775 | {C9F2E3C6-05CB-4457-AA23-CF0DB5215E3A}
ELECTRA 1101CB | {60A4E996-A662-42E2-92E6-76DADEF96986}
ELECTRA 1101CB | {0D0FEEBA-0BD3-4962-B35B-0A3278052F45}
ELECTRA 1101CB | {08DB4BC8-8606-4318-85CD-9605F541642F}
ELECTRA 1101CB | {4E1958D8-ACBD-40A7-9BB6-74B000233395}
ELECTRA 1101L3857 | {A9FE23E5-42D0-4D44-B921-6F3123864EB6}
ELECTRA 110213414 | {BE69B59B-6EEF-4362-A602-62B1E76AF725}
ELECTRA 1102285758 | {3AE63E7E-BC8A-4108-80CA-C0CC877CF92B}
ELECTRA 1102285758 | {E8D7CEBA-5C2C-41ED-B888-4A7AB35A77E3}
ELECTRA 11024756 | {564DED3E-0D7A-4078-8689-6E8E8D0239CD}
ELECTRA 11024756 | {7D7E61A9-DD15-4C94-B46D-9A82D231AEA5}
ELECTRA 11026014 | {0CAC2312-4B19-49F7-9A0A-4917B3A62B39}
ELECTRA 1102CB | {F6B2F362-298B-4DEB-8C9E-04B14858212A}
ELK 11011260 | {7792C1B7-43FA-4230-B827-5143CFAB1055}
ELK 11011272 | {F425053C-9FE0-4926-9CAB-F59A4CB15D1A}
ELK 11011272 | {3D58B5E8-C497-424C-B6D5-A78808606784}
ELK 11011272 | {C106E6C0-BE33-4DE9-BA28-0A0FBC944510}
ELK 11011272 | {62C9F82C-9B7A-4C03-B528-D0CC602C0334}
ELK 11011298 | {EAE624C5-B9BF-4507-A953-B6224BD5618E}
ELK 11011298 | {CC206E8B-BFD5-4BC9-A4B9-F9D20633FB11}
ELK 11011300 | {731B8D8A-0D26-4FAC-B904-5F57E7A23907}
ELK 1101311906 | {818DDDEB-2E77-45C3-96C4-F6724182B49A}
ELK 110137434 | {6922CCC5-514B-4036-B876-FA769B5FF66C}
ELK 11014628 | {894D739D-783F-4BF2-8769-235C809A09C6}
ELK 1101900 | {32CDF0E8-BDA5-4E37-8B42-CD1492E2A580}
ELK 110191336 | {9038FA94-855F-42C4-88E4-D362F0190E8D}
ELK 110191336 | {8492A7AF-8A1F-4223-A71C-9C76842CFDD1}
ELK 1101CB | {73B4F2ED-84BD-4C50-9DB1-F9DAD696FAA9}
ELK CREEK 11012002 | {E8F1018C-E626-4FA1-B3DB-30BAFE068623}
ELK CREEK 11012008 | {49F083FF-CCD6-4656-915A-45D76A900BBC}
ELK CREEK 11012032 | {93B1D857-8A90-4B8A-BADD-0500DBB7E745}
ELK CREEK 11012106 | {9C349921-70C5-4A1B-82FC-D82E641B2142}
ELK CREEK 11012281 | {48393E71-3C00-40DF-917B-F4D8405057D9}
ELK CREEK 1101250558 | {37F13024-276E-4BAC-9DA3-18F4824144CC}
ELK CREEK 110137334 | {D0CAFA51-0A62-4D26-BA1A-5435FD46CC21}
ELK CREEK 1101841 | {2931A5DC-B2DB-4347-BC56-1A5465CF822D}
ELK CREEK 1101873728 | {7A88DF56-F5D3-4199-8DE5-B785314DDBC4}
ELK CREEK 1101915302 | {A3FDB9E9-9009-4CEF-A0DA-9DE8B09BD5D4}
ELK CREEK 1101CB | {C805E056-6565-4701-B47E-65A72A694487}
ELK HILLS 1104334524 | {EE272388-E00B-4014-BFD4-2393C77968CF}
ELK HILLS 11043522 | {554AB938-B8F3-4290-ADAC-4EA3CAD77B4A}
ELK HILLS 11044306 | {455D593A-ACB8-4010-8D43-25C49F4EBC09}
ELK HILLS 110489376 | {455D593A-ACB8-4010-8D43-25C49F4EBC09}
ELK HILLS 1104CB | {FDA3D602-296D-429B-A147-FC7672E184AF}
ELK HILLS 1104CUS8676 | {EE272388-E00B-4014-BFD4-2393C77968CF}
ELK HILLS 1106556750 | {F086E247-E57B-4EEE-88AC-72F504ADF734}
ELK HILLS 1106639540 | {5ABC551C-6308-4592-98D9-27050306D0E4}
ELK HILLS 1106CB | {F086E247-E57B-4EEE-88AC-72F504ADF734}
EMERALD LAKE 04015163 | {850ED620-4A40-40B4-A84F-FC97B5D62108}
EMERALD LAKE 0401843236 | {66C4CA9C-A429-4F81-ADDD-DA733C2913B7}
EMERALD LAKE 0401CB | {BF748DD1-7EA7-463E-91B5-1F0876DD9BB0}
EMERALD LAKE 04028858 | {6E19C0A5-86DD-49E4-909F-112A4E9E5B6E}
EMERALD LAKE 04028872 | {18156E3B-3444-414F-97B1-9EC6878D0720}
EMERALD LAKE 0402CB | {A0667D06-51C5-41CE-85EE-7B2260B907EA}
ESQUON 11012054 | {25AD8CDA-2DAA-40D1-AF6C-EC42757AE02A}
ESQUON 1101717130 | {A375D148-F90C-4957-9740-5804C5CF1EE7}
ESQUON 1101921752 | {E2A6DEC2-4E4E-436D-8B4C-DA2C30337403}
ESTUDILLO 0401850884 | {F934F942-DE0D-4D16-AAE7-D119512DF37A}
EUREKA E 110429676 | {B8F6F54B-5EF0-44B9-9BD5-BD98BEED42D3}
EUREKA E 110435934 | {ED5921D0-8872-4201-A8A0-2E00BFA95E37}
EUREKA E 110498682 | {DD1791F2-46B7-4249-A231-CD7E88BA8BFB}
EUREKA E 1104CB | {6272DCE1-80F1-4C3A-8B1B-A5CE246BB5C1}
EVERGREEN 2103980314 | {EDD48FE8-26F3-406A-9D19-1F9CDD89623E}
EVERGREEN 2103XR074 | {EDD48FE8-26F3-406A-9D19-1F9CDD89623E}
FAIRMOUNT 0401395180 | {6981AFAE-EB4D-4375-A997-CCC0FDE33FD6}
FAIRVIEW 2207135318 | {37C3049B-4114-473C-A4B8-D2C7FF8BB619}
FAIRVIEW 2207426724 | {ADEB88BE-9D94-4EAF-9D73-CAF1584EF647}
FAIRVIEW 2207752858 | {ADEB88BE-9D94-4EAF-9D73-CAF1584EF647}
FAIRVIEW 2207820454 | {813FCD7E-3554-4FD4-A872-37FC7BB487DA}
FAIRVIEW 22078275 | {ADEB88BE-9D94-4EAF-9D73-CAF1584EF647}
FAIRVIEW 220799096 | {55278842-270D-4261-9B21-666405A19DF7}
FAIRVIEW 2207CB | {EA507D40-73C6-4FB5-9309-B2611D605E9F}
FAIRVIEW 2207CB | {659FD2EB-053C-425F-AF25-D9C58353B44F}
FAIRVIEW 2207M500R | {D1A89C8D-B410-4140-B62A-CD8F605AE080}
FAIRVIEW 2207M501R | {9F1312F5-B448-48CC-A9C3-FC2DE03C4391}
FAIRVIEW 2207M514R | {659FD2EB-053C-425F-AF25-D9C58353B44F}
FAIRVIEW 2207P142 | {0B7F62BF-A04D-4B9C-AA26-AFE69516CA65}
FAIRVIEW 2207P148 | {61CE2DCB-0D53-494B-8C34-3F4D665DD273}
FAIRVIEW 2207P150 | {0F676DC3-CFF5-456D-B8E2-CAA231B3A90A}
FAIRVIEW 2207P302 | {962C2ACC-3493-4996-A5E2-203A03BF24DC}
FAIRVIEW 2207P304 | {31523F0A-9FD2-41D0-8A36-117080631D88}
FAMOSO 11012686 | {ACEBCDD6-02C7-4E43-8216-500D51906AAE}
FAMOSO 11033652 | {D5555666-40ED-4570-B5ED-FA15649232BA}
FELLOWS 21031100 | {E6A68FB7-9DA5-412C-BF86-CB46F94D3EDD}
FELLOWS 210382182 | {EB42982D-7786-448D-A97D-1D95754A39F0}
FELLOWS 2103CB | {A2B8C63A-2E3C-415F-A84C-6AAC2DF68E0B}
FELLOWS 21041052 | {B4133E9A-3C47-443C-9B0E-8525C1EE28EC}
FELLOWS 21041073 | {837EBEEA-6D15-4355-A56E-82983C8D6DE0}
FELLOWS 21041074 | {98882D59-2D4C-4B7B-B11D-5E24933457D4}
FELLOWS 21041098 | {E7D01B0C-CE5E-46A2-9356-A74F823DB66C}
FELLOWS 2104274456 | {7F80779C-1619-4C01-8BF5-4EDD2481CA9B}
FELLOWS 210442100 | {D4386F50-ABF5-43E7-8326-09F92A4E0719}
FELLOWS 2104CB | {99CA2E77-9D49-4EAD-A742-E8CB938D605F}
FITCH MOUNTAIN 1111424 | {12685307-B1B3-4B99-A51F-5759145ED4DA}
FITCH MOUNTAIN 1111555644 | {D010A5A5-D5D9-4C0F-9746-9A3B4B4F8B0D}
FITCH MOUNTAIN 1111610 | {1D8E3949-43DF-43FB-98A9-8DD711C7AB01}
FITCH MOUNTAIN 1111752596 | {1E79F907-28BC-4BCD-8BF6-A38789A74B9B}
FITCH MOUNTAIN 1111792628 | {89345583-C072-4A34-9FA1-B63C26C09270}
FITCH MOUNTAIN 1111821431 | {85F11AC0-E7F5-415C-8928-2202FEFE7CC2}
FITCH MOUNTAIN 1111CB | {AA2E97C7-3759-4D9E-BC19-D9ED237F5DA1}
FITCH MOUNTAIN 1112CB | {B406A001-5E88-43B9-9966-330465F8E093}
FITCH MOUNTAIN 1113154 | {E5E424DC-C8C0-4A20-B0C0-11A950F19719}
FITCH MOUNTAIN 11132219 | {BB983267-01FD-4F6C-93D7-6D2CFB53106E}
FITCH MOUNTAIN 111324550 | {C4DDBB89-4E15-4D06-A02D-161343869D3B}
FITCH MOUNTAIN 111324918 | {30AC1F79-37C1-4981-9C64-81FC3670878D}
FITCH MOUNTAIN 111324918 | {A43931B2-20C5-439E-BA73-1FC41AFBF425}
FITCH MOUNTAIN 111324918 | {3FFAE1BF-259D-4785-B61C-C2D9281ECA0B}
FITCH MOUNTAIN 111324918 | {05F28242-E8E8-4E03-89FD-DB4C8AE50A21}
FITCH MOUNTAIN 111324918 | {F2FBF05E-D750-4CBF-8C55-F2FBDF0D5BD8}
FITCH MOUNTAIN 11132955 | {A7CF129A-941D-4B21-8741-387943AC77AC}
FITCH MOUNTAIN 1113352 | {F0A897EB-747B-40C7-9836-35FB75DF52B9}
FITCH MOUNTAIN 1113356 | {8B3CC79A-091E-4AAF-B32E-734671E78840}
FITCH MOUNTAIN 1113406 | {31A95017-FE64-4D4F-A4CA-39176F23B79F}
FITCH MOUNTAIN 1113443164 | {82F1B323-9F47-4844-B053-6FD72157B262}
FITCH MOUNTAIN 1113455837 | {909265AE-B9CE-4C7B-AA31-2E8C0E402FA2}
FITCH MOUNTAIN 11134566 | {7C0F49AE-FCF7-4330-B22C-F61243651B62}
FITCH MOUNTAIN 11134570 | {7BF9631F-F2B9-4D9F-A7A1-8FB9FBCDDF84}
FITCH MOUNTAIN 1113482752 | {BE29C1CC-62E1-4311-8E3E-30A3FF867046}
FITCH MOUNTAIN 111349826 | {9C1AE994-AAFB-42C4-B159-C85E938EE24E}
FITCH MOUNTAIN 1113677510 | {034C6230-F1B3-44AD-89C0-4E5511DEDDB5}
FITCH MOUNTAIN 1113769 | {A5FD1C37-F9AF-4CF2-92E3-13116C3E9E56}
FITCH MOUNTAIN 1113775992 | {D0DDB5C0-186A-4907-865A-9BE93C7A605E}
FITCH MOUNTAIN 1113824468 | {DEA1978F-46CC-423B-B61B-1E6D21D8F6B2}
FITCH MOUNTAIN 1113CB | {0452ACFB-6610-4670-BD1F-C0548BB4EE02}
FLINT 110138570 | {68DF9E12-6736-4943-BDEF-9FA6962872B3}
FLINT 110140666 | {F60C4C6E-928C-45EE-B5E3-FE18B260D743}
FLINT 110150960 | {347D4345-ECE4-4101-A340-58299F24E405}
FLINT 1101750 | {070C906B-0802-4429-8F7B-A68007FED9B4}
FLINT 1101958726 | {E5FFB0D3-B57B-4F94-B4AC-8B76666355C5}
FLINT 1101CB | {68DF9E12-6736-4943-BDEF-9FA6962872B3}
FLINT 1102CB | {C6A91D98-B704-457B-84C0-0DADC269F3D4}
FLORENCE 0401110836 | {013CB3A7-7F48-4CCC-AAF7-D8407E0657E6}
FLORENCE 0401CB | {9898F55D-4181-4FB3-A3AA-B13258B3B860}
FLORENCE 0401CR220 | {D87265E8-5674-4799-A45E-7F1EC7B446CA}
FOOTHILL 1101251688 | {2342B1BA-896A-4C52-9E39-F87AA4527061}
FOOTHILL 1101549904 | {BEF6045A-3518-436C-A876-62625F5A4B60}
FOOTHILL 1101549904 | {5DE69153-3C7C-4310-A10D-0098A2A3216B}
FOOTHILL 1101549904 | {2710935D-955C-4B3B-AB55-13FA5CE7C745}
FOOTHILL 1101645910 | {DA93CD43-4632-46CD-9EF3-906DC0AD12DA}
FOOTHILL 1101CB | {A0154153-BF56-4706-9955-FEBD0CFAAAA7}
FOOTHILL 1102300858 | {9ECBA446-F3A3-4026-8D5A-052B7A86DE4F}
FOOTHILL 1102300858 | {505AA200-73EC-4788-9C3D-D03293CBC07F}
FOOTHILL 110263550 | {1D763ED6-4861-4195-B573-B8274E1386C4}
FOOTHILL 110299432 | {7C9F6E98-6AD1-45C0-AA12-C5A39FC092A4}
FOOTHILL 1102CB | {CF5272DC-8419-42E3-A72F-BD395166C5DF}
FORESTHILL 11011802 | {9A3F5548-F595-4F3F-89FC-9574388096DE}
FORESTHILL 11011820 | {D7E3765B-F7D8-4BEF-8206-669D15220FDF}
FORESTHILL 110137238 | {05132EF1-E962-492C-8CE4-DD542C3B3D15}
FORESTHILL 110150486 | {FE85142D-4AEA-430F-BD77-45CC919584AA}
FORESTHILL 110175340 | {9A3F5548-F595-4F3F-89FC-9574388096DE}
FORESTHILL 1101890670 | {ED9435F9-E06B-4A98-B053-EB0C1DC8369F}
FORESTHILL 1101CB | {ED9435F9-E06B-4A98-B053-EB0C1DC8369F}
FORESTHILL 11022106 | {01403AE6-90D4-4B19-983B-B7AD8BDC29F6}
FORESTHILL 1102359542 | {27195F6D-400C-4416-B7C7-104E52ECD248}
FORESTHILL 1102CB | {D5AE9DC8-C124-4C49-BB35-C0CDE45BC05E}
FORT BRAGG A 11013100 | {0D62503E-67CB-4A8E-BC3C-093230B8FF31}
FORT BRAGG A 11013113 | {C40FEC6C-4399-4FDE-8ABD-E729D917D61E}
FORT BRAGG A 11013147 | {08A9420B-4071-4BCA-B16C-C3296F7AEAE2}
FORT BRAGG A 11014622 | {FD379B27-6785-4E43-84D1-7E22C4EB286F}
FORT BRAGG A 11014698 | {C40FEC6C-4399-4FDE-8ABD-E729D917D61E}
FORT BRAGG A 11016069 | {2FE3D1C5-1EED-4BFB-96F6-AE108D23C587}
FORT BRAGG A 110195294 | {68CC0E2F-7024-44BE-85E9-7639B7540AB9}
FORT BRAGG A 1101CB | {34DFDDBB-39B7-422C-B7C0-767BF9731AB2}
FORT BRAGG A 11021226 | {75E57175-6FC2-4C18-9858-49FEBB55AE91}
FORT BRAGG A 1102265870 | {E0FAB4E0-B6D5-48CE-BF78-A57BBF22B01A}
FORT BRAGG A 110231304 | {BF12DE8B-4E1C-4761-B900-F5DD3C822515}
FORT BRAGG A 110233064 | {43E4C42F-5275-4CEE-85B6-6C7E82072099}
FORT BRAGG A 110235592 | {88ABC052-C1CA-454C-9520-7292289269D5}
FORT BRAGG A 1102416218 | {39C594BB-A2EE-491E-843C-6A3739AD958F}
FORT BRAGG A 1102416218 | {7A8B738E-E99E-4EA8-B90B-160DFB70847D}
FORT BRAGG A 1102416218 | {7FA97E04-C080-43BE-9A02-7459BBEF80DD}
FORT BRAGG A 1102418 | {2F10EC8A-D66D-41A3-A96A-C091A52D1815}
FORT BRAGG A 1102529078 | {67595677-56A8-424E-B5AB-A72A83600D56}
FORT BRAGG A 1102667996 | {267610AC-9BEB-429F-830E-E78C6931DCD3}
FORT BRAGG A 1102816 | {DCB2091F-52D0-405B-8DDE-82750DB61471}
FORT BRAGG A 1102956 | {08B3D9BE-5082-4181-84EE-826761A8736F}
FORT BRAGG A 1102CB | {A11A44BE-5FF6-4EAE-B643-DC3914767492}
FORT BRAGG A 1103CB | {C8B7B79F-9539-45C9-8977-9A8FC5806A25}
FORT BRAGG A 11041316 | {BC4F0196-621B-4CEE-9F22-55FAA9EB12A8}
FORT BRAGG A 110436526 | {741F819D-F84A-48D0-B917-155D72B8DC6A}
FORT BRAGG A 11044690 | {9AB01B94-B2A5-4A8A-9109-9F42C093DB3E}
FORT BRAGG A 11044690 | {510564D1-DEEF-4962-A1E8-3812661AD494}
FORT BRAGG A 1104529076 | {ED095E9E-F3A0-4C4B-ADA3-9E3DFB5A9FCD}
FORT BRAGG A 110465894 | {DDA08885-FEC3-49A8-9C1B-A5CDAFE21444}
FORT BRAGG A 1104872358 | {F09AC1B9-9514-473B-B8B0-A2B230C8B557}
FORT BRAGG A 1104CB | {743824B8-B7E6-418C-AF37-30E4E0572D08}
FORT ORD 1101131442 | {B9D685D9-B754-4A2C-A3F1-84FA57208D0B}
FORT ORD 11019516 | {B9D685D9-B754-4A2C-A3F1-84FA57208D0B}
FORT ORD 11019518 | {B9D685D9-B754-4A2C-A3F1-84FA57208D0B}
FORT ORD 1101CB | {66CA8537-4E7C-48FF-82D7-109E7EF7B7FC}
FORT ORD 210531972 | {19A9EA23-E6EA-4421-B433-35E36EFF79AD}
FORT ORD 21059140 | {19A9EA23-E6EA-4421-B433-35E36EFF79AD}
FORT ORD 2105CB | {29DAE9CE-CAE3-4935-AB0F-06DB01859441}
FORT ORD 210633694 | {95AB47FE-6B9D-4A04-9C44-EED36F1BA13B}
FORT ORD 210637286 | {9AA16F48-39A4-4006-910E-3E37752DF955}
FORT ORD 21069136 | {AB7BD794-6A54-404B-96D0-00596CF55B93}
FORT ORD 21069138 | {74FCA6FB-B715-4BAA-AD91-FB257E0560D4}
FORT ORD 210695186 | {0139AD78-6D54-4C40-B88F-B8F196A0FC71}
FORT ORD 21069656 | {8BA4213A-D34B-4B87-B8F6-E146FF0B7281}
FORT ORD 21069658 | {6B4BEF51-729A-495B-8FC4-CA82105C9822}
FORT ORD 210736596 | {121773FD-4C4B-4842-BF5D-136BCB9BFB8D}
FORT ORD 210779670 | {018C3E1E-E9D7-4770-B296-F1B4D7801EF4}
FORT ORD 2107CB | {5AF19FAC-D5B1-4A0E-9483-EA04C351FFDD}
FORT ORD 2108CB | {AF7D3D91-B816-4BC0-A0EF-CC9A68E30A8C}
FORT ROSS 1121124 | {228A6257-66FD-4F4F-AA34-7D22FE084DBC}
FORT ROSS 1121124 | {248D14D7-7D04-4C62-A37F-140DEB3770D3}
FORT ROSS 1121134 | {D2E66D36-59AC-4BEC-BEE9-31C660B6B4ED}
FORT ROSS 1121204 | {62984F08-7842-4FBA-8D96-707DCA078F65}
FORT ROSS 1121204 | {031CA341-2C0B-4194-9FCE-C18FD57B6895}
FORT ROSS 112137326 | {56EC8BE0-B402-4A7D-9076-C44EBD9A9DDD}
FORT ROSS 11214521 | {2E329EB8-54C6-401C-9AAE-C08CEA4D7289}
FORT ROSS 11214614 | {36E821CE-0F96-4DE1-8152-1087521FEC6A}
FORT ROSS 1121560 | {C44E173D-32C1-4900-92A5-AD54BFE2000C}
FORT ROSS 1121612266 | {F813F206-BF9E-4739-A94F-434D2CFC229C}
FORT ROSS 112170288 | {19BB688C-7539-4331-8ED9-2B0221333B05}
FORT ROSS 1121CB | {6432AE5E-F371-470F-8E71-1BA304A7A433}
FORT SEWARD 11211690 | {E448EB4C-7ECC-4C43-A720-97024B873C96}
FORT SEWARD 1121CB | {F2B197B6-F439-443B-9926-76B11912B9BA}
FORT SEWARD 1121CB | {8ABCB26D-EB6A-427F-8523-A12B2F7DC850}
FORT SEWARD 1121CB | {5F6D4027-4011-4855-A106-E303E629C601}
FORT SEWARD 1121CB | {9D061223-5B52-4134-9A27-9EB1E4A74BC8}
FORT SEWARD 1121CB | {B99B71AC-5818-4B5D-B7EA-9549DEDA515F}
FORT SEWARD 1122CB | {A8BD1602-9337-4713-8C36-04951ECB999C}
FORT SEWARD 1122CB | {DDBF5221-9BD5-419F-9A17-E9260A89D7CD}
FRANKLIN 1101P132 | {6376A175-D3DE-423C-8B8A-9B6318316FA7}
FRANKLIN 1101P138 | {DB131498-A71D-4A26-A77E-BBAB941A8DB9}
FRANKLIN 1104615788 | {EC1037DF-9D9B-425C-812F-13D2FBDE6247}
FRANKLIN 1104CB | {DDFFEADB-3F2B-4296-80F5-9B1536EA3D55}
FRANKLIN 1104P136 | {F15BB3D1-0A60-48BB-96E4-777A07B496BE}
FRANKLIN 1104P146 | {4B04C7BE-F037-4E43-AD43-455E3B1A9C74}
FREMONT 11041516 | {CA0B1D0C-E4E8-4109-942A-39C0D83AA3E4}
FREMONT 1104645342 | {5FF4B67A-802C-4B9E-AA95-209BF5DD22D4}
FREMONT 1104CB | {62124451-9B9F-46EB-B50A-534B1B0CB257}
FREMONT 1104MR339 | {02184DCE-4986-4759-8E54-71AE9F6D44F7}
FREMONT 1104MR584 | {B59BCFB8-3D30-441A-916B-9810D227F102}
FREMONT 1104MR707 | {C3E4270B-E62A-43D8-B1E2-6AFA491A42A5}
FREMONT 1109MR735 | {6633ED5A-E5C5-40D0-B168-4DAA9CE2F63F}
FRENCH GULCH 11011892 | {EEFD67FE-817D-4F21-AFBD-03D493187270}
FRENCH GULCH 1101342672 | {65A2DA5F-3B76-49F9-A606-C5803E69B298}
FRENCH GULCH 1101655538 | {34291823-BC12-41A5-A3DC-31BEC52E5B56}
FRENCH GULCH 1101CB | {20DFFDEF-5135-4324-A022-CDDC3E81B3A6}
FRENCH GULCH 11021462 | {673B1BD0-3EFA-4599-AB2C-B37C28829526}
FRENCH GULCH 11022902 | {CBEFA52C-F905-473F-B9BB-602279DBF4B7}
FRENCH GULCH 1102CB | {68ED899E-4033-413B-A72A-EE83BDC8B804}
FROGTOWN 170113412 | {32DE7714-2265-4DEA-9044-817FFC428BF4}
FROGTOWN 1701376600 | {FBB8E5D7-E651-4134-994A-9086782637C7}
FROGTOWN 1701473222 | {CA437287-19DD-4564-B2C3-AF4B8EE725B9}
FROGTOWN 1701564780 | {0BFA4B23-4D57-4C40-BB23-EDE12E90512D}
FROGTOWN 1701564780 | {E5649CCC-C39D-4380-9481-95A0B24F8696}
FROGTOWN 17016807 | {CA437287-19DD-4564-B2C3-AF4B8EE725B9}
FROGTOWN 1701914602 | {357B6EC0-12C8-4B2F-B623-9C6A84C1BE09}
FROGTOWN 1701914602 | {8E20FEA0-6674-4401-B203-6D9DCFFBEF63}
FROGTOWN 1701914602 | {C3DB4E0F-C0CA-4DDC-BCD3-F233BC5939CD}
FROGTOWN 1701914602 | {CECB1DAF-988C-41CD-BDCA-E88063DD7E54}
FROGTOWN 1701914602 | {F6D53A5D-7A57-4A54-BF8D-9FAF7A9ACD4B}
FROGTOWN 1701914602 | {3F3EE457-4DDC-4A60-99A7-9E3D7C3CD558}
FROGTOWN 1701CB | {CC00F970-8F13-4247-87D9-81AC67764BAD}
FROGTOWN 170211212 | {275411B9-F65E-4C2D-AC92-04E91C75A810}
FROGTOWN 170212282 | {3C80F4C0-E9A6-46C9-A594-5586FAD2CDE6}
FROGTOWN 1702204480 | {A12EF9F2-A626-4D54-A592-A0BB35CB6549}
FROGTOWN 1702224708 | {35EE754C-7E3A-4C6F-81A6-D14B057757B0}
FROGTOWN 1702307998 | {89CC7A11-127F-43C2-800C-EB67E4FC6948}
FROGTOWN 170232556 | {9BE6D037-BD8E-46AF-A32B-7F2BB00D9E6A}
FROGTOWN 170236870 | {11F38DA8-6582-44F5-A0BF-18D25BB5EB9F}
FROGTOWN 170236870 | {94EE7076-462E-4300-BB9C-E1B2A1AE599F}
FROGTOWN 170236870 | {B8116AD6-DBDC-47A6-A391-44EDCAB46E2B}
FROGTOWN 1702423550 | {8E576958-320E-40DF-9E05-F5D342055FED}
FROGTOWN 1702423550 | {971D713E-0C35-49B7-9B14-2F7B62E40DB4}
FROGTOWN 1702423550 | {88053C0C-97C7-4782-8608-B2805392B0A9}
FROGTOWN 1702531640 | {84408236-98E9-47A1-A718-F13EC099550A}
FROGTOWN 17027108 | {3530973A-E1ED-42D6-80CA-474C64476B90}
FROGTOWN 1702737236 | {F66F5E9F-01CE-4986-95ED-652F7B3AA4E8}
FROGTOWN 1702737236 | {F0E1E0FF-88A1-4ACA-9BA3-065AFC2B6B60}
FROGTOWN 1702737236 | {491A0626-7E46-4403-B27A-531A0EB352F4}
FROGTOWN 1702739858 | {1A9CCDAC-B50D-483B-87EA-5C0A6CCF7B4E}
FROGTOWN 170274648 | {C985F098-6ECF-4C69-B902-1B5157262ED5}
FROGTOWN 170275252 | {7D119895-6544-4FC7-A1BD-CC0A5D84976F}
FROGTOWN 170275252 | {8FDFFC53-3B07-4C47-B377-A6499A0C909D}
FROGTOWN 1702812366 | {4CE434B8-E02D-4920-A230-5B04B8D42C75}
FROGTOWN 1702815616 | {AC647AA8-B527-4875-A38A-FEBD0757B10B}
FROGTOWN 1702832694 | {2D97F35B-9FCA-4093-B52E-0AE094FEFD58}
FROGTOWN 17028482 | {DEF24EAD-1BE2-4F6F-8D2A-6151341F3B41}
FROGTOWN 1702902652 | {7740C633-8749-4C6F-B889-238D2B223A2F}
FROGTOWN 1702921482 | {04E860C8-9264-495F-B263-FD14492AF068}
FROGTOWN 1702CB | {646B02DA-833B-4BEB-8A59-9FDCAF947841}
FROGTOWN 1702L5407 | {3530973A-E1ED-42D6-80CA-474C64476B90}
FRUITLAND 1141200856 | {549199A2-4261-43E8-8700-8DDEE28DEA6C}
FRUITLAND 114137410 | {CF682344-0C1A-411D-B173-CAE04AD6EAA0}
FRUITLAND 11413902 | {D6DBBF9F-6B56-42A5-8187-1FDC6DA3F5CA}
FRUITLAND 1141866852 | {7AAAEF20-BCE1-42D0-9686-CF0447F71CAB}
FRUITLAND 11418860 | {901979A9-33A5-4FBB-9019-2CBDDF98F849}
FRUITLAND 114195324 | {CC7C3C64-46F1-4FBD-8FBE-B236D52A742D}
FRUITLAND 1141CB | {2690968B-84D3-4326-843B-7CB873856615}
FRUITLAND 11422006 | {0E6F84FB-9664-4CC2-ABC9-E723037587E4}
FRUITLAND 11423751 | {D56B4A7A-14F7-4E0C-8A73-5056D5B1669B}
FRUITLAND 11426054 | {8C40E614-4E0B-4C86-B614-0076615AE897}
FRUITLAND 11426064 | {13AA4ABA-A8C5-4005-8E1B-08EF6ACA3F13}
FRUITLAND 11426064 | {4A1EC5D3-CF7E-4E3A-B115-9A4757B7DAC6}
FRUITLAND 1142615540 | {C9D02877-D683-4E00-8203-11814AA4CD46}
FRUITLAND 114263170 | {BDFC6231-C003-4BB6-9C95-EEAEA882FC5D}
FRUITLAND 114263170 | {69FD4992-2A22-402B-ACAC-E090559F2AEA}
FRUITLAND 11426865 | {656D1302-474C-4DEF-8FBE-1292CADAEAFC}
FRUITLAND 11426865 | {061944EA-54FE-4254-A923-79D0E2262C7B}
FRUITLAND 11426865 | {53F33F0A-A40C-40F9-A528-91CF661FDF57}
FRUITLAND 1142899734 | {84FB064E-BD98-4DA8-AF4F-2B45B0138D7B}
FRUITLAND 114293234 | {08481CF7-E810-460B-90F1-567535D71EC0}
FRUITLAND 114293234 | {F2F5CD46-ED54-485C-8E9F-F1D6186FA89B}
FRUITLAND 1142CB | {C08075C5-E7BA-4353-AF25-7A00C76C5CA3}
FULTON 1101CB | {30FC3806-038C-4AC3-A393-91BFE1889F67}
FULTON 1102258281 | {09E88888-5AC3-4010-8136-EE66FDCF2B20}
FULTON 1102287172 | {1B09A511-4056-470A-B00D-4FB4522380B2}
FULTON 11024334 | {F2C72F8A-06E0-42ED-81D6-01D05809B312}
FULTON 11024994 | {EA9B2479-0C7B-4A59-82AF-47AD3E8F521E}
FULTON 11025102 | {A7116264-DEE4-49AB-8F9D-DDEB0877D031}
FULTON 1102539766 | {C8A1FC38-215C-46A6-A562-4B3728659385}
FULTON 110257686 | {08567963-8339-4FA1-9F78-3A951553BB03}
FULTON 110258990 | {D9F1E4D5-6C65-4B74-B28E-1D1E2528E5E8}
FULTON 1102885254 | {FE4477F8-57EC-4E5D-AFB9-11BA35B59AC3}
FULTON 1102904058 | {A7116264-DEE4-49AB-8F9D-DDEB0877D031}
FULTON 1102CB | {6ABCE308-047E-4F2E-99AB-65F7E6BEAD99}
FULTON 1104466 | {AE97AA30-6595-4674-A3E8-E3C81CE235CD}
FULTON 11045016 | {AC56E29F-28CE-4D76-8621-1CA9BB136C25}
FULTON 1104787606 | {B52A3AF9-0A2C-446A-B74D-0963F86B07B8}
FULTON 1104CB | {86598FBB-5AAE-49A3-956D-D4079C4EFDE4}
FULTON 1105142 | {920CA8B7-5F50-470F-AECC-E88A1C8A6815}
FULTON 1105172 | {63777790-64ED-4263-AFF5-02757B725BB7}
FULTON 11054106 | {957874C2-FA06-452C-924E-A5E4C30E68F3}
FULTON 1105410856 | {BA80D288-38A8-458C-8E80-169549E41B99}
FULTON 110555802 | {957874C2-FA06-452C-924E-A5E4C30E68F3}
FULTON 1107126742 | {C134E3B9-E693-4C16-B3A4-BFE77C3B9516}
FULTON 1107145720 | {6604208B-F35A-44BE-998D-E714E06DE284}
FULTON 1107214 | {82FFCF9A-29C9-4CD0-A5CE-AFFBFF95F55A}
FULTON 110746958 | {01F2557C-4641-4BA6-8DDF-FA4264339C1A}
FULTON 11075058 | {FE78914C-A6BD-410E-9456-E7CDC05BA1D6}
FULTON 1107604 | {E553BB4B-1179-4653-BCDF-D0DE748C3124}
FULTON 110777670 | {5B55A465-FAC4-48C8-B9A5-F80EA4DBED38}
FULTON 1107914380 | {0F4D2AEB-4E7D-471D-A43E-83FDE769C4BD}
FULTON 1107CB | {72AE5EDE-AC15-4265-AF32-67B0F370C217}
GABILAN 1101270626 | {F38EBDBB-EBB5-4515-8A2A-95C4ED542B7B}
GABILAN 11013034 | {D9D7498B-EECD-46C9-B5F7-8D9ED4F7E924}
GABILAN 11013090 | {43462865-0ED2-47A6-A8E8-8B52D18F5577}
GABILAN 11013722 | {6D5B17B5-960C-48B4-806D-BF9DA1A8A3B0}
GABILAN 1101460414 | {0008E3B5-1496-4F6F-834B-CA7B37853F9B}
GABILAN 1101468770 | {46640EDA-F725-4290-91FA-745D4939F6CF}
GABILAN 1101566352 | {0B568E58-6FDD-401E-8368-A329B6DA6B93}
GABILAN 1101989608 | {65A71434-28A7-4658-91E5-E31B20037DDB}
GANSNER 11012006 | {AD16C82F-076B-43F6-B112-51D5058EB123}
GANSNER 11012424 | {7FF9C2B4-7885-497B-BE5B-64337D7948AA}
GANSNER 11012424 | {5F3FB324-95DC-4621-A360-0E95039B641B}
GANSNER 1101336664 | {233E8F5D-2496-4AA4-9731-97AA5A5CDA63}
GANSNER 1101372132 | {EA937CC6-E132-4325-A59D-A7FEA701DEB9}
GANSNER 110137550 | {2D495744-1EEC-4B5A-AB6C-8BE5D83F4E62}
GANSNER 1101489276 | {72504F1A-5BCF-43C4-ADF1-0100A2C7CFD0}
GANSNER 110152664 | {30DCFFEA-B919-4305-96B7-F6B3EA753723}
GANSNER 110152664 | {ABF9C0D8-FB4B-45D8-8766-B92175021507}
GANSNER 110152664 | {248F09B8-1D5D-4034-96B7-C372BB4594AA}
GANSNER 110152664 | {837222F9-D8A2-4260-8BFB-B6E14FA07798}
GANSNER 1101590690 | {2EBA9C84-1564-4E97-B683-C3C5B09E3911}
GANSNER 110199388 | {13627031-EE44-4823-A048-AA36CB9BE013}
GANSNER 1101CB | {40645203-FB29-4536-8849-C6C7781BFE2D}
GARBERVILLE 11011514 | {7F9C85EF-487B-454C-8489-CDBA87D32E67}
GARBERVILLE 11011604 | {905A282A-4E87-42B0-8385-244613D03E1D}
GARBERVILLE 11011617 | {F5DCCEAB-4D62-4EBC-AEE0-C0A0C3478F85}
GARBERVILLE 11011750 | {08393BA3-C925-468F-82DD-D9087C4038E5}
GARBERVILLE 11011770 | {BBD56973-ABAA-4951-A1EE-E863C47010B2}
GARBERVILLE 11011770 | {EF1A0476-C3BA-4833-B974-B689B6B09DB7}
GARBERVILLE 11011773 | {610662F4-849F-4658-9023-AAB7EE0C319E}
GARBERVILLE 1101323694 | {624B3FD3-11BE-4D35-879D-7A58EF854DA3}
GARBERVILLE 110139524 | {78F4DDEB-2C9F-459A-8954-8C704D70DD64}
GARBERVILLE 1101438596 | {39301543-F3C9-446A-ABF8-E960F80CEDFE}
GARBERVILLE 1101574630 | {7F9C85EF-487B-454C-8489-CDBA87D32E67}
GARBERVILLE 11016014 | {A4364083-2C85-4568-8856-4501BCAB9839}
GARBERVILLE 11018543 | {395B3611-CB53-470F-8FB0-E588AE0009F5}
GARBERVILLE 110197300 | {BA71994D-6A0B-4F0B-9E44-79C1DD5F42DD}
GARBERVILLE 1101CB | {E1AC8377-8E8C-4414-AED8-68291E68F4CE}
GARBERVILLE 11021510 | {1339ADD4-8465-4C5F-ADF0-25D79054621F}
GARBERVILLE 1102176634 | {270BA5E3-ABF3-4D3C-80E3-65C34292C4DF}
GARBERVILLE 11022010 | {0FD31FD2-8045-433E-9D12-C8669CFF0383}
GARBERVILLE 11022124 | {4AC60F3F-45CC-4080-B7C8-2A403EC32A74}
GARBERVILLE 11022500 | {246D7475-4433-4E0E-BFF7-D31F98B721EC}
GARBERVILLE 11022500 | {88C6809D-B02F-4C53-8336-AC5ED9CC4964}
GARBERVILLE 11022540 | {09BB38E4-7FE7-4BD1-9CFE-F62698521734}
GARBERVILLE 1102343364 | {2498B92D-AA5B-4EEA-B8BB-064A43070717}
GARBERVILLE 110237054 | {BF5AD074-5FDE-42FF-9EE4-EC1E7EF14392}
GARBERVILLE 110256048 | {BF5AD074-5FDE-42FF-9EE4-EC1E7EF14392}
GARBERVILLE 11026084 | {0A529EA6-6476-4FE6-9A4C-9E2DBC5F560C}
GARBERVILLE 1102662576 | {09BB38E4-7FE7-4BD1-9CFE-F62698521734}
GARBERVILLE 1102802246 | {D85ED4F0-3E42-430A-BAC1-4900EEA124D4}
GARBERVILLE 1102829876 | {3084C8AF-A613-4319-A6A3-265ABB06B80C}
GARBERVILLE 11028652 | {56012ECF-3863-4B00-9D44-45818E54BBA2}
GARBERVILLE 1102915978 | {5647EDBD-9C48-41AB-BE66-016C6AAA1D29}
GARBERVILLE 1102915978 | {270BA5E3-ABF3-4D3C-80E3-65C34292C4DF}
GARBERVILLE 1102939030 | {9FAB4BEC-49B9-4255-B280-32F1A0F1E3A3}
GARBERVILLE 1102CB | {76599403-EF2F-43B7-895E-85F706D26E36}
GARBERVILLE 1102CB | {EF832099-951B-4D7C-9CC7-50C2AACC0B61}
GARBERVILLE 1103674334 | {F18FD026-5429-492B-82E5-A99DF1FFA498}
GARBERVILLE 1103CB | {81BF210B-E399-451E-B158-93FB561813DD}
GATES 1101934088 | {98FD8AB2-677F-49F1-A16C-257BAE82BD34}
GATES 1101CB | {71A933C5-036E-4711-9C71-FE4CF96C2CC9}
GATES 1106755338 | {BD3133DA-EDF7-4B1E-B188-9C3D48C9C62F}
GATES 1106879496 | {3E771B8A-A2BC-4AF3-89F7-B4D332DE2C00}
GATES 11069090 | {E04B9F44-6A56-40F2-BEEF-BFDFECD43756}
GATES 110692202 | {A3462E27-E93C-4407-B866-3ED32DB5C019}
GATES 110699914 | {8B72A489-D865-42E1-9035-B61B87AB0369}
GATES 111137824 | {B7B755E1-3013-4009-A0D9-81DDBA3CD279}
GATES 11119110 | {F86A6BE1-0FB1-4237-9566-6259514B9DF3}
GATES 1111CB | {05165E57-0A30-4D3D-8FC9-A095D2F5826B}
GERBER 11021560 | {51D7DA46-9CAC-46EE-9575-3C307DF390C6}
GERBER 1102190339 | {51D7DA46-9CAC-46EE-9575-3C307DF390C6}
GEYSERVILLE 1101122 | {69EA27A3-0D2B-4A2D-A229-63A3090F6AF6}
GEYSERVILLE 1101166 | {DC4595FD-6B3F-430F-8A6B-C07BE18B58D6}
GEYSERVILLE 1101166 | {71F3D52E-769E-4E34-8AC2-D2E68D8FF914}
GEYSERVILLE 1101172096 | {A4BD27A2-3BDB-49BF-8D37-C7C2B93E2E67}
GEYSERVILLE 1101354 | {377EDE62-95BF-4247-B5CE-2FDAD489198A}
GEYSERVILLE 1101354 | {8735F018-B7F6-43BE-A1D1-DAC1AC58E1A0}
GEYSERVILLE 1101354 | {6A4F0A08-1569-46C8-8F72-C1A8C75E11C5}
GEYSERVILLE 1101354 | {02D0A0CA-B431-4FB2-AF18-E6305A42917F}
GEYSERVILLE 110135492 | {A4A124EA-8920-4709-8090-23E3A2E000DC}
GEYSERVILLE 110137454 | {8E06DD08-111B-4D73-B845-1ABBADC77B32}
GEYSERVILLE 1101406798 | {EC9348DB-6FAC-4BC4-A3C0-6B6419696175}
GEYSERVILLE 1101429006 | {7E3BECFF-8D7D-4E66-87B8-14F0BE7604FC}
GEYSERVILLE 1101480 | {B067E8FC-275B-40E3-B858-2220AFBD2EF2}
GEYSERVILLE 1101482 | {FC698F49-08CB-4375-B278-3C062280B4C5}
GEYSERVILLE 1101711966 | {1896BE4A-1AA3-4F21-93D4-ED4B47D95FC3}
GEYSERVILLE 110179788 | {CD516753-E346-488C-8A28-4021B3A7E490}
GEYSERVILLE 1101801904 | {AC125630-32B8-4336-8024-7175EE6E43AB}
GEYSERVILLE 1101975350 | {1C85BACB-B649-4EAE-8382-1B9833570386}
GEYSERVILLE 1101CB | {377EDE62-95BF-4247-B5CE-2FDAD489198A}
GEYSERVILLE 1102220154 | {4D770C11-A9C0-4B50-BC88-1E94F5926B75}
GEYSERVILLE 1102235124 | {4D75EBF2-65F6-4895-9B4E-AAD6D6F48D1D}
GEYSERVILLE 1102331444 | {D1475177-49FD-4D65-8D0F-817A6104925A}
GEYSERVILLE 1102350 | {0240FFD3-64F2-49C6-8F4A-119D98085B41}
GEYSERVILLE 1102429530 | {6B65A809-12E3-40D6-89FF-84D72C02075E}
GEYSERVILLE 1102484 | {1E362916-4E6D-4E8A-A229-F0750B3C8096}
GEYSERVILLE 110249056 | {4D770C11-A9C0-4B50-BC88-1E94F5926B75}
GEYSERVILLE 1102501402 | {603C60DE-C084-4617-B5FA-5EB5F16FC6B3}
GEYSERVILLE 1102504260 | {BA062BA2-FAD7-4707-A9BF-0F5097E508D7}
GEYSERVILLE 1102522 | {B09D42AC-0CDA-4ABD-917A-C98377E7425E}
GEYSERVILLE 1102522 | {B7726FE8-A35B-4883-A20B-6CA79C5DB82B}
GEYSERVILLE 1102522 | {C28A65D7-37D3-4F6C-9C48-AF74AD2858BE}
GEYSERVILLE 1102537096 | {1CBBA641-695F-4908-8A3F-72BA5ADCB13F}
GEYSERVILLE 1102548206 | {61A40993-1799-45E2-A875-A7E8542BA751}
GEYSERVILLE 1102735600 | {1793E18B-A8B5-4A05-B096-C6FF30B6AFC8}
GEYSERVILLE 1102756 | {5A3AA98B-24A2-41A0-8E61-B5A0B5E2F3E7}
GEYSERVILLE 1102776178 | {082C86BB-EE1F-40DF-94C4-4FB1575D2884}
GEYSERVILLE 1102785626 | {BD048B94-FDE8-4EDB-AB8C-2693863E8CA6}
GEYSERVILLE 1102868292 | {FC4A4168-3718-4179-B688-0392741460DB}
GEYSERVILLE 110289714 | {450BD680-08E6-46D0-AD80-CB37688E8C0C}
GEYSERVILLE 110289714 | {225505FE-91AC-45A2-A8F4-D9DAE66F2063}
GEYSERVILLE 1102904170 | {012EDF18-DBAC-4496-A5CF-592EEBEC324C}
GEYSERVILLE 1102CB | {B7169D14-D576-4EBC-83AD-DD429DE5E777}
GIRVAN 11011330 | {80C93813-C876-4450-B60D-BC807F1F6CE0}
GIRVAN 11011330 | {D4FAC367-8042-431B-A943-BF91A853C064}
GIRVAN 11011330 | {614F599C-8E41-4F43-93F2-0A1EC10532ED}
GIRVAN 11011636 | {2A2FAB19-EBE2-405E-9DCE-8FB9750FB831}
GIRVAN 11011833 | {8182C01C-0B22-47C7-A0CA-AD46F7FCBC50}
GIRVAN 11011833 | {392954A0-1FCA-48CC-A483-1F0968A5C893}
GIRVAN 1101257982 | {FD332C17-8990-415F-9100-8E4ED8DC0A1B}
GIRVAN 1101323094 | {70CD880F-1DDD-4F51-9E9A-370D1CA1A5D7}
GIRVAN 1101409530 | {8B1F4C30-3A4A-4A19-A6E9-5A1F7F44786A}
GIRVAN 1101409530 | {6D726E65-891E-43C9-B0C9-0777CC383184}
GIRVAN 110158717 | {A49CA078-A874-4C7B-95C8-8F3D7ED53F4B}
GIRVAN 11019732 | {8DC45689-CC4E-44C9-B4B4-F24C95E2AACE}
GIRVAN 11019732 | {AC347828-D402-4D52-85C5-6B49A3874218}
GIRVAN 1101CB | {DEF16B60-E22C-4BAF-BEFC-F4B0E169B38F}
GIRVAN 11021028 | {F99AC090-1DE1-40AB-890A-9A8208858415}
GIRVAN 1102191484 | {00DCFA1A-E0DA-4005-AFAC-6434539F4E85}
GIRVAN 1102212096 | {2CF3750C-AFAA-443E-A704-CD883AA64DE4}
GIRVAN 1102259230 | {1E5A3AA1-D2B5-4DA2-AE6A-652FB4FE0C5F}
GIRVAN 1102296428 | {88D9B85D-5E99-45AD-AA48-D39463FC6691}
GIRVAN 110255307 | {F8758432-B450-4943-97B4-52B80EF2F512}
GIRVAN 110280726 | {1C2C814F-78D0-401D-8386-69906E2875F3}
GIRVAN 11029012 | {10010FC4-3D49-44D1-8CB1-63E2C5CA1480}
GIRVAN 11029012 | {C4B0D81C-BDA3-4802-9450-D7B1216C9E01}
GIRVAN 1102CB | {F8758432-B450-4943-97B4-52B80EF2F512}
GLENN 11012010 | {3AE2325E-14FF-4D74-9D21-7255C240DDD3}
GLENN 11012012 | {79FEFA25-425D-4CA0-8714-2AC25C0E088A}
GLENN 11012550 | {699BE619-289D-4B88-AD8A-7C66E5C0CF6D}
GLENN 110137496 | {AAF1B526-755B-4552-86BF-96B7CE58000B}
GLENN 1101546764 | {81373606-34C4-45AD-BE90-3590CFB8C731}
GOLDTREE 1105551904 | {FF54465D-5764-4C87-9FA1-2FCC27FF3FF8}
GOLDTREE 1105588830 | {B3D0E152-0C21-4325-9EB8-09118935535E}
GOLDTREE 1105632306 | {6EB5BD47-A615-45E4-B8B1-B07D2D5EF483}
GOLDTREE 1105912920 | {FA7F8989-D288-4745-ADF8-EA02885A949A}
GOLDTREE 1105CB | {2BB441D5-FA7B-41CB-B4C4-3BB6BA3702C5}
GOLDTREE 1107477878 | {E099D2A0-66BE-4A41-88A9-690DFD5F2504}
GOLDTREE 1107CB | {011DEA9E-857C-400B-8F07-19E7424464B0}
GOLDTREE 110814115 | {F40F9B94-B69D-4B7D-86DD-125E8D7AC87E}
GOLDTREE 110815803 | {F40F9B94-B69D-4B7D-86DD-125E8D7AC87E}
GOLDTREE 1108939400 | {D10D4B9A-C175-4B90-B83C-07AFB5BAC607}
GOLDTREE 1108961060 | {F40F9B94-B69D-4B7D-86DD-125E8D7AC87E}
GOLDTREE 1108CB | {0CEB70F5-2209-4B8B-BEA6-B7EBAFD3DEEB}
GONZALES 11013094 | {B8E5DB63-2FB3-475E-A16D-C9AC460D90A7}
GONZALES 1101522356 | {78C3B40B-2184-449B-93EA-4EF0BE4104D7}
GONZALES 110165704 | {71137ABD-E3E9-4FF8-AD99-B6537D8F36C1}
GONZALES 110422418 | {3395126A-CD63-43AB-8DA0-76D044FC7E78}
GONZALES 110436982 | {95B89747-12CB-4CCC-9467-B997231C80DC}
GONZALES 1104415382 | {1F605782-8F30-4773-8038-34124B7BD9C5}
GRAND ISLAND 222550300 | {7F31ADC9-2843-4A5D-9F43-09EF3B1407EA}
GRAND ISLAND 22255902 | {993AB089-FCD9-407E-9F45-DB23EF6E6936}
GRASS VALLEY 11012208 | {EB8D2AF5-D980-4706-8F4A-62633BB2CEC2}
GRASS VALLEY 11012766 | {9368A9FD-8241-4EF3-80EC-43B66D341976}
GRASS VALLEY 1101657600 | {DC0239AF-D0E3-47FA-B41B-85E9605567D4}
GRASS VALLEY 1101750804 | {B0F41A34-F762-41B4-ACDB-9C11F27E225A}
GRASS VALLEY 1101CB | {B0F41A34-F762-41B4-ACDB-9C11F27E225A}
GRASS VALLEY 1102CB | {343B25CA-8FEF-457F-8025-88904C29692A}
GRASS VALLEY 11031700 | {34D5CE89-BFD0-4BEE-AD2A-0183175AD2BA}
GRASS VALLEY 11032110 | {93265DD2-4F67-493B-AD73-86D77F859402}
GRASS VALLEY 11032180 | {5AF8F290-EBD8-4203-A9EE-DEB7B6BE68A5}
GRASS VALLEY 11035485 | {7A4E9B7F-62A7-4D18-BAD1-2417828B2DC1}
GRASS VALLEY 110358498 | {EB087661-42A5-46E0-BB53-1DC1A49FC6AA}
GRASS VALLEY 1103CB | {EB087661-42A5-46E0-BB53-1DC1A49FC6AA}
GRAYS FLAT 0401904916 | {BEA45A5F-2A03-4662-9526-7C035054C1EA}
GRAYS FLAT 0401904916 | {F832BEDC-DD34-4E26-9782-93FD35112F64}
GRAYS FLAT 0401CB | {0DD81C15-0750-470B-8405-5D786A5E8465}
GREEN VALLEY 210110976 | {5C8DA4CC-DB0C-4E65-BF7D-024442DE4F36}
GREEN VALLEY 210111054 | {D718FE21-E107-484D-ACA1-7018B98129C1}
GREEN VALLEY 210112106 | {C8470ABD-D047-4E6E-A601-35B08D6D1BD2}
GREEN VALLEY 210112824 | {4709726B-1243-485D-89BF-CB13962C950E}
GREEN VALLEY 2101128618 | {47221F99-4C03-4459-B587-C3379C27406E}
GREEN VALLEY 2101135762 | {E176FCE3-EE7E-480F-BF55-388C6C19C1B5}
GREEN VALLEY 2101280116 | {05A4D4CA-801B-45B0-A9F4-6F60FE9E82FC}
GREEN VALLEY 210136820 | {05A4D4CA-801B-45B0-A9F4-6F60FE9E82FC}
GREEN VALLEY 210136820 | {0EBE586C-72F8-4C18-81D3-2D4BBB15CB1F}
GREEN VALLEY 2101380922 | {167D6A57-A795-4EF1-A1DB-E61FA7A54614}
GREEN VALLEY 2101454176 | {E90E3E0E-A1FE-49A3-B997-86202410CB3E}
GREEN VALLEY 2101509068 | {CDC61CD0-0FE2-4F7D-9501-2D67363E1B49}
GREEN VALLEY 2101555304 | {87667CF6-C0F0-4F6A-8460-5651E3CAC230}
GREEN VALLEY 21016625 | {C8470ABD-D047-4E6E-A601-35B08D6D1BD2}
GREEN VALLEY 2101769666 | {831A8D2B-577C-4A3A-8319-F06B1A94B03D}
GREEN VALLEY 2101786342 | {E7EFAEA2-16B1-4A5E-84FC-DC3AB1229037}
GREEN VALLEY 2101804170 | {1F5D567D-A202-427F-8C61-0E0B820C1730}
GREEN VALLEY 210182789 | {5C8DA4CC-DB0C-4E65-BF7D-024442DE4F36}
GREEN VALLEY 210190860 | {67D84718-A6F9-4E7B-97A1-8A07F4A83E01}
GREEN VALLEY 210190860 | {6F3DC4C6-B30E-4E87-89BD-977051E850B3}
GREEN VALLEY 2101912058 | {ECE26D3C-7148-453B-A898-2CAA39BC84BD}
GREEN VALLEY 210310932 | {71F18CE4-D284-4752-9621-5F4A7D3D2F8E}
GREEN VALLEY 21034929 | {2B332782-EA5D-4EE3-A72C-A9F69405F6B4}
GREEN VALLEY 2103593534 | {2B332782-EA5D-4EE3-A72C-A9F69405F6B4}
GREEN VALLEY 21036661 | {2B332782-EA5D-4EE3-A72C-A9F69405F6B4}
GREEN VALLEY 21039959 | {71F18CE4-D284-4752-9621-5F4A7D3D2F8E}
GREENBRAE 110182270 | {FE2E59EB-BA50-4D05-88C6-174D3F07D4AE}
GREENBRAE 11021254 | {343DAC73-DC1A-4C06-8C35-1C7245E7BB91}
GREENBRAE 110276992 | {7EEEAC07-718A-4B83-B0BD-96715D60869F}
GREENBRAE 1102CB | {AEDCB032-1AC1-4F9E-A5A8-36B12E3777AB}
GREENBRAE 1103343788 | {F008DFF3-E06F-4A9D-BE65-7AFC32973FC7}
GREENBRAE 1103718674 | {B4FDB7D9-192B-4627-9F31-9C96B3E85045}
GREENBRAE 1104107508 | {3BE2CA95-ED55-4C1C-B1D4-36EDBF365BB4}
GREENBRAE 11041302 | {E5A2D1E2-28D2-4C3F-809F-5ACCA44182B0}
GREENBRAE 1104300 | {84506FE0-5799-4537-9C92-AE6186A1DEC5}
GREENBRAE 1104575264 | {E460C92A-0C1B-4EE6-9D61-6E0297E7830B}
GREENBRAE 1104575264 | {FFBD9787-435B-41F0-A6AF-2CCE742F5476}
GREENBRAE 1104575264 | {B5CE6369-EBB9-4BAA-833A-66C144C90673}
GUALALA 1111289822 | {D1DC583D-C5B9-40FB-8ECC-467BA390902E}
GUALALA 111135562 | {FD400AC6-30E3-4FB9-965E-48825707A861}
GUALALA 1111402866 | {DDD68DD3-36B2-4580-BE12-D96815D31D50}
GUALALA 1111445166 | {69ECBFC6-9041-42D6-B70D-8E6BF5F8976F}
GUALALA 1111887180 | {F1237B34-AE98-483F-8E45-6E7314FDEDD2}
GUALALA 1111CB | {73132ABD-89F1-46DF-ADF4-0148C2A7C9B0}
GUALALA 11121294 | {6177229C-DB60-448B-B309-D4C2F1A2330C}
GUALALA 111223444 | {CAD50E3B-E1AA-4BD0-B856-9F05498FC7E2}
GUALALA 1112662 | {4C471213-8F1E-4783-A9BD-8E19C8202DBB}
GUALALA 1112CB | {8A730939-42F5-47D3-8D16-1FB3EEA2BAEF}
GUSTINE 11023285 | {EE1852A3-1650-4422-B895-0757CB23F4F1}
GUSTINE 1102362106 | {3EED540B-07EB-4AD6-9E27-49D788CA9CBB}
GUSTINE 1102409 | {3EED540B-07EB-4AD6-9E27-49D788CA9CBB}
GUSTINE 1102562202 | {4FD8C4C2-DD8D-497B-82BE-7E64568CA7E2}
GUSTINE 110264140 | {643C42D4-351A-432E-B651-277EC983F63B}
GUSTINE 11026926 | {70573641-CA59-4111-9B6C-A1864C98CC90}
GUSTINE 11029628 | {4FD8C4C2-DD8D-497B-82BE-7E64568CA7E2}
GUSTINE 1102999258 | {F1E40206-E044-4108-BCD9-C9F139D1E7A1}
HAAS 210110954 | {9258B2D2-A536-49F7-80AA-889F46A8DA16}
HAAS 2101561932 | {60CC4C1A-8161-40D9-B812-120C86651584}
HAAS 2101619597 | {F7489B80-5947-4C80-9B81-5EDD7F0DFACF}
HAAS 210187448 | {9D7D6890-8AFD-486D-8D08-EEF8971C280D}
HAAS 2101CB | {60CC4C1A-8161-40D9-B812-120C86651584}
HAAS 2101R1115 | {E1B4DCB0-E286-4ADB-B86D-DD10569FD1A9}
HAAS 2101R2640 | {918E67A3-B8AA-4550-95DB-73823B8E223E}
HAAS 2101R2770 | {FE71AAF6-F6E9-485B-A3C2-10412CBC3ED0}
HAAS 2101R4610 | {E1B4DCB0-E286-4ADB-B86D-DD10569FD1A9}
HAAS 2101R9223 | {FE71AAF6-F6E9-485B-A3C2-10412CBC3ED0}
HALF MOON BAY 1101125326 | {DA4B3A2D-36B3-42B6-B1B8-A06A1F335036}
HALF MOON BAY 11011741 | {254FC169-523A-417F-9D6F-B3F1CAD65CD2}
HALF MOON BAY 11012500 | {75B0B322-68D2-4160-BC4E-E90092A2B4DE}
HALF MOON BAY 11013031 | {46C63E61-7164-433D-84D0-35EFA5B23A12}
HALF MOON BAY 110148868 | {0C9E66AB-FF7E-4958-AED9-234BEE09CC6F}
HALF MOON BAY 110155210 | {DE5B8172-09C9-4335-BCDD-078C358807B4}
HALF MOON BAY 11016369 | {DA4B3A2D-36B3-42B6-B1B8-A06A1F335036}
HALF MOON BAY 1101818874 | {94188B54-65D0-48E4-B281-167ED6270B8E}
HALF MOON BAY 1101821698 | {4C57C032-9144-4113-A71E-DB2019EE4077}
HALF MOON BAY 1101857728 | {9D907261-0F86-4269-BCD0-948CEEC70925}
HALF MOON BAY 11018717 | {166E048E-9CB3-4039-8BAA-4E7EE58765EC}
HALF MOON BAY 11018902 | {C41F4E5E-7BB3-4EF6-9D85-B639632114A4}
HALF MOON BAY 11018940 | {2DBAB1CF-D3D1-4CC0-A406-0CDA12AB2548}
HALF MOON BAY 1101CB | {D114DA17-C3D8-4F00-837D-4551FAA55B77}
HALF MOON BAY 1102130756 | {8313E180-25A3-4E60-816D-59E34E1E0DBA}
HALF MOON BAY 11022032 | {1AC2F406-7414-45B2-894D-D807C20227F2}
HALF MOON BAY 11022032 | {FDF56751-A970-4227-9016-A2C03CEBB385}
HALF MOON BAY 11022032 | {F77723F6-7C22-4793-8B39-BFC827E81CCF}
HALF MOON BAY 1102350336 | {61D17DF6-ADDA-4D95-BD25-C42B9D51757B}
HALF MOON BAY 110258448 | {51B7F99B-37F1-44D1-A380-3A17DA62C971}
HALF MOON BAY 110260703 | {ED314414-7113-4AFA-A85A-2B6A7CE0DA2F}
HALF MOON BAY 11026097 | {FDF56751-A970-4227-9016-A2C03CEBB385}
HALF MOON BAY 11026153 | {72FA64D8-3A63-4420-A7D7-130A2E3D886E}
HALF MOON BAY 110264293 | {AE99FE40-5E2F-4EF7-A496-F7D5D1016060}
HALF MOON BAY 1102665624 | {E6EDD644-68A4-422C-8253-6913368C1272}
HALF MOON BAY 1102863822 | {EC65686F-B15A-4CBF-8005-BF1274876E69}
HALF MOON BAY 1102873618 | {ED314414-7113-4AFA-A85A-2B6A7CE0DA2F}
HALF MOON BAY 11028848 | {27B471B2-23BC-4F18-A049-DC7B6CC4B62C}
HALF MOON BAY 11028910 | {72FA64D8-3A63-4420-A7D7-130A2E3D886E}
HALF MOON BAY 110297240 | {ED314414-7113-4AFA-A85A-2B6A7CE0DA2F}
HALF MOON BAY 1102CB | {EC65686F-B15A-4CBF-8005-BF1274876E69}
HALF MOON BAY 11031127 | {1E2199F6-B2B4-4E20-8C53-02777EC7D5CA}
HALF MOON BAY 1103151166 | {7D0CBA7D-32CD-495D-96B0-A01787155EFA}
HALF MOON BAY 1103157944 | {48BE9BF6-5A0B-4C2B-8D2C-E1E36B94D446}
HALF MOON BAY 110329454 | {6106A145-F67B-4637-A42F-8BCEA85E7B24}
HALF MOON BAY 1103341542 | {D82172A1-B65E-4492-A8B4-CC58BA0F7717}
HALF MOON BAY 1103371340 | {52E95492-39A9-44E9-8BAC-FF4C34E97C64}
HALF MOON BAY 1103389114 | {2F83CE4E-0855-4D8B-B1C5-D4FFD94A6F8F}
HALF MOON BAY 1103461558 | {5B63424F-7E68-45B3-A042-84BE563149F0}
HALF MOON BAY 1103531594 | {939B38BB-613F-4A01-A922-509D65700968}
HALF MOON BAY 11036012 | {3A40FD55-A6F4-42AD-BBB6-244D25E7BB11}
HALF MOON BAY 11036012 | {7A26C173-B69B-4907-B599-46F01DDAB9CB}
HALF MOON BAY 11036014 | {C9FA3CBF-AF0B-40A6-8062-0EE0474AC48A}
HALF MOON BAY 11036018 | {2DDD3645-3AB5-4B35-8936-1A369FDDE7B2}
HALF MOON BAY 11036115 | {EF0DFD14-A156-4283-AB15-1244C325A10F}
HALF MOON BAY 1103623460 | {1E711061-9006-460A-8EEE-DB532A4DAE2D}
HALF MOON BAY 1103655644 | {8768B1B0-4DEA-4BD5-97FA-A78DED5BFD8E}
HALF MOON BAY 110376762 | {07C4DB8D-20E6-4803-A265-29C92D756E21}
HALF MOON BAY 1103791345 | {4D15CCD2-0587-4058-87C9-D71A66F8A6C8}
HALF MOON BAY 1103825502 | {753853E4-C224-414D-99C3-DFD71085C7CD}
HALF MOON BAY 1103869420 | {0F2E5DF0-5D3B-4F1F-B661-7034226F3BDD}
HALF MOON BAY 1103869420 | {6197B9AB-5C29-4235-A535-D6D9B09BFF8F}
HALF MOON BAY 1103869962 | {0FAB28AC-2D6B-4CD3-818B-0321B62F4BC8}
HALF MOON BAY 1103880484 | {2C061CFF-5BC9-419E-A2B7-324612618450}
HALF MOON BAY 11038894 | {65F40270-9C1F-4F03-A2E4-A1FA52E4266C}
HALF MOON BAY 11038898 | {F439C87D-AAE9-43A5-B8D6-BA1AB4C5C362}
HALF MOON BAY 11038920 | {326D13C2-6BC0-4D12-9CFE-64D0722362EA}
HALF MOON BAY 11039112 | {F951C9B5-DFF6-4F18-959A-6543A104D243}
HALF MOON BAY 110398440 | {0D33DD6E-C54D-4E64-89FF-46D8E0E605B6}
HALF MOON BAY 1103CB | {32412CB3-3D8C-4A7B-A553-49E12B00D983}
HALF MOON BAY 1103CB | {D0EDFCD8-2A8A-490D-A06D-0BAFCCC6E362}
HALF MOON BAY 1103H80 | {196D5A62-8277-4556-8937-1330E86D299E}
HALSEY 1101173478 | {066EDC7A-E325-4DBB-8F78-931F06D965CE}
HALSEY 11012412 | {18E06DC6-50CC-4D11-B538-30C0948104D7}
HALSEY 11012414 | {C7CE8EEC-BFCB-464B-A0B6-4DE95EE01B52}
HALSEY 11015731 | {FA7F836A-C8A0-42D3-8E43-389B5B7AEC7D}
HALSEY 110176178 | {7B5F2382-5AE2-4C66-951C-F3B7A019CDB8}
HALSEY 1101CB | {FA7F836A-C8A0-42D3-8E43-389B5B7AEC7D}
HALSEY 1102164068 | {4B3281BE-5BD0-48E2-A99C-0ACCD9AE2A68}
HALSEY 1102164068 | {61D3CA53-774C-411C-906D-B5C7A38BEC7F}
HALSEY 11022514 | {D24FE68D-C3B0-43F0-8A16-C357F1C466D0}
HALSEY 1102281660 | {FF4361AE-2C9A-41F6-9A85-9A3B186A6735}
HALSEY 1102318786 | {1F953F3A-69CC-4716-9EFF-8FDAD16E8151}
HALSEY 110239104 | {033C2E2D-A850-40FA-9417-37D899E25ED1}
HALSEY 110239104 | {7C4BE6ED-C0E9-496A-8ACC-D5FA8F57DF1E}
HALSEY 1102514616 | {DAAF3E0E-FB0F-4550-AEFD-6EE835712C5E}
HALSEY 1102664826 | {73704D7B-529D-4BE7-B911-0F988D30BD14}
HALSEY 1102676064 | {BF3289E0-80A5-4D48-A3FA-50A7D697D692}
HALSEY 1102751626 | {53861E9B-B78F-4B30-887A-55D46A9C63B9}
HALSEY 1102CB | {6A27F32B-F27B-4275-9143-92BC3703857F}
HALSEY 1102CB | {0961801B-845E-4B14-847B-854C50E3739F}
HAMILTON BRANCH 1101161872 | {7FEFC5CA-2496-46DE-BE2F-DEB25BC01D17}
HAMILTON BRANCH 11012046 | {385C1178-1E10-4C92-A2B8-B11436713899}
HAMILTON BRANCH 11012082 | {C6BC6538-2EB6-4DA5-9982-6A2D9BE60DD8}
HAMILTON BRANCH 11012436 | {637602BE-E394-4D87-B06C-9852D4AA6AF2}
HAMILTON BRANCH 11013049 | {B799CE92-A5F5-41AF-A189-4F32E6DC30EA}
HAMILTON BRANCH 110137436 | {32D1F0F9-DFF9-4513-A71D-93DBB94A9BB3}
HAMILTON BRANCH 110137534 | {B799CE92-A5F5-41AF-A189-4F32E6DC30EA}
HAMILTON BRANCH 110153192 | {D03C18EE-E1AA-4630-B396-89DAD0F5DDA8}
HAMILTON BRANCH 110187784 | {512E7C3F-C5ED-477A-A43F-85AACCF18F8D}
HAMILTON BRANCH 110190334 | {6FA22C4C-B16C-4BDC-8F70-7E0F32F87C45}
HAMILTON BRANCH 1101CB | {CF1292FF-09D7-4946-B3C9-5DF5A5CB48C9}
HAMMONDS 11019760 | {EAC018D0-6E0A-45C6-BAE5-BAE564C53C44}
HAMMONDS 110212100 | {E77096BC-6489-4F18-8D81-F6DB0984470A}
HAMMONDS 110212140 | {B1A40F69-F286-4F94-B6BE-7EB45D286CFB}
HAMMONDS 11023660 | {1F600AD5-93C2-43B0-889C-61230526C553}
HAMMONDS 110248426 | {1F600AD5-93C2-43B0-889C-61230526C553}
HAMMONDS 1102CB | {FD894490-402E-4AE2-A8E0-2A3DAB4F2C46}
HARRIS 11082062 | {0E0C2894-9F4C-4F14-AF8A-F5A44822C594}
HARRIS 1108395498 | {956DFF7A-2597-4885-8155-9B37AFB45D53}
HARRIS 11084674 | {55AE43E4-ABFA-4493-997C-A8117F747A98}
HARRIS 11084674 | {1983F28A-08C9-48B3-9CC8-597EC6A45F0E}
HARRIS 11085984 | {DE2916D5-F71A-4A38-803A-B3D1074F4DF9}
HARRIS 110866386 | {DE2916D5-F71A-4A38-803A-B3D1074F4DF9}
HARRIS 11087920 | {DE2916D5-F71A-4A38-803A-B3D1074F4DF9}
HARRIS 1108CB | {9A3D8818-9236-4C74-9C67-0369FA031A48}
HARRIS 1109183860 | {62242811-5FAB-4F8A-8BA0-8F1F1D633349}
HARRIS 1109355914 | {C9FD0E2E-E3CC-4613-86C7-481937B54700}
HARRIS 11095982 | {67161A86-6B3F-4EFE-B24D-543C56BF8F10}
HARRIS 1109700 | {B45E3CF5-024E-4735-BFDA-B714A7EDABF9}
HARRIS 1109700 | {6EE208A5-6ADB-44F7-95B4-016C09D6A385}
HARRIS 1109700 | {E7CD4EFE-FF2D-48E6-A810-D2B9643B4C3B}
HARRIS 1109884406 | {67161A86-6B3F-4EFE-B24D-543C56BF8F10}
HARRIS 1109986852 | {F1189177-3583-4B19-9169-B2601AF75574}
HARRIS 1109CB | {0E899392-4139-4EF4-8C02-780C18A47141}
HARTLEY 11011306 | {192B845C-91EF-41A9-9296-85FDC116B057}
HARTLEY 1101336932 | {192B845C-91EF-41A9-9296-85FDC116B057}
HARTLEY 11014710 | {801F0074-FB1F-4C52-9EC5-EE9281D564FB}
HARTLEY 1101658 | {7945A267-A2BE-4156-9E2E-08F223E5F748}
HARTLEY 1101658 | {D05A5F97-BA6C-4210-AA67-0AC96ADACE28}
HARTLEY 110167994 | {6B82D15B-50B5-45EA-8E9A-6CD5F7744C9B}
HARTLEY 1101738 | {7E2F1938-FEBF-4ABD-86B8-56A7EC0C222F}
HARTLEY 1101743866 | {30847EAE-2F9E-48B2-B741-E673322EAB32}
HARTLEY 1101789752 | {E87F543B-5E70-436C-8779-DF6A7EC192CF}
HARTLEY 110186876 | {0628807D-B297-4343-8118-F7F853EA05DA}
HARTLEY 1101871312 | {385BA61F-2E87-46EF-B5EE-E4C4A5DF5993}
HARTLEY 110194178 | {33AF121E-F118-4B6E-94DA-FB39FA49A86E}
HARTLEY 1101CB | {9A7B1854-4374-4D14-BB43-EA4EAD6446AB}
HARTLEY 1102113786 | {DCE882BC-8AF0-4EA1-ADB4-CEF6A7B948D0}
HARTLEY 1102247988 | {F4698279-C7C5-4840-A723-E16454FDD382}
HARTLEY 1102471 | {F4698279-C7C5-4840-A723-E16454FDD382}
HARTLEY 1102490 | {81602399-62C7-41C1-B875-F30FCB0774B7}
HARTLEY 1102567112 | {28DD1A32-F79C-472E-A72B-8E1DF6A9103F}
HARTLEY 1102567112 | {37086401-82DB-4F87-AAA3-CE470B201E53}
HARTLEY 1102841676 | {5D95B927-2424-488D-993D-ADBE978C5596}
HARTLEY 1102920190 | {FC0E3435-0D30-4899-A816-A589A6F77862}
HARTLEY 1102CB | {60D33697-692D-4938-96CD-E53257AEC032}
HARTLEY 1102CB | {5D76312F-4A10-451F-BDB1-97A9738A5919}
HARTLEY 1102CB | {BCBF8B7C-F641-49B2-AD94-3642665272A4}
HATTON 110113620 | {58814FF4-3D4D-4426-B465-D072D208645D}
HATTON 11012026 | {593FA41B-396B-4601-BD50-0DE927CB7E5A}
HATTON 110137088 | {C7A22305-CC6A-494A-88D7-7F9AE8676071}
HATTON 1101390584 | {22114B39-E262-4424-8DC1-DD6129F35586}
HATTON 1101399900 | {4ACA70E2-9D9C-40F9-8434-15B06F65DC14}
HATTON 110175304 | {CCEDCCA3-66CA-4499-B03B-2E805BEC4C06}
HATTON 1101CB | {19B86573-307E-4C6E-966B-96848CB70151}
HATTON 11022010 | {07CA7935-70B1-4CBA-B069-3C5BAF9F4438}
HATTON 11022070 | {E55048C4-CAB1-4B6B-99F6-30BB24FEA325}
HATTON 11022863 | {4FA47257-6B21-44D9-9852-E96711EE4933}
HATTON 1102325334 | {F4AB201D-A2BA-4775-A770-AD118AC7F23F}
HATTON 110240461 | {E55048C4-CAB1-4B6B-99F6-30BB24FEA325}
HATTON 110240465 | {DF6AF33C-27E3-43A2-A515-B3B27F7B49FE}
HATTON 110256680 | {15F21C1B-A03A-4E01-B20D-69BB0B19F555}
HATTON 1102648928 | {96F3BFFE-8B25-45FE-9E94-B3CC1506798D}
HATTON 1102861148 | {96F3BFFE-8B25-45FE-9E94-B3CC1506798D}
HATTON 1102CB | {DF6AF33C-27E3-43A2-A515-B3B27F7B49FE}
HERDLYN 1102437882 | {CE97333C-59D7-4EFC-8B71-0C4A3CF5BCEE}
HERDLYN 1102575178 | {ECF7F2A1-3F18-47F2-8CB6-9D963120E1F7}
HERDLYN 1102608254 | {CE97333C-59D7-4EFC-8B71-0C4A3CF5BCEE}
HERDLYN 1102609338 | {20393823-B77E-489E-817E-F72A23CAEA43}
HERDLYN 110299602 | {BD7C976E-7CD9-4ACD-A152-480ECCDE08A2}
HERDLYN 1102B569R | {596BAA7C-1DF3-458D-AE18-2114550A313B}
HERDLYN 1102CB | {6D42CB7A-C91F-4DBB-9706-F92EF8B0963E}
HICKS 1116583284 | {EC9FDCBC-C8AE-4588-B594-E3F1FCB0DA2A}
HICKS 111660050 | {AA1A8D76-D2A1-485C-9B69-D74FAC1101F8}
HICKS 1116647210 | {9B3BCE26-3F49-48E0-A9CF-1FFE9B2444C4}
HICKS 1116983580 | {26706A0A-D462-4709-8596-704DD2D34F48}
HICKS 1116CB | {887C42B0-874F-48B4-B368-C0A3D7EE375F}
HICKS 1116LB16 | {128CFE15-7FAD-449A-AC53-530ECD1ABDFD}
HICKS 1116LB16 | {D3EAA91E-0FE8-4C2F-AB93-979EB58D8FBF}
HICKS 2101257172 | {D94AB3B4-8E80-4618-894E-44BDB2DEB838}
HICKS 2101510890 | {2F4D5289-645C-4DF6-914B-49620FF25C49}
HICKS 2101921246 | {99B01E49-D2D5-4303-BA1F-1BC5ACE34F47}
HICKS 2101921246 | {8131B32E-9BC1-4F60-BBA5-8037B52C5EDA}
HICKS 2101921246 | {56CCC6BA-5D72-4C21-B685-7DEDC2A0C078}
HICKS 2101984788 | {D85A7626-E5FB-4537-BBDF-FBAAC03D082F}
HICKS 2103388316 | {209E6975-3648-4AAF-8C3C-ADE0E831256A}
HICKS 210349892 | {3DDA3AB5-4F66-4059-9899-7D014ACBE2D3}
HICKS 2103CB | {15803579-91E0-430C-A2B9-39E1716A649F}
HICKS 2103CB | {F9C1F2D6-7B0F-4CCE-9FBD-177508C9BBDA}
HICKS 2103LB50 | {7B884E42-31C4-4241-9616-799B5779F088}
HICKS 2103XR068 | {209E6975-3648-4AAF-8C3C-ADE0E831256A}
HICKS 2103XR248 | {F3C9E330-5EFE-42AE-9971-7797E81AA91A}
HICKS 2103XR262 | {209E6975-3648-4AAF-8C3C-ADE0E831256A}
HICKS 2105335978 | {D1EE16C9-A212-4A3A-9802-AAFF3A3F7044}
HICKS 2105358646 | {528A55F2-C027-4F85-89DF-6B0B8E9354F3}
HICKS 2105871316 | {C0376D9F-B470-4AB5-B207-928FB9998965}
HICKS 2105871316 | {0191284E-DF0A-436B-8611-FC3F6E5CA06E}
HICKS 2105954008 | {92BFD30A-85CC-4C25-9211-D070128FCA09}
HICKS 2105XR160 | {298C410B-3152-45EB-85DF-C4CBACBBA609}
HICKS 2111255740 | {EB7674B7-CCD0-4EFE-8467-AE9A3DE4BA98}
HICKS 2111XR210 | {CF04DCF7-F474-48E8-8533-36C336A15BD2}
HIGGINS 1103173744 | {F949235C-0860-461C-89D7-E9510F38987E}
HIGGINS 11032194 | {04FFA86D-12A8-4DCB-A786-7ABADD4FCF1A}
HIGGINS 110332120 | {EA74D320-F3F3-49EB-8286-8BD66424051C}
HIGGINS 110332120 | {42C0044E-B495-4983-9439-0351AC9E28F8}
HIGGINS 110350072 | {A589AF7C-C6C7-433C-A767-6726105D4137}
HIGGINS 110350072 | {740DE1B6-71C4-4F89-BFF6-C379E023E99F}
HIGGINS 110350072 | {440E1FF9-EC84-4B7F-8A63-9D277C0E9009}
HIGGINS 1103789714 | {D2804A73-7030-4736-9366-42176C492BFE}
HIGGINS 1103789714 | {5963F19C-E1BE-46EC-9E26-B117A913E935}
HIGGINS 1103789714 | {9B71CE7D-C37C-441F-B4CC-20AA6EF90BF7}
HIGGINS 11039753 | {5963F19C-E1BE-46EC-9E26-B117A913E935}
HIGGINS 1103995672 | {FCC40ADF-1FB7-4F80-97A9-6981FCDC8244}
HIGGINS 1103CB | {5963F19C-E1BE-46EC-9E26-B117A913E935}
HIGGINS 11041006 | {6831EC63-2DE1-4FA9-8E52-ECEB96F95CDF}
HIGGINS 11041374 | {5975A3D8-5B89-4D93-9C6D-113094290849}
HIGGINS 1104324510 | {6981E7DA-E492-47ED-85CD-F3F05BFEC3D0}
HIGGINS 1104324510 | {846DFCBB-4318-4489-A66E-A9F9ECE03BC7}
HIGGINS 1104324510 | {477268D6-DE4E-4795-ABA6-DB4CC4C4808D}
HIGGINS 11044281 | {46E9257A-F9DC-47D6-A72D-7B5FD7E2E022}
HIGGINS 11044281 | {B364E247-4FDE-41FA-876B-BFAA01BA31A1}
HIGGINS 1104498932 | {D5E00AD4-7C48-4E87-BBB1-92F5DE277EEA}
HIGGINS 1104533648 | {7316CABA-ACE0-4406-9BB2-A4017DAD0078}
HIGGINS 1104663774 | {7D76AB7E-DE4B-4DD3-A70E-E5CB10ACED2C}
HIGGINS 1104663774 | {7245CB07-72DE-4F00-AD7D-A9427C8FD37E}
HIGGINS 1104842642 | {77DD24A4-3555-45C1-AFB0-D6E3B0D6C267}
HIGGINS 1104CB | {46E9257A-F9DC-47D6-A72D-7B5FD7E2E022}
HIGGINS 11071070 | {735D1686-195C-449F-AFF7-F3F9879F6190}
HIGGINS 1107746082 | {8C53EC31-B3AB-4E33-B852-46094C79DBC8}
HIGGINS 11077559 | {735D1686-195C-449F-AFF7-F3F9879F6190}
HIGGINS 1107836688 | {B73B7429-00D8-4172-979B-F99C3A58EB55}
HIGGINS 1107CB | {AD1702BF-568D-4020-87DE-29F495495BCD}
HIGGINS 1108CB | {F3F43510-36DF-4FCC-ACB0-6058CB728BA2}
HIGGINS 1109141926 | {6BDB81EA-22D0-4D27-A365-643EA7B4092A}
HIGGINS 110950078 | {13205944-27DE-4E69-8D25-637FC945A119}
HIGGINS 110950078 | {C38DE713-3C58-42AE-B69F-E7385AE627A3}
HIGGINS 1109594 | {824F13D7-3113-4AA8-8BC2-89229A42D634}
HIGGINS 1109CB | {97806AE4-5D72-4FCC-8179-00CDE6E08736}
HIGGINS 1110166282 | {4A27E620-E258-4456-93D8-34809DB86E0F}
HIGGINS 1110166282 | {F3D6F46D-CE49-42B8-ABD9-DE4AEFF8E29E}
HIGGINS 1110197930 | {C6E8B2FD-D557-459C-B9FB-FFB281472FF9}
HIGGINS 11102408 | {71CA17E4-B079-4EB2-8611-562BAD82EEBD}
HIGGINS 1110429714 | {16907887-BEAA-4809-9B51-E8181F14104E}
HIGGINS 111051794 | {B86F1700-5A54-45AD-BE5A-60237D0F62CD}
HIGGINS 1110861610 | {C6E8B2FD-D557-459C-B9FB-FFB281472FF9}
HIGGINS 1110CB | {E56A3B9A-F6B2-438C-8FDC-DFADF12A0423}
HIGHLANDS 1101CB | {F7C77AB2-FB1A-424C-8DCB-D1ED89130316}
HIGHLANDS 11021304 | {DF76C57E-BBD1-4728-AA99-EBD33D60311E}
HIGHLANDS 1102230414 | {CD78E93A-B7DA-4A5F-A8CF-16853C69CA49}
HIGHLANDS 1102380156 | {153652DA-6F87-4EA1-8DA9-C4E69FC6FA7E}
HIGHLANDS 1102556 | {36BC008E-75DD-4032-9E44-5DB50949C39A}
HIGHLANDS 1102604702 | {4DCB4FA9-9915-461D-BB5B-612AECE3A33E}
HIGHLANDS 1102623120 | {B5C2A169-B3BF-48D4-8260-06DB123C1FCF}
HIGHLANDS 1102628 | {805F8CD4-618B-4641-8C2C-AEC1BF35DB49}
HIGHLANDS 110265650 | {D6E00327-F4CB-4F20-A907-68904C3BB997}
HIGHLANDS 110275140 | {D71C2E21-7CE4-4721-8677-0076FC6B52D7}
HIGHLANDS 1102898234 | {03AD0230-A3CB-4BB7-9D5D-A2E310402DA6}
HIGHLANDS 1102914918 | {8F7C94EC-9C6E-4FA3-83B6-0BEF18BA51B7}
HIGHLANDS 1102CB | {12D5CC7A-B2CA-4EEF-8AD4-C988E70110AA}
HIGHLANDS 11031282 | {4C4C4306-8F4C-4E14-9AEC-9513BE40A725}
HIGHLANDS 1103287766 | {AD7457DE-7857-4646-BC27-24CDE616604D}
HIGHLANDS 11034630 | {C0802380-5040-4C58-8433-9FF2FB3282BB}
HIGHLANDS 1103520 | {688940C3-4CF1-424F-B5E8-4B865274A639}
HIGHLANDS 1103520 | {20B5CFDD-9238-415D-BF03-7EE0B92100FE}
HIGHLANDS 1103520 | {BC12AAA6-2712-4A65-9684-87AB8F61CB75}
HIGHLANDS 1103568 | {DE7AF2D5-E911-47A4-AE78-DD80A28A5D4B}
HIGHLANDS 1103665096 | {7A8FDD2A-0C0A-4E57-AF74-45A4DEE663B7}
HIGHLANDS 1103726580 | {D271DF75-70E3-4A5D-9E2E-6D2BE449ADB2}
HIGHLANDS 1103828 | {F617C2F6-F9CA-4233-ADD2-A5EEE40355DB}
HIGHLANDS 1103917328 | {E2763744-304B-4C72-A146-E33A686F8B6A}
HIGHLANDS 1103973816 | {45E82633-486E-4610-936E-63E014462202}
HIGHLANDS 1103CB | {F4CEECFF-9688-4F5E-82B6-98F3F42878F8}
HIGHLANDS 1104105492 | {EC0CBAAC-D25D-4166-8326-CC1A005227F9}
HIGHLANDS 110439458 | {F73918F2-BDFA-403D-8839-D569F0C45575}
HIGHLANDS 110448262 | {05A2F271-E60C-4560-A544-2497E351C8FC}
HIGHLANDS 110476156 | {CEFF2CE3-E3F4-40F0-B7FB-D65976C4211A}
HIGHLANDS 110484640 | {E2438D63-9836-48BB-91BE-1736CBE6A21A}
HIGHLANDS 110486807 | {4153AD52-F0C3-4F94-B9A7-DBFADEA8B1B3}
HIGHLANDS 110487040 | {4153AD52-F0C3-4F94-B9A7-DBFADEA8B1B3}
HIGHLANDS 1104CB | {EC0CBAAC-D25D-4166-8326-CC1A005227F9}
HIGHWAY 1101200662 | {27D0C7EA-6E05-4947-A47E-355769B9A693}
HIGHWAY 1101738 | {27D0C7EA-6E05-4947-A47E-355769B9A693}
HIGHWAY 110181590 | {BC203773-EE00-4E3E-824E-9D091E2E0CB5}
HIGHWAY 1101992028 | {DC7BC1C1-95EE-4449-8138-4863676D68A6}
HIGHWAY 1101CB | {5C6F4134-089B-4151-9D4E-9160DBB180EF}
HIGHWAY 1102557500 | {D57ED439-6B6C-4133-8A9C-8645CBF54545}
HIGHWAY 1102684 | {02952461-D1F2-4EBC-9D49-EA26E70B4F35}
HIGHWAY 1102700 | {17274A38-F8A1-462F-93E6-49EE52FB630E}
HIGHWAY 1102815524 | {F81C8D2E-E3F7-43E9-84C0-41DBA5E7E83C}
HIGHWAY 1102976548 | {95E0520A-F418-4CA8-8CC2-AD10DFE164EF}
HILLSDALE 0401289582 | {3BC63369-8BB7-498F-AC59-3790414C1555}
HILLSDALE 040198526 | {E5751866-C01F-4B6F-A700-E0FAA4499012}
HILLSDALE 0401CB | {3840BE80-21EA-4670-95C2-6EA58C09B292}
HILLSDALE 040277056 | {6CAF4EA6-4ABD-4B11-B8DA-EB2F88BE9114}
HILLSDALE 040485812 | {2DBE6767-7D56-4562-8F78-31E59118A4C4}
HOLLISTER 21014790 | {D7821196-5543-4445-A515-B4C8A86079AA}
HOLLISTER 21014792 | {6C3CFC54-A1A4-4370-AEA1-A2570E0F37DE}
HOLLISTER 21014900 | {D7821196-5543-4445-A515-B4C8A86079AA}
HOLLISTER 210157338 | {F481797F-2ED3-4F63-A731-3075679522E4}
HOLLISTER 210193404 | {F481797F-2ED3-4F63-A731-3075679522E4}
HOLLISTER 2101CB | {D7821196-5543-4445-A515-B4C8A86079AA}
HOLLISTER 2102113634 | {AA026DE2-36FF-41BE-B277-D062A4C54501}
HOLLISTER 210228421 | {17B07670-0E53-4796-89E8-790E1D545BFE}
HOLLISTER 2102406496 | {17B07670-0E53-4796-89E8-790E1D545BFE}
HOLLISTER 21024780 | {97FCD4F4-D4FA-4E54-B458-40505BE0F481}
HOLLISTER 21024908 | {17B07670-0E53-4796-89E8-790E1D545BFE}
HOLLISTER 2102676164 | {5ED88047-4B28-4CB1-8810-2C6A7B9E00CC}
HOLLISTER 2102855412 | {1326B156-0483-47A9-A035-C6F98F761263}
HOLLISTER 2102CB | {D8069B78-C4A1-4306-A859-EF54203AE5F4}
HOLLISTER 21034402 | {916074BF-1AF6-4F02-B56E-6708946CCF82}
HOLLISTER 21034816 | {0E5DE6B0-AE33-4EDB-9E4C-46429863EB91}
HOLLISTER 21044068 | {B4FE7570-1750-4673-B760-557A7D4F2C8D}
HOLLISTER 21044403 | {AF413565-FF03-463B-9FE8-0D946F06F8F5}
HOLLISTER 21044403 | {B4FE7570-1750-4673-B760-557A7D4F2C8D}
HOLLISTER 21044782 | {805C263F-A13B-498A-9D36-2B2F08EE880F}
HOLLISTER 210515486 | {9100FDE9-374E-4C6E-9760-42D4E1E79D9F}
HOLLISTER 210515486 | {F8BCB5A6-2E9C-4401-A1EE-79CB63889B64}
HOLLISTER 210515486 | {43B0E73A-864C-4D96-BE63-3BEA4CDB46E9}
HOLLISTER 2105252148 | {602044DE-77ED-4EE0-B828-01EB8C884EF1}
HOLLISTER 2105282984 | {AD2AC90F-A368-4781-BC02-4868F07C9459}
HOLLISTER 2105282984 | {664261AE-C470-402F-BA0C-C7BED0E02F5A}
HOLLISTER 21054018 | {201D4860-5BDE-4AE7-B543-F824A85004DC}
HOLLISTER 21054042 | {1E6DC745-CC49-441C-9C9B-BCE1C0BE079C}
HOLLISTER 21054048 | {522758DC-D04C-45F3-86B0-6920B5847932}
HOLLISTER 210542224 | {102DDCC7-B669-4F67-96A4-A65E2BB45451}
HOLLISTER 21054709 | {9E37DA10-12A5-4B12-8DFE-57A391C0F5D4}
HOLLISTER 2105475946 | {36C68467-DD29-4098-9B8B-C4FA03ACDAB2}
HOLLISTER 2105480430 | {2A202711-DF81-4789-BFD4-DC7744D8ADFB}
HOLLISTER 2105620484 | {DA9432DC-5504-4AA9-BB89-C89143FA984F}
HOLLISTER 2105903238 | {0363382A-DCEC-4F0E-A9CA-F2D9B0CACBC3}
HOLLISTER 2105CB | {ED3912F5-3969-4789-A9D3-65A01A62E3A0}
HOLLISTER 2106281712 | {13BCDD68-D485-4507-BB4D-A6F297EC4EEC}
HOLLISTER 21064004 | {95C4B2EA-7339-48DF-9F61-FADDFD6FCDFA}
HOLLISTER 21064353 | {D60BE767-0736-4028-AFDB-AFDC83455E0D}
HOLLISTER 210683518 | {B3B33B44-B27E-4997-ADCB-104657A7A68D}
HOLLISTER 21074046 | {38133BFE-606B-4796-A7F0-653C5DE724A7}
HOLLISTER 210741808 | {3A7DE5A9-6F9C-4704-A7B4-637F15326CD9}
HOLLISTER 210791424 | {951B1516-4326-49B7-849D-E72573882819}
HOLLYWOOD 0401413432 | {492D154A-EE0E-4F92-B9B9-FEA1E967CA18}
HOLLYWOOD 0401811742 | {492D154A-EE0E-4F92-B9B9-FEA1E967CA18}
HOLLYWOOD 0401CB | {854414CD-0C09-471D-91AA-83170F69D473}
HONCUT 110137322 | {4580F407-B405-4F86-9F13-8318C1F1927B}
HONCUT 1101424030 | {1D757349-9BDB-43CC-B466-464A2C0E38B4}
HONCUT 11015581 | {4580F407-B405-4F86-9F13-8318C1F1927B}
HONCUT 1102301886 | {4E6B8B0B-875E-4AF2-B828-28889B8DD82C}
HONCUT 1102478754 | {B9E11B31-9989-4FA2-87A7-5FB52DF0CB03}
HONCUT 110255206 | {95CFDCE9-A6F6-4428-B8F8-A23AC65977EB}
HONCUT 110255206 | {5DFE5E0D-D07D-4654-A64F-B160393DFE04}
HONCUT 11026130 | {3DAB252C-5A42-4BD0-ADD0-23CE62160133}
HONCUT 110275350 | {3ECFF3DB-033A-4FC4-B37B-A365EAF3EE98}
HONCUT 1102976552 | {3DAB252C-5A42-4BD0-ADD0-23CE62160133}
HOOPA 1101132534 | {AF024401-1A80-41A9-87F7-1E2592E63FAD}
HOOPA 11013174 | {340CBFFC-8113-455B-B1D8-1918397994A0}
HOOPA 11013290 | {FBCD7012-56B0-4DB8-BFD1-768DDA012D1B}
HOOPA 11013304 | {72D61001-3395-45AD-8AA5-496E28074CB7}
HOOPA 110137202 | {E07D7DDC-2962-416D-9482-05DD47B79DBD}
HOOPA 1101405280 | {4A886E07-73B5-4AA1-9DE8-067CBFCADF10}
HOOPA 1101561116 | {340CBFFC-8113-455B-B1D8-1918397994A0}
HOOPA 110182542 | {AF113D3A-C32B-4AE6-9683-F0B931A2BCC2}
HOOPA 110193038 | {1C7B29C1-9766-4E63-AFC2-ED97D59270C9}
HOOPA 1101CB | {4A886E07-73B5-4AA1-9DE8-067CBFCADF10}
HOPLAND 11011100 | {49DD2761-248F-4D1E-809D-C19E1A64F359}
HOPLAND 1101154790 | {90407EF8-546C-4CC0-BAC4-A3C598D39737}
HOPLAND 11014335 | {21C06326-13EA-46A1-B352-B0F4123079A7}
HOPLAND 11014626 | {03A33F3F-5506-459A-89E7-ACD76DFFDD38}
HOPLAND 1101558 | {7D091198-DCC2-4EA1-AD83-C691E4F808C9}
HOPLAND 1101563064 | {C57CEDE5-1C9E-44E9-91E6-A83B645B0397}
HOPLAND 1101569 | {75F306C3-C54A-48C1-A746-D384EB137E6F}
HOPLAND 1101768 | {CF814E69-077B-44BB-9617-D51226ABE508}
HOPLAND 110180620 | {CEE02838-136E-45AF-B305-63BB762F2ACE}
HOPLAND 1101863408 | {ED56A653-8202-4DE7-BE98-622E59D2D269}
HOPLAND 1101865263 | {876D2A2A-E47B-4C89-903B-5E516A574F17}
HOPLAND 110194006 | {CBE8AED3-8B0C-40C3-8EB4-C54D27FFB79C}
HOPLAND 110194006 | {B460936E-76B4-4A8F-BEA6-F09DF80F2A09}
HOPLAND 110194006 | {8550FAE9-8660-4D0D-A46A-9FC5A8080BAF}
HOPLAND 1101960 | {19C74293-6BCE-4CD7-A01D-D20EFF685BEF}
HOPLAND 1101960 | {954A31A9-A213-4FDE-A099-4FA0383FC419}
HOPLAND 1101CB | {7E6065FF-2C07-4696-A18E-5408BD7025E6}
HORSESHOE 11011682 | {462E2D82-20B9-4FAD-BC05-75852F2ACF8E}
HORSESHOE 11011682 | {D177ED3D-75C8-494D-9D73-9349634329F7}
HORSESHOE 11012714 | {3E108A7D-3BD7-484D-A219-8780A55EB7A1}
HORSESHOE 1101416226 | {DDC5A35F-31F2-4622-90DD-F12D8635E350}
HORSESHOE 110150140 | {1A345E57-984B-4DBE-9F57-D104048E74E3}
HORSESHOE 110151538 | {87800A96-4222-40F6-B470-AA1E26FEFB33}
HORSESHOE 1101603250 | {6501F20E-BB6C-44CD-B10D-FA9DBEF23636}
HORSESHOE 1101CB | {88F5CEC0-E8A5-4F1C-9B7B-06545C0D954B}
HORSESHOE 110450142 | {0A3A9B56-1444-4B9A-A0ED-585B0FF1E065}
HORSESHOE 110451536 | {DCF001D4-BEE1-4DF1-BC31-9FDF6ADCEBFC}
HORSESHOE 1104CB | {3D4378F9-B822-4985-B4DC-F977157ECBFD}
HORSESHOE 11061680 | {EB648214-1376-4BEE-87F1-27A3F749B150}
HORSESHOE 11061826 | {21A22DCC-8BF8-4604-BB71-E2A99E9CF885}
HORSESHOE 1106CB | {E78C9DEE-4564-4CED-86F6-578EC71D6FE0}
HUMBOLDT BAY 1101898396 | {7054CD6B-2908-413E-912B-FCB7EE17D046}
HUMBOLDT BAY 1101CB | {91BBB89B-9333-4A31-8E04-1784413A7D4C}
HUMBOLDT BAY 1102104220 | {D2680CF4-7C25-4923-8D7B-E8DC63F621E2}
HUMBOLDT BAY 110242066 | {03AAB6DB-68E9-4678-A926-CDBF06B5410E}
HUMBOLDT BAY 11024714 | {920EB720-2DB1-489A-AA84-2DA6FD1B08BB}
HUMBOLDT BAY 11024724 | {1C14A68A-E3B6-447C-B029-17568666CAF3}
HUMBOLDT BAY 1102741980 | {3D0CD5B3-E4C3-4E4C-848A-D16C0F741C16}
HUMBOLDT BAY 11027598 | {50FDFAC9-1C29-47B2-BBE8-2C25E0E08184}
HUMBOLDT BAY 11027600 | {3BAC5763-AB5B-41F4-8A28-C43F790EEEC3}
HUMBOLDT BAY 1102CB | {712389D7-97A8-43EF-99E1-6A4B64E5B114}
IGNACIO 11011264 | {66D924F6-9A86-459E-8865-D09BDB15DD16}
IGNACIO 11011300 | {64639A8A-2672-4BE4-8EBB-2985CB356A36}
IGNACIO 11011779 | {64639A8A-2672-4BE4-8EBB-2985CB356A36}
IGNACIO 1101CB | {A57172F7-A24B-4226-8C15-DA9E4C31AFEB}
IGNACIO 11031068 | {F489C694-D583-42AD-BB91-0D15DCF9AC70}
IGNACIO 1103151462 | {FEBA400A-D767-411C-A57E-B8DCD119B2AF}
IGNACIO 1103CB | {09D14343-CC3E-46D9-99DC-4193E90EB264}
IGNACIO 1103CB | {2E2A9BE3-6328-45AB-919A-7693139C27D5}
IGNACIO 11041274 | {4117016E-C4E1-43D1-8702-FC75C137797F}
IGNACIO 11041290 | {EEF03FEE-E315-4DF5-BC12-E5292370248B}
IGNACIO 1104209870 | {77BF2D95-045E-4F12-8F58-C001B50CA1B0}
IGNACIO 1104450582 | {F91156C0-E294-4BD1-9245-277084BD5819}
IGNACIO 1104469764 | {B15C4D34-840D-4CC7-96CF-D3ABBE50E477}
IGNACIO 1104798890 | {4117016E-C4E1-43D1-8702-FC75C137797F}
IGNACIO 1104CB | {4117016E-C4E1-43D1-8702-FC75C137797F}
IGNACIO 11051943 | {E636DD2B-323A-4E65-AE99-16FA1288A9E0}
IGNACIO 1105318 | {25FEAA66-B3E3-4A2E-9CFA-07C2BE62DF67}
IGNACIO 1105490728 | {ACF50790-A77B-4E22-9362-2A36912CA1D3}
IGNACIO 1105683542 | {BB37B807-9B57-4D41-8EE3-98B7B9A98DE4}
IGNACIO 1105775176 | {E636DD2B-323A-4E65-AE99-16FA1288A9E0}
IGNACIO 1105784032 | {087FC024-1431-4D83-A955-1FB7C9160A67}
IGNACIO 110584764 | {4C2B4F6D-8805-4D54-AEC8-8F73248C6F67}
IGNACIO 110584764 | {E1F2559F-5071-40B5-BFDE-D70EABF698BC}
IGNACIO 1105908 | {1C105F4C-AE80-4099-9437-85CB973612DF}
IGNACIO 1105CB | {71399AD4-B98F-4687-A48B-364B35890C76}
INDIAN FLAT 11044580 | {62B3D471-5018-455D-85A5-F307E381688B}
INDIAN FLAT 11045456 | {85C573CB-6CAC-4BD3-9BAE-88F4FB8F62BB}
INDIAN FLAT 11045456 | {62B3D471-5018-455D-85A5-F307E381688B}
INDIAN FLAT 1104CB | {8FE2B2A5-53AD-4D02-8B28-25A33ED98DCB}
IONE 110113446 | {E7CD9906-89BD-49E9-822A-3B11AFC2B697}
IONE 1101510200 | {9C6D587D-CB16-40C3-BD97-BB988A8AB8BE}
IONE 1101863028 | {4C923680-C4B8-4FBF-9D46-305B949489AF}
IONE 1101CB | {9D5BFE02-DE54-49D0-8A6C-80BCABF7CBD7}
IONE 1101L3141 | {9C6D587D-CB16-40C3-BD97-BB988A8AB8BE}
JAMESON 1102561410 | {AEC0BEC4-452C-4105-B25C-923DF5C8A25E}
JAMESON 110265516 | {10AF2AF5-0312-4499-B6B7-F90BCDC56FEE}
JAMESON 1102865502 | {A17489AD-F8E6-4EDF-87DF-CA9C33FE9292}
JAMESON 11028842 | {51E773B6-592B-4825-9048-C7012AD18EE4}
JAMESON 11028842 | {A9A36598-2BF7-4270-99BF-EC9B9E23BB29}
JAMESON 1102CB | {CCF6C8D4-166E-445A-ACEB-16D79D2A6A88}
JAMESON 1103118944 | {8F24D563-8C81-416A-9085-5DC65E76E490}
JAMESON 1103118944 | {A2248A11-F35A-465F-8815-05FAE8AEC21C}
JAMESON 1103CB | {D66EDA38-27E9-4939-96F7-B9EFA1F3B789}
JAMESON 1104CB | {7FE056FF-7DC5-414C-994D-F58E2CAB0126}
JAMESON 110513392 | {04B6879A-FA5E-4BF4-8489-BF804FD852E1}
JAMESON 1105371694 | {CBED1D90-C1D1-43D3-861C-32471E7EFC40}
JAMESON 1105373614 | {2E285110-3BA0-4791-A5AB-C2AB3B1D84C2}
JAMESON 1105407 | {17545FD3-8E57-40AD-837B-92A323A936A8}
JAMESON 1105466348 | {8E99B7C2-09C6-4CCD-84A3-45313788DF3F}
JAMESON 11057652 | {15E7F33B-BC99-41F7-80A1-54BDC820E172}
JAMESON 11057792 | {92D5B5C0-358A-4EED-B7CE-B86787B1BE6A}
JAMESON 1105913400 | {E925FB90-0D67-4350-9303-9E202A799552}
JAMESON 11059472 | {4372CAAD-3581-4B8A-AB27-A49D177EEFCE}
JAMESON 1105CB | {41D42D82-88D5-42DA-AE8F-BA1A622569DC}
JANES CREEK 11011184 | {82D90921-E507-4935-9634-C0CEB766B38E}
JANES CREEK 110141990 | {B4EC8E85-89E6-4E1E-A58C-F910365EBD5D}
JANES CREEK 1102CB | {00625706-EEB8-45CB-9368-35DB90D22760}
JANES CREEK 11044844 | {26E770F4-F25D-4CF1-B69E-D7AF03209DEC}
JANES CREEK 1104CB | {74133F88-7C2E-41BF-994B-5D7BF579CEB8}
JARVIS 1101467034 | {B8EF4BC2-5E2B-4B38-A6C3-052DAA5C473E}
JARVIS 1101467034 | {C606228A-087B-437D-9A9F-1FD57375B95A}
JARVIS 1108289662 | {D0FD43E9-668D-474E-A42F-940591FD44BD}
JARVIS 1108548648 | {10748EFF-FE9C-43CD-9F57-5F8087C8BB9A}
JARVIS 1108767280 | {518B32E2-92EA-4E90-A3AC-D00B405E1539}
JARVIS 1108CB | {6E2BBEB0-5FF2-432A-87B6-19D6CB26C1C6}
JARVIS 1108MR366 | {4D5666F5-BD84-4CAA-B8A5-49AFE5BCCE43}
JARVIS 1108MR367 | {10748EFF-FE9C-43CD-9F57-5F8087C8BB9A}
JARVIS 1110CB | {40044BC8-4D64-4043-A6C7-1EB84CD3813F}
JARVIS 1110CB | {F27BF583-4544-41F4-91D5-3B4970C09DAF}
JARVIS 1111907698 | {756FEBB5-79F7-43A0-8D9C-AD33FFCC0DB1}
JARVIS 1111MR121 | {F5BF7E7D-4C96-4918-ABEF-C33B63B5DD64}
JARVIS 1111MR122 | {1A5CD57B-504B-4150-A099-4F8257FEDA9C}
JESSUP 11011496 | {1439A4E2-919C-4E4E-A8DD-EE8CB9F7F49B}
JESSUP 1101271314 | {B509E65A-277F-4CB2-9C36-94971C8A46D9}
JESSUP 11012839 | {4BBBA9F5-2A5C-430F-82E9-5C32AA8B7737}
JESSUP 11012849 | {1374C19D-A03E-47DA-B38C-FFBB12EFAA07}
JESSUP 11013383 | {4BBBA9F5-2A5C-430F-82E9-5C32AA8B7737}
JESSUP 110141356 | {7C8CD245-F5C5-41C8-8C39-1CC5C953323C}
JESSUP 1101509264 | {67C34A8D-7125-41A3-A0F1-303BFAA70FAB}
JESSUP 110168362 | {4BBBA9F5-2A5C-430F-82E9-5C32AA8B7737}
JESSUP 11019002 | {94370961-147A-42F3-9849-8A0C21F665DA}
JESSUP 110194468 | {D2D6973F-363A-4DAC-B85F-5E6E9B82592B}
JESSUP 1101CB | {A7720DBE-D298-421E-A3B2-FE12C335EE16}
JESSUP 1101CB | {D9430ABC-DFEB-4916-9501-6BC60BFCFBE2}
JESSUP 110210249 | {6DCE5A79-1764-4080-929F-D9BB93EF31EB}
JESSUP 11021314 | {05CEA4F2-3636-4573-A883-9C548FA0A079}
JESSUP 1102146332 | {A3024FBF-2C6F-48C5-9176-20EAC4E5CE78}
JESSUP 110238330 | {05EBFD7E-35A6-4E40-95CF-51485C56D3C6}
JESSUP 110262802 | {181F6F09-3B43-482A-8A25-A4536CBB7022}
JESSUP 110269928 | {7CA3CBB2-5BD4-44E1-9364-BA8EE2FC0FBD}
JESSUP 110296554 | {14C3CF81-5A6E-4ADC-BDB6-EF5B849D6F19}
JESSUP 1102CB | {232A469F-DE89-4EE3-AC4B-F74419E6464C}
JESSUP 1102CB | {4CDBF804-D80B-4D93-A031-15FAE373D3DC}
JESSUP 1102CB | {C668DEDD-A850-487D-8F72-3AE13FF1307C}
JESSUP 11031518 | {16E5A2EC-59F7-4145-9776-574EFD44BE58}
JESSUP 11031540 | {47DC31DB-63D1-4B41-9B4B-82351A2B9DE8}
JESSUP 1103207944 | {FF143AE6-A28D-4D09-8909-2367978C02F1}
JESSUP 110338864 | {05238085-585C-432C-A137-934EA80FC572}
JESSUP 1103728460 | {933860CE-81EB-48DD-96BA-C0297EF47CBE}
JESSUP 1103770356 | {CD04E6E9-9DF1-41F0-9406-3CAF5658019D}
JESSUP 1103770356 | {67FD1DC2-89EE-4876-ADCD-E9F08F9D2DAC}
JESSUP 11039281 | {995D3FA2-A637-43AE-9B3D-DDCFC4316118}
JESSUP 1103CB | {995D3FA2-A637-43AE-9B3D-DDCFC4316118}
JOLON 11027002 | {0490EF9F-4327-4CEC-AB8A-ADCAD043B99F}
JOLON 11027004 | {4198C21C-60CC-4B51-804E-CE0EA277ED81}
JOLON 11027040 | {EDC5A1A3-50E5-4C1C-B31C-0B8C9AE150E2}
JOLON 11027068 | {69E872AF-88D3-4B73-8E65-0B02DC82EDCF}
JOLON 11027070 | {3C29C0B2-611E-468C-9FBC-81B8ED82FB52}
JOLON 11029887 | {D62771FC-ED91-4176-B071-0296433AA8F4}
JOLON 1102CB | {370C8631-3D98-4FD6-A4A1-B8DD1604CB6A}
JOLON 1103567674 | {241CD9B0-3EC1-46D3-9336-D70AD5A6B3EE}
JOLON 11037227 | {825689AB-F4D9-455C-B7A2-5E2909D83F12}
JOLON 11038997 | {10694F67-F9AB-4E11-A85F-784C9C9FF260}
JOLON 1103950272 | {EE29FA38-FAE4-46AA-85A2-4CE14898F14A}
JOLON 1103CB | {13EB3903-13F9-40C3-94BE-AF1022EEB8B5}
KANAKA 110165606 | {342DEF5A-AA53-475D-8D7B-ABE1A3F6B4E9}
KANAKA 1101713674 | {2606BE47-0977-48E9-BB82-73A7E7CA3E60}
KANAKA 1101733624 | {FEA6C736-5618-4A67-8C3D-643D8CABAF98}
KANAKA 1101733624 | {061D6E35-9152-4475-980E-78A8F8A47FD8}
KANAKA 110183288 | {A419DB79-B16D-4DB7-B7A8-B2FF0808C0AC}
KANAKA 110183288 | {525CC7C9-75EC-4CC3-AB61-14DD9C6B53CC}
KANAKA 110183288 | {2446443F-D5BF-4DD2-81A8-93A35BEC284A}
KANAKA 110183288 | {293E7921-3E70-4022-8AE0-53800D59CB6E}
KANAKA 1101859138 | {7761BBB4-8E31-45FA-A8E9-D749B53EA866}
KANAKA 1101CB | {0C0686BD-4FFD-40DF-98D5-F53EB4C7C859}
KANAKA 1101CB | {86D5E53A-BE6F-49C7-9E72-98C031614738}
KERCKHOFF 1101582970 | {8D7DECE1-CCFD-4BF1-BB76-D7B171370458}
KERCKHOFF 1101582970 | {F2D92EC6-451A-4A52-A3CE-BDCEE5EC0BD6}
KERCKHOFF 1101CB | {5CEBE369-1234-4C2E-B50B-4FF49A63CB11}
KERCKHOFF 1101R308 | {88F7D35A-B742-45DC-AA55-32394737AD92}
KERN OIL 11043843 | {F89CAF4A-E975-476D-87A5-AE49DE300B7D}
KERN OIL 11044479 | {5ACED025-283C-4765-A990-89285810D6DA}
KERN OIL 110476778 | {1080A12B-50AC-4BDF-B6F3-449377032E50}
KERN OIL 1104CB | {9F23EB64-F3B4-4CBF-BA80-2578C2F13B01}
KERN OIL 11062794 | {7D8FB364-6EE6-4E83-8487-836BEF8D7190}
KERN OIL 11063301 | {BC48BC1B-FF6D-435C-9294-117A7961E04E}
KERN OIL 1106397902 | {CFE459FE-1CFA-431D-B9D9-918FFFA04245}
KERN OIL 110646960 | {1BEA114F-1545-4690-B5EF-CA295187FA4B}
KERN OIL 1106CB | {6ED1033E-54FE-4DD5-BA1F-9025AD47E265}
KERN OIL 11074513 | {5609ED91-A1E1-4C62-BEA7-13452AC28635}
KERN OIL 1107CB | {5609ED91-A1E1-4C62-BEA7-13452AC28635}
KERN OIL 1108786062 | {AD9A7F19-4C4A-4FE1-AE3F-88C987AFE2D7}
KERN OIL 1108CB | {AD9A7F19-4C4A-4FE1-AE3F-88C987AFE2D7}
KERN OIL 1114282252 | {4FBB9581-17A0-4487-A29E-DC6C180F57E7}
KERN OIL 1114652106 | {4FBB9581-17A0-4487-A29E-DC6C180F57E7}
KERN OIL 1114CB | {E335EB17-4704-4C71-A9C4-F06E6AF24770}
KERN OIL 1116CB | {ACDEFC38-CD3E-449C-B2B3-70CCFC15069E}
KESWICK 11011586 | {89760509-9943-408B-8BC5-66753273219C}
KESWICK 11011588 | {E337A679-257A-4862-A121-8FE4E1C11ADC}
KESWICK 11011590 | {F2F9B8C7-DF20-4B0C-A519-3E0E16F2B19B}
KESWICK 1101417066 | {12EBD860-DFFF-4DEB-897E-4876CD2E18E2}
KESWICK 110148480 | {9C6E3EC5-697A-453D-8DEA-C3F8B751E8D1}
KESWICK 1101924834 | {091789CF-F2CA-44FB-AF43-FE6B1355E1B1}
KESWICK 11019712 | {7666B122-2C0C-4302-93AF-84BE4CAB5B18}
KESWICK 1101CB | {9C6E3EC5-697A-453D-8DEA-C3F8B751E8D1}
KETTLEMAN HILLS 1101107958 | {32284C4A-5652-49E3-A5B9-81C54835615B}
KETTLEMAN HILLS 110149656 | {F98B5A6A-0489-44A5-BF30-9316D2212704}
KETTLEMAN HILLS 1101995118 | {DE4CFFA0-0DF5-4A48-A05B-49DAE4575B0D}
KETTLEMAN HILLS 1101CB | {E3191191-EC32-4B60-A32F-F8582A37B6F0}
KETTLEMAN HILLS 1101CUS6937 | {F98B5A6A-0489-44A5-BF30-9316D2212704}
KETTLEMAN HILLS 2104358094 | {838618F9-BF36-4DB4-B2E1-2625851B3DC1}
KETTLEMAN HILLS 21049020 | {B053CDDE-1D32-495C-9C06-5A87198FD76A}
KETTLEMAN HILLS 2104CB | {854D235B-BDF1-4D5B-90C0-9DFFA17AD61B}
KING CITY 11027024 | {3218C69B-BAC7-4C6F-9235-42A08CF69E6B}
KING CITY 1102728782 | {0D58B496-6AB1-442B-8B1C-174456B4DA3C}
KING CITY 1103139682 | {9E61253D-F8F8-496C-8DCF-19A52D48CF04}
KING CITY 11037038 | {6DF33D7E-A953-44F1-82DC-C36E39D2281E}
KING CITY 11038613 | {E82AAF7E-34C3-4981-A2EA-DE8161EA0554}
KING CITY 11047092 | {8B5FDE5B-06CB-46AA-8A11-AB1CDB733591}
KING CITY 1106202402 | {63D615E0-331C-41EF-8235-4A9E59F47BD7}
KING CITY 1106338712 | {56978C22-26FB-4580-8FF1-136655B3E62C}
KING CITY 1106500 | {603BF4AE-73F8-4639-B96E-2EB86DBFAC0B}
KING CITY 1106666728 | {ABCD1BFB-EAE1-45EB-B232-D35D52BE2BD5}
KING CITY 1106944510 | {1AF9D6E4-8A41-46E5-805C-196C04612AA9}
KING CITY 1106958502 | {2515B17E-1532-47B4-AD33-23C2F28EDE84}
KIRKER 2103850957 | {2FE23A6E-37E4-4492-B4B3-A7803E6DBD18}
KIRKER 2103CB | {F88B8CE0-AB57-498A-8D97-A3755A2B41A0}
KIRKER 2103P524R | {2FE23A6E-37E4-4492-B4B3-A7803E6DBD18}
KIRKER 210475648 | {C74DE802-BF47-4D57-912D-652414113F12}
KIRKER 2105A536R | {EABC5EEA-8AF0-4E4A-8184-A7D17C84C76E}
KIRKER 2105CB | {628851EA-6F67-4051-BA19-F387912741A8}
KONOCTI 1102146300 | {E9FDF1F2-3128-4F26-849F-69EE6A64E1D4}
KONOCTI 11021573 | {B09CF53E-D8B8-401D-B2E7-CA0CCACBC2E3}
KONOCTI 11022293 | {3EE95B4C-7440-4D46-99D3-576CFD7E946C}
KONOCTI 1102285178 | {5108D106-60C2-4581-99CC-8CFC3FFB91F5}
KONOCTI 1102354890 | {0F3AA7AC-0E4E-4475-B787-048239F47929}
KONOCTI 1102391062 | {4F1A778D-82FA-487B-974B-B31596F0313F}
KONOCTI 1102410004 | {3DD38877-E68D-4183-8213-2DCDEB2FC639}
KONOCTI 11024300 | {74BC573A-BB75-4EEC-A68D-D9673A89AFF2}
KONOCTI 1102532 | {43499343-6FDA-499A-9065-0F9A4F778AB9}
KONOCTI 110264664 | {B904F4CF-C6EC-4D85-9269-44343E279155}
KONOCTI 1102716 | {A6CD11D7-C915-4B46-9810-681E2F7C1DB9}
KONOCTI 110275382 | {3635FD5D-8230-40C4-B52D-81B9839A55A9}
KONOCTI 110275382 | {108A7AF2-5761-41D5-997A-6FDD944B8F82}
KONOCTI 1102806668 | {9379E03B-C4F4-489D-BBFC-90549BB13598}
KONOCTI 110288607 | {F5EC2FB4-6AFC-476C-A967-A096A494478F}
KONOCTI 1102948 | {3EE95B4C-7440-4D46-99D3-576CFD7E946C}
KONOCTI 1102965078 | {D74BE118-5F8F-4569-9B30-2D3A4418CF36}
KONOCTI 1102985276 | {D903B690-6B65-4C8C-B64F-F1B088DE29C9}
KONOCTI 1102CB | {CB616978-006D-49B9-885E-104BFB9EEDAF}
KONOCTI 11081278 | {7B7F4A99-FA71-47CD-9812-ECE462607E94}
KONOCTI 110816078 | {DFA0C4B6-8A86-4CA9-B149-8E047B35886B}
KONOCTI 110816078 | {334B29B3-C185-47CA-B2A5-48239DE8B186}
KONOCTI 11084037 | {334B29B3-C185-47CA-B2A5-48239DE8B186}
KONOCTI 11084039 | {D3BC4C4A-6AD6-4D57-ADFE-ACA0E6607A3B}
KONOCTI 11084041 | {D3BC4C4A-6AD6-4D57-ADFE-ACA0E6607A3B}
KONOCTI 1108430588 | {6FEDFF27-6826-4700-BE39-BD65EAE2E31A}
KONOCTI 1108950 | {D3BC4C4A-6AD6-4D57-ADFE-ACA0E6607A3B}
KONOCTI 1108CB | {E3192F4B-E306-4B2D-9341-C84584505AEB}
LAKEVIEW 11034488 | {DB6CF4A5-64C5-4D3C-8106-DF77F9284168}
LAKEVIEW 11064796 | {81284E87-D055-48A1-8D04-42381F10289D}
LAKEVIEW 1106668192 | {ED6FECF4-816A-4F30-94A7-04F14DC59C8D}
LAKEVIEW 11074490 | {C023EEF5-C8E7-44B6-B1B5-BCDACF03D31E}
LAKEVILLE 1101108774 | {D6BC0451-7A49-4FE4-A356-89289BFAA264}
LAKEVILLE 1101244712 | {D6BC0451-7A49-4FE4-A356-89289BFAA264}
LAKEVILLE 1101524256 | {DCB62918-25E3-416E-A1A9-9199A2CE1F5F}
LAKEVILLE 1101CB | {DCB62918-25E3-416E-A1A9-9199A2CE1F5F}
LAKEVILLE 1102272 | {5BFD6D0E-9A91-4B87-9163-8304DBF587CD}
LAKEVILLE 1102280 | {6A2CFB57-6CCB-4CA2-AE89-8A7961352771}
LAKEVILLE 1102280 | {F573D52A-B881-4B76-BAE1-75A508AA556E}
LAKEVILLE 1102280 | {EAAF8440-F1C3-4B75-B49B-64DC2B584227}
LAKEVILLE 1102347280 | {CFC0ACB5-498C-4299-AD8A-6B456236AB7F}
LAKEVILLE 1102367100 | {4BF5FD3C-5BBE-425E-88E7-6C08A33E293B}
LAKEVILLE 1102530 | {20EEDFE7-15DE-4AF7-B5E5-DDB50839E523}
LAKEVILLE 11025721 | {398D7355-1659-4C49-98DF-20EBEB99A621}
LAKEVILLE 1102677880 | {1ADA0C64-DC47-446B-9FD6-694C7BDD505C}
LAKEVILLE 110287432 | {48094849-D1F0-46E3-A13D-DB2EF3C71267}
LAKEVILLE 110287432 | {F16EF0FE-506D-4026-9FF6-A9B4826F67BC}
LAKEVILLE 1102CB | {B8DFA050-8FBD-478F-9E02-70E1BAA0DD09}
LAKEVILLE 1105CB | {F1AD241F-1F58-4A6B-9791-DB826ADDDA3E}
LAKEWOOD 1102CB | {957F3B05-D3E6-46BF-B6B1-74EF9A986684}
LAKEWOOD 110492910 | {6E990274-D878-48AF-B3D8-9102E49E31C0}
LAKEWOOD 1104W528R | {6E990274-D878-48AF-B3D8-9102E49E31C0}
LAKEWOOD 210738404 | {E6E0CE7A-9AFF-4A02-92C6-B06263224357}
LAKEWOOD 2107396264 | {9DA5BB29-24BB-43F8-B179-1425D3AF09F1}
LAKEWOOD 2107474346 | {6A1EF0E0-D264-48CD-9270-B2391364A929}
LAKEWOOD 210757670 | {8B044506-1700-4270-904E-C6B876F0B7BE}
LAKEWOOD 210769586 | {9E806E71-872A-40DE-ABFF-C0053F485B27}
LAKEWOOD 210769586 | {CE63CF49-1D39-453E-8B0B-C0FA5C180D42}
LAKEWOOD 2107CB | {C476BEC6-6566-47F3-B164-264FA9A69083}
LAKEWOOD 2107GY401/2 | {A7B9010E-B012-48FC-A72E-913A8B3156B2}
LAKEWOOD 2109432198 | {0F07F3E8-FB27-41AD-9B59-87BC4E61A218}
LAKEWOOD 210964992 | {C65A3889-43E9-4E24-9131-D549D4446C2C}
LAKEWOOD 2110139484 | {B795863C-D42D-458E-9298-B2343CABDBF4}
LAKEWOOD 211021345 | {E8852BDB-80B5-400C-8197-8CB7718DCAFD}
LAKEWOOD 2110689714 | {B795863C-D42D-458E-9298-B2343CABDBF4}
LAKEWOOD 211082806 | {E8852BDB-80B5-400C-8197-8CB7718DCAFD}
LAKEWOOD 211090650 | {8D56729D-62B8-4F70-8336-DC0D3C2D910B}
LAKEWOOD 211093966 | {00D76738-D88D-4571-9934-906827AF7F21}
LAKEWOOD 2110CB | {8D56729D-62B8-4F70-8336-DC0D3C2D910B}
LAKEWOOD 2110D578R | {ED726999-1701-4168-B617-29D7FAC0197C}
LAKEWOOD 2110W577R | {84A8C5F2-D0FD-4CA4-8FD3-BE277808997E}
LAKEWOOD 2223289858 | {82152D73-86B6-4D69-824B-841D666F7402}
LAKEWOOD 2223920366 | {82A93E76-E374-4A06-AC4F-600C97291F0D}
LAKEWOOD 2223982800 | {88CD6C9C-9F7E-42D8-991E-21DFC6F69316}
LAKEWOOD 2223CB | {DAC222F6-911D-41F8-A045-FDB37DA63ECF}
LAKEWOOD 222454676 | {478B3B8E-9ECB-4E6B-A625-A4259404ED68}
LAKEWOOD 2224568670 | {D3A4AC80-8F36-47DA-9894-6867B4AC6446}
LAKEWOOD 2224568670 | {6C96515F-B6CE-4B5E-91AB-166552C2F0C4}
LAKEWOOD 222464093 | {C61CF421-3231-4480-9835-06D68D3E030E}
LAKEWOOD 222466408 | {E8CA3C31-B411-4BE0-B116-25507E333F7F}
LAKEWOOD 22247381 | {5BA403AB-BCA6-4612-86C3-4865011547A8}
LAKEWOOD 222475242 | {9852A44D-EA15-4875-A0A8-131531AD3AAD}
LAKEWOOD 2224CB | {5BA403AB-BCA6-4612-86C3-4865011547A8}
LAKEWOOD 2224ROBLES | {DB5046C0-F316-4A2A-8BB0-71146674ABF8}
LAKEWOOD 2224W544R | {7FE65493-C4E3-44FE-B5DB-3B458CDD6C9C}
LAKEWOOD 2227W503R | {0052F236-02DD-4D59-831D-9E6CA4EBFC49}
LAMMERS 1101932641 | {1FC74B38-2F9A-4123-9EBB-CB817D34D821}
LAMMERS 1104739578 | {7EC65080-AFFE-4F77-A7A7-BBD3D477F20F}
LAMMERS 1104CB | {D830F4CE-9C3A-4ECA-A93D-207D2BE274DA}
LAMONT 110417566 | {97C1B34A-95F8-4CCE-8DCC-4962D06B743A}
LAMONT 11043855 | {8B6D49E0-C511-4F4F-89E3-A3D706258A0B}
LAMONT 11044113 | {66C7A1C8-61A2-402A-9225-A301C2795EB0}
LAMONT 11044222 | {97C1B34A-95F8-4CCE-8DCC-4962D06B743A}
LAMONT 11044575 | {28DDAF39-AE68-4213-B81B-B1ED800C91E5}
LAMONT 11049785 | {8B6D49E0-C511-4F4F-89E3-A3D706258A0B}
LAS GALLINAS A 11041220 | {FE680FDB-B6EA-4407-A9C1-F85BBCDCB812}
LAS GALLINAS A 1104304 | {7112559E-7269-4FF3-BE61-B0339A94698E}
LAS GALLINAS A 1104304 | {4AFEE6B2-EE67-4D60-98DD-A0C3D3829D68}
LAS GALLINAS A 1104304 | {99403054-A35C-43B7-8AF3-73845ED952EF}
LAS GALLINAS A 110436840 | {CC8C3E79-3183-435F-9325-201A39689CF6}
LAS GALLINAS A 1104CB | {B49A679E-AF73-47B6-A79D-47CB4D4EEA89}
LAS GALLINAS A 11051218 | {D824A6B2-681A-48EF-8928-B97846B95D59}
LAS GALLINAS A 11051218 | {14B03F10-6F59-47D6-B547-62E7404D7BC9}
LAS GALLINAS A 1105126886 | {5D12B5EC-5DC5-4C0D-85E8-621A855AB9FB}
LAS GALLINAS A 1105292234 | {48C447B2-24E6-48B0-8B58-749860660BCB}
LAS GALLINAS A 1105904 | {BA4CC229-6FEC-4C97-A427-8049E1A3A120}
LAS GALLINAS A 110599904 | {C483C6B2-63CC-448F-80AD-EB7838DB89B8}
LAS GALLINAS A 1105CB | {90D8A356-6EF7-43D5-832C-D86D9C80D726}
LAS GALLINAS A 1106206332 | {825543F8-A353-4A25-8EB9-38A89B92A91D}
LAS GALLINAS A 1106228906 | {65BDBB0B-2F19-42BF-A514-6268B91E4F4B}
LAS GALLINAS A 1106588350 | {C7454550-7479-4CDC-943D-91F340FAA6FF}
LAS GALLINAS A 1106685656 | {7BDFA48E-615C-4CCB-95C0-B267A54E309F}
LAS GALLINAS A 1106685852 | {FB62643F-8EA7-437D-B912-4A4CCD18E192}
LAS GALLINAS A 1106CB | {0EC84767-A265-4D35-8CD0-07F4DBFC6169}
LAS GALLINAS A 1107554 | {DA43FDAA-0AFD-4DA3-9BAB-E9F0ED9A89B4}
LAS GALLINAS A 1107662 | {18214BA8-F1AB-49DB-836F-E6DF072AD66A}
LAS GALLINAS A 1107980 | {A8C682C5-2600-427D-906F-0571AB1B2939}
LAS GALLINAS A 1107CB | {920034E3-10FC-4029-9455-A3F8C0B7BFF2}
LAS POSITAS 2103CB | {E9B11EC5-1293-4DCE-ACB7-DC1D6A002C40}
LAS POSITAS 2103MR161 | {E9B11EC5-1293-4DCE-ACB7-DC1D6A002C40}
LAS POSITAS 210572161 | {7B7D7303-414E-46E8-B9CA-96AA03A82DE6}
LAS POSITAS 210576660 | {7B7D7303-414E-46E8-B9CA-96AA03A82DE6}
LAS POSITAS 210598432 | {7B7D7303-414E-46E8-B9CA-96AA03A82DE6}
LAS POSITAS 2105CB | {7B7D7303-414E-46E8-B9CA-96AA03A82DE6}
LAS POSITAS 2107CB | {CE2A7196-7DDD-4220-A701-285446F4116F}
LAS POSITAS 2107MR184 | {CE2A7196-7DDD-4220-A701-285446F4116F}
LAS POSITAS 2107MR199 | {D8477CE0-E0EF-439F-B1B0-3F9E81D16F6C}
LAS POSITAS 2108263964 | {5C439D44-2750-4AFE-8031-B30D765D354B}
LAS POSITAS 2108631066 | {A35687F3-7828-400B-B177-522C0D2F58CA}
LAS POSITAS 2108794616 | {2B1147C3-9D98-4C09-9F8C-4AD8D92E147D}
LAS POSITAS 2108MR190 | {BBAD7CA8-9930-4EC0-8393-CDE6447A6BA4}
LAS POSITAS 2110282246 | {26BB588E-7ECA-45EC-9BCC-6C8ADED051BF}
LAS POSITAS 2110MR195 | {8911B60E-25FD-4A9D-AB0E-C717D3E4437C}
LAS PULGAS 0401104588 | {1A6E13FA-4170-41DB-90FF-CC50D93E5B35}
LAS PULGAS 0401544518 | {6E6DF21F-8E99-4125-A51E-53DBB31F9125}
LAS PULGAS 0401CB | {32DE72AC-BD44-46F9-BF98-F2D8B456CA9C}
LAURELES 111110141 | {71002125-9DC8-45DF-9409-D6FE96796DDC}
LAURELES 1111142184 | {368184FD-B506-4FEF-890A-EB3A9E0F3739}
LAURELES 1111192764 | {3B264D99-424A-4183-A869-AEFB82B57347}
LAURELES 11112020 | {03861487-35BB-45AB-853E-5E8CD2B590E5}
LAURELES 11112028 | {F252A13D-948A-43C3-954E-C03439B944E1}
LAURELES 11112028 | {5FDEDD55-D8A5-4F74-BF9A-2964F309FED3}
LAURELES 1111239622 | {104DF701-D80E-43EF-BC28-6C0076869C1E}
LAURELES 11112751 | {A20E150E-0A1E-4406-A015-2C7687F7F9DF}
LAURELES 1111339866 | {594193BE-D13A-480D-86FE-4FC47D590A50}
LAURELES 1111432 | {C78621C3-DA62-4FAA-872F-5C934F1DDE39}
LAURELES 1111432 | {69D303C1-9C0C-44FE-8168-9E4EF4064401}
LAURELES 1111642522 | {2EC12232-22A0-4953-B56B-A61A01F03E13}
LAURELES 11116615 | {6DF2BCD1-911A-48E2-8725-F3E9F51AACBF}
LAURELES 11116617 | {03861487-35BB-45AB-853E-5E8CD2B590E5}
LAURELES 1111822080 | {71002125-9DC8-45DF-9409-D6FE96796DDC}
LAURELES 1111CB | {6ADA1603-F38C-494F-A594-401AD43EFE67}
LAURELES 1112160478 | {FC57C47C-D6FC-4C5B-9789-EF51C1413EA1}
LAURELES 11122142 | {5E20B311-BB0A-4C97-B880-E9EFFB1FD21F}
LAURELES 11122768 | {30178FDC-BE0A-4074-95F8-23AFFDDFE15C}
LAURELES 11122935 | {4C15AC66-4DF3-4E8D-811D-79DCA200F1D9}
LAURELES 1112543790 | {8355DD95-F9FE-4048-BDAA-30DB26E42987}
LAURELES 1112562376 | {3DF232B2-C195-4351-91B0-CBF56F76D173}
LAURELES 111268454 | {2A037456-E4D6-4133-B41E-0D0ADCC9AA87}
LAURELES 1112779322 | {BE83B9CD-2DC2-4214-9C6C-BCF6CCBA05EC}
LAURELES 1112CB | {F70B7F2A-1768-433D-8A85-4CF42DC91D6A}
LAWNDALE 0401CB | {B6D7028C-DF9E-4B2B-9D76-1FFA4414C0DB}
LAYTONVILLE 11011760 | {3A2180B6-D4DF-4D1C-89D0-A3CF8D64A791}
LAYTONVILLE 11012026 | {E7486DD4-0A7D-467A-B7E3-9401480FC5B2}
LAYTONVILLE 11012463 | {6DCD8398-F65F-454F-B860-914E54D51E37}
LAYTONVILLE 1101364398 | {02BB7E3E-93A1-4134-945C-36E6779521CB}
LAYTONVILLE 1101402 | {4736216A-0E46-40F2-B710-F8C9A736BA4F}
LAYTONVILLE 1101448108 | {301116D8-18DF-4DD2-820F-B08551F93AB9}
LAYTONVILLE 1101518 | {48D8AB29-32BE-434B-A269-6B6F081BC956}
LAYTONVILLE 1101518 | {4FE48FE3-85C8-4DB4-9A07-5F45D91C38E0}
LAYTONVILLE 1101518 | {AF29DE4B-1137-4070-BCC8-1015CEA329AE}
LAYTONVILLE 1101518 | {565C01F8-C5F7-416B-AE2F-E7FBB0E971EC}
LAYTONVILLE 110189606 | {17A00714-8A49-49C0-B860-6006F3A8F3AD}
LAYTONVILLE 1101CB | {65E5FC7F-8C6A-45F6-95D3-74B8F1E3F473}
LAYTONVILLE 1102141962 | {24057538-792C-47E6-85BB-163CA71B1FC5}
LAYTONVILLE 11022502 | {71012A72-9F3A-4416-A409-5A697A15AF1C}
LAYTONVILLE 110237586 | {389365FD-B3C9-4F63-9935-3457B5B05A11}
LAYTONVILLE 1102500 | {339FA4E7-145E-4B4D-82FE-6DAA866AF8A9}
LAYTONVILLE 1102538750 | {22042EBF-768B-4F6E-A0FB-8BA05EA6F8F6}
LAYTONVILLE 1102538750 | {12CE3CF5-FBCD-48EC-AA1A-EDB743F84999}
LAYTONVILLE 1102572 | {33062E2A-6001-4611-8363-46C244F6285A}
LAYTONVILLE 1102572 | {B0D27299-3385-4D09-B4B4-A2D526F16A36}
LAYTONVILLE 1102632670 | {9B107EC7-49C5-413B-94F9-4B15782C698B}
LAYTONVILLE 110264908 | {9B107EC7-49C5-413B-94F9-4B15782C698B}
LAYTONVILLE 1102682 | {87005614-6109-4255-ADD3-BC87FF9FF06D}
LAYTONVILLE 1102682 | {9C0210C9-FBB0-4C91-A32D-9DD4D26081CB}
LAYTONVILLE 1102CB | {90C83132-41C0-4461-99CD-C9A5052731EB}
LAYTONVILLE 1102CB | {DA641DAA-071C-4BD0-8FE8-59E3AF1B073F}
LE GRAND 1104257152 | {3CEEE4D4-D663-46B2-AC68-69ECFC3C9FE4}
LE GRAND 11045010 | {2DA20832-0986-4675-BA93-1E55E4E2B6B0}
LE GRAND 11045050 | {0CA88DA8-9F93-4D25-8D94-96611094402C}
LE GRAND 1104560074 | {01A18280-CFFE-4FA9-A253-5204E4F05FC8}
LE GRAND 1104807088 | {7E6C2D4B-5B4B-4E0D-9712-5CEC41B42EB0}
LE GRAND 1104CB | {7E6C2D4B-5B4B-4E0D-9712-5CEC41B42EB0}
LE GRAND 1104RUSE | {2DA20832-0986-4675-BA93-1E55E4E2B6B0}
LE GRAND 11104600 | {B9B7E2CF-8396-4913-AA14-43F1BD9F0A32}
LE GRAND 1110606810 | {9386091A-5818-4D70-AC92-F7261719FDB4}
LE GRAND 11107120 | {B9B7E2CF-8396-4913-AA14-43F1BD9F0A32}
LE GRAND 11107130 | {16B45AFD-52A4-45F8-802F-85185631E20B}
LE GRAND 11109630 | {AC73B381-FF2D-430B-A53A-6C08DD53B598}
LE GRAND 111212020 | {AB61C412-86D5-43A5-89BA-246B1666F6F8}
LE GRAND 1112868686 | {9EEF459F-4F67-4391-8343-D5C33AE42C3E}
LERDO 11124323 | {B90BBEF1-4707-4F86-93FE-6CC7E1F4609C}
LERDO 1112499642 | {76047285-EDD8-4CF2-A245-CE9CEFB7A1FA}
LERDO 111289580 | {9FE3872F-A0E3-4AB4-85A1-BA8831629819}
LERDO 1112CB | {139F2AEC-F2EB-4205-BD06-2DB9C89291F2}
LERDO 1112CUS2394 | {76047285-EDD8-4CF2-A245-CE9CEFB7A1FA}
LERDO 11153910 | {432E130E-051C-494D-B134-233DA8DB61A0}
LERDO 1115CB | {432E130E-051C-494D-B134-233DA8DB61A0}
LERDO 1115CUS1066 | {432E130E-051C-494D-B134-233DA8DB61A0}
LERDO 1116781190 | {CC8B3025-87F1-4D28-A3EC-C32E8833BD7C}
LERDO 1116CB | {85B670DF-938B-4D4D-BF9D-077C5E868E52}
LINCOLN 11011398 | {4AE4954C-B74F-45AB-A357-66A3AEBC8125}
LINCOLN 1101210168 | {CF1461D3-D5B5-459F-A63E-DFDD8EE92A51}
LINCOLN 1101744292 | {953FB463-ACCF-445A-B11B-469D852D0D34}
LINCOLN 1101860022 | {EA2F5A18-032D-4EAD-88B5-87B9DC0F78D0}
LINCOLN 1101875554 | {EA2F5A18-032D-4EAD-88B5-87B9DC0F78D0}
LINCOLN 1101881364 | {CF6D4C7B-077F-42A7-A24E-BAE6865A7D41}
LINCOLN 110195756 | {46334C59-6E86-4DFA-8790-B3204A43F682}
LINCOLN 1101CB | {BC430285-5DBF-4545-8AE8-96AF6071F68F}
LINCOLN 11042070 | {FDA2EA55-8785-46E8-B115-1C92328E3E9B}
LINCOLN 11042072 | {A71D3F90-1807-4414-8E54-A388088D7CB1}
LINCOLN 11042308 | {FB48CF9D-FE80-482F-938D-2D781F244FF8}
LINCOLN 110451756 | {302C4176-4830-4D29-8953-2FECE7A076EF}
LINCOLN 1104535728 | {99831F0A-F4B9-4BE8-B127-F12ECAC1EFEA}
LINCOLN 1104685276 | {62CF7EB0-1F27-4DAA-93C0-D5A9F63BB597}
LINCOLN 1104693294 | {68BE4BEA-6B01-4263-BF4A-085FBF6C3513}
LINCOLN 1104818790 | {C5EA5C15-1CF5-4589-BD9C-EEF6FE17F558}
LINCOLN 2109924404 | {D78EA46A-E23B-4345-8961-C542C9C645D9}
LINDEN 11033044 | {359B83DB-DA93-4FF5-81A3-E560909275AE}
LINDEN 1103462603 | {359B83DB-DA93-4FF5-81A3-E560909275AE}
LINDEN 1103542460 | {20BF9716-345C-4355-8648-C5A90D0DDDB0}
LINDEN 11042456 | {C6A0AF02-6E9B-489C-9A21-682EA19B2089}
LIVE OAK 11041300 | {DC7977FF-D7DF-44A4-BEB1-4429D543554C}
LIVE OAK 1104309742 | {E980A912-47D9-4D36-826B-841082227DCF}
LIVE OAK 110448420 | {A807A1C3-5E34-4A3A-B496-D075D0A8772F}
LLAGAS 21013835 | {1598AD07-E47C-4EC4-B73E-67FD615040E3}
LLAGAS 21014523 | {611865E2-8B49-4014-BEAC-6B120F62309D}
LLAGAS 2101984552 | {689A7047-6554-469D-A572-0CDDE35EC73D}
LLAGAS 2101XR244 | {133545C9-FF59-4E89-AB9A-6D025A3D74E4}
LLAGAS 2101XR264 | {6D5B6410-E4BE-4661-9810-568D00627E89}
LLAGAS 2101XR584 | {611865E2-8B49-4014-BEAC-6B120F62309D}
LLAGAS 2101XR586 | {1598AD07-E47C-4EC4-B73E-67FD615040E3}
LLAGAS 2101XR586 | {B1426F28-A34B-4992-80A9-A93CA76693A1}
LLAGAS 2101XR586 | {775E1FFB-162C-4436-A1F2-3394B067012F}
LLAGAS 2104524360 | {F11F1581-106D-4267-B291-AD8060715445}
LLAGAS 2104603392 | {28E6C6D7-8DD9-401F-863B-133430EA57C4}
LLAGAS 2104735530 | {AF07F25E-155C-4D19-8872-642A3CCD5556}
LLAGAS 2104CB | {38C5DC02-2DC6-4C9C-B45B-9E93C420E849}
LLAGAS 2104XR242 | {AF07F25E-155C-4D19-8872-642A3CCD5556}
LLAGAS 2104XR294 | {F11F1581-106D-4267-B291-AD8060715445}
LLAGAS 2105XR234 | {90264C2C-3ED3-42D6-BFF5-F41E927FBBE3}
LLAGAS 2105XR234 | {A3614058-D6F6-498F-B865-E27268AA97F2}
LLAGAS 2105XR234 | {C86F8094-06A8-47C1-9F16-078F9A41AD6E}
LLAGAS 2106338878 | {699C93CA-B67B-4D5A-B3DE-FBF338954446}
LLAGAS 2106517530 | {AC148FB9-082D-4C31-9937-1A18D38D116C}
LLAGAS 2106CB | {36DDC7E6-DD90-43BE-A64F-8D62BC22EEA3}
LLAGAS 2106XR296 | {A5FA5012-AEEA-4400-AFE1-85051ECE9EFD}
LLAGAS 2107142710 | {E4B7388D-56E6-4038-9DF8-2387BF129F0C}
LLAGAS 2107374344 | {40BE7D0D-D7B9-4C64-B06B-437270976420}
LLAGAS 2107680574 | {525B3809-9D6D-4E88-A375-F82004931F4F}
LLAGAS 2107870396 | {4DC0A76E-797A-4818-B053-21B7BC501B6E}
LLAGAS 2107CB | {DD8395FC-A049-4EDA-8DC5-FEEBE3B0FF15}
LLAGAS 2107XR188 | {1B5D7998-B20D-4848-BE59-22884992869D}
LLAGAS 2107XR188 | {7FBBA027-0AB6-47D3-B07E-8956861A85DA}
LOCKEFORD 210212466 | {E9F5320B-0597-4D9F-8A65-DF92EDFD62CC}
LOCKEFORD 210212468 | {34045FAB-FD0E-4469-952F-B8E16E6D8945}
LOCKEFORD 210212472 | {020F1F1E-EAE9-4367-AEC0-098AE7412232}
LOCKEFORD 210212686 | {E683FC45-7E26-43C0-BA21-0F4F179766A6}
LOCKEFORD 2102155972 | {61450EA0-5AD6-4740-969E-B51FA5D8CE00}
LOCKEFORD 210220355 | {34045FAB-FD0E-4469-952F-B8E16E6D8945}
LOCKEFORD 2102206884 | {2D298F6A-BEA8-4B07-AC26-301AFF0706CC}
LOCKEFORD 21022130 | {025A37BA-6164-49D6-AE44-90C3E4A6334D}
LOCKEFORD 21022136 | {61450EA0-5AD6-4740-969E-B51FA5D8CE00}
LOCKEFORD 21024045 | {020F1F1E-EAE9-4367-AEC0-098AE7412232}
LOGAN CREEK 21022226 | {0DB23F18-2307-44BE-917D-7278F1DC4733}
LOGAN CREEK 21022540 | {E96F486C-62EC-4857-BEE6-A37D9D248162}
LOGAN CREEK 2102305794 | {34396821-7B8E-48C0-9B24-EA9FE3C15481}
LOGAN CREEK 210237316 | {8700E55C-38C6-41AB-AF2A-3B50EA0B2E05}
LOGAN CREEK 2102420992 | {C3B0FA01-45C5-46FE-8FB8-3A5545CB0CA4}
LOGAN CREEK 210247194 | {E96F486C-62EC-4857-BEE6-A37D9D248162}
LOGAN CREEK 210262032 | {BEFCE23A-309D-4D6F-8ABD-50878BF1EA08}
LOGAN CREEK 210269358 | {E96F486C-62EC-4857-BEE6-A37D9D248162}
LOGAN CREEK 2102767046 | {E8966EB9-3CA2-4993-8729-F6FAD99583CF}
LOGAN CREEK 2102806 | {E96F486C-62EC-4857-BEE6-A37D9D248162}
LOGAN CREEK 2102809558 | {70ECEC2D-73F3-49ED-8B79-7E412FA22378}
LONE TREE 2101CB | {9C0A4E39-81A0-49F9-8807-BE1F20686C8B}
LONE TREE 210268100 | {0F8B9B4C-E4B9-4DC3-A3FA-3F60356E9626}
LONE TREE 2102B558R | {0F8B9B4C-E4B9-4DC3-A3FA-3F60356E9626}
LONE TREE 2102CB | {0F8B9B4C-E4B9-4DC3-A3FA-3F60356E9626}
LONE TREE 2105708440 | {330BA416-CC69-4A5B-B996-95A574C9A184}
LONE TREE 2105708440 | {2DF1A9D4-3884-4795-BEBC-87145C5F4675}
LONE TREE 2105708440 | {3A3301CD-CA19-4299-84F3-37EFFB524245}
LONE TREE 21059888 | {899F0CBB-18F3-4245-A29B-92D504639716}
LONE TREE 2105CB | {BF1E0B7F-6FE5-43AC-AD5E-51535747C12F}
LOS COCHES 1101625902 | {C01DBFE3-B3A1-4C43-8C34-5A08EA142769}
LOS COCHES 110255146 | {24C662B5-8749-445E-AAC6-4B342D948886}
LOS COCHES 110256346 | {24C662B5-8749-445E-AAC6-4B342D948886}
LOS COCHES 11027046 | {24C662B5-8749-445E-AAC6-4B342D948886}
LOS COCHES 11027514 | {24C662B5-8749-445E-AAC6-4B342D948886}
LOS COCHES 110275272 | {8D6FBC1E-44FB-42A8-B471-883E8BB7B734}
LOS COCHES 1102CB | {C48784E3-4EDB-45E6-AEA2-4A807640BDC5}
LOS GATOS 110118757 | {13B92AF0-4A78-46CF-B390-D7E70CA4EA48}
LOS GATOS 1101206248 | {C5B5434F-C05F-41A4-93CB-6D3F98039D91}
LOS GATOS 1101502026 | {E1FA2A15-AD3C-4DAF-93F8-E10F60AD1FB4}
LOS GATOS 110160052 | {D47892F1-0CB0-45EA-A4B1-629482BAEB79}
LOS GATOS 110160136 | {A1B517D1-7F5E-496E-A188-34F488988F32}
LOS GATOS 1101865012 | {E42EB719-E746-430D-9917-550CC0C07043}
LOS GATOS 1101950286 | {C987EEC4-79D7-4CBA-A41E-47D4FFF82E13}
LOS GATOS 1101CB | {B81601D3-2F43-44C7-B6E6-ECFC64FD48AF}
LOS GATOS 1101CB | {168FAC6E-221A-4D80-AD26-79821278B765}
LOS GATOS 1101LB40 | {2E2463B4-F331-472F-B632-0DB9F9C1E4AF}
LOS GATOS 1102526868 | {40479F22-BBD2-4DBE-B231-5BD9D16BE0F7}
LOS GATOS 1102CB | {9CE095E8-15BC-49D7-95AC-553D14C8CC1F}
LOS GATOS 1106229258 | {8B8E42DC-1EBA-40EA-A3AE-D2E93881B931}
LOS GATOS 1106229258 | {F674098C-5738-4FE0-AF08-CDF03267FF85}
LOS GATOS 1106229258 | {B972E340-A09F-4DF5-A7C4-8E5CA1C2E126}
LOS GATOS 1106229258 | {81080B1D-E7BF-4721-A2BA-91568ECFC0A2}
LOS GATOS 1106229258 | {F8B51D0B-1496-48CB-9BC1-E546F2F6F19A}
LOS GATOS 1106648186 | {946E0443-399A-4C5D-A791-7B90E0193482}
LOS GATOS 1106697500 | {5B274F91-3DCC-4D8C-9FA0-4D35A285F7F0}
LOS GATOS 1106758116 | {36BC19D5-5B54-4EDE-A114-54D9B91BFF83}
LOS GATOS 1106848782 | {CEF29D9D-C063-420D-8FDB-6DA1E472DEE9}
LOS GATOS 1106880626 | {41876CDD-E960-4684-B78D-E48B7ECC5753}
LOS GATOS 1106880626 | {661964DE-1394-445D-8404-1E88A5E86A52}
LOS GATOS 1106880626 | {B517F834-4473-436F-8128-C6E1EFA1ADEC}
LOS GATOS 1106917258 | {F0513295-9AFE-47CC-93E8-DF299D8C11AB}
LOS GATOS 1106CB | {D03187F3-5053-4E30-B164-D057F0065569}
LOS GATOS 1106LA42 | {4EE12AFE-1CE1-4E74-ACC8-F23D91BAFEE1}
LOS GATOS 1106LB44 | {C1116056-BFA4-4C82-B51B-0F5824C94517}
LOS GATOS 1106LB44 | {A82BCF3C-DF7C-4ECB-A40D-DF548D9A8FCA}
LOS GATOS 1106LB44 | {5D70BF4D-C1AE-452C-84AB-8E4767458B84}
LOS GATOS 1106LB48 | {ED4FFAA8-32ED-4B25-8B3D-9D1525DB179F}
LOS GATOS 110722965 | {7CE16D95-DFE8-4441-B8C8-1550C26A19A8}
LOS GATOS 11073173 | {37D43165-2E85-47A3-A64E-1911105C9D09}
LOS GATOS 110760024 | {F77EAC7B-DF34-46F0-9E63-E76A1EA4BA50}
LOS GATOS 110760092 | {1C2D3194-16E0-4259-A36D-B7ED22E1325F}
LOS GATOS 110760092 | {FE58AABB-4F2E-4F6C-8A2E-70A2F4BDC1F4}
LOS GATOS 110760092 | {96A6C92D-B47A-4526-A196-0DFD267ED2E8}
LOS GATOS 110760114 | {9B2D8A48-20CB-454C-BA37-343177467945}
LOS GATOS 110760114 | {938F5BC3-1A85-482D-8A00-FAFD637D28F9}
LOS GATOS 110760118 | {996F801A-49DB-4E12-9C16-86F37BF363D7}
LOS GATOS 1107639614 | {A57DA086-5167-4A5A-95F0-BA291DD6146E}
LOS GATOS 1107772050 | {87ECDDBD-6F34-4CCC-8169-87E097323A25}
LOS GATOS 1107772050 | {81BDE7FD-9C41-41DE-9C19-426097370767}
LOS GATOS 1107772050 | {2D8F3B80-1078-4F21-A2C2-0C45F69D55BE}
LOS GATOS 1107781232 | {4B335677-1F7E-4B1E-AE3E-E2418D415555}
LOS GATOS 1107781232 | {DB1D2199-2671-4DFC-86B0-02A91629C7CA}
LOS GATOS 1107812664 | {5685685F-A6FF-42EC-B764-0A6E777F0FC6}
LOS GATOS 1107872428 | {A1E068E6-D266-47B2-8BDB-8F6658FA3D5A}
LOS GATOS 1107872428 | {6A650B21-F54A-472E-814C-0A1E51909D03}
LOS GATOS 110789897 | {168CA0CC-B69C-4348-8F2F-734D81EB2A0E}
LOS GATOS 1107914254 | {DCEB87E4-E9AF-44AC-9CD1-F1B1DDA3FBC9}
LOS GATOS 1107979638 | {F73A8E8E-1FD0-4EE3-972E-658276891759}
LOS GATOS 1107CB | {33CD1D9A-1060-4DB9-934E-28850E9FE4EE}
LOS GATOS 1107CB | {F9DF48B9-C722-406C-B401-60189B57E89A}
LOS GATOS 1107CB | {51AD81F6-59D3-47CA-B0D8-858EF37F7E2F}
LOS GATOS 1107CB | {4DDBBCC4-5EE7-47A0-87A1-0D7FE2F9C380}
LOS GATOS 110812187 | {4FEF4D5B-32F0-4BC5-8454-5A8D86F89A74}
LOS GATOS 1108590544 | {181A63BB-5CD3-4EBE-A88A-6C87700E0247}
LOS GATOS 1108CB | {52AE67FA-770A-4A3A-8316-07026BFE1782}
LOS GATOS 1108LB86 | {179FE519-944E-4835-9C33-84ABCACF7D82}
LOS MOLINOS 11011308 | {09A4B9E8-989B-4DA3-9154-EF01A44BB71B}
LOS MOLINOS 1101297862 | {98F6E8CD-AC98-43CE-B18A-0B7DA9CFD9E4}
LOS MOLINOS 110154804 | {7C1F521A-7879-4C4A-A689-ED87C735A305}
LOS MOLINOS 110163998 | {4FE42200-32F5-4A5C-912A-02E87F21A83B}
LOS MOLINOS 110171402 | {7C1F521A-7879-4C4A-A689-ED87C735A305}
LOS MOLINOS 1101CB | {2F05D844-382F-480E-A414-A8255A95CC97}
LOS MOLINOS 1102CB | {3C29BFDD-B708-4EA4-82F6-BE02F2280B00}
LOS OSITOS 21011132 | {4039D191-A1E0-4943-9C3A-CC09D2E36841}
LOS OSITOS 210164348 | {8276CB14-B72D-46E3-83F9-1F1DCC6858E6}
LOS OSITOS 21017014 | {1106E17B-9FEA-4422-BC78-03AC3BC8E250}
LOS OSITOS 21017865 | {0CC2483C-397F-4572-B5BB-6C4551D9A01E}
LOS OSITOS 2102148504 | {D24D41FB-BB5E-4935-A71E-973726960AB3}
LOS OSITOS 2102258878 | {03FDC6F0-8EFF-4D98-B64E-FE44DDCDA68D}
LOS OSITOS 2102624200 | {55FFD10E-AE85-4366-9D32-F7DB90B5CFE9}
LOS OSITOS 21027470 | {F09DB02D-C60B-4BD1-94D9-7209106E4610}
LOS OSITOS 21027592 | {3616477B-E0BC-4A69-8662-9C027B6A345B}
LOS OSITOS 2102780218 | {F09DB02D-C60B-4BD1-94D9-7209106E4610}
LOS OSITOS 2102CB | {F09DB02D-C60B-4BD1-94D9-7209106E4610}
LOS OSITOS 2103174580 | {215C3316-AD64-4D86-B319-9811218FF7C5}
LOS OSITOS 2103220608 | {B9039DB0-DC75-45BF-9F2C-149A67BBE1F8}
LOS OSITOS 2103258688 | {095C4297-BB9B-47AE-9B30-7513251297A3}
LOS OSITOS 21033010 | {528CF887-3009-4BDA-941C-23A6FE9B29B6}
LOS OSITOS 2103446928 | {B467BCE4-DAF4-4E21-88A6-11037A39AE06}
LOS OSITOS 2103606732 | {0FF5262D-4973-4432-8509-F86EEF6E48EE}
LOS OSITOS 210366936 | {29735F50-C5F4-4F83-8013-D3D04A895748}
LOS OSITOS 2103695270 | {40F1B87F-AB3F-4DE0-8638-58D9EA205806}
LOS OSITOS 21037062 | {113FEF80-B5A7-4041-A279-F58DE4B71B87}
LOS OSITOS 21037082 | {E273F09C-00C1-48A4-A71E-352A62A15E75}
LOS OSITOS 21037086 | {07660895-8772-47F6-AC16-71B847A1F61F}
LOW GAP 1101274514 | {1F44035F-9F44-4D9D-BD78-79FFE4020D74}
LOW GAP 110137498 | {BD574B29-15C8-4B0E-8A1E-85F74B10E15F}
LOW GAP 11014086 | {71DE392B-20E6-4124-9FFE-851197719244}
LOW GAP 11014160 | {C206EE4F-0006-4ECA-9B96-00B5245745DE}
LOW GAP 1101449990 | {9677DC50-AB85-42C6-9822-52AD410900D7}
LOW GAP 1101603404 | {270C7C31-4E44-4C5F-A109-764C7D9C23E5}
LOW GAP 1101750090 | {7EAB9CA9-F4EA-480A-8BE4-2E97F9009D2B}
LOW GAP 110186816 | {35FAF06A-E239-4015-A854-21F6A4EC4F03}
LOW GAP 1101CB | {5346AC49-CDE1-40C3-A681-DA76F08A9FA4}
LOYOLA 1102429970 | {13464ED5-9F48-4024-B104-3201B180FAC2}
LOYOLA 1102550291 | {DEF8A973-66EF-4B4B-8E5E-9D523DD1F02E}
LOYOLA 1102550291 | {379AF1A9-16E4-4C0C-BE5C-4BB0C4F98451}
LOYOLA 1102584588 | {85D8A8EF-2A96-41AC-90F5-E998ECCA5D4C}
LOYOLA 110260128 | {6582F831-14AD-4AED-9367-19CCB6CFBE91}
LOYOLA 110260128 | {A6F27353-D8D5-4597-90A2-CB1701C67449}
LOYOLA 1102CB | {E303C5AD-824F-4E47-B866-CA2B13090981}
LOYOLA 1102CB | {27A786CD-A523-48EE-89CB-20E33A9B5F17}
LOYOLA 1102LL64 | {8FF2C357-E560-4F49-BD6C-1A85C9D294D8}
LOYOLA 1102LL66 | {9C5A5E3E-259E-4BA4-92AC-E564F3B34976}
LOYOLA 1102LL86 | {2FF7416F-A3A8-49DE-8B6E-03DC5E89A659}
LUCERNE 11031280 | {A05AE75B-B8B1-4EF0-A327-427A302D4FDB}
LUCERNE 11031663 | {F34B7A71-9435-4BB4-952A-AC8430FF4984}
LUCERNE 110327932 | {93D2CEDB-A4A6-4F60-93F8-470CFD18E884}
LUCERNE 11034200 | {9368EE05-0B02-40F5-BB24-E9F111612527}
LUCERNE 1103438776 | {3F463C9A-62CC-48DC-94B5-9AFB49692D9B}
LUCERNE 1103630 | {F34B7A71-9435-4BB4-952A-AC8430FF4984}
LUCERNE 1103721 | {5F1D4DCA-3F79-4EF8-A5B5-E7ADFFF099F4}
LUCERNE 1103797452 | {5F1D4DCA-3F79-4EF8-A5B5-E7ADFFF099F4}
LUCERNE 1103CB | {F830099C-EEA2-4CF4-B68F-D2F012925468}
LUCERNE 1106180498 | {3863EA52-4FCC-42AA-9CFA-31E34DF2A83C}
LUCERNE 11062327 | {BFEEA045-A307-47A2-9C2E-0B69ACE24065}
LUCERNE 11062355 | {BFEEA045-A307-47A2-9C2E-0B69ACE24065}
LUCERNE 110638632 | {11292177-63B4-4D1D-9B97-B2A90B30A4AD}
LUCERNE 1106439842 | {97FE1380-8BE3-42D2-B6E3-D4904D2C8F20}
LUCERNE 110647198 | {DA9B8D37-5C46-437A-B55A-1CC1BE987A25}
LUCERNE 110647198 | {BD944265-C79A-4F2E-BE54-095144D90522}
LUCERNE 1106526 | {BFEEA045-A307-47A2-9C2E-0B69ACE24065}
LUCERNE 1106709252 | {DE7938AC-4236-44EA-970B-170B6BDC431A}
LUCERNE 110676850 | {97FE1380-8BE3-42D2-B6E3-D4904D2C8F20}
LUCERNE 1106857174 | {64C6F4FE-9745-4B83-9BA2-6905B1D464FF}
LUCERNE 1106921672 | {96ED1668-0449-4F25-BD2B-721D2C37C1E8}
LUCERNE 1106988590 | {03794043-4739-4484-8FAE-7CD50FBF19C7}
LUCERNE 1106CB | {64C6F4FE-9745-4B83-9BA2-6905B1D464FF}
MADISON 1105495270 | {D89FCFFD-10AE-4DAF-9478-18CF956ED9AB}
MADISON 1105495270 | {9D3CA3D4-94FA-4AFD-A3FA-3A4B24171F99}
MADISON 1105995448 | {9D3053DD-F2DA-4333-B421-C9281936C7AE}
MADISON 2101117644 | {85B7B134-DCF7-4F97-B0E2-4F8DFD3F20BE}
MADISON 210112321 | {0CB657DB-6DA6-4A9D-A1FF-01F4FF1F9C5B}
MADISON 21011606 | {892EE518-0261-403B-AEBB-DE522B481F93}
MADISON 2101168918 | {E7E73D27-C837-44A0-9564-E1D64AE481DD}
MADISON 21011943 | {DCC4F33D-94BC-4C20-B81E-44479B092EB6}
MADISON 210120052 | {EC60260F-F5BE-44EB-8B57-010478F5D482}
MADISON 210123272 | {C4B928B0-1315-4EFF-A9DD-F47090119304}
MADISON 2101274974 | {BBB7A181-0979-426C-AED4-D3871931C8AC}
MADISON 210134164 | {C77C2EB6-5952-4412-A7A6-B800F29794A8}
MADISON 2101351038 | {9C777D0B-81EB-422B-9E3E-C0277E2A4B3B}
MADISON 210137082 | {8E6B668B-C3B5-476E-8081-82E065E91883}
MADISON 210144634 | {522A389A-AB26-4856-B015-C925A695BEA6}
MADISON 210144634 | {3606619A-937D-46E3-AFC7-2B9E8CB032C3}
MADISON 2101484892 | {64480341-2026-4E64-974C-9602D07F2EA7}
MADISON 210163762 | {FAFBD2A1-FFC3-48C9-9B09-E9ECE3AD7FAB}
MADISON 2101647730 | {BCFA3D7A-9BB0-4F03-8EBD-9C73356DE26C}
MADISON 21016617 | {FAFBD2A1-FFC3-48C9-9B09-E9ECE3AD7FAB}
MADISON 2101725408 | {A1A5DB3C-6B99-4418-9DB8-859C77A01E6D}
MADISON 2101732852 | {1546D3A5-6746-4DBC-BBEC-516CF8874085}
MADISON 2101760730 | {0CB657DB-6DA6-4A9D-A1FF-01F4FF1F9C5B}
MADISON 21017702 | {DCC4F33D-94BC-4C20-B81E-44479B092EB6}
MADISON 2101845694 | {9F1D585F-4585-484D-A04F-23919C37AC0A}
MADISON 2101888814 | {7332DE5F-6F7A-45B8-8DD4-5630772AAE8E}
MADISON 210189332 | {D7243FB0-38B4-4640-8C10-2CD25C9CD868}
MADISON 210189332 | {42DA18CF-B1FF-48BB-B6F2-B9AA0AFAFCC6}
MADISON 2101936212 | {BB2CEA8E-784A-4217-8D58-EADEE452F20C}
MADISON 21019512 | {C556C375-7B0E-4693-B801-A5D6F39CB3E2}
MADISON 2101CB | {EA6111A8-7AB9-443D-A740-55705E7BEA72}
MAGUNDEN 1104713254 | {5241CE2D-8E22-46C4-80BB-764394B9CCF7}
MAGUNDEN 1104CB | {5241CE2D-8E22-46C4-80BB-764394B9CCF7}
MAGUNDEN 1105878284 | {59135F98-8C13-44B6-AE58-D413A6DA16EA}
MAGUNDEN 1105CB | {59135F98-8C13-44B6-AE58-D413A6DA16EA}
MAGUNDEN 1106199938 | {3F628833-4984-477E-A3C2-EFB049C04D5D}
MAGUNDEN 11064849 | {66DFEB2A-20A9-4CD9-B5EB-C970AD02C1F5}
MAGUNDEN 1106CB | {3F628833-4984-477E-A3C2-EFB049C04D5D}
MAGUNDEN 1108250674 | {9C5EB345-7F42-4EDD-AEC2-EDD4964080F0}
MAGUNDEN 1108468940 | {20D3849D-3023-452E-B171-9B7A3BFB9D93}
MAGUNDEN 1108646785 | {F050F9C4-4C6F-4F17-BD31-4602B6D69F38}
MAPLE CREEK 1101555034 | {4A7C5A51-F5FD-4AA2-8551-BD1E704B9D30}
MAPLE CREEK 11016906 | {8625CA5E-81C0-4BA4-B083-5D0354E4556D}
MAPLE CREEK 1101CB | {D3EDA1A2-8AF8-4A2A-853E-161161439812}
MARICOPA 1101931236 | {4BEF20F2-8B61-45E8-BE0E-DD28930DE8C2}
MARICOPA 1101CB | {43E6321C-B985-4E32-B929-1A46FBCBBCE0}
MARICOPA 11023082 | {F0D3E110-E06F-4F39-B085-758DD01FFE6B}
MARICOPA 11023558 | {341A5947-0E50-4A7D-9C85-BBC1E06228CA}
MARICOPA 1102453320 | {34FDF5FD-B2A0-4EFC-9338-7E46284554C8}
MARICOPA 110265196 | {341A5947-0E50-4A7D-9C85-BBC1E06228CA}
MARICOPA 1102CB | {3886D126-B275-4867-A304-EDF3653324EA}
MARIPOSA 210110215 | {2CF9040D-207D-4937-832E-9041804B9FF8}
MARIPOSA 210110240 | {4272B914-DD96-40AD-9866-404625A4A67D}
MARIPOSA 210110317 | {612A4DF1-869F-44BA-883E-7BF065A46FAE}
MARIPOSA 210110990 | {8667D6C6-0139-493E-962E-C5EBDBB9ECAB}
MARIPOSA 2101151918 | {AA9A1768-272F-4017-B4A9-F1105C658F25}
MARIPOSA 2101309438 | {F7FD2F95-B048-4568-9591-C9FC96195E8A}
MARIPOSA 2101310816 | {65369545-8B17-40D7-837E-B88373C846A6}
MARIPOSA 2101439030 | {A338E4B9-F36F-4E6D-BD6C-78D7EE471DF2}
MARIPOSA 2101439030 | {B1C3BF34-DFE5-420F-B7AD-C0CAC681FC7D}
MARIPOSA 2101439030 | {C9C8E4E3-3948-4116-9414-285699E135DB}
MARIPOSA 21014410 | {D0EAE99F-556B-4D0F-9202-C86978E77F6F}
MARIPOSA 2101724632 | {2E712FF7-46DB-4595-87CC-EBF6509EF1E0}
MARIPOSA 2101752630 | {482F0B3D-137A-48C9-9E82-504F3E80E798}
MARIPOSA 210190180 | {FC42FA3C-C2C3-4E31-A9B5-479F6C258FC9}
MARIPOSA 2101929360 | {F15FE3D9-E711-401A-B57D-CC1BD9F02B6F}
MARIPOSA 21019400 | {07425403-A718-4540-8F73-D56A4C8BD811}
MARIPOSA 21019400 | {D298C9EB-7969-4020-A299-D9B72D648E9A}
MARIPOSA 210197142 | {BE195AB2-DFE6-47E2-AD27-182086FF32D1}
MARIPOSA 2101CB | {050E06AF-91BE-429B-BDFE-3EAD80F24863}
MARIPOSA 2102105582 | {261EC4CF-46BA-4AFA-AA3C-80526D6D67D0}
MARIPOSA 210210880 | {AF85260C-2339-49D2-94BE-A2E04CBD4128}
MARIPOSA 210210880 | {92F6A9F3-F59B-40C4-9926-F2D8D117E1C0}
MARIPOSA 21021960 | {C88CD342-0019-4371-8FA7-CA6CF25A5380}
MARIPOSA 2102241564 | {2843CC6B-4B7B-4873-8040-0A60876FBD79}
MARIPOSA 210237282 | {9C7CA36A-A220-4889-B18C-7665D5C736E3}
MARIPOSA 210237282 | {C6BD4515-8683-4645-8938-F4F4DB1A65DE}
MARIPOSA 210237288 | {38642A96-8776-4716-B709-CC59463C3DA7}
MARIPOSA 2102468604 | {8B636FC3-DE65-48E2-AFB0-A79BD1DC46B6}
MARIPOSA 2102594143 | {2843CC6B-4B7B-4873-8040-0A60876FBD79}
MARIPOSA 2102851902 | {E2D52595-66C4-483A-AAD4-1CA021357A15}
MARIPOSA 2102CB | {D6398899-238B-49AC-A776-D1F3468DFF9B}
MARTELL 110111244 | {1C7FE5E5-6F77-424F-9AD6-00935E8D6AAF}
MARTELL 110111244 | {E154310E-F1E3-4CE7-BE08-29FE6DF23F68}
MARTELL 110111244 | {FC415CBA-4F79-4B55-9784-C587178D6775}
MARTELL 1101131918 | {AB585BA2-D7AE-4831-B533-45E5CAF35C33}
MARTELL 1101185268 | {9AC31B24-B4F5-4AE8-AF6A-88CA4695FB5D}
MARTELL 1101250060 | {8F8995FB-51DC-4122-872F-27F17EF06719}
MARTELL 1101473004 | {8976069E-D4D6-425D-AFC7-6113345355FC}
MARTELL 1101532836 | {2C34AC51-01A3-44C9-B45A-F5786A7BA8F0}
MARTELL 1101766574 | {2486729F-70E5-4A37-897B-69C2538DBD37}
MARTELL 1101803328 | {2C34AC51-01A3-44C9-B45A-F5786A7BA8F0}
MARTELL 110191216 | {D45B581C-2481-4A42-9A4C-E2D220FA09CF}
MARTELL 110191216 | {87487AB6-EDDD-493A-85B9-178FFED1F365}
MARTELL 110191216 | {111B8F03-A7A2-4ADC-B553-BFBB68F5B187}
MARTELL 1101915018 | {31785B7F-FA02-4970-9573-C491E47D5BE1}
MARTELL 1101954148 | {7B128A46-1F2F-48C4-9640-C140330A42DB}
MARTELL 110198374 | {277F84D3-A270-449A-A58E-FDC1A84261F4}
MARTELL 1101CB | {2C34AC51-01A3-44C9-B45A-F5786A7BA8F0}
MARTELL 1101L581 | {6EF707FE-238A-4BCF-B570-3F6EFE98BD7F}
MARTELL 110292172 | {90FE2AC1-F695-42FF-8EBC-FB82E3B206C0}
MARTELL 110299214 | {9F8CA5FE-A9BA-4EDC-994E-2CFB4235B5A0}
MARTELL 1102CB | {74DC8F54-4589-4421-89BC-E98BD5920B33}
MARTELL 11033152 | {138F1A45-4EE4-407C-9580-B6FBC2BCEC83}
MARTELL 110368192 | {2D2F9EB5-C573-4256-A9F2-6087D93C70C6}
MARTELL 1103CB | {4DC1CEF2-A050-43F8-AD47-CFA46D056F9F}
MAXWELL 11023306 | {F1C1856B-ECB8-4CF9-A778-CDB8457E4724}
MAXWELL 11053008 | {3FFCF8AB-2F3C-40D6-BE9B-68EE284722AE}
MAXWELL 1105429752 | {082FCFA1-C818-47BE-854B-960BF53ED50D}
MAXWELL 110545180 | {1605C97C-6AE7-4F3A-B791-60E70E668925}
MAXWELL 1105910362 | {F3456836-F540-4C5A-8C4E-BB2A14482B86}
MC ARTHUR 11011488 | {62976FAC-DE1E-4247-A5CB-A153442821DF}
MC ARTHUR 11011490 | {36BB4228-C5D9-43D2-9CAD-2C575004638F}
MC ARTHUR 11011492 | {4752BF93-70F8-42FC-8D3A-033549B0C98A}
MC ARTHUR 11011544 | {2548B457-03C9-4EEF-9E95-D0AA3CBA5A67}
MC ARTHUR 11011546 | {F58DF78A-C4B0-4969-9413-98D7022EFF8F}
MC ARTHUR 11012127 | {AFBEEDE5-7B55-434D-9A27-12DA2A0E0EE0}
MC ARTHUR 110137344 | {385A8486-C3EA-4FD6-BFA5-2F73ECF426BB}
MC ARTHUR 110137388 | {94162D16-0097-44C8-A147-FCAA580DD744}
MC ARTHUR 110138998 | {FAF0B739-3196-4C1D-A8BD-B6B12F707FEC}
MC ARTHUR 1101501106 | {FAF0B739-3196-4C1D-A8BD-B6B12F707FEC}
MC ARTHUR 110151398 | {85EE7B40-6D93-48B5-9C94-EBAACB072BA9}
MC ARTHUR 110153120 | {4F05ED84-FE56-4A90-8DC4-86D939A68626}
MC ARTHUR 1101648698 | {21F41FBB-70A7-4D16-B9FC-2C23C6369432}
MC ARTHUR 1101CB | {180C9221-B3D3-4A32-9DB9-CD8B7E0EF9F1}
MC ARTHUR 11021324 | {76F913B6-6D49-4D3C-ACC8-2AE24DFE45A2}
MC ARTHUR 1102542920 | {937AC6EE-B826-41A2-9509-4DF206B104A5}
MC ARTHUR 110290546 | {E9334D2F-2952-4052-8ADD-E3F42DB77666}
MC ARTHUR 1102CB | {29D96E6F-9A6D-4E41-9CE1-0E9E869E48D9}
MC ARTHUR 1102LR-RC-B | {E9334D2F-2952-4052-8ADD-E3F42DB77666}
MC FARLAND 1104521389 | {966A7A57-0F79-4428-9CDE-30D6221B3591}
MC FARLAND 1104950506 | {966A7A57-0F79-4428-9CDE-30D6221B3591}
MC FARLAND 1104956589 | {966A7A57-0F79-4428-9CDE-30D6221B3591}
MC KEE 1103333750 | {91B9F546-2D22-40C9-BFB6-88E720FB1011}
MC KEE 1103XR028 | {58E90993-9BBD-4F51-9BA9-AD36025808B4}
MC KEE 1107827486 | {625462C6-F8FB-4C1B-B9B9-64AC08211124}
MC KEE 1107864438 | {4E527F6D-26E0-4009-9296-E811BA39763B}
MC KEE 1107XR010 | {20665159-98AB-48BF-884C-B94C1C98F219}
MC KEE 1107XR032 | {22D0F857-9929-4CD2-9E4F-9210026EF7ED}
MC KEE 110870535 | {AD405CD0-0159-4CF6-B66D-D87E1CD73921}
MC KEE 110870535 | {41444F7B-0DEF-4E7D-BF1A-12A503159CC6}
MC KEE 1108XR302 | {41444F7B-0DEF-4E7D-BF1A-12A503159CC6}
MC KEE 1111247498 | {7D5CF815-4517-41ED-97D9-FB9721A1C53C}
MC KEE 1111711900 | {E158EBD1-D391-40F7-8D5C-4284F51B8199}
MCKITTRICK 11011639 | {CF351289-EF61-423E-A18B-8E646FDACDC8}
MCKITTRICK 11013043 | {3078A06A-2742-49B3-A8D3-BF979882EC92}
MCKITTRICK 11013092 | {E42ABE56-6A07-4884-B2A8-6BC8E84F5CDC}
MCKITTRICK 1101CB | {5A307946-5CD5-4050-AB0D-2E455B17B341}
MEADOW LANE 2106939564 | {640C66CB-1E65-4825-9593-E8C96FF126EE}
MEADOW LANE 2106970936 | {9C56F556-90B8-48FA-A28A-448032E1972B}
MENDOCINO 110137462 | {CBF297F1-D8F4-467D-B156-4EC62C764040}
MENDOCINO 1101450 | {8EF50422-5CB8-4728-A990-D408AE9FCE63}
MENDOCINO 110148750 | {EF680142-96BC-4632-8839-A0A3D923AC61}
MENDOCINO 110148750 | {231ED2BD-442D-4404-82B4-62A021EDEE46}
MENDOCINO 110148750 | {ACEBC5C5-BAE3-4674-A040-F1DC8C4CB67D}
MENDOCINO 1101856020 | {20843552-BA63-4B51-9A53-4527FFEFC797}
MENDOCINO 1101CB | {D8D35F92-2CE4-473E-A048-B7A252678CA3}
MENDOCINO 1102CB | {988CA71C-AB6C-46A7-920F-6295BBF50876}
MENLO 1102151590 | {57607E85-0D9E-4982-8503-00EDF257DC69}
MENLO 1102154024 | {C583B40D-86CD-4D00-B0BD-8B42D03F7715}
MENLO 1102154024 | {3C63AA14-693B-4374-A5BC-A622EB2CBC64}
MENLO 1102223286 | {ADCE2FC0-63B1-4997-AA36-C71BC01F8536}
MENLO 1102331044 | {86766416-7CB2-4969-8319-B838E7BDEB74}
MENLO 110235722 | {56AE0E26-A1EF-48A8-89D1-72A26BF969A5}
MENLO 1102362896 | {9ED0F88A-605E-4781-B4F8-A8FEAF104BB5}
MENLO 1102560798 | {40A3EEC5-BC62-4BCA-9E0F-FACC864439C1}
MENLO 1102628458 | {8DAF1791-FC97-4AAB-A29C-384C99616E7D}
MENLO 1102698072 | {FB457E3D-350F-44AA-9CE8-9F443B24091D}
MENLO 110276134 | {581EB12F-F067-4403-8173-E6BC4FBC1270}
MENLO 11028952 | {56C84CD8-CFAF-4218-882A-B93134A396EB}
MENLO 11029018 | {BBAE707F-556D-4202-B6A5-623E650EC155}
MENLO 11029092 | {CB7FED94-E514-4F6A-B3B1-FDD03272551C}
MENLO 11029110 | {2ADB84B9-4752-4713-BF49-15F96D94E1DF}
MENLO 11029110 | {4FA0951E-FDEC-4E9C-847F-B2E9B3A5118A}
MENLO 11029152 | {6B11615C-09AD-4BEB-BBFF-976212C3FB13}
MENLO 11029152 | {844542AF-23E3-4A9F-A1D2-E72C86286BF7}
MENLO 1102W80 | {82B72724-3F36-4DE0-AF4C-310E9BC3E997}
MENLO 11031721 | {6C22C535-7647-425F-9042-42388B8EC195}
MENLO 110358562 | {7E0C3FCE-17F5-4308-9D58-E63D0E2C9C4E}
MENLO 1103612726 | {F59FFFCB-61EE-4D75-A400-1E8CBED75381}
MENLO 11038512 | {8F9D0578-4CB4-4781-89AC-7B1C36D45FF0}
MENLO 1103866118 | {6C22C535-7647-425F-9042-42388B8EC195}
MENLO 11038982 | {122C7DAC-AC52-4005-A738-CAEFD4E1581A}
MERCED 210190272 | {262423F3-51D4-4C54-A6B5-FBFB42443667}
MERCED FALLS 110222774 | {A07075F3-76AA-4FC7-9158-0930DA76C5B7}
MERCED FALLS 110238748 | {E473F3E7-4790-4E95-BFB6-2DFAB51C8E70}
MERCED FALLS 11024000 | {8DA8BDD3-B9B9-42D9-AC7D-1174537479B6}
MERCED FALLS 1102482838 | {A07075F3-76AA-4FC7-9158-0930DA76C5B7}
MERCED FALLS 11027006 | {3C66AA6E-AAFB-4AC9-BCE9-F89CAFA6091F}
MERCED FALLS 11027905 | {3C66AA6E-AAFB-4AC9-BCE9-F89CAFA6091F}
MERCED FALLS 110285002 | {9E750160-198E-4DE4-9B67-A39CCFF98BD9}
MERCED FALLS 11029460 | {BFEABD68-387F-42F6-B83F-CA958769EA41}
MERCED FALLS 11029470 | {C35DFEFE-AAAB-47B8-ACD8-3B6A331D2855}
MERCED FALLS 1102CB | {3C66AA6E-AAFB-4AC9-BCE9-F89CAFA6091F}
MERIDIAN 11013002 | {708506A2-3F9E-48C9-B8FF-C68CA14E1DF2}
MERIDIAN 11013044 | {09A55B83-054B-4D44-91CC-186E49A9EE1A}
MERIDIAN 1101417104 | {09A55B83-054B-4D44-91CC-186E49A9EE1A}
MERIDIAN 110169484 | {9188B118-5EF7-4E54-9BAE-225451A81DCD}
MERIDIAN 1101CB | {708506A2-3F9E-48C9-B8FF-C68CA14E1DF2}
MERIDIAN 11023502 | {F8B524B7-E7EA-40DB-B242-2D94826225BF}
MESA 1101573430 | {B178BCF6-D522-494D-A6D8-E92359D72956}
MESA 110187454 | {7AEFEAB2-E3BE-40E9-8819-39DFE1CE52D4}
MESA 1101CB | {C61DB78B-3364-4B90-90AD-4E89668B63A7}
MESA 1101M86 | {8CD02839-6B9C-4A4E-A161-AF3A96F4F1AB}
MESA 1103126697 | {431342B2-8FA7-4C4E-B028-5E0C383A0588}
MESA 1103198354 | {B4A32525-0F6A-4115-92BB-FAB77AAEE5A6}
MESA 1103206794 | {2D61F936-7E2F-4C15-BB46-31C6DC2ADC03}
MESA 1103236053 | {C0ABDB73-42C4-4D60-9BB1-4077EF0BE355}
MESA 11038647 | {6E34D557-FB41-44E6-B10D-DE75166431A4}
MESA 1103890906 | {A7A1BDD7-02E1-4E33-81E1-2D0A5474089C}
MESA 1103890906 | {1D9768AD-9367-4361-8E84-3FE59F96E5B9}
MESA 1103890906 | {B3ACAA65-1E5A-4912-9AC5-AFDE7402E787}
MESA 1103M62 | {A1CF0EFC-4EE4-402B-B14C-F1C9D9E90F01}
MESA 1103M64 | {88268CAB-906C-4CD2-A318-8F214ED37905}
MESA 1103M68 | {A25F3E5B-484A-4624-AB7F-2585CAD6EACC}
MESA 1103M70 | {351C606D-5ACB-45C9-B1DD-61D69C884CAD}
MESA 1103M72 | {C0ABDB73-42C4-4D60-9BB1-4077EF0BE355}
MESA 1103M90 | {6E34D557-FB41-44E6-B10D-DE75166431A4}
MESA 1103M92 | {2DBCA866-9F0D-46E8-B9B3-4863FA94560D}
MESA 1103Q18 | {C0ABDB73-42C4-4D60-9BB1-4077EF0BE355}
MIDDLETOWN 1101128648 | {B7C3ED67-9905-41F0-81DC-45B8DE5466D9}
MIDDLETOWN 11011314 | {6605C9B9-1E01-4CAA-B9F4-139E3DFEC103}
MIDDLETOWN 1101148104 | {C09DA2D7-2214-4F88-820C-9055AA0CEA6E}
MIDDLETOWN 1101171414 | {BC096842-FB68-47C6-A8DF-53E2AF52BFF3}
MIDDLETOWN 1101352182 | {AEB7C7BA-C773-4591-86C0-9A5CE1531025}
MIDDLETOWN 1101433160 | {335DA010-DDD8-4033-B175-13202F25D46A}
MIDDLETOWN 1101439572 | {30AF65A1-8215-4D53-AAD5-8454B0E2F1C0}
MIDDLETOWN 11014646 | {9CD0DE6C-67D0-4975-9926-0CEC6137D8E0}
MIDDLETOWN 1101481876 | {218A19AE-6FB1-4AFF-A311-4C487EC96852}
MIDDLETOWN 1101548 | {FDE70F79-A0AF-462E-BB5B-4452D639325B}
MIDDLETOWN 1101548 | {F67E867C-FC38-4763-8DCC-25139EFCB73A}
MIDDLETOWN 1101614 | {8C7E457A-F935-48E0-AE77-B73661F39EFF}
MIDDLETOWN 1101644756 | {ADE0CDA9-E9B6-443E-8AB2-EB2705916002}
MIDDLETOWN 1101644756 | {D8404B1C-6CCC-4D8B-B9BD-7DBA7207B8E8}
MIDDLETOWN 1101644756 | {67FA5D3B-5BFA-40EE-AABA-659446964531}
MIDDLETOWN 1101657227 | {33B20BA4-E0F8-473B-84B7-87E2DDE0946B}
MIDDLETOWN 1101829164 | {2CB71B6B-D27A-41C2-BF19-6EE1B740E120}
MIDDLETOWN 1101868642 | {F542B53B-B7D1-4181-8F2D-4374C4B2D2DB}
MIDDLETOWN 1101872796 | {BEAAD6A3-94CD-4A11-9128-481E49933A68}
MIDDLETOWN 1101932140 | {50574C53-8D5E-4BF8-9D16-15E783D9947A}
MIDDLETOWN 1101959140 | {7B530842-C667-418B-ADA6-859E3E2891D3}
MIDDLETOWN 1101CB | {302C19E7-740B-49C6-83EC-9E70AC44D5CB}
MIDDLETOWN 11021312 | {2AF9EFB4-6308-47EE-AE0E-E474555BF1F9}
MIDDLETOWN 1102302610 | {74046CD3-77C7-457E-BE42-30FCD99C2435}
MIDDLETOWN 11023675 | {4726CCBB-2E0F-46BD-89BF-404DF49589FC}
MIDDLETOWN 1102414 | {01278228-324E-4DE9-A0E4-67F4CFACFDAB}
MIDDLETOWN 1102620498 | {485842B2-3086-4FF6-AAD4-021AB6CC5E2E}
MIDDLETOWN 1102632616 | {6706FB06-E99E-4FD6-81B6-1021C827BE95}
MIDDLETOWN 1102829548 | {07734FA5-818F-4056-8B78-D9186695FAC6}
MIDDLETOWN 1102878 | {41D0BC1C-9410-4D80-BAA4-E58808DC7687}
MIDDLETOWN 1102998 | {5F8C3D5E-6EE2-44BA-8DAB-1423918270D0}
MIDDLETOWN 1102CB | {7E69B413-A223-4CCD-AF98-CC3C74EA7FDA}
MIDDLETOWN 1103116930 | {6DC638BC-11F4-411C-8349-7667AAF4D7BC}
MIDDLETOWN 1103248100 | {D0A34963-C00B-473C-A62A-FDF87E0E3F8A}
MIDDLETOWN 1103248100 | {BFCA66E2-7174-4D82-9BEB-7987B154BF74}
MIDDLETOWN 1103762090 | {32E7D0CF-C321-47A0-BEF1-9DB8DDDC7A60}
MIDDLETOWN 1103CB | {EF7692CE-6490-45CF-89E0-AAC63F03AECA}
MIDWAY 11021401 | {6EB1AC34-861E-430A-9A05-9A7E1B973E2F}
MIDWAY 11021482 | {1AD1E0A4-D167-48B1-A117-ECD57A27B620}
MIDWAY 1102CB | {6EB1AC34-861E-430A-9A05-9A7E1B973E2F}
MIDWAY 11041497 | {69DE941E-36EC-4F81-85A1-186D6F371469}
MIDWAY 1104CB | {69DE941E-36EC-4F81-85A1-186D6F371469}
MILLBRAE 1104217 | {9C8D4BDE-AD71-48F6-A8FD-CAFB10D66061}
MILLBRAE 110453676 | {78D6C5D5-9F2A-45C6-A0D6-6C9E91038F45}
MILLBRAE 11045521 | {29B1D2E9-693D-479C-A160-99B72B4A4B3F}
MILLBRAE 110465748 | {9C8D4BDE-AD71-48F6-A8FD-CAFB10D66061}
MILLBRAE 110480106 | {BCA1AB36-1D1B-41D7-93BD-733AB9EA3274}
MILLBRAE 110810045 | {D144CF0B-F99D-4FA8-AE9A-F2C7682917BD}
MILLBRAE 1108639978 | {8FFF56B3-5742-48DE-8779-85060D8D7011}
MILPITAS 1105CB | {CA512FE5-1127-458F-8A35-7AA6286C673F}
MILPITAS 1105CB | {948C67E5-4E11-4F26-9822-D0D64051E31D}
MILPITAS 1106CB | {C3BB54D6-DE18-46BA-897B-998B3127F4EA}
MILPITAS 1108342498 | {89380520-9418-4EBF-BBE0-5B16221F5D8C}
MILPITAS 1108819378 | {CEA38244-9552-4630-967D-EBD8BC18D96E}
MILPITAS 1108CB | {7055FF43-DD9D-44C9-B3AE-9B73AF61A173}
MILPITAS 110913377 | {1740BDF2-252E-4BE4-939F-62DEFAA0C011}
MILPITAS 1109500490 | {DAB4DBF5-4816-4B32-9586-1BB87E6897A3}
MILPITAS 1109694832 | {47C2DB41-4B2E-4D4E-8839-9BAAAABDE275}
MILPITAS 1109903328 | {A7915D22-0E00-4421-A3B1-BE44A2D7B2FC}
MILPITAS 1109903328 | {6577B24E-0FC5-4239-89A4-458F673DCDA9}
MILPITAS 1109XR044 | {AAFA242E-CE7C-45BF-A927-201DEB4735C4}
MILPITAS 1109XR208 | {1C76A5CB-14FE-4796-B246-F53503C2A0BB}
MILPITAS 1109XR370 | {1740BDF2-252E-4BE4-939F-62DEFAA0C011}
MILPITAS 1109XR374 | {0C3DEB50-B6B5-4438-9654-82B0930BBF12}
MILPITAS 1109XR524 | {648B5D01-67D3-492E-989C-FF81490722DD}
MIRABEL 1101116 | {1FA8A5B8-216C-48A5-8B5C-D037DBE66063}
MIRABEL 1101228 | {42913E65-3605-4DBB-8857-B0B0965C9EAC}
MIRABEL 1101254 | {E6BD4324-CEC6-41E3-9006-EBD82C1FE66D}
MIRABEL 1101298 | {6CAAA373-43C9-4B25-82DD-98B4367AB548}
MIRABEL 1101298 | {1B23A4BA-CD57-4FC0-AB6D-FA127475AD96}
MIRABEL 1101310814 | {E210DFEA-B056-4D88-92EC-8046409B3438}
MIRABEL 1101688780 | {47D4786A-45B9-45D8-AF62-3522AA9D4ACB}
MIRABEL 1101774276 | {D2D7F3DD-F11E-4D5D-B608-61ABEEEF3513}
MIRABEL 1101774276 | {403F76F2-1613-4EA6-AE9B-C646D2E770BD}
MIRABEL 1101831090 | {1FA8A5B8-216C-48A5-8B5C-D037DBE66063}
MIRABEL 1101CB | {8146354A-DBE2-49BD-B0E6-646A6C01C7BC}
MIRABEL 1101CB | {0DAF681A-D0A6-472F-BDFE-814CD10BFA9B}
MIRABEL 1101CB | {27F10E9B-AFB8-46BC-9219-36028EB8F5A3}
MIRABEL 110213669 | {1A66B03F-EDFF-4D22-AE4F-0AD5445AD8C3}
MIRABEL 11022043 | {76DCCACD-E9DC-40E0-8CEA-2EC1A63EA736}
MIRABEL 1102206 | {3FDFEE62-2564-4B56-8AC9-FC80D427FADF}
MIRABEL 1102332 | {98884EB6-8FFE-4527-976C-FBFB7D667FB9}
MIRABEL 1102334 | {0A4816B0-BB69-491B-8E9D-476A9DF6F15C}
MIRABEL 110238514 | {76DCCACD-E9DC-40E0-8CEA-2EC1A63EA736}
MIRABEL 110238514 | {06DAEC22-1F82-4797-A863-26EDE54ED9B9}
MIRABEL 110238514 | {7C9E0EEA-95C0-41CC-9185-303F6237320D}
MIRABEL 110238514 | {A5155BE5-9970-4D8F-96F2-81F9FC945582}
MIRABEL 1102503000 | {4C64A62F-2F33-4421-96E8-EA9C4D2FA031}
MIRABEL 1102503000 | {02C10BAA-6FFF-4F80-AE34-8D1403D92CC8}
MIRABEL 1102503294 | {F1ABA083-74D1-4C3F-BF47-7B099CCA3C8E}
MIRABEL 1102524356 | {93EAC16B-EBC7-4B14-81C7-36C500A3A6BF}
MIRABEL 110257840 | {BDF5B432-76F8-4E7C-875F-0CD4088812BE}
MIRABEL 110286326 | {F24A6BFB-F462-4C79-8226-3FA35A366957}
MIRABEL 1102976908 | {EFEDE1C8-AA0B-47C4-96EE-71FB2C33E43D}
MIRABEL 1102CB | {C5E1652A-2EB6-4FD0-B328-E1AC1FDEB33B}
MIWUK 170110600 | {38AAAE1F-7053-4022-8941-265790AA8F13}
MIWUK 1701176798 | {E8F5F8AF-6EC9-4C69-835B-E53C764AC834}
MIWUK 1701360164 | {E8F5F8AF-6EC9-4C69-835B-E53C764AC834}
MIWUK 170153038 | {AA9722DD-9A20-411C-A91B-FCD027C3242A}
MIWUK 1701655408 | {DF4C3567-FA26-402A-B5C5-C5AE61B0EA03}
MIWUK 1701767890 | {BB39A9FB-82F3-4CEE-812A-8BCB11B79244}
MIWUK 170179118 | {7A676B71-51F1-4DF0-A596-B3D6F63218D3}
MIWUK 170193062 | {5066A7AC-53DE-4397-A56D-0A1D62BCA2F8}
MIWUK 1701953336 | {778380F2-BA49-477B-8F0F-740FAC39A283}
MIWUK 1701992162 | {8E98014F-A627-491D-9EDE-59105F8979E1}
MIWUK 1701CB | {E8F5F8AF-6EC9-4C69-835B-E53C764AC834}
MIWUK 17021808 | {E7E37BA6-3C2D-44CF-BA17-835379EB57EA}
MIWUK 170236888 | {5E0E9C3F-102B-4736-867B-523AEBC69611}
MIWUK 1702380860 | {24F2F315-9710-4B47-91DE-CD05D22EA418}
MIWUK 1702380860 | {343ED350-C8C2-4BFC-8844-DCE1062B84DF}
MIWUK 170238218 | {F58ED19F-5908-4BB5-B91D-2DADB171168F}
MIWUK 170238218 | {A925E51A-5FAE-43F8-8B37-99BC26B877A3}
MIWUK 170238218 | {A068179F-B6CC-4678-A4EC-AF469032942C}
MIWUK 170247143 | {976CA043-61DE-4F22-87BA-0696E25C4DF1}
MIWUK 1702531976 | {29DBEF63-7B51-4C6A-A786-292EB9177451}
MIWUK 1702576504 | {0C4CD1BE-E231-46BA-AA07-10AAA7A9A5DB}
MIWUK 1702667248 | {A068179F-B6CC-4678-A4EC-AF469032942C}
MIWUK 17028130 | {88A44AAA-C023-4024-A42C-99C58CDC9C64}
MIWUK 1702823548 | {F8C7B33C-BEDE-4CA6-95F7-A9AC738157CF}
MIWUK 1702823548 | {DE713724-4753-42EE-87B5-64C0693236F8}
MIWUK 17029270 | {AA0F2742-8D52-435A-9889-3CD8160159B6}
MIWUK 1702CB | {5DE457D9-5E7A-46A3-820A-688DCA33A9BB}
MIWUK 1702S2247 | {A068179F-B6CC-4678-A4EC-AF469032942C}
MOLINO 1101128824 | {3F3D20C0-ACFF-4762-8BCF-531C75A983F8}
MOLINO 1101152 | {366DDD05-C36C-4018-8E0C-E1718F820EB6}
MOLINO 1101277292 | {73A79C1D-983A-4279-A3FD-02A1B497A62F}
MOLINO 1101322 | {87C4E1DE-229A-456D-853B-731F9308D34F}
MOLINO 1101338 | {4502A0E5-A181-4FD0-A72F-EAB91B5F9EA1}
MOLINO 11014900 | {5231DB16-86D1-4843-83D5-814DD0192BCB}
MOLINO 11015034 | {5092CF9F-9D4A-405D-A02E-8142B89FC3A4}
MOLINO 11015042 | {D0E3F376-32D7-44BE-A845-A1142386C6AA}
MOLINO 11015042 | {D5D881FC-5E37-43D0-8EE8-25189C47D57C}
MOLINO 1101600112 | {561785C2-9342-42A6-8DBE-3ACD64E05D9A}
MOLINO 1101891 | {3F3D20C0-ACFF-4762-8BCF-531C75A983F8}
MOLINO 1101981740 | {0313741D-5EC1-4A00-B068-24D51DF3EBCF}
MOLINO 1101CB | {F8D0A5CD-F859-4FB9-9BDE-10A27882B6F9}
MOLINO 1102104 | {6BDF733D-8276-4FAC-977E-D46B41E69D11}
MOLINO 1102104 | {A9956E8E-82E8-4F15-86A2-41CAA5FD625E}
MOLINO 1102104 | {7D5BEB0A-06FF-4975-900C-BDCD4AFAA92D}
MOLINO 1102111666 | {2D9442B3-0FEF-4574-B297-2133787A6E1D}
MOLINO 1102141782 | {447B8131-1050-400E-81F0-E893F64CB384}
MOLINO 1102178 | {E011217D-F6B4-46C8-AC6E-B5F7ADEBD850}
MOLINO 1102178 | {52846ED2-3EF3-4ACD-B861-D51B3045E38F}
MOLINO 1102178 | {B946CC4F-A783-4D40-B2BB-6052840D6616}
MOLINO 1102344 | {A98FD5E2-DDE3-4E25-9F0F-483626AE2A81}
MOLINO 1102381468 | {60856F33-F69F-483D-A29E-5E684F09BD0B}
MOLINO 1102384 | {7FCADEEB-07B1-4335-8044-26A9BB50B5B5}
MOLINO 1102396212 | {937FE0BF-1949-4B31-99B0-C96DCB7F5DAB}
MOLINO 1102396212 | {6EEEC128-F12C-4E4F-90C6-10C765F9D8A1}
MOLINO 1102396212 | {DED611C5-BAFC-4BE0-804E-A780281DF8D8}
MOLINO 1102396212 | {3657E8A3-A103-4E90-9D5B-BFA3EA5F044A}
MOLINO 1102396212 | {CD2F7D4B-17DD-4B3E-B6B2-699CA2B6C23C}
MOLINO 1102396212 | {DB92DEC2-EF43-4597-BEB8-09E6C81EAC35}
MOLINO 1102396212 | {15DED5F7-9D08-40F6-BFAD-B663D45B0755}
MOLINO 110241392 | {447B8131-1050-400E-81F0-E893F64CB384}
MOLINO 1102485246 | {19FDD057-3D59-40B5-B132-CF89CB4144D2}
MOLINO 1102495692 | {38F7A409-B733-4A66-AD23-141CCDD939A2}
MOLINO 1102509516 | {1740079B-33AB-4B93-9EE4-D9DB46F4F893}
MOLINO 110251788 | {E88FFA7F-5F70-49D0-8DB1-373E7BB1124C}
MOLINO 1102535 | {3827F6F2-326F-4FCC-9EC1-DB4311EC910A}
MOLINO 1102613993 | {2F38AE04-1F96-44F3-B945-95C6CEDBB2B8}
MOLINO 1102658 | {08F3C995-4373-4EBD-A7D7-6CA08BB9F56E}
MOLINO 1102658 | {F138D9D4-46B7-40FF-98A4-3E0C55CB9A57}
MOLINO 1102658 | {3D43B11F-E0A3-42B9-AA78-A5A3D2CA62D8}
MOLINO 110266006 | {4AE7AB5F-C633-47AF-9F7F-61FE17B35998}
MOLINO 110266006 | {D72D6482-4E6D-4BCA-A18E-EC66B66F6D46}
MOLINO 110266006 | {EC4904F5-03CD-4A22-8022-1A704A44E57D}
MOLINO 110276066 | {8614D223-F481-4626-858F-622D47A98A6F}
MOLINO 110279306 | {B81A8616-55B2-41F9-9829-B699E6A06290}
MOLINO 1102878600 | {AE260BB9-E68C-495E-977F-D1DA4DA3D9D3}
MOLINO 1102905231 | {96DF56B4-09D9-4632-A84A-99B69DBE4320}
MOLINO 1102CB | {3827F6F2-326F-4FCC-9EC1-DB4311EC910A}
MOLINO 110313219 | {8EB3D47B-33C5-4BF9-8478-86504EAE804F}
MOLINO 1103407204 | {F9E057F8-6AEB-429D-A2C3-0345582960C3}
MOLINO 11034676 | {8EB3D47B-33C5-4BF9-8478-86504EAE804F}
MOLINO 11034682 | {7E159FF9-AE0E-42BB-9017-B4F3ED37EEB9}
MOLINO 11034894 | {AC40E023-4A81-4908-BE46-066808454E49}
MOLINO 110361850 | {7E159FF9-AE0E-42BB-9017-B4F3ED37EEB9}
MOLINO 110381008 | {7E159FF9-AE0E-42BB-9017-B4F3ED37EEB9}
MOLINO 1103CB | {81938758-C680-45F4-959B-309DC169CCCA}
MOLINO 11043281 | {5465105C-2E1E-47CE-8A44-120776A3EE22}
MOLINO 1104368158 | {4E9FB77B-2DAB-4C16-84CB-10ABD5B12CA4}
MOLINO 1104380 | {5465105C-2E1E-47CE-8A44-120776A3EE22}
MOLINO 1104468882 | {8788BBFA-A2B3-4787-825E-E3E47FE6B9D7}
MOLINO 1104543014 | {2B80AF07-90F9-45E8-AD8D-FB4C032E2538}
MONROE 210290988 | {0EBA2BBA-1703-4B1A-B59D-EED82556C743}
MONROE 2103408 | {B8CC27E9-A307-4877-A8E2-3DCDDA24938D}
MONROE 2103848530 | {AD6C9BC3-922D-4820-9E11-0EE6E0677452}
MONROE 210392868 | {18B04DCD-9DDD-4C1C-AC8D-731B4880D7B2}
MONROE 2103CB | {D546C25E-2665-4E0F-83E6-19A6D0D70A7D}
MONROE 2107380760 | {744357E4-A039-4634-8800-C090FE5B1DFD}
MONROE 2107428720 | {3D15A0FB-7F79-449E-9100-AEDACD615B82}
MONROE 2107434 | {93AD8822-3B34-4022-AD3B-499AD2080376}
MONROE 210765424 | {3D15A0FB-7F79-449E-9100-AEDACD615B82}
MONROE 210781174 | {93AD8822-3B34-4022-AD3B-499AD2080376}
MONTE RIO 1111140 | {D0D0E128-BFAA-40E9-9195-426CE62EA884}
MONTE RIO 111118253 | {EF7677D5-4C2B-40B6-B19A-E56006D1140B}
MONTE RIO 1111240 | {561B7435-E1A2-417A-BAD2-8DB925A728A4}
MONTE RIO 1111256 | {96BB4CA1-5E7C-4F0B-8472-F8BEE67F3E07}
MONTE RIO 1111292 | {2ABCFF42-2755-4831-9FA6-A7C95D1C294C}
MONTE RIO 1111292 | {1D70FB5B-E2A1-40FC-85C8-0C22D5526774}
MONTE RIO 1111292 | {E76F208E-D030-4954-AE4B-2E5BE9D9580C}
MONTE RIO 111137520 | {70221EDA-53E0-475E-B32D-2C80E9C74C87}
MONTE RIO 111137520 | {C0868086-2AE3-4A05-90EB-BF1D6E5F34F7}
MONTE RIO 1111506 | {C4F8319D-D897-4280-8AA8-30DB11490475}
MONTE RIO 111159046 | {96597AB7-8D9B-480E-B290-054AD97D3E7A}
MONTE RIO 111164758 | {229B38F9-4F6B-4F27-9C49-8D8B28596070}
MONTE RIO 111164758 | {173229A0-9A6C-4AB5-8BBC-51112D47DF20}
MONTE RIO 1111969182 | {00ACF5D2-3F52-4898-8741-EAC69506A35F}
MONTE RIO 1111969182 | {CFD49D25-5A97-4913-B570-E644DBC2B01E}
MONTE RIO 1111CB | {149DEC4B-D1C4-4F4B-922B-9B5C5A4AE0D1}
MONTE RIO 1112212 | {6F2B0102-5A32-46BE-814E-00713C2AB90D}
MONTE RIO 1112387984 | {9876A917-1407-4DF0-AF3D-654F5186EFE4}
MONTE RIO 11125040 | {2864C93C-BF52-4E0B-A5D1-FA5019DBF7C4}
MONTE RIO 1112547 | {FD227C55-02E2-42C5-8E89-FEDFC826A5D0}
MONTE RIO 111264682 | {C18B3D99-9D55-4106-9075-3E8FCDD6E228}
MONTE RIO 111264682 | {DD8BA615-FFBA-48E9-84EA-5D20532CD959}
MONTE RIO 1112933718 | {70E55192-7CAB-4C64-83AD-55CAA307DD8A}
MONTE RIO 1112933718 | {BA751F90-4970-4A71-8AFF-D081305649C1}
MONTE RIO 1112938174 | {D361D503-3790-453C-B66D-A7A3345502F7}
MONTE RIO 1112CB | {78AB2FDD-E1CA-4DC9-8362-0759A43BD212}
MONTE RIO 11131067 | {3F69DD3E-C46A-485A-8A4E-8252A760746F}
MONTE RIO 11131313 | {2E6DCA70-6B36-4F65-B853-AA4AC3CF0E30}
MONTE RIO 1113180 | {15C2C6AB-DE9A-4E17-8C2D-97DC9B78100A}
MONTE RIO 11131989 | {EA690835-9E38-4D73-A546-B5676BCE1BEA}
MONTE RIO 1113202 | {06C5DDF3-68CB-4362-94D6-24163B7FDD9B}
MONTE RIO 1113250 | {F3C44BD4-C837-40EB-9584-B17B6404063F}
MONTE RIO 1113320 | {EF630F9A-72E2-42EA-B074-23D3C9859856}
MONTE RIO 1113346 | {EA690835-9E38-4D73-A546-B5676BCE1BEA}
MONTE RIO 11133970 | {53EC2261-1200-4127-A3BA-F52DA74219E3}
MONTE RIO 1113439254 | {3A330D41-F506-49D1-A8AC-21EA6FC6FDFA}
MONTE RIO 1113477 | {3F69DD3E-C46A-485A-8A4E-8252A760746F}
MONTE RIO 11135020 | {C3FAC8CF-A105-47CA-BAFD-6A205D726950}
MONTE RIO 11135024 | {3F69DD3E-C46A-485A-8A4E-8252A760746F}
MONTE RIO 11135026 | {2E6DCA70-6B36-4F65-B853-AA4AC3CF0E30}
MONTE RIO 1113524 | {8C8983C8-884C-4E70-BBB6-36F59CD80D78}
MONTE RIO 1113539938 | {3188B2E2-9541-4BE0-B86F-D0DD55D6F8F8}
MONTE RIO 1113652 | {1A58D4D4-08C9-4897-B970-7F34BB31F59C}
MONTE RIO 1113678 | {3C769364-EC40-4452-9AEF-32B476BC5146}
MONTE RIO 1113678 | {F763F6AF-FC97-4F89-AD25-F9455AF541C2}
MONTE RIO 1113801 | {69ED90A9-D7CF-4B59-8DE4-A67EE0393C1B}
MONTE RIO 1113CB | {C3FAC8CF-A105-47CA-BAFD-6A205D726950}
MONTICELLO 1101130412 | {50BA7E67-5EAD-4941-88EC-76A715C41286}
MONTICELLO 11011780 | {4904A78C-4F30-4D7A-889F-B688535D7066}
MONTICELLO 1101256640 | {50BA7E67-5EAD-4941-88EC-76A715C41286}
MONTICELLO 11012659 | {F6417896-ABE0-4AD6-BEA7-8222959F487C}
MONTICELLO 110137384 | {9EBC498A-4473-4FB2-A278-0770D844069B}
MONTICELLO 11014360 | {6122D5A8-AE4D-48D9-9C29-4E501E315009}
MONTICELLO 110152910 | {151C0216-83E8-4EAF-9D71-0D50917A8A0E}
MONTICELLO 1101630 | {EC7479AE-9F4D-4362-8AF7-E7B5EDC2ECC7}
MONTICELLO 1101654 | {11F49F82-D386-49B9-BCC1-D0FA0566ECA0}
MONTICELLO 110165454 | {9E39C048-EF22-4DAE-9CE9-DEC0330A8321}
MONTICELLO 1101666 | {5E2D609D-433E-4CA6-9935-5DD068ECF7FE}
MONTICELLO 1101718 | {CFFE2061-0111-499A-9D10-C50262E92A10}
MONTICELLO 1101720 | {07BF8128-F528-4070-AA6F-0E3ACF3A793A}
MONTICELLO 1101909026 | {4FC73DDB-01A4-4D9E-A572-5B8425E298AC}
MONTICELLO 110193384 | {D1302290-4599-4ADB-94B8-46B42AAD5681}
MONTICELLO 1101CB | {CCC05F57-600B-48FA-93EA-7CC307C90265}
MORAGA 1101108540 | {372C45CD-D068-4E6E-9903-0ED38EA6950C}
MORAGA 1101121620 | {27593588-F872-4832-9B66-0B2A2D32D4A3}
MORAGA 1101122434 | {564AB235-16DF-45CF-988E-206774FFC22E}
MORAGA 11013442 | {5E439C6C-9351-476C-9634-FD9D0D59EEC5}
MORAGA 1101532246 | {5BBA7E94-488D-470E-9522-5BF71768AFC8}
MORAGA 1101669542 | {83605CEC-417D-4699-962F-40957BFD8A66}
MORAGA 1101669542 | {B9A70335-64B1-4C3F-8843-DB3BDADB4C77}
MORAGA 1101772406 | {B68800AA-8665-4562-B46C-56262DD45B63}
MORAGA 1101822414 | {B2892C66-0456-410A-AA55-6BB01132F335}
MORAGA 110183424 | {E1CFB432-A326-40CC-8BB1-1B7A06DF46E8}
MORAGA 1101CB | {6B23A69C-24B9-4566-AFFA-1FAEC2B2E50D}
MORAGA 1102161484 | {BF062587-F543-4494-9BCB-AB97B3FA4161}
MORAGA 1102221914 | {1B687BB2-4458-48CF-B4BC-EAC2F2DF6A24}
MORAGA 1102CB | {882C20B1-4F53-4E74-914C-118DECC8B0F8}
MORAGA 110381146 | {F07F88D2-F88A-4EFC-8A75-AE6FED02438E}
MORAGA 110381146 | {14C57C49-3FAA-493A-A967-CDA87ADFA83B}
MORAGA 1103838598 | {693F18CA-6E41-44D8-B1A1-17EC2030AA07}
MORAGA 1103880425 | {4E1314C0-96F2-46DA-A3A3-635E5ABAFDCD}
MORAGA 1103CB | {D9DC241F-0994-464E-87CB-1A64D6E40D7E}
MORAGA 1103CB | {A7850717-18DF-4BF5-B934-11A86FF92EB5}
MORAGA 1103E510R | {4C3B8436-25B4-4A62-8D40-AF9B1B8FB54A}
MORAGA 1104750618 | {D6B675EC-0BB2-4404-B1DC-E66B91C5F9F8}
MORAGA 1104CB | {65BF29A6-90D7-4E9D-9D0F-0B463AE68E56}
MORAGA 1104N532R | {8FCB98A6-A5C4-47A0-A545-FF069C01B16A}
MORAGA 1105116034 | {52D8B49E-A907-44B9-9C80-969531571B5F}
MORAGA 110531512 | {412508C2-76EC-400C-8C7E-53EB1141C78F}
MORAGA 1105553110 | {ED0CCE67-C6E8-4C9F-AA31-59CE0E37A31D}
MORAGA 1105829530 | {7BAB3DC6-3A7A-45FE-9661-6992831DBB83}
MORAGA 1105CB | {40049C8F-DAE2-4759-A9B6-0D8AA42C6AC2}
MORAGA 1105E512R | {D2286737-B438-4EE0-BE89-B719D260A085}
MORGAN HILL 2104145998 | {DE740AD5-7224-4449-BB36-490304754B67}
MORGAN HILL 2104152774 | {425217ED-9250-4ACE-9F11-E30531EC148C}
MORGAN HILL 2104CB | {107D0CE4-0125-4C25-9DF3-3408566B030B}
MORGAN HILL 2105345099 | {80793A2F-4CDD-4126-A553-60CE126AE8B0}
MORGAN HILL 210542348 | {2DBAAA9C-8985-4692-9A1B-CC370D239D9B}
MORGAN HILL 210542348 | {8A3AD693-3871-44A7-A81A-4DD472A3967C}
MORGAN HILL 2105507074 | {466C2B1C-1C77-4861-8272-8DFDED489F56}
MORGAN HILL 2105717836 | {B4A4667E-7514-48A0-8CFF-3909C4EC7F3B}
MORGAN HILL 2105CB | {CB70A94C-2E5D-4322-8C8C-C227D17BDEDF}
MORGAN HILL 2105XR152 | {91E130A2-6B12-4607-8077-CCA3F4CE535A}
MORGAN HILL 2105XR176 | {33647C9D-A594-482D-97B0-F9F1AC5928F8}
MORGAN HILL 2105XR268 | {4F22013A-C8F8-4C93-9CF0-829946636F4D}
MORGAN HILL 2105XR312 | {03C8F227-2007-4B73-A689-5FDF30542245}
MORGAN HILL 2105XR494 | {C97EA88F-37CF-413E-B387-CC0A9C345449}
MORGAN HILL 2105XR564 | {002F00BF-AB7A-4582-A318-84DD2A6C3219}
MORGAN HILL 2105XR578 | {534A451C-57DA-44B8-B8BC-2F5C24A553D0}
MORGAN HILL 2105XR602 | {DF06274D-82A7-4C1B-8F47-D036189DB7AF}
MORGAN HILL 210653992 | {92AC711D-1F72-4B85-B43C-96526CED20CC}
MORGAN HILL 2106CB | {2C56B704-0B48-474B-86AD-67CE86231708}
MORGAN HILL 2106XR002 | {2D5D4B5A-C41C-47E0-8A3E-3313CAAFF1F2}
MORGAN HILL 2106XR224 | {58A345F9-A65F-4B30-98DE-46C2DCF15710}
MORGAN HILL 2106XR324 | {5E41A8C8-B670-4C41-941F-324D15B78BC7}
MORGAN HILL 2108CB | {4DF45F56-E0C5-4EB4-A8CE-218D259985D0}
MORGAN HILL 2108XR328 | {D422348E-558F-4EA6-B8E7-CD115687A21D}
MORGAN HILL 2109574578 | {1C4F0AAD-E3B2-4C7A-88ED-CB2CF0311B95}
MORGAN HILL 2109CB | {40746EE4-53DF-4A3F-B597-DD5CDFE06F6F}
MORGAN HILL 2109XR246 | {601835A0-060D-478B-8A86-7129055F5CF4}
MORGAN HILL 21103093 | {9362E54D-FA7C-435C-B0E7-CE02E9A2869F}
MORGAN HILL 2110654924 | {674F8E15-1E29-4545-B316-3ABCD054D65C}
MORGAN HILL 2110716210 | {9362E54D-FA7C-435C-B0E7-CE02E9A2869F}
MORGAN HILL 2110791720 | {9362E54D-FA7C-435C-B0E7-CE02E9A2869F}
MORGAN HILL 2110814616 | {E9537C4E-4E0C-458C-9F28-99C225E45397}
MORGAN HILL 2110CB | {E4018ACB-C125-496A-B5B0-B421A786B3CA}
MORGAN HILL 2110XR164 | {11D639D0-BAAC-4BDC-B7F6-D7D6C9CC18B0}
MORGAN HILL 2111123422 | {AC835E08-6C41-417C-9DCE-0F2F64530550}
MORGAN HILL 2111419718 | {40B38A4F-7054-4A4B-BF09-F440B1202801}
MORGAN HILL 2111699122 | {DE03B79F-99A4-443E-8075-A283584F1321}
MORGAN HILL 2111919856 | {9425E865-2193-4800-9F65-36F91B76A0A9}
MORGAN HILL 2111997000 | {60A77C46-059F-42FD-9344-179C8ED541A4}
MORGAN HILL 2111CB | {C53CEE9F-7D61-4CE9-9445-195D1FBA8C9E}
MORGAN HILL 2111CB | {8D6AF672-1092-41FD-91A5-035B7D768884}
MORGAN HILL 2111CB | {38524ABF-273D-46D3-B737-CC26E3F4D5B4}
MORGAN HILL 2111XR292 | {7A50E1CD-B005-4744-BD76-86E8006C9FCE}
MORGAN HILL 2111XR398 | {C3FC7DAB-5E2B-4C00-BE86-ED9552703F1E}
MORGAN HILL 2111XR398 | {42CC2054-54F9-458D-A9CD-C912CAA60A36}
MORRO BAY 110115845 | {DC1CD14A-C73E-417C-A65E-B1AE2FBC8341}
MORRO BAY 1101655346 | {90233E6E-4312-4E5F-8197-A335785233C2}
MORRO BAY 1101V64 | {02238211-B668-4889-9A10-D952B009B264}
MORRO BAY 1101V66 | {DC1CD14A-C73E-417C-A65E-B1AE2FBC8341}
MORRO BAY 1101W04 | {24F44E9D-6C68-4D37-B48D-A651AA08451C}
MORRO BAY 1101W20 | {F3373B43-A9DC-45C9-B2E8-745D10B70AD6}
MORRO BAY 110247584 | {BC93D19D-B18C-449B-8A15-8B2CED2656F7}
MORRO BAY 1102868170 | {BC93D19D-B18C-449B-8A15-8B2CED2656F7}
MORRO BAY 1102CB | {4C9F3CAE-E991-4EA7-BCAB-BA03C4CEAE92}
MORRO BAY 1102V80 | {C6CF638E-9C90-41DD-9ABD-A01972E6D396}
MORRO BAY 1102V84 | {C6CF638E-9C90-41DD-9ABD-A01972E6D396}
MORRO BAY 1102V86 | {17FE32AA-9377-42CB-8A9F-BE6476105A71}
MORRO BAY 1102W22 | {419B2231-1D8F-4B2A-BF73-E14BD76078D8}
MORRO BAY 1102W24 | {17FE32AA-9377-42CB-8A9F-BE6476105A71}
MORRO BAY 1102W34 | {419B2231-1D8F-4B2A-BF73-E14BD76078D8}
MOUNTAIN QUARRIES 21011102 | {97220F1A-31F1-43CF-AD5A-7E7641130D1C}
MOUNTAIN QUARRIES 21011102 | {DF2C227C-9D6F-4146-A18D-C4063420CF16}
MOUNTAIN QUARRIES 21011130 | {3696C0F1-45DD-4488-B6E0-2639E4EE975D}
MOUNTAIN QUARRIES 21011130 | {F71097AE-E6F3-430F-8B2D-241E8D88F4AE}
MOUNTAIN QUARRIES 21011130 | {4401AE48-8842-4E05-A6D8-C050619F7D35}
MOUNTAIN QUARRIES 21011130 | {097A43FE-FBB8-4402-8D96-021DD8AD80ED}
MOUNTAIN QUARRIES 21011130 | {ACC5A18D-8809-4891-8ACC-21091B2C8A38}
MOUNTAIN QUARRIES 21011130 | {F266D2D0-26B6-498E-8272-1E04CE549628}
MOUNTAIN QUARRIES 21011130 | {BB827B61-94FF-41F0-8C34-E26E09A6DC70}
MOUNTAIN QUARRIES 2101117452 | {F6FC9A10-626B-4FC0-AEAB-599AAB0F4A9C}
MOUNTAIN QUARRIES 21011180 | {A425B909-D733-4D18-87EA-CA1BE8C7EBF2}
MOUNTAIN QUARRIES 21011180 | {B43AC0E9-618E-4C0C-902C-460E0DA9C289}
MOUNTAIN QUARRIES 21011184 | {955B96CF-04BC-4DDA-A99C-F3551BD93482}
MOUNTAIN QUARRIES 21011346 | {B959CC4A-E894-449B-BBA9-D2734BD80359}
MOUNTAIN QUARRIES 21011350 | {6752B4B6-FF0C-4C57-ADC9-D57090816B6D}
MOUNTAIN QUARRIES 21012422 | {75EC316D-75DD-4B44-B4A2-C724F062D260}
MOUNTAIN QUARRIES 21012504 | {D8BA8AE4-C717-4377-92D2-0F59CC0A31DF}
MOUNTAIN QUARRIES 2101256426 | {C879D233-9068-42D7-B3F2-F423CBBE7E0A}
MOUNTAIN QUARRIES 210135466 | {F283C4DF-68EA-4D46-BF4A-0E3EBCA0E4FA}
MOUNTAIN QUARRIES 2101486682 | {C012B9A5-7963-4E6A-B877-46101FFAFAB7}
MOUNTAIN QUARRIES 210151584 | {0BE1E4C9-DDDF-49C0-980B-2AA7763D326F}
MOUNTAIN QUARRIES 2101674140 | {D33AA4D5-0329-4D52-AAAC-E350AE539E7E}
MOUNTAIN QUARRIES 210192474 | {B1828264-E942-4507-AD5A-E7D1D60A066A}
MOUNTAIN QUARRIES 21019329 | {3C579689-B8E8-46CE-97DE-EFB83C898D90}
MOUNTAIN QUARRIES 2101979598 | {BD8F3E9A-E4BA-4240-B5BB-1CCE7EBD3EAE}
MOUNTAIN QUARRIES 2101CB | {D8BA8AE4-C717-4377-92D2-0F59CC0A31DF}
MT EDEN 1112MR365 | {A5398856-385B-4671-B566-17D8F81D2C22}
MT EDEN 1112MR537 | {A5398856-385B-4671-B566-17D8F81D2C22}
NAPA 11025039 | {CBD8A59E-6463-47E4-AF46-087923E514DE}
NAPA 1102561208 | {12961FC8-2125-43B0-A892-045A87E2B620}
NAPA 1102578510 | {E29393AB-AF27-41B0-9A33-27DFC604929D}
NAPA 1102942 | {CBD8A59E-6463-47E4-AF46-087923E514DE}
NAPA 110549856 | {A567CC7C-BB96-40C6-B54C-7AC9DFF3A542}
NAPA 1112118938 | {C2E68366-657D-4902-BBD7-D59A6C76C29A}
NAPA 11121302 | {605680BF-CE15-4E43-86C0-2D915CDAFCDB}
NAPA 11121573 | {BA7A893B-49EB-4FAF-806C-61F07C4035BA}
NAPA 1112315244 | {91380486-2659-460E-8E8C-74182A1F6A64}
NAPA 111236690 | {49C79E51-B09B-4581-9F4C-FE61ADE08510}
NAPA 1112850068 | {B5EEBD8D-5229-462C-9EA8-5264059F4EB6}
NAPA 111289474 | {D8230112-C16E-4959-B193-6B3851D10773}
NAPA 1112895680 | {9516FB9B-F6A9-46C6-900E-617F34930DEA}
NAPA 1112919436 | {0CCAD7CD-FF20-472B-B1AB-23DFD98C4B6F}
NAPA 1112943158 | {C39D5E34-C18E-41D1-A210-D8B55CE52048}
NAPA 1112CB | {C2E68366-657D-4902-BBD7-D59A6C76C29A}
NARROWS 21011202 | {63551680-2169-45C3-BF85-1608C868FCAF}
NARROWS 21011202 | {76F27F83-E433-4439-87D2-79F62B309CCE}
NARROWS 2101307774 | {1DE83126-4AE1-4391-AB52-3AE50E6D0C19}
NARROWS 2101CB | {7B0321EB-AC29-4857-8514-66B11EFDEF70}
NARROWS 21022718 | {86E697C0-19D2-49B3-8770-C861515EBF3B}
NARROWS 21022728 | {1F33AC4D-BB0A-424C-BF6E-423FE06FB054}
NARROWS 21022728 | {144B4FCA-3C98-4564-A83E-7AEFBDAF84B1}
NARROWS 210242584 | {BB1737E9-F6A8-464E-B585-0852853AAD83}
NARROWS 210248484 | {76FD4F17-DDF4-4910-B30D-69ED940511F8}
NARROWS 210276952 | {070E580D-ED42-47CA-BF5A-6C96D8E39FC5}
NARROWS 2102960916 | {1C32EBFC-8AE9-4287-9AFF-F5593AA3371B}
NARROWS 2102CB | {30B38EC8-F2E7-47AF-8BC7-D7EB75673131}
NARROWS 2104CB | {F4FF7575-EB60-4F06-920B-F33332AB37E0}
NARROWS 21052216 | {94CC379D-BE20-48E1-8496-01F284C7FE9E}
NARROWS 21052216 | {A36316CC-284E-4EA8-AB44-E4232D2C6598}
NARROWS 21052228 | {0B17CC85-B7E2-466D-81E7-7A9C0CD3AFE8}
NARROWS 21052426 | {AD8C7F05-71CF-448E-8013-A273E591A171}
NARROWS 21052426 | {8D49CCC1-AF4C-4146-915D-64772DC7F3D1}
NARROWS 21052426 | {76062427-42D5-4E1A-A36C-DB543BCA9CBA}
NARROWS 21052748 | {EEAC938D-675B-4361-87B7-7942FA5DF8E7}
NARROWS 210551582 | {D508D44B-0B7F-43CB-B9DA-F37161CA8F62}
NARROWS 2105644180 | {0725B391-7E02-4071-8E08-E9BD6A8347A4}
NARROWS 21057203 | {8D49CCC1-AF4C-4146-915D-64772DC7F3D1}
NARROWS 2105973602 | {65BDD240-8E40-4173-9154-9F995B0B041C}
NARROWS 2105CB | {EFD12602-D83F-4E42-AE19-DEB7C99E3F7B}
NARROWS 2105CB | {F0462EA2-6036-4A59-88FF-33C061E43E44}
NARROWS 2105CB | {2611646A-C593-4185-9486-0AA063D164D0}
NEWBURG 113137512 | {BE4D7FC4-1B1E-43C1-A168-77B9EA7D5DB3}
NEWBURG 113142896 | {98A83A4A-2877-4301-8F63-D1E33C62F68A}
NEWBURG 113190242 | {3A3BBF86-310F-432E-A06D-A8536237FB4D}
NEWBURG 113190644 | {2572FE04-E2DD-4CAD-BF35-98155ECF32DE}
NEWBURG 1131CB | {C16220E4-6906-4FA1-A17B-9AB4492699E3}
NEWBURG 1131CB | {C04ABA60-50E1-4D28-B0FC-7F9C72775B5F}
NEWBURG 1131CB | {A965CA4E-8283-4CE3-A9B0-927C4A2518C9}
NEWBURG 11322074 | {144E92CD-CA71-4B28-86FC-662A80108717}
NEWBURG 11322074 | {61AD59B6-3DE5-4155-9391-74B53A84E200}
NEWBURG 113237494 | {1EC16A91-B2BC-459B-BC25-4726E009B399}
NEWBURG 11326576 | {2C9C3EB7-00FC-4934-A962-9B300983DC9F}
NEWBURG 1132665674 | {F0A8EA1C-5D25-4DA2-A0EA-6346825293B2}
NEWBURG 11326982 | {0F02967E-1D6B-4BD8-8EC3-7246776F1FB8}
NEWBURG 113277894 | {80EB220B-EDCA-49B1-8388-856A3CF42050}
NEWBURG 1132CB | {2C9C3EB7-00FC-4934-A962-9B300983DC9F}
NEWBURG 113397612 | {1B3C973B-E8C8-4CCB-9A5F-D4D21840CBA9}
NEWBURG 1133CB | {DD9AEFE6-8781-45D2-A01C-A8D7D2CCC603}
NEWMAN 110542128 | {6D9E4F88-A0CF-477F-A1A4-9ED1BDD71148}
NEWMAN 110590430 | {AD5BB80F-100E-443D-B968-9FD3EF2DDDC6}
NORCO 1102CB | {CDEAC89B-EAE4-4BB8-822C-DF627E95CCED}
NORTH DUBLIN 2101176170 | {D30D6D06-835F-4B36-96BC-159C0F899260}
NORTH DUBLIN 2101CB | {298F8E6C-8C4E-4458-91EA-603E3295125F}
NORTH DUBLIN 2101MR765 | {436DC1C4-F56A-4204-87B1-78F6DDDDA501}
NORTH DUBLIN 2103248212 | {1315E3CE-6D47-41FF-A139-336A7A702069}
NORTH DUBLIN 2103248212 | {51ED7259-EE7B-43FE-8146-EC616D86F161}
NORTH DUBLIN 2103248212 | {A9FADF54-D8A8-414A-9A42-DC0268771F29}
NORTH DUBLIN 2103508004 | {938FCC6B-7D14-4E25-AC44-E7DBDEADAF0D}
NORTH DUBLIN 2103727584 | {2C0EFE8A-7C72-4220-9833-B0936FC60BBF}
NORTH DUBLIN 2103847902 | {656D8A1F-9A46-4FEE-8A99-D29B4333E923}
NORTH DUBLIN 2103CB | {7713D0FD-BB09-40ED-B7D7-E260577647D4}
NOTRE DAME 1103317782 | {E54B3868-C992-4672-B01F-A1BD60263D71}
NOTRE DAME 1103407486 | {611B5D12-B194-497D-815D-46B8449CCF48}
NOTRE DAME 1103CB | {E3ECAAF0-99B5-4E63-AE53-35BCAA42BD12}
NOTRE DAME 1104176446 | {A653535C-4696-4B65-83D8-F7031EAB38F0}
NOTRE DAME 11042028 | {68FC6E44-EFD8-4B52-B283-8EF4B688F460}
NOTRE DAME 11042408 | {BE4941E8-75D1-4DE2-AD8F-78922C143536}
NOTRE DAME 1104741302 | {8170D31E-E9E5-4FE6-B0CB-D284CE6CFF73}
NOTRE DAME 1104937710 | {3CF079B2-DF24-4674-AF57-026F1C1899BA}
NOTRE DAME 1104CB | {4C7176B3-82BB-4EC7-9074-E6E03166E224}
NOVATO 1101180632 | {E700FD05-F82B-4C09-AFA4-140066127996}
NOVATO 1101180632 | {8092C842-CB66-429C-A93C-3CE6A8BDBBDF}
NOVATO 1101405812 | {E700FD05-F82B-4C09-AFA4-140066127996}
NOVATO 110387834 | {F95FECA9-BE51-4923-A755-70AE69DDB475}
NOVATO 11041282 | {3B8D2573-46CC-4384-8812-825E9555364D}
NOVATO 110438242 | {16EA3947-70AB-44CB-89F0-74D3A6768C00}
NOVATO 1104422246 | {16EA3947-70AB-44CB-89F0-74D3A6768C00}
NOVATO 1104488340 | {1842CB75-05D4-4BC6-974F-EF96026B2FE8}
NOVATO 110449280 | {DFA09063-555C-4B48-ABDD-D054FE284D1C}
NOVATO 110455398 | {335D8DF9-D334-4C80-A8EC-F250AAC0E6C3}
NOVATO 11046137 | {30588372-5355-4D36-B660-B511FDE55CBF}
NOVATO 1104676060 | {64CF78D9-1536-455F-B223-A7030F2F7FB3}
NOVATO 1104889406 | {B0ADA7D3-946E-4D87-A626-5D6D71C05975}
NOVATO 1104904966 | {335D8DF9-D334-4C80-A8EC-F250AAC0E6C3}
NOVATO 1104CB | {1842CB75-05D4-4BC6-974F-EF96026B2FE8}
OAK 0401772122 | {FED570EA-6E71-451D-82BC-E09C185F668A}
OAK 0401946300 | {3404A894-1969-47FB-AB3F-F737D2ED0294}
OAK 0401CB | {E8FD31A9-7950-4D14-9414-D1A0A0556AE8}
OAK 0401R7252 | {0F16EE83-C04F-42F2-82FB-83FAA303C2EB}
OAKHURST 110110090 | {D4FA4CF9-389A-4C4C-89DD-16736203046B}
OAKHURST 110110090 | {8E59087F-9FB7-4FCF-A3C3-5164FC72FB46}
OAKHURST 110110090 | {0499B4AD-CC9F-479D-BE96-0CEA6A3630CF}
OAKHURST 110110672 | {CA4BC837-4816-4F0E-8284-B08210611858}
OAKHURST 110110675 | {FCDD4E01-0C82-4AD1-883F-41FA62375BF3}
OAKHURST 1101352740 | {C6B7CBA9-A121-4696-95EE-5F408A7C3658}
OAKHURST 1101466264 | {89DDF3A0-1E04-4A36-845F-B6417E8069A8}
OAKHURST 11015490 | {19617CFD-32A5-4AA4-9E54-43F64E95D667}
OAKHURST 1101618380 | {3BD097D6-9F24-4589-8A9B-760186FAF7A5}
OAKHURST 1101636114 | {C6D08398-1977-4CDB-B9B0-E15E9BAE5667}
OAKHURST 1101636114 | {4BE225D7-081D-493E-91CE-03A95C54B512}
OAKHURST 1101910120 | {544CCA12-ED7E-4449-A067-A7C3370A6363}
OAKHURST 1101932488 | {5FD72363-074F-488B-BB92-0CD76D6743F5}
OAKHURST 1101CB | {2CDF7848-B063-4FC4-9C52-AE29AA49D3FF}
OAKHURST 1102204618 | {076A05E5-4BFC-4436-8E3E-8DEEF5261574}
OAKHURST 1102333062 | {4739024B-FF85-45D7-AECF-B2FD3D7B777B}
OAKHURST 1102455174 | {7767F8D3-309F-4BA5-BBA0-85C1BA00E073}
OAKHURST 1102538042 | {CD5EC07C-7621-403E-BE45-2B4B105F5053}
OAKHURST 1102683678 | {4739024B-FF85-45D7-AECF-B2FD3D7B777B}
OAKHURST 1102963056 | {62CEF957-71A2-4F8F-B3B6-2E1C79BBD67A}
OAKHURST 1102963056 | {D0015396-1CC9-4783-A5A2-48EC4AF3208B}
OAKHURST 1102CB | {D0015396-1CC9-4783-A5A2-48EC4AF3208B}
OAKHURST 110310140 | {9D3389CA-CFE2-49B7-8B13-3D1B7ACB399D}
OAKHURST 110310190 | {15EFA531-A43D-4849-828D-DC9485A13753}
OAKHURST 110310570 | {6B3B75F9-5C6A-488D-8FAD-069FF0389692}
OAKHURST 110310570 | {3D247DD8-C725-4A26-BE65-60FA26890CB2}
OAKHURST 110311900 | {0DA18697-929C-4AB7-9F79-F379F7D7D5E9}
OAKHURST 1103121108 | {32B2079A-935B-4640-A41B-0950AB93625E}
OAKHURST 1103292044 | {0FFD9FB4-9FFE-459D-AB4C-EDC42D076C7B}
OAKHURST 110331530 | {96A8B9FB-82CF-4728-9EC7-87970059FA7F}
OAKHURST 1103464622 | {E28BFF8D-F8E2-40AB-836D-4CDEF3E6FE3D}
OAKHURST 11035120 | {36CCC1E6-2517-4B50-80DA-A74340CF2F3A}
OAKHURST 11035480 | {194E4857-C055-4CC4-9616-06A060725A90}
OAKHURST 11035726 | {337AB8AA-4352-422D-BF09-E368057A434E}
OAKHURST 110363334 | {778182E4-2AE7-465E-B2C9-C1ED6A0D9207}
OAKHURST 110363334 | {1B71693F-F2F1-4EC9-ACBD-B615502AE374}
OAKHURST 1103719490 | {0997B2C6-B46C-4942-8B54-4BA0035375E3}
OAKHURST 1103719490 | {AE0883DC-525F-4553-839F-C837CD511E13}
OAKHURST 110377384 | {B3D10DC1-455E-4DDF-8795-B604423C3B61}
OAKHURST 1103CB | {0FC43676-7F71-4151-8B57-A856F18A7815}
OAKLAND D 0407CB | {D6B258F1-A023-49ED-A291-5DC1514DFA3F}
OAKLAND D 1112775616 | {E3949547-B886-4AC0-B818-1825176C1A10}
OAKLAND D 1112775616 | {F53A9D7A-8AE8-4A2D-A636-4553F02D4DA3}
OAKLAND D 1112775616 | {79081478-9874-4F61-AC27-C396B53B5EAB}
OAKLAND J 1102126740 | {977D131F-B0F9-4D49-AC55-AA0EFBCDE0F0}
OAKLAND J 1102159816 | {859F64C2-C27C-450D-B243-6E6F38B09662}
OAKLAND J 1102208294 | {3968E6D1-D5B2-4B61-BDB8-C346AFC38AF0}
OAKLAND J 1102511776 | {0551D865-0E6D-422F-A7A5-D8972FE7561E}
OAKLAND J 1102951816 | {F44E0750-FE39-44A0-8598-B8A75709D6C1}
OAKLAND J 1102CR102 | {0FCC4668-DE07-42BB-BC4D-4288336A5D5A}
OAKLAND J 1102CR250 | {6E981B94-5C33-4038-BF67-3B35100D303C}
OAKLAND J 1102CR252 | {FD5FE64E-C40E-49F6-A1B2-6062B4E7CFF6}
OAKLAND J 1105153228 | {FD68B15D-2380-4995-ADA8-EF407A4F9E9B}
OAKLAND J 1105CR132 | {99760D35-3D8A-43D4-9A8C-B787B6697406}
OAKLAND J 1105CR150 | {B40886D4-E154-4D0B-BB2B-061EFDC2739B}
OAKLAND J 1105CR256 | {FA7AC1D5-82AB-4E51-B874-C59D71756955}
OAKLAND J 11067867 | {D707E642-9970-495B-88DA-CDC7E44E15FA}
OAKLAND J 1106CR164 | {D707E642-9970-495B-88DA-CDC7E44E15FA}
OAKLAND J 1106CR330 | {D707E642-9970-495B-88DA-CDC7E44E15FA}
OAKLAND J 1116629954 | {96EB03CB-4C09-47D7-A7E9-BD766768CD85}
OAKLAND J 1116CR328 | {38D3BFB4-B810-445A-BCA4-713A479E6C8D}
OAKLAND J 1118CR198 | {218F069D-01B3-4618-A6DA-CD10F8EDDF5D}
OAKLAND J 1118CR332 | {218F069D-01B3-4618-A6DA-CD10F8EDDF5D}
OAKLAND K 1101357838 | {B7663DD7-88A5-43F8-BDE6-6881FCA5A058}
OAKLAND K 1101462782 | {BAD456A1-64C0-4C58-9244-4CB0B49EFF5E}
OAKLAND K 1101CB | {BAD456A1-64C0-4C58-9244-4CB0B49EFF5E}
OAKLAND K 1101CR170 | {8CEAFBDA-9CAF-47DF-A93A-B3DE193C02EB}
OAKLAND K 1101CR172 | {E320AB5D-B36A-4218-B61F-1E6C684D2F8F}
OAKLAND K 1101CR174 | {FDB219FE-14C7-4B56-80C3-13B19698F631}
OAKLAND K 1101CR178 | {39624C9F-891A-4855-966B-439C473BE8D2}
OAKLAND K 1102172340 | {D34997DF-D716-4F24-A200-9AE2C7E61290}
OAKLAND K 110217430 | {02500171-BA04-46CD-BDC9-060AD340AEF8}
OAKLAND K 1102378866 | {09828EEB-C0CE-4488-A95A-E404C7913B2A}
OAKLAND K 1102CB | {D1E9CD4E-4BC6-42D5-802C-68BF9527A1E0}
OAKLAND K 1102CR014 | {B5EF99C1-ABA3-48FB-9EE2-B54D16D47CE4}
OAKLAND K 1103952364 | {A7AEEED7-B132-44AD-9127-E644C5373201}
OAKLAND K 1103CB | {9BD2CCED-08C0-4120-A490-E52866AF5C8D}
OAKLAND K 1103CR202 | {FB563E6A-FAEA-4920-ABF0-8B26398B25A7}
OAKLAND K 1103CR422 | {834BDB9E-9A30-4D9F-8424-760E012D4EC8}
OAKLAND K 1104432850 | {14CA8224-5AC7-4834-81C3-26558D7F85B9}
OAKLAND K 1104CB | {3C8EEA5A-CE4E-4740-9897-693B2E67E957}
OAKLAND K 1104CR204 | {A0999EEF-D902-4C4C-8260-3134A0D51FA5}
OAKLAND K 1104CR206 | {FDBE20C4-A243-4218-824C-85EFE8D9D967}
OAKLAND K 1104CR208 | {61E67233-CD4F-4206-8138-63FBDA895D1D}
OAKLAND K 1104CR210 | {5D6DF9FD-08CF-4E49-97A3-2B3AF27CC711}
OAKLAND K 1104CR326 | {993BD642-B43F-4A07-B618-DAD20FD40FEE}
OAKLAND X 1101688681 | {4D72F15F-C15D-414E-839E-18266D63B84A}
OAKLAND X 1104391688 | {CE464302-D75F-4110-A0B1-1E7596A4CF84}
OAKLAND X 1104438648 | {51A41992-B3B3-41BA-BF69-679DAA3E243C}
OAKLAND X 1104645092 | {14DC5424-B005-4065-8948-2B6A676B0C25}
OAKLAND X 1104711340 | {0E4E8191-99CF-4CD0-9618-70FC06227F18}
OAKLAND X 1104CB | {14DC5424-B005-4065-8948-2B6A676B0C25}
OAKLAND X 1104CR101 | {0E163071-14D9-42E7-B9B8-B27ACF143A75}
OAKLAND X 1104CR214 | {A4D00FB7-3066-4764-B528-AB78985E682B}
OAKLAND X 1104CR288 | {E0AFB0D0-4FAA-4A38-B181-558E89FECB34}
OAKLAND X 1105184672 | {274ECA5A-0B48-43A3-88F5-9E1AB810108B}
OAKLAND X 1105528554 | {D8A3F73E-152F-405F-9A1C-7432AB4CBB0C}
OAKLAND X 1105CB | {44B8C422-CD6C-4697-80AE-EEAF985A6D84}
OAKLAND X 1105CR242 | {4B545AE9-A885-48BD-BBDD-C323FFCD6AA5}
OAKLAND X 1106121588 | {93028691-B011-4DD4-9BFD-411C56E1FD61}
OAKLAND X 1106250726 | {72B65155-7706-4799-8D5D-6A7E944CD44B}
OAKLAND X 1106714420 | {6CBEECB4-A65D-4682-9F4F-669A0B0591FE}
OAKLAND X 1106735592 | {7014D81C-BAD9-4B89-B142-06674CDB91D9}
OAKLAND X 1106950688 | {AF2EF2E2-3FD9-4033-9703-73840E59FAC3}
OAKLAND X 1106CB | {FEA3C3F3-959E-472A-9376-926585E20D05}
OAKLAND X 1106CR008 | {A1C4F4D6-01EE-430E-BE68-0AE547BD756D}
OAKLAND X 1106CR020 | {6992E765-02F8-45C7-B571-2F9E479DE26D}
OAKLAND X 1106CR266 | {9B2F70E2-3822-4ABC-9A9F-F92985EE671F}
OAKLAND X 1107CR428 | {44E2AC7C-1F72-42EE-8609-62087EC4A35D}
OCEANO 110266830 | {2DECB6E4-425D-42B6-97FF-2F1DB74B6B2D}
OCEANO 1102749231 | {8546FDA1-23F8-40F3-9B1E-5EFFE01FDD01}
OCEANO 1102847440 | {45F26A7D-9F54-449D-A121-9094CE2E38B8}
OCEANO 1102862544 | {6318B7B8-7C4D-4B7F-9191-39DFB96AEC30}
OCEANO 1102CB | {53EA2B69-06B5-416F-96AE-9EC7627A84C5}
OCEANO 1102M60 | {DCC941F4-38E3-4AD8-A417-5C522DBC4598}
OCEANO 1102V56 | {6A98D8AD-262A-4E43-B52C-E7FA164E1E31}
OCEANO 110376678 | {2258BA59-F952-4D7E-A5B4-7204CE2B68CB}
OCEANO 1103839302 | {7E0AB3E6-06DD-4E76-83F1-F36EBF375722}
OCEANO 1103V22 | {77F4F191-CCC6-4075-AD1D-AD57A94CE7F5}
OCEANO 1104101636 | {B07841C3-C7FD-4CD0-B547-EC38380C531A}
OCEANO 1104104102 | {6F967F18-8991-4C9D-8139-526CA500F4D2}
OCEANO 1104337754 | {364E7C35-C794-44C0-8261-10586BEC51B1}
OCEANO 1104766140 | {7A75C7D6-EF3A-4018-8F3C-5799B21580A9}
OCEANO 1104891294 | {B4F67A9F-9FE0-45CA-A256-022486D60ACE}
OCEANO 1104CB | {EF084BAC-E8B6-45D7-885C-1A50430DEB23}
OCEANO 1104CB | {5F6C277E-7A5B-4A21-A584-FB79418743D2}
OCEANO 1104Q08 | {D6547032-0BCE-40E6-B529-0CCA8B7E9C38}
OCEANO 1104Q10 | {FB18C056-8E7F-47BF-BAE4-63685AFB3AD7}
OCEANO 1104Q10 | {F2B590C3-1895-4587-B930-9120C0B01EAA}
OCEANO 1104Q12 | {1F61853A-FECA-4E03-86FF-C3BDC269D699}
OCEANO 1104V36 | {612579F3-BEE6-43F6-ABF9-9C9C3F31A5CF}
OCEANO 1104V38 | {F2D88342-EA4A-4DE6-A5A2-0FD601C586EE}
OCEANO 110583502 | {4D468DA5-BA2A-4D9B-B631-053C455A8BC4}
OCEANO 1106CB | {2FEE1CE0-BC95-467C-8CDD-CAD4D3CD2579}
OCEANO 1106V26 | {21F0D2ED-5157-4651-9344-5CE1A886A315}
OCEANO 1106V28 | {5A21115A-46BA-4632-AD7D-E9A81D89A695}
OCEANO 1106V32 | {CF9B5783-C82F-4557-9D4A-652677BA468B}
OILFIELDS 110241992 | {30F0CC79-17F2-4C3C-8FCB-5EFF56537510}
OILFIELDS 1102591276 | {FBAA4FF3-DDEF-4B28-AACE-23EBBCBE3340}
OILFIELDS 110293788 | {207F72FF-9E9B-497E-A35C-453C13449996}
OILFIELDS 1102CB | {59A6DBF3-2585-475E-ABD4-6C09185E8D33}
OILFIELDS 1103233424 | {D1CD6BAF-3C2D-48BC-989C-18A0A5CF3122}
OILFIELDS 11032757 | {8AB39E69-C0C8-463C-8D53-0C9F3FCA08BA}
OILFIELDS 1103311126 | {CDC6585C-22C0-4542-A949-CDEE5502EA22}
OILFIELDS 1103370932 | {DD06783C-4182-4702-93A1-A61D699C1BFE}
OILFIELDS 1103441010 | {0D72FC66-890A-408E-8587-304B2BD5DE0B}
OILFIELDS 1103451760 | {14EAA451-E72D-4F75-999F-C08A856C154C}
OILFIELDS 1103643162 | {863AAC38-B427-4ED7-8C8C-48B256B58936}
OILFIELDS 11037006 | {28C87B96-17F1-4B77-AC44-88E083C74B6C}
OILFIELDS 11037064 | {8A139B57-6162-459B-9D12-F430854EC2EB}
OILFIELDS 110383158 | {B2FF44F5-E554-4874-9716-21C58C3BA291}
OILFIELDS 110387034 | {FB7AE1AC-8576-424E-830B-24A6DA8C1F01}
OILFIELDS 1103954802 | {C696666E-34BC-4556-B8A0-7C7FFB3A4F64}
OILFIELDS 1103CB | {BEB06E83-3CCD-4D08-B66B-707C171E4243}
OILFIELDS 1103N04 | {5211BDAB-5F5E-4B32-AE7D-8A73813FC3DA}
OILFIELDS 1103N40 | {5FF9C387-FCBA-4CB4-A5E3-8021D551E54B}
OILFIELDS 1103N42 | {CDC6585C-22C0-4542-A949-CDEE5502EA22}
OILFIELDS 1103N44 | {440ECBFF-AD7A-4676-BD33-1103476A2F8D}
OILFIELDS 1103N44 | {47FD814D-36E3-4524-B471-B70B44EFD5A6}
OILFIELDS 1103N48 | {8AB39E69-C0C8-463C-8D53-0C9F3FCA08BA}
OILFIELDS 1103N62 | {47FD814D-36E3-4524-B471-B70B44EFD5A6}
OLEMA 11011200 | {A8B14B0D-3BCA-44F1-B75C-F9F858D43D86}
OLEMA 11011252 | {46D411EC-386C-4DB1-B30F-D2D2AC060A49}
OLEMA 11011318 | {48696EF7-D14F-4A4B-98EA-50D58AFE2188}
OLEMA 11011677 | {FDCF9EC3-494E-4E71-8E1D-CD83B8A6AD3E}
OLEMA 11011686 | {701C0938-AA90-48C8-9BEF-CBE33E0DD08B}
OLEMA 11011889 | {181462B5-2486-4AF4-A573-0BE076CC7009}
OLEMA 1101337220 | {92ED973C-FC6F-4281-87E0-2EC9DA3D68C7}
OLEMA 1101359772 | {ED6FC814-3841-4AC9-A379-44E5BC33C241}
OLEMA 110137074 | {117C09FD-AE60-4D22-843F-8781BD8BA585}
OLEMA 1101435308 | {EEBEABC3-BE9C-4763-B96D-27E7B7BF727E}
OLEMA 110146014 | {A82D843B-628F-4D51-ABE5-7DA46EAA8FF0}
OLEMA 110149756 | {D3A0D229-F80C-49CB-8DD0-3A6BB24AE00B}
OLEMA 110150396 | {F7C05161-6A07-4797-A2B5-C7A055E43654}
OLEMA 1101512 | {818B580F-3855-41D8-9229-869A2B79816E}
OLEMA 110175686 | {702CCB2B-B1B0-4591-B980-760D81375AFB}
OLEMA 1101758594 | {EB266F6D-17EC-430D-AF10-380B2A2664C8}
OLEMA 1101946146 | {4466C1AE-C4B7-4D5D-A1C6-2C36E11ADFD5}
OLEMA 1101CB | {BE6F7E5F-020B-49FB-90DC-2F40A691D506}
OLETA 11011217 | {266221BA-D2B4-4469-81F2-F0DF035CF024}
OLETA 110113478 | {C597D1DF-05AF-4117-9139-6F79BFFC0A15}
OLETA 1101190308 | {C597D1DF-05AF-4117-9139-6F79BFFC0A15}
OLETA 1101239062 | {266221BA-D2B4-4469-81F2-F0DF035CF024}
OLETA 1101296804 | {85FEEB3E-959D-465E-A93D-BA3999C78268}
OLETA 1101440008 | {516575F6-B4E4-42BA-847E-708BCA880781}
OLETA 110151740 | {FCFE42BE-9C18-409B-9916-4C477F3B3051}
OLETA 110163500 | {869A17D4-9B8C-44A5-B65E-B210B8E19AC7}
OLETA 110163500 | {1E9F707C-392D-4DC5-A731-022ADCFFB715}
OLETA 110163500 | {0DE3898A-1208-4EC8-ABE1-FA05111C0DC6}
OLETA 1101754718 | {F9BCD513-5384-4FF0-AB87-CE22E82C21EE}
OLETA 1101928252 | {5B6438FA-7C7E-4451-8180-245B9388E3EE}
OLETA 1101994386 | {7A7D8413-3009-4325-865C-5FBA4CE9F269}
OLETA 1101CB | {3D156343-1F71-46EE-A300-26BD3EB64071}
OLETA 11021204 | {946E6116-FB8B-4590-A386-CB8F9AFD8BF3}
OLETA 11021228 | {944D67B9-350E-45E5-9370-1645B5E16FDD}
OLETA 1102186326 | {A68CE267-B165-491B-AEAA-6DAE490DB1B3}
OLETA 1102186326 | {03979F9B-3CCE-4069-8D96-9642946E6487}
OLETA 11022642 | {2ADCBD92-66F4-407E-9ADA-EA48C32C4604}
OLETA 110241396 | {6992FFBA-72E0-4D3C-898B-1A95BB5A0A16}
OLETA 1102793776 | {9DAE8EAF-539B-42A9-B23A-753111FFCF66}
OLETA 1102799924 | {B8897444-5751-4E50-98B6-2ADB95C6C270}
OLETA 110297487 | {29049AF3-C7E2-4D26-96C8-9E667A4EBF7A}
OLETA 1102CB | {23616425-EB34-423E-9DF9-30BB0AE7795F}
OLETA 1102L1619 | {56E3659F-1882-4519-AAEB-60F876DB879C}
OREGON TRAIL 11021382 | {5E999E0A-FF01-4E2B-B970-E4BD7149EAE7}
OREGON TRAIL 11021584 | {27DB2D0A-E99D-4209-B824-D94C177A7A12}
OREGON TRAIL 110249144 | {C5CBE785-E536-4CC4-8B58-7E4F16DB8A71}
OREGON TRAIL 1102CB | {D8B4A6F8-9874-47E2-910D-F4C8426E6854}
OREGON TRAIL 11031448 | {0C0482CD-DD8D-411C-9735-C68EC442433B}
OREGON TRAIL 11031500 | {31065709-9564-4E9B-B7A7-65368041A59F}
OREGON TRAIL 1103312718 | {4A57D115-47A6-4507-9D31-64278D9DBAA7}
OREGON TRAIL 110346860 | {4F1FF48F-FF8A-488F-A383-0E93A88F3890}
OREGON TRAIL 1103CB | {57A4B509-FD84-475C-B34A-463055A0DAF6}
OREGON TRAIL 1103CUS391 | {4A57D115-47A6-4507-9D31-64278D9DBAA7}
OREGON TRAIL 1104128100 | {ADD91A04-63E3-48F4-ABF3-81ABE34C691A}
OREGON TRAIL 11041574 | {6C99A7DB-F466-44F8-AE24-87D735D842AA}
OREGON TRAIL 11041634 | {6281842D-96D3-4641-90CC-4C58A4D89E7E}
OREGON TRAIL 11043310 | {DC4CEBC1-24E2-4325-802B-4D3154343BA7}
OREGON TRAIL 1104CB | {8048141D-B1E9-414C-85DA-8DE818EBAD4F}
ORO FINO 11012022 | {81205B01-8688-4570-8F47-B08F18EDCF16}
ORO FINO 1101CB | {26463A0F-9160-43C4-90A7-25599609C772}
ORO FINO 1101CB | {4F055C2B-F555-47EE-931F-D64958E5EDAE}
ORO FINO 11022090 | {D1240401-ECAA-4BD1-99E5-871723028078}
ORO FINO 11022236 | {C813897C-7FF0-4426-960C-CC77387AFFF1}
ORO FINO 11022556 | {6018A7D7-F178-44F7-B593-CA41A45039FD}
ORO FINO 110239154 | {2FC41A94-8141-4836-94D8-D074E279E487}
ORO FINO 110239154 | {A0DF0310-E76F-4503-848A-EC07BD6D9878}
ORO FINO 110239154 | {B0E99E01-0D27-4597-A594-1741A25A99A7}
ORO FINO 110239154 | {EE93E5CE-FD33-44EC-A329-FBA8C511073C}
ORO FINO 110239154 | {B1149BFB-EDFA-46D1-B822-44352980F037}
ORO FINO 110265932 | {EE93E5CE-FD33-44EC-A329-FBA8C511073C}
ORO FINO 110265932 | {220703DE-64FB-4EBF-8D4D-8F4876EBF3D2}
ORO FINO 110265932 | {D7531920-6156-40F8-93AB-696611CA4A3D}
ORO FINO 110265932 | {5618B278-348E-4F2F-99ED-BBEB44B38F25}
ORO FINO 1102787504 | {5292D5EF-8994-4D5E-873A-57C44F72ACD1}
ORO FINO 1102805744 | {FC19A6D9-DE9C-4128-8158-93D6222DFA0D}
ORO FINO 1102CB | {4BB60C53-9CA3-4098-8B28-FE44C4ECF9D3}
ORO LOMA 11063650 | {E12EEC5C-3034-4448-A5AF-CECE82A0BEF6}
ORO LOMA 1117436290 | {CD178AF8-67F3-40EC-9886-046098153739}
OROSI 11017400 | {C6FB3F90-7F71-4284-8B79-AB4E9E54C7FA}
OROSI 1101778698 | {D47909B2-5499-4CFC-B467-CF97C416E66A}
OROSI 11017839F | {652E17F8-ABE0-4899-9F8D-FDF7FAC2ACC8}
OROSI 1101939642 | {652E17F8-ABE0-4899-9F8D-FDF7FAC2ACC8}
OROSI 1101CB | {652E17F8-ABE0-4899-9F8D-FDF7FAC2ACC8}
OROSI 1102419794 | {9826F28D-8B41-44A3-BABF-A3C0C8BDA35B}
OROSI 1102617446 | {38342D33-FCBD-48C5-A427-7A9D99AAC119}
OROSI 1102CB | {283D946E-F745-4F7C-ACE9-D6EB2A3744AC}
OROSI 11037901F | {029EB0AA-88F8-4BF4-93B1-3A5396293CB7}
OROSI 1103CB | {029EB0AA-88F8-4BF4-93B1-3A5396293CB7}
OROVILLE 1102434320 | {010ABE92-9760-4A20-97C4-698DB24D3E2F}
OROVILLE 1102CB | {581D49A7-9F4F-4C9A-B76D-C943A94B162C}
OROVILLE 110313028 | {FCEE706A-0D7B-4465-9296-7C2C63F00F21}
OROVILLE 11031502 | {A54ECB41-5029-41D9-AD67-64342065DC6F}
OROVILLE 11042588 | {6CD595E0-0633-4F8D-A21D-706EDE410B88}
OROVILLE 1104CB | {DF8BB72F-C21D-4A12-8CBC-5B84FF3140AA}
ORTIGA 110611190 | {8B291346-CFF6-4C64-B9CC-BCE46E2EF12F}
ORTIGA 11063770 | {F76B220C-9B12-4060-8FD5-AA7B30439772}
ORTIGA 110677310 | {64CB3AAD-A29B-4D58-9AF0-E0ACBF523EBE}
OTTER 11012052 | {ADEA2AA0-7D11-4F36-AA83-95B5C9DEA776}
OTTER 11012052 | {E3F93E31-1671-42B2-A17F-FBDD23B44199}
OTTER 11012052 | {64CB4C99-55F9-4CDD-8DE2-173258603853}
OTTER 110140411 | {C4F8B68A-3808-4813-AAA8-02DA7D4670C3}
OTTER 1101440 | {9B3F8B66-8E8D-4C3E-B30C-F806C7A06324}
OTTER 1101CB | {BB161BB9-B628-4038-939A-BDBCD448B75E}
OTTER 11022002 | {BF5568ED-9C16-497C-B05F-AE0C967E64B7}
OTTER 11022012 | {5B008FE4-7524-4C11-8819-B0F9661FD099}
OTTER 11022166 | {C47B4B77-9CC6-4665-96AD-097EBCE52988}
OTTER 1102499 | {6A27EB06-0614-4DDD-9B6E-5F5D726771E4}
OTTER 110263868 | {11A5B6DF-81F1-427D-A78C-DE7EF2F392AC}
OTTER 1102888750 | {EA503A22-8553-4FB5-A613-918BC5053064}
OTTER 110298036 | {05EEF29D-5376-4D63-9244-FB865CD63617}
OTTER 1102CB | {D42BED5F-FA94-4772-B8B5-334F2629EC25}
PACIFIC GROVE 04222608 | {26CF3F6B-878E-4A8B-9C78-A10BD98C9FEB}
PACIFIC GROVE 04222614 | {45F66B28-3708-48B3-AEFE-0F1CE66015AD}
PACIFICA 110110067 | {2C30988A-F66E-4A90-B5B0-67ED6781F8F5}
PACIFICA 11015001 | {4118C23A-F427-46E8-85D2-FD56A1055C29}
PACIFICA 1101777484 | {4118C23A-F427-46E8-85D2-FD56A1055C29}
PACIFICA 1101CB | {0685C5F8-0970-41C6-89BD-EFB0337B96FB}
PACIFICA 1102267868 | {275774F1-4908-4480-8C4A-1E1AEF9EEB75}
PACIFICA 1102320094 | {34BD287D-7D35-4C2B-A9F7-C04740C3CDE1}
PACIFICA 110252715 | {9452BDE0-DE70-4463-B819-B9B0CA79D823}
PACIFICA 1102660408 | {002FC16A-D8E0-4EC1-BCF1-D174F5CB0D0E}
PACIFICA 110266732 | {2E2285AC-DBD4-4A01-BBCE-F25D437434C6}
PACIFICA 11026783 | {21B2A452-206C-46DF-8D00-791570670CE7}
PACIFICA 11026783 | {19E4E8D4-9C4C-4C6B-8FB5-CC59DB118DCE}
PACIFICA 11026783 | {CF80C5D9-A948-4E0A-B024-F910B6DDD0C9}
PACIFICA 1102934870 | {CFE1B2DE-63B7-4084-B6EA-A58F62A2EB56}
PACIFICA 1102968736 | {6BD2C65D-7217-43E0-B7BC-E7737DB1CECA}
PACIFICA 1102CB | {3BE78651-BE87-4B28-8A48-F46DBB91FDDB}
PACIFICA 1103398620 | {572B383E-2937-4EFC-BA24-50423EE8A457}
PACIFICA 1103885952 | {572B383E-2937-4EFC-BA24-50423EE8A457}
PACIFICA 1103915474 | {572B383E-2937-4EFC-BA24-50423EE8A457}
PACIFICA 1103CB | {5EC3A666-1799-428B-8C0E-2A981579542E}
PACIFICA 110410195 | {C0B7FBD5-C48E-49C2-A7B2-8E06D90A6C57}
PACIFICA 1104230272 | {233FC7C5-A8F9-452B-B547-9495E8EC73B6}
PACIFICA 1104CB | {EC3F19B1-655E-438D-8AA0-F3D32FED5878}
PALMER 110198478 | {68615336-79DC-4EC6-9727-806E7A643D26}
PALMER 1101CB | {EC1B6C10-3B8B-426D-86D3-39EE85F08618}
PALMER 1101CUSTREC | {EC1B6C10-3B8B-426D-86D3-39EE85F08618}
PALMER 1101M82 | {51B50550-2616-4B8D-8593-9330C414F251}
PALMER 1101M84 | {F73EB641-FFE0-4811-B0D3-9263F0EA89B1}
PALMER 1101M88 | {A85BAC06-7F10-4768-B721-E152D18C46EA}
PALO SECO 0401450678 | {CA3D00F3-FCB7-4F7A-9ADF-E9E789C26B1E}
PALO SECO 0401CB | {0E3E2146-50FB-4065-BA86-A817B98C8BBE}
PANOCHE 110110480 | {6153CF92-FD59-45F9-8E86-DBB637985FE7}
PANOCHE 11013530 | {6153CF92-FD59-45F9-8E86-DBB637985FE7}
PANOCHE 1103107270 | {9F8F9B54-61D9-473A-8686-65EC8068C547}
PANOCHE 11034008 | {0C7E1298-8ED7-4AF4-8E12-9D89E23F7125}
PANOCHE 11034010 | {8C4CDF18-070E-4712-A105-26C4CB39CA5E}
PANOCHE 11034036 | {AD986AF1-07AD-469F-94A3-573792C7B7E5}
PANOCHE 1103724590 | {5B47604F-4D22-4440-B1D0-9EB575B90DA2}
PANOCHE 1103735730 | {5B47604F-4D22-4440-B1D0-9EB575B90DA2}
PANOCHE 110390540 | {2A3253A4-EBC1-4720-AE66-B68045C8C594}
PANOCHE 1103CB | {5B47604F-4D22-4440-B1D0-9EB575B90DA2}
PANORAMA 1101713592 | {70311009-6B82-4803-BF61-8884A737A669}
PANORAMA 11019092 | {18BCFDD7-AD26-4B95-9A8E-1B5EFFBCB7AF}
PANORAMA 1101CB | {39175FAF-A6C7-4043-8D47-1A655E22AF59}
PANORAMA 1101CB | {9B056DF9-5520-41DF-AC7A-220983243590}
PANORAMA 11021342 | {6303BED6-9051-4E72-A1E9-A3825361F885}
PANORAMA 11021632 | {CE87ED54-B441-462F-AE1C-C4DF9A1FDFBB}
PANORAMA 11022009 | {A631613E-AC26-415F-BA05-B8776DE457AF}
PANORAMA 1102280170 | {F5CE5D5F-8E7F-4EC6-BC00-8B427EE9DDBA}
PANORAMA 11023320 | {A631613E-AC26-415F-BA05-B8776DE457AF}
PANORAMA 1102508502 | {1D8E176C-9DB7-4594-BA36-DE41DD4BC4BB}
PANORAMA 1102663264 | {B947D1A9-2D0E-4A86-8335-B5F6D05FA8E0}
PANORAMA 1102717242 | {F2E83CED-3C27-428E-8B4F-3AF72F0E6D37}
PANORAMA 11029762 | {C1937D12-32A7-40CA-876D-66A02478084B}
PANORAMA 1102CB | {BF983BB2-B79A-4F98-B895-74C5BCEB2BA3}
PARADISE 1101CB | {1834B56B-7B97-41B7-947A-7BB1EAF4F248}
PARADISE 110343008 | {7C830B89-C4E8-4748-BC82-72018BB296D2}
PARADISE 110353544 | {7C830B89-C4E8-4748-BC82-72018BB296D2}
PARADISE 1103CB | {916B572F-25AB-43E4-8DCE-50B2436F4EE2}
PARADISE 11042034 | {F797DCB1-C578-4B28-B5FA-B1147A5E9141}
PARADISE 11042206 | {1341CA63-432E-4CD8-BB46-467A27C9C55D}
PARADISE 110439214 | {1CCA13E6-0B87-4BF0-8C65-1F382E0EC595}
PARADISE 1104920400 | {1341CA63-432E-4CD8-BB46-467A27C9C55D}
PARADISE 1104954322 | {E166525C-A57D-4F06-BD7C-C2B52E2E9B6B}
PARADISE 1104CB | {60D04F67-B0A9-4BD6-8DCF-759CBE65FF11}
PARADISE 1105960434 | {4E875C07-9BF0-416D-8352-B1380CD2F62E}
PARADISE 1105CB | {4E875C07-9BF0-416D-8352-B1380CD2F62E}
PARADISE 1105CB | {699FF00B-7EEF-4F62-8E53-097CDFAA861F}
PARADISE 1106CB | {54AC0ECA-BD93-49A2-9B30-909ADBE15177}
PARKWAY 1101688 | {2DD92471-3439-41C4-92F0-EB7825E281D8}
PARKWAY 1101702 | {18940FE2-B098-437A-9D7C-197517E26C70}
PARKWAY 1101CB | {18940FE2-B098-437A-9D7C-197517E26C70}
PASO ROBLES 110132593 | {EDB8367F-06AF-4145-97CC-734EE720D9A7}
PASO ROBLES 110195810 | {EDB8367F-06AF-4145-97CC-734EE720D9A7}
PASO ROBLES 1102R64 | {B7E49A70-A833-4F14-A4E0-7628D7D12C4C}
PASO ROBLES 1103351084 | {8A0F9F4E-D4AB-4BFD-A1BC-FC8BA1E7A461}
PASO ROBLES 1103540954 | {1490D290-9F77-437C-9825-05494F9DE78B}
PASO ROBLES 110355374 | {7E3660A3-92BC-4694-A2D5-248E2793B9A8}
PASO ROBLES 1103CB | {5A5ABA2D-583E-4687-9FE8-7872A20C2CCC}
PASO ROBLES 1103N02 | {75A395F4-172A-4FF6-844A-F6A1B941CE83}
PASO ROBLES 1103N50 | {382A16B7-3BCC-4C59-941A-61838BC92D6A}
PASO ROBLES 1103N52 | {35122D11-1E93-423C-905C-FD3596B054C4}
PASO ROBLES 1103N54 | {3D8A845E-016A-4676-A95E-AFB35541512A}
PASO ROBLES 1103N58 | {ABB59667-7D2C-427E-8CD5-70D7C7F4474B}
PASO ROBLES 1103P08 | {1FA86F64-861A-4311-896C-8F2E15FE3A38}
PASO ROBLES 1103R18 | {029273CF-97D6-4AE6-9649-1799DF0E5FE7}
PASO ROBLES 1104998752 | {FBC10DA3-7702-4FA4-B763-5E3BEB4D8D94}
PASO ROBLES 1104998752 | {330F1436-5F6B-47F8-9E18-2B1C20154586}
PASO ROBLES 1104P02 | {8AA23B4A-11D4-4912-ABC9-3F7E49C90F6C}
PASO ROBLES 1104R12 | {4348EB98-7F3C-44FD-A7F0-CBA935871986}
PASO ROBLES 1104R14 | {037DFB22-CFED-4C3E-B1F8-0F77CACE13E7}
PASO ROBLES 1104R56 | {3A535F79-B416-456C-A3C1-BEDA8326FF1E}
PASO ROBLES 110638682 | {E892B584-48EE-4125-BACC-2451AA6482B8}
PASO ROBLES 1106CB | {569EC071-DD47-42F2-9569-DF5DC93512CB}
PASO ROBLES 1106R70 | {931CA1B4-3667-4C96-9792-EB8AF0018AF4}
PASO ROBLES 1107164828 | {5B95E912-C067-4AA0-9FFE-5697AD0ADA25}
PASO ROBLES 110764703 | {BF9A1CFA-5044-466A-9DCB-672D048DD99A}
PASO ROBLES 1107826368 | {3681E2B2-3C69-41BC-898C-6BA327012404}
PASO ROBLES 1107CB | {F753CFBD-929F-4059-9A39-67C517F8ED5B}
PASO ROBLES 1107CB | {BF9A1CFA-5044-466A-9DCB-672D048DD99A}
PASO ROBLES 1107P22 | {1C337801-E008-421B-9399-975B6DF38CC5}
PASO ROBLES 1108881950 | {5E0AA671-92D5-4AED-B632-6F04BBB895EE}
PASO ROBLES 1108CUS6036 | {5E0AA671-92D5-4AED-B632-6F04BBB895EE}
PASO ROBLES 1108P10 | {DA348341-A294-4294-8A9B-8E403A8DD5B1}
PASO ROBLES 1108P28 | {674E461B-DF8C-43E8-8C03-AA3C3BF037C3}
PASO ROBLES 1108R10 | {F6C975A3-F727-462F-BF14-05FA1E630EB4}
PAUL SWEET 210212850 | {F743E5C1-4CE6-4D65-B6FE-D0B8E82E2CBD}
PAUL SWEET 210216006 | {ACD82200-9A89-4E0D-B5FF-D276794568F7}
PAUL SWEET 2102168368 | {720DB739-6D0D-4A39-B396-1773770EDF72}
PAUL SWEET 2102337544 | {593613BC-2474-4D8A-8E89-2D049FCAFE94}
PAUL SWEET 21025291 | {ACD82200-9A89-4E0D-B5FF-D276794568F7}
PAUL SWEET 2102774760 | {494C5866-0CBE-4898-9CD2-71A0E0DFEC0C}
PAUL SWEET 2102777828 | {F548DBEB-2204-4D4F-9EDC-F093EA4A006D}
PAUL SWEET 2102CB | {E84E756D-50CD-4E19-9CC3-E6F7306D45B8}
PAUL SWEET 210312075 | {BA3D6A76-5335-48A7-9116-A38FBA76779B}
PAUL SWEET 210335240 | {BA3D6A76-5335-48A7-9116-A38FBA76779B}
PAUL SWEET 2103458558 | {BA3D6A76-5335-48A7-9116-A38FBA76779B}
PAUL SWEET 210349246 | {BA3D6A76-5335-48A7-9116-A38FBA76779B}
PAUL SWEET 210349370 | {751E8B54-6492-47D2-8237-81A7BF27A640}
PAUL SWEET 2103811390 | {BA3D6A76-5335-48A7-9116-A38FBA76779B}
PAUL SWEET 210398594 | {BA3D6A76-5335-48A7-9116-A38FBA76779B}
PAUL SWEET 2103CB | {BA3D6A76-5335-48A7-9116-A38FBA76779B}
PAUL SWEET 210410916 | {988B88E9-8AA5-4ACC-86CE-9D077C9C2397}
PAUL SWEET 2104273794 | {1B2755B5-DECF-4054-A952-1299D1C6CE0E}
PAUL SWEET 210437482 | {1FF4F77B-4C57-4B40-92BD-9BE254F0DF32}
PAUL SWEET 210438286 | {EF44D52E-8193-4375-AC6D-6EA950270447}
PAUL SWEET 21045394 | {E0421238-8872-42C1-B1A0-89190DCCE20D}
PAUL SWEET 2104867374 | {9E32E9CD-A939-47B7-8D32-52540B68C5C6}
PAUL SWEET 2104885736 | {9BB76603-65A7-482F-A2CE-E72536A0A1DF}
PAUL SWEET 2104CB | {9E32E9CD-A939-47B7-8D32-52540B68C5C6}
PAUL SWEET 210510290 | {33AE2657-6F42-4109-A970-89EF5E991C73}
PAUL SWEET 210510918 | {B00E71CA-F451-4C1E-88CF-6A90C8415E53}
PAUL SWEET 210516008 | {08D65962-CB7F-4222-BC19-55AC6F6E5F80}
PAUL SWEET 2105197474 | {4F10B184-8B51-461A-8F91-52416BCD1A14}
PAUL SWEET 2105893980 | {AAB0FB14-1BE0-48CC-8935-FE15EC775ADE}
PAUL SWEET 2105959032 | {DC6678BB-B73F-4EC1-B958-DDA4A1A4DD5B}
PAUL SWEET 2105CB | {8D1DF0FB-6A31-4B98-9D74-0EE015EF8A6D}
PAUL SWEET 210612828 | {35A821AF-CADB-4929-9F1D-038A70D8EFD3}
PAUL SWEET 2106490904 | {5B95BA53-9152-4AC0-B900-6EE497CECC41}
PAUL SWEET 21065178 | {7E071814-6E26-47AC-8D93-17E4616D1F83}
PAUL SWEET 21065178 | {3482F96A-13E2-4F4F-8107-9B0C7ED5D69B}
PAUL SWEET 21065178 | {2A54EA47-0BFA-43D7-ABE2-937F4BBA661A}
PAUL SWEET 21065178 | {CC7AE606-3471-46F7-B0D5-980B87C65360}
PAUL SWEET 2106607772 | {5CFD19E5-804C-4EC5-B475-DE099B6B0FA7}
PAUL SWEET 2106974130 | {A7C1D647-6C80-4397-A936-CB6E2BBC28B0}
PAUL SWEET 2106CB | {20C18C61-423B-413F-AE41-A93513864053}
PAUL SWEET 2106CB | {3E23A7A3-C33C-44B7-A4F6-DB4402C4D050}
PAUL SWEET 2107179744 | {F171F536-3218-49C2-B438-37B0DF63D0C5}
PAUL SWEET 210737234 | {137C6E91-EFA6-4F4A-9FB1-51BD0ED5008F}
PAUL SWEET 2107781810 | {281B3385-4F71-4EC0-B77E-390E15EC23C1}
PAUL SWEET 2107781810 | {43DF0CDA-60E3-4AB9-AB14-881CC4D8A4B6}
PAUL SWEET 2108467366 | {E52B8805-203F-48DE-9EB9-00203F902662}
PAUL SWEET 210875588 | {E52B8805-203F-48DE-9EB9-00203F902662}
PAUL SWEET 210878006 | {E52B8805-203F-48DE-9EB9-00203F902662}
PAUL SWEET 2108862930 | {E52B8805-203F-48DE-9EB9-00203F902662}
PAUL SWEET 2108CB | {62614D7C-C46B-4061-8F81-503DEACC476D}
PAUL SWEET 210910216 | {6723F687-9519-4B9C-9E73-40C91AF6B4E5}
PAUL SWEET 210912946 | {9DDD43C5-588F-4D1E-AFA3-8A122C419F83}
PAUL SWEET 2109634576 | {270FCA15-092A-4BC1-985F-1AAFCAC44027}
PAUL SWEET 2109749538 | {88BA87BD-CB4E-4D02-9B88-71CCAAF521E6}
PAUL SWEET 210977392 | {1355BE47-26F5-4F89-911F-F6F925526D9C}
PAUL SWEET 210980246 | {5B8C5D01-7F9E-4FC6-96BE-CEA07F6E2017}
PAUL SWEET 2109929132 | {CEB85E34-A4D1-44F2-A797-167211118BF1}
PAUL SWEET 2109964900 | {97C63DED-27B0-4593-BC3D-32418E81FD5B}
PAUL SWEET 2109964900 | {7FCFEDBD-6985-4E47-ABA1-988C2AB4CA93}
PAUL SWEET 2109968438 | {97C63DED-27B0-4593-BC3D-32418E81FD5B}
PAUL SWEET 2109CB | {8C8A8C09-E52E-42BB-8F77-24A43F9E99B3}
PAUL SWEET 2109CB | {12F9217C-0E98-4CB6-8403-4C09E1874A0F}
PEABODY 210218112 | {AA374A3A-F1D4-4C08-A286-4FEBB2ED33A7}
PEABODY 210240382 | {52129BA3-96A5-477E-8C41-41CBEFBDB5C8}
PEABODY 2102CB | {7F8D11BF-1C5F-4471-93CB-B0549BFFC90F}
PEABODY 210441042 | {19EBF719-4922-4070-885F-9DCECBC907B0}
PEABODY 2104CB | {19EBF719-4922-4070-885F-9DCECBC907B0}
PEABODY 210515812 | {42073265-9FB5-44FA-9F7C-25D75E02B84B}
PEABODY 210518134 | {F75E8FD9-6FE6-4F23-9B8B-6B4A9C655647}
PEABODY 21059641 | {42073265-9FB5-44FA-9F7C-25D75E02B84B}
PEABODY 2105CB | {F75E8FD9-6FE6-4F23-9B8B-6B4A9C655647}
PEABODY 210618312 | {0E7B7A5F-D902-47E6-BF01-E01C11C1B70D}
PEABODY 2106CB | {C5A3359B-293F-4CF2-8CE7-491CB52E0623}
PEABODY 2106CB | {369633AA-CFA4-4128-87F4-3265F391CCA6}
PEABODY 210718252 | {41AF2BD2-21F9-400C-9C2D-4FB3CB7C1824}
PEABODY 210718342 | {C0D20754-067C-4A97-93E6-A4D604F42652}
PEABODY 210741980 | {04E3BC76-4A83-44EB-969E-56A0D5FE6C6E}
PEABODY 21074902 | {C28C2EB2-6EA9-4744-980A-972080A5DA71}
PEABODY 210765584 | {41AF2BD2-21F9-400C-9C2D-4FB3CB7C1824}
PEABODY 210769886 | {CBF21B3C-B466-4E74-861A-D215537C4D7B}
PEABODY 210769886 | {F998AAD1-650B-46CE-9E5D-E3AF1D66F538}
PEABODY 21078502 | {65D53E83-81CD-43A8-84EB-03AFF4CA98F0}
PEABODY 21079784 | {C629EBE5-80B0-48C3-A046-7D0403D642F8}
PEABODY 2107CB | {04E3BC76-4A83-44EB-969E-56A0D5FE6C6E}
PEABODY 210813402 | {BC2B156B-5F07-4313-BE60-34EF88AFE911}
PEABODY 210818182 | {FD31089F-B875-4F53-A4C1-3C40CEE32B11}
PEABODY 2108CB | {BC2B156B-5F07-4313-BE60-34EF88AFE911}
PEABODY 2108CB | {FD31089F-B875-4F53-A4C1-3C40CEE32B11}
PEABODY 2109CB | {035ED1CF-C64B-4885-91B5-653C042B9D52}
PEABODY 2112CB | {12DBB35E-70A4-4BA6-BC3D-1E42CCA6987B}
PEABODY 211340336 | {463CEDCD-A864-4BE7-A495-4562C479EEC4}
PEABODY 211357908 | {6AA0DCBD-B26C-4407-A430-B4CB9B32E7BD}
PEABODY 211375820 | {E86B319E-6766-44A4-AF82-33EB666FB39D}
PEABODY 2113873304 | {BA425A15-9A5C-4FD6-A7BD-96EAD5DA88D3}
PEABODY 2113945670 | {6946CCA0-CBC9-4149-87BE-14A9B8AA299F}
PEABODY 2113CB | {463CEDCD-A864-4BE7-A495-4562C479EEC4}
PEABODY 2113CB | {ADE1D1FD-7F67-452E-9E37-895B8A824D56}
PEABODY 2113CB | {B470F804-F311-4B08-A332-8707C2B5977D}
PEASE 11031226 | {1AC4492D-C692-4A7F-BC33-D8F8AAC2CC64}
PEASE 11037274 | {9BFEA3FC-F858-403B-915B-27847D69BA7C}
PEASE 11037276 | {0CB044F8-A4C0-4562-85E4-BA05DA5B5425}
PEASE 11041228 | {86E8635E-120D-446E-91FE-0B00EC1EF138}
PEASE 110441262 | {90B4DB05-495B-40C8-B5D5-363F909B384E}
PENNGROVE 1101170 | {5131AC69-910D-4644-AD31-07E4800CAD58}
PENNGROVE 1101190 | {22BBE811-DD4E-4C60-8F3B-677EB9B5576F}
PENNGROVE 1101325956 | {9D558E42-88D5-42F3-808F-02B4EF74376D}
PENNGROVE 11013476 | {9D558E42-88D5-42F3-808F-02B4EF74376D}
PENNGROVE 110145574 | {992D79E1-6AF5-422C-9178-CF16A35823EE}
PENNGROVE 110145574 | {29853D86-D10B-44F9-9B31-548850DBE0F0}
PENNGROVE 1101730740 | {A0067835-951C-4E33-B8BA-E12B7D0FE2B4}
PENNGROVE 1101950828 | {B6A14AF2-2E92-4A8B-A025-34671BE1E9DE}
PENNGROVE 1101950828 | {CD37B800-2B86-40D6-B4EA-CA95E7B1359F}
PENRYN 11032198 | {15328E03-B147-4A5F-A6DD-FF57B3032B26}
PENRYN 1103512438 | {3AD27421-3325-46E9-97AB-79A8C2192338}
PENRYN 110351658 | {9E584244-489D-49B0-8EC4-8B40DD374169}
PENRYN 1103604 | {E0C71142-0733-49C8-8AA5-49865B61A687}
PENRYN 1103660 | {E80D319C-D01D-4A69-9210-7A23DDD13D1F}
PENRYN 1103CB | {87180880-8EB9-4F8B-82CC-028E4C7029F0}
PENRYN 11051342 | {C5308B22-07AE-4998-BAA1-CBC87B70637B}
PENRYN 11051378 | {1E1BA976-38CE-4912-807F-3A5F3BFF5CD1}
PENRYN 1105154362 | {A58D8351-9C68-4CA5-80CA-5BE208F9F034}
PENRYN 1105168616 | {91345D7C-F3FB-4825-B072-AFC3A521036D}
PENRYN 1105196418 | {C6ED3044-D174-430F-8880-19A3EDFC2300}
PENRYN 11052406 | {A6C70D14-E593-46FB-BE1A-9881978863D6}
PENRYN 110550548 | {00BC1CA8-06FB-48A4-95C2-0F674B5818F3}
PENRYN 110550550 | {38FA411E-5935-4516-9773-4CAD949A1A2A}
PENRYN 110550550 | {E8C857BD-8FA0-4293-8DF8-8699935C5887}
PENRYN 110550550 | {D349A8E8-4CB0-4AF5-8711-156EA1F6C1E8}
PENRYN 110551676 | {6FA4A1F6-3AB8-4114-8002-DF4E0174192B}
PENRYN 1105680290 | {FA212A2C-123D-4A6F-B182-0DF2CC1BF77C}
PENRYN 1105CB | {52904CB5-03B8-4344-8C19-2DFFF3E5223D}
PENRYN 1106212772 | {92A66D4A-ADE9-41F4-B941-D8E0EF2D1DE8}
PENRYN 110651674 | {2BBB97CC-A78B-43EC-BEB0-66A2E29BC2E3}
PENRYN 1106980728 | {1524F2FC-2DED-4951-9267-9B0CA2F011FD}
PENRYN 1106CB | {C3E0B410-F242-443E-BF4E-9C519E692FDB}
PENRYN 11072410 | {88D11C1E-94DA-491E-B166-BE630EDE0741}
PENRYN 11072704 | {3C765F3F-8878-4C34-98CF-2D3F31F6AD44}
PENRYN 11072706 | {A3F26B0A-1692-42C7-87B6-33C42D499946}
PENRYN 11072708 | {B656F43A-A721-479D-8405-E771FFE89131}
PENRYN 1107378926 | {D526C6EB-AA17-4411-B9FB-7B8C4782D6DD}
PENRYN 110790970 | {9DF5CB55-1623-4B4B-9F53-43CFDE7622F1}
PENRYN 1107CB | {44D8E601-5E0A-4B0D-A783-27A4770DE5A5}
PEORIA 1701169700 | {F105D414-EDB0-4B69-9A07-511DDEB90E10}
PEORIA 17011834 | {843F968C-C902-4C08-BE12-AD0D025C5DF3}
PEORIA 17011997 | {A406E3D6-852A-4A1F-8E5A-BC3670ECDB5D}
PEORIA 17013186 | {52FB3514-9C62-49DD-A158-2A9A7CF95D5B}
PEORIA 1701349908 | {0D0C220B-9E3C-41D4-9452-BA3E14C4B41B}
PEORIA 170169124 | {8AAD3A20-76BA-4DD7-9403-7AA47644DC04}
PEORIA 170175274 | {EA8957E8-4D9E-4768-B294-C26CA1256456}
PEORIA 170176030 | {CF97D77D-981C-448C-B149-87042BADEDF7}
PEORIA 1701813284 | {6B8BC918-E4AD-465E-B216-91C881E7FEF9}
PEORIA 1701813284 | {E418DE0D-9638-43B9-862E-E665469CF811}
PEORIA 170184318 | {CB8A5610-26AF-406C-A01C-6D3A6199376B}
PEORIA 170190090 | {CA1036D4-6988-4718-9A58-7F114C1260AF}
PEORIA 1701CB | {3B5F2B21-B073-4B15-A884-38AC36D267F6}
PEORIA 170411232 | {320BFDAF-F5A8-4096-BB62-ECF18634253B}
PEORIA 170413490 | {D6A9F596-51F2-4D36-A52E-B2F47C72F950}
PEORIA 170413494 | {1EA8CF8C-ECB4-4CEA-BCE6-3A74137F1411}
PEORIA 17041837 | {B68E2FC5-9A54-49EB-9258-EB6EA1DB9D61}
PEORIA 170449256 | {F440C80E-DEF5-43B1-88DC-EE268B4D5DB0}
PEORIA 170453392 | {F0E436AB-11C3-44FF-A180-26BA4D28B36D}
PEORIA 170459596 | {73788ED7-3EB0-46BC-B768-F67E7458E32E}
PEORIA 17046090 | {7EE01833-70BE-4E5D-9E9A-D8D904929AC9}
PEORIA 17048040 | {B68E2FC5-9A54-49EB-9258-EB6EA1DB9D61}
PEORIA 1704877670 | {2FC56DAF-3BEA-4D4D-AF4F-08FDD13FFBA2}
PEORIA 170488630 | {446FC8DD-5D58-4AC8-BAFA-7454D42952B8}
PEORIA 170490622 | {F0790E88-28B0-4563-ADD1-89D97CFB3BF2}
PEORIA 170492888 | {885453EE-C081-4617-8ED9-DAFDFB250BE8}
PEORIA 1704CB | {57BF0C33-990B-4465-98B9-17EDC5A10F72}
PEORIA 1705263072 | {C16CCA7A-E1DA-48FD-9F09-9F2AAA50BC5B}
PEORIA 1705625728 | {CDFD1731-2969-4E09-954B-5DB3F0EB7754}
PEORIA 170567898 | {50E0B9CF-D877-44E3-8923-B1CAE75FDAA7}
PEORIA 170570198 | {B8914B50-2C53-43B9-B50C-8211DA0C4B33}
PEORIA 170587222 | {08C43BB5-02C4-4FB7-9500-39371503D9F3}
PEORIA 170590374 | {8B476FB2-9EFB-4231-AA3D-ADAA150B87C8}
PEORIA 1705999 | {50E0B9CF-D877-44E3-8923-B1CAE75FDAA7}
PEORIA 1705CB | {7B5B2CF8-2901-483C-B55E-83E22B23519F}
PERRY 110114537 | {DCA684FB-D1FC-4FF3-9F51-4170CE54615E}
PERRY 1101200598 | {F3BB7464-D4D3-443C-A678-902DB9A05DA5}
PERRY 1101460229 | {7B35C98C-C7A2-450B-B33A-392880830F23}
PERRY 11015931 | {73456CC8-8BD1-494E-8C64-7A493E5FD032}
PERRY 1101618168 | {253D76B4-3BD5-4865-BAF3-63AA6DE45924}
PERRY 110179696 | {240D21FA-CC4D-471E-B74F-148F84FE5FB1}
PERRY 110185870 | {EA98B02D-6B86-41AE-8783-1ADC45A8F561}
PERRY 1101925053 | {6549D8C5-85D8-4805-BE3C-6F965C4F0199}
PERRY 1101986322 | {C7DAE941-6DB3-4215-863D-56303A6DD35B}
PERRY 1101CB | {30D7373B-D31B-4D5D-82BF-42F5B4929DAA}
PERRY 1101V74 | {03363AA4-45D4-475B-A70A-74AAA6293936}
PERRY 1101V88 | {A9641B76-4245-40CF-B912-6B76F1AD305E}
PERRY 1101W10 | {E1CC4B8A-EEA0-444B-A148-93C085F63A52}
PERRY 1101W12 | {743AA0A1-467D-436E-BBF0-31F00EC2544E}
PERRY 1101W26 | {07DF4B2B-054C-4E25-84AF-DE6FF88C6FF3}
PERRY 1101W52 | {EFFF9048-E08F-4C22-B5E1-9B1A32E0D054}
PERRY 1104175422 | {90731576-6ADC-4169-86FA-CAE47F468CEA}
PERRY 1104175422 | {73B5A601-33B5-473B-B220-C2B115C3A641}
PERRY 1104277242 | {6940DC61-A05C-4039-933B-CB03AC86E397}
PERRY 1104428516 | {15E084A7-E63F-4A4B-957E-37987ACAEB3F}
PERRY 1104489460 | {6743E3EB-2199-42BB-A8C5-E81E71D58EDE}
PERRY 1104531590 | {144A480E-C7E3-412B-89CE-AF99EC3EC7B5}
PERRY 1104858200 | {1CB4B3DE-6FA2-40BE-AA6D-BEA2EDAB4893}
PERRY 1104CB | {76CD31FD-354B-49BF-B176-66B8A5AE25B4}
PERRY 1104W50 | {98891E8E-A196-4377-815F-B850671211F6}
PETALUMA C 11081623 | {90A7C5AC-6CA0-4AC1-AFB4-612DF64B6BFC}
PETALUMA C 1108169982 | {ED738027-93FE-4DE9-B69E-3B9059E1980B}
PETALUMA C 1108208 | {23B65F3B-C52B-4779-BBDA-CC297DB72B38}
PETALUMA C 1108233646 | {380213DC-12AF-4B84-9312-495B969AE9CC}
PETALUMA C 1108296 | {87D8E969-EF8D-4B9C-90F3-5A57DD740C7C}
PETALUMA C 110835448 | {97604ABD-15A6-47B3-9D0B-A46F2D96B582}
PETALUMA C 110835452 | {D67283F3-E166-4B71-B1F9-990D049050F3}
PETALUMA C 110856774 | {E5F8D630-F65C-4493-B471-181129A51D2B}
PETALUMA C 1108594 | {0DEFD988-CCBB-4D32-93F5-9C87FB012CA2}
PETALUMA C 1108600 | {8BF925A0-2A0D-4680-BAEA-CDD0149B229D}
PETALUMA C 1108600 | {B9E22F01-648D-4F6F-B1E0-311BE99AC492}
PETALUMA C 1108618 | {789D2564-FA70-4AAC-B502-21D235CA9BD7}
PETALUMA C 1108632 | {276EDBF0-4288-4842-B2CC-B94871DC6986}
PETALUMA C 1108636 | {BE0D8CE5-BE7F-4D94-B792-C4D840A2819E}
PETALUMA C 1108883512 | {E7FE5BAC-1DF2-49C8-8397-01E71C05FBD7}
PETALUMA C 1108CB | {184EAEA4-EF9D-4F25-94EE-091BC560403A}
PETALUMA C 1109128 | {003177BD-8A4D-4A57-8E37-AC044D50D3EA}
PETALUMA C 1109142466 | {F24143BC-0F3F-452C-9357-0F3FCC2BD0E3}
PETALUMA C 1109259100 | {CBE2D558-4F9F-4EDA-8260-3A87B72F1065}
PETALUMA C 1109373772 | {3DFFA8C0-A5C6-4A12-9D4C-C201315471FE}
PETALUMA C 110948000 | {762F2724-D687-4C14-8C14-CCCD968810AC}
PETALUMA C 1109664732 | {485D794E-EDB7-4779-A265-326DD68DD55C}
PETALUMA C 1109738866 | {0A86DDE1-72D3-4AA4-946A-5E91F4735FDF}
PETALUMA C 11097811 | {FF9399FF-EC04-4AD9-AFCA-8336E87CCAB5}
PETALUMA C 1109820458 | {E3B7A6D0-5E5C-4112-ADBA-8CB389502FA6}
PETALUMA C 1109857148 | {3A66DE77-5865-4829-AC80-A8B849C71DE4}
PHILO 11013700 | {1642E076-5F84-4CD5-A49F-E61735A3F10D}
PHILO 11013700 | {2030F98C-03DF-440F-B393-A2ADFB821381}
PHILO 11013719 | {DC916B78-528D-4B84-AFFA-ED2266E2C210}
PHILO 110137222 | {B4EDF571-A5E6-4473-9456-D58C67AB0D1F}
PHILO 1101431952 | {46DD59AB-B0EB-4FA4-91D2-B47F013974C2}
PHILO 1101433886 | {357240A2-4E16-46EC-AADB-59F78CDBC9C4}
PHILO 1101CB | {A45E0124-BCF3-4DBF-9317-CD21317A326D}
PHILO 11021308 | {EADE9BC7-FA33-4E78-987B-E6772CEF7A88}
PHILO 11021308 | {453E34D2-CEBD-4802-B9EF-E27CABEFF8EB}
PHILO 11021308 | {232A2E07-1164-4F9E-9EF1-D1A7DD6AE797}
PHILO 11022600 | {3CE6E0FA-7B27-4ECA-8734-864D34B81F8D}
PHILO 11022603 | {D922B3CF-2DF3-40A8-BBB7-63EF2AF073BF}
PHILO 11022603 | {A3A878C9-1FF5-4495-AEA5-03F6AA67D889}
PHILO 11023603 | {0E362CE0-6741-4BC2-BB4B-379F4F2F7D82}
PHILO 11025117 | {EE4D0360-0EA1-4D6D-AF70-31E0A33A5A23}
PHILO 1102920 | {BC0A2CA4-638F-47ED-8CA5-834F5A792974}
PHILO 1102928 | {946F4845-815D-4480-AA93-F475D8FE739E}
PHILO 1102CB | {95C075DB-0A6D-41A1-A6CC-0BF07BF73E40}
PHILO 1102CB | {47D11162-DBA1-4478-BDF3-B67846D21C32}
PIERCY 210917515 | {A03EFA6E-C322-4C15-863E-2461E099BF81}
PIERCY 210942383 | {A03EFA6E-C322-4C15-863E-2461E099BF81}
PIERCY 2109906172 | {A03EFA6E-C322-4C15-863E-2461E099BF81}
PIERCY 2109CB | {A03EFA6E-C322-4C15-863E-2461E099BF81}
PIERCY 2109XR200 | {A03EFA6E-C322-4C15-863E-2461E099BF81}
PIERCY 2109XR202 | {D18B1CBA-5F52-4148-99A7-D19633E723D2}
PIERCY 2109XR376 | {A03EFA6E-C322-4C15-863E-2461E099BF81}
PIERCY 2109XR378 | {A03EFA6E-C322-4C15-863E-2461E099BF81}
PIERCY 2109XR482 | {A03EFA6E-C322-4C15-863E-2461E099BF81}
PIERCY 2110799154 | {44306BEB-04DC-4559-BC6D-3AB4A93FC4AC}
PIERCY 2110866388 | {901C47B4-25C2-4C9B-9657-50A16616D760}
PIERCY 2110CB | {6C9416AC-4CC1-4577-A462-96F88C7F1AEF}
PIERCY 2110XR258 | {EB657CB8-596F-4421-86E3-2C8A72D44EE1}
PIERCY 2111CB | {F69D714C-099F-426C-95FD-DACECE33C433}
PIKE CITY 11011720 | {07E52C28-7426-408F-9FC2-C4593A9ACBA6}
PIKE CITY 11011730 | {C0842696-2AC3-4174-B825-FB284EC3DBD9}
PIKE CITY 11011730 | {5771C40B-154E-478C-BBED-0818A68D33F0}
PIKE CITY 1101417084 | {B1F64389-1738-4480-91E0-805F6CAAC853}
PIKE CITY 1101935730 | {CAA18DED-EAEF-41E1-8550-BD2B57FEC276}
PIKE CITY 1101CB | {1B4AEF1E-3888-4CF0-B5B2-91A85959940F}
PIKE CITY 11028803 | {38E34556-3A95-4D26-A889-B202BD8E21AD}
PIKE CITY 1102CB | {C855B1F9-E043-4F7B-B17F-9A4E0F007042}
PINE GROVE 11013166 | {FB4870D6-B142-4F5B-9D0C-2C983965E8D9}
PINE GROVE 11013166 | {A3872159-7E00-4305-B184-0E3361D92F40}
PINE GROVE 110152088 | {1330A2A7-6F05-480E-914F-CD520FD996F9}
PINE GROVE 1101580912 | {185515EE-D08C-4503-8C48-FC208CC16838}
PINE GROVE 1101580912 | {4262276A-62D7-4338-B5E0-880257D660D2}
PINE GROVE 1101844156 | {FDC77BA4-CC53-4957-9327-68448299427A}
PINE GROVE 110194936 | {0F46298C-BD7C-494E-910E-FE65C6C90770}
PINE GROVE 1101CB | {5E0ECFE9-34C5-4F2B-8405-6E29B71598DF}
PINE GROVE 11021222 | {B84BB2A7-38F5-4777-ACCF-AE61211F946D}
PINE GROVE 11021765 | {B84BB2A7-38F5-4777-ACCF-AE61211F946D}
PINE GROVE 1102269286 | {383C6B53-F50A-4636-B23E-F279ECB1A8C3}
PINE GROVE 1102269286 | {163AD319-AD93-4675-83CD-83770D9870B7}
PINE GROVE 11023168 | {E5BA9D9A-CDF7-4CB6-8A65-6116FC9EC4DF}
PINE GROVE 11023168 | {8A9DB402-D07E-4B24-A4A9-6814E94ED6BD}
PINE GROVE 11023168 | {EAFDD43F-F7FF-4388-8EDB-D22261F3737C}
PINE GROVE 11023168 | {D4301AC4-378A-4CC5-A2C2-1573CF7FBDAB}
PINE GROVE 11023172 | {0A126708-7779-4E45-A8D5-6CB2B8C285C8}
PINE GROVE 11023172 | {167A4A24-F545-4250-A89C-0024D49B4222}
PINE GROVE 110235576 | {F4B5AEC7-64EC-4D58-9F21-2F50A7ED3B5C}
PINE GROVE 110235576 | {C8B6F5A4-B7EB-4267-93EF-866DFF4F4584}
PINE GROVE 11024088 | {799123EE-7478-4CB6-8B96-0F2B5EBEDDA3}
PINE GROVE 110245292 | {EB0CF7B2-4A78-45DE-8AED-51D903B9E71F}
PINE GROVE 1102467560 | {0D3BE776-7F21-48C6-8A4E-A95714C0EA5F}
PINE GROVE 11026080 | {49B1FC4B-7FEC-4446-8EAB-613D81FCBE67}
PINE GROVE 11026080 | {B48DDE03-609C-4554-A3F2-3D029A190740}
PINE GROVE 1102625030 | {0890696A-DBAA-42B3-BE6B-91002E6BAFA3}
PINE GROVE 1102684460 | {21AAFEB1-E3E1-4080-B23E-84CD0C3E2529}
PINE GROVE 1102696442 | {7DC1A977-4A68-4FDA-A273-23C4AF2AACBE}
PINE GROVE 110283098 | {6F523CC1-7B62-49B9-AAF8-BD03742BA043}
PINE GROVE 1102CB | {29253623-89FE-435D-961C-4E4487404246}
PINE GROVE 1102L3107 | {501E02DF-AF52-4DB1-94FE-017F8C34A16D}
PINE GROVE 1102L3107 | {591FBBCC-EEF9-4FE1-B289-45062B6C60EB}
PINE GROVE 1102L3107 | {6EA7D312-6494-4B61-A725-EF3D5FFE39F4}
PINECREST 04011818 | {D8E71690-B481-4860-BE72-8B484DD0017D}
PIT NO 1 11011552 | {47AA609B-0BD3-40D9-878F-3D1F5D334A7D}
PIT NO 1 11013312 | {603720E6-C08C-4450-9A1D-FFFC2D98E7C9}
PIT NO 1 11013312 | {78DE20C8-C70F-4F9B-8F8E-C6540F9D903B}
PIT NO 1 1101347184 | {A1FA61C2-1628-4CB0-A1DB-FAB1501D537B}
PIT NO 1 110170952 | {8AC91F5C-D86E-4B8D-B342-7C652EFA0FA1}
PIT NO 1 11019702 | {240B9597-FDF1-4E00-A581-05E13375E11A}
PIT NO 1 1101CB | {185974AB-4212-4B5F-B111-C93E97C24964}
PIT NO 1 1101LR-RC-A | {A1FA61C2-1628-4CB0-A1DB-FAB1501D537B}
PIT NO 3 21011360 | {060881A6-D014-4A68-9103-99AC74B02ACB}
PIT NO 3 21011386 | {4A0A56A3-602B-4EA0-9D5D-4F9EBD3DE945}
PIT NO 3 21011480 | {E236376B-9C17-4833-888F-1B5788910DB2}
PIT NO 3 21011482 | {23C4AB75-7BD7-4D2C-8DD3-FAC1E53F0F0D}
PIT NO 3 2101CB | {5C4A4B21-8DC0-4DD4-BD69-EB88E21328E5}
PIT NO 5 11011614 | {1BEC31F5-3F54-4C7C-921A-7E6673591BD6}
PIT NO 5 11011658 | {B21A40B5-551B-4708-A4A5-34576C3781E9}
PIT NO 5 11011660 | {06EBCEE6-C636-4CF7-B3B5-D5C157499FDB}
PIT NO 5 1101830252 | {330EDCD0-4321-4CD6-9339-87C225C88DFE}
PIT NO 5 1101884224 | {6E4D9B5D-25D6-44F1-A918-522AD02584F6}
PIT NO 5 110190846 | {B00B32D2-7E6B-47E8-9895-8153D924AA94}
PIT NO 5 1101923612 | {D99B829A-FE68-41FB-A0C0-BA93B6F47C39}
PIT NO 5 1101CB | {B85628F4-AFE8-455E-8E14-4DB09FEDE759}
PIT NO 7 1101CB | {E4590054-53CD-4399-A96C-42C934E0E3BE}
PLACER 1101106534 | {62739046-02AD-4CE7-A6F9-18132F783A35}
PLACER 1101208930 | {53E235AC-648B-4E69-8BA8-94C5D0F7B09F}
PLACER 1101CB | {D36692F8-5845-4D8F-B564-14537DDF3E03}
PLACER 1102CB | {498BEDF6-2946-45C8-8A10-174F646330D4}
PLACER 1103238990 | {E0134993-C6C7-47B2-B903-8846B3C865A5}
PLACER 1103284874 | {390506AD-DEF8-4149-9470-E4570BC394B3}
PLACER 1103429574 | {3FC818D4-1421-4E7E-A0F8-41C3D62E44F8}
PLACER 1103CB | {E0134993-C6C7-47B2-B903-8846B3C865A5}
PLACER 1104426944 | {A52EC61D-8C7F-4197-8472-76105B9A8A93}
PLACER 110451732 | {F20DF12E-C49B-40A8-AAFB-7DBBC88F8ED9}
PLACER 110451734 | {0E740EDA-2722-48A5-9962-250FDAF0A7CF}
PLACER 1104CB | {E502BFEB-ED5D-48C9-9524-9ECF207993E0}
PLACERVILLE 1109868678 | {C4A51841-0308-49DA-9C27-2509F9C64A2D}
PLACERVILLE 1109CB | {C4A51841-0308-49DA-9C27-2509F9C64A2D}
PLACERVILLE 111019582 | {1EC71CEE-6F35-4B51-874D-1E06DFFEACB0}
PLACERVILLE 1110421358 | {3AD84F54-48F7-4505-9D9D-4F3421C728D6}
PLACERVILLE 1110953474 | {237FFCF0-1392-49D9-ADF2-6A51785028AC}
PLACERVILLE 1110CB | {8F8EF18B-7E0A-4A9F-9597-8CCBE4E9FBDC}
PLACERVILLE 1110CB | {344FAF1C-9E94-492E-BF33-445657107626}
PLACERVILLE 1110CB | {396926B6-CE02-4BE9-83DD-75CE9B26FF68}
PLACERVILLE 1111508410 | {15D1F2F0-3D88-4B18-AFEC-B03FE833977B}
PLACERVILLE 1111610322 | {E8C6131A-05FF-4431-8BF6-8D1D5F5027F9}
PLACERVILLE 11118582 | {3783BA8A-4769-47A2-BDB8-6B31F03E9521}
PLACERVILLE 1111880534 | {3783BA8A-4769-47A2-BDB8-6B31F03E9521}
PLACERVILLE 1111925936 | {EB7ACE47-AB6E-4D80-8A04-7B710C1A3A26}
PLACERVILLE 1111CB | {15D1F2F0-3D88-4B18-AFEC-B03FE833977B}
PLACERVILLE 111219712 | {BC89062F-CC4C-4415-8BB6-7E334A18CE4F}
PLACERVILLE 111219742 | {2CB1DACB-35CA-492A-AB87-5D8BB9E8AB49}
PLACERVILLE 1112237902 | {8446C529-441F-4799-9032-C2B11A134C61}
PLACERVILLE 1112239390 | {C2806D70-915E-4D74-B0A4-11FF6F4DC395}
PLACERVILLE 111236794 | {79088C82-BF5B-4FBD-B7ED-E08A20855814}
PLACERVILLE 1112566624 | {5020410E-2BAC-41B3-8668-E49899519422}
PLACERVILLE 1112774186 | {5020410E-2BAC-41B3-8668-E49899519422}
PLACERVILLE 1112778710 | {5020410E-2BAC-41B3-8668-E49899519422}
PLACERVILLE 1112CB | {69C7055C-8321-466E-890B-DA1A435F5398}
PLACERVILLE 21061104 | {DC8F828A-9D78-4250-9936-BA54E6245EA8}
PLACERVILLE 21061104 | {A2148132-5AD5-4FA3-8090-8A8E5C2F5491}
PLACERVILLE 210611132 | {5979C967-A047-451E-8861-34B418227857}
PLACERVILLE 210611132 | {23693049-039B-4514-94EB-4E3AE6138ACB}
PLACERVILLE 210616570 | {25ABB496-D703-4991-A7E4-1F1E6F1218C8}
PLACERVILLE 21061792 | {F024A856-072D-4B8F-8BE0-7B4C60D09BBB}
PLACERVILLE 21061792 | {86646534-0F05-47D4-8571-92886F52E7AD}
PLACERVILLE 21061792 | {0E1E8672-B6FF-4248-9EB2-02A0D74E93D3}
PLACERVILLE 210619552 | {D8B8F5B4-A76D-49A6-AA07-ABB6ACBBEBF0}
PLACERVILLE 210619732 | {A0663868-57FC-4799-ACA3-0DE33205B8E0}
PLACERVILLE 2106207892 | {46D41402-E63A-4BF4-B88D-0C6DD86601F6}
PLACERVILLE 2106207892 | {48F4B025-789F-4A27-834C-D86ED7FBBB7F}
PLACERVILLE 21062224 | {BA672D72-863E-4FB8-9458-911126FD31A4}
PLACERVILLE 21062224 | {63093B32-7A32-49B8-9FAA-FADD2F59C84E}
PLACERVILLE 210623190 | {83B5D9E2-BFF1-452F-91D8-11E4F5A6B453}
PLACERVILLE 210631284 | {63CF1C21-8D90-4626-BEF1-66563ACD0DE0}
PLACERVILLE 2106424742 | {88178D84-0C16-479B-A17B-AB0C442DB288}
PLACERVILLE 2106458188 | {A8CF9BF8-F4EA-4590-A57D-350C35CF2CAF}
PLACERVILLE 2106560252 | {8DBDB785-6868-4880-8D93-9F473FA4D71A}
PLACERVILLE 210658118 | {86E99440-83ED-4726-A6BC-38E34FEB5B33}
PLACERVILLE 2106654798 | {A0E26123-2630-44D6-878A-7499EADE6DDF}
PLACERVILLE 2106654798 | {548DA595-CB57-4C00-9CFC-95768443E2EA}
PLACERVILLE 2106654798 | {04BA8CD0-1E81-40CB-86DC-B52B61F52B67}
PLACERVILLE 2106654798 | {CFCDB2E9-63F9-4505-AC86-1079E598E5B0}
PLACERVILLE 2106690720 | {54CC5A36-B48B-4A52-BEEB-BD82A30CD4D3}
PLACERVILLE 2106694470 | {056C1FC6-B316-402A-B278-ED4481D5EBA6}
PLACERVILLE 21067522 | {A7A5500C-8FAC-46D4-9BD4-7B5D3F1E7024}
PLACERVILLE 21067522 | {05CB5905-C4AF-4D34-BC46-D49FE7A9E135}
PLACERVILLE 2106789730 | {2F084C4F-2FE5-44F1-BDAC-60F898CE382C}
PLACERVILLE 2106869108 | {D72E7887-E0C5-4F33-A9C9-A4C38BAA3F23}
PLACERVILLE 2106909258 | {BA672D72-863E-4FB8-9458-911126FD31A4}
PLACERVILLE 210692012 | {C89C3F78-8047-4151-A21B-FC3CD22D755E}
PLACERVILLE 2106935216 | {5F5BDF47-A09A-4B9E-BE8D-D898A7829ED8}
PLACERVILLE 2106935216 | {2AFE09FA-88B1-4B78-BACA-DA079C6170B5}
PLACERVILLE 21069712 | {8E4E0CC9-6B59-4215-87F2-98199853B2C7}
PLACERVILLE 21069712 | {566B5755-B4E0-4A81-B2A5-BF871142A1CA}
PLACERVILLE 21069712 | {C89C3F78-8047-4151-A21B-FC3CD22D755E}
PLACERVILLE 2106CB | {86E99440-83ED-4726-A6BC-38E34FEB5B33}
POINT ARENA 11011296 | {827A54D0-0188-46E1-B6F0-E7D696DF4D89}
POINT ARENA 11012637 | {827A54D0-0188-46E1-B6F0-E7D696DF4D89}
POINT ARENA 11013702 | {5DD49BEE-09C2-4674-9D89-3A76B7F55110}
POINT ARENA 110137426 | {F28897FF-7717-4F16-B4F4-76C153F4DC6F}
POINT ARENA 1101474 | {89838C41-7EDA-4C42-BDDA-1698278E3E6F}
POINT ARENA 1101476 | {E7660F7E-BB9F-4573-B70D-C3EB843F48E4}
POINT ARENA 1101478 | {E4F90CB8-51CF-477D-BA6B-9F60A2DBE5A1}
POINT ARENA 110147952 | {6151271A-BC5B-476A-8700-C63C19F32AF9}
POINT ARENA 110147952 | {607BB8CE-F9B2-4916-8A2A-75F68C179EBC}
POINT ARENA 110147952 | {8A4E1914-FCD6-47C4-B7F7-B8EAB64FF580}
POINT ARENA 11014923 | {827A54D0-0188-46E1-B6F0-E7D696DF4D89}
POINT ARENA 110183354 | {B01D0AA7-5805-4227-AB93-F941564BB56C}
POINT ARENA 110198224 | {27796358-F4BA-4B47-9271-54399DB166CB}
POINT ARENA 1101CB | {72A22D65-E2E8-42C5-897F-8C8D23CE5089}
POINT MORETTI 110110726 | {F7013B1A-D0D7-4319-B5E7-A5441451D41D}
POINT MORETTI 110112122 | {9CD1A9B9-F6CA-4FBA-A861-B1CC3280E49B}
POINT MORETTI 110135874 | {0FEDAD4D-EB4E-4A00-90BC-1C811C4F991B}
POINT MORETTI 110136514 | {6B3803C4-78D9-4845-848A-F16561C51AFC}
POINT MORETTI 1101415734 | {EF958110-BB67-48F0-BCC0-A7C84F7DFFDE}
POINT MORETTI 11015074 | {744CBA45-CA46-417A-809B-2361EA738493}
POINT MORETTI 11015078 | {84EDE3F6-5DE1-49F9-B5C1-589D669F552F}
POINT MORETTI 11015078 | {FA346406-A3D0-4066-8116-4806F77ED4DD}
POINT MORETTI 11015104 | {2D522AA5-8F8F-4B96-B755-D0E01134E6CB}
POSO MOUNTAIN 21011703 | {703579BF-EEA4-4200-951E-8470D02B6E41}
POSO MOUNTAIN 21012181 | {908C371E-60A0-479A-AB4A-419AF9711AF4}
POSO MOUNTAIN 21013990 | {00D1CA6B-BA0D-48A2-AF6B-44F02D16A6FD}
POSO MOUNTAIN 21014456 | {80FE859C-5651-4408-BF07-1945D67AD54A}
POSO MOUNTAIN 2101535138 | {6A7EE3BE-DAC0-4BED-82C9-530638BEB40B}
POSO MOUNTAIN 2101618176 | {D2CF2809-E105-4AFB-BF3B-4CA49C8A57B2}
POSO MOUNTAIN 2101720132 | {D06620A3-21E5-4CBD-8A5D-D10ADF106C84}
POSO MOUNTAIN 2101730862 | {9DEB7641-86B6-4F2C-89D5-F69B09FFF284}
POSO MOUNTAIN 2101CB | {53C5BA88-884F-48FE-B87C-D7D9589897A5}
POSO MOUNTAIN 2103CB | {471EF9F3-EACE-4C92-877C-E8B23885AEA4}
POSO MOUNTAIN 2103CB | {FFDB1F5B-AEE3-4CB6-9A6F-D3D25805592F}
POSO MOUNTAIN 2104388671 | {B9DBC9F0-4947-4732-B802-049D3AB22FD5}
POSO MOUNTAIN 210448268 | {59412086-F782-4166-B6FC-4A718057E9E9}
POSO MOUNTAIN 2104CB | {AA81189C-0FB0-446B-B000-4E0A59F32937}
POTTER VALLEY P H 11051904 | {E5533EF6-8C9C-453F-A4F6-7E2D2F1E338B}
POTTER VALLEY P H 11051904 | {99C448A1-95CE-4373-846C-DC41955DCE78}
POTTER VALLEY P H 110537476 | {216E9E12-5043-456A-946D-A8BF7CCC2C71}
POTTER VALLEY P H 1105518488 | {2518929B-41FC-4606-9508-5145B64EB406}
POTTER VALLEY P H 1105546986 | {0F563298-4ED3-47AC-A822-118BBD6BD4FC}
POTTER VALLEY P H 1105640888 | {DDBE967D-510E-4AA9-8699-FA1CD4531A33}
POTTER VALLEY P H 110564118 | {8488C210-9205-46DA-B608-037FFFBDBA9E}
POTTER VALLEY P H 110576498 | {0A0C5F0B-CE32-47C8-9E33-CC208CAF8F95}
POTTER VALLEY P H 110595878 | {8D4490B9-6B4D-4F2D-8A60-88D879FECDA8}
POTTER VALLEY P H 1105990354 | {18F7A415-6C0E-4E68-A9B1-1EAFDA3A8A3D}
PRUNEDALE 110722232 | {79203305-2019-407A-BD6B-B79DCD967425}
PRUNEDALE 110722448 | {79203305-2019-407A-BD6B-B79DCD967425}
PRUNEDALE 110725695 | {79203305-2019-407A-BD6B-B79DCD967425}
PRUNEDALE 11073062 | {B4535491-B5FA-4BB1-97C9-04A3F2F345D9}
PRUNEDALE 110736920 | {3866DD60-BF41-471C-88D6-BF070A4B7C9F}
PRUNEDALE 11073712 | {9CE15D70-9BD3-4411-955B-AE06E56BCA8C}
PRUNEDALE 1107615134 | {90B96B90-2667-418D-BE51-F2E1D444C567}
PRUNEDALE 1107CB | {9055CD6F-1385-4DAA-B189-3CEA20BFACDF}
PRUNEDALE 1110134336 | {091A78C8-ECBA-474E-9159-E8F99C6CD779}
PRUNEDALE 111020059 | {CE89D4FD-128E-4AE3-8F53-291BB3498CD8}
PRUNEDALE 1110215712 | {2061D73E-702C-4340-93F9-B456241757C3}
PRUNEDALE 111022104 | {EA4AEF31-2B29-42E0-BD25-BED069AD0B05}
PRUNEDALE 111022160 | {55A8BEF6-0A82-4DF2-9C14-9045CBA42576}
PRUNEDALE 11103080 | {CE89D4FD-128E-4AE3-8F53-291BB3498CD8}
PRUNEDALE 11103716 | {7B756F98-069D-434F-A340-DDF69576DD23}
PRUNEDALE 1110607060 | {A8CB8177-0C64-42D1-A7A3-6215FC559483}
PRUNEDALE 1110711490 | {93AC9321-6B71-4898-8604-38459E393013}
PRUNEDALE 1110826224 | {664C5E09-6BFA-4699-B652-D7925B82EDA0}
PRUNEDALE 1110CB | {43A69DC1-4C36-4A90-B444-3F421C39E759}
PUEBLO 110247720 | {1AE19971-F682-43DD-B35E-DF767DF7D39D}
PUEBLO 110256136 | {1AE19971-F682-43DD-B35E-DF767DF7D39D}
PUEBLO 1102662 | {1AE19971-F682-43DD-B35E-DF767DF7D39D}
PUEBLO 1102671 | {1AE19971-F682-43DD-B35E-DF767DF7D39D}
PUEBLO 110298730 | {1AE19971-F682-43DD-B35E-DF767DF7D39D}
PUEBLO 1102CB | {1AE19971-F682-43DD-B35E-DF767DF7D39D}
PUEBLO 1104105708 | {56D5B737-FEFA-47EB-AD6B-EFAA05EC398B}
PUEBLO 1104105708 | {F4390A92-E1EF-4E00-AAD7-21DFA3AD530E}
PUEBLO 1104105708 | {C4D60A99-15D2-4609-A786-584E99B2DB18}
PUEBLO 110447912 | {C8E61154-612A-4546-9186-D3C997DC10CD}
PUEBLO 1104536006 | {EB53C457-3734-430A-A35B-404EF848B72E}
PUEBLO 1104580658 | {9B7A438C-25F0-43CD-AA1E-F241960C452C}
PUEBLO 110459106 | {A4183870-AFD5-4FAE-BBEF-716EC88D1AB1}
PUEBLO 1104640 | {425E28B1-6940-4649-A8D4-A58D56D174C1}
PUEBLO 110475462 | {937DE59D-E2A4-4423-B890-4B26446D8098}
PUEBLO 1104968601 | {17489714-54AD-404A-B125-398990CB9745}
PUEBLO 1104CB | {065E1455-5FE2-4E00-BCA8-63E4665BA32B}
PUEBLO 11053022 | {6A034A59-B030-4B42-9C02-B5134DF1FD0A}
PUEBLO 1105348368 | {CC4E6B7C-3A75-42D2-8AEA-EBA3500E2172}
PUEBLO 1105419634 | {D8943DC9-C3F8-4085-8F3C-401265EC905F}
PUEBLO 1105426584 | {B12F894A-AA1B-44DD-A0B2-C56DB14BFA67}
PUEBLO 110548260 | {AAA01DFB-2A03-4703-89CA-818D743EB4AB}
PUEBLO 110548264 | {25D9312F-33A3-462C-A74B-0E8AD09547FD}
PUEBLO 1105637242 | {76F5AEE6-B528-46EE-B628-BA0E8A65C596}
PUEBLO 11056379 | {4C36ECEF-7C4D-4D69-9431-57DD553433FD}
PUEBLO 1105642 | {2AEE294B-FE8D-44F1-8029-584BDB7857EF}
PUEBLO 1105684564 | {97C6787C-1A07-4147-A43F-2ED249921F2B}
PUEBLO 1105696 | {78AAB710-6DDE-407F-827D-71666B977FA6}
PUEBLO 1105716 | {A6A5315D-8A62-41D0-A9DC-ABFF612B9C6E}
PUEBLO 1105CB | {88C9735D-F7D9-42F3-A471-0E595E4AABD3}
PUEBLO 21021326 | {F776B1CF-724B-4DB6-A87F-FF45F4D5AD0B}
PUEBLO 2102279478 | {F6CC89DA-35B8-467A-8291-CB7D725323B5}
PUEBLO 2102279478 | {472C23CD-FA88-4D7F-8AEE-A853BB7EB294}
PUEBLO 2102378860 | {0747EA03-0104-4C39-B232-B182B2FD4D1E}
PUEBLO 2102391312 | {413AA2AE-389A-445A-BDEE-AA83E1C4150B}
PUEBLO 2102595938 | {3F0F141A-08D9-4BE0-A763-3CF7287B44A5}
PUEBLO 2102618 | {2D821F7B-3CD2-4C8D-9060-9FD2240F0305}
PUEBLO 2102656 | {95F0930E-F4E9-4090-B429-18E6DA1F891D}
PUEBLO 2102698 | {7C6C3906-0002-4B70-8FDB-4D71FEE84B86}
PUEBLO 2102698 | {EFBE7067-1C69-45D8-A9C8-472AE1406928}
PUEBLO 2102769868 | {D239647B-6B20-452B-9F55-A164C653DDB1}
PUEBLO 2102773926 | {F9DE541A-2DEB-4CE3-95CE-87C59E155BAE}
PUEBLO 2102850102 | {5456D4F0-1D4A-4239-AAEE-AF57D0A5D9CB}
PUEBLO 2102943820 | {BC3FC9AC-589D-48EE-984C-94B4C353EDD1}
PUEBLO 2102CB | {EB7314AB-7754-4D90-B11B-A641443B251F}
PUEBLO 21031970 | {6032ABA6-AF20-49E5-AB8C-90F3BD669D29}
PUEBLO 21031970 | {D374E70A-F10D-42BF-BFC9-DC52D8E99DC6}
PUEBLO 2103253312 | {D97500C1-9AD3-4748-953B-EC7E95FBED39}
PUEBLO 2103489964 | {5AAB74F0-F546-46F3-9229-78031722C605}
PUEBLO 2103678 | {2B71AD28-97C6-40FE-8942-41E801469F28}
PUEBLO 2103678 | {57474873-8703-48A2-B4C1-3A3164040E5C}
PUEBLO 2103678 | {C4F91447-A8AB-4AD6-8ED3-CCF85038539A}
PUEBLO 2103678 | {80E79C4D-3B76-415E-BA02-A8236360DA4C}
PUEBLO 2103694 | {6D5E4552-6F62-4C84-BA40-091D03218161}
PUEBLO 2103694 | {119B581D-A9F7-44FB-A1DF-83F31225E8F3}
PUEBLO 2103694 | {37307117-7712-4B70-890E-D9B3D42408D3}
PUEBLO 210398394 | {5615A966-3F9F-4D7C-A54E-42D751963807}
PUEBLO 210398394 | {49549F40-A326-4458-963A-8F0223D6E156}
PUEBLO 2103CB | {BBAA1B5B-10DE-4ADA-9508-3668952B4672}
PUEBLO 210438686 | {2EF3B194-CF16-451C-8101-C9C0F09F91D8}
PUEBLO 2104600010 | {C5942BEA-FB0B-4F3F-A02A-15F17AB72955}
PUEBLO 210475612 | {85E8B645-D897-4F43-ACD2-C6688D48A799}
PUEBLO 210475612 | {9E2011FB-314A-4E1F-BD85-EF9AED4B1586}
PUEBLO 210478504 | {EDE87926-F33E-4FF5-A8C5-E53D4266C7FF}
PUEBLO 210478504 | {CCC100A9-4ACF-4B5B-8F9F-CE807A5602C4}
PUEBLO 2104895310 | {C669F706-9156-43FF-93FE-C8CD4A8C9FE9}
PUEBLO 2104CB | {2BA2C655-091B-4624-81C3-023373AB75A1}
PURISIMA 1101104948 | {9148C0D8-07A2-46DD-848B-3477C31F1CBB}
PURISIMA 110149394 | {3CCA61DC-2699-479D-8396-73463C6B90FD}
PURISIMA 110154728 | {B456B97B-6207-41D3-9457-CFE202A63FCC}
PURISIMA 1101745714 | {36493B4F-D721-4EF8-8C20-789AA6F613EE}
PURISIMA 1101CB | {72519E2E-220A-434F-A310-3B8078E34E61}
PURISIMA 1101CUSTREC | {0E276FF7-E726-49F1-899E-4DA4E59DCF2F}
PURISIMA 1101Y40 | {0E276FF7-E726-49F1-899E-4DA4E59DCF2F}
PURISIMA 1101Y44 | {867AA1B1-4446-48B6-9D80-8E314456C23F}
PUTAH CREEK 110211461 | {3ECD8F0A-04CC-46EF-B13C-F4D244326B49}
PUTAH CREEK 1102202158 | {305442B7-01C9-4B14-8BEC-02CC707E6339}
PUTAH CREEK 110242982 | {C95502A9-654B-4E80-A0DB-D1ADCC72F914}
PUTAH CREEK 110246012 | {8A0CE410-7B0B-44D2-93E6-B3B628B03752}
PUTAH CREEK 110258340 | {EC7E3E82-534C-45F0-825C-A06402B7C3CE}
PUTAH CREEK 110264044 | {17B7D6FE-5F00-4D1F-ABC4-4972705BA2FB}
PUTAH CREEK 110267858 | {14F48B8C-8A8F-4490-B11D-9FE802AC416A}
PUTAH CREEK 1102710384 | {807BE66E-A7AB-4BA1-B8B2-4ADCA53B3B50}
PUTAH CREEK 11028352 | {89E381E1-F842-49C9-837A-CF37A4D6EF66}
PUTAH CREEK 1102CB | {EC7E3E82-534C-45F0-825C-A06402B7C3CE}
PUTAH CREEK 11033783 | {520DA4C4-E38A-4EBC-850C-F11EB0848411}
PUTAH CREEK 11033783 | {DC819193-AC84-4B68-B90F-9360B8F647B7}
PUTAH CREEK 11038362 | {520DA4C4-E38A-4EBC-850C-F11EB0848411}
PUTAH CREEK 110396792 | {520DA4C4-E38A-4EBC-850C-F11EB0848411}
PUTAH CREEK 110546162 | {B44C5067-6D0E-4713-9558-13070DEDA962}
PUTAH CREEK 1105617260 | {3FECE4A6-EA4F-4BAE-A132-55F5821EF41C}
PUTAH CREEK 1105640768 | {6A4C4853-E421-4FC6-A61D-D6238A9BF8B1}
PUTAH CREEK 1105665952 | {4E22FE5C-076B-41AE-91C0-55E48D475856}
PUTAH CREEK 1105748272 | {6B7B9ED0-0961-41C2-AC06-403CFA67D331}
PUTAH CREEK 11058812 | {6A4C4853-E421-4FC6-A61D-D6238A9BF8B1}
RACETRACK 170310850 | {56B3B60A-49BB-43A9-9EE8-443CF9005AA3}
RACETRACK 170310870 | {2C817939-22E6-4D0A-962C-2F9F458E8593}
RACETRACK 170311270 | {A39A6646-0D8C-4936-AA1B-2F242D5EE8C4}
RACETRACK 170311270 | {4D284085-0A99-44D1-B3C1-6B407E0C252E}
RACETRACK 17032553 | {155070BB-C96B-485B-99BD-6B770FC28FA3}
RACETRACK 1703291534 | {DD8D18EB-6C40-49BD-A83E-15020ECE0B91}
RACETRACK 1703441460 | {97A23306-EDD8-4486-932A-B1EF7AA42161}
RACETRACK 1703759144 | {93C7386E-15CE-4864-890D-1F577B21A67A}
RACETRACK 1703799924 | {C9E5A604-B8A8-4373-B662-59F2DA781935}
RACETRACK 1703CB | {155070BB-C96B-485B-99BD-6B770FC28FA3}
RACETRACK 170423195 | {B312FC00-28CF-4046-A454-B618E8197B3A}
RACETRACK 170455798 | {7E0EED7A-2775-40CE-B357-57739361FC2E}
RACETRACK 170455798 | {BEA46C83-5B85-48AF-BC84-E91A4D14111D}
RACETRACK 1704787277 | {A4A54225-A10C-4355-B12E-80025AE0188E}
RACETRACK 1704CB | {128383E7-96CF-4707-8041-13E4B9B7C999}
RADUM 1105420576 | {87051ACA-C17E-4D55-A6B8-1444F89F63EA}
RADUM 1105806392 | {597A5CEE-82F6-4D96-ADE3-E225B0B39A15}
RAINBOW 1106367670 | {C4DA848B-BD47-442D-B50D-ACDC98148281}
RAINBOW 1106D2116 | {ADCF8749-96F9-4F4F-9256-CFE0E46A793F}
RAINBOW 1106D7399 | {37D7033A-95CE-4BBC-B643-34090CA01EF5}
RAINBOW 1106R104 | {37D7033A-95CE-4BBC-B643-34090CA01EF5}
RAINBOW 1106R1500 | {ADCF8749-96F9-4F4F-9256-CFE0E46A793F}
RALSTON 1101100040 | {803AEA1D-DC84-436D-9016-11A398DCA769}
RALSTON 1101420730 | {C5ED9BB6-82EE-4A74-A509-3A42E5E8C396}
RALSTON 110148936 | {EA4820C6-602A-444A-A1BC-AC0CC345F5D7}
RALSTON 1101836528 | {D07EF46B-1212-40DA-B007-3854AE9B04F4}
RALSTON 1101CB | {C5ED9BB6-82EE-4A74-A509-3A42E5E8C396}
RALSTON 11021601 | {EF774119-F7FE-47E7-8D97-134D999F3AC9}
RALSTON 11022028 | {24F66B4A-94A3-4B18-925C-2BF0060C2435}
RALSTON 11029126 | {EF774119-F7FE-47E7-8D97-134D999F3AC9}
RALSTON 1102CB | {A920E716-9436-4401-AAF8-C3A905DCBD43}
RALSTON 1102CB | {9D20FBB5-A64F-4DAB-A67C-F85E7D67E017}
RAWSON 11031486 | {B3CD7E05-0789-49F2-B8EC-1C4664F6B36A}
RAWSON 11033314 | {7BD4E626-0623-483B-B7FA-C43993C96595}
RAWSON 1103428534 | {34DEAF44-1967-46DA-ABAD-F242FF32190F}
RAWSON 110385334 | {4FE71C2A-D73C-4875-8301-3BC6248AF0F6}
RAWSON 11039052 | {5385D62F-B5C4-4043-8BE0-13D849B5717D}
RAWSON 1103CB | {2BC26C95-B90F-49BD-888B-1F85DFF0BF79}
RED BLUFF 11011334 | {0CEFEC1C-E5A7-4802-97C4-53CDE555B5DF}
RED BLUFF 11011334 | {58917EF0-B5CC-4A7F-84AE-72327892A691}
RED BLUFF 11011556 | {4D690574-08A4-46C5-A589-9057A98DE023}
RED BLUFF 1101453972 | {02EE82C7-BB67-4B4A-8D7D-2704317B6250}
RED BLUFF 1101718428 | {DBFC2760-2222-4664-B92A-F340A001584C}
RED BLUFF 110176020 | {737A9C64-4C75-4B29-81A5-32595FB9B2D8}
RED BLUFF 110185837 | {732E8B04-C22F-4EFE-9E5B-6F8C0B4155ED}
RED BLUFF 1101CB | {DB04D68A-27FA-4FDB-A3B9-5AB0FF58478F}
RED BLUFF 1102CB | {C7F1169F-7F4A-4C3C-8022-D0BF917F0199}
RED BLUFF 1103234278 | {A3CC161F-1B95-41A3-B30A-2B1FE8B4155F}
RED BLUFF 1103881860 | {7C5F1641-95F9-4454-945D-1F8DC8A8FEEF}
RED BLUFF 1103CB | {7FAC2369-AB0B-45B1-8121-0A58A05D1C75}
RED BLUFF 11041302 | {D6DFAF59-685A-49A8-AAFF-CFC87952A858}
RED BLUFF 1104135854 | {34D16F6F-D35F-44EF-AB3E-A4D9BCAF8509}
RED BLUFF 1104135854 | {7A5937DD-12B9-45A4-A4A3-79E6F1361431}
RED BLUFF 11041566 | {EFAF3860-6049-4F8E-AF4B-3D1B6758C8FE}
RED BLUFF 11041630 | {89D48A42-926D-430B-837E-EDF8AFB821B9}
RED BLUFF 1104318634 | {073E91C5-4104-4384-BDFB-3256B5699418}
RED BLUFF 1104318634 | {1DA2E5AE-9242-49AA-BB96-81CB6ED0C071}
RED BLUFF 1104450404 | {6A4FE1E6-8265-47E9-9AE7-AFD0FAD872F9}
RED BLUFF 110451238 | {E9A98F80-2CD6-4193-969F-CD417879D03A}
RED BLUFF 110451238 | {A009EB05-74B9-408F-92A3-F0FECB371AA0}
RED BLUFF 1104CB | {2E1FA774-5A9F-4570-9AF6-F0EFBD272BA5}
RED BLUFF 1105146070 | {2E98A968-0F7D-44C0-B9F5-8D4D032F12CD}
RED BLUFF 11051564 | {9D2C06EE-ACC3-496B-9742-675775229618}
RED BLUFF 1105161818 | {31D1DD7F-CFDD-44BD-88FD-B9B13228B34E}
RED BLUFF 110529222 | {C9741448-890F-43D3-BE5B-974633A51AC5}
RED BLUFF 1105494814 | {E1B190FC-1EE2-469D-B651-D7219D666721}
RED BLUFF 110585632 | {2E98A968-0F7D-44C0-B9F5-8D4D032F12CD}
RED BLUFF 1105CB | {FEC690E3-0920-4E0A-BCDB-0BA1BA1CD1E2}
REDBUD 1101400 | {928EDF6A-AE60-4D52-BF0A-EE27518314CC}
REDBUD 1101558812 | {D899F1F5-45AB-4336-87CB-D9FAA637B64B}
REDBUD 1101702118 | {F9ABFDAE-2AF1-4AF1-9286-01BD248CDBAC}
REDBUD 1101708166 | {3492968E-3545-4212-B771-A444F5766479}
REDBUD 1101754544 | {084CA147-3467-4FE1-A862-8038A9834EE2}
REDBUD 110191960 | {44037CD8-DFED-4315-85FD-100A68145FAE}
REDBUD 1101CB | {3ED5FB3A-A2CD-4F13-ABBF-430305FFB318}
REDBUD 11021212 | {97D03C05-997A-42BF-BC34-AFEFA779FFC0}
REDBUD 11022013 | {D29B0306-223B-4BFF-9389-253396BA7A0F}
REDBUD 11022651 | {7552F1AB-2FB9-46CD-BC7B-64CF9D8D2618}
REDBUD 1102432 | {D29B0306-223B-4BFF-9389-253396BA7A0F}
REDBUD 110244119 | {D29B0306-223B-4BFF-9389-253396BA7A0F}
REDBUD 1102510 | {01484F25-B16D-4119-BFC6-A19899DBC158}
REDBUD 1102523244 | {6D1DA35B-F9DF-481E-9974-60E83F30F3F5}
REDBUD 1102922 | {C7B2F311-1F3F-41B5-BEF7-2254E70DD401}
REDBUD 1102CB | {5D4D8690-5B01-4EDA-9ADD-A0F82EE8F0D4}
REEDLEY 1104218022 | {CFE218EA-E766-4A80-8978-21707A20B8F1}
REEDLEY 1104243924 | {15D80CB3-430C-4D10-9907-2D2A3FAA2A64}
REEDLEY 1104274990 | {1B9CB438-3D64-400D-8827-441645AF1444}
REEDLEY 11047340 | {D4D37A1F-1F84-4F45-A461-E357A71565B6}
REEDLEY 11047892F | {1B9CB438-3D64-400D-8827-441645AF1444}
REEDLEY 1104887932 | {DE4A3F35-1098-43E3-AFD1-E0057FBA11D6}
REEDLEY 1106277111 | {00295CCB-7A82-41D2-8029-CD6AC5E909AD}
REEDLEY 11067260 | {A8E9DE08-E312-4E8B-B35D-C8DBE141AFFA}
REEDLEY 1112226548 | {C2478E24-1A2A-421D-B2B6-2DBB6FC30E5C}
REEDLEY 1112477952 | {EE0E49AF-2EA8-49CD-B4D9-4F587BDF49BA}
REEDLEY 11127240 | {0ED60982-9EAF-4A20-AAB0-618C5740E1E9}
REEDLEY 1112729390 | {209E1547-0942-41A3-9F02-1BF24BAF3FFE}
REEDLEY 11127919F | {0ED60982-9EAF-4A20-AAB0-618C5740E1E9}
RESEARCH 2102183888 | {0695BA0D-172B-47D5-B979-B42944990BF9}
RESEARCH 210263274 | {8B10C5DA-98B0-4CF4-9701-AF65D62D25BE}
RESEARCH 210263274 | {17B0EA25-D73F-4786-903D-45184AAF8053}
RESEARCH 2102644462 | {27A7DE88-D994-4126-81BF-F7729B85F967}
RESEARCH 2102779174 | {748A5B81-A79F-4986-90A0-2D101111DB07}
RESEARCH 2102CB | {16057A1D-A77A-4434-99E8-5E9C232075A4}
RESEARCH 2102D537R | {748A5B81-A79F-4986-90A0-2D101111DB07}
RESERVATION ROAD 110123818 | {1ECD8C6D-A6A3-47D1-B4A1-AA5957CE70E7}
RESERVATION ROAD 1101370948 | {0D34A135-9DC9-4BFA-B08B-5EA1A68C4D2C}
RESERVATION ROAD 1101383718 | {1ABACE31-DB52-4FF0-A8F2-ED3023CBC398}
RESERVATION ROAD 1101586340 | {1DF65F8B-4121-4333-A1ED-1B97DCAFF9C3}
RESERVATION ROAD 1101603176 | {73F2B01E-992F-4811-9C1C-FAEE6D81DDE3}
RESERVATION ROAD 1101975548 | {F1FA9138-E071-404A-A9E5-572EE0A580EB}
RESERVATION ROAD 1101CB | {D8F287F2-9F47-4079-84BA-BB2B78537313}
RESERVATION ROAD 110222136 | {C1E68105-3858-4273-9D69-DD27BF248870}
RESERVATION ROAD 11023030 | {B5391BD5-06CA-49EB-98DD-175A1FD20C36}
RESERVATION ROAD 11023032 | {966AAD61-7205-4A6B-9491-7F1C72E1ED94}
RESERVATION ROAD 1102303870 | {EC6A2D53-31D4-4E66-874C-302D8025180C}
RESERVATION ROAD 11025567 | {91E13287-B303-49F0-B0BF-E026D1BB49DF}
RESERVATION ROAD 1102741002 | {46F7E3C2-8411-49FA-8FF3-85D847712575}
RESERVATION ROAD 1102CB | {FE25DCBF-8FD2-4D0B-8589-850A3EE5ED4C}
RIDGE 0401615024 | {2FF0ED31-3EEE-48B6-8DEB-84EBA3AAB0F6}
RIDGE 0402199970 | {FE7862FE-E265-47C4-88F2-7778C84DCCC4}
RINCON 1101146053 | {3AEF342C-12B8-4583-92B0-7B9C6AC3A567}
RINCON 1101146053 | {891C4DDB-0D9F-4C0C-9738-5A61FD1CFA5C}
RINCON 1101146053 | {5AD9DA27-2087-463C-A145-A7AC2E69A5BB}
RINCON 1101146053 | {70713FBA-9F92-422C-B122-EBCB5E381F1B}
RINCON 1101146053 | {A840483E-2B53-4879-AC4C-E57DDA8C6E75}
RINCON 1101205854 | {4CE77434-2594-41C5-A3D5-54C3032AEF7A}
RINCON 1101576 | {F4C78492-32F9-47FB-AA37-4818CAE3C60E}
RINCON 1101576 | {F2BD1A32-60A3-49CF-8B6A-1E7442C97021}
RINCON 1101576 | {10BF1DCF-F31C-4230-BD34-98A3E060927C}
RINCON 1101580 | {AD59A6B0-468F-47D6-BF9D-7AE313662802}
RINCON 1101580 | {45DAEF94-8CBC-41FA-B3AC-23C4DF1DF209}
RINCON 1101828284 | {1ACDA537-7716-4EAF-B16D-5EF3BEF5AF6E}
RINCON 1101839669 | {C0A31C4D-93ED-42DB-A4BA-1A3FEE5BD36B}
RINCON 1101CB | {F102360D-42FF-446F-88B4-F431C95B2DC4}
RINCON 1102640 | {2FAB6430-43D4-439B-B7B8-4BB8DFD0CD27}
RINCON 1102644 | {A2A06826-B5AC-4037-94EC-F135DC826294}
RINCON 1102666 | {5390E08C-4E4F-47B5-99B2-BEFA4415BC86}
RINCON 110275816 | {5390E08C-4E4F-47B5-99B2-BEFA4415BC86}
RINCON 1102782389 | {06E2A336-248D-48CA-909C-FCEA57AB6ED4}
RINCON 1102802628 | {9E318DA6-BA18-4E46-B1B6-5DFB20722EC9}
RINCON 1102CB | {5988784C-46D2-4999-AEE8-C136D520A366}
RINCON 1103198 | {7F16B5BC-4060-4BCC-9EE1-D9EAFE5FD541}
RINCON 1103198 | {8F98E58F-9114-4DF1-BE64-986306B23E37}
RINCON 1103472 | {003E8DD3-C7CE-4179-B86D-B637E24AA54E}
RINCON 1103474 | {6A5817A5-7FC3-45B7-8DC9-2BBA0FD82034}
RINCON 11035152 | {1D81D8F5-A042-428A-8894-895D8E08C89E}
RINCON 1103568 | {A91227FD-6BAA-4D3E-82C2-58CC21F46A65}
RINCON 1103568 | {F346707A-4D92-4697-9B47-3B190D523E0A}
RINCON 1103649194 | {FA366DAF-5808-4A0C-A859-9FABFF5A65F0}
RINCON 1103655192 | {40BB98CB-5E98-49A0-9B1A-45D346011806}
RINCON 1103925054 | {A6030DDB-D47E-40D8-89FA-641FC9E29ED5}
RINCON 1103CB | {2A534FE3-EF17-402C-9700-8C33AB455C66}
RINCON 1104207458 | {1E4D7366-24E5-4493-933B-743F7C171401}
RINCON 1104786782 | {30C622EF-C0BC-4395-AF79-9E6C502E7680}
RINCON 1104CB | {DDE06CFF-C1C8-453E-9DCE-C51203C62E9C}
RIO DELL 1102326250 | {44430000-2BB3-4535-9661-3159F49C9C3D}
RIO DELL 11024230 | {83499CD2-C0F0-4DE8-A7FA-CECB9345AEE8}
RIO DELL 11026151 | {68D3E51B-D82F-468F-8693-722B02390473}
RIO DELL 11027124 | {AA9B3AC3-107D-4281-A065-CEC882DC5747}
RIO DELL 110275970 | {C155999E-0638-4738-B652-2E7910103A63}
RIO DELL 11028852 | {5E0A571A-4E57-4C9B-881D-B7EA8F011B21}
RIO DELL 1102CB | {63E5D0E5-2789-4426-928C-2DB4A6E4E38A}
RIO DELL 1102CB | {68D3E51B-D82F-468F-8693-722B02390473}
RIO DELL 1103CB | {E559D593-187F-4090-8DFF-D65A895D2975}
RIO DELL 11041504 | {95CE948C-0754-44B6-A9FF-1D767799797F}
RIO DELL 110438332 | {A95F636D-9823-4D40-A219-A36C35F660D1}
RIO DELL 11044834 | {18699EED-90D9-48F0-8FBD-43F0E5B04388}
RIO DELL 1104638760 | {E30D7B6D-BCB9-4C14-A0F7-CEA4F3CF381D}
RIO DELL 110470960 | {B2A085D5-4C4C-4026-B04B-46CF38E6CB2B}
RIO DELL 1104772210 | {95426769-BEDA-440D-ABB4-0984480A5A7B}
RIO DELL 11048768 | {F40CB029-270F-46C5-9305-F30A68FC7241}
RIO DELL 110492712 | {56AAB81A-EA84-498C-8B2D-C89BEB9CDBC9}
RIO DELL 110494614 | {E61FCF85-DBAD-4787-B510-EEC62F294D7C}
RIO DELL 1104CB | {3542FFF1-69DE-484C-998D-CF53D71F0157}
RISING RIVER 11011530 | {BE242D62-FFF6-4E73-8F41-DCC9F0527F50}
RISING RIVER 11011532 | {0B37F6F1-99C2-49A1-BA55-86410A38B8F1}
RISING RIVER 1101693718 | {7BF92ABF-3D2F-450D-A6D4-24924D1418C4}
RISING RIVER 11019032 | {8F4CC463-393C-4538-A842-1BB0282A8F17}
RISING RIVER 1101CB | {9F15BDD3-391E-4F68-AFF5-FA940D11CF0D}
ROB ROY 210410298 | {F407D1C7-AF54-4B98-B726-B5AC300E0031}
ROB ROY 210410714 | {0A7E84D0-9946-4059-AC56-BD0EC9107E3A}
ROB ROY 210410954 | {A588ED32-95D8-43A3-8FC4-5077DBA91F77}
ROB ROY 210410960 | {2E6975B3-903D-45C9-9C7D-960FEDF8E472}
ROB ROY 210410960 | {C07D4A32-B72B-4156-AF73-6F99A9D3449A}
ROB ROY 210412596 | {272F711A-D76D-479D-B7FF-5C57D964944A}
ROB ROY 2104236422 | {17AE212C-70C5-43DE-B73A-B89730E76AED}
ROB ROY 2104289018 | {910ACC8B-0F85-49A9-B3AA-00CD612D0B4C}
ROB ROY 2104422016 | {C8EA39C1-18B8-478D-878B-46339453F455}
ROB ROY 2104464844 | {ACE07E60-A85A-44BA-8598-8AD2924EF583}
ROB ROY 21045304 | {B079AC67-F69E-4839-9DB7-69A2C23DFB56}
ROB ROY 2104588930 | {E4D9306A-AB16-4DC5-A47E-93AFEF1B142A}
ROB ROY 210458988 | {7184B90F-F9A7-49D2-BD4C-EA882512830E}
ROB ROY 210467520 | {4F244FE6-F52A-45B3-B8F6-00E33F844A26}
ROB ROY 2104974520 | {A306B6A6-F4A4-47EC-B2AB-9B74651A417E}
ROB ROY 2104CB | {869A1D07-AF0C-4C1B-B4FB-3299F6D51C09}
ROB ROY 210511028 | {4A62797B-ED6E-4F95-8491-E8F25B750F09}
ROB ROY 210512474 | {FFC04C14-5557-4FC3-9795-3587569ECB50}
ROB ROY 210512582 | {9F9A8C20-EA90-4789-ADB1-26DC34BBE385}
ROB ROY 210512584 | {12D75819-A6BC-4E85-B057-219FF075B3A4}
ROB ROY 210512586 | {ABFDD865-4FD2-4A37-B95C-CF3A9E9EFA30}
ROB ROY 210516586 | {70BBA93C-6F85-4E1D-B761-E4CCEB78E467}
ROB ROY 210538430 | {337FC985-3DD3-4483-BEDA-15F859835747}
ROB ROY 2105439972 | {23249E89-01FA-48A5-93E2-8ED08FB21EEA}
ROB ROY 21055090 | {C85C607F-B343-4E7A-AB80-396866C4BA0B}
ROB ROY 21055090 | {97F0E264-6757-4E01-B858-9C73FC0BF875}
ROB ROY 210571630 | {7097C41D-4FD9-4503-BEF9-0B96E72F7C88}
ROB ROY 2105796388 | {A5D16FDC-5172-43FE-911F-ACEAF50DBA1C}
ROB ROY 21058281 | {ABFDD865-4FD2-4A37-B95C-CF3A9E9EFA30}
ROB ROY 2105931192 | {1C63E144-CC28-45E6-852A-59F6783E5E65}
ROB ROY 2105933888 | {3378E1E2-CCFC-44E3-9591-EC7C33C0BEEB}
ROB ROY 2105CB | {65F8EE18-25DB-48C0-8EE8-63D74E373DA3}
ROCKLIN 1101CB | {F2FB3423-E5C6-49D2-A6A3-6EDB6BF7B645}
ROSSMOOR 110136572 | {DFEFEF45-5177-43DB-BC8B-7506E80A5515}
ROSSMOOR 1101381506 | {F15F15B0-93BF-491C-865F-0C7F534D44AA}
ROSSMOOR 1101460980 | {4A6866B6-05EC-4630-B805-2F47511F44ED}
ROSSMOOR 11018132 | {71494031-9F05-4CC0-A953-4E31E51E28B7}
ROSSMOOR 110181770 | {4CA94395-6849-4C23-B9A9-BA346C47AF36}
ROSSMOOR 110192164 | {DC8B2F83-F0B1-43FA-9405-78D681BB4EBC}
ROSSMOOR 1101CB | {E76B2183-0811-41C5-8C57-31DB4D93EC1E}
ROSSMOOR 1101L501R | {192A3563-130E-4748-AE0C-092D67B95727}
ROSSMOOR 1101L503R | {93932C89-B87A-4F1E-B65E-D8FDB2772713}
ROSSMOOR 1102457174 | {1EF93EFB-6EC5-43CC-BDCD-9E975921D8A6}
ROSSMOOR 1102CB | {92F6E341-F0BC-4716-8F01-EF905EEF4BF1}
ROSSMOOR 1103CB | {A42F88CD-4606-4D31-BD89-060DAE686890}
ROSSMOOR 1103W514R | {D9FD5122-71C5-470A-9067-11BD4B38DBDB}
ROSSMOOR 1104305926 | {E7EBB058-9B4D-4CDE-B87B-5DAAEF3E4493}
ROSSMOOR 1104389334 | {7E49235D-F9DC-4244-B485-160BD4AC02B8}
ROSSMOOR 110479146 | {DE1365E8-AE71-4371-B78C-316604B54A0D}
ROSSMOOR 1104892332 | {ADD4BDEC-74F1-459E-86A1-4DF14021647A}
ROSSMOOR 110493664 | {D2330A0C-459B-4F6C-BE3B-0AABB85A2AF8}
ROSSMOOR 1104CB | {2B644C8A-1232-4056-B6E3-B09CD0D7D415}
ROSSMOOR 1104L530R | {6405B4BF-BAC2-4EF5-A48E-1FFB58F38756}
ROSSMOOR 110542088 | {F53E229F-D577-425D-ABDE-BA35CE2A6278}
ROSSMOOR 1105CB | {2CF05CCD-DA30-4E66-88FB-8AE7485C3DA7}
ROSSMOOR 1105W564R | {D451D811-EC32-4500-AC69-1F4D8CDBABAC}
ROSSMOOR 1106166550 | {4AEDCE3D-BF5C-4D21-A955-F5F1D5680D0E}
ROSSMOOR 1106384042 | {7E910363-02B7-4903-815B-B702BBD4A69D}
ROSSMOOR 110639424 | {DFA21900-F572-4D0B-90D6-E67080E9EF87}
ROSSMOOR 110639424 | {12C41010-8690-4E2B-AC58-964769362CF2}
ROSSMOOR 110654472 | {DE34AA94-F995-444B-B0E9-519FC6F293D6}
ROSSMOOR 110665858 | {DE34AA94-F995-444B-B0E9-519FC6F293D6}
ROSSMOOR 1106841730 | {A6B74454-D4C1-496B-84A9-0B2166285148}
ROSSMOOR 1106CB | {2DB57022-ABC5-45C1-B548-D5C0C8717502}
ROSSMOOR 1106CB | {DFA21900-F572-4D0B-90D6-E67080E9EF87}
ROSSMOOR 1106CB | {419AC994-D5ED-4F03-8570-4744F2BAF12E}
ROSSMOOR 1106L522R | {35E6FC31-93E6-466C-8E12-BDEF19C3F3E9}
ROSSMOOR 1106L541R | {F81A28E8-7235-47FA-8A4D-F6D87B334C4A}
ROSSMOOR 1106L552R | {52DEF6FB-138D-4E67-B717-53642F74F0D5}
ROSSMOOR 1107857172 | {02242195-DF47-49D6-A6EF-C9A51FB3D431}
ROSSMOOR 110798488 | {748E6AB1-94A7-498F-8F09-FF430BCD1517}
ROSSMOOR 1107CB | {DC54959B-747A-4CC9-B9A5-4B8CDE5FA47E}
ROSSMOOR 1108180088 | {79F8CD15-91A5-4922-9C30-E743E1A159BA}
ROSSMOOR 110845268 | {7DDF8536-9630-4E95-BAC2-3F8D7B68665E}
ROSSMOOR 1108543356 | {9FF00501-65FD-4E14-AFDC-F4B11FE19B4B}
ROSSMOOR 1108CB | {812F7F32-99CA-4B11-A2F5-E536332A91A6}
ROSSMOOR 1109266602 | {C56741FC-B98A-4CE9-A61D-A05F5CB14F16}
ROSSMOOR 1109724062 | {80876183-ECA7-4120-8036-545B0D2B5AC8}
ROSSMOOR 1109724062 | {2D5FE1CC-7A21-49C2-BCB1-D308E91FC77A}
ROSSMOOR 110982962 | {72BC10DA-E2B4-4F9E-B1C6-B2A54D23C7DA}
ROSSMOOR 1109847274 | {886E8B4C-F26F-42C3-BC9C-0CCD43A2C958}
ROSSMOOR 1109847274 | {3141710D-4E1F-480A-88B2-BC542204BF63}
ROSSMOOR 1109847274 | {0CE8F530-A970-46AD-9EB5-F1661AB9BB9E}
ROSSMOOR 1109890534 | {24E172FD-D392-49B4-BDCF-9D27B2C7E92E}
ROSSMOOR 1109892648 | {07D08030-E53C-4555-923F-76DCDA7152BE}
ROSSMOOR 1109961536 | {6DCAEE0E-EF55-4731-9878-3906C6B80014}
ROSSMOOR 1109CB | {A19250ED-73EF-497C-80D4-3643AA1817C6}
ROUND MOUNTAIN 1101CB | {C6179221-3CD6-4B67-835E-943EE03CA383}
RUSS RANCH 110196276 | {35E834E5-9FE3-4B04-BFD2-7F38E4FACAB8}
RUSSELL (SMUD) 210141212 | {A07C96F4-8449-421A-915C-8369960CFDEC}
SALINAS 11043018 | {37BE6D71-E3BC-4DC2-9D89-ECD973BA9436}
SALMON CREEK 1101194 | {4BB38AE8-B760-4E43-B459-E75BDA0EF348}
SALMON CREEK 1101196 | {05737260-3AA4-4F7E-BF36-A5BD94AF80DD}
SALMON CREEK 1101242382 | {196179E3-0F18-4F79-A1AB-13E8430D60AE}
SALMON CREEK 110137368 | {5DC6F02B-24BF-4504-9E01-B7C3B166BE28}
SALMON CREEK 110137368 | {4871E88C-317C-471F-A579-A7D86B4A7AD4}
SALMON CREEK 1101460 | {227E29C2-4875-4BDB-945B-C5CAEB5F0B81}
SALMON CREEK 1101567868 | {51ED0676-1306-4CF0-BD67-6B5222667B7A}
SALMON CREEK 1101567868 | {4BB38AE8-B760-4E43-B459-E75BDA0EF348}
SALMON CREEK 1101571972 | {AC8C3E38-A041-499C-9BB2-FE26BAA0252C}
SALMON CREEK 1101654 | {FFF2586F-2F7B-403E-A22A-6FE170AFE85E}
SALMON CREEK 1101660 | {DD137AF2-2749-480C-8784-159970C4FC2E}
SALMON CREEK 1101668 | {4AA7E9BF-D824-42F7-B4F3-AF51F29BCC9C}
SALMON CREEK 1101676 | {4DCB6ED2-9B7F-4AF7-86F4-3A84466B49F2}
SALMON CREEK 110188998 | {2FFE3F5E-20F1-4C4A-B741-4DF0040A4D91}
SALMON CREEK 1101CB | {227E29C2-4875-4BDB-945B-C5CAEB5F0B81}
SALT SPRINGS 210110416 | {3B618A90-1F99-49FA-8702-76A28A158E81}
SALT SPRINGS 21011216 | {CFBBFBB1-419F-4DD9-BB1F-9B2617993BDF}
SALT SPRINGS 21011232 | {9EF30C64-8412-466B-8695-929E20570E0C}
SALT SPRINGS 210117012 | {6DEB16A6-E94C-4F55-B525-DA7D39192AB7}
SALT SPRINGS 21013116 | {DE9905F1-4C65-4778-858E-371103A18BB4}
SALT SPRINGS 2101935178 | {E756833A-3717-4186-8FEB-E91C2CD3CEE8}
SALT SPRINGS 21023118 | {D994308E-6BA7-47A2-B17C-AE5C708F1F3C}
SALT SPRINGS 21023142 | {82FE0D9D-1FBB-4AFC-A891-DB6D49616A6D}
SALT SPRINGS 21023142 | {02A7F8A8-C04E-4BEC-9371-7E028745EF63}
SALT SPRINGS 21023142 | {31EFB8EC-9037-4E2A-A03A-16D15C4387DC}
SALT SPRINGS 21023142 | {D4B9D4DE-EBBA-422D-A84B-7EBF5D569DAD}
SALT SPRINGS 210237300 | {635F8134-C2A6-4C23-A242-6F5A1291D1C6}
SALT SPRINGS 21024796 | {3283BC52-8DC8-4138-8A4A-A54B9DB31F1C}
SALT SPRINGS 2102817165 | {B55D466C-C953-4591-90F5-4F6196439FC2}
SALT SPRINGS 21028442 | {02C4638B-890A-4131-8AEF-2E0622DB34D6}
SALT SPRINGS 210297924 | {77733CA8-C469-4656-B2CC-06892BE8F14F}
SAN ARDO 1101610148 | {F18C83A7-CEE5-4B8D-BCBF-91CD7A22A1C2}
SAN ARDO 1101650772 | {95D85FFC-A839-44B4-BC87-E5DB06C5C285}
SAN ARDO 11017054 | {67AA257B-431D-4AAD-A8EC-E3FDCC37246D}
SAN ARDO 11017094 | {A9BAF716-D950-4219-B81C-E6209F590D56}
SAN ARDO 11017632 | {05828C1E-8E18-466B-88E7-9FC0E3CD182B}
SAN ARDO 11017945 | {67AA257B-431D-4AAD-A8EC-E3FDCC37246D}
SAN ARDO 110193072 | {67AA257B-431D-4AAD-A8EC-E3FDCC37246D}
SAN ARDO 1101CB | {D178EAD0-51DA-46C3-AC83-7A5FC311BC88}
SAN ARDO 1102323708 | {99FC5371-1655-489D-BA84-20DCFA934D5E}
SAN ARDO 1102502 | {DAB3BC36-43FB-41D1-88AE-89CBCEF6CBDB}
SAN ARDO 110265604 | {A30EDBA7-9AAC-4E4B-A35C-8F3268903239}
SAN ARDO 11027000 | {A30EDBA7-9AAC-4E4B-A35C-8F3268903239}
SAN ARDO 11027030 | {531BE6B3-C431-4299-B6F9-340C07FC847B}
SAN ARDO 11027066 | {8AD3688B-AF38-466D-9653-33A0316A94CF}
SAN ARDO 11027107 | {EB6B4095-ED29-484F-973C-3079393E2455}
SAN ARDO 11027109 | {703D63B2-9038-4829-BAA8-1350FFA37ECC}
SAN ARDO 110273254 | {DAB3BC36-43FB-41D1-88AE-89CBCEF6CBDB}
SAN ARDO 11027437 | {3EC83540-191F-4FC4-9131-F0D0CC76889C}
SAN ARDO 110283166 | {A30EDBA7-9AAC-4E4B-A35C-8F3268903239}
SAN ARDO 1102896438 | {9EB13092-0095-4090-9968-38872A3310B9}
SAN ARDO 110291894 | {3A8CC481-FD54-4503-B6C3-B374A7E06AA7}
SAN ARDO 110294020 | {A30EDBA7-9AAC-4E4B-A35C-8F3268903239}
SAN ARDO 1102CB | {A30EDBA7-9AAC-4E4B-A35C-8F3268903239}
SAN BENITO 2101295566 | {02E6ABF5-EA12-4934-8526-CDD1BECA0A7E}
SAN BENITO 2101310344 | {704F36F9-D5B3-4825-B3A9-C3E524F82C72}
SAN BENITO 2101355426 | {309BC145-CE1F-4552-9344-E193E2F32C60}
SAN BENITO 210136912 | {26DCF52C-88DB-4369-A95E-5AA543DE6A37}
SAN BENITO 210136912 | {90A67B0B-7B04-4738-A6BC-63EA48062380}
SAN BENITO 2101506268 | {704F36F9-D5B3-4825-B3A9-C3E524F82C72}
SAN BENITO 210192468 | {01EC9E13-C42F-4AE1-9ABA-978B217EC65C}
SAN BENITO 2101CB | {D701BA36-CC53-4635-AF00-A21AD8BDB3B2}
SAN BENITO 21024918 | {3E995A52-2E2B-4A8B-8296-4A7FC20162C6}
SAN BENITO 210275262 | {5F376FC3-2A9D-4ADF-B538-90322F89F684}
SAN BENITO 2102CB | {3E995A52-2E2B-4A8B-8296-4A7FC20162C6}
SAN BENITO 2104785888 | {A0912651-34EB-4686-B7CD-51CC5436D4BA}
SAN BENITO 210488772 | {1ED2FD17-894E-4836-A934-5237FD5BF8EA}
SAN BENITO 2104CB | {BECA105B-BD3C-4CFB-85DF-E12EFB68ADA7}
SAN BERNARD 1101438074 | {BF5DD9D5-AD1F-4BC7-AC27-542684EB7C5A}
SAN BERNARD 1101641042 | {46FF504D-69DB-445C-A616-F2DCD009D8E4}
SAN BERNARD 1101830398 | {0FCD66A3-9E49-49FB-A934-531E12B8CE6F}
SAN BERNARD 1101CB | {A1011A88-A66E-4DA3-B03F-1383046CA8FD}
SAN CARLOS 0402CB | {5D32D1B4-08FE-48B9-8413-A6C8374335DE}
SAN CARLOS 0404CB | {997E35A5-4F56-4E03-9F74-715398B359A5}
SAN CARLOS 0405CB | {55F8A6BE-5507-412F-A65C-4CFD7B83CA1D}
SAN CARLOS 0406CB | {E4554E11-1488-4093-BA83-414508537E1C}
SAN CARLOS 1103313472 | {5D822BC7-216C-455F-A29D-9BF065B0A46B}
SAN CARLOS 1103586832 | {02A7DB92-9630-4650-93A6-9495D8FC0CB0}
SAN CARLOS 11039148 | {976CCE27-9CBA-45DD-8002-F8BFB98C14D4}
SAN CARLOS 11039148 | {2AF16592-8ACF-4420-875B-6CA353988F31}
SAN CARLOS 110436864 | {9E2BE648-1876-419E-9EA6-9561CF55CBC8}
SAN CARLOS 1104636064 | {9E2BE648-1876-419E-9EA6-9561CF55CBC8}
SAN CARLOS 1104699632 | {29D0150D-9878-4E59-901F-2306DBADDF8B}
SAN CARLOS 1104733896 | {45C2D967-E7B2-4C4E-B6BA-EDA724402EF2}
SAN CARLOS 110475210 | {30A0D7F0-FF87-4B5E-B98B-6A0711429281}
SAN CARLOS 1104833770 | {184D8D5D-E270-4177-8D06-41B2ADC4598A}
SAN CARLOS 11048846 | {4B35CC98-8B7D-4556-87A5-A4000634AA4A}
SAN CARLOS 11048942 | {7C12A412-D2AF-4E21-A226-597936BFB6C3}
SAN CARLOS 11049010 | {98FA686F-C0FD-4E53-94B4-4278583D2FA4}
SAN CARLOS 11049052 | {3B6CB851-40C4-4A4E-8C82-B4A7B88943F2}
SAN JOAQUIN #2 110310320 | {6E730337-737F-4AF4-89D0-F209BD78A056}
SAN JOAQUIN #2 110310320 | {73DB8416-0959-40A9-9784-A1AC456605F9}
SAN JOAQUIN #2 1103157026 | {5512EE79-F6AF-4543-8A7B-B7E11740B6C7}
SAN JOAQUIN #2 1103212664 | {5450FF12-8A34-46AB-A5D2-C442B92DC01C}
SAN JOAQUIN #2 1103CB | {65F04F88-77E2-416B-8718-E84D34A90738}
SAN JOAQUIN #3 1101673480 | {1AD6607D-F312-473D-9241-E313EE11C5E3}
SAN JOAQUIN #3 1101751914 | {3E893698-E7EF-451C-8E5C-76F173901057}
SAN JOAQUIN #3 1101CB | {5A8D30A3-8AE5-4F6B-B53A-735A17ABC0FB}
SAN JOAQUIN #3 110210342 | {F2F4DFE2-A71E-4AEB-AA05-9FF7D56E28F8}
SAN JOAQUIN #3 1102CB | {F2F4DFE2-A71E-4AEB-AA05-9FF7D56E28F8}
SAN JOAQUIN #3 110310368 | {B3F85F33-B4F9-42AA-82E4-462763566D30}
SAN JOAQUIN #3 1103363884 | {625BCE43-4A6B-409B-86FF-4FF4FD3C75B3}
SAN JOAQUIN #3 1103374484 | {94DD32BF-346F-4771-B618-F98877DD57D7}
SAN JOAQUIN #3 1103403515 | {4CAF538D-CE7F-452E-B2C8-DD5DB29918D4}
SAN JOAQUIN #3 1103403515 | {FF81549D-0FDE-4FB3-A90C-3283E1A7D150}
SAN JOAQUIN #3 11035565 | {02B55053-8173-4178-BF76-6387F3BD910B}
SAN JOAQUIN #3 1103976942 | {662AF8BD-C39C-4C44-9890-8BB7973ED23E}
SAN JOAQUIN #3 1103CB | {A6A3BCCC-F462-4ECA-85D9-4927341E1902}
SAN JUSTO 110136902 | {37C0E6FA-9A39-4134-9B6F-8111077BFC3C}
SAN JUSTO 11014002 | {2C164092-CA7A-489F-BE73-58BB17CAEFD1}
SAN JUSTO 1101CB | {6AD7BBB4-B1FA-43B0-AA8E-62099AF74BBC}
SAN JUSTO 1101CB | {01D6D09A-4701-4A4A-B6BC-8E8154C01835}
SAN LEANDRO U 1109936988 | {0A0CA719-3BA2-4B10-8DAF-28B4D94E2A5D}
SAN LEANDRO U 1109CR002 | {0A0CA719-3BA2-4B10-8DAF-28B4D94E2A5D}
SAN LEANDRO U 1109CR182 | {A2C189F4-1155-43D0-9466-3E701D18918E}
SAN LEANDRO U 1109CR284 | {42064D42-EDBF-4ED5-8222-65863B241E1D}
SAN LEANDRO U 1109CR344 | {D888F259-DA4B-44A5-A254-AC7BF27B35F0}
SAN LEANDRO U 1114213524 | {A807698D-F940-498F-A1CC-0E26E202721D}
SAN LEANDRO U 1114415780 | {5532AE5B-2A9C-4A33-8635-E69715765EC3}
SAN LEANDRO U 1114458451 | {968A63FA-7805-450A-99C2-EB254D5B48D8}
SAN LEANDRO U 1114501762 | {C98515D1-8118-4F7F-9133-7ABF5BE205C0}
SAN LEANDRO U 1114523960 | {A807698D-F940-498F-A1CC-0E26E202721D}
SAN LEANDRO U 1114653758 | {535694D1-FE48-4344-BC96-5C27E6A571BF}
SAN LEANDRO U 1114MR544 | {399AB5C7-22B7-4F32-8432-A7E05E9E2D06}
SAN LEANDRO U 1114MR545 | {4B9E4541-F21D-43AC-ADB7-3A92CC33D20B}
SAN LUIS OBISPO 1101302148 | {6095BEE0-0C36-47E1-939F-BFF38B2ABD81}
SAN LUIS OBISPO 1101483444 | {6095BEE0-0C36-47E1-939F-BFF38B2ABD81}
SAN LUIS OBISPO 1101592368 | {87C2089E-844B-4CDB-8CA8-FEE8A9986F8E}
SAN LUIS OBISPO 1101CB | {AD6746AA-B778-4E12-B7CD-DBCB8C9B3412}
SAN LUIS OBISPO 1101V12 | {8FC2A9EE-B601-409D-8255-6619716FEDEB}
SAN LUIS OBISPO 1102357407 | {607A19A7-FE06-4D0F-B488-D2CD33F1131A}
SAN LUIS OBISPO 1102V96 | {48C4E8E9-57B9-4973-B056-E1FB481593A7}
SAN LUIS OBISPO 1103153199 | {47D9D526-74AC-4FE6-92E3-2FC62834180F}
SAN LUIS OBISPO 1103191498 | {53668CA1-F0BD-426B-87AA-933BC191323C}
SAN LUIS OBISPO 1103365572 | {AF070101-B27C-4E73-95B1-32ABEB0162BE}
SAN LUIS OBISPO 110342344 | {EB029C6B-1104-4127-A12F-6B1C6DB20B5A}
SAN LUIS OBISPO 1103486690 | {EB029C6B-1104-4127-A12F-6B1C6DB20B5A}
SAN LUIS OBISPO 1103CB | {E103D78B-3107-47BD-87A1-E99667F6EAD2}
SAN LUIS OBISPO 1103CB | {80BB619F-1520-4563-BF62-E97585F4D6B9}
SAN LUIS OBISPO 1103V82 | {FCC7352B-1F1B-4520-9419-DD9582012EFB}
SAN LUIS OBISPO 1104236895 | {C973CDEF-EC23-4057-BBA7-53EE9EC7C18D}
SAN LUIS OBISPO 1104459340 | {A3CD7649-1CF1-47C7-BAC6-D853ACFE5E9E}
SAN LUIS OBISPO 1104507764 | {7DD3FAA8-10F0-4EBA-BCB6-5E20A1982C3A}
SAN LUIS OBISPO 1104721823 | {CD120F30-B41B-4ECF-BCCF-D7752F5F6E79}
SAN LUIS OBISPO 1104777686 | {4B433B40-0A9F-4E4A-AD28-C0C25FE24FB2}
SAN LUIS OBISPO 1104798282 | {4B433B40-0A9F-4E4A-AD28-C0C25FE24FB2}
SAN LUIS OBISPO 1104982992 | {48D82405-914A-45BE-AD86-2A9FA02155BB}
SAN LUIS OBISPO 1104CB | {1E7B350B-AD4E-4AFC-A31E-0B3A3DCAB1B5}
SAN LUIS OBISPO 1104CB | {12F1A144-2063-4E28-8860-F6ADF2052849}
SAN LUIS OBISPO 1104V10 | {553967E8-15E4-4695-8C2C-6D609687BE1B}
SAN LUIS OBISPO 1104V14 | {25830136-A5D5-4A08-9B85-05018D7569FD}
SAN LUIS OBISPO 1104V40 | {84A17C4B-1356-4E5D-9790-C7A137661BEE}
SAN LUIS OBISPO 1104V46 | {02896B1A-0763-4C6D-956E-B1F4B47D7741}
SAN LUIS OBISPO 1104V46 | {CBD36712-B594-4F34-A37D-472C41AE69E4}
SAN LUIS OBISPO 1105796050 | {81973749-CAB3-49C6-B105-0C3D389524EF}
SAN LUIS OBISPO 1105796050 | {1A101991-3846-4FAA-AA28-18EF626C5B54}
SAN LUIS OBISPO 110596874 | {5F18F1B6-CBB8-4C1C-BF98-6DFB5D98EA76}
SAN LUIS OBISPO 1105994498 | {81973749-CAB3-49C6-B105-0C3D389524EF}
SAN LUIS OBISPO 1105CB | {81973749-CAB3-49C6-B105-0C3D389524EF}
SAN LUIS OBISPO 1106359656 | {087F0030-803E-4C49-946A-34AD10AB6C1E}
SAN LUIS OBISPO 110676140 | {B624A5E1-E20B-47A2-B81C-D2BE021754FD}
SAN LUIS OBISPO 1106809986 | {C04A8A77-2923-4392-929E-CA5CCA0C5A48}
SAN LUIS OBISPO 1106CB | {9774EED9-2266-4E1B-A8CF-06100CCCBF9F}
SAN LUIS OBISPO 1106V92 | {C52A9A84-A488-4A38-B021-D43C1B677295}
SAN LUIS OBISPO 1107136678 | {20AA80FC-38F3-451E-A79F-A0EADE4A8B5E}
SAN LUIS OBISPO 1107168196 | {1874B6D4-324E-48F8-9278-EEA356F45778}
SAN LUIS OBISPO 1107248566 | {93AB4944-1A1F-422D-B748-968CE7493B5C}
SAN LUIS OBISPO 1107456456 | {3DF66803-0F69-4309-AD56-FCA17132AD95}
SAN LUIS OBISPO 1107834556 | {33B1C341-9620-418F-AA59-B21E9EF2425B}
SAN LUIS OBISPO 110788962 | {3B54DCC0-9E34-4A0D-BB42-D31181D2C4D7}
SAN LUIS OBISPO 1107981014 | {FD8BA716-29C5-4BDC-8A9D-F523FC0D7B3D}
SAN LUIS OBISPO 1107CB | {FE7ADF6B-5FAD-4650-8E18-1F81A8FDEE84}
SAN LUIS OBISPO 1107V02 | {1413E321-0BD6-4E14-989C-C8FF6A4A6DD1}
SAN LUIS OBISPO 1107V18 | {B173AA79-0772-4E9C-A86B-1D2E09D38BFA}
SAN LUIS OBISPO 1107V58 | {3B54DCC0-9E34-4A0D-BB42-D31181D2C4D7}
SAN LUIS OBISPO 1107V60 | {331D14B2-6B0F-4273-9F56-8DD687C4B860}
SAN LUIS OBISPO 1107V62 | {331D14B2-6B0F-4273-9F56-8DD687C4B860}
SAN LUIS OBISPO 1108144690 | {FA97EBC4-7DF7-4291-B59F-FFD92DA4891B}
SAN LUIS OBISPO 1108348318 | {051A03F6-32E2-4CDD-AEAE-C9F09D230069}
SAN LUIS OBISPO 1108497078 | {523E0E57-4D82-43DB-81A5-54E463CC2157}
SAN LUIS OBISPO 1108497078 | {BB99A914-387F-48D8-919A-BB8BCFE90D9F}
SAN LUIS OBISPO 1108597518 | {22E96A5A-3667-455E-A58A-C0A9770DDF94}
SAN LUIS OBISPO 1108883526 | {0947A58E-A054-4FCF-BC8E-28577FE76435}
SAN LUIS OBISPO 1108CB | {BB99A914-387F-48D8-919A-BB8BCFE90D9F}
SAN MATEO 04048554 | {5D607F0F-481D-4D2A-862A-231FF7901489}
SAN MATEO 0408CB | {72F4A567-A9CD-48CF-9E88-AA2F9E6053A6}
SAN MATEO 04109068 | {5F8605AA-7B64-48E3-B49A-133A5E452602}
SAN MIGUEL 1105765824 | {5DAC96E6-D800-4242-8BE0-8DEA9CB14558}
SAN MIGUEL 1105CB | {9DE0BAA2-B8C4-4631-BEBA-CFB3AF750506}
SAN MIGUEL 1105CB | {E94610AC-EC7D-49B9-AE54-6AEAB572BD2A}
SAN MIGUEL 1106428314 | {44EE4AB8-A105-4D73-948F-79D5A2357B21}
SAN MIGUEL 1106605393 | {AE0302DD-E961-46A4-9A94-0278CDDD5E25}
SAN MIGUEL 1106CB | {DC9AC6DA-C366-497D-A431-13D5888CCACE}
SAN MIGUEL 1106N34 | {19CBB8DD-B0DD-40C9-99D6-9DC6A38717ED}
SAN MIGUEL 1106N38 | {7351BABC-DA39-4A67-B463-17C1BA8F0959}
SAN MIGUEL 1107401092 | {038EAEF3-38F6-4732-A338-B905F4A6A1F1}
SAN MIGUEL 1107608338 | {FE0C3808-9DBD-4EB0-98BE-950CD466D1E5}
SAN MIGUEL 1107895760 | {65A32950-46E1-4C84-AA7A-A0D0D951C05E}
SAN MIGUEL 1107954082 | {D0A5F575-D022-443D-85F2-E2AC3A537B53}
SAN MIGUEL 1107CB | {9AFFCF48-B4BB-4816-B96D-D0BF56E32579}
SAN MIGUEL 1107R54 | {44EB9D6F-C95C-4275-8EE8-1FAA212EEB1F}
SAN MIGUEL 1107R58 | {65A32950-46E1-4C84-AA7A-A0D0D951C05E}
SAN MIGUEL 1107R66 | {D2A5E177-BE75-4C23-A08D-DCCEBD7AADF8}
SAN MIGUEL 1107R66 | {C460B3EB-84FA-4843-B153-26A891483044}
SAN MIGUEL 1107R88 | {C7BB1503-DD28-48B3-9C96-3F6DD2B88AD1}
SAN PABLO 1104266518 | {42E9ACA1-0D1F-4BA6-BAA1-48060EFAFA14}
SAN PABLO 1104340304 | {6D0EE36B-9581-4C70-B356-16618206EC5C}
SAN PABLO 110448074 | {542170A0-AF21-4477-9621-56E272BDAD4D}
SAN RAFAEL 11011210 | {C15D2B27-11D0-43EC-9B15-374D2297640F}
SAN RAFAEL 11011250 | {0DD641FC-11BF-40FB-8EF7-3A88160AB0B4}
SAN RAFAEL 1101312 | {94913A85-54AF-40E8-AC46-898A3991828B}
SAN RAFAEL 110139156 | {332AA22A-A859-478E-AF82-419A23B67FF8}
SAN RAFAEL 1101546438 | {D3437865-FD72-4BD7-976C-C052BE1AC57C}
SAN RAFAEL 110168970 | {0E23B264-3DB8-4CEC-B1FE-F1CB20A30CF5}
SAN RAFAEL 1101725106 | {1A3DCF6A-D8D9-4366-A0A3-6456AFF85AD5}
SAN RAFAEL 11042235 | {D55F51BD-E8EF-4769-B2FD-EC63A6CBD0C9}
SAN RAFAEL 1104289890 | {8E0CAF6C-8AA8-4CDE-A8BC-7F142F4EB9CC}
SAN RAFAEL 1104717160 | {D55F51BD-E8EF-4769-B2FD-EC63A6CBD0C9}
SAN RAFAEL 1104CB | {33CCC2F4-F827-4C07-9171-27096EF33E3C}
SAN RAFAEL 11051278 | {DF15C3A9-3287-472A-8D42-2F8516FD478B}
SAN RAFAEL 11051806 | {3E85D65E-30F3-42DB-9ECD-6ED09FB2A985}
SAN RAFAEL 1105194366 | {73B969AA-9422-4313-8799-666FFF6134B7}
SAN RAFAEL 1105220386 | {25A73CC9-0B81-408B-9142-F5D6802BB119}
SAN RAFAEL 1105544824 | {6C0139D5-EF28-447A-8798-DD6F8DC2F6B3}
SAN RAFAEL 1105645362 | {CC6A4E26-740D-42F4-A649-35571E3A45ED}
SAN RAFAEL 1105CB | {CAD39F6E-68B6-4287-AF02-0FE0584C53BF}
SAN RAFAEL 1105CB | {BA67EE88-1E6D-48B2-9DBA-46721926CAE7}
SAN RAFAEL 11061230 | {56251AED-64E1-4D3E-BDB2-E270FC24852B}
SAN RAFAEL 1106155772 | {6E85E84C-7D1E-4092-853B-542CF5DCF10B}
SAN RAFAEL 110648752 | {768B2119-8E04-4A0B-9516-B163D4D61FBB}
SAN RAFAEL 110648752 | {85056666-4A2B-4DAF-B399-DC93301E78AA}
SAN RAFAEL 1106588020 | {93B83BF6-0390-40F7-ADB3-1AD8B7256ABB}
SAN RAFAEL 1106837 | {56251AED-64E1-4D3E-BDB2-E270FC24852B}
SAN RAFAEL 1106910 | {97049330-0F64-4B73-9906-EB2DC1343DE8}
SAN RAFAEL 1106910 | {5D059BF5-F769-4312-8893-6A2C828C685C}
SAN RAFAEL 1106991658 | {56251AED-64E1-4D3E-BDB2-E270FC24852B}
SAN RAFAEL 1106CB | {A84CB2C0-9849-4D74-A8E8-7B5529F6398B}
SAN RAFAEL 11071166 | {8C50B8C8-9524-4FBC-8629-0E606688418D}
SAN RAFAEL 11071166 | {64A83390-336F-46D2-AA1C-9D91A30B0162}
SAN RAFAEL 11071276 | {1BC84E1C-4DF2-4B45-A425-8E2D6B0450F7}
SAN RAFAEL 11071415 | {AC6B2CFB-8470-47A8-8CFF-360D120857F5}
SAN RAFAEL 1107155890 | {64A83390-336F-46D2-AA1C-9D91A30B0162}
SAN RAFAEL 1107501128 | {7DB3B65A-9BC0-48E9-AEAF-56397C577A2D}
SAN RAFAEL 1107CB | {AC6B2CFB-8470-47A8-8CFF-360D120857F5}
SAN RAFAEL 11081262 | {B486F4D0-4246-4914-B521-4CE6A759247F}
SAN RAFAEL 11081457 | {D8F4D209-BA0C-476A-8E47-817CA5AE5916}
SAN RAFAEL 1108516 | {F2E5D603-195F-45A5-9636-597C9B053516}
SAN RAFAEL 1108583502 | {D8F4D209-BA0C-476A-8E47-817CA5AE5916}
SAN RAFAEL 110863598 | {62B0F5C5-018B-42C2-9DA1-D8CCE6714B61}
SAN RAFAEL 1108CB | {8BC2020E-62FB-478E-A2C9-53FD6549A421}
SAN RAFAEL 1109418 | {466136A5-5029-445B-8434-F48A32643962}
SAN RAFAEL 1109519234 | {6E0BDE0D-99E8-4590-9CE3-122B81DDFF03}
SAN RAFAEL 1109535284 | {292E168B-A807-4BEB-8205-853DD377A6FA}
SAN RAFAEL 1109692576 | {324DF6E6-DDC1-4554-BC31-1F7629DC4812}
SAN RAFAEL 110969860 | {8BF78D64-4A44-4B53-8AB6-8417D27FFB87}
SAN RAFAEL 110969860 | {A5DF76D9-626E-4A2E-8281-6888B77A577F}
SAN RAFAEL 110969860 | {F3377C26-9ACD-45A4-83CE-C549A11C2D6A}
SAN RAFAEL 110991742 | {BFF521B9-A860-4F51-B554-94546E79EB8D}
SAN RAFAEL 1109CB | {B783060E-D866-4158-B26D-888D25122311}
SAN RAFAEL 1110189400 | {852F6C12-DBB5-4040-A2CA-B7AA0AE353A3}
SAN RAFAEL 1110854822 | {19311019-956D-4A95-87DB-92D336722225}
SAN RAMON 2101CB | {D5C8CF3A-0CA8-4CD2-870D-AC7D1B010386}
SAN RAMON 2102CB | {AFA2F3E5-5A6D-403E-A015-1BB8AB0D90BE}
SAN RAMON 2106CB | {9140C526-29BF-4637-A62D-8BE823C11E2E}
SAN RAMON 2106MR285 | {BEA60D98-CFF5-4E7B-A41B-182A021D5BAE}
SAN RAMON 2107818336 | {772B9C3A-4112-4E6C-8E48-73C0CBC8A027}
SAN RAMON 2107824562 | {89815FEC-0F53-4C82-9066-992A709E730C}
SAN RAMON 2107CB | {772B9C3A-4112-4E6C-8E48-73C0CBC8A027}
SAN RAMON 2107MR284 | {2E4E6C28-14B9-4C70-8E9A-7A518F26B360}
SAN RAMON 2107MR441 | {D7460C95-B7A0-4A1E-8E17-20B67F2A4B04}
SAN RAMON 2108378518 | {9642BDB4-1904-435A-8789-F733E59A81DB}
SAN RAMON 2108CB | {B814E637-1BB9-4F04-B0A4-F99C92D5342E}
SAN RAMON 2108CB | {2A643A5D-A97F-4EE9-81CA-C352718D1D06}
SAN RAMON 2117CB | {C84D6789-7EC5-4B63-96CB-78D964DC0C39}
SAN RAMON 2118CB | {03B7D51D-EB4E-462C-A768-27297DD9EA9C}
SAN RAMON 2119107418 | {E5DEAFA8-6962-4AC4-A2C5-9DF95C2483CB}
SAN RAMON 211995606 | {E5DEAFA8-6962-4AC4-A2C5-9DF95C2483CB}
SAN RAMON 2119CB | {0CC5B62D-8E39-47F2-A113-AB2F434531F0}
SAND CREEK 1103416018 | {5990CA25-ABD6-4335-8BA0-9D129C882978}
SAND CREEK 1103458780 | {617FEA9E-6288-4335-BF3A-D016F8191B65}
SAND CREEK 11037110 | {D40D6BB9-1863-4357-9803-EF56709C4086}
SAND CREEK 11037140 | {2D5FBF93-4F75-44A4-A3B6-356A65A990D3}
SAND CREEK 11037992 | {983EE7DB-85C5-4BEA-A7AC-497AE67B4765}
SAND CREEK 11037994F | {7561A7AA-EABD-41D6-A6BF-2F5626187560}
SAND CREEK 1103818064 | {C96A45FF-DEE0-4C33-8854-8B3570C7CD3E}
SAND CREEK 1103818064 | {904E4C44-1C98-4593-BD77-E458AD2081ED}
SAND CREEK 1103818064 | {9A2D2339-E5F9-409A-A974-1E7A285F1F80}
SAND CREEK 1103818064 | {423C9B0A-0DEF-4E1E-BC04-DBF544B0F952}
SAND CREEK 1103818064 | {D602B5AB-8B6A-4520-976C-9CD9B026A50C}
SAND CREEK 110397354 | {1C32E9CE-3898-49FE-891B-A309867CC97B}
SAND CREEK 1103CB | {E54C0E82-949E-4C90-9607-A30CD2E7D9C4}
SANGER 110864662 | {3F249268-EA74-445A-BCA7-12F3AA739C18}
SANGER 110892484 | {41D7915D-4CD5-4BDA-B37D-1B991DD15121}
SANGER 1108R544 | {97137431-D7BB-489B-AF10-51A975C597B1}
SANTA MARIA 1108M122 | {144012D8-3B80-4D17-BAEC-5B5A7515DDFE}
SANTA MARIA 1108M18 | {516D977A-EB39-4268-8E04-4AF0198F88DB}
SANTA MARIA 1108M80 | {D0FCA825-EE19-45C5-82C2-01947841A1DF}
SANTA MARIA 1108M80 | {FDE7F051-73E6-4B45-AA2F-257777E32CC6}
SANTA MARIA 1108M80 | {AE487922-28EA-4910-8549-E0B0D200102F}
SANTA MARIA 1110M04 | {8160FBFE-8963-42C5-980E-33F661B1E4FB}
SANTA MARIA 1110M138 | {8160FBFE-8963-42C5-980E-33F661B1E4FB}
SANTA MARIA 1110M44 | {AB8C651F-9450-4421-8365-26483FDBD268}
SANTA MARIA 1110M76 | {8160FBFE-8963-42C5-980E-33F661B1E4FB}
SANTA NELLA 1101CB | {D9B42920-8795-457D-8506-B9A1003BB3E6}
SANTA NELLA 110211370 | {B6B3BC62-45BB-442B-AE75-28B8C30922B2}
SANTA NELLA 1102594884 | {B6B3BC62-45BB-442B-AE75-28B8C30922B2}
SANTA NELLA 1102790416 | {2D76AD67-E721-4C44-87BE-57355AF41235}
SANTA NELLA 1102CB | {1DD8AB71-6D63-4F34-BB36-E497CE7B6974}
SANTA NELLA 1102CUS8000 | {B6B3BC62-45BB-442B-AE75-28B8C30922B2}
SANTA NELLA 1103507032 | {A141770B-B92E-40DB-B684-188561615951}
SANTA NELLA 11037200 | {54EB001A-C75B-4E5F-A364-1EC2210A8870}
SANTA NELLA 1103CB | {F639887C-4CF2-4C98-9948-8AAD1729538E}
SANTA NELLA 11043130 | {D412B745-D070-4998-9104-DFC87BB22A4F}
SANTA NELLA 110438984 | {3C652A08-AEE3-462E-A457-1B577628C52A}
SANTA NELLA 1104395692 | {3C652A08-AEE3-462E-A457-1B577628C52A}
SANTA NELLA 1104611232 | {9B89E5D4-E3CF-421E-9973-405ECEC9F5B3}
SANTA NELLA 11049600 | {3C652A08-AEE3-462E-A457-1B577628C52A}
SANTA NELLA 11049660 | {DCB08685-977E-4D66-92AA-7783C3C126A8}
SANTA NELLA 1104CB | {3C652A08-AEE3-462E-A457-1B577628C52A}
SANTA ROSA A 1104173590 | {BF693435-FC48-417F-BBCC-18F887A0E298}
SANTA ROSA A 1104210 | {53C74AF7-2A69-47CF-8DFD-9E70E0E39334}
SANTA ROSA A 1104220 | {E0B89CB3-82B2-49F5-867A-BBE81476E709}
SANTA ROSA A 1104220 | {97A379E6-C657-4B3B-9AC8-B4B0F3BA119F}
SANTA ROSA A 110432180 | {B37312AE-80D7-4090-A893-C81D3025336C}
SANTA ROSA A 110439786 | {697A1F90-C46B-4A32-BA8E-838CA80BD5D2}
SANTA ROSA A 1104642 | {DA22FBE8-4AE4-4189-B8A0-D6F473C1FE0F}
SANTA ROSA A 1104716 | {F8BEFC4B-3D6B-4BB7-B77D-7582CBA169BE}
SANTA ROSA A 1104782496 | {0B2A1B5E-CCE5-4304-A0E4-4EEDC842D165}
SANTA ROSA A 1104782496 | {7956CC24-117F-4724-9582-2E87B368DA45}
SANTA ROSA A 1104782496 | {54C3FF00-D613-4ADF-B3B7-FDD938F310A8}
SANTA ROSA A 1104991788 | {A7207572-E958-47AE-A2AE-E5F117C7F1E9}
SANTA ROSA A 1107184 | {E4999502-8D37-4994-A3E2-356DD7D6D5B1}
SANTA ROSA A 110775422 | {1E67C109-CF10-458A-ADCB-5ED4521414E3}
SANTA ROSA A 1107813800 | {CD69EFC4-75C2-4740-8520-E2AE309900C4}
SANTA ROSA A 110798988 | {DF7F99F8-6267-47B6-90B3-AE2097419136}
SANTA ROSA A 1107CB | {66A6713B-EEF9-4672-883A-89D2D2628FA8}
SANTA ROSA A 1108626 | {B916F1BC-FDC7-4604-9F1E-064F6D66F284}
SANTA ROSA A 1108626 | {B3F22D98-1F2E-4E30-9576-F5EA667C1327}
SANTA ROSA A 111092962 | {116DE352-2E18-465B-A34B-4DEAE4404EE5}
SANTA ROSA A 111095984 | {116DE352-2E18-465B-A34B-4DEAE4404EE5}
SANTA ROSA A 111099918 | {93D64AED-6AD4-4AFF-BDFB-1B1DAAB3072F}
SANTA ROSA A 1111147198 | {67140A91-07CE-4EA7-9BA4-49867563AE33}
SANTA ROSA A 1111526 | {43D8F0ED-7B5E-4F41-AC7E-32FC77F4AD71}
SANTA ROSA A 1111758024 | {FFCF3ECB-BCF6-4D7C-80BD-D22A2A7318FC}
SANTA ROSA A 111175924 | {43D8F0ED-7B5E-4F41-AC7E-32FC77F4AD71}
SANTA ROSA A 111179354 | {77B8D94F-2EC6-49F7-A5A0-3C2CCD32D5EE}
SANTA ROSA A 1111907192 | {F22F662E-FA91-4A27-BD1D-488EE11D41A9}
SANTA ROSA A 1111907192 | {4A84F814-6F3F-408F-ABCF-98294BC9307C}
SANTA ROSA A 111199050 | {499987DB-7F14-42C6-AFB9-42B010DA6CFD}
SANTA ROSA A 1111CB | {4D91C141-515F-4F14-8290-C8268E13D106}
SANTA ROSA A 1111CB | {86D21844-80CB-4D82-9997-89E0A5ECE9C1}
SANTA YNEZ 1101277014 | {C3C0680A-C277-44D4-BC9F-C389F4D7DF4D}
SANTA YNEZ 1101608390 | {0EE7FFD9-7EF6-4389-A6C6-F9370C916628}
SANTA YNEZ 1101673618 | {AB14F8FE-EE00-4DB6-A9D1-E7044AA1EEF8}
SANTA YNEZ 1101980192 | {CCDAB0AA-FC42-4576-8856-F9CCAB22AC0D}
SANTA YNEZ 1101CB | {08A02557-738F-41D7-89E3-E3805DA8D735}
SANTA YNEZ 1101Y52 | {CDC11A25-DBD9-42BE-AA95-70647385571E}
SANTA YNEZ 1102320270 | {5627B063-B665-4EAB-9B4A-39C8A753C0BC}
SANTA YNEZ 11026149 | {B07E575E-DBD2-446D-9D7F-BBD05FF7E21F}
SANTA YNEZ 1102694296 | {C4B5DAFE-E623-4F32-97C6-68D1ECAEC001}
SANTA YNEZ 1102CB | {248D5525-98DB-494D-8A88-8F5511E7C8B0}
SANTA YNEZ 1102Y18 | {CB331419-4415-4607-87D8-B05BBD8C7F9E}
SANTA YNEZ 1104117616 | {C577CDCB-ED67-4302-B33F-D351377518F3}
SANTA YNEZ 1104430910 | {7D4C5967-90F3-46CC-8998-F98C521BAB8A}
SANTA YNEZ 1104512912 | {7679D85F-4172-4810-B5B5-B8198D816699}
SANTA YNEZ 1104564710 | {6D4FB307-8040-4939-9E2E-40C3CC67F06E}
SANTA YNEZ 1104644624 | {79837C47-078B-4D74-9730-011C9BADDCEC}
SANTA YNEZ 1104664392 | {96EDCC4C-FBE2-4ED7-95CE-EB30E535CF4E}
SANTA YNEZ 1104685160 | {D82CFC78-0AF6-4ED3-B064-C26DDC2F5970}
SANTA YNEZ 110477098 | {30375F5B-5F9A-4C1C-992C-DEDED43F1FC3}
SANTA YNEZ 110488746 | {3F797584-019D-48E0-A377-BC3C335B4E76}
SANTA YNEZ 1104CB | {36F02C24-D26B-4B85-8C08-B8C39025E135}
SANTA YNEZ 1104Y04 | {1E768305-B6AF-4963-B2D5-92FDAB6A5028}
SANTA YNEZ 1104Y28 | {D5DD389C-0EE7-4085-B05C-70F106F6B79D}
SANTA YNEZ 1104Y30 | {1B8DB8B3-1D13-4E12-A58F-43F8C34F8820}
SANTA YNEZ 1104Y66 | {B46D742B-3DDA-4738-A51C-19ABAD3AA23C}
SARATOGA 1103LC16 | {D8FA53F1-4F5D-4A3B-A2ED-DEA75FD0EA10}
SARATOGA 1103LC40 | {9D2E9787-9F58-4CCA-BF31-59BAA6A88EA6}
SARATOGA 1103LC40 | {127E8C02-0F52-4889-8484-FC0593326DBE}
SARATOGA 1103LC40 | {A0069F30-9735-482E-85CC-36443E960AEF}
SARATOGA 1103LC40 | {8C0E6ED7-7018-4183-AAD9-66702B134D45}
SARATOGA 1103LC82 | {8DC14E6C-EC17-4B68-AA1F-34B2D141CBFE}
SARATOGA 1104209146 | {08103A51-41C2-42FD-9E38-357AC9FA03F6}
SARATOGA 1105431214 | {BC196764-5ADD-4C81-A2B3-C9F42938CD96}
SARATOGA 1105CB | {0AC2A538-D1DE-4BF0-89DD-0FB685A31962}
SARATOGA 1105LC14 | {D8F111B1-64B9-41D7-9211-8173FEC05653}
SARATOGA 1106340986 | {76A04BD1-4382-473D-8157-2FE1C012AABD}
SARATOGA 1106408318 | {01EC17A2-1468-4F09-861E-AAA869333E5B}
SARATOGA 1106CB | {D3EE6D7F-47FA-4D89-A2C1-869E892A4C05}
SARATOGA 110715763 | {6AE17DF9-6061-4C72-A7B1-FB94CD38FC2C}
SARATOGA 110715777 | {4BC039F7-5762-4278-9F96-086DAB6850E1}
SARATOGA 1107167792 | {C30A348E-D0A0-48B1-A7F3-47E07379CBA0}
SARATOGA 110722489 | {A5D45FD4-6B7B-49F7-B23A-13D11A283795}
SARATOGA 11073370 | {4D45311D-F072-451A-A54E-53459E91E5F7}
SARATOGA 1107397522 | {5CD9ED02-1B29-4908-8FBB-14217A932D61}
SARATOGA 1107413816 | {717BE6DE-1A86-4939-B958-630A186C1AF4}
SARATOGA 11075696 | {01343684-2E22-4CD1-B45D-70EFDFE53735}
SARATOGA 1107667000 | {1C6BB5A9-7570-409D-B67F-8C01502A28E2}
SARATOGA 11076867 | {1EECCE5A-2560-4A1B-BCA1-BF5B03357FA1}
SARATOGA 1107808992 | {83E12293-4767-4982-800C-FE2EA1715D00}
SARATOGA 1107899344 | {BBDA6BAB-A6E1-4EF2-A377-B93BB222DBB3}
SARATOGA 1107899344 | {C761A6A1-1CC4-4C35-8E73-B393DCE15285}
SARATOGA 1107899344 | {56A63DE8-C9C4-4C32-8EDA-118B87F13D85}
SARATOGA 1107CB | {1EECCE5A-2560-4A1B-BCA1-BF5B03357FA1}
SARATOGA 1107LC26 | {AB3D61A8-2047-43B4-8648-838CA93AAC23}
SARATOGA 1115463510 | {D41C5049-957B-48AE-B573-6564E214A3B4}
SARATOGA 1115729940 | {3EC237F5-0BC9-4CBE-A033-E81139F3C035}
SAUSALITO 11011270 | {D140947F-0C1B-40AD-B2F0-4E3897A9B1FE}
SAUSALITO 1101221834 | {356E1F49-CF0F-4248-9806-AB9FD58A1CFC}
SAUSALITO 1101302204 | {74E17B43-07FD-4538-8342-FEE05984D7AF}
SAUSALITO 1101331806 | {8796524B-A1FD-4229-B2E4-3A9BEDC52EE3}
SAUSALITO 1101688590 | {FB370B4C-A340-488C-B2BF-3C5B30E54274}
SAUSALITO 1101CB | {89972505-5E8F-4A2D-AA5C-D59B16608028}
SAUSALITO 11021224 | {BE77E89E-D575-4124-AA7C-BF07ADE3CD3D}
SAUSALITO 11021268 | {8F1701AB-AC20-48A5-8989-61140107D373}
SAUSALITO 1102134362 | {4C4BBD0E-42C5-4F3D-9FA2-E84AC7702DBB}
SAUSALITO 11021500 | {7E93EFF6-2E9C-40C7-BE6F-763B6DBD01F0}
SAUSALITO 11022033 | {C4565A92-D596-47B2-9090-4B093697665D}
SAUSALITO 1102211348 | {4C4BBD0E-42C5-4F3D-9FA2-E84AC7702DBB}
SAUSALITO 1102577290 | {C4565A92-D596-47B2-9090-4B093697665D}
SAUSALITO 1102758798 | {AA8B7A88-5864-4CC9-B505-AF4723BAEEC8}
SAUSALITO 110284278 | {EEE9A4DD-4FFF-4813-917D-2CD2DA44AB21}
SAUSALITO 1102916006 | {4C4BBD0E-42C5-4F3D-9FA2-E84AC7702DBB}
SAUSALITO 1102964592 | {EE9BA2A3-B7F1-4ADE-BF30-423061F0C66F}
SERRAMONTE 1104293810 | {29A8579D-AE5E-4724-8C17-1522017AE0E5}
SERRAMONTE 110456936 | {CA9AE8D8-3F69-4DA6-A06D-C225FBC9B6E7}
SERRAMONTE 11046055 | {29A8579D-AE5E-4724-8C17-1522017AE0E5}
SERRAMONTE 110467957 | {EF6A3579-A609-4474-B9E0-837DC3E5EA77}
SERRAMONTE 110496308 | {806875D3-1765-49DE-914B-6404BD52E1F0}
SERRAMONTE 1104CB | {806875D3-1765-49DE-914B-6404BD52E1F0}
SF H 110114687 | {0FDA22EA-8D9D-4A31-8D7C-30D06A8C13ED}
SF H 11016225 | {0FDA22EA-8D9D-4A31-8D7C-30D06A8C13ED}
SF H 1101CB | {0FDA22EA-8D9D-4A31-8D7C-30D06A8C13ED}
SF H 110510345 | {AF4D3751-08B9-4FD3-87FB-4CE0255479AA}
SF H 110588460 | {AF4D3751-08B9-4FD3-87FB-4CE0255479AA}
SF H 1110326008 | {9B813ADD-EB7E-4E3F-A928-B1E8CB95733F}
SF H 111041644 | {9B813ADD-EB7E-4E3F-A928-B1E8CB95733F}
SF H 111071826 | {336171B8-1332-4529-935B-1DF43A9971DB}
SF H 111084104 | {B802E4D1-E2C4-4D2F-9729-B36750A80B66}
SF H 1110CB | {9B813ADD-EB7E-4E3F-A928-B1E8CB95733F}
SHADY GLEN 1101100230 | {7571D52F-AC0B-4626-BC1C-DC3468E02FE7}
SHADY GLEN 1101145584 | {21FB0D05-9884-4ADA-A008-CD751AAD143D}
SHADY GLEN 11012768 | {7B6835CB-0292-4C0B-96D9-CB73CB830193}
SHADY GLEN 110132726 | {06CC8AF2-BC8E-4ED8-995E-FC6706948255}
SHADY GLEN 110151696 | {0FE524F2-DA0B-43E6-AE33-7B106122C864}
SHADY GLEN 1101578248 | {2A97FDE4-439A-4BDA-B17F-CC5F982FB1C5}
SHADY GLEN 1101585766 | {CF94DB3B-64E2-4CC4-B91F-66E1EA10F2F3}
SHADY GLEN 1101820080 | {7571D52F-AC0B-4626-BC1C-DC3468E02FE7}
SHADY GLEN 1101898212 | {FD00970A-E42A-4988-9A3C-EBB0640D1B8A}
SHADY GLEN 1101941844 | {5B17B94F-37DF-478F-8F5E-F2EC95447F5B}
SHADY GLEN 1101941844 | {C617CBCD-ADE9-465A-83AD-32897DDC05B7}
SHADY GLEN 1101941844 | {D1463BB4-C6D8-4652-B8D6-F5D55EAF695A}
SHADY GLEN 1101CB | {2295C6B5-DB5C-485B-935E-32BBB76DDD81}
SHADY GLEN 11022232 | {17B538A8-7FD4-42EA-BD3A-67B883A27038}
SHADY GLEN 110248894 | {1F323A0D-3C08-4F07-A424-801F7C955EF5}
SHADY GLEN 1102743098 | {47A636B8-C05E-4F5D-AB59-245CAE44CE68}
SHADY GLEN 1102864004 | {134B94EB-8866-4028-A071-AEB289377BA5}
SHADY GLEN 1102864004 | {698BB99A-F798-4B3F-9A98-D42F2DBD9C85}
SHADY GLEN 1102864004 | {0D579674-F75B-492C-9062-53C837D80316}
SHADY GLEN 1102CB | {A8C871E9-A558-4EBE-96DF-EF0BB9E9DE44}
SHEPHERD 2109CB | {89BBC033-4F66-4B2D-9C3D-0EF7B33BF58B}
SHEPHERD 2111327814 | {1AB1D05B-5D25-411E-9B9F-D694DA4A6518}
SHEPHERD 2111443696 | {546202B9-2D3E-48A7-A1E5-9D5B7441FD88}
SHEPHERD 2111537008 | {E96DE61C-94D8-44EC-B1DA-8923104268C8}
SHEPHERD 2111688294 | {1AB1D05B-5D25-411E-9B9F-D694DA4A6518}
SHEPHERD 2111707358 | {043E8F07-84F7-4AE7-BB3D-18F6172375EA}
SHEPHERD 2111CB | {637B1638-4F89-4723-A4FD-5030BB254C71}
SHEPHERD 211275088 | {F8636BBA-7E7D-44BF-85A5-953A867B1833}
SHEPHERD 2112CB | {F8636BBA-7E7D-44BF-85A5-953A867B1833}
SHEPHERD 2112R1743 | {F8636BBA-7E7D-44BF-85A5-953A867B1833}
SHEPHERD 2112R4588 | {F8636BBA-7E7D-44BF-85A5-953A867B1833}
SHINGLE SPRINGS 11038319 | {796B44E0-7415-46CA-BEFC-A0258D1DDCE5}
SHINGLE SPRINGS 11038752 | {4A6A0D61-C41A-479C-A0D9-3D6225EB935A}
SHINGLE SPRINGS 1103CB | {21717BF3-E14B-476C-94A8-5495C36BA027}
SHINGLE SPRINGS 110419502 | {68D0B16F-430E-46D7-92D4-FB0EB0D57376}
SHINGLE SPRINGS 1104556218 | {38C837DF-F86F-4C34-B834-12EBAE0AE6ED}
SHINGLE SPRINGS 1104CB | {40341932-C636-415B-BE6F-5D9D8CD0A383}
SHINGLE SPRINGS 210511172 | {91D53CD4-6008-41E0-B5BC-B59F60B0DDAC}
SHINGLE SPRINGS 2105268384 | {5E029290-BC80-4D26-AA48-47AB3F30D7EF}
SHINGLE SPRINGS 210551738 | {82A82E49-B7B9-4B20-91CE-19896367619D}
SHINGLE SPRINGS 2105CB | {F8F7136D-4B7B-4975-BCB7-4503BD4299E2}
SHINGLE SPRINGS 210819622 | {CB8A7131-E06A-4656-A911-121C2EEBE232}
SHINGLE SPRINGS 210819622 | {02AD3F8B-383A-4100-8272-7B96BBE97F5D}
SHINGLE SPRINGS 210819622 | {726DA3D3-7FED-4A36-992D-B5901BD6AC6B}
SHINGLE SPRINGS 210819622 | {AAF450BF-385F-4DA3-89D7-F922C335EAC1}
SHINGLE SPRINGS 210819622 | {6D1C9F2B-A3CE-4A05-923B-4034C88DC906}
SHINGLE SPRINGS 210819622 | {05D87CF6-0F40-4D84-81B2-3F7FD9CE96DD}
SHINGLE SPRINGS 210819762 | {37338E68-AEEA-49C6-B1EE-76E1EAD86B81}
SHINGLE SPRINGS 2108294550 | {F31C2ABF-BD69-44A7-B0D2-5CCC3426ACD2}
SHINGLE SPRINGS 2108449638 | {2803490A-7633-47C3-B696-C54B5F6A03E3}
SHINGLE SPRINGS 210851474 | {67DE249B-565B-4EB7-8D26-D40F13D2E8F1}
SHINGLE SPRINGS 210851476 | {E8E1663E-363E-4F96-A961-F91861C11573}
SHINGLE SPRINGS 2108878418 | {9E7A5D58-B393-43D5-A7EF-AFB9DC7D3E6A}
SHINGLE SPRINGS 2108CB | {31F15014-5008-45D5-9481-1A850055776D}
SHINGLE SPRINGS 210911092 | {B50857A5-6260-480D-ADCC-BFF89F70D492}
SHINGLE SPRINGS 210911092 | {8BA0AE1A-F027-4154-A622-70C699E73A1E}
SHINGLE SPRINGS 210912392 | {728A41CD-A46C-41BE-8099-075D0704E7A6}
SHINGLE SPRINGS 210912392 | {459A0F58-D313-4135-91DE-CD6B07FCFAA0}
SHINGLE SPRINGS 210912392 | {8E7E05E8-657F-41A9-8C07-27317920779C}
SHINGLE SPRINGS 210913322 | {149A11CA-7CE8-41C1-895F-45BC975D8F7A}
SHINGLE SPRINGS 210913322 | {15EFBBFC-1402-46CB-88DB-271887B99E65}
SHINGLE SPRINGS 21092679 | {8E7E05E8-657F-41A9-8C07-27317920779C}
SHINGLE SPRINGS 2109576170 | {27097EEC-9CFC-4746-AAF9-881A597C47F0}
SHINGLE SPRINGS 210961892 | {FE625157-4A14-40D2-B1D3-1A0A93F86C88}
SHINGLE SPRINGS 210981390 | {DF428FBA-A19F-4678-A15D-08B87DAE1997}
SHINGLE SPRINGS 210985766 | {B0804F69-4532-4191-9CE3-95D88026BC3C}
SHINGLE SPRINGS 210985766 | {B8FC48D9-05C7-4124-AF99-942526CDF2D7}
SHINGLE SPRINGS 21099372 | {27097EEC-9CFC-4746-AAF9-881A597C47F0}
SHINGLE SPRINGS 2109CB | {8CA8A29D-825E-4F83-82F2-58C55E66E077}
SHINGLE SPRINGS 2109CB | {79888703-E94D-4039-8D18-C65928665D60}
SHINGLE SPRINGS 2110386572 | {FC00237C-3D62-4C01-88CF-5974E60BEBEE}
SHINGLE SPRINGS 211051790 | {189FDEE6-C0C8-4312-8E54-D1B717348AC0}
SHINGLE SPRINGS 211051800 | {027EA52B-9771-4584-AAFD-2CA838E196C2}
SHINGLE SPRINGS 2110634118 | {F2E26CFC-5FA2-449C-9EC1-27B166FC49B4}
SHINGLE SPRINGS 2110CB | {064C2459-8C22-4F74-A2C9-18905DBD3086}
SILVERADO 21021605 | {E326F578-EEFA-49EE-9931-A6B7908F4DC3}
SILVERADO 21021607 | {3B1DD141-3F56-4F3B-8777-EAB2A9BEA43E}
SILVERADO 21022495 | {E417384C-CD10-4D00-B136-62F02EAF1C4A}
SILVERADO 2102285782 | {7650C201-F544-4286-9EA7-A492BFABD887}
SILVERADO 21023010 | {B8F94D37-4665-475E-83A6-71024C2C2EB0}
SILVERADO 210234959 | {03890B2D-86C2-4585-9C1D-5FAACC6CEB0E}
SILVERADO 2102437194 | {7001DE25-A96B-4176-B38D-AB056F29A6CA}
SILVERADO 210258626 | {05AC1C5B-D6E1-429E-A072-263D6E199803}
SILVERADO 2102714 | {65C50E41-4A19-4EF0-8E02-55AD7C68E0C7}
SILVERADO 2102772792 | {A1E340CE-2BA1-4C87-8C2A-156A4355C24F}
SILVERADO 2102794484 | {74903617-CE8D-4EA4-9ABF-16328C3F52EE}
SILVERADO 2102914108 | {2DA6C6FB-2E85-48DE-AF07-51EB1C93AF73}
SILVERADO 2102922022 | {11969599-658C-4879-9EBE-BD3B4F21FB32}
SILVERADO 2102942170 | {9649E146-C697-4C91-9D1B-52A6DDB0BE7E}
SILVERADO 210298998 | {B9DFD3D4-5938-44FA-A6FD-F2608641C707}
SILVERADO 2102CB | {E417384C-CD10-4D00-B136-62F02EAF1C4A}
SILVERADO 2103315138 | {F44BA444-8496-4474-93B0-D93B349142F1}
SILVERADO 2103403102 | {CFFB1C96-B030-4780-B25A-3AB8C753331F}
SILVERADO 2103507513 | {5DB6403E-B6A2-4C39-88E1-26D243AA9FAC}
SILVERADO 2103617828 | {F7F03C40-551D-4024-8031-59C5BBC7C6D4}
SILVERADO 2103920793 | {86671C53-A1BD-408B-B0CD-99AC0557F97B}
SILVERADO 2103CB | {66AAADD9-54A2-4D43-B82B-F401906AF14B}
SILVERADO 2103CB | {822043CD-ACC1-4D8C-B9F0-A2C7CAEA0795}
SILVERADO 2104106272 | {DB39D3A8-D12A-477D-A9BF-F354330F84E4}
SILVERADO 2104201918 | {9432B5F9-88B8-4093-BF61-CAC532120542}
SILVERADO 2104324994 | {BE30A806-C028-4AAE-BD97-BF2ACA23C5AE}
SILVERADO 2104324994 | {7059E145-7DB1-4280-BEA3-DE79205E5125}
SILVERADO 2104324994 | {52F85645-24BD-4BC9-86B1-206C2D8B3AF0}
SILVERADO 210437632 | {13A712E3-B547-41AB-8639-0CAD4756D0FC}
SILVERADO 2104428742 | {B587A7F0-9C46-4B73-8DDD-2D7E86802E43}
SILVERADO 2104493770 | {DE4B1785-E52E-4A21-B7C2-44BD64C8C56D}
SILVERADO 2104515946 | {05AA93CC-3E16-4AA0-9C09-002C77C18466}
SILVERADO 2104580928 | {7AE17F76-C5C1-4C6D-B5A6-7396BDB8D29E}
SILVERADO 2104632 | {D40F4D8A-3C27-46DA-8593-D13991F9D4C8}
SILVERADO 2104632 | {841AD544-FFC0-4D92-904D-46B27F7D9430}
SILVERADO 2104633600 | {6697AFF9-8F2D-420E-9557-3177BC3896A0}
SILVERADO 2104646776 | {2B351D0D-34E9-4ED5-B9F6-58321332BC38}
SILVERADO 2104722 | {73D28043-CFDC-4F62-93B5-37CC33588BEA}
SILVERADO 2104773670 | {F3A1C4E6-A684-4E09-A08F-17B11C141149}
SILVERADO 210478268 | {49BFB9F2-5C6B-4B7C-8CFC-569E7EA29701}
SILVERADO 2104806500 | {301D5A5E-E790-4FFB-8489-CD78F4CA45CF}
SILVERADO 2104909390 | {9CFA751A-E598-45D5-9140-70A53C2E0011}
SILVERADO 2104940 | {64400634-E6FB-4B73-87DB-F50EC6751223}
SILVERADO 210495817 | {19801268-58A0-46E2-9758-098816D4F4C3}
SILVERADO 2104959428 | {7167A295-5954-42C6-87AA-CF2E83E5E432}
SILVERADO 2104CB | {BCC000F2-427B-4C85-BE86-EBEAE729A62B}
SILVERADO 21051306 | {C410A5EB-606F-456C-A426-9DF296A1E7C4}
SILVERADO 21051306 | {A2AE86BF-29D9-46AB-AC07-62E08E2FA633}
SILVERADO 21051308 | {E61E149E-984B-41E5-BBE8-57BFA4C46C56}
SILVERADO 2105131568 | {8DF4CE8D-8809-41EC-B891-BD4155C95E45}
SILVERADO 2105167360 | {0F3794E1-7800-452D-B826-F4E0E0581557}
SILVERADO 2105167360 | {C6357E73-88D5-4CF6-AB92-B3C80346E152}
SILVERADO 2105247660 | {99F7BEAE-C3B5-4D12-B703-F0449CE0ADD3}
SILVERADO 2105268508 | {CB375860-1455-437C-9D56-A713AFD8D3D0}
SILVERADO 2105309298 | {EDAF832D-485E-485A-8E39-0DDC0E96BD34}
SILVERADO 2105337226 | {0739C7E7-C007-4087-BADB-1D9A705F476F}
SILVERADO 2105359428 | {9FD052B0-6B15-4CAB-B530-047A5976AD91}
SILVERADO 2105394844 | {1CC6DAE7-1C84-4AF4-A013-6D8C6FB1596D}
SILVERADO 2105533226 | {4F585A0F-3E69-42C6-8427-3D94B7790006}
SILVERADO 2105658898 | {991CF770-C017-4F1E-B905-05B063249BE8}
SILVERADO 2105764650 | {A2AE86BF-29D9-46AB-AC07-62E08E2FA633}
SILVERADO 2105768606 | {4F585A0F-3E69-42C6-8427-3D94B7790006}
SILVERADO 210578326 | {B655B7C5-A303-4182-BAA2-E2266C974130}
SILVERADO 210581662 | {B655B7C5-A303-4182-BAA2-E2266C974130}
SILVERADO 2105861266 | {AA30177A-A383-43BF-A978-435A7E84A10D}
SILVERADO 2105900104 | {0F244ACF-9662-41CA-9B67-43260BA1D97A}
SILVERADO 2105990552 | {6A947491-FB60-4043-BF5D-F50FFBCF57D9}
SILVERADO 2105CB | {6A947491-FB60-4043-BF5D-F50FFBCF57D9}
SISQUOC 1101CB | {335463E4-7716-4BC6-BF55-B39E4654D44F}
SISQUOC 1101M96 | {ABA8F0B5-44C5-49D7-B132-C788FC15DD52}
SISQUOC 1102113874 | {90FA5417-D8FA-438A-93C0-B2EEC4458855}
SISQUOC 1102143322 | {718BCCF8-1AD2-4292-A8E8-C94E0C244C6A}
SISQUOC 11022017 | {1891E209-B59B-44C0-BBDB-26A59AF0194F}
SISQUOC 1102846970 | {45F0F66F-6587-459B-82EF-26081FA86173}
SISQUOC 1102CB | {92EB9460-E02A-4A24-A181-995BD1F9489E}
SISQUOC 1102M26 | {A7DBE1CA-9F00-48F2-A774-10607AA3DA85}
SISQUOC 1102M52 | {B8793525-C43B-4B72-9E84-4F6812828DC2}
SISQUOC 1102M54 | {96906956-5C77-4774-B51C-564876632563}
SISQUOC 110346137 | {8ECB845B-0FB8-468B-83B4-A62D31D6E955}
SISQUOC 1103858898 | {258E8CE1-3F22-41A9-95CF-5107746239B3}
SISQUOC 1103867486 | {E782E12A-3164-4752-BB70-4CC8003C0253}
SISQUOC 1103M14 | {BE479CE6-8809-4A3B-A6FB-86A2FCDE06C2}
SISQUOC 1103M98 | {72D51786-0F19-4A21-BD91-493BA8FA331E}
SMARTVILLE 1101CB | {90A2FAB3-9517-4F41-ABE9-643E537A58ED}
SNEATH LANE 110134438 | {5A5EFB63-6847-4F33-8DBE-F9C3D6DCF54A}
SNEATH LANE 11015311 | {609F8931-DB33-4C51-8B0A-74D7E061F069}
SNEATH LANE 11016525 | {609F8931-DB33-4C51-8B0A-74D7E061F069}
SNEATH LANE 110168070 | {AE75174C-F0FD-4D78-8720-D705019718D7}
SNEATH LANE 1101CB | {E63B66A6-F711-492C-AE55-754D3FBB9FA4}
SNEATH LANE 110210255 | {8A816A2B-67AF-49BA-86E3-913A836D9CEF}
SNEATH LANE 110210287 | {0DD20D6F-1E6A-4169-86A0-ECA4BB0DDDE3}
SNEATH LANE 110275844 | {AC57E8D0-E406-43BB-B0B4-92AB46A557F5}
SNEATH LANE 1102CB | {40980895-4B8E-4C74-B15F-E13FF900DC4F}
SNEATH LANE 110611792 | {4F4DF911-DB67-45FB-B7A6-F7D53A0399D7}
SNEATH LANE 11061339 | {942A1F20-74CB-4B0F-A8B8-16F691C971BA}
SNEATH LANE 1106CB | {66ED3CF0-2002-44E6-BE2F-18363B4298A8}
SNEATH LANE 11101277 | {8E15B458-F29C-4328-B8BB-225EB178302D}
SNEATH LANE 111015341 | {935F9503-A6EA-4581-B689-528244098488}
SNEATH LANE 111048338 | {83D7785E-7AE6-4CFF-B401-9FB72EBCD47F}
SNEATH LANE 1110631914 | {25DE707B-452A-45E2-85A5-3DC23B164593}
SNEATH LANE 111096530 | {387BB7F7-C1FA-403D-B1F2-AEFE2A510405}
SNEATH LANE 1110CB | {C91E7D5A-1B05-42D0-8CD4-CBFAF694E7D5}
SO. CAL. EDISON #3 1101CB | {5456497F-E6D1-4A61-8929-89D313B5537F}
SO. CAL. EDISON #3 1101CB | {2930446B-6F6A-4AE7-9663-D1ACD14CCB1A}
SO. CAL. EDISON #3 1101CB | {A682EEBB-6AE6-4657-88BB-F6D984C7AC46}
SO. CAL. EDISON #3 1101CB | {FEFF3CD8-2343-48D8-93C4-6004850FEF87}
SO. CAL. EDISON #3 1101CB | {226F8C50-CE54-4E67-B9F5-B8A492EBF4DF}
SOBRANTE 110142914 | {D5713EAC-4361-483E-B20A-724A36C5F247}
SOBRANTE 1101429924 | {93DE1225-0921-4A74-95E1-2FD618C5107B}
SOBRANTE 1101934036 | {21AC5929-6E59-49F5-90AA-DFB268A45B54}
SOBRANTE 1101CB | {AC34AADC-41EC-4F75-A750-22A938BF80E6}
SOBRANTE 1101L534R | {25DCD8D9-03C2-4BC1-93F7-DF5BB3FCC448}
SOBRANTE 1102690098 | {2B19DC4F-7A35-4B7B-9AF2-F2CF56BFB136}
SOBRANTE 1102CB | {FAE87638-3327-4270-9C08-0DC3E3B13CC0}
SOBRANTE 1102L510R | {2F07459D-47C1-4462-B0ED-65839CB76ED4}
SOBRANTE 1103215046 | {6AFEB52D-9F4A-444E-B3FC-D10C077C8013}
SOBRANTE 11033342 | {4892CAAF-65E7-4660-A10F-F15BB35B52DD}
SOBRANTE 1103401514 | {D5F18742-859C-45AE-BB95-2396135F0809}
SOBRANTE 1103CB | {D5F18742-859C-45AE-BB95-2396135F0809}
SOBRANTE 1103LA401R | {6DF01F7D-D94B-4655-BAF6-B3A3B3F7FF40}
SOLEDAD 2101107872 | {13A55BCC-4738-480A-B6AB-19B8FE7F095B}
SOLEDAD 2101631378 | {65776CB2-268B-468E-9260-D0824B0949C2}
SOLEDAD 21017048 | {820718CC-7467-4DD2-B2F8-381F3D5B3CFD}
SOLEDAD 21017048 | {31A9BD2C-C5E0-444C-8986-49C4476C94B7}
SOLEDAD 2101775342 | {F417DA2A-C751-4206-9B93-7957CC7AB9E6}
SOLEDAD 2101823854 | {C9EB66D5-F17E-475C-84E3-A6D209341971}
SOLEDAD 2101955138 | {9A077527-882A-4F06-B221-C25746AA1F96}
SOLEDAD 2102304826 | {1DEF416A-A481-48CF-9FEF-A85EC33985E3}
SOLEDAD 21027008 | {92CC6932-4E6B-4837-8F22-F7E11087FB82}
SOLEDAD 2102858388 | {14F60B66-6FBD-423A-A8D4-1F6DF8B5B464}
SOLEDAD 210435306 | {B67EAAD0-18CE-4C8C-8264-33FF5297FE06}
SOLEDAD 2104413916 | {FD7651EF-898B-49C0-B621-C2068E1D4495}
SOLEDAD 2105125484 | {E0D1D31B-EE07-4A3C-BA17-91B209FA1390}
SOLEDAD 21053076 | {4A9E1292-DD86-40E5-AF21-635E9616CDA8}
SOLEDAD 2105315500 | {9FC0A9A6-641B-4A0C-A239-731EDA3A94A8}
SOLEDAD 21053720 | {CD225AA9-85A3-4FE2-8F75-3046ED999AC3}
SOLEDAD 2105404754 | {45F2F69A-4C2B-4AA3-A4EC-6985ACDF99C7}
SOLEDAD 2105526864 | {808566FE-4218-496F-82E2-45FBB311011A}
SOLEDAD 21057056 | {36177CF1-DF55-4FEE-893C-1AD0F53C4183}
SONOMA 1102113082 | {4BCD6EE2-7FEC-4152-907C-A38A16D3BF51}
SONOMA 1102118 | {4BCD6EE2-7FEC-4152-907C-A38A16D3BF51}
SONOMA 110213367 | {2300EEC9-D815-4DFC-98C2-FB3F79503060}
SONOMA 1102441730 | {4F0353F4-993B-4228-9665-B8F36201BBD8}
SONOMA 1102CB | {2300EEC9-D815-4DFC-98C2-FB3F79503060}
SONOMA 11033052 | {4B7DC187-5EE3-45A7-A2F4-3F80A5EC9C80}
SONOMA 1103307032 | {7F61224B-DBFA-4BF3-A98E-2E051DF976A7}
SONOMA 11033138 | {FDB820A4-08B8-4A93-87E2-56D137A8F9D2}
SONOMA 1103470636 | {989A9D45-A06C-4EF7-99F0-5A8D5A73FF7C}
SONOMA 1103581588 | {989A9D45-A06C-4EF7-99F0-5A8D5A73FF7C}
SONOMA 1103849082 | {F69AA987-5730-4EE0-9E35-B096CCC08119}
SONOMA 1103880540 | {C15AE5B8-7C8B-4C0A-941A-BC50C59FC9B4}
SONOMA 1104412 | {13C5D467-3A5D-46D1-9164-0C6474ACC9E0}
SONOMA 1104414 | {13C5D467-3A5D-46D1-9164-0C6474ACC9E0}
SONOMA 11045661 | {9E74C19B-FD10-4380-8F7F-0DF0A358D1AB}
SONOMA 1104578282 | {820699FD-C2BA-4E28-8398-D087F148A4C7}
SONOMA 110478372 | {883C1192-DE93-49B0-9D61-992A9165A32C}
SONOMA 110478372 | {1DE290BD-4832-4BDD-BC66-181BBE569E93}
SONOMA 110478372 | {8636A63A-DB6E-4004-A8FD-B5DFB3BDC1F2}
SONOMA 1104914376 | {9E74C19B-FD10-4380-8F7F-0DF0A358D1AB}
SONOMA 1104943126 | {13C5D467-3A5D-46D1-9164-0C6474ACC9E0}
SONOMA 1105138 | {7B41A8E9-FC21-424B-BE2E-1E6F807F59E5}
SONOMA 1105229588 | {13B9141B-C5BC-4FB2-B1B5-84BF6E8CCF1E}
SONOMA 1105404 | {780C7404-CFFA-4D6A-B96A-03648D9F464C}
SONOMA 1105435024 | {2B737C15-F621-4E73-AF75-8131ECC2AA24}
SONOMA 11054456 | {4BB2B9D0-8D98-43BA-87AD-9BC7CE46F8C2}
SONOMA 1105539450 | {83741DC0-AB8A-4A6A-AF87-708226B87F58}
SONOMA 1105575872 | {D464C20D-2D07-4CD1-B506-ECBC5597DD8D}
SONOMA 1106144234 | {CABEF95E-D9B3-43F6-8F17-95D79FE7A971}
SONOMA 11061678 | {CABEF95E-D9B3-43F6-8F17-95D79FE7A971}
SONOMA 1106296492 | {55EA2698-B693-4D7C-84A6-FBA73C981197}
SONOMA 1106376 | {3704160C-56F4-464C-949D-B0353C9BFECB}
SONOMA 1106510055 | {E5FD210F-062C-4CDB-BD2B-F92685B10DF5}
SONOMA 1106746130 | {437C52F9-8046-44AF-BB7B-4DC75E8FC7F1}
SONOMA 1106CB | {80158D87-8FBA-4904-925F-F73ECFE1E50A}
SONOMA 1107126 | {8F27A86E-670B-4331-ABF1-9BA9A6222879}
SONOMA 11071309 | {35F57AD2-0209-4C33-8C6F-331DBFF4518F}
SONOMA 1107294 | {3B664FB4-D4E1-4366-BCB7-69C73E2E329F}
SONOMA 1107294 | {35F57AD2-0209-4C33-8C6F-331DBFF4518F}
SONOMA 110749132 | {2EE5BEAB-3902-47F4-9A0A-6CB1BF0D45D8}
SONOMA 1107606 | {0D983ECD-BEFB-48BA-BD2A-39BC764D1C4E}
SONOMA 1107844168 | {DFD9B477-AC78-4483-B663-8671DA768CEC}
SONOMA 1107CB | {B66DFA6A-6131-4186-B4AB-0BA7B611120F}
SPAULDING 1101578852 | {4B4ECB86-924B-4487-850F-9E73F5ADEBBF}
SPENCE 1102276712 | {4738DB4A-9FDF-4C6A-833D-7B9AB689B6AF}
SPENCE 1102321000 | {E93A7BD3-7283-4B37-990A-F7132697460F}
SPENCE 1102990464 | {E5160FAE-67B2-410A-AE3B-822157B58701}
SPENCE 1104965598 | {E9D1075E-68D1-4D19-916B-47C6CD439F6E}
SPRING GAP 170210720 | {A2735C5A-AC0C-48E2-9CB7-2F6A791B6D33}
SPRING GAP 1702110731 | {DD7FBEE4-E9D5-48FA-89BB-28045AB32D11}
SPRING GAP 1702188426 | {430BD33F-FEB4-414F-BF1F-8CCB997A468A}
SPRING GAP 1702693441 | {F823B297-BE7E-454D-B946-D904DF33E9F1}
SPRING GAP 170286032 | {17340C5D-4E9A-414F-A76B-922497EBB75D}
SPRING GAP 17029280 | {EF855D85-A8A9-46E0-809B-873120E44CEB}
SPRING GAP 17029690 | {06F65D45-2D82-470F-9B27-5D880652F1A1}
SPRING GAP 1702CB | {64CDB5CA-B54E-4043-BB09-802AFEE142DC}
STAFFORD 11011082 | {FF138367-96EF-4586-B73C-AE42FDD878F0}
STAFFORD 1101902998 | {8F8067F5-9FE3-45D1-9A1C-8D0428818BCB}
STAFFORD 1101CB | {42AA63AD-C552-4EF9-BEF2-2D7A46307F74}
STAFFORD 11021048 | {B779C83B-3DC2-4512-9F97-360CB13A0909}
STAFFORD 11021202 | {07D78386-6A73-46DA-81CA-B20D2445579F}
STAFFORD 11021258 | {67620093-3D29-47F3-861E-D41DF7A61FA6}
STAFFORD 1102152280 | {FF37B8BF-D19E-4CBC-AE89-7CF4DAB703A8}
STAFFORD 1102168654 | {890FBE04-45F2-477D-ABCA-3FF18127DAFA}
STAFFORD 1102361952 | {58E1DDBF-27C2-479B-8E69-60E9501D29C8}
STAFFORD 110242542 | {C9CC8490-6E43-45D4-87C2-A85ACD7797AC}
STAFFORD 11026121 | {890FBE04-45F2-477D-ABCA-3FF18127DAFA}
STAFFORD 1102784704 | {58E1DDBF-27C2-479B-8E69-60E9501D29C8}
STAFFORD 1102CB | {C9CC8490-6E43-45D4-87C2-A85ACD7797AC}
STANISLAUS 17011331 | {8B63126D-C179-4060-8EFD-1D102ADB1624}
STANISLAUS 1701147234 | {0CA4BBBB-7814-4FCB-804E-C1D4BD68A76F}
STANISLAUS 17011812 | {F869548A-07AA-432B-9AB3-E71C5754DCAD}
STANISLAUS 1701315980 | {8B63126D-C179-4060-8EFD-1D102ADB1624}
STANISLAUS 17017144 | {7D21037C-0E26-46A9-9F85-242421CEDF13}
STANISLAUS 17017144 | {605ED3D0-AB08-4D08-8D8B-AC5B669889EA}
STANISLAUS 170179826 | {2EBFCB83-8CD9-4937-9DF1-5F0721235A72}
STANISLAUS 1701862450 | {848519AE-1A7F-49AA-975C-EBBED7574A28}
STANISLAUS 1701CB | {918E0B8F-0C42-4226-8DC0-E78B4BED7E6D}
STANISLAUS 17021804 | {7A6C2092-3A26-4926-BE3F-3A04290F7325}
STANISLAUS 17021850 | {FAC65080-C9D5-4DDF-BE03-E3F1BC9093EC}
STANISLAUS 17021888 | {295DAE28-567E-401E-83AE-7C5667C00B15}
STANISLAUS 1702247448 | {37586EEA-E2E0-4DD8-8498-F5E685A4DFBD}
STANISLAUS 170237276 | {C3619A95-0ECC-48A6-ABDA-B7A0B8AC9A76}
STANISLAUS 170237278 | {DBBC669E-53C3-46F8-B180-51E0DC203C00}
STANISLAUS 17024905 | {1826E0CD-4869-46ED-AD7F-E218402FE773}
STANISLAUS 17025159 | {DD359EE2-F9C7-4897-9C1A-39FEFDA95B30}
STANISLAUS 1702601442 | {1826E0CD-4869-46ED-AD7F-E218402FE773}
STANISLAUS 170275348 | {16824C49-9897-44F9-8F97-3EB3779FE449}
STANISLAUS 1702888312 | {10BFE110-A6FF-4630-B91C-E1A0B3DDC38F}
STANISLAUS 1702CB | {5ACF71BC-5CB9-4FB2-84D8-E7796B319ECF}
STELLING 1108LM42 | {54B1742D-9454-4E0A-BDA8-E9A3850417C6}
STELLING 110913228 | {5E0E3DC2-02E2-401D-B8B6-13F779F80288}
STELLING 110913228 | {917A151E-1390-4562-B55D-B5C1B6D595D0}
STELLING 110913228 | {2F843716-F8D0-4F7B-9D4D-8575D36E9BFE}
STELLING 110913228 | {76970631-2436-4433-8ABE-AE41F160A6E0}
STELLING 1109412852 | {CB7AAD7D-0EC6-4DCD-8905-B19AA99C3EAF}
STELLING 1110112322 | {09BF9503-B333-45C1-A026-2F8BE22A711A}
STELLING 1110396595 | {9194A519-A8B3-47FA-9F1B-13F504BA79E3}
STELLING 1110530922 | {D91D0674-692C-4189-BD81-0B7AB70C7F8A}
STELLING 1110568350 | {7775BE17-D642-4D7B-B4F2-1F4CD1AD8FA6}
STELLING 1110568350 | {77468423-F556-4C9F-AB94-614809B07531}
STELLING 111060094 | {FAA8803D-2611-43AC-BDBE-E6661DD92FFB}
STELLING 111060094 | {526796B6-BB52-4DA1-91C4-1DAB8D2BFB27}
STELLING 1110733294 | {877E8EF7-F426-4EC0-9032-6E0C314907A6}
STELLING 1110881330 | {BB7AB05A-F6F1-4C97-8DCE-5C8338B638FC}
STELLING 11109265 | {77468423-F556-4C9F-AB94-614809B07531}
STELLING 1110CB | {8E953D43-E75B-4D09-B2DE-0248B8D89E29}
STELLING 1110LL72 | {510ED089-9B5B-49AE-8C69-BD6EC85BCAAA}
STELLING 1111502940 | {404F24CA-49DB-4360-974C-A33CD3E7F45C}
STELLING 111160020 | {04E89A01-7DB9-4E29-BE3B-E16251E3C1EC}
STELLING 1111LM10 | {307FE037-C258-4846-929C-EC4CD8169D9B}
STELLING 1111LM10 | {FD8BD22C-3C83-4570-8D67-A3202624CF83}
STILLWATER 11011320 | {7010B5A1-248E-4D8C-92BA-99C3D3CD7971}
STILLWATER 1101217504 | {59CCD17B-B63B-487B-90E6-A04047E8C25B}
STILLWATER 1101217504 | {969D0165-AB0E-4940-9C38-BF9AB022DA97}
STILLWATER 110148950 | {2473E4CF-72E3-4517-88B6-37E3090DCE92}
STILLWATER 1101747294 | {CCF6FF9B-457E-425D-A957-8AE034D58DB1}
STILLWATER 1101913434 | {FEFE500F-0532-4698-B2CB-49651843D0FF}
STILLWATER 1101CB | {05FAE411-CB1F-4ADD-9163-2A2B0A61C7F7}
STILLWATER 11021466 | {430AA5A2-7BC0-4425-A05E-76360F269642}
STILLWATER 110248952 | {096694C8-1954-4FED-B3CE-6072F54B2C4B}
STILLWATER 1102828624 | {24F85043-C9C5-415B-8FAE-F25FD358B540}
STILLWATER 1102CB | {942A5D01-90B2-440A-92F6-C8D3C90D4346}
STONE CORRAL 1108255186 | {0CA201EF-0A9B-4A84-97A7-EB95F1056EB9}
STONE CORRAL 11087100 | {7C3F27CE-B3FE-4A3A-A517-4F1EC2F3B587}
STONE CORRAL 11087310 | {D645E96A-BF8C-42A8-A769-6DEFC59FD6D5}
STONE CORRAL 11087592F | {9C22AB4D-7471-42A3-9430-CD197230D588}
STONE CORRAL 11087759F | {D645E96A-BF8C-42A8-A769-6DEFC59FD6D5}
STONE CORRAL 110878844 | {D645E96A-BF8C-42A8-A769-6DEFC59FD6D5}
STONE CORRAL 1108CB | {9C22AB4D-7471-42A3-9430-CD197230D588}
STONE CORRAL 1109252006 | {F0CC0456-A07A-4237-A319-6D9A730221F4}
STONE CORRAL 1110189488 | {DB3D7864-7F45-444C-BD96-835D23E12B3A}
STONE CORRAL 111048350 | {5F51CA57-01FD-453C-ADEA-6BC243A2DB16}
STONE CORRAL 11107320 | {D090E99D-0335-45D1-8BE3-75B46FB44EC9}
STONE CORRAL 11107481F | {2BE56CEB-D130-4F64-98EE-3834ECE93155}
STONE CORRAL 111075288 | {2BE56CEB-D130-4F64-98EE-3834ECE93155}
STONE CORRAL 11107778F | {D090E99D-0335-45D1-8BE3-75B46FB44EC9}
STONE CORRAL 1110894956 | {28CCBA34-60FA-4FD7-81DE-39D9BA572A75}
STONE CORRAL 1110975698 | {475C3D60-9DB4-42CF-BD54-DCB20C6AF853}
STONE CORRAL 1110CB | {5F51CA57-01FD-453C-ADEA-6BC243A2DB16}
STOREY 1108239026 | {3CD9AF3E-06C8-4447-8E06-E70EA4441EDC}
STOREY 110838522 | {DD340360-4423-451E-A384-A6E8BB0ACB8D}
STOREY 11086010 | {885BF000-616A-4AEB-8E20-32110D81F399}
STOREY 11086460 | {6AE73511-EF6B-4E51-AA33-609D47CF7500}
STOREY 110890070 | {F48DE272-7A2C-46A5-AC26-F43A52DE4286}
STOREY 1109145572 | {660659D4-DD98-4354-A4FB-FBED5F8FA2EE}
STOREY 110921859 | {F6521ECD-18B4-4A6C-9FB9-B5018A20E90A}
STOREY 1109264976 | {496391A9-5ECC-4F6F-B96D-BA7C79ED56A3}
STOREY 1109272650 | {8F74FD6A-3179-4FA8-9F55-6A7F6F2DE3F5}
STOREY 110934630 | {B3E9CFE3-A820-463B-8FBF-E49E207F42CD}
STOREY 1109402242 | {B3E9CFE3-A820-463B-8FBF-E49E207F42CD}
STOREY 11095200 | {4D0A0B73-B583-4FE5-B586-370A34CDD62B}
STOREY 11095580 | {F6521ECD-18B4-4A6C-9FB9-B5018A20E90A}
STOREY 11096230 | {058A93F4-6569-4330-A864-2D8651B9B5E5}
STOREY 11096250 | {CF730332-C23A-46B0-9CD4-00048FC4712B}
STOREY 1109629466 | {B3E9CFE3-A820-463B-8FBF-E49E207F42CD}
STOREY 1109801452 | {B3E9CFE3-A820-463B-8FBF-E49E207F42CD}
STOREY 1109CB | {B3E9CFE3-A820-463B-8FBF-E49E207F42CD}
SUMMIT 110147786 | {BF34499B-FDC5-40B4-A25C-74F3C2847771}
SUMMIT 110148632 | {E1505A10-613C-46C7-B0BB-34C322CF97E4}
SUMMIT 110148636 | {BC06A3DB-78BE-4381-AABB-ACBB02D3E9CD}
SUMMIT 11016627 | {E1505A10-613C-46C7-B0BB-34C322CF97E4}
SUMMIT 110168706 | {A427B0F7-F35D-4F9B-B915-6E1C81266A58}
SUMMIT 1101742 | {BF34499B-FDC5-40B4-A25C-74F3C2847771}
SUMMIT 110186658 | {CD142DCA-BFBC-491B-9C29-D02961854E56}
SUMMIT 1101CB | {CD142DCA-BFBC-491B-9C29-D02961854E56}
SUMMIT 11022302 | {8D5B0682-D75F-42CC-9788-D166FC869B51}
SUMMIT 110249484 | {9B45EC1B-15DE-404E-A8B2-A4576946A1FC}
SUMMIT 110249484 | {4D17090F-B031-42D9-8E52-3D09021DC1AB}
SUMMIT 1102CB | {5BBF8789-23F7-470F-B0A3-CCE750BDABFE}
SUNOL 1101298061 | {93B7DD45-07C7-4F4C-9962-0F0D4EAA6CD8}
SUNOL 110148180 | {4F589EB1-04B1-4740-ACAC-1766B4EEFC97}
SUNOL 1101605520 | {80474683-8128-4BE5-9DA4-10CEDF2ABB74}
SUNOL 1101904308 | {83D8DCCD-BCDE-421B-AFFC-11B0296CA2C4}
SUNOL 1101CB | {6830085F-FF28-4A85-9104-F5B6CFD24479}
SUNOL 1101MR169 | {B5661D23-7C34-4D9E-9398-9CFA9B995F70}
SUNOL 1101MR297 | {144B98B4-D8D8-4444-BA16-D1CC613F7105}
SUNOL 1101MR387 | {475B4CFB-84F1-46E3-9FF3-409BD1FA54D8}
SUNOL 1101MR650 | {531B9791-D7B4-4DAF-8D61-5A68DAA7C3F6}
SWIFT 2102889948 | {B3225BC2-63D3-45D3-BA96-2AD2A0AB8E9E}
SWIFT 2102CB | {BE64DC1C-3443-4966-940E-5A564C032974}
SWIFT 2102XR440 | {FFD6BA3B-C5FA-489A-8D0D-7DFA9F7D07AD}
SWIFT 2107XR086 | {7CB97158-4C16-4CA5-9FF2-9C62CE30BD07}
SWIFT 2107XR526 | {F1466976-3470-44F4-BFAC-1A77DCF2CCD2}
SWIFT 2108XR364 | {C6F71820-794E-4615-8E5F-9F4308B5AA73}
SWIFT 2109XR300 | {17D989D5-D004-4CEC-9F17-89364403A1F1}
SWIFT 2109XR300 | {C1139140-8329-4FF9-96D1-1E3CB2E9BA54}
SWIFT 2109XR386 | {63AAF8AC-A447-481C-8FD7-216A552C90BD}
SWIFT 211015541 | {065BA8DD-AC6A-45FE-B039-032B4916D3F7}
SWIFT 2110616022 | {F246BE39-0175-4986-BDB0-A6E32868FF88}
SWIFT 2110853720 | {24852CCC-5C31-4279-BF1F-19F7950A318A}
SWIFT 2110XR254 | {F246BE39-0175-4986-BDB0-A6E32868FF88}
SWIFT 2110XR332 | {DF04272D-0020-4DFE-BB56-C7BF45BF962F}
SWIFT 2110XR366 | {10854A52-7EF2-416D-830E-BF803A6482A0}
SYCAMORE CREEK 1109147812 | {34A08EBE-3CC8-4A40-AD5E-BBD3CA97182A}
SYCAMORE CREEK 11092458 | {D8E1416B-8EF5-47BF-B9D0-C8BC9A8079CE}
SYCAMORE CREEK 110979474 | {BEF311A1-A486-4265-8EB8-C5A6755295FB}
SYCAMORE CREEK 1109CB | {6DD04BFB-4C98-43A2-94E5-EF1AAF874533}
SYCAMORE CREEK 1111153260 | {39E14DE7-CA2E-4F61-9B12-2EF706A95B5E}
SYCAMORE CREEK 11112014 | {9FD8CC5B-B764-4FC0-90D0-B9293DA570EE}
SYCAMORE CREEK 11112544 | {6C35DB00-845C-40F1-84BE-49555DDA5E5C}
SYCAMORE CREEK 11112602 | {5CDF71A4-CDCE-4614-B4AE-BACB8DC21516}
SYCAMORE CREEK 1111579750 | {999F5F71-1BDE-4099-9D8F-A77D79948BD8}
SYCAMORE CREEK 1111976428 | {78341850-739C-48F1-B508-024DE20CD1AD}
SYCAMORE CREEK 1111CB | {D9A2A699-962C-4607-98AB-EA01299FAAB8}
TAFT 11013512 | {9F78ACEA-6E57-49AC-8DFA-333811B0506D}
TAFT 110136578 | {9F78ACEA-6E57-49AC-8DFA-333811B0506D}
TAFT 110189056 | {77B4A01C-C02A-48DD-BA2C-A9E404E90D6A}
TAFT 1101CB | {1033EB02-278D-4C49-8FF8-7C5FDBD52935}
TAFT 1102CB | {CDFE84D6-ACAD-41FE-8A0F-D3AED3D3CA7B}
TAFT 11033068 | {69A2CD74-6612-489A-BDCF-3373E4592094}
TAFT 1103CB | {792E4625-A87D-4E9E-8B15-2D1820144D37}
TAFT 11041556 | {D049A86C-8DD2-46C0-A241-5F42510DBDA0}
TAFT 110439520 | {D049A86C-8DD2-46C0-A241-5F42510DBDA0}
TAFT 1104CB | {9413E5DC-3D76-4E6D-813A-A0A2E45AE8B9}
TAFT 11061666 | {2AA3369C-6035-44AE-8C8A-C76BB4589688}
TAFT 11063065 | {2AA3369C-6035-44AE-8C8A-C76BB4589688}
TAFT 1106CB | {801D62DC-C212-485D-91DD-4D89CC4B76FD}
TAFT 1108CB | {D9BDA5F5-8C3D-45DE-A08D-1BA4A1C9AE96}
TAMARACK 1101291312 | {FEB92E46-4E4F-4CB9-B4AA-257412799ABB}
TAMARACK 1101CB | {1755A18B-6E24-4507-ACE5-9CCC118C7159}
TAMARACK 1102482896 | {FB391052-56E6-4289-94C4-964DB7340649}
TAMARACK 1102604920 | {BB1AEC9C-4FB2-4E8E-AAEA-C3392E4AFF13}
TAMARACK 1102CB | {A8FAA54E-764C-43E1-B056-AE15ABB7C1D1}
TAR FLAT 0401922858 | {D165BF4B-3C2E-48AE-BC41-B95BCB317ED4}
TAR FLAT 0401CB | {EA023699-472E-4198-908E-801A3A6750F5}
TAR FLAT 04023144 | {C73A5D7F-692C-413A-8D72-DC21C7152C9F}
TAR FLAT 0402327672 | {A02A5B52-889C-4954-A0B9-9F5E9723A680}
TAR FLAT 0402588710 | {A02A5B52-889C-4954-A0B9-9F5E9723A680}
TAR FLAT 0402CB | {15F62F46-8DEB-4CCA-80E4-1A07793D2B95}
TASSAJARA 21032705 | {8EC1A708-A381-44FE-BED2-93671C99AE76}
TASSAJARA 2103333618 | {1FB237C4-A6C4-4F56-B334-6B6A30D4990E}
TASSAJARA 2103404426 | {8EC1A708-A381-44FE-BED2-93671C99AE76}
TASSAJARA 2103883664 | {63B2FCDD-700B-4526-B8EA-5613D1DDBB60}
TASSAJARA 2103883664 | {AB1F9F6B-B0DE-4E2C-BE82-F445E39109BE}
TASSAJARA 2103889410 | {3050EEA6-76E4-429E-BC85-D261A23C0367}
TASSAJARA 210389624 | {E8F0C479-89C2-4F09-8A5C-0BFE009388AD}
TASSAJARA 2103CB | {C740351C-623B-4A79-8F81-B59FA4E58E72}
TASSAJARA 2104967234 | {C3684BEB-D6C3-4700-A1EE-12D50A9D5B18}
TASSAJARA 2104967234 | {103FEA08-938C-4D23-B382-73080A49CB26}
TASSAJARA 2106203380 | {C6A4A4CF-A03A-49E5-B0DC-3DB8EE99EA58}
TASSAJARA 2106CB | {0F972632-618F-44CB-A965-3BB4F6195935}
TASSAJARA 210791094 | {9BFCBF13-2D3A-4A17-97C5-BD97C03AE6D0}
TASSAJARA 2107CB | {9B0F8112-6AAA-47D5-A7C6-B8C0314DE7DA}
TASSAJARA 2108189700 | {8C428159-8CA3-458B-A6CE-F60FA4399D97}
TASSAJARA 2108437582 | {1F178C0C-3D96-4828-8101-5BB05F8FC5F8}
TASSAJARA 210875010 | {F949AA4B-CECE-442A-AA8D-703A33BB749B}
TASSAJARA 2108846900 | {94F3383E-6B40-41DC-A8C9-1639EE59E040}
TASSAJARA 2109CB | {E1A9F699-2041-4569-A9A7-03860994D8BC}
TASSAJARA 211218305 | {9C6C41CE-D642-4C1A-9DC2-AC4FBEC61EB3}
TASSAJARA 21123202 | {FFB25F94-DDAE-4CA7-A7FA-E0E40AD2E7D0}
TASSAJARA 211238868 | {2ACF67F1-3B06-40EC-A04A-B6A9C336FB36}
TASSAJARA 211238868 | {35E43F5D-B0C5-49AA-8F19-3E66AABB890E}
TASSAJARA 2112430240 | {35E43F5D-B0C5-49AA-8F19-3E66AABB890E}
TASSAJARA 2112676362 | {F9AD6B4B-3819-4B81-9BE7-73908ECEFCE0}
TASSAJARA 2112725488 | {35E43F5D-B0C5-49AA-8F19-3E66AABB890E}
TASSAJARA 2112791386 | {0D1DD5D5-DD54-49CD-8DC6-C13ECFED047D}
TASSAJARA 2112900058 | {35E43F5D-B0C5-49AA-8F19-3E66AABB890E}
TASSAJARA 2112925966 | {873003E9-3643-470C-9743-466E3DC30B9F}
TASSAJARA 2112CB | {4D869EED-AD00-4E5D-B02B-0CB786403D3A}
TASSAJARA 2112D514R | {3FFF1795-1315-4A71-8E91-178B9A0CCDE5}
TASSAJARA 2113MR276 | {3C13801D-CC64-4F61-AF69-C39F394BB25E}
TASSAJARA 2113MR280 | {B9D0F1F0-F20F-489B-8E21-22409D603A4D}
TASSAJARA 2113MR457 | {B9D0F1F0-F20F-489B-8E21-22409D603A4D}
TEJON 1102234580 | {6E248E69-5334-44F4-BB88-9697823ED075}
TEJON 11022878 | {F5B58D0D-3D6A-436B-9C40-AFEED4581FEF}
TEJON 11023751 | {4B521436-E3BB-4895-8AE5-975B51993458}
TEJON 11023760 | {6C424A0E-18F6-4E95-BDD7-E63E2F8C4F83}
TEJON 11024525 | {58DF11D2-6D0E-4BD8-9469-17767B55297B}
TEJON 1102CB | {FFCCB51D-8ABA-4A3C-849A-11EC19C62E8E}
TEJON 1103145334 | {13DF9C76-E2F4-4659-999F-3B0C5114903E}
TEJON 1103286542 | {E47780AD-DBC7-46C5-8517-B5A92A1EF564}
TEJON 1103CB | {6C85A72E-093E-407B-A7B1-8F9B3C7E0353}
TEJON 110595130 | {40C1DF09-4C4A-4C34-B88D-7039796DE37E}
TEJON 1105CB | {40C1DF09-4C4A-4C34-B88D-7039796DE37E}
TEJON 11062436 | {05492903-5FB8-425E-B355-2E08D61369E8}
TEJON 1106382086 | {2F0DF82D-09E8-4074-9EF4-9B09DD2DE502}
TEJON 1106384430 | {6209C891-6B82-47BB-AF4D-F01DAA8351E1}
TEJON 110668778 | {D0E00DBF-D9AF-4D53-A519-635922C7E4F0}
TEJON 1106722150 | {83F2630F-3718-4D96-9025-3FBFCB1E4F32}
TEJON 1106CB | {CCFF6D58-7183-4CC2-A8F3-DEB0EB0D5355}
TEJON 1106CUS3626 | {05492903-5FB8-425E-B355-2E08D61369E8}
TEJON 1106CUS3845 | {83F2630F-3718-4D96-9025-3FBFCB1E4F32}
TEJON 1106CUS7186 | {D0E00DBF-D9AF-4D53-A519-635922C7E4F0}
TEJON 1106CUS7948 | {6209C891-6B82-47BB-AF4D-F01DAA8351E1}
TEJON 1107CB | {2FDD3A04-FA55-4FA7-A6C4-8150817E0BED}
TEMBLOR 11041034 | {EDE5D035-EA87-4974-9C88-E52F81828966}
TEMBLOR 1104284004 | {B49E0763-A81E-4BF5-9E55-0D9FC2A3D0E6}
TEMBLOR 11043013 | {99CF017F-6ED0-462F-8AD1-7CD56A44DE93}
TEMBLOR 110437694 | {64667C04-D783-4B1E-90AB-B21364F54C53}
TEMBLOR 110459326 | {64667C04-D783-4B1E-90AB-B21364F54C53}
TEMBLOR 1104818756 | {98F2C78E-6EEE-4220-BF1E-521818DB5FBD}
TEMBLOR 1104CB | {C2992F46-2554-463F-8E87-219C3C230B9E}
TEMBLOR 2103642990 | {7BC84E9C-B995-4C94-9292-BDD97C189BDF}
TEMBLOR 2103768638 | {7BC84E9C-B995-4C94-9292-BDD97C189BDF}
TEMBLOR 2103CB | {C4BB92A1-A52F-41A8-82C7-49DB073069C3}
TEMBLOR 2103CUST | {7BC84E9C-B995-4C94-9292-BDD97C189BDF}
TEMPLETON 2108553934 | {A994B98A-69FE-4A67-9390-68FC4BFAE2BA}
TEMPLETON 21085777 | {4E56AABA-E208-4168-987C-AD9B6E34D222}
TEMPLETON 2108788466 | {CFD770DC-2A70-4F18-976F-28AC168D7008}
TEMPLETON 2108A38 | {4E56AABA-E208-4168-987C-AD9B6E34D222}
TEMPLETON 2108A40 | {4E56AABA-E208-4168-987C-AD9B6E34D222}
TEMPLETON 2108A54 | {0E2CFA72-5A43-4A9D-8F59-E36D3A5C5028}
TEMPLETON 2108A64 | {FFDFCD62-3D83-4DB1-8291-20A4384347C8}
TEMPLETON 2108CB | {3F210877-7C55-4139-88CB-B237BD20F584}
TEMPLETON 2109313404 | {3A9A14B5-4831-413C-90EB-22B1436113DC}
TEMPLETON 2109315228 | {0220B1F2-AE36-41DE-BAA7-BAC60A6F1D2C}
TEMPLETON 2109868666 | {23FDF1DB-782E-4000-92DD-5A064AF483AC}
TEMPLETON 2109CB | {3D2DC8C9-F0E2-4189-8946-5553A87031B9}
TEMPLETON 2109P14 | {6D875320-5976-4E50-AFA6-46CAAFBD24E5}
TEMPLETON 2109P32 | {BE3D916E-88E2-482C-892F-AF61F2F67735}
TEMPLETON 2109P68 | {DD7BFBA2-59F2-4AF7-93E5-DA92AEFE3901}
TEMPLETON 2109R34 | {D690C4D2-AB5F-4E55-BE78-1BFC0A0158F8}
TEMPLETON 2109R50 | {E9F4AFB5-1012-46CB-93BD-65999630DF83}
TEMPLETON 2109R52 | {881400C0-59DE-4789-9E3A-A9795EA7ADF7}
TEMPLETON 2109R74 | {F87787AF-678D-4205-8ADE-894EA1E48F04}
TEMPLETON 2109R78 | {23FDF1DB-782E-4000-92DD-5A064AF483AC}
TEMPLETON 2109R92 | {03B90DE8-00D2-4B58-B65C-ED90C57EE070}
TEMPLETON 2110211842 | {816EE1E7-10CB-4545-BFF4-506903516309}
TEMPLETON 21102675 | {716A2EFF-D45F-4D5E-A38C-66D2E48AC445}
TEMPLETON 2110307832 | {EAF87279-EF23-4A44-B5E2-CCA62D5C53AA}
TEMPLETON 2110317796 | {F014BBB3-CA2E-47B6-9852-740165FD3020}
TEMPLETON 21105583 | {2A4D1201-89B9-4953-B99F-24CF4E1C2459}
TEMPLETON 21105585 | {A2D4F8B6-C1F0-4262-B006-6264DEE33824}
TEMPLETON 2110901690 | {C383B6E8-D569-48F8-A225-7445F785217A}
TEMPLETON 2110941946 | {BC8B43E1-B72C-41FC-BFAC-30FCC8E9DB81}
TEMPLETON 2110CB | {43D83959-6253-49E9-BD6A-065B7EF0ABAF}
TEMPLETON 2110N28 | {81A758E1-AFEC-4C06-AC45-0A2AE6646585}
TEMPLETON 2110N30 | {F8FF5E67-EE4D-44BA-B232-2D0879C01CDF}
TEMPLETON 2110N32 | {81A758E1-AFEC-4C06-AC45-0A2AE6646585}
TEMPLETON 2110R02 | {43D83959-6253-49E9-BD6A-065B7EF0ABAF}
TEMPLETON 2110R06 | {29732AB3-8644-4D02-B399-63E828AF790C}
TEMPLETON 2110R90 | {EAF87279-EF23-4A44-B5E2-CCA62D5C53AA}
TEMPLETON 2110R94 | {C64A1C77-F715-47FB-B91C-102C85AEBD60}
TEMPLETON 2110R94 | {FC873605-7277-48A0-87D0-9099F9E8FCFE}
TEMPLETON 21112537 | {F2B63704-911C-4690-AED1-D856835800A9}
TEMPLETON 2111461692 | {64CA956D-BEEE-4621-BAE2-E108B65904AD}
TEMPLETON 2111514592 | {E68CFE85-A05C-455F-90E9-908250F636D6}
TEMPLETON 2111A02 | {F4592309-FF5C-4AE7-B40E-CF8D73FD01E6}
TEMPLETON 2111A66 | {CD2443C5-9F0F-40FA-9737-DB91D76D5878}
TEMPLETON 2111CB | {1A1B9828-BB7B-4831-9B29-12F7B7720C90}
TEMPLETON 2111R38 | {E068C598-6807-40BC-B63F-804DC57F436F}
TEMPLETON 2111R76 | {E068C598-6807-40BC-B63F-804DC57F436F}
TEMPLETON 2111R86 | {C1DF3268-8D83-469E-AB38-F1D09D72570E}
TEMPLETON 2111R86 | {0CBBEFB6-9229-4A1C-A848-15AD84ED6B51}
TEMPLETON 2112116402 | {3329F03A-165F-42EE-9423-F38D6F793EB9}
TEMPLETON 2112238418 | {C5F748E0-B9D3-42AF-ADB5-0714F403D060}
TEMPLETON 2112485608 | {F888EA83-160B-4C8A-947C-3FEEFB60DC7F}
TEMPLETON 2112CB | {5E55D6F2-0179-4A06-BFE4-E717E82210A3}
TEMPLETON 2112R28 | {F888EA83-160B-4C8A-947C-3FEEFB60DC7F}
TEMPLETON 2112R80 | {3E696401-4261-4D08-869B-B3D4019E7D36}
TEMPLETON 2112R98 | {A02025E9-4653-4FCA-9857-C09241833C40}
TEMPLETON 2113175566 | {53AC1DBA-3753-413F-853D-848DA3C879BF}
TEMPLETON 211318370 | {BB6C0819-95BB-4C15-AFC3-7605E64025A8}
TEMPLETON 2113205874 | {6DAFE91D-9A97-407E-B8BF-0F2EE33C22FB}
TEMPLETON 211321954 | {72FFFCF1-373B-4CE9-940E-FB854B837B88}
TEMPLETON 2113245596 | {3F63C7BE-6B36-490B-AFFD-E53826E11A92}
TEMPLETON 21132949 | {0909EB5E-BC9A-4986-A3ED-F6D08601F4FB}
TEMPLETON 21135143 | {C1753829-A208-4D44-95AF-06BA0A1458F3}
TEMPLETON 2113520924 | {C7B2A344-3A4A-4AD9-9687-D3F86839CEE1}
TEMPLETON 2113587564 | {0AF55F6B-6D61-4EC5-ACAE-2DB5E6CBA844}
TEMPLETON 2113641367 | {FE304B9F-DFAE-423B-9FF6-FD34CCDB383B}
TEMPLETON 2113848137 | {FB380A98-AA0D-4842-98E9-EA318AC8BB0D}
TEMPLETON 2113942274 | {EAE61108-5D41-42FC-A07B-B63F0A10FA72}
TEMPLETON 2113A08 | {ED2FD62D-73A2-48E2-BABA-F5CBA9685A6D}
TEMPLETON 2113A10 | {E6F3FB48-7B73-44A2-9D22-75A3F05024E8}
TEMPLETON 2113A10 | {91D5BB83-4E60-4485-89F2-310D2F0EF681}
TEMPLETON 2113A10 | {0EE3C5D9-65DF-422E-B5D4-7F41B1834DD8}
TEMPLETON 2113A12 | {F518F823-D39A-4E63-8BF7-DA50E4754F15}
TEMPLETON 2113A20 | {0C5237BF-927B-47A5-B97E-2B394BFF5111}
TEMPLETON 2113A24 | {F59172C1-69CB-4876-A528-BC5CC9282F3C}
TEMPLETON 2113A30 | {982A8403-6DD7-4479-B96A-84BF654A0654}
TEMPLETON 2113A32 | {B5262924-E8BA-494C-94F2-552AF4F4F88E}
TEMPLETON 2113A70 | {0909EB5E-BC9A-4986-A3ED-F6D08601F4FB}
TEMPLETON 2113CB | {DD694EAA-A9BC-4C03-B675-60DCE9DF4147}
TEMPLETON 2113CB | {D86BE20E-930F-418E-B48F-A1FCF37B5587}
TEMPLETON 2113R82 | {F7BD212B-7F44-4A16-B423-2BCFB7829D6C}
TIDEWATER 2104226374 | {19823827-C5EA-4E2D-9FF7-7BB963BC816B}
TIDEWATER 210447828 | {15A35C1A-AEE8-44EE-A6A5-ED276523BD62}
TIDEWATER 210614072 | {A74482B6-4F98-4489-A417-0B9C2832ACBF}
TIDEWATER 210614072 | {7EBB7DBD-3233-4897-9C70-1CE800CC2803}
TIDEWATER 2106175854 | {3A206BA9-0A62-43D7-8B34-C6DB19D74D6D}
TIDEWATER 210618982 | {ABE849AD-DD99-43F2-AAF9-9EAC93F8BB98}
TIDEWATER 21062290 | {2CBEB58E-8C6C-48A4-AF77-398D7460FE13}
TIDEWATER 21062290 | {F744B448-0B02-4F78-8431-F101D634FBF9}
TIDEWATER 21062290 | {BE753D24-8AD5-497B-932F-CCEA608A77CC}
TIDEWATER 210638108 | {6B3BA6D5-A493-4AA4-84D1-29361093CE83}
TIDEWATER 210638866 | {C72BC650-7C75-41A3-A6D7-BB319B3F8372}
TIDEWATER 210657926 | {E1F3686F-1904-468B-8A6D-069DA557A173}
TIDEWATER 210665866 | {3A206BA9-0A62-43D7-8B34-C6DB19D74D6D}
TIDEWATER 2106703654 | {C72BC650-7C75-41A3-A6D7-BB319B3F8372}
TIDEWATER 2106875792 | {0807BB52-A426-4A8C-843A-18AAD53E7545}
TIDEWATER 2106905039 | {A4CE0343-6E2C-44CC-AED1-7435453D6570}
TIDEWATER 210695842 | {DECD64D5-E92D-44EE-BF28-1EF0D6E10478}
TIDEWATER 2106C514R | {8FCD9F0C-12A9-46C8-B7B1-BF847BD03786}
TIDEWATER 21091784 | {55A3EE44-C99D-4B83-BD89-BF3E3CE96ADF}
TIDEWATER 210967868 | {90FC9C0B-9B12-4728-8B3D-BF26560465BD}
TIDEWATER 2109777736 | {55A3EE44-C99D-4B83-BD89-BF3E3CE96ADF}
TIDEWATER 210978302 | {55A3EE44-C99D-4B83-BD89-BF3E3CE96ADF}
TIDEWATER 2109878884 | {90FC9C0B-9B12-4728-8B3D-BF26560465BD}
TIDEWATER 21098830 | {55A3EE44-C99D-4B83-BD89-BF3E3CE96ADF}
TIDEWATER 21098835 | {55A3EE44-C99D-4B83-BD89-BF3E3CE96ADF}
TIGER CREEK 0201320746 | {C7F675D5-2B2A-49BD-AF13-9888C7E4FCA2}
TIGER CREEK 0201CB | {42CE80CD-1575-4D75-9DA9-13CC191BD6F8}
TIVY VALLEY 11067150 | {90E00265-C0CF-4482-89EA-4364E2D4853A}
TIVY VALLEY 11067210 | {D8E13D73-EB68-4157-8FED-21C11BDD3D42}
TIVY VALLEY 1106CB | {36113653-5563-4401-879E-ECEBC9923AFA}
TIVY VALLEY 1106D8492 | {90E00265-C0CF-4482-89EA-4364E2D4853A}
TIVY VALLEY 1106R1450 | {90E00265-C0CF-4482-89EA-4364E2D4853A}
TIVY VALLEY 1107248306 | {BE7D1774-079A-4F76-A335-3394843B4D82}
TIVY VALLEY 110737522 | {DA50CC20-DF93-4A26-9942-3A43E97DCAC4}
TIVY VALLEY 1107584840 | {69DA4F1C-E07E-4189-8040-902C89E5A469}
TIVY VALLEY 1107599142 | {B0EAA688-0840-4FBA-BE74-3B15BA6BD7F3}
TIVY VALLEY 1107718068 | {5B8906BB-8EFE-4B1D-806F-A5C2303E7A64}
TIVY VALLEY 1107718068 | {6429C044-DD69-4871-9673-CAAF3DBE20CA}
TIVY VALLEY 1107718068 | {F70EA087-4DD5-4147-AA26-0D5F1FC47FFD}
TIVY VALLEY 11077380 | {755777FC-6215-430E-868E-B21D92A14A1A}
TIVY VALLEY 11077972F | {42672FB2-63E2-4627-8712-4CA7AD457C9E}
TIVY VALLEY 11077986F | {384C64C6-30B6-4162-9786-1DD25A62B49C}
TIVY VALLEY 1107822606 | {8C528F18-9D07-401C-90F8-07B202001D80}
TIVY VALLEY 1107822606 | {2CCB588B-990A-4DA3-9CC6-802905504EF9}
TIVY VALLEY 1107869946 | {8685FED6-DA63-4202-8ADA-3D58BFE83B0E}
TIVY VALLEY 1107CB | {B007F88B-9403-4642-A8D2-16BDDDACB785}
TOKAY 1101CB | {11EDF2B5-A0C5-48FD-9A56-5F2C5A063907}
TRES PINOS 1111203126 | {899DF856-B7D3-491D-B16E-756ACF7692DC}
TRES PINOS 11114032 | {BD94B291-9C0B-4C28-8C7B-50F4F86D7051}
TRES PINOS 11114064 | {68C1BEAC-9E07-4A35-9BA1-6FC5E18C5BE8}
TRES PINOS 1111CB | {81D7ACD1-11AF-45F6-91F4-8D9CD5CC46FD}
TRIDAM POWERHOUSE 2101CB | {A0F1DBF1-292A-454C-A5DF-A955BFE4DEBB}
TULARE LAKE 1104225890 | {059E4C88-1543-49DA-B841-26A92830195D}
TULARE LAKE 1104378350 | {9B5963FE-E5F3-4A27-8F57-605E12C02D26}
TULARE LAKE 1104378350 | {80B4B2E0-A828-47B6-8AE1-5376B89CFFDC}
TULARE LAKE 1104748282 | {80B4B2E0-A828-47B6-8AE1-5376B89CFFDC}
TULARE LAKE 1104884818 | {FF113BEB-7BE2-4333-8D15-EC8E29B17D69}
TULARE LAKE 110491874 | {2A28C53E-B200-47D9-B8F7-99521BDDB79A}
TULARE LAKE 1104CB | {059E4C88-1543-49DA-B841-26A92830195D}
TULARE LAKE 1104CB | {2A28C53E-B200-47D9-B8F7-99521BDDB79A}
TULARE LAKE 1106109984 | {04D17EA0-FF90-4F05-8725-70098C754E9D}
TULARE LAKE 1106565102 | {43770374-AD08-472E-A1A0-0430B4D1E827}
TULARE LAKE 110675538 | {04D17EA0-FF90-4F05-8725-70098C754E9D}
TULARE LAKE 110693686 | {04D17EA0-FF90-4F05-8725-70098C754E9D}
TULARE LAKE 1106CB | {04D17EA0-FF90-4F05-8725-70098C754E9D}
TULARE LAKE 110854074 | {56DB22B5-CE56-48B6-8FE4-9109734E0A42}
TULARE LAKE 1108572416 | {48A295FD-A0E0-4D43-9DC7-2E2C3E94F794}
TULARE LAKE 11089050 | {48A295FD-A0E0-4D43-9DC7-2E2C3E94F794}
TULARE LAKE 1108943184 | {48A295FD-A0E0-4D43-9DC7-2E2C3E94F794}
TULARE LAKE 1108976256 | {0B5264C1-7854-4468-8A56-C6635FB25F77}
TULARE LAKE 11089910 | {48A295FD-A0E0-4D43-9DC7-2E2C3E94F794}
TULARE LAKE 1108CB | {48A295FD-A0E0-4D43-9DC7-2E2C3E94F794}
TULARE LAKE 1108CUS8806 | {48A295FD-A0E0-4D43-9DC7-2E2C3E94F794}
TULUCAY 1101137224 | {8B251851-C2C3-4099-9FE2-37D1C843B1BA}
TULUCAY 11012280 | {D5040DDA-C582-40B5-8A53-2E3901DC0B08}
TULUCAY 1101323426 | {8B251851-C2C3-4099-9FE2-37D1C843B1BA}
TULUCAY 1101504524 | {4EA48B47-47EA-4694-BDCC-7065AA75E603}
TULUCAY 1101613014 | {DF39F4D3-AC3E-40A8-AD9B-36C95CD551B7}
TULUCAY 1101628 | {E6EA8FFD-93FC-4EE2-B4B3-05C67BB86274}
TULUCAY 11019999 | {DF39F4D3-AC3E-40A8-AD9B-36C95CD551B7}
TULUCAY 1101CB | {D5040DDA-C582-40B5-8A53-2E3901DC0B08}
TWISSELMAN 1102398782 | {0527D363-2242-444F-B9D4-B23BE5FB6366}
TYLER 11051522 | {0D1643DB-604E-4FBB-B45F-DBA97992B887}
TYLER 11051536 | {8FC5AABE-9067-41E2-B562-CCB95292040F}
TYLER 11051704 | {E58E84BF-2C2E-494E-AE66-0D141BD137C3}
TYLER 1105503690 | {99B508DB-4544-4193-87F9-B11616D1BA85}
TYLER 1105816852 | {E58E84BF-2C2E-494E-AE66-0D141BD137C3}
TYLER 1105CB | {AAAE8701-80F0-46AE-8702-4013E06C972E}
UKIAH 1111144510 | {C78630C5-8620-41E5-91C9-61A86B1AB982}
UKIAH 1111379946 | {405F1015-C662-4950-99EE-1E4A689283D9}
UKIAH 1111422886 | {3930EA03-8A68-4667-BDD8-17EFADBAA87A}
UKIAH 1111422886 | {93D393BB-7553-4CDF-A3C5-3EDDACF2D482}
UKIAH 1111433984 | {90D9EBEA-E8B3-45BF-93FF-595A29473B29}
UKIAH 1111477890 | {C19836E9-D34E-4A81-923F-AE30E5CB731B}
UKIAH 1111789282 | {0679194D-94A5-4BEE-A3BC-BCA5B0434E05}
UKIAH 1111807988 | {183B4AB8-E049-4175-AED7-96F466044CA0}
UKIAH 1111CB | {FBA231AA-2A4C-4C3A-9CF9-4FC7651694D6}
UKIAH 1113548420 | {CD90789A-8C40-4BA6-B727-13DE18B4CBFD}
UKIAH 1113691436 | {6C8F23E8-D864-4646-ABCC-F348028A767E}
UKIAH 1113691436 | {684DE428-4DA6-41EF-B070-9A42DD367718}
UKIAH 1113968652 | {81BDBB43-850C-4250-9194-B1A69ADA9BF8}
UKIAH 1113CB | {57AE83F3-7C35-4A08-BEA4-B10AAC4F4015}
UKIAH 1113CB | {056DA4FC-3963-4A38-A47D-C0DB965F519F}
UKIAH 1114206824 | {47F1875F-3F15-4519-A49C-1F4ECD7BF06F}
UKIAH 11143363 | {701CA21D-6BFD-4B4A-ADB9-CC5788801645}
UKIAH 1114380432 | {7CFF91C6-6122-459F-BD71-B9F17BE39EB0}
UKIAH 1114408 | {51D9F3E7-D9FC-4F6D-B9B5-400B76D74D25}
UKIAH 1114437 | {2FE1D905-DEDC-4D61-87FD-361B10F164AA}
UKIAH 1114544 | {4F4D60A8-18DF-4AD7-9533-2FDA5C5224B4}
UKIAH 111472990 | {7D69F374-F9B0-4F64-806B-E0305A606677}
UKIAH 1114737 | {214A05C9-B8F7-4DC9-9A64-BBB03ACB2B3C}
UKIAH 1114822 | {2D9FE14A-68D2-46A5-B4CD-1EF83FC0FBCE}
UKIAH 1114822 | {25631ED6-284A-4BC5-AD2C-3D40503B38F5}
UKIAH 1114844294 | {E31B357F-7D66-4467-A543-DD5E914AB51D}
UKIAH 1114911132 | {4F4D60A8-18DF-4AD7-9533-2FDA5C5224B4}
UKIAH 1114943840 | {F0BB0AAE-662A-48EA-9E79-24EA77E16FE7}
UKIAH 1114CB | {D98BCE06-B639-4635-9566-7FA7CFE5BC8F}
UKIAH 11151216 | {190ED11E-6BBE-4AB9-A430-D568E91970DF}
UKIAH 1115168892 | {E7C123E6-BA30-4506-A3E6-3FDF5CDF33DB}
UKIAH 1115534 | {7D8C1D44-5CC9-4E75-B479-CE3AA2BCFF70}
UKIAH 1115534 | {CD599840-F925-4A8F-AC72-601D0F3A1898}
UKIAH 1115731892 | {1F4C19A2-B5C9-4AF3-BE21-A4D815C3D032}
UKIAH 1115732918 | {524ABA47-5E18-42CF-AC16-E675374D5DF3}
UKIAH 1115899594 | {3FF9A88F-E2C0-476A-97B0-2B726DE9CB26}
UKIAH 1115CB | {A99474C6-C1F9-4A19-8465-2D8ED25CEFB7}
UKIAH 1115CUS6608 | {524ABA47-5E18-42CF-AC16-E675374D5DF3}
UPPER LAKE 11011121 | {8A09DFAD-5DF8-4E46-BDAC-6FE52B1709AB}
UPPER LAKE 11012217 | {B43238F4-CF98-4A9D-BABC-CCF102BA40FC}
UPPER LAKE 1101412 | {CEA08BFB-7016-4016-B5B7-B9CA2EAF8E9F}
UPPER LAKE 110142378 | {B4FEFEF6-4949-40A0-B2AB-64F4BB223B69}
UPPER LAKE 1101472084 | {6A48DD4C-8096-4848-9316-CAF03427E24D}
UPPER LAKE 1101660 | {0F0F521B-1DED-434B-B495-1C9D87139123}
UPPER LAKE 1101668050 | {8EE4FE62-50D5-4FC4-8E15-06E555952C5A}
UPPER LAKE 110175370 | {5002339C-3B44-461E-A16D-6DB263D4D731}
UPPER LAKE 1101861806 | {911C4C68-2E5A-42A2-8C57-88BC3B5D0196}
UPPER LAKE 1101CB | {6A48DD4C-8096-4848-9316-CAF03427E24D}
VACA DIXON 1101139898 | {AE7E6891-05E6-46B9-AC20-6D7C3DA9F6B6}
VACA DIXON 110115779 | {E531C5A9-C4E1-47FC-A5FB-E58402771000}
VACA DIXON 110118292 | {C14F8C7D-2418-4308-A5BD-32845AC90D2E}
VACA DIXON 1101392848 | {3BE6396D-6D17-4036-BB25-F9592AB5B612}
VACA DIXON 1101454328 | {9837C0F6-0F2F-4E27-A1F9-23B2A5A0AE60}
VACA DIXON 1101604552 | {24619094-D4BA-4F34-8E61-5CF30DBB0C99}
VACA DIXON 1101628308 | {EF20F4FD-42A6-47E6-BDFD-6030249E700E}
VACA DIXON 110175740 | {AE7E6891-05E6-46B9-AC20-6D7C3DA9F6B6}
VACA DIXON 1105965390 | {DF536E94-F9F9-48D4-A625-EBCDF4893D0B}
VACA DIXON 11059792 | {30E4D883-8616-4202-B2EA-1D70554D1ADA}
VACA DIXON 11059792 | {E29DDFD8-87C7-4111-AD68-0CCC26FD3BAF}
VACAVILLE 1103CB | {404CB668-CECA-42E3-95F0-FB6161DA4FDC}
VACAVILLE 1104293462 | {6E87673B-0332-4D64-B876-B31C65A7FB01}
VACAVILLE 1104CB | {CBB1E17F-BE5D-42E9-AB86-48D61CF7F4ED}
VACAVILLE 1108341974 | {581E59F1-CA4F-4FEC-AAD6-8177DA1775CC}
VACAVILLE 110847860 | {54E0D9F0-5A0E-4C2B-BA84-938E576B6A76}
VACAVILLE 1108530880 | {8A0CA8A9-94D5-4C26-B439-D32BD61C2E27}
VACAVILLE 1108922767 | {BAE6CC17-1005-410C-815D-1B7C2B8B4161}
VACAVILLE 110941782 | {D12E3D2F-1998-4DA6-942A-7BE316909F83}
VACAVILLE 1109592742 | {695B9A66-1C5D-4614-8CBB-D52A4B4D47A7}
VACAVILLE 1109799940 | {4751B483-ECAD-4AAB-B56B-99664044B1D2}
VACAVILLE 1111486280 | {C5A7E5A8-AFE6-471D-B5C3-D5602E2A860C}
VACAVILLE 1111905076 | {2101ADD9-8EAD-46F4-A7CD-716FE2008CDF}
VACAVILLE 1111CB | {1F08C74E-1D18-453D-9F09-2E91ADE9AFB1}
VACAVILLE 1112239276 | {D860A6A4-4492-4A71-A749-BCD6B53CBA01}
VACAVILLE 1112354578 | {6407F04E-6CB0-4F44-9E99-762FC3F45056}
VACAVILLE 1112CB | {5828CFD8-0F34-469A-AB4B-4395B45CE3D2}
VALLEY HOME 17023214 | {C60A300E-1779-4404-8D97-28A5A6037B50}
VALLEY HOME 17031532 | {F0B34ED0-42FC-4061-AC8E-1112027FAE68}
VALLEY HOME 17031558 | {1005EDC8-1357-436D-879A-4415102F0FE3}
VALLEY HOME 170339660 | {A2F287EF-C287-4618-B3E6-557974E96CE4}
VALLEY HOME 170356266 | {F896935A-7AAB-4D4B-9917-44373B280809}
VALLEY HOME 1703768534 | {F896935A-7AAB-4D4B-9917-44373B280809}
VALLEY HOME 1703CB | {F896935A-7AAB-4D4B-9917-44373B280809}
VALLEY VIEW 1103218424 | {0AF2BCCE-C158-41A1-A8FA-127B4D2028A8}
VALLEY VIEW 1103CB | {6F4A4EA4-DB8C-41B8-B673-0FAE8635F67C}
VALLEY VIEW 1103P158 | {21C35FC6-3AB5-408E-9078-4C07DECDACFE}
VALLEY VIEW 1103P160 | {2371EFC2-B46C-4698-931C-537DFFB0D5A5}
VALLEY VIEW 1105305072 | {A9274254-950F-4772-BD6F-0C6FB4FEF4A4}
VALLEY VIEW 1105CB | {7F8D329C-2906-4CB9-89A6-48A9455878D0}
VALLEY VIEW 1105P190 | {75634943-F60A-4935-9A1D-02ADD9591487}
VALLEY VIEW 1106865650 | {B79581BD-E589-4E72-A7CE-26316DC5699E}
VALLEY VIEW 1106CB | {D9DED303-0FA6-4611-A466-91E33B741947}
VALLEY VIEW 1106P128 | {30491B06-175D-4B50-9477-0E42FFDBA4F5}
VALLEY VIEW 1106P166 | {064EA0EC-DFDE-4FA8-8393-49958A6F3357}
VALLEY VIEW 1106P176 | {1A50D894-CA6E-4856-B84F-5DA7159938A7}
VALLEY VIEW 1106P176 | {B787A327-E708-4D5C-865B-C65998470D53}
VALLEY VIEW 1106P180 | {27893E9C-0A5B-4290-96D8-63CEC0636192}
VALLEY VIEW 1106P182 | {772F24AF-7DA1-47C8-B6AE-4C4810E9D260}
VASCO 1101MR290 | {9512CE5C-7E76-48C1-A07D-A46BF4EF0B55}
VASCO 1102208712 | {A9FBDDA8-24C2-4BE2-8132-60998883919B}
VASCO 1102530878 | {28C1D480-46CB-490C-8F65-AE19B53DBA69}
VASCO 1102530878 | {EC1C4CEC-F9A4-44C8-8625-FDE413BDA728}
VASCO 1102530878 | {940E4DBA-804F-4033-AFB1-1900E1E5DF1D}
VASCO 1102530878 | {EC8BD8EC-8ABE-48B0-90C7-7FC8E8AE0806}
VASCO 1102546328 | {940E4DBA-804F-4033-AFB1-1900E1E5DF1D}
VASCO 1102886522 | {4653D811-6732-4F47-994C-B6C9ADAB66CF}
VASCO 1102CB | {0F0CF89A-377C-4F92-805F-45C88532891D}
VASCO 1102MR178 | {C757B1E5-E864-41C5-8F1F-450BE13C3852}
VASCO 1102MR418 | {263677AF-C833-4A6E-AF5D-6FC3FEA3BA3F}
VASCO 1103964102 | {DA001B7B-04D4-4B91-80D8-0CD4D55EE955}
VASCO 1103CB | {D777EA4E-3A7C-4425-B34B-DA242E9EFE4C}
VASONA 1106944560 | {D5583FAD-E457-4793-A47C-008117308B38}
VIEJO 220131852 | {11A2851C-72B1-4A62-98D6-D6E2FFA710C1}
VIEJO 2201431508 | {B33BF328-93C8-4AA5-A6AC-C69DE6A33DBC}
VIEJO 2201563516 | {DE1EEE83-8C6C-447F-B024-0ED2E3DD3250}
VIEJO 22019490 | {D5629837-45B4-4B33-A660-AFDD9F409AB3}
VIEJO 22019698 | {7C0AA1F8-3024-4D35-BAB8-1475B467A597}
VIEJO 22019704 | {3D5F5882-266F-4D3B-88D4-82F44D2D1486}
VIEJO 2201CB | {11A2851C-72B1-4A62-98D6-D6E2FFA710C1}
VIEJO 22022179 | {15DC668C-70E0-40EE-8D60-C0D788E24E93}
VIEJO 22022606 | {DA30E872-22F6-4600-80CD-C659254182C9}
VIEJO 220235388 | {5487E49D-3A5D-43A1-BCCA-6878D14EA68E}
VIEJO 2202578112 | {C0E685DA-91DE-46EE-8BE7-A61FD23415F4}
VIEJO 220285904 | {C94EFA28-C1F1-4A0B-925C-0A3777669A3F}
VIEJO 22029100 | {15DC668C-70E0-40EE-8D60-C0D788E24E93}
VIEJO 22029104 | {AD318D3F-F8E0-477A-9CA4-DF6AF7B738B6}
VIEJO 22029118 | {BA7590D4-FA7A-4E66-A4E2-9385E2F5FD08}
VIEJO 22029120 | {3A16450D-C56F-42B5-80F8-8369EAD6F0C2}
VIEJO 220292792 | {C8ECEDCB-3AAA-445C-9FF2-2773F53D5EAE}
VIEJO 2202942280 | {8A74C7DC-B877-419C-BF66-1FAB21022889}
VIEJO 22029488 | {8E85DA31-E8CD-4D80-BE55-60AFA6937F74}
VIEJO 220298146 | {761219CB-0066-4657-90C4-9A36DE51CBBD}
VIEJO 2202CB | {204F3E15-8D98-42F3-A6B0-F8D2FC5C7EAD}
VIEJO 22032016 | {4DC9724F-62CE-4CE8-B9B2-FC8D42753B78}
VIEJO 22032628 | {4DC9724F-62CE-4CE8-B9B2-FC8D42753B78}
VIEJO 22032634 | {B3DAF752-D08B-4E1F-A920-D89FDCCD38AE}
VIEJO 22032636 | {47D62398-F637-4892-AC6D-1C572EFFA589}
VIEJO 2203573610 | {4DC9724F-62CE-4CE8-B9B2-FC8D42753B78}
VIEJO 22039094 | {BCAEB21F-2017-4B30-B93C-AB6BCBE099D0}
VIEJO 220393964 | {4DC9724F-62CE-4CE8-B9B2-FC8D42753B78}
VIEJO 2203947314 | {2745EA16-9172-4362-B554-6BC9B1A69619}
VIEJO 2203CB | {4DC9724F-62CE-4CE8-B9B2-FC8D42753B78}
VIEJO 220436948 | {DB34AA1E-C0F6-41DF-BFC5-43E5CD8E6B2B}
VIEJO 2204385618 | {84E279B4-A57A-4132-ABEC-C7AA0EE5903D}
VIEJO 2204481042 | {540DA92C-2BA2-4C83-857C-5060FD1BE289}
VIEJO 2204746866 | {DB34AA1E-C0F6-41DF-BFC5-43E5CD8E6B2B}
VIEJO 220486890 | {82047029-EAC1-4E39-B4D2-10647DA90BC3}
VIEJO 22049440 | {35D3CEF8-0523-4ECA-BC11-26CD68907349}
VIEJO 22049540 | {D3AE8800-862E-498F-9908-541EA621BA7E}
VIEJO 2204CB | {DB34AA1E-C0F6-41DF-BFC5-43E5CD8E6B2B}
VINA 11011570 | {427F674F-2998-4807-8909-FFE2EF8784B5}
VINA 11012681 | {427F674F-2998-4807-8909-FFE2EF8784B5}
VINA 11013302 | {8FBDBB0A-7AA3-4738-B64B-BAAA6EF4DAFB}
VINA 110135730 | {DE33B171-715A-4B55-A52C-48E0D345F70B}
VINEYARD 2107246084 | {6B7CA8C5-9E7E-4E93-8E32-6FC9E10FCF47}
VINEYARD 2107978364 | {3BBA2979-D28D-4292-8651-8D6BC40655D3}
VINEYARD 2107CB | {A183346D-F285-4000-8E25-4FAC2F51DCC1}
VINEYARD 2107MR332 | {5E4EB8F1-F20C-4A10-9616-09E586C03349}
VINEYARD 2108609690 | {C0C2BC4D-C77F-44B1-A615-4456E8EEC076}
VINEYARD 2108MR172 | {719ECDBC-AADB-4BEE-A55F-93F185A30BDE}
VINEYARD 2108MR172 | {FB1D650B-43DB-469E-AC02-52DB71621BCA}
VINEYARD 2108MR172 | {3E10AC02-E1B1-4131-82DD-82507C09BB71}
VINEYARD 2108MR172 | {D247C9D4-2385-4C86-98D9-FAEFF0DAB6B3}
VINEYARD 211056610 | {4B9A456E-40C9-431E-A74D-1C7F9C39E74C}
VINEYARD 211056610 | {6CDF911A-C085-403E-BA70-06765797CBC0}
VINEYARD 2110CB | {14A8794B-8A75-4FC8-9957-3059A6D6C76B}
VOLTA 1101118977 | {2BE482C0-C39F-40F6-B229-4547EBDB75E8}
VOLTA 11011516 | {ED33FD5F-C222-4440-B96F-9A832331CF99}
VOLTA 1101152784 | {5DCDF102-E183-4740-8B95-F1F007A05D49}
VOLTA 11011596 | {2F8DBBAA-A379-4ECE-8007-F482E8F75EAA}
VOLTA 11011640 | {DF67F6ED-C0C1-4634-A8E7-5650468AFAD4}
VOLTA 1101239094 | {1CF589A8-259B-4332-9E59-8C8CB511B137}
VOLTA 1101239094 | {5E2B226D-15A7-4DAE-8B71-5E0F740447DB}
VOLTA 110149742 | {2B3F7DCA-485E-4940-AF70-C148286D4D0A}
VOLTA 1101507876 | {BF0E4538-86EF-4A16-BC6B-FF3CC49B1D10}
VOLTA 1101519282 | {9BE38A1B-D71B-46ED-A9A4-A91DA3C8C238}
VOLTA 1101524364 | {29B56916-106D-4AB3-8600-E01F3A340C4A}
VOLTA 110153118 | {0F8042BD-810A-4C9D-833A-F377AF6EE4DF}
VOLTA 110165764 | {375728DD-644E-4E4B-9A8F-230DD2D4E917}
VOLTA 110167672 | {265C7E9E-E16C-4C9A-AF14-3F77D32329BC}
VOLTA 110185234 | {ED0B6774-A707-41C7-AD0B-86162B275429}
VOLTA 1101914816 | {5F524D99-5A7F-42DE-BC2E-51D7912A1CAB}
VOLTA 1101914816 | {F1CAE000-63B0-4EAF-BBEE-3360EF144539}
VOLTA 1101CB | {F21A680A-E282-4C69-AC36-05BB391457FE}
VOLTA 11021502 | {1EA4A0A1-3D5B-4E8F-B75B-661AF3FEE831}
VOLTA 11021504 | {2D79CCBE-1B8B-472A-B9BB-B34254CCD666}
VOLTA 11021646 | {82B5D74E-1D42-49A6-873C-1363407619B8}
VOLTA 11021650 | {FEE27DB0-3817-4D7E-9EF5-189449263C1D}
VOLTA 1102281296 | {6381DBA6-6F66-4F8E-9BD7-1A77E260C1A5}
VOLTA 110237350 | {82B5D74E-1D42-49A6-873C-1363407619B8}
VOLTA 1102453266 | {98C4DD6D-D3EE-4676-9123-391728297153}
VOLTA 110253130 | {1EA4A0A1-3D5B-4E8F-B75B-661AF3FEE831}
VOLTA 110254932 | {3AA926AF-5D59-48E9-968A-65279153CE9D}
VOLTA 1102641544 | {06F73A44-E6BF-4E7C-AE40-21A987895C90}
VOLTA 1102765366 | {2D79CCBE-1B8B-472A-B9BB-B34254CCD666}
VOLTA 110280982 | {2D79CCBE-1B8B-472A-B9BB-B34254CCD666}
VOLTA 110293418 | {06F73A44-E6BF-4E7C-AE40-21A987895C90}
VOLTA 11029742 | {666559A7-03EB-4157-BF3B-FDC9527EC86F}
VOLTA 11029742 | {A7123BEC-B365-4766-B96E-6C5017CAB086}
VOLTA 110297816 | {A7123BEC-B365-4766-B96E-6C5017CAB086}
VOLTA 1102CB | {DC239059-B1DA-4C89-A482-3310C8764DA5}
Valley Springs 110111158 | {441CFEC9-1CA0-48DF-94A7-C868FF359EA8}
Valley Springs 110113498 | {A0B72D64-342D-4CD8-B398-D7C01DA365B3}
Valley Springs 1101179382 | {657DBFAC-1DEB-4C8D-A356-BB20B766D324}
Valley Springs 1101207256 | {744E490C-4B9D-43E3-89F3-EC14E8D89F45}
Valley Springs 1101236904 | {744E490C-4B9D-43E3-89F3-EC14E8D89F45}
Valley Springs 1101631634 | {28704A09-C793-46D7-AE1F-226444F90A98}
Valley Springs 1101746860 | {1DBAC692-C02F-4D85-9C55-E0939D0D2D10}
Valley Springs 1101746860 | {BF3CE71C-DA63-4B28-B09D-86F471DF5871}
Valley Springs 1101750010 | {7465C87A-2B17-44E2-A07D-3F978BE2E64E}
Valley Springs 1101752104 | {744E490C-4B9D-43E3-89F3-EC14E8D89F45}
Valley Springs 1101769000 | {5BEB7DB3-3BFD-435F-AD8B-9A82CD60EDEF}
Valley Springs 1101805992 | {E975FAAC-12FF-49D2-9A07-5B70D23C8C2C}
Valley Springs 1101CB | {657DBFAC-1DEB-4C8D-A356-BB20B766D324}
Valley Springs 1102124762 | {419611F0-18F7-4695-B6DF-BDA8A5FA000F}
Valley Springs 1102188892 | {F19F2971-6A5B-4D7A-B330-5B2DEED67E3D}
Valley Springs 1102191544 | {207C6256-DB81-41B8-B8E9-FF1EC6E289A9}
Valley Springs 1102191544 | {83D94760-5CB8-41DD-B92C-46864926E4CC}
Valley Springs 11022646 | {3FB47D58-B406-4320-8238-19B8B73E9349}
Valley Springs 11022646 | {572F5560-3521-4149-BE47-7119ED6CEDD6}
Valley Springs 11022646 | {C97744A0-F0AF-4C46-A8A3-EC1E583B92FA}
Valley Springs 110236880 | {9437F877-1333-4C22-9F2B-1B73DBE0D156}
Valley Springs 110236880 | {2CE7DA92-EEC1-4680-BEC4-A1E05BA2B50C}
Valley Springs 1102526600 | {DE8A973B-7FE7-4F57-923A-5C13B8211F2F}
Valley Springs 1102606522 | {DE8A973B-7FE7-4F57-923A-5C13B8211F2F}
Valley Springs 1102748874 | {E1EA6528-CFA0-4077-92F4-6EDC0C6A98B2}
Valley Springs 1102CB | {DE8A973B-7FE7-4F57-923A-5C13B8211F2F}
WAHTOKE 11087160 | {8C61B566-2CE9-45F0-BA5B-3320FF1AC522}
WAHTOKE 11087180 | {8C61B566-2CE9-45F0-BA5B-3320FF1AC522}
WAHTOKE 11087570 | {4582E0EF-483F-43C4-95C4-EC5D22AC2028}
WALDO 0402258792 | {41C45E4C-83D0-45DA-8DDC-FF29D2FC8610}
WALDO 0402965216 | {B6A1E84D-F904-4E0D-8713-BF77906CA63F}
WALNUT CREEK 0404CB | {D56BF5EB-906E-4B51-BA5A-E962F016AADF}
WATERSHED 0402402/2 | {7F61A8AE-BB41-406C-ACF6-605D5BCD3BF7}
WATSONVILLE 21015470 | {F48692A7-9435-491C-A540-835A2616866A}
WATSONVILLE 21015470 | {2C7BC800-10C3-4DC0-9802-A63A1E430DC6}
WEIMAR 11012058 | {3EC318A0-0829-42F7-A409-490651B77C0C}
WEIMAR 11012058 | {77B75A1F-CEB2-4775-8F57-5AD0D012EF37}
WEIMAR 11012084 | {38AEC874-AA24-4AF0-80B3-26C46CCF1F16}
WEIMAR 11012084 | {62E8BF4C-1057-4015-8FCB-6C7AA1C84050}
WEIMAR 11012084 | {7AE2D43F-262D-417F-8DA9-8659A611CA1F}
WEIMAR 11012084 | {8ED71507-346D-4047-B5E4-6D462F431AA4}
WEIMAR 11012740 | {DA254098-CE2F-4B1D-8DCD-E2A142ECA867}
WEIMAR 11012740 | {4DA3237C-43DD-44C3-ABA5-31860411C7FE}
WEIMAR 11012764 | {CBE676E4-58AB-460F-8EF4-93AB8DD21D9C}
WEIMAR 11016193 | {8073A82C-5541-4488-B7C0-03B138997621}
WEIMAR 1101963878 | {3F2C9EA4-8A25-4199-991D-03F34AC1B306}
WEIMAR 1101CB | {C6D2DBB1-9437-46D3-8E37-6D1AD2333690}
WEIMAR 1102CB | {576CF59E-86D2-4E41-A7A3-27CEB8B77F40}
WELLFIELD 11022842 | {94668338-D057-4AD5-892F-BB0D86C28946}
WELLFIELD 1102CB | {B75AE0C3-AE32-4560-9D2E-0C12544F84C7}
WEST POINT 110112256 | {10618A90-ED86-44CD-8B76-773E3BF2AE42}
WEST POINT 110113444 | {1F21142A-72EE-4D4A-A8F0-E9702D60226C}
WEST POINT 11014706 | {E8E54876-15CA-4535-8C00-844AA0076F05}
WEST POINT 11014706 | {EB249B11-E020-422F-B912-48991FFADA06}
WEST POINT 1101846128 | {4B75004F-4E27-4349-9299-9E15DD22EC27}
WEST POINT 1101CB | {B92F58F2-6135-47A4-8467-3E84B6151393}
WEST POINT 1101L1969 | {10618A90-ED86-44CD-8B76-773E3BF2AE42}
WEST POINT 1101L2137 | {E46FABFB-55FB-4D4F-BA75-5DD91E93E72E}
WEST POINT 11021369 | {05B4A0D6-7A96-4090-A1BD-DACFFC66B22B}
WEST POINT 110234416 | {0EFB4216-A177-4018-B731-828073FEC64E}
WEST POINT 110236676 | {A8732E28-B88B-4AD3-83C5-02301897DD37}
WEST POINT 110236676 | {1445490F-C0B5-460E-8F6D-3B7658CD2546}
WEST POINT 110236676 | {26B08941-3AF1-4A0A-A71C-585088EF4D20}
WEST POINT 11024788 | {7DA2EEB5-1A19-437C-8020-DD813277F9CC}
WEST POINT 11024788 | {051C6601-5FFD-4D3A-A601-011F78DA88CB}
WEST POINT 11024790 | {BC28DA89-C644-4420-8340-E07D2A106004}
WEST POINT 11024790 | {4C31F9F3-FF43-4013-B249-266EFA0B514A}
WEST POINT 110251104 | {8ACE71D9-D8E5-45BD-957F-176761941B85}
WEST POINT 1102550341 | {B4775ECF-089E-4B59-886F-29CC5F61BC2E}
WEST POINT 110272036 | {4D3D5180-6A6C-4C43-B692-915E3881962C}
WEST POINT 110277204 | {6211F369-8BB0-4A6F-AF12-1490B4F377A4}
WEST POINT 1102837804 | {78F6C23F-A7D6-421C-AA40-7E8FA02771DF}
WEST POINT 1102865252 | {D5DB4E72-4F1F-4A3B-8179-F66F899D3FE2}
WEST POINT 1102911834 | {38A333B0-520D-4BFA-8897-52BDCDFFA8DB}
WEST POINT 1102911834 | {6CADE958-C5E6-4E3B-8C5D-26AAB0EA0CC3}
WEST POINT 1102911834 | {6E390106-E444-45C7-BF86-18C0B1F1128F}
WEST POINT 110293116 | {2DE74D61-95A1-4D32-9CCA-28AB5E692CE7}
WEST POINT 1102946726 | {D49AA913-EECB-4BCA-BA4C-7C19F169FD45}
WEST POINT 110298894 | {F2514EBA-645B-4C44-97D3-B59148622E8A}
WEST POINT 1102CB | {79B5F90A-1D47-4A2C-AFB7-278FDA451FB3}
WEST POINT 1102CB | {EC11255E-1283-4994-89AE-376C709CBC76}
WEST POINT 1102CB | {386D733D-CD43-4317-BE17-EAA2ED2E8030}
WEST POINT 1102CB | {464BE3F4-8F80-4353-BC55-4219CA5C3327}
WEST POINT 1102L1641 | {4F96F9A8-1C55-4C8A-A6A0-C38F62DCE59B}
WESTLEY 110111736 | {A40369F9-5BFB-4A69-8B09-DA1A82DE5EFA}
WESTLEY 1101463982 | {E05B0763-14F9-4FE9-A6CE-D2FD7DA8396A}
WESTLEY 1101820958 | {5D9D0169-9A60-4F2E-81FE-3563A32A79B5}
WESTLEY 1103237522 | {248AE4B1-0618-414C-9295-0197646733FC}
WESTLEY 11039010 | {0DB6DB9D-7804-4D10-B639-1A5CA91DDA98}
WESTLEY 11039900 | {6963786F-9EB8-4472-87D4-58E714762935}
WHEATLAND 11041348 | {86B4B4F4-9AA5-4F80-9B50-3C90FCAE3FE6}
WHEATLAND 11042218 | {0E4E35BF-C95D-4A21-8E64-F22502FD43CB}
WHEATLAND 11042220 | {05DF9274-5A55-475F-A57B-2374DB373170}
WHEATLAND 11042700 | {4B414DEC-F869-45CA-863F-BA162E505527}
WHEATLAND 110436326 | {4BB9E4F1-1B56-47EF-93A2-A594617F11C3}
WHEATLAND 1104CB | {F940122A-B8E4-40C2-BAEA-270BDBE4B973}
WHEATLAND 1105199134 | {BD7C5753-41E8-4E66-BECF-6C25BFB68211}
WHEATLAND 1105248490 | {373720FB-6F75-4350-A081-94440166CEBB}
WHEATLAND 110591170 | {B814ECD9-6160-4057-8AF0-345725EF4AA1}
WHEATLAND 1105CB | {26785F21-BFE8-4E36-8ADA-402E572F7611}
WHEELER RIDGE 110170228 | {7E64131D-F8C1-49DF-856D-35C664347508}
WHITMORE 11011594 | {6D09044C-C5BE-4454-95FA-4A81291B04F9}
WHITMORE 11011598 | {0A7498D4-3D67-421B-B0F9-EE472ACD2B71}
WHITMORE 11012211 | {FD008D02-CB89-4998-9621-14861264532E}
WHITMORE 110145262 | {D9E3C410-A0BF-4EA8-96F2-E696EF9ADFFA}
WHITMORE 1101589578 | {9B3AF54F-5B2F-4275-8A5D-51F2329D7BA1}
WHITMORE 1101903576 | {E86AD7F5-5911-4575-950F-165EE3A6B82A}
WHITMORE 1101CB | {E0835FD3-053C-4202-87EB-465B52D17969}
WHITMORE 1101WTGLR | {E0835FD3-053C-4202-87EB-465B52D17969}
WILDWOOD 11011454 | {D78DCFCA-A3F5-48E7-AD4B-409B173DF385}
WILDWOOD 11011576 | {57B8A89B-DB5A-4A47-A82F-ABC7F06A8571}
WILDWOOD 11011576 | {43DD62F5-F75F-45BE-9843-E49C81EA56F2}
WILDWOOD 1101384582 | {DE2BE838-418E-479A-846C-D45336A92EC1}
WILDWOOD 110185112 | {47D06C81-6B61-4B8B-8054-D7C4BE7B9ED2}
WILDWOOD 110198896 | {BF76B4C8-9530-427B-8649-806B9F48C554}
WILDWOOD 1101CB | {47D06C81-6B61-4B8B-8054-D7C4BE7B9ED2}
WILLIAMS 110230232 | {9BDCE959-CD8D-43E4-9213-A39207147448}
WILLITS 11021270 | {1C1CA89F-8D6E-4D8E-B038-38C87CE5A599}
WILLITS 1102350324 | {E32B6BE0-3764-43AD-A424-17E7100BD267}
WILLITS 1102CB | {9734DBF0-6F90-4CE9-BF04-F2CD4B5AEADC}
WILLITS 1102CUS8736 | {9734DBF0-6F90-4CE9-BF04-F2CD4B5AEADC}
WILLITS 11032506 | {3B860DB0-A747-4B2B-900E-A58BF536B758}
WILLITS 11032506 | {A3C632CF-39C5-465A-9D49-202E0ECD77BA}
WILLITS 11032831 | {F6349692-FD4B-4AF4-B5ED-833A28988598}
WILLITS 110337504 | {00459A21-49A7-4C9F-B533-C9081A2B5652}
WILLITS 110337506 | {0E5984A8-2AB8-4609-A4AD-A7903A25522F}
WILLITS 1103409216 | {9EA45B12-9DAE-41DD-A093-6F45C691C648}
WILLITS 1103538 | {BE2F5686-D520-4116-B2FF-E45C57EBCDE2}
WILLITS 1103538 | {A107BEB8-0DB9-4C08-823A-F131F13779EC}
WILLITS 1103564506 | {4F653083-189E-4DD0-AEDF-74D1A3A4FADD}
WILLITS 1103696 | {F57C31EA-DB2F-41EB-82F4-E33CB26AFF7A}
WILLITS 1103696 | {EC79F2BF-D405-4EF8-A570-37C7BDE7D1BE}
WILLITS 1103826 | {72556B33-F33B-4E33-8959-39723007B093}
WILLITS 110391810 | {75E7E1B3-D461-49A0-A0AB-E84CDEE528DF}
WILLITS 110391948 | {69FCB8B8-95BC-4541-BD6A-BC578FAA27C9}
WILLITS 1103964 | {B6068DE4-2B76-4559-A97F-83EC4465ECB7}
WILLITS 1103966 | {BD0977E2-D82F-4AAC-B014-EDCBC19E0BA7}
WILLITS 1103968 | {7E4735B5-33E8-4CD6-9F8D-A9385ABC1901}
WILLITS 1103CB | {46D54C37-C2FC-4DC4-B1D4-D353347D542B}
WILLITS 1103CB | {30B0A48E-C3E5-42AA-9273-8BF1B6001968}
WILLITS 1104171684 | {BDFE1355-9D5B-4F1E-B747-8DA12AFB661A}
WILLITS 1104188268 | {F170EA1C-ED28-4FA0-9674-709AC3DC1CC0}
WILLITS 11042785 | {691ED4C7-2A4B-4A5E-A8F9-C77C81898485}
WILLITS 1104329646 | {B6D81FD3-E8F1-4789-8A3D-786E0C133AC6}
WILLITS 110434008 | {5B3D2F2F-DF90-45C0-963C-1589633A1498}
WILLITS 1104341020 | {C8AC2F19-57DB-4CAC-8DED-1C04E1045CB4}
WILLITS 1104341020 | {47E718CA-B049-4197-84E1-96CD58F2DA8A}
WILLITS 11044650 | {CBE7DCF1-ECDA-4517-A76B-79D934ABEB82}
WILLITS 11044759 | {B956F73E-F4AA-4A33-B086-BB7D86EB5875}
WILLITS 1104627552 | {E29C36BB-A169-479C-AE48-87F28EBCCCAD}
WILLITS 1104936096 | {8248C880-166C-430F-A087-7EE0312E38BC}
WILLITS 1104CB | {19EB4414-DC45-4E37-BE88-7022C918AAEC}
WILLOW CREEK 110129362 | {1D151194-CF04-464D-9004-1F697BF4DA48}
WILLOW CREEK 1101294292 | {807F51AD-F942-43EC-8048-0E101D541BCD}
WILLOW CREEK 11013050 | {339F8F9F-E6E2-48FC-94D7-73A8490708ED}
WILLOW CREEK 11014904 | {2D4A5008-1C90-406A-A2B7-E4FA7A353F8A}
WILLOW CREEK 11015002 | {F93B7399-B5D7-47F7-B54D-9C6933AF7A2F}
WILLOW CREEK 1101609914 | {E4F920B4-3AE4-471E-9396-F19C0792BF57}
WILLOW CREEK 1101729000 | {2D4A5008-1C90-406A-A2B7-E4FA7A353F8A}
WILLOW CREEK 110191926 | {ABEF63BB-FD93-485F-8439-718A3A0F3B42}
WILLOW CREEK 1101CB | {D8B02D5B-6C13-4C05-89BB-FB46690FC150}
WILLOW CREEK 110237374 | {E5474BC9-1FBC-47D7-924C-371BAFB1C79B}
WILLOW CREEK 1102CB | {0F7FFA32-0648-474C-B64E-A51E578D757F}
WILLOW CREEK 1103205028 | {14EDF25B-565E-45F6-929A-4EE758947CA8}
WILLOW CREEK 11032936 | {2C99C690-D2AE-47A9-8969-EBD60FC1E2F7}
WILLOW CREEK 11033090 | {999C3E0D-1E31-46AC-B115-3B4EB4A2A32A}
WILLOW CREEK 11033090 | {82912C06-14DC-427A-919C-E1D70C234067}
WILLOW CREEK 110347966 | {17DD54A2-E0AC-4BEA-A392-1296720E1866}
WILLOW CREEK 110347966 | {E7E4CCFA-1ADF-4735-A0EC-4090945D6801}
WILLOW CREEK 11035012 | {315E4027-C3C2-48C5-87DF-DFA709D95931}
WILLOW CREEK 11037514 | {2ADAB335-F68D-4E0E-93A5-403C7C54DA76}
WILLOW CREEK 1103CB | {A739E4CD-6027-447C-8193-CB877EF24141}
WILLOW PASS 2107175082 | {D2B6CA0D-AEE9-42DD-8D3A-6B945BF279F0}
WILLOW PASS 2107273996 | {85D52075-D52D-4D71-A7CF-355529F177DC}
WILLOW PASS 2107537100 | {9E92B87E-CCDA-4E6D-9002-98170A096742}
WILLOW PASS 2107CB | {24C8C7E8-733A-453C-8A4F-FE8CF59DAF59}
WILLOW PASS 2107CB | {D2B6CA0D-AEE9-42DD-8D3A-6B945BF279F0}
WILLOW PASS 2108152874 | {F4D0AF9A-071E-4C57-9A34-14AB7BA67617}
WILLOW PASS 2108328308 | {19BF5C42-2FB2-48D5-80B4-FA2CC74812CB}
WILLOW PASS 2108759230 | {96432DBA-7407-4CD2-8507-A73886C02BC6}
WILLOW PASS 210879972 | {B0B4A69F-5291-4620-A23B-AC6563CC0845}
WILLOW PASS 2108959924 | {1FEB7E65-DDE1-46AE-83AD-B5F30417F926}
WILLOW PASS 2108CB | {31EEDA66-62CC-4E94-9F57-70FF511E1CF4}
WILLOW PASS 2108CB | {DC51FFAF-E56E-43F8-8D9C-2D899538D5AA}
WILLOW PASS 2108CB | {1FEB7E65-DDE1-46AE-83AD-B5F30417F926}
WILSON 1102332156 | {B6116FA1-77DF-48E1-B2A7-810222902CE8}
WILSON 110290190 | {2A5E1F67-43A6-4E11-9EA9-5BBBA29654D3}
WILSON 1102CB | {94671B02-0241-41D7-A046-02BF25A5BCE4}
WILSON 110310690 | {AF1FCC9F-86FE-4322-89E3-0305F3D521A4}
WILSON 110310700 | {A00E5CF4-6899-44EE-A933-0226B983CD0B}
WILSON 1103291366 | {15C3F357-1CEB-4066-AE54-EA70099793FB}
WILSON 110347636 | {AF1FCC9F-86FE-4322-89E3-0305F3D521A4}
WILSON 110348236 | {A1AC7D41-B778-451D-ABF3-8E1F77E14CAD}
WILSON 1103873156 | {AF1FCC9F-86FE-4322-89E3-0305F3D521A4}
WILSON 11039080 | {13DF9192-8079-4D25-A11A-CB527977D7C9}
WINDSOR 1102382 | {8BAFFC14-6408-458C-A293-E7A624D7DE6D}
WINDSOR 11025066 | {7E2347F1-9A9D-45A2-8B25-599E2528C493}
WINDSOR 1102596 | {A5AB3023-8A67-40D2-8ABC-A7E44AB6E684}
WINDSOR 1103171410 | {E7AFB8F0-D502-427F-8F0D-B495CABCC789}
WINDSOR 11035060 | {5C89CE05-2636-4AC9-BAFC-5707AC921B94}
WINDSOR 1103701650 | {A5156E9B-2E85-425B-86C4-9A651651BB23}
WINDSOR 1103CB | {AC54FADD-7787-4603-A3A1-1A1440375EA4}
WISE 110163199 | {919A8A04-B874-4A68-AF90-D4143250C76A}
WISE 1101CB | {919A8A04-B874-4A68-AF90-D4143250C76A}
WISE 1102126726 | {DC576B2D-0C2F-4C55-87C5-46BF8669B29A}
WISE 11022054 | {E6EC7043-C8B2-457F-AB90-031C70C010CA}
WISE 11022230 | {F1207558-CC1A-4752-93E1-1A45AF2EEAFE}
WISE 11022234 | {2EBA7959-7933-4246-BD38-55C2DE2602D7}
WISE 1102307494 | {DAD370F0-D502-456B-9D6C-C04B93F7ABC9}
WISE 1102449556 | {51CECB7D-FE74-4A7F-A054-30E9A1B3F446}
WISE 1102465074 | {551FC8A6-8E47-4C6B-BA77-51B1DF1DDFC3}
WISE 1102697216 | {64620CA8-4B52-4298-8F14-91A606AD81F8}
WISE 1102697216 | {BFD9E547-EC0B-4BBF-83A2-6E5AE3B0CA31}
WISE 1102CB | {605358FE-4007-4349-A521-8A072F22F69A}
WISHON 1101514298 | {CACEDC8F-E904-428B-BE98-B04E14D43479}
WOOD 0401CB | {1F25C3BD-C09D-4433-9558-CEA0BEA55FCC}
WOOD 0401CB | {F6FBF5EF-0F39-43BE-9573-8D14EE89543A}
WOOD 0401CB | {8F0A48D9-A322-4FA2-98F5-9BA99B0B225E}
WOODACRE 11011456 | {1ACD7F45-5073-4366-9697-A511E06B0768}
WOODACRE 1101404 | {9E6A6B97-69AF-4332-A126-23324C3DC522}
WOODACRE 110191900 | {E06395F6-DD21-46DD-ADD6-944DE9391F88}
WOODACRE 110191900 | {315B41A4-2763-4241-B96A-998B94A74075}
WOODACRE 110196844 | {829ACA47-635E-4880-92A0-8C929EC179A6}
WOODACRE 1101CB | {0C1EAF38-D291-4410-BD5A-7EDE35C497EC}
WOODACRE 11021280 | {ED174F92-41BA-4C7D-B7B6-A8F138C95BC3}
WOODACRE 1102137662 | {C3672683-8002-442C-8DD0-CA97E76D56C3}
WOODACRE 1102137662 | {F012BA5A-7B46-481B-AEC2-676335F74B39}
WOODACRE 11022387 | {13C233D7-9C8E-4920-B738-858245F99E0C}
WOODACRE 1102372168 | {9F757E42-86CB-44B3-9904-4A09B4006B81}
WOODACRE 1102851 | {61FE98E8-80EF-4BDB-989C-5A04CDB81F15}
WOODACRE 1102CB | {61FE98E8-80EF-4BDB-989C-5A04CDB81F15}
WOODSIDE 1101210272 | {A320B6CE-3722-4188-814B-DF3FC009437C}
WOODSIDE 1101210272 | {2C96F5E7-EFFA-439D-98B4-19B9F97DA294}
WOODSIDE 11012299 | {0C4874FF-D222-478C-B9D7-BED0F08FA35C}
WOODSIDE 110147872 | {3F2B4E81-3F76-4F92-B31C-17D1A0284314}
WOODSIDE 1101509438 | {AE7048D1-B6D6-4F66-8C2D-AEADECFC750D}
WOODSIDE 1101509438 | {DD629E4A-2008-4D06-86C3-F17FC5F5EC00}
WOODSIDE 110171768 | {F24BE38E-053B-419A-9307-26152E3F26F4}
WOODSIDE 110176194 | {D1B97B5C-C0C0-4C1A-A0E9-54FF1BD58307}
WOODSIDE 110179892 | {B37068EA-10E5-4EBE-BB13-FA7A8D9F573E}
WOODSIDE 11018522 | {0C4874FF-D222-478C-B9D7-BED0F08FA35C}
WOODSIDE 11018884 | {186E48AF-259D-47A2-9F95-CEE4ED2E744B}
WOODSIDE 11018884 | {E37F33F6-1C0A-4C76-AC62-7F0B65A2F196}
WOODSIDE 11018912 | {429461DA-3754-40D0-8283-6B07C0ED0208}
WOODSIDE 11018972 | {31C2E01B-7B87-407B-9DC8-52C242320576}
WOODSIDE 11018974 | {95843233-31DE-4B8A-A7FD-7E8E48EA1CD1}
WOODSIDE 1101CB | {74C9689B-27E2-45AE-B69F-F01C8E2CB358}
WOODSIDE 1102215176 | {8F5867B0-6A5C-404F-9C5E-1A6497606D84}
WOODSIDE 110239574 | {BF6AF21E-B6B4-453B-837A-E823913B38FF}
WOODSIDE 1102472928 | {DEE5BC84-14D0-4B16-967C-4B20A0B07E86}
WOODSIDE 1102555372 | {73C37461-BB3B-432F-BC96-82FA7CA2E859}
WOODSIDE 1102840856 | {4E2033A2-5AAF-48B0-9734-692F3716AA51}
WOODSIDE 11028862 | {4C49C25B-7AC8-408B-8A99-E4CB51688164}
WOODSIDE 11029046 | {C11916FA-6FAD-4311-9B4B-F7146CB311CB}
WOODSIDE 11029134 | {6CA5F052-F51C-4718-B95C-B6EA83132FE8}
WOODSIDE 1102CB | {1A7707ED-44BC-402D-AC12-5D698199529B}
WOODSIDE 11042337 | {10950626-E142-4C01-A7D6-AB7791C4D86E}
WOODSIDE 11043583 | {667BD340-2F0C-44FC-9DF0-112C78D0C5E3}
WOODSIDE 1104420146 | {39508B32-B583-4F3B-8AB5-C8A9DFC4FCD3}
WOODSIDE 110444222 | {667BD340-2F0C-44FC-9DF0-112C78D0C5E3}
WOODSIDE 1104456052 | {B5C1CCF7-3737-412C-9D78-BAC61B5ECBAC}
WOODSIDE 1104520832 | {2CDC70D4-A195-46DD-838C-5A22FD1041DB}
WOODSIDE 11049032 | {10950626-E142-4C01-A7D6-AB7791C4D86E}
WOODSIDE 11049116 | {37A21F97-AEE6-4520-B851-056330FD3EDF}
WOODSIDE 1104931904 | {ABDE444A-2BE8-4532-B3C2-F916DD3C67D7}
WOODSIDE 1104CB | {C0699A77-D9F1-4326-8400-EC5E43167E10}
WOODSIDE 110551262 | {26A9FAEC-8CF7-4F97-B931-A8825176EECC}
WOODSIDE 11059160 | {096B2FA2-EAB3-4D1A-B901-D527C1E71A4D}
WOODSIDE 1105CB | {B0B93653-ABAA-40D2-863C-C601369FC194}
WOODWARD 210192860 | {CF17BBEC-B42C-4B87-B43B-51811F485652}
WOODWARD 2101CB | {CF17BBEC-B42C-4B87-B43B-51811F485652}
WOODWARD 2101R1210 | {CF17BBEC-B42C-4B87-B43B-51811F485652}
WOODWARD 2101R1220 | {CF17BBEC-B42C-4B87-B43B-51811F485652}
WOODWARD 2107850960 | {78848184-5B8B-4162-9179-CD46675AB16A}
WOODWARD 2107CB | {F7CD3382-D3E1-4D13-A56C-A6191C22A69C}
WOODWARD 2108441553 | {DFA037CB-555B-4A08-AEBD-309552344CE5}
WOODWARD 21085060 | {8476058D-CCFA-425A-8D9D-8591EF3E3149}
WOODWARD 21085591 | {78B7A12E-23D3-400C-8E4C-8FFD1AF5C8A2}
WOODWARD 2108703608 | {8314795F-0D04-45BD-AE69-B7277494B0E9}
WOODWARD 210878448 | {54379B90-C0BC-4B7C-8E22-0C10DD6F3A72}
WOODWARD 210892960 | {8476058D-CCFA-425A-8D9D-8591EF3E3149}
WOODWARD 2108935396 | {54379B90-C0BC-4B7C-8E22-0C10DD6F3A72}
WOODWARD 2108979850 | {61F2ACD6-570E-4D22-AC3A-276FF7469BBF}
WOODWARD 2108CB | {8314795F-0D04-45BD-AE69-B7277494B0E9}
WOODWARD 2108CUS1164 | {61F2ACD6-570E-4D22-AC3A-276FF7469BBF}
WOODWARD 2108CUS5875 | {41DA8C6A-A66B-4741-8630-05B8383240D3}
WOODWARD 2108R2860 | {41DA8C6A-A66B-4741-8630-05B8383240D3}
WOODWARD 2108R867 | {EF729FAE-1FE3-49C9-BDE2-A77C80F041B6}
WRIGHT 111011942 | {034E37ED-5306-407C-A605-FC7D5A32C1EE}
WRIGHT 1110262244 | {034E37ED-5306-407C-A605-FC7D5A32C1EE}
WRIGHT 1110288242 | {034E37ED-5306-407C-A605-FC7D5A32C1EE}
WRIGHT 11103220 | {B0D331FB-073A-4004-8987-5A047180EE74}
WRIGHT 11103800 | {AD751D3C-E21D-4C2B-848E-120233376733}
WRIGHT 1110756056 | {034E37ED-5306-407C-A605-FC7D5A32C1EE}
WRIGHT 111084280 | {339E2C7E-2DBD-42B5-BF29-414F5F6E8F92}
WRIGHT 1110869016 | {034E37ED-5306-407C-A605-FC7D5A32C1EE}
WRIGHT 1110888088 | {2FE3EF13-67AC-48D9-BB80-8C1E4F784A4A}
WRIGHT 11109090 | {034E37ED-5306-407C-A605-FC7D5A32C1EE}
WRIGHT 1110CB | {ABB28193-DF6D-40B9-BA16-1713A8EF4B58}
WYANDOTTE 110213916 | {6520C128-A5D2-408B-801E-4626440008FB}
WYANDOTTE 1102521288 | {229CA9E0-C79B-4E62-A678-3151AF589B57}
WYANDOTTE 1102CB | {835C2D90-E2D1-4649-9C53-DD5E51FB29AE}
WYANDOTTE 110313018 | {FD9CCA92-C052-4A36-88EE-05418588C974}
WYANDOTTE 11031508 | {1F5D8008-7EA4-4278-A040-64AB0E7AD925}
WYANDOTTE 1103640652 | {59B1EFCE-EA13-4733-ADA9-7461CE4DCF90}
WYANDOTTE 110366146 | {44DEC261-543D-4709-894B-61B8ADC18491}
WYANDOTTE 1103716082 | {ED98A6D0-06D7-43E4-A03B-484FE67F86A6}
WYANDOTTE 1103CB | {729134BB-0DFA-4145-807F-650A6E064048}
WYANDOTTE 1105329930 | {C09D41C2-6107-4911-B847-897C1DB6C91E}
WYANDOTTE 1105601234 | {2426BD3B-3A69-4A04-A051-7581B14322B3}
WYANDOTTE 1105CB | {2426BD3B-3A69-4A04-A051-7581B14322B3}
WYANDOTTE 11061046 | {830E8D18-621D-4CC3-9150-C991F796F6A1}
WYANDOTTE 110613016 | {73895C48-E496-423A-BB9D-D8E6858BCD72}
WYANDOTTE 110613046 | {64FCD432-5001-4119-BCAF-E00A7100833A}
WYANDOTTE 11061512 | {29C2B584-F455-4FA3-B4A4-3F4E989317C3}
WYANDOTTE 1106304014 | {64FCD432-5001-4119-BCAF-E00A7100833A}
WYANDOTTE 110641650 | {87BD5616-A670-4B3C-B36B-8B72CB70DFA6}
WYANDOTTE 110697550 | {64FCD432-5001-4119-BCAF-E00A7100833A}
WYANDOTTE 1106CB | {29C2B584-F455-4FA3-B4A4-3F4E989317C3}
WYANDOTTE 11071026 | {F4C4052A-4712-4518-990B-FE0E43960860}
WYANDOTTE 11071510 | {66E54FBC-1250-4CE5-89C7-25C58E4AEAFF}
WYANDOTTE 11071510 | {B12A6A50-9D07-4B81-92A6-6C7B62B046E1}
WYANDOTTE 11071510 | {B35C88CD-B2A5-4084-BA79-7F68510417CA}
WYANDOTTE 11071510 | {DE25CE3D-1135-419F-B68E-CEAA7D225690}
WYANDOTTE 1107165010 | {4A43564A-AF0D-48C1-9373-69C578381EFF}
WYANDOTTE 1107219854 | {0E127264-C3E4-4550-BC79-8854D7BB9B29}
WYANDOTTE 110737472 | {B3E100DA-AA63-42D1-94E1-A7F9E0DF29D9}
WYANDOTTE 110738438 | {112CEC5D-7594-450C-A06E-88C65F1E5892}
WYANDOTTE 110738438 | {A9B54913-4AA0-4D92-944E-0BB105A09A6C}
WYANDOTTE 110738438 | {3C055996-4533-470E-B9D4-C8A385908A5F}
WYANDOTTE 11075549 | {514F6992-142D-4643-AADC-8278CDD246B8}
WYANDOTTE 110777578 | {E0470028-6FEE-4E7A-BA03-DFBD06B93819}
WYANDOTTE 1107805958 | {5BFA77A3-EFF0-4693-89D5-42ACEC913789}
WYANDOTTE 1107829470 | {112CEC5D-7594-450C-A06E-88C65F1E5892}
WYANDOTTE 1107829470 | {078CC006-3CA8-4368-A64F-B4DBD02526AB}
WYANDOTTE 110796390 | {B74488FF-9B39-410B-9AAC-30106EC9509F}
WYANDOTTE 1107CB | {C8520005-9EA7-4C87-B336-C3E6B2DAE20B}
WYANDOTTE 1107CB | {0E127264-C3E4-4550-BC79-8854D7BB9B29}
WYANDOTTE 1107CB | {BDA7E326-12C4-4DD0-876F-746C4DA51193}
WYANDOTTE 11091040 | {10790C99-0AC4-4885-95AD-50DB99DD62BD}
WYANDOTTE 110913052 | {790FA841-FFAA-4636-AEC1-FF360B754DBB}
WYANDOTTE 1109170732 | {EEE67C1F-6C23-4D81-9B06-45B190348549}
WYANDOTTE 110931758 | {4018E6B5-9FD7-42B6-984E-3899183793C0}
WYANDOTTE 110940608 | {203DA6C6-E1D8-4D44-919F-A0D6E1325E80}
WYANDOTTE 11095575 | {203DA6C6-E1D8-4D44-919F-A0D6E1325E80}
WYANDOTTE 11095607 | {790FA841-FFAA-4636-AEC1-FF360B754DBB}
WYANDOTTE 11095973 | {10790C99-0AC4-4885-95AD-50DB99DD62BD}
WYANDOTTE 1109702710 | {EEE67C1F-6C23-4D81-9B06-45B190348549}
WYANDOTTE 1109758802 | {EC08C284-9906-406B-94E5-ADD7510D64ED}
WYANDOTTE 1109759354 | {4C66E0D5-78ED-42EB-9F37-6A9ACA5BD894}
WYANDOTTE 110979932 | {67B8C4D8-FEA1-4243-99E7-B5C8BD7D2FA9}
WYANDOTTE 1109CB | {A372AD67-1459-47B8-8964-55AFC8B0D599}
WYANDOTTE 11101952 | {07294D9F-EAF7-4C29-990A-7734F4A30766}
WYANDOTTE 11101952 | {71D65F92-7967-4876-9BA1-F0A855497989}
WYANDOTTE 11101954 | {652E0C25-B4E5-4F56-A678-A27ED9716769}
WYANDOTTE 11102590 | {EF5D8957-32CC-44F0-808E-217DC0A13E35}
WYANDOTTE 1110747922 | {C2FFAB6E-BB47-4E4C-9C7B-280A4F919308}
WYANDOTTE 1110873858 | {B9243DFE-989F-4BFE-A52A-70EF1DB7EE8E}
WYANDOTTE 1110CB | {B4858E1E-C2DC-43E7-A857-62EE09547E47}
ZACA 1101607054 | {562FB887-6919-47D3-9581-26BA249C579B}
ZACA 1101CB | {84844AA6-33FE-4B77-BE7F-2142383F94DA}
ZACA 1101Y70 | {C56ADC1A-9E36-443A-A4AD-EABCB05C5CD5}
ZACA 1101Y72 | {1D20AD79-1B20-4BDE-B0E8-CF4AA41EFB2A}
ZACA 1102109268 | {E675E4FE-1E8A-4C73-86ED-E17505ED6453}
ZACA 1102263406 | {EF11E3FD-D55F-4A7F-9C68-59132EE034F4}
ZACA 1102304952 | {700ACDDC-5CC8-42C5-8C56-C21FBEF21FC1}
ZACA 110255088 | {B69E8608-A146-4FB0-86EC-4193D08AC0C6}
ZACA 1102624984 | {3DDC2AA6-8302-4417-BAD5-9DBB0988C6D4}
ZACA 1102CB | {06AE963E-8682-491C-931E-D311BC02A28D}
ZACA 1102Y02 | {615A0700-A424-4825-ACAC-C9AB34833626}
ZACA 1102Y48 | {F0EEEA2A-131A-4CF1-A8F9-FEBD7A9B0FAB}
ZACA 1102Y54 | {49C145C8-C8F5-459A-817E-3F37A5597C7A}

## YTD EPSS Ignition Data
fixed_index_no | OIS_Numbers | ignition_start_create_timestamp (First reported) | dev_plbk_instruction | epss_circuit_opnum | circuit | circuit_protection_zone | fire_size | Response Time (PG&E)
20250495 | 2775657, 2775627, 2775629 | 2025-05-05 09:48 | FTS | 043141102-CB | MIDDLETOWN 1102 | MIDDLETOWN 1102CB | 0.26-9.99 | 35.65
20250650 | 2794610, 2794611 | 2025-05-28 12:13 | N/A | 153652105-11857 | SHINGLE SPRINGS 2105 | SHINGLE SPRINGS 210511857 | 1 meter - <3 meters | 21
20250750 | 2807968, TR9524062, 2808107 | 2025-06-13 08:46 | FTS | 043361104-CB | HIGHLANDS 1104 | HIGHLANDS 1104CB | 3 meters - 0.25 Acres | 9.2
20250797 | 2811937 | 2025-06-18 14:07 | FTS | 102361101-2046 | HAMILTON BRANCH 1101 | HAMILTON BRANCH 11012046 | 1 meter - <3 meters | 10
20250826N | 2815463 | 2025-06-21 19:22 | FTS | 103031102-2236 | ORO FINO 1102 | ORO FINO 11022236 | 3 meters - 0.25 Acres | 29.55
20250840 | 2816964 | 2025-06-23 16:18 | FTS | 254151101-R314 | AUBERRY 1101 | AUBERRY 1101R314 | 3 meters - 0.25 Acres | 24.03
2025_174000049605080 | 2826270 | 2025-07-03 17:11 | FTS | 252941107-822606 | TIVY VALLEY 1107 | TIVY VALLEY 1107822606 | 10-99 | 23.93
2025_174000049778669 | 2839165 | 2025-07-20 17:37 | N/A | 192171103-7514 | WILLOW CREEK 1103 | WILLOW CREEK 11037514 | 0.26-9.99 | 24
2025_174000049872779 | 2845739 | 2025-07-28 13:22 | FTS | 163751102-1222 | PINE GROVE 1102 | PINE GROVE 11021222 | 3 meters - 0.25 Acres | 35.27
2025_174000049893420 | 2846919 | 2025-07-30 04:09 | FTS | 042601101-3700 | PHILO 1101 | PHILO 11013700 | 3 meters - 0.25 Acres | 57.63
2025_174000049939324 | 2849689 | 2025-08-02 11:42 | FTS | 183052110-317796 | TEMPLETON 2110 | TEMPLETON 2110317796 | 0.26-9.99 | 43.2
2025_174000049942372 | 2850129 | 2025-08-03 10:24 | FTS | 182631107-CB | SAN LUIS OBISPO 1107 | SAN LUIS OBISPO 1107CB | 0.26-9.99 | 21
2025_174000050016236 | 2855385 | 2025-08-08 22:56 | FTS | 043051101-WIRE DOWN 8 SP SSD 1921 | MONTICELLO 1101 | MONTICELLO 11011708 | 0.26-9.99 | 34.7833
2025_174000050103170 | 2861653 | 2025-08-16 11:15 | FTS | 192171103-7169 | WILLOW CREEK 1103 | WILLOW CREEK 11032936 | 3 meters - 0.25 Acres | 65
2025_174000050307625 | 14600 | 2025-09-03 19:06 | FTS | 103541105-494814 | RED BLUFF 1105 | RED BLUFF 1105494814 | 0.26-9.99 | 49.3167
2025_174000050394689 | 22209 | 2025-09-11 00:44 | FTS | 254151102-CB | AUBERRY 1102 | AUBERRY 1102CB | 0.26-9.99 | 9.65
2025_174000050493305 | TR234136 | 2025-09-19 08:39 | FTS | 153662102-836878 | APPLE HILL 2102 | APPLE HILL 2102836878 | 3 meters - 0.25 Acres | 28.38
2025_174000050503294N | 31067, 31074 | 2025-09-20 11:25 | FTS | 103721101-CB | PIT NO 1 1101 | PIT NO 1 1101CB | 3 meters - 0.25 Acres | 0.66667