## Sheet1
Utility Name | Notified of Incident | County Name | Incident City | Incident Date | Cause of Incident | Facility Damage | Material Damaged | Damaged Caused By | Pipe Diameter | MAOP of Operator | Operating Pressure | Gas Leak | Operator Caused Fire | Non-Operator Caused Fire | Natural Gas Explosion | Injured Employees | Non-Employees Injured | Non-Employees Injured NA | Employee Fatalities | Non-Employee Fatalities | Non-Employee Fatalities NA | Cost Damage | Cost Damage NA | Customers Effected | Customers Effected NA | Damage Party Name | Damage Party City | Damage Party State | Damage Party Work Operator | Damage Done To SUOF | Underground Service Alert | Valid USA Ticket | Property Mark Facility | Properly Timely Mark Facility | Standby Provided | Delineations Found | Struck Within Delineations | Summary
Pacific Gas and Electric | N | ALAMEDA | ALAMEDA | 2020-11-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 15 | 12 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1828 |  | 1 |  | PIPE SPY | OAKLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | ALAMEDA | 2020-04-29 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | BENJAMIN FRANKLIN PLUMBING | SAN RAFAEL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavated prior to legal excavation start date and time
Pacific Gas and Electric | N | ALAMEDA | ALAMEDA | 2020-09-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 0.5 | 0.38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1450 |  | 1 |  | HOMEOWNER | ALAMEDA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | ALAMEDA | 2020-06-11 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 3 | 0.5 | 0.38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2474 |  | 0 |  | WESTLAND CONTRACTORS INC. | OAKLAND | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | ALAMEDA | 2020-10-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3121 |  | 1 |  | HOMEOWNER | ALAMEDA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | ALAMEDA | 2020-12-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2511 |  | 1 |  | HOMEOWNER | ALAMEDA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | ALAMEDA | 2020-09-09 | Operator excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 2 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2541 |  | 0 |  | MILLER PIPELINE | INDIANAPOLIS | CA | Y | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | ALAMEDA | 2020-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1766 |  | 1 |  | RANGER PIPELINES | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | ALAMEDA | 2020-10-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 146 |  | 1 |  | WESTLAND CONSTRUCTION INC | OAKLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | ALAMEDA | 2020-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1823 |  | 1 |  | FREMONT FENCE | NEWARK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | ALAMEDA | ALAMEDA | 2020-11-25 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | AMPCO NORTH INC. | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | ALAMEDA | 2020-11-25 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 40 |  | 3 |  | J.H. FITZMAURICE INC | OAKLAND | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | ALAMEDA | ALAMEDA | 2020-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 21 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1278 |  | 1 |  | RANGER PIPELINES | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | ALAMEDA | 2020-09-25 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3614 |  | 0 |  | MILLER PIPELINE | ALAMEDA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT INFORMATION OR MARKS
Pacific Gas and Electric | N | ALAMEDA | ALBANY | 2020-09-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 15 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1963 |  | 1216 |  | HOMEOWNER | ALBANY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | ALBANY | 2020-06-17 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 2 | 25 | 17 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3632 |  | 1 |  | HOMEOWNER | EL CERRITO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | ALBANY | 2020-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 17 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 664 |  | 0 |  | RANGER PIPELINE | SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2020-10-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HAHN GARDEN AND DESIGN | BERKELEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2020-08-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 813 |  | 0 |  | DAVID B. COLLINS BUILDER | RICHMOND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2020-03-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 598 |  | 0 |  | KEENE BUILDER | BERKELEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2020-06-03 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 980 |  | 0 |  | MILLER PIPELINE | BERKELEY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2020-06-16 | Operator excavation damage | Main | Polyethylene Pipe | Hand Tools | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1542 |  | 0 |  | MILLER PIPELINE | ALAMEDA | CA | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2020-06-15 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1428 |  | 0 |  | MILLER PIPELINE | ALAMEDA | CA | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2020-05-27 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4096 |  | 4 |  | MILLER PIPELINE | BERKELEY | CA | Y | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2020-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1451 |  | 1 |  | HOMEOWNER | BERKELEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2020-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 8803 |  | 1 |  | HOMEOWNER | BERKELEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2020-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2021 |  | 1 |  | HOMEOWNER | BERKELEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2020-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2586 |  | 0 |  | HOMEOWNER | BERKELEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2020-08-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 0.5 | 0.38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 712 |  | 0 |  | INDIAN ROCK LANDSCAPE | RICHMOND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2020-02-28 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1591 |  | 1 |  | MILLER PIPELINE | BERKLEY | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2020-02-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1301 |  | 0 |  | HOMEOWNER | BERKELEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2020-03-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 15 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 782 |  | 0 |  | DUVAL CONSTRUCTION | EL CERRITO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATED PRIOR TO LEGAL EXCAVATION START DATE AND TIME
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2020-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 0.43 | 0.33 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2302 |  | 1 |  | EAST BAY MUD | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2020-12-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 719 |  | 1 |  | WEST COAST ARBORISTS INC. | PINOLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2020-09-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 483 |  | 1 |  | RANGER PIPELINES | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2020-10-15 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MILLER PIPELINE | ALAMEDA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Inadequate Excavation Practices
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2020-05-29 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 1.25 | 25 | 19 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6658 |  | 0 |  | PONDERUS | SAN PABLO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2020-05-29 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 1.25 | 15 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | PONDEROSA TREE SERVICE | OAKLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavated outside delineated area
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2020-08-12 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 25 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 716 |  | 0 |  | MILLER PIPELINE | INDIANAPOLIS | CA | Y | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2020-06-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1431 |  | 1 |  | PRECISION ENGINEERING | BERKELEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2020-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1909 |  | 0 |  | PRECISION ENGINEERING | BERKELEY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2020-06-04 | Operator excavation damage | Main | Polyethylene Pipe | Hand Tools | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1839 |  | 0 |  | MILLER PIPELINE | BERKELEY | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2020-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1636 |  | 1 |  | PRECISION ENGINEERING | SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2020-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1138 |  | 1 |  | THE PLUMBING MINISTRY | SAN LEANDRO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2020-08-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 0.5 | 0.38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1108 |  | 0 |  | HOMEOWNER | BERKELEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2020-08-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 663 |  | 0 |  | STAR ROOTER PLUMBING | HAYWARD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2020-08-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 941 |  | 0 |  | DINARDO DESIGN AND CONSTRUCTION | BERKELEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2020-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1714 |  | 1 |  | HOMEOWNER | BERKELEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2020-06-25 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 234 |  | 0 |  | MILLER PIPELINE | ALAMEDA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2020-08-17 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1534 |  | 1 |  | MILLER PIPELINE | BERKELEY | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2020-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 15 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1401 |  | 1 |  | D''ARCY & HARTY | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2020-11-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Directional Drilling | 0.75 | 15 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2836 |  | 0 |  | EAST BAY MUD | OAKLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | ALAMEDA | CASTRO VALLEY | 2020-08-19 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1814 |  | 0 |  | RANGER PIPELINES | SAN FRANCISCO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | ALAMEDA | CASTRO VALLEY | 2020-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 50 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | STREAMLINE PLUMBING & DRAIN CO | RICHMOND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Dig with Care
Pacific Gas and Electric | N | ALAMEDA | CASTRO VALLEY | 2020-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1477 |  | 0 |  | PELLEGRINI CONSTRUCTION | SAN LEANDRO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | DUBLIN | 2020-10-27 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2023 |  | 0 |  | COLUMBIA ELECTRIC | SAN LEANDRO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | ALAMEDA | EMERYVILLE | 2020-04-30 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 54 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | THE PLUMBING MINISTRY | OAKLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Dig with Care
Pacific Gas and Electric | N | ALAMEDA | EMERYVILLE | 2020-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1453 |  | 1 |  | HOMEOWNER | EMERYVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | EMERYVILLE | 2020-08-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Directional Drilling | 1 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1311 |  | 1 |  | ARON AMBRUS CONSTRUCTION | BRENTWOOD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | FREMONT | 2020-03-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2365 |  | 0 |  | MOUNTAIN CASCADE | LIVERMORE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | FREMONT | 2020-11-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | HOMEOWNER | FREMONT | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | FREMONT | 2020-02-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3090 |  | 1 |  | PACIFIC PLUMBING | MILPITAS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | FREMONT | 2020-11-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1439 |  | 1 |  | NATIONAL CONSTRUCTION RENTALS | SAN LEANDRO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | FREMONT | 2020-01-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 654 |  | 1 |  | MIKE O''SHAUGHNESSY CONSTRUCTION | SAN FRANCISCO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORERCT INFORMATION/MARKS
Pacific Gas and Electric | N | ALAMEDA | FREMONT | 2020-07-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1413 |  | 1 |  | HOMEOWNER | FREMONT | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | FREMONT | 2020-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1254 |  | 0 |  | PT MASONORY | CAMPBELL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | FREMONT | 2020-11-13 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4307 |  | 0 |  | PRESTIGE UTILITY | SAN JOSE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | ALAMEDA | FREMONT | 2020-05-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5699 |  | 1 |  | HOMEOWNER | FREMONT | CA | N | Y | No | No | No | No | No | No | No | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | ALAMEDA | FREMONT | 2020-10-08 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | UNDERGROUND ELECTRIC CONSTRUCTION CO | BENICIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Inadequate Excavation Practices
Pacific Gas and Electric | N | ALAMEDA | FREMONT | 2020-08-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3397 |  | 2 |  | UNIQUE HOME DISIGNS | REDWOOD CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | ALAMEDA | FREMONT | 2020-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3348 |  | 1 |  | HOMEOWNER | FREMONT | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | FREMONT | 2020-07-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 1.25 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3335 |  | 0 |  | DUN RITE EXCAVATING INC | LIVERMORE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | FREMONT | 2020-10-05 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | BUTTERFIELD ELECTRIC INC | WOODLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | ALAMEDA | FREMONT | 2020-08-03 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7415 |  | 1 |  | POOL PROS | SAN JOSE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | HAYWARD | 2020-12-15 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 4 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 13712 |  | 0 |  | THE PLUMBING MINISTRY | SAN LEANDRO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | HAYWARD | 2020-08-11 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3116 |  | 0 |  | VALUE PLUMBING | OAKLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | HAYWARD | 2020-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 653 |  | 0 |  | MOUNTAIN CASCADE | LIVERMORE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | HAYWARD | 2020-09-28 | Third party excavation damage | Miscellaneous/Other | Steel | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10115 |  | 0 |  | DPI | LIVERMORE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT INFORMATION OR MARKS
Pacific Gas and Electric | N | ALAMEDA | HAYWARD | 2020-09-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 725 |  | 0 |  | AAA MECA CONSTRUCTION | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | HAYWARD | 2020-07-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1655 |  | 1 |  | ANDRE DEMO/HAULING | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | HAYWARD | 2020-09-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2492 |  | 0 |  | EVERGREEN LANDSCAPE SOLUTIONS | LODI | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | HAYWARD | 2020-11-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1488 |  | 0 |  | DIRT MOVERS | STOCKTON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | ALAMEDA | HAYWARD | 2020-03-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1710 |  | 0 |  | BOMBAY CONSTRUCTION | SUNNYVALE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | HAYWARD | 2020-10-03 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9124 |  | 1 |  | KK BUILDERS | HAYWARD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | ALAMEDA | HAYWARD | 2020-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1.25 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 0 |  | BERKLEY CEMENT INC | BERKELEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | HAYWARD | 2020-10-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1432 |  | 0 |  | GEORGE D. GARCIA INC | SAN JOSE | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | ALAMEDA | HAYWARD | 2020-11-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2457 |  | 0 |  | JANCO INDUSTRIES INC | TRACY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | LIVERMORE | 2020-05-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 865 |  | 1 |  | AAA BUILDERS | SAN LEANDRO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | LIVERMORE | 2020-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1027 |  | 1 |  | HOMEOWNER | LIVERMORE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | LIVERMORE | 2020-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 904 |  | 1 |  | BORG FENCE | LIVERMORE | CA | N | Y | Yes | Yes | Yes | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | LIVERMORE | 2020-03-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6150 |  | 1 |  | JALOS | HAYWARD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | LIVERMORE | 2020-04-27 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 0.75 | 55 | 49 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | WEST VALLEY CONSTRUCTION | CAMPBELL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Inadequate Excavation Practices
Pacific Gas and Electric | N | ALAMEDA | NEWARK | 2020-10-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | NEWARK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | NEWARK | 2020-06-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | ARMER NORMAN | SAN LEANDRO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment
Pacific Gas and Electric | N | ALAMEDA | NEWARK | 2020-11-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | FREMONT | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | NEWARK | 2020-07-29 | Third party excavation damage | Main | Polyethylene Pipe | Trencher | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3523 |  | 0 |  | KOMAC ELECTRIC | MARTINEZ | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | NEWARK | 2020-06-03 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2509 |  | 0 |  | RICH''S PAVING | LIVERMORE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | NEWARK | 2020-05-07 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6403 |  | 2 |  | ROTO ROOTER PLUMBING | LIVERMORE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1485 |  | 0 |  | AMERICAN EAGLE PLUMBING | OAKLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-07-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3802 |  | 1 |  | INDINGO HILLS LANDSCAPE | WALNUT GROVE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | EBMUD | OAKLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-04-30 | Third party excavation damage | Main | Steel | Augur | 2 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 410 |  | 0 |  | LARA''S CONCRETE INC | WALNUT CREEK | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-10-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-05-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 25 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3196 |  | 2 |  | AAA TREE SERVICE | HAYWARD | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-11-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 0.43 | 0.32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CONTRACTOR | NA |  | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9464 |  | 1 |  | AJW CONSTRUCTION | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-09-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 21 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1283 |  | 1 |  | ALBION PLUMBING AND ROOTER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-11-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 500 |  | 1 |  | ORIGINS ELECTRIC LLC | DULZURA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 21 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 362 |  | 2 |  | EAST BAY LANDSCAPING | SAN PABLO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-11-25 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3184 |  | 1 |  | EAST BAY MUD | OAKLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-03-02 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3824 |  | 4 |  | EBMUD | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | HOMEOWNER | OAKLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | No USA Ticket
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 0.5 | 0.38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3219 |  | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-05-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | WARRIORS PLUMBING | NA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-08-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 0.5 | 0.38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5118 |  | 1 |  | WARRIORS PLUMBING | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | EAST BAY MUD | OAKLAND | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-02-18 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7782 |  | 1 |  | THE PLUMBING MINISTRY | SAN LEANDRO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-06-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 0.5 | 0.38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1470 |  | 2 |  | RAY ELECTRIC | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 0.5 | 0.38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2317 |  | 1 |  | ANDES CONSTRUCTION | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-03-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1479 |  | 2 |  | PACIFIC TRENCHLESS | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-08-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1624 |  | 1 |  | JMV CONSTRUCTION | OAKLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT INFORMATION OR MARKS
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-09-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 302 |  | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 0.5 | 0.38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 159 |  | 2 |  | COLUMBIA ELECTRIC | SAN LEANDRO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2220 |  | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-08-20 | Third party excavation damage | Main | Polyethylene Pipe | Grader/Scraper | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2255 |  | 0 |  | GRIFFIN SOILS | SUNOL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1413 |  | 1 |  | COLUMBINE LANDSCAPING | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 25 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 360 |  | 1 |  | MIRANDA LANDSCAPING | SAN PABLO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-12-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2410 |  | 1 |  | TINKA CONSTRUCTION | MARTINEZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-03-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7548 |  | 0 |  | ER PLUMBING | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3357 |  | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-02-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 0.5 | 0.38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1537 |  | 1 |  | ANDES CONSTRUCTION | OAKLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-01-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2401 |  | 1 |  | MARTIN LUTHER WILLIAMS | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-03-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 25 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1426 |  | 1 |  | CITY OF OAKLAND | OAKLAND | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1862 |  | 1 |  | EBMUD | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 883 |  | 1 |  | SEWER CONNECTION INC | EL SOBRANTE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-10-12 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 25 | 17 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | EAST BAY MUD | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-05-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 25 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1396 |  | 1 |  | BWD GARDENS | RICHMOND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4069 |  | 2 |  | HARRY CLARK PLUMBING | OAKLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | NA | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | No USA Ticket
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-01-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1653 |  | 0 |  | Z&Z PLUMBING | OAKLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 25 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 483 |  | 2 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-12-03 | Third party excavation damage | Main | Steel | Hand Tools | 2 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 22634 |  | 2 |  | MILLER PIPELINE | ALAMEDA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-04-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1587 |  | 1 |  | A-Z CAPITAL CONSTRUCTION | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-08-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1236 |  | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-03-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3742 |  | 1 |  | EBMUD | OAKLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-10-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2256 |  | 1 |  | ROTO ROOTER | LIVERMORE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 904 |  | 2 |  | ALEJANDRO JIMENEZ ELECTRIC | VACAVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-01-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 500 |  | 1 |  | DECADE CONSTRUCTION | WALNUT CREEK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-11-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1444 |  | 2 |  | BEYOND BROADBAND SOLUTIONS | FORNEY | TX | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-09-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3193 |  | 2 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 3 |  | STAR ROOTER & PLUMBING | HAYWARD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-06-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | HOMEOWNER | OAKLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | No USA Ticket
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-12-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2279 |  | 0 |  | HOMEOWNER | OAKLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-07-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1335 |  | 0 |  | SM LANDSCAPING AND CONCRETE | SAN LORENZO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-11-05 | Third party excavation damage | Riser | Steel | Miscellaneous/Other | 0.75 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NA | NA | CA | N | Y | No | No | No | No | No | No | No | CONTRACTOR DAMAGED SERVICE VALVE
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-06-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1016 |  | 0 |  | J ARWIN CONSTRUCTION | VALLEJO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-03-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4102 |  | 2 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-04-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1121 |  | 4 |  | J&B FENCE | PACHECO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-06-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 17 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1676 |  | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-03-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1856 |  | 0 |  | HOMEOWNER | OAKLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-12-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2353 |  | 4 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2020-02-13 | Third party excavation damage | Main | Steel | Miscellaneous/Other | 16 | 60 | 54 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | COMCAST | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | No USA Ticket
Pacific Gas and Electric | N | ALAMEDA | PIEDMONT | 2020-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1321 |  | 1 |  | PARADIGM CONCRETE AND CONSTRUCTION | ANTIOCH | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | PIEDMONT | 2020-11-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | PIEDMONT | 2020-02-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1373 |  | 1 |  | LIAISON LANDSCAPE CONSTRUCTION | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | PIEDMONT | 2020-09-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1194 |  | 1 |  | HOMEOWNER | PIEDMONT | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | PLEASANTON | 2020-02-20 | Third party excavation damage | Transmission Line in an HCA area | Steel | Hand Tools | 8 | 55 | 49 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | BAY CITIES PAVING & GRADING | CONCORD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees
Pacific Gas and Electric | N | ALAMEDA | PLEASANTON | 2020-04-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1896 |  | 1 |  | ARON AMBRUS CONSTRUCTION | BRENTWOOD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | PLEASANTON | 2020-12-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 954 |  | 0 |  | MAXIMUM CONSTRUCTION INC | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | PLEASANTON | 2020-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1502 |  | 2 |  | M&G HAULING | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | SAN LEANDRO | 2020-09-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2144 |  | 1 |  | WARRIORS PLUMBING | OAKLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | SUNOL | 2020-10-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4 |  | 1 |  | INTERSTATE FENCE CO | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | ALAMEDA | UNION CITY | 2020-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2156 |  | 0 |  | HOMEOWNER | UNION CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | UNION CITY | 2020-05-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1114 |  | 1 |  | BEYOND BROAD BANDS | FORREY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | AMADOR | IONE | 2020-07-27 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4790 |  | 0 |  | MOZINGO CONSTR. | OAKDALE | CA | N | Y | No | No | No | No | No | No | No | INCORRECT INFORMATION OR MARKS
Pacific Gas and Electric | N | AMADOR | JACKSON | 2020-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1571 |  | 0 |  | HOMEOWNER | JACKSON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | AMADOR | JACKSON | 2020-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 116 |  | 0 |  | MCCUEN CONST. INC. | LOOMIS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | AMADOR | SUTTER CREEK | 2020-11-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1303 |  | 0 |  | HOMEOWNER | SUTTER CREEK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | BUTTE | CHICO | 2020-03-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 402 |  | 0 |  | NA | CHICO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | CHICO | 2020-10-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | THRIFTY ROOTER | CHICO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | BUTTE | CHICO | 2020-10-20 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 4 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | AERIAL ACES CONSTRUCTION | ORLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | CHICO | 2020-10-01 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6000 |  | 0 |  | DAVE''S BACKHOE SERVICE | MEADOW VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | BUTTE | CHICO | 2020-04-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | STEVE P RADOS INC | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | BUTTE | CHICO | 2020-11-06 | Third party excavation damage | Main | Polyethylene Pipe | Probing Device | 4 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | AERIAL ACES CONSTRUCTION | ORLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | CHICO | 2020-04-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2342 |  | 0 |  | HOMEOWNER | CHICO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | BUTTE | CHICO | 2020-12-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1396 |  | 0 |  | NEW ENGLAND LEAD BURNING COMPANY | BURLINGTON | MA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | CHICO | 2020-07-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2978 |  | 1 |  | JOR CONSTRUCTION | FOREST RANCH | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | BUTTE | CHICO | 2020-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 982 |  | 1 |  | M&M FENCING CO. INC. | CHICO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | BUTTE | CHICO | 2020-12-14 | Operator excavation damage | Main | Steel | Vacuum Equipment with no Agreement | 4 | 60 | 54 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MGE UNDERGROUND | PASO ROBLES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Inadequate Excavation Practices
Pacific Gas and Electric | N | BUTTE | CHICO | 2020-04-13 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2065 |  | 0 |  | JASON ABEL CONSTRUCTION | CORNING | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | BUTTE | DURHAM | 2020-10-30 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 220 |  | 0 |  | HOMEOWNER | DURHAM | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | BUTTE | DURHAM | 2020-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2000 |  | 0 |  | REM CONSTRUCTION DAN SCHELL | CHICO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | BUTTE | DURHAM | 2020-03-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 402 |  | 0 |  | HOMEOWNER | CHICO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | BUTTE | GRIDLEY | 2020-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 863 |  | 1 |  | HUNTER CONSTRUCTION | GRIDLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | BUTTE | GRIDLEY | 2020-10-16 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Farm Equipment | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 15937 |  | 0 |  | BB DEEP RIPPING AND EXCAVATING INC | GRIDLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | BUTTE | GRIDLEY | 2020-06-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | HOMEOWNER | GRIDLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | No USA Ticket
Pacific Gas and Electric | N | BUTTE | OROVILLE | 2020-08-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1348 |  | 1 |  | HOMEOWNER | OROVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | BUTTE | OROVILLE | 2020-04-17 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2102 |  | 0 |  | LEXIBGTON CONSTRUCTION | OROVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | BUTTE | PARADISE | 2020-12-03 | Operator excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 60 | 55 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CENTRAL VALLEY MECHANICAL | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Inadequate Excavation Practices
Pacific Gas and Electric | N | BUTTE | PARADISE | 2020-05-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 878 |  | 0 |  | QCI | SUTTER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | PARADISE | 2020-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3219 |  | 1 |  | ARB | BAKERSFIELD | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | BUTTE | PARADISE | 2020-07-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1086 |  | 0 |  | DUDLEYS EXCAVATION | GERBER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | PARADISE | 2020-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 895 |  | 2 |  | ARB | BAKERSFIELD | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | PARADISE | 2020-10-01 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6000 |  | 1 |  | ARB INC | PITTSBURG | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | PARADISE | 2020-10-10 | Operator excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 3 |  | VETERANS POWER INC. | BENECIA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | BUTTE | PARADISE | 2020-11-23 | Operator excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1238 |  | 0 |  | COX & COX CONSTRUCTION | REDDING | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | PARADISE | 2020-06-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 956 |  | 1 |  | CE CONSTRUCTION | CHICO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | BUTTE | PARADISE | 2020-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 60 | 56 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | HOMEOWNER | PARADISE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment
Pacific Gas and Electric | N | BUTTE | PARADISE | 2020-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 464 |  | 1 |  | K.W. EMERSON | SAN ANDREAS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | PARADISE | 2020-01-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Directional Drilling | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4651 |  | 0 |  | QUATTUOR CONSTRUCTION INC | SUTTER | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | BUTTE | PARADISE | 2020-11-12 | Operator excavation damage | Main | Steel | Backhoe/Trackhoe | 0.75 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1768 |  | 0 |  | VETERAN PIPELINE COMPANY (VPC) | BENICIA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CALAVERAS | SAN ANDREAS | 2020-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 98 |  | 1 |  | HOMEOWNER | SAN ANDREAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | COLUSA | WILLIAMS | 2020-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1278 |  | 0 |  | ORANGE CONTRACTORS | YUBA CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ALAMO | 2020-09-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | HOMEOWNER | ALAMO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ALAMO | 2020-08-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1077 |  | 1 |  | ALFREDO''S CONCRETE | HAYWARD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ALAMO | 2020-08-27 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6915 |  | 4 |  | ORMAN AND ASSOCIATES | DANVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | ALAMO | 2020-03-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1807 |  | 1 |  | ALL IN ONE REMOVAL DEMOLITION & RECYCLING | LAFAYETTE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | ALAMO | 2020-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 884 |  | 0 |  | THE PLUMBING MINISTRY | SAN LEANDRO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | ALAMO | 2020-11-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3104 |  | 1 |  | HOMEOWNER | ALAMO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ALAMO | 2020-10-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 4 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3719 |  | 0 |  | HOMEOWNER | ALAMO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | CONTRA COSTA | ALAMO | 2020-09-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1258 |  | 1 |  | HOMEOWNER | ALAMO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ALAMO | 2020-06-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1181 |  | 1 |  | WALTER''S BUILDERS INC | OAKLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | ANTIOCH | 2020-03-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 639 |  | 1 |  | GRANITE ROCK | CONCORD | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | ANTIOCH | 2020-10-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5 |  | 1 |  | HOMEOWNER | ANTIOCH | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ANTIOCH | 2020-08-05 | Third party excavation damage | Main | Polyethylene Pipe | Grader/Scraper | 1.25 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3377 |  | 1 |  | HENSLEY''S PAVING AND GENERAL | WATERFORD | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | ANTIOCH | 2020-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 56586 |  | 1 |  | CALIFORNIA TRENCHLESS | DUBLIN | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | CONTRA COSTA | ANTIOCH | 2020-12-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 959 |  | 1 |  | HOMEOWNER | ANTIOCH | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ANTIOCH | 2020-11-05 | Operator excavation damage | Main | Steel | Backhoe/Trackhoe | 20 | 58 | 52 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ARB INC | FAIRFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Inadequate Excavation Practices
Pacific Gas and Electric | N | CONTRA COSTA | ANTIOCH | 2020-10-06 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2292 |  | 2 |  | D.A. WOOD CONSTRUCTION INC | OAKDALE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | ANTIOCH | 2020-12-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 689 |  | 2 |  | CALIFORNIA TRENCHLESS | HAYWARD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | BAY POINT | 2020-08-20 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1195 |  | 32 |  | UNDERGROUND CONSTRUCTION | BENICA | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | BAY POINT | 2020-10-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2309 |  | 1 |  | HOMEOWNER | BAY POINT | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | BLACKHAWK | 2020-07-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1699 |  | 2 |  | HOMEOWNER | BLACKHAWK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | BYRON | 2020-04-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 1.25 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2351 |  | 0 |  | WILLIAMS CUSTOM VINEYARD MANAGEMENT | LODI | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | CLYDE | 2020-03-19 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Augur | 2 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 20299 |  | 1 |  | TIB''S EUROPEAN QUALITY CONSTRUCTION | CONCORD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | CONCORD | 2020-01-27 | Operator excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1632 |  | 0 |  | VULCAN CONSTRUCTION | SANTA CLARA | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | CONTRA COSTA | CONCORD | 2020-04-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | Y | N | 0 | 0 |  | 0 | 0 |  | 800 |  | 2 |  | HOMEOWNER | CONCORD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | CONCORD | 2020-10-16 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Vacuum Equipment with no Agreement | 0.75 | 60 | 54 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CONTRA COSTA WATER DISTRICT | CONCORD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | CONCORD | 2020-12-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 321 |  | 1 |  | HOMEOWNER | CONCORD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | CONCORD | 2020-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1187 |  | 1 |  | SOLAR UNION | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | CROCKETT | 2020-01-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 28 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2142 |  | 1 |  | ECAST ENGINEERING INC | OAKLAND | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | CONTRA COSTA | CROCKETT | 2020-09-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 27 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 924 |  | 0 |  | EBMUD | OAKLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | CONTRA COSTA | DANVILLE | 2020-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | NED CLYDE CONSTRUCTION | CONCORD | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | DANVILLE | 2020-08-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 993 |  | 1 |  | ARAGON COMMERCIAL LANDSCAPING | LIVERMORE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | DANVILLE | 2020-10-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1083 |  | 1 |  | CRATUS INC | SOUTH SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | DANVILLE | 2020-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 212 |  | 1 |  | NA | NA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | DANVILLE | 2020-01-22 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | PG&E | SAN FRANCISCO | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | Incorrect information or marks
Pacific Gas and Electric | N | CONTRA COSTA | DANVILLE | 2020-08-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1919 |  | 1 |  | CRATUS INC | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | DANVILLE | 2020-09-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1108 |  | 1 |  | CRATUS INC | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | DANVILLE | 2020-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | TEICHERT CONSTRUCTION | PLEASANTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | DANVILLE | 2020-02-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 655 |  | 1 |  | JJ&T CONCRETE | GILROY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | DANVILLE | 2020-02-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1471 |  | 1 |  | REUBEN BORG FENCE | SAN RAMON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | DANVILLE | 2020-12-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1342 |  | 1 |  | HOMEOWNER | DANVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | DANVILLE | 2020-09-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 845 |  | 0 |  | NA | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | DANVILLE | 2020-10-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1150 |  | 1 |  | SMITH & DENISON CONSTUCTION | LIVERMORE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | CONTRA COSTA | DIABLO | 2020-09-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2232 |  | 1 |  | CALIFORNIA HAULERS | EL CERRITO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | DIABLO | 2020-08-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 963 |  | 1 |  | CUSTOM GATE & ACCESS INC. | WEST SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | DIABLO | 2020-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 531 |  | 0 |  | HOMEOWNER | DIABLO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | DISCOVERY BAY | 2020-07-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2441 |  | 1 |  | GOLDEN OAKS CONSTRUCTION | DISCOVERY BAY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | EL CERRITO | 2020-03-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2121 |  | 1 |  | HOMEOWNER | EL CERRITO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | EL CERRITO | 2020-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1531 |  | 0 |  | HOME HEALING RENOVATIONS | BERKELEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | EL CERRITO | 2020-12-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1858 |  | 1 |  | HOMEOWNER | EL CERRITO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | EL SOBRANTE | 2020-12-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2692 |  | 1 |  | HOMEOWNER | EL SOBRANTE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | EL SOBRANTE | 2020-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2519 |  | 0 |  | HOMEOWNER | EL SOBRANTE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | EL SOBRANTE | 2020-06-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2092 |  | 1 |  | HOMEOWNER | EL SOBRANTE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | KENSINGTON | 2020-02-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1139 |  | 1 |  | FENCE AND GATE CRAFTERS | CONCORD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | KENSINGTON | 2020-01-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 658 |  | 0 |  | HOMEOWNER | KENGSINGTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | LAFAYETTE | 2020-12-04 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 926 |  | 1 |  | MILLER PIPELINE | ALAMEDA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | LAFAYETTE | 2020-10-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ADVANCED TRENCHLESS INC | MARTINEZ | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | LAFAYETTE | 2020-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 855 |  | 0 |  | TUTUILA LANDSCAPING & TREE SERVICE | FREMONT | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | LAFAYETTE | 2020-07-14 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 23012 |  | 1 |  | HOMEOWNER | LAFAYETTE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | LAFAYETTE | 2020-12-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4912 |  | 1 |  | HOMEOWNER | LAFAYETTE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | LAFAYETTE | 2020-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1829 |  | 1 |  | ALL ABOVE PLUMBING | NEWARK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | LAFAYETTE | 2020-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 725 |  | 2 |  | BETTER ROOTER | RICHMOND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | MARTINEZ | 2020-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 20016 |  | 2 |  | PACIFIC TRENCHLESS | OAKLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | MARTINEZ | 2020-04-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1083 |  | 8 |  | PREFERRED PLUMBING AND DRAIN | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | MARTINEZ | 2020-05-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 338 |  | 2 |  | HOMEOWNER | MARTINEZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | MARTINEZ | 2020-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 200 |  | 2 |  | VALENTINE CORPORATION | SAN RAFAEL | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | MARTINEZ | 2020-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1551 |  | 1 |  | BUSBY CONSTRUCTION | MARTINEZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | MARTINEZ | 2020-09-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | NA | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | MARTINEZ | 2020-04-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | MARTINEZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | MARTINEZ | 2020-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1144 |  | 1 |  | HOMEOWNER | MARTINEZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | OAKLEY | 2020-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1284 |  | 1 |  | HOMEOWNER | OAKLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | OAKLEY | 2020-08-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2529 |  | 2 |  | HOMEOWNER | OAKLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | OAKLEY | 2020-04-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1864 |  | 0 |  | HOMEOWNER | OAKLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | OAKLEY | 2020-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2580 |  | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | OAKLEY | 2020-11-13 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 4 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | KNIFE RIVER CONSTRUCTION | STOCKTON | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | ORINDA | 2020-02-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1350 |  | 1 |  | ALVAH CONTRACTORS | SOUTH SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INCORRECT INFORMATION OR MARKS
Pacific Gas and Electric | N | CONTRA COSTA | ORINDA | 2020-07-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2566 |  | 1 |  | HOMEOWNER | ORINDA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ORINDA | 2020-01-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1240 |  | 1 |  | HOMEOWNER | ORINDA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ORINDA | 2020-12-01 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 18068 |  | 1 |  | GILDOS GENERAL CONSTRUCTION | ANTIOCH | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ORINDA | 2020-03-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1251 |  | 0 |  | IBS USA | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ORINDA | 2020-02-27 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 2 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 38384 |  | 1 |  | HOMEOWNER | ORINDA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | CONTRA COSTA | ORINDA | 2020-02-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1923 |  | 0 |  | HOMEOWNER | ORINDA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ORINDA | 2020-10-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | ORINDA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ORINDA | 2020-12-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1204 |  | 0 |  | MARTINEZ CONSTRUCTION | BRENTWOOD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY COULD NOT BE FOUND OR LOCATED
Pacific Gas and Electric | N | CONTRA COSTA | ORINDA | 2020-04-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 200 |  | 1 |  | HOMEOWNER | ORINDA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ORINDA | 2020-01-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2072 |  | 0 |  | HOMEOWNER | ORINDA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | PINOLE | 2020-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1000 |  | 1 |  | HOMEOWNER | PINOLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | PITTSBURG | 2020-04-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | HOMEOWNER | PITTSBURG | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | PITTSBURG | 2020-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1502 |  | 1 |  | GOLD COAST PIPELINES | PITTSBURG | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | PITTSBURG | 2020-10-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 17 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 3 |  | BAY LINE CUTTING & CORING INC. | SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | PITTSBURG | 2020-07-08 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2150 |  | 1 |  | UNDERGROUND CONSTRUCTION | BENECIA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | PITTSBURG | 2020-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 2 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1000 |  | 0 |  | NA | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | PITTSBURG | 2020-12-17 | Third party excavation damage | Riser | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1229 |  | 0 |  | NA | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | PLEASANT HILL | 2020-11-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 866 |  | 1 |  | ADVANCED TRENCHLESS INC | MARTINEZ | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | PLEASANT HILL | 2020-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2128 |  | 1 |  | HOMEOWNER | PLEASANT HILL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | PLEASANT HILL | 2020-07-31 | Third party excavation damage | Main | Steel | Boring Equipment | 2 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 14876 |  | 0 |  | BORE ONE INC | GILROY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | CONTRA COSTA | PLEASANT HILL | 2020-08-20 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2518 |  | 0 |  | BENCHMARK CIIVIL CONSTRUCTION | NAPA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | PLEASANT HILL | 2020-07-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1809 |  | 1 |  | HOMEOWNER | PLEASANT HILL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2020-12-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | W.R. FORDE ASSOCIATES INC. | RICHMOND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2020-03-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3890 |  | 1 |  | W.R. FORDE | RICHMOND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2020-09-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 533 |  | 0 |  | EBMUD | OAKLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | LOCATING WIRE MISSING OR BROKEN
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2020-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3409 |  | 7 |  | HOMEOWNER | RICHMOND | CA | N | Y | No | No | No | No | No | No | No | USA NOTIFICATION ERROR
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2020-01-13 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | EBMUD | OAKLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2020-04-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2914 |  | 1 |  | PG&E | SAN FRANCISCO | CA | Y | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2020-12-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1437 |  | 1 |  | BAY PACIFIC PIPELINE | NOVATO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2020-03-26 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 3 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 11796 |  | 0 |  | STATEWIDE | RICHMOND | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2020-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | RICHMOND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2020-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Directional Drilling | 4 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 26428 |  | 1 |  | HOMEOWNER | RICHMOND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2020-07-30 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1.25 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 11575 |  | 1 |  | B N S F. RAILROAD | RICHMOND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2020-07-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1946 |  | 3 |  | BEYOND BROADBAND | GARLAND | TX | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2020-04-29 | Third party excavation damage | Riser | Steel | Miscellaneous/Other | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 307 |  | 0 |  | HOMEOWNER | RICHMOND | CA | N | N | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2020-01-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2615 |  | 1 |  | EBMUD | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2020-05-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1157 |  | 0 |  | HOMEOWNER | RICHMOND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2020-02-25 | Operator excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | PG&E | SAN FRANCISCO | CA | Y | Y | Yes | Yes | No | No | No | No | No | Facility was not located or marked
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2020-07-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 862 |  | 0 |  | HOMEOWNER | RICHMOND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2020-05-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 652 |  | 0 |  | HOMEOWNER | RICHMOND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2020-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 5 | 4 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2277 |  | 0 |  | KASTEN BUILDERS | RICHMOND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2020-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 25 | 17 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 45 |  | 1 |  | HOMEOWNER | RICHMOND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2020-01-30 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1322 |  | 0 |  | EBMUD | OAKLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | RODEO | 2020-11-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 883 |  | 0 |  | HOMEOWNER | RODEO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | SAN PABLO | 2020-08-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1335 |  | 1 |  | HOMEOWNER | SAN PABLO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | SAN PABLO | 2020-02-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3097 |  | 0 |  | PLATINUM PIPE LINE | LIVERMORE | CA | N | Y | Yes | Yes | Yes | Yes | No | No | No | Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible
Pacific Gas and Electric | N | CONTRA COSTA | SAN RAMON | 2020-04-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1292 |  | 1 |  | REPUBLIC TELECOM SERVICES | WYLIE | TX | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | SAN RAMON | 2020-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1844 |  | 1 |  | REPUBLIC TELECOM SERVICES, INC | SAN RAMON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | SAN RAMON | 2020-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2062 |  | 1 |  | GP CONSTRUCTION | ROSEVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | SAN RAMON | 2020-06-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1233 |  | 0 |  | A MUNOZ LANDSCAPING | MORGAN HILL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | SAN RAMON | 2020-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3483 |  | 1 |  | REUBEN BORG FENCE | SAN RAMON | CA | N | Y | No | No | No | No | No | No | No | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | CONTRA COSTA | SAN RAMON | 2020-08-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1715 |  | 1 |  | HOMEOWNER | SAN RAMON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | SAN RAMON | 2020-09-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1288 |  | 1 |  | TRIVALLEY FENCEWORKS | LIVERMORE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | SAN RAMON | 2020-06-17 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1.25 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 713 |  | 7 |  | JD PARTNERS CONCRETE | FREMONT | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | SAN RAMON | 2020-07-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5863 |  | 1 |  | HOMEOWNER | SAN RAMON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | CONTRA COSTA | SAN RAMON | 2020-04-21 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 4 | 55 | 49 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | MCH ELECTRIC | LIVERMORE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | No USA Ticket
Pacific Gas and Electric | N | CONTRA COSTA | VINE HILL | 2020-04-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1913 |  | 0 |  | JIM FREETHY EXCAVATING | DANVILLE | CA | N | Y | No | No | No | No | No | No | No | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2020-10-23 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | TIERRA GROUP | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2020-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1942 |  | 1 |  | EVERLAST CONSTRUCTION | WALNUT CREEK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2020-04-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1500 |  | 0 |  | ENVISION LANDSCAPED | WALNUT CREEK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2020-12-15 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3872 |  | 4 |  | PHASE 3 COMMUNICATIONS INC | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2020-04-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 153 |  | 1 |  | DR LEMINGS CONSTRUCTION | CONCORD | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2020-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 486 |  | 2 |  | ACE 1 ELECTRIC | RICHMOND | CA | N | Y | Yes | Yes | No | Yes | No | No | No | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2020-07-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1519 |  | 0 |  | BAY VALLEY CONTRACTORS | CONCORD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2020-07-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1644 |  | 1 |  | GN HENLEY | CLAYTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2020-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | BAY SIDE FENCING CO | ANTIOCH | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2020-09-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1522 |  | 1 |  | HOMEOWNER | WALNUT CREEK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2020-08-25 | Third party excavation damage | Riser | Steel | Miscellaneous/Other | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1321 |  | 1 |  | HOMEOWNER | WALNUT CREEK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2020-06-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1497 |  | 0 |  | JACK''S PATIO COMPANY | CONCORD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2020-08-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Probing Device | 1 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1617 |  | 1 |  | ADVANCED TRENCHLESS | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2020-06-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1094 |  | 2 |  | MORGAN''S FENCE & AWNING | CONCORD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2020-10-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | PRECISION ENGINEERING | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | EL DORADO | EL DORADO | 2020-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1278 |  | 0 |  | FOUR SEASONS POOL | EL DORADO HILLS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | EL DORADO | EL DORADO HILLS | 2020-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1626 |  | 1 |  | MP NEXT LEVEL | ELK GROVE | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | EL DORADO | EL DORADO HILLS | 2020-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | TOM SNELL CONSTRUCTION | RIO LINDA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | EL DORADO | EL DORADO HILLS | 2020-05-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1594 |  | 1 |  | BRIAN WILLIAMS CONCRETE | ELDORADO HILLS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | EL DORADO | EL DORADO HILLS | 2020-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1630 |  | 3 |  | SUNRISE LANSCAPE SERVICES | CITRUS HEIGHTS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | EL DORADO | EL DORADO HILLS | 2020-11-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | WESTERN WATER FEATURES | EL DORADO HILLS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | EL DORADO | EL DORADO HILLS | 2020-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1955 |  | 1 |  | HERNANDEZ FENCE | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | EL DORADO | EL DORADO HILLS | 2020-02-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1486 |  | 1 |  | CAL SIERRA SEALCOATING | PLACERVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | EL DORADO | EL DORADO HILLS | 2020-01-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3821 |  | 1 |  | HOMEOWNER | EL DORADO HILLS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | CLOVIS | 2020-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1756 |  | 0 |  | MMS ELECTRIC | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | CLOVIS | 2020-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1823 |  | 0 |  | ASHEE EXCAVATION | CLOVIS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | FRESNO | CLOVIS | 2020-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 0 |  | ASPHALT TECHNOLOGY | CLOVIS CA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | CLOVIS | 2020-05-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1179 |  | 0 |  | LANDSCAPE DEVELOPMENT | CLOVIS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | CLOVIS | 2020-05-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1873 |  | 0 |  | LASAR UNDERGROUND | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | FAILED TO DELINEATE JOBSITE
Pacific Gas and Electric | N | FRESNO | CLOVIS | 2020-01-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2250 |  | 0 |  | WEST TECH | CLOVIS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | FRESNO | CLOVIS | 2020-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 830 |  | 0 |  | BASE BUILDERS | SAN MATEO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | CLOVIS | 2020-06-04 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1859 |  | 3 |  | HOMEOWNER | CLOVIS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | CLOVIS | 2020-12-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2202 |  | 2 |  | HOMEOWNER | CLOVIS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | CLOVIS | 2020-11-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 639 |  | 2 |  | JTS TRENCHING | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | CLOVIS | 2020-01-08 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1629 |  | 0 |  | MAG ENGINEERING | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | CLOVIS | 2020-03-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 764 |  | 2 |  | DYNAMIC ELECT | CLOVIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FIREBAUGH | 2020-10-21 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 24 |  | 1 |  | AVISON CONST. | MADERA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FIREBAUGH | 2020-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 861 |  | 0 |  | JERRYS TRENCHING | FRESNO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | FRESNO | FOWLER | 2020-02-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1444 |  | 1 |  | HOMEOWNER | FOWLER | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-07-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 87 |  | 1 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-11-10 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Farm Equipment | 3 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7164 |  | 0 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 37 |  | 1 |  | HOMEOWNER | CLOVIS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-03-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1269 |  | 1 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-01-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | BROWNING CONTRACTORS | FRESNO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Incorrect facility records/maps
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-11-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1165 |  | 0 |  | LANDSCAPE CONNECTION | CLOVIS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1304 |  | 1 |  | SEBASTIAN CONSTRUCTION | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-06-26 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4812 |  | 0 |  | PG&E | SAN FRANCISCO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-09-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1325 |  | 2 |  | BRINER & SON LANDSCAPE | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-07-08 | Third party excavation damage | Main | Polyethylene Pipe | Probing Device | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2422 |  | 0 |  | CITY OF FRESNO | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-09-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1000 |  | 1 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-02-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1733 |  | 0 |  | BANKS AND CO | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-04-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1281 |  | 1 |  | WALTZ PLUMBING | CLOVIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-08-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2746 |  | 1 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2009 |  | 1 |  | CENTRAL VALLEY ASPHALT | LINDSEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-12-23 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 54 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CR ELECTRIC | NA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-06-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1651 |  | 1 |  | EMMETTS CONSTRUCTION | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-10-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 196 |  | 1 |  | LASAR UNDERGROUND CONSTRUCTION | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-06-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1656 |  | 1 |  | EMMETTS EXCAVATION | CLOVIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-04-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1394 |  | 1 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-05-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2083 |  | 0 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-12-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1299 |  | 1 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-10-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2965 |  | 2 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-03-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 523 |  | 1 |  | DAVE CHRISTIANSON CONST | FRESNO | CA | N | Y | No | No | No | No | No | No | No | EXCAVATED PRIOR TO LEGAL EXCAVATION START DATE AND TIME
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-05-15 | Third party excavation damage | Main | Polyethylene Pipe | Trencher | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1051 |  | 0 |  | TOUCH OF GREEN LANDSCAPING | CLOVIS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3833 |  | 1 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-01-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1944 |  | 0 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-04-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1671 |  | 1 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-07-06 | Third party excavation damage | Riser | Steel | Farm Equipment | 0.75 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 125 |  | 0 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-04-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 191 |  | 0 |  | LARRY SHAW AUTO | MADERA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-12-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1532 |  | 0 |  | MARC OF EXCELLENCE | WOODLAKE | CA | N | Y | Yes | Yes | No | Yes | No | No | No | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-08-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1349 |  | 2 |  | CITY OF FRESNO | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1745 |  | 0 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-05-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5129 |  | 0 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1154 |  | 0 |  | ASHPALT DESIGN | FRESNO | CA | N | Y | No | No | No | No | No | No | No | TICKET CLOSED IN ERROR
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-09-30 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2484 |  | 0 |  | HP COMMUNICATIONS | UNION CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-12-21 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4872 |  | 1 |  | COELLOS CONSTRUCTION | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-10-01 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 322 |  | 1 |  | CITY OF FRESNO | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3466 |  | 0 |  | CVIN VAST NETWORKS LLC | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 1.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1000 |  | 1 |  | CVIN VAST NETWORKS LLC | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-10-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 49 |  | 1 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-12-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5000 |  | 1 |  | WEST VALLEY CONSTRUCTION | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-03-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1100 |  | 1 |  | UNKNOWN HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-03-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1336 |  | 1 |  | ROBERT S MARKS PLUMBING | VISALIA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-01-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3984 |  | 9 |  | TIECHERT | FRESNO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | LOCATING WIRE MISSING OR BROKEN
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-02-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1137 |  | 1 |  | TEICHERT | SACRAMENTO | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | INCORRECT INFORMATION OR MARKS
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1469 |  | 2 |  | LASAR UNDERGROUND | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-05-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-03-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 904 |  | 0 |  | CROWN CONSTRUCTION | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-06-29 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2490 |  | 0 |  | VALVERDE CONSTRUCTION | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1527 |  | 2 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-04-08 | Operator excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Probing Device | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1339 |  | 2 |  | PG&E | FRESNO | CA | Y | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-10-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 24 |  | 1 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-08-26 | Operator excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 1.25 | 0.5 | 0.38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1291 |  | 0 |  | ARB | BAKERSFIELD | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 830 |  | 1 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-06-22 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 12 | 60 | 54 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | CITY OF FRESNO | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-12-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1000 |  | 1 |  | HOMEOWNER | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-06-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1372 |  | 0 |  | WESTECH SYSTEMS | CLOVIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2770 |  | 1 |  | LUSARDI CONSTRUCTION | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-03-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1802 |  | 1 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-07-20 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9912 |  | 48 |  | JOHNSON CONTROLS | FRESNO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1787 |  | 1 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-04-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2230 |  | 0 |  | WEST TECH SYSTEMS | CLOVIS | CA | N | Y | No | No | No | No | No | No | No | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-06-03 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2798 |  | 0 |  | BROWNING CONSTRUCTION | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO REQUEST REMARKS
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-08-14 | Third party excavation damage | Main | Polyethylene Pipe | Directional Drilling | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6050 |  | 0 |  | HP COMMUNICATION | CARONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-04-27 | Third party excavation damage | Main | Steel | Miscellaneous/Other | 6 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | VALVERDE CONSTRUCTION | SANTA FE SPRINGS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-03-31 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3539 |  | 0 |  | JERRYS TRENCHING | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment
Pacific Gas and Electric | N | FRESNO | FRESNO | 2020-01-04 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6172 |  | 0 |  | HENSON GENERAL ENGINERING | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | EXCAVATED OUTSIDE DELINEATED AREA
Pacific Gas and Electric | N | FRESNO | KERMAN | 2020-11-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1845 |  | 0 |  | JDI ELECTRICAL SOLUTIONS | PERRIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | KERMAN | 2020-12-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 1 | 53 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1000 |  | 0 |  | TIOGA LUMBER AND FENCING | SAN JUAN BAUTISTA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | KERMAN | 2020-12-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 53 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | TIOGA LUMBER AND FENCING | SAN JUAN BAUTISTA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | KERMAN | 2020-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 137 |  | 1 |  | MARKO CONSTRUCTION GROUP INC. | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | KERMAN | 2020-01-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3362 |  | 0 |  | HOMEOWNER | KERMAN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | MENDOTA | 2020-09-24 | Third party excavation damage | Main | Polyethylene Pipe | Trencher | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1706 |  | 0 |  | MADCO ELECTRIC | SELMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | MENDOTA | 2020-11-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1500 |  | 1 |  | MEDINA CONSTRUCTION ENGINEERS | CLOVIS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | SANGER | 2020-10-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 379 |  | 0 |  | MARK OF EXCELLENCE | WOODLAKE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | FRESNO | SANGER | 2020-08-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1404 |  | 1 |  | HOMEOWNER | SANGER | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | SANGER | 2020-03-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1022 |  | 0 |  | TRUE GREENSCAPES | TULARE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | SANGER | 2020-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1.25 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1229 |  | 5 |  | AGEE CONSTRUCTION | CLOVIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | SELMA | 2020-11-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3104 |  | 2 |  | HOMEOWNER | SELMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | SELMA | 2020-12-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2093 |  | 0 |  | HOMEOWNER | SELMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | SELMA | 2020-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1587 |  | 2 |  | HOMEOWNER | SELMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | GLENN | GLENN | 2020-10-12 | Third party excavation damage | Transmission Line in a non-HCA area | Steel | Backhoe/Trackhoe | 12 | 1300 | 800 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | HOMEOWNER | GLENN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | GLENN | ORLAND | 2020-06-25 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 48 | 40 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | APCO ETTNER INC | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | No USA Ticket
Pacific Gas and Electric | N | HUMBOLDT | BLUE LAKE | 2020-06-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1462 |  | 6 |  | KERNEN CONST | ARCATA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | HUMBOLDT | EUREKA | 2020-05-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2633 |  | 1 |  | HOMEOWNER | EUREKA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | HUMBOLDT | EUREKA | 2020-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9340 |  | 2 |  | SPENCER ELECTRIC | CUTTEN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | HUMBOLDT | EUREKA | 2020-10-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MAD RIVER PLUMBING | ARCATA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | HUMBOLDT | EUREKA | 2020-06-30 | Operator excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 45 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | SJL CONSTRUCTION | FORTUNA | CA | Y | Y | No | No | No | No | No | No | No | No USA Ticket
Pacific Gas and Electric | N | HUMBOLDT | EUREKA | 2020-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 2 | 0 |  | 3553 |  | 2 |  | HOMEOWNER | EUREKA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | HUMBOLDT | EUREKA | 2020-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 19 |  | 1 |  | STEVE SEPTIC | MCKINLEYVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | HUMBOLDT | EUREKA | 2020-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1703 |  | 1 |  | STEVE SEPTIC | MCKINLEYVILLE | CA | N | Y | No | No | No | No | No | No | No | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | HUMBOLDT | EUREKA | 2020-06-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1352 |  | 1 |  | HOMEOWNER | EUREKA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | HUMBOLDT | FORTUNA | 2020-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3958 |  | 2 |  | HOMEOWNER | FORTUNA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | HUMBOLDT | FORTUNA | 2020-08-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2479 |  | 1 |  | HOMEOWNER | FORTUNA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | HUMBOLDT | FORTUNA | 2020-05-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 51 |  | 0 |  | DANCO | ARCATA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | HUMBOLDT | FORTUNA | 2020-05-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3024 |  | 0 |  | DANCO | ARCATA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | HUMBOLDT | FORTUNA | 2020-06-11 | Third party excavation damage | Main | Steel | Miscellaneous/Other | 2 | 45 | 41 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | STEVE WILLS LOGGING | FORTUNA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | No USA Ticket
Pacific Gas and Electric | N | HUMBOLDT | MCKINLEYVILLE | 2020-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 171 |  | 2 |  | HOMEOWNER | MCKINLEYVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | HUMBOLDT | MCKINLEYVILLE | 2020-04-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | MCKINLEYVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | HUMBOLDT | PINE HILLS | 2020-04-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2203 |  | 1 |  | HOMEOWNER | EUREKA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | HUMBOLDT | PINE HILLS | 2020-04-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Farm Equipment | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1106 |  | 1 |  | HOMEOWNER | EUREKA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2020-12-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1559 |  | 1 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2020-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1927 |  | 0 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2020-05-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1434 |  | 0 |  | MARTIN CONSTRUCTION | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2020-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 0.5 | 0.38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2181 |  | 4 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2020-02-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 598 |  | 1 |  | RELIANCE FENCE CO. | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2020-01-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1283 |  | 4 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2020-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 51 | 47 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | SIERRA CONSTRUCTION AND EXCAVATION | BAKERSFIELD | CA | N | Y | No | No | No | Yes | No | Yes | Yes | Inadequate Excavation Practices
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2020-06-04 | Operator excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 58 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1714 |  | 1 |  | PG&E | BAKERSFIELD | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2020-12-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 726 |  | 1 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2020-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3111 |  | 1 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2020-11-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1712 |  | 5 |  | DRAIN PRO | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2020-12-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1283 |  | 1 |  | HOMEOWNER | TAFT | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2020-01-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | APT GENERAL ENGINEERING | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | No USA Ticket
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2020-07-27 | Operator excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1258 |  | 2 |  | PG&E | BAKERSFIELD | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | ABANDONED/DEACTIVATED FACILTY ISSUE
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2020-03-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 486 |  | 1 |  | BROADBAND | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2020-12-03 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3860 |  | 1 |  | BOWMAN ASPHALT | BAKERSFIELD | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2020-02-04 | Operator excavation damage | Main | Polyethylene Pipe | Probing Device | 2 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4821 |  | 8 |  | PG&E | BAKERSFIELD | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2020-10-26 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 51 | 47 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | BIG BOY PLUMBING | BAKERSFIELD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2020-10-27 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 4 | 51 | 47 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | GRIFFITH COMPANY | BREA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2020-07-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 669 |  | 1 |  | GOLDEN EMPIRE ELECTRIC | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2020-06-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 931 |  | 0 |  | RUBENS PIPELINE | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2020-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 53 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 148 |  | 1 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2020-04-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 25 |  | 0 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2020-01-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1074 |  | 1 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2020-12-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5000 |  | 0 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2020-10-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | DIVERSIFIED CONSTRUCTION SOLUTIONS | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2020-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1181 |  | 2 |  | LASAR UNDERGROUND | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2020-12-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 810 |  | 2 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2020-07-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 11035 |  | 47 |  | WEST VALLEY CONSTRUCTION | BAKERSFIELD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2020-03-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1310 |  | 0 |  | LANDSCAPE DEVELOPMENT INC | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2020-11-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1698 |  | 1 |  | RUBENS PIPELINE | BAKERSFIELD | CA | N | Y | Yes | No | No | No | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2020-10-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1081 |  | 1 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2020-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 956 |  | 2 |  | LASAR UNDERGROUND | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2020-03-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1659 |  | 1 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2020-12-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1057 |  | 2 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2020-10-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 24 |  | 8 |  | LASAR UNDERGROUND CONSTRUCTION | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2020-11-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1089 |  | 1 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2020-07-10 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 150 |  | 1 |  | HP COMMUNICATIONS | CORONA, CA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | KERN | BEAR VALLEY SPRINGS | 2020-07-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 186 |  | 1 |  | HOMEOWNER | BEAR VALLEY SPRINGS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | KERN | BEAR VALLEY SPRINGS | 2020-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1211 |  | 1 |  | HOMEOWNER | BEAR VALLEY SPRINGS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BEAR VALLEY SPRINGS | 2020-12-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2791 |  | 1 |  | WEST AND SONS CONSTRUCTION | ROSAMOND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | KERN | RIDGECREST | 2020-05-29 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6447 |  | 0 |  | SO CAL CONTRATORS | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | RIDGECREST | 2020-02-20 | Operator excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2322 |  | 0 |  | PG&E | BAKERSFIELD | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible
Pacific Gas and Electric | N | KERN | RIDGECREST | 2020-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1552 |  | 1 |  | HOMEOWNER | RIDGECREST | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | RIDGECREST | 2020-01-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7564 |  | 33 |  | SO CAL EDISON | HESPERIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment
Pacific Gas and Electric | N | KERN | TAFT | 2020-12-16 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 25 | 27 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3912 |  | 0 |  | WEST KERN WATER | TAFT | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | KERN | TEHACHAPI | 2020-11-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1970 |  | 1 |  | HOMEOWNER | TEHACHAPI | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KINGS | AVENAL | 2020-02-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2273 |  | 0 |  | HOMEOWNER | AVENAL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MADERA | CHOWCHILLA | 2020-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1500 |  | 0 |  | ALW ENTERPRISES | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MADERA | CHOWCHILLA | 2020-09-18 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 689 |  | 0 |  | LYLES UTILITY CONSTRUCTION | VISALIA | CA | Y | Y | Yes | Yes | Yes | Yes | Yes | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MADERA | MADERA | 2020-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1193 |  | 2 |  | HOMEOWNER | MADERA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MADERA | MADERA | 2020-11-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1349 |  | 0 |  | CENTRAL VALLEY LANDSCAPE | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MADERA | MADERA | 2020-12-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1835 |  | 1 |  | HOMEOWNER | MADERA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MADERA | MADERA | 2020-02-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2272 |  | 0 |  | LENNER HOMES | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MADERA | MADERA | 2020-05-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 0.75 | 60 | 54 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | NA | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Inadequate Excavation Practices
Pacific Gas and Electric | N | MADERA | MADERA | 2020-12-21 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1744 |  | 4 |  | BERRY DEVELOPMENT | MADERA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MADERA | MADERA | 2020-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 42 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 701 |  | 0 |  | WESTECH SYSTEMS | CLOVIS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MADERA | MADERA | 2020-05-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3102 |  | 1 |  | A&C FUNDING | VISALIA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MADERA | MADERA | 2020-04-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | JIM CRAWFORD CONSTRUCTION | CLOVIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible
Pacific Gas and Electric | N | MADERA | MADERA | 2020-11-30 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2000 |  | 0 |  | A-C ELECTRIC | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MADERA | MADERA | 2020-01-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3021 |  | 0 |  | BROWNING CONTR | FRESNO | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | MARIN | BELVEDERE | 2020-01-31 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | ARB | SAN FRANCISCO | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | Incorrect information or marks
Pacific Gas and Electric | N | MARIN | BELVEDERE | 2020-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3141 |  | 1 |  | BEYOND BASICS | DANVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | CORTE MADERA | 2020-11-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1046 |  | 1 |  | HOMEOWNER | CORTE MADERA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | CORTE MADERA | 2020-09-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1490 |  | 2 |  | DARCY & HARDY | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | CORTE MADERA | 2020-06-30 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 15 |  | 0 |  | GHILOTTI CONSTRUCTION | SAN RAFAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | CORTE MADERA | 2020-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5702 |  | 1 |  | GHILOTTI CONSTRUCTION | SANTA ROSA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | FACILITY ENCASED IN CONCRETE
Pacific Gas and Electric | N | MARIN | CORTE MADERA | 2020-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1945 |  | 1 |  | DARCY & HARDY | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | CORTE MADERA | 2020-05-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 474 |  | 0 |  | GREEN DIAZ CONSTRUCTION | RICHMOND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | CORTE MADERA | 2020-05-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2705 |  | 0 |  | HOMEOWNER | CORTE MADERA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | CORTE MADERA | 2020-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 913 |  | 1 |  | DARCY & HARDY | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | FAIRFAX | 2020-06-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2702 |  | 1 |  | BOESEL DESIGN & CONSTRUCTION | SAN ANSELMO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | FAIRFAX | 2020-06-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | HOMEOWNER | FAIRFAX | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | FAIRFAX | 2020-05-24 | Third party excavation damage | Main | Steel | Hand Tools | 2 | 57 | 51 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | HOMEOWNER | FAIRFAX | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | No USA Ticket
Pacific Gas and Electric | N | MARIN | FAIRFAX | 2020-03-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1024 |  | 0 |  | NELSON CONSTRUCTION | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | FAIRFAX | 2020-12-03 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2273 |  | 1 |  | ALVAH CONTRACTORS INC | SOUTH SAN FRANCISCO | CA | Y | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | FAIRFAX | 2020-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | FAIRFAX | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | FAIRFAX | 2020-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1795 |  | 1 |  | HOMEOWNER | FAIRFAX | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | FAIRFAX | 2020-08-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2228 |  | 1 |  | RMR CONSTRUCTION | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | KENTFIELD | 2020-09-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3448 |  | 1 |  | AC ENTERPRISE | HAYWARD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | KENTFIELD | 2020-05-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1069 |  | 0 |  | HOMEOWNER | KENTFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | KENTFIELD | 2020-03-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1047 |  | 0 |  | LEVINE DESIGN AND CONSTRUCTION | SAN ANSELMO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | KENTFIELD | 2020-04-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2106 |  | 0 |  | AM CONSTRUCTION | KENTFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | KENTFIELD | 2020-06-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1975 |  | 1 |  | TRENCHLESS TITAN | LARKSPUR | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | MARIN | KENTFIELD | 2020-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1890 |  | 1 |  | FLOYD CONSTRUCTION | SAN RAFAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | KENTFIELD | 2020-01-15 | Operator excavation damage | Main | Steel | Backhoe/Trackhoe | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7359 |  | 38 |  | PG&E | SAN FRANCISCO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | KENTFIELD | 2020-07-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2814 |  | 1 |  | MIKE BROWN ELECTRIC CO. | COTATI | CA | N | Y | Yes | Yes | No | Yes | No | No | No | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | MARIN | LARKSPUR | 2020-07-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ANELLO CONSTRUCTION | NOVATO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | LARKSPUR | 2020-12-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2369 |  | 1 |  | MICHAEL PAUL COMPANY | PETALUMA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | MARIN | LARKSPUR | 2020-11-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2374 |  | 0 |  | LINSCOTT ENGINEERING | SAN RAFAEL | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | LARKSPUR | 2020-12-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | UNLICENSED CONTRACTOR | NA |  | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | LARKSPUR | 2020-12-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2070 |  | 1 |  | SOLIS LANDSCAPE | HOLLISTER | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | LARKSPUR | 2020-09-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1137 |  | 1 |  | HOMEOWNER | LARKSPUR | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | LARKSPUR | 2020-10-23 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 15055 |  | 0 |  | RIVAS CONCRETE | SAN RAFAEL | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT INFORMATION OR MARKS
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2020-12-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1020 |  | 1 |  | HOMEOWNER | MILL VALLEY | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2020-08-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1300 |  | 1 |  | HOMEOWNER | MILL VALLEY | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2020-04-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1538 |  | 0 |  | K.J. WOODS CONSTRUCTION | SAN FRANCISCO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2020-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 782 |  | 1 |  | K.J. WOODS CONSTRUCTION | SAN FRANCISCO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2020-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1614 |  | 1 |  | JOHNSON ELECTRIC | SAN RAFAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2020-06-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3155 |  | 1 |  | HOMEOWNER | MILL VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2020-12-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3191 |  | 1 |  | HOMEOWNER | MILL VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2020-07-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3321 |  | 1 |  | E DIAZ CONCRETE | RICHMOND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2020-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1038 |  | 1 |  | SEWER TEK | PITTSBURG | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2020-06-07 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2297 |  | 1 |  | PG&E | SAN FRANCISCO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2020-05-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 650 |  | 0 |  | MARIN MUNICIPAL WATER DISTRICT | CORTE MADERA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2020-12-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1134 |  | 1 |  | VAN MIDDE & SON CONCRETE | SAN RAFAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2020-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2576 |  | 0 |  | PACIFIC INFRASTRUCTURE | PLEASANTON | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2020-08-06 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Trencher | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3570 |  | 0 |  | DANIELS GARDENING | ANTIOCH | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2020-08-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1621 |  | 0 |  | PLR BUILDERS | NOVATO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | NOVATO | 2020-09-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2309 |  | 1 |  | HOMEOWNER | NOVATO | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | NOVATO | 2020-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1220 |  | 1 |  | HOMEOWNER | NOVATO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | MARIN | NOVATO | 2020-10-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | NOVATO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | NOVATO | 2020-10-01 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 2 | 56 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3909 |  | 1 |  | MARTIN LANDSCAPING | RHONERT PARK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | MARIN | NOVATO | 2020-09-04 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1454 |  | 2 |  | STAGGS CONTRACTOR | SEBASTOPOL | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | NOVATO | 2020-09-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1779 |  | 1 |  | CONSTRUCTION SYSTEMS BUILDING AND DESIGN | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | ROSS | 2020-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1355 |  | 0 |  | CARROWZA GROUP | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | ROSS | 2020-11-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1989 |  | 1 |  | ROJAS PLUMBING | RICHMOND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | ROSS | 2020-09-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3043 |  | 1 |  | HOMEOWNER | ROSS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN ANSELMO | 2020-01-30 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Directional Drilling | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7814 |  | 1 |  | HARDIMAN CONSTUCTION | LARKSPUR | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | GAS LINE ENCASED IN CONCRETE
Pacific Gas and Electric | N | MARIN | SAN ANSELMO | 2020-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 351 |  | 1 |  | G FAMILY CONSTRUCTION | SAN RAFAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN ANSELMO | 2020-09-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 796 |  | 1 |  | HOMEOWNER | SAN ANSELMO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | SAN ANSELMO | 2020-10-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | LIBERTY EXCAVATION & DEMO | RICHMOND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN ANSELMO | 2020-02-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3301 |  | 1 |  | MONTEZ CONSTRUCTION | ORINDA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN ANSELMO | 2020-10-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CONCERUM OPERIS INC | RICHMOND | CA | N | Y | Yes | Yes | Yes | Yes | No | No | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | SAN ANSELMO | 2020-04-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5000 |  | 0 |  | HOMEOWNER | SAN ANSELMO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN ANSELMO | 2020-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3544 |  | 1 |  | MDC BUILDERS | PITTSBURGE | CA | N | Y | Yes | No | Yes | No | No | No | Yes | EXCAVATED OUTSIDE OF DELINEATED AREA
Pacific Gas and Electric | N | MARIN | SAN ANSELMO | 2020-03-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2008 |  | 0 |  | HOMEOWNER | SAN ANSELMO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN ANSELMO | 2020-06-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1101 |  | 1 |  | HOMEOWNER | SAN ANSELMO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2020-10-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | SAN RAFAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2020-09-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 785 |  | 1 |  | HOMEOWNER | SAN RAFAEL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2020-06-18 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1498 |  | 0 |  | VAN MIDDE & SON CONCRTE | SAN RAFAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2020-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1022 |  | 1 |  | SEQUOIA PROPERTY SERVICE | SAN LEANDRO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2020-02-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | Y | N | 0 | 0 |  | 0 | 0 |  | 1017 |  | 0 |  | GHILOTTI BROTHERS | SAN RAFAEL | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | USA EXPIRED
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2020-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1343 |  | 1 |  | HOMEOWNER | SAN RAFAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2020-02-24 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Augur | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | BENJAMIN FRANKLIN | NOVATO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY COULD NOT BE FOUND OR LOCATED
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2020-11-02 | Third party excavation damage | Main | Steel | Hand Tools | 2 | 57 | 51 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | HOMEOWNER | SAN RAFAEL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2020-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2998 |  | 0 |  | NORTH CAL RESTORATION | POINT REYES STATION | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2020-07-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1074 |  | 0 |  | HOMEOWNER | SAN RAFAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2020-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 283 |  | 1 |  | KEREX ENGINEERING | PLEASANT HILL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2020-07-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4093 |  | 1 |  | HOMEOWNER | SAN RAFAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAUSALITO | 2020-11-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 999 |  | 1 |  | STEEL ROOTS LANDSCAPING | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAUSALITO | 2020-07-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1502 |  | 0 |  | LIVE OAK BUILDING AND DESIGN | BERKELEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | SAUSALITO | 2020-07-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1999 |  | 0 |  | LIVE OAK BUILDING AND DESIGN | BERKELEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAUSALITO | 2020-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2198 |  | 2 |  | HOMEOWNER | SAUSALITO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAUSALITO | 2020-07-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1 |  | 2 |  | PMM CONSTRUCTION | MILL VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAUSALITO | 2020-11-19 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 6 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 144 |  | 1 |  | MAGGIORA & GHILOTTI | SAN RAFAEL | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | SAUSALITO | 2020-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1642 |  | 1 |  | MAGGIORA & GHILOTTI | SAN RAFAEL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | TIBURON | 2020-08-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1082 |  | 2 |  | SEWER CONNECTION | EL SOBRANTE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | TIBURON | 2020-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1453 |  | 1 |  | MALONEY CONSTRUCTION | NOVATO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | TIBURON | 2020-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1898 |  | 1 |  | MALONEY CONSTRUCTION | NOVATO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | TIBURON | 2020-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2056 |  | 1 |  | SEWER TEK | PITTSBURG | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | TIBURON | 2020-05-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1819 |  | 1 |  | HOMEOWNER | TIBURON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MENDOCINO | TALMAGE | 2020-07-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3587 |  | 2 |  | HOMEOWNER | UKIAH | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MENDOCINO | UKIAH | 2020-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ST FRANCIS ELECTRIC | SAN LEANDRO | CA | N | Y | Yes | No | Yes | Yes | Yes | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MENDOCINO | UKIAH | 2020-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2072 |  | 1 |  | HOMEOWNER | UKIAH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MENDOCINO | UKIAH | 2020-11-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 146 |  | 1 |  | HOMEOWNER | UKIAH | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MENDOCINO | UKIAH | 2020-05-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 25 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 177 |  | 13 |  | HOMEOWNER | UKIAH | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MENDOCINO | WILLITS | 2020-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1008 |  | 1 |  | HOMEOWNER | WILLITS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MENDOCINO | WILLITS | 2020-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | WILLITS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MENDOCINO | WILLITS | 2020-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | JOHNSON QUALITY TREE CARE | UKIAH | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MENDOCINO | WILLITS | 2020-11-02 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 48 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2821 |  | 0 |  | ARB INC | FAIRFIELD | CA | Y | Y | Yes | Yes | Yes | Yes | Yes | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MERCED | ATWATER | 2020-07-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1056 |  | 1 |  | HOMEOWNER | ATWATER | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MERCED | ATWATER | 2020-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 212 |  | 0 |  | BK WELDING | LOVELAND | CO | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MERCED | DELHI | 2020-02-28 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1444 |  | 0 |  | HOMEOWNER | DELHI | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MERCED | GUSTINE | 2020-12-31 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2000 |  | 0 |  | TAYLOR BACKHOE SERVICE | MERCED | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | MERCED | GUSTINE | 2020-08-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1221 |  | 2 |  | PSG FENCE | LOS BANOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MERCED | LIVINGSTON | 2020-01-15 | Third party excavation damage | Main | Steel | Not Available | 2 | 42 | 36 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | CITY OF LIVINGSTON | LIVINGSTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavated prior to legal excavation start date and time
Pacific Gas and Electric | N | MERCED | LIVINGSTON | 2020-01-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1970 |  | 1 |  | HOMEOWNER | LIVINGSTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MERCED | LOS BANOS | 2020-08-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1157 |  | 0 |  | CENTRAL VALLEY LAWN | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MERCED | LOS BANOS | 2020-01-24 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1500 |  | 0 |  | MCH ELECTRIC | LIVERMORE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MERCED | MERCED | 2020-01-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | CITY OF MERCED | MERCED | CA | N | Y | No | No | No | No | No | No | No | No USA Ticket
Pacific Gas and Electric | N | MERCED | MERCED | 2020-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 338 |  | 2 |  | HOMEOWNER | MERCED | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MERCED | MERCED | 2020-04-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 514 |  | 1 |  | HOMEOWNER | MERCED | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MERCED | MERCED | 2020-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1274 |  | 1 |  | LAWLER CONSTRUCTION | MERCED | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MERCED | MERCED | 2020-10-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2200 |  | 1 |  | BONNER ELECTRIC | MERCED | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MERCED | MERCED | 2020-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1617 |  | 2 |  | TAK COMMUNICATAIONS | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MERCED | MERCED | 2020-06-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 321 |  | 1 |  | HOMEOWNER | MERCED | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | AROMAS | 2020-05-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1189 |  | 1 |  | ARROYO LANDSCAPING | AROMAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | CARMEL | 2020-12-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1726 |  | 1 |  | HOMEOWNER | CARMEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | CARMEL | 2020-03-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 238 |  | 2 |  | MONTEREY PENNINSULA ENGINEERING | MARINA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | CARMEL | 2020-03-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1087 |  | 1 |  | TRUJILLO LANDSCAPING | SALINAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | CARMEL VALLEY | 2020-01-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 928 |  | 1 |  | ASTURI CONSTRUCTION | MODESTO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | MONTEREY | CARMEL VALLEY | 2020-02-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 971 |  | 1 |  | HOMEOWNER | CARMEL VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | CARMEL VALLEY | 2020-01-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1432 |  | 1 |  | HOMEOWNER | CARMEL VALLEY | CA | N | Y | No | No | No | No | No | No | No | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | MONTEREY | CARMEL VALLEY | 2020-06-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1.25 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | DANIEL CLARK CONSTRUCTION | SALINAS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | CARMEL VALLEY | 2020-05-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | HOMEOWNER | CARMEL VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | No USA Ticket
Pacific Gas and Electric | N | MONTEREY | CARMEL-BY-THE-SEA | 2020-07-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2000 |  | 1 |  | HOMEOWNER | DOS PALOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | CARMEL-BY-THE-SEA | 2020-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 637 |  | 1 |  | SANCHEZ LANDSCAPING CO | CARMEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | CARMEL-BY-THE-SEA | 2020-10-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | STOCKER & ALLAIRE GENERAL CONTRACTORS | MONTEREY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | KING CITY | 2020-10-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | JAMES SOMMERVILLE INC | SALINAS | CA | N | Y | Yes | Yes | Yes | Yes | Yes | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | MONTEREY | MARINA | 2020-04-15 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 15 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5959 |  | 0 |  | ALLIANCE RESIDENTIAL | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | MARINA | 2020-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 689 |  | 2 |  | L&D CONSTRUCTION | SAN JOSE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | MARINA | 2020-05-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1981 |  | 1 |  | HOMEOWNER | MARINA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | MONTEREY | 2020-09-29 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3681 |  | 6 |  | FMG (CLSB 796046) | WATSONVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | MONTEREY | 2020-12-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2000 |  | 1 |  | GOLD STONE MASONRY | SAND CITY | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | MONTEREY | 2020-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | LUNDMARK CONSTRUCTION | SARATOGA | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | MONTEREY | 2020-02-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4520 |  | 1 |  | HOMEOWNER | MONTEREY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | MONTEREY | 2020-07-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1439 |  | 1 |  | CLIFTON PLUMBING AND HEATING | MONTEREY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | MONTEREY | 2020-02-25 | Third party excavation damage | Main | Steel | Grader/Scraper | 2 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 13991 |  | 26 |  | GRIFFIN SOIL GROUP | STOCKTON | CA | Y | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | MONTEREY | 2020-06-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1710 |  | 1 |  | HOMEOWNER | MONTEREY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | MONTEREY | 2020-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MONTEREY PENNINSULA ENGINEERING | MARINA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | MONTEREY | 2020-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 614 |  | 0 |  | MONTEREY PENNINSULA ENGINEERING | MARINA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | MONTEREY | MOSS LANDING | 2020-12-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2836 |  | 1 |  | MOSS LANDING MARINE LAB | MOSS LANDING | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | PACIFIC GROVE | 2020-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 894 |  | 1 |  | MDH CONSTRUCTION | MONTEREY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | PACIFIC GROVE | 2020-12-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 29 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1368 |  | 0 |  | CAL AM | PACIFIC GROVE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | PACIFIC GROVE | 2020-12-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 29 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 463 |  | 1 |  | CLIFTON PLUMBING | MONTEREY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | PACIFIC GROVE | 2020-05-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 931 |  | 0 |  | GROZA CONSTRUCTION | MONTEREY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | PEBBLE BEACH | 2020-06-25 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1175 |  | 0 |  | ROCKSTAD POWER | ATASCADERO | CA | Y | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | PEBBLE BEACH | 2020-08-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1375 |  | 1 |  | HARRY WILLIAMS CONSTRUCTION | WATSONVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | PEBBLE BEACH | 2020-12-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2000 |  | 1 |  | MR ROOTER PLUMBING | SALINAS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | PEBBLE BEACH | 2020-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | STOWE CONTRACTING | MARINA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | PEBBLE BEACH | 2020-09-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1162 |  | 1 |  | HARVEST CONSTRUCTION | MONTEREY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | PEBBLE BEACH | 2020-01-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 888 |  | 1 |  | MISSION CONSTRUCTION | SEASIDE | CA | N | Y | No | No | No | No | No | No | No | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | MONTEREY | PEBBLE BEACH | 2020-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 275 |  | 1 |  | CALIFORNIA AMERICAN WATER | PACIFIC GROVE | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | SALINAS | 2020-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1562 |  | 1 |  | HOMEOWNER | SALINAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | SALINAS | 2020-02-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2028 |  | 2 |  | HOMEOWNER | SALINAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | SALINAS | 2020-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1289 |  | 1 |  | CARNERO CONSTRUCTION | CARMEL VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | SALINAS | 2020-11-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | HOMEOWNER | SALINAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | SALINAS | 2020-09-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6886 |  | 1 |  | TROY CONSTRUCTION | PASO ROBLES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT INFORMATION OR MARKS
Pacific Gas and Electric | N | MONTEREY | SALINAS | 2020-09-01 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 4 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 23683 |  | 3 |  | TROY CONSTRUCTION | PASO ROBLES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | SALINAS | 2020-05-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3105 |  | 1 |  | HOMEOWNER | SALINAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | SALINAS | 2020-08-25 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2976 |  | 1 |  | CEN-CAL CONSTRUCTION | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | MONTEREY | SALINAS | 2020-11-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3397 |  | 1 |  | HOMEOWNER | SALINAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | SALINAS | 2020-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1928 |  | 1 |  | SIMS FIRE PROTECTION | PASO ROBLES | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | SALINAS | 2020-08-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2003 |  | 1 |  | HOMEOWNER | SALINAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | SALINAS | 2020-07-31 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3491 |  | 3 |  | CAL WEST FENCE | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | SAND CITY | 2020-10-29 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 22 |  | KJ WOODS CONSTRUCTION | SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | SEASIDE | 2020-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1543 |  | 3 |  | JD''S PLUMBING | SEASIDE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | MONTEREY | SEASIDE | 2020-11-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2000 |  | 2 |  | HOMEOWNER | SEASIDE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | SOLEDAD | 2020-06-22 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2683 |  | 1 |  | IHS INTEGRATED HOME SOLUTIONS | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | SOLEDAD | 2020-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1 |  | 0 |  | TEICHERT CONSTRUCTION | PLESANTON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT INFORMATION OR MARKS
Pacific Gas and Electric | N | NAPA | AMERICAN CANYON | 2020-12-09 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1070 |  | 1 |  | GHILOTTI BROTHERS CONSTRUCTION | SAN RAFAEL | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | NAPA | AMERICAN CANYON | 2020-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | Y | N | N | 0 | 0 |  | 0 | 0 |  | 1929 |  | 1 |  | CITY OF AMERICAN CANYON | AMERICAN CANYON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | NAPA | AMERICAN CANYON | 2020-12-11 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6993 |  | 0 |  | HOMEOWNER | AMERICAN CANYON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NAPA | AMERICAN CANYON | 2020-02-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2888 |  | 1 |  | CENTRAL VALLEY ENGINEERING AND ASPHALT | ROSEVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | NAPA | AMERICAN CANYON | 2020-12-22 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10000 |  | 3 |  | GHILOTTI BROTHERS CONSTRUCTION | SAN RAFAEL | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | NAPA | CALISTOGA | 2020-04-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2406 |  | 1 |  | VETERAN POWER | BENICIA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | NAPA | DEER PARK | 2020-11-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3504 |  | 3 |  | SJM FARMING | CALISTOGA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NAPA | NAPA | 2020-04-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 872 |  | 1 |  | HOMEOWNER | NAPA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NAPA | NAPA | 2020-09-24 | Third party excavation damage | Riser | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 341 |  | 0 |  | NA | NA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | NAPA | NAPA | 2020-01-30 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 667 |  | 0 |  | PENNY PINCHING CONSTRUCTOIN | NAPA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NAPA | NAPA | 2020-07-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 500 |  | 1 |  | JMB | SAN FRANSISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | NAPA | NAPA | 2020-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 21741 |  | 2 |  | HOMEOWNER | NAPA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NAPA | NAPA | 2020-10-27 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 6 |  | J&D EXCAVATION INC | ROCKLIN | CA | Y | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NAPA | NAPA | 2020-04-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5000 |  | 0 |  | HOMEOWNER | NAPA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NAPA | NAPA | 2020-04-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2415 |  | 1 |  | HOMEOWNER | NAPA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NAPA | NAPA | 2020-09-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 54 | 48 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 733 |  | 1 |  | M3 GENERAL ENGINEERING | NAPA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | NAPA | NAPA | 2020-04-30 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6061 |  | 6 |  | WEBBER ENGINEERING | WINTERS | CA | N | Y | No | No | No | No | No | No | No | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | NAPA | NAPA | 2020-05-26 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7812 |  | 40 |  | IRISH CONSTRUCTION | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NAPA | NAPA | 2020-11-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 119 |  | 1 |  | HOMEOWNER | NAPA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NAPA | NAPA | 2020-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7 |  | 6 |  | STEVE''S EXCAVATING | LOOMIS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NAPA | NAPA | 2020-12-11 | Third party excavation damage | Transmission Line in an HCA area | Steel | Hand Tools | 10 | 855 | 450 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | JMB CONSTRUCTION | SOUTH SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | NAPA | RUTHERFORD | 2020-02-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | HOMEOWNER | NAPA | CA | N | Y | No | No | No | No | No | No | No | No USA Ticket
Pacific Gas and Electric | N | NAPA | SAINT HELENA | 2020-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1865 |  | 0 |  | HOMEOWNER | ST. HELENA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NAPA | SAINT HELENA | 2020-12-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1365 |  | 1 |  | TRUGRADE CONSTRUCTION | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NAPA | ST HELENA | 2020-01-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1500 |  | 1 |  | VIDA BUILDING SYSTEMS | BOLINAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NEVADA | GRASS VALLEY | 2020-04-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1815 |  | 2 |  | HOMEOWNER | GRASS VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NEVADA | GRASS VALLEY | 2020-09-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2291 |  | 1 |  | HOMEOWNER | GRASS VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NEVADA | GRASS VALLEY | 2020-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 100 |  | 1 |  | HOMEOWNER | GRASS VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NEVADA | GRASS VALLEY | 2020-01-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2333 |  | 6 |  | PRO BUILDERS | ORANGEVALE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NEVADA | GRASS VALLEY | 2020-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2828 |  | 1 |  | APEX CONTRACTOR SERVICES | GRASS VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT INFORMATION OR MARKS
Pacific Gas and Electric | N | NEVADA | GRASS VALLEY | 2020-11-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1785 |  | 1 |  | HOMEOWNER | GRASS VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NEVADA | NEVADA CITY | 2020-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1016 |  | 1 |  | ALESSANDRO ELECTRIC | RANCHO CORDOVA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | PLACER | AUBURN | 2020-05-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1189 |  | 1 |  | RUSTY HALL CONSTRUCTION | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | AUBURN | 2020-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2184 |  | 1 |  | OUT DOOR LIVING | RANCHO CORDOVA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | AUBURN | 2020-10-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | AUBURN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | AUBURN | 2020-10-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | AUBURN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | AUBURN | 2020-12-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1282 |  | 0 |  | FREED EXCAVATING | AUBURN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | AUBURN | 2020-06-27 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | HOMEOWNER | AUBURN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | No USA Ticket
Pacific Gas and Electric | N | PLACER | AUBURN | 2020-04-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | SCHREIBER CONSTRUCTION | GRASS VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Dig with Care
Pacific Gas and Electric | N | PLACER | AUBURN | 2020-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1565 |  | 1 |  | HOMEOWNER | AUBURN | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | PLACER | AUBURN | 2020-04-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1865 |  | 0 |  | HOMEOWNER | ROSEVILLE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | PLACER | GRANITE BAY | 2020-12-08 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 4 | 60 | 55 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | KP MARTIN INC | AUBURN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | PLACER | GRANITE BAY | 2020-12-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 964 |  | 0 |  | PERFECT SQUARE | LOOMIS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | GRANITE BAY | 2020-05-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | HOMEOWNER | GRANITE BAY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment
Pacific Gas and Electric | N | PLACER | GRANITE BAY | 2020-12-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1258 |  | 1 |  | HOMEOWNER | GRANITE BAY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | GRANITE BAY | 2020-07-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1701 |  | 1 |  | ARCADIAN FENCE | IOWA HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | PLACER | GRANITE BAY | 2020-05-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1335 |  | 1 |  | WAVE COMMUNICATION | ROCKLIN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | LINCOLN | 2020-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Vacuum Equipment with no Agreement | 0.75 | 50 | 45 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | TEICHERT CONSTRUCTION | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Inadequate Excavation Practices
Pacific Gas and Electric | N | PLACER | LINCOLN | 2020-01-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1184 |  | 1 |  | GERONDAKIS & SONS | POLLOCK PINES | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | LOOMIS | 2020-09-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2873 |  | 1 |  | LYLE''S CONSTRUCTION | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | PLACER | LOOMIS | 2020-12-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1026 |  | 1 |  | FOOTHILL FIRE PROTECTION | LOOMIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | PLACER | LOOMIS | 2020-08-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2229 |  | 1 |  | HOMEOWNER | LOOMIS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | LOOMIS | 2020-12-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | PERFECT SQUARE | LOOMIS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | NEWCASTLE | 2020-08-16 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | NEWCASTLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | PENRYN | 2020-08-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1486 |  | 2 |  | ALEXANDER FENCE PROS | NEWCASTLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | PLACER | PENRYN | 2020-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4 |  | 1 |  | HOMEOWNER | PENRYN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | ROCKLIN | 2020-09-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4044 |  | 1 |  | HOMEOWNER | ROCKLIN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | ROCKLIN | 2020-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2191 |  | 2 |  | CAL SIERRA FENCE | ROCKLIN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | ROCKLIN | 2020-01-21 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1375 |  | 0 |  | UNLIMITED COMUNICATIONS | WOODLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | PLACER | ROCKLIN | 2020-07-31 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1212 |  | 0 |  | CEC | ROCKLIN | CA | N | Y | Yes | Yes | No | No | No | Yes | Yes | INCORRECT INFORMATION OR MARKS
Pacific Gas and Electric | N | PLACER | ROSEVILLE | 2020-02-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1358 |  | 1 |  | UNIVERSAL DESIGN | POLLOCK PINES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | PLACER | ROSEVILLE | 2020-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1358 |  | 0 |  | FLOWLINE CONTRACTORS | SACRAMENTO | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | PLACER | ROSEVILLE | 2020-12-21 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4952 |  | 1 |  | TRIP HAZARD | SANTA ROSA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | PLACER | ROSEVILLE | 2020-11-05 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3157 |  | 0 |  | CITY OF ROSEVILLE | ROSEVILLE | CA | N | Y | Yes | Yes | No | No | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | PLACER | ROSEVILLE | 2020-01-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2705 |  | 2 |  | HOMEOWNER | ROSEVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | ROSEVILLE | 2020-08-05 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5445 |  | 1 |  | GILL BALWINDER | ROSEVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | ROSEVILLE | 2020-07-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3443 |  | 1 |  | HOMEOWNER | ROSEVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | ROSEVILLE | 2020-05-13 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | BLACKROCK | ROCKLIN | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | PLACER | ROSEVILLE | 2020-06-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1164 |  | 1 |  | HOMEOWNER | ROSEVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | ROSEVILLE | 2020-06-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2787 |  | 1 |  | CITY OF ROSEVILLE | ROSEVILLE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | PLACER | ROSEVILLE | 2020-05-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1653 |  | 1 |  | SUPERIOR FENCE | ROSEVILLE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | PLACER | ROSEVILLE | 2020-03-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1699 |  | 1 |  | MCGUIRE & HESTER | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | PLACER | ROSEVILLE | 2020-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1834 |  | 1 |  | HOMEOWNER | ROSEVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | ROSEVILLE | 2020-03-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1098 |  | 0 |  | HOMEOWNER | ROSEVILLE | CA | N | Y | No | No | No | No | No | No | No | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | SACRAMENTO | ANTELOPE | 2020-08-11 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 6 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 15860 |  | 0 |  | M & M ELECTRIC | SACRAMENTO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | CARMICHAEL | 2020-06-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2335 |  | 1 |  | CLASSIC FENCE CO | RANCHO CORDOVA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | CARMICHAEL | 2020-10-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | GREEN FUTURE LANDSCAPING | CARMICHAEL | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | CARMICHAEL | 2020-02-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2443 |  | 2 |  | CSI ENGINEERING | CARMICHAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | CARMICHAEL | 2020-01-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 203 |  | 1 |  | ALI CONSTRUCTION | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | CITRUS HEIGHTS | 2020-09-18 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 8247 |  | 10 |  | MITCHELL CONCRETE | RANCHO CORDOVA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | CITRUS HEIGHTS | 2020-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1497 |  | 1 |  | THE TRENCHLESS COMPANY | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | CITRUS HEIGHTS | 2020-06-30 | Operator excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | TEICHERT CONSTRUCTION | SACRAMENTO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | CITRUS HEIGHTS | 2020-12-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1394 |  | 1 |  | HOMEOWNER | CITRUS HEIGHTS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | CITRUS HEIGHTS | 2020-09-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1770 |  | 1 |  | WAITER BENNETT | CITRUS HEIGHTS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | CITRUS HEIGHTS | 2020-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1769 |  | 1 |  | HOMEOWNER | CITRUS HEIGHTS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | CITRUS HEIGHTS | 2020-11-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2557 |  | 1 |  | HOMEOWNER | CITRUS HEIGHTS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | CITRUS HEIGHTS | 2020-12-15 | Third party excavation damage | A service line with no excess flow valve installed | Copper | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9480 |  | 1 |  | DONE RIGHT PAVING AND GRADING | OAKDALE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | CITRUS HEIGHTS | 2020-05-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4184 |  | 1 |  | J & S ASPHALT | ROCKLIN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | CITRUS HEIGHTS | 2020-02-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1668 |  | 1 |  | HOMEOWNER | CITRUS HEIGHTS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | EXCAVATED PRIOR TO LEGAL EXCAVATION START DATE AND TIME
Pacific Gas and Electric | N | SACRAMENTO | CITRUS HEIGHTS | 2020-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | HOMEOWNER | CITRUS HEIGHTS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | No USA Ticket
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2020-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2647 |  | 0 |  | LA TIERRA VERDE | STOCKYON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2020-06-09 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 4 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 14599 |  | 2 |  | NV COMMUNICATIONS | WOODLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2020-02-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2267 |  | 0 |  | MILLCREEK ELECTRICAL | CERES | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2020-12-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1987 |  | 3 |  | KDC CONSTRUCTION | ROSEVILLE | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2020-11-02 | Third party excavation damage | Main | Polyethylene Pipe | Directional Drilling | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | CABLECOM | MCCLELLAN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2020-10-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9564 |  | 4 |  | UNITED BUILDING CONTRACTORS | CHICO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2020-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2395 |  | 1 |  | HOMEOWNER | ELK GROVE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2020-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7369 |  | 1 |  | GM CONSTRUCTION | CITRUS HEIGHTS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2020-12-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6976 |  | 0 |  | NV COMMUNICATION | GARDNERVILLE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2020-12-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2139 |  | 2 |  | CABLECOM | MCCLELLAN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2020-05-05 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 55 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | TEICHERT CONSTRUCTION | SACRAMENTO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Incorrect information or marks
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2020-07-13 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2000 |  | 0 |  | OCHOA''S BACKHOE SERVICE | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2020-05-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1821 |  | 1 |  | ELK GROVE PLUMBING | ELK GROVE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2020-01-06 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1107 |  | 0 |  | POWER PLUS | SACRAMENTO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | SACRAMENTO | ELVERTA | 2020-05-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5440 |  | 1 |  | HOMEOWNER | ELVERTA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | FAIR OAKS | 2020-02-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1987 |  | 1 |  | HOMEOWNER | FAIR OAKS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | FAIR OAKS | 2020-05-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2859 |  | 0 |  | ROOTER HERO | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | FAIR OAKS | 2020-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | SACRAMENTO SEWER DISTRICT | SACRAMENTO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | FAIR OAKS | 2020-09-16 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1774 |  | 1 |  | VETERAN PIPELINE CONSTRUCTION | BENECIA | CA | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | FLORIN | 2020-01-10 | Third party excavation damage | Main | Steel | Augur | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 24180 |  | 0 |  | NEWLAND ENTITIES INC | YUBA CITY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | FLORIN | 2020-02-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1427 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | FOLSOM | 2020-10-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 17 |  | 1 |  | PROGRESSIVE LANDSCAPE | FOLSOM | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | FOLSOM | 2020-11-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4378 |  | 1 |  | HOMEOWNER | FOLSOM | CA | N | Y | No | No | No | No | No | No | No | USA NOTIFICATION ERROR
Pacific Gas and Electric | N | SACRAMENTO | FOLSOM | 2020-12-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1699 |  | 0 |  | CHANCELLOR BACKHOE SERVICES | FOREST HILL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | FOLSOM | 2020-02-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3209 |  | 0 |  | OUTDOOR DIMENSIONS | ANAHEIM | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | FOLSOM | 2020-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | HEMINGTON LANDSCAPE SERVICE | CAMERON PARK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | FOLSOM | 2020-02-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3412 |  | 1 |  | HOMEOWNER | FOLSOM | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | FOLSOM | 2020-10-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CTS CONCRETE | FOLSOM | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | FOLSOM | 2020-09-22 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4944 |  | 0 |  | J.R. PIERCE PLUMBING CO. INC. | ROCKLIN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | FOLSOM | 2020-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 500 |  | 1 |  | HOMEOWNER | FOLSOM | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | FOLSOM | 2020-01-27 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5420 |  | 1 |  | BC ELECTRIC INC | RESCUE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | GALT | 2020-12-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2746 |  | 0 |  | C G ELECTRIC | ESCALON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | GALT | 2020-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2693 |  | 1 |  | HOMEOWNER | GALT | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | LA RIVIERA | 2020-02-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3113 |  | 2 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | NORTH HIGHLANDS | 2020-11-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2634 |  | 1 |  | HOMEOWNER | NORTH HIGHLANDS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | NORTH HIGHLANDS | 2020-05-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 33728 |  | 0 |  | MARQUES | RIO LINDA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | NORTH HIGHLANDS | 2020-05-21 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 4 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1000 |  | 0 |  | MARQUES | RIO LINDA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | NORTH HIGHLANDS | 2020-04-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 101 |  | 1 |  | AMERIGAS | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | ORANGEVALE | 2020-09-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | AUBURN POOLS | AUBURN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | RIO LINDA | 2020-02-28 | Third party excavation damage | Riser | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1602 |  | 0 |  | NA | NA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | ROSEMONT | 2020-02-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1338 |  | 1 |  | SACRAMENTO COUNTY SEWER DISTRICT | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-03-24 | Third party excavation damage | Main | Steel | Boring Equipment | 2 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 12803 |  | 0 |  | UNLIMITED COMMUNICATIONS | WOODLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 50 | 46 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Dig with Care
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-09-17 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5000 |  | 2 |  | WEST CAL CONCRETE | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-07-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2787 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | THEIS ENGINEERING INC. | RANCHO CORDOVA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-11-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | PASQUETTI ENTERPRISES | LINCOLN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 608 |  | 0 |  | AUSTERMAN INC | WEST SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-06-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1581 |  | 2 |  | SACRAMENTO SEWER DISTRICT | SACRAMENTO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-10-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1998 |  | 0 |  | ROTO ROOTER | SACRAMENTO | CA | N | Y | Yes | Yes | No | No | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-12-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1562 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 740 |  | 4 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1987 |  | 1 |  | ZELLARS CONCRETE | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-01-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | No USA Ticket
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-02-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1309 |  | 1 |  | PROCADA LANDSCAPING | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-05-01 | Operator excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3748 |  | 6 |  | TEICHERT CONSTRUCTION | SACRAMENTO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-05-01 | Operator excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 6 |  | TEICHERT CONSTRUCTION | SACRAMENTO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-07-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1637 |  | 1 |  | DEL RAY FABRICATION | ELK GROVE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-06-25 | Third party excavation damage | Transmission Line in an HCA area | Steel | Vacuum Equipment with no Agreement | 12 | 240 | 215 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | NV COMMUNICATIONS | WOODLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Inadequate Excavation Practices
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-08-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2000 |  | 1 |  | CITY OF SACRAMENTO | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-08-26 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 1.25 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1 |  | 0 |  | ALL AMERICAN CONTRUCTION INC. | LIVE OAK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-05-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1209 |  | 2 |  | JAZ DEVELOPMENTS | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | No | No | EXCAVATED OUTSIDE OF DELINEATED AREA
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-12-11 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 13854 |  | 0 |  | CSI ENGINEERING | CARMICHAEL | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-06-02 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 22558 |  | 2 |  | ARROW CONSTRUCTION | SACRAMENTO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | PIPE WAS ENCASED IN CONCRETE
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-08-06 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2372 |  | 0 |  | BUTTERFIELD ELECTRIC | WOODLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ALWAYS AFFORDABLE PLUMBING | SACRAMENTO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1643 |  | 1 |  | FRIENDLY NEIGHBOR FENCE REPAIR | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-04-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 500 |  | 1 |  | UNLIMITED COMMUNICATIONS | WOODLAND | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-05-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1522 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-07-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 1 | 0.5 | 0.38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2754 |  | 0 |  | NA | NA | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-06-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1803 |  | 1 |  | MARTIN GENERAL ENGINEERING | RANCHO CORDOVA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | M&M ELECTRIC | SACRAMENTO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Incorrect information or marks
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-04-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 11548 |  | 1 |  | PRIMARY CONTRACTOR | CORONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-01-01 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 13513 |  | 0 |  | NA | NA | CA | N | Y | No | No | No | No | No | No | No | NO USA TICKET
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-05-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1889 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-10-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | GOLDEN STATE FENCE | RANCHO CORDOVA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 1 | 0.5 | 0.38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 448 |  | 2 |  | 360 COMMUNICATIONS | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-03-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1365 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-09-29 | Operator excavation damage | Main | Steel | Boring Equipment | 6 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3164 |  | 0 |  | ARROW CONSTRUCTION | SACRAMENTO | CA | Y | Y | Yes | No | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-02-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1660 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-04-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2364 |  | 0 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-02-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1208 |  | 1 |  | HOMEOWNER | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-04-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1926 |  | 0 |  | LIFESCAPING | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-10-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2000 |  | 2 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-08-28 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1100 |  | 2 |  | VPC CHARGE | BENECIA | CA | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 0.5 | 0.38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2398 |  | 2 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-02-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1408 |  | 1 |  | EXPRESS SEWER AND DRAIN | RANCHO CORDOVA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-12-18 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2408 |  | 1 |  | BAMUM AND CELILLO ELEC | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-11-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3172 |  | 1 |  | THE TRENCHLESS CO. | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-11-05 | Operator excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2215 |  | 1 |  | VETERAN PIPELINE COMPANY (VPC) | BENICIA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-11-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 500 |  | 0 |  | ONTRAC EARTHWORKS | GRANITE BAY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-10-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1212 |  | 1 |  | GARDEN TUTORS | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-11-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2070 |  | 0 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-09-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2075 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-11-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1822 |  | 1 |  | FLORES PAVING | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-07-20 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1091 |  | 1 |  | VETERAN PIPELINE CONSTRUCTION | BENECIA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-05-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1690 |  | 2 |  | NV COMMUNICATIONS | SACRAMENTO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-06-02 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1835 |  | 2 |  | TEICHERT CONSTRUCTION | SACRAMENTO | CA | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-09-29 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 500 |  | 2 |  | OLYMPUS ELECTRIC | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-01-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1880 |  | 0 |  | GRADE TREK | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-02-27 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4088 |  | 0 |  | EAGLE COMPANIES INC | AUBURN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4944 |  | 1 |  | NAVAJO PIPELINES | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | PIPE WAS ENCASED IN CONCRETE
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2613 |  | 1 |  | PACIFIC COAST CONSTRUCTION | ELK GROVE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | PACIFIC COAST CONST. SERVICE INC. | ELK GROVE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-11-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | FLOREZ PAVING | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3200 |  | 1 |  | S&S FENCE COMPANY | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-11-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 33 |  | 7 |  | S&S FENCE COMPANY | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-05-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1777 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-12-07 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 50 | 44 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | HOMEOWNER | SACRAMENTO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-12-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3930 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-09-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 862 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5326 |  | 0 |  | MP NEXT LEVEL | ELK GROVE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-11-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2935 |  | 0 |  | BLUE IRON | FRESNO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-10-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Trencher | 0.75 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-11-02 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 50 | 44 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CUSTOM GRADING INC., | LINCOLN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 550 |  | 1 |  | JOSHUA CORNSILK. LASAR UNDERGROUND CO | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-05-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1635 |  | 1 |  | PROUDA LANDSCAPING | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-08-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6362 |  | 2 |  | CABLECOM | MCCLELLAN PARK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-02-11 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5116 |  | 0 |  | NV COMMUNICATION | MCCLELLAN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-06-18 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7946 |  | 0 |  | SIERRA ASPHALT INC | RANCHO CORDOVA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-08-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1354 |  | 1 |  | CABLECOMM | MCCLELLAN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-06-17 | Third party excavation damage | Main | Polyethylene Pipe | Trencher | 8 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9793 |  | 0 |  | TEICHERT CONSTRUCTION | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-05-26 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1811 |  | 0 |  | VETERAN POWER | BENICIA | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-01-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2108 |  | 1 |  | CITY OF SAC,DEPT OF UTIL,WASTEWATER&DRAINAGEDIVISI | SACRAMENTO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2933 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2457 |  | 1 |  | JD PASQUETTI | LINCOLN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-06-18 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 813 |  | 0 |  | ARROW CONSTRUCTION | SACRAMENTO | CA | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-11-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2870 |  | 0 |  | SKILLED TRADE SERVICES | SACRAMENTO | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-04-24 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Vacuum Equipment with no Agreement | 0.75 | 50 | 44 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | SAINT FRANCIS ELECTRIC | SAN LEANDRO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Dig with Care
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-06-08 | Third party excavation damage | Main | Steel | Vacuum Equipment with no Agreement | 20 | 50 | 44 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | UNLIMITED COMMUNICATIONS | WOODLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Inadequate Excavation Practices
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-12-29 | Third party excavation damage | Main | Polyethylene Pipe | Directional Drilling | 4 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 27306 |  | 0 |  | MP NEXLEVEL | ELK GROVE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-04-23 | Third party excavation damage | Transmission Line in an HCA area | Steel | Vacuum Equipment with no Agreement | 4 | 425 | 400 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | SEFNCO | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Inadequate Excavation Practices
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-05-05 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 266 |  | 0 |  | LUND CONST | NORTH HIGHLANDS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-07-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 950 |  | 0 |  | M&M ELECTRIC | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2020-07-06 | Operator excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 20000 |  | 5 |  | VETERAN PIPELINE CONSTRUCTION | BENICIA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN BENITO | HOLLISTER | 2020-09-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1062 |  | 1 |  | MCELVANY INC | LOS BANOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN BENITO | HOLLISTER | 2020-09-17 | Third party excavation damage | Main | Steel | Grader/Scraper | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DURDEN CONSTURUCTION | SAN JUAN BAUTISTA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | SAN BENITO | HOLLISTER | 2020-08-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1299 |  | 0 |  | AMERICAN UNDERGROUND CONTRACTORS | BYRON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN BENITO | HOLLISTER | 2020-12-31 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 885 |  | 0 |  | GOLD COAST ELECTRIC | HOLLISTER | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | NOT MARKED DUE TO EXPIRED USA TICKET
Pacific Gas and Electric | N | SAN BENITO | HOLLISTER | 2020-05-22 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1212 |  | 0 |  | SATELLITE GRADING | LOS BANOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN BENITO | PAICINES | 2020-07-19 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5963 |  | 2 |  | HOMEOWNER | PAICINES | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN BENITO | RIDGEMARK | 2020-02-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1951 |  | 1 |  | HOMEOWNER | HOLLISTER | CA | N | Y | No | No | No | No | No | No | No | NO USA TICKET
Pacific Gas and Electric | N | SAN BENITO | SAN JUAN BAUTISTA | 2020-01-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1164 |  | 0 |  | HOMEOWNER | SAN JUAN BAUTISTA | CA | N | Y | No | No | No | No | No | No | No | NO USA TICKET
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-08-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2899 |  | 1 |  | M SQUARED | SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-01-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1000 |  | 1 |  | A RUIZ CONSTRUCTION | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1.25 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4020 |  | 5 |  | SF GONZALEZ CONCRETE | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | EXCAVATED OUTSIDE OF DELINEATED AREA
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-11-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DLB PLUMBING | ANTIOCH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1778 |  | 1 |  | PHOENIX ELECTRIC | SAN FRANCISCO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | LOCATING WIRE MISSING OR BROKEN
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-08-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3050 |  | 0 |  | OARCON INC | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1699 |  | 1 |  | SEATON PACIFIC CONSTRUCTION | RICHMOND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-09-30 | Operator excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MISSION CONSTRUCTION | SAN FRANCISCO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-07-22 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 4 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2173 |  | 0 |  | SF WATER DEPT | SAN FRANCISCO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT INFORMATION OR MARKS
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-01-10 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3861 |  | 1 |  | NA | NA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-10-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4883 |  | 1 |  | HARTY PIPELINES INC | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-04-14 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2000 |  | 4 |  | O''SHAUGHNESSY CONSTRUCTION | SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3211 |  | 2 |  | PRISM ENGINEERING | HAYWARD | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-11-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3875 |  | 4 |  | CRATUS INC | SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-03-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10683 |  | 1 |  | PRECISION ENGENEARING | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-04-01 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 6 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 14952 |  | 9 |  | MITCHELL ENGINEERING | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-04-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 500 |  | 1 |  | PERCISION ENGINEERING | SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-01-14 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9382 |  | 0 |  | SETON PACIFIC CONSTRUCTION | SAN FRANCISCO | CA | N | Y | Yes | No | No | Yes | No | Yes | No | ABANDONED/DEACTIVATED FACILTY ISSUE
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 165 |  | 0 |  | HOSELEY CORPORATION | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-03-19 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 60 | 50 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | MITCHELL ENGINEERING | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | Excavated outside delineated area
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2023 |  | 1 |  | DPR CONSTRUCTION | REDWOOD CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-05-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1809 |  | 1 |  | D''ARCY & HARTY | SAN FRANCISCO | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-04-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 51 |  | 1 |  | HOMEOWNER | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-07-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1000 |  | 1 |  | A RUIZ CONSTRUCTION | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-01-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | CRATUS INC | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-10-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | FONTENOY ENGINEERING | SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6776 |  | 2 |  | FONTENOY ENGENEERING | SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-04-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1559 |  | 1 |  | D''ARCY & HARTY | SAN FRANCISCO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-04-29 | Third party excavation damage | Main | Polyethylene Pipe | Trencher | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6070 |  | 0 |  | TRANSWORLD CONSTRUCTION | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-02-27 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Trencher | 1.25 | 0.5 | 0.38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | Dï¿½ARCY & HARRY CONSTRUCTION | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-02-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 1 | 15 | 12 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | SWINERTON BUILDERS | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Dig with Care
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1252 |  | 1 |  | ACE PLUMBING | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-04-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1065 |  | 1 |  | SF WATER DEPT | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-09-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2388 |  | 2 |  | KJ WOODS CONSTRUCTION | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-04-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 500 |  | 2 |  | SAN FRANCISCO WATER DEPT | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | J FLORES CONSTRUCTION | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-12-07 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9235 |  | 1 |  | SF WATER DEPT | SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2417 |  | 1 |  | KJ WOODS CONSTRUCTION | SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-11-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 42 |  | 1 |  | SF WATER DEPT | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-08-27 | Third party excavation damage | Riser | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1374 |  | 0 |  | HOMEOWNER | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-06-01 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 35 | 29 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | MISSION CONSTRUCTORS | SAN FRANCISCO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-07-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 14 | 10 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2206 |  | 0 |  | HOMEOWNER | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-07-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3006 |  | 1 |  | PRECISION ENGENEERING | BELMONT | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-02-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1505 |  | 1 |  | NTK CONSTR | SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-01-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4268 |  | 0 |  | SHEERAN PIPELINE | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-01-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1891 |  | 2 |  | N+K CONSTRUCTION | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-04-03 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 51 |  | 8 |  | SF WATER DEPT | SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2761 |  | 4 |  | MITCHELL ENGINEERING | SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-10-02 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 16804 |  | 0 |  | NTK CONSTRUCTION INC | SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2594 |  | 1 |  | J WOODS | SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-03-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1117 |  | 1 |  | VALLE GARDENING AND LANDSCAPING | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-04-07 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 16563 |  | 0 |  | NTK CONSTRUCTION | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-05-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1579 |  | 1 |  | SUPERB BUILDERS | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-01-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | COLLECTING FLOWERS GARDEN & DESIGN | SAN FRANCISCO | CA | N | Y | Yes | No | Yes | No | No | No | No | EXPIRED USA TICKET
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-08-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2702 |  | 1 |  | REUBEN BROG FENCE | SAN RAMON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1822 |  | 1 |  | PHOENIX ELECTRIC CO | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-05-27 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3233 |  | 1 |  | OSMOSE UTILITIES SERVICE | PEACHTREE CITY GEORGIA | GA | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | PRECISION ENGINEERING | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-04-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5000 |  | 0 |  | STEPHEN HARTY/ HARTY PIPELINES | SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-09-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1282 |  | 1 |  | SF WATER DEPT | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2250 |  | 1 |  | ANGELS PLUMBING CO | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-11-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 630 |  | 0 |  | TRIPLE BK LANDSCAPE | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-10-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3173 |  | 1 |  | DAMIEN TORRES CONSTRUCTION | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-02-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1821 |  | 2 |  | HOMEOWNER | MILLBRAE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2020-03-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5156 |  | 1 |  | THOMPSON BUILDERS | NOVATO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SAN JOAQUIN | ACAMPO | 2020-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1293 |  | 1 |  | MENCHOR SALGADO-BENTON FENCING | ACAMPO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | AUGUST | 2020-02-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1360 |  | 0 |  | HOMEOWNER | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | FRENCH CAMP | 2020-03-05 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Farm Equipment | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 12099 |  | 0 |  | GOLDEN ACRES CUSTOM FRAMING | MANTECA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | FRENCH CAMP | 2020-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1000 |  | 1 |  | UNITED PAVING | CERES | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | FRENCH CAMP | 2020-09-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | HOMEOWNER | FRENCH CAMP | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | LATHROP | 2020-07-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2861 |  | 2 |  | HOMEOWNER | LATHROP | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | LATHROP | 2020-03-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1406 |  | 0 |  | HOMEOWNER | LATHROP | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | LATHROP | 2020-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5935 |  | 0 |  | ALL PHASE SYSTEM INTEGRATION | OLIVEHURST | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | LATHROP | 2020-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2353 |  | 0 |  | KNIFE RIVER CONSTRUCTION | STOCKTON | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | SAN JOAQUIN | LINDEN | 2020-07-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1263 |  | 1 |  | HOMEOWNER | LINDEN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | LINDEN | 2020-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 46 |  | 1 |  | HOMEOWNER | LINDEN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | LOCKEFORD | 2020-04-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 162 |  | 0 |  | EDISON PARK VINEYARDS | LOCKEFORD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | LODI | 2020-09-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3454 |  | 1 |  | BARNEY JORDAN PLUMBING | STOCKTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | LODI | 2020-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 902 |  | 1 |  | ADAMS UNDERGROUND | WATERFORD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | LODI | 2020-02-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2539 |  | 0 |  | HOMEOWNER | LODI | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | LODI | 2020-07-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1482 |  | 0 |  | JARED SWEETIN JS CONSTRUCTION | SACRAMENTO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | SAN JOAQUIN | LODI | 2020-07-16 | Third party excavation damage | Main | Polyethylene Pipe | Directional Drilling | 1.25 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4053 |  | 0 |  | WESTECH INDUSTRIES INC | GALT | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | LODI | 2020-07-22 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6932 |  | 0 |  | TEICHERT CONSTRUCTION | PLESANTON | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2020-04-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 100 |  | 1 |  | CENTRAL VALLEY BAPTIST | MANTECA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2020-08-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1709 |  | 1 |  | HANSON GENERAL CONSTRUCTION | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2020-11-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 12000 |  | 2 |  | THE CITY OF MANTECA | MANTECA | CA | N | Y | Yes | Yes | No | No | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2020-06-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1290 |  | 2 |  | HOMEOWNER | MANTECA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2020-07-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 50 |  | 1 |  | CITY OF MANTECA | MANTECA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2020-12-02 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1195 |  | 0 |  | VALUE PLUMBING INC | BYRON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2020-12-04 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3389 |  | 0 |  | VALUE PLUMBING INC | BYRON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2020-10-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 257 |  | 0 |  | YARD CREATIONS | MANTECA | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2020-11-09 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3000 |  | 0 |  | ADAMS UNDERGROUND | WATERFORD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2020-01-31 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 217 |  | 0 |  | HUMPHREY''S PLUMBING | TURLOCK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2020-04-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 212 |  | 1 |  | RILEY ELECTRIC | MANTECA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2020-03-17 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2015 |  | 0 |  | MORENO TRENCHING | RIO VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2020-06-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1836 |  | 1 |  | HOMEOWNER | MANTECA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2020-07-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1288 |  | 1 |  | HOMEOWNER | MANTECA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | MOUNTAIN HOUSE | 2020-03-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3087 |  | 0 |  | PEREZ NURSERY AND LANDSCAPING | BRENTWOOD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | MOUNTAIN HOUSE | 2020-01-17 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 8158 |  | 0 |  | MBS CONSTR | SAN RAMON | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | INCORERCT INFORMATION/MARKS
Pacific Gas and Electric | N | SAN JOAQUIN | MOUNTAIN HOUSE | 2020-09-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2322 |  | 0 |  | GROUNDWORKS INC. | BRENTWOOD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | RIPON | 2020-07-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2077 |  | 1 |  | TITAN FENCE INC | MODESTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2020-02-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1591 |  | 0 |  | DOLPHIN POOLS | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2020-09-08 | Third party excavation damage | Riser | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 0 |  | CHARLES HOWARD 2 | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2020-02-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 0.5 | 0.38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 919 |  | 1 |  | LEDVIDO | STOCKTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2020-09-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2740 |  | 1 |  | MR. ED''S PLUMBING & ROOTER SERVICE | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2020-11-30 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 0.75 | 60 | 54 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | UNKNOWN | NA |  | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2020-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1941 |  | 0 |  | HOMEOWNER | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2020-07-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1656 |  | 1 |  | HOMEOWNER | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2020-04-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 8905 |  | 1 |  | HOMEOWNER | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2020-02-21 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3015 |  | 2 |  | PG&E | SAN FRANCISCO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2020-08-06 | Operator excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3738 |  | 5 |  | PG&E | SROCKTON | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2020-10-20 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 110 |  | 92 |  | ST. FRANCIS ELECTRIC | SAN LEANDRO | CA | N | Y | Yes | No | Yes | Yes | Yes | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2020-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 694 |  | 1 |  | HOMEOWNER | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2020-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1924 |  | 1 |  | COOK ENGINEERING | RANCHO CORDOVA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2020-06-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 922 |  | 0 |  | CVC CONTRACTOR | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2020-03-10 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | PG&E | SAN FRANCISCO | CA | Y | Y | Yes | Yes | No | No | No | No | No | Facility was not located or marked
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2020-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 65 |  | 2 |  | HOMEOWNER | STOCKTON | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2020-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2686 |  | 0 |  | DELTA BAY CONCRETE CUTTING | OAKLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2020-06-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 749 |  | 1 |  | HOMEOWNER | STOCKTON | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2020-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1.25 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 18320 |  | 0 |  | SEFNCO | LATHROP | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2020-11-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1809 |  | 1 |  | HOMEOWNER | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2020-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1349 |  | 1 |  | POOL PROS | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | EXCAVATED OUTSIDE OF DELINEATED AREA
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2020-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1846 |  | 0 |  | LEAM BACKHOE | HUGHSON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2020-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 813 |  | 0 |  | BAYLOR SERVICES | LOCKFORD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2020-05-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2830 |  | 0 |  | HOMEOWNER | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2020-09-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6000 |  | 0 |  | MEDINA CONSTRUCTION | NA | CA | N | Y | Yes | Yes | No | No | No | Yes | Yes | EXCAVATED PRIOR TO POSITIVE CONTACT
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2020-10-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 269 |  | 1 |  | DELTA POOLS | LODI | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2020-03-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1528 |  | 1 |  | SIZEMORE CONSTRUCTION | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2020-06-08 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1185 |  | 2 |  | VULCAN CONSTRUCTION | FRESNO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2020-04-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1540 |  | 0 |  | SIZEMORE & SONS CONSTRUCTION | OAKLEY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2020-07-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2253 |  | 4 |  | G&N CONSTRUCTION | STOCKTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2020-06-30 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 4 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 30000 |  | 10 |  | GRANITE CONSTRUCTION | FRENCH CAMP | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | SAN JOAQUIN | THORNTON | 2020-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1618 |  | 1 |  | GNC SEPTIC | THORNTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | TRACY | 2020-08-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1803 |  | 0 |  | ARP LANDSCAPE INC | TRACY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | TRACY | 2020-03-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1054 |  | 0 |  | LASAR UNDERGROUND | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | TRACY | 2020-12-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2786 |  | 0 |  | MIKE MCCALL LANDSCAPING | CONCORD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | TRACY | 2020-02-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1553 |  | 0 |  | EVERGREEN LANDSCAPE | TRACY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | TRACY | 2020-07-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 125 |  | 1 |  | MISSION ELECTRIC | FREMONT | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | TRACY | 2020-06-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2393 |  | 0 |  | JMI | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | TRACY | 2020-05-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2311 |  | 1 |  | HOMEOWNER | TRACY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | TRACY | 2020-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2664 |  | 1 |  | ALL AMERICAN FENCE | DANVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | TRACY | 2020-02-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7106 |  | 40 |  | UNITED FENCE SERVICE | TRACY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | TRACY | 2020-01-07 | Third party excavation damage | Main | Polyethylene Pipe | Grader/Scraper | 4 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1000 |  | 0 |  | GOOD FELLOW BROS | LIVERMORE | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | TRACY | 2020-04-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 191 |  | 1 |  | LASAR UNDERGROUND | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | TRENCH COLLAPSED
Pacific Gas and Electric | N | SAN JOAQUIN | TRACY | 2020-05-29 | Operator excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 28 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | PG&E | SAN FRANCISCO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Incorrect facility records/maps
Pacific Gas and Electric | N | SAN JOAQUIN | TRACY | 2020-03-11 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1586 |  | 0 |  | SMITH DENISON CONSTRUCTION | LIVERMORE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | ATHERTON | 2020-10-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1.25 | 34 | 31 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | SUPPLE HOMES INC | MENLO PARK | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | ATHERTON | 2020-06-01 | Third party excavation damage | Riser | Steel | Hand Tools | 0.75 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1136 |  | 0 |  | SITEWORK LANDSCAPING INC | RICHMOND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | CONTRACTOR THOUGHT LINE WAS ABANDONED
Pacific Gas and Electric | N | SAN MATEO | ATHERTON | 2020-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | QCC CONSTRUCTION | SAN CARLOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | ATHERTON | 2020-07-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1435 |  | 1 |  | PONY CONSTRUCTION | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | ATHERTON | 2020-09-28 | Third party excavation damage | Main | Steel | Boring Equipment | 2 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6858 |  | 0 |  | TIGHT ACCESS EXCAVATION | SEBASTOPOL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | ATHERTON | 2020-09-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 483 |  | 1 |  | JENN''S GARDENING | SAN CARLOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | ATHERTON | 2020-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5229 |  | 0 |  | YUA HUA CONSTRUCTION | CAMPBELL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | BELMONT | 2020-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2451 |  | 1 |  | HALLMARK FINE GARDENS | BELMONT | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | BRISBANE | 2020-09-02 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4085 |  | 3 |  | JMB CONTRUCTION | SOUTH SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | BURLINGAME | 2020-11-09 | Third party excavation damage | Main | Steel | Miscellaneous/Other | 2 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10000 |  | 5 |  | MITCHELL ENGINEERING | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | BURLINGAME | 2020-09-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2020 |  | 1 |  | HOMEOWNER | BURLINGAME | CA | N | Y | Yes | No | Yes | Yes | No | Yes | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | BURLINGAME | 2020-03-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 479 |  | 1 |  | RG DEVELOPMENTS | HILLSBOURGH | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | BURLINGAME | 2020-11-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 95 |  | 0 |  | LATALA HOMES INC | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | BURLINGAME | 2020-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 820 |  | 1 |  | NV COMMUNICATIONS | MCCLELLAN PARK | CA | N | Y | Yes | No | Yes | Yes | No | Yes | No | EXCAVATED OUTSIDE OF DELINEATED AREA
Pacific Gas and Electric | N | SAN MATEO | BURLINGAME | 2020-05-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 895 |  | 1 |  | LOMA VERDE GARDENS | SAN MATEO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | BURLINGAME | 2020-01-30 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 303 |  | 0 |  | EVANS BROTHERS INC | LIVERMORE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | BURLINGAME | 2020-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1811 |  | 1 |  | EDT TEC | LIVERMORE | CA | N | Y | No | No | No | No | No | No | No | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | SAN MATEO | COLMA | 2020-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 17 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2386 |  | 1 |  | RK ENGINEERING INC | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | DALY CITY | 2020-05-28 | Operator excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1635 |  | 0 |  | VULCAN CONSTRUCTION | FRESNO CA | CA | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | DALY CITY | 2020-03-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 29 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1785 |  | 2 |  | D&D PIPELINE | SAN ANSELMO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | DALY CITY | 2020-03-02 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6254 |  | 0 |  | D&D PIPELINES | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | DALY CITY | 2020-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 500 |  | 1 |  | HOMEOWNER | DALY CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | EAST PALO ALTO | 2020-10-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5749 |  | 0 |  | BROWN & FESLER INC | LIVERMORE | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | FACILITY COULD NOT BE FOUND OR LOCATED
Pacific Gas and Electric | N | SAN MATEO | EAST PALO ALTO | 2020-08-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2221 |  | 1 |  | HOMEOWNER | REDWOOD CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | EAST PALO ALTO | 2020-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1434 |  | 1 |  | AL THOMPSON | MILPITAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | EL GRANADA | 2020-05-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1227 |  | 1 |  | VSG CONCRETE | MOSS BEACH | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | EL GRANADA | 2020-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1433 |  | 2 |  | SOIL TECHNOLOGIES INC | SAN JOSE CA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | FOSTER CITY | 2020-12-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2185 |  | 0 |  | OVERAA CONSTRUCTION | RICHMOND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | FOSTER CITY | 2020-02-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1536 |  | 1 |  | HOMEOWNER | FOSTER CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | FOSTER CITY | 2020-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1266 |  | 1 |  | REAL TIME CONSTRUCTION | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | FOSTER CITY | 2020-07-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2770 |  | 2 |  | COMMUNITY RECONSTRUCTION SOLUTIONS. | BURLINGAME | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | FOSTER CITY | 2020-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1 |  | 1 |  | COMMUNITY RECONSTRUCTION SOLUTION | BURLINGAME | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | HALF MOON BAY | 2020-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1324 |  | 1 |  | ANDREINI BROTHERS INC | HALF MOON BAY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | HALF MOON BAY | 2020-07-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2025 |  | 2 |  | AMERICAN BUILDERS | PACIFICA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | HILLSBOROUGH | 2020-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7357 |  | 1 |  | PAVER LIFE INC | FREMONT | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | HILLSBOROUGH | 2020-09-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1030 |  | 0 |  | HOMEOWNER | HILLSBOROUGH | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | HILLSBOROUGH | 2020-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | RG DEVELOPMENTS INC | BURLINGAME | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | No USA Ticket
Pacific Gas and Electric | N | SAN MATEO | HILLSBOROUGH | 2020-08-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2206 |  | 1 |  | CACCIA PLUMBING | SAN MATEO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | HILLSBOROUGH | 2020-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2284 |  | 1 |  | JH MEJIA CONSTRUCTION | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | HILLSBOROUGH | 2020-03-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1493 |  | 1 |  | BH CONTRACTING SERVICES | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | HILLSBOROUGH | 2020-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1455 |  | 0 |  | HOMEOWNER | HILLSBOROUGH | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | HILLSBOROUGH | 2020-09-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1016 |  | 0 |  | ALL PHASE BUILDERS | SAN CARLOS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | HILLSBOROUGH | 2020-06-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.75 | 34 | 31 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | HOMEOWNER | HILLSBOROUGH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Dig with Care
Pacific Gas and Electric | N | SAN MATEO | MENLO PARK | 2020-10-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 3 |  | PAVEMENT RECYCLING SYSTEMS, INC. | RIO LINDA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | MENLO PARK | 2020-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1974 |  | 0 |  | QLM INC | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | MENLO PARK | 2020-12-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1840 |  | 1 |  | E J PLUMBING | PALO ALTO | CA | N | Y | Yes | Yes | Yes | Yes | Yes | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | MENLO PARK | 2020-08-27 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 802 |  | 0 |  | GORDITOS PLUMBING | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | MENLO PARK | 2020-12-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1318 |  | 2 |  | WEST VALLEY CONSTRUCTION | REDWOOD CITY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | MENLO PARK | 2020-12-30 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 34 | 27 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NORTH MNGMNT SERV; US GEO SURVEY, DEPT OF INTERIOR | NA |  | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | MENLO PARK | 2020-06-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1587 |  | 2 |  | HOMEOWNER | MENLO PARK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | MENLO PARK | 2020-11-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1536 |  | 0 |  | LINDSTROM COMPANY | SAN MATEO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | MENLO PARK | 2020-11-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1288 |  | 1 |  | LINDSTROM COMPANY | MENLO PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | MENLO PARK | 2020-09-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 878 |  | 1 |  | JPM CONSTRUCTION | SAN MATEO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | MONTARA | 2020-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2053 |  | 1 |  | LOPEZ FENCE | MOSS BEACH | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | MOSS BEACH | 2020-02-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4025 |  | 0 |  | ANDREINI BROS | MOSS BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | NORTH FAIR OAKS | 2020-04-23 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5867 |  | 1 |  | WEST VALLEY CONSTRUCTION | REDWOOD CITY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | PACIFICA | 2020-09-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1530 |  | 1 |  | C2R ENGINEERING | MOUNTAIN VIEW | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | PACIFICA | 2020-01-28 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 2 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6975 |  | 0 |  | ERICKS CONSTRUCTION INC | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | PACIFICA | 2020-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 29 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1801 |  | 1 |  | HOMEOWNER | PACIFICA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | PACIFICA | 2020-05-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 29 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 200 |  | 1 |  | YACOB CONSTRUCTION | PETALUMA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | PORTOLA VALLEY | 2020-11-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 145 |  | 1 |  | UTILITY CONSTRUCTION | SOUTH SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | PORTOLA VALLEY | 2020-03-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1350 |  | 1 |  | ALLIANCE INTERLOCKING PAVERS | MOUNTAIN VIEW | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | PORTOLA VALLEY | 2020-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3144 |  | 1 |  | SIONE''S CONCRETE CONSTRUCTION | REDWOOD CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2020-10-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 6 |  | CASEY CONSTRUCTION | EMERALD HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2020-02-03 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1435 |  | 6 |  | CASEY CONSTRUCTION | EMERALD HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2020-02-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2632 |  | 1 |  | MASTER''S TOUCH BUILDERS | VACAVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2020-11-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10988 |  | 0 |  | CASEY CONSTRUCTION | EMERALD HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2020-12-07 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3928 |  | 1 |  | O''GRADY PAVING INC | MOUNTAIN VIEW | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2020-12-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4003 |  | 1 |  | HOMEOWNER | REDWOOD CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2020-03-13 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3666 |  | 0 |  | KDC CONSTRUCTION | WEST SACRAMENTO | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | FACILITY COULD NOT BE FOUND OR LOCATED
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2020-11-16 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4071 |  | 0 |  | ARB INC | FAIRFIELD | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2020-06-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3304 |  | 1 |  | HOMEOWNER | REDWOOD CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2020-08-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1165 |  | 1 |  | HOMEOWNER | REDWOOD CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2020-05-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 700 |  | 0 |  | SABBATINI PLUMBING INC. | HOLLISTER | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SAN BRUNO | 2020-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6145 |  | 1 |  | RANGER PIPELINES | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SAN BRUNO | 2020-10-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | SAN BRUNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | SAN BRUNO | 2020-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3754 |  | 3 |  | JMB CONSTRUCTION | SOUTH SAN FRANCISCO | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | FACILITY COULD NOT BE FOUND OR LOCATED
Pacific Gas and Electric | N | SAN MATEO | SAN BRUNO | 2020-02-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6974 |  | 1 |  | JMB CONSTRUCTION | SOUTH SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SAN BRUNO | 2020-06-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6167 |  | 2 |  | MCK SERVICES | MARTINEZ | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SAN MATEO | SAN BRUNO | 2020-12-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1570 |  | 0 |  | REDWOOD ELECTRIC GROUP | SANTA CLARA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SAN CARLOS | 2020-01-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1176 |  | 1 |  | MODERN PAVING | SAN LEANDRO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | SAN CARLOS | 2020-08-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2523 |  | 0 |  | CASEY CONSTRUCTION | EMERALD HILLS CA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SAN CARLOS | 2020-02-19 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 8872 |  | 0 |  | J MORAGA CONSTRUCTION | MERCED | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SAN CARLOS | 2020-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 922 |  | 0 |  | MARINA LANDSCAPE | LODI | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | SAN MATEO | SAN CARLOS | 2020-04-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1300 |  | 1 |  | MARINA LANDSCAPE | LATHROP | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SAN CARLOS | 2020-10-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 102 |  | 1 |  | RAMU ARUNCHALAM | SAN CARLOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | SAN CARLOS | 2020-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1175 |  | 1 |  | KLAUSER ELECTRIC INC. | CAMPBELL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SAN CARLOS | 2020-02-14 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 13268 |  | 0 |  | KELLY''S STUMP REMOVEL | SAN CARLOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | SAN CARLOS | 2020-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1857 |  | 0 |  | CASTILLO CONSTRUCTION CO | MORGAN HILL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | SAN CARLOS | 2020-02-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 982 |  | 1 |  | FUNK LANDSCAPE DESIGN & CONSTRUCTION | REDWOOD CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2020-04-28 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4915 |  | 10 |  | JMB CONSTRUCTION | SOUTH SAN FRANCISCO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2020-10-23 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 60 |  | 1 |  | BERINGER CONSTRUCTION | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2020-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 34 | 31 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | EXTERIOR PAVERS DESIGNS, INC. | SAN CARLOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2020-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1277 |  | 1 |  | WEST VALLEY CONSTRUCTION | CAMPBELL | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2020-05-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2644 |  | 1 |  | WORKS PLUMBING | PACIFICA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2020-08-24 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1.25 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3812 |  | 1 |  | HH FENCE AND DECK COMPANY | SAN BRUNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2020-11-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1407 |  | 1 |  | ONE STOP CONCRETE | ANTIOCH | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2020-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1938 |  | 0 |  | MOA PLUMBING | FREMONT | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2020-03-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1459 |  | 0 |  | BAY COUNTIES CONSTRUCTION SERVICES | BRISBANE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2020-01-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3020 |  | 0 |  | KRAKOW COMPANY | BURLINGAME | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2020-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 26267 |  | 1 |  | DAVEY TREE | COLMA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2020-05-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5469 |  | 1 |  | INNOVATE CONCRETE AND ENGINEERING | SANTA CLARA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2020-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2048 |  | 1 |  | EXPRESS PLUMBING | SAN MATEO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2020-12-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3080 |  | 1 |  | W BRADLEY ELECTRIC. | NOVATO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2020-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 917 |  | 1 |  | HOMEOWNER | SAN MATEO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2020-11-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1 |  | 1 |  | HOMEOWNER | SAN MATEO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2020-08-13 | Third party excavation damage | Main | Steel | Boring Equipment | 2 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3387 |  | 0 |  | EXPRESS PLUMBING | SAN MATEO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2020-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 550 |  | 0 |  | EXPRESS PLUMBING | SAN MATEO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2020-12-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 979 |  | 0 |  | BELL PLUMBING | SAN CARLOS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2020-09-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2294 |  | 1 |  | ALADDIN HAULING | BURLINGAME | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2020-09-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1679 |  | 1 |  | HOMEOWNER | SAN MATEO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2020-11-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1166 |  | 1 |  | ROSAS BROTHERS CONSTRUCTION | OAKLAND | CA | N | Y | Yes | Yes | Yes | Yes | Yes | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SOUTH SAN FRANCISCO | 2020-01-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2076 |  | 2 |  | GROUND CONTROL CORROPATE | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SOUTH SAN FRANCISCO | 2020-04-15 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1508 |  | 2 |  | DALEO INC. | GILROY | CA | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | WOODSIDE | 2020-11-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 48 |  | 1 |  | HOMEOWNER | WOODSIDE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | WOODSIDE | 2020-08-27 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Augur | 0.75 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1852 |  | 1 |  | BAY AREA DESIGN & CONSTRUCTION | CAMPBELL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | ALUM ROCK | 2020-01-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1415 |  | 1 |  | RICHARD HARO INC | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | CAMPBELL | 2020-10-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | AFFORDABLE PROPERTY MANAGEMENT | UNION CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | CAMPBELL | 2020-03-30 | Operator excavation damage | A service line with no excess flow valve installed | Steel | Vacuum Equipment with no Agreement | 0.75 | 60 | 56 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | MGE UNDERGROUND | SAN JOSE | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Inadequate Excavation Practices
Pacific Gas and Electric | N | SANTA CLARA | CAMPBELL | 2020-09-10 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7450 |  | 2 |  | MEDRANO ELECTRIC | GILROY | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | CAMPBELL | 2020-03-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | HOMEOWNER | CAMPBELL | CA | N | Y | No | No | No | No | No | No | No | No USA Ticket
Pacific Gas and Electric | N | SANTA CLARA | CAMPBELL | 2020-03-10 | Third party excavation damage | Main | Steel | Vacuum Equipment with no Agreement | 2 | 60 | 56 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | SMART COMMUNICATIONS | APOLLO BEACH | FL | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Inadequate Excavation Practices
Pacific Gas and Electric | N | SANTA CLARA | CUPERTINO | 2020-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 600 |  | 0 |  | SHOW BEST CONSTRUCTION | NEWARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | EXCAVATED OUTSIDE OF DELINEATED AREA
Pacific Gas and Electric | N | SANTA CLARA | CUPERTINO | 2020-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1042 |  | 1 |  | DEEP CLIFF GOLF COURSE | CUPERTINO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | CUPERTINO | 2020-02-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 56 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | MIRANDA ELECTRICAL SERVICE | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | No | No | Failed to Delineate Work Site With Required Markings
Pacific Gas and Electric | N | SANTA CLARA | CUPERTINO | 2020-09-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 555 |  | 1 |  | ELIOS SOLAR | STOCKTON | CA | N | Y | Yes | Yes | Yes | No | No | No | No | FAILED TO DELINEATE JOB SITE
Pacific Gas and Electric | N | SANTA CLARA | CUPERTINO | 2020-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 57 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | WEST VALLEY CONSTRUCTION | CAMPBELL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Dig with Care
Pacific Gas and Electric | N | SANTA CLARA | CUPERTINO | 2020-06-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1457 |  | 1 |  | MP CONSTRUCTION CO CIVIL ENGINEERS | SANTA CLARA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | GILROY | 2020-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1036 |  | 0 |  | ROBERT D. LEHMAN CONSTRUCTION | PRUNEDALE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | GILROY | 2020-12-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2981 |  | 1 |  | NA | NA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | CONTRACTOR DAMAGED SERVICE LINE
Pacific Gas and Electric | N | SANTA CLARA | LOS ALTOS | 2020-11-06 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1091 |  | 1 |  | PG&E | SAN FRANCISCO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | LOS ALTOS | 2020-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2337 |  | 0 |  | HOMEOWNER | LOS ALTOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | LOS ALTOS | 2020-12-01 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 57 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | HOMEOWNER | LOS ALTOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | LOS ALTOS | 2020-03-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 56 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | JLM BUILDER INC | CUPERTINO | CA | N | Y | No | No | No | No | No | No | No | No USA Ticket
Pacific Gas and Electric | N | SANTA CLARA | LOS ALTOS | 2020-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1403 |  | 1 |  | SHANE KAVANAUGHY CONSTRUCTION | MOUNTAIN VIEW | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | LOS ALTOS HILLS | 2020-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 927 |  | 1 |  | TKS CONSTRUCTION | MORGAN HILL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | LOS ALTOS HILLS | 2020-12-17 | Operator excavation damage | Main | Steel | Vacuum Equipment with no Agreement | 2 | 60 | 57 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MGE UNDERGROUND | PASO ROBLES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Inadequate Excavation Practices
Pacific Gas and Electric | N | SANTA CLARA | LOS ALTOS HILLS | 2020-11-16 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | EXPRESS PLUMBING | SAN MATEO | CA | N | Y | Yes | Yes | Yes | Yes | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | LOS ALTOS HILLS | 2020-08-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2108 |  | 0 |  | DOUBLE O ENGINEERING | SAN CARLOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | LOS GATOS | 2020-04-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 126 |  | 0 |  | UNITED PLUMBING CONTRACTORS | LOS GATOS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | LOS GATOS | 2020-02-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1891 |  | 1 |  | HOMEOWNER | SARATOGA | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | LOS GATOS | 2020-03-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1043 |  | 1 |  | STATE ELECTRIC GENERATOR | SCOTTS VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | LOS GATOS | 2020-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1165 |  | 1 |  | OCTAGON PAVERS | EAST PALO ALTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | LOS GATOS | 2020-11-06 | Third party excavation damage | Main | Polyethylene Pipe | Directional Drilling | 1.25 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2000 |  | 3 |  | CALIFORNIA UTILITY COMPANY | LOS GATOS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | LOS GATOS | 2020-02-06 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 60 | 56 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | WEST VALLEY CONSTRUCTION | REDWOOD CITY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Failed to Contact Operator/811 When Marked Facilities Could Not Be Located With Hand Tools in Tolerance Zone
Pacific Gas and Electric | N | SANTA CLARA | LOS GATOS | 2020-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1000 |  | 1 |  | HOMEOWNER | LOS GATOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | LOS GATOS | 2020-02-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2047 |  | 1 |  | RANDAZZO DEMO | CASTROVILLE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | LOS GATOS | 2020-02-07 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 56 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | WEST VALLEY CONSTRUCTION | REDWOOD CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment
Pacific Gas and Electric | N | SANTA CLARA | MILPITAS | 2020-02-11 | Third party excavation damage | Main | Steel | Hand Tools | 2 | 60 | 56 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | CRYSTAL CLEAR PLUMBING | HAYWARD | CA | N | Y | No | No | No | No | No | No | No | No USA Ticket
Pacific Gas and Electric | N | SANTA CLARA | MILPITAS | 2020-02-14 | Operator excavation damage | A service line with no excess flow valve installed | Steel | Vacuum Equipment with no Agreement | 0.75 | 60 | 56 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | MGE UNDERGROUND | SAN JOSE | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | Incorrect facility records/maps
Pacific Gas and Electric | N | SANTA CLARA | MILPITAS | 2020-11-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4481 |  | 2 |  | SAMI & SONS INC | MILPITAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | MILPITAS | 2020-08-11 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 15194 |  | 0 |  | HCH ELECTRIC | LIVERMORE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | MILPITAS | 2020-01-24 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1.25 | 60 | 56 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | MOUNTAIN CASCADE | LIVERMORE | CA | N | Y | Yes | Yes | No | No | No | No | No | Facility was not located or marked
Pacific Gas and Electric | N | SANTA CLARA | MILPITAS | 2020-12-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2160 |  | 1 |  | TECHCON | MORGAN HILL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | MILPITAS | 2020-01-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4227 |  | 5 |  | HOMEOWNER | FREMONT | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | MONTE SERENO | 2020-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1553 |  | 1 |  | YV MASONRY | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | MORGAN HILL | 2020-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5000 |  | 1 |  | HOMEOWNER | MORGAN HILL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | MORGAN HILL | 2020-06-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6165 |  | 1 |  | HOMEOWNER | MORGAN HILL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | MORGAN HILL | 2020-11-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 500 |  | 1 |  | HOMEOWNER | MORGAN HILL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | MORGAN HILL | 2020-11-03 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3196 |  | 2 |  | E.R. BROTHERS | CAMPBELL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | SANTA CLARA | MORGAN HILL | 2020-01-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3748 |  | 1 |  | WIRING CONNECTION | GARDENA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | MORGAN HILL | 2020-08-22 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10000 |  | 0 |  | NA | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | MORGAN HILL | 2020-01-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1147 |  | 6 |  | KJ WOODS CONSTRUCTION | SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | MORGAN HILL | 2020-09-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1589 |  | 1 |  | BEAR ELECTRICAL SOLUTIONS | ALVISO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | MOUNTAIN VIEW | 2020-02-25 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 56 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | WIZARD PLUMBING AND DRAIN | SAN MATEO | CA | N | Y | Yes | Yes | Yes | Yes | No | No | No | Excavated Prior to Receiving a Positive Response From All Utilities
Pacific Gas and Electric | N | SANTA CLARA | MOUNTAIN VIEW | 2020-03-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 56 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | DAVID RAINEY CONSTRUCTION | SUNNYVALE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Dig with Care
Pacific Gas and Electric | N | SANTA CLARA | MOUNTAIN VIEW | 2020-10-19 | Third party excavation damage | Main | Steel | Hand Tools | 2 | 60 | 57 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | SMELLY MEL''S PLUMBING | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | MOUNTAIN VIEW | 2020-12-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1381 |  | 1 |  | COLUMBIA ELECTRIC | SAN LEANDRO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | MOUNTAIN VIEW | 2020-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1280 |  | 1 |  | PRESTON PIPELINE | SACRAMENTO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | MOUNTAIN VIEW | 2020-01-31 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3542 |  | 0 |  | DISTINCT BUILDERS | MOUNTAIN VIEW | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | MOUNTAIN VIEW | 2020-04-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 477 |  | 1 |  | BAEZ GEOTECHNICAL GROUP | TURLOCK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | MOUNTAIN VIEW | 2020-03-06 | Third party excavation damage | Main | Steel | Hand Tools | 2 | 60 | 56 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | FLOWRITE INC | GILROY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Dig with Care
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1000 |  | 0 |  | CITY OF SAN JOSE | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-07-27 | Third party excavation damage | Main | Polyethylene Pipe | Directional Drilling | 2 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6057 |  | 0 |  | JPI UTILITY SERVICES | SAN DIEGO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-11-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9249 |  | 1 |  | LEWIS & TIBBITTS | SAN JOSE | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-06-03 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Vacuum Equipment with no Agreement | 0.75 | 60 | 57 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | PRESTIGE UTILITY | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Inadequate Excavation Practices
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-09-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | TENNYSON ELECTRIC | LIVERMORE | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | FACILITY COULD NOT BE FOUND OR LOCATED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Vacuum Equipment with no Agreement | 0.75 | 60 | 57 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MASTEC | UNION CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1472 |  | 2 |  | INTEGRATED TECH GROUP LABORER | GALLANTIN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-06-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3524 |  | 1 |  | HOMEOWNER | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 57 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | LEWIS & TIBBITTS | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 16386 |  | 1 |  | RICHARD HARO DRAFTING | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-05-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Vacuum Equipment with no Agreement | 0.75 | 60 | 57 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | CALIFORNIA UTILITY COMPANY | SARATOGA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Inadequate Excavation Practices
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-07-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1.25 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6750 |  | 2 |  | HOMEOWNER | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-11-13 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 57 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | J MORAGA CONSTRUCTION | MERCED | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-09-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2793 |  | 1 |  | HOMEOWNER | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-03-06 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 56 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | HP COMMUNICATIONS | UNION CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Dig with Care
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-03-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3125 |  | 1 |  | PAN-PACIFIC MECHANICAL | MENLO PARK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-05-01 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Vacuum Equipment with no Agreement | 0.75 | 60 | 57 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | CALIFORNIA UTILITY COMPANY | SARATOGA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Inadequate Excavation Practices
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-02-20 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3325 |  | 0 |  | S J WATER CO. | SAN JOSE | CA | N | Y | Yes | No | No | Yes | No | No | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-04-09 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Vacuum Equipment with no Agreement | 0.75 | 60 | 57 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | PRESTIGE UTILITY | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Inadequate Excavation Practices
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-05-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10000 |  | 1 |  | PRECISE CONCRETE SAWING | SAN JOSE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-04-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1000 |  | 2 |  | STEVE P RADOS INC | SAN JOSE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-10-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | SPEELMAN EXCAVATION | RIPON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-01-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1916 |  | 1 |  | STEVE P RADOS CORP | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-07-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5036 |  | 1 |  | HOMEOWNER | SAN JOSE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | DID NOT WAIT FOR POSITIVE CONTACT
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-06-23 | Third party excavation damage | Main | Steel | Vacuum Equipment with no Agreement | 3 | 60 | 57 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | MASTEC UTILITY SERVICES | CORAL GABLES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Inadequate Excavation Practices
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1162 |  | 1 |  | A & J CALIFORNIA BUILDERS | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-03-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 736 |  | 2 |  | G C FENING | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-11-21 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 17693 |  | 1 |  | MARCO TREE SERVICES | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-02-24 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Vacuum Equipment with no Agreement | 2 | 60 | 56 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | MASTEC | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Dig with Care
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-05-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | HOMEOWNER | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-07-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 500 |  | 1 |  | HOMEOWNER | SAN JOSE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-10-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 317 |  | 0 |  | HAI QUOC MAC | LOS GATOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-11-09 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 0.43 | 0.31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | DALEO INC | GILROY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Inadequate Excavation Practices
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-03-09 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 56 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | D T QUALITY CONSTRUCTION | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | No USA Ticket
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-10-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 73 |  | 1 |  | STOCKER & ALLAIRE GENERAL CONTRACTORS | MONTEREY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1469 |  | 1 |  | Q2 FCI | MURRIETA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-03-03 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Vacuum Equipment with no Agreement | 0.75 | 60 | 56 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | MASTEC | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Inadequate Excavation Practices
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-04-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 481 |  | 1 |  | INTEGRATED TECH GROUP | GALLATIN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-01-13 | Third party excavation damage | Main | Steel | Vacuum Equipment with no Agreement | 2 | 60 | 56 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | PRESTIGE UTILITY | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Dig with Care
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-06-23 | Third party excavation damage | Main | Steel | Miscellaneous/Other | 4 | 60 | 57 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | ELECTRIC TECH CONSTRUCTION | CONCORD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-05-20 | Third party excavation damage | Main | Steel | Vacuum Equipment with no Agreement | 2 | 60 | 57 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | CABLECOM | SANTA CLARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Inadequate Excavation Practices
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-02-06 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Vacuum Equipment with no Agreement | 0.75 | 60 | 56 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | Q2 FIBER COMMUNICATIONS INC. | MURRIETA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Dig with Care
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-09-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1084 |  | 2 |  | HOMEOWNER | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 781 |  | 1 |  | HOMEOWNER | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1280 |  | 1 |  | HOMEOWNER | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | AAA FENCE | SANTA CLARA, CA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-12-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 673 |  | 40 |  | BROWN & FESLER INC | LIVERMORE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Vacuum Equipment with no Agreement | 0.75 | 60 | 57 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | MASTEC UTILITY SERVICES | CORAL GABLES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Inadequate Excavation Practices
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1686 |  | 1 |  | ALL ONE LANDSCAPE | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-05-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2443 |  | 1 |  | SAM''S CONSTRUTION | MILPITAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-12-02 | Third party excavation damage | Main | Steel | Not Available | 2 | 60 | 57 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | BELLOWS PLUMBING AND HEATING | SAN RAFAEL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-08-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3577 |  | 1 |  | MASTEC | SAN JOSE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-11-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 48 |  | 0 |  | HOMEOWNER | SAN JOSE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-11-17 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5000 |  | 2 |  | DALEO INC | GILROY | CA | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-12-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 748 |  | 0 |  | LEWIS & TIBBITTS | SAN JOSE | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | ABANDONED/DEACTIVATED FACILTY ISSUE
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-01-21 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Vacuum Equipment with no Agreement | 0.75 | 60 | 56 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | SMART COMMUNICATIONS SYSTEM INC | APOLLO BEACH | FL | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Dig with Care
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-07-02 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1 |  | 1 |  | SUNBAY CONSTRUCTION | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-06-18 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | ROSAS BROS CONSTRUCTION | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-12-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1178 |  | 2 |  | HOMEOWNER | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-05-05 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Vacuum Equipment with no Agreement | 0.75 | 60 | 57 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | MASTEC UTILITY SERVICES | CORAL GABLES | FL | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Inadequate Excavation Practices
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 57 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | SMART COMMUNICATION SYSTEMS | APOLLO BEACH | FL | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Dig with Care
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-03-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1873 |  | 0 |  | ROCHA & SON CONSTRUCTION | HALF MOON BAY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-11-05 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 54 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | J MORAGA CONSTRUCTION | MERCED | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 15000 |  | 2 |  | DATALINX COMMUNICATIONS INC. | LANCASTER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | UNKNOWN | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2028 |  | 1 |  | CPA DEMOLITION INC | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-03-31 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3633 |  | 2 |  | PACIFIC UNDERGROUND CONSTR | SAN JOSE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-11-05 | Third party excavation damage | Main | Steel | Boring Equipment | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 167 |  | 7 |  | DATALINX COMMUNICATIONS INC | LANCASTER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10467 |  | 1 |  | NEKTARIOS MATHEOU | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1665 |  | 2 |  | SIMON CONSTRUCTION | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-09-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2318 |  | 0 |  | HOMEOWNER | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-08-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2320 |  | 1 |  | HOMEOWNER | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-11-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 200 |  | 1 |  | HOMEOWNER | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1725 |  | 1 |  | ERGEON FENCE | NA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-03-04 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Vacuum Equipment with no Agreement | 0.75 | 60 | 56 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | MASTEC | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Inadequate Excavation Practices
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-12-07 | Third party excavation damage | Transmission Line in an HCA area | Steel | Backhoe/Trackhoe | 10 | 734 | 400 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | WEST VALLEY CONSTRUCTION | REDWOOD CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-02-12 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 3 | 60 | 56 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | CALIFORNIA UTILITY COMPANY | WOODSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Inadequate Excavation Practices
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-02-12 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Vacuum Equipment with no Agreement | 0.75 | 60 | 56 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | J MORAGA CONSTRUCTION | MERCED | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Dig with Care
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Directional Drilling | 4 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | PRISM ENGINEERING | SAN RAMON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-12-23 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 0.75 | 60 | 57 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | PRISM ENGINEERING | MADERA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-01-15 | Third party excavation damage | Main | Steel | Vacuum Equipment with no Agreement | 4 | 60 | 56 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | CALIFORNIA UTILITY COMPANY | WOODSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Dig with Care
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-01-22 | Third party excavation damage | Main | Steel | Vacuum Equipment with no Agreement | 2 | 60 | 56 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | CALIFORNIA UTILITY COMPANY | WOODSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Dig with Care
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-06-26 | Third party excavation damage | Main | Steel | Vacuum Equipment with no Agreement | 2 | 60 | 57 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | PRESTIGE UTILITY | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Inadequate Excavation Practices
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2020-07-28 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 1.25 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 8402 |  | 3 |  | COLUMBIA ELECTRIC | SAN LEANDRO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN MARTIN | 2020-12-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | INTERSTATE PAVING AND CONSTRUCTION | SOUTH SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN MARTIN | 2020-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1443 |  | 1 |  | MORTON SEPTIC SERVICE | MORGAN HILL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SANTA CLARA | 2020-09-10 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1.25 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4206 |  | 4 |  | COMCAST | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SANTA CLARA | 2020-10-30 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3522 |  | 0 |  | SANCO PIPELINES | LOS GATOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SANTA CLARA | 2020-06-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2153 |  | 1 |  | ACTON ADU | CAMPBELL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | EXCAVATED OUTSIDE OF DELINEATED AREA
Pacific Gas and Electric | N | SANTA CLARA | SANTA CLARA | 2020-06-24 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10000 |  | 0 |  | ARB | SAN FRANCISCO | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | SANTA CLARA | SARATOGA | 2020-10-09 | Operator excavation damage | A service line with no excess flow valve installed | Steel | Vacuum Equipment with no Agreement | 0.75 | 60 | 57 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MGE UNDERGROUND | PASO ROBLES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Inadequate Excavation Practices
Pacific Gas and Electric | N | SANTA CLARA | SARATOGA | 2020-01-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1000 |  | 1 |  | GOMEZ PLUMBING | LOS BANOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SARATOGA | 2020-10-05 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 57 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | GEERï¿½S EXCAVATION | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SARATOGA | 2020-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1100 |  | 0 |  | SAN JOSE WATER | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SARATOGA | 2020-04-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 153 |  | 1 |  | C&G ELECTRIC | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SARATOGA | 2020-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | R B TRAVIS PLUMBING | LIVERMORE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SARATOGA | 2020-03-13 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 56 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | WEST VALLEY CONSTRUCTION | REDWOOD CITY | CA | N | Y | Yes | Yes | No | No | No | No | No | Facility was not located or marked
Pacific Gas and Electric | N | SANTA CLARA | SARATOGA | 2020-01-22 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 0.75 | 60 | 56 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | SANCO PIPELINES | LOS GATOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment
Pacific Gas and Electric | N | SANTA CLARA | SARATOGA | 2020-04-24 | Third party excavation damage | Main | Steel | Vacuum Equipment with no Agreement | 4 | 60 | 57 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | CALIFORNIA UTILITY COMPANY | SARATOGA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Inadequate Excavation Practices
Pacific Gas and Electric | N | SANTA CLARA | STANFORD | 2020-03-11 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 6 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4874 |  | 0 |  | PRESTON PIPELINES | MILPITAS | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment
Pacific Gas and Electric | N | SANTA CLARA | SUNNYVALE | 2020-01-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2177 |  | 1 |  | QUANTA TELE COMMUNICATIONS | HOUSTON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | SANTA CLARA | SUNNYVALE | 2020-03-04 | Third party excavation damage | Main | Steel | Not Available | 3 | 60 | 56 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | NA | NA | CA | N | Y | No | No | No | Yes | No | Yes | Yes | Inadequate Excavation Practices
Pacific Gas and Electric | N | SANTA CLARA | SUNNYVALE | 2020-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 804 |  | 1 |  | HOMEOWNER | SUNNYVALE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SUNNYVALE | 2020-06-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 796 |  | 1 |  | NOECON INC. | ALVISO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SUNNYVALE | 2020-06-26 | Third party excavation damage | Main | Steel | Hand Tools | 2 | 60 | 57 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | SANCO PIPELINES | LOS GATOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Dig with Care
Pacific Gas and Electric | N | SANTA CLARA | SUNNYVALE | 2020-10-19 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 4 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 220 |  | 0 |  | GUERRA CONSTRUCTION | SANTA CLARA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SUNNYVALE | 2020-10-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ELITE HOME REPAIR | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SUNNYVALE | 2020-05-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Augur | 0.75 | 60 | 57 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | MEDRANO ELECTRIC INC. | GILROY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Incorrect information or marks
Pacific Gas and Electric | N | SANTA CLARA | SUNNYVALE | 2020-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1590 |  | 1 |  | MEDALLION LANDSCAPING | MORGAN HILL | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CRUZ | APTOS | 2020-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1387 |  | 1 |  | FALL CREEK LANDSCAPE | CAPITOLA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | APTOS | 2020-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1034 |  | 1 |  | COSTA BELLA BUILDERS | SANTA CRUZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | APTOS | 2020-07-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 25 |  | 1 |  | HOMEOWNER | APTOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | APTOS | 2020-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 506 |  | 1 |  | GARCIA CONCRETE LIC#849964 | WATSONVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | APTOS | 2020-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1000 |  | 1 |  | HOMEOWNER | APTOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | BEN LOMOND | 2020-10-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | BEN LOMOND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | BEN LOMOND | 2020-10-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | BEN LOMOND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | BEN LOMOND | 2020-03-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 614 |  | 2 |  | HOMEOWNER | BEN LOMOND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | BEN LOMOND | 2020-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1958 |  | 1 |  | HOMEOWNER | BEN LOMOND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | BOULDER CREEK | 2020-03-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1081 |  | 1 |  | DAHLEN STRUCTURAL INC | SANTA CRUZ | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | SANTA CRUZ | CAPITOLA | 2020-12-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 27 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1524 |  | 1 |  | PUTNEY CONSTRUCTION | SOQUEL | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CRUZ | CAPITOLA | 2020-02-07 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 60 | 27 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 21430 |  | 3 |  | ANDERSON PACIFIC | SANTA CLARA | CA | N | Y | No | No | No | No | No | No | No | Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible
Pacific Gas and Electric | N | SANTA CRUZ | CAPITOLA | 2020-04-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | TOM RALSTON CONCRETE | SANTA CRUZ | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CRUZ | CAPITOLA | 2020-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1000 |  | 1 |  | BRAZIL CONSTRUCTION | SCOTTS VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | CAPITOLA | 2020-05-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 27 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7000 |  | 1 |  | ANDERSON PACIFIC | SCOTTS VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | SANTA CRUZ | FELTON | 2020-06-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 958 |  | 1 |  | HOMEOWNER | PRUNEDALE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | FELTON | 2020-10-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1000 |  | 1 |  | GOOD EARTH LANDSCAPE DESIGN | SANTA CRUZ | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CRUZ | LA SELVA BEACH | 2020-08-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1154 |  | 1 |  | EARTHWORKS | CAPITOLA | CA | N | Y | Yes | Yes | Yes | Yes | No | No | No | EXCAVATED OUTSIDE OF DELINEATED AREA
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2020-03-05 | Third party excavation damage | Main | Steel | Vacuum Equipment with no Agreement | 2 | 30 | 26 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | MGE UNDERGROUND | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Inadequate Excavation Practices
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2020-06-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 848 |  | 1 |  | RODRIGUEZ CONCRETE | MORGAN HILL | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2020-10-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | SANTA CRUZ | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2020-04-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1500 |  | 1 |  | PAUL STANGER | SANTA CRUZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2020-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 319 |  | 2 |  | DOGERTY CONSTRUCTION | SANTA CRUZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2020-02-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 807 |  | 0 |  | TORRES LANDSCAPING | APTOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2020-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 478 |  | 1 |  | COMMONS & BURK CONSTR. | SANTA CRUZ | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2020-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 121 |  | 1 |  | CITY OF SANTA CRUZ WATER DISTRUBUTION | SANTA CRUZ | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2020-05-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2865 |  | 1 |  | HOMEOWNER | SANTA CRUZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2020-09-03 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 51 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2682 |  | 2 |  | RMG UNDERGROUND | OAKLEY | CA | N | Y | No | No | No | No | No | No | No | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2020-08-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 500 |  | 1 |  | HOMEOWNER | SANTA CRUZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2020-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | BUDDY GRIGGS PLUMBING | SANTA CRUZ | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2020-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | KJ WOODS CONSTRUCTION | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2020-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2000 |  | 1 |  | MGE UNDERGROUND | SAN JOSE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2020-06-18 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3430 |  | 2 |  | MGE UNDERGROUND | PASO ROBLES | CA | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2020-04-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2175 |  | 1 |  | HOMEOWNER | SANTA CRUZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2020-02-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2475 |  | 1 |  | M.S. BUILDERS | SANTA CRUZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | SOQUEL | 2020-05-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3000 |  | 1 |  | GARNEY CONSTRUCTION | MONTEREY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CRUZ | SOQUEL | 2020-09-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 500 |  | 1 |  | HOMEOWNER | SOQUEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | SOQUEL | 2020-09-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1430 |  | 1 |  | HOMEOWNER | SOQUEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | SOQUEL | 2020-05-18 | Third party excavation damage | Main | Polyethylene Pipe | Probing Device | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1522 |  | 5 |  | GARNEY CONSTRUCTION | SCOTTS VALLEY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CRUZ | SOQUEL | 2020-03-18 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 0.75 | 50 | 44 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | NA | NA | CA | N | Y | No | No | No | Yes | No | Yes | Yes | Inadequate Excavation Practices
Pacific Gas and Electric | N | SANTA CRUZ | TWIN LAKES | 2020-08-04 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3685 |  | 19 |  | JOHNSON AND COMPANY | SANTA CRUZ | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CRUZ | WATSONVILLE | 2020-11-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1338 |  | 1 |  | QUEZADA CONSTRUCTION | HOLLISTER | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CRUZ | WATSONVILLE | 2020-06-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1575 |  | 3 |  | HOMEOWNER | WATSONVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | WATSONVILLE | 2020-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1980 |  | 1 |  | HOMEOWNER | WATSONVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | WATSONVILLE | 2020-10-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.75 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | HOMEOWNER | WATSONVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | WATSONVILLE | 2020-06-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1306 |  | 1 |  | HOMEOWNER | WATSONVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | WATSONVILLE | 2020-03-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 505 |  | 3 |  | MR. ROOTER | WATSONVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | SHASTA | REDDING | 2020-10-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2770 |  | 2 |  | CAMCO CONSTRUCTION | REDDING | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SHASTA | REDDING | 2020-06-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2882 |  | 1 |  | HOMEOWNER | REDDING | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SHASTA | REDDING | 2020-11-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2500 |  | 0 |  | CUSTOM CONCRETE | RED BLUFF | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SHASTA | REDDING | 2020-07-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1205 |  | 0 |  | LAHR CONSTRUCTION | REDDING | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SHASTA | REDDING | 2020-04-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1000 |  | 1 |  | COX & COX INC | REDDING | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SHASTA | REDDING | 2020-12-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 451 |  | 0 |  | SEEGERT CONSTRUCTION | WEST SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SHASTA | REDDING | 2020-11-04 | Third party excavation damage | Main | Steel | Miscellaneous/Other | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 14404 |  | 3 |  | CITY OF REDDING | REDDING | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SHASTA | REDDING | 2020-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 995 |  | 8 |  | AXNER EXCAVATING | REDDING | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SHASTA | REDDING | 2020-05-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2992 |  | 0 |  | MUSE CONCRETE | REDDING | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SHASTA | REDDING | 2020-01-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 953 |  | 1 |  | EDDIE AXNER CONSTRUCTION | REDDING | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | SHASTA | REDDING | 2020-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1931 |  | 0 |  | MD SITE GRADING | RED BLUFF | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SHASTA | REDDING | 2020-02-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1652 |  | 2 |  | HOMEOWNER | REDDING | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SHASTA | REDDING | 2020-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1000 |  | 0 |  | HOMEOWNER | REDDING | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SHASTA | REDDING | 2020-03-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 759 |  | 0 |  | LAHR CONSTRUCTION | REDDING | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SHASTA | REDDING | 2020-04-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | LAHR CONSTRUCTION | REDDING | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Incorrect facility records/maps
Pacific Gas and Electric | N | SHASTA | REDDING | 2020-04-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1369 |  | 0 |  | LAHR CONSTRUCTION | REDDING | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | SHASTA | REDDING | 2020-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1000 |  | 1 |  | MARK BEHNKE CONSTRUCTION | PALO CEDRO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SHASTA | REDDING | 2020-04-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1049 |  | 0 |  | LAHR CONSTRUCTION | REDDING | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SHASTA | REDDING | 2020-07-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1345 |  | 0 |  | VINGENZO COLLETI | SHINGLETOWN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SHASTA | REDDING | 2020-04-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2094 |  | 0 |  | SHASTA DESIGN SCAPES | SHASTA LAKE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SHASTA | REDDING | 2020-04-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1604 |  | 0 |  | BUILT UP CONSTRUCTION | REDDING | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SHASTA | REDDING | 2020-02-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2099 |  | 0 |  | SHASTA DESIGNSCAPE | SHASTA LAKE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | BENICIA | 2020-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 425 |  | 1 |  | G&G DECK AND FENCE | PLEASANT HILL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | BENICIA | 2020-07-15 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1652 |  | 3 |  | UNDERGROUND CONSTRUCTION | BENICA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SOLANO | BENICIA | 2020-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2897 |  | 4 |  | RICK BROWN CONSTRUCTION | BENICIA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | BENICIA | 2020-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 100 |  | 2 |  | HOMEOWNER | BENICIA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | BENICIA | 2020-11-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3660 |  | 0 |  | TRI VALLEY EXCAVATING | SUNOL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | DIXON | 2020-07-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | HOMEOWNER | DIXON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | DIXON | 2020-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4491 |  | 1 |  | C&R CONCRETE CONSTRUCTION | WOODLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | DIXON | 2020-05-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 18619 |  | 1 |  | HOMEOWNER | DIXON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | DIXON | 2020-05-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1603 |  | 2 |  | FRANCISCO''S LANDSCAPING | CONCORD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SOLANO | DIXON | 2020-07-29 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5683 |  | 0 |  | JUAN''S EXCAVATING SERVICE | OLIVEHURST | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | FAIRFIELD | 2020-12-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 791 |  | 1 |  | GOLD COAST PIPELINE | PITTSBURG | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SOLANO | FAIRFIELD | 2020-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | HOMEOWNER | FAIRFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | FAIRFIELD | 2020-08-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2215 |  | 1 |  | CB PLUMBING | KELSEYVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | FAIRFIELD | 2020-09-29 | Third party excavation damage | Riser | Polyethylene Pipe | Miscellaneous/Other | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2799 |  | 1 |  | NA | NA | CA | N | Y | No | No | No | No | No | No | No | VANDALISM
Pacific Gas and Electric | N | SOLANO | FAIRFIELD | 2020-07-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4573 |  | 1 |  | ALEJANDRO''S PLUMBING | FAIRFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | FAIRFIELD | 2020-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 50 | 44 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | CITY OF FAIRFIELD | FAIRFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment
Pacific Gas and Electric | N | SOLANO | FAIRFIELD | 2020-04-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2004 |  | 2 |  | MOUNTAIN CASCADE | LIVERMORE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SOLANO | FAIRFIELD | 2020-11-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | FAIRFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | FAIRFIELD | 2020-06-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1137 |  | 1 |  | HOMEOWNER | FAIRFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | FAIRFIELD | 2020-10-16 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 6 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | K.O UNDERGROUND CONST INC. | WINTERS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SOLANO | FAIRFIELD | 2020-01-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1000 |  | 1 |  | PARIDISE VALLEY MAINTENANCE | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | RIO VISTA | 2020-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1968 |  | 1 |  | HOMEOWNER | RIO VISTA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | RIO VISTA | 2020-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | RIO VISTA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | SUISUN CITY | 2020-05-05 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | VACA VALLEY EXCAVATING AND TRUCKING | VACAVILLE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SOLANO | SUISUN CITY | 2020-04-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4180 |  | 1 |  | HOMEOWNER | SUISUN CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | VACAVILLE | 2020-08-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2187 |  | 1 |  | HOMEOWNER | VACAVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | VACAVILLE | 2020-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3000 |  | 2 |  | HOMEOWNER | VACAVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | VACAVILLE | 2020-04-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1616 |  | 2 |  | HOMEOWNER | VACAVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | VACAVILLE | 2020-02-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2147 |  | 1 |  | GREG MILLAM MASONRY | VACAVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | VACAVILLE | 2020-02-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1685 |  | 1 |  | A2Z LANDSCAPING | VACAVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SOLANO | VACAVILLE | 2020-07-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1217 |  | 1 |  | WMA LAND SCAPPING | LIVERMORE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | VACAVILLE | 2020-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | VACAVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | VACAVILLE | 2020-09-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1751 |  | 1 |  | HOMEOWNER | VACAVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | VACAVILLE | 2020-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 51 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 640 |  | 1 |  | HOMEOWNER | VACAVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | VACAVILLE | 2020-03-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 51 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 762 |  | 1 |  | LLOYD''S FENCING | FAIRFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | VALLEJO | 2020-11-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 25 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | VALLEJO | CA | N | Y | No | No | No | No | No | No | No | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | SOLANO | VALLEJO | 2020-06-13 | Third party excavation damage | Main | Steel | Hand Tools | 2 | 25 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2395 |  | 0 |  | UP 2 CODE | BENECIA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | VALLEJO | 2020-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1792 |  | 0 |  | CITY OF VALLEJO | VALLEJO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | VALLEJO | 2020-03-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 1 | 25 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3426 |  | 1 |  | VALLEJO WATER DEPT | VALLEJO | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | CLOVERDALE | 2020-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | PIAZZA CONSTRUCTION | SONOMA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | SONOMA | COTATI | 2020-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1846 |  | 4 |  | PAVEMENT RECYCLING SYSTEMS | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | COTATI | 2020-11-19 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 121800 |  | 0 |  | ACCU-BORE DIRECTIONAL | BENICIA | CA | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | FETTERS HOT SPRINGS-AGUA CALIENTE | 2020-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 2 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 13887 |  | 1 |  | EMH CONSTRUCTION | SONOMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | GEYSERVILLE | 2020-05-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1130 |  | 0 |  | NORTHWEST GENERAL ENGINEERING | SANTA ROSA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | GEYSERVILLE | 2020-10-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2254 |  | 0 |  | DANIEL RONCHELLI INC | PETALUMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | GRATON | 2020-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1643 |  | 1 |  | HOMEOWNER | SEBASTOPOL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | HEALDSBURG | 2020-05-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | SUTTON EXCAVATING | SANTA ROSA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | No USA Ticket
Pacific Gas and Electric | N | SONOMA | HEALDSBURG | 2020-12-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3885 |  | 1 |  | CHAPMAN CONSTRUCTION | HEALDSBURG | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | HEALDSBURG | 2020-05-26 | Third party excavation damage | Main | Steel | Augur | 4 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 120573 |  | 300 |  | AT&T | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | SONOMA | HEALDSBURG | 2020-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 865 |  | 1 |  | CONLEY PLUMBING | HEALDSBURG | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | HEALDSBURG | 2020-06-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1026 |  | 0 |  | STAGGS | SEBASTOPOL | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | HEALDSBURG | 2020-05-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SHOOK AND WALLER | WINDSOR | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | HEALDSBURG | 2020-12-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ARGONAUT CONSTRUCTORS | SANTA ROSA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | KENWOOD | 2020-01-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2218 |  | 2 |  | DIRT FARMER & CO | KENWOOD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | PETALUMA | 2020-07-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2637 |  | 1 |  | SOL LANDSCAPES | PETALUMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | PETALUMA | 2020-02-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1534 |  | 1 |  | HOMEOWNER | PETALUMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | PETALUMA | 2020-12-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1125 |  | 1 |  | NOR CAL SOLAR | PETALUMA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | PETALUMA | 2020-02-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 921 |  | 1 |  | MITCHELL LANDSCAPE INC | PETALUMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | PETALUMA | 2020-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2548 |  | 1 |  | GARCIA LANDSCAPING SERVICES | NOVATO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | PETALUMA | 2020-04-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2388 |  | 1 |  | EDT TEC | PETALUMA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | SONOMA | PETALUMA | 2020-02-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1462 |  | 1 |  | MIKE BROWN ELECTRIC | COTATI | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | PETALUMA | 2020-08-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2617 |  | 1 |  | CENTURY FENCING | WINDSOR | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | PETALUMA | 2020-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 50 | 44 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | MITCHELL LANDSCAPING | PETALUMA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Dig with Care
Pacific Gas and Electric | N | SONOMA | PETALUMA | 2020-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 884 |  | 0 |  | LAFFERTY COMMUNITIES | SAN RAMON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | PETALUMA | 2020-11-05 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3233 |  | 0 |  | COASTSIDE CONCRETE | SANTA ROSA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | SONOMA | ROHNERT PARK | 2020-07-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 944 |  | 0 |  | HOMEOWNER | ROHNERT PARK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | ROHNERT PARK | 2020-10-01 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1000 |  | 0 |  | D&M | PETALUMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2020-02-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1766 |  | 0 |  | HOMEOWNER | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2020-04-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 354 |  | 1 |  | HOMEOWNER | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2020-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 358 |  | 1 |  | STACY & WITBECK INC | ALAMEDA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2020-08-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3177 |  | 1 |  | HOMEOWNER | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2020-09-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2019 |  | 2 |  | ST FRANCIS ELECTRIC | SAN LEANDRO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2020-05-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 152 |  | 1 |  | HOMEOWNER | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2020-05-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 792 |  | 0 |  | REYFF ELECTRIC | ROHNERT PARK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2020-06-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 956 |  | 1 |  | GHILOTTI CONSTRUCTION | SAN RAFAEL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2020-06-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 982 |  | 0 |  | POWER POLE CO | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2020-09-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3889 |  | 0 |  | HOMEOWNER | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2020-11-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1562 |  | 1 |  | NORTHWEST GENERAL ENGINEERING | SANTA ROSA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2020-12-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1562 |  | 1 |  | CMC CONCRETE INC | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2020-05-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 126 |  | 1 |  | HOMEOWNER | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2020-06-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1904 |  | 1 |  | HOMEOWNER | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2020-11-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2866 |  | 0 |  | HOMEOWNER | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2020-03-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 999 |  | 0 |  | HOMEOWNER | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SEBASTOPOL | 2020-12-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 910 |  | 1 |  | HOMEOWNER | SEBASTOPOL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | SEBASTOPOL | 2020-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1267 |  | 1 |  | HOMEOWNER | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SEBASTOPOL | 2020-03-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1689 |  | 2 |  | HOMEOWNER | SEBASTOPOL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SEBASTOPOL | 2020-10-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | STILLPOINT INC. | SANTA ROSA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | SEBASTOPOL | 2020-05-23 | Third party excavation damage | Riser | Steel | Farm Equipment | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1986 |  | 0 |  | HOMEOWNER | SEBASTOPOL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SONOMA | 2020-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | TRIANGLE EXCAVATION | DIXON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment
Pacific Gas and Electric | N | SONOMA | SONOMA | 2020-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 42 | 36 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | HOMEOWNER | SONOMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SONOMA | 2020-02-06 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3441 |  | 0 |  | HOMEOWNER | SONOMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SONOMA | 2020-11-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 928 |  | 1 |  | HOMEOWNER | SONOMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SONOMA | 2020-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3824 |  | 1 |  | M3 INTEGRATED SERVICES | SANTA ROSA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | SONOMA | 2020-03-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1430 |  | 1 |  | BLUE BAY CONSTRUCTION | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SONOMA | 2020-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 42 | 36 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | HOMEOWNER | SONOMA | CA | N | Y | No | No | No | No | No | No | No | No USA Ticket
Pacific Gas and Electric | N | SONOMA | TEMELEC | 2020-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 895 |  | 1 |  | LIFESCAPING | SACRAMENTO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | SONOMA | WINDSOR | 2020-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | STAGGS CONTRACTOR | SEBASTOPOL | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | FAILED TO MAINTAIN MARKS
Pacific Gas and Electric | N | STANISLAUS | CERES | 2020-09-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2631 |  | 2 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | CERES | 2020-08-31 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2159 |  | 1 |  | ROLFE CONSTRUCTION | ATWATER | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | STANISLAUS | CERES | 2020-08-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1869 |  | 2 |  | TID | TURLOCK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | CERES | 2020-04-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 25 |  | 1 |  | HOMEOWNER | CERES | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | CERES | 2020-12-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 950 |  | 0 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | CERES | 2020-04-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 996 |  | 1 |  | FALANY FENCE | MERCED | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | CERES | 2020-05-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5000 |  | 1 |  | COLLINS ELECTRIC | STOCKTON | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | CERES | 2020-04-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1783 |  | 0 |  | HOMEOWNER | CERES | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | DEL RIO | 2020-03-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1306 |  | 1 |  | HENDRIX LANDSCAPE | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | DENAIR | 2020-02-22 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1429 |  | 0 |  | HOMEOWNER | DENAIR | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | HICKMAN | 2020-04-30 | Third party excavation damage | Main | Steel | Vacuum Equipment with no Agreement | 4 | 60 | 54 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | INDEPENDENT IRRIGATION SYSTEMS | ATWATER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Dig with Care
Pacific Gas and Electric | N | STANISLAUS | HUGHSON | 2020-12-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 765 |  | 0 |  | HOMEOWNER | DENAIR | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | HUGHSON | 2020-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 1 |  | TREVOR GARNETT | HUGHSON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | STANISLAUS | KEYES | 2020-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2890 |  | 0 |  | HOLIDAY CONSTRUCTION | KEYES | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | KEYES | 2020-01-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1093 |  | 1 |  | HOMEOWNER | KEYES | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2020-11-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1030 |  | 1 |  | M I ELECTRIC | MODESTO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2020-09-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1515 |  | 1 |  | MEDINAS WELDING | MODESTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2020-10-30 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 15783 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2020-05-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 12000 |  | 0 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2020-07-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1004 |  | 1 |  | UNITED PAVING | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2020-05-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1386 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2020-03-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1840 |  | 0 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2020-04-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 12000 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2020-09-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1496 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2020-01-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1000 |  | 1 |  | ALECO ELECTRIC | VACAVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2020-07-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 794 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2020-10-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 425 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2020-01-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1466 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2020-09-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 775 |  | 2 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2020-09-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 181 |  | 0 |  | JANOVICH ELECTRIC | NA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2020-11-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1589 |  | 1 |  | PROGRESSIVE EXCAVATION & GRADING INC | HILMAR | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2020-11-12 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1879 |  | 0 |  | HALEY UNDERGROUND | MODESTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2020-11-03 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2922 |  | 0 |  | HALEY UNDERGROUND | MODESTO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INCORRECT INFORMATION OR MARKS
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2020-10-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3407 |  | 0 |  | MOZINGO CONTRUCTION | OAKDALE | CA | N | Y | Yes | Yes | No | No | No | No | No | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2020-10-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2020-10-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | HOMEOWNER | MODESTO | CA | N | Y | Yes | No | Yes | Yes | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2020-04-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1425 |  | 0 |  | DA WOODS | OAKDALE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2020-06-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1311 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2020-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2298 |  | 2 |  | TITAN FENCE | MODESTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2020-11-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1000 |  | 2 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2020-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1673 |  | 1 |  | TONYS PLUMBING SERVICE | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2020-11-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2000 |  | 2 |  | ADAMS UNDERGROUND | WATERFORD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2020-09-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 2 |  | HOMEOWNER | MODESTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2020-04-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2474 |  | 0 |  | SALS PLUMBING | TURLOCK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | EXCAVATED OUTSIDE OF DELINEATED AREA
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2020-07-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1317 |  | 1 |  | ROLFE CONSTRUCTION | ATWATER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2020-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 808 |  | 1 |  | ROLFE CONSTRUCTION | ATWATER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2020-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1829 |  | 2 |  | SYNERGIES TECH SERVICES | MODESTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2020-04-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 112 |  | 0 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2020-05-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1436 |  | 0 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2020-05-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1528 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2020-04-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 25 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2020-03-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 346 |  | 3 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2020-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 4 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9701 |  | 0 |  | PLATINUM PIPELINE | LIVERMORE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2020-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1637 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2020-08-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1815 |  | 2 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2020-11-24 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | PG&E | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Inadequate Excavation Practices
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2020-07-29 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7813 |  | 2 |  | VAN DUYN FAMILY FARMS | RIPON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | OAKDALE | 2020-10-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | LAYMAN ELECTRIC | MODESTO | CA | N | Y | Yes | Yes | Yes | Yes | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | OAKDALE | 2020-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3756 |  | 0 |  | HOMEOWNER | OAKDALE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | OAKDALE | 2020-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Augur | 0.75 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2276 |  | 1 |  | HOMEOWNER | OAKDALE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | OAKDALE | 2020-09-29 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 4 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1052 |  | 0 |  | UNITED PAVEMENT | HUGHSON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | OAKDALE | 2020-09-28 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 714 |  | 0 |  | HALEY UNDERGROUND CONSTRUCTION | MODESTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | PATTERSON | 2020-07-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1582 |  | 1 |  | THORSEN''S-NORQUIST INC | TURLOCK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | PATTERSON | 2020-04-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1107 |  | 1 |  | STANISLAUS PLUMBING INC | CERES | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | PATTERSON | 2020-01-03 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4020 |  | 1 |  | DALEO INC | GILROY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | SALIDA | 2020-08-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2464 |  | 1 |  | HOMEOWNER | SALIDA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | SALIDA | 2020-08-23 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1887 |  | 4 |  | HOMEOWNER | SALIDA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | SHACKELFORD | 2020-01-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2008 |  | 0 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | TURLOCK | 2020-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Farm Equipment | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5943 |  | 0 |  | HOMEOWNER | TURLOCK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | TURLOCK | 2020-08-04 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2642 |  | 0 |  | SWAN POOLS | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | TURLOCK | 2020-07-08 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2186 |  | 0 |  | CITY OF TURLOCK | TURLOCK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | STANISLAUS | TURLOCK | 2020-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3000 |  | 1 |  | HOMEOWNER | TURLOCK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | TURLOCK | 2020-10-14 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 6 | 60 | 54 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MHK CONSTRUCTION INC. | HUGHSON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | NOT MARKED CORRECTLY
Pacific Gas and Electric | N | STANISLAUS | TURLOCK | 2020-01-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 907 |  | 1 |  | COLLINS ELECTRIC | STOCKTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | TURLOCK | 2020-11-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3009 |  | 1 |  | HOMEOWNER | TURLOCK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | TURLOCK | 2020-08-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 633 |  | 1 |  | OAKDALE FENCE COMPANY | OAKDALE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | TURLOCK | 2020-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1653 |  | 1 |  | HOMEOWNER | TURLOCK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | WATERFORD | 2020-04-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1106 |  | 1 |  | HOMEOWNER | WATERFORD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SUTTER | LIVE OAK | 2020-09-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1828 |  | 1 |  | DESILVA GATES | DUBLIN | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SUTTER | LIVE OAK | 2020-11-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3636 |  | 1 |  | HAMMOND ELECTRIC | YUBA CITY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | USA NOT CALLED
Pacific Gas and Electric | N | SUTTER | WHEATLAND | 2020-12-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 56 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | WHEATLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SUTTER | YUBA CITY | 2020-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 572 |  | 1 |  | HOMEOWNER | YUBA CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SUTTER | YUBA CITY | 2020-10-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DARREN TAYLOR CONST. | ANDERSON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SUTTER | YUBA CITY | 2020-07-25 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10118 |  | 0 |  | ELITE PLUMBING | ELVERTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SUTTER | YUBA CITY | 2020-06-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 132 |  | 1 |  | FLETCHERS PLUMBING | YUBA CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SUTTER | YUBA CITY | 2020-10-15 | Third party excavation damage | Main | Steel | Grader/Scraper | 4 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 30527 |  | 16 |  | TAYLOR CONCRETE CONSTRUCTION | YUBA CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | TEHAMA | RED BLUFF | 2020-05-06 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4490 |  | 4 |  | NA | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | TEHAMA | RED BLUFF | 2020-03-24 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2130 |  | 0 |  | C & K BUILDERS | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YOLO | DAVIS | 2020-07-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | GTO CONSTRUCTION | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | YOLO | DAVIS | 2020-04-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 178 |  | 1 |  | HOMEOWNER | DAVIS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YOLO | DAVIS | 2020-10-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | POWER PLUS | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | YOLO | DAVIS | 2020-10-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 25 |  | 1 |  | HOMEOWNER | DAVIS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YOLO | DAVIS | 2020-07-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | WELLS POOLS | RANCHO CORDOVA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YOLO | DAVIS | 2020-04-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4257 |  | 1 |  | HOMEOWNER | DAVIS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YOLO | DAVIS | 2020-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1999 |  | 1 |  | CASTILLO FENCING | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATED PRIOR TO POSITIVE CONTACT
Pacific Gas and Electric | N | YOLO | DAVIS | 2020-11-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1202 |  | 1 |  | BAY CITIES PAVING AND GRADING INC | CONCORD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | YOLO | DAVIS | 2020-05-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2572 |  | 1 |  | TAK COMMUNITCATIONS AARON WURZ | SACRAMENTO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | YOLO | DAVIS | 2020-06-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1903 |  | 1 |  | HOMEOWNER | CARMICHAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YOLO | DAVIS | 2020-02-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1497 |  | 1 |  | MINERVA PREPERTIES INC | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YOLO | DAVIS | 2020-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1540 |  | 1 |  | PRO-MAX PLUMBING | ESPARTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YOLO | WEST SACRAMENTO | 2020-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3000 |  | 2 |  | HOMEOWNER | WEST SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YOLO | WEST SACRAMENTO | 2020-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5328 |  | 0 |  | HOMEOWNER | WEST SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YOLO | WEST SACRAMENTO | 2020-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2695 |  | 1 |  | HOMEOWNER | WEST SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YOLO | WEST SACRAMENTO | 2020-02-19 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 50 | 44 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | HOMEOWNER | WEST SACRAMENTO | CA | N | Y | No | No | No | No | No | Yes | Yes | Failed to Protect, Support or Remove Subsurface Installation While Excavation Is Open to Safeguard Employees
Pacific Gas and Electric | N | YOLO | WEST SACRAMENTO | 2020-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Directional Drilling | 0.75 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 36021 |  | 1 |  | PIONEER UNDERGROUND CONSTRUCTION | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | YOLO | WEST SACRAMENTO | 2020-01-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1000 |  | 1 |  | NORCAL RAMJACK | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | YOLO | WEST SACRAMENTO | 2020-02-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3172 |  | 1 |  | HOMEOWNER | WEST SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | NO USA TICKET
Pacific Gas and Electric | N | YOLO | WEST SACRAMENTO | 2020-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4158 |  | 1 |  | SACRAMENTO SEWER AND DRAIN | PLACERVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YOLO | WEST SACRAMENTO | 2020-01-02 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3534 |  | 0 |  | CITY OF WEST SACRAMENTO | WEST SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | YOLO | WINTERS | 2020-10-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | WINTERS PUBLIC WORKS | WINTERS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | YOLO | WOODLAND | 2020-07-09 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 2 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 3 |  | CJB CONSTRUCTION | WOODLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YOLO | WOODLAND | 2020-02-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 753 |  | 2 |  | NICHOLS PLUMBING | WOODLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | YOLO | WOODLAND | 2020-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 50 | 46 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CITY OF WOODLAND | WOODLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | YOLO | WOODLAND | 2020-06-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 715 |  | 1 |  | HOMEOWNER | WOODLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YOLO | WOODLAND | 2020-02-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Vacuum Equipment with Agreement | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 330 |  | 1 |  | CITY OF WOODLAND | WOODLAND | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | YOLO | WOODLAND | 2020-09-03 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 46613 |  | 1 |  | BAILEYS TRENCHLESS INC | WOODLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | YOLO | WOODLAND | 2020-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Vacuum Equipment with Agreement | 0.5 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4054 |  | 1 |  | GOLDEN STATE UTILITY | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | YOLO | WOODLAND | 2020-08-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2845 |  | 1 |  | HOMEOWNER | WOODLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YOLO | WOODLAND | 2020-06-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2815 |  | 1 |  | HOMEOWNER | WOODLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YOLO | WOODLAND | 2020-08-11 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2259 |  | 2 |  | MICHELS | RIO VISTA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | YOLO | WOODLAND | 2020-02-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3578 |  | 2 |  | HOMEOWNER | WOODLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YOLO | WOODLAND | 2020-04-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2214 |  | 1 |  | PREMIER POOLS AND SPAS | RANCHO CORDOVA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | YUBA | LINDA | 2020-02-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1321 |  | 1 |  | HOMEOWNER | MARYSVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YUBA | MARYSVILLE | 2020-07-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1703 |  | 1 |  | PLUMBING DOCTOR | YUBA CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YUBA | MARYSVILLE | 2020-10-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2397 |  | 1 |  | HOMEOWNER | MARYSVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | YUBA | OLIVEHURST | 2020-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1000 |  | 1 |  | DUDLEYS EXCAVATING INC | GERBER | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | YUBA | OLIVEHURST | 2020-03-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Vacuum Equipment with no Agreement | 0.5 | 54 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2030 |  | 1 |  | YUBA COUNTY PLUBIC WORKS | MARYSVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | YUBA | OLIVEHURST | 2020-08-12 | Third party excavation damage | Main | Steel | Miscellaneous/Other | 2 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7795 |  | 4 |  | ROCK MORGAN ENTERPRISES | IONE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | YUBA | OLIVEHURST | 2020-10-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1991 |  | 0 |  | HOMEOWNER | OLIVEHURST | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | Y | MENDOCINO | UKIAH | 2020-08-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1933 |  | 6 |  | ST FRANCIS ELECTRIC | SAN LEANDRO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | Y | SANTA CLARA | SAN JOSE | 2020-01-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 57 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | -504 |  | 5 |  | ELECTRIC TECH CONSTRUCTION | CONCORD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | ABANDONED/DEACTIVATED FACILTY ISSUE
San Diego Gas and Electric | N | SAN DIEGO | ALPINE | 2020-08-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | NEW WEST INVESTMENT GROUP | EL CAJON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 1 inch poly with ditch witch
San Diego Gas and Electric | N | SAN DIEGO | BONITA | 2020-11-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | ROGELIO SALINAS | LA MESA | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging fr a culvert
San Diego Gas and Electric | N | SAN DIEGO | CARDIFF | 2020-08-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | CONTRACTOR WORKING FOR HOMEOWNER | CARDIFF | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was trenching to install deck drains when they hit the 0.5 inch poly service.
San Diego Gas and Electric | N | SAN DIEGO | CARDIFF | 2020-09-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | DAVID SALAZAR | CARDIFF | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 0.5 inch PE with pole hole digger.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2020-09-12 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2674 |  |  | NA | WALTON BROS | MURRIETA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor digging to install electric conduit hit 0.75 inch steel stub. Service is marked in the sidewalk from previous mark out. Service was RFSD at some point and the stub extended past PL. Maps show servicer is still active. Locator tried contacting NC supervision to see if service was RFSD, due to the general contractor stating the service was RFSD at the main.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2020-05-22 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 11740 |  |  | NA | SELECT ELECTRIC | VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor using a backhoe with an auger attachment drilled into the 4 inch poly main
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2020-12-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | Y | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | ED CICONE | CARLSBAD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failure to use adequate caution while digging near gas service.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2020-06-23 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3023 |  |  | NA | CONSTRU ONE GENERAL ENGINEERING | ONTARIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor boring for communication bored into a 2 inch poly stub causing a Broken and Blowing.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2020-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3023 |  |  | NA | RIVERSIDE DIRECTIONAL DRILLING | RIVERSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hit 2 inch PE stub with boring drill
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2020-03-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | PR FRAME CONSTRUCTION | VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was digging with a shovel to upgrade the gas and electric to the house when they hit the 0.5inch poly service causing a B B
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2020-02-14 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3023 |  |  | NA | INLAND VALLEY PIPELINE | TEMECULA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor digging with a backhoe to install dry utilities struck the 2 poly tee causing a B B Failed to pot by hand
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2020-03-05 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3023 |  |  | NA | PACIFIC PRODUCTION PLUMBING | RIVERSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor digging with a backhoe to install wet utilities to a new housing track hit the 2 poly main causing a bnb
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2020-12-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | DEL RANCHO POOLS | ENCINITAS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Cut 0.5 inch PE Service with sawzaw while installing gas line for pool
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2020-12-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1732 |  | 2 |  | MARIO AVILES | WHITTIER | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA, did not pothole
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2020-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | PETER SALAMEH | CARLSBAD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was digging a hole with a shovel to plant a tree when he hit the 0.5 inch poly service causing a Broken and Blowing.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2020-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | LEO CRUZ | VISTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging with a shovel for an irrigation line hit the 0.5 inch poly service.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2020-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1651 |  | 4 |  | DENIS TRAGER | LAKE HAVASU CITY | AZ | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Property owner had landscapers digging to install a new tree when they severed the 0.5 inch poly service with a digging bar.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2020-05-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | COOKSON ENTERPRISES INC | ESCONDIDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was shading the 1 inch poly service when they hit it causing a Broken and Blowing with a shovel.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2020-02-19 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3023 |  |  | NA | SCHILLING PARADISE | EL CAJON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging with a backhoe to do tie ins for natural gas mains hit the 2 poly main
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2020-01-06 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 11740 |  |  | NA | HENKELS AND MCCOY INC | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was digging to install a communication box when they hit the 4 poly main
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2020-01-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3093 |  | 1 |  | FYDAQ | FULLERTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging with a backhoe to install wet utilities severed the 2 poly main
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2020-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | SALVADOR ALMIRANO | NA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Failure to use caution while digging near gas service.
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2020-01-16 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 4 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 11810 |  | 1 |  | CHRIS FORDYCE | CHULA VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On 01 16 2020, a third party damage occurred on a 4inch plastic gas main at 1120 Eastlake Pkwy, Chula Vista, by a contractor driving in a fence stake for a grading project. SDGE crews responded, controlled the gas, and made permanent repairs by replacing a section of main. There were no injuries nor further damages resulted from this incident. Investigation of the incident revealed the gas line was properly marked, however, the contractor failed to maintain marked facilities which resulted in the damage. This incident was reported to the CPUC when SDGE became aware of media coverage
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2020-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  | 0 |  | BEN ALLEN | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | On 05-06-2020, SDG E received a report of a third-party damage on a 1-inch plastic gas service at 1266 3rd Ave, Chula Vista. The third-party contractor had fully exposed the 1-inch gas service line before dropping a rebar cage into the hole which damaged the gas service. Company crews responded, controlled the gas, and made permanent repairs by removing the damaged section and fusing a 1-inch coupling. There were no injuries or further damages resulting from this incident. Investigation of the incident showed that there was no valid USA ticket for the contractor. This incident was reported to the CPUC due to the release of gas and major media coverage.
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2020-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | RANCHO PAVING | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failure to use caution while excavating.
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2020-04-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | CHRIS WARBURTON | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit gas line while installing new houseline
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2020-02-05 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3023 |  |  | NA | BRIGHT VIEW LANDSCAPE | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failure to pothole prior to excavation
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2020-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2674 |  |  | NA | JAIRO HERRERA | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 0.75 inch stub snapped at squeeze
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2020-04-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 15064 |  | 177 |  | ESTELI GRIJALVA | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On 04-11-20, SDGE was made aware of a third party damage at 360 H St, Chula Vista. The third party contractor was boring to install conduit, hit an unexposed 0.75-inch steel gas line, causing a release of gas. SDGE personnel were sent to the scene to control the gas. Gas was controlled on 04-11-20 at 2 37PM. There were no injuries nor further damage reported due to the release of gas. At 11 03AM this morning 04-13-20, SDGE was made aware of media coverage on this incident. This is being reported to the CPUC due to SDGE becoming aware of media coverage.
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2020-08-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5252 |  |  | NA | ESTELI GRIJALVA | EL CAJON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Unknown as contractor hit 2 inch main and did not notify anyone
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2020-07-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | SOUTHERN CONTRACTING | SAN MARCOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failure to use caution while digging near gas facilities.
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2020-03-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | NICK CASILLAS | CHULA VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hot 0.5inch PE service with shovel
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2020-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | JUSTIN MAXWELL | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging to install solar 3rd party contractor hit 0.5 inch poly
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2020-09-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1755 |  | 3 |  | CCL CONTRACTING | ESCONDIDO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On 9/23/2020 CCL a third party contractor damaged a 1 inch plastic service at Plaza Bonita Rd and Bonita Rd in Chula Vista while potting for gas service. Gas crews responded and controlled gas at 05:36. There were no injuries or fatalities resulting from this incident. This incident was reported to CPUC due to the release of natural gas and media coverage.
San Diego Gas and Electric | N | SAN DIEGO | CORONADO | 2020-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | LONNIE JAMES | EL CAJON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Not calling 811 USA
San Diego Gas and Electric | N | SAN DIEGO | CORONADO | 2020-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | ZMK CONSTRUCTION | ESCONDIDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 1 inch PE Service while digging to lower water.
San Diego Gas and Electric | N | SAN DIEGO | CORONADO | 2020-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | MEZZ CONSTRUCTION | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Cracked 1 inch PE service with shovel
San Diego Gas and Electric | N | SAN DIEGO | CORONADO | 2020-07-13 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2744 |  | 1 |  | JOSE CARDENAS | TEMECULA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation.
San Diego Gas and Electric | N | SAN DIEGO | CORONADO | 2020-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | FARO LAFATA ENTERPRISES | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failure to use caution while digging near facility.
San Diego Gas and Electric | N | SAN DIEGO | CORONADO | 2020-11-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | MG LIFETIME CONSTRUCTION INC | VALLEY CENTER | CA | N | Y | Yes | No | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was excavating to install electrical conduit
San Diego Gas and Electric | N | SAN DIEGO | CORONADO | 2020-02-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | JOE BELMONTE | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1 PE Service hit by contractor
San Diego Gas and Electric | N | SAN DIEGO | DEL MAR | 2020-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2674 |  |  | NA | FORREST CONTRACTING | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was cutting roots out of the way while digging a hole for deck support when they cut into the 0.75 inch steel service with a saw zaw.
San Diego Gas and Electric | N | SAN DIEGO | DEL MAR | 2020-05-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | JOSH HOLMES | VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | potholing lines to run electric
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2020-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2814 |  | 2 |  | DAVID SANCHEZ | EL CAJON | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 0.75 inch steel service with jackhammer
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2020-03-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | VICTOR LOPEZ | NA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 0.5inch PE Service while digging hole to plant tree No USA ticket
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2020-12-09 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2674 |  |  | NA | JUSTIN OR MIKE GAFA | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | WHile doing a house demolition a 0.75 inch riser was struck with hand tools
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2020-12-27 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2744 |  | 1 |  | HIPOLITO REYES | EL CAJON | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Cut 0.75 inch Steel Service with Sawzaw while planting tree
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2020-06-16 | Third party excavation damage | Main | Steel | Grader/Scraper | 3 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2897 |  | 7 |  | ROOTER SOLUTIONS | CHULA VISTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Cut 3 inch Steel main with Grinder
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2020-10-07 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3697 |  | 4 |  | CASS ARRIETA | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was trenching to install water main
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2020-08-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | ITHIEL CRUZ | EL CAJON | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation.
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2020-08-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | FRED MOKOU | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Customer was clearing roots from trench and cut into poly service
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2020-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | ALPINE FENCE | ALPINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 0.5 inch PE service with fence post
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2020-06-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | VINCENT STURKEY | EL CAJON | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5 inch PE service hit with shovel
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2020-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | NASHWAN YAKUB | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 0.5inch PE service with morning
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2020-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | AM ORTEGA | LAKESIDE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | AMO was potting laterals and excavator ripped through 0.5 inch pe service.
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2020-11-05 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | AM ORTEGA | LAKESIDE | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | DIG IN BY 2ND PARTY WORKING FOR SDGE
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2020-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | AMO | LAKESIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | AMO was digging and hit gas service with shovel.
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2020-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3583 |  | 8 |  | LARRY LEONE | LAKESIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hit 2 inch PE Main
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2020-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2674 |  |  | NA | MARK PEARSON | CARDIFF | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Cut into 0.75 inch steel service with saw
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2020-07-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | LOPEZ ENGINEERING | GLENDORA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was auguring to install footing for a post for a trash enclosure when they drilled into the 1.25 inch poly stub. No usa
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2020-09-10 | Third party excavation damage | Main | Polyethylene Pipe | Grader/Scraper | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3023 |  |  | NA | EXECUTIVE LANDSCAPE | FALLBROOK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Trenching with equipment.
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2020-05-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | WESTERN OUTDOOR DESIGN BUILD | SAN MARCOS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify dig alert prior to excavation.
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2020-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | SALVADOR RODRIGUEZ | ENCINITAS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hit 1 inch service with backhoe
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2020-09-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | TIM BESTAMENTE | ENCINITAS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Homeowner hit 1 inch PE service with shovel
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2020-09-28 | Third party excavation damage | Main | Polyethylene Pipe | Grader/Scraper | 3 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7035 |  | 17 |  | KOCH GENERAL ENGINEERING | EL CAJON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Hit 3 inch PE service with Skidster.
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2020-03-03 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6405 |  | 8 |  | COCH GENERAL ENGINEERING | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor digging with a backhoe to install conduits for electric hit the 3 poly main causing a B B
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2020-05-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | DIVERSIFIED ELECTRIC | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failure to use adequate caution while digging near gas service.
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2020-10-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | OLIVIO IRRIGATION | OCEANSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 0.5 inch PE
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2020-11-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | RACHEL GARNIN | ENCINITAS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5 inch PE service hit with shovel
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2020-05-12 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | SOUTHERN GENERAL ENGINEERING | SAN MARCOS | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was digging with a shovel to install and anchor for a pole when the hit the 0.5 inch poly service causing a Broken and Blowing.
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2020-02-12 | Third party excavation damage | Main | Polyethylene Pipe | Grader/Scraper | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3023 |  |  | NA | MUNSCH HOMES | RANCHO SANTA FE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging without valid USA ticket
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2020-08-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | MARC ATTINASI | ENCINITAS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation.
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2020-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | TIM TURNER DESIGNS | ENCINITAS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 0.5 inch PE Service with excavator
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2020-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | BAKER ELECTRIC | ESCONDDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2020-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | HOMEOWNER | ENCINITAS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner and a day labor were ripping out the old driveway when they severed the 1 inch poly service with a backhoe
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2020-08-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | HOME OWNER HAD A HELPER | ENCINITAS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner and helper were digging for drains when they hit the 0.5 inch poly service causing a BandB
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2020-04-16 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2674 |  |  | NA | JASON SCHAFER | ESCONDIDO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was using a saw zaw to remove a tree stump when they cut into the 0.75 inch steel service.
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2020-11-04 | Third party excavation damage | Main | Steel | Boring Equipment | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5252 |  |  | NA | RAMIRO MARTINEZ | EL CAJON | CA | N | Y | Yes | Yes | No | No | No | Yes | Yes | 2 inch Steel Main hit with grundo. Main was not marked out.
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2020-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | STAN THORP | ESCONDIDO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation.
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2020-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | DANIEL EMBRY | ESCONDIDO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 0.5 inch PE service with shovel
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2020-10-03 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2814 |  | 2 |  | BARBARA DONNELLY | ESCONDIDO | CA | N | Y | Yes | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 1 inch Steel service while grading
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2020-01-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | MOON VALLEY NURSERIES | ESCONDIDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was in the process of digging a hole for a large plant when they hit the 0.5inch poly service with a shovel
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2020-05-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | NA | ESCONDIDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging with a backhoe to install wet utilities when they severed the 1 inch poly service. They left the scene before the crew arrived
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2020-05-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | SHASTA LANDSCAPING INC | SAN MARCOS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was trenching with a backhoe for drainage when they severed the 1 inch poly service.
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2020-11-12 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2911 |  | 22 |  | ANGEL MARCUCCI | SANTA FE SPRINGS | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 0.5 inch PE service hit with shovel
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2020-10-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | REYES LANDSCAPE MAINTENANCE INC | VISTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 1 inch PE Service with excavator
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2020-06-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | HOMEOWNER | ESCONDIDO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was trenching with a shovel for irrigation when he struck the 0.5 inch poly service causing a Broken and Blowing
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2020-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 1.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3275 |  | 28 |  | PAUL ROSE | ESCONDIDO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to understand the USA mark outs. Failure to identify steel gas service instead of a tree root.
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2020-02-12 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7923 |  | 70 |  | MARINA LANDSCAPE | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was digging with a shovel and digging bar to install a main irrigation line when they hit the 2 poly main causing a B B
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2020-08-03 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | ARB | LAKE FOREST | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor trenching for a new gas line with a backhoe hit the 1 inch poly service
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2020-01-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | SHASTA LANDSCAPE | SAN MARCOS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging with a mini ex to install drains when they hit the 1 poly service causing a B B
San Diego Gas and Electric | N | SAN DIEGO | FALLBROOK | 2020-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | TL PREMIER PLUMBING | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation.
San Diego Gas and Electric | N | SAN DIEGO | FALLBROOK | 2020-05-20 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4773 |  | 25 |  | FILANC CONSTRUCTION | ESCONDIDO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was digging for a new water line with a backhoe when part of the road gave and fell on the 2 inch poly main causing a Broken and Blowing.
San Diego Gas and Electric | N | SAN DIEGO | FALLBROOK | 2020-11-17 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3023 |  |  | NA | RAND ENGINEERING | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Cut 2 inch PE main with sawzaw
San Diego Gas and Electric | N | SAN DIEGO | FALLBROOK | 2020-02-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | SOLCIUS SOLAR | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor trenching with hand tools to install a conduit for solar hit the 0.5inch poly service causing a B B
San Diego Gas and Electric | N | SAN DIEGO | FALLBROOK | 2020-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | INFINITY PLUMBING | FALLBROOK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hit 1 inch PE stub with backhoe.
San Diego Gas and Electric | N | SAN DIEGO | FALLBROOK | 2020-05-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | SABER YOVMAN | FALLBROOK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Homeowner was grading with a backhoe when they hit the 0.5 inch poly service causing a Broken and Blowing.
San Diego Gas and Electric | N | SAN DIEGO | FALLBROOK | 2020-12-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | ALFREDO RODRIGUEZ | FALLBROOK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 0.5 inch PE Service with shovel
San Diego Gas and Electric | N | SAN DIEGO | FALLBROOK | 2020-11-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | BOBS SEPTIC SERVICE | ESCONDIDO | CA | N | Y | Yes | No | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5 inch PE Service hit with shovel
San Diego Gas and Electric | N | SAN DIEGO | IMPERIAL BEACH | 2020-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2674 |  |  | NA | BRETT ARMSTRONG | IMPERIAL BEACH | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Was removing trash can from existing pond pump housing and cut 0.75 inch steel pipe with sawzaw
San Diego Gas and Electric | N | SAN DIEGO | IMPERIAL BEACH | 2020-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2076 |  | 16 |  | NV5 | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failure to pothole facility prior to excavation
San Diego Gas and Electric | N | SAN DIEGO | LA JOLLA | 2020-05-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | CHARLES SHER | LA JOLLA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation.
San Diego Gas and Electric | N | SAN DIEGO | LA JOLLA | 2020-08-21 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2674 |  |  | NA | ANDRES CENCIO | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation. Failure to use caution while working near gas facility.
San Diego Gas and Electric | N | SAN DIEGO | LA JOLLA | 2020-06-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Wood Stake through Gas Service
San Diego Gas and Electric | N | SAN DIEGO | LA JOLLA | 2020-06-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | HOMEOWNER | LA JOLLA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation.
San Diego Gas and Electric | N | SAN DIEGO | LA JOLLA | 2020-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2674 |  |  | NA | ISRAEL ZEA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation.
San Diego Gas and Electric | N | SAN DIEGO | LA JOLLA | 2020-07-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | HOMEOWNER | LA JOLLA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation.
San Diego Gas and Electric | N | SAN DIEGO | LA JOLLA | 2020-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2211 |  | 12 |  | PIPERIN | ESCONDIDO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On 08-03-20, SDG&E was notified of a third party damage at 8256 Caminito Lacayo St, La Jolla. Third party contractor damaged a 0.50 inch plastic natural gas service with a shovel while trying to expose the gas service. The damage to the 0.50 inch plastic natural gas service caused a release of gas. SDG&E personnel were sent to the scene and safely controlled the gas. There were no injuries reported due to the release of gas. This was reported to the CPUC due to the release of gas and media coverage.
San Diego Gas and Electric | N | SAN DIEGO | LA JOLLA | 2020-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | TOP GRADE GENERAL ENGINEERING | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was digging with a mini ex to install a new electric service when they severed the 0.5 inch poly service.
San Diego Gas and Electric | N | SAN DIEGO | LA JOLLA | 2020-03-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | UNDERGROUND LINK | NATIONAL CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failure to use caution while boring near gas facility
San Diego Gas and Electric | N | SAN DIEGO | LAKESIDE | 2020-06-19 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3023 |  |  | NA | MIKE FLETCHER | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Water service broke, blowing hole in side of PE main.
San Diego Gas and Electric | N | SAN DIEGO | LAKESIDE | 2020-10-09 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2674 |  |  | NA | MIKE SHIELDS | LAKESIDE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 0.75 inch Steel service with grading
San Diego Gas and Electric | N | SAN DIEGO | LAKESIDE | 2020-05-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | JILL MARSH | LAKESIDE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 0.5 inch PE service with shovel
San Diego Gas and Electric | N | SAN DIEGO | LEMON GROVE | 2020-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | SRK ENGINEERING | ESCONDIDO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hit 0.5 inch PE service with shovel
San Diego Gas and Electric | N | SAN DIEGO | LEMON GROVE | 2020-12-03 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2954 |  | 4 |  | OROZCO AYALA | ESCONDIDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Party digging for retaking wall. Homeowner Homeowner states she found these guys through a friend to dig dirt and break existing concrete wall to put up new retaining wall. She stated she was try to save money and do without permits and hired these guys to save money. The 0.75 inch stl. gas service was hit with jackhammer. No USA was called in.
San Diego Gas and Electric | N | SAN DIEGO | NATIONAL CITY | 2020-08-04 | Third party excavation damage | Main | Steel | Grader/Scraper | 1.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3555 |  | 32 |  | PRATT EQUIPMENT COMPANY | VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On 08-04-20, SDG&E was notified of a third party damage at 799 Civic Center Dr, National City. While digging with an excavator, the third party contractor damaged an 1.50 inch steel gas main while removing a concrete footing. The gas main was marked out correctly, but the third party contractor failed to pot the gas main to verify location. SDG&E personnel were sent to the scene and safely controlled the gas. No injuries were reported due to the release of gas. This was reported to the CPUC due to the release of gas and media coverage.
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2020-04-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | LINCOLN MILITARY HOUSING | CAMP PENDLETON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was digging with a post hole digger to install a pull up bar hit the 0.5 inch poly service causing a Broken and Blowing
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2020-11-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | DUSTIN HUDSON | TEMECULA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5 inch PE Service hit with excavator
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2020-03-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | CHRIS DONAHUE | OCEANSIDE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was grading his backyard with a bobcat when he severed the 0.5inch poly service causing a B B
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2020-02-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | DOHERTY CONCRETE | OCEANSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor digging for an electric conduit with a backhoe hit the 0.5inch poly service causing a B B
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2020-05-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1581 |  | 3 |  | UWE DEGENHARDT | OCEANSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Homeowner was trenching for a new electric service when he put a wood stake into the 0.5 inch poly service causing a Broken and Blowing.
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2020-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | A2M CONTRACTORS | CHULA VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hit 0.5 inch PE service with shovel.
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2020-12-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | GREG STEPHENS | SAN MARCOS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 0.5 inch PE service with shovel
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2020-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | WADE WEBER | OCEANSIDE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 0.5 inch Dupont service with shovel
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2020-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | HCI INC | NORCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failure to use caution while digging near gas service
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2020-10-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | TRI CITY ELECTRICAL | SAN MARCOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hit 0.5 inch PE Service with shovel
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2020-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | MARKOS VALENCIA | OCEANSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 0.5 inch PE service with electric jackhammer.
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2020-02-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | GREEN BEE CONCRETE CONSTRUCTION | PERRIS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor grading with a mini ex to install footings hit the 1 poly stub severing it in half
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2020-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | ELLIS CONTRACTING INC | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was potting the stub to set it up for an RFS when they sliced into the 1 inch poly stub causing a Broken and Blowing
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2020-03-30 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2674 |  |  | NA | BROOKS APARTMENTS MAINTENANCE | OCEANSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No one was on scene but it looked as the maintenance crew for the apartments was digging around the riser when they caused it to leak
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2020-12-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | DON MILLER | OCEANSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hit 0.5 inch PE Service with shovel
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2020-03-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | HOMEOWNER | OCEANSIDE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscaper was hired by homeowner to install fence post when the landscaper hit the 0.5inch poly service with a post hole digger shovel causing a B B
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2020-04-24 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | HENKELS MCCOY | SAN DIEGO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was potting the 0.5 inch poly service during a dimp project when they sliced the 0.5 inch poly service causing a Broken and Blowing.
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2020-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2674 |  |  | NA | H 7 CONTRACTING AND ENGINEERING INCE | MURRIETA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor trenching for a new sewer line when they hit the 0.75 inch steel service with a backhoe
San Diego Gas and Electric | N | SAN DIEGO | POWAY | 2020-11-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | WILLIAM BRICKNER | POWAY | CA | N | Y | Yes | Excavation occurred on private property by a non-contractor. | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to maintain valid USA ticket.
San Diego Gas and Electric | N | SAN DIEGO | POWAY | 2020-02-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | MIKE MILLER GENERAL CONTRACTOR | ESCONDIDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging with a trencher to install a sleeve across the driveway cut into the 1 poly service causing a B B
San Diego Gas and Electric | N | SAN DIEGO | POWAY | 2020-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | HR PLUMBING | OCEANSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging a weld hole for a gas service when they hit the 1.25 inch poly service with a shovel.
San Diego Gas and Electric | N | SAN DIEGO | POWAY | 2020-06-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | TR CONSTRUCTION | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor digging to install a new electric conduit severed the 0.5 inch poly service with a digging bar.
San Diego Gas and Electric | N | SAN DIEGO | POWAY | 2020-10-22 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | ADRIAN MADRIGAL | SANTA FE SPRINGS | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contract crew potting the gas line in hard ground damaged the 0.5 inch PE service
San Diego Gas and Electric | N | SAN DIEGO | POWAY | 2020-11-10 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | SANTOS MARTINEZ | LAKESIDE | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hit 0.5 inch PE Service with shovel
San Diego Gas and Electric | N | SAN DIEGO | POWAY | 2020-10-21 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | DAVID HITZEMAN | LAKESIDE | CA | Y | Y | Yes | Yes | No | No | No | Yes | No | Hit 0.5 inch PE service with shovel
San Diego Gas and Electric | N | SAN DIEGO | POWAY | 2020-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | KEEGAN ELECTRIC SOLAR | SANTEE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failure to use adequate caution while digging near gas service.
San Diego Gas and Electric | N | SAN DIEGO | POWAY | 2020-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | VETERANS DEMOLITION AND EXCAVATION | CALEXICO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation.
San Diego Gas and Electric | N | SAN DIEGO | POWAY | 2020-01-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | HAWKEYE BUILDERS | ESCONDIDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was using a jackhammer to dig for a new footing on a house remodel when they severed the 0.5inch poly service
San Diego Gas and Electric | N | SAN DIEGO | RANCHITA | 2020-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | WESTERN OUTDOOR DESIGN AND BUILD | SAN MARCOS | CA | N | Y | Yes | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 0.5 inch PE service with clay digger.
San Diego Gas and Electric | N | SAN DIEGO | RANCHO SANTA FE | 2020-05-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | HOME OWNER | RANCHO SANTA FE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was grading on the side of his house when he hit the 1 inch poly service with a pick axe causing a Broken and Blowing
San Diego Gas and Electric | N | SAN DIEGO | RANCHO SANTA FE | 2020-09-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | LUIS CARDENAS | RANCHO SANTA FE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 1 inch PE service with backhoe.
San Diego Gas and Electric | N | SAN DIEGO | RANCHO SANTA FE | 2020-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | JANELLE KANESHIRO | RANCHO SANTA FE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hit 1 inch PE service with Backhoe
San Diego Gas and Electric | N | SAN DIEGO | RANCHO SANTA FE | 2020-01-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | CHARLIE WILSON | RANCHO SANTA FE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working directly for the homeowner was digging with a mini ex for a new houseline hit the 1 poly service causing a B B
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-02-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | JUAN MIRANDA | SANTEE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Drain cleaning equipment such as snakes, etc. | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | JOVONE MURPHY | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The steel cable used to pull through a copper water line cut the gas line.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | ANTONIO MEDINA | IMPERIAL | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was moving a spectrum box out of the way and was digging without USA ticket and hit 0.5 inch PE.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-03-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | SILVERTHORN CONSTRUCTION - DONNIE WALLACE | ALPINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | On March 27th, a third party contractor was excavating to install building footings and struck a 1inch plastic gas service with a backhoe, causing a release of gas. There were no injuries resulting from this incident. SDGE Crews responded, controlled the leak and made repairs the same day by replacing a 3feet section of 1inch plastic pipe. Further investigation showed that the contractor did not have a valid USA DigAlert ticket. The incident was reported to the CPUC as SDGE became aware of media coverage.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | LENNAR HOMES | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Using a cutting tool saw into the ground without verifying underground facilities
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-08-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | ALLIED CONSTRUCTION SERVICES | NA | NJ | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was digging a weld hole to upgrade the gas meter when they hit the 1 inch poly service.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-09-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3023 |  |  | NA | HYLAND ELECTRIC | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 2 inch PE Main while trenching for water
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-12-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | VINYL PRO FENCE | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 0.5 inch PE service while installing fence post
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-05-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | MAGDALENA REVALCABA | SAN DIEGO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-03-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | ALPINE FENCE | ALPINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-11-04 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | ARB | LAKE FORREST | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hit 0.5 inch PE Service with shovel
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-08-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2082 |  | 7 |  | HAROLD WILLIAMS | SAN DIEGO | CA | N | Y | Excavation was for emergency reasons. | Excavation was for emergency reasons. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | San Diego water department was running a new service as there was a major leak and as they were pulling the service through it rubbed against out main and caused a BandB.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-03-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | AMV GENERAL | SANTEE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging with a shovel to re do the water proofing on a retaining wall when the hit the 0.5inch poly service causing a B B
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-05-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 1.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1315 |  |  | NA | NA | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Cut into the 1.5 inch steel service thinking it was inserted.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | SMITH ELECTRIC | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failure to use caution while digging near gas facility.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Trencher | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2674 |  |  | NA | ABDEL CASTELLO | SPRING VALLEY | CA | N | Y | Yes | Yes | No | No | No | Yes | Yes | Trenching with rockwheel
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-11-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | ADVANCED CONSTRUCTION | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor was digging for a foundation for the homeowner.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | JESUS INIGUEZ | CHULA VISTA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Hit 0.5 inch PE service with shovel
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-01-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2674 |  |  | NA | WILSON CORPORATION | SPRING VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Operator hit unmarked 0.75inch service stub
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-05-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | MARCO PEREDA | SAN DIEGO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 0.5 inch Dupont with shovel
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | WHITE HORSE ELECTRIC CO | NA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-07-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | LENNON ELECTRIC | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was trenching with a shovel for a new electric conduit when they hit the 0.5 inch poly service
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-10-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | HL MASONRY | ESCONDIDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1 inch PE Service hit with backhoe
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-04-16 | Third party excavation damage | Main | Steel | Trencher | 1.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 3 |  | TROY HENDERSON | ALPINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While cutting asphalt with saw cutter for trenching, the gas line was hit.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-09-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | THOMAS SOMMER | SAN DIEGO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 0.5 inch PE service with shovel.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-10-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2674 |  |  | NA | VALENTINO | SAN DIEGO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.75 inch Steel service hit with backhoe while removing tree stump
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-03-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | EPX GROUP | TEMECULA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 0.5inch PE service with shovel
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-03-11 | Third party excavation damage | Riser | Steel | Miscellaneous/Other | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | DRAINHELP.COM - ALI TUNCBILEK | EL CAJON | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | On 03 11 2020, a third party damage occurred on a 1inch service riser by a contractor plumber working on a meter set assembly to install an earthquake valve. SDGE crews responded, controlled the gas by utilizing a curb meter valve, and made permanent repairs by rethreading a new service valve to the service riser. There were no injuries or further damages resulted from this incident. This incident was reported to CPUC when SDGE became aware of media coverage
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-04-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | MANGENERAL ENGINEERING INC | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hit 0.5 inch PE service with shovel
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-03-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1581 |  | 3 |  | Z AND T BUILDER | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was digging with a shovel to relocate part of the gas service when they hit the 0.5inch poly service causing a B B
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-02-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | WEST COAST GENERAL BUILDING CONTRACTORS | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 0.5inch PE service with shovel
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-02-21 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3023 |  |  | NA | HORIZON BACKHOE EQUIPMENT | PERRIS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging with a backhoe for sewer tie ins hit the 2 poly main No USA
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | CESARIO CABRERA AYALA | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | landscaping in the front yard and hit a 0.5 inch poly gas line
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-01-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | JUSTIN SOLBERG | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Trenching for electric upgrade
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5252 |  |  | NA | LEVEL 3 CONSTRUCTION | VISTA | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor installed fiber optics and hit our 2 steel line and didnt notify us. They backfilled it and left leak which we found at a later date.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5226 |  | 61 |  | ANTONIO JARAMILLO | SAN MARCOS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | On 05-04-2020, SDG E received a report of a third-party damage at 2414 Grove Ave, San Diego. Correction to original address reported on 2381 Grove Ave . Third-party contractor damaged a 1.25-inch plastic gas service with a rock wheel trenching to install electric conduit. Company crews responded, controlled the gas, and made repairs by fusing 1-ft of 1.25-inch plastic pipe. There were no injuries or damages from the gas release. Investigation of the incident showed that there was a valid USA ticket for the contractor, however, the 1.25-inch plastic service was not marked due to a mapping error in GIS. Updates to GIS mapping system are in progress. This incident was reported to the CPUC due to the release of gas and major media coverage.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-10-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1581 |  | 3 |  | FERNANDO FLORES | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hit 0.5 inch PE Service with shovel
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-05-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1872 |  | 4 |  | KTA CONSTRUCTION | ALPINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-12-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | COLDWELL BANKER | CHULA VISTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging to install fence.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | BURGESS TRENCHING INC | BONITA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-10-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | TL SCANLEN CONSTRUCTION INC | ALPINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 0.5 inch PE service with excavator
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-04-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1931 |  | 8 |  | JONATHAN GARDENHIRE | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hot 0.5 inch PE service with shovel
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-12-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | DOMINICK UTEG | LA MESA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 0.5 inch PE Service with shovel
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-11-10 | Third party excavation damage | Main | Steel | Trencher | 1.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 12095 |  | 154 |  | GLENN THEVENOT | EL CAJON | CA | N | Y | Yes | Yes | No | No | No | Yes | Yes | On November 10, 2020 at 2965 Redwood St, San Diego, a third party contractor was trenching for traffic light signals damaged a 1.5 inch steel gas main with a trencher vehicle. SDGE personnel were sent to the scene and safely controlled the gas. There were no injuries reported due to the release of gas. The 1.5 inch steel gas main was repaired and services were restored same day. Further investigation showed the third party contractor had a valid USA ticket. However, no visible marks for the 1.5 inch steel gas main were made in the immediate vicinity of the damage. The SDGE employee failed to mark the 1.5 inch steel gas main due the site being a large construction project with multiple contractors. The incident was reported to CPUC as SDGE became aware of media coverage.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-12-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2012 |  | 6 |  | RICK COLLETTE | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit gas line with excavator.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-10-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1581 |  | 3 |  | WILLIAM PERRINE | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Homeowner was installing fence posts
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-12-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | PREMIER POOLS | SANTEE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging for gas houseline for jacuzzi 0.5 inch poly was hit with hand tools by 3rd party contractor
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-01-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 1.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3275 |  | 28 |  | CARLOS WAUMAN | EL CAJON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | On 01 15 2020, SDGE received a report of a third-party contractor damaging a 1.5 inch steel gas service at 3154 Imperial Ave, San Diego, while using a rock wheel to install communication conduit (Correction to original address reported at 32nd St and Imperial Ave). Company crews responded, controlled the gas, and made permanent repairs by inserting 1 inch plastic through the 1.5 inch steel service line. No further damages nor injuries associated to the gas release have been reported. Investigation of the incident revealed the Contractor did not notify USA Dig Alert prior to digging. This incident became reportable as soon as SDGE became aware of media coverage.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-05-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | BRANDON CLENDENON OPERATOR | JAMUL | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 0.5 inch Dupont Service with Mini Excavator
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-12-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | SE PIPELINE CONSTRUCTION | SANTA FE SPRINGS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Excavation occurred before legal start time
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-03-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | GENERATION CONTRACTING | POWAY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Did not notify ISA prior to excavation Did not use caution while digging near underground facility
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-04-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | ATARI AHMED | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA ticket. Hit 0.5 inch service with excavator.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | KRASI ELECTRIC | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-05-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | ALR CONSTRUCTION CO | SOUTH EL MONTE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 0.5 inch Poly hit with pick
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | ALAN ZUCKERMAN | SAN DIEGO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-04-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | JOHN HERSE | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit gas line with shovel
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-02-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1711 |  | 2 |  | WESTERN OUTDOOR DESIGN - JESUS HERRERA | SAN MARCOS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | On February 26, 2020 at 3556 Millikin Ave, San Diego, a 0.5inch plastic natural gas service was struck by an excavator causing a leak. Crews responded and controlled the gas. No injuries or further damage resulted from this incident. The 0.5inch plastic service was repaired by replacing a short section of the pipe with new pipe and couplings. Investigation of the incident showed that there was a no valid USA ticket for the contractor. The incident was reported to CPUC when SDGE became aware of media coverage.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-08-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | T AND D SERVICES | MURRIETA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failure to use caution while excavating.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | LAWRENCE FINDAHL | ALPINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failure to pot hole prior to using equipment to excavate.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-05-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | JAMES WILLS | MURRIETA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On 05-14-2020, a third-party damage occurred on a 0.50-inch plastic gas service at 3616 Yosemite Street, San Diego, by a contractor clearing roots around the service with a shovel. SDG E crews responded, controlled the gas, and made permanent repairs by replacing a 1-ft section of 0.50-inch plastic pipe. There were no injuries or further damages resulting from this incident. Investigation of the incident showed there was a valid USA ticket for the contractor and the 0.50-inch service was properly marked. This incident was reported to the CPUC when SDG E became aware of media coverage.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-04-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4106 |  | 45 |  | ROGACINO DOMINGUEZ | ENCINITAS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On 04-16-20, SDG E was notified of a third party damage at 3670 Logan Ave, San Diego. The third party contractor was trenching with a backhoe to install a new water main, hit an unexposed 1.25 inch plastic gas line, causing a release of gas. SDG E personnel were sent to the scene to control the gas. There were no injuries nor further damage reported due to the release of gas. This was reported to the CPUC due to the release of gas and media coverage.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-01-22 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7083 |  | 58 |  | PK MECHANICAL SYSTEMS - DAVID SPINDLER | WILDOMAR | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On 01 22 2020, a third party damage occurred on a 2 inch plastic gas main at 3702 Monroe Ave, San Diego, by a contractor trenching to install water line. Original address reported as 37th Street & Monroe Ave. SDGE crews responded, controlled the gas, and made permanent repairs by replacing a 2 ft section of main. There were no injuries or further damages resulted from this incident. Investigation of the incident revealed the gas line was properly marked, however, the contractor failed to pothole prior to excavating which resulted in the damage. This incident was reported to the CPUC when SDGE became aware of media coverage.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | AARON MAGAGNA | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failure to use caution while excavating near facility.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | EMILY KUHN | SAN DIEGO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | digging with shovel
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | SCOTT RIERSON | SAN DIEGO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 0.5 inch PE Service with Shovel
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-03-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 15861 |  | 207 |  | BURTECH PIPELINE - GUMARO GARCIA | ENCINITAS | CA | N | Y | Yes | Yes | No | No | No | Yes | Yes | On 03 16 2020, SDGE received a report of a third party damage at 3875 47th Street, San Diego, while a contractor trenching to install water line damaged a 0.50inch plastic service with a backhoe. Company crews responded, controlled the gas by cold squeezing 2inch steel main, and replaced a section of 0.50inch service line. There were no injuries or further damages resulted from this incident. Investigation of the incident showed the damaged service line was not marked. Investigatory interviews for the two employees involved with the locate and mark activities are pending. SDGE intends to continue investigatory interviews and conduct any counseling as soon as both employees return to work. This incident was reported to the CPUC due to the release of gas and when SDGE became aware of major media coverage on 03 16 2020 at 16:30.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-01-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3051 |  | 24 |  | CARLOS WAUMAN | EL CAJON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Rock wheel trenching for fiber
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2981 |  | 23 |  | TL SCANLAN CONSTRUCTION | ALPINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-12-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2674 |  |  | NA | CITY OF SAN DIEGO | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While stripping pavement for sewer project City of San Diego pulled 0.75 inch steel gas service
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | HUGO SANTAELLA | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 0.5inch PE Service with pick axe
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-09-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | TONY HEREDIA | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | DAVID WAGEMAN | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hit 0.5 inch PE service with pick axe.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-08-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | MARDEX INC | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hit 0.5 inch service while grading backyard
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-08-17 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2674 |  |  | NA | JARED D ONOFRIO | SAN DIEGO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-07-28 | Operator excavation damage | Main | Steel | Miscellaneous/Other | 1.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2435 |  | 16 |  | JORGE LIZARRAGA | SAN DIEGO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On 07/28/20, A contractor was doing saw cutting for SDG&E at 4107 36th St, San Diego. As the contractor was ensuring they had cut all the way through the concrete, they struck a 1.5 inch steel main causing a release of gas. An SDG&E crew was on site, controlled the gas and all repairs were completed. There were no injuries nor further damage that resulted from this incident. This was reported to CPUC when SDG&E became aware of media coverage.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-01-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | CHAPIN CONSTRUCTION | BONITA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Stuck probe into ground and hit the pipe
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-02-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2814 |  | 2 |  | TYLER STONEBRAKER | SAN DIEGO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | failure to notify USA and failure to expose underground facilities prior to excavation
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-03-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2674 |  |  | NA | ESP CONSTRUCTION | POWAY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Pulled 0.75inch steel stub with excavator than cut with sawzaw to verify what utility it was
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-11-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | JOSE HERNANDEZ | SAN DIEGO | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | plumber was removing houseline for header truck to remove meter
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-04-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | GEORGE LAFIGUERA | SAN DIEGO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Trenching for new gas line, hit 0.5 inch PE service with shovel.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-07-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | KTA | ALPINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hit 1.25 inch service with mini ex.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-09-18 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | AZ PLUMBING | EL CAJON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Trenching for sewer installation
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-03-25 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3023 |  |  | NA | KENNEDY ELECTRIC | LA MESA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failure to use caution while digging near gas main
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-05-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | CHRIS SALAZAR | JAMUL | CA | N | Y | Yes | Yes | No | No | No | Yes | Yes | SDGE failed to mark out gas service.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-05-16 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | SDGE | SAN DIEGO | CA | Y | Y | Excavation was for emergency reasons. | Excavation was for emergency reasons. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Employee was investigating a leak when he stuck pin bar through the 1/2 poly service.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-01-23 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3417 |  |  | NA | NIVA NAKHSHAB | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging with an excavator for a new building construction hit the 1.25inch steel stub causing a B B
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-10-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | SCOTT DEGRASSENREID | LA MESA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to use caution while operating equipment near gas riser.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-10-28 | Third party excavation damage | Main | Steel | Grader/Scraper | 1.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6086 |  | 35 |  | ROCKY ANDERSON | SANTEE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On 10/28/2020, a third-party damage occurred on a 1.50-inch steel gas main at 4569 Dwight Street, San Diego, by a contractor excavating to install sewer/water utilities. SDGE crews responded, controlled the gas, and made permanent repairs by replacing a section of main. There were no injuries or further damages resulting from this incident. Investigation of the incident showed there was a valid USA ticket for the contractor and the 1.50-inch main was properly marked. This incident was reported to the CPUC when SDGE became aware of media coverage.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-10-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | BOBBY MCCARRON | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failure to use caution while digging near gas service.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | ROBERT MCCARRON | SAN DIEGO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Trenching for gas houseline
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-01-13 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3474 |  | 400 |  | AVERY WYNN | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Dug outside of delineation
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-08-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | NOE HERNANDEZ | CHULA VISTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | VICTOR VARGAS | CHULA VISTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 0.5 inch poly gas service while trenching for foundation
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-12-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | SERGIO ESTRADA | VISTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Original addresses of 4820 and 4838 - service tech confirmed it is at 4835
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-08-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | COLEPEPPER PLUMBING | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber was digging up sewer line to clean out and in the process stuck out gas service.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-09-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1861 |  | 7 |  | RAMON ROMO | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit gas line with hand tools while digging to remove tree stump
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-11-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | A FRAME CONSTRUCTION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-11-12 | Third party excavation damage | Main | Polyethylene Pipe | Grader/Scraper | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3023 |  |  | NA | DOOSE LANDSCAPE INC | ESCONDIDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was excavating with excavator for irrigation
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1581 |  | 3 |  | ALAN LOGAN | LA JOLLA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-07-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | SIERRA LANDSCAPE | BONSALL | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | LB3 ENTERPRISES | LAKESIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Dry utilities installation
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-02-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | DIAMOND PACIFIC CONSTRUCTION INC | LA MESA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA or hand expose service
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | LINDA LITTLE | SAN DIEGO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging for drain. Contractor left b4 GERC arrived unknown what line was hit with
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-09-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | MATT MARQUEZ | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 1 inch PE Service with Drill
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-03-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | MARTIN VACA | NA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5inch PE Service hit with shovel No USA Ticket
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-05-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1651 |  | 4 |  | TREEIUM | VALLEY VILLAGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | hit 0.5 inch DuPont with excavator
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-11-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | CLEAR EXPECTATIONS POOL BUILDER | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hit 0.5 inch PE service with backhoe
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-10-26 | Third party excavation damage | Main | Steel | Grader/Scraper | 1.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1315 |  |  | NA | ORION CONSTRUCTION | VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit 0.75 inch unmarked service stub.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-12-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | ABED DEVESTER | SAN DIEGO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Struck 0.5 inch poly line with digging bar.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | MERAM CONSTRUCTION | EL CAJON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging with a backhoe when they hit the 1 inch poly service causing a bnb.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-07-22 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4213 |  | 17 |  | CASS ARRIETA | EL CAJON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was pulling water service and collar slice the 2 inch main
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | SCOTT VARGAS | NA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failure to use caution while excavating near gas facility.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-06-01 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3444 |  | 11 |  | ORION CONSTRUCTION CORPORATION | VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failure to hand expose prior to using equipment.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-01-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | ERIC MERCHEHI | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Trenching for electric
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-07-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | ORION CONSTRUCTION | VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failure to protect facilities during excavation.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-04-30 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2884 |  | 3 |  | DJ HENSON | VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failure to use adequate caution while digging near gas facility.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-08-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | JOHN AND MARY TURNER | SAN DIEGO | CA | N | Y | Yes | Excavation occurred on private property by a non-contractor. | Yes | Yes | No | Yes | Yes | Failure to maintain current USA ticket. Failure to use caution while digging near gas facility.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-05-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | ORION CONSTRUCTION | VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failure to protect gas service from damage.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | HORIZON BACKHOE EQUIPMENT | WINCHESTER | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was trenching with a backhoe for wet utilities when they hit the 1 inch poly service.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | BINH HUA | SAN DIEGO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | HUE LE | SAN DIEGO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | customer digging on his property.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-10-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | WINSTEAD AND SONS | NA |  | N | Y | Yes | No | No | No | No | Yes | No | Failure to maintain current USA ticket. Failure to use caution while digging near gas service.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | UNKNOWN | NA |  | N | Y | Excavation was for emergency reasons. | Excavation was for emergency reasons. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Unknown
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-03-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | JOSH LESCH | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA and use caution while digging near facility
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-03-27 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2744 |  | 1 |  | GRUNOW CONSTRUCTION | LA JOLLA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Pulled up gas lane with backhoe breaking 0.75inch steel line at the meter
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-07-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3583 |  | 8 |  | CITY OF SAN DIEGO WATER DISTRICT | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged 2 inch PE Main with steel cable.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-08-04 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3513 |  | 7 |  | MMJS | ESCONDIDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-02-25 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5845 |  |  | NA | JG CONSTRUCTION | CHINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3 PE Main hit with excavator
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-03-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | MATTHEW MEGNA | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging with a shovel to install an electric conduit when they hit the 0.5inch poly service causing a B B
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-10-08 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5845 |  |  | NA | HL MASONRY | ESCONDIDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 3 inch PE Stub with backhoe
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-02-13 | Third party excavation damage | Main | Polyethylene Pipe | Not Available | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3023 |  |  | NA | HUGO DELGADO | EL CAJON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | MA
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-10-16 | Third party excavation damage | A service line with an excess flow valve installed | Steel | Not Available | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2674 |  |  | NA | PALM ENGINEERING CONSTRUCTION | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to hand expose. Failure to notify USA prior to excavation.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-04-23 | Third party excavation damage | Main | Steel | Directional Drilling | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7422 |  | 31 |  | HP COMMUNICATIONS INC | CORONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | Hit 2 inch main with Boring Drill
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-05-18 | Third party excavation damage | Main | Polyethylene Pipe | Grader/Scraper | 3 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5845 |  |  | NA | MCTC | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor digging with equipment
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-02-13 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3223 |  | 0 |  | SCHILLING PARADISE - HUGO DELGADO | EL CAJON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | On 02 13 20, SDGE was notified of a third-party damage at Sea Fire Point and Del Sol Way in San Diego. A third-party contractor was digging to install utilities in a new development when they damaged a 2inch plastic gas main with a backhoe resulting in a gas release. SDGE personnel were sent to the scene and controlled the gas. Third party contractor was digging on an expired USA ticket. No injuries resulted from this incident. SDGE also received area odor complaints in the vicinity due to gas release for this incident. This incident was reported to the CPUC because of gas release and media coverage
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2020-10-12 | Third party excavation damage | Main | Polyethylene Pipe | Grader/Scraper | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3023 |  |  | NA | DOOSE LANDSCAPING | SAN MARCOS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 2 inch PE main
San Diego Gas and Electric | N | SAN DIEGO | SAN MARCOS | 2020-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | D B GENERAL | OCEANSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging with a mini ex to install drainage and irrigation along with hardscape when they severed the 0.5inch poly service
San Diego Gas and Electric | N | SAN DIEGO | SAN MARCOS | 2020-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | PAUL TURNER | SAN MARCOS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 0.5 inch PE service with Mini Excavator
San Diego Gas and Electric | N | SAN DIEGO | SAN MARCOS | 2020-06-29 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3093 |  | 1 |  | DRAGON LAZOVIC | SAN MARCOS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was trenching with a backhoe for sewer when he hit the 2 inch poly main causing a Broken and Blowing. No USA
San Diego Gas and Electric | N | SAN DIEGO | SAN MARCOS | 2020-11-24 | Third party excavation damage | Main | Polyethylene Pipe | Grader/Scraper | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3233 |  | 3 |  | DND CONSTRUCTION | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 2 inch PE main with backhoe
San Diego Gas and Electric | N | SAN DIEGO | SAN YSIDRO | 2020-06-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | BOB JOHNSON | SANTEE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hit 0.5 inch PE service while potting.
San Diego Gas and Electric | N | SAN DIEGO | SANTEE | 2020-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | ROBLES CONSTRUCTION | LAKE ELSINORE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 0.5 inch line with shovel, no USA mark out.
San Diego Gas and Electric | N | SAN DIEGO | SANTEE | 2020-06-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | LAURA ROACH | SANTEE | CA | N | Y | Yes | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1 inch PE hit with shovel
San Diego Gas and Electric | N | SAN DIEGO | SANTEE | 2020-09-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1511 |  | 2 |  | HCI INC | SAN MARCOS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | Hit PE service with shovel.
San Diego Gas and Electric | N | SAN DIEGO | SANTEE | 2020-12-01 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3163 |  | 2 |  | PADRE DAM MUNICIPAL WATER DISTRICT | SANTEE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Failure to pot hole facility prior to excavation.
San Diego Gas and Electric | N | SAN DIEGO | SANTEE | 2020-10-07 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3023 |  |  | NA | RICHARD MARTELLI | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to pot gas main. When excavating for sewer installation hit 2 inch PE dead end. Causing B and B. No marks visible do to files of dirt everywhere and failure to maintain marks
San Diego Gas and Electric | N | SAN DIEGO | SANTEE | 2020-08-14 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2744 |  | 1 |  | FRANK VAN BUREN | SANTEE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation.
San Diego Gas and Electric | N | SAN DIEGO | SANTEE | 2020-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2814 |  | 2 |  | SCOTTYS LANDSCAPING | NA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation.
San Diego Gas and Electric | N | SAN DIEGO | SANTEE | 2020-02-26 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | MUNICIPAL WATER DISTRICT | SANTEE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Steel cable cut through 1.25inch PE main
San Diego Gas and Electric | N | SAN DIEGO | SOLANA BEACH | 2020-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2674 |  |  | NA | PACIFIC WEST COMMUNICATION | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was using an earth saw to install communications when they cut through the 0.75 inch steel service.
San Diego Gas and Electric | N | SAN DIEGO | SPRING VALLEY | 2020-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | DAD PAVERS | EL CAJON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit pipe while pulling stump out with bobcat.
San Diego Gas and Electric | N | SAN DIEGO | SPRING VALLEY | 2020-12-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | RONALD BROOKINS | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | None
San Diego Gas and Electric | N | SAN DIEGO | SPRING VALLEY | 2020-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2674 |  |  | NA | JOHN MERZ | SPRING VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Business owner was doing work for himself water sewer
San Diego Gas and Electric | N | SAN DIEGO | SPRING VALLEY | 2020-05-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | LB CIVIL CONSTRUCTION INC | ESCONDIDO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failure to use adequate caution while digging near gas facility.
San Diego Gas and Electric | N | SAN DIEGO | SPRING VALLEY | 2020-06-07 | Third party excavation damage | A service line with an excess flow valve installed | Steel | Grader/Scraper | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2814 |  | 2 |  | JAMES WILLIAMSON | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Broke 0.75 inch steel service with excavator
San Diego Gas and Electric | N | SAN DIEGO | SPRING VALLEY | 2020-01-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | MANUEL LOPEZ | SPRING VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 0.5inch PE service with pick axe
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2020-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | THE APARTMENT COMPANY | ENCINITAS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 0.5 inch PE service with shovel
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2020-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | DEAN NESBITT | VISTA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner was digging with a shovel to install a footing for a retaining wall when he hit the 0.5 inch poly service causing a BandB.
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2020-03-26 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 3 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5845 |  |  | NA | CITY OF VISTA | VISTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | City of Vista employee was hitting a sign post into the ground when they hit the 3 poly main causing a B B
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2020-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | BUENA VISTA LANDSCAPING | VISTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5 inch PE service hit with shovel
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2020-08-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | RICARDO GUTIERREZ | VISTA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Failure to notify USA prior to excavation.
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2020-06-12 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4773 |  | 25 |  | SCHILLING PARADISE | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hit 2 inch PE main with Mini X
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2020-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | HENKELS AND MCCOY | POMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | hit 1 inch PE Service with Backhoe
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2020-01-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | X3 MANAGEMENT SERVICES INC | VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | hit line with mini ex &,(), /, :
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2020-03-26 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3023 |  |  | NA | HENKELS AND MCCOY INC | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was boring to install a new Verizon fiber line when they bored into a 2 poly stub
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2020-11-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | JOSH DIVEN | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5 inch PE service hit with shovel
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2020-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | RAFEAL ALVIZO | VISTA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 0.5 inch PE service with shovel
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2020-03-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1802 |  | 3 |  | GING LI | VISTA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was trenching with a backhoe to install a new electric conduit when they hit the 1 poly service causing a B B
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2020-10-27 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1371 |  |  | NA | SEAN CROWLEY | SANTA FE SPRINGS | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hit 0.5 inch PE service with shovel
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2020-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1592 |  |  | NA | CALEB UNDERGROUND CONSTRUCTION | RAMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hit 1 inch PE Stub with Backhoe
San Diego Gas and Electric | Y | SAN DIEGO | SAN DIEGO | 2020-07-16 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 6 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 727387 |  | 3278 |  | PAR ELECTRIC CONTRACTORS | ESCONDIDO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On 07/16/2020, a contractor was excavating to install electrical conduits on Orange Avenue in San Diego and struck a fitting attached to a 6-inch medium pressure steel gas main, causing a release of gas. SDG&E gas Crews responded and controlled the leak by utilizing mainline valves in the vicinity. Further investigation found that the main was marked correctly and the contractor was not using hand tools to fully expose the gas lines. There were no injuries resulting from this incident. The incident was first reported to the CPUC when SDG&E became aware of media coverage, and later reported to the DOT when SDG&E determined that customer restore costs would result in total expenses exceeding $50,000.
Southern California Gas Company | N | FRESNO | KINGSBURG | 2020-10-10 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 1 |  | NA | KINGSBURG | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per LCT. Luis Lopez Home owner James Reed cut through gas service line with reciprocating saw while installing a water line.
Southern California Gas Company | N | FRESNO | KINGSBURG | 2020-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | KINGSBURG | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Jose Mojarro damaged the SCG gas service while excavating to repair a fence.ï¿½ He did not notify USA.
Southern California Gas Company | N | FRESNO | LATON | 2020-11-09 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Trencher | 0.75 | 20 | 15 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 7 |  | HAPPY GROWING LANDSCAPE | CLOVIS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged steel service while excavating without a usa ticket.
Southern California Gas Company | N | FRESNO | ORANGE COVE | 2020-05-19 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 36 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  |  | NA | AJ EXCAVATION INC | FRESNO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor damaged a 2 inch gas main, crew made permanent repairs.
Southern California Gas Company | N | FRESNO | PARLIER | 2020-10-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ANDERSON BALLOU INC | SANGER | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Contractor damaged 1 inch plastic service while excavating prior to having a valid usa ticket.
Southern California Gas Company | N | FRESNO | REEDLEY | 2020-12-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | REEDLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner damaged 0.5 inch plasticï¿½service with pick axe while digging to repairï¿½water line, USA was not called.
Southern California Gas Company | N | FRESNO | REEDLEY | 2020-08-19 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 4 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  | 1 |  | VAST NETWORKS | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to pothole over a 1 inch plastic gas line and damaged it while performing directional boring, crew made permanent repairs.
Southern California Gas Company | N | FRESNO | REEDLEY | 2020-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 15 | 10 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | RICK CARSEY CONSTRUCTION | FOWLER | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged a 0.5 inch plastic gas line, crew made permanent repairs. Contractor was educated about USA law.
Southern California Gas Company | N | IMPERIAL | BRAWLEY | 2020-02-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | BRAWLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer was digging to install a pole for a punching bag
Southern California Gas Company | N | IMPERIAL | BRAWLEY | 2020-01-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 36 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LUCIANO GARCIA | BRAWLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor struck service line w backhoe
Southern California Gas Company | N | IMPERIAL | BRAWLEY | 2020-04-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | BRAWLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | HO cut through service with a sawzall.
Southern California Gas Company | N | IMPERIAL | BRAWLEY | 2020-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | BRAWLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was digging to install a pole for fencing and struck the branch service. No USA.
Southern California Gas Company | N | IMPERIAL | CALEXICO | 2020-02-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CESAR LANDSCAPING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 0.5inch service and riser with backhoe while grading demo structure Leak repaired by cutback on service ï¿½
Southern California Gas Company | N | IMPERIAL | CALEXICO | 2020-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RAMCO | CALEXICO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was trenching for City of Calexico and struck the service stub with a backhoe.
Southern California Gas Company | N | IMPERIAL | CALEXICO | 2020-12-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HAZARD CONSTRUCTION | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was removing curb and gutters for the City of Calexico with a backhoe and failed to hand dig to expose SCG service line.
Southern California Gas Company | N | IMPERIAL | CALEXICO | 2020-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | CITY OF CALEXICO | CALEXICO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor was digging and hit a service line with a backhoe.ï¿½
Southern California Gas Company | N | IMPERIAL | CALEXICO | 2020-10-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 45 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SERVICE MASTER | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was using a backhoe for building demolition due to a structure fire USA not called in.
Southern California Gas Company | N | IMPERIAL | CALEXICO | 2020-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 45 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JORGE VENEGAS | CALEXICO | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No | No damage to SUOF. | No damage to SUOF. | Contractor ran over the manifold with a bobtail while clearing out an empty lot.
Southern California Gas Company | N | IMPERIAL | EL CENTRO | 2020-05-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | EL CENTRO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer trenching for sewer and cut gas line. No USA
Southern California Gas Company | N | IMPERIAL | EL CENTRO | 2020-10-07 | Third party excavation damage | Riser | Polyethylene Pipe | Grader/Scraper | 0.5 | 35 | 29 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | GILBERT ZAZUETA | BRAWLEY | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | Damaged riser breaking concrete sidewalk private property
Southern California Gas Company | N | IMPERIAL | EL CENTRO | 2020-01-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | EL CENTRO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | dig in at riser with backhoe while razing house ï¿½
Southern California Gas Company | N | IMPERIAL | EL CENTRO | 2020-10-22 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 35 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ROVE ENGINEERING INC | EL CENTRO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Party contractor damaged 2 inch plastic main while excavating with backhoe
Southern California Gas Company | N | IMPERIAL | EL CENTRO | 2020-04-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | EXECUTIVE LANDSCAPING INC | EL CENTRO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscaper was trenching to install irrigation and hit the service line.
Southern California Gas Company | N | IMPERIAL | EL CENTRO | 2020-10-05 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RMC CONSTRUCTION | THOUSAND PALMS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging with a backhoe to install the foundation for a brick wall fence.
Southern California Gas Company | N | IMPERIAL | EL CENTRO | 2020-02-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | EL CENTRO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner s son was digging for sewer and damaged service with shovel No USA called
Southern California Gas Company | N | IMPERIAL | EL CENTRO | 2020-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 35 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | EL CENTRO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | customer cut service while digging holes to plant trees
Southern California Gas Company | N | IMPERIAL | HEBER | 2020-02-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 42 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | HEBER | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was hand digging a post hole trying to install a fence
Southern California Gas Company | N | IMPERIAL | HOLTVILLE | 2020-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ROVE CONSTRUCTION | HOLTVILLE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging to install a manhole, severed the service line and exposed 15 of pipe.
Southern California Gas Company | N | IMPERIAL | HOLTVILLE | 2020-10-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | HOLTVILLE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | H O was digging fence post holes and hit the service line with a shovel.
Southern California Gas Company | N | IMPERIAL | IMPERIAL | 2020-06-30 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | G4 CONSTRUCTION | IMPERIAL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Trenching to install water service line.
Southern California Gas Company | N | IMPERIAL | IMPERIAL | 2020-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ESTRATA OUTDOOR POOL | EL CENTRO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was trenching to install lines for new pool.
Southern California Gas Company | N | IMPERIAL | IMPERIAL | 2020-10-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | IMPERIAL | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was digging to remove a tree and hit the service line.
Southern California Gas Company | N | IMPERIAL | IMPERIAL | 2020-10-21 | Third party excavation damage | Riser | Steel | Not Available | 0.75 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JOHN ROSS | IMPERIAL | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | Riser was struck by riding lawn mover and broken off at ground level
Southern California Gas Company | N | IMPERIAL | IMPERIAL | 2020-12-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DRAIN MAN PLUMBING | EL CENTRO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was trenching to replace a sewer line and hit the service line.
Southern California Gas Company | N | IMPERIAL | NILAND | 2020-01-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | NILAND | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was using post hole digger when they damaged the 0.5inch plastic service
Southern California Gas Company | N | IMPERIAL | NILAND | 2020-03-18 | Third party excavation damage | Miscellaneous/Other | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | ARTURO RUIZ | IMPERIAL | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party Contractor using backhoeï¿½damagedï¿½service line ï¿½ Contractor did not have a USA ticket
Southern California Gas Company | N | IMPERIAL | SEELEY | 2020-08-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 25 | 21 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | A R CONSTRUCTION | BRAWLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to stop and hand dig. Original USA ticket
Southern California Gas Company | N | IMPERIAL | WESTMORLAND | 2020-05-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | VICTOR BALDEZ | SANTA BARBARA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Handyman was hand digging to repair sewer line for homeowner when he damaged the service line.
Southern California Gas Company | N | IMPERIAL | WESTMORLAND | 2020-05-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | WESTMORLAND | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was hand digging with a shovel to install an irrigation system when he damaged service line.ï¿½
Southern California Gas Company | N | KERN | ARVIN | 2020-05-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NA | ARVIN | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged service by digging up sewer that had been bored through by SCG Service in 2010
Southern California Gas Company | N | KERN | ARVIN | 2020-12-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | BLUE RIVER FARMS | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Backhoe had began digging without a USA and hit 0.5 inch serviceï¿½
Southern California Gas Company | N | KERN | ARVIN | 2020-08-31 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  |  | NA | LYLES UTILITIES | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was excavating to install water main and struck 4 inch plastic main withï¿½ï¿½backhoe bucket in the intersection.ï¿½
Southern California Gas Company | N | KERN | BAKERSFIELD | 2020-04-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | TOMAS PLUMBING INC | BAKERSFIELD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Thomas Plumbing was digging to repair sewer to Apt and struck service with shovel. NO USA company did state they are aware of 811
Southern California Gas Company | N | KERN | BAKERSFIELD | 2020-10-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | KERN POOLS | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Customer was excavating to install poolï¿½
Southern California Gas Company | N | KERN | BAKERSFIELD | 2020-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Customerï¿½ï¿½Struck 0.50 inch PLA Service with shovel. USA was called in and area Delineatedï¿½
Southern California Gas Company | N | KERN | BAKERSFIELD | 2020-02-03 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 6 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 14903 |  | 0 |  | CROWN ENGINEERING | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | On February 3rd, 2020, a third party contractor was boring to install communication lines and hit a 6inch plastic gas main, causing a gas release. SoCalGas Crews responded and controlled the gas. There were no injuries and no outages resulting from this incident. The 6inch plastic main was repaired same day by means of altering a small section and gassed up early on February 4th. Further investigation showed accurate marks of the involved 6inch gas line to the East of the incident site, however, no visible marks for that particular line were made in the immediate vicinity of the damage. The SoCalGas employee followed company procedures for locating & marking; he stated he made a mistake and missed one segment of main on a very large ticket. The SoCalGas OQ department re-evaluated the employee on February 10th for task 05.01-DIS and stated that he clearly demonstrated he has the knowledge, skills and ability to perform 5.01 Locate & Mark duties. The incident was reported to CPUC as SoCalGas became aware of media coverage.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2020-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | PAVLETICH ELECTRIC AND COMMUNICATIONS | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Digging to put in utilities service was damaged by mini Excavatorï¿½
Southern California Gas Company | N | KERN | BAKERSFIELD | 2020-03-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TRITON ELECTRICAL INC | HESPERIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Trenching for electrical and struck gas stubï¿½
Southern California Gas Company | N | KERN | BAKERSFIELD | 2020-12-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | CALIFORNIA CONCRETE DESIGN | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Concrete Company was pulling out Tree stump and hit service. NO USAï¿½
Southern California Gas Company | N | KERN | BAKERSFIELD | 2020-01-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | JOSE RODRIGUEZ | BAKERSFIELD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was having rose bushes removed and damaged company facilityï¿½
Southern California Gas Company | N | KERN | BAKERSFIELD | 2020-10-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | KERN COUNTY PUBLIC WORKS ROADS DIVISION | BAKERSFIELD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per LCT Jerry Marsh Kern County Inspector Scott Cunningham of the County Roads Division was testing ground compaction with a pogo stick in preparation for future sidewalk work.ï¿½ Cunningham claims he was doing work in the area at approx. 930AM and was unaware that he had hit our service line.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2020-01-16 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PCL CONSTRUCTION | BAKERSFIELD | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | PCL construction was excavating to build a structure and piping system and hit our main they had worked outside of delineation called by the USAï¿½
Southern California Gas Company | N | KERN | BAKERSFIELD | 2020-12-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Resident was digging for a drain to install and was digging over the service and hit it with a shovel. All mark were visible and located correctly. struck service within Delineation.ï¿½
Southern California Gas Company | N | KERN | BAKERSFIELD | 2020-01-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | BAKERSFIELD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | SERVICE LINE DIGGING SPRINKLER PIPE UP HIT BY SHOVEL
Southern California Gas Company | N | KERN | BAKERSFIELD | 2020-02-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | BAKERSFIELD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner had been augering for posts for fence and hit our service Customer did not have active USAï¿½
Southern California Gas Company | N | KERN | BAKERSFIELD | 2020-03-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HERITAGE EQUIPMENT COMPANY | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Framer was Excavating to install ï¿½water line and damaged our 2 Main marks were visible and USA Validï¿½
Southern California Gas Company | N | KERN | BAKERSFIELD | 2020-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | BALLES NURSERY | BAKERSFIELD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscaping company ï¿½was digging to install catch basin on the side of the house and struck or service with digging barï¿½
Southern California Gas Company | N | KERN | BAKERSFIELD | 2020-08-11 | Operator excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | LYLES UTILITY | BAKERSFIELD | CA | Y | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | On August 11, 2020 at 2416 Dean Ave, Bakersfield, a 1ï¿½ plastic natural gas service was damaged with a shovel by a second party contractor installing meter guards causing a leak. SoCalGas crews responded and controlled the gas. No injuries or further damage resulted from this incident. Investigation of the incident showed that there was no valid USA ticket. The incident was reported to CPUC when SoCalGas became aware of media coverage.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2020-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BG LANDSCAPE SERVICES | BAKERSFIELD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscapers were driving stakes in for trees to have them supported and drove stake into our 1 inch serviceï¿½
Southern California Gas Company | N | KERN | BAKERSFIELD | 2020-04-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CAL WATER COMPANY | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Cal Water struck and danged our service right over the delineated marks with a listening rodï¿½
Southern California Gas Company | N | KERN | BAKERSFIELD | 2020-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | KEVIN DUNN CONSTRUCTION | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor Using trencher for irrigation line onï¿½ Nursery Property and damaged 1 inch serviceï¿½
Southern California Gas Company | N | KERN | BAKERSFIELD | 2020-08-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | WARD CONCRETE | GRANITE BAY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Concrete Company for apartment was setting form for Driveway and hit service with concrete stakeï¿½
Southern California Gas Company | N | KERN | BAKERSFIELD | 2020-06-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | BAKERSFIELD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was auger drilling holes to install fence posts and damaged service. gas had migrated to foundation and evacuated homes
Southern California Gas Company | N | KERN | BAKERSFIELD | 2020-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CROWN COMMUNICATIONS | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Crown Communications was pot holing for work to be done by bore machine and broke the serviceï¿½
Southern California Gas Company | N | KERN | BAKERSFIELD | 2020-08-05 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | TEICHRET | NA |  | Y | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was installing service and was not using proper caution when excavating around GASCO facilityï¿½
Southern California Gas Company | N | KERN | BAKERSFIELD | 2020-08-06 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | TEICHERT PIPELINE | CHINO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Teichert Pipelines was installing New services to Apartment and they were digging around facility not using caution and had hit our service line with shovelï¿½
Southern California Gas Company | N | KERN | BAKERSFIELD | 2020-01-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | WALLACE SMITH GENERAL CONTRACTORS | BAKERSFIELD | CA | N | Y | Yes | No | Yes | Yes | No | Yes | No | DIGGING TO INSTALL SEWER LINE
Southern California Gas Company | N | KERN | BAKERSFIELD | 2020-08-18 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | NA |  | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | CT was digging to repair leak and failed to use caution while digging up service and hit it with shovelï¿½
Southern California Gas Company | N | KERN | BAKERSFIELD | 2020-10-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | LAZAR UNDERGROUND CONSTRUCTION | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was digging to splice ATandT and hitï¿½
Southern California Gas Company | N | KERN | BAKERSFIELD | 2020-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | NA | BAKERSFIELD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer was digging fence post and damaged gas service. No USA was called.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2020-11-27 | Third party excavation damage | Main | Polyethylene Pipe | Probing Device | 2 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | CAL WATER SERVICE | NA |  | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Cal Water Service employee Angel Hinojos appeared to have hit the main while probing trying to locate their water line. His contact number is 6614287503
Southern California Gas Company | N | KERN | BAKERSFIELD | 2020-01-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  |  | NA | NA | BAKERSFIELD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner had previously prior to Gas Co Coming to Location had put in an additional fence pouring concrete and putting fence post directly over service which had created a leakï¿½
Southern California Gas Company | N | KERN | BAKERSFIELD | 2020-05-07 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 4 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 11740 |  | 0 |  | LEO TIDWELL EXCAVATING | PASO ROBLES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On 05-07-2020, SoCalGas received a report of a third-party damage at 9600 Brimhall Rd, Bakersfield, while a contractor hit a 4-inch plastic gas main boring for Verizon conduit. Gas crews responded, controlled the gas, and made permanent repairs by replacing a section of main by method of fusion. There were no injuries or further damages resulted from this incident. Investigation of the incident showed the contractor had potholed the marked 4-inch main but did not bore deep enough and clipped the bottom of main with directional bore. The contractor did not exercise adequate caution while boring near gas main. This incident was reported to CPUC when SoCalGas became aware of media coverage.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2020-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PACIFIC UTILITIY | PORTERVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Pacific Utility was digging to install electric and hit stub with shovelï¿½
Southern California Gas Company | N | KERN | BUTTONWILLOW | 2020-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RTS AGRI BUSINESS LLC | BAKERSFIELD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Demo of mobile homes in a farm field and struck old service lineï¿½
Southern California Gas Company | N | KERN | CALIFORNIA CITY | 2020-08-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | CAL CITY WATER | CALIFORNIA CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit our service line with probe while trying to uncover our facility.ï¿½
Southern California Gas Company | N | KERN | DELANO | 2020-01-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | DELANO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged Service working in Yard and was unaware of any 811 Call for creating a USAï¿½
Southern California Gas Company | N | KERN | DELANO | 2020-03-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit service while working on a water line
Southern California Gas Company | N | KERN | DELANO | 2020-11-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 7 |  | NA | DELANO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was digging to put in a tree and dug in to service using Post Hole Diggerï¿½
Southern California Gas Company | N | KERN | DELANO | 2020-03-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JM PIPELINE CONSTRUCTION COMPANY | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor states that the shoring box due to cave in came down and struck the gas line there was no shoring box in trench near service and contractor states it happened or broke after they had left the job site Contractor should be billed for damage
Southern California Gas Company | N | KERN | FRAZIER PARK | 2020-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ELITE ROOTER | CAMARILLO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Elite Rooter failed to call in an USA ticket before excavating to repair a water line.ï¿½
Southern California Gas Company | N | KERN | FRAZIER PARK | 2020-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Augur | 0.75 | 58 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | HAMPTON TEDDER | MONTCLAIR | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor working for Edison was augering to install a new power pole and damaged gas company line.ï¿½
Southern California Gas Company | N | KERN | LAMONT | 2020-08-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | LAMONT | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant was trying to removeï¿½a tree out of his yard and hit he service with a shovelï¿½
Southern California Gas Company | N | KERN | LAMONT | 2020-02-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 52 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | LAMONT | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was attempting to repair irrigation Sprinkler line and hit our serviceï¿½
Southern California Gas Company | N | KERN | LEBEC | 2020-03-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | none
Southern California Gas Company | N | KERN | LOST HILLS | 2020-01-27 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 13 |  | PRECISION GRADING AND PAVING | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Paving Contractor was excavating a concrete column to be removed in a portion of rd that had been taken down below subgrade while removing column excavator had hit our 3 Mainï¿½
Southern California Gas Company | N | KERN | LOST HILLS | 2020-09-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | LOST HILLS TRAILER PARK | LOST HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Facility not marked. Owner was doing landscaping and irrigation and hit while using shovelï¿½
Southern California Gas Company | N | KERN | MCFARLAND | 2020-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 3 |  | MORTON BROWN PLUMBING | DELANO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber was digging trench to fix sewer line ï¿½as they were digging had hit our service.
Southern California Gas Company | N | KERN | MOJAVE | 2020-05-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | MOJAVE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer excavating for a new sewer line found a root and cut it out with a sawzall. The customer did not see the gas service in the root.
Southern California Gas Company | N | KERN | MOJAVE | 2020-02-10 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 338 | 325 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | KEMIRA WATER SOLUTIUONS INC | MOJAVE | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No | No damage to SUOF. | No damage to SUOF. | property owner unloading and moving steel beams at night backing intoï¿½
Southern California Gas Company | N | KERN | PERRIS | 2020-12-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RANCHO WEST LANDSCAPING | MURRIETA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Crew was called out for a No Gas order. Upon further investigation, they discovered that the gas service had been damaged and backfilled without notifying the Gas Co.
Southern California Gas Company | N | KERN | SHAFTER | 2020-04-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | QUEST IRRIGATION | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was digging to install water line and had struck 0.75 unknown line. line previously shows had been abandoned and was not done correctlyï¿½
Southern California Gas Company | N | KERN | SHAFTER | 2020-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | RV AG SERVICES | PORTERVILLE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | RV Ag Service hit service trying to locate out their irrigation line. USA ticket was Expiredï¿½
Southern California Gas Company | N | KERN | SHAFTER | 2020-09-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PGE | WASCO | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | PGE was installing pole when service that had been installed on 914 was hit. PGE called in ticket 92 and ticket was addressed 94. Work done after USA was called PGE was un not aware of service. ETD had Located facilities with in delineation of ticket. New service was installed after was marked for work to beginï¿½
Southern California Gas Company | N | KERN | SHAFTER | 2020-02-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | SHAFTER | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Was digging to remove damaged fence post and hit the service customer did not have USA
Southern California Gas Company | N | KERN | TEHACHAPI | 2020-06-19 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 37 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ARIZONA PIPELINE | CHATSWORTH | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Company Contractor APL had damaged a 0.5 inch CTS service while hand excavating during a service replacement.
Southern California Gas Company | N | KERN | TEHACHAPI | 2020-01-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 3 |  | NA | TEHACHAPI | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | HO excavating to install irrigation lines
Southern California Gas Company | N | KERN | TEHACHAPI | 2020-12-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | NA | TEHACHAPI | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | homeowner hit plastic gas service with shovel
Southern California Gas Company | N | KERN | TEHACHAPI | 2020-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 37 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SOUTHERN SIERRA CONSTRUCTION | TEHACHAPI | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | EXPIRED USA
Southern California Gas Company | N | KERN | TEHACHAPI | 2020-04-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 37 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SOUTHERN SIERRA CONSTRUCTION | TEHACHAPI | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | expired USA ticket, service was located correctly, flags and whiskers were still present. contractor failed to take precaution
Southern California Gas Company | N | KERN | TEHACHAPI | 2020-05-23 | Third party excavation damage | Riser | Steel | Backhoe/Trackhoe | 0.75 | 37 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | BELFOR | BAKERSFIELD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor demolishing a large shed caused some debris to fall on the MSA that served the main house. No request for abandonment pending.
Southern California Gas Company | N | KERN | TEHACHAPI | 2020-05-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 37 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | TEHACHAPI | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hand exposing leaking water service found large roots. Used sawzall to remove roots. Gas service fully encased in root was cut in the process.
Southern California Gas Company | N | KERN | WASCO | 2020-02-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | WASCO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was trenching to build a block wall and damaged the 0.5inch serviceï¿½
Southern California Gas Company | N | KERN | WASCO | 2020-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | TRIPLE CROWN FENCE | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | USA ticket was expired. Was augering for fence postsï¿½
Southern California Gas Company | N | KERN | WASCO | 2020-12-07 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 1 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 3 |  | NA | NA |  | Y | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | none
Southern California Gas Company | N | KINGS | CHINO | 2020-10-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GREENBE CONCRETE | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor trenching for footings of new homes. No USA ticket
Southern California Gas Company | N | KINGS | HANFORD | 2020-01-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | HOTLINE CONSTRUCTION | PORTERVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was digging for electric project damaged a 1 plastic main crew made permanent repairs
Southern California Gas Company | N | KINGS | HANFORD | 2020-02-12 | Third party excavation damage | Miscellaneous/Other | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CARVALHO CONSTRUCTION | LEMOORE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to pothole the gas line as required
Southern California Gas Company | N | KINGS | HANFORD | 2020-02-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | IRISH ELECTRIC | TULARE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged a 0.5inch plastic gas service contractor pot holed over mark and was unable to confirm pipe location contractor failed to notify our locator about not finding the gas line
Southern California Gas Company | N | KINGS | HANFORD | 2020-03-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 4 |  | HOTLINE CONSTRUCTION | PORTERVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | NA
Southern California Gas Company | N | KINGS | HANFORD | 2020-11-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | REYES CONSTRUCTION | PORTERVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Per LCT Luis Lopez Reyes Construction hit 0.5 inch plastic service with shovel while excavating to installï¿½electrical facilities.
Southern California Gas Company | N | KINGS | HANFORD | 2020-02-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | IRISH ELECTRIC | TULARE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor had USA ticket but the marks by the locator were off
Southern California Gas Company | N | KINGS | HANFORD | 2020-05-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | HANFORD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer was digging to install fence when service was struck. USA was not notified. Customer educated on USA laws. Crew made permanent repairs.ï¿½
Southern California Gas Company | N | KINGS | HANFORD | 2020-02-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TDJ CONSTRUCTION | HANFORD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor did not call for a valid USA ticket prior to digging
Southern California Gas Company | N | KINGS | HANFORD | 2020-12-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | HANFORD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant damaged a 0.5 inch plastic gas line, crew made permanent repairs.
Southern California Gas Company | N | KINGS | HANFORD | 2020-09-08 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  | 2 |  | ROGER STOCKTON | HANFORD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was installing a sewer lateral with no USA ticket and damaged our 2 inch main.
Southern California Gas Company | N | KINGS | HANFORD | 2020-02-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | CENTRAL VALLEY INFILL DEVELPMENT | FRESNO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging for electrical work and damaged the gas line contractor was educated about USA law
Southern California Gas Company | N | KINGS | HANFORD | 2020-02-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CENTRAL VALLEY INFILL DEVELOPMENT | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hand digging over marked facility did not maintain clearance when digging
Southern California Gas Company | N | KINGS | LEMOORE | 2020-11-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | BUSH CONSTRUCTION | HANFORD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged a 2 inch plastic gas line, crew made permanent repairs.
Southern California Gas Company | N | KINGS | LEMOORE | 2020-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 0.75 | 400 | 390 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | CALTRANS | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Cal trans pulled up HP service while excavating without a USA ticket.
Southern California Gas Company | N | LOS ANGELES | ACTON | 2020-08-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | ACTON | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant Rick Ramirez damaged service line with shovel while installing electrical conduit.
Southern California Gas Company | N | LOS ANGELES | AGOURA HILLS | 2020-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | LPGC CUSTOM BUILDS | OXNARD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit service while digging
Southern California Gas Company | N | LOS ANGELES | AGOURA HILLS | 2020-05-01 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ARB | NA |  | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Company contractor ARB had struck a 0.5 inch CTS service line while hand digging.
Southern California Gas Company | N | LOS ANGELES | AGOURA HILLS | 2020-05-01 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ARB | NA |  | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor ARB damaged 0.50 CTS service while hand excavating.
Southern California Gas Company | N | LOS ANGELES | AGOURA HILLS | 2020-06-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | IMAGINE BUILDERS INC | CANOGA PARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging with no USA ticket but marks were still on concrete due to old USA ticket
Southern California Gas Company | N | LOS ANGELES | AGOURA HILLS | 2020-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | IMAGINE BUILDERS | CANOGA PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor digging out around the footing of house and hit gas line
Southern California Gas Company | N | LOS ANGELES | AGOURA HILLS | 2020-07-20 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ARB INC | LAKE FOREST | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service was damaged while contractorï¿½was exposingï¿½gas line.
Southern California Gas Company | N | LOS ANGELES | AGOURA HILLS | 2020-10-09 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 35 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ARB | NA |  | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | ARB INC was working on services for a DIMP Main Replacement when they nicked a plastic service line. ARB crew had new service line in and abandoned the old line at SMC. no repair was required.
Southern California Gas Company | N | LOS ANGELES | AGOURA HILLS | 2020-04-17 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | PSC | LAKE FOREST | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor ARB installing a new service. Laborers first day and damaged existing gas service with shovel.
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2020-04-22 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RITZ PLUMBING | LOS ANGELES | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | Plumber cut riser with sawzaw by mistake. He thought it was the house line.
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2020-07-07 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | DRAGON BUILDERS | FULLERTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor did not call USA.
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2020-12-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | ALHAMBRA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner digging to install irrigation lines hit branch gas service No usa was called inï¿½
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2020-07-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | EFI ENGINEERING | TUSTIN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was potholing gas service.
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2020-11-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 4 |  | WESTERN ROOTER | ALHAMBRA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per LCT Mario Souquette Western Rooter employees hit SCG service line with shovels while excavating to perform sewer work.
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2020-12-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | VCI CONSTRUCTION | UPLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to maintain a safe distance while using Mini Excavator near out gas facilityï¿½
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2020-08-12 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 2 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | EFI ENGINEERING | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit service while potholing
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2020-01-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 3 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | VERDUZCO ELECTRIC INC | COMPTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | CONTRACTOR HIT 3 PLASTIC MAIN WITH SHOVEL DAMAGE VERY TINY COULD BARELY TELL ANY DAMAGE OCCURRED NEEDED SOAPY WATER TO IDENTIFY LEAK HAD TO ALTER MAIN FOR PERMANENT REPAIR
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2020-10-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | ALHAMBRA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hit line with shovel while installing fence.
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2020-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 7 |  | INTERNATIONAL LINE BUILDERS | JURUPA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor working for Edison installing anchors when gas service was hit with sharp shooter shovel.
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2020-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ALLEN PIPELINE INC | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor performing the work failed to expose the 0.5 inch plastic line by hand.
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2020-10-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JUAN LOPEZ LANDSCAPING SERVICES | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor installing fence hit line with shovel.
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2020-02-06 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1.25 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | VCI | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor broke plastic service line with backhoe Service was marked
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2020-02-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | VCI | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor dug with a backhoes and hit our service
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2020-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | EBA TEAM | COLUMBUS | OH | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was using a mini excavator to dig within 24 inch of our plastic main without hand exposing.
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2020-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HENKLES AND MCCOY | BALDWIN PARK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | CONTRACTOR HIT PLASTIC SERVICE OUTSIDE OF SPECIFIED WORK AREA. PER TICKET TO MARK WITHIN 25 SERVCE HIT AT 27
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2020-08-26 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 4 |  | ROBERT BRKICH CONSTRUCTION CORP | MONROVIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit 2 inch plastic main with back hoe
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2020-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | BRKICH CONSTRUCTION CORP | MONROVIA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Damaged 1 service while trenching to install Water. Contractor did not expose line prior to excavating.
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2020-09-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | J C RAMIREZ CONSTRUCTION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party doing work for resident was open trenching for irrigation and houseline for gas. Crew hit service because they did not call USA.
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2020-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ROBERT BCKICH CONSTRUCTION INC | MONROVIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | CONTRACTOR HIT PLASTIC SERVICE WITH SHOVEL WHILE ATTEMPTING TO EXPOSE SERVICE. HARD ROCKY SOIL CONDITIONS.
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2020-08-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | LANARD JENKINS | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Sawzall used to cut out an water line when he accidentally cut into gas line
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2020-05-01 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 3 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  |  | NA | EFI ENGINEERING | TUSTIN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor bored into pla main
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2020-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JESUS CARBAJAL | ALTADENA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CONTRACTOR WAS USING A JACK HAMMER TO BREAK CONCRETE IN THE WAY OF PLANTING A TREE WHEN HE HIT AN UNMARKED LINE DUE TO NO USA.
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2020-04-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | EFI ENGINEERING | TUSTIN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractors hit service while hand digging trying to expose plastic line
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2020-11-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ALLEN PIPELINE INC | MONROVIA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor hit plastic service while trenching. Did not attempt to pothole service to verify location. Service was mismarked not locatable and mark via company measurement.
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2020-10-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 4 |  | ROBERT BRKICH CONTRUCTION CORP | MONROVIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor installing water line hit gas service with backhoe. Did not hand expose the plastic service.
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2020-07-13 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 4 |  | EFI ENGINEERING | TUSTIN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | utility crew installing conduit pot holed over the marks before boring but exposedï¿½the old steel lines and assumed that they were the activeï¿½gas lines. The marks clearly stated that the line was plastic and the crew failed to proper expose the active gas lines ahead of directional boring.ï¿½
Southern California Gas Company | N | LOS ANGELES | ARCADIA | 2020-11-24 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | HARDY HARPER INC | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Locator did mark earlier in project. marks had faded due to traffic or due to work. Locator says that he marked the end of main according to GIS footages. Contractor was instructed to call hand digï¿½when they got to end of main and failed to do so. Contractor failed to exposed main by hand and did so with backhoe.
Southern California Gas Company | N | LOS ANGELES | ARCADIA | 2020-05-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | ARCADIA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA WAS REQUESTED, DIGGING FOR SPRINKLERS
Southern California Gas Company | N | LOS ANGELES | ARCADIA | 2020-12-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | TRIPLE M CONCRETE | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged coupling at riser while excavating for concrete footing
Southern California Gas Company | N | LOS ANGELES | ARCADIA | 2020-01-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ROCKWOOD DEVELOPMENT | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | digging to install sewer lines CONTRACTOR WAS DIGGING WITH THE BACKHOE WHEN THEY HIT THE PLASTIC SERVICE ï¿½ CONTRACTOR COULD NOT PROVIDE US WITH A TICKET NUMBER ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | ARCADIA | 2020-06-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BADE CONSTRUCTION INC | ARCADIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit plastic service with shovel. No USA
Southern California Gas Company | N | LOS ANGELES | ARCADIA | 2020-05-16 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | S G PLUMBING | SAN CARLOS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 0.75 inch steel service with hacksaw in the process of cutting tree roots to install sprinkler system.
Southern California Gas Company | N | LOS ANGELES | ARCADIA | 2020-04-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | ARCADIA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner damaged 0.5 inch plastic service with shovel while digging to repair water line. Gas company crew onsite informed customer to call USA 811 at anytime when planning to dig so the utilities can be located.
Southern California Gas Company | N | LOS ANGELES | ARCADIA | 2020-09-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | GARCIA LANDSCAPING | ARCADIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscaper hit plastic service with shovel while digging to plant a tree. No USA was called.
Southern California Gas Company | N | LOS ANGELES | ARCADIA | 2020-08-31 | Third party excavation damage | Main | Steel | Directional Drilling | 2 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5252 |  | 7 |  | EFI ENGINEERING | TUSTIN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On 08-31-20, SoCalGas was notified of a third party damage at 50 N 1st Ave. The third party contractor was boring in fiber optic conduit. As the bore rod was pulled back a 2 inch steel gas main was damaged. SoCalGas personnel were sent to the scene and safely controlled the gas. There were no injuries or further damages resulting from this incident. The investigation showed the contractor had a valid USA ticket A202190651. The main was correctly marked and exposed (potholed). This was reported to the CPUC due to the release of gas and media coverage.
Southern California Gas Company | N | LOS ANGELES | ARCADIA | 2020-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  | 1 |  | VP DESIGN CONSTRUCTION | SHERMAN OAKS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor failed to call in USA. Damaged Company facility
Southern California Gas Company | N | LOS ANGELES | ARCADIA | 2020-01-27 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | PASADENA WATER COMPANY | PASADENA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging to repair water leak
Southern California Gas Company | N | LOS ANGELES | ARTESIA | 2020-11-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | J A SALAZAR CONSTRUCTION | LA HABRA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Water Company Contractor, Ruben Quezada, stated that they hit service while digging to expose our facilities. Markings were right on line.
Southern California Gas Company | N | LOS ANGELES | ARTESIA | 2020-11-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DOMINGUEZ GENERAL ENG INC | POMONA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Water Contractor was digging by hand attempting to expose facility
Southern California Gas Company | N | LOS ANGELES | AZUSA | 2020-11-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | ANDRES CHAVEZ | ONTARIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was putting in wood forms to pour a foundation and they came across out 0.75in steel casing. It was in their way and they wanted to cut it out. They did not have a USA and did not know that an active plastic service was in the casing.ï¿½
Southern California Gas Company | N | LOS ANGELES | AZUSA | 2020-05-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | AZUSA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | home owner broke service line with shovel
Southern California Gas Company | N | LOS ANGELES | AZUSA | 2020-09-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 4 |  | ROOTER MAN LA | SUN VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | sewer contractor didnt call USA and hit CTSï¿½service while pot holing for boring in new sewer.ï¿½
Southern California Gas Company | N | LOS ANGELES | AZUSA | 2020-10-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CITY OF AZUSA WATER | AZUSA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Azusa Water Company Hit Plastic Service With Shovel While Working A Water Leak.
Southern California Gas Company | N | LOS ANGELES | BALDWIN PARK | 2020-03-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | E R CONSTRUCTION | BALDWIN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | CONTRACTOR WAS TRENCHING FOR NEW WATER WHEN THEY HIT THE PLASTIC SERVICE ï¿½ SERVICE WAS MARKED
Southern California Gas Company | N | LOS ANGELES | BALDWIN PARK | 2020-04-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | GENTRY BROTHERS | BALDWIN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service marked correctly butï¿½was shallow. Buried just under asphalt. Backhoe was used to pull up large piece of asphalt and pulled service with it. No way to avoid this.
Southern California Gas Company | N | LOS ANGELES | BALDWIN PARK | 2020-11-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | BALDWIN PARK | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | none
Southern California Gas Company | N | LOS ANGELES | BALDWIN PARK | 2020-12-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | NA | BALDWIN PARK | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | damage service while digging with backhoe no usa
Southern California Gas Company | N | LOS ANGELES | BELL GARDENS | 2020-07-30 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 28 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | JT DEVELPMENT | LA VERNE | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service while digging to install bollards
Southern California Gas Company | N | LOS ANGELES | BELL GARDENS | 2020-09-09 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 28 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LMS ELECTRIC | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to expose pipe by hand digging prior to trenching with backhoe
Southern California Gas Company | N | LOS ANGELES | BELL GARDENS | 2020-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 28 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | D CORPORATION | NUEVO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor struck gas service while trenching for water main installation.ï¿½ Gas service was not located due to MSA inaccessibility.
Southern California Gas Company | N | LOS ANGELES | BELL GARDENS | 2020-01-24 | Third party excavation damage | Riser | Steel | Backhoe/Trackhoe | 0.75 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MADRIGAL CONSTRUCTION | WHITTIER | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | On 1 24 20 While grading a vacant lot where the house had already been demolished third party contractor Manuel Tinajero damaged a one half inch gas service with a backhoe ï¿½ Manuel had stated that he thought the gas service had already been abandoned since the house was already demolished ï¿½ Manuel did not call DigAlert notifying them of his work and he did not have a valid USA ticket ï¿½ SCG supervisor explained the importance of calling USA prior to any excavations ï¿½ Manuel said that he understood ï¿½ SCG crew arrived on scene and made repairs by cutting back the gas service ï¿½ Manuel was told that he or his boss would need to call SCG to have a planner plan a full abandonment and that the live gas service was still within the property
Southern California Gas Company | N | LOS ANGELES | BELL GARDENS | 2020-05-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 28 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | BELL GARDENS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | USA not notified
Southern California Gas Company | N | LOS ANGELES | BELLFLOWER | 2020-05-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | BELLFLOWER | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | On 5 30 20 while hand digging with a shovel to repair a leaking gas house line, home owner Ken Grant damaged a one half inch plastic gas service.ï¿½ Mr. Grant did not notify Dig Alert of the work he was doing and did not have a valid USA ticket.ï¿½ SCG crew arrived on site and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | BELLFLOWER | 2020-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | FODDRILL CONSTRUCTION | CHINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor while hand digging struck 0.5 inch plastic service .
Southern California Gas Company | N | LOS ANGELES | BELLFLOWER | 2020-12-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NATIONAL OIL WELL ARCO | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Per Armando Quirarte Lct Workers Were Digging Around Concrete Footing Of Street Light Pole In Order To Remove It And Strucked Plastic Pipeline While Digging.ï¿½
Southern California Gas Company | N | LOS ANGELES | BELLFLOWER | 2020-10-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MARJANI BUILDERS | MISSION VIEJO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor hit a shovel with a shovel while digging in the area of the marks.
Southern California Gas Company | N | LOS ANGELES | BELLFLOWER | 2020-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | BELLFLOWER | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Trying to locate gas line and the contractorï¿½ended up hitting our line with shovel.
Southern California Gas Company | N | LOS ANGELES | BELLFLOWER | 2020-11-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 5 |  | TURN AROUND COMMINUTION | BALDWIN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor Damaged A Plastic Service With A Directional Bore Machine Prior To Verifying The Marks. Per The Locator The Marks Were Not Visible, Possible Removed Or Washed Off By Contractor During Their Work. No Remarks Were Called In.
Southern California Gas Company | N | LOS ANGELES | BELLFLOWER | 2020-10-12 | Third party excavation damage | Riser | Polyethylene Pipe | Hand Tools | 1 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MARJANI BUILDERS | MISSION VIEJO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per Damage Report USA Not Required.ï¿½Contractor Was Working On Houseline Leak Repair At The Property And Tried To Turn The Service Valve Off. The Tang Broke Off Causing Uncontrolled Gas To Be Released.
Southern California Gas Company | N | LOS ANGELES | BELLFLOWER | 2020-04-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | BARRAZA SONS | BELL GARDENS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Trying to remove a tree stump and damaged line with sawzall in private property.
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2020-08-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | KENN CO | SANTA CLARITA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | contractor hit plastic service while digging in trench with shovel
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2020-07-06 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | MIETZER ENGINEERING | CASTAIC | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 2 inch PLA main damaged with backhoeï¿½
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2020-11-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | MOON NURSERY | BEVERLY HILLS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5 IPS PE Service hit by 3rd Party contractor while attempting to install tree. Homeowner refused to provide contractor info and is taking responsibility for damage. Note, line was marked however no valid USA was found for the work.
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2020-10-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HAMPTON TEDDER ELECTRIC | MONTCLAIR | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Damaged 0.5 inch cts service with shovel
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2020-11-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | TORO ENTERPRISES | OXNARD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor was excavating in the street to replace a water main. The contractor hit a 1 inch PLA service with a backhoe.
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2020-04-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | GLOBUS BUILDERS | NORTH HOLLYWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 0.50 IPSï¿½ service while hand digging to install retaining walls.
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2020-02-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | SUBSURFACE DESIGNS INC | SYLMAR | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1 service with shovel
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2020-03-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MONDRAGON BUILDERS | LANCASTER | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | IPS plastic service hit with shovel by contractor laborer
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2020-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | RICHARD LUSK LANDSCAPE DESIGN | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While performing pool excavation contractor hit 0.5 CPS
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2020-11-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CENTURY PLUMBING INC | RESEDA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer contractor was preparing a trench for SoCalGas pipeline installation.ï¿½ Our company contractor was scheduled to come out and install the new service into the customer provided trench the next week.
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2020-03-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | WILLIE GRIFFIN | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While hand excavating for drainage repair 3rd party excavator struck and damaged 0.5inch PLA service Spoke with Willie Griffin and he stated he didn t think he needed to call USA Informed him to call USA to issue emergency ticket and then wait 48 business hours before excavating again
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2020-05-22 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | PADILLA CO INC CSLB564257 | SAN FERNANDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 0.75 steel service with backhoe while doing demolition related work on property. NO USA. Marks from another ticket visible and accurate.
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2020-11-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TORO ENTERPRISE | OXNARD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 1 inch pla service while digging to install water. Henry Campos was the incident commander for this incident.
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2020-05-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | BEVERLY HILLS | CA | N | Y | Yes | Excavation occurred on private property by a non-contractor. | Yes | Yes | No | Yes | Yes | 0.50 inch CTS service struck with shovel
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2020-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ROCCOBELA | SANTA MONICA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 0.5 inch IPS service with shovel while digging entry gate pilon hole for new gate.
Southern California Gas Company | N | LOS ANGELES | BRADBURY | 2020-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | FOWLER CONSTRUCTION | ALTA LOMA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CONTRACTOR WAS INSTALLING A NEW WATER SERVICE TO A NEW CONSTRUCTION HOME WHEN THEY HIT OUR 2 PLASTIC SERVICE ï¿½ CONTRACTOR STATED THAT THEY NEW THE LINE WAS THERE AND FORGOT ABOUT IT ï¿½ WE FOUND THAT THE CONTRACTOR WAS INSTALLING THE NEW WATER MAIN TOO CLOSE TO THE GAS SERVICE AND DIDN T HAVE A MINIMUM 3 CLEARANCE ï¿½ THE CREW CUT THE SERVICE BACK TO THE NEAREST POINT THAT HAD THE MINIMUM CLEARANCE
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2020-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JOSE HERNANDEZ | NORTH HOLLYWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer was getting a new sewer line exposed for replacement.ï¿½ ï¿½Existing line close to Gas Service line.ï¿½ ï¿½Service line was in their way and they proceeded to cut Steel Gas Service with Sawzall.ï¿½ ï¿½
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2020-08-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ROOTER GUARD | VAN NUYS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | hit 0.5ï¿½PE service
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2020-11-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | NA | BURBANK | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit service line while grading.ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2020-03-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 4 |  | DRAIN DEFENDER | NORTH HOLLYWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumbing company contracted to work on sewer line for homeowner damaged the plastic service inside copper casing with a hacksaw The plumbers thought the steel line next to it was the gas line They failed to notify USA prior to digging
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2020-10-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | BURBANK | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer cut into service line with angle grinder while attempting to plant tree. USA was not called. Customer was advised to contact USA for any future digging projects.
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2020-07-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 15 |  | NA | CHINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Belco struck line with boring machine due to not exposing marked gas service.ï¿½
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2020-05-29 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DELTA PIPELINE INC | LONG BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Developer had exposed service and main when excavating for storm drain access point. Trench box was used to support the excavation. The trench box had to be extracted at an angle due to overhead power pole anchor line over excavation. When the box was lifted, it caughtï¿½the service causing the damage.
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2020-02-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | BURBANK | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant cutting tree roots out of post hole for new fence using a sawzall tool The service was embedded in the tree root No USA ticket for this location
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2020-10-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | YEN LANDSCAPING DESIGN | BURBANK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 0.5 inch plastic service line with shovel while digging for irrigation. USA was not called.
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2020-12-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3830 |  | 2 |  | NA | SUN VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor was excavating to install a fiber optic vault with a back-hoe and struck a 2inch plastic main causing a gas leak. Crew responded and controlled the leak. Investigation of the incident determined the excavator failed to use hand tool where required. This incident was reported to CPUC when SoCalGas became aware of media coverage.
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2020-06-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PROFESSIONAL PLUMBING SERVICES | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service line while excavating to make repairs to water houseline
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2020-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | LANDOM CONSTRUCTION | TUJUNGA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Laborer struck line while trying to expose water line for repairs.ï¿½ ï¿½Gas Service line repeatedly hit by laborer and was properly marked.ï¿½
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2020-08-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | BURBANK | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner was using a backhoe and they hit the plastic service.
Southern California Gas Company | N | LOS ANGELES | CALABASAS | 2020-09-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | LIL JOHN S ROOTER PLUMBING | VENTURA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hand digging to expose old sewer line.
Southern California Gas Company | N | LOS ANGELES | CALABASAS | 2020-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 42 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LIL JOHN ROOTER PLUMBING | VENTURA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor performing work for Mobile home park damaged 0.5 IPS
Southern California Gas Company | N | LOS ANGELES | CALABASAS | 2020-01-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MARK CONRAD | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per GIS Svc to prop is shown extending from Woodman into prop ï¿½ No other svc shown ï¿½ Patch in st indicates svc was abandoned dry hole ï¿½ Branch extending from 7024 extended into 7040 ï¿½ Building was demo d and old branch was damaged ï¿½ Capped branch at damage and heavily marked line with paint to PL ï¿½ Will put in for full abandonment ï¿½ No one on site found service abandonment was never done ï¿½ No USA found for demo
Southern California Gas Company | N | LOS ANGELES | CALABASAS | 2020-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ALPHA TWO OMEGA | SYLMAR | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damagedï¿½ 0.5 CTS service , didnt hand expose
Southern California Gas Company | N | LOS ANGELES | CALABASAS | 2020-12-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ROOTER MAN | SUN VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging to make repairs for sewer lateral with no USA
Southern California Gas Company | N | LOS ANGELES | CALABASAS | 2020-06-03 | Third party excavation damage | Riser | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | JOSE LOTZOJ | PASADENA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was installing natural gas line when they struck the meter. No USA.
Southern California Gas Company | N | LOS ANGELES | CALABASAS | 2020-12-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | HAMPTON TEDDER | VENTURA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit marked gas service whileï¿½digging for electrical.
Southern California Gas Company | N | LOS ANGELES | CALABASAS | 2020-03-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | TIDWELL EXCAVATING | NORWALK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor for Edison hit 1 plastic line while digging hole over marked gas service Gas did not migrate Tidwell excavating worker was Danny Zozaya
Southern California Gas Company | N | LOS ANGELES | CALABASAS | 2020-08-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | EKACERINA | CALABASAS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NOUSA contractor damaged 1 inchPLA service with Backhoe
Southern California Gas Company | N | LOS ANGELES | CALABASAS | 2020-11-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | WARP CORPORATION | SANTA PAULA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd. Party Contractor failed to pothole over gas service
Southern California Gas Company | N | LOS ANGELES | CALABASAS | 2020-12-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 44 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | BENS ASPHALT CONCRETE | SANTA ANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor claimed large rock fell on buriedï¿½service and severed gas line.
Southern California Gas Company | N | LOS ANGELES | CALABASAS | 2020-12-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LA BULD CORP UNITED EXCAVATING GROUP | WOODLAND HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | Contractor excavating outside of delineation. Domo at concrete slab for where a trash Bin enclosure was previously located.ï¿½
Southern California Gas Company | N | LOS ANGELES | CANOGA PARK | 2020-06-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged our service with a backhoe while trenching to install conduit.ï¿½ No one on scene to get damaging info.
Southern California Gas Company | N | LOS ANGELES | CANOGA PARK | 2020-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GROUND BREAKERS CONSTRUCTION | LEBEC | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damage NB service, no meters , deadend Cap with Backhoe no USA.
Southern California Gas Company | N | LOS ANGELES | CANOGA PARK | 2020-01-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ARAM CHOLLIYAN | CANOGA PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor doing trenching for sewer line ï¿½ Hit plastic service with shovel ï¿½ Not only had to fix damage section but had to replace 4 feet of branch due to contractor pouring concrete over service ï¿½ 2nd time svc has been hit in the same place ï¿½ Line was marked correctly ï¿½
Southern California Gas Company | N | LOS ANGELES | CANOGA PARK | 2020-03-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | PETTRELLI ELECTRIC | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Petrelli Electric Co contractor for DWP hit 0.5inch IPS service while augeringï¿½ to replace a power pole ï¿½Service was miss marked within delineation Locator was unable to get a strong signal andï¿½went off of Maps measurements
Southern California Gas Company | N | LOS ANGELES | CANYON COUNTRY | 2020-02-11 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | BOUDREAU PIPELINE CONTRACTORS | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor excavating for sewer with backhoe struck a 4 main No current USA ticket
Southern California Gas Company | N | LOS ANGELES | CANYON COUNTRY | 2020-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 2 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3270 |  | 1 |  | OMEGA PAVING | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | On 9/29/2020, SoCal Gas was notified that a third party contractor damaged a 2 inch plastic service with an auger while installing guard rails for shopping baskets at 18649 Via Princessa, Santa Clarita. Investigation of the incident showed that there was no USA ticket. Company crews responded and controlled gas at 07:44. There were no injuries or fatalities resulting from this incident. This incident was reported to CPUC due to natural gas and media coverage.
Southern California Gas Company | N | LOS ANGELES | CANYON COUNTRY | 2020-03-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | 2020 PLUMBING | RIVERSIDE | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Ticket expired on 6 10 19 Contractor was excavating for a sewer line when they hit the service with a backhoe
Southern California Gas Company | N | LOS ANGELES | CANYON COUNTRY | 2020-09-09 | Third party excavation damage | Riser | Polyethylene Pipe | Not Available | 1 | 45 | 40 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PARDEE HOMES | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavator bent riser no leak.
Southern California Gas Company | N | LOS ANGELES | CANYON COUNTRY | 2020-07-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DAVID GARFINKEL | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging trench to install water fountain
Southern California Gas Company | N | LOS ANGELES | CANYON COUNTRY | 2020-02-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DESERT PLUMBING | SANTA CLARITA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging for sewer with back hoe hit the stub USA ticket was expired
Southern California Gas Company | N | LOS ANGELES | CANYON COUNTRY | 2020-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ENHANCE LANDSCAPING | THOUSAND OAKS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor landscaping co, was replacing a water valve, and hit service while excavating.
Southern California Gas Company | N | LOS ANGELES | CANYON COUNTRY | 2020-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | 800 BUILDERS | CANYON COUNTRY | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Per LCT Steven Hodgkiss Contractor was trenching to install gas yardline for new pool heater.
Southern California Gas Company | N | LOS ANGELES | CANYON COUNTRY | 2020-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | SOUTHERN CALIFORNIA EDISON | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service hit by SOCAL Edison. No USA
Southern California Gas Company | N | LOS ANGELES | CANYON COUNTRY | 2020-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 6 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | BRIGHTVIEW LANDSCAPE | NA |  | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | This is new business track Marks were never requested by the excavator because there was no gas facilities in the area The main was installed and gassed up twoï¿½days prior to the damage The excavator was warned that the gas main was installed but never are called to update the USA ticket for re marks
Southern California Gas Company | N | LOS ANGELES | CARSON | 2020-12-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | JAIME | NA |  | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Third Party Contractor Damaged Main with Backhoe while digging for trench.ï¿½
Southern California Gas Company | N | LOS ANGELES | CARSON | 2020-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 1.25 | 49 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | UNITED PAVING COMPANY | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | United Paving was grading to resurface the parking lot at 1058 E. 230th St and the grader hit the 1.25 inch steel svc that was correctly marked out. Marks were visible.
Southern California Gas Company | N | LOS ANGELES | CARSON | 2020-06-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | KINDNESS GENERAL CONTRACTOR | CYPRESS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | HIT LINE BY 3RD PARTY WITH BACKHOE WHILE EXCAVATING TO INSTALL CONDUIT FOR ELECTRIC LINES.
Southern California Gas Company | N | LOS ANGELES | CARSON | 2020-09-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 49 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 1 |  | KEN MATHEWSON GENERAL FIRE CONTROL | NA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | no usa, 3rd party contractor hit 3 inch plastic service
Southern California Gas Company | N | LOS ANGELES | CARSON | 2020-03-05 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 49 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SE PIPELINNE | SANTA FE SPRINGS | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 2 service while trying to expose it
Southern California Gas Company | N | LOS ANGELES | CARSON | 2020-10-12 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | FONSECA CONSTRUCTION INC | RIVERSIDE |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor dig in on a 2 inch pla main with a backhoe while excavating to replace a water riser. USA was not called.
Southern California Gas Company | N | LOS ANGELES | CARSON | 2020-07-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | W A RASIC CONSTRUCTION | LONG BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | damaged 0.5 ips service with backhoe
Southern California Gas Company | N | LOS ANGELES | CARSON | 2020-02-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LAGNAY CORP | RANCHO PALOS VERDES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit line then wrapped with rubber and taped up
Southern California Gas Company | N | LOS ANGELES | CARSON | 2020-07-21 | Third party excavation damage | Riser | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | AMERICAN INTEGRATED SERVICE | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | This is in theï¿½carson carousel area. contractor didnt have a USA
Southern California Gas Company | N | LOS ANGELES | CARSON | 2020-04-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 49 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 16 |  | AMCO CONTRACTING | ANAHEIM | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor did not provide delineation.ï¿½ Gas Co. locator called several times asking for delineation.ï¿½ Contractor ignored yellow caution tape over gas service.
Southern California Gas Company | N | LOS ANGELES | CASTAIC | 2020-06-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | CASTAIC | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner digging trench for sewer without USA. Contractor has USA and is coming Saturday June 27 to install. Customer was advised that they needed their own ticket, and that work cannot begin before USA is valid.
Southern California Gas Company | N | LOS ANGELES | CASTAIC | 2020-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HONEST PLUMBING AND ROOTER | SYLMAR | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Installing a septic tankï¿½
Southern California Gas Company | N | LOS ANGELES | CHATSWORTH | 2020-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | SYLMAR | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per LCT Victor Cruz contractor digging to install new sewer line with backhoe cut service with electric saw.
Southern California Gas Company | N | LOS ANGELES | CHATSWORTH | 2020-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 5 |  | G3 DEVELOPMENT | TORRANCE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 0.5 PE service but PT was compromise and 2 inch PE main had to be altered he also was digging over Gas Facility Plastic Main and did not hand expose he claims he was exposing gas service to be abandoned on later date ,. damaged with Backhoe, also address came in as 10883 N Bee Cyn rd, correct address for service is 10811 Topanga Blvd, Lct made corrections on damage report.
Southern California Gas Company | N | LOS ANGELES | CHATSWORTH | 2020-02-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | CONTRACTOR NO NAME PROVIDED | PACOIMA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per LCT Paul Cespedes spoke to contractor stated hit 0.5inch inch plastic service with shovel while installing repairing water leak Contractor claimed that the home owner would take responsibility for the damage
Southern California Gas Company | N | LOS ANGELES | CHATSWORTH | 2020-04-21 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 45 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 11810 |  | 1 |  | AMPAM PARKS MECHANICAL | CARSON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit 4 inch plastic main while digging with backhoe for new drains. Uncommon Developers Foreman evacuated 250 constructionï¿½site employees from area.ï¿½Contractor was aware of expired USA ticket and was made aware my Gas Co employees to call for new ticket before continuing work.
Southern California Gas Company | N | LOS ANGELES | CHATSWORTH | 2020-09-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 59 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | CHUCK STEVENS | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Developer struck stub service while grading for development.ï¿½ ï¿½Once we arrived on scene nobody from the developers crew was present.ï¿½
Southern California Gas Company | N | LOS ANGELES | CHATSWORTH | 2020-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ORANGE ELECTRICAL | ORANGE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 0.50 cts service while digging trench for electric conduits for light poles
Southern California Gas Company | N | LOS ANGELES | CHATSWORTH | 2020-08-12 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  |  | NA | TRILOGY PLUMBING | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Per LCT Jose Garcia third party grading with backhoe for sewer hit 2 inch plastic main.
Southern California Gas Company | N | LOS ANGELES | CHATSWORTH | 2020-08-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | DOMENT CONSTRUCTION | BEVERLY HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party damage by contractor, hit 0.5 inch plastic service with shovel while digging for irrigation.
Southern California Gas Company | N | LOS ANGELES | CHATSWORTH | 2020-02-05 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ASPLUNDH | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 4 plastic main was hit with auger by 3rd party contractor while drilling USA ticket Delineation Bracketsï¿½was for east side of street only and main was hit on west side of street ï¿½
Southern California Gas Company | N | LOS ANGELES | CHATSWORTH | 2020-10-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JOVI V HALOG | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | was digging to put in sewer lines and hit gas service
Southern California Gas Company | N | LOS ANGELES | CHATSWORTH | 2020-12-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 1 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | CONSTRUCT MAINTAIN CORP | LAGUNA HILLS |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging for post with no USA
Southern California Gas Company | N | LOS ANGELES | CLAREMONT | 2020-03-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CONTRACTOR WAS REMOVING CONCRETE IN THE DRIVEWAY WHEN THEY HIT THE SERVICE ï¿½ CONTRACTOR WAS UNSURE IF THERE WAS A USA TICKET CALLED IN FOR THE JOB ï¿½ IT WAS EXPLAINED TO THEM THE IMPORTANCE OF CALLING FOR USA BEFORE ANY WORK IS TO BEGIN
Southern California Gas Company | N | LOS ANGELES | CLAREMONT | 2020-01-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CARNIELLO GENERAL CONTRACTOR | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | CONTRACTOR WAS DIGGING TO INSTALL CASING FOR A NEW GAS SERVICE WHEN THEY HIT A 0.5inch CTS PLASTIC STUB THAT WAS NOT MAPPED OR RECORDED IN SAP ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | CLAREMONT | 2020-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | BEST BOBCAT INC | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CONTRACTOR WAS GRADING FOR A NEW DRIVEWAY WHEN THEY HIT OUR PLASTIC SERVICE.ï¿½ THEY WERE GRADING LOWER THAN THE EXISTING DEPTH OF THE PLASTIC SERVICE.ï¿½ WE CUT THE SERVICE BACK IN THE PARKWAY SO THEY CAN FINISH THEIR WORK AND THEY WERE TOLD TO GET A HOLD OF THE PLANNER TO GET THE SERVICE LOWERED.
Southern California Gas Company | N | LOS ANGELES | CLAREMONT | 2020-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | LINE WORK CONSTRUCTION | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CONTRACTOR WAS INSTALLING NEW COMMUNICATIONS LINE WHEN THEY HIT THE PLASTIC SERVICE.ï¿½ THEY WERE TRYING TO HAND EXPOSE THE PLASTIC SERVICE WHEN THEY HIT IT.ï¿½ THERE WAS USA CALLED IN.ï¿½ TICKET BUT NOGGIN WILL NOT LET ME CLOSE IT OUT IF I INPUT THE INFORMATION.ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | CLAREMONT | 2020-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | GNG VINYL FENCING | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer had no gas at meter. After investigation it was discovered that the EFV had tripped because the service was damaged the week prior by fence contractor. No USA was called.ï¿½
Southern California Gas Company | N | LOS ANGELES | CLAREMONT | 2020-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | CLAREMONT | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer hit 0.5 inch plastic service while hand digging to bury pet.
Southern California Gas Company | N | LOS ANGELES | COMPTON | 2020-02-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | GJ ENGINEERING CONSTRUCTION | TEMECULA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Locator did not locate because records show corner house fed off other main
Southern California Gas Company | N | LOS ANGELES | COMPTON | 2020-11-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | COMPTON | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor digging drain cut cts service
Southern California Gas Company | N | LOS ANGELES | COMPTON | 2020-02-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 0 | 0 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ENRIQUE RODRIGUEZ | COMPTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | home owner digging out tree stump
Southern California Gas Company | N | LOS ANGELES | COMPTON | 2020-02-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NA | COMPTON | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | home owner was digging out tree stump
Southern California Gas Company | N | LOS ANGELES | COMPTON | 2020-02-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | HOUSING AUTHORITY LA COUNTY | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | none
Southern California Gas Company | N | LOS ANGELES | COMPTON | 2020-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TRI CORE CONSTRUCTION | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Per LandM CMP02 meet with customer and customer explained only digging in backyard and Locator advised no conflict. Customer provided incorrect information on the ticket.
Southern California Gas Company | N | LOS ANGELES | COMPTON | 2020-05-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | SMARTECH | GARDENA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor digging cable for repair damaged PE line.
Southern California Gas Company | N | LOS ANGELES | COVINA | 2020-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RIO JORDAN CONSTRUCTION | PICO RIVERA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CONTRACTOR WAS INSTALLING A NEW SEWER LINE WHEN THEY HIT THE PLASTIC SERVICE.ï¿½ CONTRACTOR EXPOSED THE OLD STEEL SERVICE AND THOUGHT THAT WAS THE ACTIVE SERVICE EVEN THOUGH THE MARKS ON THE CURB CLEARLY SHOWS PLASTIC.ï¿½ CONTRACTOR CLAIMS TO HAVE AN ACTIVE USA BUT COULD NOT PROVIDE US WITH A TICKET NUMBER.
Southern California Gas Company | N | LOS ANGELES | COVINA | 2020-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | SAMAYOA PLUMBING INC | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | THE CONTRACTOR WAS DIGGING TO INSTALL A SEWER LINE WHEN THEY HIT THE PLASTIC SERVICE.ï¿½ THEY FAILED TO MAINTAIN THE MARKS THAT WERE PUT DOWN DUE TO THEIR EXCAVATIONS ON SITE.ï¿½ THIS IS THE SECOND TIME THEY HAVE HIT THE PLASTIC SERVICE AT THIS ADDRESS FOR THE SAME PROJECT.
Southern California Gas Company | N | LOS ANGELES | COVINA | 2020-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | GONZALO ALVAREZ | COVINA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor digging by hand with no USA called.ï¿½
Southern California Gas Company | N | LOS ANGELES | COVINA | 2020-05-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | VIA HOMES INC | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CONTRACTOR WAS INSTALLING CONDUIT FOR STREET LIGHTING INSIDE A NEW COMPLEX WHEN THEY HIT THE SERVICE WITH A TRENCHER. CREW MADE REPAIRS TO THE 1 inch PLASTIC SERVICE.ï¿½ï¿½ï¿½SERVICE HAD AN EFV.ï¿½ THEY DID NOT HAVE USA.
Southern California Gas Company | N | LOS ANGELES | COVINA | 2020-05-26 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | VIA HOMES INC | TEMPLE CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CONTRACTOR WAS REPAIRING THE WATER SERVICE WHEN THEY HIT OUR 2 inch PLASTIC MAIN WITH A PICK AX.ï¿½ THEY CLAIM TO HAVE USA BUT COULD NOT PROVIDE THE NUMBER.ï¿½ THE MAIN WAS PROPERLY MARKED WITH FLAGS IN THE DIRT BUT THE FLAGS WERE REMOVED WHERE THE WORK WAS TAKING PLACE.
Southern California Gas Company | N | LOS ANGELES | COVINA | 2020-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | HOME MAINTANCE REPAIR AND REMODELING | COVINA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor was potholing gas and failed to use caution when hand exposing.ï¿½
Southern California Gas Company | N | LOS ANGELES | COVINA | 2020-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10001 |  | 1 |  | BIG BEN CONSTRUCTION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CREW WAS DISPATCHED TO INVESTIGATE CODE 1 CONDITIONS AT THIS RESIDENCE.ï¿½ AFTER CENTERING LEAK, THE CREW COULDNT SAFELY DIG UP THE SOURCE OF THE LEAK.ï¿½ SO, THEY HAD TO DROP BACK AND SQUEEZE THE 2 inch PLASTIC MAIN TO GET THE LEAK UNDER CONTROL.ï¿½ AFTER EXPOSING THE LEAK, THE SERVICE WAS FOUND PULLED AWAY FROM THE SERVICE SADDLE APPROXIMATELY 2 inch AWAY.ï¿½ AS THE CREW WAS REPLACING THE SERVICE VIA INSERT, THE CREW FOUND THAT THE NEW SERVICE STOPPED INSERTING RIGHT WHERE THE NEW WATER MAIN WAS INSTALLED.ï¿½ THE CREW DUG UP THE OLD STEEL GAS SERVICE TO CUT OUT THE OBSTRUCTION AND THAT IS WHEN THEY FOUND THAT THE SERVICE WAS DAMAGED.ï¿½ IT APPEARS TO HAVE BEEN DAMAGED WHEN THEY WERE INSTALLING THE NEW WATER MAIN AND APPEARS TO HAVE BEEN DAMAGED BY A 2 BUCKET FROM A BACKHOE.ï¿½
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2020-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Independent contractor trenching on customers property doing landscaping.
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2020-10-27 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 2 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CPE | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | contractor damaged 20 foot stub while boring.
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2020-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LA HOUSING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Backhoe operator hit 0.5 inch cts service, while replacing water service lines at building 56. Asked Daniel for the USA Ticket twice but did not get one.
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2020-05-14 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | INNOCENTI CONSTRUCTION | CAMARILLO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | none
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2020-02-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DELAMO CONSTRUCTION | TORRANCE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor damaged service while hand digging
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2020-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | LA CITY HOUSING AUTHORITY | CULVER CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractors were digging for water and damaged gas service line.ï¿½ services and mains on property are maintained by gas co but meters are not
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2020-06-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | VISTA GENERAL ENG | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | while trenching contractor damaged gas service, had no USAï¿½
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2020-07-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | VISTA GENERAL ENG | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | service was damaged while excavatingï¿½
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2020-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | VISTA GENERAL ENG | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor was exposing sewer line to make repairs and struck our plastic service line in private property.ï¿½ They did not use caution around our gas line.ï¿½
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2020-04-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | PINICCO CONTRTACTING CORP | WOODLAND HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit a gas line with an excavator while excavating with a trencher.
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2020-05-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PINNACLE CONTRACTING | WOODLAND HILLS | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Plastic service hit by shovel while hand digging , USA tickets given are expired
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2020-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | THW KAULI FOUNDATION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged a plastic service with a backhoe digging for construction footings.
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2020-08-31 | Third party excavation damage | Riser | Polyethylene Pipe | Grader/Scraper | 1 | 43 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | HITT CONTARACTING | LOS ANGELES | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No | No damage to SUOF. | No damage to SUOF. | Contractor cut into 1 inch plastic riser to expedite Branch svc removal Abandonment
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2020-02-27 | Third party excavation damage | Transmission Line in an HCA area | Steel | Hand Tools | 12 | 465 | 177 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 40001 |  |  | NA | INNOCENTI CONSTRUCTION | CAMARILLO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | On February 27 2020 at approximately 5 45pm Transmission Line 317 L317 was damaged by a 3rd party contractor Innocenti Construction Inc working for Golden State Water Company in Culver City The 3rd party was attempting to weld a 2 inch half coupling on what they thought was a 16 inch water line The pipeline they were welding on was 12 inch L317 located along Blanco Park at 5801 Sawtelle Blvd in Culver City The welder burned through the pipeline causing a release of gas from a quarter inch opening The contractor notified the Fire Department and SoCalGas of an area odor and Transmission crews immediately responded There were no injuries and no lost customers from this incident. The damage occurred because Innocenti Construction Inc was excavating in an unmarked area without a valid USA ticket and welding on the incorrect sub structure The 3rd Party Contractor provided two USA tickets to SoCalGas management while repairs were occurring but they were expired and the delineated area for those tickets was approximately 220 ft away from the damaged pipeline.
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2020-10-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Unreported damage,ï¿½ ï¿½landscapers puncturedï¿½ 1 inchï¿½ IPS gas service with wooded stake for new tree installation and was unreported
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2020-02-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | INNOCENTI CONSTRUCTION | CAMARILLO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | gas facilities were damaged while contractor was pot holingï¿½
Southern California Gas Company | N | LOS ANGELES | DIAMOND BAR | 2020-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | L G CABLE CONSTRUCTION | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | L and G cable crew hit 0.5 cts service with shovel while installing conduit for spectrum
Southern California Gas Company | N | LOS ANGELES | DIAMOND BAR | 2020-04-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | WALNUT VALLEY WATER DISTRICT | WALNUT | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 0.50 inch plastic stub with backhoe while digging to repair water line.ï¿½ The contractor excavation on an emergency ticket prior to USA 48 hour notice.ï¿½ Locator arrived shortly after contractor hit line.ï¿½
Southern California Gas Company | N | LOS ANGELES | DIAMOND BAR | 2020-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | LINE ELECTRIC INC | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 0.50 inch plastic service with shovel while digging to install drain.
Southern California Gas Company | N | LOS ANGELES | DOWNEY | 2020-09-14 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ACCESS GENERAL CONTRACTING | CORONA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On 91420 while using a jackhammer to break a bollard concrete footing to remove the bollard and install a protective block wall around the gas company meter for SCG, Anthony Keto with Access General Construction damaged a one inch plastic gas service.ï¿½ï¿½ï¿½The damaged gas service was embedded in the concrete footing and was not exposed prior to chipping at the concrete footing.ï¿½ Access General Construction had a valid USA ticket.ï¿½ SCG crew arrived on site and made permanent repairs.ï¿½
Southern California Gas Company | N | LOS ANGELES | DOWNEY | 2020-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DB ELECTRIC INC | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor attempting to locate water line and hit gas line
Southern California Gas Company | N | LOS ANGELES | DOWNEY | 2020-12-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 45 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | TECHNICO | GARDENA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor cut 0.5 plastic service with sawzall while cutting newly installed conduitï¿½
Southern California Gas Company | N | LOS ANGELES | DOWNEY | 2020-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SELECT ELECTRIC INC | CERRITOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On 1 06 20 while auguring with a backhoe Select Electric damaged a one inch plastic gas service ï¿½ The marks provided by the SCG locator were not maintained ï¿½ The flags were removed and the concrete that had the marks had been replaced ï¿½ Gregg Case with Select Electric told SCG supervisor Jerry Jones that his employee had potholed the gas service prior and remembered that it was there but he had thought it was a little further over ï¿½ Select Electric had a valid USA ticket ï¿½ SCG crew arrived on site and made permanent repairs ï¿½ ï¿½
Southern California Gas Company | N | LOS ANGELES | DOWNEY | 2020-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GROUP ADAM DEVELOPMENT | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | On 81920 while hand digging to install a drain, Miguel Uribeï¿½ï¿½was attempting to exposed a one half inch plastic gas service when he damaged it with a shovel.ï¿½ Miguel stated that he knew the line was there.ï¿½ Miguel did not notify USA of this work to be performed and did not have a valid USA ticket.ï¿½ SCG crew arrived on site and made permanent repairs.ï¿½
Southern California Gas Company | N | LOS ANGELES | DOWNEY | 2020-09-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | CASTILLO IRONWORKS | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | On 91220 while hand digging to install a new gate, Jose Castillo damaged a one half inch plastic gas service.ï¿½ Mr. Castillo did not notify DigAlert of the work to be performed and he did not have a valid USA ticket.ï¿½ SCG crew arrived on site and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | DOWNEY | 2020-04-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | PLUMBING AROUND THE CLOCK | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber hit service and had no USA they were already gone when the fire dept and crew showed up.
Southern California Gas Company | N | LOS ANGELES | DOWNEY | 2020-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TIM GREENLEAF ENGINEERING | HUNTINGTON BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While grading contractor hit gas line.
Southern California Gas Company | N | LOS ANGELES | DOWNEY | 2020-10-20 | Operator excavation damage | Riser | Steel | Hand Tools | 0.75 | 45 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NPL | BREA | CA | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor cut live gas service instead of abandoned service
Southern California Gas Company | N | LOS ANGELES | DOWNEY | 2020-10-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | DOWNEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | home owner struck the service with shovel
Southern California Gas Company | N | LOS ANGELES | DOWNEY | 2020-02-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | COSBY PLUMBING | ALTADENA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | On 2 25 20 while excavating with a backhoe to replace water line to a fire station Anthony from Crosby Plumbing damaged a one inch plastic gas service ï¿½ Crosby Plumbing did not have a USA ticket ï¿½ SCG crew arrived on scene and cutback the service ï¿½ SCG crew returned a few weeks later to re instate the gas service after all water pipe work was completed
Southern California Gas Company | N | LOS ANGELES | DUARTE | 2020-12-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  |  | NA | CALIFORNIA AMERICAN WATER | MONROVIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | water crew was digging trench with back hoe and did not hand expose line before digging with the hoe. The service was marked properly and the contractor is totally at fault.ï¿½
Southern California Gas Company | N | LOS ANGELES | DUARTE | 2020-06-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | FODDRILL | CHINO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | CONTRACTOR HIT PLASTIC SERVICE WHILE DIGGING TO INSTALL NEW STREET LIGHTING POLE
Southern California Gas Company | N | LOS ANGELES | DUARTE | 2020-05-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | DUARTE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hit line while grading dirt.ï¿½ HOMEOWNER DID NOT KNOW ABOUT USA.ï¿½ IT WAS EXPLAINED TO HIM THE IMPORTANCE OF CALLING USA BEFORE ANY DIGGING IS TO TAKE PLACE.ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | EL MONTE | 2020-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | LORENZO RUBALCABA | SOUTH EL MONTE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor did not call in USAï¿½
Southern California Gas Company | N | LOS ANGELES | EL MONTE | 2020-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | SERVICE CHAMPIONS PLUMBING | BREA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor confused gas line for water line
Southern California Gas Company | N | LOS ANGELES | EL MONTE | 2020-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Drain cleaning equipment such as snakes, etc. | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | LA HYDRO JET AND ROOTER SERVICE INC | SUN VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA REQUESTED, CUSTOMER HIRED CONTRACTOR TO SNAKE SEWER PIPES plastic service line in sewer when hit.
Southern California Gas Company | N | LOS ANGELES | EL MONTE | 2020-07-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HARIK CONSTRUCTION | GLENDORA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA, CUSTOMER INSTALLING GAS HOUSELINE
Southern California Gas Company | N | LOS ANGELES | EL MONTE | 2020-10-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | ROSEMEAD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Owner was digging to install fence and hit service. No USA ticket.
Southern California Gas Company | N | LOS ANGELES | EL MONTE | 2020-08-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | EL MONTE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CUSTOMER DID NOT REQUEST FOR USA, CUSTOMER DIGGING TO REPAIR SEWER
Southern California Gas Company | N | LOS ANGELES | EL SEGUNDO | 2020-06-01 | Third party excavation damage | Main | Steel | Miscellaneous/Other | 3 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SMOKEY HALLOW INDUSTRIES | MANHATTAN BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor exposed 3 inch gas main cut into it with sawzall clamped until gas company crew arrived.
Southern California Gas Company | N | LOS ANGELES | EL SEGUNDO | 2020-02-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | KCE ELECTRIC | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractors left a unlocatable ï¿½stub service in the ground Work had stopped due to rain and there was no riser to indicate a service was installed
Southern California Gas Company | N | LOS ANGELES | EL SEGUNDO | 2020-01-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | KLM ENGINEERING CONTRACTORS | HERMOSA BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit service digging with a shovel
Southern California Gas Company | N | LOS ANGELES | EL SEGUNDO | 2020-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 3 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DAVID MILLS DEVELOPER | EL SEGUNDO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was dismantling our Meter Set Assembly and used a Sawzall and cut our riser.
Southern California Gas Company | N | LOS ANGELES | EL SEGUNDO | 2020-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | EL SEGUNDO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per YU56, broken plastic service due to hand digging for sewer
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2020-06-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HERBERT ZALAYA | SIMI VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor struck gas service with post hole digger while digging for fencing.ï¿½
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2020-04-18 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | JOE DE LA SANTOS PLUMMER | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was excavating to reroute drain line when the service was hit. Third party contractor was using a hand saw.ï¿½
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2020-01-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 0 |  | M M DEISGN | ENCINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | M M designs hit the 0.5inch CTS plastic line while demolishing the house 17319 Magnolia Blvd bent the plastic back to stop the gas flow ï¿½
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2020-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MODERN 8 ED HE CONSTRUCTION | ENCINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Digging to install sewer line
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2020-02-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PICTURE BUILD | SYLMAR | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer service on site said contractor hit 0.5inch plastic service and 0.5inch CTS riser
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2020-10-03 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 4 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 4 |  | NA | CANOGA PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | LCT was working on a leak. stuck backhoe in ground and cause damage to 4 inch mainï¿½
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2020-02-11 | Third party excavation damage | Miscellaneous/Other | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | ENCINO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer hit 0.5inch IPS service while trenching near riser for new drain Pinched plastic altered damagedï¿½section of service
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2020-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | THE DRAIN DEFENDER | NORTH HOLLYWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor did not have a USA ticket while performing inchsplit and pull inch of new sewer lateral.ï¿½ While splitting old sewer Lat. with large cable, existing gas svc was broken in half.
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2020-12-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | VALLEY VILLAGE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Owner of property hit 0.5 inch plastic service because he did not want to pay for an abandonment. While onsite he confided in Supervisor Kurtis Rodriguez this info. Sent info to damage prevention Juan Garcia Lopez
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2020-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor dug to post fence and hit plastic service.ï¿½ No USA was called.
Southern California Gas Company | N | LOS ANGELES | GARDENA | 2020-11-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 9 |  | PRECISION PIPELINE INC LIC 405 968 | NORWALK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Gas line was struck within delineation area, Abandoned copper gas line was located not new plastic Gas line.ï¿½
Southern California Gas Company | N | LOS ANGELES | GARDENA | 2020-11-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PRECISION PIPELINE INC | NORWALK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Gas line was struck within delineation area with shovel while exposing.
Southern California Gas Company | N | LOS ANGELES | GARDENA | 2020-04-24 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PREMIER DESIGN | IRVINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CONTRACTOR HIT A CUTBACK STUB
Southern California Gas Company | N | LOS ANGELES | GARDENA | 2020-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 0.75 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.75 inch pipe wrap damaged
Southern California Gas Company | N | LOS ANGELES | GARDENA | 2020-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DOMINGUEZ GENERAL ENGINEERING | POMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | broke gas service after exposed
Southern California Gas Company | N | LOS ANGELES | GARDENA | 2020-07-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JA SALAZAR | LA HABRA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | unknown abandoned serviceï¿½
Southern California Gas Company | N | LOS ANGELES | GARDENA | 2020-05-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | EPC COMPANY | EL MONTE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | SOCAL Edison damaged the gas service line while installing a grounding rod.ï¿½
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2020-07-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LINEWORK CONSTRUCTION INC | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged service while digging with backhoe
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2020-06-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ARIS CONSTRUCTION CO | BURBANK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Trenching in new gas line and hit service with hand shovel.
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2020-01-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor failed to notify USA Service was cut into by contractor
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2020-10-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | GLENDALE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Owner, working on Landscape damaged 0.5 service, with drill, company crew made permanent repairs , NO USA
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2020-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | VCI CONSTRUCTION LLC | UPLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor states potholing with hand shovel and hit service line.
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2020-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | J DE SIGIO CONSTRUCTION INC | BALDWIN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged the service but was not leaking.
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2020-10-06 | Operator excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | WA RASIC | LONG BEACH | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was saw Cutting to pot hole 0.75 inch steel service in 8 inch thick concrete with a 9 inch concrete Blade, Gas service was located directly under concrete and service was cut into and damaged.
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2020-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JDC | BALDWIN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to properly identify the material of the pipe. Markings indicated 0.5 inch plastic and they found stl pipe thinking the plastic was inside. Contractor hit the service with a shovel while hand digging hole.
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2020-01-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | TIM GREENLEAF ENGINEERING | HUNTINGTON BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was removing spoil and managed to dig into the service locationï¿½damaging the 4 IPS line ï¿½ Contractor then shut off the plastic ball valve atï¿½the sidewall location which shut off all the gas to the school Contractor did not have a valid USA ticket at the time but seemed to call one in after the fact Company Crew made permanent repairs and customer services restored the school ï¿½
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2020-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 4 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  | 2 |  | BALFOUR BRATTY | NEWPORT BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Unified school district Contractor, Balfour Betty, had a sub contractor auguring holes to install fencing. Both companies failed to call USA to locate and mark line. Contractor working for Balfour auguredï¿½through the top of the 4 inchIPS service and they ended up shutting off the gas with the curb valve for service. This is the second hit this year on the same service. Sub Contractor name Econo Fence Inc, Compï¿½ 951 453 2533, Supervisor name Jud Leslie.
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2020-07-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JDC | BALDWIN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was potholing by hand, with a shovel, to expose gas service and hit the 0.5 CTS service. Service hasï¿½EFV and managed to shutoff when it got hit.
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2020-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | WESTERN ALLIED ELECTRIC | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Line was found already damaged, damaged date and time unknown. No USA for job site.ï¿½
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2020-07-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JORGE ROJAS | GLENDALE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscaping company was digging by hand with shovels to plant a couple trees. They hit the 0.5 inch CTS pipe in the process,ï¿½the landscapingï¿½company did not have a valid USA ticket for the site.ï¿½
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2020-08-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | 911 PLUMBING SERVICES | GLENDALE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumbers digging to repair sewer line hit gas service while digging with shovel.
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2020-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | GLENDALE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging onï¿½property near gas meter, homeowner struck 0.5 inch CTS Aldylay service with a shovel and it started leaking. No valid USA
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2020-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 9 |  | SEWER PIPELINE GENERAL ENGINEERING | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor installing sewer Lateral was potholing gas service and struck 0.5 Plastic service with a shovel. ï¿½
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2020-08-26 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ARIZONA PIPELINE COMPANY | CHATSWORTH | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was replacing the gas service. While hand exposing the existing gas service, the contractor hit the 0.5 inch CTS service with their sharp shooter shovel. The marks according to the foreman were removed when they broke out the asphalt, but knew the gas service was there.
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2020-02-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | SYLMAR | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Line was located by ETD the service is 0.5inch cts and partially in cased on a 0.75inch stl pipe ï¿½The steel casing for the service seemed to be making contact with another steel line that was abandoned Crew dug it out in a control hole and come to find out it was not the actual service pipe ï¿½After investigating it seemed as the locatingï¿½wire was not properly installed to the end of the pipe casing and the casing was touching the abandonï¿½steel line Two types of locators were used and both kept locating the wrong pipe Contractor was unaware of gas line being in conflict with his trench because the markings and whisker were a couple feet away The contractor struck the 0.5inch pe service with mini excavator
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2020-04-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 1 |  | PACIFIC OUTDOOR LIVING | NORTH HOLLYWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor doing the work for customer did not have a valid USA onsite. Contractor was trenching and came upon two steel pipes that were unknownï¿½to them and figured they were abandoned, so they went ahead to cut them out of the way. The contractor used a concrete demo saw and cut the 0.75 inch Steel service.ï¿½ Crew manage to do temporary repairs and came back the next day to replace the service for the permanent repair.ï¿½
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2020-11-19 | Third party excavation damage | Main | Steel | Not Available | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 134 |  | GLENDALE WATER POWER | GLENDALE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Glendale DWP was potholing Gas Main and wile Digging with Backhoe and failing to Excavate with shovel to exposed The facility, They struck an Abandon service Tee on The main causing the Leak.ï¿½
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2020-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | NA | GLENDALE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Property Owner had a crew working on removing tree trunks for a new fence they were going to install. The crew was hand digging to cut roots and hit the 0.5 inch CTSï¿½service with shovel. Line was blowing at some point but fire department stuck a wooden plug and stopped it. Crew was able to Squeeze the CTS pipe upon arrival forï¿½under control. Developer property owner did not have a valid USA for property.ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2020-05-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DESERT EMPIRE HOMES | GLENDALE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No valid USA, Contractor was hand excavating a holeï¿½to plant a palm treeï¿½and hit 0.50 inch CTSï¿½ service with shovel.
Southern California Gas Company | N | LOS ANGELES | GLENDORA | 2020-02-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | DORICK CONSTRUCTION | PICO RIVERA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | none
Southern California Gas Company | N | LOS ANGELES | GLENDORA | 2020-04-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DOREK CONSTRUCTION | PICO RIVERA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CONTRACTOR WAS REPLACING THE WATER MAINS AND SERVICES WHEN THE PLASTIC SERVICE WAS DAMAGED.ï¿½ CONTRACTOR HAD THE LINE EXPOSED IN THEIR TRENCH BUT A ROCK HAD FALLEN ON TOP OF THE SERVICE CAUSING THE DAMAGE.ï¿½ THERE WAS AN EXISTING USA WITH BUT NOGGIN WILL NOT TAKE IT AS VALID. ï¿½ ï¿½
Southern California Gas Company | N | LOS ANGELES | GLENDORA | 2020-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | JEM CONSULTING | RIVERSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractorï¿½did not pot hole service by hand before digging with backhoe. USA marks were correct and visibleï¿½
Southern California Gas Company | N | LOS ANGELES | GLENDORA | 2020-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | VCI | UPLAND | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CONTRACTOR WAS INSTALLING A NEW WATER MAIN WHEN THE GAS SERVICE WAS DAMAGED.ï¿½ SERVICE CAME OUT AT A 90 FROM THE CMB NOT STRAIGHT HOW THE LOCATOR MARKED IT OUT TO BE
Southern California Gas Company | N | LOS ANGELES | GLENDORA | 2020-10-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | LONGYUN IRN ENTERPRISE | SOUTH EL MONTE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractors Were Installing A Post For A New Fence For The Homeowner When They Hit The Plastic Service.ï¿½ The Homeowner Claims That They Knew Where The Gas Service Was But Accidentally Hit It Anyways.ï¿½ They Thought It Was A Little Bit Over From Where They Were Digging For The Post.ï¿½ They Did Not Have Usa.ï¿½ It Was Explained To Them The Importance Of Having Usa Before Any Excavation Work Is To Begin
Southern California Gas Company | N | LOS ANGELES | GLENDORA | 2020-05-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ROOTER RANGER | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor did not called Dig Alert.
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2020-02-25 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | NA | GRANADA HILLS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Cust service first on site said homeowner was taking tree root out and didn t know it was branched from his house
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2020-05-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | GRANADA HILLS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service line leak. Contractor h it service line with shovel while digging to install sewer line.
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2020-04-24 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NA | GRANADA HILLS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging for new footing
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2020-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | AMERICAN ELECTRIC COMPANY | CANYON COUNTRY | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 0.5 PE service, did not wait 48 b4 digging, also didnt hand expose.
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2020-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | GRANADA HILLS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor cut 0.75 line with zaw saw when trenching to install pool line.
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2020-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA HOMEOWNER HIRED HIM | CANYON COUNTRY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party that works for home owner hit 0.75 inch steel service with skip loader.
Southern California Gas Company | N | LOS ANGELES | HACIENDA HEIGHTS | 2020-04-08 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | WA RASIC | LONG BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged correctlyï¿½ marked 1 inch plastic service with sharpshooter while potholing for water line.ï¿½ Gas company crew onsite advised contractor to be more cautious while excavating around underground substructures, even if by hand.
Southern California Gas Company | N | LOS ANGELES | HACIENDA HEIGHTS | 2020-09-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | HACIENDA HEIGHTS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Jerry Luna was digging up his drain and punctured 0.5 cts plastic service in the process.
Southern California Gas Company | N | LOS ANGELES | HARBOR CITY | 2020-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | STERLING PLUMBING | SANTA ANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | hit svc no usa
Southern California Gas Company | N | LOS ANGELES | HARBOR CITY | 2020-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | WILCOX WILCOX CORP | CANOGA PARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | HIT SVC NO VALID USA
Southern California Gas Company | N | LOS ANGELES | HAWTHORNE | 2020-07-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | svc hit USA called in as emergency on 720
Southern California Gas Company | N | LOS ANGELES | HAWTHORNE | 2020-05-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | HAWTHORNE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | HO hit svc while digging for fence footing no usa.
Southern California Gas Company | N | LOS ANGELES | HAWTHORNE | 2020-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | GARDENA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | HO digging to replace HL hit svc.
Southern California Gas Company | N | LOS ANGELES | HAWTHORNE | 2020-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | YOUSUF MOHAMAD | HAWTHORNE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer installing a sewer line and damaged our gas service.ï¿½811 was not notified.ï¿½
Southern California Gas Company | N | LOS ANGELES | HAWTHORNE | 2020-03-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 4 |  | NA | HAWTHORNE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CONTRACTOR HIT SVC WHILE WORKING ON SEWER WATER
Southern California Gas Company | N | LOS ANGELES | HAWTHORNE | 2020-12-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 3 |  | RETRO ROOTER PLUMBING | MONTEREY PARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | pipe damaged during sewer dig out for repairs.
Southern California Gas Company | N | LOS ANGELES | HAWTHORNE | 2020-07-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Contractor hit gas service and attempted repair. dug up make shift clamp.ï¿½
Southern California Gas Company | N | LOS ANGELES | HERMOSA BEACH | 2020-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | HERMOSA BEACH | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | svc hit with posthole digger no USA
Southern California Gas Company | N | LOS ANGELES | HERMOSA BEACH | 2020-08-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DALINGHAUS CONSTRUCTION | LAKE ELSINORE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | svc hit while hand digging
Southern California Gas Company | N | LOS ANGELES | HERMOSA BEACH | 2020-07-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ALLIED PLUS LOW VOLTAGE | COMPTON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor hit unmapped stub while auguring for ground rod
Southern California Gas Company | N | LOS ANGELES | HUNTINGTON PARK | 2020-11-06 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | SE PIPELINE | SANTA FE SPRINGS | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor damaged 2 inch plastic main with shovel
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2020-04-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ROOTER HERO PLUMBING | GARDENA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor assumed that the service was tied over from E Fairview Blvd
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2020-01-13 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | INGLEWOOD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | gas service was damaged while excavating
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2020-12-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | INGLEWOOD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hit gas line with excavator.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2020-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 21 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | D A HOME RENOVATIONS | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | home owner was digging when service was damagedï¿½
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2020-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 21 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | INGLEWOOD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor cut into sag service without calling for Dig Alert to mark utilities
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2020-08-25 | Operator excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | ARB | NA |  | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | ARB contractor was trying to locate main using Probe only 24 inch down and damaged pipe going straight through top and bottom of aldyl main.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2020-02-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 8 |  | BOOMRANG INC | ALHAMBRA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor damaged plastic gas line with backhoe after continuing to dig once located abandoned steel service abandoned steel svc was the incorrect svc live service is a 1 pla svc ï¿½
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2020-11-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | R3 CONTRACTORS INC | ANAHEIM | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor assumed stub wasï¿½
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2020-01-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | KATO LANDSCAPE INC | FOUNTAIN VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per ETD Fong Kato Landscaping Inc Sub contractor did not have a valid Dig Alert ticket for themselves
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2020-06-18 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | DOWNEY PLUMBING | DOWNEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | none
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2020-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | GOLDEN STATE WATER | NUEVO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | water company installing water service
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2020-10-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DORECK CONSTRUCTION | PICO RIVERA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Party Damage, Hit 3 0.5 inch plastic services by time LCT arrived.ï¿½ 500, 512, and 520 E. Hillsdale St.ï¿½ Trenching to install water main.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2020-01-17 | Operator excavation damage | Main | Steel | Backhoe/Trackhoe | 4 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | SE PIPELINE | SANTA FE SPRINGS | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | NA
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2020-10-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 22 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DORECK CONSTRUCTION | PICO RIVERA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was potholing over our facilities and damaged several of our services while doing so.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2020-10-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HP COMMUNICATION | GARDENA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor Rep hit gas service while hand digging.ï¿½ USA ticket not valid until 10 26 2020.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2020-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 22 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | DORECK CONSTRUCTION | PICO RIVERA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged multiple plastic gas services while hand exposing.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2020-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 22 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | DORECK CONSTRUCTION | PICO RIVERA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas facilities while hand exposing service.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2020-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | INLAND ENGINEERING SERVICES INC | GARDENA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | Contractor damaged 0.50 ips service
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2020-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DOTY BROS | NORWALK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Party damage. Edison contractor trenching to install conduits hit 1 inch PLA Service with hand tools.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2020-12-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 21 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | WARMISDE | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Foreman had backhoe operator digging over service without exposing first.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2020-04-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 21 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HOMEOWNER | INGLEWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer digging for sewer line, hit our gas line, did not have a USA number.ï¿½
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2020-11-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | KEITH KC LEE INC | MISSION HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Crew damaged a 2 inch service line and did not care that they caused damage.ï¿½
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2020-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 22 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PGMR CONSTRUCTION INC | PACOIMA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | contractor was aware that he was digging with an expired USA ticket.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2020-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10001 |  |  | NA | NA | NA |  | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | none
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2020-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 21 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  |  | NA | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor dug into 0.50 inch Cts pipe digging trench for sewer.
Southern California Gas Company | N | LOS ANGELES | LA CANADA FLINTRIDGE | 2020-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MSL ELECTRIC INC | ANAHEIM | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | Contractor said they were removing light post foundation and hit 1 inch plastic service.ï¿½ Contractor then moved backhoe out of area.
Southern California Gas Company | N | LOS ANGELES | LA CANADA FLINTRIDGE | 2020-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ERNEST GONZALEZ | PASADENA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging trench with a mini excavator and damagedï¿½CTS gas service. There was no valid USA called in or onsite .
Southern California Gas Company | N | LOS ANGELES | LA CANADA FLINTRIDGE | 2020-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ARMSTRONG CONTRACTORS | GLENDALE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | Contractor stated they were using backhoe to demo foundation and hit our service.
Southern California Gas Company | N | LOS ANGELES | LA CANADA FLINTRIDGE | 2020-10-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NONE PROVIDED | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor while digging damaged the service line with a shovel.
Southern California Gas Company | N | LOS ANGELES | LA CANADA FLINTRIDGE | 2020-07-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | KALYOUNG LANDSCAPING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner was digging in yard for pool and damaged our plastic service in casing.ï¿½ No USA was called.
Southern California Gas Company | N | LOS ANGELES | LA CANADA FLINTRIDGE | 2020-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HARDY HARPER | LAKE FOREST | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was grinding street and cut our line with saw, NO USA.
Southern California Gas Company | N | LOS ANGELES | LA CANADA FLINTRIDGE | 2020-02-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | LA CANADA FLINTRIDGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Workers struck 0.5inch PE serviceï¿½while digging for sprinklers and plant work No USA was called in puncture was done by shovel ï¿½
Southern California Gas Company | N | LOS ANGELES | LA CANADA FLINTRIDGE | 2020-05-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | WJ LANDSCAPE MAINTENANCE | LA CANADA FLINTRIDGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No Valid USA for Job site. Contractor was trenching to install new water pipe, while hand digging the trench the contractor hit 0.50 inch CTS service.ï¿½
Southern California Gas Company | N | LOS ANGELES | LA CANADA FLINTRIDGE | 2020-10-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | LA CANADA FLINTRIDGE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscaping contractor hit 0.5 inch CTS service line while digging to install French drain pipe and low voltage wiring.ï¿½ Line was split apart and found bent back and taped. ï¿½
Southern California Gas Company | N | LOS ANGELES | LA CANADA FLINTRIDGE | 2020-11-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MIRANDA WEST | LA CANADA FLINTRIDGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscape company was planting trees on Saturday 11 14, around 5PM and nicked the service with a metal stake. According to company they did not realized that they had damage the CTS pipe at the time. On 11 16 they were digging and damaged the CTS pipe more by cutting it with the shovel. Landscape company then bent back the CTS service and tied it with wire and vise grips.ï¿½NO USA WAS CALLED IN AND IS 2ND TIME ITS HIT.
Southern California Gas Company | N | LOS ANGELES | LA CANADA FLINTRIDGE | 2020-08-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ARIZONA PIPELINE | CHATSWORTH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service was cut with a shovel.ï¿½ Contractor was digging to put in a new service.
Southern California Gas Company | N | LOS ANGELES | LA CANADA FLINTRIDGE | 2020-02-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CONEX DEVELOPMENT | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Property is under construction for remodeling Contractor was breaking out concrete with theï¿½jack hammer and damaged the 0.5inch serviceï¿½at the transition fitting ï¿½
Southern California Gas Company | N | LOS ANGELES | LA CANADA FLINTRIDGE | 2020-11-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JESSE RUIZ | LA CANADA FLINTRIDGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Gardener was hand digging garden to plant a plant and accidently hit the 0.5 inch cts service. No USA was valid at the time.
Southern California Gas Company | N | LOS ANGELES | LA CANADA FLINTRIDGE | 2020-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MISTIC WATER GARDEN | ENCINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging with mini backhoe to remove a tree for landscaping and severed our 0.5 inch plastic service.ï¿½ No USA was called.
Southern California Gas Company | N | LOS ANGELES | LA CANADA FLINTRIDGE | 2020-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | VCI CONSTRUCTION | SUN VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was digging with shovel to daylight service and accidentally struct plastic service while doing so.
Southern California Gas Company | N | LOS ANGELES | LA CANADA FLINTRIDGE | 2020-03-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LC CONSTRUCTION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor
Southern California Gas Company | N | LOS ANGELES | LA CANADA FLINTRIDGE | 2020-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | KENDALL HALES GENERAL CONTRACTOR | LA CANADA FLINTRIDGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Arrived at location to reevaluate leak and found code 1 conditions at foundation of new construction building.ï¿½ Seems as someone from construction site attempted to move gas line away from new foundation and damaged 0.5 inch plastic service line in copper casing.ï¿½ Service line was found coming up out of ground and angling away from building to clear foundation.ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | LA CANADA FLINTRIDGE | 2020-10-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ROBERT BRKICH CONSTRUCTION COMP | MONROVIA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | Contractor, Robert Brkich, while trenching to install new water line damaged 0.5 inch PLA service incased in 0.75 inch copper with backhoe. Marks were visible 15 feet away. ï¿½
Southern California Gas Company | N | LOS ANGELES | LA CRESCENTA | 2020-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | SHAWN RUBEN | RESEDA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working for home owner damaged 0.5 inch plastic service line with shovel wile digging near meter Location. No USA was called in
Southern California Gas Company | N | LOS ANGELES | LA CRESCENTA | 2020-12-09 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 0.75 | 60 | 35 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ARC CONSTRUCTION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party Contractor pulled out service from ground, not leaking.ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | LA HABRA | 2020-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | OMABS REMODELING | TUSTIN | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavator digging without USA. Installing conduit for decorative lighting around perimeter of yard. Damaged line with sharp shooter pick. No USA, failure to protect in place.
Southern California Gas Company | N | LOS ANGELES | LA HABRA | 2020-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer installing new planter struck 0.5 plastic service with shovel.
Southern California Gas Company | N | LOS ANGELES | LA PUENTE | 2020-08-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | C M CONTRACTOR | LA HABRA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit 1 inch plastic service with shovel while digging to clear water supply pipe.
Southern California Gas Company | N | LOS ANGELES | LA PUENTE | 2020-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | LA PUENTE |  | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging without a USA, broke 0.5inch PLA service pinched PLA and made repairs
Southern California Gas Company | N | LOS ANGELES | LA PUENTE | 2020-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | GONZALES PLUMBING | VAN NUYS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party digging with backhoe for sewer line work.
Southern California Gas Company | N | LOS ANGELES | LA PUENTE | 2020-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | WHITMAN ELECTRIC | WALNUT | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor hit 0.50 inch plastic service while hand digging to install electric conduit.ï¿½ Contractor exposed an old abandoned 0.50 inch service and continued digging and struck live 0.50 inch plastic service.ï¿½
Southern California Gas Company | N | LOS ANGELES | LA PUENTE | 2020-05-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | PHASE ELECTIRC | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit line with backhoe while trenching to install electric line. Contractor did not contact Dig Alert.
Southern California Gas Company | N | LOS ANGELES | LA PUENTE | 2020-11-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MEL SMITH ELECTRIC | SAN FERNANDO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3Rd Party Contractor Damaged 2 Inch Plastic Main With Backhoe
Southern California Gas Company | N | LOS ANGELES | LA VERNE | 2020-02-04 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 15 |  | NORIEGA PIPELINE | FONTANA | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | CONTRACTOR DIGGING IN ALLEY WITH A BACKHOE AND HIT GAS MAIN ï¿½ MAIN WAS RECENTLY REPLACED AND MARKS WERE STILL ON THE OLD MAIN AND NOT REMOVED BY OUR CONTRACTORS ï¿½ MADE REPAIRS BY ALTERING MAIN
Southern California Gas Company | N | LOS ANGELES | LA VERNE | 2020-01-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CARNELO ENTERPRISES | LA VERNE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | none
Southern California Gas Company | N | LOS ANGELES | LA VERNE | 2020-04-27 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ACCESS GENERAL CONTRACTOR | WESTMINSTER | CA | Y | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | ACCESS GENERAL WAS INSTALLING A BOLLARD FOR THE GAS METER.ï¿½ THEY ARE A CONTRACTOR FOR SO CAL GAS.ï¿½ THEY SAW A GAS METER THAT NEEDED A BOLLARD AND DECIDED TO INSTALL ONE WITHOUT CALLING USA.ï¿½ THAT IS WHEN THEY HIT THE PLASTIC SERVICE.ï¿½ IT WAS EXPLAINED TO THEM THE IMPORTANCE OF CALLING IN USA BEFORE ANY EXCAVATION IS TO BEGIN.
Southern California Gas Company | N | LOS ANGELES | LA VERNE | 2020-08-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | CITY OF LA VERNE | LA VERNE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CITY OF LA VERNE WAS REPAIRING A WATER LEAK WHEN THEY HIT AN UNMARKED STUB.ï¿½ STUB WAS UNLOCATEABLE AND THE CREW AND ETD ON SITE COULD NOT GET A SIGNAL EITHER.ï¿½ THERE WAS AN ACTIVE USA TICKET BUT LOGGIN WILL NOT LET ME COMPLETE THIS TAB WITH THIS TICKET NUMBER.
Southern California Gas Company | N | LOS ANGELES | LA VERNE | 2020-07-18 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NPL | MIRA LOMA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | NPL was working a main replacement when they hit the plastic service.ï¿½ They are opquald to mark the gas lines ahead of their project.ï¿½ the marks were accurate for this service but hit the gas service as they were trying to expose it.ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | LA VERNE | 2020-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NPL | BREA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | OUR CONTRACTORS ARE WORKING A MAIN REPLACEMENT ï¿½ THEY WERE TRYING TO EXPOSE THE PLASTIC SERVICE LINE WHEN THEY DAMAGED IT WITH A SHOVEL
Southern California Gas Company | N | LOS ANGELES | LA VERNE | 2020-12-15 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | NPL | MIRA LOMA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | NPL was replacing the gas lines in the community and had failed to pot hole gas service before digging with back hoe. Contractor is responsible for locating gas lines before digging and hand exposing plastic before digging with backhoe.ï¿½
Southern California Gas Company | N | LOS ANGELES | LAKEWOOD | 2020-03-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ALICIA JUAREZ | LAKEWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | On 03 29 20 while digging for water line to repair gas line was hit and broken Customer plugged broken line to control gas leak Family friend making repairs to water line The homeowner did not notify USA of any work being performed and did not have a valid USA ticket SCG crew arrived on site and made permanent repair
Southern California Gas Company | N | LOS ANGELES | LAKEWOOD | 2020-02-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 44 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | W A BASIC CONSTRUCTION | LONG BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged service while digging Lots of roots in excavation Space was tight
Southern California Gas Company | N | LOS ANGELES | LAKEWOOD | 2020-01-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | MASONRY BY JOE | LONG BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | On 1 29 20 while digging a trench with a backhoe for a block wall footing Joe Routh of Masonry By Joe damaged a one half inch plastic gas service ï¿½ Joe did not have a valid USA ticket ï¿½ SCG supervisor explained to Joe Routh of the importance in notifying Dig Alert prior to any excavations so the utilities can respond and mark the approximate location of their company facilities ï¿½ SCG crew arrived on scene and made permanent repairs
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2020-04-28 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 35 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RC BECKER JAVIER MADRIL | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor excavating and grading for new curb and gutters. found 2 inch PVC vent casing along with 2 inch PE casing with deep well anode wires encased in concrete
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2020-10-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Farm Equipment | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | LANCASTER | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was pulling a tree out. In the process he caused damage to our service.ï¿½
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2020-09-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | LANCASTER | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer hit 0.5 inch service line with Mini Excavator digging footings.
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2020-12-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | LANCASTER | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage to plastic service. Customer digging in front yard for no apparent reason damaged the gas service.ï¿½
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2020-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | LANCASTER | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was hand digging to install fence post and hit plastic gas line. USA was not called
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2020-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage caused by auger used to set fence post and lack of calling for USA 811.
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2020-07-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | LANCASTER | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | digging for irrigation line with trencher
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2020-10-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | QUARTZHILL WATER | LANCASTER | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Quartz Hill water company broke our unmarked service while digging with a backhoe.
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2020-12-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 40 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | LANCASTER | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.75 inch steel service pull out of ground and riser bent. No leak found.ï¿½
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2020-04-29 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MOUNTAIN WEST | CAMARILLO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | underground utility company excavating with backhoe for sewer laterals
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2020-09-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | WICOX AND WILCOX COMMUNCATIONS | CANOGA PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor struck service with a shovel when hand digging.
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2020-06-04 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 25 | 23 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | GALL BROTHERS | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd part Contractor scrapedgouged out 3 inch main with Backhoe. Contractor was using backhoe to dig over utility.
Southern California Gas Company | N | LOS ANGELES | LITTLEROCK | 2020-04-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MAURICO GUERRA | PALMDALE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was installing a water line and damaged the plastic service on the property with a backhoe.
Southern California Gas Company | N | LOS ANGELES | LITTLEROCK | 2020-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | LITTLEROCK | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home Owner installing fence struck service with a post hole digger Did not call USA
Southern California Gas Company | N | LOS ANGELES | LOMITA | 2020-01-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | LOMITA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | USA WAS NOT CALLED
Southern California Gas Company | N | LOS ANGELES | LOMITA | 2020-11-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LOMITA WATER DEPARTMENT | LOMITA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Lomita Water Co damaged CTS service with backhoe. clearly marked
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 43 | 39 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Home owner called in as damage found abandoned line.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 26 |  | TECHINCO | BELLFLOWER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | gas service was marked. locator went by locator but while looking GIS there was no svc shown on GIS. Locator spoke with contractor and sent multiple messages where contractor needed to pot hole service for verification. contractor did not pot hole but dug with backhoe and damaged gas svcï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 10 |  | BOUCLARD COMMUCATIONS | NORTH HOLLYWOOD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit service while digging trench. Service was located and marked correctly
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-01-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor demoing bldg and hit service with backhoe ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-05-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | DWP | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | ContractorDWP damaged correctly marked gas facility while digging with a backhoe. Gas company crew on site informed contractorDWP to expose all underground located gas pipelines by hand digging. On site crew also advised the contractorDWPï¿½to use more caution while excavating around underground substructures, even if by hand.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JUDD BURTON LICENSE 981184 | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor damaged 0.50 plastic service.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-10-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | VERONO HOMES | BURBANK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas service and did not call for an Underground Service Alert USA ticket. The crew onsite informed the contractor to always call Underground Service Alert USA at 811 Dig alert before digging, even when in private property.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BUILDERS TEAM | WEST HOLLYWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor cut into a plastic service with a sawzall while removing tree roots
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 22 | 19 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NORTHWEST EXCAVATION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Facility was not marked
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-06-10 | Third party excavation damage | Riser | Steel | Hand Tools | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JL CONSTRUCTION | HUNTINGTON BEACH | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | Contractor sheered stopcock aboveï¿½riser believing the service was abandoned. Contractor did not call for an Underground Service Alert USA ticket. The crew onsite informed the contractor to always call Underground Service Alert USA at 811 Dig alert before digging, even when in private property
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-08-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DC CUSTOM PLUMBING | PALMDALE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor was hand digging and hit service with shovel
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 21 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | ORDONEZ CONSTRUCTION | HAWTHORNE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Found 0.5 inch CTS service with makeshift repair to damaged service. Pinched service to make repairs and restored service. Construction work for block wall. NO USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-07-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | RITZ PLUMBING AND HEATING SERVICES | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While installing water softener system, 3rd party contractor hired by property owner, struck and damaged 0.5 inch PLA service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-07-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | W A RASIC | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | contractor damaged a 0.5 inch cts svc while digging to install a vault
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-06-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 4 |  | SMA BUILDERS | VAN NUYS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service and main marked correctly
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-03-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  |  | NA | NO COMPANY NAME PROVIDED | MALIBU | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | H O contracted Coastline Engineering and Development for drilling shoring work While excavating on the north side of the property Coastline Eng Dev was notified by CSF HO71 of live underground gas on the south side of the property At which point Coastline Eng Dev pulled off job H O then called her own independent contractor to investigate live gas line While excavating independent contractor struct and damaged 0.5inch PLA service at meter set area HO71 returned again for a second time and was first on scene Service was abandoned at SMC short side
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-01-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 0.75 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third Party contractor was installing electrical conduit and sewer line when service was damaged Unsure of what tools were being used ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-10-23 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TECHNICO TV INC | BELLFLOWER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor used machine to dig trench before potholing marked gas service and struck line with excavator.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-09-02 | Third party excavation damage | Main | Steel | Miscellaneous/Other | 4 | 40 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 6 |  | SE PIPELIINE | SANTA FE SPRINGS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor seen marks on ground from a DWP ticket that was called in within close proximity of job site. Company approved contractor SE Pipeline did not have their own marks on ground. Marks on ground indicated inch4 inch STL inch, but crew found 3 inch STL in ground. Did not dig tolerance zone. Crew failed to pothole correctly, they need to be billed.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-07-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | TURBO PULMBING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was working on sewer line when damaged gas service ,
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MYCONTRUCTION INC | MONTROSE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged a service while working without a valid Dig Alert ticket
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-01-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | DWP | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | there are 2 services for this propety
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-10-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HOME OWNER | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 0.5 inch plastic service while replacing a sewer lateralï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-05-20 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 12 | 140 | 139 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 30001 |  | 0 |  | WALSH SHEA CONSTRUCTION | INGLEWOOD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party damaged a 12-inch high pressure distribution main resulting in a release of gas. Crew responded and worked to control the gas. No injuries resulted from this incident. Line was marked correctly and contractor did NOT call for High Priority standby prior to excavating
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-03-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | AGUIRRE ROSALES CONSTRUCTION INC | NORTHRIDGE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Active USA marks visible in sidewalk While grading for home remodel 3rd party excavator pulled and ripped out 0.5inch PLA service in private property Marks visible in sidewalk but greater than 24 from location of 0.5inch PLA service
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | contractor damaged service while excavating
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-09-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HERNANDEZ GARDENING MAINTENANCE | SUNNYVALE | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | While grading for new driveway and sidewalk for 1119 and 1125, 3rd party excavator hired by 1119 developer, exposed 1 inch stl pipe with 0.5 inch PLA encased. Excavator cut out portion of 1 inch STL pipe and in process, severed active 0.5 inch PLA pipe. Excavator, in an attempt to control gas, folded back 0.5 inch PLA service and tied it off.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-05-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working on sewer line was hand digging with shovel and hit theï¿½0.50 inch cts plastic service. No Valid USA for jobsite.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor his 1 Pla service with small backhoe while digging a trench for the sewer lateral ï¿½ permanent repairs were made
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-04-17 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 22 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SOLA RENTALS | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | per worker handing with shovel and damaged 2 inchplastic main
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-05-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per LCT comments, a 0.50 inch plastic service was damaged while excavating with a hand shovel.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-10-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging in backyard against hill, homeowner cut into exposed 0.75 inch steel casingcutting into 0.5 inch cts pla gas service
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-12-06 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.38 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | LA DWP | SAN PEDRO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | LA DWP was digging for a main water leak repair.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-09-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner working on sewer hi 0.5 inch plastic service
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-05-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No valid USA ticket, contractor was grading property with hand tools and hit 0.50 inch CTS gas service with clay spade. Serviceï¿½was not leaking but did get badly gouged from the clay spade.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-08-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 22 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | DOCTOR ROOTER CO | WEST COVINA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third Party Contractor damaged plastic gas service while excavating to install sewer.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-06-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 30 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The excavator found the old steel service, but damaged the newer P.E. gasline.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | LADWP | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | ï¿½ Contractor found one plastic service in the trench, but there were actually two present for the same parcel. Should not be billed for damages.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-10-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | OCEAN CONSTRUCTION | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer claimed that he had called SCG to have two service abandonments. Heï¿½was under the impression that the abandonments have been completed.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-10-22 | Third party excavation damage | Riser | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MARK SCHEVERS | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor stated that he pulled on exposed riser service and that it cut on the 0.75 steel casing. 0.5 inch CTS line looked like it was cut in half by some sort of shovel hand tool and service was also protected from casing ring
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 7 |  | VAL VERDE CONSTRUCTION | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Per locator, he and the contractor had an agreed area that would be marked due to the lene length of the project. The contractor got ahead of the agreed upon area and damaged a 1 inch plastic service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | MATTHEW STEWART | SIGNAL HILL | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | No wire at riser location Used measurements off service history Marks were correct at curb but not at SMC service angled at SMC
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA was requested. Customer digging for sewer.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-05-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DOMINGUEZ GEN CONTRACTORS | POMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hand digging to expose water line damaged gas line
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 22 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 3 |  | DREAM SPACE | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | gas service was damaged while excavatingï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 3 |  | MATT STEWARTS | SIGNAL HILL | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Gas service mis located by gas co locator ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-21 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | FREE CREATIONS INC | CANOGA PARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor thought digging in the front yard was private property
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit and damaged a 2 inch plastic gas main in the parkway. The main was damaged by a mini excavator.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-12-22 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Augur | 0.75 | 39 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | KE BUILDERS 1049318 | LONG BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit water line and was using hacksaw to cut out damaged water line to repair then contractor cut into gas line that was directly beneath water line
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-10-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | G A CONTRACTORS | VAN NUYS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | The contractor was excavating to install power conduit in the street. He hit the 1 inch plastic service with a backhoe.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-11-19 | Operator excavation damage | Main | Steel | Miscellaneous/Other | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SE PIPELINE | SANTA FE SPRINGS | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged correctly marked gas facility while attempting to hand expose. Gas company crew on site informed contractor to use more caution while excavating around underground substructures, even if by hand.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-14 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  | 3 |  | MARK COMPANY | ORANGE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to exposeï¿½2 Plasticï¿½main andï¿½exposed a steel 2 pipe instead Marks on ground clearly stated size 2 and Material Plastic Contractor after exposing steel pipe went ahead and continued to dig with mini excavator and resulted onï¿½striking our 2 plastic main ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Augur | 1.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SHORING ENGINEERS | SANTA FE SPRINGS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor augered through a service that was properly marked
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-04-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | ENF BUILDERS | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | During constructionremodeling processing, 3rd party contractor struck and hit 0.50 inch PLA service. It is unknown when damage occurred, as upon arrival and inspection, location of damage was wrapped in rubber plumbers tape and worm gear drive clamp. CSF JN72 interviewed home owner, Tom, and revealed damage may have possible occurred back on August of 2019 when USA ticketï¿½ was called in. It is documented that ETD Sanchez met with and informed inchNiro inch of location of underground gas lines, which were in conflict of proposed excavation site for new water line on private property.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-04-23 | Third party excavation damage | Riser | Polyethylene Pipe | Miscellaneous/Other | 1 | 22 | 19 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | LOS ANGELES | CA | N | N | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | damaged riser unknown what was causeï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-10-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | AMERICAN INTEGRATED SERVICES | WILMINGTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor hit the service line with a backhoe while excavating to remove soil from the property.ï¿½ Gas facilities were properly marked. ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-04-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SK CONSTRUCTION | SAN DIMAS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor did not call in aï¿½ USA and was excavating a trench for the gas Co. to alter service and damaged our facility while in the process.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 22 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was excavating to remove tree roots.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-06-23 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ON GRADE D DITCH EXCAVATE | FONTANA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor struck a 1 inch plastic gas main while trenching with a h a mini excavator. No visible signs of pothole over marks
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-09-30 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  | 68 |  | WA RASIC | LONG BEACH | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor dug using a Backhoe near the Gas company facility without hand exposing the Gas Co. substructures.ï¿½ Backhoe broke the 2 inch main line which created around 70 outages to the services downstream of the damage.ï¿½ The Gas substructure was marked correctly and within the 24 inch allowance. ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-04-16 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | CITY OF LA PUBLIC WORKS | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Public Works acknowledged that facilities were marked out correctly they also hadï¿½hit a water service prior to hitting gas service
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-09-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | DAVINCI BUILDERS | GARDENA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | while exposing sewer lateral, 0.5 inch plastic pipe was hit with shovel
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PINNER CONSTRUCTION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor did not notify USA and damaged a 1 inch plastic service
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | damage 0.50 inch service with shovel
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-11-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | RAMONA GRBAVAC MLADEN | ARCADIA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | city of los angeles was using backhoe over gas service. contractor was not did not hand expose and damaged plastic gas service with backhoe bucket
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-05-07 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CHANNEL DEVELOPMENT CO | ENCINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged a 0.75 inch steel serviceï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-01-22 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | none
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-06-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | INDEPENDENT CONTACTOR | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | worker damaged PE line with pick
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-09-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | WHITCO PLUMBING | WOODLAND HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 0.5 CTS service line, while repairing sewer line
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GH CONSTRUCTION | GLENDALE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit plastic service with shovel while installingï¿½retaining wall
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-03-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | ADEEDO PLUMBING LICENSE 1042744 | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Adeedo Plumbing excavating to access residential cleanout on private property While excavating contractor struck and damaged direct burial 0.5inch PLA service Excavator stated he exposed a STL line and thought it was the gas line so he continued to excavate
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-11-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | COWBOY PLUMBING CO | SYLMAR | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged 0.5 inch CTS service by homeowner replacing sewer line.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NSA CONSTRUCTION | TARZANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | LAUSD 3rd parity contractor digging to install ballard poles in parking lot Dug into the gas service
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-10-20 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 4 |  | ACE DEMOLITION COMPANY | RESEDA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractors worker said they were using the excavator to perform work on sewer line and cut straight thru service.ï¿½ USA Tix unknown expired.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | SKY HOMELAND | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plastic service was damaged by 3rd party contractor during excavation to install wall
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-08-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | SELECT ELECTRIC | CERRITOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | service marked correctly and visibleï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-03-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 22 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | LADWP damaged facility while excavatingï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-08-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | EVOLVED CONTRACTING INC | SUN VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While excavating with hand tools for sewer lateral work, 3rd party contractor struck and damaged 0.5 inch PLA service on private property.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-03-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 25 | 21 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | COMMERCIAL PAVING COATING | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor exposed abandoned steel did not realize the service was marked plastic
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-05-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SEQEL CONTRACTORS INC | SANTA FE SPRINGS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged CTS line in casting with backhoe.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-01-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 22 |  | ESAB CONSTRUCTION | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to hand expose and protect service prior to digging with backhoe
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-06-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BEN KISLER | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While excavating on private property, 3rd party contractors struck and damaged 1 inch PLA service on property. No valid USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | DigIn Damage. 3rd party contractor did not expose the pipe by hand digging.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 21 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BAKSH CONSTRUCTION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor was excavating and damaged service during the process
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | homeowner digging for sewer damaged plastic service
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-10-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | OL DEVELOPMENT | BURBANK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor did not call for a USA ticket and nicked gas service with shovel while digging to repair water line. Homeowner and contractor was advised by company crew to call Underground Service Alert USA at 811 whenever digging, even when in private property.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-11-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | LOS ANGELES | CA | N | Y | Yes | Excavation occurred on private property by a non-contractor. | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | NO Valid USA, contractor was hand digging a trench with shovel for new wall and hit the gas service. Contractor damaged the 0.5 inch CTS service at PL and taped the damage shut. ï¿½NOTE two addresses on property 1520 and 1518 Tonawanda Ave, Los Angeles
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-08-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 10 |  | SEACON CONSTRUCTION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | All paving was removed,ï¿½ inchG inch painted in yellow on wall and a row of gas meters thereï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 22 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | EBV | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor cut service back due to being in the way and did not wish to contact SCGï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-07-21 | Third party excavation damage | Riser | Steel | Backhoe/Trackhoe | 0.75 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | H L FOOD SERVICE INC | LOS ANGELES | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No | No damage to SUOF. | No damage to SUOF. | Riser was damaged by employee with Forklift while moving pallets stacked against the MSAï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-03-12 | Third party excavation damage | Meter | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per onsite crew the contractors did not provide a company name when they damaged our gas facilities
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | AGI GO TECHNICAL | VAN NUYS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit 0.5inch plastic service with auger for soil samples Valid USA Contractor failed to pot hole before they augered Marked correctly Augger was withing tolerance zone of marks
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-11-17 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Cleaning crew was cleaning building and wall collapsed during work and sheared off service valveï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-03-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged company facilities while excavating
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-03-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | OBSIDIAN DEVELOPMENT LLC | IRVINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NB site contractor not on site Neighbor called Gas Co because of odor Found damaged buried line taped up
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 15001 |  | 1 |  | GMZ ENGINEERING | THOUSAND OAKS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival found opened trench with service broken and blowing ï¿½ Contractor crew hit service with backhoe ï¿½ Contractor did not expose the pipe by hand digging
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 0.75 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | SELECT ELECTRIC INC | CERRITOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Select Electric damage 0.75 inch steel service with bore reamer.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-04-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 0.50 plastic service. No USA but marked and marked correctly.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 22 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LEO MESA | GARDENA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer altered gas service on his own due to service being in the way of their work.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-05-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RED LILY PLUMBING | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.50 inch cts service damaged with shovel
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-10-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 34 |  | OL DEVELOPMENT | BURBANK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor hit miss marked ï¿½ï¿½ plastic gas service. Service was damaged 5ft. north of mark. Contractor potholed at mark, and didnï¿½t find the service within 3ft, Contractor notified ETD, ETD was on site on phone with supervisoin when contractor hit service. While investigating it was found that the ETD used all available resources including direct method of connection, RD8100 locator, GIS, and service history to locate service. Upon our invetigation it was found that service history and GIS were incorrect Employee was counseled to always inform contractor to stop the job until service can be properly located exposed.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-06-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 0.50 inch plastic service with shovel
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-04-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 28 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | LOUIS RIVERA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor did not wait for service to be abandon
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5 inch IPS service damaged by homeowner
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-08-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged 0.5 inch service while grading for new stairs landing
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-11-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor excavating at vacant lot hit 0.5 inch plastic service
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 0.75 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RIGID DESIGN AND CONSTRUCTION | ENCINO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor cut into service while excavating.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-06-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  |  | NA | VCI CONSTRUCTION | UPLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | VCI construction, while backhoe excavating trench site for ATandT, struckï¿½and damaged 2 inch PLA main. Excavator, Rocky Romer stated he saw visible, accurate marks for 2 inch PLA main but failed to exercise proper technique.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 21 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeownerï¿½was excavating for sewer and damaged plastic gas svc in the process
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | KOKONUT KONKRETE | GRANADA HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5 inch CTS service damaged while excavating to install fence.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-03-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 20 |  | MALCOLM ENGINEERING | BALDWIN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged 0.5inch cts service with Backhoe
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-01-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 4 |  | OL DEVELOPMENT | BURBANK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | Third Party Contractor was installing electrical conduit when Gas service was damaged by Back hoe Unmarked service was outside of delineation
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | DWP | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | LADWP installing new water main While excavating backhoe operator damaged 1 direct burial PLA gas line Marks for PLA w CSG visible next to LADWP water main trench cut accurate Direct burial 1 PLA damage inside of trench 1 STL pipe sitting directly on top of 1 PLA gas line Possible Badger potholed for LADWP and exposed 1 STL line and mistakenly labeled that as our gas line
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-10-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | RITZ PLUMBING | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Ritz Plumbing damaged 0.5 inch cts service with electric clay spade.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-12-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JF LANDSCAPING | ONTARIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | ï¿½According to damage report Landscaper Jose Fernandez explained that his son Jose Manuel was clearing around the gas line with a shovel when he accidentally hit the service line. Contractor did not call for a USA ticket and nicked gas service with shovel while digging to repair sewer line. Homeowner and contractor was advised by company crew to call Underground Service Alert USA at 811 whenever digging, even when in private property
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DANIEL STEDNITZ PLUMBING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | USA NOT NOTIFIED
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-07-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CENTRAL PROPERTY MANAGEMENT | BAKERSFIELD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party Contractor hired by property owner, while excavating to repair sewer clean out at two different locations on property, exposed 1.5 inch STL pipe. Excavator cut window into exposed line and in the process, damaged encased 0.5 inch CTS plastic line.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-09-23 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 39 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | LADWP came in contact with our facilities while fixing water line due to service ID not being inside the system. Information in the process of being updated.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-07-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit plastic service with shovel while digging for sewer
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 6 |  | EDUARDO TREE SERVICE | PICO RIVERA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner removing tree stump hit 0.5 inch CTS service with stump grinder no USA ticket for location.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-10-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  | 114 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 2 inch PLA main damaged by LADWP with backhoe. DWP crew failed to expose by hand as required.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BUILD GROUPS | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 0.5 IPS stub with graderï¿½by 3rd party. NO information on GIS.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DYNALECTRIC | LOS ALAMITOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged correctly marked gas facility while attempting to hand expose. Gas company crew on site informed contractor to use more caution while excavating around underground substructures, even if by hand.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-01-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 4 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | LADWP installing new service for 1940 S Bedford ST While potholing to locate 2 PLA main with shovel excavator struct 0.5inch PLA service within 24 of visible marks
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-04-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | WESTCO SERVICE CO | COSTA MESA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged 0.50 inch CTS service with backhoeï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-03-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | WILLIAM ROBLES | LYNWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas line while digging
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-11-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HARDLEY | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Homeowner hired a third party contractor who, while digging within the delineated area to install a grounding rod, hit the 0.5 inch cts service. Service was marked with flags in the yard and yellow paint on the sidewalk. Locator marks were accurate.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-03-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | EGAL CONSTRUCTION | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 0.5inch cts service
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | WEINSTEIN RETRO FITTING CONSTRUCTION | VAN NUYS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 0.5 inch CTS service with electric jackhammer. 2 residents evacuated.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 22 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JM COMMUTATIONS | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was digging trench to install conduit and damaged the clearly marked gas service
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-11-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Crew was digging to run a new gas line, when he hit the 0.5 inch CTS with a shovel.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 22 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | IVAN PLUMBING SERVICE | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | gas service was damaged while excavatingï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TND CONSTRUCTION | PALMDALE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged a service while excavating
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-10-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | TRI WEST DEVELOPMENT LLC | MARINA DEL REY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor did not call for a USA ticket and nicked gas service when installing garden post.ï¿½ Contractor was advised by company crew to call Underground Service Alert USA at 811 whenever digging, even when in private property
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-11-19 | Third party excavation damage | Riser | Polyethylene Pipe | Hand Tools | 1 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HANDYMAN | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged riser installing fence post.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ARI SHERIF | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | While using a mini backhoe for grading, 3rd party contractor hit service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-06-16 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 15 |  | INTERIOR DEMOLITION INCORPORATED | MONTROSE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party contractorï¿½damaged main with backhoe while excavating to move water pipe. ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | W LANDVIEW LANDSCAPE | OXNARD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor failed to call for USA and hit our 0.5inch plastic gas line while digging to install irrigation lines ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | RANDEL MARTINEZ | VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor wasï¿½pot holing to install street light conduit and gas line.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-07-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DIXSON CONSTRUCTION | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 0.5 inch CTS service wile hand digging for footing, no USA ticket was called in
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-09-01 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HENKELS MCCOY | CHINO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor for SCG hit service line while digging to install anode.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-11-03 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | APL | CHATSWORTH | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was replacing gas service. They had removed 4 inches of concrete and started hand digging for the 0.5 inch CTS gas service. The service had 12 inch inches of cover with poor backfill. In the process of pot holing it, the crew was removing rocks with a sharp shooter and nicked pipe damaging it with the sharp shooter.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-03-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BM NATIONAL | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While excavating for electrical foundation and new fence 3rd party contractor struck and damaged 0.5inch PLA service for neighboring property of 3158 Silverado Dr PLA service was direct burial and was struck by shovel while hand excavating No active USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-05-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TRUNK LINE CONSTRUCTION | GRANADA HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor pot holed to very pipe and depth.ï¿½Contractor damaged correctly marked gas facility while attemptingï¿½toï¿½removeï¿½old steel main, the plastic service ran above the old main, thus causing it to break upon removal of old main.ï¿½Gas company crew on site informed contractor to use more caution while excavating around underground substructures, even if by hand.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-11-18 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ACCESS PACIFIC INC | PASADENA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was grading and damaged the service to the building.ï¿½ Crew made repairs.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-12-02 | Third party excavation damage | Riser | Steel | Hand Tools | 0.75 | 22 | 19 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | LOS ANGELES | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | Contractor Thought Gas Line Was Abandoned And Cut Into It With A Grinder
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-10-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  |  | NA | NAXTEC CONSTRUCTION | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor pulled 0.75 inch STL casing with backhoe. Causing 0.5 inchCTS pipe inside pulled off from metfit, near tee in neighbors yard. USA was called after damage.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-04-08 | Operator excavation damage | Main | Steel | Miscellaneous/Other | 2 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | ARIZONA PIPELINE | CHATSWORTH | CA | Y | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | none
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-06-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TC GREEN HOMES | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged a plastic service with a mini excavator while digging for a fence
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | KANIT LICKITWONGSE | WINNETKA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Party Contractor excavating for new development electric trenching SCG marks visible at smc street and curbface Excavator while using backhoe failed to pothole to locate 1 PLA service and as a result struck and damaged gas facility
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 22 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LOCO PRO | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damaged gas service while excavating to repair sewer lateralï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-09-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10001 |  | 3 |  | NONSTOP PLUMBING LIC 1046510 | PASADENA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA FOUND IN KORWEB, CONTRACTOR DIGGING TO REPLACE EXISTING SEWER LINE HIT GAS SERVICE AT MULTIPLE LOCATIONS IN SERVICE RUN.ï¿½ CONTRACTOR EXPLAINED HE DID NOT NEED A USA SINCE HE KNEW WHERE THE GAS LINE IS RUNNING.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 3 |  | DOMINGUEZ GENERAL ENGINEERING | POMONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | locator went by footage. issues locationg that block.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HIGHLAND LLC | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor crew stated they hit service with backhoe while trenching to put in new sidewalk
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-01-10 | Third party excavation damage | Riser | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PADILLA S COMPANY INC | SAN FERNANDO | CA | N | N | Yes | No damage to SUOF. | Yes | Yes | No damage to SUOF. | Yes | Yes | Employee Alex was told by developer Yoni Arbel that gas service was abandoned and to go ahead and remove 0.5inch cts riser
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SELECT ELECTRIC INC | VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged 0.5 inch ips service with shovel
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-01-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | PADILLA S COMPANY INC | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Per LCT Ramirez the contractor pulled on a steel gas service casing while digging causing a leak on the plastic gas service inserted in the existing steel
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-11-06 | Third party excavation damage | Meter | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JPL | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 0.5 inch CTS service by contractor installing footing for retaining wallï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-12-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HESLER DEVELOPERS | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit water line and was using hacksaw to cut damaged water line to repair then cut into gas line directly beneath water line.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-03-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 22 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | DR ROOTER | VAN NUYS | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | contractor called USA after damaging the plastic service while digging for drain
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-01-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | AMERICAN SOLAR POWER | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor was drilling forï¿½foundation to hold Solar Panels Unmarked service running in this property to the property next door Line was not marked ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-01-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | AMERICAN SOLAR AND POWER | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party Contractor digging trenching for Gas Company crew to alter service Hit plastic service with shovelï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-10-17 | Third party excavation damage | Main | Polyethylene Pipe | Not Available | 2 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | WA RASIC CONSTRUCTION | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | The contractor had change of work direction and began trenching on 15th street before it was LandM. Apparently the contractor was not allowed that morning to work in the alley as the locator and contractor agreed.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 21 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 3 |  | NA | LOS ANGELES | CA | N | Y | Yes | Excavation occurred on private property by a non-contractor. | No | Yes | No | Yes | No | Customer damaged 0.75 inch steel line while grading with a uniloader, ticket was expired.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | PREMIER PLUMBING | PASADENA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit plastic service while hand digging NO USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-10-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was digging to repair a sewer line. Homeowner did not call for a USA ticket and damaged theirï¿½own gas service with drillï¿½whileï¿½repairing sewer line. Homeowner was advised by company crew to call Underground Service Alert USA at 811 whenever digging, even when in private property.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | SELECT ELECTRIC | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor, Select Electric, working for city of Los Angeles to install street lighting conduit. While hand excavating to pothole for scg facilities, 3rd party contractor struct and damaged 0.50 inch PLA gas service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-10-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | 12 TOWERS INCOME | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas service and did not call for an Underground Service Alert USA ticket. The crew onsite informed the contractor to always call Underground Service Alert USA at 811 Dig alert before digging, even when in private property.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-06-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | A TEAM PLUMBING SERVICES INC | NORTH HOLLYWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | ATeam plumbing services, while hand excavating to perform work for sewer cleanout, struck and damaged 0.50 inch IPS PLA service at address. When interviewed by John Cun, Robert Ferman stated he knew where the gas line was from previous sewer work completed at the address, which is why he did not open USA dig alert ticket.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-10-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MMM GENERAL CONSTRUCTIONS | DOWNEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas stub and did not call for an Underground Service Alert USA ticket. The crew onsite informed the contractor to always call Underground Service Alert USA at 811 Dig alert before digging, even when in private property.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-03-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HOMEOWNER OF 2450 AARON ST | LOS ANGELES | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | While excavating for property line fence 3rd party excavator struck and damaged 0.5inch PLA service with hand tools Fire Department Engine 20 was called and responded placing redwood plug in 0.5inch PLA service and then left scene before CSF arrived on scene Spoke with both property owners Edmund Soohoo and Ruben Guerra ï¿½who are going 50 50 on construction of property line fence Informed them both to call 811 and create USA dig alert ticket and necessary to wait 48 business hours before excavating again No active USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | SELECT ELECTRIC | CERRITOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Select Electric, performing street light install for LADWP, while directional boring, failed to expose visibly and accurately marked 0.50 inch PLA gas service and as a result, struck and damage 0.50 inch PLA cts service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-01-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | MICHAEL WALKER DESIGN BUILD INC | TOLUCA LAKE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 0.5inch CTSï¿½service with shovel while digging trench for sewerï¿½with shovel
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | MARK MENZO CONSTRUCTION | HAWTHORNE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit plastic service. Valid USA. Marksï¿½visible and correct.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | REFINED CONSTRUCTION | PALMDALE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor was hand digging for drain install
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-07-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner and contractor damaged own gas service while digging to install decking footing. Since the homeowner was completely unaware of 811 Underground Service Alert, Gas company crew on site informed the homeowner to call Underground Service Alert USA at 811 anytime when planning to dig so the utilities can be located, even in private property.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-03-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 22 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Homeowner was excavating for new house line owner damaged CTS service in process
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-03-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor damaged service while digging with a pick ax
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-09-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | WESTERN BUILT CONSTRONTUCTION | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 0.5 CTS service with backhoe.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-03-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 21 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Riser to this service was broken by the Demo contractor ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-07-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit plastic service while trying to remove tree stump
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | NA | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged correctly marked gas facility while attempting to hand expose. Gas company crew on site informed contractor to use more caution while excavating around underground substructures, even if by hand.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-05-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 22 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 3 |  | BULOV PLUMBING | SAN PEDRO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber did not call in a USA and damaged our gas service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-01-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LA DWP | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | DWP hit 0.5inch CTS service while excavating with backhoe Valid USA Service wasn t marked ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged the service with an excavator
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-05-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 22 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | LADWP | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO TICKET SHOWN, BUT DUG BEFORE LOCATOR COULD ARRIVE. DID NOT EXPOSE THE PIPE BY HAND DIGGING AS REQUIRED.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-06-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | MENENES CONSTRUCTION | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 0.50 inch IPS service with shovel
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-27 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 20 | 18 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | THE FISHEL COMAPNY | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | Contractor was excavating with backhoe when the pinched our pipe No leak
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | TEAM FISHEL | SANTA ANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was trenching for their conduits and damaged a 0.5inch cts service The contractor found the incorrect line and decided to dig with their mini excavator within the gas mark and which resulted on strikingï¿½the live gas service ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-04-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Property Owner, Edmond Burzycki, damaged the 0.5 inch plastic service with aï¿½shovel while excavation trench for his sewer. No USA was calledï¿½in for the property.ï¿½Crew made permanent repairs to service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-09-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 6 |  | ADDO PLUMBING | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per CR32, Third Party Contractor Plumber was digging to install drain for building. Service was hit with hand shovel.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-20 | Third party excavation damage | Riser | Steel | Not Available | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | 3CON FREIGHT | CARSON | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | This was not a DIG in vehicle hit riser ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-01-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | F F G CONSTRUCTION CONTRACTING CO | SANTA ANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hit plastic line ï¿½ Huge hole dug out but still hit line ï¿½ could not find USA ticket number and wasnt provided ï¿½ However clear marks present in regards to all service and main gas lines in construction area
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer digging for sewer repair, cut plastic line with shovel.ï¿½ No USA Ticket
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MOTO GROUP | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit riser with excavator while grading
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-05-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | FRANK FERRI | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No Valid USA, contractor hit 0.50 inch IPS service while trenching for sewer with backhoe. Company crew made permanent repairs needed.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-01-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | SELECT ELECTRIC | CERRITOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit gas line while potholing for our service Gas line was clearly and correctly marked ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | SELF PROPERTY OWNER | BURBANK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA Contractor was demoing a retention wall to install aï¿½ new retention wall During that process he damaged SCG service line SCG FOS2 explained to contractor the importance in calling 811
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-03-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 22 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | worker damaged gas service Did not call for a USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-10-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | VICTORS ROOTER AN PLUMBING | SYLMAR | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumbers were making repairs to the sewer lateral. they did not call in a USA ticket and attempted to locate the gas line themselves and were unsuccessful. ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-04-01 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ACRETE CONSTRUCION | GLENDALE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Live service was already exposed. Contractor lifted it up to move it out of the way. Service looked like it had been moved multiple times, it should have been abandoned before constructon
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-09-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 4 |  | TRIWEST DEVELOPMENT LLC | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per LCT Michael Ayala, Third Party Contractor was installing conduit when service line was struck with hand shovel.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | AMERICAN TRAINWORK PLUMBING | CULVER CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor damaged plastic svc with shovel while excavatingï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-01-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 21 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | SAMUEL CAMPOS LANDSCAPE | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | landscaper damaged gas service while attempting to remove tree stump
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-03-05 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 5 |  | CITY OF LA DEPT OF WATER POWER | NORTH HOLLYWOOD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Damaged 2 plastic main with backhoe
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DREAM LANDSCAPING | PACOIMA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Per HO23, Third party contractor was digging to work on electrical conduit.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LADWP | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | LADWP replacing water main hit plastic service while installing new water main Service did not show on GIS to be on the street it was hit Also the property service ran to was a vacant parking lot ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-03-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | MEDIA CONCRETE CONSTRUCTION | WEST COVINA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No Valid USA for excavation contractor was digging out sewer trench and came across plastic service Contractor damaged 0.5inch CTS with mini excavator ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-12 | Third party excavation damage | Miscellaneous/Other | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service while hand digging No USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-12-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | 909 803 4992 | WILMINGTON |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor removed large palm tree with crane. root wrapped round CTS service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-01-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CALIFORNIA FOUNDATION WORKS | BEVERLY HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While trenching for drain contractor struck gas service Contractor failed to contact USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-11-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | KREIK CONSTRUCTION | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavating with backhoe and hit gas line. No USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-03-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | SELECT ELECTRIC INC | VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged 0.5inch cts service DPA Entry Form ï¿½Contractor potholing and attempted to verify marked line was plastic encased in steel and damaged plastic service while cutting hole in steel casing
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-01-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | VASIL J INC | BALDWIN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third Party Contractor was installing a sewer main when the Gas Service was damaged
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-05-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner damaged 0.50 inch plastic service while digging to install retaining wall.ï¿½ USA was not notified.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-05-21 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DWP | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Damaged 0.75 inch steel service with backhoe.ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-10-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 4 |  | JUST RIGHT PLUMBING JUAN G OR JOHN PIPKIN | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractorï¿½ hit plastic service while trenching for sewer
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-04-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DI BARA MASONRY | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 0.50 plastic service while breaking concrete with jackhammer. Shallow service.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-05-19 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 3 |  | VASILJ | BALDWIN PARK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Digging to replace sewer
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-07-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | FORTE CONTRACTORS | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was excavating to install a drain conduit when service line was struck by an electric saw.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-09-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SELECT ELECTRIC INC | CERRITOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged 0.5 inch IPS service with shovel
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BEST DEMOLITION AND RECYCLING | GRANADA HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractorï¿½while digging damaged a serviceï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-05-04 | Operator excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 12 |  | ARIZONA PIPELINE | HESPERIA | CA | Y | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | SCG DRIP contractor was hammer drilling concrete and hit the buried bypass for riser. The bypass was buried in concrete an not visible.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | W A RASIC | LONG BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged 0.50 inch cts service backhoe
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-06-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NUNEZ CONTRACTORS | LYNWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor said they were grading the property and hit line where there was suppose to be no gas.ï¿½ Contractor claims they had USA Ticket.ï¿½ Show no USA Called.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3752 |  | 28 |  | SELECT ELECTRIC | VISTA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | On 02 17 20, SoCalGas was notified of a third party damage at 3411 W Olympic Blvd, Los Angeles. After arriving to the scene, the correct address was 992 S Gramercy Place. The contractor damaged a 1inch plastic gas service while directional boring to install traffic signal conduit. SoCalGas crew arrived and controlled the gas. No USA marks at the damage location due to GIS error. GIS will be updated with the correct information. There were no injuries that resulted from this incident. This incident was reported to CPUC when SoCalGas became aware of media coverage.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-05-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | RCR CONTRACTORS | SAN FERNANDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged our service while grading to build a retaining wall.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-03-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | FIRE STAR FAMILY HOMES | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor damaged service while excavating to fix sewer
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-06-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DYNAELECTTIC | LOS ALAMITOS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Damaged 0.50 inch IPS service with trencher.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-11-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 14 |  | TECHNICO CONSTRUCTION | BELLFLOWER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 1 inch plastic service with hand tools while digging to install pull box.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RESONNE BUILDING AND DESIGN | NORTHRIDGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was installing metal stakes to form for the cement pore they accidentally puncturedï¿½one side of the plastic 1 ips pipe Customer had no USA so when they so no markings of service were in place Customer at fault
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-09-24 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 17 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HP COMMUNICATIONS | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 2 inch PE Main was struck by a mini excavator by 3rd party contractor HP Communications excavating to install fiber optics
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MPS INC | BALDWIN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While replacing sewer for LADWP 3rd party contractor hit our plastic gas line with excavator L Mï¿½within 24 of mark Contractor tied back plastic service and continued to excavate and replace sewer pipe before calling Gas Company ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-29 | Third party excavation damage | Main | Polyethylene Pipe | Not Available | 4 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MOUNTAIN BREAKING CO | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Locate and Mark EE located main and two services on East side of Overland Ave He was unaware of 4 main on the west side of the street
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-09-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging to remove a bush and roots in home owner backyard, hit 0.5 inch cts aldylay service
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-04-17 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | AARON KIRMAN PARTNERS | BEVERLY HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service with backhoe while digging in lotï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-06-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | LEO ROBLES | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Owner stated the contractors were digging to locate water line and in process cut thru gas service with shovel.ï¿½ Customer also said he did not believe there was an 811 ticket.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-01-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CONTRACTOR WAS GRADING HIT SERVICE WITH SHOVEL
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 22 | 19 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | HERMES | NA |  | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor cut into exposed gas service
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-04 | Third party excavation damage | Riser | Polyethylene Pipe | Not Available | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | STEPHAN BLOOM | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Gardner smelled gasï¿½ upon arrival riser was found buried ï¿½ Looks like construction work must have damaged service and left it ï¿½ there is an EFV on the service and who ever hit the line saw no gas and left it as is ï¿½ Later as the EFV reset gas was now flowing back out ï¿½ Only have name of Contractor on site of job ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 22 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | REPIPING PROFESSIONALS | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damaged gas svc while excavatingï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-12-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | MIGUEL CARDIEL | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | gas service was damaged while using jackhammer during removal of concrete. No USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-04-05 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | home owner hit 0.75 inch steel service while installing fence pole. No USA. Service was marked and marked correctly.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-04-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 22 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | SUPERIOR HOMES | ARCADIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor damaged gas service while excavatingï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 22 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MOTIVE ENERGY TELECOMMUNICATIONS | CORONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | contractors damaged gas service while trenching with backhoe ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-05-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 22 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ROSALES CONSTRUCTION | SUNLAND | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor did not call in a USA and damaged our gas service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | LOS ANGELES DEPARTMENT OF WATER AND POWER | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | LADWP crew hit gas service with backhoe while working on replacing a water main.ï¿½ Backhoe operator had received inchGo ahead inch from prospector to continue digging and did not feel the steel service being pulled until he saw it coming up out of the trench.ï¿½ Locator marks were visible but off at 3 from actual service location.ï¿½ Locator picked up water service which may have been touching gas line.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-04-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | H VAC PLUMBING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor drilled through copper casing and struck a plastic service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-01-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 22 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | THE MAURRY COMPANY | COMPTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor damaged svc while excavating while using backhoe ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | ECO CONCRETE INCORPORATED | BALDWIN PARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging trench for new drainage and hit our service line.ï¿½ There was no USA called in.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-04-13 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 22 | 19 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TCDC TRI COUNTY DEVELOPMENT COMPANY INC | RIVERSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor damaged service with backhoe while digging to replace the paving.ï¿½ Service was marked correctly.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-11-23 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BALI CONSTRUCTION | SOUTH EL MONTE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor hit steel service.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-06-22 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 5 |  | JILK HEAVY CONSTRUCTION | BREA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was excavating and in process cut right thru service.ï¿½ Contractor said they had usa ticket and work is being done for City of LA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-09-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | LANDSCAPING REMOVAL TREES | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hired 3rd party contractor to remove tree in private property. While in the process of removing tree, 3rd party contractor pulled and removed 3 section of 1 inch PLA service. EFV was tripped and as a result, damaged gas line was not discovered until homeowner reported no gas on property and in appliances.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-01-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 18 | 17 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | FULLEY MILLER | BREA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working on repairing the sidewalk hit a 0.5inch cts service ï¿½ The old marks were removed when the old sidewalk was removed ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | WAR CONSTRUCTION | LONG BEACH | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 0.50 plastic service with backhoeï¿½while digging to install conduit for DWP.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-08-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ORTIZ SPECIALTY SEWERS | MISSION HILLS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged service that was incorrectly marked. After an investigation with Gas company Locator, reviewing GIS, WebView, Service History, and measurements it was found that all of the tools the locator used were not up to date in the system. Service History indicated plastic pipe in casing and all the measurements, GIS, WebView and Service History indicated the location the contractor exposed and found steel pipe in the exact location. The real service was a plastic pipe direct burial approximately ten feet away. Locator used all available tool since he could not gain access to the MSA location.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | damaged 0.5 inch CTS service by homeowner
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | LEVEL 5 DESIGNED | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 22 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | AMG | SANTA CLARITA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Gas service was damaged while excavatiing
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-04-24 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 4 | 22 | 19 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | SKANSKA RCC REGIONAL CONNECTOR CONTRACTORS | LOS ANGELES | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor hit a 2 inch plastic main while working on Metro rail project.ï¿½ USA ticket wasï¿½ expired, but the old marks where still visible outside of work area.ï¿½ Permanent repairs were made.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 22 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | DWP | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | there is no service history of any kind for this service service history shows gas service was abandoned in 1985 and no reinstatement GIS shows no signs of gas service
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-01-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 22 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | CHAAPS CONSTRUCTION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging a trench for a water line in private property The contractor hit a 0.5inch plastic gas service with a shovel and a as a result created a leak There were no active DigAlert tickets at this address per CRN05 Crenshaw locators designated area
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-05-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 20 |  | MARTIN CONSTRUCTION | YUCAIPA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged 1 plastic service while excavating with backhoe. Line was not marked correctly at excavation site. Signal was leading the locator to a different location. The SMC mark was correct.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-12-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NEW GENERATION PLUMBING | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor did not call for a USA ticket and nicked gas service with shovel while digging to repair sewer line. Homeowner and contractor was advised by company crew to call Underground Service Alert USA at 811 whenever digging, even when in private property
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-11-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JUAN G CASIANO | LOS ANGELES |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damaged service while excavating for sewer.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-12-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | OCEAN PROPERTIES | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Grading for new development
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-10-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 22 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | LOS ANGELES |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor did not call in a USA and damaged gas service whileï¿½digging to install new sewer.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-10-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | CALIFORNIA ELECTRIC CONSTRUCTION SERVICES | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit line with backhoe.ï¿½ No USA was called in.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CALIFORNIA ELECTRIC CONSTRUCTION SERVICES INC | CANOGA PARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Operator ripped through 0.5 inch cts service with backhoe without first exposing pipe by hand digging. Also most recent USA Ticket number for this address for California Electric and Construction Services expired 2 5 20.ï¿½ ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-06-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RANDY STINE | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | USA was not called in. Service was damaged while excavatingï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-07-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | MONTEBELLO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit service with pick axe while digging for sewer repair.ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-07-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor said they were digging and he hit the service line.ï¿½ He put what appeared to be eletrical tape and line was not blowing but leaking.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-11-27 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 18 | 16 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 8 |  | BOOMERANNG ENGINEERING INC | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | No | Contractor digging for electric hit two inch main. Main hit outside of the mark.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CC AND E COMPANIES | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 0.5 inch plastic service while working on drain in vacant home
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-06-24 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BUILT IN 72 INC | CALABASAS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit a steel service while grading
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-12-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | NA | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging to repair a sewer line
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-08-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HYDRO JET | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging trench for sewer damaged 1 inch PLA service, NO USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | TOMOVICH ASSOCIATES | PICO RIVERA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor did not expose correct pipe they found one and starting digging with backhoe without confirming line Contractor then stuck the line in the same pothole ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | none
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-03-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 60 | 55 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MADRIGAL CONSTRUCTION | BELL GARDENS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Approved
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  | 28 |  | NA | ARCADIA | CA | N | N | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No damage to SUOF. | No damage to SUOF. | No | No damage to SUOF. | No damage to SUOF. | EE spoke with employee of contractor and told him area was excavated with excavator 3 months prior and claims they didnt cause the damage.ï¿½ Evidence shows hand tools were used to damage pipe contradicting his statement.ï¿½ Contractor turned off all 28 meters including riser for header before first responder was on scene.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-01-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | homeowner was digging holes for retaining wall when they struck gas service no usa was called ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-11-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | ERICSSON INC | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit plastic service while trenching
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Installing gas houseline
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-12-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | AGL PLUMBING | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor Hit 1 Inch Plastic Service That Was Exposed While Digging To Install Water.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-07-08 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ESCOBAR CONTRACTING CO | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | Upon arrival, found damaged main with temporary repairs made by contractor.ï¿½ They stated hit pipe wbackhoe.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 22 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TEAM FISHEL | SANTA ANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service was marked and called out correctly. Excavator failed to hand expose and damaged service while digging with Back hoe.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | WH RAFIC CONST | LONG BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor Hit abandoned service stub with backhoe.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SELECT ELECTRIC | CERRITOS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Unmarked service damaged by horizontal bore motor
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-07-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HARBOR PAVING STONE | LOMITA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party excavator, while trenching and excavating for electrical fence install, was driving wooden stake into ground, causing damage to 0.5 inch CTS plastic and release of gas. Upon release of gas, excavator taped off portion of damage in attempt to limit release of gas.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 13 |  | LA DWP | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service hit while replacing a water main
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 21 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | HP COMMUNICATIONS | GARDENA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party did not keep distance from gas service and damaged while excavatingï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | BUSY BEE PLUMBING | VAN NUYS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer contractor hit the 0.5inch plastic service ï¿½ They failed to call 811 and get the facilities marked out
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-03-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 21 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SELF CONTRACTOR | VAN NUYS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor cut into the service with a sawzall ï¿½ Crew made permanent repairsï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-09-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ALABOUT PLUMBING | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1 PLA service damaged with shovel by third party.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 22 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ANDREW WAGNER | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | facility was damaged while trenchingï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-11-12 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer claims while hand digging in trench, hit gas service and noticed odor hissing. Upon crew arrivalaudible leak, gas service not exposed
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-11-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HANOVER BUILDERS | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | damaged gas service by third party. No USA called in.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 22 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | GATES ENTERPRISES | IRVINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was grading lot, damaged service and buried it. The contractor did not call the damage in. DWP flagged down one of our EEs to make us aware that the contractor had damaged the gas service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-12-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | MARTIN CONSTRUCTION INC | YUCAIPA | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit service while boring on public street, company crew made permanentï¿½repairs. Service was not marked
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-09-01 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 1 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | WA RASSICK | LONG BEACH | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 1 inch abandoned stub hit with backhoe.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | DYNA ELECTRIC | LOS ALAMITOS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 0.5 inch plastic service hit while boring to install street lights
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NA | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | none
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-12-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | VICTOR PEREZ | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Worker was digging with shovel next to MSA and hit service line no USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | HO digging rose bush and hit svc with shovel. Service was shallow and ran along edge of house.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-01-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | MIRAGE CONSTRUCTION INC | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was working on grading property and while using the jackhammer he broke the 0.5inch cts service line running through the property contractor did not have a valid USA ticket at the time
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-10-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RESONNE BUILDING DESIGN | PANORAMA CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged gas line while exposing it by hand digging.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-03-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | LAS CASAS REALTY INC | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | workers were working on remodeling for house while hand diggingï¿½they damaged the 0.5inch CTS service No valid USA for property customer at fault
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-12-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ECS BUILDERS | STUDIO CITY | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | The contractor was digging to clear dirt from area. In the process the 0.5inch cts service was damaged with a shovel.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-05-13 | Operator excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | ARIZONA PIPELINE | CHATSWORTH | CA | Y | Y | Yes | Yes | No | No | No | Yes | Yes | Damaged 2 inch PE main by ARB. Excavating to install punch tee to check for possible water in main. DIMP job and DIMP supervisors on scene.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | PEDDICORE CONSTRUCTION | THOUSAND OAKS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged plastic service with shovel
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-05-15 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ARIZONA PIPELINE | CHATSWORTH | CA | Y | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Company contractor damaged exposed gas line while digging to install new gas line. No USA. Spoke with foreman and told him to extend delineations or call in a new ticket for his job site. Company crew spoke to contractor crew about the correct way to dig around plastic services to prevent this from happening again.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-12-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 22 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | A PLUS DRAIN DAMAGED | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaging Party should be billed
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | SELECT ELECTRIC | VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor did not expose plastic service
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-03-31 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 22 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | CITY WIDE INVESTMENTS | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | none
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | H AND L ENVIRONMENTAL DEMOLITION | ORANGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Demolition crew clearing property for new construction of residential property While demolition crew working damaged 0.5inch plastic service while using bulldozer Riser was not present on property or retrieved by company crew Eight foot section of 0.75inch steel pipe with 0.5inch inserted PLA pipe was retrieved in nearby spoil pile created by demolition crew Damaged section of live gas line not identified or excavated by company crew excessive tree roots
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 6 |  | ESVIN RIVERA | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was installing a post for a rod iron gate While installing post service was damaged Third party contractor was using hand tools
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | INGLEWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Responsible party was installing a guard post and damaged gas service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-03-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RALPH STONE AND COMPANY | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA was called in by the contractor No Valid USA Contractor was digging holes for landscaping and hit the 0.5inch gas service ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 12 | 10 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | HAC LA | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Housing Authority was installing a sewer line for a temporary construction trailer.ï¿½ Did not call in USA.ï¿½ Broke 1 inch plastic service line. Line is a housing authority line after the main MSA for housing project.ï¿½ Gas Co. had to repair per long standing agreement.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-28 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 2 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | MALCOLM DRILLING | IRWINDALE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor welding over exposed main While welding some melted metal landed on the main and burned a hole through it ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-01-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 21 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | LINCOLN CONSTRUCTION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged a plastic service digging a post hole for a fence
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | SANTA ANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor dug into plastic service even though it was marked correctly due to hard dirt.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-07-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | CESAR CONTRERAS | INGLEWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor struck gas service while, digging for fencing.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-11-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 0.75 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DYNA ELECTRIC | LOS ANGELES |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 0.75 inch steel service with bore while installing street light conduitï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-09-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | FORZA CONSTRUCTION | VALENCIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 2 inch service damaged with backhoe by 3r party contractor digging trench for drain lineï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-19 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3223 |  | 0 |  | DOJA INC. | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On 02 19 20, SoCalGas was notified of a third party damage at 6207 W Sunset Blvd, Hollywood. Third party contractor had large section of 2 inch plastic main exposed. While excavating alongside the exposed 2inch plastic main, the contractor damaged it with a mini excavator. SoCalGas crews responded, and controlled the gas. There were no injuries nor damage that resulted from the release of gas. This incident was reported to CPUC when SoCalGas became aware of media coverage.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-03-18 | Third party excavation damage | Miscellaneous/Other | Polyethylene Pipe | Trencher | 0.5 | 20 | 18 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | service was raised up and out from underground due to being in way of new foundation owner did not make contact with SCG to properly care for gas service service is a plastic service in casing plastic service was folded over steel service which caused plastic to fold and kink left unsafe by home owner
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-01-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NORTH WEST EXCAVATING | NORTHRIDGE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | DWP was cleaning dirt around 0.5inch IPS pipe and damaged the service
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-08-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Property owner damaged 0.5 inch PE service while grading for driveway improvements.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | R H CONSTRUCTION | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third Party contractor was excavating for Grading purposes Property is being redeveloped ï¿½Gas mirgrated to 633 N Detriot Evacuees 6
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-06-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | APPLIED SOIL TECHNOLOGY | GLENDALE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was augering for soil samples and hit our service line.ï¿½ No USA.ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-04-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | homeowner dug trench to replace sewer. Cut a copper line, unaware that it was casing for 0.50 inch cts service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-10-30 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 3 |  | EDUARDO MOLINA | BELL GARDENS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per LCT Al Sanchez, Third Party contractor was digging to repair sewer. They were using Hand tools. Hand Shovels. No USA ticket obtained.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 3 |  | TOM | SYLMAR | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Party contractor doing electric work for new development at 642 N Commonwealth Ave While excavating in street contractor struck and damaged 0.5inch PLA service for 641 N Commonwealth marks were visible for 641 N Commonwealth at the sidewalk curbface and gutter Excavator Chris Angel project manager for JM Communications claims marks were not visible in the street where excavation was performed SCG confirmed marks were laid in street during initial USA visit however street top layer of 2 removed to insert STL plates to cover trench John Cun informed Chris Angel in the future if marks are visible in this case at 641 N commonwealth in the sidewalk and gutter pot hole to expose SCG facility and or contact SCG for marks verification
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-12-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ON TIME ROOTERS PLUMBING GUYS INC | MONTEREY PARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Working with no USA, contractor damaged service while shoveling
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | SULLY MILLER CONTRACTING | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service was marked correctly and contractor did not expose the pipe by hand digging as required
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ANGEL ROSCO | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner contracted 3rd party to grade front yard to create new walkway and stairs to left side of home While excavating with pick axe 3rd party struck 0.5inch PLA encased in STL service
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-07-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | NEWPORT BEACH | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Surveyor was walking map and found service line folded over and taped.ï¿½ Surveyor called dispatch to have crew repair damaged service. No one working on site to determine cause and responsible party. Further investigating, District was able to speak with property ownerï¿½on 72020,ï¿½ The property owner states he did not know at the time that the service was live, due to the EFV shutting off the service when it gotï¿½hit. Property owner has made arrangements with SCG planner to alter service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-10-12 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 35 | 29 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SEWER LINE SERVICES | GRANADA HILLS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor was excavating with backhoe and damaged unmarked 2 inch plastic main
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | AG B | BALDWIN PARK | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | USA was expire Markings were faded away Service was damaged with mini excavator
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | TUI SONS CONCRETE CONTRACTORS | GARDENA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5 inch IPS service was hit w a shovel while trying to remove a plant to pour concrete on back side of curb, service was 6 inch below grade at damage, no valid USA.ï¿½ Explained to the contractor how to call USA for any future digging and the importance of doing so, no matter how deep digging.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 2 |  | CREW INC | COMPTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | USA was not called. USA ticket was expired and not renewed for remarking. Old markings were removed due to asphalt was removed.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PADILLAS COMPANY INC | SAN FERNANDO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While hand excavating for natural gas service replacement for branch service at neighboring address 3rd party struck 0.5inch PLA service with pick axe Service was exposed while excavating Excavator did not take caution while excavating USA from previous NLR Updateï¿½ ticket Marks on private property were refreshed on 02 27 2020 from a damage occuring on that day This is the second damage on the same property
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | PADILLAS COMPANY INC | SAN FERNANDO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd Party Excavator trenching for gas line on private property While backhoe excavating for new trench for neighbor s gas replacement currently branch 0.5inch PLA service branch was damaged Active nolocaterequired update USA ticket Last marked in 10.5inch7 2019 Existing marks on private property not maintained or visible
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-03-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PADILLA S COMPANY INC | SAN FERNANDO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged gas service with backhoe digging trench to relocate gas service
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-04-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | PADILLAS COMPANY INC 564257 | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner of 7062 Lexington called in saying he had no gas. Upon crew arrival they found a damaged 1 inch plastic service in empty lot next door. Homeowner claimed he didnt have gas once they installed temporary power pole next door in empty lot.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GENERAL NATIVE GREEN | SUNLAND | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While excavating for installation of new fence and tree planting, 3rd party excavator, hired by homeowner, struck and damaged 0.5 inch CTS plastic gas line. Upon the release of gas, excavator cut and tied back gas line in attempt to minimize release of gas.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-09-17 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 35 | 29 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | LADWP | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | LADWP hit unmarked Stub Service While excavating.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-07-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TOPLING CONSTRUCTION | NORTH HOLLYWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 1 inch plastic service with backhoe
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-05-26 | Third party excavation damage | Riser | Steel | Miscellaneous/Other | 0.75 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | JEFF BUCHANNAN TREE SERVICE | FULLERTON | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | Contractor was trimming a tree and one of the branches fell on the bypass on the rise and broke.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-01-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ESTRELLA CONSTRUCTION | COVINA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA CALLED IN FOR LOCATION
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ORTIZ SPECIALTY SEWERS | MISSION HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor didnt call for a USA ticket and nicked gas service with shovel while digging to repair sewer line. Homeowner and contractor was advised by company crew to call Underground Service Alert USA at 811 whenever digging, even when in private property
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | W C BUILDERS | WEST HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor cut into casing with 0.5 inch CTS service inside. NO USA CALLED IN
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-12-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LA DWP | SAN PEDRO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | LADWP Hit 0.5 inch CTS service while digging up water main leak.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-03-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | JOEL OROS | PANORAMA CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | USA WAS NOT CALLED
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-01-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 38 |  | DWP | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | none
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | ELECTRIC SERVC | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA Contractor was installing electrical conduits in back yard While digging he puncture a hole in SCG steel service line Fos2 communicated to him the importance of calling 811
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 4 |  | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged gas service while digging to repair own water line. Gas company crew on site informed the homeowner to call Underground Service Alert USA at 811 anytime when planning to dig so the utilities can be located
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-11-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging roots from under tree to dig trench for sewer and accidently hit plastic 0.5 inch CTS gas service
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | MARTIN BROTHERS PLUMBING SERVICES | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service damaged by plumber repairing sewer line.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MARK BARRUETA | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 0.50 inch plastic service while trenching for new water line.ï¿½ USA was not notified.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-06-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | PADILLA S COMPANY INC | SAN FERNANDO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | While excavating with backhoe, 3rd party contractor struck and damaged 1 inch PLA service for adjacent property, 3385 W 8th St, which ran inside of property line of 758 S Kingsley Dr. Service history and GIS do not show active service for 3385 W 8th St, which is being looked into by local management and planning.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-06-04 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  | 2 |  | VEPO DESIGNS | LOS ANGELES | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 3 inch main damaged with backhoe by contractor.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-04-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MOISES LARA | INGLEWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | service damaged with shovel while digging to remove tree stump
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-10-09 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | BARCO ENGINEERING CONTRUCTION | CANYON COUNTRY | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | Contracror Broke Riser While Trying To Move Msa Close To The Wall
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged correctly marked gas facility while digging with a backhoe. Locate marks and flags were either covered or removed. Gas company crew on site informed contractor to expose all underground located gas pipelines by hand digging. On site crew also advised the contractor to use more caution while excavating around underground substructures, even if by hand.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-05-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LA DESIGN AND BUILD INC | ALHAMBRA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor did not have a valid USA.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | JOHN BYRNE CONSTRUCTION | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit a 0.50 inch plastic service with a shovel
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-07-08 | Third party excavation damage | Main | Polyethylene Pipe | Grader/Scraper | 2 | 35 | 29 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TI SPECIALTIES | TORRANCE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor Kerry V Cornet claims that the mini excavator used by his crew came in contact with the gas facilities creating a blowing leak
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-03-18 | Third party excavation damage | Main | Polyethylene Pipe | Not Available | 2 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | LADWP | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | damaged 2 plastic main with backhoe Per summary from DPA Entry Form ï¿½LADWP damaged 2 PLA main with backhoe while performing water main replacement Per FOSII Henry Campos locator unable to get signals from any nearby risers or from wire on main when hooked up to it after damage Trace wire was old white coated wire
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-07-09 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 12 |  | J DE SIGIO CONSTRUCTION INC | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Per Edwin Alvarez, DWP were digging with a backhoe and hit the plastic main.ï¿½ He said he saw 1 line but not the other.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-04-01 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | KBA CONSTRUCTION | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor used Saw to cut into 0.75 steel service
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-05-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 22 | 19 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | TCDC | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged facility while attempting to expose 0.50 inch CTS plastic service
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | hit plastic line on private property with post hole digger
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-12-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 4 |  | PACIFIC WEST COMMUNICATIONS | SAN DIMAS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit line with excavator.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-03-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | CRP PLUMBING | LYNWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor broke service line while trying to repair sewer
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | SULLY MILLER | BREA | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Cut Back Service no records
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | DREYFUSS CONSTRUCTION 668225 | WEST SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Active USA marks visible and accurate Excavator failed to maintain 24 clearance from marked pipeline As a result excavator while digging with backhoe struck and damaged abandoned tee and stub
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-10-30 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1.25 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | INLINE CONRETE SAWING AND BREAKING INC | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor grading hit 1.25 inch STL service. No USA ticket called in by Inline Concrete Sawingand Breaking for work being done. Working under USA ticket for Pankow Builders.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DOUBLE GREEN LANDSCAPING | VENICE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging w excavator , cut pipe
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HANOVERS BUILDERS | THOUSAND OAKS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1935 service runs under dry creek bed, contractor thought it went around on bridge
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-12-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 22 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging trench for sewer hit 0.5inch CTS service
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-01-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA at the time of damage Per LCT contractor did not want to identify themselves and homeowner was taking reponsibility for the damage
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-03-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | WINNCO BUILDERS INC CSLB 1037580 | GRANADA HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | H O contracted Winnco Builders INC to install sewer lateral for new ADU in back of property While trenching for sewer lateral excavator exposed approximately 30 of 0.5inch PLA service and the riser Excavator states that while breaking out a concrete footing for fencing at the riser area 0.5inch PLA service was struck and damaged
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-11-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | SELF | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit plastic service while installing sewer
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-10-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 0 |  | ODIC ENVIROMENTAL | BREA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | contractor hit service while taking soil samples
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GENERAL SERVICE STANDARD | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | LA city worker checking compaction ï¿½damaged line with with DCP ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-02-18 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 25 | 21 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | HHS CONSTRUCTION | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor digging to locate communications conduit damaged the transition fitting
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-10-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PENA DEMOLITION | SUN VALLEY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Mark and marked correctly.ï¿½ Bill contractor
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-10-16 | Third party excavation damage | Riser | Steel | Grader/Scraper | 0.75 | 21 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | LOS ANGELES | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | Contractor Mike hit riser while grading in private property
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-03-27 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 40 | 35 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | TERRY ELLIS PROJECT MANAGER | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While excavating in street for repaving 3rd party contractor pulled 0.75inch STL service No leak found by crew Crew re wrapped pipe and was able to remediate kink in 0.75inch STL service
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-04-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ENDRIZZI ENTERPRISES | ANAHEIM | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | signal interference in Jordan Downs housing projects.ï¿½
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-04-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PORTRAIT CONSTRUCTION | CORONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | LA Housing Authority. No records and bad locating wire
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2020-07-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SUB CONTRACTOR FOR ERIC PONCE | SIMI VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While grading for new driveway, 3rd party excavator struck and damaged 1 inch PLA service with wooden stake
Southern California Gas Company | N | LOS ANGELES | LYNWOOD | 2020-09-03 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | AMERICAN CONSTRUCTION SERVICES | PARAMOUNT | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor digging to install bollard damaged cts service
Southern California Gas Company | N | LOS ANGELES | LYNWOOD | 2020-11-17 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 16 |  | ALL CITIES ENGINEERING | JURUPA VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | The Gas Company is at fault
Southern California Gas Company | N | LOS ANGELES | LYNWOOD | 2020-12-04 | Third party excavation damage | Riser | Steel | Hand Tools | 0.75 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | LYNWOOD | CA | N | N | Yes | No damage to SUOF. | Yes | Yes | No damage to SUOF. | Yes | Yes | none
Southern California Gas Company | N | LOS ANGELES | LYNWOOD | 2020-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DORECK CONSTRUCTION | PICO RIVERA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit line after exposing 1 inch steel line. Line was marked out Plastic.
Southern California Gas Company | N | LOS ANGELES | LYNWOOD | 2020-05-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | HARDY HARPER INC | LAKE FOREST | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | contractor pulled svc in casing while grading.
Southern California Gas Company | N | LOS ANGELES | LYNWOOD | 2020-06-11 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SE PIPELINE | NA |  | Y | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor did not evacuate gas facility before trying to bore pass gas service.
Southern California Gas Company | N | LOS ANGELES | LYNWOOD | 2020-01-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | LYNWOOD | CA | N | Y | Yes | Excavation occurred on private property by a non-contractor. | No | Yes | No | Yes | Yes | Home owner digging for fence post Called USA after damage
Southern California Gas Company | N | LOS ANGELES | LYNWOOD | 2020-05-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 5 |  | GM PLUMBING | LONG BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor Hit 0.50 IPS line. no USA
Southern California Gas Company | N | LOS ANGELES | LYNWOOD | 2020-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 7 |  | STEVEN DERRICK EQUIPMENT RENTAL | PICO RIVERA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor was installing water main.ï¿½ Service was missed. Service is cross lot in private property.ï¿½
Southern California Gas Company | N | LOS ANGELES | LYNWOOD | 2020-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SEQUEL CONTRACTORS | SANTA FE SPRINGS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | while contractor potholing damagedï¿½ gas service.
Southern California Gas Company | N | LOS ANGELES | LYNWOOD | 2020-12-01 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 1.25 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 4 |  | HHS | ONTARIO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor bored over 1.25 inch steel service, scraping over the top of the steel service until it leaked.
Southern California Gas Company | N | LOS ANGELES | MALIBU | 2020-08-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ELI JR PUMPING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged a plastic service digging with a mini excavator. No one onsite on arrival.
Southern California Gas Company | N | LOS ANGELES | MALIBU | 2020-06-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MIKE MERU | NEWBURY PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor digging for footing for retaining wall struck 0.50 inchips service.
Southern California Gas Company | N | LOS ANGELES | MALIBU | 2020-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 48 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ISLAND PACIFIC | VISTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | employee stated they were digging hole with track hoe, for water line when gas line was hit. he stated that he jumped in the hole and stopped gas from blowing.
Southern California Gas Company | N | LOS ANGELES | MALIBU | 2020-10-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 48 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | MALIBU | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party was trenching for water service on private property and damaged gas svc
Southern California Gas Company | N | LOS ANGELES | MALIBU | 2020-03-30 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 49 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CELENTANO CONSTRICTION | THOUSAND OAKS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor cut into a 0.75inch steel service
Southern California Gas Company | N | LOS ANGELES | MALIBU | 2020-09-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 48 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SE PIPELINE | SANTA FE SPRINGS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Per SM52 order commentsï¿½Backhoe hit our service line while digging for sidewalk.ï¿½
Southern California Gas Company | N | LOS ANGELES | MALIBU | 2020-02-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 48 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PROPERTY DEVELOPERS GROUP | THOUSAND OAKS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor damaged 0.75inch steel service with chipping gun while excavating for drain
Southern California Gas Company | N | LOS ANGELES | MALIBU | 2020-11-19 | Third party excavation damage | A service line with an excess flow valve installed | Steel | Grader/Scraper | 0.75 | 48 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ALFONSO SAABEDRA | CANOGA PARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | During removal of tree stumps gas service was damaged they didint have a USA
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2020-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ASPLUNDH CONSTRUCTION | ANAHEIM | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | UNMARKED SVC HIT during utility work for the city.
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2020-11-05 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 42 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ASPLUNDH CONSTRUCTION | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor dug into our Gas main while excavating with a BackHo.ï¿½
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2020-06-24 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | STC NETCOM | FONTANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor setting up shoring screwed into plastic gas main and created a small leak
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2020-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | BEAGLE PLUMBING | HERMOSA BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | svc hit no usa....contractor called for USA after the fact
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2020-10-06 | Third party excavation damage | Main | Polyethylene Pipe | Grader/Scraper | 2 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  | 50 |  | MAYA CONSTRUCTION | LAWNDALE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor uncovered old steal gas line and thought it was live did not realize active gas line was plastic... hit plastic gas line
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2020-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ADEEDO | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | plumber hit svc while digging for sewer no usa
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2020-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | FLORES MASONRY | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2020-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | TURBO PLUMBING AND ROOTER | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | damaged natural gas lineï¿½ while excavating for plumbing
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2020-01-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | DOUG GALLOWAY PLUMBING | LAWNDALE | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | WAS NOT ABLE TO FIND USA NO USA
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2020-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | PACIFIC COAST CONSTRUCTION | LAWNDALE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | the company locator stated he went to this address at the time to locate this service but the meter was inaccessible due to large dog on property. COMMENTS ARE inchUsed G on curb and measurements to locate 1 0.5 inch plastic service for 1826 11thst and used measurements, patches and old marks to locate 1 2 inch steel main infront address.Marked with yellow paint inchï¿½ THE SERVICE WENT AT A SHARP ANGLE AT THE CURB SERVICE WAS HIT 2 TO 3 OFF MARK.
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2020-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CASNER CONSTRUCTION | REDONDO BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | hit svc no usa
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2020-10-12 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 2 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 2 |  | GOLDEN STATE PLUMBING AND HEATING | GARDENA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaging party was using a battery operated saw and cut into the Gas Company 2 inch plastic main.
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2020-02-06 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Augur | 0.75 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | WALSH CONSTRUCTION | PALOS VERDES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor hit svc while installing support columns for future remodel
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2020-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JUSTIN | REDONDO BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit svc with shovel
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2020-01-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | PENA GRADING AND DEMO | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | USA WAS NOT CALLEDï¿½
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2020-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | PEARCE UTILITIES | TORRANCE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | cts svc hit with shovel svc correctly marked
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2020-12-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | PRECISION CONTRACTING | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor demoing building.ï¿½
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2020-09-09 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | LONG BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | main was exposed in 2 locations 1 on each side of the damage.ï¿½ the contractor hit the gas line with a backhoe
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2020-10-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | C A RASMSSP INC | VALENCIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA requested
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2020-02-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CLEAR ALL ROOTER | TORRANCE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor thought pa svc was a root and broke it
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2020-08-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | A I R SUB CONTRACTOR | NEWPORT BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | hit svc
Southern California Gas Company | N | LOS ANGELES | MARINA DEL REY | 2020-04-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TECHNICO TV | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor hit 0.50 inch IPS service with Backhoe
Southern California Gas Company | N | LOS ANGELES | MAYWOOD | 2020-07-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 28 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | PRO PROPERTIES | MAYWOOD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer did not notify USA
Southern California Gas Company | N | LOS ANGELES | MISSION HILLS | 2020-05-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NA | MISSION HILLS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner not aware of 811 underground service alert. Hit gas service while trenching new sewer line.ï¿½
Southern California Gas Company | N | LOS ANGELES | MONROVIA | 2020-03-08 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 3 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | JES ENGINEERING | MISSION VIEJO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was back filling with equipment without proper coverage
Southern California Gas Company | N | LOS ANGELES | MONTEBELLO | 2020-11-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 21 | 17 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | WA RASIC CONSTRUCTION | LONG BEACH | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Foremen dug into plastic service with a backhoe as they were trenching for water main install
Southern California Gas Company | N | LOS ANGELES | MONTEREY PARK | 2020-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | VCI | UPLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor excavating for communications who wereï¿½installing conduit in ground.
Southern California Gas Company | N | LOS ANGELES | MONTEREY PARK | 2020-03-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DSRM CABLE CONSTRUCTION | POMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit service while pot holing
Southern California Gas Company | N | LOS ANGELES | MONTEREY PARK | 2020-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | LA HYDROJET | SUN VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas service by digging directly over marked utilityï¿½
Southern California Gas Company | N | LOS ANGELES | MONTEREY PARK | 2020-04-24 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | VCI CONSTRUCTION | UPLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor did not pothole and damaged service with backhoe.
Southern California Gas Company | N | LOS ANGELES | MONTEREY PARK | 2020-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ADC CONSTRUCTION | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Digging with backhoe to install water line when 2 inch Stub was hit.
Southern California Gas Company | N | LOS ANGELES | MONTEREY PARK | 2020-05-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 0.75 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | AB CONSTRUCTION | SANTA ANA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Stub that was damaged was unmarked due to no records in service history.
Southern California Gas Company | N | LOS ANGELES | MONTEREY PARK | 2020-06-03 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 3 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | VI CONSTRUCTION | UPLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was working for Verizon to install electrical conduits.ï¿½
Southern California Gas Company | N | LOS ANGELES | MONTROSE | 2020-08-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MAX PICTURE PERFECT CONSTRUCTION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No Valid USA for property. Contractor was grading with skid steer and dug into gas service. Contractor hit line and folded pipe back and taped it shut.ï¿½ Depth of actual pipe could not be taken, since a lot of the sub grade was removed.
Southern California Gas Company | N | LOS ANGELES | NEWHALL | 2020-01-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | NEWHALL | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner digging up septic tank lid hit service No USA He was advised to always call before digging
Southern California Gas Company | N | LOS ANGELES | NEWHALL | 2020-03-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SUPERIOR CONSTRUCTION | SANTA CLARITA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor excavating to replace water line and flat work
Southern California Gas Company | N | LOS ANGELES | NEWHALL | 2020-03-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | BRIAN MCBRIDE | NEWHALL | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit service while trenching for a gas line to a new pool heater
Southern California Gas Company | N | LOS ANGELES | NORTH HILLS | 2020-02-12 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | NORTH HILLS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was installing fence in new construction when they struck 0.75inch steel gas branch It appears as if they drilled a whole over the service to what it was there was no USA called
Southern California Gas Company | N | LOS ANGELES | NORTH HILLS | 2020-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | NORTH HILLS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner digging with shovel hit plastic 0.5 inch service.ï¿½ Claims USA no provided.
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2020-04-14 | Third party excavation damage | Meter | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DYNA ELECTRIC | LOS ALAMITOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was excavating in the property and cut into the plastic service with a sawsall. They had a valid USA but failed to ask what the line was as it was in casing. Damaging party should be billed AG
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2020-03-04 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | FROST CHAPPOCU DEVELOPERS LLC | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor was excavating next to foundation was aware of gas service and marked out correctly there was no history of a stub serviceï¿½
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2020-10-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor states damage caused by vandalism riser was twisted. Police was contactedï¿½
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2020-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | COAST TO COAST CUSTOM DESIGNS | SAN BERNARDINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service line by striking it with shovel while digging to make repairs to clogged sewer line.ï¿½
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2020-09-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | SHERMAN OAKS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Owner confirmed sub was hired to remove foliage and was unaware they had struck service with a backhoe.ï¿½ ï¿½
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2020-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | LADWP | NORTH HOLLYWOOD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | DWP hit service line while performing work on water line. Crew had to replace entire service due to it being separated from transition fitting. Gas service had been accurately and visibly marked by locator.
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2020-09-04 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DWP | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | DWP leak was existing but service was hit by backhoe that caused bake to fall off.ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2020-12-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | NORTH HOLLYWOOD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Owner and his plumbers were replacing water line and hit service line with shovel.ï¿½
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2020-07-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | NORTH HOLLYWOOD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | gas service stub was struck by occupant. SCG crew had installed new service but old service was stubbed back to PL but not abandoned.ï¿½
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2020-05-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | NORTH HOLLYWOOD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer Homeowner was digging with a shovel trying to install sprinkler line when he struck our facility and cut the service line in half.ï¿½ ï¿½
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2020-11-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Arizona Pipeline damaged plastic service while digging the SMC to replace service.
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2020-10-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | GSI CONSTRUCTION | NORTH HOLLYWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party digging with backhoe for a driveway at market.
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2020-01-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | COLICH AND SONS | GARDENA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Customer service first on site ï¿½ Contractor hit service with back hoe ï¿½ Marks off actual service crossed lot
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2020-03-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NA | NORTH HOLLYWOOD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CSF first on site said contractor hit service with EFV while digging for tree
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2020-02-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | NORTH HOLLYWOOD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Plumber was trenching to install sewer when they accidentally hit the Branch service line because they thought it was a root ï¿½
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2020-02-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 15 |  | LADWP | NORTH HOLLYWOOD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service was damaged by DWP in the street with a backhoe DWP found an abandoned line and thought it was the gas line and damaged the gas line that was 18 under where they found the other pipe Responsible party should be billed
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2020-02-21 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 30 |  | LADWP | VAN NUYS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | When hooking up our locator located and mark an old line and not the correct 2 plastic this was a miss mark by our locator ï¿½
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2020-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | SMART IRA | VAN NUYS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Sub contractor hit plastic line with shovel while digging a trench
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2020-07-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | LADWP | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | LADWP was excavating to install pole when they found gas pipe was already leaking and stopped the job and contacted Gas Co.ï¿½
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2020-02-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | UNITED EXCAVATION GROUP INC | WEST HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working on property was unaware of the steel line in the property At one point there was two lots and the contractor only called to get one lot abandoned They failed to call for the other to be abandoned and thatï¿½s the one that was damaged They failed to notify USA prior to digging
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2020-01-08 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CALLEX ENGENIER CO | NEWHALL | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was grading empty lot when they hit 2 PE Stub
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2020-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | TORRENT RESOURCES | PHOENIX | AZ | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Service Was Not Striaght And Could Not Be Located
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2020-09-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CALIFORNIA PAVING AND GRADING | NORTH HOLLYWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 1 inch plastic service while grading with bobcat. Service was marked, but USA ticket was expired at time of digin.
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2020-11-30 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4017 |  | 9 |  | NA | PLACENTIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On 11/30/2020 SoCalGas was notified of a third party damage at 6814 Gentry Ave North Hollywood. Third party contractor damaged a 2 inch plastic natural gas main with a backhoe while digging to install a storm drain. The damage to the 2 inch plastic natural gas main caused a release of gas. SoCalGas personnel were sent to the scene and safely controlled the release of gas. There were no injuries reported. This was reported to the CPUC due to the release of gas and public attention.
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2020-04-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | NORTHRIDGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Open trench found with gas service cut by electric saw.ï¿½ ï¿½
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2020-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | NORTH HOLLYWOOD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner demo house and is building a new one, from the ground up. He did not call USA and hit the 0.5 inch plastic service with a shovel.
Southern California Gas Company | N | LOS ANGELES | NORTHRIDGE | 2020-07-09 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 36 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 1 |  | WA RASIC CONSTRUCTION 310 488 0132 | BELL GARDENS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | CONTRACTOR FAILED TO EXPOSED GAS LINES WITH HAND TOOLS, DIGGING FOR UNDERGROUND VAULTS, DIDN inchT POTHOLE GAS UTILITY AS REQUIRED.
Southern California Gas Company | N | LOS ANGELES | NORTHRIDGE | 2020-01-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LOCAL SERVICE PRO PLUMBING COM | TARZANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 0.5inch service when excavating trench for Sewer NO USA
Southern California Gas Company | N | LOS ANGELES | NORTHRIDGE | 2020-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | B CHAUDHRY | VAN NUYS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 0.5 PLA service when digging to install post, NO USA
Southern California Gas Company | N | LOS ANGELES | NORTHRIDGE | 2020-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | FAR WEST CONTRACTOR | PLACENTIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged 0.5 service with shovel , gas facility located correctly.
Southern California Gas Company | N | LOS ANGELES | NORTHRIDGE | 2020-10-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | NORTHRIDGE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per LCT Raynaldo Rodriguez homeowner Elmer Turcios was hand digging with a shovel to install a gasline to his pool
Southern California Gas Company | N | LOS ANGELES | NORTHRIDGE | 2020-11-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RAY PONTE | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3RD. party contractor for DWP was removing pavers and asphalt when they pulled up service
Southern California Gas Company | N | LOS ANGELES | NORTHRIDGE | 2020-09-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | RESEDA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | digging to install electrical conduitï¿½
Southern California Gas Company | N | LOS ANGELES | NORTHRIDGE | 2020-12-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | BDS CONSTRUCTION CUSTOM HOME BUILDERS | WEST HILLS | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | Contractor trenching for sewer install without valid USA ticket. This is the same contractor that had dug for Dist Gas Line installation. Became confident they were aware of where the lines were installed. Contractor damaged 1 inch PE Gas Service to one of the new homes.
Southern California Gas Company | N | LOS ANGELES | NORWALK | 2020-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 42 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | WICKETTS PLUMBING | PLACENTIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumbing company doing irrigation work hit line with backhoe.
Southern California Gas Company | N | LOS ANGELES | NORWALK | 2020-07-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HIGH VOLT ELECTRIC | CHATSWORTH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor installing conduit. hit our 1 inch plastic service causing a small leak.
Southern California Gas Company | N | LOS ANGELES | NORWALK | 2020-09-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | COVA CONSTRUCTION | ONTARIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 1 inch service while utilizing auger on uniloader
Southern California Gas Company | N | LOS ANGELES | NORWALK | 2020-05-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | NORWALK | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was removing tree stump and hit service line with shovel
Southern California Gas Company | N | LOS ANGELES | NORWALK | 2020-01-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 4 |  | ARIJET COMMUNICATIONS | POMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On 1 29 20 while hand digging with a shovel to expose the plastic gas service a contractor installing fiber optics damages the gas service ï¿½ The contractor had a valid USA ticket and the service was marked correctly ï¿½ SCG crew arrived on scene and made permanent repairs
Southern California Gas Company | N | LOS ANGELES | NORWALK | 2020-02-25 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | VASILJ INC | BALDWIN PARK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | On 2 25 20 Sal De lara found an unmarked pipe and drilled a small into it ï¿½ The pipe was a steel gas service that had been cutback ï¿½ The locate and mark employee was unaware of the cutback due to it not being in GIS and no service history records of it ï¿½ SCG crew arrived on scene and made permanent repairs
Southern California Gas Company | N | LOS ANGELES | PACIFIC PALISADES | 2020-06-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | EDUARDO HERNANDEZ | WINNETKA | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | Bobcat operator hit service riser and snapped the bypass off.
Southern California Gas Company | N | LOS ANGELES | PACIFIC PALISADES | 2020-02-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MIETZMER ENGINEERING | CASTAIC | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged a 1 plastic gas service with a backhoe while excavating
Southern California Gas Company | N | LOS ANGELES | PACIFIC PALISADES | 2020-08-29 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | PACIFIC PALISADES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CUSTOMER REMOVING TREE AND HIT ARE GAS LINE
Southern California Gas Company | N | LOS ANGELES | PACIFIC PALISADES | 2020-11-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MVC MANAGEMENT | HERMOSA BEACH | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service with shovel
Southern California Gas Company | N | LOS ANGELES | PACIFIC PALISADES | 2020-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DOWER CONSTRUCTION | THOUSAND OAKS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor knew it was there, clipped riser with bobcat
Southern California Gas Company | N | LOS ANGELES | PACIFIC PALISADES | 2020-02-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | UKNOWN NAME | PACOIMA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit and damaged a 0.5inch IPS service while digging in the property
Southern California Gas Company | N | LOS ANGELES | PACIFIC PALISADES | 2020-12-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | VOSHALL CONSTRUCTION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor damaged a stub
Southern California Gas Company | N | LOS ANGELES | PACIFIC PALISADES | 2020-11-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | TACONIC BUILDERS | CULVER CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor installing new electric line hit the 1 inch plastic service
Southern California Gas Company | N | LOS ANGELES | PACOIMA | 2020-11-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | EASY FLOW PLUMBING INC | RESEDA | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | contractor struck our service line while hand digging.ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | PACOIMA | 2020-12-31 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | 3RD PARTY | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Mr. Perez cut service line that was in casing with a reciprocating saw.ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | PACOIMA | 2020-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | PACOIMA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor thought they had exposed a water line and it needed to be removed. They cut it with a sawzall and found gas pipe inside copper pipe.
Southern California Gas Company | N | LOS ANGELES | PACOIMA | 2020-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | ARLETA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeless mansquatter living on vacant lot, cut into 0.5 inch service in an attempt to steal gas for his RV
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2020-03-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | KURT BOHMERS PLUMBING | CANYON COUNTRY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | USA WAS NOT CALLED
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2020-12-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 2 | 35 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  |  | NA | GALL BROTHERS | PALMDALE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Gall Brothers was using a trencher over 2 inch main and ripped main in half.
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2020-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DAN MOORE ELECTRIC | TORRANCE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavator damage to 1 plastic gas service line
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2020-12-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 2 |  | NA | LITTLEROCK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per LCT Jesse Jones Contractor Chris Starks hit SCG service line with shovel while digging to install gas yardline for pool.
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2020-12-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | PALMDALE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per Grado he spoke to owner who said there was a USA called Paul Palma and he said there is no valid ticket here.
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2020-08-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | PALMDALE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner building a wall. Struck gas line while excavating for footings. No USA. Customer advised to always call USA 48 hours prior to excavating.
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2020-07-07 | Third party excavation damage | Riser | Steel | Miscellaneous/Other | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DUMP DASH | SYLMAR | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No | No damage to SUOF. | No damage to SUOF. | 3rd party contractor was grading and hit MSA with bobcat tractor. MSA was broken, MTU was broken, and Riser was broken and blowing.ï¿½
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2020-04-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | PALMDALE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA HOMEOWNER DIGGING TO REPLACE WOODEN POST
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2020-05-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | VIASSAT SATELLITE | PALMDALE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor excavating to install satellite postï¿½
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2020-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SOLAR SHOPPERS | PALMDALE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per LCT Miller Solar Shoppers hit service while hand digging for generator.ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2020-09-02 | Third party excavation damage | Riser | Steel | Miscellaneous/Other | 0.75 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | AAA CONTRUCTION | BURBANK | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No | No damage to SUOF. | No damage to SUOF. | 3rd party contractor had damaged a 0.75 inch service when they were trying to chip out out stop cock that had concrete foundation poured around it. When contractor had broken line it was blowing in the hall way in the middleï¿½of the house.ï¿½
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2020-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | PALMDALE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was digging a post hole for a new fence when he hit 0.5 inch plastic service.ï¿½
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2020-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | PALMDALE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Homeowner digging trench with shovel and hit our line next to tree roots. Trench was being dug for electrical to be run to garage. Our line was properly marked.ï¿½
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2020-10-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | TIDEWELL | VENTURA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Miss marked line struck with backhoe.
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2020-08-04 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | NA | PALMDALE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per LCT J.Miller homeowner installing block wall. SCG believes this to be within the limits of the street. Per the home owner, the city of Palmdale advised them it was their property.
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2020-08-28 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  |  | NA | GENUINE CONCRETE | SANTA CLARITA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party Contractor struck our main with a concrete form stake that was hammered into the ground. Main was shallow where damage occurred.ï¿½
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2020-01-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PNL PLUMBING | SIMI VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor digging to install sewer lateral
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2020-04-29 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | P L PLUMBING INC | SIMI VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor excavating to install water lines No USA
Southern California Gas Company | N | LOS ANGELES | PALOS VERDES | 2020-02-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | DRAIN FOREST PLUMBING | SAN PEDRO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor working on drain hit cts svc no USA
Southern California Gas Company | N | LOS ANGELES | PALOS VERDES | 2020-11-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | BAY CITIES PAVING CO | LOMITA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | No Ticket Number Was Provide, Markings Seen On Ground, Contractor Failed To Use Caution While Digging
Southern California Gas Company | N | LOS ANGELES | PALOS VERDES | 2020-08-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | BENNET LANDSCAPE | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | svc hit while hand digging
Southern California Gas Company | N | LOS ANGELES | PALOS VERDES | 2020-08-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | W A RASIC | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | hit exposed svc with backhoe
Southern California Gas Company | N | LOS ANGELES | PALOS VERDES | 2020-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | K P S PLUMBING CO INC | TORRANCE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor doing sewer work hit our line while excavating. Our marks were off.ï¿½
Southern California Gas Company | N | LOS ANGELES | PALOS VERDES | 2020-12-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JSC MASONRY | SAN PEDRO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor accidently hit our gas line while installing a rain gutter.ï¿½
Southern California Gas Company | N | LOS ANGELES | PALOS VERDES | 2020-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 4 |  | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | suspect gas line was pulled during water main project with in the last 2 years
Southern California Gas Company | N | LOS ANGELES | PALOS VERDES | 2020-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 43 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | LOGRANDE BUILDERS | SAN PEDRO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor struck 0.50 inch plastic service while installing concrete forms for new driveway.
Southern California Gas Company | N | LOS ANGELES | PALOS VERDES | 2020-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | PALOS VERDES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | none
Southern California Gas Company | N | LOS ANGELES | PALOS VERDES | 2020-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | VALENZUELA NAVARRO VICTOR | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | svc hit with shovel
Southern California Gas Company | N | LOS ANGELES | PALOS VERDES | 2020-04-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | PIERCE CONSTRUCTION | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor hit svc while hand digging
Southern California Gas Company | N | LOS ANGELES | PANORAMA CITY | 2020-10-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | AA GONZALEZ | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging to install drainage at new tract homes, contractor hit 0.5 inch service in 3 places triggering the EFV
Southern California Gas Company | N | LOS ANGELES | PANORAMA CITY | 2020-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | CITY OF LA STREET LIGHTING DEPARTMENT | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | LA City street lighting dept. digging to install conduits for new street lights hit marked 0.5 inch PE service w a sharpshooter. Fire dept on scene first, evacuated 5 homes w approx. 15 evacuees. Valid USA Sent pictures and otherï¿½infoï¿½as requested to Salvador Rodriguez Senior Claims Advisor by email on 10 20 2020 at 1258pm.
Southern California Gas Company | N | LOS ANGELES | PANORAMA CITY | 2020-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | NA | PANORAMA CITY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | HIT LINE WITH AXE WHILE TRYING TO PULL OUT TREE
Southern California Gas Company | N | LOS ANGELES | PARAMOUNT | 2020-12-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | TECHNICO CONSTRUCTION | GARDENA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor did not fully expose service prior to removal of roots around the service.ï¿½ Contractor struck top of 1 inch plastic with sharpshooter shovel thought he was striking the roots. ï¿½
Southern California Gas Company | N | LOS ANGELES | PARAMOUNT | 2020-03-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | PARAMOUNT | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA ON FILE CUSTOMER PLANTING A TREE ï¿½ On 3 28 20 while hand digging with a shovel to plant a tree homeowner Sun Charlie Chong damaged a one half inch plastic gas service ï¿½ Mr Chong did not notify USA of his plans to excavate ï¿½ SCG crew arrived on scene and made permanent repairs ï¿½
Southern California Gas Company | N | LOS ANGELES | PARAMOUNT | 2020-07-06 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | WA RASIT CONSTRUCTION | NA |  | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On 7062020 while excavating with a backhoe to install gas and electric for SCG MHP project, W. A. Rasik Mike Droge damaged a one inch plastic gas service.ï¿½ W. A. Rasik had a valid USA ticket and had marked the location of the gas service accurately.ï¿½ SCG crew arrived on site and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2020-01-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ACE S ROOTER | AZUSA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber was trying to repair sewer line and cut into steel line in their excavtion
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2020-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CHABAO OF PASEDENA | PASADENA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Per Mr. Hanoka. His workercontractor hit service while hand digging with shovel and caused leak at service fittingelbow. Mr. Hanoka did not want to provide contractors information and aid he would be responsible for damages caused by contractor.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2020-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | LANDSCAPING CREW | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | plastic service was hit with shovel. NoUSA
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2020-08-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JOSE LUIS LOPEZ | PASADENA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Lanscaper hit plastice service with a shovel while digging to install irrigation line.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2020-12-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ELIAS BARHOUM | PASADENA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 0.5inch cts service at 24inch while excavating for sewer lateral
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2020-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | PASADENA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | homeowner and contractor trenching with shovel to install sewer line
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2020-12-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CEASAR GARCIA | MONROVIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Cesar Garcia was digging to install a sewer tank manhole discharge
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2020-07-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | PASADENA | CA | N | Y | Yes | Excavation occurred on private property by a non-contractor. | Yes | Yes | No | Yes | Yes | ho hit line with shovel after removing flags form trenchline. All other flags in place. D Galdi 7102020
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2020-07-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | AMANDO ORTIZ | PASADENA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit service with hand tool while open trenching. Customer stated USA was called and gave USA number, USA ticket not verified. D Galdi 7102020
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2020-02-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 27 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | BYCOR CONTRACTORS | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was trenching for conduit installation and hit the service on private property The service was no potholed prior to trenching On arrival there were no flags over the entire service because the whole property was recently graded There was a flag and markings at the property line only about 10 feet away from where the service was damaged The contractor never called to have new flags installed after grading happened Contractor stated that the service was going to be abandoned soon and there was clear delineation in the street
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2020-03-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | KENT ELECTRIC | GLENDALE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CREW WAS LAYING DOWN ELECTRICAL CONDUITS WHEN THEY STRUCK COMPANY SERVICE LINE WITH MINI EXCAVATOR
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2020-08-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ROOTER PATROL PLUMBING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber hit 0.5 inch plastic service with shovel while digging for sewer.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2020-08-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | PASADENA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | none
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2020-04-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | FS CONTRACTORS INC | SYLMAR | CA | N | Y | Yes | Yes | No | No | No | Yes | Yes | Locator did not locate ticket due to rain. Putï¿½ in project to return the following week and never returned to this exact job due to contractor calling in multiple tickets due on same day.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2020-01-30 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 7 |  | CITY OF PASADENA WATER DEPT | PASADENA | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Water company excavating to repair water leak hit plastic gas main with back hoe Dug with heavy equipment before we had an opportunity to mark the lines
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2020-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | VEGA ELECTRIC | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor his service using a sawzall to cut away pipe.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2020-08-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | LANDSCAPE DEVELOPMENT | LA CANADA FLINTRIDGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit plastic service while trenching to install gas line for pool.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2020-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ALLIANCE UNITED PLUMBERS | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Trench dug to install new water and sewer lines. Plumber was welding new water line and damaged plastic service with the welding torch
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2020-07-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | ALTADENA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA REQUESTED, CUSTOMER HIRED CONTRACTOR WAS PLANTING TREES
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2020-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BEDROCK COMPANY | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party contractor was demoing concrete when they hit service with a backhoe. Unsure if there was aï¿½USA or not. Claims they think there was one called in but not sure. FYIï¿½ï¿½USA ticket number provided by contractor did not come up in system.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2020-08-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | WIRING CONNECTION | GARDENA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | 3RD PARTY DUG OUT OF DELINEATED AREA AND HIT 0.5 IPS SERVICE WITH CLAY SPADE.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2020-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ROGERS ELECTRIC | IRVINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service was previously installed and marked but new contractor doing digging did not request a new USA.ï¿½ They hit our line with an excavator.ï¿½
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2020-02-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | AWARD CONTRUCTION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CONTRACTOR WAS INSTALLING NEW WATER LINES TO A NEW FIRE SYSTEM TO A NEW HOUSE WHEN HE SNAGGED OUR 1 PLASTIC SERVICE INSIDE A 2 PLASTIC CASING ï¿½ THE PIPE WAS DAMAGED BUT WAS NOT LEAKING ï¿½ CREW ALTERED THE SERVICE FOR PERMANENT REPAIRS ï¿½ THE CREW CREATED AN ALTER SERVICE ORDER TO SHOW THE ALTERATION ON THE SERVICE AND TO SHOW TIME ON THE JOB ï¿½ THE CONTRACTOR COULD NOT PROVIDE A USA TICKET NUMBER
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2020-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ARIEL S IMPROVEMENT ELECTRIC AND PLUMBING | TUJUNGA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged Plastic service while excavating to install houselineï¿½
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2020-12-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | PASADENA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | owner digging trench to install water line hit our service at the plastic coupling.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2020-03-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SK CONSTRUCTION | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Worker on site stated that damaged was caused by hand digging trench for service alteration
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2020-08-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HENRY CHEN | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CONTRACTOR WAS DIGGING FOR NEW FOOTING WHEN THEY HIT THE PLASTIC SERVICE.ï¿½ MARKS SHOWED THE SERVICE GOING STRAIGHT BUT ACTUALLY WENT AT AN ANGLE FROM THE RISER.ï¿½ CONTRACTOR CLAIMS TO HAVE USA BUT WE COULD NOT FIND AN ACTIVE TICKET
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2020-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ECHO INDUSTRIES AND DEVELOPMENTS | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit service with jackhammer trying to remove concrete footing.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2020-01-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ROBERT BERKICH CONSTRUCTION | MONROVIA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | PASADENDA WATER CO HIT GAS LINE WHILE WORKING ON WATER LINE
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2020-03-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | NA |  | N | Y | Yes | No | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | CONTRACTOR WAS DEMOING THE BUILDING WHEN HE HIT THE PLASTIC GAS SERVICE ï¿½ HE DID NOT VERIFY THAT THE GAS SERVICE WAS ABANDONED ï¿½ THERE WERE GAS FLAGS OVER THE SERVICE ï¿½ IT WAS EXPLAINED TO HIM THE IMPORTANCE OF VERIFYING THAT ALL UTILITIES ARE ABANDONED BEFORE DEMOING ANY BUILDING AND THAT THE FLAGS WERE A GOOD INDICATION THAT THE SERVICE WAS STILL LIVE
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2020-01-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DONG QING WANG | MONROVIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | builder damage riser with some sort of hand tool The builder was gone on arrivalï¿½
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2020-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JEFF HOGAN BUFFA | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor was digging trench for new gas houseline. Hit line with shovel
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2020-09-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MARCO CARBAJAL | PASADENA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor states he hit 0.5 cts service while digging with shovel
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2020-12-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | PASADENA WATER DEPT | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | City of Pasadena Water damaged plasticï¿½0.5 inch ips service while excavating. our marks were more that 2 feet off
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2020-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | BRIGHT CONCEPTS POOL SPA CONSTRUCTION | SAN DIMAS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit gas line trenching for pool line. No usa
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2020-12-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 25 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | BRANDON LANDSCAPE | MONROVIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was working on the sewer and hit the gas service with his backhoe.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2020-03-24 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3023 |  | 0 |  | WILLIAMS PIPELINE CONTRACTORS | SOMIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On March 24th, a 2inch plastic gas main was damaged by a 3rd Party Contractor using a backhoe, trenching to install water main. SoCalGas crews responded and controlled the gas at 12:45. Repairs were made same day by replacing a short section of plastic main. There were no injuries or other damages resulting from the incident. After further investigation, the contractor, Victor Hernandez, stated he found a steel pipe and assumed that was the gas line, even though it was clearly marked as 2inch plastic. The 3rd Party Contractor failed to expose the 2inch plastic gas line as marked. This was reported to the CPUC due to Public Awareness, after receiving 10 odor complaint calls in the same vicinity.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2020-05-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MARK FIELDS | ARCADIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber damaged plastic service while trenching to repair sewer pipe. No USA ticketï¿½
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2020-02-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | SHAY ABOAB | BEVERLY HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor struck service with a shovel while hand exposing USA expired and not renewed
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2020-09-23 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 15 |  | E R CONSTRUCTION | BALDWIN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | contractor digging along 2 pla main. had exposed about 15ï¿½ and finally punctured because backhoe bucket was too close while excavating
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2020-01-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MAJESTIC FIRE PROTECTION | VAN NUYS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working on Fire Prevention sprinkler system cut service in half while digging with a mini excavator No USA was called
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2020-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 10 |  | CLEAN OUT PLUMBING AND ROUTER | LA HABRA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | damage occurred while digging to find leak on houseline. Damaged 1inch plastic service with shovel
Southern California Gas Company | N | LOS ANGELES | PICO RIVERA | 2020-07-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CELL TECH | ANAHEIM | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor digging with backhoe to install a vehicle recharge station when unrecorded no service history service stub was hit. Service history has now been updated with stub info.
Southern California Gas Company | N | LOS ANGELES | PICO RIVERA | 2020-01-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SEQUEL CONTRACTORS INC | SANTA FE SPRINGS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Unmapped stl cutback hit by contractor grading driveway approach for city street improvement
Southern California Gas Company | N | LOS ANGELES | PICO RIVERA | 2020-02-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | D M PLUMBING | BASSETT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor cut gas pipe with saw zall while trying to cut tree roots for water service installation
Southern California Gas Company | N | LOS ANGELES | PLAYA DEL REY | 2020-12-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 29 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | PLAYA DEL REY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was digging with shovel to remove tree roots andï¿½contractor hit 0.5 inch cts service.
Southern California Gas Company | N | LOS ANGELES | PLAYA VISTA | 2020-06-26 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | 2020 PLUMBING HEATING INC | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Sub contractor was digging for a water line and struck our 2 inch PL gas line.ï¿½ No USA was called.ï¿½ all cuts in Dirt part of a track home development.
Southern California Gas Company | N | LOS ANGELES | POMONA | 2020-11-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ILB | JURUPA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor hit 0.5 inch plastic service with shovel while attempting to expose service.
Southern California Gas Company | N | LOS ANGELES | POMONA | 2020-11-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | MERCADO LANDSCAPING | HESPERIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | HOA contractor hit 0.5 inch Plastic service
Southern California Gas Company | N | LOS ANGELES | POMONA | 2020-06-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | POMONA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner hit line with shovel while digging for fence post, and usa was not called for location
Southern California Gas Company | N | LOS ANGELES | POMONA | 2020-02-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CITY OF POMONA | POMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | WATER COMPANY PERFORMING MAINTENANCE
Southern California Gas Company | N | LOS ANGELES | POMONA | 2020-08-11 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | MORA EQUIPMENT | PICO RIVERA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | AM ORTEGA WAS DOING A DIMP MAIN REPLACEMENT JOB WHEN THEY HIT THE 2 inch PLASTIC MAIN.ï¿½ THE MAIN WAS MARKED OUT BY AM ORTEGA AND THE MARKS WERE CORRECT.ï¿½ MARKS WERE VISIBLE WHEN THEY HIT THE MAIN.ï¿½ THEY WERE TOLD THAT THEY SHOULD BE HAND DIGGING OUR FACILITIES ESPECIALLY WHEN IT IS A PLASTIC MAIN.
Southern California Gas Company | N | LOS ANGELES | POMONA | 2020-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | J A J DESIGN | WALNUT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party constructor hit 0.5 inch plastic service while hand digging to install sewer.ï¿½ NO USA was called in.ï¿½
Southern California Gas Company | N | LOS ANGELES | POMONA | 2020-04-04 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | WFC CONSTRUCTION INC | LA VERNE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | builder was working to remove steel, but ended digging up abandon service
Southern California Gas Company | N | LOS ANGELES | POMONA | 2020-08-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | POMONA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner doing yardwork hit line with shovel.
Southern California Gas Company | N | LOS ANGELES | POMONA | 2020-10-30 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 1.25 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | FORCE ENVIRONMENTAL | PALA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No digging involved. Contractor wasï¿½cleaning upï¿½debris when they noticed riser was leaking. Home was burned down.
Southern California Gas Company | N | LOS ANGELES | POMONA | 2020-04-16 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | FFG CONSTRUCTION | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | the contractor was digging over plastic main and did not expose the facility because he thought the service and main were same depth
Southern California Gas Company | N | LOS ANGELES | PORTER RANCH | 2020-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DONALD TATE ELECTRIC | LANCASTER | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | New 0.5 plastic serviceï¿½damaged by 3rd pty, digging for power conduits, No USA
Southern California Gas Company | N | LOS ANGELES | PORTER RANCH | 2020-11-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SITE WORKS INC | SIMI VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was grading damaged exposed stub with a shovel. NO USA
Southern California Gas Company | N | LOS ANGELES | PORTER RANCH | 2020-12-15 | Third party excavation damage | Riser | Steel | Backhoe/Trackhoe | 0.75 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TOLL BROTHERS | PORTER RANCH | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | Riser was hit by Mini X
Southern California Gas Company | N | LOS ANGELES | PORTER RANCH | 2020-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | PORTER RANCH | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging with hand tools to install sewer pipe
Southern California Gas Company | N | LOS ANGELES | PORTER RANCH | 2020-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HOTLINE PLUMBING | BURBANK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor struck gas line while trenching for irrigation.
Southern California Gas Company | N | LOS ANGELES | PORTER RANCH | 2020-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | NORTHRIDGE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was digging for sewer when he struck gas service. no usa was called
Southern California Gas Company | N | LOS ANGELES | PORTER RANCH | 2020-08-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TOLL BROTHERS | ORANGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Developer Toll Brothers digging with excavator hit 0.5 inch plastic service.
Southern California Gas Company | N | LOS ANGELES | PORTER RANCH | 2020-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | REMINGTON GRADING INC | CAMARILLO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5inch Service hit by grader blade while creating a flat surface grading for driveway
Southern California Gas Company | N | LOS ANGELES | PORTER RANCH | 2020-07-21 | Third party excavation damage | Riser | Polyethylene Pipe | Not Available | 0.5 | 35 | 30 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TOLL BROTHERS | NORTHRIDGE | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No | No damage to SUOF. | No damage to SUOF. | Called in by contractor TOLL BROTHERS CONTRACTOR , damaged riser no leak at location
Southern California Gas Company | N | LOS ANGELES | PORTER RANCH | 2020-02-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LANDSCAPE DEVELOPMENT INC | VALENCIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Andres Campos stated hit plastic service while digging with mini excavator installing stone grade brick wall
Southern California Gas Company | N | LOS ANGELES | PORTER RANCH | 2020-06-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MJD CONCRETE WORKS | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | upon arrival everyone was gone. It seemed like they were doing framing for laying concrete.ï¿½
Southern California Gas Company | N | LOS ANGELES | RANCHO PALOS VERDES | 2020-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | COMM COMPANY | TORRANCE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer installing a electricityï¿½ï¿½line and damaged our gas service. 811 was not notified.
Southern California Gas Company | N | LOS ANGELES | RANCHO PALOS VERDES | 2020-01-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | NA | RANCHO PALOS VERDES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Property developer was digging in to install a irrigation line No USA
Southern California Gas Company | N | LOS ANGELES | RANCHO PALOS VERDES | 2020-05-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JUAN MORENO | GARDENA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Gardener was digging to install a valve for a sprinkler system when he damaged 0.50 inch plastic service.ï¿½ USA was not notified.
Southern California Gas Company | N | LOS ANGELES | RANCHO PALOS VERDES | 2020-10-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | P D DEVELOPMENT | LOMITA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Property owner contractor was breaking concrete and dropped a bolder on top of the plastic main, damaging it.
Southern California Gas Company | N | LOS ANGELES | RANCHO PALOS VERDES | 2020-04-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | MIKE DIAMOND PLUMBING | GARDENA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | svc hit while installing drain line no usa
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2020-12-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | REDONDO BEACH | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner could not tell pipe from roots
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2020-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DOWNEY PLUMBING | DOWNEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor digging with a shovel to expose water for repair and hit gas line.
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2020-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | MIKE PRUCH SONS CO | BALDWIN PARK | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | contractor dug before USa was valid
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2020-08-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | HOT LINE CONSTRUCTION | BRENTWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | damaged plastic service
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2020-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | PAUL SCHIPPA | REDONDO BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer was installing new water line. Our plastic service was exposed and when they went to fuse a piece together, accidentally hit our line causing a small melt in the plastic service line
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2020-09-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 3 |  | SOCAL EDISON | TORRANCE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | SCE hit 0.5 inch CTS SVC with an auger while doing emergency pole repair due to a car accident. Called in Ticket at 1553 9192020
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2020-06-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | REDONDO BEACH | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | customer cut svc while removing tree
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2020-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CASTRO 21 CONSTRUCTION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit service while hand digging
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2020-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RE PIPE PRO | BURBANK | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | contractor struck service while digging for sewer replacement
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2020-05-11 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | ARB | NA |  | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | arb hit svc with shovel in process of replacing main and svc
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2020-06-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HP COMMUNICATIONS INCORPORATED | GARDENA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor hit long side 0.50 inch plastic service while boring.ï¿½ Contractor failed to expose location of bore rod crossing over gas service.
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2020-04-17 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | ARB | NA |  | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor cut into svc
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2020-01-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DOTY BROTHERS | NORWALK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | USA WAS CALLED FOR THIS BUT NO TICKET INFORMATION WAS AVAILABLE
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2020-04-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | REDONDO BEACH | CA | N | Y | Yes | Excavation occurred on private property by a non-contractor. | Yes | Yes | No | Yes | Yes | Repairman was digging to expose pipes to be repaired, and couldnt tell the difference between the roots and the gas pipe. A
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2020-02-27 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 6 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 25000 |  |  | NA | DOTY BROS | NORWALK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavator new gas main was there but thought it ran parallel to trench
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2020-11-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | REDONDO BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd parity contractor dropped a bolder on a Gas Mainï¿½he exposed.ï¿½
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2020-03-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | REDONDO BEACH | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | damaged gas line due to no USA ï¿½ customer called planner for hit line not call center
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2020-08-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | RIGGO CONSTRUCTION | CHINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | cut into encased service with sawzall
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2020-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PACIFIC ELECTRIC | PARAMOUNT | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | contractor hit 1 inchpe svc while installing electrical conduit. Svc not marked locator saw park and did not think a svc ran through park.
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2020-02-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RJO PLUMBING SERVICES | SANTA ANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA
Southern California Gas Company | N | LOS ANGELES | RESEDA | 2020-02-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working for homeowner sawed through copper casing into plastic CTS branch service
Southern California Gas Company | N | LOS ANGELES | RESEDA | 2020-07-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | GOODMAN ELECTRICAL INC | NA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 0.5 pe service when digging trench for conduit , NO USA
Southern California Gas Company | N | LOS ANGELES | RESEDA | 2020-07-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | RESEDA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 0.5 cts service when digging trench for sewer, NO USA
Southern California Gas Company | N | LOS ANGELES | RESEDA | 2020-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 8 |  | WALLER MECHANICAL AND ELECTRICAL INCORPORATED | CHATSWORTH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damaged 0.5 plastic service when hand digging trench to install irrigation pipe
Southern California Gas Company | N | LOS ANGELES | RESEDA | 2020-07-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 35 | 30 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | WPIT | MONROVIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged new plastic service when trenching and grading no leak at this location, but gas facility damaged plastic
Southern California Gas Company | N | LOS ANGELES | RESEDA | 2020-07-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | WA RASIC | BELL GARDENS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Damaged gas company facility 0.5 service located correctly, didnt expose by hand.
Southern California Gas Company | N | LOS ANGELES | ROLLING HILLS | 2020-11-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | W A RASIC CONSTRUCTION | LONG BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Gas line was struck within delineation area with BackHoï¿½while exposing. Service Line marked correctly However found flags buriedï¿½in a mound of dirt near excavation.ï¿½
Southern California Gas Company | N | LOS ANGELES | ROSEMEAD | 2020-04-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | DOMINGUEZ GENERAL ENGINEERING | POMONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor hit mismarked service. Locator was unable to locate service with locator and use company measurements and had contractor pothole area. Marks were off by 10 feet.
Southern California Gas Company | N | LOS ANGELES | ROSEMEAD | 2020-04-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | DOMINGUEZ GENERAL ENGINEERING | POMONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor hit mismarked service. Locator was unable to locate service with locator. Locator used company measurements but were incorrect.
Southern California Gas Company | N | LOS ANGELES | ROSEMEAD | 2020-03-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DOMINGUEZ GENERAL ENGINEERING INC | POMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was potholing with shovel when hit gas service
Southern California Gas Company | N | LOS ANGELES | ROSEMEAD | 2020-05-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 4 |  | RJ NG CONSTRUCTION | APPLE VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA REQUESTED. CONTRACTOR DIGGING FOR TREE REMOVAL
Southern California Gas Company | N | LOS ANGELES | ROSEMEAD | 2020-11-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | CITY OR ROSEMEAD WATER | ROSEMEAD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Rosemead City worker damaged gas line with backhoe while repairing leaking water line. He was instructed to always hand excavate over gas lines.
Southern California Gas Company | N | LOS ANGELES | ROSEMEAD | 2020-01-07 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  | 47 |  | DOMINGUEZ GENERAL ENGINEERING | POMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor cut through 2 plastic main with a sharp shooter shovel while trying to expose find our main
Southern California Gas Company | N | LOS ANGELES | ROSEMEAD | 2020-01-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SAN GABRIEL WATER DEPARTMENT | BALDWIN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor found old steel service but did not realize the service was marked plastic
Southern California Gas Company | N | LOS ANGELES | ROWLAND HEIGHTS | 2020-05-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | LEGACY COMMUNICATIONS | MONTCLAIR | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | third-party contractor was digging with a mini excavator and damaged a 1-inch plastic gas service causing a release of gas. A SoCalGas crew responded and controlled the gas. There were no injuries resulting from this incident. The SoCalGas crew squeezed the 1-inch plastic pipe and replaced 2ft of 1- inch plastic pipe, using 2 socket fusion couplings. Further investigation showed that there was a current USA DigAlert ticket and the service was correctly marked. The third-party contractor failed to expose the 1ï¿½ plastic service by hand digging, as required per DigAlert laws. This incident was reported to the CPUC when SoCalGas became aware of media coverage
Southern California Gas Company | N | LOS ANGELES | ROWLAND HEIGHTS | 2020-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 10 |  | COSTAL ELECTRIC GROUP | IRVINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | third party contractor hit 1 inch pla with backhoe while digging to install conduit
Southern California Gas Company | N | LOS ANGELES | ROWLAND HEIGHTS | 2020-10-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No Usa Requested, Contractor Trenching For A Wall
Southern California Gas Company | N | LOS ANGELES | SAN DIMAS | 2020-07-16 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 2 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CROSSTOWN ELECTRICAL AND DATA | IRWINDALE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | CONTRACTOR WAS BORING IN NEW CONDUIT FOR TELEPHONE WHEN THEY HIT THE 2 inch PLASTIC SERVICE.ï¿½ SERVICE WAS HARD TO LOCATE DUE TO IT BEING HALF STEEL AND HALF PLASTIC.ï¿½ MEASUREMENTS IN SERVICE HISTORY WERE INCORRECT.ï¿½ MARKS WERE ABOUT 12 OFF ACTUAL LOCATION OF THE PLASTIC SERVICE.ï¿½ CONTRACTOR POTHOLED MARKS THAT WERE PUT DOWN BY THE ETD BUT COULD NOT FIND IT EVEN AFTER GOING 5 DEEP AND EXPANDING TO 3 AROUND.ï¿½ CONTRACTOR FAILED TO NOTIFY SO CAL GAS AFTER NOT BEING ABLE TO FIND IT WHILE POTHOLING.ï¿½ AFTER NOT BEING ABLE TO FIND IT DURING THEIR POTHOLING ACTIVITIES THEY PROCEEDED TO BORE AND HIT OUR PLASTIC SERVICE.
Southern California Gas Company | N | LOS ANGELES | SAN DIMAS | 2020-09-16 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | FENCE WORKS INC | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor putting in fencing for developer. No USA called.ï¿½
Southern California Gas Company | N | LOS ANGELES | SAN DIMAS | 2020-02-10 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 4 |  | BIG BEN CONSTRUCTION | IRVINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | CONTRACTOR WAS REPLACING THE WATER MAIN WHEN THEY DAMAGED THE 2 PLASTIC MAIN ï¿½ THE MARKS WERE VISIBLE BUT WAS FADED WITH DIRT DUE TO THE WORK THEY WERE PERFORMING ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | SAN DIMAS | 2020-04-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | BIG BEN CONSTRUCTION | IRVINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CONTRACTOR WAS REPLACING THE WATER MAINS AND SERVICES WHEN THEY HIT THE PLASTIC SERVICE.ï¿½ SERVICE WAS MARKED BUT WAS MORE THAN 2 AWAY.ï¿½ THE SERVICE SIGNAL WERE ON THE MARKS WHICH WERE NOT OVER THE ACTUAL SERVICE.ï¿½ THE CREW GOT THE SAME SIGNAL OVER THE MARKS WHEN THEY CAME OUT TO REPAIR THE SERVICE.ï¿½ THERE IS AN EXISTING USA FOR THE JOB.ï¿½ NOGGIN WILL NOT LET ME COMPLETE THE ORDER WITH IT INPUTTED.ï¿½ THE EXPIRATION DATE IS 4 9 2020.ï¿½ THE TICKET WAS CURRENT AT THE TIME OF THE DAMAGE, STRUCK WITHIN DELINEATED AREA, SERVICE MARKS WERE VISIBLE BUT MARKED 4 AWAY.
Southern California Gas Company | N | LOS ANGELES | SAN FERNANDO | 2020-03-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | SAN FERNANDO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | HO excavating in front yard removing tree roots advised about 811 prior to digging
Southern California Gas Company | N | LOS ANGELES | SAN FERNANDO | 2020-09-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | SAN FERNANDO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | damage service
Southern California Gas Company | N | LOS ANGELES | SAN FERNANDO | 2020-06-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | FABIAN MENDEZ | SAN FERNANDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 0.50 inch CTS service while digging to replace apart of customers water service. Damage was tied back upon arrival, no USA.
Southern California Gas Company | N | LOS ANGELES | SAN FERNANDO | 2020-02-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | GRB | BALDWIN PARK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Locator traced signal to a location later found to be telecom conduit 2nd locator received ticket update and saw marks present but failed to verify
Southern California Gas Company | N | LOS ANGELES | SAN GABRIEL | 2020-08-10 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | VCI CONSTRUCTION | UPLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor struck Punch tee cap while excavating to install conduitï¿½for communication line installationï¿½
Southern California Gas Company | N | LOS ANGELES | SAN GABRIEL | 2020-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 3 |  | VCI CONSTRUCTION | UPLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor caused damage to Gas service whileï¿½ doingï¿½Directional bore to install conduitï¿½
Southern California Gas Company | N | LOS ANGELES | SAN GABRIEL | 2020-10-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | VCI CONSTRUCTION LLC | UPLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor used mini excavator to dig with out verifying location of plastic service that was marked.
Southern California Gas Company | N | LOS ANGELES | SAN GABRIEL | 2020-08-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | SCOTT CLARK | SAN GABRIEL | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor failed to contact usa , and tried to provide a fake usa number
Southern California Gas Company | N | LOS ANGELES | SAN GABRIEL | 2020-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HIGH SPEED ROOTER PLUMBING | MONTEREY PARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | High Speed Rooter employee cut through 0.5 inch cts gas service with clay spadeï¿½
Southern California Gas Company | N | LOS ANGELES | SAN GABRIEL | 2020-04-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SEQUEL CONTRACTORS INC | SANTA FE SPRINGS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | CONTRACTOR DID NOT POTHOLE BEFORE EXCAVATING
Southern California Gas Company | N | LOS ANGELES | SAN MARINO | 2020-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JERRY CHEN | SAN MARINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | customer seemed to be digging in a trenched out area.ï¿½ Our plastic 0.5 inch pipe was already exposed and they hit it with their shovel.
Southern California Gas Company | N | LOS ANGELES | SAN MARINO | 2020-11-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ARTISTIC TOUCH LANDSCAPE | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscaper damaged 0.5 plastic service while digging hole to plant tree
Southern California Gas Company | N | LOS ANGELES | SAN PEDRO | 2020-04-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 2 |  | NA | SAN PEDRO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Strong odor outside led to crew excavating leak in private business district. Upon centering the leak, the discovered that slurry had been poured directly over our service. That stress cause a crack in the plastic service, this was in the same trench as the ATT conduit trench. This work was done about two years ago per property management.
Southern California Gas Company | N | LOS ANGELES | SAN PEDRO | 2020-01-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | SAN PEDRO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner damaged gas line while digging fence post
Southern California Gas Company | N | LOS ANGELES | SAN PEDRO | 2020-01-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | LONG BEACH | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd parity contractor struct gas service while excavating ï¿½
Southern California Gas Company | N | LOS ANGELES | SAN PEDRO | 2020-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NA | SAN PEDRO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | hit svc with no usa
Southern California Gas Company | N | LOS ANGELES | SAN PEDRO | 2020-01-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 45 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TONY S PLUMBING | HARBOR CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor replacing waterline for business ï¿½
Southern California Gas Company | N | LOS ANGELES | SAN PEDRO | 2020-03-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | AGUIRRE MASONARY | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor installing a wall for the customer Did not call USA
Southern California Gas Company | N | LOS ANGELES | SAN PEDRO | 2020-04-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | SAN PEDRO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer dug a hole to plant a tree. while digging he struck the gas service.
Southern California Gas Company | N | LOS ANGELES | SAN PEDRO | 2020-11-30 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | MARK COMPANY | ORANGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor Grading On huge new construction site. Was potholing and struck our main. No USA.ï¿½
Southern California Gas Company | N | LOS ANGELES | SAN PEDRO | 2020-10-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 48 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | HOME OWNER | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Developer dropped a rock on or gas line he exposed causingï¿½damage.
Southern California Gas Company | N | LOS ANGELES | SAN PEDRO | 2020-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | JOHN ELMICH CONTRUCTION | SAN PEDRO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3 party contractor was excavating for a sewer line and dug into the gas service
Southern California Gas Company | N | LOS ANGELES | SANTA CLARITA | 2020-05-12 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | OAKRIDGE LANDSCAPE | SANTA CLARITA | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Oakridge Landscaping hit new 4 inch main with mini excavator while digging a trench for irrigation. USA was valid, but mutual agreement to meet and mark on the following day was not honored.
Southern California Gas Company | N | LOS ANGELES | SANTA CLARITA | 2020-08-14 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | AMPAM PARTS MECHANICAL | CARSON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumbing company damaged 4 inch PLA main while digging for irrigation
Southern California Gas Company | N | LOS ANGELES | SANTA CLARITA | 2020-01-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BILLS LANDSCAPING | LANCASTER | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscaping contractor struck service while trenching No USA Advised to always call for USA
Southern California Gas Company | N | LOS ANGELES | SANTA CLARITA | 2020-07-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | SANTA CLARITA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hit service line while trying to remove tree stump in yard.
Southern California Gas Company | N | LOS ANGELES | SANTA CLARITA | 2020-06-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ELEMENTS GROUND MANAGEMENT | VALENCIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor cut service accidentally while removing a section of water pipe with a saw. No USA.
Southern California Gas Company | N | LOS ANGELES | SANTA CLARITA | 2020-10-19 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | OAKRIDGE LANDSCAPING | VALENCIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Backhoe damaged 4inch PE gas main while trenching for irrigation. Line was marked out with yellow feathers.ï¿½
Southern California Gas Company | N | LOS ANGELES | SANTA CLARITA | 2020-10-07 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CAL WEST UNDERGROUND | NORCO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged end of 2 inch stub main. Crew made permanent fitting only repair.
Southern California Gas Company | N | LOS ANGELES | SANTA FE SPRINGS | 2020-09-03 | Third party excavation damage | Main | Polyethylene Pipe | Vacuum Equipment with no Agreement | 2 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 3 |  | TRINITY WESTCOM | NORWALK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Pothole crew using vac truck and water jet ahead of telecom job. Water jet damaged pipe.
Southern California Gas Company | N | LOS ANGELES | SANTA FE SPRINGS | 2020-04-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TURN AROUND COMMUNICATION | WEST COVINA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On 400.500 while hand digging with a shovel to install communications, Damien Gomez with Turn Around Communication,damaged a one inch plastic gas service.ï¿½ They had a valid ticket and the marks provided by the gas company employee were accurate.ï¿½ SCG crew arrived on scene and made permanent repairs.ï¿½ The Santa Fe Fire Department arrived on scene, shut the curb valve and left prior to gas company arrival.
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2020-06-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | LILIPUT LANDSCAPING COMPANY | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit a plastic service while working in the yard of the home owner
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2020-03-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | SANTA MONICA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Customer claimed the gas line had been previously exposed and he slipped and nicked it with a shovel
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2020-04-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BROWN OSVALDSFON INC | SANTA MONICA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged a gas service while excavating in property.
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2020-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NEW LEAF REMODELING | AGOURA HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | hit with shovel when hand digging
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2020-03-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PACIFIC WEST BUILDERS | SIMI VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor struck a gas facility while excavating with a backhoe there was no valid USA ticket at the address
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2020-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DOMINGUEZ GENERAL ENGINEERING | POMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | gas line was marked , hit with shovel wile hand exposing
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2020-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DOMINGUEZ GENERAL ENGINEERING INC | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | On arrival found crew onsite installing new water line along Pico Blvd. Crew member stated that as they were removing dirt from trench, heavy equipment attachment caught on service line. They taped it off at damage point and called in invident
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2020-05-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | SOCAL ELECTRICAL FIRM | TORRANCE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | PER LCT TICKET NOT AVAILABLE AT THE MOMENT
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2020-06-25 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | GNH CONTRACTORS INC | SANTA MONICA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor cut gas service with a sawzall
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2020-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NORTHWEST EXCAVATING INC | NORTHRIDGE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor digging with Backhoe hit 1 inch PLA Service. Firefighters on site, suited with fresh air. Abd Service at SMC, permanent repairs made.ï¿½
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2020-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ARRIAGA CONCRETE CO | CULVER CITY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor did not update ticket or request remarks
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2020-07-30 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | WACONAH CONSTRUCTION | VENICE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit 0.5 inch IPS service with backhoe while grading
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2020-11-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JOHN WHITE PLUMBING | SANTA MONICA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Had a lot of pipes and roots within the excavation causing damageï¿½
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2020-12-14 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JOHN H AKERBLOM SONS | MALIBU | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor cut into 0.75 inch STL Service service with Sawzallï¿½
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2020-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PR BUILDERS INC | LANCASTER | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging with excavator hit 0.50 IPS service and cut service in half, contractor p inched service and tied it with wire . no valid USA
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2020-11-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DOMINGUEZ GENERAL ENGINEERING | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | contractor was installing water service and came in contact with a unmarked PLA service 4 feet away from marks that were put on ground. replaced 2 feet of 0.5 inch CTS. Updated Facility records.
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2020-10-09 | Third party excavation damage | Riser | Polyethylene Pipe | Grader/Scraper | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BLUE SUMMER PARTNERS LLC | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Riser was hit and or run over by skid steer. Operator was the only one on site and refused to give any information pertaining to job to supervision.ï¿½
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2020-01-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ALTA CONSTRUCTION | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Firefighters hammered in redwood plug to slow down leak gas not blowing when we arrived Contractor said that excavators were hand digging alongside service and then decided to use backhoe to finish trench They assumed the service went straight out to alley however it dog legged
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2020-07-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | J STUART HILLIARD | VAN NUYS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor cut into 0.5 inch plastic service
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2020-01-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JERRY | SUN VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USAï¿½
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2020-04-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PROJEKTA INC | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor was hand digging when damaged gas service
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2020-07-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PROJECTA INC | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging trench hit 0.5 inch IPS service with jackhammer
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2020-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | UNITED SITE SERVICES | EL MONTE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit service digging for temporary power pole
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2020-04-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | SANTA MONICA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner is having some work done on the home and was having some drainage lines worked on and it appears that they damaged the service line, however, it was not reported as a damaged line, order came in as an A2 meter leak and upon investigation it was discovered that the service line was damaged and taped up by someone.ï¿½
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2020-11-10 | Third party excavation damage | A service line with no excess flow valve installed | Material not known | Hand Tools | 0.75 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | LEVY CONSTRUCTION | SANTA MONICA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was Excavating and thought our line was dead and cut through it.ï¿½
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2020-05-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | SOCAL ELECTRICAL | BELLFLOWER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor digging for new power hit service that was marked with back hoe.ï¿½ Back hoe operator spoke with locater before he started the job and was told where the lines were.ï¿½
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2020-06-03 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 32 |  | COMMUNITY CORPORATION OF SANTA MONICA | SANTA MONICA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit a 0.75 inch steel service with a pointed pry bar trying to remove concrete at fence post
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2020-11-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CATHERINE BACK | SHERMAN OAKS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumbing contractor trenching without valid USA ticket damaged 0.5 inch Gas Service. Homeowner refused to release their information and asked to be billed directly.
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2020-02-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | FONTANA | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | unmarked service was hit by mini backhoe while trenching 2 away from plastic main while service was unmarked hand digging should be done if working 2 or closer to plastic main
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2020-04-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | LA DWP | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | No | DWP cut through our service in casing with sawsaw.ï¿½
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2020-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | 14650 VALLEY VISTA LLC | SHERMAN OAKS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While trenching for foundation of new house, 0.5 inch CTSï¿½line hit.
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2020-11-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ARBI CONSTRUCTION | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging footing for new home, contractor hit 0.5 inch pla service. Cutback w 0.5 inch cap.ï¿½
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2020-11-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per LCT Victor no one on scene upon arrival unsure who hit line.
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2020-08-14 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 4 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | AJ PEDELFORD | CERRITOS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per LCT Alex Kwon 4 inch plastic main hit by grounding stake.
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2020-02-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | VARTAN YOLCHIAN | TUJUNGA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor trenching for wall footing hit service ï¿½ Per supervisor due to street moratorium we cut back in parkway 0.5inch plastic service
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2020-11-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PETRA LONGO | NORTH HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Sewer company digging for sewer repairs No USA called in.
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2020-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | SHERMAN OAKS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per LCT Ramon Sanchez No one on site to provide information.ï¿½ Service appeared to be cut with a sawzall.ï¿½ï¿½ Per CIS memo Contractor Zvi Forkosh hit line with shovel while digging trench for new gas lines.
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2020-12-07 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | APL | CHATSWORTH | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Crew Was potholing to expose service line in private property, and struck 0.5 inch CTS Line with shovel.
Southern California Gas Company | N | LOS ANGELES | SOUTH EL MONTE | 2020-09-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NA | EL MONTE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor failed to notify USAï¿½
Southern California Gas Company | N | LOS ANGELES | SOUTH GATE | 2020-04-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | damaged service with shovel. No 811
Southern California Gas Company | N | LOS ANGELES | SOUTH GATE | 2020-07-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | SOUTH GATE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged plastic gas service by owner installing fence
Southern California Gas Company | N | LOS ANGELES | SOUTH GATE | 2020-04-16 | Third party excavation damage | Riser | Steel | Miscellaneous/Other | 0.75 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | NA | NA |  | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | Lawnmower ran over inactive service riser MSA removed by company previous to incident ï¿½in overgrown grass, severed riser below shutoff valve.
Southern California Gas Company | N | LOS ANGELES | SOUTH GATE | 2020-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | SOUTH GATE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | hit service line while digging to install a sewer line
Southern California Gas Company | N | LOS ANGELES | SOUTH GATE | 2020-08-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | JOSE | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor cut into exposed 0.5 inch plastic service with a Sawzall.
Southern California Gas Company | N | LOS ANGELES | SOUTH GATE | 2020-02-17 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 8 |  | HERMAN WEISKER | RIVERSIDE | CA | Y | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Company Contractor installing new gas main was using directional bore when they hit a 2 plastic main Heavy electrical that caused major interference with signal as you cross over Garfield into shopping center GIS shows an unknown service North of Southern Pacific Rd and no main feeding shopping center This damage was at the unmapped main that feeds the shopping center ï¿½
Southern California Gas Company | N | LOS ANGELES | SOUTH GATE | 2020-04-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | SOUTH GATE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | homeowner damaged cts line with shovel
Southern California Gas Company | N | LOS ANGELES | SOUTH GATE | 2020-06-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 39 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | SOUTH GATE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | homeowner digging to fix water leak and damaged 0.50 cts line.
Southern California Gas Company | N | LOS ANGELES | SOUTH PASADENA | 2020-06-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | TAN CONSTRUCTION | HACIENDA HEIGHTS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CONTRACTOR DIGGING TO INSTALL WATER LINE
Southern California Gas Company | N | LOS ANGELES | SOUTH PASADENA | 2020-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 10 |  | NA | SOUTH PASADENA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | SOMEONE HIRED BY THE OWNER STRUCK THE SERVICE WITH Aï¿½ BACK HOE. THE OPERATOR WAS ONE UPON MY ARRIVAL
Southern California Gas Company | N | LOS ANGELES | SOUTH PASADENA | 2020-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 10 |  | CALVARY CHURCH | SOUTH PASADENA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor knowingly digging without a USA ticket. work being performed was to repair a sewer lateral
Southern California Gas Company | N | LOS ANGELES | SOUTH PASADENA | 2020-06-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | SOUTH PASADENA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging for homeowner without USA ticket. Hit service that was stubbed into property.ï¿½
Southern California Gas Company | N | LOS ANGELES | SOUTH PASADENA | 2020-12-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DUNRITE PLUMBING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | PLUMBER WAS DIGGING UP THE SEWER LINE AT THIS ADDRESS TO INSTALL A CLEAN OUT WHEN THEY HIT THE PLASTIC SERVICE.ï¿½ THEY DIDï¿½ NOT HAVE USA FOR THE WOR THEY WERE DOING.ï¿½ THE SERVICE WAS BENT BACK AND UNDER CONTROL UPON ARRIVAL.
Southern California Gas Company | N | LOS ANGELES | STEVENSON RANCH | 2020-10-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 1 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | OWNER NAME IS JAY JULIEN | PALMDALE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Party Contractor struck service with excavator while digging to install electrical communication boxes.
Southern California Gas Company | N | LOS ANGELES | STEVENSON RANCH | 2020-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NA | STEVENSON RANCH | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner was digging to expose house line for plumber to repair leaking houseline when homeowner damaged Service line while digging with shovel.ï¿½
Southern California Gas Company | N | LOS ANGELES | STEVENSON RANCH | 2020-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | STEVENSON RANCH | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging to install a grounding rod for solar panels.
Southern California Gas Company | N | LOS ANGELES | STEVENSON RANCH | 2020-05-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | STEVENSON RANCH | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner struck gas service while excavating for sewer repair. No USA ticket.
Southern California Gas Company | N | LOS ANGELES | STUDIO CITY | 2020-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ROSS CONSTRUCTION | UPLAND | CA | N | Y | Yes | No | Yes | Yes | No | Yes | No | While digging to install a retaining wall, contractor dug outside of USA delineation and pulled up on 0.75 inch steel service
Southern California Gas Company | N | LOS ANGELES | STUDIO CITY | 2020-06-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ALEX REUSS | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit plastic service with pick hand tool while trenching.ï¿½ No USA
Southern California Gas Company | N | LOS ANGELES | STUDIO CITY | 2020-04-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | STUDIO CITY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging to extend a wall
Southern California Gas Company | N | LOS ANGELES | STUDIO CITY | 2020-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | FERREIRA COASTAL CONSTRUCTION | RANCHO CUCAMONGA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | While digging to install sewer, contractor pulled on and broke anï¿½unmarked 0.75 inch steel stub Contractor had a valid USA
Southern California Gas Company | N | LOS ANGELES | STUDIO CITY | 2020-09-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | STUDIO CITY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per LCT Ray Rodriguez homeowner taking responsibility hit line with backhoe while grading. 0.5 inch cts aldylayno valid USA
Southern California Gas Company | N | LOS ANGELES | STUDIO CITY | 2020-02-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | TEMPLE CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA for grading
Southern California Gas Company | N | LOS ANGELES | STUDIO CITY | 2020-05-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | LA CANADA FLINTRIDGE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | HomeownerContractor was installing sewer to new home.ï¿½ Trenching on Oeste Ave. Mapping issue says that hit service was standard and branch.ï¿½ But found two standards.ï¿½ GIS and service history was not accurate.ï¿½ Contractor hit service with backhoe.
Southern California Gas Company | N | LOS ANGELES | STUDIO CITY | 2020-05-20 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 2 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | ALTAMIRA LANDSCAPE DESIGN | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor was installing landscaping logs along the hill of property and one of the steel rebars was inserted into the ground puncturing our 2 inch plastic main.
Southern California Gas Company | N | LOS ANGELES | STUDIO CITY | 2020-02-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | DEROAN CONSTRUCTION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged our service while digging up a trench to install a drain system
Southern California Gas Company | N | LOS ANGELES | SUN VALLEY | 2020-08-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | SUN VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner digging a trench for electrical with backhoe struck branch service. No USA.
Southern California Gas Company | N | LOS ANGELES | SUN VALLEY | 2020-05-20 | Third party excavation damage | Riser | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | SUN VALLEY | CA | N | N | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | property owner moving tires and struck the MSA Riser
Southern California Gas Company | N | LOS ANGELES | SUN VALLEY | 2020-11-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | SUN VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor did not call USA
Southern California Gas Company | N | LOS ANGELES | SUN VALLEY | 2020-01-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service was damaged by contractor with a shovel while working on the property They were installing new irrigation lines and failed to notify USA as they were not aware of the service Responsible party should be billed
Southern California Gas Company | N | LOS ANGELES | SUN VALLEY | 2020-03-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | SHAWNA CONTRACTORS GENERAL | MOORPARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working on property damaged newly installed service They damaged the plastic 2 service with a backhoe They failed to notify USA prior to digging
Southern California Gas Company | N | LOS ANGELES | SUN VALLEY | 2020-03-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | FACILITY BUILDERS AND ERRECTERS INC | SAN FRANCISCO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Correct address is 11219 Randall St This used to be a complex with 4 different plastic services and at one point all services were abandoned One was left as a cutback and contractor damaged the plastic service cutback Locator had no way to locate the services as GIS showed it abandoned They had a valid USAï¿½
Southern California Gas Company | N | LOS ANGELES | SUN VALLEY | 2020-07-05 | Third party excavation damage | Riser | Steel | Backhoe/Trackhoe | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | EMIL GEDAYAN | SUN VALLEY | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No | No damage to SUOF. | No damage to SUOF. | moving cars in junk yard with forklift
Southern California Gas Company | N | LOS ANGELES | SUN VALLEY | 2020-05-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | SUN VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner struck service line while placing stake for a concrete form. No USA.
Southern California Gas Company | N | LOS ANGELES | SUNLAND | 2020-12-27 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | SUNLAND | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupants employee ripped out service using their backhoe while digging for drain line.ï¿½
Southern California Gas Company | N | LOS ANGELES | SUNLAND | 2020-10-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | SUNLAND | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | trenching to install new sprinkler system and hit line with shovel
Southern California Gas Company | N | LOS ANGELES | SUNLAND | 2020-03-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DE LA TORRE BUILDERS | PANORAMA CITY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor was working on the property and damaged the branch service crossing lot to the neighbor Service was marked properly with chalk but marks were not visible upon arrival of crew The ticket expired on 1 31 2020
Southern California Gas Company | N | LOS ANGELES | SUNLAND | 2020-04-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | AMERICAN PROPERTY ENS | SUNLAND | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged plastic service with backhoe. Homeowner noticed yellow paint in curb and assumed the line was far from his excavation. No USA was called and homeowner was advised to call USA before digging. Damaging party should be billed AG
Southern California Gas Company | N | LOS ANGELES | SUNLAND | 2020-08-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NA | SUNLAND | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner stated they were digging to install a sprinkler system and hit the gas line with the shovel.
Southern California Gas Company | N | LOS ANGELES | SUNLAND | 2020-05-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | SUNLAND | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | HO excavating to replace sewer lateral No USA
Southern California Gas Company | N | LOS ANGELES | SUNLAND | 2020-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | SUNLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor damaged gas service line while excavating for water service.ï¿½
Southern California Gas Company | N | LOS ANGELES | SUNLAND | 2020-12-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOME OWNER | SUNLAND | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While 3rd party contractor was digging, they hit the service while using hand tools.
Southern California Gas Company | N | LOS ANGELES | SUNLAND | 2020-11-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RSI PLUMBING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor severed service line while excavating for sewer line repair.ï¿½
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2020-10-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | RJ S PROPERTY MANGEMENT | TUJUNGA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was using backhoe to dig repair hole for a water leak and damaged 1inch PLA service. Contractor was advised to contact 811 when doing any digging in the future
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2020-02-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GOTHIC LANDSCAPING | VALENCIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging with shovel to install irrigation lines 0.5inch ips service was damaged while digging No USA was called ï¿½
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2020-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | M TECH COMMUTATIONS | NORTH HOLLYWOOD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | Service was struck while digging to install cable television. Service was mismarked.
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2020-11-19 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | UNITED EXCAVATION FROM WOODLAND HILLS | WEST HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged happened while there was a building demolition.
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2020-06-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | SYLMAR | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 1 inch IPS line with backhoe while trenching for electric conduit. Warning mesh was in place and accurate. No USA ticket.
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2020-08-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | SELVIN GODINEZ | VAN NUYS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was digging to install water and drain line to ADU and hit 0.5 inch IPS line.
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2020-04-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ANGUIANO SONS | PACOIMA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was grading in the property and punctured a whole on the steel service. Contractor was told to call USA for any future work.
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2020-01-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | NEWHALL | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Operator struck stub while excavating for gas trench No USA had been Called He was advised to always call USA
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2020-10-15 | Third party excavation damage | Riser | Steel | Grader/Scraper | 1 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | SYLMAR | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | Contractor, hired by owner, cut into msa nipple while using a Sawzall to trim nearby bush
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2020-05-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BOCA GD CONSTRUCTION | GARDENA | CA | N | Y | No | No | No | No | No | No | No | Contractor hit 1 inch plastic service while trenching for sewer. EFV was tripped and crew made repairs. Contractor was digging without USA.
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2020-03-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 3 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | EUINCE VELEZ | SYLMAR | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | USA ticket was from 2017 No marks visible due to time and construction work Operator using a bobcat hit 3 service while excavating for sewer
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2020-06-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | NA | SYLMAR | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Steel service found bent over and above ground by an ETR attempting to turn on the gas. It appears the house was remodeled. No record or request to alter service for new construction.
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2020-07-01 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | APL | CHATSWORTH | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Company contractor APL damaged service line while digging to abandon branch service
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2020-05-14 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 2 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | SYLMAR | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant was driving a 30 inch stake into the ground for a gazebo support. Stake pierced the 2 inch main in the backyard through the top and bottom of the main.
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2020-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CARLOS MUNOZ CONSTRUCTION | SHERMAN OAKS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit wiht shovel installing power pole per Carlos Munoz 8184034888
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2020-01-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JIREH BUILDING | CHATSWORTH | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | GC Jireh Building Inc Employee Fabricio Amador was using a trencher to excavate for a drainage line The service was damaged in process of trenching The service was found folded back and taped No USA ticket He was advised to always call USA
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2020-11-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ADVANCED GENEREAL CONSTRUCTION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service with shovel
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2020-11-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ADVANCE GENERAL CONSTRUCTION | VAN NUYS | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | contractor dug prior to having has line marked out
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2020-12-01 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 3 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | MTEK | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Per workers, while using hand tools, punctured main.
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2020-12-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | M TEK COMMUNICATIONS | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | ATandT Contractor stated laborer cut through 0.5 CTS Service that was crossing in their trench path with shovel.
Southern California Gas Company | N | LOS ANGELES | TARZANA | 2020-12-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ELEMENTS LICENSE 1004972 | WOODLAND HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was had digging and hit CTS line
Southern California Gas Company | N | LOS ANGELES | TARZANA | 2020-04-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | PARKER BROWN GENERAL CONTRACTORS | CANOGA PARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor Parker Brown General Contractors hit 0.50 inch cts service while grading in yard, contractor was also digging with expired USA. Expired ticket
Southern California Gas Company | N | LOS ANGELES | TARZANA | 2020-05-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | FLOOD BROTHERS PLUMBING | STUDIO CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 0.50 inch IPS Service with shovel while digging up the sewer line. Advised to call USA before digging next time.
Southern California Gas Company | N | LOS ANGELES | TARZANA | 2020-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ASI IFRAH | TARZANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was grading with bob cat and hit steel service.ï¿½
Southern California Gas Company | N | LOS ANGELES | TARZANA | 2020-10-27 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | NA | TARZANA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service with bobcat while grading for concrete.
Southern California Gas Company | N | LOS ANGELES | TARZANA | 2020-09-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DANIEL JAHANIAN | TARZANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 1 inch PE, digging trench for foundation, No USAï¿½
Southern California Gas Company | N | LOS ANGELES | TARZANA | 2020-12-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | TARZANA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner digging for irrigation water leak. No USA
Southern California Gas Company | N | LOS ANGELES | TARZANA | 2020-01-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | F E CONSTRUCTION BUILDING NEW CENTURY | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Gas service found damaged leaking and buried Lester Building New Century stated F E construction damaged and buried gas service
Southern California Gas Company | N | LOS ANGELES | TARZANA | 2020-12-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 70 |  | DALCO FORENSIC CONSULTANTS | SIMI VALLEY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor hit 1 inch PLA Aldylay main feeding aprox.1520 apartment units w a backhoe while trying to fix waterï¿½leak. Contractor had a USA which was not valid yet, although our facilities were already located correctly and visible. SCG crew had to pinch 2 inch PLA main in a control hole downstream dropping approx. 58 units. All picsï¿½and required info has been sent to claims and damage prevention. Estella Rheinhardt, John Mena, Sarah Callen, Sal Rodriguez and Juan Garcia Lopez
Southern California Gas Company | N | LOS ANGELES | TARZANA | 2020-01-27 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | PACIFIC GREEN HOMES | VAN NUYS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA grading damaged 0.75inch steel service stub
Southern California Gas Company | N | LOS ANGELES | TEMPLE CITY | 2020-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TURN AROUND COMMUNICATIONS | IRWINDALE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | ETD Carlos talked to Michael from Turn Around Communications on 717 and was told by Michael the job will not start until 727.ETDCarlos explained that he hasï¿½not located all gas facilities within the delineation. ETDCarlos noted the conversation on the ticket. Due to lack of communication within the contractor crew and Michael they stared the job on 724 and bored into an unmarked gas service.
Southern California Gas Company | N | LOS ANGELES | TEMPLE CITY | 2020-02-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 2 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | TURNAROUND COMMUNICATION | WALNUT | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Installing electric conduit
Southern California Gas Company | N | LOS ANGELES | TEMPLE CITY | 2020-02-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | DAVE WOODARD | TEMPLE CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor did not call USA They were removing oldï¿½concrete footing at PL for tree and roots removal
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2020-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | NA | TORRANCE | CA | N | N | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | construction debris fell on riser cracking service vale.
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2020-07-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MARTIN RAMIREZ | GARDENA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | homeowner cut into copper line unaware that plastic cts was inside customer assumed line was water
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2020-03-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | TORRANCE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home Owner was digging to remove tree roots and struck our line No USA
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2020-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SOUTH CONSTRUCTION | HUNTINGTON BEACH | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | SVC HIT WITH BACKHOE
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2020-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | TORRANCE FENCE COMPANY | TORRANCE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per RB84, Third party Contractor was digging to install new fencing when the 0.5 inch plastic service was hit.ï¿½
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2020-08-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | LAWNDALE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit service line while digging for sewer line no USA. LCT advised to call 811
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2020-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | WWW SALSPLUMBING COM | TORRANCE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | damaged 0.5 inch gas line THIS IS THE SECOND TIME THIS SERVICE WAS DAMAGED IN THE LAST WEEK.
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2020-02-14 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 8 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10001 |  |  | NA | PERMA CITY SKYBRIDGE | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator struck gas main while digging a trench with a Back Ho
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2020-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | TORRANCE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | hit svc
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2020-11-30 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 35 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | EUGENE SZABADOS | BURBANK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor trenching to install low voltage camera line. Hit line with ditchwitch. ï¿½
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2020-05-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CITY OF TORRANCE WATER CO | TORRANCE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Closed ticket out in error with out marking the ticket, locator has been counsel on this issue.
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2020-08-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | VIDEO VOICE DATA COMMUNICATIONS | GARDEN GROVE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | svc hit while potholing svc marked correctly
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2020-03-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CITY OF TORRANCE WATER | NA |  | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | Water service damage boring in water line
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2020-05-08 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 30 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 47 |  | SRM GENERAL CONTACTOR | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor excavating new home construction damaged main
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2020-05-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | S P BEAGLE | GARDENA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor struck svc with backhoe while installing Edison conduit.
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2020-04-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | RYAN COMPANY | MINNEAPOLIS | MN | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Service was marked for the riser and meter in service. There was a branch coming from the standard, that headed east. It was cut back near the east most dock about 225ï¿½feet away that had no sign of it on the map. Whole parking lot was graded so i couldnt see if there was signs of a patch or other indications of another service.ï¿½
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2020-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | RYAN COMPANIES US INC | LA JOLLA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third Party Excavating to expose serviceï¿½damaged pipe with Back Hoe
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2020-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RYAN COMPANY | HUNTINGTON BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 2 inch plastic gas line with trencher.ï¿½ No USA
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2020-10-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RYAN COMPANIES | LA JOLLA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to verify presence of gas lines.ï¿½
Southern California Gas Company | N | LOS ANGELES | TUJUNGA | 2020-01-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HAKOT MURDAYAN | TUJUNGA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CUSTOMER TRENCHING TO INSTALL GAS HOUSELINE
Southern California Gas Company | N | LOS ANGELES | TUJUNGA | 2020-02-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | TUJUNGA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer was in the process of driving piece of EMT Conduit for tree support when he struck our facility ï¿½
Southern California Gas Company | N | LOS ANGELES | TUJUNGA | 2020-10-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 33 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | TUJUNGA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While contractor was using a shovel, they hit the gas service.
Southern California Gas Company | N | LOS ANGELES | TUJUNGA | 2020-06-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | ENERGY SALON PARTNERS | TORRANCE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Solar contractor excavating to install conduit was cutting roots and cut the service in the process. They inserted a drill bit and taped it in place to slow the escaping gas.
Southern California Gas Company | N | LOS ANGELES | TUJUNGA | 2020-11-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | TUJUNGA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | occupant installing fence post next to MSA riser location
Southern California Gas Company | N | LOS ANGELES | TUJUNGA | 2020-04-18 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | LADWP | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | line hit with steel rod that is used to locate water leaks
Southern California Gas Company | N | LOS ANGELES | TUJUNGA | 2020-05-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | TUJUNGA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | HO excavating to install water drainage lines No USA
Southern California Gas Company | N | LOS ANGELES | TUJUNGA | 2020-05-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 3 |  | NA | TUJUNGA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer was hand digging holes for fence posts and hit plastic service.ï¿½ ï¿½
Southern California Gas Company | N | LOS ANGELES | TUJUNGA | 2020-10-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Gardener was removing tree stump and cut through 0.75 inch steel service with sawzall.
Southern California Gas Company | N | LOS ANGELES | TUJUNGA | 2020-01-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | TUJUNGA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was trenching for footing of wall when they hit our gas line No USA was called
Southern California Gas Company | N | LOS ANGELES | TUJUNGA | 2020-02-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | THE ONLY ONE TRUCKING | GRANADA HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was grading in the street and failed to call USA and managed to damage our facility ï¿½
Southern California Gas Company | N | LOS ANGELES | TUJUNGA | 2020-01-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | TUJUNGA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor cut into service with a saw thinking it was a water line
Southern California Gas Company | N | LOS ANGELES | TUJUNGA | 2020-07-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | PETRELLI ELECTRIC | AGOURA HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor struck gas line while digging to install electrical pole.ï¿½ ï¿½Line struck with shovel.ï¿½
Southern California Gas Company | N | LOS ANGELES | TUJUNGA | 2020-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | TUJUNGA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was digging on their property and damaged the plastic service with a shovel. Homeowner was unaware of USA and was told to call USA for any future work on the property.
Southern California Gas Company | N | LOS ANGELES | TUJUNGA | 2020-08-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NA | TUJUNGA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was installing water line and mistakenly cut gas line believing it was old water line
Southern California Gas Company | N | LOS ANGELES | VALENCIA | 2020-04-21 | Third party excavation damage | Riser | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 52 |  | STAY GREEN LANDSCAPING INC | SANTA CLARITA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscaping contractor excavating to repair a water leak hit the pigtail of the riser. USA was not notified. The damage location prevented squeezing the pipeline after the branch connections. This resulted in 52 units being shutdown.
Southern California Gas Company | N | LOS ANGELES | VALENCIA | 2020-06-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PATRIOT POOL BUILDERS | SANTA CLARITA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service Damaged by Pool contractor using electric jack hammer.ï¿½ ï¿½
Southern California Gas Company | N | LOS ANGELES | VALENCIA | 2020-06-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | WIRED ELECTRIC | SANTA CLARITA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavator exposing 2 inch gas stub for NB installation struck stub with Backhoe. They did not renew ticket because there was a inchmarker inch showing where the gas line was. Marker was a piece of 0.50 inch plastic pipe with a wire for locating the stub.
Southern California Gas Company | N | LOS ANGELES | VALENCIA | 2020-01-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | VISTA VALENCIA GOLF COURSE | SANTA CLARITA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Gold course employee was excavating for irrigation line hit 1 plastic service line
Southern California Gas Company | N | LOS ANGELES | VALENCIA | 2020-09-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GOTHIC LANDSCAPING | VALENCIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While customer using back hoe to excavate, they hit service line.
Southern California Gas Company | N | LOS ANGELES | VALENCIA | 2020-08-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | GERLUND INC | VALENCIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit service with shovel
Southern California Gas Company | N | LOS ANGELES | VALENCIA | 2020-02-26 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 10 |  | ARIZONA PIPELINE | CHATSWORTH | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | Main ropes unexpectedly away from the curb Broken wire prevented proper locating Measurements and potholes indicated main was a few feet to the east of the excavator Main was struck in the roped section
Southern California Gas Company | N | LOS ANGELES | VALLEY VILLAGE | 2020-08-28 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | W A RASIC CONSTRUCTION | LONG BEACH | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While digging to replace gas main, W. A. Rasic dug into 1 inch plastic gas service.ï¿½ Service was marked correctly, crew forgot about it and did not pothole first.
Southern California Gas Company | N | LOS ANGELES | VALLEY VILLAGE | 2020-09-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 11 |  | ON THE SPOT CONSTRUCTION | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per LCT Ray Rodriguez Contractor Richard Salgado hit SCG service line with shovel while digging to install a water line.
Southern California Gas Company | N | LOS ANGELES | VALLEY VILLAGE | 2020-01-20 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | WILCOX WILCOX CONSTRUCTION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor struck 2 inch gas main with backhoe while digging for sewer
Southern California Gas Company | N | LOS ANGELES | VALLEY VILLAGE | 2020-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | VALLEY VILLAGE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | digging a trench unknown what for customer failed to call 811 underground service alertï¿½
Southern California Gas Company | N | LOS ANGELES | VALLEY VILLAGE | 2020-07-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | YOSI SABAG | VALLEY VILLAGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner demolished home and did not call USA.ï¿½ Broke 0.5 inch pla svc. w bhoe. Planned on building new home over gas service.ï¿½ LCT Kwon abandoned service at PL for safety reasons.ï¿½ Informed homeowner he needs to call USA and SoCalGas planning to have service reinstated.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2020-11-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ATMOSPHERE LANDSCAPING | VENTURA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscaper hit service with a shovel while excavating for irrigation. No USA ticket. They were advised to always call 811 before digging.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2020-11-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | KOLOE INC | STUDIO CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per LCT service was hit with some sort of hand tool.ï¿½ Upon ETR arrival, no one on site.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2020-01-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 5 |  | DWP | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service was damaged by backhoe while trenching for water main DWP did not hand expose socalgas facilities ï¿½
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2020-07-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 5 |  | LADWP | NORTH HOLLYWOOD | CA | N | N | Yes | Yes | No damage to SUOF. | Yes | No | Yes | Yes | While excavating to install new water main, LADWP potholed over visible marks w vacuum truck could not find recalled the ticket per foreman, while waiting for response from SoCalGas locater, they dug w bhoe and were going to stop 10ft from gas svc. marks.ï¿½ They hit said gas service w last scoop10 feet from gas svc. marks and called it in.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2020-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DWP | NORTH HOLLYWOOD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | During the process of trenching for new water line trench, DWP damaged an unmarked 0.75 inch unknown cutback service. SCG Crew made repairs with proper leak clamp.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2020-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 3 |  | PORTAKAN | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor struck gas service with hand tools while excavating for fencing. NO USA was called.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2020-01-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | VAN NUYS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was excavating with hand digging with shovel and struck service causing a leak
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2020-01-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 7 |  | UNITED EXCAVATION GROUP INC | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged our service while grading on the property ï¿½ Contractor damaged our service to 14633 which is the branch service
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2020-01-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 7 |  | UNITED EXCAVATION GROUP | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractorï¿½damaged plastic branch service toï¿½14633 vanowenï¿½st while grading ï¿½ï¿½ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2020-01-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | UNITED EXCAVATORS | WOODLAND HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | LCT spoke with Raffi who stated service nicked with shovel as they were looking for PE service
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2020-06-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged the branch service while trenching for new footing.ï¿½
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2020-04-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | VALLEY PRESBYTERIAN HOSPITAL | VAN NUYS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CST and IST on stie and smelled gas.ï¿½ Dug up area and found damaged 1 plastic service taped and clamped by contractor that just worked on house line.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2020-06-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | JM COMMUNICATIONS | PANORAMA CITY | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was open trenching for communication, when they struck long side PE service. Trench running roughly 5 feet parallel of gas main. Upon arrival no usa delineationsï¿½or Gas main service were visible. The area had been grinded for recess plating.ï¿½
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2020-11-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | VAN NUYS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging trench in private property, contractor working for homeowner hit plastic service
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2020-05-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MGBD COMPANY | TEMPLE CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was trenching to install new sewer lineï¿½without a USA. Contractor hit 0.50 inch CTS service while hand digging with shovel.ï¿½
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2020-10-10 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was digging and found our service pitted and was leaking.ï¿½ There was not a hit line at this location.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2020-11-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | VAN NUYS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Diggingï¿½ a trench to install a wall
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2020-11-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GENESIS PLUMBING | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumbing contractor was trenching without a valid USA, trenching for sewer lateral install. During the process they damaged 0.5 inch IPS gas service line.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2020-04-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | VAN NUYS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging to remove a tree
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2020-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | VCI CONSTRUCTION | UPLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | While digging with backhoe contractor damaged 0.5inch CTS plastic marked incorrectly USA was notified
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2020-03-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | VCI | UPLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Digging to install electrical conduit
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2020-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | VAN NUYS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner digging new trench to install sewer lateral hit 0.5 inch cts aldylay service w ï¿½a shovel. No valid USA.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2020-02-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RAFAEL DALCAZAR | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit our service while grading with bobcat
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2020-02-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PRECISION CONSTRUCTION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged our service while trenching to install a drain
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2020-06-13 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ARAKAL GRIGORYAN | VAN NUYS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third Party contractor was trenching to install a new drain when the service was hit.ï¿½
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2020-03-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | VAN NUYS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged over service while digging a hole for the new location of the 2 meter manifold.ï¿½ No fire, no police, no street closures, damage amount 5001000.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2020-10-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | JR CONSTRUCTION | VAN NUYS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Per LCT Gennady service hit with jackhammer while third party installing service line for customer.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2020-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | JABS POOL AND SPA | PANORAMA CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor severed our plastic service while digging to install waterline for pool.ï¿½ No valid USA ticket.ï¿½ After damaging our line, they bentï¿½it back and tied with metal stringrope and backfilled with concrete and did not report damage to Gas Co.ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2020-12-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | MM PLUMBING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd. party contractor cut into a copper line thinking it was water and cut through the casing damaging 0.5 inch CTS line. No USA was called in.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2020-06-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | VAN NUYS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer hired contractor to install Irrigationï¿½pipes, didnt call for USA, damaged 0.50 cts pipe.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2020-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | VAN NUYS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor owner damaged 0.50 service when digging trench for Fence. NO USA
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2020-12-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | VAN NUYS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging to install a new sewer line to backhouse, contractor working for H O hit 0.5 inch cts aldylay service. Fire department evacuated 1 building w 3 occupants.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2020-11-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ENVIRONMENTAL RESTORATION SERVICES | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | At arrival, nobody on site contractor digging trench for homeowner hit 0.5 inch aldylay service w backhoe.
Southern California Gas Company | N | LOS ANGELES | VENICE | 2020-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 43 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | GROUND CONTROL | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | hit 0.75inch steel stub
Southern California Gas Company | N | LOS ANGELES | VENICE | 2020-05-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MATTHEW STUART CO | SIGNAL HILL | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Valverde Construction severed a 1 inch plastic gas service while excavating with large backhoe. Per ETD statement, he and the contractor agreed on a area that would be marked given the length of the project. The contractor excavated ahead of the agreed upon area.
Southern California Gas Company | N | LOS ANGELES | VENICE | 2020-04-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | VARSITY PLUMBING | CARSON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | House under construction said they called USA but no
Southern California Gas Company | N | LOS ANGELES | VENICE | 2020-06-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | AVANTI POOLS INC | VAN NUYS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Arrived to job site to abandon gas line and install new line and came across cut service that was tied back up with wire. Audible Leak called supervision and notified Julie Fermino. will abandon service at SMC
Southern California Gas Company | N | LOS ANGELES | VENICE | 2020-05-13 | Third party excavation damage | Main | Steel | Hand Tools | 0.75 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LADWP | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per LCT, LADWP cut a 4 inch steel stub thinking it was abandoned.
Southern California Gas Company | N | LOS ANGELES | VENICE | 2020-01-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LORDS OF PLUMBING | INGLEWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor saw sawed through a 0.5inch IPS gas service while cutting roots sewer pipe
Southern California Gas Company | N | LOS ANGELES | VENICE | 2020-10-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | AYALA SEWER CONTRACTORS UNDERGROUND UTILITIES | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 0.5 inch CTS service while excavating for sewer.
Southern California Gas Company | N | LOS ANGELES | WALNUT | 2020-01-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | GG DECOR | WALNUT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor was digging a trench and hit a service line
Southern California Gas Company | N | LOS ANGELES | WALNUT | 2020-04-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | LEGACY CONCRETE | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | while contractor was removing the concrete steps, they hit our service with an axe
Southern California Gas Company | N | LOS ANGELES | WALNUT | 2020-02-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MIKE CARUSO | ALHAMBRA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Digging to install communications Dig not dig with caution
Southern California Gas Company | N | LOS ANGELES | WALNUT | 2020-01-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NX UTILITIES | SAN MARCOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | while the contractor was digging for the service they struck and damaged our plastic facility with a hand tool
Southern California Gas Company | N | LOS ANGELES | WEST COVINA | 2020-02-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NA | WEST COVINA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage was caused by homeowner Customer was digging to plant tree in yard with out calling USA because customer was unaware of USA service
Southern California Gas Company | N | LOS ANGELES | WEST COVINA | 2020-06-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | WEST COVINA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged 0.5 inch plastic service with shovel while digging to plant tree. Gas company crew onsite advised customer to always call USA 811 when planning to dig so utilities can be located.
Southern California Gas Company | N | LOS ANGELES | WEST COVINA | 2020-12-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | WEST COVINA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hit 0.5 inch plastic service with shovel while digging to remove dirt around riser.ï¿½
Southern California Gas Company | N | LOS ANGELES | WEST COVINA | 2020-09-23 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | E R CONSTRUCTION INC | BALDWIN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor had line exposed butï¿½hit the service after pausing work for a bit and forgot that line was there.ï¿½
Southern California Gas Company | N | LOS ANGELES | WEST COVINA | 2020-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | E R CONSTRUCTION INC | BALDWIN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Party Contractor was installing new water main when gas line was hit with backhoe.ï¿½ CONTRACTOR FAILED TO EXPOSE 24 inch IN BOTH DIRECTIONS OF THE MARK TO VERIFY LOCATION OF THE PLASTIC SERVICE.ï¿½ HE FOUND AN OLD STEEL LINE AND THOUGHT THAT WAS THE SERVICE EVEN THOUGH THE MARKS CLEARLY STATED PLA.ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | WEST COVINA | 2020-12-16 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10001 |  | 2 |  | E AND R CONSTRUCTION | SAN DIMAS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | crew was digging for water service on water main job. the main was marked twice. once for new plastic and old abandoned steel. plastic main marks were within the 2 feet but they failed to pot hole before digging with back hoe. The backhoe was still in the hole on arrival.
Southern California Gas Company | N | LOS ANGELES | WEST COVINA | 2020-02-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | THE FISHEL COMPANY | SANTA ANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | CONTRACTORS WERE POTHOLING SUBSTRUCTURES AHEAD OF DIRECTIONAL BORING WHEN THEY HIT OUR PLASTIC SERVICE ï¿½ THEY HIT OUR PLASTIC SERVICE WITH A BACKHOE ï¿½ THEY HIT THE SERVICE BECAUSE THEY THOUGHT THE DEPTH ON THE SERVICE WOULD BE DEEPER ï¿½ IT WAS EXPLAINED TO THEM THE IMPORTANCE OF EXPOSING OUR LINE BY HAND BEFORE ANY WORK IS TO BEGIN
Southern California Gas Company | N | LOS ANGELES | WEST COVINA | 2020-12-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SUBURBAN WATER | WEST COVINA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor hit 1 inch plastic main with shovel.ï¿½
Southern California Gas Company | N | LOS ANGELES | WEST HILLS | 2020-01-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 3 |  | TIM BLODGETT | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 0.5inch Plastic service with Backhoe Gas facility was located correctly didn t expose by hand
Southern California Gas Company | N | LOS ANGELES | WEST HOLLYWOOD | 2020-03-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | FLAMINGO CONSTRUCTION | STUDIO CITY | CA | N | N | Yes | Yes | Yes | Yes | No damage to SUOF. | Yes | Yes | damaged 0.5inch IPS service
Southern California Gas Company | N | LOS ANGELES | WEST HOLLYWOOD | 2020-12-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 119 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PACIFIC GREEN HOMES DEVELOPER | VAN NUYS |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor states they ran over service while excavating
Southern California Gas Company | N | LOS ANGELES | WEST HOLLYWOOD | 2020-01-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | LADWP hit facilities while exposing excavation area by hand Service hit by hand shovel LADWP was replacing a water service ï¿½
Southern California Gas Company | N | LOS ANGELES | WEST HOLLYWOOD | 2020-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | DWP | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | LADWP water main replacement project Foreman Dan Kirksey and crew identified gas mark for PLA service for 1401 Rising Glen at curbface in front of property but stated no mark was visible at SMC or within delineated work area While excavating with backhoe LADWP crew struck and damaged 0.5inch IPS PLA service
Southern California Gas Company | N | LOS ANGELES | WEST HOLLYWOOD | 2020-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PAH AIR CONDITIONING ELECTRICAL | FONTANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Resident while doing trench work on private property to install new power conduit exposed our half inch PLA service encased in three quarter inch STL Resident believed line was abandoned and put tapping screwing into PLA line and discovered it was live Resident made multiple attempts to get SCG to identify and rule out line as abandoned Upon speaking with customer customer stated EE from SCG told him line was abandoned but could not mark it as such PLA line was mismarked Technician marked service as branch instead of standard
Southern California Gas Company | N | LOS ANGELES | WEST HOLLYWOOD | 2020-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Damaged 1 inch steel stub
Southern California Gas Company | N | LOS ANGELES | WEST HOLLYWOOD | 2020-07-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DWP | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | DWP hit plastic service while trenching. Service was marked incorrectly.ï¿½
Southern California Gas Company | N | LOS ANGELES | WEST HOLLYWOOD | 2020-12-03 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | AR PIPING | NEWBURY PARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party damage. Crew was digging for sewer with backhoe and hit stub for 725 N. Croft Avenue. Fresh air used to stop leak and weld stub. permanent repair complete.
Southern California Gas Company | N | LOS ANGELES | WEST HOLLYWOOD | 2020-01-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | CANOGA PARK | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer was digging for irrigation and hit 0.5inch plastic service Usa was called but not ticket number was provided Service was clearly marked in the street but not in private property ï¿½
Southern California Gas Company | N | LOS ANGELES | WEST HOLLYWOOD | 2020-02-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | WEST HOLLYWOOD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer was digging with post hole digger to set a post for a fence he was installing ï¿½ He failed to call for USA and hit the 0.5inch plastic service line
Southern California Gas Company | N | LOS ANGELES | WEST HOLLYWOOD | 2020-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 6 |  | B E PLUMBING | SUN VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party Contractor while performing grading work for new driveway and sidewalk for new development, was driving in 0.5 inch steel rebar into ground and struck and damaged 0.5 inch CTS plastic gas line. No active USA.
Southern California Gas Company | N | LOS ANGELES | WEST HOLLYWOOD | 2020-11-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit plastic service than buried it.ï¿½
Southern California Gas Company | N | LOS ANGELES | WEST HOLLYWOOD | 2020-11-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | MMJJ ENGINEERING | ESCONDIDO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The contractor was excavating to install power conduit. He hit 0.5 inch CTS service with hand tool tunnel bar.
Southern California Gas Company | N | LOS ANGELES | WEST HOLLYWOOD | 2020-12-18 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 0.75 | 40 | 35 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | LA DWP | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | DWP damaged wrap on steel service
Southern California Gas Company | N | LOS ANGELES | WESTLAKE VILLAGE | 2020-05-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | PAULINO MARTINEZ | PACOIMA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Gardner hit plastic service with shovel
Southern California Gas Company | N | LOS ANGELES | WESTLAKE VILLAGE | 2020-11-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TITAN BROTHERS PLUMBING | WESTLAKE VILLAGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA called in for this job.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2020-10-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | WILLIAMS PIPELINE CONTRACTORS INC | SOMIS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Service correctly marked. Damaged by backhoe. Failure to protect in place.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2020-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | WILLIAMS PIPELINE CONTRACTORS INC | SOMIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator trenching for water hit marked service with backhoe. Service correctly marked, was even marked by pothole sub as well. Failure to exercise adequate caution, protect in place.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2020-06-30 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NOBEST INC | WESTMINSTER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Potholing crew working ahead of street rehab put probe through service line. Marks were accurate. Excavator failed to protect in place.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2020-10-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | THE RJ NOBLE COMPANY | ORANGE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service was correctly marked, had been potholed by contractor and they marked it too. Still yanked service with backhoe. Failure to protect in place maintain clearance.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2020-04-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | COLE PLUMBING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor doing emergency repair on sewer, hit our 0.50 inch service with a shovel.ï¿½ No USA called in.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2020-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | FELIPE SANCHEZ | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | excavator digging with out USA hit a plastic 0.5 inch service
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2020-06-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NOBEST INC | WESTMINSTER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator grading, removing old curb and gutter for street rehab. Hit marked service line.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2020-04-24 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | RJ NOBLE | ORANGE | CA | N | N | Yes | Yes | Yes | Yes | No damage to SUOF. | Yes | Yes | Contractor had potholed SMC on other side of alley, found depth, assumed depth was static. It was not. While grading with loader, hooked steel service, snapped MSA. Gas controlled at service valve. No underground leakage. Service bent. Was replaced.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2020-12-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | RJ NOBLE | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor grinding for street improvement, hit 0.75 inch steel serviceï¿½
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2020-03-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CALWEST LANDSCAPING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 0.5inch IPS stub with backhoe while installing new tree New Business Track NO USA
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2020-03-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CALWEST LANDSCAPING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | excavator struck gas stub while planting a tree with backhoe No USA New development No evacuations
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2020-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CAL NATIVE LANDSCAPING | WHITTIER | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavator digging without USA. Damaged 0.5 inch service line.ï¿½
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2020-12-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ELITE PLUMBING AND HYDROJETTING | WHITTIER |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging for sewer work, damaged plastic service with shovel.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2020-10-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 23 |  | CHRISTENSEN BROS GENERAL ENGINEERING | APPLE VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Backhoe trenching for sewer replacement damaged service. Marks not accurate due to incorrect measurement records in Service History.ï¿½
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2020-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | CHRISTENSEN BROS GEN ENGR | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas services next to 13426 Sunset Dr. per Tony Sampson. Installing sewer main.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2020-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 6 |  | CHRISTIAN BROTHERS GENERAL ENGINEERING | APPLE VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | the sewer contract companyï¿½were pot holing for services, whenï¿½theyï¿½cut through a 1 inch PE service line with the shovel. Improper excavation techniques
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2020-03-03 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 2 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 8 |  | SOUTHERN CALIFORNIA EDISON | SANTA FE SPRINGS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Edison Crew using large auger drill to install new transmission pole drilled directly into 2 plastic main
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2020-09-14 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | CHRISTENSEN BROTHERS | APPLE VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor acknowledged marks, said they had potholed, confirmed main location. Using backhoe to scrape banks of excavation, hit plastic main.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2020-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SS BUILDER | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA on file.ï¿½ Contractor hit steel service with a digging bar, causing a mild leakï¿½
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2020-12-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SHOFFEITT PIPELINE INC | IRVINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor installing storm drain, hit 2 inch PE main. no USA called in
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2020-12-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SHOFFITT PIPELINE INC | IRVINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | third party was digging to install a storm drain when they dugin our 2 inch PE main.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2020-12-22 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | SAFEWAY ELECTRIC | COLTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged line with backhoe while installing conduits.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2020-09-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BUCCOLA LANDSCAPING | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscaping contractor digging for drain system damaged service line. No USA, dug past warning mesh over service as well.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2020-06-23 | Third party excavation damage | Main | Polyethylene Pipe | Grader/Scraper | 2 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | REED THOMAS CO FOREST MOORE | SANTA ANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor grading at new housing tract hit 2 inch PLA main. No USA. Failure to hand expose, failure to protect in place.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2020-10-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | WHITTIER | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contactor was grading yard and clipped the 0.5inch service line. Digging with out a USA
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2020-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | SUBURBAN WATER SYSTEMS | LA MIRADA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Main mismarked further south due to signal interference from water main. Service marked correctly at curb but not clear how service marked at SMC near damage as marks were removed when water Co did their excavation. service was hit by backhoe.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2020-12-02 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SAFE WAY ELECTRIC | COLTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party excavator hit 2 inch PE main while digging for Edison lines
Southern California Gas Company | N | LOS ANGELES | WILMINGTON | 2020-12-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | WILMINGTON | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer was digging trench and hit our service line. No USA.
Southern California Gas Company | N | LOS ANGELES | WILMINGTON | 2020-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MSL ELECTRIC | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor pot hole over SCG mark exposed an old copper line thought that was it and bored under hitting live plastic service
Southern California Gas Company | N | LOS ANGELES | WILMINGTON | 2020-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | JOSE SOLACHE | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer was digging to set some small plants and was using a post hole shovel when they struck our gas line. No USA.
Southern California Gas Company | N | LOS ANGELES | WILMINGTON | 2020-12-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SULLY MILLER S COMPANY | BREA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | While Grading, Contractor struck a unknown unmarked riser that was covered in weeds and bushes. GIS records show no service to this empty lot.ï¿½
Southern California Gas Company | N | LOS ANGELES | WINNETKA | 2020-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | WINNETKA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | customer was digging a trench to install concrete steps.ï¿½
Southern California Gas Company | N | LOS ANGELES | WINNETKA | 2020-03-31 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MATEO S PAINTING | WOODLAND HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging to install sewer expired USA
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2020-06-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | VAN GROSSMAN | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 0.50 service while trenching for water service TRENCH. made repairs.
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2020-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MG PLUMBING | THOUSAND OAKS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Plumber hit abandoned stub while digging to install water main.
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2020-12-07 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 0.75 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | NA |  | N | Y | Excavation was for emergency reasons. | Excavation was for emergency reasons. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | This was not a Digin. This was a code 1
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2020-09-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | VINYL CONCEPTS | NEWBURY PARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | trenching to make a hole for post
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2020-12-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | WOODLAND HILLS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was digging inside his property to plant some trees and hit our 0.5 inch plastic service.ï¿½ No USA.ï¿½ Service was altered and repaired with 2 coupling and about 2 feet of new pipe.ï¿½ï¿½
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2020-06-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | WOODLAND HILLS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor owner damaged 0.75 service with saw installed clamp
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2020-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | WOODLAND HILLS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner struck gas service with hand tool while digging for post hole.
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2020-02-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HUMBERTO HERNANDEZ | NEWHALL | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per Humberto hit gas service with electric shovel while doing work for home owner and trenching for house addition in the back workers have no license Per Humberto home owner will be responsible for all charges
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2020-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | WOODLAND HILLS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging to install drainage
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2020-12-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | JW CONTRACTOR | CANYON COUNTRY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor was digging for stormï¿½drain and Hitï¿½0.5 inch cts branch. Branch was not updated in GIS. both house say that they are standard lines. no Branch ring on either riser
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2020-12-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JW GENERAL CONTRACTING | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit service for the second time while digging for sewer.
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2020-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NA | WOODLAND HILLS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA called for work being performed, damaged 0.5 cts service
Southern California Gas Company | N | ORANGE | ALISO VIEJO | 2020-02-18 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 50 | 44 | Y | Y | N | N | 0 | 0 |  | 0 | 0 |  | 3783 |  | 8 |  | LSR BUILDERS INC | SANTA ANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | On 02 18 20, SoCalGas was notified of a third party damage at 22902 Pacific Park Dr, Aliso Viejo. Third party was digging to install a sewer line when they hit a 2inch plastic gas main. The release of gas from the damage location ignited. Crews responded and safely controlled the gas. Investigation showed that the contractor had no USA ticket. No injuries nor damage was reported due to the release of gas. This was reported to CPUC when SoCalGas became aware of media coverage.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2020-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 18 |  | NA | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Company crew damaged 0.75inch service tee while digging
Southern California Gas Company | N | ORANGE | ANAHEIM | 2020-05-07 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 3 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CABLE COM | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | Cable Com was boring to install telecom.ï¿½ They did not hand expose prior to boring.ï¿½ More importantly they working digging outside of their delineated work area.ï¿½ï¿½ï¿½
Southern California Gas Company | N | ORANGE | ANAHEIM | 2020-11-13 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 3 |  | HOMEOWNER TED BEFAKUDO | PICO RIVERA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging holes in the ground to put in fence posts in private property.ï¿½ Contractor drilled through the steel service with a hand power drill.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2020-05-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | LINCOLN CONSTRUCTION | ANAHEIM | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | excavator did hot hand expose or call for remarks before continuing excavation after they claim they could not find our utility after potholing. No evidence of hand excavation before damage. Locate marks were off measurements and in line with riser. signal confirmed location however signal was generated from electrical service. actual gas service was offset 19 from mapped location and signal strength location.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2020-10-08 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 44 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NPL | CERRITOS | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to use caution while exposing gas line
Southern California Gas Company | N | ORANGE | ANAHEIM | 2020-12-09 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TELEDATA COMMUNICATIONS | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor utilizing backhoe for excavation over 2 inch plastic main.ï¿½ Contractor hit main with backhoe.ï¿½ Contractor contacted USA to report damage.ï¿½ Company Crew found plastic main leaking upon arrival.ï¿½
Southern California Gas Company | N | ORANGE | ANAHEIM | 2020-12-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ARPAD MIZTI | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA Requested, home owner digiing for sewer repair
Southern California Gas Company | N | ORANGE | ANAHEIM | 2020-06-09 | Third party excavation damage | Main | Steel | Boring Equipment | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | TRIPLE J DRILLING | PERRIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damage 2 STL main in the process of bulling back with bore rod when he started to smell gas. Contractor failed to pothole.ï¿½
Southern California Gas Company | N | ORANGE | ANAHEIM | 2020-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JAMBOREE HOUSING CORP | IRVINE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor was grading in private property before the service was scheduled to be abandoned. Damaged 0.5 inch plastic service
Southern California Gas Company | N | ORANGE | ANAHEIM | 2020-01-14 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 4 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 12300 |  | 8 |  | POWER TECH | FULLERTON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | On 01 14 2020, SoCalGas received a report of a third party damage at 2870 E La Palma Ave, Anaheim, while a contractor hit a 4inch plastic gas main boring for electrical conduit (Correction to original address reported on 2893 E La Palma Ave) . Gas crews responded, controlled the gas, and made permanent repairs by replacing a section of main. There were no injuries or further damages resulted from this incident. Investigation of the incident showed that there was a valid USA ticket for the contractor, however, the 4inch plastic main was not properly marked. Per the Locate and Mark employee, gas main was not mapped correctly in GIS mapping system and locator signal did not provide accurate main location. Updates to GIS mapping system are in progress. This incident is reported to CPUC when SoCalGas became aware of media coverage
Southern California Gas Company | N | ORANGE | ANAHEIM | 2020-05-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | LINCOLN CONSTRUCTION | ANAHEIM | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | marks were more than 2 away from actual location. Gis and measurements were wrong. Service took a dog leg that moved it away from riser location. Signal was strong and lined up with GIS measurements. Signal was coming off of electrical. More importantly, contractor did not hand expose prior to excavating with a back hoe.ï¿½ Contractor claims they hand exposed prior but there was no evidence of that since the back hoe trench was 100 past damage location and trench was only 14 inch wide.ï¿½ contractor started hand diggingï¿½over marks when crewï¿½arrived.ï¿½ We also stated that if Contractor is unable to find our service after digging over marks then they are required to call us before continuing with work Per Dig alert regulations.ï¿½ï¿½ï¿½ï¿½ï¿½ï¿½
Southern California Gas Company | N | ORANGE | ANAHEIM | 2020-05-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SEREFIN LANDSCAPING CO | WESTMINSTER | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscaping Co. was digging to repair broken sprinkler. 0.50 ips svc was under root. Worker attempted to cut root and cut gas service.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2020-12-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | LINCOLN CONSTRUCTION | ANAHEIM | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | contractor installing conduit for the city of Anaheim hit our line while digging, the line wasï¿½ mismarked.ï¿½Company locator got bad signal with the tracerï¿½wire, company crew used fishtape to located the service and still got bad location.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2020-11-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | LINCOLN CONSTRUCTION | ANAHEIM | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor was installing Elec Gas when gas was hit by mini excavator.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2020-11-18 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 40 | 36 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | LINCOLN CONSTRUCTION | NA |  | N | Y | Yes | Yes | No | No | No | Yes | Yes | Contractor was installing underground electric and telephone lines when they dented our pipe with a backhoe.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2020-12-07 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | LINCOLN CONSTRUCTION | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Trenching with backhoe for electric conduit install and damaged 2 inch plastic main
Southern California Gas Company | N | ORANGE | ANAHEIM | 2020-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 44 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | WESTERN CONSTRUCTION | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | ETD could not locate service with the location wire so he went by measurements, Service history use incorrect by by over 24 inch. The contractors failed to contact us while potholing to inform us they could not find our pipe giving us the opportunity to use otherï¿½ methods of location our service line.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2020-03-02 | Third party excavation damage | A service line with an excess flow valve installed | Steel | Hand Tools | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JUAN LOPEZ | FRESNO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | steel service damage when digging drain trenchï¿½
Southern California Gas Company | N | ORANGE | ANAHEIM | 2020-12-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | SPARTA FENCE | FULLERTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | digging to install a post
Southern California Gas Company | N | ORANGE | ANAHEIM | 2020-08-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | LINCOLN CONSTRUCTION | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | LCT COULD NOT PROVIDE USA NUMBER, DIGGING COMPANY FAILED TO USE CAUTION WHILE EXPOSING GAS LINE, DIGGING TO INSTALL ELECTRICAL.ï¿½ Service was marked correctly however contractor could not provide USA number when asked.ï¿½ Service may have been previously marked.ï¿½ï¿½
Southern California Gas Company | N | ORANGE | ANAHEIM | 2020-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | OUTSOURCE UTILITIES | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | hit service while potholing the find depth
Southern California Gas Company | N | ORANGE | ANAHEIM | 2020-06-13 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | ANAHEIM | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Gas Service hit by shovel by home owner, No USA called.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2020-10-28 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | CALIFORNIA BORING | ANAHEIM | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | Cal Bore hit a 0.5 inch plastic service that could not be located while doing work for our contractors NPL
Southern California Gas Company | N | ORANGE | ANAHEIM | 2020-04-24 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  |  | NA | CABLE COM LLC | ANAHEIM | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor bore into unmarked service. Locator failed to do exploratory work and did not see curb meter box of damage service.ï¿½
Southern California Gas Company | N | ORANGE | ANAHEIM | 2020-12-18 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | NPL | CERRITOS | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor bored into 0.5 inch plastic service while replacing service.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2020-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 0.75 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HHS COMMUNICATIONS | AZUSA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Third party contractor installing street lighting hit and damaged our service while directional boring.
Southern California Gas Company | N | ORANGE | BREA | 2020-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | H P MOBILE GEOCHEMISTRY INC | CARLSBAD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Excavator dug prior to valid start date.ï¿½ The area had not been marked yet.ï¿½ contractor hit 2 inch service and water line resulting in gas entering building requiring an evacuation.ï¿½ï¿½
Southern California Gas Company | N | ORANGE | BREA | 2020-09-17 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 53 |  | BIG BEN ENGINEERING | IRVINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor did not hand dig.
Southern California Gas Company | N | ORANGE | BREA | 2020-03-05 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | AVALON BAY | EMERYVILLE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | On 3 05 20 while digging a trench with a backhoe Sean Thomas employee damage a three inch gas main ï¿½ Sean stated that the gas main was just installed days prior and that they knew it was there ï¿½ He said that he instructed his employee to di six inches but he employee dug down 18 inches damaging the gas main Sean also said that they tried to shut off the gas by turning the curb valve 0.5inch a turn but it began to just spin ï¿½ SCG supervisor Jerry Jones explained that the valve was a 1 4 turn valve and that they had damaged the valve by over turning it ï¿½ Jones also explained that they should have called Dig Alert to get a USA ticket ï¿½ SCG crew arrived on scene and made permanent repairs to the main ï¿½ Another crew had to return at a later date to replace the damaged curb valve
Southern California Gas Company | N | ORANGE | BREA | 2020-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ARIZONA PIPELINE | CORONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Arizona Pipeline hit a plastic service while hand digging for Edison. service line was marked incorrectly, broken or missing wire.
Southern California Gas Company | N | ORANGE | BREA | 2020-07-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | SNYDER LANKSTON | IRVINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | dug with backhoe over known plastic substructure.ï¿½
Southern California Gas Company | N | ORANGE | BREA | 2020-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | STEPHEN DORECK EQUIPMENT RENTALS | PICO RIVERA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor installing water hit unmarked cutback serviceï¿½with backhoe.ï¿½ Service history and GIS both show gas line to be fully abandoned.
Southern California Gas Company | N | ORANGE | BUENA PARK | 2020-02-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | POWER PRO PLUMBING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber damaged riser and phone line while working ï¿½ No USA called ï¿½
Southern California Gas Company | N | ORANGE | CAPISTRANO BEACH | 2020-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | CAPISTRANO BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hitline damage , no USA. Crew and supervisor explained to contractor the importance in calling 811
Southern California Gas Company | N | ORANGE | CORONA DEL MAR | 2020-02-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | TIGHT QUARTERS | SANTA ANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No Valid USA ticket
Southern California Gas Company | N | ORANGE | CORONA DEL MAR | 2020-01-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 46 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NIV CONSTRUCTION | ORANGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Permanent repairs completed.
Southern California Gas Company | N | ORANGE | CORONA DEL MAR | 2020-05-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 46 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | JASMINE CREEK HOL | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was replacing sprinkler lines.ï¿½ Found our service to be damaged.ï¿½ Found steel hose clampsï¿½around a piece of copper pipe inside our facility.
Southern California Gas Company | N | ORANGE | CORONA DEL MAR | 2020-01-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 46 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NIV CONSTRUCTION | ORANGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | ORANGE | CORONA DEL MAR | 2020-11-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 46 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | EDWARD SAMEN | CORONA DEL MAR | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA Requested, Customer Digging For A Trench
Southern California Gas Company | N | ORANGE | CORONA DEL MAR | 2020-05-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 46 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | BEST BORING BURSTING | COSTA MESA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator fail to maintain clearance after verifying markings. The Crew and Sup explained to contractor the importance of maintain clearance after verifying substructures
Southern California Gas Company | N | ORANGE | CORONA DEL MAR | 2020-08-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 46 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ACCO ENGINEERED SYSTEMS | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor trenching with backhoe to install water line hit our service.
Southern California Gas Company | N | ORANGE | CORONA DEL MAR | 2020-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 46 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MIKE KILBRIDE LTD | NEWPORT BEACH | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor trenching with backhoe to install electric conduit.
Southern California Gas Company | N | ORANGE | COSTA MESA | 2020-11-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TCI ENEGINEER | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor is liable did not call a USA while using auger
Southern California Gas Company | N | ORANGE | COSTA MESA | 2020-12-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | JASON HARRIS | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged expose STL service while cutting out roots . Gas migrated underneath structure and one person was evacuated . Company crew controlled gas and aerated gas from foundation . Supervisor explained to contractor the importance of being careful while working around expose gas lines.
Southern California Gas Company | N | ORANGE | COSTA MESA | 2020-05-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BECKCO DEMOLITION | POMONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA NUMBER PROVIDED, CONTRACTOR WAS GRADING
Southern California Gas Company | N | ORANGE | COSTA MESA | 2020-03-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | HOME TEAM YARDS | HUNTINGTON BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | damaged pe service NO USA
Southern California Gas Company | N | ORANGE | COSTA MESA | 2020-11-19 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 59 | 44 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ALL AMERICAN ASPHALT | CORONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | The contractors were removing asphalt for new paving the pipe was exposed already.
Southern California Gas Company | N | ORANGE | COSTA MESA | 2020-06-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | I WIRE SO CAL | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plastic service hit with trencher while digging drain trench. No Valid USA.
Southern California Gas Company | N | ORANGE | COSTA MESA | 2020-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | GWENCO CONSTRUCTION | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Third party contractor excavating for water main hit 1 inch steel service.ï¿½ Service was unmarked and not in GIS.ï¿½ Service fed apartment building which GIS showed it was fed off of 2 inch plastic on Bear St.ï¿½
Southern California Gas Company | N | ORANGE | COSTA MESA | 2020-03-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | GALLAGHER CONSTRUCTION | COSTA MESA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor damaged correctly marked service while attempting to hand expose
Southern California Gas Company | N | ORANGE | COSTA MESA | 2020-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | PAR ELECTRICAL | ORANGE | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Excavator dug prior to valid start datetime . Crew and Supervisor explained the importance of making positive communication before digging if not marked.
Southern California Gas Company | N | ORANGE | COSTA MESA | 2020-08-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | STILLWELL CONSTRUCTION INC | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1 service hit with backhoe while digging for telephone lines.ï¿½
Southern California Gas Company | N | ORANGE | COSTA MESA | 2020-04-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JV CONSTRUCTION | CANOGA PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | USA ON FILE, CONTRACTOR FAILED TO DIG WITH CAUTION WHILE EXPOSING GAS LINE
Southern California Gas Company | N | ORANGE | COSTA MESA | 2020-07-14 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 55 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | TIGHT QUARTERS INC | SANTA ANA | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was grading an empty residential lot when gas service was hit. Dug prior to valid start datetime.
Southern California Gas Company | N | ORANGE | COSTA MESA | 2020-08-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | INDEPENDENT CONTRACTOR | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA was called in. Independent contractor working for homeowner was trenching for electrical when gas line was hit with a pickaxe.
Southern California Gas Company | N | ORANGE | COSTA MESA | 2020-02-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | GERRY GONZALEZ | COSTA MESA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Homeowner hit service while digging to install a pool Shovel hit
Southern California Gas Company | N | ORANGE | CYPRESS | 2020-03-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | NA | POMONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Company contractor struck 2 plastic main with backhoe No marks visible in work area
Southern California Gas Company | N | ORANGE | CYPRESS | 2020-12-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | CYPRESS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA.ï¿½ Homeowner was digging to remove an old fence and install a new fence.ï¿½ He hit the service with a shovel.
Southern California Gas Company | N | ORANGE | CYPRESS | 2020-10-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | DOMINGUEZ GENERAL ENGINEERING | POMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 3rd partyï¿½
Southern California Gas Company | N | ORANGE | CYPRESS | 2020-03-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | PRIME BORE | ONTARIO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor called claiming they could smell gas and hear hissing Contractor said they didn t hit anything They think it was disturbed somehow
Southern California Gas Company | N | ORANGE | DANA POINT | 2020-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | SUPREME MASONRY | MISSION VIEJO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor installed GasElectric hit line. Contractor didnt think stub went that far into property. USA was not called. Repaired by installing new cap.
Southern California Gas Company | N | ORANGE | DANA POINT | 2020-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ALS ENGNERRING | LAGUNA NIGUEL | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | USA ticket was expired and contractor hit gas main with backhoe without exposing it. They dug all the way down with backhoe and did not HAND expose it
Southern California Gas Company | N | ORANGE | DANA POINT | 2020-09-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SHORELINE CONTRUCTION CUSTOM HOME | SAN CLEMENTE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | USA WAS NOT CALLED, CONTRACTOR WAS DIGGING FOR A RETAINING WALL HIT WITH ELECTRIC CLAY SPADE
Southern California Gas Company | N | ORANGE | DANA POINT | 2020-11-04 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | L AND S CONSTRUCTION | ORANGE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor working to install water lines.
Southern California Gas Company | N | ORANGE | DANA POINT | 2020-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 16 |  | LEWIS ELECTRIC | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged plastic service with a backhoe while digging trench for electric and gas utilities. Marks were visible and accurate.
Southern California Gas Company | N | ORANGE | DANA POINT | 2020-07-10 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | A M ORTEGA | CORONA | CA | Y | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | AMO forgot about the branch and bored into service. Branch service was not located out. AMO knows that they were at fault.
Southern California Gas Company | N | ORANGE | DANA POINT | 2020-12-17 | Third party excavation damage | A service line with an excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SOCO BUILDERS | SANTA ANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | USA Marks were good. Homeowner and contractor hit a STL cap and it was leaking crew just changed out the cap. Homeowner contractor also pulled on another service for across the street and we had to replace it. Locator marks were GOOD
Southern California Gas Company | N | ORANGE | FOUNTAIN VALLEY | 2020-05-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ESSENTIAL DESIGN ENIVATOR | GARDEN GROVE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Remodeling contractor hit plastic service with a pick axe.ï¿½ No USA was called in.ï¿½ Crew permanently repaired service, fire on scene.
Southern California Gas Company | N | ORANGE | FOUNTAIN VALLEY | 2020-04-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CONCEPT PAVINE SOLUTIONS INC | ORANGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 0.50 plastic service with mini excavator
Southern California Gas Company | N | ORANGE | FULLERTON | 2020-03-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 40 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | none
Southern California Gas Company | N | ORANGE | FULLERTON | 2020-12-11 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | NPL | BREA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit line while exposing SMC.
Southern California Gas Company | N | ORANGE | FULLERTON | 2020-01-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ARIZONA PIPLINE | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Could not tell if marks were within 2 feet becauseï¿½existing marks at damage location had been removed and other marks were 10 away along a curved roped service ï¿½ Excavator states they were removing soil and trying to expose buried facility using the excavator ï¿½ Admitted to not hand digging during excavation ï¿½ï¿½ï¿½ï¿½
Southern California Gas Company | N | ORANGE | FULLERTON | 2020-11-12 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | SULLY MILLER COMPANY | BREA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor using track hoe, hit steel service, did not use proper excavating practices while using trenching. marks were accurate. did not hand expose service
Southern California Gas Company | N | ORANGE | FULLERTON | 2020-06-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BRISENO LANDSCAPE CONSTRUCTION INC | FULLERTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CUSTOMER DIGGING FOR FOOTINGS FOR A RETAINING WALL
Southern California Gas Company | N | ORANGE | FULLERTON | 2020-05-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | BIG BEN | IRVINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator claims the marks were covered by debris and he did not see them.ï¿½ Service was struck with a back hoe.ï¿½ marks were dead on.ï¿½ï¿½
Southern California Gas Company | N | ORANGE | FULLERTON | 2020-09-17 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NPL | BREA | CA | Y | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NPL damaged gas service while excavating to expose it
Southern California Gas Company | N | ORANGE | FULLERTON | 2020-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ROYAL COMMUNICATION GROUP | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Telecom sub hand digging for junction box placement. Hard dirt. Hit service line. Actual service location within 2 tolerance zone of mark.
Southern California Gas Company | N | ORANGE | FULLERTON | 2020-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ARTISAIN OUTDOOR | COSTA MESA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | none
Southern California Gas Company | N | ORANGE | FULLERTON | 2020-08-05 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Trencher | 0.75 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | CORBEL COMMUNICATIONS INDUSTRIES LLC | AUSTIN | TX | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Trenching to install communication line.
Southern California Gas Company | N | ORANGE | FULLERTON | 2020-07-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CORBEL COMM IND | STANTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Corbel Communications Contractor trenched and hit 0.5 inch service.
Southern California Gas Company | N | ORANGE | FULLERTON | 2020-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | GRFCO INC | PERRIS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Tickets Had Expired. Contruction Company Excavation A Trench For The City Of Fullerton
Southern California Gas Company | N | ORANGE | FULLERTON | 2020-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JRN ENGINEERING | RANCHO CUCAMONGA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | used backhoe to grade at curbï¿½and gutter. Didnt pothole marked main and service and tore off 2 inch service tee.ï¿½
Southern California Gas Company | N | ORANGE | FULLERTON | 2020-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GRFCO INC | MORENO VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor installing sewer hit line with shovel.
Southern California Gas Company | N | ORANGE | FULLERTON | 2020-11-17 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CORBEL COMMUNICATIONS | AUSTIN | TX | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor did not expose the pipe by hand digging as required. Advised them they need to hand dig and if there are any questions on markings then they need to call us and we would answer their questions.ï¿½ Continuing issue with this contractor refusing to hand dig.ï¿½ï¿½
Southern California Gas Company | N | ORANGE | FULLERTON | 2020-10-30 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Trencher | 0.75 | 44 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | CORBEL COMMUNICATIONS INDUSTRIES | AUSTIN | TX | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 0.75 inch steel service was miss marked by 14 feet where the crew installing communication lines hit us with a micro trencher Ditch Witch
Southern California Gas Company | N | ORANGE | GARDEN GROVE | 2020-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TUI UNDERGROUND UTILITY CONTRACTOR | SAN JACINTO | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 2 inch stub to service in private property.ï¿½
Southern California Gas Company | N | ORANGE | GARDEN GROVE | 2020-11-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CHI CONSTRUCTION | ANAHEIM | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | While digging for new sewer trench, contractor hit unmarked stub service. locator did not mark service, service was not on GIS print.ï¿½
Southern California Gas Company | N | ORANGE | GARDEN GROVE | 2020-10-07 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | RJ NOBLE COMPANY | ORANGE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor called for locate, then removed asphalt that had location marks. customer was aware of location of gas line, was under the impression it was deeper.ï¿½
Southern California Gas Company | N | ORANGE | GARDEN GROVE | 2020-06-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | NEXT CONSTRUCTION | GARDEN GROVE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Developer was digging to install water line when svc was hit.
Southern California Gas Company | N | ORANGE | GARDEN GROVE | 2020-03-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 4 |  | BLANCO CONSTRUCTION INC | BUENA PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Blanco Construction was potholing for edison by hand when 0.5inch ips PA service was damage with shovel ï¿½
Southern California Gas Company | N | ORANGE | GARDEN GROVE | 2020-12-01 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  | 22 |  | CHI CONSTRUCTION | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor working for the city of Garden grove damaged 2 inch PLA main with backhoe, gas facilities were marked out properly by company locator.ï¿½
Southern California Gas Company | N | ORANGE | GARDEN GROVE | 2020-10-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | GARDEN GROVE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner and Laborers hit service line with shovel while trenching for water lines.ï¿½
Southern California Gas Company | N | ORANGE | GARDEN GROVE | 2020-03-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  | 1 |  | CITY OF GARDEN GROVE | GARDEN GROVE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damage 2 plastic svc with backhoe when digging for water service
Southern California Gas Company | N | ORANGE | GARDEN GROVE | 2020-02-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SO CAL FENCING SOLUTIONS | SANTA ANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 0.5inch service with post hole digger while excavating to install fence in private property
Southern California Gas Company | N | ORANGE | GARDEN GROVE | 2020-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ALAMEDA CONSTRUCTION SERVICES INC | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Our contractor that installs bollards damaged 0.5 inch IPS service with shovel
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2020-02-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BURKE MASONERY | SANTA ANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1 inch plastic service.
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2020-10-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TWIN OAKS | WRIGHTWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscaping company digging with trencher, hit service line. EFV stopped flow of gas, contractor claims yellow flags were in place.ï¿½
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2020-11-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | PAULUS ENGINEERING | ANAHEIM | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | contractor damaged 2 inch service while digging with excavator. Service runs through large dirt lot for 5050 Skylab. Service location on GIS was incorrect.
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2020-02-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | GRASON CONSTRUCTION | FOUNTAIN VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA 3rd party damaged service Claims he stepped on it Cut back service Not occupied Unsafe to reinstate due to debris and material
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2020-09-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HUMBERTO REYES | HUNTINGTON BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractors sub plumber hit line with hand tool.
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2020-11-06 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SERGIO CERDA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging for a Fence post, 3rd party contractor damaged gas line. permanent repairs made by distribution crew.ï¿½
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2020-02-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CALIFORNIA HOME CONSTRUCTION | HUNTINGTON BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | none
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2020-11-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | J A FENCE | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Fencing contractor damaged 0.5 inch plastic service while installing a fence. No USA
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2020-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | HUNTINGTON BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged 0.50 inch cts service while digging
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2020-08-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | KURTIS BISTTLGUR | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging for post for fence
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2020-09-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | UC LANDSCAPER | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit line, Third party damage Per Incident Commander Daniel Mariscal At 1125 Fire department was notified of hit 0.5 IPS plastic service at 226 19th St, Huntington Beach. Service hit by irrigation contractor with a backhoe. Fire department arrived on scene at approximately 1130 and evacuated 5 units. Partial street closure, no media or other emergency services on scene. No injuries or fatalities reported. Gas leak controlled at 1420, with Repairs completed at 1526. Evacuations lifted and all streets reopened at 1500. Incident commander Daniel Mariscal CSF FOSII Garden Grove base arrived on scene at 1400 and departed at 1530.
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2020-09-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BRASH ENGINEERING | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Gas service mistaken for root and hit with shovel.
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2020-04-01 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NPL | BREA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Company contractor damaged 0.50 inch plasticï¿½service with shove while potholing.
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2020-02-28 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 50 | 44 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 7 |  | GRP CONSTRUCTION | BUENA PARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit 2 gas main with breaker attached on backhoe No USA
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2020-05-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JOSE OSC LANDSCAPING | HUNTINGTON BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 0.50 inch plastic service while digging to install a tree.
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2020-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ELEVEN WESTERN BUILDERS | ESCONDIDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party contractor damaged service riser while demolishing a wall.ï¿½
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2020-11-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 5 |  | GRP CONTRACTORS INC | BUENA PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor digging to install electrical conduit, failed to use caution while exposing gas line
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2020-09-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ARIZONA PIPELINE CO | CORONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged 0.5 inch plastic service with mini excavator.
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2020-12-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | BEACH CITY FENCE | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 0.5 inch plastic service with posthole digger while installing fence
Southern California Gas Company | N | ORANGE | IRVINE | 2020-03-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ROBERT GUERRERO | BUENA PARK | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Hand digging for conduits
Southern California Gas Company | N | ORANGE | IRVINE | 2020-05-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 16 |  | PRO TECH TURF | ORANGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor were removing swings from play area and pulled service damaging it . Crew and supervisor explained the Importance of 811
Southern California Gas Company | N | ORANGE | IRVINE | 2020-11-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JAG UTILITY CONSTRUCTION INC | IRVINE | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Contractor dug before 48 hour, Locator was on site to mark service. contractor hit service and bent back service with tape.
Southern California Gas Company | N | ORANGE | IRVINE | 2020-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 5 |  | AIR JET COMMUNICATIONS | POMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Party Contractor hit service digging with shovel installing communications.
Southern California Gas Company | N | ORANGE | IRVINE | 2020-09-02 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | ACCESS GENERAL CONSTRUCTION | CORONA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Company contractor damaged plastic service while hand digging to install a bollard to protect the MSA.
Southern California Gas Company | N | ORANGE | IRVINE | 2020-04-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 44 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GINGER MASONARY | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor excavating for wall hit and broke our 1 inch plastic service.ï¿½ No USA was called in.
Southern California Gas Company | N | ORANGE | IRVINE | 2020-09-29 | Third party excavation damage | Riser | Polyethylene Pipe | Not Available | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PACIFIC LINE | LAGUNA NIGUEL | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No | No damage to SUOF. | No damage to SUOF. | none
Southern California Gas Company | N | ORANGE | IRVINE | 2020-05-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | ALPHA REGIONAL INC | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumbing contractor hit a 0.50 inch PE service with a shovel while digging to expose an irrigation water leak.ï¿½ The contractor did not contact USA prior to beginning excavation.
Southern California Gas Company | N | ORANGE | IRVINE | 2020-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JAG UTILITY CONSTRUCTION INC | VISTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Our
Southern California Gas Company | N | ORANGE | IRVINE | 2020-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2222 |  | 8 |  | 4WEST PIPELINE INC | QUAIL VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Trenching with backhoe to install conduit.
Southern California Gas Company | N | ORANGE | IRVINE | 2020-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CALIFORNIA PACIFIC HOMES | IRVINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA was called in by contractor,ï¿½contractor hit service.
Southern California Gas Company | N | ORANGE | IRVINE | 2020-11-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | VALENTIN ALVAREZ | BREA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | DIGGING TO INSTALL COMMUNICATIONS, FAILED TO USE CAUTION WHILE DIGGING
Southern California Gas Company | N | ORANGE | IRVINE | 2020-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | URBAN CONCRETE | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor did not call in for USA and while grading for foundation they hit our 0.5 inch IPS service.
Southern California Gas Company | N | ORANGE | IRVINE | 2020-11-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CORBEL COMMUNICATION INDUSTRY | STANTON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor digging for communication lines hit line with hand tools.
Southern California Gas Company | N | ORANGE | IRVINE | 2020-03-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | NA |  | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | no USA called in and contractor hit riser while grading yard with backhoe
Southern California Gas Company | N | ORANGE | IRVINE | 2020-08-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | IRVINE | CA | N | Y | Yes | Excavation occurred on private property by a non-contractor. | Yes | Yes | No | Yes | Yes | Homeowner grading for foundation hit line with shovel.
Southern California Gas Company | N | ORANGE | IRVINE | 2020-03-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor doing a remodel hit our 0.5inch plastic service with a shovel causing the line to rupture ï¿½ Contractor did not call 811 Dig alert prior to digging
Southern California Gas Company | N | ORANGE | IRVINE | 2020-07-08 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NPL | BREA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | As experience crew member was shaving hard soil off the side of the pothole to expose the 0.5 IPS, shovel struck the side of the Aldyl A pipe causing small nicked.
Southern California Gas Company | N | ORANGE | IRVINE | 2020-05-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CASEY SPOLAR | CORONA | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Contractor for SoCalEdison hit line with backhoe installing electricity.
Southern California Gas Company | N | ORANGE | IRVINE | 2020-12-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | GOTHIC LANDSCAPE | RIVERSIDE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor dug prior to USA becoming valid.ï¿½ They also did not pothole the service before using an excavator to dig a large hole for a tree.
Southern California Gas Company | N | ORANGE | IRVINE | 2020-05-01 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CAL BORE | NA |  | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | Unmarked cut back stub, no tracer wire and not in CIS.ï¿½
Southern California Gas Company | N | ORANGE | IRVINE | 2020-10-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | PACIFIC WEST COMMUNICATIONS | SAN DIMAS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor bored and damaged 2 inch PLA service feeding complex . Improper potholing by excavator . Mark visible and accurate by SCG .
Southern California Gas Company | N | ORANGE | IRVINE | 2020-05-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NA | IRVINE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was hammering a post to hang his water hose without calling USA . He damaged service line which caused gas to migrate in home . Family was evacuated . Crew and supervisor explained to homeowner the importance of 811
Southern California Gas Company | N | ORANGE | IRVINE | 2020-02-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | A ELECTRICIAN | RESEDA | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Pipe damaged with grounding rod Trying to install solar
Southern California Gas Company | N | ORANGE | IRVINE | 2020-12-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JERRY FEW SO CAL BOBCAT | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor that was digging did not have a USA. Contractor hit gas service with backhoe.
Southern California Gas Company | N | ORANGE | IRVINE | 2020-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SCHOFFEITT PIPELINE INC | IRVINE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Developer hit 1 inch plastic stubbed service in a new business tract.ï¿½ USA was on file, hit newly installed plastic stub.ï¿½ Stub was not yet input into GIS.
Southern California Gas Company | N | ORANGE | IRVINE | 2020-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BRIGHTVIEW | FOUNTAIN VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor using ditch witch to excavate a trench for shoring damaged our plastic service. Upon arrival, there were no marks present. was originally completed on 6122020 and was renewed by the contractor several times however, they did not request remarks. The contractor failed to maintain marks.
Southern California Gas Company | N | ORANGE | IRVINE | 2020-05-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SHOFFEITT PIPLINE | LAKE FOREST | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Developer hit our stubbed plastic service.ï¿½ Received notification from a SCG contractor that the damaged the facility.ï¿½ Crew repaired stub.
Southern California Gas Company | N | ORANGE | LA HABRA | 2020-04-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | LA HABRA | CA | N | Y | Yes | Excavation occurred on private property by a non-contractor. | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | digging for pool gas line in private property. Expired USA ticket. Owner did not maintain marks or call for remarks
Southern California Gas Company | N | ORANGE | LA HABRA | 2020-11-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | TORRES PLUMBING | SANTA ANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit service line while installing sewer line. Digging without USA.
Southern California Gas Company | N | ORANGE | LADERA RANCH | 2020-04-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PLATINUM LANDSCAPE | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor did not haveï¿½a USA and while digging with a backhoe for a planter they hit 0.50 inch service.
Southern California Gas Company | N | ORANGE | LADERA RANCH | 2020-01-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NEW HOMES COMPANY | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor did not keep proper clearance while digging with backhoe
Southern California Gas Company | N | ORANGE | LADERA RANCH | 2020-08-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BRIGHTVIEW LANDSCAPE DEVELOPMENT | FOUNTAIN VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Party Contractor hit line while grading.
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2020-03-27 | Third party excavation damage | Meter | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | none
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2020-12-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JOUD CONSTRUCTION | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor did not call in for a USA Ticket and in result they hit our gas service.
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2020-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 8 |  | THE TRADESMAN ELECTRIC | SANTA MARGARITA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Noï¿½USA.ï¿½ Contractor hit a 1 inch PE service with a shovel while digging to install conduit for electrical lines.
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2020-09-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JOHN DELANGIS | LAGUNA BEACH | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor was digging with backhoe and forgot service was there and hit it. All marksflags were visible.ï¿½
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2020-10-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JETT X | SAN CLEMENTE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged plastic cutback service while trenching for electric utilities. GIS does not show a cutback service going to property, service history has cutback service addressed to incorrect address number, and service location measurements are vague. Service history indicates that sketch is required to accurately measure service location, however a records search in Anaheim was unable to locate the sketch. There was no EM ball installed. There was a G on the curb however, notes from ticket number indicate that there was no delineation.
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2020-10-26 | Operator excavation damage | Main | Steel | Miscellaneous/Other | 2 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | TEICHERT PIPELINES | NA |  | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Teichert tapped through 3 inch STL casing that has 2 inch STL main inside of it. They were replacing a CP10 service.
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2020-10-03 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NPL | MIRA LOMA | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | SCG company contractor damaged SCG facility while digging out service to alter
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2020-03-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ANCHOR BUILDING | GARDEN GROVE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged our plastic service with hand tools No USA
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2020-10-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | LAGUNA BEACH | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA.ï¿½ Homeowner was digging a trench for a drain line and hit a 0.5 inch PE service with a shovel.
Southern California Gas Company | N | ORANGE | LAGUNA HILLS | 2020-07-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | LAGUNA HILLS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged 0.5 inch service while installing fence post.
Southern California Gas Company | N | ORANGE | LAGUNA HILLS | 2020-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SUPERIOR PLUMBING | LAGUNA HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | USA . Company crew and Supervisor explained to contractor the importance of calling 811
Southern California Gas Company | N | ORANGE | LAGUNA HILLS | 2020-04-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | REID CONCRETE CONSTRUCTION INC | MISSION VIEJO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor did not have a USA and while digging they hit 0.50 inch service.
Southern California Gas Company | N | ORANGE | LAGUNA NIGUEL | 2020-04-22 | Third party excavation damage | Main | Steel | Boring Equipment | 4 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 6 |  | CITY BORE COMMUNICATION | RIALTO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Locator said he got a signal but was weak where the damage occurred. Locator tried to locate passed an insulator that being the reason he got weak signal. Locator will get note to file.
Southern California Gas Company | N | ORANGE | LAGUNA NIGUEL | 2020-07-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | DEGENNARO PLUMBING | ORANGE | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor did NOT CALL IN FOR USA, so they hit gas service not knowing where it was at.
Southern California Gas Company | N | ORANGE | LAGUNA NIGUEL | 2020-08-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | LAGUNA NIGUEL | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor didnt call for a USA and while digging trench for power in apartment complex they hit gas service.
Southern California Gas Company | N | ORANGE | LAGUNA NIGUEL | 2020-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | S S MECHANICAL | MISSION VIEJO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging to repair leaks on a water line.ï¿½
Southern California Gas Company | N | ORANGE | LAGUNA NIGUEL | 2020-02-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | ORANGE | LAKE FOREST | 2020-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | ENR DEMOLITION | BELLFLOWER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Installing a sewer line.ï¿½
Southern California Gas Company | N | ORANGE | LAKE FOREST | 2020-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | LAKE FOREST | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA was called and and landscaping hit 0.5 inch IPS service while trying to remove tree in front of house.
Southern California Gas Company | N | ORANGE | LOS ALAMITOS | 2020-08-04 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | LOS ALAMITOS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner cut service with concrete saw during construction
Southern California Gas Company | N | ORANGE | LOS ALAMITOS | 2020-05-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RJL BUILDER | DOWNEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor used sawzall to cut root and damaged service
Southern California Gas Company | N | ORANGE | MISSION VIEJO | 2020-12-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JAVIER DENA | MISSION VIEJO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor did have a USA and locator did mark out service but while contractor was digging for power they hit gas service with a shovel. contractor did know that gas was there, they just hit it on accident. Contractor knows they are at fault.
Southern California Gas Company | N | ORANGE | MISSION VIEJO | 2020-02-25 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | LOS GATOS LANDSCAPE | SANTA ANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor did not call in for USA and they hit our gas main
Southern California Gas Company | N | ORANGE | MISSION VIEJO | 2020-01-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | SANTA MARGARITA WATER DISTRICT | SANTA MARGARITA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor did not call us back out to try and locate again they dug out hole with backhoe and not a shovel
Southern California Gas Company | N | ORANGE | MISSION VIEJO | 2020-06-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PATRIOT PIPELINE | WILDOMAR | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | All marks and flags were visible, contractor didnt keep proper clearance while digging with a backhoe.
Southern California Gas Company | N | ORANGE | MISSION VIEJO | 2020-09-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PG BUILDERS LANDSCAPE INC | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | There was NO USA, contractor did not call in for one. While they were digging to install brick wall they hit 0.5 inch IPS service that resulted in 2 houses losing gas STD and Branch.
Southern California Gas Company | N | ORANGE | MISSION VIEJO | 2020-11-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | STEVE GILLETT | SAN CLEMENTE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged plastic service with shovel while trenching to install a new electric service.
Southern California Gas Company | N | ORANGE | MISSION VIEJO | 2020-04-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | VCI CONSTRUCTION LLC | UPLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | Contractor dug outside of Delineated area and once they dug down they cut 2 inch Service with a grinder.
Southern California Gas Company | N | ORANGE | MISSION VIEJO | 2020-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | 5T2 PIPELINE INC | VISTA | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Contractor dug prior to USA being legal.ï¿½ No marks had been provided at the time of damage, because ticket was not yet valid.
Southern California Gas Company | N | ORANGE | MISSION VIEJO | 2020-12-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 48 |  | OFFICIAL | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | No | Contractor did have a USA. Talked to locator to see what happen and he said he just did not see that service on GIS, that he just over looked it. locator knows he missed up with this one, it was an honest mistake. Locator will get pulled into office and talked to and get a note to file. we will go over policy with him about locating and using ALL resources.ï¿½
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2020-06-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | PIERRE LANDSCAPE | BALDWIN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service lineï¿½was damage while hand digging during tree removal. Line was exposed, they hit service with tunnel bar.ï¿½
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2020-05-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | WPE LANDSCAPE INC | IRVINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor hit 1 inch PE service with mini excavator.ï¿½ No USA was called.
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2020-03-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 55 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HBA INC | ANAHEIM | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | all locations requested on USA ticket were marked except this one Contractor was asked to call for remarks and ask for a no show since all other locations were marked he needs a positive response on all locations
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2020-11-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ASPLUNDH CONSTRUCTION | ANAHEIM | CA | N | N | Yes | Yes | No damage to SUOF. | Yes | No damage to SUOF. | Yes | Yes | Contractor hitï¿½ stub that was not abnd . Crew arrivedï¿½controlled gas and abnd stub .ï¿½
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2020-05-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ARIZONA PIPE LINE | CORONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Third party contractor hit and bent 0.75 inch steel service.ï¿½ Service was unmarked and not recorded properly on GIS.
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2020-05-07 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ASPLUND CONSTRUCTION CORP | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Per contractorContractor found 0.50 inch abandoned stubbedï¿½copper service.ï¿½ Contractor dug around copper service and then bent it back by hand to give themselves more room to excavate.ï¿½ï¿½Inï¿½the process of bending the copper service, they cracked damaged it cause it to rupture and leak.ï¿½
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2020-03-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ALCANTRA PLUMBING | ARTESIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor installing water service to residence cut into our newly installed 1 PE service ï¿½ They hit and cut our line with a saw they were using to cut their PVC line placed withing 2 on top of our service ï¿½ Contractor did not call 811 prior to excavating or moving soil
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2020-08-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 46 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | NEWPORT BEACH | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA WAS REQUESTED, CUSTOMER DIGGING TO INSTALL FENCE POST
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2020-09-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 46 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NATIVE LANDSCAPING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscape contractor damaged 0.5 inch service
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2020-10-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 46 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | INSTANT LANDSCAPE | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party landscape workers damaged line
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2020-01-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 12 |  | HBA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | no USA
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2020-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | PIERRE LANDSCAPING | IRWINDALE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA REQUESTED CONTRACTOR WORKING FOR CUSTOMER PLANTING PALM TREES
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2020-11-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 46 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | EARTHCO COMM LANDSCAPING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging with back hoe and rip out the service line. No USA . Crew and supervisor explained the importance of call 811
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2020-03-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ASPLUNDH CONSTRUCTION CORP | ANAHEIM | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor hit unmarked 1 plastic service with a mini excavator while digging trench to install Edison conduit ï¿½ GIS shows the service in the proper location and a good locate is possible if going direct
Southern California Gas Company | N | ORANGE | NEWPORT COAST | 2020-02-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | REDLINE GRADING EXCAVATING | NEWPORT BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contactor damaged unmarked gas facility while hand digging for new electric line USA was not called
Southern California Gas Company | N | ORANGE | NEWPORT COAST | 2020-10-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 46 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JUAN POZA | NORTH HOLLYWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hitline no USA . Customer was removing tree stump and pulled service .Crew and Sup explained to contractor the importance in calling 811
Southern California Gas Company | N | ORANGE | ORANGE | 2020-08-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | PATRIOT PIPELINE | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor hit 2 inch PE service with excavator.ï¿½ Damage resulted in a response from Orange Fire and PD.ï¿½ Resulting in the construction site being evacuated and neighboring business to be evacuated.ï¿½ Traffic was re routed on Town and Country.ï¿½ Contractor failed to notify USA Dig Alert prior to excavating.
Southern California Gas Company | N | ORANGE | ORANGE | 2020-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | LEONIDA BUILDERS INC | CANYON COUNTRY | CA | N | N | Yes | No damage to SUOF. | Yes | Yes | No | No damage to SUOF. | No damage to SUOF. | Contractor was demoing building.ï¿½ Building fell on top of our riser and caused an escape and blowing of gas.ï¿½ Our facility was located, however, there was no ticket on file for the address.
Southern California Gas Company | N | ORANGE | ORANGE | 2020-04-28 | Operator excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NPL CAL BORE | MIRA LOMA | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | UNABLE TO FIND USA TICKET IN CLICK inchNPL inch DOING WORK FOR GAS CO. CAL BORE DAMAGED 2 inch PLASTIC MAIN
Southern California Gas Company | N | ORANGE | ORANGE | 2020-07-17 | Operator excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 41 | 19 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 15001 |  |  | NA | NPL | CHINO | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | NPL foreman was machine excavating over a sewer lateral when he damaged a 2 inch gas main that was in the proposed running line.
Southern California Gas Company | N | ORANGE | ORANGE | 2020-12-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 1 |  | D O CONSTRUCTION | ORANGE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party hit 1 inch service line while excavating with hand tools.ï¿½
Southern California Gas Company | N | ORANGE | ORANGE | 2020-02-04 | Third party excavation damage | Meter | Steel | Backhoe/Trackhoe | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | SANTA ANA | CA | N | N | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | Contractor by owner was pulling a tree with a backhoe and snapped the gas line
Southern California Gas Company | N | ORANGE | ORANGE | 2020-08-21 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | NA | ORANGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was trenching driveway for a retaining wall and contractor cut service thinking it was customerï¿½ house line.
Southern California Gas Company | N | ORANGE | ORANGE | 2020-07-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DC DRILLING | RIVERSIDE | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Contractor boring hit 1 inch PE service while boring.ï¿½ Contractor dug before having a valid USA ticket.
Southern California Gas Company | N | ORANGE | ORANGE | 2020-04-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CONSCIENCE ENVIRONMENTS | YORBA LINDA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging around electrical box in front yard to lower box deeper in ground, while digging inside of box SVC was damage with shovel. No USA
Southern California Gas Company | N | ORANGE | ORANGE | 2020-07-27 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 3 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BIG BEN ENGINEERING | IRVINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | CUSTOMER WAS USING A BACKHOE AND PUSH DEBRIS INTO GAS PIPE
Southern California Gas Company | N | ORANGE | ORANGE | 2020-04-23 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | ORANGE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Property owner was removing tree stump with sawzall.ï¿½ Knicked 0.75 inch steal service that was under root that was being cut.
Southern California Gas Company | N | ORANGE | ORANGE | 2020-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | BEN VO | NA |  | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No | No damage to SUOF. | No damage to SUOF. | none
Southern California Gas Company | N | ORANGE | ORANGE | 2020-03-06 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Directional Drilling | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 3 |  | CABLE COMM | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 0.75inch steel svc hit with directional bore ï¿½
Southern California Gas Company | N | ORANGE | PLACENTIA | 2020-05-22 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ROCK WOOD CONSTRUCTION | SAN JUAN CAPISTRANO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | developer excavating hit new stub service.ï¿½ No USA
Southern California Gas Company | N | ORANGE | PLACENTIA | 2020-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ARMANDO SASUETA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | homeowner having drainage install in sideyard and didnt call USA. Damaged 0.75 steel svc while trenching for drainline
Southern California Gas Company | N | ORANGE | PLACENTIA | 2020-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | EMPIR PLUMBING | STANTON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | USA number not provided by contractor digging for grease interceptor gas migrated into facility evacuated construction workers in and around the building wire did not provide signal in the area signal jumped onto another substructure ï¿½
Southern California Gas Company | N | ORANGE | PLACENTIA | 2020-06-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ROCKWOOD CONSTRUCTION | SAN JUAN CAPISTRANO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | grading property and didnt pothole or call USA
Southern California Gas Company | N | ORANGE | PLACENTIA | 2020-11-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | PLACENTIA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was performing irrigation when gas line was hit withï¿½a backhoe. No USA . Company crew and Supervisor explained to contractor the important of 811
Southern California Gas Company | N | ORANGE | PLACENTIA | 2020-08-04 | Third party excavation damage | Main | Polyethylene Pipe | Not Available | 2 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GOLDEN STATE WATER COMP | PLACENTIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Southwest Waterï¿½Company hit gas line while repairing water leak.
Southern California Gas Company | N | ORANGE | PLACENTIA | 2020-11-14 | Third party excavation damage | Main | Steel | Hand Tools | 4 | 45 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 6 |  | METRO WATER DISTRICT OF CA | RIVERSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator struck line while exposing with hand tools
Southern California Gas Company | N | ORANGE | SAN CLEMENTE | 2020-12-08 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CITY OF SAN CLEMENTE | SAN CLEMENTE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | San Clemente Water Company knew our gas line was there and when they were pulling back there new water service they ripped off our 1 inch svc tee. They said they knew the main svc was there. All marks were within 2 feetï¿½
Southern California Gas Company | N | ORANGE | SAN CLEMENTE | 2020-05-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | WEB CONSTRUCTION | SAN CLEMENTE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 0.50 inch plastic service with a probing tool while trenching for a new electric service.
Southern California Gas Company | N | ORANGE | SAN CLEMENTE | 2020-05-22 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TEICHERT PIPELINES | CHINO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor for Teichert Pipelines was adjusting the accupunch with a tunnel bar when he punctured our service.
Southern California Gas Company | N | ORANGE | SAN CLEMENTE | 2020-11-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CHRIS KING CONSTRUTION INC | LAGUNA NIGUEL | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA was called in. Contractor was digging with a Postal Digger and struck service.
Southern California Gas Company | N | ORANGE | SAN CLEMENTE | 2020-03-03 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 4 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  |  | NA | VCI CONSTRUCTION | SAN MARCOS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged main Main did not locate correctly and measurements in GIS were incorrect Signal over locators marks was strong
Southern California Gas Company | N | ORANGE | SAN JUAN CAPISTRANO | 2020-07-23 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PACIFIC EXCAVATION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA WAS CALLED IN, contractor was digging with backhoe and resulting in them hitting our 2 inch PE gas main.
Southern California Gas Company | N | ORANGE | SAN JUAN CAPISTRANO | 2020-11-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MACIAS GARDENING | SAN PEDRO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA was called in, contractor was probing to find drain he was there to fix and struck service with probe.
Southern California Gas Company | N | ORANGE | SAN JUAN CAPISTRANO | 2020-11-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | SAN JUAN CAPISTRANO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | hit line by customer
Southern California Gas Company | N | ORANGE | SAN JUAN CAPISTRANO | 2020-05-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit line with shovel. House being remodeled and is vacant. Contractor digging for owner to run electrical. Contractor could not provide USA ticket number.ï¿½Line was marked but contractor said ticket was a few months old.
Southern California Gas Company | N | ORANGE | SAN JUAN CAPISTRANO | 2020-06-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JAVIER AVILA | BUENA PARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner did call in for USA.
Southern California Gas Company | N | ORANGE | SAN JUAN CAPISTRANO | 2020-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | PREMIER BROADBAND SERVICES INC | CORONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor was boring for fiber install when they hit unmarked gas service. Locator missed service. Locator DID GET NOTE TO FILE and did get talked to about error.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2020-12-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | EBS GENERAL ENGINEERING | NA |  | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor did not have a USA and then starting digging and while using a pickaxe they hit 0.5 inch svc. Homeowner knows they are at fault.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2020-10-06 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ALDRIDGE | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | third party contractor was auguring for electrical poles for a street car.ï¿½ Auger went thought the side of the main.ï¿½ Newly installed main was properly marked by company locator and marks were visible.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2020-06-10 | Third party excavation damage | Riser | Steel | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | COUSIN GRADING DEMO | FOUNTAIN VALLEY | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | While demoing building backhoe damage riser. Service was never abandon before demo.ï¿½
Southern California Gas Company | N | ORANGE | SANTA ANA | 2020-10-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | S S DIRECTIONAL DRILLING | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor struck service with shovel when attempting to remove rock under pipe.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2020-06-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | CURT WILSON | SANTA ANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA . Crew and supervisor explained the importance in calling 811
Southern California Gas Company | N | ORANGE | SANTA ANA | 2020-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Directional Drilling | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | ARI JET COMMUNICATION | POMONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 0.75 stl service while boring across .SCG was marked properly .ï¿½Crew and Supervisor explained the important of proper excavation practices
Southern California Gas Company | N | ORANGE | SANTA ANA | 2020-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 2 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | INTEORPIPE CONTRACTORS | SANTEE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor cut into 2 inch steel service stub with saw.ï¿½ Facility was located on the curb and seemed to be pot holed.ï¿½ Contractor did hit it with excavator, however the hit did not cause the line to rupture.ï¿½ Release of gas caused by cutting into the stub with a saw.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2020-05-22 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NEX GEN AIR | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | plumbing contractor repiping home was shooting accubore to install new water line and damaged 2 inchgas main in the parkway.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2020-05-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | SANTA ANA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was drilling holes to place steel rods into the ground to act as footings for a steel rolling entry gate track.ï¿½ They did not have a USA ticket.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2020-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | SPIRO | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging for Charging station with back hoe. hit gas line.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2020-04-20 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | RIGG S BACKHOE SERVICE | YUCAIPA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor struck a 2 inch plastic gas line with a backhoe.ï¿½ 2 inch was properly marked.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2020-02-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 6 |  | CAL BORING | ANAHEIM | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Unmarked stub struck with boring bit during boring operation Stub was not in GIS or paperwork provided to contractor ï¿½
Southern California Gas Company | N | ORANGE | SANTA ANA | 2020-06-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | SANTA ANA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was digging to remove stump and used a sawzall to cut our steel service thinking that it was a root.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2020-03-19 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JESUS TAPIA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor thought steel service was abandon and try to cut it out of the way when they notice gas escaping ï¿½
Southern California Gas Company | N | ORANGE | SANTA ANA | 2020-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | OC STONE AGE MASONRY | SAN JUAN CAPISTRANO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was trenching for drainage when gas line was hit with shovel.No USA .
Southern California Gas Company | N | ORANGE | SANTA MARGARITA | 2020-07-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JOSE CAMPOY | SANTA MARGARITA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging with NO USA, they were digging out to repair houseline for gas.
Southern California Gas Company | N | ORANGE | SEAL BEACH | 2020-01-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | PVD PLUMBING | LONG BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber damaged 0.5inch service
Southern California Gas Company | N | ORANGE | STANTON | 2020-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JC HAULING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per oncall LCT Bill Nhek, damage occurred earlier in the day and no one onsite. It appears service was damaged with a trencher when digging to install footing for a fence.ï¿½
Southern California Gas Company | N | ORANGE | STANTON | 2020-02-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | PINHERO CONSTRUCTION | MURRIETA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 2 service while installing fence post
Southern California Gas Company | N | ORANGE | SURFSIDE | 2020-05-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | COMMAND PERFORMANCE | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 0.50 inch service inserted into 0.75 steel with mini excavator while grading. No USA
Southern California Gas Company | N | ORANGE | SURFSIDE | 2020-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | COLUCCI BROS PLUMBING LLC | LONG BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Handing digging to expose all substructures and hit service with shovel. No usa
Southern California Gas Company | N | ORANGE | TRABUCO CANYON | 2020-07-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | LANDSEA HOMES | IRVINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA.ï¿½ A 1 inch PE stub was found by our contractor, NPL, to have been previously damaged.ï¿½ NPL was on site to extend the stub.ï¿½ NPL called local supervision to repair the damaged stub so they could return to extend the stub.ï¿½ It is unknown who caused the damage developer information will be provided for damaging party information.
Southern California Gas Company | N | ORANGE | TRABUCO CANYON | 2020-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | CLESCERI CONSTRUCTION | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor Did Not Call For A USA And Hit Service With A Shovel.
Southern California Gas Company | N | ORANGE | TUSTIN | 2020-06-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | 711 PLUMBING | HUNTINGTON BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party cut pipe with saw installing drain.. Crew and Supervisor explained the importance in calling 811 . NO USA
Southern California Gas Company | N | ORANGE | TUSTIN | 2020-06-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DANS TRACTOR SERVICE | SANTA ANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was doing demolition work and damaged service line . Crew explained the importance of 811 . No USA
Southern California Gas Company | N | ORANGE | TUSTIN | 2020-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | OC POOLSCAPE | ALISO VIEJO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party company doing pool construction and hitline with bob cat excavator
Southern California Gas Company | N | ORANGE | TUSTIN | 2020-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | SANTA ANA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No Usa . Crew and Supervisor explained the Importance of 811 to homeowner
Southern California Gas Company | N | ORANGE | TUSTIN | 2020-12-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | POWERTEC COMPANY INC | FULLERTON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Company hit the pla was marked off measurements and markings were 2 feet or
Southern California Gas Company | N | ORANGE | TUSTIN | 2020-05-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | FLOW LINE CONCRETE | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party damaged 0.50 inch plastic service with mini excavator.ï¿½ Service was marked correctly and on GIS.ï¿½ Gas migrated into the structure garage, found by cust. service.
Southern California Gas Company | N | ORANGE | VILLA PARK | 2020-07-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 1 |  | NA | VILLA PARK | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner hit plastic service.ï¿½ I did not see and delineation for marks, however there was a current USA ticket on file.ï¿½ Service also mapped wrong on GIS.
Southern California Gas Company | N | ORANGE | VILLA PARK | 2020-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RAY S CONCRETE SYSTEMS | ORANGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor cut plastic service with sawzall while cutting drain.
Southern California Gas Company | N | ORANGE | VILLA PARK | 2020-12-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 17 |  | KNIGHT PLUMMING | ORANGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Business owner David contracted plumbing crew in order to fix plumbing issues with the buildingsï¿½sewage system. Plumbing Contractor shoved crowbar into stormï¿½drain filled with dirt. 1 inch Plastic gas service was running directly through storm drain to nearby MSA. Contractor pierced through the side of theï¿½1 inch gasï¿½line with the crowbar which caused an uncontrollable release of gas. No USA ticket was called in prior to work from plumbing contractor nor business owner.
Southern California Gas Company | N | ORANGE | VILLA PARK | 2020-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 0.75 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | S AND B CONSTRUCTION SERVICES | NATIONAL CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor bored though 1 inch steel service stub.ï¿½ S and B Construction doing the drilling had no USA ticket on file, they were working for TVC.ï¿½ Dug control hole and pinched 1 inch steel service stub.
Southern California Gas Company | N | ORANGE | VILLA PARK | 2020-01-31 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | STRUCTURE BUILDING SERVICES | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plastic service hit with shovel when digging drain trench ï¿½
Southern California Gas Company | N | ORANGE | VILLA PARK | 2020-10-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SERRANO WATER DISTRICT | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While contractor using backhoe to excavateï¿½ hit service.
Southern California Gas Company | N | ORANGE | VILLA PARK | 2020-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | JLC CONSTRUCTION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hired by homeowner was trying to connect a sewer line
Southern California Gas Company | N | ORANGE | WESTMINISTER | 2020-10-09 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 9 |  | HOSADA BROS | GARDENA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Delivery man Damaged bypass stopcock with pallet jack, Police and fire on scene and several businesses evacuated. SoCalGas responded, Distribution crew made permanent repairs.ï¿½
Southern California Gas Company | N | ORANGE | WESTMINSTER | 2020-12-23 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NPL | NA |  | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | NPL was boring in new service and damaged existing gas service with underground bore.ï¿½
Southern California Gas Company | N | ORANGE | WESTMINSTER | 2020-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | GINO GARCIA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor cut 0.75 inch steel service with a sawzall while attempting to remove a tree stump.ï¿½ Contractor did not contact USA prior to beginning excavation.
Southern California Gas Company | N | ORANGE | WESTMINSTER | 2020-10-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | TURN AROUND COMMUNICATIONS | WALNUT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party contractor hit PE service with sharp shooter shovel
Southern California Gas Company | N | ORANGE | YORBA LINDA | 2020-12-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | CORONA | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | The contractor was working wit a USA ticket that expired in April of 2019 and marks where removed.
Southern California Gas Company | N | ORANGE | YORBA LINDA | 2020-11-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MG CONSTRUCTION DECKS | WEST HOLLYWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working for home owner hit our line and had no USA ticket
Southern California Gas Company | N | ORANGE | YORBA LINDA | 2020-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | IRVIN FENCE INC | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor installing fence did not call USA
Southern California Gas Company | N | ORANGE | YORBA LINDA | 2020-12-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | SHENZHEN BEAUTIFUL GARDEN LANDSCAPE | IRVINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | called for a BPP. surveyor found indications and crew found service that had been damaged at some point in the past.
Southern California Gas Company | N | ORANGE | YORBA LINDA | 2020-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | LANDSCAPE CENTER | RIVERSIDE | CA | N | Y | Yes | No | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | none
Southern California Gas Company | N | ORANGE | YORBA LINDA | 2020-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | WESTERN PAVERS | SAN MARCOS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | customer digging to install pool line.ï¿½ No USA
Southern California Gas Company | N | ORANGE | YORBA LINDA | 2020-07-13 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 6 |  | ARIZONA PIPELINE | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | crew used backhoe to dig without exposing plastic main.
Southern California Gas Company | N | ORANGE | YORBA LINDA | 2020-02-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ROD ELLINGTON | LAGUNA HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Electrical contractor did how hand dig over marks ï¿½ trenched through service line with mini excavator ï¿½ properly marked
Southern California Gas Company | N | ORANGE | YORBA LINDA | 2020-07-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | A S CONCREATE | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor doin work for City repairing replacing curbsidewalk placed stake thru plastic serviceï¿½
Southern California Gas Company | N | ORANGE | YORBA LINDA | 2020-09-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 6 |  | J K SOLAR | VICTORVILLE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | solar company drove ground rod into Service line. no USA Called.ï¿½ gas migrated under foundation.ï¿½ï¿½
Southern California Gas Company | N | ORANGE | YORBA LINDA | 2020-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | YORBA LINDA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Installing houseline for gas .ï¿½ Homeowner digging with no USA
Southern California Gas Company | N | ORANGE | YORBA LINDA | 2020-01-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | WEST COAST CONSTRUCTION | PERRIS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor claimed they had hand exposed our line and while trying to clear dirt from around it they hit ourï¿½line with a shovel ï¿½ No USA provided a the time ï¿½ï¿½
Southern California Gas Company | N | RIVERSIDE | BANNING | 2020-03-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CREW INC | COMPTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor over excavating No USA Service was marked for another excavator installing conduit
Southern California Gas Company | N | RIVERSIDE | BANNING | 2020-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | BANNING | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | HO was digging for a carport post and hit the service. No USA
Southern California Gas Company | N | RIVERSIDE | BANNING | 2020-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Farm Equipment | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | FRANCISCO MACIAS | BANNING | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor removing a tree stump for homeowner.ï¿½ Contractor dug around stump and try removing it with a vehicle.ï¿½ Root that had grown around gas service broke service in half.ï¿½ No USA notification.
Southern California Gas Company | N | RIVERSIDE | BANNING | 2020-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | DOMINGUEZ SONS LANDSCAPE | YUCAIPA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged service with NO USA. Thought Reservation was on propane.ï¿½
Southern California Gas Company | N | RIVERSIDE | BANNING | 2020-05-11 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 50 | 40 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | WEKA INC | HIGHLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor damaged unmarked cutback svc history showed as abandoned.ï¿½
Southern California Gas Company | N | RIVERSIDE | BANNING | 2020-05-13 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | WEKA INC | HIGHLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor had exposed gas stub and damaged when backfilling.ï¿½
Southern California Gas Company | N | RIVERSIDE | BEAUMONT | 2020-02-29 | Third party excavation damage | Miscellaneous/Other | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PASQUALE BALDI | BEAUMONT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor installing sewer saw existing marks from service install and thought the service would be deeper ï¿½ No USA
Southern California Gas Company | N | RIVERSIDE | BEAUMONT | 2020-11-06 | Third party excavation damage | Riser | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HE HAMMER CONSTRUCTION | YUCAIPA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Grader hit riser in vacant lot.ï¿½
Southern California Gas Company | N | RIVERSIDE | BEAUMONT | 2020-10-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | FLORITE ROOTERS PLUMBING | BANNING | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was aware of gas service in the vicinity. He was excavating with hand tools when he accidently hit the service.
Southern California Gas Company | N | RIVERSIDE | BEAUMONT | 2020-02-10 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ELECTRIC VEHICLE INC | UPLAND | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | CONTRACTOR WAS INSTALLING ELECTRICAL CONDUIT AND HIT GAS MAIN WITH BACKHOE
Southern California Gas Company | N | RIVERSIDE | BEAUMONT | 2020-06-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | BEAUMONT | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner using excavating with no USA.ï¿½
Southern California Gas Company | N | RIVERSIDE | BEAUMONT | 2020-11-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ORTIZ ENTERPRIZES | IRVINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Area of work was clearly mark correctly. Contractor did not use caution exposing the 2 inch PE main.ï¿½
Southern California Gas Company | N | RIVERSIDE | BEAUMONT | 2020-03-25 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 40 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | MERLIN JOHNSON CONSTRUCTION | MENTONE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor snagged 2 PE main while trenching within 24 of main Main was gouge but not leaking Crew altered main ï¿½
Southern California Gas Company | N | RIVERSIDE | BEAUMONT | 2020-09-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | VACATION POOLS | NA |  | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No | No damage to SUOF. | No damage to SUOF. | No USA was called. contractor was digging for a pool installation and struck the service line.ï¿½
Southern California Gas Company | N | RIVERSIDE | BEAUMONT | 2020-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SANTIAGO NUNGARAY | BEAUMONT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged riser with skip locator.
Southern California Gas Company | N | RIVERSIDE | BEAUMONT | 2020-03-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MERLIN JOHNSON CONSTRUCTION | MENTONE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor digging with backhoe it service near main ï¿½
Southern California Gas Company | N | RIVERSIDE | BEAUMONT | 2020-11-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | BEAUMONT | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | customer hit service line with excavator while digging to plant trees, installed 2 0.5 cts couplings and 6 ft of cts pipe for repair
Southern California Gas Company | N | RIVERSIDE | BEAUMONT | 2020-04-02 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 4 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PARDEE HOMES | BEAUMONT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor installing temp power poles hit 4 inch pe main with auger.ï¿½
Southern California Gas Company | N | RIVERSIDE | BLYTHE | 2020-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DOGGONE BUILDERS INC | ANZA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was hand digging to remove the sidewalk and hit the service line no USA prior to the damage.
Southern California Gas Company | N | RIVERSIDE | CABAZON | 2020-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | CABAZON | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | damaged service while digging for drainage line.
Southern California Gas Company | N | RIVERSIDE | CALIMESA | 2020-04-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ARNOLDS VACCUM SERVICE | SANTA MARGARITA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Fence contractor was using auger for post and had no USA. Developer told them where they thought the gas line was at.ï¿½
Southern California Gas Company | N | RIVERSIDE | CALIMESA | 2020-03-13 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MCZ CONSTRUCTION | YUCAIPA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator was digging and did not maintain marks rain and mud Saw marks and assumed main would be behind him ï¿½
Southern California Gas Company | N | RIVERSIDE | CALIMESA | 2020-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | CALIMESA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Property owner hit riser with lawn mower.ï¿½
Southern California Gas Company | N | RIVERSIDE | CALIMESA | 2020-12-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TBU INC | BEAUMONT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was excavating to replace crushed conduit paralleling our 2 inchPE Main. contractor did not call USA and proceeded to excavate resulting in a damage to the gas main
Southern California Gas Company | N | RIVERSIDE | CALIMESA | 2020-01-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CSI CONSTRUCTION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor did not have a USA Service was marked however contractor assumed service was deeper ï¿½
Southern California Gas Company | N | RIVERSIDE | CATHEDRAL CITY | 2020-02-18 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | A S TRUCKING CONSTRUCTION | INDIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging to connect to sewer lateral No USA Severed 2 PA main outside of property line in public ROW CCFD blocked street and re routed traffic Low EPM alarm also sent out due to damage M R responded
Southern California Gas Company | N | RIVERSIDE | CATHEDRAL CITY | 2020-11-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | CATHEDRAL CITY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The homeowner was digging for irrigation and hit plastic service. The home owner did not contact USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | CATHEDRAL CITY | 2020-12-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | CATHEDRAL CITY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home Owner hit plastic service while diggingï¿½to installï¿½private gas line.
Southern California Gas Company | N | RIVERSIDE | CATHEDRAL CITY | 2020-04-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | CATHEDRAL CITY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner was repairing a sprinkler valve while digging it up hit PLA service with shovel. NO USA was called
Southern California Gas Company | N | RIVERSIDE | CATHEDRAL CITY | 2020-09-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | TRUJILLO CONSTRUCTION | CATHEDRAL CITY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor excavating to install gas line for pool damaged service. Tied back on arrival per ETR. Expired USA
Southern California Gas Company | N | RIVERSIDE | CATHEDRAL CITY | 2020-09-25 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BECKER PIPELINE | RIVERSIDE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor Failed to maintain adequate marks. Contractor is fully Responsible.
Southern California Gas Company | N | RIVERSIDE | CATHEDRAL CITY | 2020-11-04 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TBU INC | CATHEDRAL CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 2 inch gas stub while excavating for sewer. Contractor did not have a USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | CATHEDRAL CITY | 2020-10-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SUPERIOR MASONRY | COLTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor Hit plastic service while excavating to install a block wall. Contractor failed to call USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | CATHEDRAL CITY | 2020-03-03 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | HPH HOMEBUILDER | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor was digging to install new conduit when they hit a 2 main that they failed to pothole to verify USA was good and marks and flags were good
Southern California Gas Company | N | RIVERSIDE | CATHEDRAL CITY | 2020-01-27 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | PMD PLUMBING | CATHEDRAL CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor cut into 0.75inch STL line not knowing it was the gas line contractor didn t call USA
Southern California Gas Company | N | RIVERSIDE | CATHEDRAL CITY | 2020-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | CATHEDRAL CITY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Owner digging to install plants on property. No USA notification. Secondary contact for home owner Ceaser Toxquiï¿½760 4490633
Southern California Gas Company | N | RIVERSIDE | CATHEDRAL CITY | 2020-08-31 | Third party excavation damage | Main | Polyethylene Pipe | Trencher | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | SIERRA PACIFIC ELECTRICAL | JURUPA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was trenching over two inch plastic main knowing it was there. Contractor said he thought it would be deeper and admitted to knowing it was wrong to trench over SCG facility. Contractor is fully responsible.
Southern California Gas Company | N | RIVERSIDE | COACHELLA | 2020-05-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | IMPERIAL IRRIGATION DISTRICT | LA QUINTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA notification Contractor IID excavating for electric repairs damaged service
Southern California Gas Company | N | RIVERSIDE | COACHELLA | 2020-09-10 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | J GINGER MASONRY LP | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor failed to call in USA and hit 2 inch plastic main while excavating with a backhoe. Contractor is fully Responsible.
Southern California Gas Company | N | RIVERSIDE | COACHELLA | 2020-03-10 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TBU ENGINEERING | BEAUMONT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was digging up for gas install and hit main with backhoe looks like the company let the USA expireï¿½
Southern California Gas Company | N | RIVERSIDE | COACHELLA | 2020-01-09 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | PLATINUM LANDSCAPE INC | PALM DESERT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was digging for irrigation and landscaping and hit 2 gas line No USA was called
Southern California Gas Company | N | RIVERSIDE | COACHELLA | 2020-07-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | VACATION POOLS | INDIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Excavating for pool line. Branch service damaged, 1 outage
Southern California Gas Company | N | RIVERSIDE | COACHELLA | 2020-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | T B U | BEAUMONT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit Gas service while exposing it by hand. Contractor failed to contact USA and receive their own USA ticket.
Southern California Gas Company | N | RIVERSIDE | COACHELLA | 2020-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | TBU INC | BEAUMONT | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Excavator dug prior to valid USA. Excavator had previous damage earlier in day at same tract without a USA
Southern California Gas Company | N | RIVERSIDE | COACHELLA | 2020-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TBU INC | BEAUMONT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging to expose gas line when they hit gas service with shovel.ï¿½ Contractor failed to call USA. Contractor is fully responsible.
Southern California Gas Company | N | RIVERSIDE | COACHELLA | 2020-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TBU INC | BEAUMONT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor Crew digging to expose SCG stub when contractor severed 0.5 inch service with shovel, marks were visible.
Southern California Gas Company | N | RIVERSIDE | CORONA | 2020-02-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | LENNAR | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit service while installing drainage No USA
Southern California Gas Company | N | RIVERSIDE | CORONA | 2020-04-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PLATINUM LANDSCAPES | PALM DESERT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit service installing drainage
Southern California Gas Company | N | RIVERSIDE | CORONA | 2020-07-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HCI | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor damaged correctly marked gas facility while excavating to repair cable TV. contractor was asked to always hand expose gas line prior to any other excavating to prevent injury and property damage. BB 72020
Southern California Gas Company | N | RIVERSIDE | CORONA | 2020-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 44 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JAY CORNIN | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party damage. no USA
Southern California Gas Company | N | RIVERSIDE | CORONA | 2020-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | CORONA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavator struck gas line while trenching with a pick axeï¿½
Southern California Gas Company | N | RIVERSIDE | CORONA | 2020-12-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | FULLER CONSTRUCTION | ONTARIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging to install gas service struck stub.ï¿½ Failed to call USA for markings.
Southern California Gas Company | N | RIVERSIDE | CORONA | 2020-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Home Owner damaged correctly marked gas facility while trenching for a new block wall with backhoe. Owner was asked to always hand expose all utilities prior to using heavy equipment to prevent injury or property damage. BB 5720
Southern California Gas Company | N | RIVERSIDE | CORONA | 2020-07-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BLUE TOP INC | APPLE VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor damaged correctly marked gas service while trenching for new sewer. contractor was asked to call for remarks when the flags are removed prior to excavating to prevent injury or property damage. BB 71720
Southern California Gas Company | N | RIVERSIDE | CORONA | 2020-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JOE PRIEUR BLUE TOP INC | APPLE VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor damaged unmarked gas facility while excavating to repair sewer. USA was not notified. Contractor was asked to always call USA 2 days prior to any excavating to prevent injury or property damage. Contractor claimed to have a USA ticket but could not provide it. He also stated that he knew the facility was there since he had previously potholed. BB 9320
Southern California Gas Company | N | RIVERSIDE | CORONA | 2020-07-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | CORONA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | home owner damaged unmarked gas facility while trenching for a wall. USA was not notified. Home owner was asked to always notify USA so all utilities can mark facilities prior to any excavating to prevent injury or property damage. BB 73020
Southern California Gas Company | N | RIVERSIDE | CORONA | 2020-06-04 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MEDIA COMMUNICATIONS | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged unmarked 2 inchpem at end of main. Locator did not mark to end of main. EE was given documented counseling. contractor was asked to call for remarks when no marks or NO SCG marked is visible. BB 61220. USA ticket number was valid and this tab will not accept
Southern California Gas Company | N | RIVERSIDE | CORONA | 2020-05-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SRG CONTRACTORS | CORONA | CA | N | Y | Excavation was for emergency reasons. | Excavation was for emergency reasons. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor damaged unmarked gas facility while grading. USA was not called. contractor was asked to always call dig alert prior to any excavating to prevent injury or property damage. BB 52020
Southern California Gas Company | N | RIVERSIDE | CORONA | 2020-05-27 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SRG | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor damaged unmarked gas facility with backhoeï¿½while trenching for electric conduit. USA was not notified. Contractor was asked to always call dig alert prior to any excavating so the utilities can be marked to prevent injury and property damage. BB 52920
Southern California Gas Company | N | RIVERSIDE | CORONA | 2020-12-29 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PACIFIC UTILITY | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor damaged correctly marked gas facility while exposing a gas stub to be extended. contractor was asked to always hand expose prior to using backhoe to prevent injury and property damage. BB 1 5 21
Southern California Gas Company | N | RIVERSIDE | CORONA | 2020-01-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | none
Southern California Gas Company | N | RIVERSIDE | CORONA | 2020-03-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MORGAN CONSTRUCTION COMPANY | TEMECULA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit service that was marked while digging up sewer
Southern California Gas Company | N | RIVERSIDE | CORONA | 2020-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 3 |  | CITY OF CORONA | CORONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | locator signal jumping to other facilities. ETD did not mark service due to signal taking him outside delineation. SVC history does not line up with marks and bad signal cause of miss mark no mark. backhoe digging freely due to no marks causing damage.
Southern California Gas Company | N | RIVERSIDE | CORONA | 2020-06-26 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 44 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 8 |  | ACCESS GENERAL | WESTMINSTER | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Second Party Damage. Access general installing ballards for SCG damaged service while hand exposing
Southern California Gas Company | N | RIVERSIDE | CORONA | 2020-04-30 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PLATINUM LANDSCAPE | PALM DESERT | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor damaged correctly marked gas facility while trenching for drainage. contractor was asked to always hand expose prior to using heavy equipment to prevent injury or property damage. BB 51220
Southern California Gas Company | N | RIVERSIDE | CORONA | 2020-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PACIFIC CONSTRUCTION GROUP | IRVINE | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | ï¿½ damaged pe service unmarked. service history showed as abandon but it was only cut back
Southern California Gas Company | N | RIVERSIDE | CORONA | 2020-11-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ABEL OCAMPO | SANTA ANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | hit service removing bush. No USA
Southern California Gas Company | N | RIVERSIDE | CORONA | 2020-08-13 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CJW | MURRIETA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | excavator damaged gas main with backhoe
Southern California Gas Company | N | RIVERSIDE | CORONA | 2020-06-18 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 44 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | PACIFIC WEST UNDERGROUND INC | YUCAIPA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Third party contractor damage main while digging tie in for future main. USA was valid and marked correctly. Damage with back hoe while exposing. Failed to hand expose.
Southern California Gas Company | N | RIVERSIDE | CORONA | 2020-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | GRIFFIN RESIDENTIAL | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor damaged unmarked gas facility while trenching to install new water line. USA was not notified. Contractor was asked to always contact USA 2 days prior to any excavating so that utilities can be marked to prevent injury or property damage. BB 72720
Southern California Gas Company | N | RIVERSIDE | DESERT HOT SPRINGS | 2020-01-29 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 7 |  | O DUFFY CONSTRUCTION | MENIFEE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor potholed main 8 south of damage location and main was at 94 deep due to prior main alteration being lowered for this project but main was at standard 38 depth where the damage occurred
Southern California Gas Company | N | RIVERSIDE | DESERT HOT SPRINGS | 2020-02-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | O DUFFY CONSTRUCTION | ROMOLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor hit gas service while trenching to install new sewer line Gas line wasn t marked USA was called Gis has no record of service that was installed in 95 but service shows in service history ï¿½
Southern California Gas Company | N | RIVERSIDE | DESERT HOT SPRINGS | 2020-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | O DUFFY CONSTRUCTIONS | MENIFEE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging prior to updating USA, working on a expired ticket.
Southern California Gas Company | N | RIVERSIDE | DESERT HOT SPRINGS | 2020-12-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | PEDRO SALAZAR | DESERT HOT SPRINGS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Home owner excavating to plant tree, damaged branch service.
Southern California Gas Company | N | RIVERSIDE | DESERT HOT SPRINGS | 2020-12-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TIM REYNOLDS | SAN JACINTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | vacant lot service hit by contractor doing work for developer
Southern California Gas Company | N | RIVERSIDE | DESERT HOT SPRINGS | 2020-02-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | DESERT HOT SPRINGS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | 3rd party contractor was digging for sewer delineations were marked for Backyard contractor hit service on side of yard 3rd party contractor failed to call in new USA to change scope of job
Southern California Gas Company | N | RIVERSIDE | DESERT HOT SPRINGS | 2020-03-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NPL CONSTRUCTION | MIRA LOMA | CA | Y | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NPL was doing service replacements and hit our line with a shovel ETR RFA d for a crew who went out and made the repairs on the 0.5inch CTS Underground samples were negative no migrating gas No outage as gas was off to vacant building
Southern California Gas Company | N | RIVERSIDE | DESERT HOT SPRINGS | 2020-01-07 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | O DUFFY CONSTRUCTION | ROMOLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor potholed all tie ins and services when company potholed they found a steel main connected to plastic crew hit PLA main that had a jog in it Markings were off by 5
Southern California Gas Company | N | RIVERSIDE | DESERT HOT SPRINGS | 2020-05-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 9 |  | O DUFFY CONSTRUCTION | MENIFEE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator damaged service. Previously potholed service but what was found was abandoned. As excavation continued, active service was damaged.ï¿½
Southern California Gas Company | N | RIVERSIDE | DESERT HOT SPRINGS | 2020-07-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | J G CONSTRUCTION | INDIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor excavating to install fence damaged service. Assumed service wasnt there
Southern California Gas Company | N | RIVERSIDE | EASTVALE | 2020-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | RIVERSIDE FENCE | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor damaged unmarked gas facility while using a post hole digger to install new fence. USA was not notified. Contractor was asked at damage site to always notify USA Dig alert 2 days prior to any excavating so utilities can mark facilities to prevent injury or property damage. BB 11 9 20
Southern California Gas Company | N | RIVERSIDE | EASTVALE | 2020-07-01 | Third party excavation damage | Miscellaneous/Other | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CENTURY COMMUNICATIONS | NEWPORT BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit end of stub while trenching for electric.ï¿½ Marks visible but could not find ticket number could have been from different company calling in ticket. Either way marks were on and visible.
Southern California Gas Company | N | RIVERSIDE | EASTVALE | 2020-09-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DIABLO BROTHERS SERVICES | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor damaged unmarked gas facility while excavating for gas line. USA was not called. Contractor was asked to always notify USA 2 days prior to any excavating so utilities can mark out there facilities to prevent injury or property damage. BB 91020
Southern California Gas Company | N | RIVERSIDE | EASTVALE | 2020-05-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged service while pot holing.ï¿½
Southern California Gas Company | N | RIVERSIDE | EASTVALE | 2020-05-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CLASSIC LANDSCAPE | COLTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor damaged unmarked gas facility while trenching for a new drain pipe. USA was not called. Contractor was asked to always contact Dig Alert so that all utilities can be marked prior to any excavating in order to prevent injury or property damage. BB 51520
Southern California Gas Company | N | RIVERSIDE | ELSINORE | 2020-12-03 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 4 |  | INTERNATIONAL LINE BUILDERS | JURUPA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor struck facility with excavator.ï¿½ Marks Visible and accurate.
Southern California Gas Company | N | RIVERSIDE | HEMET | 2020-08-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 6 |  | CITY OF HEMET WATER | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Damage Backhoe hit 2 inch plastic service. USA was called but was not marked in the area in which was delineated.
Southern California Gas Company | N | RIVERSIDE | HEMET | 2020-10-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | INTERNATIONAL LINE BUILDERS | JURUPA VALLEY | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Damage third party working for Edison. Hit a 0.5 inch IPS. USA was called in but started to dig before 48 hour time requirement not all utilities were marked. Evcavator dug prior to valid start date time
Southern California Gas Company | N | RIVERSIDE | HEMET | 2020-03-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | HEMET | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | service damaged by backhoe NO USA
Southern California Gas Company | N | RIVERSIDE | HEMET | 2020-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | HEMET | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was landscaping their yard when they hit gas line with shovel.
Southern California Gas Company | N | RIVERSIDE | HEMET | 2020-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | RAMON LOPEZ THE HIT HILLDALE GROUP | MURRIETA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Earth was extremely hard per contractor and they could not find the service, they chose to grade with bobcat and hit the line with the bobcat bucket.
Southern California Gas Company | N | RIVERSIDE | HEMET | 2020-07-06 | Third party excavation damage | Riser | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ROGER CROTT Z BEST CONCRETE | NA |  | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No | No damage to SUOF. | No damage to SUOF. | Damage third party contractor hit riser when grading to install side walk. No USA
Southern California Gas Company | N | RIVERSIDE | HEMET | 2020-11-09 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PACIFIC UTILITY INSTALLATION | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged 2 inch PE main. Contractor failed to pot hole main and damaged it with a backhoe.
Southern California Gas Company | N | RIVERSIDE | HEMET | 2020-11-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PACIFIC UTILITY INSTALLATION PUI | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged stub service by 3rd party contractor. USA was called. Marks visible and accurate.
Southern California Gas Company | N | RIVERSIDE | HEMET | 2020-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CHARTER SPECTRUM CONTRACTOR | HOMELAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damage
Southern California Gas Company | N | RIVERSIDE | HEMET | 2020-10-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | R R FARM AND HEAVY EQUIPEMENT | HOMELAND | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Old residential track 2 inch main damaged by grading of slope, track getting ready for future install. Crew squeezed and capped main. No USA.ï¿½
Southern California Gas Company | N | RIVERSIDE | HEMET | 2020-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PACIFIC UTILITIES | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage. The foreman for Pacific Utilities acknowledged that the plastic gas service was damage because they didnt hand dig hit line was backhoe. USA was current and marked correctly.
Southern California Gas Company | N | RIVERSIDE | HEMET | 2020-08-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TAYLOR UNDERGROUND | SAN JACINTO | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Damage, USA was called. Service was not indicated in GISï¿½ therefore it was not marked or mapped.
Southern California Gas Company | N | RIVERSIDE | HOMELAND | 2020-04-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | GRANITE CONSTRUCTION | INDIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged service while trying to expose drain
Southern California Gas Company | N | RIVERSIDE | HOMELAND | 2020-09-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | GRANITE CONSTRUCTION | INDIO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 0.75 inch steel service was pulled by backhoe. Service was not marked. Mapped incorrectly in GIS. Active USA
Southern California Gas Company | N | RIVERSIDE | INDIAN WELLS | 2020-07-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | FARWEST MASONRY | INDIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor excavating for block wall, damaged service. Expired USA from 2019.ï¿½
Southern California Gas Company | N | RIVERSIDE | INDIAN WELLS | 2020-12-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DWLC II INC LANDCARE MANAGEMENET | THOUSAND PALMS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscaping contractor hit plastic service while trying to plant a Bougainvillea. Contractor failed to call USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | INDIAN WELLS | 2020-11-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | PHANTOM DEVELOPMENT | RANCHO MIRAGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged plastic service when pulling up tree roots. Contractor failed to call in for a USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | INDIAN WELLS | 2020-07-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | TESERRA OUTDORRS | COACHELLA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Hand digging to plant tree, damaged 1 inch service w EFV.ï¿½ï¿½
Southern California Gas Company | N | RIVERSIDE | INDIO | 2020-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | INDIO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner s Grandfather was making repairs to water line while digging next to service said he smelt gas and heard hissing Exposed line and found cut riser No USA was called
Southern California Gas Company | N | RIVERSIDE | INDIO | 2020-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | none
Southern California Gas Company | N | RIVERSIDE | INDIO | 2020-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RNS PLUMBING | BERMUDA DUNES | CA | N | Y | Yes | No | No | Yes | No | Yes | No | No USA. Excavator digging to install grease pits for restaurant. Claimed to have USA ticket but unable to produce ticket number. Ticket found in KorWeb, but ticket expired 87ï¿½
Southern California Gas Company | N | RIVERSIDE | INDIO | 2020-09-03 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LAZER BACKHOE SERVICE | GRAND TERRACE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party Contractor failed to call in USA. Contractor knew location of 2 inch plastic main due to previous marks but was potholing with a backhoe. Contractor is fully Responsible for this damage.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2020-12-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TBU | BEAUMONT | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit plastic stub while hand exposing it.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2020-03-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CJW | SAN JACINTO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | none
Southern California Gas Company | N | RIVERSIDE | INDIO | 2020-07-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | INDIO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner excavating to remove tree stump and hit service with a shovel
Southern California Gas Company | N | RIVERSIDE | INDIO | 2020-11-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TBU INC | BEAUMONT | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Third Party contractor hit unmarked stub while excavating for electric. The locater did not mark service due to nothing showing on GIS and he did not pick up anything with EM ball locater. The locater did not have access to Service History. HIs access to service history has been requested multiple times by FOS. Locater did use all other Resources.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2020-09-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Unknown person digging with a shovel damaged service line.ï¿½
Southern California Gas Company | N | RIVERSIDE | INDIO | 2020-05-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | DAVIS RESTORATION | PALM DESERT | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator hit service while digging for post hole
Southern California Gas Company | N | RIVERSIDE | INDIO | 2020-01-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | COCHRAN COMMUNICATIONS | CATHEDRAL CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was replacing a curb vault when digging out to install new one contractor hit service with shovel No USA was called
Southern California Gas Company | N | RIVERSIDE | INDIO | 2020-03-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | INDIO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Owner of property was trying to remove tree and hit service No USA was called
Southern California Gas Company | N | RIVERSIDE | INDIO | 2020-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | WALTON BROTHERS ENTERPRISES INC | SAN JACINTO | CA | N | Y | Yes | No | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Crew excavating utility trench to install gas, crew claims gas line leaking prior to them exposing gas.ï¿½ Crew working on an expired USA ticket.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2020-04-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DESERT ISLES | INDIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was installing a housline when the hit service line with shovel. NO USA was Calledï¿½
Southern California Gas Company | N | RIVERSIDE | INDIO | 2020-01-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | INDIO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While compacting dirt with water to backfill trench Home owner hit service with shovel
Southern California Gas Company | N | RIVERSIDE | INDIO | 2020-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ALMS UNDERGROUND CONSTRUCTION INC | CATHEDRAL CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Excavator digging to install irrigation, damaged 1 inch serviceï¿½
Southern California Gas Company | N | RIVERSIDE | INDIO | 2020-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | INDIO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging to repair gate that suffered wind damage, Homeowner hit service with shovel
Southern California Gas Company | N | RIVERSIDE | INDIO | 2020-05-13 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | LAZER BACKHOE ARNULFO | GRAND TERRACE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Lazer backhoe excavating for sewer install. Area located for Pride Backhoe. No ticket for Lazer Backhoe. Marks still visible. Damaged 2 inch PE main
Southern California Gas Company | N | RIVERSIDE | INDIO | 2020-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JAMES A SHIRLEY CONSTRUCTION | YUCCA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | James Shirley excavating for underground utilities, damaged 0.5 inch stub. Valid USA, marked correctly
Southern California Gas Company | N | RIVERSIDE | INDIO | 2020-04-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | WAKEFIELD CONSTRUCTION | TEMECULA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor was digging to get ready for gas install and hit stub with backhoe. USA was Good and marks were good
Southern California Gas Company | N | RIVERSIDE | INDIO | 2020-03-09 | Third party excavation damage | Miscellaneous/Other | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CJW GENERAL CONTRACTORS | SAN JACINTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor stated that they potholed and found main hit and folded back USA was good and marked
Southern California Gas Company | N | RIVERSIDE | INDIO | 2020-12-10 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TBU | BEAUMONT | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to hand expose 2 inch plasticï¿½main and damaged it while trenching with a backhoe.
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2020-11-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | MURRIETA DEVELOPERS | TEMECULA | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor called in USA after Damage had occurred.ï¿½ Ticket not valid during time of damage.ï¿½ï¿½
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2020-06-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | JURUPA VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging with shovel, plastic service was hit and damaged.
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2020-05-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HERMAN WEISSKER | JURUPA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor did not take caution while excavating and struck out service line
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2020-05-22 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SOUTHWEST V DITCH | RIVERSIDE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Southwest V Ditch was augering to set railing when they stuck out marked 2 inch.
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2020-09-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HERMAN WISSKER INC | JURUPA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hit our service with a shovel while working to install conduit.ï¿½
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2020-10-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | EDUARDO SANCHEZ | SAN BERNARDINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | customer was installing fence posts and struck gas facility.ï¿½ No USA called.
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2020-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | JURUPA VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | installing a new gas houseline and struck PLA service.ï¿½ No USA called.
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2020-10-24 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | JURUPA VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer cut into service with Sawzall removing tree.ï¿½ No USA.
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2020-01-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MOBILE HOME PARK | JURUPA VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer digging for fence struck service with posthole digger
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2020-12-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RC EARTHWORKS INC | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor failed to notify USA and Struck facilities.ï¿½
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2020-09-23 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | CM BACKHOE SERVICES | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USAï¿½notification prior to damage. Excavator digging to install sewerï¿½
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2020-09-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | SKY CONSTRUCTION SERVICES | YUCCA VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging with backhoe when they hit 1 inch plastic service. Contractor failed to call USA. Contractor is fully responsible.
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2020-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LUXTEC BUILDERS INC | PALM DESERT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | OGC Inc working for Luxtec Builders Inc were digging for some sort of drainage and hit plastic stub with a track excavator.
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2020-02-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HORTECH LANDSCAPE MANAGEMENT | INDIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Due to the hard ground the 3rd party contractor hit the service with the shovel USA was called but failed to pothole to confirm location
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2020-05-11 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | FIRST STONE LANDSCAPE COMPANY | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor failed to call USA and hit 2 inch IPS main, Called USA after he hit the main.
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2020-10-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PLATINUM LANDSCAPE INC | PALM DESERT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging with a shovel for drainageï¿½when they hit 1 inch plastic service. Contractor failed to contact USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2020-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | KNAPP LANDSCAPING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit service with shovel while hand Digging.. Contractor failed to call in USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2020-03-02 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 3 |  | J J PLUMBING | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor digging for sewer lateral failed to hand expose main
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2020-10-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | VELASQUEZ MASONRY | CATHEDRAL CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 1 inch plastic service with mini excavator while excavating for a block wall. Contractor failed to contact USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2020-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TBU INC | BEAUMONT | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | USA valid. Unable to locate stubs in area due to lack of proper documentation. GIS prints incorrect and service history incorrect. Size of lots also changed from original installation in 2007
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2020-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TBU INC | BEAUMONT | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Excavator digging for electrical, damaged 1 inch stub. No markings or EM ball for locator to find stub. Lot sizes have also changed since original installation of stub in 2007
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2020-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | EDGAR PASCUAL | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | hand digging to install irrigation and knicked the plastic service.
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2020-02-04 | Third party excavation damage | Main | Steel | Not Available | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | none
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2020-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 14 |  | NA | LAKE ELSINORE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage NO USA
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2020-04-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SHANE PLUMBING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor installing water using trencher damaged service. Plumber had no USA ticket. Marks visible from previous ticket on still existing pavement. Area of damaged pavement already removed.
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2020-04-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | LAZER BACKHOE | LAKE ELSINORE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service with backhoe while digging to install sewer. No USA.
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2020-12-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | service damaged by homeowner and workers
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2020-01-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | BELCO ELECNOR GROUP | CHINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor punctured service line while hand exposing ahead of bore
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2020-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | T E ROBERTS | ORANGE | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | signal issues involving steel main and pe service. Team member unable to back trace service line.
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2020-08-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | TE ROBERTS | ORANGE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor working for EVMWD on main and service replacements damaged long side gas service. Existing Marks that wereï¿½away from excavation area should markings at 24 inch, unable to determine what markings were in excavation area due to work being done. Locator also had signal interference and a sharp turn that caused issues with locating.ï¿½
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2020-08-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JAG CONSTRUCTION | IRVINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage was found by Company EE.ï¿½ It was a stub service line found taped back.ï¿½ No USA and actual damaging party not onsite.ï¿½ Info is from Developer.
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2020-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | BONANZA PLUMBING | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 2 inch PE main damaged by 3rd party contractor excavating for sewer. Marks visible. Contractor did not pot hole.
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2020-07-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CANSECO ELECTRIC CONTRACTING | ALISO VIEJO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor failed to call for USA while using a trencher device to install electrical.
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2020-02-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | WALTON BROS | SAN JACINTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor found a substructureï¿½line near marks and assumed it was the gas line They continued to excavate with excavator and damaged actualï¿½service line
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2020-02-05 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | WALTON BROTHERS ENTERPRISE | SAN JACINTO | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Service not properly mapped or posted in GIS.
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2020-01-28 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | WALTER BROS ENTERPRISE | SAN JACINTO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Facility had incorrect mapping Locator had to rely on measurements unable to get signal at this location Contractor was advised that main should have been potholed if main wasn t found contractor could have contacted locator for more assistance
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2020-01-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BECKER PIPELINE | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA notification made
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2020-04-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | BUCCOLA LANDSCAPE SERVICES | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged Marked service
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2020-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CAL WEST UNDERGROUND | NORCO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage 2 inch main no USA
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2020-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | PAULEY CONSTRUCTION | WINCHESTER | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged by 3rd party contractor. Dug before ticket was valid
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2020-06-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | FODDRILL CONSTRUCTION CORP | CHINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage service
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2020-06-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | FODDRILL CONSTRUCTION CORP | CHINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage third party hit 0.50 inch plastic service with backhoe while excavating to install street lights. No USA
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2020-11-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RICHARD LOPEZ CONSTRUCTION | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | USA was not notified
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2020-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | MENIFEE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer was digging for fence post and damaged the 0.5 inch pe pipe which did not cause a leak. No USA.
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2020-03-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RICHARD LOPEZ CONSTRUCTION | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was potholing for utilities and hit 0.5inch gas line with shovel
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2020-03-17 | Third party excavation damage | Miscellaneous/Other | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RICHARD LOPEZ CONSTRUCTION | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor was potholing when they struck our gas serviceï¿½
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2020-06-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JUAN IBARRA | MENIFEE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer damaged service while installing fence, no USA.ï¿½
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2020-10-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 53 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TEMP POWER SYSTEMS | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Found temporary electrical pole installed above service and caused damage. Had to have electrical contractor come out and move pole till repairs could be completed.ï¿½
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2020-07-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | AMERICAN LANDSCAPE MAINTENANCE | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage No USA
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2020-05-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JEFF CARPENTER INC | PERRIS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | ETD found service stub damaged when performing trench inspection for next day extend stub install. No USA.ï¿½
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2020-04-27 | Third party excavation damage | Riser | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | JARED DITWORTH | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Bobcat hit Riser while grading
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2020-01-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | AMERICAN LANDSCAPE AND MAINTENANCE INC | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA and nobody on scene upon arrival
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2020-05-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | QUALITY CUSTOM POOLS | MENIFEE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged Service while digging for electricalpool
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2020-07-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ALVIZIA CORPORATION | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA notification made.
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2020-04-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | SUPERIOR COMPANY | NEWPORT BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Area being dug out to install brick wall between new tract homes. No usa, service with EFV damaged.ï¿½
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2020-03-25 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | KANA CONSTRUCTION | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA called
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2020-05-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged service with EFV. No USA. Damaged by trencher.ï¿½
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2020-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 55 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RANCHO WEST LANDSCAPE | MURRIETA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor failed to notify USA dig alert and damaged service line with trencher.
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2020-10-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CAL WEST UNDERGROUND INC | NORCO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage Hit 0.5 inch service with a backhoe when digging trench for street lights. No USA
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2020-03-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CAL WEST UNDERGROUND | NORCO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA notification made
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2020-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ALVIZIA CORP | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 2 inch PL main
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2020-02-05 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TRENCHERS WEST | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA notification made
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2020-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 0 | 0 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JAG CONSTRUCTION | IRVINE | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No | No damage to SUOF. | No damage to SUOF. | none
Southern California Gas Company | N | RIVERSIDE | MIRA LOMA | 2020-10-12 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NOVI ENVIRONMENTAL INC | LAKE ELSINORE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to hand exposing while grading and struck facility.ï¿½ Marks Visible.
Southern California Gas Company | N | RIVERSIDE | MIRA LOMA | 2020-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | DOWNING CONSTRUCTION | REDLANDS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor Struck service while excavating for Sewer.ï¿½ Marks visible and accurate.ï¿½
Southern California Gas Company | N | RIVERSIDE | MIRA LOMA | 2020-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | DOWNING CONSTRUCTION INC | REDLANDS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to protect pipe after exposing and debris fell onto pipe.ï¿½ USA valid and marks visible.
Southern California Gas Company | N | RIVERSIDE | MIRA LOMA | 2020-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ALVARADOS MASONARY | MIRA LOMA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor trenching for water line struck PLA service.ï¿½ No USA.ï¿½ Due to proximity to structures residents evacuated.
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2020-03-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | MORENO VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer Installing Fence removing tree
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2020-06-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ALAMO FENCE | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage 0.50 inch service no USA
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2020-07-21 | Operator excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NPL | EASTVALE | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was trying to expose SMC to install EFV. Pipe had been installed in Conduit? and there was a large kink in pipe SMC. Pipe was not in line with service
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2020-08-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PAULEY CONSTRUCTION | WINCHESTER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damage third party contractor was hand digging to repair telephone line and damage a clearly markedï¿½ 0.5 inch plastic gas service. USA was called ticket
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2020-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ALABASSI CONSTRUCTION AND ENGINEERING | PERRIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damage a markedï¿½0.50 inch service
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2020-11-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | H O 14227 | MORENO VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage. No USA third party contractor was using a clay spade while dig to build wall. Hit 0.5 inch CTS service.
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2020-12-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | POWER SURGE | CAPISTRANO BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage NO USA Third Party contractor hit stub when trenching with ditch witch.
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2020-05-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | W A RASIC CONSTRUCTION | LONG BEACH | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 0.50 inch stub NOT in GIS at this address
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2020-04-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HOT LINE CONSTRUCTION INC | BRENTWOOD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | contractor crew damaged 0.50 inch plastic service.ï¿½
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2020-03-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | MORENO VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | per homeowner making repairs to sewer line
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2020-11-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | EASTERN MUNICIPAL WATER DISTRICT | PERRIS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Damage EMWD hit 0.5 inch CTS with backhoe. Current USA ..ETD did not locate the area they assumed that EMWD would not be digging near the service
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2020-06-25 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | CHRIS SWVD | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor digging for drain piping system hit gas line with backhoe
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2020-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MITCHELL GENERAL CONTRACTORS | IRVINE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Damaged stub not shown in GIS
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2020-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | EMD | PERRIS | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | EMWD employee damaged Gas service while probing for water main. Current USA. Service was marked clear and correct.
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2020-11-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | INTERNATIONAL LINE BUILDERS | JURUPA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Emergency Open Trench To Install New Pipe Electrical Conduit
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2020-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MOS DEMOLITION | FONTANA | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | Damaged Riser
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2020-07-18 | Third party excavation damage | Riser | Steel | Grader/Scraper | 0.75 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 6 |  | NA | MORENO VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage No USA
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2020-09-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | MORENO VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage No USAï¿½
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2020-11-22 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | NA | MORENO VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 2 inch PX main
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2020-08-24 | Third party excavation damage | Riser | Steel | Grader/Scraper | 0.75 | 60 | 5 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | SAIZ LANDSCAPING | MORENO VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While removing debris at jobsite , contractor hitï¿½ MSA meter guard covered with vegetation. Meter Guard reinstalled
Southern California Gas Company | N | RIVERSIDE | MURRIETA | 2020-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | 3T FENCE | MURRIETA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor installing fence hit branch service with post hole digger Contractor had no USA Contractor advised by supervision to always contact 811 when digging
Southern California Gas Company | N | RIVERSIDE | MURRIETA | 2020-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | MURRIETA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner installing fence did not notify USA Dig alert prior to excavating
Southern California Gas Company | N | RIVERSIDE | MURRIETA | 2020-01-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | MURRIETA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer was potholing for drain irrigation repair of some kind with an improvised digging tool using water pressure
Southern California Gas Company | N | RIVERSIDE | MURRIETA | 2020-12-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | MURRIETA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner was replacing fencing when they hit the service with a post hole digger. Customer advised to call USA digalert, a free service for facility line locates.
Southern California Gas Company | N | RIVERSIDE | MURRIETA | 2020-08-19 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 6 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | DOTY BROS | NORWALK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | COntractor was excavating trench for gas line installation. They dug with mechanical means over main causing damage.
Southern California Gas Company | N | RIVERSIDE | MURRIETA | 2020-10-23 | Third party excavation damage | Main | Polyethylene Pipe | Grader/Scraper | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HEARTLAND GRADING SHAWN MCLEIN | CARLSBAD | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor did not request for remarks. This is a new project with new main and stubs installed. They repeatedly called in for update only through USA digalert. They were grading attempting to remove large boulders and damaged the 2 inch PEM.
Southern California Gas Company | N | RIVERSIDE | MURRIETA | 2020-10-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PACIFIC PRODUCTION PLUMBING | MURRIETA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging forï¿½sewer with backhoe and damaged service stub. Contractor had no USA.ï¿½
Southern California Gas Company | N | RIVERSIDE | MURRIETA | 2020-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | MURRIETA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer hit service while installing fence.
Southern California Gas Company | N | RIVERSIDE | MURRIETA | 2020-05-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | JGC JOHN GRIFFIN CONSTRUCTION | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor did not pothole properly by hand prior to using mini excavator.
Southern California Gas Company | N | RIVERSIDE | MURRIETA | 2020-06-30 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MCGEE CONTRACTING | MURRIETA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor failed to notify USA dig alert prior to excavating
Southern California Gas Company | N | RIVERSIDE | MURRIETA | 2020-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | GARY ROSE | MURRIETA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged Service while installing fencing
Southern California Gas Company | N | RIVERSIDE | MURRIETA | 2020-08-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TRENCHER WEST CONSTRUCTION | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | CONTRACTOR FAILED TO USE CAUTION WHILE EXPOSING GAS LINE, CONTRACTOR TRENCHING FOR OTHER UTILITIES
Southern California Gas Company | N | RIVERSIDE | NORCO | 2020-07-02 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 44 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 15 |  | ALABASSI CONSTRUCTION | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party damage. Valid USA. correctly marked.
Southern California Gas Company | N | RIVERSIDE | NORCO | 2020-10-12 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 1 |  | R I COMMUNICATION ISIDRO ROJAS | BLOOMINGTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | Contractor damaged unmarked gas facility while directional boring in conduit. The struck facility was outside of the contractors delineation. Contractor was asked to always call for remarks if they plan on working outside of delniated work area to prevent injury or property damage. BB 10 16 20
Southern California Gas Company | N | RIVERSIDE | NORCO | 2020-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | RANDI COMMUNICATIONS | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | signal interference with other utilities in area. Service missmarked by 3
Southern California Gas Company | N | RIVERSIDE | NORCO | 2020-04-23 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HHS COMMUNICATION | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | locator signal jumped to other utilities that stayed along curb at end of cul de sac. our 2 inchpem continued straight.
Southern California Gas Company | N | RIVERSIDE | NORCO | 2020-08-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HCI | NORCO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | contractor damages unmarked gas facility. contractor was asked to call for remarks to verify markings to prevent injury or property damage. company locator was counselled to verify that all facilities are marked within the delineation. BB 9320
Southern California Gas Company | N | RIVERSIDE | NORCO | 2020-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ALABBASI CONSTRUCTION | PERRIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damagedï¿½facilities while exposing it by hand digging.ï¿½ USA marks good.
Southern California Gas Company | N | RIVERSIDE | NORCO | 2020-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ALABBASI CONSTRUCTION | PERRIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | USA valid and marks accurate. Contractor failed to use adequate caution while excavating around service.ï¿½
Southern California Gas Company | N | RIVERSIDE | NORCO | 2020-08-30 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | NORCO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Occupant digging for fence
Southern California Gas Company | N | RIVERSIDE | NORCO | 2020-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Augur | 0.75 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | C ONE COMMUNICATIONS | FONTANA | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | USA was not current. Expired 92920 and damage occurred on 93020.
Southern California Gas Company | N | RIVERSIDE | NORCO | 2020-06-04 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 11 |  | ALABBASI | RIVERSIDE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | contractor damaged gas facility with backhoe. theï¿½ facility was mismarked. the contractor exposed the marked abandon main. the locator did not open the WHIP cloud to see the main replacement. BB 6920
Southern California Gas Company | N | RIVERSIDE | NORCO | 2020-06-01 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ALABBASI CONSTRUCTION | PERRIS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor installing storm drain hit unmarked gas facility with backhoe. the service was mapped incorrectly. ETD was asked to sweep area of excavating while locating. Steel service was replaced with plastic and will be mapped correctly. BB 6320
Southern California Gas Company | N | RIVERSIDE | NORCO | 2020-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | ALABASSI CONSTRUCTION | PERRIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Unsafe excavation practices by not hand exposing service laterals prior to machine excavation. Marks buried and not maintained. Contractor has admitted fault. Marks good.
Southern California Gas Company | N | RIVERSIDE | NORCO | 2020-08-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | ALABBASI CONSTRUCTION | PERRIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to use safe excavation practices and hand expose service crossings. Also did not maintain marks and covered them with spoil. Contractor has admitted fault.ï¿½
Southern California Gas Company | N | RIVERSIDE | NORCO | 2020-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | NORCO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | no usa, homeowner installing sewer and hit service with backhoe.
Southern California Gas Company | N | RIVERSIDE | NORTH PALM SPRINGS | 2020-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HERMAN WEISSKER | JURUPA VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Unmapped service in GIS. Service history was split between 2 different outputs due to street named differently. Locator unable to search. Locked property with no meter at site, riser only
Southern California Gas Company | N | RIVERSIDE | NUEVO | 2020-06-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | NUEVO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner planting trees on the property and struck service with backhoe. No USA
Southern California Gas Company | N | RIVERSIDE | NUEVO | 2020-06-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | INTERNATIONAL LINE BUILDERS | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | crew was digging with backhoe when they damaged 0.50 inch cts line. Crew potholed gas marks and found communication line and assumed it to be the gas line.
Southern California Gas Company | N | RIVERSIDE | NUEVO | 2020-09-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | NUEVO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging for electrical, home owner damaged service
Southern California Gas Company | N | RIVERSIDE | NUEVO | 2020-03-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 500 |  | 1 |  | JOAQUIN GARCIA | NUEVO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Trenching for electricity
Southern California Gas Company | N | RIVERSIDE | NUEVO | 2020-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | JOEL ROSALES | NUEVO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner digging to repair sewerseptic struck service with backhoe. Failed to notify USA crew marked and they were advised of digalert811
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2020-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ITX CONSTRUCTION | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor failed to call USA.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2020-09-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | THE LAKES FACILITY MAINTENANCE | PALM DESERT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor Failed to call USA. Contractor is fully Responsible.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2020-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GEN 3 EARTHWORKS | LA QUINTA | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Contractor dug before 48 hour time requirement. Contractor is fully responsible.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2020-01-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TOMMY ROOTER PLUMBING COMPANY | INDIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was working on sewer and hit 0.5inch cts service with shovel No USA was called
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2020-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | CONSERVE LAWNCARE | THOUSAND PALMS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging with shovel to install irrigation lines when gas line was hit.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2020-09-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JOSE CASTANEDA | CATHEDRAL CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit plastic service while performing sewer work. Contractor failed to call USA and is fully responsible.ï¿½
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2020-12-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DOWNING CONSTRUCTION INC | REDLANDS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged plastic service while excavating for water installation. Contractor did not call in for a USA until after they damaged plastic service.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2020-06-30 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | ALISO ELECTRIC | LAGUNA HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plastic service damaged by Contractor with a backhoe while excavating to install electric conduit. No USA
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2020-01-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | WOODHAVEN COUNTRY CLUB | PALM DESERT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was installing a new water service when they hit a 0.5inch CTS service with their shovel No USA was called
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2020-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | PALM DESERT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hire by HOA to repair some irrigation hit service line with shovel. No USA was called.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2020-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | SOUTHWEST PLUMBING INC | THOUSAND PALMS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to pothole utility knowing it was there. Contractor is fully responsible.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2020-01-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | STURGEON ELECTRIC | CHINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractorï¿½ claimed that when they were pulling out concrete that it hit the 1 service line line was marked and potholed
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2020-09-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | LEONIDA BUILDERS INC | CANYON COUNTRY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to hand expose plastic service. Verification was made by LCT that marks were visible.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2020-09-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | EVERGREEN LANDSCAPING | CATHEDRAL CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service with shovel while excavating to plant a tree. Contractor failed to call USA. Contractor is fully responsible.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2020-04-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ALMS UNDERGROUND CONSTRUCTION | CATHEDRAL CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor failed to pothole service before digging with backhoe. USA was good and current.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2020-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | SW PLUMBING | THOUSAND PALMS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor Failed to call USA. Contractor is fully Responsible.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2020-12-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CALIFORNIA BORING INC | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Cal Bore deviated from their orginal bore path and hit plastic service in a area ï¿½that was not exposed.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2020-07-30 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ACCESS GENERAL CONTRACTING | WESTMINSTER | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Access General SCG Contractor for GIPP damaged service while excavating to install meter guards. Valid USA, marked correctly
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2020-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | PALM DESERT | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Assumed abandoned steel service was active. Service is actually plastic
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2020-06-12 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | LEONS LANDSCAPING TREE SERVICE INC | INDIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was installing drains for landscaping when 2 inchï¿½ Main was damaged with shovel. No USA notification
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2020-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | PALM DESERT | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner claiming responsibility. Hired day laborer for installation ofï¿½wall who damaged service
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2020-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | DUNN S DESERT LANDSCAPING | PALM DESERT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscaper putting in palm trees and hit line with shovel.No USA notification
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2020-10-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | COCHRAN COMMUNICATION CONSTRUCTION | CATHEDRAL CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging to replace cable vault hit gas service with shovel. Contractor failed to contact USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2020-09-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | DOWNING CONSTRUCTION INC | REDLANDS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator claims to have been hand exposing service and severed with shovel
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2020-09-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DOWNING CONSTRUCTION INC | REDLANDS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged while pulling boulder out of excavation. Contractor is fully responsible.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2020-10-19 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LAZER BACKHOE SERVICES | GRAND TERRACE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was aware of 2 inch plastic main but assumed it was deeper. Contractor failed to call USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2020-05-22 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HERMAN WEISSKER | RIVERSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | Weissker excavating for electrical work, hit 1 inch stub. Stub was located 10 outside of delineations. inchG inch chiseled on curb. Long side stub across street from 60115 Range View. No home at location, open lot.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2020-02-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ARCHITECTURAL BLUE | PALM SPRINGS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was grading for landscaping when the hit a inserted line with a bobcat No USA was called
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2020-02-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JOHN GINGER MASONARY | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per developer the 3rd party contractor digging there footings for their block walls hit the service with a backhoe No USA was calledï¿½
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2020-07-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | INTERNATIONAL LINE BUILDERS | JURUPA VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor bored in street lighting under sidewalk and damaged 1 inch service. Service noted properly in GIS and service history, but unmarked
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2020-08-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ROSARIO GARDENING | PALM SPRINGS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party Contractor excavating to repair irrigation leak and damaged gas service. Contractor did not contact dig alert and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2020-03-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SOUTHWEST PLUMBING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was digging around service to repair sewer and hit service with shovel No USA was called
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2020-06-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PLUMBING CONCEPTS WADE | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavating for water service, 1 inch service line hit by backhoe. No USA
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2020-07-10 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | CONSERVE LANDCARE | THOUSAND PALMS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA notification. 2 inch PU main damaged while excavating for tree. Hit occurred near end of main
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2020-11-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | BLUE SKY LANDSCAPE | CATHEDRAL CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Contractor removing tree and damaged serviceï¿½
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2020-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | BELLA BLUE WATER | INDIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to hand expose gas line to verify location. Contractor is fully responsible.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2020-02-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PERFECT POOLS AND CONSTRUCTION | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor failed to pothole service Hit service with backhoe while trying to go thru tree roots USA was called
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2020-10-14 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HORIZON BACKHOE | WINCHESTER | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit plastic main while excavating for sewer. Contractor failed to call in a USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2020-06-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | PALM SPRINGS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner excavating for drainage system. Hit service with a shovel, NO USA
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2020-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | PALM SPRINGS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service marked from previous USA tickets, but no current ticket on file. Service hit w shovel while trenching to install new gas service line
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2020-07-24 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 7 |  | HERMAN WEISSKER AHMAD LOWE | JURUPA VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Mismarked 2 inch main damaged by 3rd party Contractor. 7 outages. Hit by backhoe
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2020-05-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HAL J HALL CONSTRUCTION | CATHEDRAL CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavating to install palm tree. Damaged 1 inch PE service. No USA notification
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2020-09-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NBI LANDSCAPE DEVELOPMENT | SANTA ANA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | Excavator dug beyond parameters of initial ticket. Stub was marked on curb per notes in ticket by ETDï¿½
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2020-05-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | OCUG PROFESSIONAL LANDSCAPING | NUEVO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor failed to notify USA Dig alert.
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2020-06-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | PERRIS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged service while grading
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2020-12-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | 2020 PLUMBING | RIVERSIDE | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Upon arrival, 0.5 inch cts stub service was damaged and bent back. USA was called after the damage had occurred.
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2020-03-31 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Augur | 0.75 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | STURGEON ELECTRIC | CHINO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Service was mismarked EE was counseled and corrected to use all resources provided
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2020-08-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | GUS CARRILLO | PERRIS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging on expired ticket and called in new ticket but dug before 48hrs. Marks visible from previous ticket.
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2020-01-03 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | EMWD | PERRIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EMWD was installing a new water service ï¿½ They were trying to hand expose our gas pipeline and used a probing device to find our gas pipeline ï¿½ The probing device punctured a small hole in the top of ourï¿½gas main ï¿½
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2020-01-09 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Trencher | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | GIL PAMATZ | MENIFEE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Operator was trenching towards water meter box when their machine grabbed and badly bent our steel service ï¿½
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2020-08-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | PERRIS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit service line with shovel while digging wall footing.
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2020-03-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | PERRIS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | none
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2020-12-17 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | 2020 PLUMBING | RIVERSIDE | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 2 inch PE main was damaged with the backhoe. USA was called. Contractor was digging before valid start time.
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2020-05-12 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | EASTERN MUNICIPAL WATER DISTRICT | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged 2 inch PU Main......found main squeezed upon arrival
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2020-06-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MARCELINO MARTINEZ | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage by third party contractor when removing debris from a house fire DATE FIRE August 2018
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2020-11-24 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | UNDERGROUNG CONSTRUCTION | ONTARIO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Compnay contractor hitï¿½PE svc with backhoe while excavating trench for gas main replacement.ï¿½
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2020-02-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | ALABBASI CONSTRUCTION AND ENGINEERING | PERRIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor Damaged Service that was within 24 inches of visible marks Contractor failed to pothole mark
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2020-02-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | S S DIRECTIONAL DRILLING | NORCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor damaged our lines while using shovel to hand dig to expose our gas line
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2020-05-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TVEC INC | PERRIS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 0.50 inch PU Service
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2020-04-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | PERRIS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged service digging for fence post
Southern California Gas Company | N | RIVERSIDE | RANCHO MIRAGE | 2020-02-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | EVANKO S REMODEL | RANCHO MIRAGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor failed to call USA before digging ï¿½
Southern California Gas Company | N | RIVERSIDE | RANCHO MIRAGE | 2020-04-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PULTE HOMES | RANCHO MIRAGE | CA | N | Y | Yes | No | No | No | No | No | No | Shirley Construction found stub had previously been damaged by contractor installing irrigation and tied back.
Southern California Gas Company | N | RIVERSIDE | RANCHO MIRAGE | 2020-03-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | SO CAL BUILDERS | PALM DESERT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5inch branch service damaged while excavating to install new electrical panel No USAï¿½
Southern California Gas Company | N | RIVERSIDE | RANCHO MIRAGE | 2020-05-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | REDS CONSTRUCTION AND LANDSCAPE | INDIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Excavator grading lot and removed at least 1 of cover from previously installed SCG service line. Contractor cliamed installed shallow after removinglowering grade and service hit. Service cut back due to trench being backfilled and unable to safely reinstate service. Secondary contact for excavator isï¿½ 760 7026286
Southern California Gas Company | N | RIVERSIDE | RANCHO MIRAGE | 2020-06-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | RAMMELL CONSTRUCTION | PALM SPRINGS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was running lines for pool equipment and hit line with shovel. Existing USA on property was for demolition by another Company. Damaging party had no USA.
Southern California Gas Company | N | RIVERSIDE | RANCHO MIRAGE | 2020-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | WHITLEY S CONSTRUCTION | PALM DESERT | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator digging for pool line, damaged service. Service marked correctlyaccurately. Failed to potholeï¿½
Southern California Gas Company | N | RIVERSIDE | RANCHO MIRAGE | 2020-02-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | RANCHO MIRAGE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Owner of home was digging to install some electrical conduit No USA was called
Southern California Gas Company | N | RIVERSIDE | RANCHO MIRAGE | 2020-05-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | DL LANDCARE INC | CATHEDRAL CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscapers digging for irigation for palm tree damaged service. No USA
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-09-14 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 4 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | BLANCO CONSTRUCTION | BUENA PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to keep main exposed while boring and struck PLA gas main.ï¿½ USA marks were visible and accurate.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-06-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | WEKA INC | HIGHLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to maintain markings.ï¿½ Said they potholed but did not find service so they dug anyway.ï¿½ Reminded contractor to maintain markings and to call update to ticket to remark as needed.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-06-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | WEKA INC | HIGHLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor potholed marked line but it was abandoned.ï¿½ Signal for locator jumped to abandoned line resulting in active service not being marked and was struck with backhoe.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-07-17 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | CAMARILLO DRILLING INC | NUEVO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to pothole our service while boring in a fiber optic service.ï¿½
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | ALL AMERICAN ASPHALT | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor exposed service then began to excavate next to it when they struck it. Service was on mark.ï¿½
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | KATO LANDSCAPE CONSTRUCTION | FOUNTAIN VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Struck our marked service while digging to install conduit.ï¿½
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | O DUFFY CONSTURCTION | MENIFEE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to pothole facility and struck with an excavator.ï¿½ Service was accurately marked and visible.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-08-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | RIVERSIDE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant was removing a tree stump.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-11-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 48 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | RIVERSIDE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner excavating near gas line andï¿½struck gas svc with shovel.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-06-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SPECTRUM | COLTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged service with shovel No USA
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-11-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | WANKE DEVELOPMENT GROUP | ROWLAND HEIGHTS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor failed to call USA and struck facility hand digging.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-07-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NUTECH CONSTRUCTION | NUEVO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | After exposing our utility, they struck it with a shovel. Service was on mark.ï¿½
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | HCI | NORCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | A stub was struck within 24 inch of the main. Stub was not marked but was within tolerance of the main markings.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-06-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | RIVERSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Customer called in USA but did not have delineations.ï¿½ Locator still marked service and main.ï¿½ Marks accurate and visible.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-02-17 | Third party excavation damage | Riser | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | RIVERSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged Service installing fence post
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-04-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | WESTERN MUNICIPAL WATER DISTRICT | MARCH AIR RESERVE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor struck 2 inch main that was already exposed.ï¿½ The backhoe operator moved bucket and struck main causing the damage.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-07-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1.5 | 42 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | FENCE WORKS | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit main with Auger. No USA
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-05-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JUAN GONZALES | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging for wall footings failed to notify USA and struck Plastic service.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CHAMPION FIRE SYSTEMS INCORPORATED | RANCHO CUCAMONGA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor digging to repair water line struck service hand digging while removing tree roots.ï¿½ Marks were visible and accurate.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 12 |  | G M GRADING ENGINEERING | LAKE FOREST | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor digging for sewer install to new development hit unmarked gas line ï¿½ The locator marked within the incorrect delineation and failed to notice the additional delineation further in the intersection ï¿½ Locator said has been out there multiple times on other USA tickets for this new development and marked what he thought was the correct area
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-03-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ALEX MENDEZ | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor failed to notify USA and struck service while trenching for irrigation
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-01-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | DEMOLITION SERVICES | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While excavating for building construction contractor damaged service with backhoe ï¿½
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-09-08 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | KIP INCORPORATED | MURRIETA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Their ticket was on Autorenew since Feb 2020. Since then we have installed main in the area. Contractor did not request for remarks and struck our 2 main.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | RIVERSIDE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Son of owner was saw cutting root when he struck our service.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | CAMARILLO DRILLING | NUEVO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Stuck our service with a shovel while attempting to locate it.ï¿½
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-08-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CAMARILLO DRILLING | NUEVO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The service was struck by a directional drill. Service was not marked. The contractor was boring on the edge of their delineation.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-08-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SC FENCE COMPANY | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Fencing company was digging for a fence post and struck a service. No USA.ï¿½
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-08-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ALL PLUMBING AIR SOLUTIONS | RIVERSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Stuck service with shovel while attempting to expose it.ï¿½
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-05-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 48 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | RIVERSIDE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner digging with shovel in yard and hit neighbors service line. Home owner was digging a ditch to prevent parking on the yard
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NCI VERIZON | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was digging a trench within inches our our main and marks. They stuck an service within our main marks.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-06-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CAL EMPIRE ENGINEERING | REDLANDS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor struck and abandoned service within 24 inch of main. Main was on Mark.ï¿½
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-05-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | RIVERSIDE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | home owner damages unmarked gas facility while excavating to remove a tree in his yard. USA was not notified. Home owner was asked to always contact dig alert prior to any excavating so utilities can be marked to prevent injury or property damage. BB 6320
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-11-23 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RANJO CONTRACTORS | COLTON | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor cut through 2 inch plastic main while cutting wood for sewer repair.ï¿½ Digging on expired USA ticket.ï¿½ Marks still visible.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | SCOT HOCHSTETLER CONTRACTING INC | HEMET | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Plumbing company excavated before their 48 hours.ï¿½
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-11-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ALLEN LIGHTING SERVICES | COLTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While potholing for our service, they damage a 1 inch plastic line with a shovel.ï¿½
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ALPHA COMPANY | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor installing fencing and failed to notify USA and struck facilities hand digging.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-01-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | PAUL BOGNER POOLS | RIVERSIDE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Service was in casing and signal bled onto older steel pipe ï¿½ Contractor was cutting pipe out of the way that was not marked and caused leak to plastic insert
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-12-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | LISTON CONSTRUCTION | RIVERSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hand digging for sewer struck facilities.ï¿½ Marks visible and accurate.ï¿½
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-11-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | ARI JET COMMUNICATIONS | POMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While attempting to directional drill in fiber casing, they struck a 0.5 plastic service. They potholed and located an abandoned steel line but did not find the newer plastic service under it.ï¿½
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MP7 | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor boring in conduit potholed gas service but misjudged their shot and struck service with a directional bore.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-12-22 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | NA |  | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor Struck plastic service while hand exposing.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-06-12 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CITY OF RIVERSIDE WATER DEPARTMENT | RIVERSIDE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Water company struck main due to mismark.ï¿½ Bare tracer wire and locator signal jumped to other utilities in the area.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-09-28 | Third party excavation damage | Riser | Steel | Backhoe/Trackhoe | 0.75 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DEMOLITION SPECIALIST INC | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Gradingcleaning lot and struck riser causing damage.ï¿½ No USA called.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-09-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | J M LEYVA GENERAL ENGINEERING | PERRIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Struck our service while hand digging to locate their sewer line.ï¿½
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-10-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 48 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | RIVERSIDE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hit plastic service with shovel while excavating for water line repair.ï¿½
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-12-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ARISET COMMUNICATIONS | POMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor potholing to expose and struck facility while hand digging.ï¿½ Marks visible and accurate.ï¿½ï¿½
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-05-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | RIVERSIDE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner was grading backyard with skid steer when he struck our meter, causing a leak.ï¿½
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-01-16 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | 4 WEST PIPE LINE INC | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | No mapping for service line that was cut back ï¿½ Hit with excavator ï¿½ service line has been properly abandoned
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-03-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SUPERIOR CONCRETE AND MASNRY | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor failed to notify USA and struck service
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-06-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 44 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NAGDA HOME GROUP | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party damage. NO USA
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-06-13 | Third party excavation damage | Riser | Polyethylene Pipe | Not Available | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | damage to Riser by unknown person, possibly developer doing work. New homes not yet occupied.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-07-06 | Third party excavation damage | Riser | Steel | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PAUL BINNQUIST | NA |  | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No | No damage to SUOF. | No damage to SUOF. | Contractor grading lot struck riser without calling USA.ï¿½ Fire department shut off curb valve and departed scene.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-11-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | ECOWORKZ | BREA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor failed to notify USA and struck service with shovel while installing electric line for homeowner.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-02-03 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | BECKER PIPELINE | RIVERSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to pothole marked service and struck with backhoe digging for a drain
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-12-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | CAMARILLO DRILLING | NUEVO | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Foreman hit plastic service with bore machine. no gas marks. company was drilling with no marks yet. Informed contractor to verify with gas company before digging.ï¿½ï¿½Contractor dug before markings completed with a new work to begin date confirmed by both parties.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HENKELS MCCOY | FONTANA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor struck an unmarked service while digging to install electric conduit.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2020-06-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | RIVERSIDE | SAN JACINTO | 2020-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | INTEGRITY GENERAL ENGINEERING | CORONA | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Damage0.5 inch service was hit by 3rd party contractor with shove. USA was not valid until the following day.ï¿½ Working without a USA
Southern California Gas Company | N | RIVERSIDE | SAN JACINTO | 2020-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SD DESIGN CONSTRUCTION | WEST COVINA | CA | N | N | Yes | Yes | Yes | Yes | No | Yes | Yes | Damage
Southern California Gas Company | N | RIVERSIDE | SAN JACINTO | 2020-09-29 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 3 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7862 |  | 1 |  | AAA PARING | RIALTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | A 3 inch steel gas Main was damaged by a 3rd Party Contractor using a Grader. SoCalGas crews responded and controlled the gas at 12:30. There were no injuries or other damages resulting from the incident. This was reported to the CPUC due to Public Awareness, after receiving 10 odor complaint calls in the same vicinity.
Southern California Gas Company | N | RIVERSIDE | SAN JACINTO | 2020-01-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TBU CONSTRUCTION | BEAUMONT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage to stub service occurred when Contractor struck line with trencher while digging to install street light conduit NO USA ticket ï¿½
Southern California Gas Company | N | RIVERSIDE | SAN JACINTO | 2020-10-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JAIME OLIVAS | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage Hit 0.5 inch service with backhoe. No USA
Southern California Gas Company | N | RIVERSIDE | SAN JACINTO | 2020-11-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | PLUMBING 4 LESS | HEMET | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging for some plumbing work failed to notify USA and struck facilities.ï¿½
Southern California Gas Company | N | RIVERSIDE | SAN JACINTO | 2020-06-29 | Third party excavation damage | Main | Polyethylene Pipe | Trencher | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | SLATER INC | FONTANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage 2 inch main, no USA
Southern California Gas Company | N | RIVERSIDE | SAN JACINTO | 2020-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CLARK CONTRACTORS INC | MURRIETA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1 inch PLastic service
Southern California Gas Company | N | RIVERSIDE | SAN JACINTO | 2020-07-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | KANA PIPELINE INC | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor trenching to install water line.
Southern California Gas Company | N | RIVERSIDE | SAN JACINTO | 2020-03-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JL BLODGETT POOLS | HEMET | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit service with shovel while digging for drainage and water to install pool
Southern California Gas Company | N | RIVERSIDE | SAN JACINTO | 2020-08-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | NA | SAN JACINTO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | line was hit with post hole digger
Southern California Gas Company | N | RIVERSIDE | SAN JACINTO | 2020-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 2 |  | NA | SAN JACINTO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | uncovered damaged service line hit with shovel
Southern California Gas Company | N | RIVERSIDE | SAN JACINTO | 2020-03-09 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 4 |  | NPL | MIRA LOMA | CA | Y | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor digging up service using shovel when they encountered a large root above our gas line They pushed through the root with the shovel and hit ruptured the gas service ï¿½
Southern California Gas Company | N | RIVERSIDE | SAN JACINTO | 2020-03-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NPL | MIRA LOMA | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Company Contractor was doing Main and Service replacement
Southern California Gas Company | N | RIVERSIDE | SAN JACINTO | 2020-01-30 | Third party excavation damage | A service line with an excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | SAN JACINTO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | property owner was demolishing his home NO USAï¿½
Southern California Gas Company | N | RIVERSIDE | SAN JACINTO | 2020-01-17 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Trencher | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PBU | SAN JACINTO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | damaged stub
Southern California Gas Company | N | RIVERSIDE | SUN CITY | 2020-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | FODDRILL CONSTRUCTION | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damage USA was marked should have hand dig
Southern California Gas Company | N | RIVERSIDE | TEMECULA | 2020-11-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SHAWN MCDADE | LAKE ELSINORE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor failed to notify USA digï¿½ alert of excavation and damaged service line
Southern California Gas Company | N | RIVERSIDE | TEMECULA | 2020-10-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | H S CONSTRUCTION | ONTARIO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Locator error in interpreting GIS service locations as posted. Unable to find MSA overgrown with bushes at building where damage occurred.
Southern California Gas Company | N | RIVERSIDE | TEMECULA | 2020-01-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DOWNING CONSTRUCTION | REDLANDS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Incorrect company recordsï¿½
Southern California Gas Company | N | RIVERSIDE | TEMECULA | 2020-06-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | INTERNATIONAL LINE BUILDERS | JURUPA VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor failed to hand expose prior to using mechanical means per the USA Law. They failed to call for remarks. They were working onï¿½electrical facilities.
Southern California Gas Company | N | RIVERSIDE | TEMECULA | 2020-06-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | TEMECULA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer while digging up roots damaged service. Supervision had locator recently markï¿½line for following week to squeeze service while roots and stumps removed. Customer decided to start digging before and damaged service.ï¿½
Southern California Gas Company | N | RIVERSIDE | TEMECULA | 2020-12-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ACTION POWER COMPANY | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor placing temporary power pole without USA and damaged service line
Southern California Gas Company | N | RIVERSIDE | TEMECULA | 2020-07-13 | Third party excavation damage | A service line with an excess flow valve installed | Material not known | Hand Tools | 0 | 60 | 55 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CASS ARRIETA | MENIFEE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas service while installing electrical box. SCG facilities not gassed up, air only.
Southern California Gas Company | N | RIVERSIDE | TEMECULA | 2020-07-13 | Third party excavation damage | A service line with an excess flow valve installed | Material not known | Hand Tools | 0 | 60 | 55 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CASS ARRIETA | MENIFEE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas service while installing electrical box. SCG facilities not gassed up, air only.Contractor damaged gas service while installing electrical box. SCG facilities not gassed up, air only.
Southern California Gas Company | N | RIVERSIDE | TEMECULA | 2020-03-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ILB INTERNATIONAL LINE BUILDER | JURUPA VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Unmarked stub not mapped in GIS system
Southern California Gas Company | N | RIVERSIDE | TEMECULA | 2020-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | W A RASIC CONSTRUCTION | LONG BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Crew failed to pothole by hand prior to using mechanical means. Unable to find active USA ticket for this contractor or area, newly submitted ticket found for this work area is with a legal start date of 762020
Southern California Gas Company | N | RIVERSIDE | TEMECULA | 2020-01-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BEDON CONSTRUTION INC | TEMECULA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | corrections made to EIR for IC
Southern California Gas Company | N | RIVERSIDE | TEMECULA | 2020-01-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | AMERICAN LANDSCAPES | NA | CA | N | N | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA NOTIFICATION MADE
Southern California Gas Company | N | RIVERSIDE | TEMECULA | 2020-11-18 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | MAMCO DBA ALABBASI CONSTRUCTION | PERRIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor replacing a water main.ï¿½
Southern California Gas Company | N | RIVERSIDE | TEMECULA | 2020-04-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | DOWNING CONSTRUCTION | REDLANDS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Damaged Stub that was not marked due to no info in service history and GIS mapping. Crew did abandonï¿½stub.ï¿½
Southern California Gas Company | N | RIVERSIDE | THERMAL | 2020-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | CITADEL COMMUNICATIONS GROUP | INDIO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor hit inserted plastic service while trenching for telephone. Locator failed to mark service and verify with Service history.
Southern California Gas Company | N | RIVERSIDE | THERMAL | 2020-11-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JONES BROS | COACHELLA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to hand expose as required and hit plastic service with a backhoe.
Southern California Gas Company | N | RIVERSIDE | THOUSAND PALMS | 2020-09-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | THOUSAND PALMS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner excavating to install fence posts, damaged service. No USA notification
Southern California Gas Company | N | RIVERSIDE | THOUSAND PALMS | 2020-11-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | THOUSAND PALMS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner hit plastic service while digging up a tree stump. Owner did not contact USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | THOUSAND PALMS | 2020-06-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SEWER SEPTIC PRO INC | DESERT HOT SPRINGS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Party Contractor installing sewer lateral and hit line with backhoe. Failed to pothole service. Service marked correctly
Southern California Gas Company | N | RIVERSIDE | THOUSAND PALMS | 2020-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 1 |  | KEN DIAMOND | THOUSAND PALMS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | a homeowner was digging with a shovel to repair a water service line and damaged a 0.5-inch plastic gas service, causing a release of gas. A SoCalGas crew responded and controlled the gas. There were no injuries resulting from this incident. Repairs were made to the plastic service and gas service was restored same day. Further investigation showed that No USA ticket was requested prior to the excavating. This incident was reported to the CPUC when SoCalGas became aware of media coverage.
Southern California Gas Company | N | RIVERSIDE | WILDOMAR | 2020-11-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | W E S A | LAKE ELSINORE | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Locator failed to utilize all resources to mark gas facilityï¿½
Southern California Gas Company | N | RIVERSIDE | WILDOMAR | 2020-06-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RICHARD OSORIO | SANTA ANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA notification made to one call system.
Southern California Gas Company | N | RIVERSIDE | WILDOMAR | 2020-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | INTERNATIONAL LINE BUILDERS | WILDOMAR | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | hard ground led to damage as crew was hand exposing
Southern California Gas Company | N | RIVERSIDE | WINCHESTER | 2020-09-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | FRIEND | WINCHESTER | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging to install new fence. hit gas line
Southern California Gas Company | N | RIVERSIDE | WINCHESTER | 2020-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NP MECHANICAL | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failure to pothole by hand prior to using mechanical equipment.
Southern California Gas Company | N | RIVERSIDE | WINCHESTER | 2020-06-22 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | TRAXX | LOS ALAMITOS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor was digging on expired USA ticket, failed to pothole by hand as required and damaged 4 inch PE main with backhoe bucket.
Southern California Gas Company | N | RIVERSIDE | YUCAIPA | 2020-10-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | DOTY BROTHERS CONSTRUCTION | NORWALK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor installing electrical for SCE hit unmarked 0.75 inch steel stub with backhoe. No record of stub in service history.
Southern California Gas Company | N | SAN BERNARDINO | ADELANTO | 2020-06-22 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HERMAN WEISSKER | JURUPA VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | damage to 2 inch plastic stub by contractor digging up trench to install underground substructures and conduits.
Southern California Gas Company | N | SAN BERNARDINO | BLOOMINGTON | 2020-11-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | BLOOMINGTON | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged service with backhoe. No USA
Southern California Gas Company | N | SAN BERNARDINO | BLOOMINGTON | 2020-12-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 1.25 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | KPRS | BREA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | 1.25 inch stub was hit by grader. No service history for this service. A plastic service was abandoned previously for the same lot. The steel service was not on GIS or service history.
Southern California Gas Company | N | SAN BERNARDINO | BLOOMINGTON | 2020-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 0 | 0 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | JOHN RUIZ | BLOOMINGTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The owner was trying to remove a tree stump from his property and cut through our service line with a saw He said he did not call 811 to locate our service line
Southern California Gas Company | N | SAN BERNARDINO | BLOOMINGTON | 2020-07-01 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NPL | ONTARIO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Our contractor NPL did not locate handï¿½expose our 0.5 inch IPS service.
Southern California Gas Company | N | SAN BERNARDINO | BLOOMINGTON | 2020-02-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MCKINNEY CONSTRUCTION | FONTANA | CA | N | N | Yes | Yes | No damage to SUOF. | Yes | No damage to SUOF. | Yes | Yes | While trenching for Water contractor hit un marked stub Locator could not locate it so marked it off GIS which ended up being 13 off
Southern California Gas Company | N | SAN BERNARDINO | BLOOMINGTON | 2020-10-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GUY YOCOM CONSTRUCTION INC | NORCO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | This was an damage to our 2 inch PLA service with out USA.
Southern California Gas Company | N | SAN BERNARDINO | BLOOMINGTON | 2020-06-26 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NPL | MIRA LOMA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Gas service damaged by contractor NPL while digging with backhoe. Contractor failed to pothole prior to excavating. Facility was marked. Damage fully repaired.
Southern California Gas Company | N | SAN BERNARDINO | BLUE JAY | 2020-11-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PALMERS PLUMBING | RIMFOREST | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | PE service struck while digging with out a USA
Southern California Gas Company | N | SAN BERNARDINO | CEDAR GLEN | 2020-08-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SCORPION BACKHOE | WINCHESTER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1 inch PE stub was hit by contractor excavating on location with a backhoe. he did not hand excavate to find the service.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | CEDAR GLEN | 2020-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | CEDAR GLEN | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Locate USA not requested
Southern California Gas Company | N | SAN BERNARDINO | CEDAR GLEN | 2020-02-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SECC | CHINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging to install post hit service with shovel No USA
Southern California Gas Company | N | SAN BERNARDINO | CEDARPINES PARK | 2020-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | CEDARPINES PARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer hand digging to set footing with no USA. Hit service.
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2020-06-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 44 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DOTY BROS | NORWALK | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Third party damage. No service history or service ID. Unmapped on GIS
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2020-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | BIG BEN ENGINEERING | IRVINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Piece ofï¿½ concrete fell into excavation where our gas service was potholed. Gas line was damaged.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2020-08-17 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | BIG BEN CONSTRUCTION | IRVINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | excavator damaged gas service with shovel while potholing our pipe.
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2020-06-08 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 44 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BIG BEN ENGINEERING | IRVINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party damage. USA valid. Correctly Marked. Failed to pothole.
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2020-04-28 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 44 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | BIG BEN CONSTRUCTION | IRVINE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Third party damage. Mismark. valid USA. Locator received good signal with RD8100. Location of damage was right where steel main transitioned to plastic. Hooked up again at jobsite and verified marks were consistant with locator signal. Employee was coached and counseled.
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2020-04-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 44 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BIG BEN CONSTRUCTION | IRVINE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Third party contractor damaged unmapped stub. USA valid
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2020-10-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BIG BEN CONSTRUCTION | IRVINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service damaged by backhoe. failed to pothole. USA marks correct
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2020-05-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 44 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | CHINO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party Damage. No USA
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2020-03-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 44 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CITY OF CHINO | CHINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party damage. USA valid. Marked correctly. Failed to hand expose. Back hoe pulled on steel service and pulled on service
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2020-07-23 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 4 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CROWN COMMUNICATIONS | ONTARIO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor installing conduit bored through main. GIS inaccurately shows main jogging south. marks off 3. Valid USA
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2020-04-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 2 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PARKCREST CONSTRUCTION INC | ONTARIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor cored through 2 inch main. No USA called.
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2020-01-28 | Third party excavation damage | Miscellaneous/Other | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CAL WEST UNDERGROUND INC | NORCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | Contractor was installing electrical conduit and hit service with backhoe
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2020-10-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CAL WEST UNDERGROUND | NORCO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party damage, contractor hit plastic service while excavating for barrier post.
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2020-06-15 | Third party excavation damage | Riser | Steel | Backhoe/Trackhoe | 1 | 44 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RCA CONSTRUCTION CLEAN UP | ONTARIO | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | Not a Dig in. Third party contractor working for developer hit bypass stop cock with skip loader. New construction area.
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2020-01-21 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | H7 | TEMECULA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was trenching to install utility services with backhoe they hit the gas main
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2020-07-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 44 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SCW CONTRACTORS | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | No | miss marked service location , gas marks off byï¿½32 inches
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2020-07-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SCW CONTRACTING CORP | FALLBROOK | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Marked abandoned line. Live line 4 inch out of tolerance. USA expired 61520
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2020-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | BIG BEN CONSTRUCTION | IRVINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Backhoe hit service, trenching for water. Marks correct
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2020-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BIG BEN CONSTRUCTION INC | IRVINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator used backhoe to dig within 2 feet of our plastic service and damaged our pipe
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2020-02-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2020-04-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 20 | 15 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | AAA PAVING | RIALTO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | none
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2020-06-12 | Third party excavation damage | Miscellaneous/Other | Steel | Backhoe/Trackhoe | 0.75 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DOWNING CONSTRUCTION INC | REDLANDS | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | excavator removing other abandoned pipe damaged unknown stub not found on GISï¿½
Southern California Gas Company | N | SAN BERNARDINO | CHINO HILLS | 2020-11-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | INCEPTION ELECTRIC CO | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Electrical worker was installing grounding rod and struck gas svc.
Southern California Gas Company | N | SAN BERNARDINO | CHINO HILLS | 2020-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | AMERICAN INTEGRATED SERVICES | WILMINGTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working for SCE were digging soil with hand tools and struck our gas line.
Southern California Gas Company | N | SAN BERNARDINO | CHINO HILLS | 2020-04-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | CHINO HILLS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | while excavating for landscapingï¿½ HO damage 0.50 IPS service line
Southern California Gas Company | N | SAN BERNARDINO | CHINO HILLS | 2020-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 26 |  | CITY OF CHINO HILLS | CHINO HILLS |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Water company pulled steel water service out of excavation with bumper of truck and damaged plastic gas service
Southern California Gas Company | N | SAN BERNARDINO | CHINO HILLS | 2020-11-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ALL AROUND UNDERGROUND CONTRACTORS | ORANGE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | excavator damaged gas service with Mini X.
Southern California Gas Company | N | SAN BERNARDINO | CHINO HILLS | 2020-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | A CUT ABOVE GRADING | MURRIETA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | excavator struck buried riser with backhoe. Unmarked.
Southern California Gas Company | N | SAN BERNARDINO | CHINO HILLS | 2020-01-15 | Third party excavation damage | Meter | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit gas service with pick axe and blowing
Southern California Gas Company | N | SAN BERNARDINO | CHINO HILLS | 2020-03-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | H O ROBERT HOLLINSWORTH | CHINO HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | while excavating to install new sewer line the contractor damage the 0.5inch CTS service
Southern California Gas Company | N | SAN BERNARDINO | COLTON | 2020-11-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PACIFIC COAST PIPE | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Construction crew replacing water service broke gas service
Southern California Gas Company | N | SAN BERNARDINO | COLTON | 2020-07-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MANUEL SCHOENEN | HELENDALE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | no USA was called in for work area.
Southern California Gas Company | N | SAN BERNARDINO | COLTON | 2020-11-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | VWC BUILDERS | COLTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per the builders, it is unknown how damage occurred.ï¿½ They claim the riser was already damaged upon their arrival.ï¿½ The riser was sheered at grade.ï¿½ Permanent repairs were made by SCG crew.
Southern California Gas Company | N | SAN BERNARDINO | COLTON | 2020-01-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LEVI LANDSCAPING | FOOTHILL RANCH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 1 PE service while landscaping
Southern California Gas Company | N | SAN BERNARDINO | COLTON | 2020-05-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MARCOS SUNES | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit plastic service line with posthole digger while installing fence NO USA, I educated homeowner and Contractor on USA law.
Southern California Gas Company | N | SAN BERNARDINO | COLTON | 2020-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RODRIGUEZ DISKING | SAN BERNARDINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | grader doing weed abatement for fire dept. damaged gas line.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | COLTON | 2020-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HP COMMUNICATIONS | FONTANA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While potholing gas facilities contractor damaged 0.5 inch cts service with shovel.
Southern California Gas Company | N | SAN BERNARDINO | COLTON | 2020-10-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MEDIA COMMUNICATIONS | FONTANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | this was a 0.5 CTS service damage by a 3rd party contractor with a current USA.
Southern California Gas Company | N | SAN BERNARDINO | COLTON | 2020-12-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | COLTON | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner was expanding hole at foundation digging near gas meter and hit 0.5 cts service line with shovel.
Southern California Gas Company | N | SAN BERNARDINO | COLTON | 2020-01-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NOBLE EMC | BUENA PARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | EE of contractor says he was digging out trench and gas line was already leaking so he capped it to stop leak
Southern California Gas Company | N | SAN BERNARDINO | COLTON | 2020-05-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | COLTON | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was digging with No USA to planï¿½trees in front of his yard ï¿½
Southern California Gas Company | N | SAN BERNARDINO | CRESTLINE | 2020-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | GILBERT ACUNA PLUMBING | CRESTLINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | USA was not called.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | CRESTLINE | 2020-08-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | BATES CONTRACTING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service hit with shovel
Southern California Gas Company | N | SAN BERNARDINO | CRESTLINE | 2020-03-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | BENNETT EXCAVATION | CRESTLINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor probing for Septic tank hit gas service Did not call for USA
Southern California Gas Company | N | SAN BERNARDINO | CRESTLINE | 2020-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 1 |  | PAR ELECTRIC | RANCHO CUCAMONGA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Par was drilling to install guide wireï¿½
Southern California Gas Company | N | SAN BERNARDINO | CRESTLINE | 2020-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | PAR ELECTRIC | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Replacing pole and hit PE service.
Southern California Gas Company | N | SAN BERNARDINO | CRESTLINE | 2020-04-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged service
Southern California Gas Company | N | SAN BERNARDINO | CRESTLINE | 2020-07-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ASCENCIO GENERAL CONSTRUCTION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | no ticket number givenï¿½by LCT
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2020-12-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PAULUS ENGINEERING ROBERT BENITEZ | ANAHEIM | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | This was a damage to a 0.5 inch CTS stub service that was not properly mapped on GIS and service history , ETD marked service 3 feet North of actual location of service line by service history and weak signal.
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2020-03-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 44 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | FONTANA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | third party damage Home owner hit service with shovel while attempting to dig hole for post to fence
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2020-01-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | SHAWNEE CONST | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit svc line with trencher
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2020-04-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 16 |  | KANA PIPELINE | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor hit 2 inch main did not see any marks in the area.
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2020-05-18 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NOVI GENERAL ENGINEERING | LAKE ELSINORE | CA | N | Y | Yes | Yes | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Found 1 inch steel service damaged.
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2020-06-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Directional Drilling | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HP COMMUNICATION | CORONA | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | while contractor was DBoring to install new Verizon line the contractor bore hit our 1 inch PLA stub serviceï¿½
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2020-11-24 | Third party excavation damage | Riser | Steel | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | WALLACE P JOHNSON AND PLUMBING | ATWOOD | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | this was a damage to an AL riser while 3rd party contractor was grinding for walk way.
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2020-01-28 | Third party excavation damage | Miscellaneous/Other | Polyethylene Pipe | Hand Tools | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BRYAN RITCHIE | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor was landscaping for irrigation system and hit an undocumented 2 PE stub
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2020-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 0 | 0 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | GREEN BEE | PERRIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor servered half inch IPS with shovel gas was not blowing due to EFV
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2020-11-25 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | T E ROBERTS | ORANGE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | while installing water pipelines for the City of Fontana the 3rd party contractor damage our 0.75 inch service line.
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2020-04-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HECTO CO CONSTRUCTION | BLOOMINGTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA on this address.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2020-04-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HECTOR CONSTRUCTION INC | BLOOMINGTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor dug over marks with mini excavator he stated he forgot the marks were right there.
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2020-10-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | FONTANA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged unmarked gas facility while excavating for electrical. USA was not notified. Contractor was asked at site to always notify USA Dig alert 2 days prior to any excavating to prevent injury or property damage. BB 10 26 2020
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2020-11-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | STEVE JULIUS CONSTRUCTION | SAN CLEMENTE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Third party damaged 1 inch plastic service with excavator during demolition of a building.ï¿½ Facility was properly marked with paint and feathers.
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2020-11-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HERMAN WEISSKER INC | JURUPA VALLEY | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | this was a damage to a 1 inch PLA service not marked due to incorrect facility record on GIS, also no valid expired ticket.
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2020-04-20 | Third party excavation damage | Riser | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 45 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | CORONA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | none
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2020-08-25 | Third party excavation damage | Riser | Material not known | Grader/Scraper | 0 | 60 | 45 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | LENNAR | CORONA | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No | No damage to SUOF. | No damage to SUOF. | none
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2020-04-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | none
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2020-08-20 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RICHARD LOPEZ CONSTRUCTION | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | while excavating to install Electric lines the 3rd party contractor damage our 2 inch PLA main, No USA was called in for the site.
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2020-09-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | PARAMOUNT FENCE BUILDERS INC | JURUPA VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor installing a fence hit line with shovel.
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2020-01-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 44 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JBS | FONTANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Caller Contractor Nicholas Jimenez claims had called for a USA over a month and a half ago LCT informed him they expire Contractor did not provide USA ï¿½
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2020-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | FONTANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Valid USA, marks were good. customer failed to use caution while excavating near service.
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2020-03-13 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NPL | NA |  | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | NA
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2020-09-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MCKINLEY GENERAL ENGINEERING | FONTANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | this was a damage to a PLA service that was hit with a backhoe.
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2020-05-07 | Third party excavation damage | Main | Polyethylene Pipe | Trencher | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CAL WEST UNDERGROUND | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 2 inch PE main with backhoe. Main was marked at corner of intersection.
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2020-11-12 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MCKINNLEY CONSTRUCTION | FONTANA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | This was a damage to a 2 inch PLA mainï¿½
Southern California Gas Company | N | SAN BERNARDINO | GRAND TERRACE | 2020-08-27 | Operator excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 18 |  | NA | NA |  | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While working a leak and excavating in hard soil he hit PE tee.
Southern California Gas Company | N | SAN BERNARDINO | GRAND TERRACE | 2020-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CM CORP | GRAND TERRACE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | while prepping to demo house the contractor damage our 0.5 IPS service.
Southern California Gas Company | N | SAN BERNARDINO | GRAND TERRACE | 2020-09-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CM CORP | LAGUNA HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Second time damaged, was cut back previously. Will be abandoned.
Southern California Gas Company | N | SAN BERNARDINO | GRAND TERRACE | 2020-02-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ARTISONS CONSTRUCTION | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor grading with skid steer hit plastic service
Southern California Gas Company | N | SAN BERNARDINO | GRAND TERRACE | 2020-05-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BUILD IT GROUP LIC 461162 | NA |  | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged a second time previous gone, ticket expired. Previously marked same contractor. Did not take caution.
Southern California Gas Company | N | SAN BERNARDINO | GREEN VALLEY LAKE | 2020-07-30 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | GREEN VALLEY MUTAL WATER COMPANY | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | damaged 0.5 cts service while digging for water service repaired with 2ft of cts pipe and 2 fusion couplings.
Southern California Gas Company | N | SAN BERNARDINO | HESPERIA | 2020-02-05 | Third party excavation damage | Transmission Line in an HCA area | Material not known | Backhoe/Trackhoe | 36 | 782 | 650 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | H P COMMUNICATIONS | NA |  | N | Y | Yes | Yes | Yes | Yes | Yes | Yes | Yes | pipeline damaged while potholing
Southern California Gas Company | N | SAN BERNARDINO | HIGHLAND | 2020-11-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | UNITED PAVING CO | HIGHLAND | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged a 1 inch plastic service with a backhoe while digging to replace a water service.ï¿½ USA was not called.
Southern California Gas Company | N | SAN BERNARDINO | HIGHLAND | 2020-07-18 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  | 32 |  | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1 inch PE main damage by third party with a small back hoe.ï¿½ No USA notification.
Southern California Gas Company | N | SAN BERNARDINO | HIGHLAND | 2020-04-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | HERMAN WEISSKER | JURUPA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged 0.50 inchï¿½service with a shovel
Southern California Gas Company | N | SAN BERNARDINO | HIGHLAND | 2020-11-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | HIGHLAND | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner Hit The Plastic Service While Diggin To Install Retaining Wall.ï¿½ Homeowner Did Not Have Usa.ï¿½ It Was Explained To The Homeowner The Importance Of Having Usa Before Any Excavation Work Is To Begin.ï¿½ Let The Homeowner Know To Contact A Field Planner To Have The Plastic Lowered Before Resuming Work On The Retaining Wall.ï¿½ï¿½
Southern California Gas Company | N | SAN BERNARDINO | HIGHLAND | 2020-12-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HCI | NORCO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor hit plastic unknow stub, Locator was not picking up stub or showed in GIS.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | HIGHLAND | 2020-11-17 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RESOURCE ENVIRONMENT | LONG BEACH | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged gas service when attempting to remove footing of building.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | HIGHLAND | 2020-07-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | HIGHLAND | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | homeowner didï¿½not call for USA., hired a contractor to build block wall, and struck plastic service with rebarï¿½
Southern California Gas Company | N | SAN BERNARDINO | JOSHUA TREE | 2020-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JOSHUA BASIN WATER DISTRICT | JOSHUA TREE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Joshua Basin Water District was installing a water line when gas line was hit with anï¿½excavator. Current USA, mismarked SCG facilities
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2020-10-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | VINCE MESSINA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged service while digging footings for steps. Did not have a USA.
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2020-09-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SCORPION BACKHOE | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | crew was digging out power to set a box and damage two in main
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2020-02-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BATES CONSTRUCTION | CRESTLINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party failed to hand exposed has line and hit gas service with backhoe
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2020-07-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | OSCAR ORTEGA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | building retaining wall
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2020-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | RAY S PLUMBING | CRESTLINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged branch service.
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2020-11-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ELROD FENCE | JURUPA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged caused by excavator who did not protect in place the PE service marked out
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2020-06-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | LAKEARROWHEAD COM WTR DIST | BLUE JAY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Water company hit our service line with shovel and made comment to the crew they thought they didnt have to call 811 if they were hand digging.
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2020-09-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | LAKE ARROWHEAD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | no USA was called. contractor hit service while excavating footings.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2020-10-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CITY OF COMMERCE | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor did not call USA. was hand digging for poles then struck the service
Southern California Gas Company | N | SAN BERNARDINO | LOMA LINDA | 2020-11-30 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | TK CONSTRUCTION | SAN BERNARDINO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | crew hit svc with backhoe
Southern California Gas Company | N | SAN BERNARDINO | LOMA LINDA | 2020-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | LOMA LINDA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | homeowner and friend damaged plastic service while trying to dig up front yard to install sewer line. Plastic service was wrapped up inside a root. They didnt realize until it was too late that there was a gas line inside the root.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | LOMA LINDA | 2020-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | EHB E H BUTLAND CORP | RESEDA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging to expose Edison substructures damaged gas service with excavator
Southern California Gas Company | N | SAN BERNARDINO | MENTONE | 2020-01-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | WRIGHT SEPTIC | SAN JACINTO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | SAN BERNARDINO | MONTCLAIR | 2020-03-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 2 | 44 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | STURGEON ELECTRIC | CHINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor damaged 2 Steel main with a trencher Company potholed facility but failed to maintain clearance after potholing Facilities were correctly marked
Southern California Gas Company | N | SAN BERNARDINO | MONTCLAIR | 2020-02-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | THE HILL DALE GROUP | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service hit while hand exposing to verify location
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2020-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 44 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MORENO CARREON | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party damage. No usa
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2020-07-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 44 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 4 |  | PRECISION GENERAL CONTRACTORS | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor damaged PE main in private property while digging to repair a water leak. No usa.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2020-09-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | R I COMMUNICATIONS | BLOOMINGTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | excavator struck gas service while exposing with shovel
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2020-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | INTERNATIONAL LINE BUILDERS | RIVERSIDE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | excavator damaged unmarked branch service with shovel.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2020-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | J L DEVELOPMENT GROUP | POMONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged service with backhoe. No USA
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2020-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CITY OF ONTARIO | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service damaged with backhoe while digging for water. Correctly marked
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2020-11-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 44 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LANE SECURITY PAVING | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | repairing cable tv wires
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2020-11-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ALLIED PLUS | LA HABRA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Installing fiber optics
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2020-09-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ANY PROMO COM | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Owner grading to install footing for wall damaged service hand digging. No USA.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2020-07-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | EZ FENCO CO | JURUPA VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor Augering to install fence hit service line. No marks in delineated area. Valid USA
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2020-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | LARRY JACINTO CONSTRUCTION | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service while grading. Marks on curb within delineation. Contractor failed to pothole prior to grading.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2020-03-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Boring Equipment | 2 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ULTIMATE INTERNET ACCESS | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Pot hole was dug out in the street over 10 from bore path Visible marks for a stub were at the location of the damage The damaging party did not locate the line while potholing prior to boring The line was later found in the same pothole excavation after the damage occurred
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2020-10-30 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 44 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | CHRISTIANSON BROS GENERAL ENG INC | APPLE VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service was damage with a backhoe.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2020-06-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Homeowner excavating to expose gas line damaged pipe with shovelï¿½
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2020-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 44 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | CITY OF ONTARIO | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | THird party damage. Asphalt fell on service after facilities were exposed.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2020-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CHRISTENSEN BROTHERS | APPLE VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3 Party damage Installing sewer pipeï¿½
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2020-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 44 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BELLA AGUA SWIM | CHINO HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | excavator damaged gas service with a shovelï¿½
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2020-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NATHAN PLUMMER | ALTA LOMA | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Storm drain contractor hit unmarked service line with backhoe while trenching. Locator did not mark line after looking at GIS and seeing the service line coming off a side street Gingerwood Rd.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2020-07-31 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SAFEWAY ELECTRIC | COLTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging trench damaged service with mini excavator. No USA
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2020-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | LEVI LANDSCAPE LIC 804485 | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service line using trench excavator.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2020-06-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 44 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SAFEWAY ELECTRIC | COLTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party damage. No usa
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2020-03-11 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 44 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PACIFIC PRODUCTION PLUMBING | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor damaged 2 PE main while digging to install sewer
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2020-09-23 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GOTHIC LANDSCAPE | RIVERSIDE | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was excavating to install irrigation lines.ï¿½ No Visible delineations were visible and no SCG marks.ï¿½ Contractor struck 2 inch pla main.ï¿½ Main was not in GIS due to being a new track development.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2020-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 44 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SCOTT MCLEOD PLUMBING | RANCHO CUCAMONGA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party damage No USA
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2020-10-08 | Third party excavation damage | Main | Steel | Augur | 6 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  | 22 |  | CRISTENSEN BROTHER | APPLE VALLEY |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Coring machine damaged 6 inch steel gas main
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2020-12-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ULTIMATE INTERNET ACCESS INC | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was potholing to expose service prior to boring. Hit line with shovel. USA valid, Marked correctly.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2020-01-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CARLOS POOL CONSTRUCTION | SAN DIMAS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging to install a pool and hit a service line
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2020-12-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | KSE | RIVERSIDE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Backhoe struck unmarked gas service while trenching
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2020-11-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | ARJ CONSTRUCTION | ARCADIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor struck gas service while trenching by hand
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2020-08-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | NA | ONTARIO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Land owner contractor damaged 1 inchPA svc while excavating with mini back hoe to install drainage line
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2020-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 0.75 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | PANORAMA VISION | RIVERSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Directional Bore struck our gas service.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2020-12-10 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | damage riser with bobcat cleaning debris from demo. No USA
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2020-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | FERRIERA CONSTRUCTION | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | excavator struck riser while removing debris with a large excavator
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2020-07-13 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | JIMMY BOSCHMA | ONTARIO | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No | No damage to SUOF. | No damage to SUOF. | Cut back service hit while grading. No USA
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2020-07-13 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JIMMY BOSCHMA | ONTARIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Grading operator hit cutback service while grading. No USA
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2020-01-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JAG CONSTRUCTION | IRVINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | hit line with backhoe digging for underground utilities
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2020-01-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JAG UTILITY CONSTRUCTION | IRVINE | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was installing dry utilities
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2020-06-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 44 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | OSMENT GRADING EXCAVATING OGE | LAKE ELSINORE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | third party damage. NO usa. Valid usa was for other contractor. This company was trying to piggy back on other contractors usa.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2020-01-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | JAG CONSTRUCTION | IRVINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | JAG construction crew digging under ground utilities damaged service plastic with backhoe
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2020-05-12 | Third party excavation damage | Main | Steel | Grader/Scraper | 3 | 44 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | AAA PAVING COMPANY | RIALTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | service damaged while grading. Service marked correctly.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2020-02-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | MSI ELECTRIC INC | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Backhoe operator damaged facility while digging to install conduits failed to maintain marks
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2020-03-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | H7 CONTRACTING AND ENGENEERING | MURRIETA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Backhoe hit stub service while trenching for fiber optic trench line
Southern California Gas Company | N | SAN BERNARDINO | PHELAN | 2020-11-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RICK PARDUE TRENCHING | HESPERIA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd Party contractor dug into 1 inch PE service with shovel while trenching for conduit .ï¿½
Southern California Gas Company | N | SAN BERNARDINO | PHELAN | 2020-06-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | RAFAEL CALDERON | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor crew damaged 1 inch plastic service while trenching to install communications line
Southern California Gas Company | N | SAN BERNARDINO | PHELAN | 2020-08-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | AB CABLING | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service was damaged with shovel while digging
Southern California Gas Company | N | SAN BERNARDINO | POMONA | 2020-09-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | POMONA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | occupant pulled stump out with vehicle and damaged gas service.
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2020-11-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | ONTARIO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | occupant digging forï¿½ new gate post pierced gas line with shovel.
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2020-11-24 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | FULLMER BUILDING | ONTARIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third Party Damage, no USA, contractor hit main with backhoe. 2nd damage of day at same location.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2020-11-24 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | WALLACE P JOHNSON AND PLUMBING | ATWOOD | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Third Party Damage, contractor hit 2 inch plastic main with backhoe, no currentï¿½USA, old marks on street were accurate, no potholes over main prior to machine excavation.
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2020-03-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 44 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | APEX | POMONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged stub while exposing to prepare svc reinstate
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2020-01-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | WC CONTRACTORS | UPLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit gas service with shovel while digging trench for electricalï¿½
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2020-01-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | WC CONSTRUCTION | UPLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit 0.5inch CTS gas service while trenching with mini excavator for electrical The damaged address is 6958 Canosa Pl
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2020-04-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 44 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | RANCHO CUCAMONGA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party damage. Service damaged with a shovel. Digging on expired usa
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2020-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | GJ GENTRY | UPLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Dig in with backhoe by third party contractor, valid USA, good marks, no hand exposure by contractor.
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2020-01-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 44 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | FM SON S INC | SANTA ANA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party damage Marks not properly maintained Contractor did not have its own USA ï¿½ Service damaged while grading
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2020-12-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HORIZON UNDERGROUND | NORCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third Party Damage, plastic service hit by shovel, valid and accurately marked USA.
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2020-01-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | SCOTT MCLEOD PLUMBING | RANCHO CUCAMONGA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service while excavating for sewer line repair
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2020-10-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HHS CONSTRUCTION | ONTARIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was digging to expose CATV conduit and hit plastic service with shovel. No USA
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2020-12-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | D R HORTON | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Builder approached surveyor notifying him of damage caused by his contractor. No USA
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2020-01-13 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BORDEN EXCAVATING CONTRACTORS | CALIMESA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 2 main struck while
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2020-04-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LBC CONSTRUCTION SERVICES | REDLANDS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor was digging footing for extension.ï¿½ Found old looking line and said he was told that a new service was installed.ï¿½ Contractor attempted to remove old looking pipe and found plastic service inside old metal service.
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2020-07-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MATICH | SAN BERNARDINO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Unknown and unmarked stub was struck during street rehab work.ï¿½ Stub was left behind during home remodel years back. New service was installed with new home to the same property as stub found.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2020-05-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | MATICH CORP | SAN BERNARDINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged service
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2020-04-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | KC LEE INC | MISSION HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage to 1 inch PE service
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2020-05-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | W WOOD ASCOCIATES | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage to so cal gas facility due to installation of HL gas line install
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2020-01-28 | Third party excavation damage | Main | Steel | Miscellaneous/Other | 4 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | NA
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2020-05-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MIGUEL MOLINA | REDLANDS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscaper repair irrigation line while hand digging struck 0.50 inch CTS gas service with shovel damaging service a creating a leak. No Dig Alert ticket was called in prior to work starting.
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2020-04-17 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | BORDEN EXCAVATING INC | SAN BERNARDINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | CONTRACTOR KNEW WHERE WE WERE LOCATED AND EXCAVATED TOO DEEP.
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2020-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 2 |  | MATICH | SAN BERNARDINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | as svc. was struck by 3rd party contractor after they removed the locate mark for the svc they hit. did not protect marks for future work.
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2020-10-16 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | GREG ELECTRIC | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Greg electrical company was excavating, while excavating they ran over service with excavator.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2020-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PATRICK SEPTIC TANK SERVICE | YUCAIPA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5inch pe svc hit during excavating
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2020-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | REDLANDS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer claims service was leaking when he exposed it by hand but LCT believes service was hit by excavator due to tracks in dirt.
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2020-10-06 | Third party excavation damage | Main | Polyethylene Pipe | Not Available | 4 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | AARON LAWRENCE | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor damaged 4 inch plastic main while digging for a retaining wall NO USA ticket.
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2020-10-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | MATICH CORPORATION | SAN BERNARDINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Matich Corporation was grading and broke svc that they did not pothole.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2020-03-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SHANE BOARDAN CONSTRUCTION | CALIMESA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Service took a 45 degree turn in the middle of the streetï¿½just before the water main running line ï¿½ Marks were about 4 off
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2020-03-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | MCC PIPELINE | YUCAIPA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Locator located the old steelï¿½service that was just replaced and a new PE service that was bored in
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2020-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | REDLANDS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | damaged 0.5 pe service while digging footings for wall at garage, repair with 2 0.5 coupling compressionï¿½and 2ft of 0.5 cts pipe
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2020-10-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | REDLANDS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner was cutting tree root and cut plastic service in the process.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2020-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NA | REDLANDS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | customer installing cable internet line
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2020-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | MATICH CORPORATION | SAN BERNARDINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor working for city damaged 0.5 inch pe service will grading street with backhoe
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2020-02-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MCC PIPELINE | YUCAIPA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | none
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2020-03-30 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BORDEN EXCAVATING | CALIMESA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Main line on the street where the water line was being installed was marked ï¿½ The intersection where the main teed and crossed the intersectionï¿½was not marked ï¿½ï¿½
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2020-03-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | none
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2020-06-02 | Third party excavation damage | Main | Steel | Hand Tools | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SELECT ELECTRIC INC | CERRITOS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor working for the City of Redlands doing some electrical work when gas line was hit with a handheld circular saw.
Southern California Gas Company | N | SAN BERNARDINO | RIALTO | 2020-06-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | EMAAR ENTERPRISE | BLOOMINGTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | This was a 0.50 inchIPS stub service that was damage by a 3rd party contractorï¿½
Southern California Gas Company | N | SAN BERNARDINO | RIALTO | 2020-01-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | COLONIAL ELECTRIC | CHINO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor was digging to install electric lines and hit an unmarked un mapped unable to locateï¿½1 PE Stub ï¿½
Southern California Gas Company | N | SAN BERNARDINO | RIALTO | 2020-08-27 | Operator excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NPL | MIRA LOMA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | This was an 1 inch PLA service that was damage due to the facility not mapped correctlyï¿½on GIS.
Southern California Gas Company | N | SAN BERNARDINO | RIALTO | 2020-01-08 | Operator excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 0 | 0 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | NPL | EASTVALE | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Crew replacing NPL crew hit 2 inch main at service to main connection at saddle
Southern California Gas Company | N | SAN BERNARDINO | RIALTO | 2020-09-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | RC CONSTRUCTION SERVICES INC | RIALTO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | This was a damage to an 1 inch PLA service with no USA.
Southern California Gas Company | N | SAN BERNARDINO | RIALTO | 2020-12-31 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MCC | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor while trenchingï¿½ hit our 1 inch plastic service. No USA was called for that contractor.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | RIALTO | 2020-05-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | RIALTO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Owner was trenching to install electrical for lights and hit marked service with shovel. Expired USA ticket.
Southern California Gas Company | N | SAN BERNARDINO | RIALTO | 2020-05-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 47 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | RIALTO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer was digging to repair fence
Southern California Gas Company | N | SAN BERNARDINO | RIALTO | 2020-07-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 44 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | RIALTO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party damage. no USA
Southern California Gas Company | N | SAN BERNARDINO | RIALTO | 2020-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 3 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | USA SHADE | ORANGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | this was a damage that was caused by a 3rd party contractor using a auger to install a pole
Southern California Gas Company | N | SAN BERNARDINO | RIALTO | 2020-10-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | RIALTO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner digging to install drainage. No USA.
Southern California Gas Company | N | SAN BERNARDINO | RIALTO | 2020-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BILL HIGGINS CONTRACTORS | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | grading lot and struck stub gas plastic . any usa marks gone due to the fact that 2 ft of dirt had been graded away.
Southern California Gas Company | N | SAN BERNARDINO | RUNNING SPRINGS | 2020-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TIM HUBBS EXCAVATING | RUNNING SPRINGS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The end of the stub service was correctly marked. when the contractor did not find the service at the mark provided where they were crossing, they continued with a backhoe to excavate. they did not call for the locator to remark or give a updated location.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | RUNNING SPRINGS | 2020-01-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 0 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | RUNNING SPRINGS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customers contractor digging footing for block retaining wall and cut into 0.5inch PEï¿½ service Contractor new the Gas service was there but failed to dig with care No USA called
Southern California Gas Company | N | SAN BERNARDINO | RUNNING SPRINGS | 2020-05-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | HIGHLAND | CA | N | Y | No | No | No | No | No | No | No | 3rd party damaged service while digging to install water.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2020-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 4 |  | RALPH CURRIO | SAN BERNARDINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging to add fence post, and struck our gas service with hand tool.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2020-01-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 1.25 | 60 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | SAN BERNARDINO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer assumed the gas service was the water service ï¿½ Customer cut into the line with a saw ï¿½ Customer was informed to always call Dig Alert when performing any excavations
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2020-06-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 2 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | POWER TECH | FULLERTON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor crew damaged 2 inch plastic service while boring in telecommunicaitons line in parkway. Contractor crew did not pothole to verify location of plastic service, and gas company crew had difficulties in locating the service to control gas and make repairs.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2020-04-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Direct burial PEï¿½service damaged.ï¿½ Our records indicated the service was in casing.ï¿½ The contractor exposed our casing and continued excavating and broke a direct burial service less than 1 away.ï¿½ We cut into the casing that they exposed and found dead state of the art plastic inside.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2020-02-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | EAST VALLEY WATER DISTRICT | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Service not mapped on print ï¿½ Flag lot
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2020-07-23 | Operator excavation damage | Main | Steel | Not Available | 4 | 28 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | UNDERGROUND CONSTRUCTION COMPANY | ONTARIO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | company contractor bored thru 4in steel main while installing gas service
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2020-10-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 5 |  | NA | SAN BERNARDINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working for the property owner was hand digging to repair a plugged sewer line when branch service was hit with a shovel.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2020-08-20 | Operator excavation damage | Riser | Steel | Hand Tools | 0.75 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | UNDERGROUND UTILITILY COMPANY | NA |  | Y | N | Yes | Yes | Yes | Yes | No | Yes | Yes | contractorï¿½ for company , underground construction co 1150 Hellman ave , Ontario ca. 91764 ,ï¿½ ï¿½cut riser before abandonment
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2020-12-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RADOS INC | SANTA ANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Company locaters struggle to get a good locate on service but put a dot down on the street were strongest read was picking up. Damage was right on top of dot.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2020-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HIGHER QUALITY CONSTRUCTION | TEMECULA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner install a wall
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2020-08-25 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  |  | NA | HERMAN WEISSKER | JURUPA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Party contractor excavating with a backhoe damaged 3 inch PE main.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2020-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | HISPANO INVESTORS INC | RIVERSIDE | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No | No damage to SUOF. | No damage to SUOF. | Gas riser was damaged while grading.ï¿½ No USA
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2020-04-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | OPTION 1 PLUMBING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | USA no notified. PE service cut with shovel.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2020-08-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | PACIFIC PRODUCTION PLUMBING | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged PE gas service on Lennar Homes property.ï¿½ Unknown who damaging party is.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2020-02-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | PAYLESS FOR PLUMBING INC | SAN BERNARDINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5inch service damaged by plumbing contractor installing a clean out
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2020-06-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GEORGE ELZAWY EARTHMOVERS | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor damaged our service line while clearing dirt from around the line while using a backhoe. No currentvalid USA .ï¿½
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2020-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | RIVERSIDE | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No | No damage to SUOF. | No damage to SUOF. | 3rd party contractor damaged riser with bulldozer while grading dirt and demoing home.ï¿½ contractor claims that he thought the line was abandoned but there was an order created for an abandonment for this address that wasnt completed yet.ï¿½ the crew cut the service back at the riser location.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2020-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | SAN BERNARDINO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home Owner was digging for sprinklers and hit 0.5 inch PLA service with mini Ex. No USA.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2020-03-30 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | T E ROBERTS INC | ORANGE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 2 PE main struck while excavating
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2020-11-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 5 |  | NA | SAN BERNARDINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working for property owner damaged a 0.5 inch cts service while digging with a shovel.ï¿½ There were a total of 5 outages.ï¿½ Damaging party information is unknown and were not on site upon arrival.ï¿½ All repairs are made permanent.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2020-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 35 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | EL CO CONTRACTORS | SAN BERNARDINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor damaged steel service with backhoe while digging for new water main.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2020-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 35 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | EL COMPANY CONTRACTOR | SAN BERNARDINO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | contractor damaged our service line while trenching with a backhoe to install water line.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2020-07-06 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 35 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | EL CO CONTRACTORS | SAN BERNARDINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor damaged steel service while digging for waterline.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2020-04-02 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 35 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | NA |  | N | Y | Yes | Yes | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | none
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2020-01-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | PACIFIC WEST UNDERGROUND INC | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5inch PE Service damage
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2020-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | SAN BERNARDINO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was digging for fence post and hit CTS SVC.ï¿½ï¿½
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2020-09-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | COLTON | CA | N | N | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No damage to SUOF. | No damage to SUOF. | No | No damage to SUOF. | No damage to SUOF. | Possible dump truck ran over 0.75 steel riser.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2020-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | SAN BERNARDINO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging to install a post for fence.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2020-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | INLAND BUILDING CONSTRUCTION COMPANY | SAN BERNARDINO | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Digging for Fire line and broke service with excavator.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2020-06-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CRUZ CONSTRUCTION | SAN BERNARDINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was hand digging and still struck the service due to hard soil.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2020-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | SAN BERNARDINO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | PE service damagedï¿½ while installing drainage. Damaged byï¿½hand powered clay spade.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2020-08-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | SAN BERNARDINO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer damaged service while removing tree approx. 12 weeks prior calling. Poured concrete over damage.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2020-03-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | CIAIS CONSTRUCTION CO | JURUPA VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor grading and excavating to install a retaining wall for the homeowner
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2020-06-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HOME OWNER | SAN BERNARDINO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | USA was not called.ï¿½ Gas facility damaged.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2020-06-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | SAN BERNARDINO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | customer claims to have been doing yard work removing bushes when damage occurred.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2020-01-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | NELVI CONSTRUCTION INC | SAN BERNARDINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | DIGGING TO LOCATE SEWER FOR A REMODAL
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2020-03-14 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | JESSE RAMIREZ | SAN BERNARDINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit service riser while demoing house ï¿½ No USA called ï¿½ Service History showed serviced as abandoned the service was still active
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2020-08-17 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | MACADEE ELECTRICAL CONSTRUCTION | CHINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged steel service while boring to install street light conduits. Contractor had previously pot holed 10 away from actual bore location and failed to pot hole at actual bore.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2020-07-17 | Third party excavation damage | Main | Steel | Boring Equipment | 2 | 28 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BNSF RAILWAY COMPANY | SAN BERNARDINO | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 2 inchsteel line by boring parallel to train tracks to install conduit for train signals.ï¿½ USA ticket called after damage.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2020-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CITY OF SAN BERNARDINO WATER DISTRICT | SAN BERNARDINO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Stub was damaged by contractor digging to remove water service
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2020-03-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | N K DEMOLITION | SAN BERNARDINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 2 PE Stub hit by 3rd party contractor
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2020-12-15 | Operator excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | NPL | MIRA LOMA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | NPL was removing shoring boards with backhoe and struck 2in PE transit fittingï¿½
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2020-01-10 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | NA | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | NA
Southern California Gas Company | N | SAN BERNARDINO | TWENTYNINE PALMS | 2020-10-09 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | TWENTYNINE PALMS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor cut steel service with grinder thinking it was abandoned. Contractor failed to call in for a USA and is fully responsible.
Southern California Gas Company | N | SAN BERNARDINO | TWENTYNINE PALMS | 2020-07-20 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 41 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NPL FOREMAN DAMIEN FAUSTO | MIRA LOMA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Company Contractor excavating to replace service damaged 0.5 inch service with shovel
Southern California Gas Company | N | SAN BERNARDINO | TWENTYNINE PALMS | 2020-05-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | TWENTYNINE PALMS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner excavating to access water service. No USA
Southern California Gas Company | N | SAN BERNARDINO | TWIN PEAKS | 2020-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | TIMBERWOLF CONSTRUCTION | SAN BERNARDINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA called and service was hit during excavatingï¿½
Southern California Gas Company | N | SAN BERNARDINO | TWIN PEAKS | 2020-04-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | TWIN PEAKS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | digging for retaining wall, no USA. Hit service with shovel.
Southern California Gas Company | N | SAN BERNARDINO | TWIN PEAKS | 2020-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ALTMEYER CONSTRUCTION | CEDAR GLEN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Water Pipeline contractor was using a trachoe to excavate the street and did not use caution or hand dig for marked facilities.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | UPLAND | 2020-04-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 44 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RJP GENERAL CONTRACTOR | ONTARIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party damage. NO usa. Hit while hand exposing to repair sewer
Southern California Gas Company | N | SAN BERNARDINO | UPLAND | 2020-10-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | MOE S CONCRETE | ONTARIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party damage, contractor hit branch service while grading for new block wall. No USA.
Southern California Gas Company | N | SAN BERNARDINO | UPLAND | 2020-08-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | T E ROBERTS INC | ORANGE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Excavator struck service marked incorrectly
Southern California Gas Company | N | SAN BERNARDINO | UPLAND | 2020-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | T E ROBERTS INC | ORANGE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Excavator struck gas service. Marks were off for gas line.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | UPLAND | 2020-12-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 10 |  | GENTRY BROTHERS | IRWINDALE |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | excavator struck gas service with backhoe. Marks within 2 feet.
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2020-07-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | YUCAIPA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer damaged PLA service with shovel while excavating to plant tree.ï¿½ No notification to USA.
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2020-02-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CHRISTENSEN BROTHERS | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | none
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2020-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CHRISTIAN BROS ENGINEERING INC | APPLE VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service damaged by post hole digger
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2020-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | YUCAIPA VALLEY WATER DISTRICT | YUCAIPA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor claims to have found 2 other lines, but had not seen the plastic service they damaged the plastic service.
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2020-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | YUCAIPA VALLEY WATER DISTRICT | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Water District was fixing a pothole when gas line was hit with backhoe.
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2020-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | VICTORIA KLEIN | YUCAIPA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service damage during excavating
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2020-07-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | SOUTH MESA WATER DISTRICT | CALIMESA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | while excavating to install new water line the contractor damage the 0.5 IPS services.
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2020-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PFOY CONCRETE CONSTRUCTION | YUCAIPA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Crew broke svc while excavating with trencher for block wall footing.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2020-10-12 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ACCESS GENERAL CONTRACTING | WESTMINSTER | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damage 0.5inch plastic service with shovel in the process of installing meter post.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2020-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | KIM MCCULLOUGH | YUCAIPA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | digging to lay electrical conduits. hit stub service with shovel
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2020-01-24 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CHRISTENSEN BROTHERS GENERAL ENG | APPLE VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Damage to unmarked and undocumented 0.75inch service
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2020-05-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | YUCAIPA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged service
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2020-05-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | YUCAIPA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer hit service with mini excavator, no USA called.
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2020-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ALEX LANDSCAPE | SAN BERNARDINO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA Called. contractor damaged service
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2020-12-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | RAMIROAVELA | YUCAIPA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | damage to 0.5 inch CTS gas line by homeowner while digging with trencher.ï¿½ NO valid USA ticket found. Last ticket found for this address was which expired in early Nov 2020 for planting of trees.ï¿½
Southern California Gas Company | N | SAN BERNARDINO | YUCCA VALLEY | 2020-09-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HI DESERT WATER DISTRICT | YUCCA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | HDWD digging to install water main, failed to hand expose gas service. USA current. Marked correctly
Southern California Gas Company | N | SAN BERNARDINO | YUCCA VALLEY | 2020-04-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | UNIVERSAL CONCRETE CONSTRUCTION | INDIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator has potholed several other services and found them to be deeper than expected, so assumed this service was the same and failed to pothole it.
Southern California Gas Company | N | SAN BERNARDINO | YUCCA VALLEY | 2020-05-14 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | YUCCA VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Homeowner excavating to find sewer lateral stub, hit 2 inch gas main. Marks for main 10 north of actual location. Excavator digging from South to North. 1 way feed main, pressure held 5 pounds at furthest locations. Main bypassed to maintain feed before shutdown
Southern California Gas Company | N | SAN BERNARDINO | YUCCA VALLEY | 2020-11-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ACTION PUMPING | YUCCA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Marked and marked correctly. Contractor excavating to replace septic tank, failed to pothole service and damaged plastic pipe.
Southern California Gas Company | N | SAN BERNARDINO | YUCCA VALLEY | 2020-02-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ACTION PUMPING INC | YUCCA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor excavating for sewer lateral connection did not pothole service Marked with paint in street and flags over service line in earth
Southern California Gas Company | N | SAN BERNARDINO | YUCCA VALLEY | 2020-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SELF EMPLOYED CHAD PRICE | JOSHUA TREE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner digging to install fence post, hit service hand digging. No USA notification. 1 outage
Southern California Gas Company | N | SAN BERNARDINO | YUCCA VALLEY | 2020-06-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 5 |  | AMERICAS BEST PLUMBING | YUCCA VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging with shovel to install sewer. Crew believes a backhoe was used but contractor claims it was a shovel. Excavator USA expired 520.50020. Marks visible for branch, but standard service not marked
Southern California Gas Company | N | SAN BERNARDINO | YUCCA VALLEY | 2020-06-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MARCOS CERVANTES | JOSHUA TREE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator failed to pothole long side service. We focused on not damaging main
Southern California Gas Company | N | SAN BERNARDINO | YUCCA VALLEY | 2020-04-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 6 |  | WILLIAM SELLERS PLUMBING | YUCCA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavating to install sewer line, nicked 1 inch gas service to 6 meter manifold. 6 outages
Southern California Gas Company | N | SAN BERNARDINO | YUCCA VALLEY | 2020-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | WILLIAM FELLER S PLUMBING | YUCCA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator damaged 0.5inch CTS service while digging for sewer lateral connection Failed to pothole branch service Marked correctly ï¿½
Southern California Gas Company | N | SAN BERNARDINO | YUCCA VALLEY | 2020-04-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | WEEKS PLUMBER | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator digging to replace irrigation lines, failed to pothole for service
Southern California Gas Company | N | SAN BERNARDINO | YUCCA VALLEY | 2020-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | WILLIAM SELLERS PLUMBING | YUCCA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | William Seller Plumbing digging to install sewer hit service while inchhand digging inch to expose
Southern California Gas Company | N | SAN BERNARDINO | YUCCA VALLEY | 2020-03-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ACTION PUMPING | YUCCA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | According to excavator service line was hit while potholing for gas line Service marked correctly valid USA
Southern California Gas Company | N | SAN BERNARDINO | YUCCA VALLEY | 2020-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | WILLIAM SELLERS PLUMBING | YUCCA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | installing sewer. Damaged service with backhoe Claimed to be hand exposing, but then admitted that they failed to hand expose per USA law
Southern California Gas Company | N | SAN BERNARDINO | YUCCA VALLEY | 2020-03-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | YUCCA VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner excavating for water drain Assumed gas line was not in conflict with trenching
Southern California Gas Company | N | SAN BERNARDINO | YUCCA VALLEY | 2020-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ACTION PUMPING INC | YUCCA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit gas service with backhoe while doing sewer lateral Contractor added 2nd set of delineations after area was located but failed to update original USA ticket
Southern California Gas Company | N | SAN BERNARDINO | YUCCA VALLEY | 2020-12-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JOHN MAHANY PLUMBLING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contactor hit service line while digging for fence posts, USA was expired. ï¿½
Southern California Gas Company | N | SAN BERNARDINO | YUCCA VALLEY | 2020-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HIGH DESERT WATER | YUCCA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator potholing for service, damaged with shovel. Marked correctly, USA valid
Southern California Gas Company | N | SAN BERNARDINO | YUCCA VALLEY | 2020-09-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | CLAY GIBERT | JOSHUA TREE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor excavating for sewer lateral installs. Assumed main line roped between fire hydrant and curb, but it didnt. No USA. No outages
Southern California Gas Company | N | SAN LUIS OBISPO | ARROYO GRANDE | 2020-12-22 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | INTEGRITY GENERAL ENGINEERING | CORONA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Company contractor was excavating, struck 0.5 inch ips line with grounding rod.
Southern California Gas Company | N | SAN LUIS OBISPO | ARROYO GRANDE | 2020-05-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LANDSCAPE DEVELOPMENT | SAN LUIS OBISPO | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Expired USA ticket
Southern California Gas Company | N | SAN LUIS OBISPO | ARROYO GRANDE | 2020-01-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | FAMCO DEVELOPMENT | ARROYO GRANDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | USA not called for work being performed
Southern California Gas Company | N | SAN LUIS OBISPO | ARROYO GRANDE | 2020-07-17 | Third party excavation damage | Riser | Steel | Grader/Scraper | 0.75 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ERICK JONES LANDSCAPING | NIPOMO | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No | No damage to SUOF. | No damage to SUOF. | Skidsteer struck meter while driving by. No excavation work being performed near SCG facilities.ï¿½
Southern California Gas Company | N | SAN LUIS OBISPO | ARROYO GRANDE | 2020-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | NA | TEMPLETON | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No valid USA, post hole digger damaged plastic service
Southern California Gas Company | N | SAN LUIS OBISPO | ARROYO GRANDE | 2020-09-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | OLCOTT CONSTRUCTION | LOS OSOS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No valid USA
Southern California Gas Company | N | SAN LUIS OBISPO | ATASCADERO | 2020-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | RJB GRADING EXCAVATION | TEMPLETON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | none
Southern California Gas Company | N | SAN LUIS OBISPO | ATASCADERO | 2020-11-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | ATASCADERO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Per LCT Jonathan Dial Homeowner Seth Leigan hit service line with auger while excavating to install fencing
Southern California Gas Company | N | SAN LUIS OBISPO | ATASCADERO | 2020-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | VIBORG CONTRACTOR | PASO ROBLES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.50 inch plastic service was damaged while contractor TJ Gingg was removing asphalt from the driveway. Service was only 2 inch at the time of the damage. No USA was called. Service will be replaced to mitigate the depth issue.
Southern California Gas Company | N | SAN LUIS OBISPO | ATASCADERO | 2020-10-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | WESTERN FENCE | ATASCADERO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | Fencing company contractor hit Neighbors service out side of delineation.
Southern California Gas Company | N | SAN LUIS OBISPO | ATASCADERO | 2020-08-23 | Third party excavation damage | Riser | Steel | Backhoe/Trackhoe | 0 | 400 | 360 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | ATASCADERO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer backed into Above Ground First Stage Reg Set and broke the nipple past the service valve while they were brush clearing. Company was unaware of any work being performed in this area.
Southern California Gas Company | N | SAN LUIS OBISPO | ATASCADERO | 2020-04-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | ATASCADERO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner excavating in yard without USA.ï¿½ Hit gas line with hand tools.
Southern California Gas Company | N | SAN LUIS OBISPO | ATASCADERO | 2020-12-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | AMERICAN DREAM CONSTRUCTION | ATASCADERO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor building a retaining wall for homeowner struck gas service. No USA.
Southern California Gas Company | N | SAN LUIS OBISPO | ATASCADERO | 2020-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | ATASCADERO MUTUAL WATER CO | ATASCADERO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator uncovered abandoned line above the new service and assumed they potholed the live line. They struck the new service. Valid USA
Southern California Gas Company | N | SAN LUIS OBISPO | ATASCADERO | 2020-05-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | ATASCADERO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner stated that the damage occurred while excavating for a post. No USA was called.
Southern California Gas Company | N | SAN LUIS OBISPO | ATASCADERO | 2020-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Vacuum Equipment with no Agreement | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | BADGER DAYLIGHTING | SHAFTER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service was damaged with vacuum excavation equipment. USA ticket was called in however the contractor dug before the 48 hour requirement. Our contractor Herman Weissker hired Badger Daylighting to perform the vacuum excavation work.ï¿½
Southern California Gas Company | N | SAN LUIS OBISPO | ATASCADERO | 2020-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 6 |  | SOUZA CONSTRUCTION | SAN LUIS OBISPO | CA | N | Y | Yes | Yes | No | No | No | Yes | Yes | Souza Construction was installing a new drainage line at 8250 Morro Rd in Atascadero. Morro Rd is also know as state hwy 41. Souzaï¿½ construction had a valid USA ticket. The locator for SoCalGas looked up GIS for this work area and cleared it for no conflict per GIS. GIS showed the service being fed from Santa Ynez Ave and not HWY 41. GIS was incorrect and the service was indeed fed from HWY 41. The locator did not hook up to verify. Service History also showed this service as a standard for 8250 Morro Rd. The address shouldve been 8280 Morro Rd and a branch service needs to be created for 8250 Morro Rd to reflect the field findings. An updateï¿½request was submitted to the GIS Team.ï¿½
Southern California Gas Company | N | SAN LUIS OBISPO | CAMBRIA | 2020-09-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | CAMBRIA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No valid USA
Southern California Gas Company | N | SAN LUIS OBISPO | CAMBRIA | 2020-03-24 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | HERMAN WEISSKER INC | RIVERSIDE | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 2nd party damage by company contractor Hard soil hit service while hand exposing line
Southern California Gas Company | N | SAN LUIS OBISPO | CAMBRIA | 2020-07-20 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | H WEISSEKER | ARROYO GRANDE | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The Gas company contractor, Wiseker, was hand digging trying to expose a gas service and struck the plastic service pipe causing a blowing leak.ï¿½
Southern California Gas Company | N | SAN LUIS OBISPO | CAMBRIA | 2020-10-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | TIERNEY CONSTRUCTION | CAMBRIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No valid USA
Southern California Gas Company | N | SAN LUIS OBISPO | CAMBRIA | 2020-05-04 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | HERMAN WEISSEKER | RIVERSIDE | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | Company Contractor performing Gas Main and Service Replacement project was hand digging a spot hole for new gas service 2 ft away from marks for 0.5 inch PLA service and hit the existing gas service with a shovel on the edge of the excavation. The service line located in a straight line near the gas riser and at the street curb, but near the location of the damage there was signal interference around the area of the branch tee. Later determined that the service roped to the east away from the riser and then back to the west before crossing the curb, leading the contractor to believe that the service line was in a straight line between the 2 marks. Service History and GIS also were incorrect, showing the standard and branch service to be reverse from their actual locations.
Southern California Gas Company | N | SAN LUIS OBISPO | CAMBRIA | 2020-05-04 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | HERMAN WEISSEKER | RIVERSIDE | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | Company Contractor performing Gas Main and Service Replacement project was hand digging a spot hole for new gas service 2 ft away from marks for 0.50 inch PLA service and hit the existing gas service with a shovel on the edge of the excavation. The service line located in a straight line near the gas riser andï¿½at the street curb, but near the location of the damage there was signal interference around the area of the branch tee. Later determined that the service roped to theï¿½east away from the riser and then back to the west before crossing the curb, leading the contractor to believe that the service line was in a straight line between the 2 marks. Service History and GIS also were incorrect, showing the standard and branch service to be reverse from theirï¿½actual locations.
Southern California Gas Company | N | SAN LUIS OBISPO | CAMBRIA | 2020-12-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LANDSCAPER | CAMBRIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per LCT Allen Johnson Diego Merced hit service line while excavating to install support post for palm tree.
Southern California Gas Company | N | SAN LUIS OBISPO | CAMBRIA | 2020-08-03 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | HWI | SAN LUIS OBISPO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | SCG contractor hit line while replacing service
Southern California Gas Company | N | SAN LUIS OBISPO | CAYUCOS | 2020-01-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | BOB ALMEKINDERS SONS CONSTRUCTION | CAYUCOS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | USA not valid contractor working on expired ticket ï¿½
Southern California Gas Company | N | SAN LUIS OBISPO | CAYUCOS | 2020-02-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ROGALL PAINTING CONSTRUCTION | MORRO BAY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | USA not called no valid ticket
Southern California Gas Company | N | SAN LUIS OBISPO | LOS OSOS | 2020-05-04 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  |  | NA | NA | LOS OSOS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No valid USA, homeowner using excavator ripped through 2 inch main
Southern California Gas Company | N | SAN LUIS OBISPO | LOS OSOS | 2020-12-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 3 |  | STEVE BOYLE CONSTRUCTION | SAN LUIS OBISPO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No valid USA
Southern California Gas Company | N | SAN LUIS OBISPO | LOS OSOS | 2020-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NA | LOS OSOS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hit gas service while excavating for fence post ï¿½ No USA called
Southern California Gas Company | N | SAN LUIS OBISPO | LOS OSOS | 2020-02-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | A DAM HANDYMAN | LOS OSOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator dug prior to verifying all marks He saw a mark further away thinking it was the gasï¿½service but it was actually the orange ATT marks ï¿½
Southern California Gas Company | N | SAN LUIS OBISPO | LOS OSOS | 2020-11-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | LOS OSOS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The occupant was hand digging a trench to install a French drain and hit the service line with the shovel.ï¿½ There was no evacuations and no injuries.ï¿½ The crew made the repair and two homes were restored.
Southern California Gas Company | N | SAN LUIS OBISPO | LOS OSOS | 2020-04-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | NA | LOS OSOS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | USA not called
Southern California Gas Company | N | SAN LUIS OBISPO | LOS OSOS | 2020-05-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | LOS OSOS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Property owner was digging around sewer lateral and hit 0.50 inch pe has service.
Southern California Gas Company | N | SAN LUIS OBISPO | LOS OSOS | 2020-07-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | LOS OSOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The occupant was digging to install drainage pipe
Southern California Gas Company | N | SAN LUIS OBISPO | LOS OSOS | 2020-08-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LEGACY BUILDERS AND DESIGN INC | TEMPLETON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | USA not notified
Southern California Gas Company | N | SAN LUIS OBISPO | LOS OSOS | 2020-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CRIZER CONSTRUCTION | LOS OSOS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No valid USA
Southern California Gas Company | N | SAN LUIS OBISPO | MORRO BAY | 2020-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | MORRO BAY | CA | N | Y | Yes | Excavation occurred on private property by a non-contractor. | Yes | Yes | No | Yes | Yes | Homeowner hit line with posthole digger.ï¿½ Was not aware of 2 buffer zone.
Southern California Gas Company | N | SAN LUIS OBISPO | NIPOMO | 2020-05-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | RANDY MARTYN HANDYMAN SERVICES | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party Contractor was digging in private with no USA to fix water leak.ï¿½
Southern California Gas Company | N | SAN LUIS OBISPO | NIPOMO | 2020-08-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TROUGH CONSTRUCTION | ARROYO GRANDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | SCG marks were correct. 3rd Party contractor not exposing utilities by hand damaged line with mini excavator.ï¿½
Southern California Gas Company | N | SAN LUIS OBISPO | NIPOMO | 2020-07-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | VIOLA CONSTRUCTION | ARROYO GRANDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavator didnt hand expose facilities while digging. Excavator knew where it was but still hit line with backhoe. USA ticket was a renew ticket for remarks no.ï¿½
Southern California Gas Company | N | SAN LUIS OBISPO | NIPOMO | 2020-05-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | MAYOLA CONSTRUCTION | ARROYO GRANDE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Excavator knew where the gas line was but damaged pipe while hand excavating. The USA ticket was on a remark norenew ticket status. Last time Locator was required to be there was 4 7 20. Contractor failed to maintain marks and didnt use safe practice while exposing gas line.ï¿½
Southern California Gas Company | N | SAN LUIS OBISPO | NIPOMO | 2020-10-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | NIPOMO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per LCT. J. Tesoro Homeowner David Ibarra hit SCG service line with a posthole digger while excavating to install fence posts.
Southern California Gas Company | N | SAN LUIS OBISPO | NIPOMO | 2020-06-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | NIPOMO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA, homeowner hand dug for fencing, hit service
Southern California Gas Company | N | SAN LUIS OBISPO | NIPOMO | 2020-05-18 | Operator excavation damage | Riser | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LYLES CONSTRUCTION | NA |  | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Lyles Co. with Residential Meter Guard project damaged service line with shovel. USA marks were good.
Southern California Gas Company | N | SAN LUIS OBISPO | NIPOMO | 2020-11-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | REX ROOTER | NIPOMO | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | 3rd Party contractor hit 0.5 inch ctsï¿½ on private property with excavator prior to legal start date.ï¿½
Southern California Gas Company | N | SAN LUIS OBISPO | NIPOMO | 2020-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 59 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GREG NESTOR | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party excavator hit 1 inch pla service with backhoe. No USA.
Southern California Gas Company | N | SAN LUIS OBISPO | OCEANO | 2020-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | OCEANO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No valid USA
Southern California Gas Company | N | SAN LUIS OBISPO | PASO ROBLES | 2020-12-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JC CONSTRUCTION | MORRO BAY |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging for fence post damaged gas service. No USA.
Southern California Gas Company | N | SAN LUIS OBISPO | PASO ROBLES | 2020-06-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 5 |  | SALVADOR OROZCO | PASO ROBLES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging to replace fencing when they struck the gas service. No USA ticket.
Southern California Gas Company | N | SAN LUIS OBISPO | PASO ROBLES | 2020-06-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | LEE WILSON ELECTRIC | ARROYO GRANDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Lee Wilson Electric did not have their own USA ticket, they were working under Souza Constructions ticket. The service was located correctly for Souza however when Souza potholed the service, they wrote down the wrong depth. When Lee Wilson Electric went to trench over the 0.50 inch plastic service in 0.75 inch steel casing, they cut it in half with the trenching machine.
Southern California Gas Company | N | SAN LUIS OBISPO | PASO ROBLES | 2020-11-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | PASO ROBLES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Homeowner was digging to install a drain when they struck the service. They were trying to use caution while hand exposing the service however the soil was hard and the shovel damaged the line. USA ticket was valid and marked correctly.
Southern California Gas Company | N | SAN LUIS OBISPO | PASO ROBLES | 2020-12-16 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PAPICH CONSTRUCTION | ARROYO GRANDE | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Valid USA ticket however per Job Foreman Dominic Judge, Papich Construction was NOT supposed to be working in the area where they struck the main. Dominic forgot to include the new worksite into the USA ticket.
Southern California Gas Company | N | SAN LUIS OBISPO | PASO ROBLES | 2020-01-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 3 |  | DONALD KIRKBY CONSTRUCTION | CRESTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Kirkby construction was hand digging to install a sewer lateral They struck the 0.5inch CTS service with a shovel while attempting to expose it by hand digging They had a valid USA ticket and the marks were visible
Southern California Gas Company | N | SAN LUIS OBISPO | PASO ROBLES | 2020-06-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ISRAEL HUERRA | PASO ROBLES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor, Isreal, was digging a hole for a fence post and hit the service.ï¿½ USA was not called.
Southern California Gas Company | N | SAN LUIS OBISPO | PASO ROBLES | 2020-10-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | PASO ROBLES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | USA Ticket was expired. Marks were clearly visible and marked correctly.ï¿½
Southern California Gas Company | N | SAN LUIS OBISPO | PISMO BEACH | 2020-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | GREEN AND CLEAN | SELMA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hit service while hand exposing
Southern California Gas Company | N | SAN LUIS OBISPO | PISMO BEACH | 2020-01-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | TOWON LANDSCAPE | PISMO BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | USA not called
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2020-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | KIRK CONSTRUCTION | ATASCADERO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Valid USA, service not marked within delineation
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2020-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 3 |  | NA | SAN LUIS OBISPO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Property owner Bruce Smith was putting in fencing and struck 0.5 service with a post hole digger. Mr. Smith did not contact USA before digging.
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2020-11-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | ORMONDE TRUCK TRACTOR | ARROYO GRANDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor digging for site improvements, broke the existing gas service. They knew the location of the pipe and were attempting to hand expose it when they sliced into the PE Pipe.
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2020-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | D-KAL ENGINEERING | SAN LUIS OBISPO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | On 06-30-2020, SoCalGas was notified of a third-party damage at 265 South Street, San Luis Obispo. The third-party contractor damaged a 1-inch plastic gas service stub with a backhoe while digging to repair a sinkhole for the city. Gas crews responded and controlled gas at 11 54. There were no injuries or further damages resulting from this incident. This incident was reported to CPUC when SoCalGas became aware of media coverage
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2020-09-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | SAN LUIS OBISPO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party Damage.ï¿½ No USA.ï¿½ Hand digging.
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2020-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | THE KING GENEAL CONSTRUCTION | NIPOMO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No valid USA
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2020-07-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HAYWORD EXCAVATING | SAN LUIS OBISPO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | none
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2020-01-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 4 |  | NA | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | CONTRACTOR EXPOSED WATER LINES AND GAS LINE CROSSING WATER LINE PREVIOUS DAMAGE CAUSED BY OTHER Unknown CONTRACTOR FOUND DAMAGED LINE THAT WAS TAPED AND COVERED BY DIRT
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2020-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | NA | SAN LUIS OBISPO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Party Contractor Dug Without Potholing 2Inch Pla Serviceï¿½
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2020-11-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | NA | SAN LUIS OBISPO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to pothole 2inch gas service and hit with backhoe
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2020-11-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PORTNEY ENVIRONMENTAL | PASO ROBLES | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Expired USA and excavator failed to maintain marks from locate
Southern California Gas Company | N | SAN LUIS OBISPO | SANTA MARGARITA | 2020-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | SANTA MARGARITA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Digging by hand to expose gas line and nicked it, digging for sprinklers.
Southern California Gas Company | N | SAN LUIS OBISPO | TEMPLETON | 2020-06-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NA | TEMPLETON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Home owner was digging with a shovel over the service and hit it.ï¿½ Service was about 16 inch deep where it was hit.ï¿½ It was properly marked and the homeowner knew to handï¿½dig carefully to expose it but still hit it.ï¿½
Southern California Gas Company | N | SANTA BARBARA | BUELLTON | 2020-10-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | BUELLTON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | USA ticket said work being done in backyard. No delineation in front yard. Locator marked inchNo Gas In Backyard inch on pavement in front of house.
Southern California Gas Company | N | SANTA BARBARA | CARPINTERIA | 2020-04-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HIGHLIGHT ELECTRIC | COLTON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Signal went straight across the street and GIS showed the same. There was an undocumented jog on the service.
Southern California Gas Company | N | SANTA BARBARA | CARPINTERIA | 2020-10-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GARDNER | CARPINTERIA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner had contractor install a root barrier against her backyard fence line.ï¿½ Contractor hit 0.5 inch service with shovel.ï¿½ No USA called.
Southern California Gas Company | N | SANTA BARBARA | CARPINTERIA | 2020-08-26 | Third party excavation damage | Riser | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CARPINTERIA VALLEY WATER DISTRICT | CARPINTERIA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Water Department trenching for service line to new construction at 3290 Beach Club Road.ï¿½ Backhoe damaged service to 3282 Beach Club Road.
Southern California Gas Company | N | SANTA BARBARA | CARPINTERIA | 2020-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ASPHALT PROFESSIONALS INC | CAMARILLO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Subcontractor placing curb forms in for parking spaces.ï¿½ While staking forms into the ground, stake punctured 1 inch service not connected to 4 unit condo project.ï¿½ Building Superintendent stated he knew where the line was and did not call for USA ticket.
Southern California Gas Company | N | SANTA BARBARA | CARPINTERIA | 2020-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TORRO ENTERPRISE INC | OXNARD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | Miller Equipment Company was grinding surface street for City Toro Enterprises and grinder came in contact with 0.75 inch cut back service near the midcenter of street from 5095 8th street, Carpinteria.ï¿½ Grinder pulled 0.75 steel gas line out of the ground approximately 3 feet.
Southern California Gas Company | N | SANTA BARBARA | CARPINTERIA | 2020-11-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RHC CONSTRUCTION INC | SANTA BARBARA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Site supervisor was having landscaper expose underground electrical when they hit newly installed service.ï¿½ No USA called.
Southern California Gas Company | N | SANTA BARBARA | CARPINTERIA | 2020-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MONTEVERDE LANDSCAPES | SANTA BARBARA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA.
Southern California Gas Company | N | SANTA BARBARA | CARPINTERIA | 2020-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | TORRO ENTERPRISES | OXNARD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor did not maintain marks in ally and hit it with a backhoe. When asked if it was mark the foreman stated inchummm im not sure inch the Locator and foreman both stated that they had walked the job together.,
Southern California Gas Company | N | SANTA BARBARA | GOLETA | 2020-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TORO ENTERPRISES INC | OXNARD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor hit 0.5 inch service with shovel while potholing.
Southern California Gas Company | N | SANTA BARBARA | GOLETA | 2020-08-03 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6092 |  | 19 |  | TORO ENTERPRISE INC | OXNARD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On 08/03/20, SoCalGas was made aware of a third party damage at 150 Orange Ave, Goleta. The third party contractor struck a 2-inch steel main causing the release of natural gas. SoCalGas personnel were sent to the damage location to safely control the gas. Investigation shows that the line was marked correctly. The contractor did not maintain the markouts, and damaged the 2 inch steel gas main while digging with a backhoe. There were no injuries nor further damage reported due to the release of gas. This was reported to the CPUC due to the release of gas and media coverage.
Southern California Gas Company | N | SANTA BARBARA | GOLETA | 2020-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | NA | SIMI VALLEY | CA | N | Y | Yes | No | No | No | No | Yes | Yes | On 11/02/2020, SoCalGas was notified of a third-party damage at 5811 Calle Real, where a contractor was boring to install communication conduit and damaged a 1-inch plastic gas service, causing a gas leak. SoCalGas crew responded, controlled the gas, and repaired a section of service line by method of Fusion. There were no injuries or further damages resulting from this incident. The investigation showed the contractor was working on an expired USA Ticket. This incident was reported to the CPUC when SoCalGas became aware of media coverage
Southern California Gas Company | N | SANTA BARBARA | GOLETA | 2020-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 4 |  | ARROYO SECO CONSTRUCTION | SANTA BARBARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service while excavating while hand digging. Marks were clearly visible.
Southern California Gas Company | N | SANTA BARBARA | GOLETA | 2020-04-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 43 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | TORO ENTERPRISE | OXNARD | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Contractor dug before legal start time. was using a backhoe did not see any visible marks but work had been going on for a couple of weeks.
Southern California Gas Company | N | SANTA BARBARA | GOLETA | 2020-06-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  |  | NA | SHADE FARM MANAGEMENT | SUMMERLAND | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | D8 dozer was plowing land to rip upremove tree roots from recently removed citrus trees.ï¿½ No USA Called. Estimated dozer was operating 2 days before this incident was notified to us.
Southern California Gas Company | N | SANTA BARBARA | GOLETA | 2020-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | RAWLAND DEVELOPMENT LLC | GOLETA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Landowner employees were exposing gas lines while trenching to plant new orchard.ï¿½ Employee struck gas line while hand exposing.
Southern California Gas Company | N | SANTA BARBARA | GUADALUPE | 2020-05-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 59 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TJN BACKHOE | SANTA MARIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Excavator was building a trash enclosureï¿½for a new apartment building. Hit the 1 inch pla service with a mini excavator.ï¿½
Southern California Gas Company | N | SANTA BARBARA | LOMPOC | 2020-10-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CHESTNUT VILLAGA HOA | LOMPOC | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA Ticket for work to replace fence post.ï¿½ 1 inch plastic service damage by posthole digger.
Southern California Gas Company | N | SANTA BARBARA | LOMPOC | 2020-03-31 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RW SCOTT | SANTA MARIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damage No USA ticket 0.5inch plastic service alter No meter at model home in new tract
Southern California Gas Company | N | SANTA BARBARA | LOMPOC | 2020-06-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | LOMPOC | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home Owner struck 0.50 inch Plastic Service with a post hole digger while building a fence. No USA.ï¿½
Southern California Gas Company | N | SANTA BARBARA | LOMPOC | 2020-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 2 |  | NA | LOMPOC | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | none
Southern California Gas Company | N | SANTA BARBARA | LOMPOC | 2020-04-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | WALLACE SMITH CONSTRUCTION | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | 3rd party damage. Excavator dug outside of delineation.
Southern California Gas Company | N | SANTA BARBARA | LOMPOC | 2020-05-07 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 8 | 340 | 170 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 25001 |  | 1 |  | NA | LOMPOC | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party Damage.ï¿½ Employee of business using large earth mover to clear brush and weed abatement.
Southern California Gas Company | N | SANTA BARBARA | LOMPOC | 2020-12-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | LOMPOC | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Owner was digging to expose sewer. No USA
Southern California Gas Company | N | SANTA BARBARA | LOMPOC | 2020-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ERNESTO PAZ | LOMPOC | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA.ï¿½ Maintenance contractor Casimiro Gomez hit gas service line while digging with a shovel to install a fence.
Southern California Gas Company | N | SANTA BARBARA | LOS OLIVOS | 2020-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | LOS OLIVOS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damage.ï¿½ No USA. Plastic Service damaged with post hole digger.
Southern California Gas Company | N | SANTA BARBARA | LOS OLIVOS | 2020-07-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 59 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CRAIG LITTLE | SANTA YNEZ | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was digging to find the septic tank with a probe and poked through a 0.5 inch pla service. No USAï¿½
Southern California Gas Company | N | SANTA BARBARA | LOS OLIVOS | 2020-12-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | LOS OLIVOS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was handï¿½digging in theï¿½yard. ï¿½There was an expired USA ticket and some marking but where he was digging the marking were gone.ï¿½ The homeowner suspected there was a gas line in the area and was trying to be careful but still hit the line.
Southern California Gas Company | N | SANTA BARBARA | LOS OLIVOS | 2020-12-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JOHNSON EXCAVATION | BUELLTON | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor damaged service line in property while excavating for sewer. USA called in, Gas within delineation was marked out correctly, But Excavation took place prior to legal start date.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LINE WORKS | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged our pipe with a shovel while potholing utilities.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-12-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | EARTHBOUND ELEC INC | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Electrical contractor was trenching to install conduit for city.ï¿½ Was aware of mark but continued with trencher over 0.5 plastic service.ï¿½ Contractor stated they were trying to raise the trencher when it hit the underground substructure.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-01-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PHELAN CONSTRUCTION | NIPOMO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavator thought potholed service continued in other direction
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-12-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | SANTA BARBARA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-03-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HOTLINE CONSTRUCTION | SANTA PAULA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit clearly flagged service
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-11-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | DIEGO | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Most flags removed. Hit service while potholing.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | LASH CONSTRUCTION | SANTA BARBARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Lash Construction was trenching for city water main.ï¿½ Exposed properly mark gas service and cut service with shovel as they were clearing the trench.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GARCIA LANDSCAPING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner contracted third party to dig a new yard line for pool.ï¿½ Third party struck 0.5 service directly in front of gas service.ï¿½ No USA called.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-10-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LASH CONSTRUCTION | SANTA BARBARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was hand digging to expose clear service line and hit plastic service with shovel.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | B CABRERA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner lifting old home for new foundation.ï¿½ While trenching to place support jacks he hit 0.5 plastic service to unoccupied home.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-05-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | VICTOR RAMIREZ | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging for water, no USA
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | SANTA BARBARA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA working on back porch
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RODOLFO ESTRADA | CARPINTERIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor trenching to install a new sewer line.ï¿½ Had a current USA, was aware of service location, and cut service with shovel while trenching near the meter location.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LASH CONSTRUCTION INC | SANTA BARBARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator ripped up a 0.50 inch pla service digging a trench for a new water main.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-08-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | BAILEY CONSTRUCTION | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor clearing area for electrical conduit installation.ï¿½ While removing dirt, contractor hit service with shovel.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-11-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | JR PLUMBING | SANTA BARBARA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-08-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | ROTO ROOTER | VISTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Roto Rooter was digging to uncover the sewer clean out access cover.ï¿½ Was not aware of any gas line in the area he was excavating.ï¿½ Hit 0.5 inch service for two units with electric jack hammershovel.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-01-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | SANTA BARBARA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit with a shovel no USA called
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-01-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | STONE CONCEPTS | BUELLTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA Service hit with pick
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-11-13 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SOCAL EDISON | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor excavating to install electric conduit junction box.ï¿½ Struck 1 inch service with backhoe.ï¿½ Service unmarked at dig in location.ï¿½ Location was marked up street for 1530 Roble service from service history records footage. Pothole was requested at that location due to poor tracer line signal.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-10-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | TIERRA CONTRACTING | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Company employee and contractor had site visit and verbal agreement on where gas service was prior to excavation while HP Standby SCG employee with transmission was present.ï¿½ Contractor stated he knew the service was in location and hand dug.ï¿½ They believed they found service was actually 1 inch water line and while exposing further in hard dry clay soil they made a small slice in 1 inch service.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-08-12 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | INTEGRITY CONTRACTORS INC | CORONA | CA | Y | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Our contractor was exposing by hand a service incased in a hard slurry when they nicked our service.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-11-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | SANTA BARBARA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5 inch service damaged by shovel during landscaping activities.ï¿½
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-10-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MGS INC JOSE MARTINEZ | SANTA BARBARA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No current USA.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | LASH CONSTRUCTION INC | SANTA BARBARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit line with large bucket on the backhoe.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | SANTA BARBARA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowners brother was trenching sewer line for repairs.ï¿½ While digging he struck 0.5 inch exposed gas line with shovel.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | private contractor hit 0.5 inch pla service with shovel, no USA ticket and ho not home.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-12-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ROOTER TIME | CAMARILLO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged plastic service with shovel.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-10-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | 323 574 8800 | SYLMAR | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Owner had landscaper trench to install irrigation line to the rear yard.ï¿½ Owner was unaware USA was required prior to having the excavation work started.ï¿½ Contractor was seen loading excavation equipment on trailer and driving away upon first responders arrival. Owner provided landscapers information over the phone.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | SUPERIOR CONCRETE | LOMPOC | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | third party contractor dug without a valid USA and damaged a 0.5 inch pla service.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-08-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA, Service tied back upon arrival
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-08-17 | Third party excavation damage | Main | Polyethylene Pipe | Grader/Scraper | 2 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TOWER COMMUNICATIONS | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party hit an unmarked main while trenching for atandt
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TURN AROUND COMMUNICATIONS | COVINA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor working for ATT, to install telecommunication conduit, hit 0.5 inch service with shovel while cleaning trench for conduit installation.ï¿½ Marks were correct and visible from work location.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | OBDULIO GARCIA | SANTA BARBARA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Owner of property was having gardener plant some shrubs near the main house when gardener hit 0.5 inch service to a two meter manifold master meter
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | TIERRA CONTRACTING | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor hit service with shovel while extending the trench.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-07-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LASH CONSTRUCTION | SANTA BARBARA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Third party hit 0.5 inch pla service with backhoe. Service was not on GIS.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-12-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ELITE ROOTER | VENTURA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Elite Rooter repairing sewer line for 316 Pedregosa in the alley way.ï¿½ Was told by another plumber there was no utilities in alleyway.ï¿½ Marc, of Elite, used a grinder to cut 0.75 steel line out of his way to work on sewer.ï¿½ 0.75 inch steel line was old gas line being used as casing for pressured 0.5 plastic line.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-01-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | KEN KOSTER QUALITY TREE INC | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | USA was not called for this job
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-08-12 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 36 |  | TIJERA CONSTRUCTION | SANTA BARBARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Tierra was trenching for a water main and hit our 2 inch main with a backhoe within delineated area and all facilities were marked.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-07-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | ANACAPA CONCRETE | SANTA BARBARA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party trenching to install electric across customer driveway for electric security gate.ï¿½ During excavation, contractor cut service to home.ï¿½ No USA requested.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | OMAR LAZCANO | BUELLTON | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Expired USA.ï¿½
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-10-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JESUS LASCANO | BUELLTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 0.5 plastic service. USA was current and located and marked correctly.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-07-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | WALLACE AND WYBLE LANDSCAPE | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor dug through our 0.5 inch service with a shovel.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-07-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | OMAR S LANDSCAPING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Omar Landscaping was trenching to install a footingblock wall. Struck 0.5 inch service with shovel.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-09-16 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 24 |  | LAST CONSTRUCTION | SANTA BARBARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor severed 1 way fed main
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-11-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | LASH CONSTRUCTION INC | SANTA BARBARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor found steel pipe that was directly over our incased PLA service. Hit our service with backhoe.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-11-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LASH CONSTRUCTION | SANTA BARBARA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor did not call when they could not find our main.ï¿½
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | LASH CONSTRUCTION | SANTA BARBARA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third part excavating to install water line for city.ï¿½ While trenching, hand shovel cut service with shovel.ï¿½ Contractor was aware of service location. ï¿½
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-08-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | VITALIY BUBNYAK | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA, hit service line while digging for irrgation
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-08-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | GOLETA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 1 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SPIELES CONSTRUCTION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber was removing old piping in the area to install new water and irrigation lines.ï¿½ Used a Sawzall to cut what was thought to be a abandon water line.ï¿½ Cut into an active 1 inch gas service.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-04-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JESUS AND SON LANDSCAPING | GOLETA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscaper hit service with a shovel.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-10-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | AAA DEVELOPMENT | CAMARILLO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor excavating for irrigation line hit 1 inch service with trachoe.ï¿½ Stated, upon arrival, he hit line with jackhammer.ï¿½ When questioned by supervisor the contractor stated he tore line with bucket on excavating hydraulic equipment.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-11-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | SUPERIOR CONCRETE | LOMPOC | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was trenching over gas service to dig new construction footings.ï¿½ Hit 0.5 inch service with backhoe.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-08-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PACIFIC NETWORKS | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 4 |  | PRESERVE PLUMBING | GOLETA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor replacing sewer drain hit 0.5 inch service with shovel while hand digging around our service line.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-01-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ELITE ROOTER | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber broke service with cable while pulling new sewer lateral
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TIDWELL EXCAVATION | VENTURA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | excavator hit 0.5 inch service. gis showed an abandoned servive but it was still live.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-02-12 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | HERMAN WIESSKER | JURUPA VALLEY | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Company contractor hit service while exposing.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | SANTA BARBARA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Lynn Morris Contractor. Foothill Nursery and Landscape, Inc Lic. 946905, removing old Ficus tree roots over 1 inch gas service.ï¿½ Small nick was found on 1 inch service by cut tree root.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-02-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ALLIED FENCE | LOMPOC | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-01-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CLEARWATER ENGINEERING | SANTA BARBARA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA Excavator hit service
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-07-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BOWMAN CONSTRUCTION | SANTA YNEZ | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor hit 0.5 inch line with shovel while digging trench, all facilities were marked.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-06-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JBI ENGINEERING | VENTURA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-11-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | REVIVE | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor dug out of his said work area.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | SANTA BARBARA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-07-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LINDSAY ADAMS CONSTRUCTION | SUMMERLAND | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hot 0.5 inch service while excavating with shovel.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-02-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GAMBLE CONSTRUCTION | GOLETA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator hit service with backhoe
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SANTA BARBARA TURF | SANTA BARBARA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor hit our 0.50 inch pla service with a shovel. Contractor was digging without a valid USA ticket.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2020-04-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | MAIN LINE ENGINEERING | LOMPOC | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor was excavating with backhoe to install sewer manhole and hit a 0.50 inch service that was unmarked.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2020-01-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA Stub was damaged with a shovel
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2020-12-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | ARRON SHEPHARD | SANTA MARIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | none
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2020-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | TRU CARE LANDSCAPE | NIPOMO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damage.ï¿½ No USA ticket.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2020-12-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | WILSON EXCAVATING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor struck line while excavating.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2020-07-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | SANTA MARIA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner damaged 0.5 inch pla service with Shovel. No USA
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2020-10-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | SANTA MARIA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per LCT. Jonathan Tesoro The renter of 1845 S Flora Way, Adan Aldana, was excavating with a post hole digger to install new fencing.ï¿½ï¿½
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2020-03-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | DARRIN BERRY | SANTA MARIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party Damage No USA ticket ï¿½ 2 plastic service damaged while digging drainage ditch
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2020-07-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TEIXEIRA FARMS | SANTA MARIA | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Farmer Ripping Field.ï¿½ Damaged 2 inch service.ï¿½ Dug before ticket was valid.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2020-07-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | SANTA MARIA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hit line with posthole digger.ï¿½ No USA ticket.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2020-11-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | SANTA MARIA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party damage.ï¿½ No USA ticket. 0.5 inch plastic service damaged by hand tool, posthole digger.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2020-02-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JOSE ESTRADA | SANTA MARIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party damage Post hole digger damaged 0.5inch CTS service ï¿½ MCR for evacuation of home while gas was escaping
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2020-01-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SHEA HOMES | NIPOMO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | none
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2020-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 43 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | DAVE BIDDLE | PISMO BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor didnt have USA. Was hand digging to trench new yard house lines to new unit. 0.50 inch pla service was damaged but not leaking. Found by ETR.ï¿½
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2020-09-25 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LYLES | SANTA MARIA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 2nd Party Damage. Lyles Contractor hit plastic service while hand digging.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2020-02-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | HERRERA CORPORATION | SANTA MARIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA Excavating to inspect and fix leaking water valve Dug into 2 PLA service with Backhoe ï¿½
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2020-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NA | SANTA MARIA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party Damage, No USA ticket
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2020-05-20 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JOE RADWAY | JURUPA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | HWI hit buried 0.5 inch PLA service while exposing it by hand.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2020-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | SANTA MARIA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Son of home owner was putting up a fence and hitï¿½the gas line with shovel.ï¿½
Southern California Gas Company | N | SANTA BARBARA | SANTA YNEZ | 2020-03-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | SANTA YNEZ | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party Damage No USA ticket ï¿½ Digging with Mini Excavator to replace irrigation
Southern California Gas Company | N | SANTA BARBARA | SOLVANG | 2020-07-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ANGELO CACIOLA ARCHITECT BUTCH WITTED | SOLVANG | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor ripped out service and tied it back. Then left the riser and meter off to the side of the construction site. It was two months later SCG employee found it while walking leak survey.ï¿½
Southern California Gas Company | N | SANTA BARBARA | SOLVANG | 2020-05-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ALLIED FENCE CO | LOMPOC | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damage. Post hole digger damaged 0.50 inch CTS plastic service.ï¿½ No USA
Southern California Gas Company | N | SANTA BARBARA | SUMMERLAND | 2020-10-20 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | RICARDO LANDSCAPE CONSTRUCTION | OXNARD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging next to Edison electrical vault struck 2 inch gas main.ï¿½ No USA called.ï¿½ Gas Company wooded post next to excavation.
Southern California Gas Company | N | SANTA BARBARA | TORRANCE | 2020-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RYAN | LA JOLLA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Multiple locators could not locate service to this address. service not marked.
Southern California Gas Company | N | TULARE | ALPAUGH | 2020-07-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | RV IRONWORKS | PORTERVILLE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | WORKERS HIT A MAIN LINE ON SIDE OF ROAD WITHï¿½ EXCAVATOR WHILE DIGGING TO REPAIR WATER LINE.
Southern California Gas Company | N | TULARE | DINUBA | 2020-02-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | STANLEY A WARD CONSTRUCTION | DINUBA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Bill Nulick of Stanley A Ward Construction hit service with shovel while digging to install electrical tie in USA was notified excavator failed to maintain clearance Crew made permanent repairs
Southern California Gas Company | N | TULARE | DINUBA | 2020-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | JOSE SANCHEZ | KINGSBURG | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Electrical contractor Jose Sanchez, J.D.S. Electrical, was digging a trench with a pick when service was struck. USA was not notified. Contractor was educated on USA laws, crew made permanent repairs.ï¿½ ï¿½
Southern California Gas Company | N | TULARE | DINUBA | 2020-05-28 | Third party excavation damage | Main | Steel | Hand Tools | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | BRAVO CONSTRUCTION | FRESNO | CA | N | Y | Yes | No | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged a 2 inch gas line, crew made permanent repairs.
Southern California Gas Company | N | TULARE | DINUBA | 2020-12-17 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | BILL NELSON GENERAL ENGINEERING | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged a 0.75 inch steel service, crew made permanent repairs.
Southern California Gas Company | N | TULARE | DINUBA | 2020-03-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | C F IRRIGATION | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged a 2 plastic main with probe crew made permanent repairs
Southern California Gas Company | N | TULARE | DINUBA | 2020-01-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 35 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | REEDLEY IRRIGATION SYSTEM | REEDLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging to replace concrete water stand pipe struck service line USA was not notified Contractor educated on USA law Crew made permanent repairs
Southern California Gas Company | N | TULARE | DINUBA | 2020-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BILL NELSON CONSTRUCTION | FRESNO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged an ï¿½unmarked 0.75 inch steel gas service, crew made permanent repairs.
Southern California Gas Company | N | TULARE | DINUBA | 2020-05-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 0.75 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | CVIN | FRESNO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor was Boring in fiber optic cable and struck gas line.ï¿½ USA was current Service was not marked.
Southern California Gas Company | N | TULARE | DINUBA | 2020-08-13 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | BROWNING CONTRACTORS | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to pothole the gas facilities and damaged a 2 inch plastic main, crew ï¿½made permanent repairs.
Southern California Gas Company | N | TULARE | DINUBA | 2020-01-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 2 |  | NA | DINUBA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner digging for fence replacement damaged the gas line homeowner was educated about USA law crew made permanent repairs
Southern California Gas Company | N | TULARE | EARLIMART | 2020-05-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | IRIS ELECTRIC | TULARE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor did not hand exposeï¿½prior to digging with the backhoe and then hit the gas service.
Southern California Gas Company | N | TULARE | EARLIMART | 2020-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | HAYDON CONSTRUCTION | CLOVIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 0.5 inch service that was marked incorrectly.
Southern California Gas Company | N | TULARE | EXETER | 2020-11-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 3 |  | HOLMES LANDSCAPE | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscaper working for homeowner struck service line with shovel while digging. USA was not notified. Contractor educated on USA laws. Crew made permanent repairs.
Southern California Gas Company | N | TULARE | EXETER | 2020-11-11 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 4 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 30001 |  |  | NA | AJ EXCAVATION | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 2in and 4in steel main while grading, contractor did not pothole main to check depth.
Southern California Gas Company | N | TULARE | EXETER | 2020-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | AJ EXCAVATION | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged a 0.75 inch steel service, crew made permanent repairs.
Southern California Gas Company | N | TULARE | EXETER | 2020-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | SUPREME POOLS | LINDSAY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant damaged a 0.50 inch plastic gas line, crew made permanent repairs.
Southern California Gas Company | N | TULARE | EXETER | 2020-04-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | PRISTINE POOLS | VISALIA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor damaged a 0.50 inch gas line, crew made permanent repairs
Southern California Gas Company | N | TULARE | EXETER | 2020-06-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | NA | EXETER | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged a gas riser, crew made permanent repairs.
Southern California Gas Company | N | TULARE | EXETER | 2020-02-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 35 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 6 |  | SO CAL EDISON | TULARE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged a 2 plastic main crew made permanent repairs
Southern California Gas Company | N | TULARE | FARMERSVILLE | 2020-09-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DON BERRY CONSTRUCTION | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Per Contractor, Hit Line with disk and tractor while digging. Stub was not marked. Known facility, shown in service history. Locator failed to mark stub.
Southern California Gas Company | N | TULARE | FARMERSVILLE | 2020-11-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | MARTIN CONSTRUCTION | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged a 0.5 inch plastic gas line, crew made permanent repairs.
Southern California Gas Company | N | TULARE | FARMERSVILLE | 2020-05-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 2 |  | NA | FARMERSVILLE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant damaged a 0.50 inch plastic gas line, crew made permanent repairs.
Southern California Gas Company | N | TULARE | FARMERSVILLE | 2020-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | FARMERSVILLE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer was digging to install fence when service was struck. USA was not notified. Customer educated on USA laws, crew made permanent repairs.
Southern California Gas Company | N | TULARE | FARMERSVILLE | 2020-08-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | FARMERSVILLE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer failed to notify USA.ï¿½ He damaged SCGs service while excavating to repair water line.
Southern California Gas Company | N | TULARE | FARMERSVILLE | 2020-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | WIRING CONNECTION | FARMERSVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged a 0.50 inch gas service, crew made permanent repairs.
Southern California Gas Company | N | TULARE | FARMERSVILLE | 2020-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | FARMERSVILLE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner was probing for sewer leak when he probed into gas line
Southern California Gas Company | N | TULARE | KINGSBURG | 2020-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 32 | 27 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | BRIAN MONROI | KETTLEMAN | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractordug without calling USA dig alert andï¿½damaged a 0.50 inch gas line, crew made permanent repairs.
Southern California Gas Company | N | TULARE | LINDSAY | 2020-06-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NA | LINDSAY | CA | N | Y | Yes | Excavation occurred on private property by a non-contractor. | Yes | Yes | No | Yes | Yes | Homeowner dug on expired USA ticket and damaged a 0.50 inch plastic gas line, crew made permanent repairs.
Southern California Gas Company | N | TULARE | LINDSAY | 2020-05-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | LINDSAY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer was digging with post hole digger when service was struck. USA was not notified. Customer educated on USA laws. Crew made permanent repairs.
Southern California Gas Company | N | TULARE | LINDSAY | 2020-10-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | WOODLAKE |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per LCT Luis Lopez Contractor Giovanni De La Torre excavating to install electric facilities for property owner.ï¿½ De La Torre was hand digging with shovel.ï¿½ Claimed he had a USA ticket but could not find the ticket number.
Southern California Gas Company | N | TULARE | LINDSAY | 2020-04-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | AMERICAN INC | VISALIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged a 2 inch gas service, crew made permanent repairs.
Southern California Gas Company | N | TULARE | PIXLEY | 2020-06-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor worked without calling USA dig alert,ï¿½damaged a 0.50 inch gas line, crew made permanent repairs.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2020-04-07 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ARB | LAKE FOREST | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged a 0.5 inch gas line, crew made permanent repairs.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2020-08-18 | Third party excavation damage | Main | Polyethylene Pipe | Probing Device | 2 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  | 1 |  | LANDMARK IRRIGATION | MADERA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged main with steel probe, crew made permanent repairs.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2020-07-20 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 45 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  | 1 |  | ARB | BAKERSFIELD | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged a 0.5 inch plastic line, crew made permanent repairs.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2020-02-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | PORTERVILLE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner Uriel Loya damaged service line while removing a tree from his property
Southern California Gas Company | N | TULARE | PORTERVILLE | 2020-05-11 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NADER DEVELOPEMENT INC | PORTERVILLE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CONTRACTOR DIGGING FOR PLUMBING.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2020-08-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | BILL NELSON ENGINEERING | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor potholed overï¿½unknown 1 inch pipe and ï¿½damaged a 1 inch plastic gas line, crew made permanent repairs.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2020-10-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ARTHUR RODRIGUEZ | SPRINGVILLE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 0.5 inch plastic service while digging for a water line without a valid usa ticket.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2020-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | RPP INC | PORTERVILLE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor excavated without USA and damaged a 1 inch plastic gas line, crew made permanent repairs.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2020-02-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | PORTERVILLE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service hit by 3rd party
Southern California Gas Company | N | TULARE | PORTERVILLE | 2020-09-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | PORTERVILLE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer was hand digging to remove tree stump when service was struck. USA was not notified, homeowner educated on USA laws. Crew made permanent repairs.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2020-02-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GORDON TROTT | PORTERVILLE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged a 0.5inch plastic service crew made permanent repairs
Southern California Gas Company | N | TULARE | PORTERVILLE | 2020-08-12 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | MIKE EMMERICH | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to pothole the gas facilities and damaged a 2 inchï¿½steel main, crew made permanent repairs.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2020-11-24 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | BILL NELSON CONSTRUCTION | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged a 0.75 inch steel gas line, crew made permanent repairs.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2020-10-13 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | PRECISION | SAUSALITO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 2 inch plastic main while digging to install sewer line without a valid usa ticket.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2020-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | CAL VALLEY CONSTRUCTION | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged steel service which was marked correctly.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2020-08-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | BILL NELSON CONSTRUCTION | FRESNO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged a 0.5 inch plastic line, crew made permanent repairs. Contractor provided invalid USA ticket number.
Southern California Gas Company | N | TULARE | RICHGROVE | 2020-04-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | SPECTRUM SOLAR | FRESNO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged a 0.50 inch plastic gas line, crew made permanent repairs.
Southern California Gas Company | N | TULARE | TIPTON | 2020-12-16 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | RENEWABLE SOLAR | HANFORD | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 2in service downstream of FSR while trenching for electrical, contractor exvcavated prior to USA ticket being valid.
Southern California Gas Company | N | TULARE | TIPTON | 2020-10-27 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | LYLES UTILITY CONSTRUCTION | VISALIA | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged 0.5 inch service while exposing service to install bollards.
Southern California Gas Company | N | TULARE | TULARE | 2020-08-21 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MAC GENERAL | PORTERVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to pothole as required and damaged a 1 inch steel gas service, crew made permanent repairs.
Southern California Gas Company | N | TULARE | TULARE | 2020-06-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | TULARE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant damaged a 0.50 inch gas line, crew made permanent repairs.
Southern California Gas Company | N | TULARE | TULARE | 2020-01-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | AMERICAN FENCE BUILDERS | TULARE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor crew was excavating holes via bobcat auger and struck 1 plastic service in the process Explained to the contractor the importance of calling 811
Southern California Gas Company | N | TULARE | TULARE | 2020-08-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | MAC GENERAL ENGINEERING | PORTERVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to pothole as required and damaged a 0.75 inch steel gas service, crew made permanent repairs.
Southern California Gas Company | N | TULARE | TULARE | 2020-08-17 | Third party excavation damage | Main | Steel | Miscellaneous/Other | 2 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 15001 |  | 3 |  | MAC CONSTRUCTION | PORTERVILLE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was working on redoing the road. Basic road work.ï¿½Contractor worked outside the delineated area and damaged 2 inch steel main, crew made permanent repairs.
Southern California Gas Company | N | TULARE | TULARE | 2020-12-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LAZER UNDERGROUND | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 0.5 inch service while hand digging to install ATT line.
Southern California Gas Company | N | TULARE | TULARE | 2020-05-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | TULARE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | digging to install a fence. hit service with manual post digger
Southern California Gas Company | N | TULARE | TULARE | 2020-02-18 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | FRESNO PLUMBING | TULARE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Fresno Plumbing backhoe operator hit line while digging for sewer line USA was notified Excavator failed to maintain clearance contractor was educated on USA law Crew made permanent repairs
Southern California Gas Company | N | TULARE | TULARE | 2020-05-26 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | FRESNO PLUMBING | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor did not hand expose the main prior to digging with the backhoeï¿½and hit the gas main.
Southern California Gas Company | N | TULARE | TULARE | 2020-01-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | IRISH ELECTRIC | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Irish Electric crew was digging to install conduit and damaged the marked gas line
Southern California Gas Company | N | TULARE | TULARE | 2020-05-07 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 4 |  | RCC CONCRETE | PORTERVILLE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged a 2 inch plastic main, crew made permanent repairs.
Southern California Gas Company | N | TULARE | TULARE | 2020-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | RV AG | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was trenching to install a gas line for dairy equipment.ï¿½
Southern California Gas Company | N | TULARE | TULARE | 2020-07-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | 99 PIPELINE | PORTERVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged a 0.5 inch plastic service while working a water project, crew made permanent repairs.
Southern California Gas Company | N | TULARE | TULARE | 2020-08-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | MAC | PORTERVILLE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor failed to renew USA ticket, damaged a 0.5 inch plastic service. Crew made permanent repairs.
Southern California Gas Company | N | TULARE | TULARE | 2020-12-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | TULARE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damages 0.5 inch plastic service while digging to remove tree stump, USA was not called.
Southern California Gas Company | N | TULARE | TULARE | 2020-05-29 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | DCW CONTRACTORS | VISALIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | PER JOSH HOUSEY CHANGING FIRE HYDRANT, WHEN LIFTING CONCRETE, CLIPPED GAS LINE, GAS ESCAPING
Southern California Gas Company | N | TULARE | TULARE | 2020-03-31 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DCW CONTRACTORS | VISALIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to excavate with hand tools as required damaged a 2 plastic main crew made permanent repairs
Southern California Gas Company | N | TULARE | TULARE | 2020-02-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 1 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | HAYDEN CONSTRUCTION | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractorï¿½ damaged the gas line while hand digging to pot hole it
Southern California Gas Company | N | TULARE | TULARE | 2020-11-12 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 15001 |  | 2 |  | PAREMENT RECYCLING | MIRA LOMA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 2in main with grader, main was clearly and correctly marked. Contractor did not pothole for depth.
Southern California Gas Company | N | TULARE | TULARE | 2020-05-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | TULARE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Gas line hit while customer was digging
Southern California Gas Company | N | TULARE | TULARE | 2020-09-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | 99 PIPE LINE | PORTERVILLE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged a 0.5 inch plastic gas line, crew made permanent repairs. Contractor provided invalid USA ticket number.
Southern California Gas Company | N | TULARE | TULARE | 2020-04-07 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 2 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | ROMANAZZI GENERAL ENGINEERING | EXETER | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor cut into live service with electric saw, crew made permanent repairs.
Southern California Gas Company | N | TULARE | TULARE | 2020-02-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | TULARE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home ownerï¿½was excavating to install a Gazebo in backyard and hit PE service in the process no USA was called
Southern California Gas Company | N | TULARE | TULARE | 2020-09-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | CHASE WHITNEY POOLS | WASCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | none
Southern California Gas Company | N | TULARE | TULARE | 2020-09-16 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  | 6 |  | 99 PIPELINE | PORTERVILLE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged 2 inch main that was mismarked during a sewer line installation.
Southern California Gas Company | N | TULARE | TULARE | 2020-06-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | CENTRAL VALLEY AWNING | CLOVIS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor dug without USA, damaged a 1 inch plastic gas line, crew made permanent repairs. Aerating was required due to code 1 indications at foundation.
Southern California Gas Company | N | TULARE | VISALIA | 2020-09-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | VISALIA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CUSTOMER HAND DIGGING FOR FLAG POLE. USA WAS NOT NOTIFIED, HOME OWNER EDUCATED ON USA LAWS. CREW MADE PERMANENT REPAIRS.ï¿½
Southern California Gas Company | N | TULARE | VISALIA | 2020-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LASER UNERGROUND CONSTRUCTION | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged a 0.5 inch plastic gas line with shovel, crew made permanent repairs.
Southern California Gas Company | N | TULARE | VISALIA | 2020-01-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ROBERTSON MCLAUGHLIN PLUMBING | VISALIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging to make sewer repairs and damaged the gas line
Southern California Gas Company | N | TULARE | VISALIA | 2020-02-17 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | THE LAKE HOUSING COMMUNITY | VISALIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged the gas line while digging for electric conduit contractor was using hand tools he was educated about USA law Crew made permanent repairs
Southern California Gas Company | N | TULARE | VISALIA | 2020-06-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 1 |  | CROAD ELECTRIC | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged a 1 inch plastic gas line, crew made permanent repairs.
Southern California Gas Company | N | TULARE | VISALIA | 2020-04-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  |  | NA | A1 CONTRACTORS | VISALIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to exercise caution while potholing the gas line.
Southern California Gas Company | N | TULARE | VISALIA | 2020-06-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 1 |  | PACIFIC UTILITY TRENCHING | PORTERVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged a 1 inch plastic gas line, crew made permanent repairs.
Southern California Gas Company | N | TULARE | VISALIA | 2020-07-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ROBERT LARA | FRESNO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging for fence work, contractor damaged a gas line, crew made permanent repairs, contractor was educated about USA law.
Southern California Gas Company | N | TULARE | VISALIA | 2020-03-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | VISALIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Workers digging to install electrical without a valid USA hit the service with shovel
Southern California Gas Company | N | TULARE | VISALIA | 2020-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | AMERICAN CUTTING AND DEMOLITION | VISALIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged riser while demoing a building.
Southern California Gas Company | N | TULARE | VISALIA | 2020-01-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | LIVING WATER POOLS | TULARE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging trench for electrical work and damaged the gas line Contractor was educated about USA law
Southern California Gas Company | N | TULARE | VISALIA | 2020-09-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | SO CAL EDISON | TULARE | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit service line while augering to install power pole.
Southern California Gas Company | N | TULARE | VISALIA | 2020-11-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | LANDSCAPE DEVELOPMENT | CLOVIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 1 inch service that was marked correctly.
Southern California Gas Company | N | TULARE | VISALIA | 2020-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | DURANGO FENCING | VISALIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging for fence post, contractor damaged a 0.5 inch plastic gas line. Contractor was educated about USA law.
Southern California Gas Company | N | TULARE | VISALIA | 2020-01-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NA | VISALIA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged the gas line while digging to install electric conduit Crew made permanent repairs Contractor was educated about USA law
Southern California Gas Company | N | TULARE | VISALIA | 2020-11-25 | Third party excavation damage | Main | Polyethylene Pipe | Trencher | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | WESTECH SYSTEMS | CLOVIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to pot hole our 2in gas main that was marked correctly and marks were visible. They damaged our line while trenching with a trencher.
Southern California Gas Company | N | TULARE | VISALIA | 2020-08-06 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ARB | LAKE FOREST | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Company contractor damaged a 0.5 inch plastic line whileï¿½potholing with a shovel.
Southern California Gas Company | N | TULARE | VISALIA | 2020-12-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | HAYDON CONSTRUCTION | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 1 in service while excavating to install sewer line. Service was marked correctly.
Southern California Gas Company | N | TULARE | VISALIA | 2020-10-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | JUAN INIGUEZ | TULARE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged a 0.5 inch plastic gas line, crew made permanent repairs. Contractor was educated about USA law.
Southern California Gas Company | N | TULARE | VISALIA | 2020-06-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | EMPOWER SOLAR | FRESNO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged a 0.50 inch gas line, crew made permanent repairs. Contractor was unable to provide a valid USA ticket.
Southern California Gas Company | N | TULARE | VISALIA | 2020-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | SPENCE FENCE COMPANY | VISALIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged a 0.50 inch plastic gas line, crew made permanent repairs.
Southern California Gas Company | N | TULARE | VISALIA | 2020-03-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | 3 R CONSTRUCTION | DINUBA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service damaged by 3rd party ï¿½ USA was currant and correct ï¿½ Contractor failed to use caution while digging around gas service
Southern California Gas Company | N | TULARE | VISALIA | 2020-01-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | VISALIA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant was removing a tree stump and cut the gas line
Southern California Gas Company | N | TULARE | VISALIA | 2020-10-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | SO CAL EDISON | TULARE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged a 0.5 inch plastic gas line, crew made permanent repairs, contractor failed to call USA.
Southern California Gas Company | N | TULARE | VISALIA | 2020-12-05 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | WESTECH SYSTEMS | CLOVIS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged a 2 inch plastic main, crew made permanent repairs. USA given by contractor appears to be invalid number.
Southern California Gas Company | N | TULARE | VISALIA | 2020-02-21 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | QUALITY LANDSCAPE CONSTRUCTION | VISALIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged a 2 plastic main while digging for landscaping crew made permanent repairs contractor was educated about USA law
Southern California Gas Company | N | TULARE | VISALIA | 2020-07-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | LASER UNDERGROUND | CLOVIS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor excavated without calling USA and damaged a 0.5 inch service, crew made permanent repairs.
Southern California Gas Company | N | TULARE | VISALIA | 2020-05-21 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | NORTHERWESTERN INCORPORATED | OAKHURST | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged a 2 inch plastic main, crew made permanent repairs.
Southern California Gas Company | N | VENTURA | CAMARILLO | 2020-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SAULET MASONRY | CAMARILLO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA called for this job.
Southern California Gas Company | N | VENTURA | CAMARILLO | 2020-12-16 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 50 | 35 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | A A CONCRETE | VENTURA |  | N | Y | Yes | No | No | Yes | No | Yes | Yes | Contractor dug prior to legal date and time allowed.
Southern California Gas Company | N | VENTURA | CAMARILLO | 2020-02-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SCOTT HUNTER | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA called for this job
Southern California Gas Company | N | VENTURA | CAMARILLO | 2020-07-06 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  |  | NA | PACIFIC HYDROTECH CORP | PERRIS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging with out USA ticket and broke 2 inch PLA Main.
Southern California Gas Company | N | VENTURA | CAMARILLO | 2020-04-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | KENNY RILEY | THOUSAND OAKS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA called for this job.
Southern California Gas Company | N | VENTURA | CAMARILLO | 2020-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | TORO ENTERPRISES INC | OXNARD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Service was not marked. USA was current.ï¿½
Southern California Gas Company | N | VENTURA | CAMARILLO | 2020-12-21 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 50 | 40 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | OLTMAS CONSTRUCTION | CAMARILLO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | The locator marks incorrectly indication theï¿½3 inch main ended in a location away from where the damage occurred. The damage to the main did not cause a leak and a 50 foot section of main was abandonedï¿½in lieu of a repair to the main.ï¿½
Southern California Gas Company | N | VENTURA | CAMARILLO | 2020-06-10 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | TORO ENTERPRISES | OXNARD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor pot holing for gas line hit main with a backhoe.
Southern California Gas Company | N | VENTURA | FILLMORE | 2020-05-18 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TORO GENERAL CONTRACTORS | OXNARD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA ticket. Contractor digging for new utilities. NB track
Southern California Gas Company | N | VENTURA | FILLMORE | 2020-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | FILLMORE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner was digging with a mini excavator when they hit service line.
Southern California Gas Company | N | VENTURA | FILLMORE | 2020-10-14 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | P L PLUMBING INC | SIMI VALLEY |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavator damaged facility during trenching operations.ï¿½
Southern California Gas Company | N | VENTURA | FILLMORE | 2020-12-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | AMERICAN INVESTMENTS | VENTURA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was trenching for Irrigation when they hit a 0.5 inchcts gasï¿½service. No USA ticket.
Southern California Gas Company | N | VENTURA | MOORPARK | 2020-07-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | REDS PLUMBING | SYLMAR | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging for sewer repair when they hit SCG Line.
Southern California Gas Company | N | VENTURA | MOORPARK | 2020-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | I RAMIREZ | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | I. Ramirez Corporation Was Boring for Spectrum When they hit an unmarked SCG Stub.
Southern California Gas Company | N | VENTURA | MOORPARK | 2020-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ASPHALT PROFESSIONALS INT | NEWBURY PARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged Service while hand digging. Potholing for power when they hit gas service.
Southern California Gas Company | N | VENTURA | NEWBURY PARK | 2020-02-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | NEWBURY PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Home owner failed to take caution while digging
Southern California Gas Company | N | VENTURA | NEWBURY PARK | 2020-10-23 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | APL | CHATSWORTH | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Arizana Pipeline struck Plastic gas service with shovel while hand exposing to bore in new gas service.
Southern California Gas Company | N | VENTURA | NEWBURY PARK | 2020-10-12 | Operator excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 3 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | APL | CHATSWORTH | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | APL Installed a new gas main and dropped hot asphalt causing a burn through.
Southern California Gas Company | N | VENTURA | OAK PARK | 2020-03-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit gas service line while digging with shovels to install irrigation No USA Service was at 21
Southern California Gas Company | N | VENTURA | OAK VIEW | 2020-06-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | OAK VIEW | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA.
Southern California Gas Company | N | VENTURA | OAK VIEW | 2020-01-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 4 |  | MARTIN CONST | YUCAIPA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | USA is current and gas service was mappedï¿½incorrectly on GIS
Southern California Gas Company | N | VENTURA | OAK VIEW | 2020-07-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | OAK VIEW | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA called for this job.
Southern California Gas Company | N | VENTURA | OJAI | 2020-05-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | OJAI | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service while pot holing for water line.
Southern California Gas Company | N | VENTURA | OJAI | 2020-11-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | EH IRON FENCE | FILLMORE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA called for this job.ï¿½
Southern California Gas Company | N | VENTURA | OJAI | 2020-05-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | BRYAN DUSKE | OXNARD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA was called for this job.
Southern California Gas Company | N | VENTURA | OJAI | 2020-12-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | SANTA PAULA | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Land Owner was Digging a trench for water line when he hit a 1 inch Plastic gas service. Owner was digging be for legal start date.
Southern California Gas Company | N | VENTURA | OJAI | 2020-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | I RAMIREZ CORPORATION | SAN FERNANDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1 inch plastic service hit during excavation.ï¿½
Southern California Gas Company | N | VENTURA | OJAI | 2020-05-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CHAD CARPER | OJAI | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party Contractor damaged 0.50 inch plastic with a backhoe. No USA called for this job.
Southern California Gas Company | N | VENTURA | OXNARD | 2020-04-27 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 0.75 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | CITY OF OXNARD | OXNARD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Stub was not marked. It is showing on GIS but has no other information on service history.
Southern California Gas Company | N | VENTURA | OXNARD | 2020-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | TORO ENTERPRISES INC | OXNARD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Unknown stub service was hit by Contractor. Stub not showing on maps and any other reference.
Southern California Gas Company | N | VENTURA | OXNARD | 2020-04-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | TORO | OXNARD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Locator did not marked stub service showing on GIS.
Southern California Gas Company | N | VENTURA | OXNARD | 2020-12-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | GERALDO POSADES | OXNARD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA called in for this job.
Southern California Gas Company | N | VENTURA | OXNARD | 2020-06-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ESTATE PUMBING | VENTURA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA called for this job.
Southern California Gas Company | N | VENTURA | OXNARD | 2020-12-09 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 3 | 50 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | TVC GROUP | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party Contractor damage main while performing boring operations.ï¿½
Southern California Gas Company | N | VENTURA | OXNARD | 2020-05-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10001 |  |  | NA | AMANDO REYES | OXNARD | CA | N | Y | No | No | No | No | No | No | No | No USA called for this job.
Southern California Gas Company | N | VENTURA | OXNARD | 2020-04-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | MEIER PLUMBING INC | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working on a sewer line hit 0.50 service. No USA was called for this job.ï¿½
Southern California Gas Company | N | VENTURA | OXNARD | 2020-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | OXNARD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging to relocate houseline for planned service alter, service line was hit. Order in the system for planning to alter service. Suspected that contractor hit line to see if So Cal Gas would alter the line then and the customer wouldnt have to wait.
Southern California Gas Company | N | VENTURA | OXNARD | 2020-12-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CATALINOS BERRY FARMS LLC | OXNARD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The 2 inch PLA service was damaged by a shovel during farming operations. The service did not feed an MSA or Reg Station. This service was abandoned at the parkway as it was not feeding a facility.ï¿½
Southern California Gas Company | N | VENTURA | OXNARD | 2020-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | VENTURA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit plastic service with shovel.
Southern California Gas Company | N | VENTURA | OXNARD | 2020-01-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | G R HAMMER CONSTRUCTION | OXNARD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | installing a fence line in alley
Southern California Gas Company | N | VENTURA | OXNARD | 2020-07-08 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 16 |  | THE COLONY AT MANDALAY BAY HOA | OXNARD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumbing being performed by HOA approved contractor. No USA requested. Main damaged caused during excavation.ï¿½No gas indications detected inside the residences. Gas migrated to foundation of residential units. 8 Units evacuated.ï¿½ï¿½
Southern California Gas Company | N | VENTURA | OXNARD | 2020-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CAL PRESTIGE CONSTRUCTION | OXNARD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor excavating for electric conduit damaged 0.50 plastic service.ï¿½
Southern California Gas Company | N | VENTURA | OXNARD | 2020-08-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NICODEMUS CONSTRUCTION | OXNARD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit Service Line caused by shovel putting a post into the ground.
Southern California Gas Company | N | VENTURA | OXNARD | 2020-01-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | INDEPENDENT CONCRETE CUTTING INC | OXNARD | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Contractor dug before 48 hour time requirement
Southern California Gas Company | N | VENTURA | OXNARD | 2020-12-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BUILT HARDY | NEWBURY PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damage 0.5 inch service while trenching.
Southern California Gas Company | N | VENTURA | OXNARD | 2020-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MORAS CONSTRUCTION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Worker hit line with pick. It looked like workers were trying to cut pipe to see what type of line it is.
Southern California Gas Company | N | VENTURA | OXNARD | 2020-12-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 35 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | OXNARD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor nicked plastic service with shovel.
Southern California Gas Company | N | VENTURA | OXNARD | 2020-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LUIS PEREZ | OXNARD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damage 0.5 service with shovel. Located and marked correctly.
Southern California Gas Company | N | VENTURA | PIRU | 2020-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PURE WATER PLUMBING | SIMI VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor severed and tied back service while excavating.
Southern California Gas Company | N | VENTURA | PORT HUENEME | 2020-02-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CITY OF PORT HUENEME | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | USA was current and marks were accurate
Southern California Gas Company | N | VENTURA | PORT HUENEME | 2020-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | DOLON PLUMBING | OXNARD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damage service with shovel.ï¿½
Southern California Gas Company | N | VENTURA | SANTA PAULA | 2020-10-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 50 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TORO ENTERPRISE INC | OXNARD |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damage 0.5 inch plastic service. Locator hooked up locator and located and marked service but only put in one markï¿½ on the street with yellow paint for Contractor.ï¿½
Southern California Gas Company | N | VENTURA | SANTA PAULA | 2020-11-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | TORO ENTERPRISES | OXNARD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 0.5 inch gas service damage by excavator during trenching operations.ï¿½
Southern California Gas Company | N | VENTURA | SANTA PAULA | 2020-09-10 | Operator excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 18 |  | TEICHERT PIPELINE | CHINO | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | DIMP Contractor damaged service T on top of 2 main.
Southern California Gas Company | N | VENTURA | SANTA PAULA | 2020-06-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LANDSCAPE DEVELOPMENT | VALENCIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA called for this job.ï¿½
Southern California Gas Company | N | VENTURA | SANTA PAULA | 2020-06-02 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | ARB | LAKE FOREST | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Company contractor ARB damaged 0.5 plastic service line. USA was current. DIMP Supervisor Jeremy Jansen will be satisfying the Contractor evaluation on ISN.
Southern California Gas Company | N | VENTURA | SANTA PAULA | 2020-01-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TORO | OXNARD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Unknown Stub was hit by backhoe
Southern California Gas Company | N | VENTURA | SANTA PAULA | 2020-10-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MCKNIGHT CONSTRUCTION INC | SIMI VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Gas service damaged during hand digging excavation. No LandM requested.ï¿½
Southern California Gas Company | N | VENTURA | SANTA PAULA | 2020-08-25 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | TEICHART PIPELINE | CHINO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Company contractor hit plastic service with clay spade.
Southern California Gas Company | N | VENTURA | SANTA PAULA | 2020-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | SANTA PAULA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer Brayen Guzman was using mini backhoe digging to repair damaged water line when gas line was hit. No USA called per Brayen Guzman
Southern California Gas Company | N | VENTURA | SANTA PAULA | 2020-10-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | TORO ENTERPRISE INC | OXNARD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Plastic service was located and mark correctly. Contractor Damaged 0.5 inch plastic service with backhoe
Southern California Gas Company | N | VENTURA | SHAFTER | 2020-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CENTURY LANDSCAPING | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Landscapers trenching for sprinklers and hit and damaged 1 inch serviceï¿½
Southern California Gas Company | N | VENTURA | SIMI VALLEY | 2020-03-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | CAL PECK LANDSCAPE | SEAL BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor digging for irrigation
Southern California Gas Company | N | VENTURA | SIMI VALLEY | 2020-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SO CAL EDISON | WESTLAKE VILLAGE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Edison was digging by a light pole and damaged the plastic service. No USA was called.
Southern California Gas Company | N | VENTURA | SIMI VALLEY | 2020-04-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | SIMI VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Line damaged by homeowner when grading for driveway.
Southern California Gas Company | N | VENTURA | SIMI VALLEY | 2020-04-29 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | LDI LANDSCAPING | VALENCIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party Contractor damaged 4 inch PLA main with excavator trying to install storm drain with no USA.
Southern California Gas Company | N | VENTURA | SIMI VALLEY | 2020-11-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | SIMI VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was installing fence and damage the standard and branch service. 2 homes evacuated. Gas service reinstated restored to the homes on the same day.ï¿½
Southern California Gas Company | N | VENTURA | SIMI VALLEY | 2020-12-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 2 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | MATSUNAGA | IRVINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Matsunaga Landscape was working for Uprite construction when they hit a 2 inch plastic service with a mini excavator. Matsunaga did not have a USA ticket.
Southern California Gas Company | N | VENTURA | SIMI VALLEY | 2020-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | IRISH CONSTRUCTION | ROSEMEAD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Irish Construction hit a marked SCG service with sharp shooter while trenching for ATandT install.
Southern California Gas Company | N | VENTURA | SIMI VALLEY | 2020-02-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | SANTA YNEZ VALLEY FENCING | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Fencing Contractor struck line when trying to remove old fence post No USA
Southern California Gas Company | N | VENTURA | SIMI VALLEY | 2020-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | SIMI VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner was digging to replace fenceï¿½post and struck service
Southern California Gas Company | N | VENTURA | SIMI VALLEY | 2020-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | SIMI VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging with backhoe for sewer install when hit service.
Southern California Gas Company | N | VENTURA | SIMI VALLEY | 2020-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | WIRELESS TECHNOLOGY SERVICES | WOODLAND HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | ATandT Contractor was tunneling from one hole to another when they struck a SCG service line with a hand tool.
Southern California Gas Company | N | VENTURA | SIMI VALLEY | 2020-12-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ALMOC ALBERCAS | SIMI VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging for swimming pool. when they hit a 0.75 inch steel service with bobcat.ï¿½Contractor did not have a USA.
Southern California Gas Company | N | VENTURA | SOMIS | 2020-05-02 | Operator excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 2 |  | H ENKELS AND MCKOY PSEP | NA |  | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | PSEP CREW HIT AN UNMARKED SERVICE STUB 2 inch
Southern California Gas Company | N | VENTURA | SOMIS | 2020-05-02 | Operator excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 2 |  | HENKELS AND MCKOY PSEP | NA |  | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit gas service with
Southern California Gas Company | N | VENTURA | SOMIS | 2020-06-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | SOMIS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | USA was current and locator failed to mark service and mains on delineated area.
Southern California Gas Company | N | VENTURA | SOMIS | 2020-05-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | SOMIS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner digging for sewer repair damaged service line with shovel. They did not call for USA.
Southern California Gas Company | N | VENTURA | SOMIS | 2020-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | SOMIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damage 1 inch plastic service while excavating for gas service that will be relocated.
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2020-01-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | SWINKS CREATIONS KOU FOX | SIMI VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | USA was current and was located and marked accurately Per Contractor they removed flags to complete work
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2020-07-16 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 60 |  | TIDWELL | VENTURA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | Tidwell Excavating Inc performing underground work for So Cal Edison damaged 2 inch service causing an outage of 60 residential units.
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2020-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | GARET WERTH MASONRY | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging for New gas line install. line was marked. Contractor digging did not have USA ticket.
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2020-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | GARY WERTH MASONRY | WOODLAND HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor was digging trench for new gas line install.
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2020-10-06 | Operator excavation damage | A service line with no excess flow valve installed | Steel | Augur | 0.75 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HENKELS MCCOY | POMONA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | HandM was using auger to install anodes. HandM did not pot hole marked SCG line and struck 2 SCGï¿½Service lines.
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2020-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | THOUSAND OAKS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor for home owner was installing a drain when they struck a 0.5 inch plastic gas service with a hand tool.
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2020-08-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | THOUSAND OAKS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Owner was digging a trench in his front yard attempting to locate his sewer line hit the 1 inch gas service line. EFV shut the gas flow and prevented excessiveï¿½gas release. Gas Company crew found black tape that the owner installed as a temporary repair onï¿½damage pipe.
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2020-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | THOUSAND OAKS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per On Call LCT unknown if there USA ticket exist. Work being performed was for irrigation.ï¿½
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2020-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HEATH CARPENTER | MURRIETA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractorï¿½HIT 0.75 ABND stub that was not mapped correctly on GIS and service history
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2020-10-10 | Third party excavation damage | A service line with no excess flow valve installed | Material not known | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | THOUSAND OAKS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Property owner digging damaged line during hand digging excavation.ï¿½
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2020-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | PINPOINT LEAK DETECTION | VENTURA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was probing for water leak when they struck gas line. No USA ticket.
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2020-08-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SUSTAINABLE SOLUTIONS | THOUSAND OAKS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was digging to repair a drain and hit gas line with shovel.
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2020-03-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | NA | THOUSAND OAKS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2020-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | BC SON CONSTRUCTION | THOUSAND OAKS | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | BC and Sons Damaged 0.5 Plastic service while digging trench for foundation.
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2020-09-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | BC SON CONSTRUCTION | THOUSAND OAKS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | BC and Sons were digging a trench for foundation when the struck out 0.5 IPS service. Service was clearly marked.
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2020-06-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DREAM HOMES | CANOGA PARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | rd party damage occurred when a contractor was excavating to install a sewer. There was no USA obtained
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2020-06-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | PEYMAN HOMAYAN | CANOGA PARK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged our line with a shovel and they had no USA ticket
Southern California Gas Company | N | VENTURA | VENTURA | 2020-02-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LOYD TONSING MASONRY | OXNARD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA was called for this job
Southern California Gas Company | N | VENTURA | VENTURA | 2020-04-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 42 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 7 |  | JBI ENGINEERING | VENTURA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damage was with in the 2 feet mark on the main.
Southern California Gas Company | N | VENTURA | VENTURA | 2020-09-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NA | VENTURA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA called for this job. HO excavating in yard to plant trees.
Southern California Gas Company | N | VENTURA | VENTURA | 2020-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | VENTURA | CA | N | Y | Yes | Excavation occurred on private property by a non-contractor. | No | Yes | No | Yes | Yes | Service damage by excavator owned and operated by home owner. Trenching being done on private property.ï¿½
Southern California Gas Company | N | VENTURA | VENTURA | 2020-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | VENTURA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavation being performed by owneroperator will valid USA. SCG service was accurately marked with paint near location of damage.ï¿½ï¿½ï¿½
Southern California Gas Company | N | VENTURA | VENTURA | 2020-05-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 7 |  | VCI CONSTRUCTION | SUN VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | USA was current. Located and marked correctly.
Southern California Gas Company | N | VENTURA | VENTURA | 2020-11-17 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 36 |  | JBI ENGINEERING | VENTURA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | SCG facility was not exposed prior to backhoe trenching operations. 2 inch main was damaged by a backhoe bucket.ï¿½
Southern California Gas Company | N | VENTURA | VENTURA | 2020-11-24 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | STANDARD INDUSTIRES | VENTURA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 2 inch Gas main was damaged by backhoe excavator during trenching and grading operations.ï¿½
Southern California Gas Company | N | VENTURA | VENTURA | 2020-10-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 42 | 40 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CANNON CONSTRUCTORS | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Trenching being performed with excavator.ï¿½
Southern California Gas Company | N | VENTURA | VENTURA | 2020-10-16 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | PSC ARB | LAKE FOREST | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 2nd party Contractor hit 0.5 plastic service with shovel. This is a DIMP Job.
Southern California Gas Company | N | VENTURA | VENTURA | 2020-05-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 42 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | VENTURA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CONTRACTOR HIT PLASTIC SERVICE
Southern California Gas Company | N | VENTURA | VENTURA | 2020-10-29 | Operator excavation damage | Riser | Steel | Hand Tools | 0.75 | 42 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | ARB | VENTURA | CA | Y | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | Company Contractor abandoning service cut the riser by mistake.
Southern California Gas Company | N | VENTURA | VENTURA | 2020-09-23 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ARB | NA |  | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor ARB working on DIMP job hit plastic service with a shovel.
Southern California Gas Company | N | VENTURA | VENTURA | 2020-12-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | CASITAS MUNICIPAL WATER DISTRICT | OAK VIEW | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Casitas Municipal Water was digging got a water line break when they struck a unmarkedï¿½ 0.5 inch Plastic gas service with Backhoe.
Southern California Gas Company | N | VENTURA | VENTURA | 2020-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JOHN MACLEAN | VENTURA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA called for this job
Southern California Gas Company | N | VENTURA | VENTURA | 2020-09-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GUARD BUILDING CORP | VALENCIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit plastic service with shovel while digging trench for gas line to be relocated.
Southern California Gas Company | N | VENTURA | VENTURA | 2020-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ASPEN HORTICULTURE | CAMARILLO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Steel service hit by farming equipment in field.
Southern California Gas Company | N | VENTURA | VENTURA | 2020-10-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 42 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | JBI ENGINEERING | VENTURA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor hit line with backhoe during excavation.ï¿½
Southern California Gas Company | N | VENTURA | VENTURA | 2020-07-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 1 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MIKE KIMBLE PLUMBING | VENTURA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA called for this job.
Southern California Gas Company | N | VENTURA | WESTLAKE VILLAGE | 2020-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | AQUA TEK POOLS INC | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 0.5 inch IPS service with shovel while digging a trench for a new drain pipe.
Southern California Gas Company | N | VENTURA | WESTLAKE VILLAGE | 2020-03-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | M C L M | SIMI VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service damaged removing driveway
Southern California Gas Company | N | VENTURA | WESTLAKE VILLAGE | 2020-03-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hand digging trench for underground electrical conduit when our facility was damaged
Southern California Gas Company | N | VENTURA | WESTLAKE VILLAGE | 2020-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  |  | NA | RHINO CONSTRUCTION | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged plastic service while digging out forms for the driveway. No USA was called.
Southern California Gas Company | Y | KERN | WASCO | 2020-05-14 | Third party excavation damage | Transmission Line in a non-HCA area | Steel | Backhoe/Trackhoe | 16 | 718 | 610 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1623114 |  | 35 |  | SOUTH VALLEY FARMS | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | South Valley Farms damaged a 16-inch steel Transmission line while operating a front-end loader over the pipeline. SoCalGas crews responded, controlled the gas by operating main line valves, and blew down the line to assess damages. There were no injuries or further damage resulting from this incident. The 16-inch main was repaired by welding two wedding bands. Investigation of the incident showed that there was no valid USA ticket for the contractor and no standby was present during the excavation activity near the Transmission line. This incident was reported to DOT and CPUC due to gas release and estimated property damage of $50,000 or more
Southern California Gas Company | Y | LOS ANGELES | WEST HOLLYWOOD | 2020-05-08 | Third party excavation damage | Main | Steel | Boring Equipment | 6 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 57045 |  | 0 |  | HP COMMUNICATION INC. | CORONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | a third-party contractor damaged a 6-inch steel gas main while boring to install conduit. SoCalGas crews responded and controlled the gas with pressure control equipment. There were no injuries or further damage resulting from this incident. The 6-inch main was repaired by welding a wedding band. Investigation of the incident showed that there was a valid USA ticket, however, the 6-inch main was not marked out by the locator. Ticket had been left open in "project" status by the locator to return on a later date to complete. The locator did not address the ticket before the due date upon his return to work from his time off 7 days . This incident was reported to DOT and CPUC due to gas release and estimated property damage of $50,000 or more
Southern California Gas Company | Y | TULARE | CUTLER | 2020-05-05 | Operator excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 175 | 170 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 104266 |  | 0 |  | SOCALGAS | VISALIA | CA | Y | Y | Yes | Yes | Yes | Yes | Yes | Yes | Yes | SoCalGas crew was working on a service abandonment job and damaged a 1-inch service tee with a backhoe. The service was fed from a 4-inch steel high pressure main. Gas was controlled by cold pinching the 4-inch high pressure steel main at two locations to the east and west of the damage. There were no injuries or further damage resulting from this incident. The 4-inch main was repaired by welding on pressure control fittings, stopping the main with pressure control equipment, cutting out the cold squeezes, and replacing a section of the pipe. Investigation of the incident showed that there was a valid USA ticket and the 4-inch main was properly marked. SoCalGas crew failed to use hand tools where required. This incident was reported to DOT and CPUC due to gas release and estimated property damage of $50,000 or more
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2020-05-01 | Operator excavation damage | Miscellaneous/Other | Polyethylene Pipe | Backhoe/Trackhoe | 0.75 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | ARIZONA PIPELINE COMPANY | CARSON CITY | NV | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | Southwest Gas contractor hit a unmapped stub with a backhoe.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2020-05-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.75 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 459 |  | 1 |  | OCCUPANT | SOUTH LAKE TAHOE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The homeowner thought the gas line was a root and tried to cut it out of the way with a wood saw.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2020-12-04 | Third party excavation damage | Riser | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | UNKNOWN | NA |  | N | N | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Vehicle vs. MSA
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2020-12-25 | Third party excavation damage | Meter | Steel | Miscellaneous/Other | 0.75 | 35 | 35 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | OCCUPANT | SOUTH LAKE TAHOE | CA | N | N | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Vehicle vs. MSA
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2020-03-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 323 |  | 1 |  | OCCUPANT | SOUTH LAKE TAHOE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was digging to install new retaining wall and hit a 1/2" PE service with a shovel.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2020-07-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 215 |  | 1 |  | BURDICK EXCAVATING CO INC | KINGS BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Burdick Construction operator failed to pothole and damaged a service line.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2020-09-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 274 |  | 1 |  | OCCUPANT | SOUTH LAKE TAHOE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner performing landscaping damaged service with a shovel.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2020-09-10 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 45 | 45 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | ARIZONA PIPELINE COMPANY | CARSON CITY | NV | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged main when a shovel and rocks fell onto the main while installing a service.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2020-05-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 520 |  | 1 |  | OCCUPANT | SOUTH LAKE TAHOE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The homeowner hit service line with a shovel.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2020-05-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 315 |  | 1 |  | OCCUPANT | SOUTH LAKE TAHOE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The homeowner hit service line with a post hole digger while installing a fence.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2020-10-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 194 |  | 1 |  | ARIZONA PIPELINE COMPANY | CARSON CITY | NV | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Company Contractor was hand digging to inspect gas line and hit 1" service with shovel.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2020-10-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.75 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1399 |  | 1 |  | TAHOE BEAR BOX | CARNELIAN BAY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service hit with a shovel while digging to install bear box garbage container.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2020-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1032 |  | 1 |  | OCCUPANT | CAMPBELL | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Tenant digging on behalf of property owner to repair sewer line damaged service.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2020-05-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 451 |  | 1 |  | TAHOE OUTDOOR LIVING | SOUTH LAKE TAHOE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit service line while digging for an electrical conduit.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2020-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 0.75 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | UNKNOWN | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Discovered previous damage to wrap from an installed meter shed caused cossosion damage to service.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2020-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 587 |  | 0 |  | ARIZONA PIPELINE COMPANY | CARSON CITY | NV | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service with shovel.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2020-06-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 127 |  | 2 |  | ARIZONA PIPELINE COMPANY | CARSON CITY | NV | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit service with shovel, while potholing where there were excessive tree roots around pipe.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2020-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 274 |  | 1 |  | OCCUPANT | SOUTH LAKE TAHOE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hit service line with shovel while trying to cut roots.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2020-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 700 |  | 0 |  | TAHOE BEAR BOX | CARNELIAN BAY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas line with a shovel while digging to install bear box garbage container.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2020-07-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 199 |  | 1 |  | OCCUPANT | SOUTH LAKE TAHOE | CA | N | Y | Yes | No | Yes | Yes | No | No | Yes | Excavator damaged service line with a backhoe.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2020-09-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 309 |  | 1 |  | ARIZONA PIPELINE COMPANY | CARSON CITY | NV | Y | Y | Yes | Yes | Yes | Yes | No | No | Yes | Contractor hit service line with shovel while working a problem locate.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2020-06-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 269 |  | 1 |  | Z''S LAWN AND LANDSCAPE | SOUTH LAKE TAHOE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscaper damaged service with pick-ax while trenching.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2020-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ARIZONA PIPELINE COMPANY | CARSON CITY | NV | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Southwest Gas contractor damaged service line with shovel while potholing.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2020-06-24 | Operator excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1449 |  | 10 |  | ARIZONA PIPELINE COMPANY | CARSON CITY | NV | Y | Y | Yes | Yes | Yes | Yes | No | Yes | No | Southwest Gas contractor damaged line while performing tapping procedure.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2020-07-27 | Operator excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 209 |  | 1 |  | ARIZONA PIPELINE COMPANY | CARSON CITY | NV | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit service with a sharp shooter during a replacement project.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2020-06-01 | Third party excavation damage | Main | Steel | Hand Tools | 2 | 60 | 60 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | SOUTH LAKE TAHOE PUBLIC UTILITIES | SO LAKE TAHOE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | South Tahoe Public Utility damaged wrap during pothole for water line install.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2020-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 403 |  | 2 |  | HAEN CONTRACTORS | SOUTH LAKE TAHOE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator damaged a stub.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2020-10-13 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1693 |  | 2 |  | GREGG EXCAVATING | STATELINE | NV | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator damaged main with backhoe while working on expired dig tickets.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2020-05-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | UNKNOWN | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Southwest Gas crews discovered previous excavation damage that had been covered up by unknown person.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2020-09-23 | Third party excavation damage | Main | Steel | Hand Tools | 2 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 343 |  | 0 |  | THOMAS HAEN COMPANY, INC | SOUTH LAKE TAHOE | CA | N | N | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator cut into steel main with grinder thinking it was a water line.
Southwest Gas Company | N | EL DORADO | TAHOMA | 2020-10-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | UNKNOWN | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Previous damage discovered, stake was driven through 1 inch PE service by unknown party.
Southwest Gas Company | N | EL DORADO | TAHOMA | 2020-07-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2739 |  | 2 |  | OCCUPANT | HOMEWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavator hit pipeline with mini excavator.
Southwest Gas Company | N | EL DORADO | TAHOMA | 2020-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 394 |  | 1 |  | OCCUPANT | TAHOMA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged service with a posthole digger.
Southwest Gas Company | N | NEVADA | TRUCKEE | 2020-05-29 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 60 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 1479 |  | 0 |  | MEYERES EARTHWORKS | ANDERSON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator damaged main, no release of gas.
Southwest Gas Company | N | NEVADA | TRUCKEE | 2020-09-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1117 |  | 1 |  | GRATEFUL GARDENS | TRUCKEE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | Yes | Contractor hit PE service with mini excavator while digging gas line for a fire pit.
Southwest Gas Company | N | NEVADA | TRUCKEE | 2020-10-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 815 |  | 1 |  | B & T CONSTRUCTION | SPARKS | NV | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas line with excavator.
Southwest Gas Company | N | NEVADA | TRUCKEE | 2020-12-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | UNKNOWN | NA |  | N | N | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Previous damage discovered on odor call, unknown damaging party.
Southwest Gas Company | N | NEVADA | TRUCKEE | 2020-09-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | UNKNOWN | NA |  | N | N | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged pipe/sleeving with skid steer.
Southwest Gas Company | N | NEVADA | TRUCKEE | 2020-12-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 886 |  | 1 |  | GEERS EXCAVATING INC | SAN JOSE | CA | N | N | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit gas line with excavator.
Southwest Gas Company | N | NEVADA | TRUCKEE | 2020-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 771 |  | 1 |  | HIGGINBOTHAM CONSTRUCTION | TRUCKEE | CA | N | Y | Yes | Yes | No | No | No | Yes | Yes | Contractor damaged gas line with mini excavator.
Southwest Gas Company | N | NEVADA | TRUCKEE | 2020-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 623 |  | 1 |  | TUI ENTERPRISE | TRUCKEE | CA | N | Y | Yes | Yes | Yes | No | No | Yes | Yes | The contractor hit service with a mini-excavator while digging to upgrade an electrical conduit.
Southwest Gas Company | N | NEVADA | TRUCKEE | 2020-09-17 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 60 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | ARIZONA PIPELINE COMPANY | CARSON CITY | NV | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged main with shovel.
Southwest Gas Company | N | NEVADA | TRUCKEE | 2020-07-30 | Third party excavation damage | Main | Polyethylene Pipe | Trencher | 2 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1047 |  | 0 |  | RUPPERT INC | TAHOE CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit main with an excavator.
Southwest Gas Company | N | PLACER | CARNELIAN BAY | 2020-09-17 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 60 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | LAKESIDE PAVING | TAHOE CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Lakeside Paving damaged steel service with backhoe while replacing stormdrain. No release of gas.
Southwest Gas Company | N | PLACER | KINGS BEACH | 2020-08-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 404 |  | 1 |  | LAZZARESCHI CONSTRUCTION | KINGS BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavator severed gas service with equipment.
Southwest Gas Company | N | PLACER | KINGS BEACH | 2020-10-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1081 |  | 0 |  | OCCUPANT | KINGS BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | Yes | Excavator damaged a 1/2 inch line with hand tools.
Southwest Gas Company | N | PLACER | KINGS BEACH | 2020-08-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 60 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 404 |  | 1 |  | OCCUPANT | KINGS BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was digging trench for water when gas line was damaged.
Southwest Gas Company | N | PLACER | KINGS BEACH | 2020-10-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 275 |  | 0 |  | F W CARSON COMPANY | INCLINE VILLAGE | NV | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Pipe was scratched and scrapped by mini excavator
Southwest Gas Company | N | PLACER | KINGS BEACH | 2020-08-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 543 |  | 2 |  | TAPCO CONSTRUCTION INC. | KINGS BEACH | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Pipeline was hit with mini excavator.
Southwest Gas Company | N | PLACER | KINGS BEACH | 2020-05-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 553 |  | 3 |  | LAZZARESCHI CONSTRUCTION | KINGS BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | Excavator damaged service with mini Excavator
Southwest Gas Company | N | PLACER | KINGS BEACH | 2020-08-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 403 |  | 1 |  | OLIVER PHILLIPS | CARNELIAN BAY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit a PE line with shovel.
Southwest Gas Company | N | PLACER | TAHOE CITY | 2020-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 834 |  | 1 |  | ARTEMIOS LANDSCAPINGS | TAHOE CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | Yes | Landscaper struck gas service with excavator.
Southwest Gas Company | N | PLACER | TAHOE CITY | 2020-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 799 |  | 1 |  | VINCIGUERRA CONSTRUCTION | JACKSON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was digging for water company and hit service with an excavator.
Southwest Gas Company | N | PLACER | TAHOE CITY | 2020-06-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 216 |  | 1 |  | GUSTAVO DIAZ EXCAVATING | VERDI | NV | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavator drove a piece of rebar through the pipe.
Southwest Gas Company | N | SAN BERNARDINO | ADELANTO | 2020-08-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 549 |  | 1 |  | VARGAS GARDENING SERVICES | HESPERIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas service while hand digging.
Southwest Gas Company | N | SAN BERNARDINO | ADELANTO | 2020-04-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1597 |  | 0 |  | ESHAWA CONSTRUCTION INC | CORONA | CA | N | Y | No | No | No | No | No | No | No | Contractor damaged gas service with hand tools.
Southwest Gas Company | N | SAN BERNARDINO | APPLE VALLEY | 2020-05-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 578 |  | 2 |  | STRAIGHT UP CONSTRUCTION | HESPERIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas service while excavating.
Southwest Gas Company | N | SAN BERNARDINO | APPLE VALLEY | 2020-05-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 534 |  | 2 |  | OCCUPANT | SAN CLEMENTE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Homeowner damaged gas service while excavating.
Southwest Gas Company | N | SAN BERNARDINO | APPLE VALLEY | 2020-03-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 466 |  | 0 |  | OCCUPANT | APPLE VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged gas service while hand digging.
Southwest Gas Company | N | SAN BERNARDINO | APPLE VALLEY | 2020-07-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 439 |  | 1 |  | GARY SWANK LANDSCAPING | VICTORVILLE | CA | N | Y | No | No | Yes | No | No | No | No | Contractor damaged gas service while trenching.
Southwest Gas Company | N | SAN BERNARDINO | APPLE VALLEY | 2020-10-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 398 |  | 4 |  | KELLEY''S UNDERGROUND CONSTRUCTION | APPLE VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas service while potholing.
Southwest Gas Company | N | SAN BERNARDINO | APPLE VALLEY | 2020-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 703 |  | 2 |  | KELLEY''S UNDERGROUND CONSTRUCTION | APPLE VALLEY | CA | N | Y | Yes | Yes | No | No | No | Yes | Yes | Contractor damaged unmarked gas service while excavating.
Southwest Gas Company | N | SAN BERNARDINO | APPLE VALLEY | 2020-06-25 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 40 | 40 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 497 |  | 0 |  | LIBERTY UTILITIES (UTILITY) | APPLE VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged PE main with a hand tool while backfilling, no release of gas.
Southwest Gas Company | N | SAN BERNARDINO | APPLE VALLEY | 2020-12-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 349 |  | 1 |  | OCCUPANT | APPLE VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged gas service with hand tools.
Southwest Gas Company | N | SAN BERNARDINO | APPLE VALLEY | 2020-05-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 694 |  | 1 |  | HIGH DESERT UNDERGROUND | HESPERIA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged gas service while trenching.
Southwest Gas Company | N | SAN BERNARDINO | APPLE VALLEY | 2020-11-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1092 |  | 1 |  | OCCUPANT | APPLE VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant damaged gas service while excavating.
Southwest Gas Company | N | SAN BERNARDINO | APPLE VALLEY | 2020-05-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 762 |  | 2 |  | HIGH DESERT UNDERGROUND | HESPERIA | CA | N | Y | Yes | Yes | No | No | No | Yes | Yes | Contractor damaged gas service due to incomplete locate.
Southwest Gas Company | N | SAN BERNARDINO | APPLE VALLEY | 2020-09-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 552 |  | 1 |  | MINEO BROTHERS SEPTIC | HESPERIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas service while probing.
Southwest Gas Company | N | SAN BERNARDINO | APPLE VALLEY | 2020-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 777 |  | 1 |  | TORRENT RESOURCES | PHOENIX | AZ | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas service while potholing.
Southwest Gas Company | N | SAN BERNARDINO | APPLE VALLEY | 2020-11-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1146 |  | 2 |  | OCCUPANT | APPLE VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant damaged gas service with a stake.
Southwest Gas Company | N | SAN BERNARDINO | APPLE VALLEY | 2020-02-11 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 543 |  | 2 |  | ARIZONA PIPELINE COMPANY | HESPERIA | CA | Y | Y | Yes | Yes | Yes | No | No | Yes | Yes | Contractor damaged gas service while excavating.
Southwest Gas Company | N | SAN BERNARDINO | APPLE VALLEY | 2020-11-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 562 |  | 1 |  | CISNEROS BROTHERS PLUMBING INC | HESPERIA | CA | N | Y | Yes | No | Yes | Yes | No | No | No | Contractor damaged gas service while potholing.
Southwest Gas Company | N | SAN BERNARDINO | APPLE VALLEY | 2020-08-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1023 |  | 1 |  | OCCUPANT | APPLE VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupants'' son damaged gas service while augering.
Southwest Gas Company | N | SAN BERNARDINO | APPLE VALLEY | 2020-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 276 |  | 1 |  | ROLAND ENGINEERING | APPLE VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas service while probing for service line.
Southwest Gas Company | N | SAN BERNARDINO | APPLE VALLEY | 2020-05-11 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 37 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 2401 |  | 0 |  | HITT PLUMBING | APPLE VALLEY | CA | N | Y | No | No | No | No | No | No | No | Contractor damaged gas main with backhoe.
Southwest Gas Company | N | SAN BERNARDINO | BARSTOW | 2020-05-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2315 |  | 2 |  | OCCUPANT | BARSTOW | CA | N | Y | Yes | No | Yes | Yes | No | No | No | Homeowner damaged gas service while excavating.
Southwest Gas Company | N | SAN BERNARDINO | BARSTOW | 2020-05-11 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1241 |  | 16 |  | FM SERVICES | MORENO VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas service while hand digging.
Southwest Gas Company | N | SAN BERNARDINO | BARSTOW | 2020-10-21 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1996 |  | 24 |  | HENKELS & MCCOY | POMONA | CA | Y | Y | Yes | Yes | Yes | Yes | No | No | No | Contractor damaged gas service with trackhoe while digging within tolerance zone. Damage was 18" from marks.
Southwest Gas Company | N | SAN BERNARDINO | BARSTOW | 2020-09-17 | Operator excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 120 | 115 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3638 |  | 0 |  | ARIZONA PIPELINE COMPANY | HESPERIA | CA | Y | Y | Yes | Yes | No | Yes | Yes | Yes | Yes | Undocumented stub damaged while trenching.
Southwest Gas Company | N | SAN BERNARDINO | BARSTOW | 2020-08-12 | Operator excavation damage | Main | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 231 |  | 3 |  | ARIZONA PIPELINE COMPANY | HESPERIA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas main while hand digging.
Southwest Gas Company | N | SAN BERNARDINO | BARSTOW | 2020-07-22 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 515 |  | 1 |  | ARIZONA PIPELINE COMPANY | HESPERIA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas service while potholing.
Southwest Gas Company | N | SAN BERNARDINO | BARSTOW | 2020-11-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 632 |  | 2 |  | OCCUPANT | BARSTOW | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged gas service while excavating.
Southwest Gas Company | N | SAN BERNARDINO | BARSTOW | 2020-02-18 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3064 |  | 0 |  | CHRISTENSEN BROTHERS | APPLE VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged an undocumented stub.
Southwest Gas Company | N | SAN BERNARDINO | BARSTOW | 2020-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2014 |  | 1 |  | OCCUPANT | FULLERTON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged gas service while excavating.
Southwest Gas Company | N | SAN BERNARDINO | BARSTOW | 2020-10-07 | Third party excavation damage | Main | Steel | Grader/Scraper | 4 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3635 |  | 0 |  | UNDERGROUND CONSTRUCTION | BENICIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas main while grading.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR CITY | 2020-10-07 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 510 |  | 2 |  | BIG BEAR CITY COMMUNITY SERVICES DISTRICT | BIG BEAR CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | No | No | Contractor damaged gas service due to mismark.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR CITY | 2020-01-30 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 675 |  | 0 |  | PACIFIC MH CONSTRUCTION, INC | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | No | No | Contractor relocated SWG riser causing leaks.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR CITY | 2020-08-21 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1483 |  | 0 |  | MODERN LANDSCAPE CONSTRUCTION INC | OCEANSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas main with backhoe.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR CITY | 2020-11-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 220 |  | 1 |  | MC CORD''S TRACTOR SERVICE | BIG BEAR CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas line while excavating.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR LAKE | 2020-08-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 681 |  | 1 |  | PAVEMENT RECYCLING SYSTEMS, INC | JURUPA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas service while performing road work.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR LAKE | 2020-06-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 589 |  | 1 |  | APPLE VALLEY CONSTRUCTION | APPLE VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas service with backhoe.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR LAKE | 2020-06-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | HERRERA CONSTRUCTION | BIG BEAR LAKE | CA | N | Y | Yes | Yes | Yes | Yes | No | No | No | Contractor damaged gas service with mechanical clay spade.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR LAKE | 2020-05-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 289 |  | 2 |  | BORDEN EXCAVATING INC. | CALIMESA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas service while excavating.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR LAKE | 2020-09-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 539 |  | 1 |  | KENNY SEAMAN CONSTRUCTION | BIG BEAR LAKE | CA | N | Y | Yes | Yes | No | No | No | Yes | Yes | Contractor damaged gas service while trenching.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR LAKE | 2020-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 709 |  | 1 |  | BORDEN EXCAVATING INC. | CALIMESA | CA | N | Y | Yes | Yes | Yes | Yes | No | No | No | Contractor damaged gas service while excavating.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR LAKE | 2020-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 211 |  | 1 |  | BORDEN EXCAVATING INC. | CALIMESA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas service with hand tools.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR LAKE | 2020-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 318 |  | 1 |  | BORDEN EXCAVATING INC. | CALIMESA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas service while excavating.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR LAKE | 2020-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1194 |  | 2 |  | ELITE PAVING | PERRIS | CA | N | Y | No | No | No | No | No | Yes | No | Gas service damaged with stake.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR LAKE | 2020-09-15 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 663 |  | 1 |  | MILE HIGH EQUIPMENT | BIG BEAR LAKE | CA | N | Y | No | No | No | No | No | No | No | Contractor damaged gas service while digging.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR LAKE | 2020-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 678 |  | 1 |  | SCOTTY''S PLUMBING | BIG BEAR | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas service with hand tools.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR LAKE | 2020-07-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 282 |  | 1 |  | GORDON EQUIPMENT | BIG BEAR CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas service while excavating.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR LAKE | 2020-06-26 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 986 |  | 0 |  | APPLE VALLEY CONSTRUCTION | APPLE VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | No | Yes | Contractor damaged gas main with backhoe.
Southwest Gas Company | N | SAN BERNARDINO | FAWNSKIN | 2020-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 513 |  | 2 |  | ES BUILDERS INC. | BIG BEAR CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas service with backhoe.
Southwest Gas Company | N | SAN BERNARDINO | FAWNSKIN | 2020-08-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 366 |  | 1 |  | BORDEN EXCAVATING INC. | CALIMESA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas service while excavating.
Southwest Gas Company | N | SAN BERNARDINO | FAWNSKIN | 2020-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 221 |  | 1 |  | BORDEN EXCAVATING INC. | CALIMESA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas service while excavating.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2020-04-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 320 |  | 1 |  | OCCUPANT | HESPERIA | CA | N | Y | No | No | No | No | No | No | No | Homeowner damaged gas service while augering.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2020-12-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 203 |  | 1 |  | OCCUPANT | HESPERIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Occupant damaged gas service with mini excavator.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2020-04-16 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 2 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1636 |  | 16 |  | FODDRILL CONSTRUCTION CORPORATION | CHINO | CA | N | Y | Yes | No | No | No | No | No | No | Contractor damaged gas main while augering.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2020-03-18 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2057 |  | 0 |  | ATKINSON MASONRY | LANCASTER | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas main while excavating.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2020-12-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 558 |  | 2 |  | ALL AMERICAN FENCE | HESPERIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas service while augering.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2020-06-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 424 |  | 2 |  | OCCUPANT | HESPERIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaaged gas service while hand digging.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2020-09-10 | Operator excavation damage | Riser | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 583 |  | 6 |  | ARIZONA PIPELINE COMPANY | HESPERIA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas riser with backhoe bucket while digging.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2020-08-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 329 |  | 1 |  | DE LEON ELECTRIC | HESPERIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas service while hand digging.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2020-11-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 569 |  | 1 |  | SORRENTO HOMES | ADELANTO | CA | N | Y | Yes | Yes | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas service that was not marked by APL after gas line installation on customer provided trench.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2020-07-20 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1069 |  | 1 |  | ARIZONA PIPELINE COMPANY | HESPERIA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas service with hand tools.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2020-08-24 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 744 |  | 2 |  | ARIZONA PIPELINE COMPANY | HESPERIA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas service while hand digging.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2020-08-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 474 |  | 1 |  | OCCUPANT | HESPERIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant damaged gas service while trenching.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2020-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 491 |  | 1 |  | ALL AMERICAN FENCE CO. | HESPERIA | CA | N | Y | Yes | Yes | Yes | Yes | No | No | No | Contrator damaged gas service with hand tools.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2020-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 233 |  | 1 |  | ROTO ROOTER | VICTORVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas service while hand digging.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2020-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 612 |  | 1 |  | FM POOL CONSTRUCTION INC. | JURUPA VALLEY | CA | N | Y | No | No | No | No | No | No | No | Contractor damaged gas service while trenching.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2020-03-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 704 |  | 2 |  | OCCUPANT | HESPERIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged gas service while hand digging.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2020-10-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1461 |  | 1 |  | WU CONSTRUCTION | ROSEMEAD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas service while excavating.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2020-07-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 751 |  | 2 |  | OCCUPANT | HESPERIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant damaged gas service while hand digging.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2020-10-27 | Operator excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4328 |  | 32 |  | SOUTHWEST GAS CORPORATION | LAS VEGAS | NV | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged gas main while excavating.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2020-07-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 40 | 38 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 492 |  | 0 |  | OCCUPANT | HESPERIA | CA | N | Y | Yes | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Handyman for property manager at park damaged gas service while grading.
Southwest Gas Company | N | SAN BERNARDINO | LUCERNE VALLEY | 2020-01-17 | Operator excavation damage | A service line with no excess flow valve installed | PVC Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 664 |  | 2 |  | ARIZONA PIPELINE COMPANY | HESPERIA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas service while hand digging.
Southwest Gas Company | N | SAN BERNARDINO | LUCERNE VALLEY | 2020-05-15 | Operator excavation damage | A service line with no excess flow valve installed | PVC Pipe | Hand Tools | 0.5 | 40 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 197 |  | 1 |  | ARIZONA PIPELINE COMPANY | HESPERIA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas service while hand digging.
Southwest Gas Company | N | SAN BERNARDINO | LUCERNE VALLEY | 2020-09-18 | Operator excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1860 |  | 0 |  | ARIZONA PIPELINE COMPANY | HESPERIA | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | Undocumented stub damaged while trenching.
Southwest Gas Company | N | SAN BERNARDINO | NEEDLES | 2020-02-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | DON BROWN CONSTRUCTION | NEEDLES | CA | N | N | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 1"PE 8100 with excavator while digging trench.
Southwest Gas Company | N | SAN BERNARDINO | OAK HILLS | 2020-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 608 |  | 1 |  | HP COMMUNICATIONS INC. | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas service with hand tools.
Southwest Gas Company | N | SAN BERNARDINO | OAK HILLS | 2020-06-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 475 |  | 1 |  | OCCUPANT | OAK HILLS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged gas service while excavating.
Southwest Gas Company | N | SAN BERNARDINO | OAK HILLS | 2020-04-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 53 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1083 |  | 1 |  | OCCUPANT | OAK HILLS | CA | N | Y | No | No | No | No | No | No | No | Homeowner damaged gas service while excavating.
Southwest Gas Company | N | SAN BERNARDINO | SUGARLOAF | 2020-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 218 |  | 1 |  | DEAN FARRAR CONSTRUCTION | BIG BEAR CITY | CA | N | Y | No | No | No | No | No | No | No | Contractor damaged gas service while hand digging.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2020-09-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 40 | 38 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 284 |  | 0 |  | UNKNOWN | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service line was damaged by unknown party, no release of gas.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2020-10-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 994 |  | 0 |  | GOTHIC LANDSCAPE | RIVERSIDE | CA | N | Y | Yes | Yes | No | No | No | No | No | Contractor damaged gas service while excavating.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2020-08-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 337 |  | 0 |  | TRILOGY PLUMBING, INC | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas service while excavating.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2020-09-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 382 |  | 1 |  | RICHARD LOPEZ CONSTRUCTION | CORONA | CA | N | Y | Yes | Yes | No | Yes | No | No | No | Contractor damaged gas service wile excavating.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2020-03-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 594 |  | 0 |  | PACIFIC WEST UNDERGROUND | YUCAIPA | CA | N | Y | No | No | No | No | No | No | Yes | Contractor damaged gas service while excavating.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2020-04-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 352 |  | 2 |  | GRAY CONSTRUCTION | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas service while grading.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2020-10-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 488 |  | 1 |  | OCCUPANT | HESPERIA | CA | N | Y | Yes | Yes | Yes | Yes | No | No | No | Occupant damaged gas service while digging.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2020-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 542 |  | 2 |  | OCCUPANT | VICTORVILLE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant damaged gas service while excavating.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2020-04-29 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 356 |  | 4 |  | ARIZONA PIPELINE COMPANY | HESPERIA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas service while potholing.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2020-11-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 532 |  | 1 |  | OCCUPANT | VICTORVILLE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant damaged gas service with backhoe.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2020-05-07 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 373 |  | 2 |  | ARIZONA PIPELINE COMPANY | HESPERIA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas service while removing asphalt with backhoe.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2020-04-20 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1773 |  | 3 |  | ARIZONA PIPELINE COMPANY | HESPERIA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas service while excavating.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2020-07-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 40 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 473 |  | 1 |  | OCCUPANT | VICTORVILLE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant damaged gas service while excavating.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2020-01-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 325 |  | 0 |  | DAVID OLLIS LANDSCAPE DEVELOPMENT | REDLANDS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas service while excavating.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2020-01-15 | Operator excavation damage | A service line with no excess flow valve installed | PVC Pipe | Vacuum Equipment with Agreement | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 765 |  | 3 |  | ARIZONA PIPELINE COMPANY | HESPERIA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas service during PVC replacement.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2020-09-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 846 |  | 14 |  | CAL PACIFIC | RIVERSIDE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged gas service while excavating.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2020-05-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 440 |  | 2 |  | OCCUPANT | VICTORVILLE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged gas service with hand tools.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2020-04-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 552 |  | 2 |  | OCCUPANT | VICTORVILLE | CA | N | N | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner cut through gas line with hand tools while repairing water line.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2020-03-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 895 |  | 2 |  | FENCE GUYS | HESPERIA | CA | N | Y | Yes | Yes | Yes | Yes | No | No | No | Contractor damaged gas service while had digging.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2020-04-17 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 2 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3589 |  | 0 |  | ABC LIOVIN DRILLING | SIGNAL HILL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas main while drilling.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2020-10-08 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 507 |  | 0 |  | ONARCH, INC. | RIALTO | CA | N | Y | No | No | Yes | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas main while excavating without a USA ticket. Existing marks in work area found and were accurate.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2020-10-09 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 40 | 36 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 1351 |  | 0 |  | JMI GENERAL ENGINEERING CONTRACTOR | RIVERSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas main while trenching, trench wall collapsed causing damage to pipe.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2020-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 489 |  | 0 |  | PACIFIC UTILITY INSTALLATION INC. | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas service with backhoe.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2020-03-26 | Operator excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1663 |  | 0 |  | ARIZONA PIPELINE COMPANY | HESPERIA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas main while excavating.