## Sheet1
Utility Name | Notified of Incident | County Name | Incident City | Incident Date | Cause of Incident | Facility Damage | Material Damaged | Damaged Caused By | Pipe Diameter | MAOP of Operator | Operating Pressure | Gas Leak | Operator Caused Fire | Non-Operator Caused Fire | Natural Gas Explosion | Injured Employees | Non-Employees Injured | Non-Employees Injured NA | Employee Fatalities | Non-Employee Fatalities | Non-Employee Fatalities NA | Cost Damage | Cost Damage NA | Customers Effected | Customers Effected NA | Damage Party Name | Damage Party City | Damage Party State | Damage Party Work Operator | Damage Done To SUOF | Underground Service Alert | Valid USA Ticket | Property Mark Facility | Properly Timely Mark Facility | Standby Provided | Delineations Found | Struck Within Delineations | Summary
Alpine Gas | N | CALAVERAS | VALLEY SPRINGS | 2023-05-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.75 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 250 |  | 1 |  | ANDRIA FIERRO | VALLEY SPRINGS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner and friend struck gas line with jack hammer. No USA ticket, Cal Fire on scene. Blowing Gas (Grade 1) times 84 minutes til gas stopped.
Alpine Gas | N | CALAVERAS | VALLEY SPRINGS | 2023-05-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.75 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 300 |  | 2 |  | MICHAEL LANE | VALLEY SPRINGS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeownerwhile digging without a USA ticket nicked the gas line Grade 3 leak no blowing gas.
Alpine Gas | N | CALAVERAS | VALLEY SPRINGS | 2023-05-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.75 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 191 |  | 1 |  | UNDERGROUND ELECTRIC CONSTRC. COMPANY | NA |  | N | Y | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Contractor while digging with shovel, struck gas line. The service line was inside the marks provided by the Utility. Operator inattention. Blowing gas times 12 minutes.
Alpine Gas | N | CALAVERAS | VALLEY SPRINGS | 2023-10-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.75 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 283 |  | 1 |  | HOMEOWNER''S DAUGHTER AND TENANT, KRISTINA HAMILTON | VALLEY SPRINGS | CA | N | Y | No | No | No | No | No | No | No | The Tenant (& daughter of the Homeowner) while attempting to repair a broken water line, struck gas line with a shovel. No USA ticket prior to this work being performed was requested.
Alpine Gas | N | CALAVERAS | VALLEY SPRINGS | 2023-04-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.75 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 191 |  | 1 |  | UNDERGROUND ELECTRIC CONSTRC. COMPANY | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | Contractor while digging with excavator, struck gas line. The service line was outside the marks provided by the Utility. Utility mismarked but Contractor did not call for remark when line not found inside marks. Blowing gas times 15 minutes.
Alpine Gas | N | CALAVERAS | VALLEY SPRINGS | 2023-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.75 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 231 |  | 1 |  | ACME CONSTRUCTION | NA | CA | N | Y | No | No | No | No | No | No | No | The Contractor while digging with EXCAVATOR, struck gas line. No USA ticket prior to this work being performed was requested.
Alpine Gas | N | CALAVERAS | VALLEY SPRINGS | 2023-07-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.75 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 198 |  | 1 |  | PLATINUM DIRT WORK | MODESTO | CA | N | Y | No | No | No | No | No | No | No | The Contractor while digging with EXCAVATOR, struck gas line. No USA ticket prior to this work being performed was requested.
Pacific Gas and Electric | N | ALAMEDA | ALAMEDA | 2023-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2761 |  | 1 |  | CARROLL CONSTRUCTION | ALAMEDA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | ALAMEDA | 2023-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 15 | 12 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2373 |  | 1 |  | B R CONCRETE | ALAMEDA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | ALAMEDA | 2023-07-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1805 |  | 1 |  | AVALON SERVICES INC | FREMONT | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | ALAMEDA | 2023-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1918 |  | 1 |  | HOMEOWNER | ALAMEDA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | ALAMEDA | 2023-05-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 15 | 12 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4947 |  | 2 |  | DENNY''S BOBCAT SERVICE | HAYWARD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | ALAMEDA | 2023-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 15 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1990 |  | 1 |  | KATOA CONCRETE | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | ALBANY | 2023-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 15 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2745 |  | 1 |  | HOMEOWNER | ALBANY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2023-06-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 15 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1332 |  | 2 |  | HOMEOWNER | BERKELEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2023-10-27 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 15 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6435 |  | 1 |  | WEST VALLEY CONSTRUCTION | CAMPBELL | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2023-02-07 | Operator excavation damage | Main | Polyethylene Pipe | Hand Tools | 1.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5000 |  | 1 |  | MILLER PIPELINE | INDIANAPOLIS | IN | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2023-03-23 | Operator excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6000 |  | 8 |  | MILLER PIPELINE | INDIANAPOLIS | IN | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2023-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 15 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2870 |  | 1 |  | HOMEOWNER | BERKELEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2023-01-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1000 |  | 1 |  | TRACY ROOTER | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2023-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 15 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1149 |  | 1 |  | WEST VALLEY CONSTRUCTION | HAYWARD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKED INACCURATELY
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2023-05-01 | Operator excavation damage | Main | Polyethylene Pipe | Hand Tools | 1.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 16542 |  | 2 |  | MILLER PIPELINE | ALAMEDA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2023-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CV CONSTRUCTION INC | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2023-11-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2596 |  | 1 |  | ALBERT NAHMAN PLUMBING | BERKELEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2023-09-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2181 |  | 1 |  | HECTOR RUIZ COMPANY | RICHMOND | CA | N | Y | No | No | No | No | No | No | No | No USA Ticket
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2023-07-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 15 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | PALO ALTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2023-10-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7121 |  | 2 |  | HOMEOWNER | BERKELEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2023-09-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2035 |  | 2 |  | UNLICENSED CONTRACTOR | BERKELEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2023-11-14 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Trencher | 3 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1294 |  | 1 |  | HOMEOWNER | BERKELEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2023-02-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 4 |  | HOMEOWNER | BERKELEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2023-02-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5000 |  | 3 |  | SUREWAY PAVING | PLEASANTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2023-09-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NA | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2023-01-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 16245 |  | 1 |  | SOSETO ENGINEERING INC. | LIVERMORE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | OTHER
Pacific Gas and Electric | N | ALAMEDA | BERKELEY | 2023-06-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 15 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 13025 |  | 1 |  | ANDES CONSTRUCTION | OAKLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | ALAMEDA | CASTRO VALLEY | 2023-09-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1245 |  | 1 |  | HOMEOWNER | CASTRO VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | CASTRO VALLEY | 2023-07-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 109 |  | 1 |  | PLUMBING GUYS | HAYWARD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | CASTRO VALLEY | 2023-10-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1686 |  | 1 |  | VILAND PLUMBING | LIVERMORE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | CASTRO VALLEY | 2023-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2710 |  | 1 |  | HOMEOWNER | CASTRO VALLEY | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | CASTRO VALLEY | 2023-01-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1000 |  | 2 |  | ELITE ROOTER | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | DUBLIN | 2023-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3709 |  | 5 |  | NA | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | DUBLIN | 2023-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | ELECTRIC NETWORK | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment
Pacific Gas and Electric | N | ALAMEDA | DUBLIN | 2023-04-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2187 |  | 2 |  | K.J.WOODS CONSTRUCTION | SOUTH SAN FRANCISCO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | ALAMEDA | DUBLIN | 2023-02-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1625 |  | 0 |  | R&B EQUIPMENT INC | HAYWARD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | DUBLIN | 2023-10-10 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 6 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 33994 |  | 0 |  | MARKETSHARE INC | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | FREMONT | 2023-08-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3401 |  | 6 |  | JPA LANDSCAPE & CONSTRUCTION | LIVERMORE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | ALAMEDA | FREMONT | 2023-05-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2172 |  | 0 |  | JANCO INDUSTRIES INC. | TRACY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | FREMONT | 2023-06-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2442 |  | 1 |  | ALLSITE CORPORATION | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | FREMONT | 2023-07-21 | Third party excavation damage | Not Available | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | UNLICENSED CONTRACTOR | EAST PALO ALTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | HAYWARD | 2023-06-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 8711 |  | 1 |  | ROTO ROOTER | HAYWARD | CA | N | Y | Yes | Yes | No | No | No | No | No | FACULITY WAS NOT LOCATED OR MARKETED
Pacific Gas and Electric | N | ALAMEDA | HAYWARD | 2023-12-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1609 |  | 1 |  | VANGAURD CONSTRUCTION | BURLINGAME | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | HAYWARD | 2023-07-13 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3187 |  | 0 |  | WESTLAND CONTRACTOR | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | HAYWARD | 2023-02-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1000 |  | 1 |  | CENTINELA GENERAL ENGINEERING | SALINAS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | HAYWARD | 2023-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1625 |  | 1 |  | STREAMLINE PLUMBING | SAN LEANDRO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | ALAMEDA | HAYWARD | 2023-05-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | DIABLO GENERAL ENGINEERING | CONCORD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | HAYWARD | 2023-09-20 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 17490 |  | 6 |  | CITY OF HAYWARD PUBLIC WORKS | HAYWARD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | HAYWARD | 2023-04-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 1.25 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 246 |  | 1 |  | ORFIL CONSTRUCTION | HAYWARD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | LIVERMORE | 2023-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 0.75 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 22634 |  | 1 |  | SEFNCO | LIVERMORE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | LIVERMORE | 2023-02-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1936 |  | 1 |  | CALIFORNIA FENCES | LIVERMORE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | LIVERMORE | 2023-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1536 |  | 1 |  | REUBEN BORG FENCE | LIVERMORE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | LIVERMORE | 2023-01-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 400 |  | 1 |  | INNOVATION CONSTRUCTION | SAN LEANDRO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | LIVERMORE | 2023-11-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1549 |  | 1 |  | A MUNOZ LANDSCAPE CONSTRUCTION | MORGAN HILL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | LIVERMORE | 2023-08-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 933 |  | 1 |  | BAY SIDE FENCING | BRENTWOOD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | NEWARK | 2023-05-24 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | NEWARK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2023-02-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1337 |  | 0 |  | NA | NA | CA | N | Y | No | No | No | No | No | No | No | OTHER
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2023-05-11 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5557 |  | 5 |  | VNH BUILDERS | BURLINGAME | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2023-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2308 |  | 1 |  | LEVITCH ASSOCIATES | BERKELEY | CA | N | Y | No | No | No | No | No | No | No | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2023-06-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4336 |  | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2023-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 50 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2609 |  | 2 |  | LAZAR LANDSCAPE DESIGN & CONSTRUCTION INC | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2023-11-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1.25 | 0.5 | 0.38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5245 |  | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2023-04-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 90 |  | 1 |  | HOMEOWNER | PIEDMONT | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2023-10-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2422 |  | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2023-02-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 704 |  | 2 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2023-09-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1797 |  | 1 |  | UNLICENSED CONTRACTOR | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2023-03-03 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4772 |  | 2 |  | D LINE | OAKLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2023-01-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 106 |  | 1 |  | CREST LANDSCAPE | PLEASANTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2023-09-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 0.5 | 0.38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2171 |  | 1 |  | ROSAS BROTHERS CONSTRUCTION | OAKLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2023-05-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 0.43 | 0.33 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7491 |  | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2023-10-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1756 |  | 1 |  | THE PLUMBING MINISTRY | SAN LEANDRO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2023-10-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1906 |  | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2023-06-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 950 |  | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2023-10-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1953 |  | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2023-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3532 |  | 2 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2023-11-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2107 |  | 1 |  | THE PLUMBING MINISTRY | SAN LEANDRO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2023-02-23 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 6 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 100 |  | 1 |  | ALBERT NAHMAN PLUMBING | BERKELEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2023-02-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 54 | 48 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3724 |  | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2023-03-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 144 |  | 0 |  | D LINE | OAKLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | OTHER
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2023-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2713 |  | 1 |  | FCO-S CONCRETE CONSTRUCTION | VALLEJO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2023-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1183 |  | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2023-01-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 500 |  | 1 |  | KNOX SEWER AND BACKHOE | OAKLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | OTHER
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2023-07-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 0.5 | 0.38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1561 |  | 2 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2023-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2179 |  | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2023-08-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3288 |  | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2023-08-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3081 |  | 2 |  | ASSOCIATED CONTRACTORS PLUMBING | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2023-09-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1892 |  | 1 |  | SAN FRANCISCO REMODEL | RICHMOND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2023-06-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 950 |  | 1 |  | TYRONE PERCY LANDSCAPING INC | OAKLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKED INACCURATELY
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2023-06-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 0.43 | 0.33 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2520 |  | 1 |  | CALISCO LANDSCAPE LLC | PITTSBURG | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2023-09-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 0.5 | 0.38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 913 |  | 1 |  | UNLICENSED CONTRACTOR | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2023-12-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1414.86 |  | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2023-08-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4084 |  | 1 |  | HOMEOWNER | OAKLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2023-06-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2668 |  | 0 |  | C S DEVELOPMENT AND CONSTRUCTION | DANVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | OAKLAND | 2023-10-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 3 |  | MILLER PIPELINE | ALAMEDA | CA | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | Facility Embedded in Concrete
Pacific Gas and Electric | N | ALAMEDA | PIEDMONT | 2023-01-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 159 |  | 1 |  | STREAM LINE PLUMBING | CASTRO VALLEY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | No | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | ALAMEDA | PIEDMONT | 2023-03-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1000 |  | 1 |  | JOEY MOTA LANDSCAPING | PIEDMONT | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | PIEDMONT | 2023-09-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1995 |  | 1 |  | DEVEN GENZO COMPANY | LAFAYETTE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | ALAMEDA | PIEDMONT | 2023-11-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1936 |  | 1 |  | PACIFIC HOME SERVICES INC. | PLEASANTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | PIEDMONT | 2023-05-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | DOT CONSTRUCTION | BURLINGAME | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | PLEASANTON | 2023-08-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 977 |  | 1 |  | HOMEOWNER | PLEASANTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | PLEASANTON | 2023-11-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2418 |  | 1 |  | CALIFORNIA FENCES | LIVERMORE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Dig with Care
Pacific Gas and Electric | N | ALAMEDA | PLEASANTON | 2023-07-22 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 2 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9444 |  | 6 |  | HOMEOWNER | PLEASANTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | PLEASANTON | 2023-09-16 | Third party excavation damage | Not Available | Polyethylene Pipe | Hand Tools | 1 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2908 |  | 1 |  | UNLICENSED CONTRACTOR | PLEASANTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | PLEASANTON | 2023-12-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1842 |  | 1 |  | HOMEOWNER | PLEASANTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | SAN LEANDRO | 2023-10-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1276 |  | 1 |  | MONARCH PLUMBING | HAYWARD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | ALAMEDA | SAN LEANDRO | 2023-05-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | SAN LEANDRO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | SAN LEANDRO | 2023-12-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1334 |  | 1 |  | RAD COMMUNICATION | LIVERMORE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | ALAMEDA | SAN LEANDRO | 2023-11-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1951 |  | 2 |  | ANDES CONSTRUCTION INC. | OAKLAND | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | SAN LEANDRO | 2023-05-05 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2141 |  | 1 |  | ANDYS CONSTRUCTION | SAN RAFAEL | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | ALAMEDA | SAN LEANDRO | 2023-01-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1591 |  | 1 |  | WESTLAND CONTRACTORS INC. | OAKLAND | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | LOCATING WIRE MISSING OR BROKEN
Pacific Gas and Electric | N | ALAMEDA | SAN LEANDRO | 2023-11-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2933 |  | 1 |  | PUZZLE CONSTRUCTION | SAN LEANDRO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | ALAMEDA | SAN LEANDRO | 2023-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1538 |  | 1 |  | JML ENGINEERING CONSTRUCTION | RICHMOND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | ALAMEDA | SAN LEANDRO | 2023-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1166 |  | 2 |  | GALY ENTERPRISE | LIVERMORE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | SAN LEANDRO | 2023-10-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1269 |  | 1 |  | PG&E | OAKLAND | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | UNION CITY | 2023-09-11 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5943 |  | 2 |  | D21 TECHS | MONUMENT | CO | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | ALAMEDA | UNION CITY | 2023-08-23 | Third party excavation damage | Main | Polyethylene Pipe | Not Available | 2 | 58 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2914 |  | 2 |  | CENTURY ROOF AND SOLAR | HAYWARD | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | AMADOR | IONE | 2023-06-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2353 |  | 1 |  | A. CASTILLO & SONS PLUMBING COMPANY | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | AMADOR | JACKSON | 2023-11-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3884 |  | 2 |  | WESTCON CONTRUCTION CORPORATION | NEWCASTLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | AMADOR | JACKSON | 2023-05-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1906 |  | 1 |  | HOMEOWNER | JACKSON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | BUTTE | BIGGS | 2023-06-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 618 |  | 0 |  | HOMEOWNER | BIGGS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | BUTTE | CHICO | 2023-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 15000 |  | 1 |  | HOMEOWNER | CHICO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | BUTTE | CHICO | 2023-10-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2279 |  | 1 |  | R & R HORN CONTRACTORS INC | CHICO | CA | N | Y | No | No | No | No | No | No | No | FAILED TO MAINTAIN FIELD MARKS
Pacific Gas and Electric | N | BUTTE | CHICO | 2023-04-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 0.43 | 0.33 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | CHICO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | BUTTE | CHICO | 2023-02-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 53 |  | 0 |  | ROCK CREEK CONSTRUCTION | CHICO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | BUTTE | CHICO | 2023-10-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2073 |  | 4 |  | HOMEOWNER | CHICO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | BUTTE | CHICO | 2023-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3997 |  | 3 |  | M & M HANSEN COMMUNICATIONS | PALO CEDRO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | CHICO | 2023-11-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Trencher | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1556 |  | 0 |  | HOMEOWNER | CHICO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | BUTTE | CHICO | 2023-03-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2444 |  | 3 |  | HOMEOWNER | CHICO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | BUTTE | CHICO | 2023-12-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 875 |  | 0 |  | HOMEOWNER | CHICO | CA | N | Y | No | No | No | No | No | No | No | USA NOTIFICATION ERROR
Pacific Gas and Electric | N | BUTTE | CHICO | 2023-09-06 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 1.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3500 |  | 0 |  | WALBERG INC | CORNING | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | BUTTE | OROVILLE | 2023-10-17 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5746 |  | 1 |  | DUKE SHERWOOD CONTRACTING, INC | OROVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | OROVILLE | 2023-11-29 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 20205 |  | 35 |  | GINNO CONSTRUCTION | CHICO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | BUTTE | PARADISE | 2023-08-25 | Third party excavation damage | Main | Polyethylene Pipe | Not Available | 2 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 337 |  | 0 |  | VETERAN PIPELINE CONSTRUCTION | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | PARADISE | 2023-10-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1868 |  | 1 |  | PG&E GAS | OAKLAND | CA | Y | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | PARADISE | 2023-06-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 614 |  | 0 |  | DUDLEY''S EXCAVATING INC | GERBER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | PARADISE | 2023-05-01 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | DUDLEY''S EXCAVATING INC | GERBER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | PARADISE | 2023-07-31 | Third party excavation damage | Main | Steel | Not Available | 2 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3396 |  | 0 |  | C&C UTILITY | CHICO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | PARADISE | 2023-11-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2942 |  | 1 |  | HOMEOWNER | PARADISE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | BUTTE | PARADISE | 2023-02-15 | Operator excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 106 |  | 0 |  | TEICHERT CONSTRUCTION | PLEASANTON | CA | Y | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | BUTTE | PARADISE | 2023-08-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1504 |  | 1 |  | HOMEOWNER | PARADISE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | BUTTE | PARADISE | 2023-04-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | RCI GENERAL ENGINEERING | OROVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | BUTTE | PARADISE | 2023-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1.25 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | MJ SHELTON GENERAL ENGINEERING | CHICO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | PARADISE | 2023-11-22 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | KW EMERSON | SAN ANDREAS | CA | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | FACILITY COULD NOT BE FOUND OR LOCATED
Pacific Gas and Electric | N | BUTTE | PARADISE | 2023-03-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1613 |  | 0 |  | DUDLEY''S EXCAVATING INC | GERBER | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | BUTTE | PARADISE | 2023-05-10 | Operator excavation damage | Main | Polyethylene Pipe | Vacuum Equipment with Agreement | 1.25 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3390 |  | 0 |  | C&C UTILITY | CHICO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | PARADISE | 2023-08-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1600 |  | 1 |  | HOMEOWNER | PARADISE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | BUTTE | PARADISE | 2023-08-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2551 |  | 0 |  | C & C UTILITY | CHICO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INCORRECT INFORMATION OR MARKS
Pacific Gas and Electric | N | BUTTE | PARADISE | 2023-11-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1263 |  | 1 |  | C & C UTILITY | CHICO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | BUTTE | PARADISE | 2023-08-24 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 0.75 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2564 |  | 0 |  | BADGER DAYLIGHTING | REDDING | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CALAVERAS | SAN ANDREAS | 2023-07-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2337 |  | 1 |  | MOZINGO CONSTRUCTION | OAKDALE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CALAVERAS | VALLEY SPRINGS | 2023-05-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1387 |  | 0 |  | SIERRA EXCAVATION | YUBA CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | COLUSA | MAXWELL | 2023-12-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 418 |  | 1 |  | HOMEOWNER | MAXWELL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | COLUSA | WILLIAMS | 2023-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2136 |  | 2 |  | HOMEOWNER | WILLIAMS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ALAMO | 2023-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1562 |  | 1 |  | HOMEOWNER | ALAMO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ALAMO | 2023-01-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 133 |  | 1 |  | SPECTRUM POOL & LANDSCAPE | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ALAMO | 2023-08-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 826 |  | 1 |  | J. R. ROSSI CONSTRUCTION | ALAMO | CA | N | Y | No | No | No | No | No | No | No | Failed to Dig with Care
Pacific Gas and Electric | N | CONTRA COSTA | ALAMO | 2023-03-06 | Third party excavation damage | Main | Polyethylene Pipe | Probing Device | 1.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 53 |  | 0 |  | WILLIAMS UNDERGROUND CONSTRUCTION | OAKLAND | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | ANTIOCH | 2023-01-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 53 |  | 1 |  | STEWART PLUMBING AIR CONDITIONING | PITTSBURG | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | ANTIOCH | 2023-10-09 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5400 |  | 1 |  | MILLER PIPELINE | ALAMEDA | CA | Y | Y | No | No | No | No | No | No | No | FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | CONTRA COSTA | ANTIOCH | 2023-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1145 |  | 1 |  | VETERAN POWER INFRASTRUCTURE | BENICIA | CA | Y | Y | No | No | No | No | No | No | No | Failed to Dig with Care
Pacific Gas and Electric | N | CONTRA COSTA | ANTIOCH | 2023-05-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | CLP CONSTRUCTION | BRENTWOOD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ANTIOCH | 2023-10-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | ANTIOCH | CA | N | Y | No | No | No | No | No | No | No | No USA Ticket
Pacific Gas and Electric | N | CONTRA COSTA | ANTIOCH | 2023-11-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2784 |  | 0 |  | AL FRESCO LANDSCAPING | HOLLISTER | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ANTIOCH | 2023-09-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1886 |  | 1 |  | HOMEOWNER | ANTIOCH | CA | N | Y | No | No | No | No | No | No | No | No USA Ticket
Pacific Gas and Electric | N | CONTRA COSTA | ANTIOCH | 2023-07-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | ANTIOCH | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | BAY POINT | 2023-02-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 264 |  | 1 |  | HOMEOWNER | BAY POINT | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | CONTRA COSTA | BAY POINT | 2023-08-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2179 |  | 1 |  | HOMEOWNER | BAY POINT | CA | N | Y | No | No | No | No | No | No | No | Failed to Dig with Care
Pacific Gas and Electric | N | CONTRA COSTA | BAY POINT | 2023-12-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3375 |  | 3 |  | HOMEOWNER | BAY POINT | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | BRENTWOOD | 2023-02-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 170 |  | 1 |  | WILLIAMS SANITARY SERVICE | BRENTWOOD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | BRENTWOOD | 2023-05-03 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4649 |  | 1 |  | SHENANDOAH EXCAVATING | FIDDLETOWN | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | CONTRA COSTA | BRENTWOOD | 2023-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3074 |  | 1 |  | HOMEOWNER | BRENTWOOD | CA | N | Y | No | No | No | No | No | No | No | Failed to Dig with Care
Pacific Gas and Electric | N | CONTRA COSTA | BRENTWOOD | 2023-01-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 372 |  | 1 |  | VPI | CONCORD | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | CLAYTON | 2023-03-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1413 |  | 1 |  | HOMEOWNER | CLAYTON | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | CONCORD | 2023-10-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1471 |  | 1 |  | POWER SOURCE | PITTSBURG | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | CONCORD | 2023-12-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3224 |  | 1 |  | HOMEOWNER | CONCORD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | CONTRA COSTA | CONCORD | 2023-01-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1803 |  | 0 |  | COCO COUNTY DRAIN CLEANING & PLUMBING | NEVADA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | CONTRA COSTA | CONCORD | 2023-10-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2510 |  | 1 |  | ORTAK CONSTRUCTION INC. | ORANGEVALE | CA | N | Y | No | No | No | No | No | No | No | FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | CONTRA COSTA | CONCORD | 2023-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | WAYNE E SWISHER CONCRETE | ANTIOCH | CA | N | Y | No | No | No | No | No | No | No | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment
Pacific Gas and Electric | N | CONTRA COSTA | CONCORD | 2023-06-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Directional Drilling | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2220 |  | 1 |  | CQ COMMUNICATION CORP | PACIFICA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | CONCORD | 2023-11-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1756 |  | 1 |  | RAY?S ELECTRIC | OAKLAND | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | CONTRA COSTA | CONCORD | 2023-09-07 | Third party excavation damage | Main | Polyethylene Pipe | Not Available | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4644 |  | 0 |  | CROUSE GENERAL ENGINEERING | CONCORD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment
Pacific Gas and Electric | N | CONTRA COSTA | CROCKETT | 2023-08-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 27.5 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2129 |  | 1 |  | HOMEOWNER | CROCKETT | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | CROCKETT | 2023-11-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 27.5 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1749 |  | 1 |  | BILL''S UNDERGROUND | EL SOBRANTE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | DANVILLE | 2023-09-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1843 |  | 1 |  | MI CASA CONSTRUCTION | BAY POINT | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Failed to Dig with Care
Pacific Gas and Electric | N | CONTRA COSTA | DANVILLE | 2023-11-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2273 |  | 1 |  | GM PIOMBO CONSTRUCTION | DANVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | DANVILLE | 2023-06-01 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 290 |  | 0 |  | MILZ DEVELOPMENT & CONSTRUCTION | DANVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | DANVILLE | 2023-06-26 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 443 |  | 1 |  | BARNARD PIPELINE INC | WOODLAND | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKED INACCURATELY
Pacific Gas and Electric | N | CONTRA COSTA | DANVILLE | 2023-05-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 103 |  | 1 |  | HOMEOWNER | DANVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | DANVILLE | 2023-11-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3149 |  | 1 |  | LANDSCAPE EXPERTS | DANVILLE | CA | N | Y | No | No | No | No | No | No | No | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | CONTRA COSTA | DANVILLE | 2023-01-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1000 |  | 1 |  | HOLDER PINTO ACTION HAULING | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | DIABLO | 2023-02-21 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 1.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 50708 |  | 1 |  | PLUMBING TECHNOLOGY INC | LIVERMORE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | DISCOVERY BAY | 2023-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3125 |  | 1 |  | HOMEOWNER | DISCOVERY BAY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | EL CERRITO | 2023-04-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 255 |  | 1 |  | BUZZ LANDSCAPE | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | EL CERRITO | 2023-12-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3224 |  | 1 |  | FOUNDATION REPAIR OF CA | LIVERMORE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Incorrect Facility Records / Maps
Pacific Gas and Electric | N | CONTRA COSTA | EL CERRITO | 2023-10-24 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 1.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 14067 |  | 3 |  | EDT TEC | LIVERMORE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | EL SOBRANTE | 2023-10-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1703 |  | 0 |  | SOUZA | RODEO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | EL SOBRANTE | 2023-05-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2006 |  | 4 |  | BILL''S UNDERGROUND | EL SOBRANTE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | CONTRA COSTA | EL SOBRANTE | 2023-05-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1666 |  | 1 |  | EM CONSTRUCTION & CONCRETE INC. | BENECIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | HERCULES | 2023-02-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5000 |  | 0 |  | R&B EQUIPMENT INC | HAYWARD | CA | N | Y | No | No | No | No | No | No | No | OTHER
Pacific Gas and Electric | N | CONTRA COSTA | KENSINGTON | 2023-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3689 |  | 1 |  | HOMEOWNER | NEWPORT BEACH | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | KENSINGTON | 2023-09-19 | Third party excavation damage | Main | Polyethylene Pipe | Not Available | 3 | 15 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7933 |  | 12 |  | EBMUD | OAKLAND | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | CONTRA COSTA | KENSINGTON | 2023-09-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 15 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1961 |  | 1 |  | EBMUD | OAKLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Other Error
Pacific Gas and Electric | N | CONTRA COSTA | LAFAYETTE | 2023-06-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1142 |  | 1 |  | AIRTIGHT CONSTRUCTION | CONCORD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | LAFAYETTE | 2023-02-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2229 |  | 1 |  | HOMEOWNER | LAFAYETTE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | LAFAYETTE | 2023-06-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 643 |  | 1 |  | TRI VALLEY FENCE WORKS | LIVERMORE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | LAFAYETTE | 2023-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7977 |  | 2 |  | EL SOBRANTE SEWER REPAIR | EL SOBRANTE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Incorrect Information or Marks
Pacific Gas and Electric | N | CONTRA COSTA | LAFAYETTE | 2023-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6173 |  | 3 |  | GHILOTTI CONSTRUCTION | LIVERMORE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | CONTRA COSTA | LAFAYETTE | 2023-10-31 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1652 |  | 1 |  | PACIFIC CREST CONSTRUCTION | WALNUT CREEK | CA | N | Y | Yes | No | No | No | No | Yes | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | LAFAYETTE | 2023-03-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 106 |  | 1 |  | ENCHANTING PLANTING | ORINDA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | LAFAYETTE | 2023-07-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4972 |  | 1 |  | HOMEOWNER | LAFAYETTE | CA | N | Y | No | No | No | No | No | No | No | No USA Ticket
Pacific Gas and Electric | N | CONTRA COSTA | LAFAYETTE | 2023-01-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1200 |  | 1 |  | SANTIAGO SAMAYOA LANDSCAPING | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | MARTINEZ | 2023-06-20 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1071 |  | 1 |  | DEVANEY ENGINEERING INC | SAN FRANCISCO | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | MARTINEZ | 2023-02-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 212 |  | 1 |  | HOMEOWNER | MARTINEZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | MARTINEZ | 2023-04-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3 |  | 1 |  | HOMEOWNER | MARTINEZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | MARTINEZ | 2023-07-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 50 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DEVENGENZO LANDSCAPING & GEN ENGINEERING | WALNUT CREEK | CA | N | Y | No | No | No | No | No | No | No | Failed to Dig with Care
Pacific Gas and Electric | N | CONTRA COSTA | MORAGA | 2023-11-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2110 |  | 1 |  | J&M LANDSCAPE | NAPA | CA | N | Y | Yes | Yes | No | No | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | CONTRA COSTA | MORAGA | 2023-01-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 159 |  | 1 |  | HOMEOWNER | MORAGA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | MORAGA | 2023-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4437 |  | 1 |  | HOMEOWNER | MORAGA | CA | N | Y | No | No | No | No | No | No | No | DETERIORATED OR FRAGILE FACILITY
Pacific Gas and Electric | N | CONTRA COSTA | MORAGA | 2023-05-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | ECHO PLUMBING | CONCORD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | OAKLEY | 2023-05-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1284 |  | 1 |  | DIABLO WATER DISTRICT | OAKLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | OAKLEY | 2023-11-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3660 |  | 1 |  | HOMEOWNER | OAKLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | OAKLEY | 2023-07-17 | Third party excavation damage | Main | Polyethylene Pipe | Not Available | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | VALUE PLUMBING CO. | OAKLEY | CA | N | Y | No | No | No | No | No | No | No | No USA Ticket
Pacific Gas and Electric | N | CONTRA COSTA | ORINDA | 2023-10-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1723 |  | 1 |  | HOMEOWNER | ORINDA | CA | N | Y | No | No | No | No | No | No | No | Failed to Dig with Care
Pacific Gas and Electric | N | CONTRA COSTA | ORINDA | 2023-07-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | LARWOOD CONSTRUCTION | ORINDA | CA | N | Y | No | No | No | No | No | No | No | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment
Pacific Gas and Electric | N | CONTRA COSTA | ORINDA | 2023-06-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1311 |  | 1 |  | COWAN & THOMPSON | MARTINEZ | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | ORINDA | 2023-09-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1011 |  | 1 |  | UNLICENSED CONTRACTOR | ORINDA | CA | N | Y | No | No | No | No | No | No | No | No USA Ticket
Pacific Gas and Electric | N | CONTRA COSTA | ORINDA | 2023-08-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1256 |  | 1 |  | HOMEOWNER | ORINDA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ORINDA | 2023-09-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 933 |  | 0 |  | CR CONSTRUCTION | EL SOBRANTE | CA | N | Y | No | No | No | No | No | No | No | No USA Ticket
Pacific Gas and Electric | N | CONTRA COSTA | ORINDA | 2023-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1156 |  | 1 |  | HOMEOWNER | ORINDA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ORINDA | 2023-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3213 |  | 1 |  | COWAN & THOMPSON CONSTRUCTION INC | MARTINEZ | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | ORINDA | 2023-02-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NEW BAY CONSTRUCTION | CONCORD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ORINDA | 2023-05-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | CREATIVE ENVIRONMENTS | ALAMO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | ORINDA | 2023-10-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2848 |  | 0 |  | VICTOR GARCIA LANDSCAPING | DANVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | PITTSBURG | 2023-06-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1715 |  | 0 |  | ENVIROMENTAL LANSCAPES | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | PITTSBURG | 2023-06-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 17 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4741 |  | 1 |  | A #1 DEVELOPERS | WALNUT CREEK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | PITTSBURG | 2023-07-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 42 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 193 |  | 2 |  | HOMEOWNER | PITTSBURG | CA | N | Y | No | No | No | No | No | No | No | No USA Ticket
Pacific Gas and Electric | N | CONTRA COSTA | PITTSBURG | 2023-09-13 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 42 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 8451 |  | 4 |  | HENNESSEYS FENCING | BRENTWOOD | CA | N | Y | No | No | No | No | No | No | No | No USA Ticket
Pacific Gas and Electric | N | CONTRA COSTA | PITTSBURG | 2023-04-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | PITTSBURG | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | PITTSBURG | 2023-05-23 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 42 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6058 |  | 3 |  | CITY BORE COMMUNICATION INC | SAN BERNADINO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | CONTRA COSTA | PLEASANT HILL | 2023-08-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2988 |  | 1 |  | HOMEOWNER | DALY CITY | CA | N | Y | No | No | No | No | No | No | No | No USA Ticket
Pacific Gas and Electric | N | CONTRA COSTA | PLEASANT HILL | 2023-11-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1435 |  | 2 |  | BAY AREA UNDERPINNING | FAIRFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | CONTRA COSTA | PLEASANT HILL | 2023-01-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2400 |  | 0 |  | LRL BUILDERS | WALNUT CREEK | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | PLEASANT HILL | 2023-02-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1000 |  | 1 |  | DISTINCTIVE DESIGNS | SAN RAMON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | PLEASANT HILL | 2023-06-29 | Third party excavation damage | Main | Steel | Hand Tools | 4 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 28335 |  | 3 |  | NA | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | PLEASANT HILL | 2023-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 488 |  | 1 |  | RC CONSTRUCTION | MERCED | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2023-10-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2472 |  | 1 |  | HOMEOWNER | RICHMOND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2023-11-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 8452 |  | 1 |  | EBMUD | OAKLAND | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2023-10-30 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9875 |  | 7 |  | EBMUD | OAKLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Incorrect Information or Marks
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2023-05-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 103 |  | 0 |  | HOMEOWNER | RICHMOND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2023-04-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 1.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | RICHMOND COUNTRY CLUB | RICHMOND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2023-09-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1370 |  | 1 |  | KINGDOM CONCRETE CONTRACTOR | RICHMOND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2023-08-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2927 |  | 1 |  | HOMEOWNER | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2023-11-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 0.5 | 0.38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2295 |  | 1 |  | SCBA TREE CONSULTING | RICHMOND | CA | N | Y | Yes | Yes | No | Yes | Yes | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2023-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2226 |  | 1 |  | MONTES CONSTRUCTION | PINOLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | RICHMOND | 2023-03-17 | Third party excavation damage | Main | Steel | Hand Tools | 2 | 12 | 9 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5000 |  | 0 |  | NA | NA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT INFORMATION OR MARKS
Pacific Gas and Electric | N | CONTRA COSTA | RODEO | 2023-11-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5652 |  | 1 |  | HOMEOWNER | RODEO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | SAN PABLO | 2023-03-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1162 |  | 1 |  | HOMEOWNER | SAN PABLO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | SAN RAMON | 2023-04-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | SAN RAMON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | SAN RAMON | 2023-02-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 300 |  | 1 |  | DEVLUX CONSTRUCTION | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | SAN RAMON | 2023-10-24 | Third party excavation damage | Main | Polyethylene Pipe | Trencher | 2 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9053 |  | 0 |  | DESILVA GATES CONSTRUCTION | DUBLIN | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2023-06-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1004 |  | 0 |  | ABERLE CONCRETE EXCAVATING & GRADING INC | FREMONT | CA | N | Y | Yes | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2023-01-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 4 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4595 |  | 0 |  | EBMUD | OAKLAND | CA | N | Y | Yes | No | Yes | Yes | Yes | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2023-05-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 54 | Y | N | Y | N | 0 | 0 |  | 0 | 0 |  | 1427 |  | 1 |  | NA | NA | CA | N | Y | No | No | No | No | No | No | No | House fire damaged service
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2023-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4316 |  | 1 |  | EDT TEC | LIVERMORE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2023-11-30 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1314 |  | 1 |  | ZECENA | WALNUT CREEK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2023-12-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1393 |  | 2 |  | HOMEOWNER | WALNUT CREEK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2023-11-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1476 |  | 1 |  | HINKSON CONSTRUCTION INC. | CONCORD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2023-05-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | ACCESS SOIL DRILLING | SAN MATEO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2023-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1000 |  | 1 |  | PRECISION ENGINEERING | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2023-12-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1481 |  | 1 |  | DIGITEK ENGINEERING | COLORADO | CO | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2023-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1431 |  | 1 |  | ADVANCED TRENCHLESS | MARTINEZ | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2023-11-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1609 |  | 1 |  | JC GUZMAN CONTRUTION | SAN RAMON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | CONTRA COSTA | WALNUT CREEK | 2023-03-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1430 |  | 0 |  | ADVANCED TRENCHES | MARTINEZ | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | EL DORADO | EL DORADO HILLS | 2023-08-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1759 |  | 1 |  | TAK COMMUNICATIONS INC | SACRAMENTO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | EL DORADO | EL DORADO HILLS | 2023-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4166 |  | 0 |  | AMERISCAPE LANDSCAPE | RANCHO CORDOVA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | EL DORADO | EL DORADO HILLS | 2023-04-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | GRADE TEK | EL DORADO HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | BIOLA | 2023-11-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 1 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1394 |  | 1 |  | HOMEOWNER | BIOLA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | CLOVIS | 2023-09-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1431 |  | 4 |  | MAYRIDGE CONSTRUCTIONI IF | MERCED | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | CLOVIS | 2023-05-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | CLOVIS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | CLOVIS | 2023-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1399 |  | 1 |  | HOMEOWNER | CLOVIS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | CLOVIS | 2023-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | CLOVIS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | CLOVIS | 2023-07-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | TOP CHOICE FENCING | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FIREBAUGH | 2023-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 45 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1500 |  | 0 |  | VALLEY FENCE CO | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FIREBAUGH | 2023-10-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3586 |  | 1 |  | HOMEOWNER | FIREBAUGH | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FIREBAUGH | 2023-11-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1770 |  | 0 |  | HOMEOWNER | FIREBAUGH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FOWLER | 2023-11-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 0.5 | 0.38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1440 |  | 1 |  | HOMEOWNER | FOWLER | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2023-09-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1470 |  | 1 |  | AVISON CONSTRUCTION INC | MADERA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2023-04-03 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 103 |  | 0 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2023-05-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2023-08-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3041 |  | 1 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2023-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | JVH SEPTIC AND WELL | CLOVIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2023-02-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 258 |  | 2 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2023-08-01 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9472 |  | 1 |  | SDT EQUIPMENT | BAKERSFIELD | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | INCORRECT INFORMATION OR MARKS
Pacific Gas and Electric | N | FRESNO | FRESNO | 2023-07-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2057 |  | 1 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2023-10-08 | Third party excavation damage | A service line with no excess flow valve installed | Copper | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2023-08-29 | Third party excavation damage | Main | Polyethylene Pipe | Trencher | 1.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3702 |  | 6 |  | AMPLE SUN ENERGY | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2023-10-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3961 |  | 1 |  | HOMEOWNER | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2023-11-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2000 |  | 1 |  | KERB APPEAL FENCEWORKS | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2023-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 4 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | VALVERDE CONSTRUCTION | FRESNO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2023-01-31 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2218 |  | 1 |  | WEST VALLEY CONSTRUCTION | FRESNO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | OTHER
Pacific Gas and Electric | N | FRESNO | FRESNO | 2023-03-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1891 |  | 1 |  | WEST VALLEY CONSTRUCTION | FRESNO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT INFORMATION OR MARKS
Pacific Gas and Electric | N | FRESNO | FRESNO | 2023-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7457 |  | 1 |  | HO COMM INC | FRESNO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | FRESNO | FRESNO | 2023-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2023-03-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 53 |  | 1 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2023-05-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2023-04-15 | Third party excavation damage | Riser | Steel | Farm Equipment | 1.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | NA | NA | CA | N | Y | No | No | No | No | No | No | No | Riser cut with mower daming party left the scene
Pacific Gas and Electric | N | FRESNO | FRESNO | 2023-11-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1920 |  | 1 |  | CLOVIS PLUMBING SERVICES | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2023-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | BIG JOE''S PLUMBING | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2023-08-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1461 |  | 1 |  | OTT GENERAL CONTRACTORS- JAMES OVALLE | CLOVIS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2023-04-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 8 |  | 7 |  | INNOVATION LANDSCAPE | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2023-02-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1000 |  | 1 |  | FORD RANCHES | CLOVIS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2023-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1687 |  | 1 |  | LOZANO FENCING | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2023-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | GOOD GUY ELECTRIC AND SOLAR | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2023-09-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2546 |  | 1 |  | SOLAR MAINTENANCE PROS | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2023-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | ON POINT GRADING AND PAVING | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2023-11-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 642 |  | 2 |  | VULCAN | FRESNO | CA | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2023-08-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1596 |  | 2 |  | TRUE SOLAR & ELECTRIC INC. | KERMAN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | FRESNO | 2023-11-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2092 |  | 1 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2023-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3574 |  | 0 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2023-10-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1689 |  | 1 |  | HOMEOWNER | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2023-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1338 |  | 1 |  | KC CONSTRUCTION | CLOVIS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | FRESNO | 2023-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 1.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | HOMEOWNER | SAN FRANSICO | CA | N | Y | No | No | No | No | No | No | No | OTHER
Pacific Gas and Electric | N | FRESNO | FRESNO | 2023-08-31 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1912 |  | 0 |  | NA | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | HURON | 2023-04-12 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 60 |  | 0 |  | TODD COMPANIES | VISALIA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | FRESNO | KERMAN | 2023-01-25 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 53 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1000 |  | 4 |  | SNAKE AND LATERALS | CLOVIS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | KERMAN | 2023-11-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 53 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4100 |  | 1 |  | HOMEOWNER | KERMAN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | KERMAN | 2023-03-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 53 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1887 |  | 1 |  | HERITAGE BONITE | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | KERMAN | 2023-04-12 | Third party excavation damage | Main | Polyethylene Pipe | Grader/Scraper | 2 | 53 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | JIM CRAWFORD CONSTRUTION | CLOVIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | KERMAN | 2023-09-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 53 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1049 |  | 0 |  | JOSEPH CROWN CONSTRUCTION | FRESNO | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | MENDOTA | 2023-10-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1455 |  | 1 |  | AVISON | MADERA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | MENDOTA | 2023-06-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1441 |  | 0 |  | HOMEOWNER | MENDOTA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | SANGER | 2023-05-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 214 |  | 1 |  | COONES FENCES | SANGER | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | SANGER | 2023-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 328 |  | 2 |  | EFI ENGINEERING | TUSTIN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | SANGER | 2023-04-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | EFI ENGINEERING | TUSTIN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | FRESNO | SELMA | 2023-11-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2451 |  | 1 |  | HOMEOWNER | SELMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | FRESNO | SELMA | 2023-10-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5056 |  | 1 |  | HOMEOWNER | SELMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | GLENN | HAMILTON CITY | 2023-03-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2500 |  | 0 |  | MEDINAS CONSTRUCTION | WATSONVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | GLENN | WILLOWS | 2023-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2511 |  | 0 |  | HOMEOWNER | WILLOWS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | HUMBOLDT | EUREKA | 2023-01-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 241 |  | 1 |  | HOMEOWNER | EUREKA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | HUMBOLDT | EUREKA | 2023-08-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Vacuum Equipment with Agreement | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1117 |  | 1 |  | HUMBOLDT COMMUNITY SERVICES DISTRICT | EUREKA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | HUMBOLDT | EUREKA | 2023-05-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | MR. ROOTER PLUMBING | EUREKA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | HUMBOLDT | EUREKA | 2023-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2915 |  | 1 |  | SPENCER ELECTRIC | EUREKA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | HUMBOLDT | FORTUNA | 2023-09-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2432 |  | 1 |  | HOOVES & CO INC | MCKINLEYVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | HUMBOLDT | FORTUNA | 2023-07-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DCI BUILDERS | FERNDALE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | HUMBOLDT | FORTUNA | 2023-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | FORTUNA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | HUMBOLDT | HYDESVILLE | 2023-05-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 437 |  | 0 |  | HOMEOWNER | HYDESVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | HUMBOLDT | MCKINLEYVILLE | 2023-06-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 568 |  | 1 |  | HOMEOWNER | MCKINLEYVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | HUMBOLDT | MCKINLEYVILLE | 2023-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | MCKINLEYVILLE | CA | N | Y | No | No | No | No | No | No | No | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | HUMBOLDT | MCKINLEYVILLE | 2023-06-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2380 |  | 2 |  | MILLERS FARM | MCKINLEYVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | HUMBOLDT | MCKINLEYVILLE | 2023-08-18 | Third party excavation damage | Not Available | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1966 |  | 0 |  | HOMEOWNER | MCKINLEYVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | HUMBOLDT | RIO DELL | 2023-03-21 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 36 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4067 |  | 1 |  | HOMEOWNER | RIO DELL | CA | N | Y | No | No | No | No | No | No | No | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2023-12-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2009 |  | 1 |  | POOL TEK | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2023-07-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1597 |  | 1 |  | OILDALE MUTUAL WATER COMPANY | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2023-08-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1644 |  | 1 |  | TOMMY?S LIGHTING | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2023-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | TOWER COMMUNICATIONS | POMONA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2023-07-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1382 |  | 1 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2023-12-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1066 |  | 2 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2023-07-31 | Third party excavation damage | Main | Polyethylene Pipe | Not Available | 2 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 52555 |  | 4 |  | WEST VALLEY CONSTRUCTION | BAKERSFIELD | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | LOCATING WIRE MISSING OR BROKEN
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2023-04-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | GRIFFITH COMPANY | LOS ANGELES | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2023-07-03 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1.25 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 6 |  | UNDERGROUND EXPRESS CO | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2023-11-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1946 |  | 1 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2023-04-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2023-09-13 | Third party excavation damage | Main | Polyethylene Pipe | Not Available | 1.25 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2124 |  | 4 |  | WM LYLES CO | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2023-11-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1333 |  | 1 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2023-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3200 |  | 4 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2023-05-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1176 |  | 0 |  | LENTZ CONSTRUCTION | BAKERSFIELD | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2023-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1212 |  | 1 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2023-04-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2023-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1065 |  | 1 |  | LASAR UNDERGROUND CONSTRUCTION, INC | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2023-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1159 |  | 1 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2023-08-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1529 |  | 0 |  | NA | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2023-08-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 698 |  | 2 |  | HERITAGE SOLAR AND CONSTRUCTION | BAKERSFIELD | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2023-08-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1512 |  | 2 |  | HERITAGE SOLAR AND CONSTRUCTION | BAKERSFIELD | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2023-11-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2391 |  | 1 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2023-12-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1792 |  | 1 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2023-05-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | TMJ CONSTRUCTION | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2023-01-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 156 |  | 2 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | OTHER
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2023-04-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BAKERSFIELD | 2023-01-20 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 48 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | KERN DELTA WATER DISTRICT | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BEAR VALLEY SPRINGS | 2023-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 48 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3137 |  | 1 |  | HOMEOWNER | BEAR VALLEY SPRINGS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | BORON | 2023-02-16 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | HOMEOWNER | BORON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | RIDGECREST | 2023-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | EVERLEVEL CONSTRUCTION | CHINO HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | KERN | RIDGECREST | 2023-04-12 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 12 |  | 8 |  | RACE COMMUNICATIONS | TEHACHAPI | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | KERN | RIDGECREST | 2023-02-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | LINE WORKS CONSTRUCTION | LA VERN | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | OTHER
Pacific Gas and Electric | N | KERN | RIDGECREST | 2023-02-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | LINE WORKS | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | OTHER
Pacific Gas and Electric | N | KERN | RIDGECREST | 2023-03-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 811 |  | 2 |  | SENNZA CONSTRUCTION | ALPINE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | OTHER
Pacific Gas and Electric | N | KERN | RIDGECREST | 2023-04-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7 |  | 0 |  | BORING BROS CONST. | RANCHO MISSION VIEJO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | KERN | RIDGECREST | 2023-01-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 53 |  | 2 |  | RACE COMMUNICATIONS | BURLINGAME | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | KERN | RIDGECREST | 2023-01-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1752 |  | 1 |  | RP CABLE | EL CAJON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | OTHER
Pacific Gas and Electric | N | KERN | RIDGECREST | 2023-08-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10889 |  | 1 |  | INTERNATIONAL UNDERGROUND SERVICE | SAN BERNADINO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | RIDGECREST | 2023-02-18 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 68 |  | PRO PLUMBING | RIDGECREST | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | TAFT | 2023-01-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 18 | 15 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5159 |  | 0 |  | NA | NA | CA | N | Y | Yes | Yes | Yes | Yes | No | No | Yes | OTHER
Pacific Gas and Electric | N | KERN | TAFT | 2023-02-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 18 | 15 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 76 |  | 2 |  | HOMEOWNER | TAFT | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | KERN | TAFT | 2023-08-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 18 | 15 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1376 |  | 0 |  | BROWN''S CONSTRUCTION | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment
Pacific Gas and Electric | N | MADERA | CHOWCHILLA | 2023-10-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 43 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5266 |  | 1 |  | HOMEOWNER | CHOWCHILLA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MADERA | CHOWCHILLA | 2023-09-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 554 |  | 1 |  | HOMEOWNER | CHOWCILLA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MADERA | CHOWCHILLA | 2023-01-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2000 |  | 1 |  | IMPECCABLE POOLS | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATED OUTSIDE OF DELINEATION
Pacific Gas and Electric | N | MADERA | MADERA | 2023-11-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 42 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4191 |  | 1 |  | HOMEOWNER | MADERA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MADERA | MADERA | 2023-11-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2860 |  | 1 |  | HOMEOWNER | MADERA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MADERA | MADERA | 2023-05-01 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | MADERA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MADERA | MADERA | 2023-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 42 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | JFS ENTERPRISES | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MADERA | MADERA | 2023-02-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1500 |  | 0 |  | HOMEOWNER | MADERA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MADERA | MADERA | 2023-12-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 42 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2603 |  | 1 |  | GRM CONSTRUCTION | MADERA | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MADERA | MADERA | 2023-09-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1981 |  | 0 |  | DULEYS LANDSCAPING INC | PRATHER | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible
Pacific Gas and Electric | N | MADERA | MADERA | 2023-10-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1773 |  | 0 |  | COMCAST | MADERA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | BELVEDERE | 2023-11-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2121 |  | 1 |  | HOMEOWNER | TIBURON | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | MARIN | BELVEDERE | 2023-12-01 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4919 |  | 1 |  | HARDIMAN CONSTRUCTION | LARKSPUR | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Facility Embedded in Concrete
Pacific Gas and Electric | N | MARIN | BELVEDERE TIBURON | 2023-05-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3119 |  | 1 |  | HOMEOWNER | TIBURON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | CORTE MADERA | 2023-10-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1493 |  | 1 |  | MAGGIORA & GHILOTTI | SAN RAFAEL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | MARIN | CORTE MADERA | 2023-09-28 | Third party excavation damage | Not Available | Polyethylene Pipe | Not Available | 1 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1411 |  | 1 |  | HOMEOWNER | CORTE MADERA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | CORTE MADERA | 2023-12-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3780 |  | 1 |  | LOD CONSTRUCTION | RICHMOND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | FAIRFAX | 2023-01-23 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5054 |  | 1 |  | JNG PIPELINE CONSTRUCTION | HAYWARD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | MARIN | KENTFIELD | 2023-02-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | DELUXE SHOTCRETE & CONCRETE | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | KENTFIELD | 2023-11-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1386 |  | 1 |  | HOMEOWNER | KENTFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | KENTFIELD | 2023-10-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3487.47 |  | 1 |  | PRECISION ENGINEERING | SAN FRANCISCO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | MARIN | KENTFIELD | 2023-02-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5000 |  | 1 |  | WESTWARD BUILDERS INC | SAN RAFAEL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | MARIN | KENTFIELD | 2023-11-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1928 |  | 1 |  | PRECISION ENGINEERING | SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | KENTFIELD | 2023-09-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1438 |  | 1 |  | MARIN MUNICIPAL WATER DISTRICT | CORTE MADERA | CA | N | Y | Yes | Yes | Yes | Yes | No | No | Yes | Excavated outside delineated area
Pacific Gas and Electric | N | MARIN | LARKSPUR | 2023-12-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2346 |  | 1 |  | HOMEOWNER | LARKSPUR | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | LARKSPUR | 2023-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2948 |  | 1 |  | UNLICENSED CONTRACTOR | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2023-11-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5250 |  | 1 |  | HOMEOWNER | MILL VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2023-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | DUDLEY''S EXCAVATING INC | GERBER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2023-04-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7 |  | 1 |  | SFT CONSTRUCTION | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2023-10-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3205 |  | 1 |  | HOMEOWNER | MILL VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2023-06-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1600 |  | 1 |  | DE LUNA CONSTRUCTION | SAN RAFAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2023-08-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6514 |  | 2 |  | HOMEOWNER | MILL VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2023-01-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 235 |  | 1 |  | CHELSEA PACIFIC REAL ESTATE | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2023-02-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | MILL VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2023-02-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 500 |  | 1 |  | HOMEOWNER | MILL VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | MILL VALLEY | 2023-10-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Probing Device | 1 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3428 |  | 1 |  | HELIOTROPE LANDSCAPE CONSTRUCTION AND DESIGN | FAIRFAX | CA | N | Y | No | No | No | No | No | No | No | FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | MARIN | NOVATO | 2023-02-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 56 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1179 |  | 0 |  | CABLE COM | BOTHELL | WA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | MARIN | NOVATO | 2023-11-07 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 56 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 19232 |  | 13 |  | R&S CONSTRUCTION MANAGEMENT INC. | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | NOVATO | 2023-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 56 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1711 |  | 1 |  | BRIGHT FUTURE BUILDERS | VACAVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | NOVATO | 2023-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 56 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2574 |  | 1 |  | HOMEOWNER | NOVATO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | NOVATO | 2023-03-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 56 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1554 |  | 1 |  | GOLDEN STATE UTILITY CO | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | NOVATO | 2023-04-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 56 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | NOVATO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | NOVATO | 2023-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 56 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | NOVATO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | NOVATO | 2023-01-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 56 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4431 |  | 0 |  | SJ CIMINO ELECTRIC | SANTA ROSA | CA | N | Y | Yes | No | Yes | Yes | Yes | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | MARIN | NOVATO | 2023-06-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 56 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 484 |  | 1 |  | G FAMILY PLUMBING SERVICES | SAN RAFAEL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | NOVATO | 2023-07-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 56 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CABLECOM | FAIRFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | NOVATO | 2023-09-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 56 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1279 |  | 2 |  | UNLICENSED CONTRACTOR | NOVATO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | ROSS | 2023-11-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1829 |  | 1 |  | SINGLE POINT DESIGN INC | SAUSALITO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | ROSS | 2023-03-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1619 |  | 1 |  | JIM GLOMB CONSULTANTS | SEBASTOPOL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN ANSELMO | 2023-11-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3893 |  | 1 |  | CLOUGH CONSTUCTION | SAN RAFAEL | CA | N | Y | Yes | Yes | No | Yes | No | No | Yes | incorrect information or marks
Pacific Gas and Electric | N | MARIN | SAN ANSELMO | 2023-01-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 213 |  | 1 |  | HOMEOWNER | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN ANSELMO | 2023-11-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4430 |  | 1 |  | GILLIS CONSTRUCTION | PETALUMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN ANSELMO | 2023-11-17 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2214 |  | 1 |  | HOMEOWNER | SAN ANSELMO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN ANSELMO | 2023-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 518 |  | 1 |  | HOMEOWNER | SAN ANSELMO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | SAN ANSELMO | 2023-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3628 |  | 1 |  | HOMEOWNER | SAN ANSELMO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN ANSELMO | 2023-09-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1631 |  | 1 |  | A REYES CONSTRUCTION COMPANY | RICHMOND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN ANSELMO | 2023-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2242 |  | 1 |  | A REYES CONSTRUCTION | VACAVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | MARIN | SAN ANSELMO | 2023-10-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | A REYES CONSTRUCTION COMPANY | HAYWARD | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | MARIN | SAN ANSELMO | 2023-05-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2484 |  | 1 |  | FERNANDEZ LANDSCAPING INC | SAN RAFAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN ANSELMO | 2023-06-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1044 |  | 1 |  | HOMEOWNER | CALIFORNIA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2023-09-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 2 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9195 |  | 1 |  | RIVAS CONCRETE INC | RICHMOND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT PROPERLY LOCATED OR MARKED
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2023-08-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 814 |  | 1 |  | SIERRA?S CONCRETE CONSTRUCTION | SAN PABLO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2023-08-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1378 |  | 1 |  | HOMEOWNER | SAN RAFAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2023-02-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 53 |  | 1 |  | HOMEOWNER | SAN RAFAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2023-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 858 |  | 2 |  | HOMEOWNER | SAN RAFAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2023-12-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1327 |  | 2 |  | BOMAN DESIGN & CONSTRUCTION | WALNUT CREEK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2023-06-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 898 |  | 1 |  | HOMEOWNER | SAN RAFAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2023-09-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1541 |  | 1 |  | UNLICENSED CONTRACTOR | SAN RAFAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2023-03-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1749 |  | 1 |  | HOMEOWNER | SAN RAFAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2023-12-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2099 |  | 1 |  | DIVINE ELECTRIC AND PLUMBING | SAN RAFAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2023-06-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1931 |  | 1 |  | MCARDELL LANDSCAPE INC | PETALUMA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2023-10-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1171 |  | 1 |  | HOMEOWNER | SAN RAFAEL | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2023-11-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1562 |  | 0 |  | MARIN FENCING INC | SAN RAFAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2023-02-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 3 |  | HOMEOWNER | SAN RAFAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAN RAFAEL | 2023-04-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.75 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1047 |  | 2 |  | GHILOTTI BROTHERS | SAN RAFAEL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | SAUSALITO | 2023-05-23 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1514 |  | 2 |  | ARB INC. | FAIRFIELD | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | SAUSALITO | 2023-10-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2812 |  | 1 |  | HOMEOWNER | SAUSALITO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | SAUSALITO | 2023-08-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1386 |  | 2 |  | G LANDSCAPE DIVISION LLC | SAN RAFAEL | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | MARIN | TIBURON | 2023-06-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2514 |  | 1 |  | COMMUNITY PLAYGROUNDS | VALLEJO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MARIN | TIBURON | 2023-12-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Probing Device | 1 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2437 |  | 1 |  | FARNSWORTH LANDSCAPING | NOVATO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MARIN | TIBURON | 2023-09-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2052 |  | 0 |  | HURRICANE HAULING AND DEMOLITION | SAN RAFAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MENDOCINO | REDWOOD VALLEY | 2023-05-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 6 |  | SUPERIOR PUMP | FORT BRAGG | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MENDOCINO | REDWOOD VALLEY | 2023-02-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 556 |  | 1 |  | HOMEOWNER | REDWOOD VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MENDOCINO | UKIAH | 2023-06-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3570 |  | 0 |  | JMT ELECTRIC | MIDDLETOWN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MENDOCINO | UKIAH | 2023-08-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2561 |  | 1 |  | HOMEOWNER | UKIAH | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MENDOCINO | UKIAH | 2023-12-12 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 25 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | GHILOTTI CONSTRUCTION | SANTA ROSA | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Incorrect Facility Records / Maps
Pacific Gas and Electric | N | MENDOCINO | UKIAH | 2023-12-05 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 25 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 239 |  | 0 |  | ARB INC | HAYWARD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Incorrect Facility Records / Maps
Pacific Gas and Electric | N | MENDOCINO | UKIAH | 2023-04-16 | Third party excavation damage | Riser | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 25 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 113 |  | 0 |  | NA | NA | CA | N | Y | No | No | No | No | No | No | No | Riser was found broken off in field no daming party at scene
Pacific Gas and Electric | N | MENDOCINO | UKIAH | 2023-05-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3646 |  | 1 |  | HOMEOWNER | UKIAH | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MENDOCINO | UKIAH | 2023-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 0 | 0 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 634 |  | 0 |  | GROW WEST | UKIAH | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MERCED | ATWATER | 2023-05-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 45 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | MCKUIN PIPELINE INC | HOLLISTER | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | MERCED | ATWATER | 2023-12-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1732 |  | 1 |  | HOMEOWNER | ATWATER | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MERCED | ATWATER | 2023-01-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 999 |  | 4 |  | SOARES LUMBER P.S G INC | LOS BANOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MERCED | ATWATER | 2023-01-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1500 |  | 1 |  | HOMEOWNER | ATWATER | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MERCED | ATWATER | 2023-05-08 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | IMPERIAL UNDERGROUND DEVELOPMENT INC | MERCED | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MERCED | ATWATER | 2023-02-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1500 |  | 1 |  | HOMEOWNER | ATWATER | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MERCED | ATWATER | 2023-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | ATWATER | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MERCED | ATWATER | 2023-05-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | SHOCK ELECTRIC | MERCED | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MERCED | DOS PALOS | 2023-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 42 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4378 |  | 0 |  | HOMEOWNER | SOUTH DOS PALOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | Excavated outside the delineated area
Pacific Gas and Electric | N | MERCED | HILMAR | 2023-03-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2000 |  | 0 |  | HOMEOWNER | HILMAR | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MERCED | LOS BANOS | 2023-06-12 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 42 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9575 |  | 15 |  | CORONADO CONSTRUCTION | HAYWARD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MERCED | LOS BANOS | 2023-05-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 77 |  | 1 |  | HOMEOWNER | LOS BANOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MERCED | LOS BANOS | 2023-09-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 42 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2754 |  | 2 |  | LAND DEVOLOPMENT INC. LDI | CLOVIS | CA | N | Y | No | No | No | No | No | No | No | Excavated Prior to Receiving a Positive Response From All Utilities
Pacific Gas and Electric | N | MERCED | LOS BANOS | 2023-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1756 |  | 1 |  | HOMEOWNER | LAFAYETTE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MERCED | MERCED | 2023-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | MERCED | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MERCED | MERCED | 2023-09-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2947 |  | 1 |  | MORA PLUMBING | MERCED | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MERCED | MERCED | 2023-12-08 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4494 |  | 0 |  | POLMAGRANATE UNDERGROUND | MERCED | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MERCED | MERCED | 2023-12-05 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 4 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5948 |  | 4 |  | MERCED CALVARY CEMETEY | MERCED | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MERCED | MERCED | 2023-08-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 55 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1497 |  | 1 |  | KROEKER INC | FRESNO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MERCED | MERCED | 2023-04-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | MERCED | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MERCED | MERCED | 2023-06-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1477 |  | 1 |  | HOMEOWNER | MERCED | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MERCED | MERCED | 2023-06-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 74 |  | 2 |  | FLOREZ PAVING | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MERCED | MERCED | 2023-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1690 |  | 0 |  | RANCHWOOD | LOS BONOS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Incorrect Information or Marks
Pacific Gas and Electric | N | MERCED | WINTON | 2023-07-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | WINTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | CARMEL | 2023-07-03 | Third party excavation damage | Not Available | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | CARMEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | CARMEL | 2023-08-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1433 |  | 1 |  | HOMEOWNER | CARMEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | CARMEL | 2023-06-01 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 51 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 14651 |  | 3 |  | WEST VALLEY CONSTRUCTION | SALINAS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | MONTEREY | CARMEL | 2023-08-31 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 51 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1310 |  | 0 |  | KELLY CONSTRUCTION | CARMEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | CARMEL VALLEY | 2023-01-07 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 51 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 398 |  | 1 |  | HOMEOWNER | CARMEL VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | CARMEL VALLEY | 2023-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2622 |  | 1 |  | HOMEOWNER | CARMEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | CARMEL-BY-THE-SEA | 2023-09-07 | Third party excavation damage | Main | Polyethylene Pipe | Not Available | 1.25 | 51 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3089 |  | 6 |  | RK WILSON PLUMBING | SEASIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | Excavated outside delineated area
Pacific Gas and Electric | N | MONTEREY | CARMEL-BY-THE-SEA | 2023-04-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | EASY DRAINS PLUMBING | MONTEREY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | DEL REY OAKS | 2023-04-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 51 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1946 |  | 1 |  | HOMEOWNER | DEL REY OAKS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | GREENFIELD | 2023-10-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2968 |  | 0 |  | DANNY SIMS CONSTRUCTION | BAKERSFIELD | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | MARINA | 2023-10-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 56 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1764 |  | 3 |  | HOMEOWNER | MARINA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | MARINA | 2023-01-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.75 | 15 | 12 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 291 |  | 3 |  | HOMEOWNER | PLEASANTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | MARINA | 2023-03-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 56 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1101 |  | 0 |  | HOMEOWNER | HOLLISTER | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | MARINA | 2023-09-30 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 56 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3217 |  | 1 |  | JD''S UNDERGROUND INC | MARINA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | MONTEREY | 2023-11-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 57 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2836 |  | 1 |  | HOMEOWNER | MONTEREY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | MONTEREY | 2023-08-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1.25 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1549 |  | 1 |  | BRYTEMOVE ENERGY | MONTEREY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | MONTEREY | 2023-10-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1662 |  | 1 |  | HOMEOWNER | MONTEREY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | MONTEREY | 2023-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 532 |  | 1 |  | JIMINEZ LANDSCAPING | MARINA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | MONTEREY | 2023-01-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2467 |  | 1 |  | HOMEOWNER | MONTEREY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | MONTEREY | 2023-08-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1998 |  | 2 |  | MISSION LANDSCAPING | MONTEREY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | PACIFIC GROVE | 2023-05-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 29 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1401 |  | 3 |  | MONTEREY PENINSULA ENGINEERING | MARINA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | PACIFIC GROVE | 2023-07-19 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 29 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ANRAK CORPORATION | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | PEBBLE BEACH | 2023-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 795 |  | 1 |  | HOMEOWNER | PEBBLE BEACH | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | PRUNEDALE | 2023-09-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1239 |  | 1 |  | HOMEOWNER | PRUNEDALE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | PRUNEDALE | 2023-01-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | JMS | SALINAS | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | PRUNEDALE | 2023-10-27 | Third party excavation damage | Riser | Steel | Backhoe/Trackhoe | 0.75 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | HOMEOWNER | ROYAL OAKS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | SALINAS | 2023-10-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2247 |  | 1 |  | RADIANT LANDSCAPING | SALINAS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | SALINAS | 2023-02-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 500 |  | 0 |  | HOMEOWNER | SALINAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | SALINAS | 2023-05-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2706 |  | 1 |  | HOMEOWNER | SALINAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | SALINAS | 2023-01-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 164 |  | 1 |  | TEICHERT CONSTRUCTION | PLEASANTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | MONTEREY | SALINAS | 2023-09-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2658 |  | 1 |  | HOMEOWNER | SALINAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | SALINAS | 2023-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1216 |  | 1 |  | HOMEOWNER | SALINAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | SALINAS | 2023-01-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | Y | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | FIBERTEL | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | SALINAS | 2023-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1562 |  | 1 |  | HOMEOWNER | SALINAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | SALINAS | 2023-08-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1836 |  | 1 |  | CJ COAST CONSTRUCTION | SALINAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | MONTEREY | SOLEDAD | 2023-06-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1299 |  | 0 |  | A. MUNOZ LANDSCAPING | MORGAN HILL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NAPA | ANGWIN | 2023-09-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 868 |  | 1 |  | HOMEOWNER | ANGUIN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NAPA | ANGWIN | 2023-08-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 56 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6795 |  | 1 |  | PINA VINEYARD MANAGEMENT | NAPA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NAPA | CALISTOGA | 2023-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2538 |  | 1 |  | KORTE?S BACKHOE SERVICE | CALISTOGA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | NAPA | CALISTOGA | 2023-08-31 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4036 |  | 0 |  | INNOVATE CONCRETE | SANTA CLARA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | NAPA | CALISTOGA | 2023-12-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2302 |  | 4 |  | HOMEOWNER | CALISTOGA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NAPA | NAPA | 2023-06-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 908 |  | 1 |  | NAPA BUILDING SUPPLY | NAPA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NAPA | NAPA | 2023-05-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1754 |  | 1 |  | HOMEOWNER | NAPA | CA | N | Y | Yes | Yes | Yes | Yes | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | NAPA | NAPA | 2023-09-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3442 |  | 2 |  | HOMEOWNER | NAPA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NAPA | NAPA | 2023-03-20 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 54 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 958 |  | 0 |  | PINNACLE POWER SERVICES | VALLEJO | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT INFORMATION OR MARKS
Pacific Gas and Electric | N | NAPA | SAINT HELENA | 2023-09-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 343 |  | 1 |  | CARRIERO BUILDERS INC. | SANTA ROSA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Other Error
Pacific Gas and Electric | N | NAPA | SAINT HELENA | 2023-02-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 500 |  | 1 |  | HOMEOWNER | ST HELENA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NAPA | SONOMA/NAPA | 2023-07-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 40646 |  | 2 |  | NELSON?S BULLDOZING | HEALDSBURG | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NEVADA | GRASS VALLEY | 2023-05-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 20 | 16 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 417 |  | 4 |  | C&D CONTRACTORS | GRASS VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | NEVADA | GRASS VALLEY | 2023-07-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 4 |  | FENTON CONSTRUCTION | COLFAX | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NEVADA | NEVADA CITY | 2023-08-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2239 |  | 1 |  | ESTEY ELECTRIC | NEVADA CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NEVADA | NEVADA CITY | 2023-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2405 |  | 1 |  | YUBA RIVER SWIMMING POOLS | GRASS VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NEVADA | NEVADA CITY | 2023-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | NEVADA CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | NEVADA | PENN VALLEY | 2023-01-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 81 |  | 1 |  | HOMEOWNER | PENN VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | AUBURN | 2023-10-31 | Operator excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5341 |  | 6 |  | PG&E | OAKLAND | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | PLACER | AUBURN | 2023-12-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3048 |  | 1 |  | HOMEOWNER | AUBURN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | AUBURN | 2023-11-30 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2194 |  | 0 |  | PCWA | AUBURN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | GRANITE BAY | 2023-07-07 | Operator excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2313 |  | 0 |  | PG&E | SACRAMENTO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | PLACER | GRANITE BAY | 2023-08-29 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4390 |  | 2 |  | KP MARTIN GENERAL ENGINEERING | SUBURN | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | PLACER | GRANITE BAY | 2023-09-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5692 |  | 2 |  | MAJESTIC BUILDERS INC | GOLD RIVER | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | GRANITE BAY | 2023-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | GRANITE BAY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | GRANITE BAY | 2023-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 518 |  | 1 |  | HOMEOWNER | GRANITE BAY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | PLACER | GRANITE BAY | 2023-03-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1514 |  | 1 |  | GRANITE BAY''S LOCAL | GRANITE BAY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | PLACER | GRANITE BAY | 2023-02-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 205 |  | 1 |  | LAFLEUR EXCAVATING | CITRUS HEIGHTS | CA | N | Y | No | No | No | No | No | No | No | OTHER
Pacific Gas and Electric | N | PLACER | LINCOLN | 2023-07-18 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | TEICHERT | ROCKLIN | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | PLACER | LOOMIS | 2023-04-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 180 |  | 1 |  | HOMEOWNER | LOOMIS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | LOOMIS | 2023-04-07 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5 |  | 0 |  | KP MARTIN | AUBURN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | PLACER | PENRYN | 2023-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 53 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3278 |  | 1 |  | DDC | PENRYN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | ROCKLIN | 2023-08-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1887 |  | 2 |  | HOMEOWNER | ROCKLIN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | ROCKLIN | 2023-11-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2217 |  | 1 |  | LUXERA | FREMONT | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | ROCKLIN | 2023-10-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2187 |  | 1 |  | HOMEOWNER | ROCKLIN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | ROCKLIN | 2023-04-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | ROCKLIN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | ROCKLIN | 2023-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | LEGACY CONSTRUCTION | FRESNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | ROCKLIN | 2023-07-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | JD PASQUETTI | LINCOLN | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | PLACER | ROCKLIN | 2023-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1306 |  | 0 |  | PARADIGM CONSTRUCTION | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | ROSEVILLE | 2023-03-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1500 |  | 2 |  | WEBER GENERAL ENGINEERING | DIXON | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | PLACER | ROSEVILLE | 2023-06-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 53 |  | 2 |  | HOMEOWNER | ROSEVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | ROSEVILLE | 2023-05-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 4 |  | ELITE EXPRESS | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | ROSEVILLE | 2023-01-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 239 |  | 1 |  | N6 LLC | GLENDALE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | PLACER | ROSEVILLE | 2023-09-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1701 |  | 0 |  | AG PLUMBING | RIO LINDA | CA | N | Y | Yes | No | No | No | No | Yes | Yes | Incorrect Information or Marks
Pacific Gas and Electric | N | PLACER | SHERIDAN | 2023-08-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 46 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4937 |  | 1 |  | HOMEOWNER | ROCKLIN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | ANTELOPE | 2023-09-11 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6868 |  | 0 |  | PRECISION PLUMBING AND DRAIN | ANTELOPE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | CARMICHAEL | 2023-11-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2186 |  | 0 |  | US TRENCHLESS | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | CARMICHAEL | 2023-05-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1736 |  | 1 |  | SEFNCO COMMUNICATIONS | SUMMER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | CARMICHAEL | 2023-09-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2092 |  | 2 |  | NATURAL GREEN | CARMICHAEL | CA | N | Y | No | No | No | No | No | No | No | No USA Ticket
Pacific Gas and Electric | N | SACRAMENTO | CARMICHAEL | 2023-04-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3 |  | 1 |  | ROMERO LANDSCAPING | GRASS VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | CARMICHAEL | 2023-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Trencher | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | CARMICHAEL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | CARMICHAEL | 2023-11-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2306 |  | 4 |  | HOMEOWNER | CARMICHAEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | CITRUS HEIGHTS | 2023-10-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ELITE OUTDOOR SOLUTIONS | YUBA CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | CITRUS HEIGHTS | 2023-05-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | TORO STRONG FENCING | NORTH HIGHLANDS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | CITRUS HEIGHTS | 2023-08-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1656 |  | 1 |  | NA | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | CITRUS HEIGHTS | 2023-02-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CABRALES LAWN SERVICE | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | CITRUS HEIGHTS | 2023-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CYNTEK CONSTRUCTION SERVICES | RESCUE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | CITRUS HEIGHTS | 2023-08-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4742 |  | 1 |  | HOMEOWNER | CITRUS HEIGHTS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | CITRUS HEIGHTS | 2023-06-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3262 |  | 4 |  | HOMEOWNER | FAIR OAKS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | CITRUS HEIGHTS | 2023-09-16 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4468 |  | 1 |  | HOMEOWNER | CITRUS HEIGHTS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | CITRUS HEIGHTS | 2023-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1162 |  | 16 |  | SPRING CREEK APARTMENTS | CITRUS HEIGHTS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | CITRUS HEIGHTS | 2023-11-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2295 |  | 1 |  | HOMEOWNER | CITRUS HEIGHTS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | CITRUS HEIGHTS | 2023-01-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4884 |  | 1 |  | HOMEOWNER | CITRUS HEIGHT | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | LOCATING WIRE MISSING OR BROKEN
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2023-10-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4382 |  | 1 |  | STRUCK CONSTRUCTION | NORTH HIGHLANDS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2023-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3251 |  | 3 |  | NV COMMUNICATIONS | MCCLELLAN PARK | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2023-10-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1597 |  | 1 |  | A FENCE REPAIR | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | Failed to Dig with Care
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2023-01-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | M&M ELECTRIC | SACRAMENTO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2023-10-14 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6645 |  | 0 |  | ALVO LANDSCAPE INC | OAKLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2023-11-20 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3216 |  | 1 |  | MILLCREEK CONSTRUCTION | CERES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2023-11-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1379 |  | 1 |  | JHP ELECTRIC | ELK GROVE | CA | N | Y | No | No | No | No | No | No | No | Failed to Dig with Care
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2023-06-13 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5527 |  | 0 |  | UNLIMITED COMMUNICATIONS | LODI | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2023-07-28 | Third party excavation damage | Main | Polyethylene Pipe | Not Available | 8 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 56110 |  | 0 |  | ST FRANCIS ELECTRIC | SAN LEANDRO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2023-07-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | TENNYSON ELECTRIC | LIVERMORE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | ELK GROVE | 2023-08-18 | Third party excavation damage | Main | Steel | Not Available | 4 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 46040 |  | 0 |  | PLATINUM PIPELINE | LIVERMORE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | ELVERTA | 2023-11-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2535 |  | 1 |  | IRISH CONSTRUCTION | PITTSBURG | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | ELVERTA | 2023-09-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1406 |  | 1 |  | HOMEOWNER | ELVERTA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | FAIR OAKS | 2023-06-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2257 |  | 1 |  | VASKO ELECTRIC | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | FAIR OAKS | 2023-11-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1952 |  | 1 |  | SACRAMENTO AREA SEWER DISTRICT | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | FAIR OAKS | 2023-03-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1194 |  | 1 |  | HOMEOWNER | FAIR OAKS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | FOLSOM | 2023-07-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5931 |  | 1 |  | HOMEOWNER | FOLSOM | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | FOLSOM | 2023-08-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2765 |  | 2 |  | SEFNCO | LIVERMORE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | FOLSOM | 2023-11-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1929 |  | 1 |  | LB CONSTRUCTION | SAN RAMON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | FOLSOM | 2023-01-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 212 |  | 1 |  | HURLEY CONSTRUCTION INC | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | FOLSOM | 2023-04-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | PACIFIC PARKS LANDSCAPING | AUBURN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | FOLSOM | 2023-12-28 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2875 |  | 2 |  | NEXT CRAFTED | ROSEVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | GALT | 2023-05-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Farm Equipment | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | HOMEOWNER | GALT | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | GALT | 2023-11-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4745 |  | 2 |  | HOMEOWNER | GALT | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | NORTH HIGHLANDS | 2023-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | NORTH HIGHLANDS | 2023-02-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | NORTH HIGHLANDS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | NORTH HIGHLANDS | 2023-08-21 | Third party excavation damage | Main | Steel | Not Available | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 19334 |  | 2 |  | RHINO ENGINEERING | PLACERVILLE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | NORTH HIGHLANDS | 2023-11-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1612 |  | 2 |  | HOMEOWNER | NORTH HIGHLANDS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | SACRAMENTO | ORANGEVALE | 2023-05-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2752 |  | 1 |  | HOMEOWNER | ORANGEVALE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | ORANGEVALE | 2023-03-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7265 |  | 1 |  | HOMEOWNER | ORANGEVALE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | RANCHO CORDOVA | 2023-11-10 | Third party excavation damage | Main | Polyethylene Pipe | Trencher | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7733 |  | 2 |  | SEFNCO COMMUNICATIONS | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | RANCHO CORDOVA | 2023-05-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2917 |  | 0 |  | DIRT MOVERS | STOCKTON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | SACRAMENTO | RANCHO CORDOVA | 2023-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2113 |  | 2 |  | SEFNCO COMMUNICATIONS | SACRAMENTO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | SACRAMENTO | RANCHO CORDOVA | 2023-02-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3017 |  | 1 |  | SEFNCO | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | OTHER
Pacific Gas and Electric | N | SACRAMENTO | RANCHO CORDOVA | 2023-04-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | PBM CONSTRUCTION | ROCKLIN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | RANCHO CORDOVA | 2023-12-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4538 |  | 4 |  | HOMEOWNER | RANCHO CORDOVA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | RANCHO CORDOVA | 2023-06-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2208 |  | 0 |  | PROCIDA LANDSCAPING | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | RIO LINDA | 2023-05-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Directional Drilling | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3 |  | 1 |  | NV COMMUNICATION | GARDNERVILLE | NV | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | RIO LINDA | 2023-05-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1 |  | 2 |  | RAWLES ENGINEERING | FOLSOM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2051 |  | 2 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-04-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NATCH PREGRA INC. DAB: LIFESCAPING | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-06-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5134 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-08-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1874 |  | 1 |  | P M T CONCRETE | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2411 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | BONNEY PLUMBING | RANCHO CORDOVA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-10-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2467 |  | 1 |  | MGE UNDERGROUND | RANCHO CORDOVA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Failed to Dig with Care
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-07-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1.25 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6978 |  | 4 |  | PACIFIC EXCAVATION | SACRAMENTO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1978 |  | 2 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | Failed to Dig with Care
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-07-25 | Third party excavation damage | Main | Polyethylene Pipe | Not Available | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 9 |  | BLANCHARD CONSTRUCTION | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-05-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 389 |  | 2 |  | FREEDOM FENCING | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-10-10 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4612 |  | 1 |  | SHENANDOAH EXCAVATING | FIDDLETOWN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-07-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | LIFESCAPING OUTDOORS | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-06-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2884 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-03-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10000 |  | 1 |  | CASTILLO FENCING | SACTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Farm Equipment | 1 | 0 | 0 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1992 |  | 0 |  | NATOMAS CENTRAL MUTUAL WATER COMPANY | RIO LINDA | CA | N | Y | Yes | Yes | No | No | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-05-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-08-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2364 |  | 1 |  | CLASSIC FENCE | RANCHO CORDOVA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-08-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2082 |  | 1 |  | BAY CITY PAVING | WEST SACRAMENTO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-09-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1534 |  | 1 |  | MARTIN GENERAL ENGINEERING | RANCHO CORDOVA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-01-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 286 |  | 2 |  | MAKO CUSTOM HOMES | RESCUE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | OTHER
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-05-22 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | CAL WORKS CONSTRUCTION | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-11-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2442 |  | 1 |  | CITY OF SACRAMENTO | NORTH HIGHLANDS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-10-17 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | NA | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-02-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5000 |  | 0 |  | CSI ENGINEERING | BENICIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-12-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6652 |  | 1 |  | LUND CONSTRUCTION | NORTH HIGHLANDS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-12-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2025 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-11-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2582 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-12-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1193 |  | 2 |  | ANCHORED TINY HOMES | FAIR OAKS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-12-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1688 |  | 4 |  | ANCHOR TINY HOMES | FAIR OAKS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4791 |  | 2 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-06-27 | Third party excavation damage | Riser | Polyethylene Pipe | Grader/Scraper | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1574 |  | 0 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-02-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-03-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2048 |  | 0 |  | LUND CONSTRUCTION | NORTH HIGHLANDS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-08-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | C & C CONSTRUCTION | HACIENDA HEIGHTS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-05-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-04-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-01-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 80 |  | 1 |  | CITY OF SACRAMENTO | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2361 |  | 2 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-06-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Trencher | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1428 |  | 2 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-06-05 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4199 |  | 0 |  | CAPITAL CITY ELECTRIC WEST INC | MATHER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1760 |  | 2 |  | JD WELCH | RIO LINDA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2557 |  | 2 |  | IRISH CONSTRUCTION | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-04-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-02-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-10-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2074 |  | 1 |  | CHAMP ROOTER & DRAIN | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-10-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1911 |  | 1 |  | CHAMP ROOTER & DRAIN | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-06-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1715 |  | 2 |  | ALWAYS AFFORDABLE PLUMBING | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 8919 |  | 1 |  | SANDCOM | ANTIOCH | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-06-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3478 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-04-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | LUND CONSTRUCTION | NORTH HIGHLANDS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-10-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3984 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-09-11 | Third party excavation damage | Main | Steel | Not Available | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3038 |  | 0 |  | CITY OF SACRAMENTO, SEWER | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-09-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1438 |  | 2 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-08-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1710 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-01-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 179 |  | 1 |  | SANDRIDGE HOME IMPROVEMENT | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-08-16 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 8 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 23976 |  | 1 |  | TEICHERT CONSTRUCTION | PLEASANTON | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-07-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | TEICHERT CONSTRUCTION | PLEASANTON | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | CITY OF SACRAMENTO | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-11-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1887 |  | 1 |  | EMP ELECTRIC | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-06-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1902 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6051 |  | 2 |  | RIVER CITY CARPENTRY | ANTELOPE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-05-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1749 |  | 1 |  | SCOTT CARVER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-01-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 79 |  | 2 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-03-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1.25 | 50 | 44 | Y | N | Y | N | 0 | 0 |  | 0 | 0 |  | 10000 |  | 2 |  | FIBERCO INC | RIVERSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-05-07 | Third party excavation damage | Riser | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 44 | Y | N | Y | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NA | NA | CA | N | Y | No | No | No | No | No | No | No | House fire
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-06-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2253 |  | 1 |  | EASON & TAMBORNINI, A LAW | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-04-19 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 4 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4 |  | 0 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-02-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4447 |  | 1 |  | GUINNESS CORPORATION | BAKERSFIELD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-11-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2450 |  | 2 |  | LUND CONSTRUCTION | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-11-08 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 8722 |  | 0 |  | FLETCHER PLUMBING | YUBA CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-07-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3617 |  | 1 |  | J GARCIA CONCRETE | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SACRAMENTO | SACRAMENTO | 2023-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2020 |  | 1 |  | HOMEOWNER | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN BERNARDINO | AMBOY | 2023-07-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 10 |  | HI-DESERT PLUMBING INC | YUCCA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | Excavated outside delineated area
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2023-12-13 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3648 |  | 0 |  | MICHAEL O''SHAUGHNESSY CONSTRUCTION | SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2023-04-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | CAL LINE TREE CARE | CONCORD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2023-01-25 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 1.5 | 0.5 | 0.38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4000 |  | 1 |  | K.J. WOODS CONSTRUCTION | SOUTH SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2023-03-28 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 40000 |  | 0 |  | SAN FRANCISCO WATER DEPARTMENT | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2023-11-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3101 |  | 6 |  | JDB & SONS CONSTRUCTION, INC. | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2023-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 13297 |  | 1 |  | JDB & SONS CONSTRUCTION, INC. | SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2023-01-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3000 |  | 1 |  | NTK CONSTRUCTION | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2023-07-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2023-10-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1833 |  | 1 |  | NTK CONSTRUCTION | SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2023-11-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2747 |  | 1 |  | NTK CONSTRUCTION, INC. | SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2023-05-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | MICHAEL O''SHAUGHNESSY CONSTRUCTION | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2023-07-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4104 |  | 1 |  | KROWN CONSTRUCTION | TURLOCK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2023-07-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SEAFIELD LANDSCAPING INC | PACFICA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2023-05-17 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5849 |  | 0 |  | PACIFIC STATE ENVIRONMENTAL CONTRACTORS | DUBLIN CA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2023-04-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | M SQUARED CONSTRUCTION | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2023-04-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4900 |  | 1 |  | J M CONSTRUCTION LLC | SOUTH SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2023-04-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 9.2 | 7 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NTK CONSTRUCTION INC. | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2023-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 9.2 | 7 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4900 |  | 1 |  | SAN FRANCISCO WATER DEPT | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2023-08-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 0.5 | 0.38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5086 |  | 2 |  | NTK CONSTRUCTION | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2023-02-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 0.5 | 0.38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5000 |  | 1 |  | PROSPER CONSTRUCTION DEVELOPMENT | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2023-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 0.5 | 0.25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4917 |  | 1 |  | GOLDEN LINE CONCRETE CUTTING | TRACY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2023-09-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2250 |  | 3 |  | DARCY & HARTY CONSTRUCTION, INC. | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2023-01-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3000 |  | 0 |  | ADD A GARAGE INC | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2023-08-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1176 |  | 1 |  | SF UNDERGROUND | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2023-02-09 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 3 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 27251 |  | 0 |  | PRECISION ENGINEERING | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2023-07-23 | Third party excavation damage | Main | Polyethylene Pipe | Not Available | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 16718 |  | 8 |  | SAN FRANCISCO WATER DEPARTMENT | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2023-11-15 | Third party excavation damage | Main | Polyethylene Pipe | Probing Device | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9982 |  | 15 |  | CITY OF SAN FRANCISCO | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2023-03-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 20000 |  | 7 |  | R&S CONSTRUCTION MANAGEMENT INC. | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | No | No | OTHER
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2023-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5777 |  | 1 |  | J FLORES CONSTRUCTION | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2023-06-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4245 |  | 1 |  | JDB &SONS | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2023-01-24 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 160 |  | 6 |  | SAN FRANCISCO WATER DEPARTMENT | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2023-11-28 | Third party excavation damage | Main | Steel | Directional Drilling | 4 | 12 | 10 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5158 |  | 0 |  | PINNACLE PIPELINE INSPECTION INC | CAMPBELL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2023-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1.25 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7245 |  | 1 |  | R&S CONSTRUCTION | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2023-05-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9994 |  | 1 |  | JBD AND SONS CONSTRUCTION | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2023-10-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2055 |  | 1 |  | A RUIZ CONSTRUCTION COMPANY | SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2023-12-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1629 |  | 1 |  | JDB & SONS CONSTRUCTION, INC. | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2023-06-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2992 |  | 1 |  | SFWD | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2023-02-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5000 |  | 1 |  | M SQUARED | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2023-07-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | TERRA LANDSCAPE | OAKLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2023-01-17 | Operator excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4124 |  | 4 |  | PHOENIX ELECTRIC | SAN FRANCISCO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2023-10-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2380 |  | 1 |  | DISCOUNT PLUMBING | DALY CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2023-10-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2800 |  | 1 |  | JMB CONSTRUCTION INC | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN FRANCISCO | SAN FRANCISCO | 2023-12-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4788 |  | 0 |  | JMB CONSTRUCTION INC | SOUTH SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | ESCALON | 2023-04-01 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Farm Equipment | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3735 |  | 1 |  | HOMEOWNER | ESCALON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | LATHROP | 2023-04-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | PCL MANAGEMENT INC | BYRON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | LATHROP | 2023-11-10 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5597 |  | 0 |  | TEICHERT CONSTRUCTION | SACRAMENTO | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Incorrect Information or Marks
Pacific Gas and Electric | N | SAN JOAQUIN | LATHROP | 2023-11-10 | Third party excavation damage | Main | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1082 |  | 0 |  | TEICHERT CONSTRUCTION | PLESANTON | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | SAN JOAQUIN | LINDEN | 2023-12-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1718 |  | 1 |  | CHINCHIOLO FARMS | LINDEN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | LODI | 2023-02-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 100 |  | 2 |  | JUSTIN BARTH FENCING | LODI | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2023-09-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2358 |  | 2 |  | TITANIUM SOLAR GONAZALO VILLIEGAS | MANTECA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2023-11-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3965 |  | 1 |  | HOMEOWNER | MANTECA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2023-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | GOLDEN STATE UTILITY | MANTECA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2023-10-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3536 |  | 1 |  | HOMEOWNER | MANTECA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2023-12-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1375 |  | 0 |  | EVERGREEN LANDSCAPING | MANTECA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2023-02-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MANTECA UNIFIED SCHOOL DISTRICT | MANTECA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2023-05-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | MANTECA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2023-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2467 |  | 1 |  | HOMEOWNER | MANTECA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | MANTECA | 2023-03-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1573 |  | 2 |  | HOMEOWNER | MANTECA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | MOUNTAIN HOUSE | 2023-04-28 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | PETROLEUM BUILDERS | TURLOCK | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | RIPON | 2023-12-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2477 |  | 1 |  | HOMEOWNER | RIPON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | RIPON | 2023-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1904 |  | 1 |  | FENCE SOLUTIONS | LIVERMORE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | RIPON | 2023-03-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5000 |  | 1 |  | JAVIER FENCING | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2023-10-25 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10569 |  | 0 |  | WEST VALLEY | STOCKTON | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Incorrect Information or Marks
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2023-10-31 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2317 |  | 1 |  | HOMEOWNER | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2023-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1994 |  | 1 |  | SORACCO INC. | LODI | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2023-11-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2636 |  | 1 |  | HOMEOWNER | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2023-02-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3599 |  | 1 |  | UNITED PAVEMENT | MODESTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2023-05-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 0.43 | 0.31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4 |  | 1 |  | PACAS COMPANY | STOCKTON | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2023-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6118 |  | 1 |  | HOMEOWNER | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2023-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 4 | 0.5 | 0.38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | QRS REMODELING | LIVERMORE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2023-03-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1126 |  | 1 |  | PATMON COMPANY | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2023-08-16 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2708 |  | 1 |  | WEST COAST PLUMBING AND SEWER | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2023-03-03 | Operator excavation damage | Main | Polyethylene Pipe | Trencher | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 11088 |  | 7 |  | PG&E | STOCKTON | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2023-12-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5536 |  | 1 |  | LASAR UNDERGROUND CONSTRUCTION INC. | FRESNO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2023-02-22 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5000 |  | 1 |  | VULCAN CONSTRUCTION | SANTA CLARA | CA | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2023-01-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5000 |  | 1 |  | HOMEOWNER | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2023-04-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3 |  | 1 |  | PORT OF STOCKTON | STOCKTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2023-10-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1965 |  | 2 |  | HOMEOWNER | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2023-06-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1056 |  | 1 |  | SIERRA SERVICES | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2023-12-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2906 |  | 2 |  | LEGACY ELECTRICAL SERVICE & CONSTRUCTION | VACAVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2023-04-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2023-01-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2000 |  | 1 |  | HOMEOWNER | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2023-09-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1328 |  | 1 |  | MCFADDEN CONSTRUCTION INC. | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2023-10-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1867 |  | 0 |  | JRH ENGINEERING | STOCKTON | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2023-11-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2059 |  | 1 |  | SORACCO INC | LODI | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2023-04-18 | Third party excavation damage | Main | Steel | Boring Equipment | 6 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 104749 |  | 29 |  | SEFNCO | LATHROP | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2023-01-02 | Operator excavation damage | A service line with no excess flow valve installed | Steel | Augur | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 17676 |  | 1 |  | PG&E | STOCKTON | CA | Y | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2023-08-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 861 |  | 0 |  | CAPITOL CITY UTILITIES | MATHER | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2023-07-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1560 |  | 1 |  | RIVERMAID TRADING CO | LODI, CA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2023-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1934 |  | 2 |  | SMG COMMUNICATIONS INC. | COLUSA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2023-05-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | CALIFORNIA SHINE CONSTRUCTION | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2023-04-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2023-08-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1709 |  | 1 |  | KNIFE RIVER | STOCKTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2023-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2025 |  | 0 |  | GSE CONSTRUCTION | LIVERMORE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | SAN JOAQUIN | STOCKTON | 2023-10-17 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 11311 |  | 0 |  | SAN JOAQUIN COUNTY PUBLIC WORKS DEPARTMENT | STOCKTON | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | TRACY | 2023-03-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | WILSON GENERAL CONTRACTING | EL SOBRANTE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | TRACY | 2023-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1756 |  | 2 |  | SUNSET FENCING | TRACY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | TRACY | 2023-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1146 |  | 1 |  | DON LAWLEY COMPANY | OAKDALE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN JOAQUIN | TRACY | 2023-05-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | HOMEOWNER | TRACY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN JOAQUIN | WOODBRIDGE | 2023-05-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | FARM FENCING | LINCOLN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | ATHERTON | 2023-10-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1735 |  | 1 |  | MEDEIROS CONSTRUCTION | BRENTWOOD | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | SAN MATEO | ATHERTON | 2023-10-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2948 |  | 1 |  | ATONDO TRENCHING | ATHERTON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Incorrect Information or Marks
Pacific Gas and Electric | N | SAN MATEO | BELMONT | 2023-05-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.25 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2999 |  | 0 |  | M&G HAULING | SAN MARTIN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | BELMONT | 2023-04-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 116 |  | 1 |  | HOMEOWNER | BELMONT | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | BELMONT | 2023-05-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1017 |  | 1 |  | ALLIANCE DEMOLITION | SAN MATEO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | BELMONT | 2023-03-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 300 |  | 1 |  | R B LANDSCAPE | REDWOOD CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | BELMONT | 2023-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 199 |  | 1 |  | HOMEOWNER | BELMONT | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | BURLINGAME | 2023-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3891 |  | 1 |  | HOMEOWNER | BURLINGAME | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | BURLINGAME | 2023-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1703 |  | 2 |  | HOMEOWNER | BURLINGAME | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | BURLINGAME | 2023-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 1 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3649 |  | 1 |  | MALDONADO FENCE | DALY CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | BURLINGAME | 2023-12-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7415 |  | 1 |  | CRATUS INC | SAN FRANCISCO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Incorrect Information or Marks
Pacific Gas and Electric | N | SAN MATEO | BURLINGAME | 2023-05-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1608 |  | 1 |  | DURHAM FENCE COMPANY | MILLBRAE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | BURLINGAME | 2023-05-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1257 |  | 0 |  | SEBASTIANI DESIGN SERVICES | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | BURLINGAME | 2023-05-09 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 111 |  | 1 |  | CRATUS INC. | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SAN MATEO | BURLINGAME | 2023-10-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2798 |  | 1 |  | JD CESARE CONSTRUCTION | BURLINGAME | CA | N | Y | Yes | Yes | Yes | No | No | Yes | Yes | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | BURLINGAME | 2023-12-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2105 |  | 1 |  | ARBOR CO TREE CARE | SAN MATEO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | BURLINGAME | 2023-11-27 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Trencher | 0.75 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 17566 |  | 1 |  | BAY LINE CUTTING AND CORING | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | EAST PALO ALTO | 2023-02-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 500 |  | 1 |  | BREAKTHROUGH BUILDERS | LOS ALTOS | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SAN MATEO | EL GRANADA | 2023-03-24 | Operator excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2878 |  | 1 |  | ARB UNDERGROUND | FAIRFIELD | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT INFORMATION OR MARKS
Pacific Gas and Electric | N | SAN MATEO | EL GRANADA | 2023-03-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 15000 |  | 1 |  | HOMEOWNER | EL GRANADA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | EL GRANADA | 2023-05-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1669 |  | 1 |  | HOMEOWNER | EL GRANADA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | EL GRANADA | 2023-08-01 | Third party excavation damage | Main | Polyethylene Pipe | Not Available | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | ARB INC | PITTSBURG | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Other Error
Pacific Gas and Electric | N | SAN MATEO | EL GRANADA | 2023-06-13 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2012 |  | 1 |  | ARB/PSC PRIMORIS | FAIRFIELD | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | FOSTER CITY | 2023-04-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2950 |  | 1 |  | NEW GENERATION FENCING | SAN JOSE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | SAN MATEO | FOSTER CITY | 2023-06-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1378 |  | 1 |  | HH FENCE AND DECK CO. | SAN BRUNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | FOSTER CITY | 2023-12-12 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9767 |  | 5 |  | FREEDOM UNDERGROUND PLUMBING | SAN JOSE | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | SAN MATEO | HALF MOON BAY | 2023-08-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2823 |  | 1 |  | COASTSIDE CONSTRUCTION, INC. | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | HALF MOON BAY | 2023-10-31 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2391 |  | 1 |  | VERDURA CONTRACTOR | HALF MOON BAY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | HALF MOON BAY | 2023-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 952 |  | 1 |  | HOMEOWNER | HALF MOON BAY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | HILLSBOROUGH | 2023-10-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4139 |  | 1 |  | GOLDEN GREEN LANDSCAPING | SAN MATEO | CA | N | Y | Yes | Yes | Yes | No | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | HILLSBOROUGH | 2023-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1751 |  | 1 |  | NIEVES BROS | MENLO PARK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | HILLSBOROUGH | 2023-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1646 |  | 1 |  | NORGO ENGINEERING | AMERICAN CANYON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | HILLSBOROUGH | 2023-07-08 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | PINNACLE POWER SERVICE | VELLEJO | CA | Y | Y | Yes | Yes | Yes | No | No | Yes | Yes | EXCAVATED PRIOR TO POSITIVE RESPONSE
Pacific Gas and Electric | N | SAN MATEO | MENLO PARK | 2023-03-07 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1200 |  | 0 |  | REBUILD GREEN | PALO ALTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | MENLO PARK | 2023-08-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 852 |  | 0 |  | CASEY CONSTRUCTION | EMERALD HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | MENLO PARK | 2023-04-19 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 301 |  | 0 |  | TRENCH FREE CSLB 971016 | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | MENLO PARK | 2023-08-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2325 |  | 1 |  | C FER CONSTRUCTION | PACHECO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | MILLBRAE | 2023-09-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2407 |  | 1 |  | DEL CONTE?S H&M LANDSCAPE CONSTRUCTION, INC. | FREMONT | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Dig with Care
Pacific Gas and Electric | N | SAN MATEO | MILLBRAE | 2023-06-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2157 |  | 1 |  | PASCACIO GENERAL CONSTRUCTION | SAN LEANDRO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | MOSS BEACH | 2023-12-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2484 |  | 1 |  | ALL FENCE COMPANY | REDWOOD CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | MOSS BEACH | 2023-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1872 |  | 1 |  | SIGMA PRIME GEO SCIENCES | HALF MOON BAY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | PACIFICA | 2023-03-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10000 |  | 1 |  | WEB BUILDERS INC. | REDWOOD CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | PACIFICA | 2023-04-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 35 | 29 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 216 |  | 1 |  | HOMEOWNER | PACIFICA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | PORTOLA VALLEY | 2023-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1295 |  | 1 |  | CASEY FOGLI CONCRETE CONTRACTOR | HAYWARD | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | PORTOLA VALLEY | 2023-06-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1397 |  | 1 |  | BAYSCAPE MANEGMENT | ALVISO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2023-10-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1806 |  | 1 |  | HOMEOWNER | REDWOOD CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2023-06-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Directional Drilling | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2 |  | 1 |  | AMERICAN DRILLING | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2023-10-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2597 |  | 1 |  | CASEY CONSTRUCTION | REDWOOD CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Dig with Care
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2023-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1316 |  | 1 |  | FONNZ | REDWOOD CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2023-04-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 1 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 169 |  | 0 |  | TREMORS PLUMBING AND SEWER | SAN MATEO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2023-10-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4151 |  | 1 |  | BEST BROTHER BUILDERS | SANTA CLARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2023-04-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | RETT CONSTRUCTION | PALO ALTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2023-03-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1268 |  | 2 |  | HOMEOWNER | REDWOOD CITY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2023-07-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SUBTERRA CONSTRUCTION | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Dig with Care
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2023-07-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1853 |  | 1 |  | HOMEOWNER | REDWOOD CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2023-09-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1145 |  | 0 |  | CALIFORNIA UTILITY COMPANY | LOS GATOS | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2023-06-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 2 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | REDWOOD CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | REDWOOD CITY | 2023-06-13 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1747 |  | 1 |  | HOMEOWNER | REDWOOD CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | SAN BRUNO | 2023-02-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7000 |  | 1 |  | WEST VALLEY CONSTRUCTION | REDWOOD CITY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | OTHER
Pacific Gas and Electric | N | SAN MATEO | SAN BRUNO | 2023-07-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | SAN BRUNO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | SAN BRUNO | 2023-05-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | JMB CONSTRUCTION | SOUTH SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SAN MATEO | SAN CARLOS | 2023-02-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 800 |  | 0 |  | SEAN MARTINA SM LANDSCAPE | REDWOOD CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | OTHER
Pacific Gas and Electric | N | SAN MATEO | SAN CARLOS | 2023-09-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1989 |  | 1 |  | MARTIN SANCHEZ CONSTRUCTION | SAN CARLOS | CA | N | Y | Yes | Yes | No | No | No | No | No | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | SAN MATEO | SAN CARLOS | 2023-10-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1138.67 |  | 1 |  | MARTIN SANCHEZ CONSTRUCTION | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SAN CARLOS | 2023-08-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1274 |  | 0 |  | BAYSCAPE MANAGEMENT | SAN CARLOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | SAN CARLOS | 2023-03-02 | Third party excavation damage | Main | Steel | Miscellaneous/Other | 2 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 24685 |  | 0 |  | SMELLY MEL''S PLUMBING | SOUTH SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2023-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Augur | 0.75 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4178 |  | 2 |  | TENNYSON ELECTRIC | LIVERMORE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2023-01-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1935 |  | 1 |  | HOMEOWNER | SAN MATEO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2023-04-13 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 32 |  | 0 |  | NEXT LEVEL PLUMBING SERVICES | BURLINGAME | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2023-10-30 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 950 |  | 0 |  | MAKITA CONSTRUCTION COMPANY | SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2023-08-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 0.75 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1570 |  | 1 |  | WEST VALLEY CONSTRUCTION | CAMPBELL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2023-11-27 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 8391 |  | 0 |  | WEST VALLEY CONSTRUCTION | CAMPBELL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2023-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4238 |  | 0 |  | BELL PLUMBING OF SAN MATEO | SAN CARLOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2023-08-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3184 |  | 0 |  | MARSH FENCE & DECK | SOUTH SAN FRANCISCO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2023-05-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HERNANDEZ GARDEN SERVICE | SAN MATEO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2023-07-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1877 |  | 1 |  | MICHAEL ROBERTS CONSTRUCTION | CAMPBELL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2023-12-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1947 |  | 1 |  | ZOWA CONSTRUCTION | BURLINGAME | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2023-11-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2175 |  | 1 |  | MONARCH LANDSCAPE COMPANIES | EAST PALO ALTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | SAN MATEO | 2023-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1442 |  | 1 |  | R B LANDSCAPING | REDWOOD CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SOUTH SAN FRANCISCO | 2023-09-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 839 |  | 1 |  | ACE DRILLING & EXCAVATION | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SAN MATEO | SOUTH SAN FRANCISCO | 2023-04-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 16 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2 |  | 2 |  | DISCOUNT PLUMBING | REDWOOD CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | SOUTH SAN FRANCISCO | 2023-04-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 16 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 26356 |  | 2 |  | MERCOZA | SAN JOSE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | SAN MATEO | WOODSIDE | 2023-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3905 |  | 1 |  | HOMEOWNER | WOODSIDE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | WOODSIDE | 2023-05-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | WOODSIDE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SAN MATEO | WOODSIDE | 2023-04-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 106 |  | 1 |  | HOMEOWNER | WOODSIDE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | CUPERTINO | 2023-09-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1625 |  | 1 |  | HOMEOWNER | CUPERTINO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | CUPERTINO | 2023-05-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1668 |  | 2 |  | HOMEOWNER | CUPERTINO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | CUPERTINO | 2023-08-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1298 |  | 1 |  | CORTECHNOLOGIES | HAYWARD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | CUPERTINO | 2023-03-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 784 |  | 1 |  | HOMEOWNER | CUPERTINO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | GILROY | 2023-08-22 | Third party excavation damage | Main | Polyethylene Pipe | Not Available | 2 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2603 |  | 0 |  | HAWKINS INFORMATION TECHNOLOGY | NA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | GILROY | 2023-11-29 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 50 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 14419 |  | 33 |  | BT FARMS | GILROY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | LOS ALTOS | 2023-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10804 |  | 1 |  | ALLIANCE INTERLOCKING PAVERS | MOUNTAIN VIEW | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | LOS ALTOS | 2023-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1358 |  | 1 |  | IBUILD | EAST PALO ALTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | LOS ALTOS | 2023-04-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | LOS ALTOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | LOS ALTOS | 2023-10-27 | Third party excavation damage | Main | Steel | Farm Equipment | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 21950 |  | 1 |  | BELLAGIO PAVERS | RICHMOND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | LOS ALTOS HILLS | 2023-11-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3755 |  | 1 |  | MS GARDENING INC. | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | LOS ALTOS HILLS | 2023-09-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2363 |  | 1 |  | AMERICAN LEAK DETECTION | LOS ALTOS HILLS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | LOS ALTOS HILLS | 2023-08-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1174 |  | 1 |  | FINCON INC. | LOS ALTOS HILLS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | LOS ALTOS HILLS | 2023-03-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 581 |  | 1 |  | C2R ENGINEERING | MOUNTAIN VIEW | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | SANTA CLARA | LOS GATOS | 2023-01-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 309 |  | 0 |  | GRANADA DESIGN AND CONSTRUCTION | LOS GATOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | LOS GATOS | 2023-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2527 |  | 1 |  | A. MUNOZ LANDSCAPE CONSTRUCTION INC. | MORGAN HILL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | LOS GATOS | 2023-10-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1515 |  | 1 |  | RR BUILDERS | SAN MARTIN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | LOS GATOS | 2023-11-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1404 |  | 1 |  | HOMEOWNER | LOS GATOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | LOS GATOS | 2023-05-03 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | DRUMMOND AND SONS INC | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | LOS GATOS | 2023-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MIKE COUNSIL PLUMBING | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | MILPITAS | 2023-05-04 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 1.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7826 |  | 10 |  | BORE ONE INC | MINOT | ND | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | SANTA CLARA | MORGAN HILL | 2023-02-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2960 |  | 1 |  | GOLDEN STATE UTILITY CO | FREMONT | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | SANTA CLARA | MORGAN HILL | 2023-12-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1047 |  | 1 |  | HOMEOWNER | MORGAN HILL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | MORGAN HILL | 2023-06-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 933 |  | 2 |  | HOMEOWNER | MORGAN HILL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | MORGAN HILL | 2023-12-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1459 |  | 0 |  | NEWPATH LANDSCAPE SERVICE INC. | MORGAN HILL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | MORGAN HILL | 2023-09-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2756 |  | 1 |  | TRUST CONSTRUCTION COMPANY | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | MORGAN HILL | 2023-08-05 | Third party excavation damage | Main | Polyethylene Pipe | Not Available | 1.25 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | PLATINUM ROOTER AND PLUMBING | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | MORGAN HILL | 2023-09-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2844 |  | 1 |  | HOMEOWNER | MORGAN HILL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | MORGAN HILL | 2023-09-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3814 |  | 1 |  | JV GREEN VIEW INC | TRACY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | MOUNTAIN VIEW | 2023-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1772 |  | 1 |  | SKYLINE LANDSCAPES | REDWOOD CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | MOUNTAIN VIEW | 2023-04-04 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1 |  | 2 |  | RUDOLPH & SLETTEN | SAN CARLOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | MOUNTAIN VIEW | 2023-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 500 |  | 1 |  | GOLDEN STATE MARBLE | MOUNTAIN VIEW | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2023-05-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7529 |  | 1 |  | J.A.R. UNDERGROUND ELECTRIC | SAN JOSE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2023-11-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3158 |  | 1 |  | HOMEOWNER | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2023-04-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | GARCIA''S ORNAMENTAL IRON WORKS | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2023-08-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3589 |  | 1 |  | J. MORAGA CONSTRUCTION | MERCED | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2023-10-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2131 |  | 1 |  | GOLDBAR BUILDERS | SONORA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2023-03-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2737 |  | 2 |  | ABODU | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2023-03-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2675 |  | 1 |  | HOMEOWNER | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2023-10-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 163 |  | 2 |  | JIMENEZ CONCRETE | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2023-05-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | SPV CONSTRUCTION | CUPERTINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2023-11-14 | Third party excavation damage | Main | Steel | Boring Equipment | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 32235 |  | 1 |  | EJ PLUMBING | SANTA CLARA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2023-02-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | BURTON DESIGN & CONSTRUCTION | LOS GATOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2023-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 3 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 133 |  | 0 |  | STOMPER COMPANY | HAYWARD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2023-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | NEW TECH PLUMBING | UNION CITY | CA | N | Y | Yes | Yes | No | Yes | No | No | No | Excavated Prior to positive response
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2023-09-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1864 |  | 1 |  | ALERT PLUMBING | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2023-02-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 11075 |  | 1 |  | PINNACLE GROUND WORKS | HARBOR CITY | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | LOCATING WIRE MISSING OR BROKEN
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2023-11-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2323 |  | 1 |  | HOMEOWNER | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2023-09-07 | Third party excavation damage | Main | Polyethylene Pipe | Not Available | 1.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7885 |  | 2 |  | HOMEOWNER | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2023-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4 |  | 1 |  | CAL COAST ELECTRIC | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2023-08-21 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6611 |  | 0 |  | DOYLES WORK CO | GILROY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2023-11-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1880 |  | 1 |  | ALFA ELECTRIC | CONCORD | CA | N | Y | Yes | Yes | No | No | No | No | No | Incorrect Information or Marks
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2023-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 0.5 | 0.38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2742 |  | 1 |  | MAYAS FENCES/ MARISOL 408-775-3988 | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2023-12-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1161 |  | 1 |  | FIX-IT PLUMBING | MILPITAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2023-10-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5068 |  | 2 |  | CHANDLER PLUMBING | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2023-01-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5000 |  | 1 |  | BAY MODULAR | OAKLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2023-05-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4 |  | 1 |  | BAILEY FENCE COMPANY | HAYWARD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2023-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 25000 |  | 1 |  | SUMMIT PROPERTIES & DEVELOPMENT CO. | CLARKSTON | MI | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2023-03-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1500 |  | 0 |  | BDS CONSTRUCTION GROUP | SAN JOSE, CA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2023-07-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3493 |  | 1 |  | HOMEOWNER | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2023-12-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 254 |  | 1 |  | LEWIS & TIBBITS | SAN JOSE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2023-06-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4137 |  | 1 |  | HOMEOWNER | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2023-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | UNLICENSED CONTRACTOR | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2023-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1025 |  | 1 |  | HOMEOWNER | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2023-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5000 |  | 2 |  | QUALITY BUILDER | SAN YSIDRO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2023-03-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1572 |  | 1 |  | QUALITY BUILDER | SAN YSIDRO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2023-01-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5000 |  | 1 |  | ORIGINS ELECTRIC | NA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2023-04-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HILLS LANSCAPING | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2023-10-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1973 |  | 1 |  | SUPER BUILDERS INC | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2023-05-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | JJR CONSTRUCTION | SAN MATEO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SAN JOSE | 2023-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6106 |  | 1 |  | INFINIUM SOLAR | CAMPBELL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN MARTIN | 2023-01-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 2 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 153 |  | 0 |  | HOMEOWNER | SAN MARTIN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SAN MARTIN | 2023-04-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 351 |  | 0 |  | CORRALITOS CREEK LLC | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SANTA CLARA | 2023-10-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3698 |  | 2 |  | CITY OF SANTA CLARA | SANTA CLARA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | SANTA CLARA | SANTA CLARA | 2023-03-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2031 |  | 5 |  | TIERRA GROUP INC | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SANTA CLARA | 2023-04-25 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3303 |  | 5 |  | C. HAMMOND CONSTRUCTION | RICHMOND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SANTA CLARA | 2023-06-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3865 |  | 1 |  | GENMOR PLUMBING | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SANTA CLARA | 2023-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4340 |  | 2 |  | SILICON VALLEY POWER | SANTA CLARA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | SANTA CLARA | SANTA CLARA | 2023-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4383 |  | 1 |  | A&B CONSTRUCTION | OAKLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Inadequate Excavation Practices
Pacific Gas and Electric | N | SANTA CLARA | SANTA CLARA | 2023-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | SMART LILY BUILDER | CUPERTINO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SARATOGA | 2023-09-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1916 |  | 0 |  | JESUS TORRES CONCRETE | MORGAN HILL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SARATOGA | 2023-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | COBALT POWER SYSTEMS INC. | MOUNTAIN VIEW | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | STANFORD | 2023-04-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 31 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4 |  | 1 |  | MCGUIRE HESTER | ALAMEDA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SUNNYVALE | 2023-07-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MODERN LANDSCAPE | CAMPBELL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SUNNYVALE | 2023-10-17 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6244 |  | 2 |  | SILICON VALLEY TELECOM | SAN JOSE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CLARA | SUNNYVALE | 2023-05-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | SUNNYVALE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SUNNYVALE | 2023-09-12 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2376 |  | 0 |  | AMF FIRE | SANTA CLARA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SUNNYVALE | 2023-08-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2645 |  | 2 |  | STANLEY TEAM CONSTRUCTION | CUPERTINO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CLARA | SUNNYVALE | 2023-12-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Directional Drilling | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5112.32 |  | 1 |  | SAFETY FIRST ELECTRIC | SUNNYVALE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | APTOS | 2023-01-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 89 |  | 1 |  | SANTANA PAVING & GRADING | CAPITOLA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CRUZ | APTOS | 2023-07-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | UNLICENSED CONTRACTOR | NA | CA | N | Y | Yes | Yes | No | Yes | No | No | Yes | No USA Ticket
Pacific Gas and Electric | N | SANTA CRUZ | APTOS | 2023-02-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 78 |  | 1 |  | HOMEOWNER | SANTA CRUZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | APTOS | 2023-07-27 | Third party excavation damage | Not Available | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1024 |  | 1 |  | TERRA NOVA ECOLOGICAL LANDSCAPING | N/A | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | APTOS | 2023-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | GARCIA CONCRETE CONSTRUCTION | WATSONVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | APTOS | 2023-09-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 822 |  | 1 |  | PLANT LANDSCAPE | CAPITOLA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Failed to Dig with Care
Pacific Gas and Electric | N | SANTA CRUZ | APTOS | 2023-11-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Farm Equipment | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 907 |  | 1 |  | HOMEOWNER | APTOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | APTOS | 2023-01-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1277 |  | 1 |  | HOMEOWNER | APTOS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | APTOS | 2023-08-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MR ROOTER | SANTA CRUZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | APTOS | 2023-11-09 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4009 |  | 11 |  | LINDEX EXCAVATING | SOQUEL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SANTA CRUZ | BEN LOMOND | 2023-06-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1244 |  | 1 |  | HOMEOWNER | BOULDER CREEK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | BEN LOMOND | 2023-12-06 | Third party excavation damage | Main | Steel | Hand Tools | 2 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 12790 |  | 4 |  | JMB CONSTRUCTION | SOUTH SAN FRANCISCO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | BOULDER CREEK | 2023-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3018 |  | 1 |  | HOMEOWNER | BOULDER CREEK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CRUZ | BROOKDALE | 2023-07-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4824 |  | 0 |  | ANDERSON PACIFIC ENGINEERING CONSTRUCTION INC | SANTA CLARA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CRUZ | CAPITOLA | 2023-09-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1550 |  | 1 |  | ABERLE CONCRETE | FREMONT | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | CAPITOLA | 2023-04-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6 |  | 4 |  | TAVIO''S GENERAL CONST. | SCOTTS VALLEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | CORRALITOS | 2023-05-05 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | BUILT RITE CONSTRUCTION | WATSONVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | CORRALITOS | 2023-10-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | PAXTON LAMDACAPING | MONTEREY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | FELTON | 2023-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 7 |  | HOMEOWNER | FELTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | FELTON | 2023-02-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1000 |  | 1 |  | HOMEOWNER | FELTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | FREEDOM | 2023-05-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | MCKIM CONSTRUCTION | GILROY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CRUZ | LA SELVA BEACH | 2023-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2705 |  | 1 |  | RAM CONSTRUCTION | WATSONVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | MOUNT HERMON | 2023-07-28 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2181 |  | 2 |  | MTM TRUCK AND TRACTOR | BEN LOMOND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | MOUNT HERMON | 2023-06-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 985 |  | 1 |  | HOMEOWNER | FELTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2023-10-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1326 |  | 1 |  | SANTA CRUZ GREEN BUILDERS | SANTA CRUZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2023-09-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1848 |  | 1 |  | EVO-FLOW PLUMBING & DRAIN | SANTA CRUZ | CA | N | Y | No | No | No | No | No | No | No | No USA Ticket
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2023-02-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1000 |  | 1 |  | GREEN FOLIAGE UNLIMITED | SAN JOSE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2023-01-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1929 |  | 1 |  | BLACK DIAMOND PAVER STONES & LANDSCAP | SAN JOSE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | OTHER
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2023-05-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | SANTA CRUZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2023-06-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 481 |  | 2 |  | MCGUIRE & HESTER | ALAMEDA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2023-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 173 |  | 1 |  | MCGUIRE & HESTER | ALAMEDA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2023-11-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2062 |  | 1 |  | HOMEOWNER | SANTA CRUZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2023-07-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | SANDMAN CONSTRUCTION | SANTA CRUZ | CA | N | Y | No | No | No | No | No | No | No | EXPIRED USA TICKET
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2023-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1510 |  | 1 |  | CRESTLINE CONSTRUCTION | SANTA CRUZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2023-05-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | AKD MANAGEMENT | REDWOOD CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2023-08-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3767 |  | 1 |  | CLOVERLEAF PLUMBING | CAPITOLA | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2023-03-16 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1.25 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 99 |  | 5 |  | BELLOWS PLUMBING | SANTA CRUZ | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | OTHER
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2023-01-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 88 |  | 1 |  | HOMEOWNER | SANTA CRUZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2023-12-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2172 |  | 1 |  | CYPRESS COAST FENCE | WATSONVILLE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2023-03-07 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1619 |  | 1 |  | ALBERT''S PLUMBING | SANTA CRUZ | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | OTHER
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2023-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1029 |  | 1 |  | BUDDY GRIGGS PLUMBING | SANTA CRUZ | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2023-11-20 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2706 |  | 4 |  | PROGRESSIVE LANDSCAPES INC | FOLSOM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2023-03-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6191 |  | 1 |  | HOMEOWNER | SANTA CRUZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2023-08-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1004 |  | 1 |  | GRANITEROCK | WATSONVILLE | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CRUZ | SANTA CRUZ | 2023-01-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | SANTA CRUZ | CA | N | Y | No | No | No | No | No | No | No | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SANTA CRUZ | SCOTTS VALLEY | 2023-05-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2378 |  | 0 |  | NA | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | SCOTTS VALLEY | 2023-12-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1907 |  | 1 |  | FALLCREEK LANDSCAPING | SCOTT''S VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Dig with Care
Pacific Gas and Electric | N | SANTA CRUZ | SCOTTS VALLEY | 2023-07-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | RDR DESIGN AND BUILD | SANTA CRUZ | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Dig with Care
Pacific Gas and Electric | N | SANTA CRUZ | SOQUEL | 2023-10-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1257 |  | 1 |  | HOMEOWNER | SOQUEL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | SOQUEL | 2023-07-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | WORK BENCH CONSTRUCTION | SOQUEL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SANTA CRUZ | TWIN LAKES | 2023-09-18 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | NA | NA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | ABANDONED/DEACTIVATED FACILTY ISSUE
Pacific Gas and Electric | N | SANTA CRUZ | TWIN LAKES | 2023-05-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | SANTA CRUZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | TWIN LAKES | 2023-04-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6 |  | 1 |  | SPACE CAMP STUDIO | SANTA CRUZ | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | WATSONVILLE | 2023-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1450 |  | 1 |  | HOMEOWNER | WATSONVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | WATSONVILLE | 2023-07-28 | Third party excavation damage | Not Available | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1956 |  | 1 |  | HOMEOWNER | WATSONVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | WATSONVILLE | 2023-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3508 |  | 1 |  | HOMEOWNER | WATSONVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | WATSONVILLE | 2023-07-03 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 50 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DOBLER & SONS | WATSONVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SANTA CRUZ | WATSONVILLE | 2023-08-11 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9589 |  | 0 |  | FAR WEST SAFETY | LODI, CA | CA | N | Y | Yes | No | No | No | No | No | No | Excavated prior to legal excavation start date and time
Pacific Gas and Electric | N | SANTA CRUZ | WATSONVILLE | 2023-05-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | KINGS GARAGE DOORS | SALINAS | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SHASTA | ANDERSON | 2023-01-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 53 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1000 |  | 0 |  | HOMEOWNER | REDDING | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | OTHER
Pacific Gas and Electric | N | SHASTA | ANDERSON | 2023-04-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 53 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1402 |  | 0 |  | NORTHSTATE EXCAVATING | COTTONWOOD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT INFORMATION OR MARKS
Pacific Gas and Electric | N | SHASTA | ANDERSON | 2023-04-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 53 | Y | N | Y | N | 0 | 0 |  | 0 | 0 |  | 6341 |  | 1 |  | HOMEOWNER | ANDERSON | CA | N | Y | No | No | No | No | No | No | No | Structure fire damaged riser and meter
Pacific Gas and Electric | N | SHASTA | REDDING | 2023-12-20 | Third party excavation damage | Main | Polyethylene Pipe | Trencher | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6530 |  | 44 |  | HOMEOWNER | REDDING | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SHASTA | REDDING | 2023-09-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1573 |  | 2 |  | JOHN?S TREE | REDDING | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SHASTA | REDDING | 2023-07-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2420 |  | 0 |  | UNLICENSED CONTRACTOR | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SHASTA | REDDING | 2023-04-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 27 |  | 1 |  | BROCKMAN OUTDOOR SERVICES | REDDING | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SHASTA | SHASTA LAKE | 2023-07-05 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 53 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SUNRISE EXCAVATING | REDDING | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | SHASTA | SHASTA LAKE | 2023-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 53 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | SHAST LAKE CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | BENICIA | 2023-04-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2 |  | 1 |  | R G CARTER COMPANY | VALLEJO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | BENICIA | 2023-02-13 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2000 |  | 8 |  | KEREX ENGINNERING INC | PLEASANT HILL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SOLANO | DIXON | 2023-10-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1577 |  | 2 |  | HOMEOWNER | DIXON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | DIXON | 2023-12-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1163 |  | 0 |  | LISTER CONSTRUCTION | VACAVILLE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | SOLANO | DIXON | 2023-08-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1520 |  | 1 |  | HOMEOWNER | DIXON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | DIXON | 2023-10-16 | Third party excavation damage | Transmission Line in a non-HCA area | Steel | Backhoe/Trackhoe | 10 | 792 | 597 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9981 |  | 0 |  | HOMEOWNER | DIXON | CA | N | Y | No | No | No | No | Yes | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | FAIRFIELD | 2023-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | FAIRFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | FAIRFIELD | 2023-10-09 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1.25 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3472 |  | 2 |  | ADVANCED PLUMBING | VACAVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FAILED TO DIG WITH CARE
Pacific Gas and Electric | N | SOLANO | FAIRFIELD | 2023-09-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1078 |  | 1 |  | LEGACY ELECTRICAL SERVICE AND CONSTRUCTION | VACAVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SOLANO | FAIRFIELD | 2023-09-27 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1316 |  | 0 |  | UNDERGROUND CONSTRUCTION COMPANY | BENICIA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Incorrect Facility Records / Maps
Pacific Gas and Electric | N | SOLANO | FAIRFIELD | 2023-09-27 | Third party excavation damage | Main | Steel | Not Available | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3916 |  | 0 |  | UNDERGROUND CONSTRUCTION COMPANY | BENICIA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | SOLANO | FAIRFIELD | 2023-05-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | COOKIE CUTTER POOLS | FOLSOM | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | SUISUN CITY | 2023-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | SUISUN CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | VACAVILLE | 2023-04-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 51 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2690 |  | 2 |  | CALIFORNIA TRENCHLESS INC. | HAYWARD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | SOLANO | VACAVILLE | 2023-03-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 51 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5049 |  | 12 |  | ARONSON LANDSCAPE | AUBURN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | VACAVILLE | 2023-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 51 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | UNDERGROUND CONSTRUCTION COMPANY | BENECIA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SOLANO | VALLEJO | 2023-06-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3931 |  | 2 |  | HOMEOWNER | VALLEJO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | VALLEJO | 2023-04-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | VALLEJO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | VALLEJO | 2023-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 19 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | UNLICENSED CONTRACTOR | VALLEJO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SOLANO | VALLEJO | 2023-09-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1207 |  | 2 |  | HOMEOWNER | AMERICAN CANYON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | COTATI | 2023-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1210 |  | 1 |  | HOMEOWNER | COTATI | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | COTATI | 2023-03-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2000 |  | 1 |  | HOMEOWNER | COTATI | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | FORESTVILLE | 2023-08-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2439 |  | 1 |  | ARGONOUT CONSTRUCTORS | SANTA ROSA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | GLEN ELLEN | 2023-11-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4026 |  | 0 |  | HOMEOWNER | GLEN ELLEN | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | GLEN ELLEN | 2023-05-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | WEST SIDE PAVING | PETALUMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | HEALDSBURG | 2023-11-16 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7138 |  | 6 |  | HARRIS CONSTRUCTION | PETALUMA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | SONOMA | HEALDSBURG | 2023-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 187 |  | 0 |  | DEVINCENZI CONTRACTOR | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | PENNGROVE | 2023-05-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 180 |  | 1 |  | COGGINS FENCE | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | PETALUMA | 2023-10-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3179 |  | 1 |  | GRANITE ROCK | WATSONVILLE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | PETALUMA | 2023-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1837 |  | 0 |  | STUDIO 101 CORP | PETALUMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | PETALUMA | 2023-05-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2627 |  | 1 |  | GHILOTTI | PETALUMA | CA | N | Y | Yes | Yes | Yes | Yes | Yes | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | PETALUMA | 2023-07-20 | Third party excavation damage | Main | Steel | Hand Tools | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | ROOTER HERO | ROHNERT PARK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | PETALUMA | 2023-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 577 |  | 0 |  | DIRT DUDES EXCAVATING INC | FULTON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | ROHNERT PARK | 2023-09-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 587 |  | 1 |  | A1 ELECTRICAL INC. | SACRAMENTO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment
Pacific Gas and Electric | N | SONOMA | ROHNERT PARK | 2023-08-10 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 4 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 15772 |  | 5 |  | TAK COMMUNICATIONS | SACRAMENTO | CA | N | Y | Yes | No | Yes | Yes | Yes | Yes | Yes | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment
Pacific Gas and Electric | N | SONOMA | ROHNERT PARK | 2023-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2061 |  | 1 |  | CABLECOM | SANTA CLARA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2023-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 831 |  | 0 |  | FLORES PAVING | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2023-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2446 |  | 1 |  | HOMEOWNER | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2023-06-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1 |  | 1 |  | SHOOK AND WALLER CONSTRUCTION | WINDSOR | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2023-04-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | GHILOTTI BROS | SAN RAFAEL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2023-11-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2767 |  | 0 |  | JLP LANDSCAPE CONTRACTONG INC | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2023-12-22 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6039 |  | 1 |  | HOMEOWNER | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2023-02-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2023-08-30 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | TERRACON CONSTRUCTION | HEALDSBURG | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2023-04-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1 |  | 0 |  | PASEO VISTA INC. | WINDSOR | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2023-12-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1947 |  | 1 |  | ARGONAUT | SANTA ROSA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Failed to Dig with Care
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2023-01-12 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | R D PAVING CONSTRUCTION | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2023-09-05 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1.25 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1309 |  | 1 |  | ADVANCED TEL COM | PLAIN CITY | UT | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Failed to Dig with Care
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2023-02-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | JHA REMEDIATION | SACRAMENTO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | OTHER
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2023-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4812 |  | 1 |  | HOMEOWNER | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2023-03-03 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5306 |  | 2 |  | LIGHTHOUSE AUTOMOTIVE EQUIPMENT | BENICIA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2023-01-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 951 |  | 1 |  | HOMEOWNER | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2023-01-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1414 |  | 0 |  | RCX | NA | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2023-09-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2781 |  | 1 |  | HOMEOWNER | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2023-09-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 984 |  | 1 |  | THOMPSON''S EXCAVATING | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2023-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2436 |  | 1 |  | HOMEOWNER | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2023-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3908 |  | 1 |  | HOMEOWNER | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2023-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 350 |  | 1 |  | HOMEOWNER | SANTA ROSA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SANTA ROSA | 2023-09-06 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2340 |  | 0 |  | GHILLOTI BROS | SAN RAFAEL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | SEBASTOPOL | 2023-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3027 |  | 1 |  | HOMEOWNER | SEBASTOPOL | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment
Pacific Gas and Electric | N | SONOMA | SEBASTOPOL | 2023-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2182 |  | 1 |  | HOMEOWNER | SEBASTOPOL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Dig with Care
Pacific Gas and Electric | N | SONOMA | SEBASTOPOL | 2023-08-22 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | SEBASTOPOL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SEBASTOPOL | 2023-08-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5778 |  | 1 |  | HOMEOWNER | SEBASTOPOL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SEBASTOPOL | 2023-11-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2797 |  | 0 |  | BROTHERS CONTSRUCTION | SEBASTOPOL | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SONOMA | 2023-09-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 42 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 12762 |  | 1 |  | HOMEOWNER | SONOMA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SONOMA | 2023-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | DAHER DEVELOPMENT, INC. | GLEN ALLEN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SONOMA | SONOMA | 2023-09-06 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 42 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10321 |  | 1 |  | WINE COUNTRY LANDSCAPING | SONOMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SONOMA | 2023-03-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3177 |  | 0 |  | HOMEOWNER | SONOMA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SONOMA | SONOMA | 2023-09-20 | Third party excavation damage | Main | Polyethylene Pipe | Not Available | 2 | 50 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4150 |  | 7 |  | FARWEST SAFETY INC. | LODI | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | SONOMA | WINDSOR | 2023-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1303 |  | 2 |  | REDWOOD RESIDENTIAL FENCE. JUAN NUNEZ | SANTA ROSA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Dig with Care
Pacific Gas and Electric | N | STANISLAUS | CERES | 2023-07-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | UNITED PAVING | CERES | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Failed to Expose Facility with Hand Tools Prior to Use of Power-Driven Excavation Equipment or Boring Equipment
Pacific Gas and Electric | N | STANISLAUS | CERES | 2023-12-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2799 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | CERES | 2023-02-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | HOMEOWNER | CERES | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | CERES | 2023-09-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2115 |  | 1 |  | HOMEOWNER | CERES | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | CERES | 2023-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3325 |  | 1 |  | HOMEOWNER | CERES | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | CERES | 2023-05-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | HOMEOWNER | CERES | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | CERES | 2023-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1625 |  | 0 |  | ADAMS UNDERGROUND | WATERFORD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | CERES | 2023-12-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 890 |  | 1 |  | HOMEOWNER | CERES | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | DENAIR | 2023-10-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 937 |  | 1 |  | HOMEOWNER | DENAIR | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | DENAIR | 2023-11-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2993 |  | 1 |  | HOMEOWNER | DENAIR | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | EMPIRE | 2023-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5361 |  | 7 |  | KIRKES ELECTIRC | TURLOCK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | GRAYSON | 2023-07-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2493 |  | 1 |  | DA WOOD CONSTRUCTION, INC. | OAKDALE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | GRAYSON | 2023-08-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1986 |  | 1 |  | D.A. WOOD CONSTRUCTION | OAKDALE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | HUGHSON | 2023-09-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 52 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2689 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | KEYES | 2023-11-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2088 |  | 1 |  | J.A. HERNANDEZ CONSTRUCTION | ATWATER | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2023-03-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 58 | 52 | Y | N | Y | N | 0 | 0 |  | 0 | 0 |  | 1013 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2023-04-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2023-04-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2023-06-27 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6203 |  | 3 |  | PHASE 1 CONSTRUCTION | ATWATER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2023-12-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2175 |  | 0 |  | A TEEPLES PLUMBING | CERES | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2023-05-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | RANGER PIPLINES | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2023-01-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2000 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2023-09-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 162 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2023-03-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3500 |  | 1 |  | RANGER PIPELINE | SAN FRANCISCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2023-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | TITANIUM SOLAR | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2023-12-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2820 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2023-10-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1669 |  | 1 |  | SOLO CONCRETE | RIPON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2023-05-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | HUMPHREY PLUMBING | TURLOCK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2023-03-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3000 |  | 1 |  | 7-11 MATERIALS | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2023-07-25 | Third party excavation damage | Miscellaneous/Other | Steel | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3310 |  | 0 |  | CITY OF MODESTO | MODESTO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2023-03-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3000 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2023-06-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1823 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2023-06-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Farm Equipment | 0.5 | 58 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2117 |  | 0 |  | STANISLAUS COUNTY | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2023-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1343 |  | 0 |  | MILLCREEK ELECTRICAL | CERES | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2023-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1387 |  | 1 |  | TGE HONEY DO GUY/ JEFF PILLOW | MODESTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2023-04-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2023-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2585 |  | 0 |  | KNIFE RIVER CONSTRUCTION | SUTTER CREEK | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2023-05-04 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 4 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 25149 |  | 3 |  | CITY OF MODESTO | MODESTO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2023-11-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2075 |  | 0 |  | MODESTO SAND & GRAVEL | MODESTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2023-10-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2212 |  | 22 |  | LANDSCAPE DEVELOPMENT INC | VALENCIA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2023-12-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1084 |  | 2 |  | MOZINGO CONSTRUCTION | OAKDALE | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2023-04-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4 |  | 2 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2023-11-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2279 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2023-09-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1258 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2023-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2023-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1500 |  | 2 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2023-09-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 402 |  | 1 |  | VJR CONSTRUCTION | EAST PALO ALTO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Failed to Dig with Care
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2023-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 506 |  | 2 |  | VGR CONSTRCTION | EAST PALO ALTO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2023-10-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1088 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2023-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2023-12-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1567 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2023-09-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1154 |  | 2 |  | HOMEOWNER | MODESTO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2023-04-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2023-04-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | GEORGE REID INC | MODESTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2023-05-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2023-04-12 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | NBC FARMS | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2023-03-30 | Third party excavation damage | Main | Steel | Grader/Scraper | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 8000 |  | 1 |  | MOUNTAIN CASCADE INC. | LIVERMORE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2023-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4 |  | 1 |  | ST FRANCIS ELECTRIC | SAN LEANDRO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | MODESTO | 2023-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 989 |  | 1 |  | SKYLINE SMART ENERGY | DOWNEY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | NEWMAN | 2023-07-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | RICHTER FENCE. JOSE ALCARAZ | RIPON | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | NEWMAN | 2023-09-18 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3304 |  | 2 |  | HENSLEY PAVING | WATERFORD | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | OAKDALE | 2023-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1874 |  | 1 |  | OCHOA''S BACKHOE SERVICES | ANAHEIM | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | OAKDALE | 2023-09-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1392 |  | 1 |  | T/A GENERAL ELECTRIC INC. | MODESTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | OAKDALE | 2023-09-08 | Third party excavation damage | Main | Polyethylene Pipe | Not Available | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2472 |  | 0 |  | AC INDUSTRIES, INC. | MERCED | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | OAKDALE | 2023-06-09 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4686 |  | 28 |  | ROLFE CONSTRUCTION | ATWATER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | OAKDALE | 2023-12-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2786 |  | 2 |  | HOMEOWNER | RIVERBANK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | OAKDALE | 2023-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1605 |  | 0 |  | HOMEOWNER | OAKDALE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | OAKDALE | 2023-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1.25 | 0.5 | 0.38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | HOMEOWNER | OAKDALE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | OAKDALE | 2023-01-28 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2827 |  | 1 |  | PG&E | STOCKTON | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | PATTERSON | 2023-05-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | WESTLY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | PATTERSON | 2023-01-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 2 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | 24/7 CONCRETE | EMERYVILLE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | OTHER
Pacific Gas and Electric | N | STANISLAUS | PATTERSON | 2023-07-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 0.75 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | UNITED PAVEMENT MANAGEMENT | HUGHSON | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | RIVERBANK | 2023-06-19 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | STEVES EXCAVATING | LOOMIS CORNERS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | STANISLAUS | RIVERBANK | 2023-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | HENSLEY PAVING | HICKMAN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | TURLOCK | 2023-02-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1500 |  | 2 |  | HOMEOWNER | TURLOCK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | TURLOCK | 2023-03-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3000 |  | 2 |  | HOMEOWNER | TURLOCK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | TURLOCK | 2023-04-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 60 | 54 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | TURLOCK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | TURLOCK | 2023-06-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1181 |  | 2 |  | HOMEOWNER | TURLOCK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | TURLOCK | 2023-04-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | HOMEOWNER | TURLOCK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | TURLOCK | 2023-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 353 |  | 2 |  | TRIPLE J CONSTRUCTION | CERES | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | TURLOCK | 2023-05-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 1 |  | HOMEOWNER | TURLOCK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | STANISLAUS | TURLOCK | 2023-09-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1157 |  | 0 |  | TRADEMARK POOL AND SPA | TURLOCK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | STANISLAUS | TURLOCK | 2023-05-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 2 |  | ARIA GENERAL BUILDING | TURLOCK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | TURLOCK | 2023-03-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2500 |  | 1 |  | HOMEOWNER | TURLOCK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | TURLOCK | 2023-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1993 |  | 1 |  | HOMEOWNER | TURLOCK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | TURLOCK | 2023-02-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3000 |  | 1 |  | HOMEOWNER | TURLOCK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | TURLOCK | 2023-03-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | Y | N | 0 | 0 |  | 0 | 0 |  | 1071 |  | 1 |  | HOMEOWNER | TURLOCK | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | STANISLAUS | WESTLEY | 2023-06-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1841 |  | 2 |  | MID CAL PIPELINE | MERCED | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SUTTER | LIVE OAK | 2023-06-14 | Third party excavation damage | Main | Polyethylene Pipe | Grader/Scraper | 2 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | FRANKLIN CONSTRUCTION | CHICO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SUTTER | LIVE OAK | 2023-06-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4210 |  | 1 |  | FRANKLIN CONSTRUCTION | CHICO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SUTTER | LIVE OAK | 2023-04-04 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 287 |  | 0 |  | JAUN''S EXCAVATION SERVICE | OLIVEHURST | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SUTTER | SUTTER | 2023-01-23 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 80 |  | 1 |  | HOMEOWNER | YUBA CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SUTTER | YUBA CITY | 2023-07-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | MAVEN UTILITY GROUP | YUBA CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SUTTER | YUBA CITY | 2023-12-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4004 |  | 1 |  | TOP RAIL FENCE CORPORATION | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SUTTER | YUBA CITY | 2023-07-12 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MORELLO CONSTRUCTION | CHILOQUIN | OR | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SUTTER | YUBA CITY | 2023-05-07 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | HOMEOWNER | YUBA CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SUTTER | YUBA CITY | 2023-09-26 | Third party excavation damage | Main | Polyethylene Pipe | Not Available | 2 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2613 |  | 0 |  | SMITH PLUMBING | MODESTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | SUTTER | YUBA CITY | 2023-09-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 920 |  | 1 |  | MORELLO CONSTRUCTION | KLAMATH FALLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | SUTTER | YUBA CITY | 2023-04-03 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7021 |  | 0 |  | PERRIN CONSTRUCTION | REDDING | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | TEHAMA | CORNING | 2023-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 53 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2542 |  | 2 |  | BETTER EARTH ELECTRIC INC | NA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | TEHAMA | CORNING | 2023-09-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 53 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2404 |  | 0 |  | UNITED BUILDING CONTRACTORS INC | CHICO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | TEHAMA | GERBER | 2023-04-03 | Operator excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 23 |  | 0 |  | HENKELS & MCCOY INC | FRESNO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | TEHAMA | RED BLUFF | 2023-09-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 40 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2747 |  | 1 |  | HOMEOWNER | ORLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | TRINITY | MAD RIVER | 2023-07-09 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 1.25 | 35 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 15 |  | HOMEOWNER | MAD RIVER | CA | N | Y | No | No | No | No | No | No | No | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | TUOLUMNE | MILL VALLEY | 2023-05-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1796 |  | 1 |  | INTERACTIVE LANDSCAPES | SAN PABLO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | TUOLUMNE | STRAWBERRY | 2023-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 57 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3707 |  | 14 |  | TILTON PACIFIC CONSTRUCTION | SANTA CLARA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | FACILITY WAS NOT LOCATED OR MARKED
Pacific Gas and Electric | N | YOLO | DAVIS | 2023-07-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CHRISTOPHER CRAWFORD CONSTRUCTION | DAVIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to Maintain Field Marks or Request Re-Marks When No Longer Visible
Pacific Gas and Electric | N | YOLO | DAVIS | 2023-04-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2 |  | 1 |  | MEGA POWER ELECTRIC | LOS ANGELES | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YOLO | ESPARTO | 2023-01-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2000 |  | 1 |  | ESPARTO BROADBAND | ESPARTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YOLO | ESPARTO | 2023-11-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2540 |  | 2 |  | RML PAVING | SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YOLO | WEST SACRAMENTO | 2023-11-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5128 |  | 1 |  | MASTEC | SACRAMENTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | YOLO | WEST SACRAMENTO | 2023-03-23 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 21905 |  | 1 |  | UCI CONSTRUCTION | FAIRFIELD | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YOLO | WEST SACRAMENTO | 2023-09-07 | Third party excavation damage | Main | Polyethylene Pipe | Not Available | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5494 |  | 6 |  | NUNEZ CONSTRUCTION | WEST SACRAMENTO | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YOLO | WEST SACRAMENTO | 2023-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | B&M BUILDERS | RANCHO CORDOVA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | YOLO | WINTERS | 2023-01-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 10 |  | ROBO MAN PLUMBING | VACAVILLE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YOLO | WOODLAND | 2023-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3311 |  | 2 |  | HOMEOWNER | WOODLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YOLO | WOODLAND | 2023-08-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 6361 |  | 0 |  | PACIFIC UTILITY CONSTRUCTION | WOODLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | INCORRECT FACILITY RECORDS\MAPS
Pacific Gas and Electric | N | YOLO | WOODLAND | 2023-05-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2865 |  | 1 |  | PACIFIC UTILITY CONSTRUCTION | WOODLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | FACILITY MARKINGS INADEQUATE
Pacific Gas and Electric | N | YOLO | WOODLAND | 2023-06-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1393 |  | 0 |  | BIG S ASPHALT | YUBA CITY | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YOLO | WOODLAND | 2023-04-14 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 105 |  | 0 |  | CIMAS LANDSCAPING | RANCHO CORDOVA | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YOLO | WOODLAND | 2023-11-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 1 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3839 |  | 1 |  | MONTOY LANDSCAPING | WOODLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YUBA | OLIVEHURST | 2023-02-17 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 3 | 54 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 25614 |  | 0 |  | LAMON | YUBA CITY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | INADEQUATE EXCAVATION PRACTICES
Pacific Gas and Electric | N | YUBA | OLIVEHURST | 2023-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1919 |  | 2 |  | LAMON CONSTRUCTION | YUBA CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EXCAVATOR FAILURE TO USE HAND TOOLS
Pacific Gas and Electric | N | YUBA | OLIVEHURST | 2023-06-01 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2565 |  | 0 |  | HOMEOWNER | ANTELOPE | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
Pacific Gas and Electric | N | YUBA | WHEATLAND | 2023-01-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 56 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 194 |  | 0 |  | HOMEOWNER | WHEATLAND | CA | N | Y | No | No | No | No | No | No | No | USA NOT CALLED
San Diego Gas and Electric | N | SAN DIEGO | ALPINE | 2023-11-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | LIBERTY CHARTER HIGH STAFF | ALPINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Gas line had been damaged by a student while digging to install a pole and sign with a shovel.
San Diego Gas and Electric | N | SAN DIEGO | BONITA | 2023-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CARLOS MARTINEZ | BONITA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Carlos stated he was hired by Manuel to trench from the front yard to the rear of property to install plumbing. Carlos explained while excavating in the front yard with an electric hammer, the 1/2" joint gas service was damaged. Carlos stated he was not fully aware of Dig Alert law and does not have a valid USA ticket.
San Diego Gas and Electric | N | SAN DIEGO | BONITA | 2023-02-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ELITE LIVING & REMODELING | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Trenching with shovel and damaged a ï¿½ï¿½ï¿½inch plastic gas service.
San Diego Gas and Electric | N | SAN DIEGO | BONITA | 2023-11-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | MOUNTAIN VIEW | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging to plant a tree when he struck the gas.
San Diego Gas and Electric | N | SAN DIEGO | CARDIFF | 2023-07-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | BYLDIN HOMES INC | ENCINITAS | CA | N | Y | No | No | Yes | No | No | Yes | Yes | Digging with a sharp shooter when he hit the gas.
San Diego Gas and Electric | N | SAN DIEGO | CARDIFF-BY-THE-SEA | 2023-11-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | ADOLFO NUNEZ-CONTRACTOR | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging to plant a tree when he managed to hit the gas.
San Diego Gas and Electric | N | SAN DIEGO | CARDIFF-BY-THE-SEA | 2023-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | ELEVATION 92 CONSTRUCTION SERVICES | DEL MAR | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Mike New statement on May 12th at 1:00pm that he was chipping away the concrete when he hit the 3/4" stl that was imbedded in the concrete.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2023-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | LAEL LEONE | CARLSBAD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Lael Leone stated on June 30th at 4:59 pm that he was pulling the tree trunk out from the ground when he cracked the gas line.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2023-02-27 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | LEO VASQUEZ LANDSCAPING | CARLSBAD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hand digging and used an axe to cut away the tree root and hit the gas line in the root.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2023-11-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | Y | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DARIN WILLIAMSON | CARLSBAD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Gas line had been damaged while excavating to replace his fence with a shovel in his front yard.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2023-09-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | DOHERTY CONCRETE | MORGAN HILL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Knew the gas was there and he happen to yank on it with the mini excavator while removing roots. He also stated that the marks were accurate and it was flagged out and painted on the ground before excavation.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2023-02-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | GLENN MACGRAY | CARLSBAD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Cutting to replace damaged drain and cut into the gas line with Hackzall.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2023-10-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | THAT GUY CONSTRUCTION | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Excavating to tie into the water service when the unmarked 1/2" joint plastic service was damaged with an electric jackhammer.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2023-10-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | THAT GUY CONSTRUCTION | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | NA
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2023-04-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | WG CONSTRUCTION INC | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging with a shovel when the gas was hit.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2023-10-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | THE ENERGY COMPANY | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Putting a 8ft ground rod when he manage to damage the gas.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2023-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | OLIVENHAIN WATER DISTRICT | ENCINITAS | CA | N | Y | No | No | Yes | No | No | Excavator provided no markings for the proposed excavation on site. | No | Olivenhain Water District crew stated the gas line had been damaged while using probing rod by the water meter to install cathodic protection.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2023-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | RINCON | ESCONDIDO | CA | N | Y | No | No | Yes | No | No | Excavator provided no markings for the proposed excavation on site. | No | Greg Whilock was grading and hit the gas. Didn''t know it was in the area.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2023-07-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ECE INC | SAN MARCOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Trenching with a shovel close to the meter when he hit the gas.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2023-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SIM ENGINEERING | FALLBROOK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Digging to expose the gas when she managed to damage it.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2023-11-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ONE SOURCE STONE | VICTORVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Digging for a panel upgrade when he hit the gas.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2023-07-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | LANDERS ELECTRIC | VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Was digging with a shovel when he hit the gas.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2023-02-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | PAR CONSTRUCTION CO | CARLSBAD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging with a shovel and hit the gas line.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2023-06-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 4 |  | PEREZ CONSTRUCTION GROUP LLC | ROCK SPRINGS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Spoke with Ramon Perez of Perez Construction Group who stated his team was attempting to run a new conduit for fiber installation when the grundo boring tool damaged the 2" plastic gas main in the sidewalk. Ramon said the 2" plastic gas main was not potted for or exposed prior to boring.
San Diego Gas and Electric | N | SAN DIEGO | CARLSBAD | 2023-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | BCS BUILDERS | SANTA ANA | CA | N | Y | Yes | No | Yes | No | No | Yes | Yes | Bodie Suter stated that he knew the gas was there and still managed to hit it.
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2023-06-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | DREAM POOLS | BONITA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Carlos explained he was attempting to remove a tree stump located next to the gas MSA when he hit the 1/2" plastic gas service with a shovel. Carlos stated he was also excavating to trench in the front yard for a drainage system. Carlos stated he is aware of DigAlert and did not have a valid USA ticket.
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2023-04-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SCHILLING CORP | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On-site I spoke to Ken Krupa foreman for Schilling Corp who stated they had been trenching with mechanized equipment when they damaged the marked gas line. Ken added they had potholed the service closer to the main and it had been deeper than what they came across at the location of the damage. I advised Ken to always pothole and find at the exact location where they plan to cross the existing utility, it''s not good to assume the line will stay at the same depth. It is clear Schilling failed to pothole and damaged an accurately marked gas service line.
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2023-04-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | PARK WEST LANDSCAPE | ESCONDIDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | On-site, I spoke to Virgilio Ramos, Foreman of ParkWest Landscape, and Ivan Nunez, Supervisor of ParkWest Landscape, who informed me ParkWest workers were excavating for reclaimed water installation over a 1" plastic gas service with a mini excavator. Virgilio stated the excavator damaged the 1" plastic gas service.
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2023-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 4 |  | ALEX Tï¿½LLEZ | CHULA VISTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | On-site I spoke to homeowner Alex Tï¿½llez who stated he was making holes for a new fence with electric jackhammer when he damaged the gas line. Alex was unable to provide a valid USA dig alert ticket.
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2023-11-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SUNSHINE COMMUNICATIONS INC | EL CAJON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavating on the homeowner?s side yard when they damaged the 1/2" plastic gas service with a sharp shooter shovel.
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2023-12-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | HYDER PROPERTY MANAGEMENT | SAN MARCOS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Gas line had been damaged while excavating to repair the private water line with hand tools.
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2023-08-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | PACIFIC PLUMBING | SANTA BARBARA | CA | N | Y | No | No | Yes | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged the 1/2" plastic gas service with a mini excavator while trenching to install new sewer.
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2023-10-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | BLUE LINE BUILDERS INC | SANTEE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavating to install a new sewer lateral for the homeowner when he damaged the 1/2" plastic joint gas service.
San Diego Gas and Electric | N | SAN DIEGO | CHULA VISTA | 2023-11-30 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 3 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | 3D ENTERPRISES | SAN DIEGO | CA | N | Y | Yes | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged the gas line while grading. Unaware their subcontractor was excavating with an expired USA ticket.
San Diego Gas and Electric | N | SAN DIEGO | CORONADO | 2023-04-05 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2912 |  | 0 |  | SEMPER FI DEMOLITON SERVICES LLC | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | SDG&E crews responded to a third-party excavation incident. A third party contractor struck a 1 1/4 in steel natural gas line with an excavator while removing debris from a home demolition, causing a release of natural gas. SDG&E crews responded and controlled the release of natural gas. The third-party contractor did have a valid USA ticket. No injuries or fatalities resulted from this incident. This incident was reported to the CPUC when SDG&E became aware of media coverage.
San Diego Gas and Electric | N | SAN DIEGO | CORONADO | 2023-12-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | CLEAR VISION PLUMBING | OXNARD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2? plastic service gas line had been damaged while excavating to repair the sewer line with a shovel.
San Diego Gas and Electric | N | SAN DIEGO | CORONADO | 2023-09-01 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 20 |  | SDGE | SAN DIEGO | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | Gas line had been damaged while excavating to replace the utility pole with auger.
San Diego Gas and Electric | N | SAN DIEGO | CORONADO | 2023-10-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | CORONADO ALLDREDGE BUILDERS INC | CORONADO | CA | N | Y | Yes | Yes | Yes | Yes | No | No | No | Excavation was taking place to install a new water line on the property. Excavating with a trenching shovel when the 1/2" plastic joint gas service was damaged.
San Diego Gas and Electric | N | SAN DIEGO | CORONADO | 2023-06-21 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DALLEY MANSORY | RAMONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Spoke to Matt Thorn with Dalley Mansory who stated they cut into the exposed 3/4? steel pipe thinking it was abandoned line with a saw.
San Diego Gas and Electric | N | SAN DIEGO | CORONADO | 2023-04-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 32 |  | PROPERTY OWNER WILLEM VAN WAAY | CORONADO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | On-site I spoke to property owner Willem Van Waay who stated he was using a hand saw to cut roots to be able to get rid off the tree stump. Willem Van Waay was unaware there was gas running right below the stump. I informed Willem to request a valid USA dig alert ticket any time he plans to do any type of landscaping work so he is aware of the location of the existing utilities.
San Diego Gas and Electric | N | SAN DIEGO | DEL MAR | 2023-02-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | GOLDEN WOODS NURSURY AND LANDSCAPING | ESCONDIDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging for fence post and struck the gas line.
San Diego Gas and Electric | N | SAN DIEGO | DEL MAR | 2023-10-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | VINYL PRO FENCE | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging to put a fence post in when he managed to hit the gas.
San Diego Gas and Electric | N | SAN DIEGO | DEL MAR | 2023-08-02 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ROLLINS CUSTOM ELECTRIC | VALLEY CENTER | CA | N | Y | Yes | No | Yes | No | No | Yes | Yes | Homeowner had his own guy hand digging to expose the gas when he hit it with a shovel.
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2023-05-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | TAD EXCAVATION | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On-site I spoke with Todd Hanna foreman for TAD Excavation who stated the gas line had been damaged while trenching with backhoe to install new utilities. Todd added him and his crew were unaware this was a joint gas service since they did not see the flags between the bushes. I advised Todd to request re-marks or clarifications if he ever has any questions with the mark out.
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2023-12-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CARLOS BENITO | EL CAJON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Installing an underground drain for homeowner when the 1/2" plastic gas service was damaged with a shovel.
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2023-08-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MEJIA RENOVATORS INC | RAMONA | CA | N | Y | No | No | Yes | No | No | Excavator provided no markings for the proposed excavation on site. | No | Gas service line had been damaged while removing a tree with mechanized equipment.
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2023-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SAN DIEGO POOLS | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged the 1/2? plastic service while trying to remove tree roots with a hand saw.
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2023-06-09 | Third party excavation damage | Main | Steel | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 160 |  | S C VALLEY ENGINEERING | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Crew thought the pipe was abondoned and purposely driiled into the pipe.
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2023-06-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | FOUNDATION FLOORING CO | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The 1/2? plastic gas line was damaged while excavating with shovel for a retaining wall.
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2023-03-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MOHAMMED NURISTANI | EL CAJON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavating to install a new drain with mechanized equipment and damaged ï¿½ï¿½ï¿½inch plastic gas service.
San Diego Gas and Electric | N | SAN DIEGO | EL CAJON | 2023-04-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | BLUE MONARCH LANDSCAPE | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | On-site I met Alex Casillas owner of Blue Monarch Landscape who informe me his crew was working on grading to place a retaining wall when they damaged the gas service line with the backhoe.
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2023-06-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | SOUTHLAND PAVING | ESCONDIDO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Spoke with Ryan Walker, Foreman for Southland Paving, who stated that the 1/2" plastic joint gas service and an 8" clay sewer line were potholed with hand tools and completely exposed at approximately 4? deep. Ryan stated the gas line was sitting on top of the sewer line. While trenching at approximately 7? deep, Ryan stated the excavator was using a trackhoe bucket to loosen the hard dirt. When the dirt was broken with the mechanized equipment, the dirt around the 1/2" gas line and 8" sewer line was also disturbed; that disturbance caused the 8" clay sewer line to break, causing the 1/2" plastic gas line to break. Ryan reported excavation for a new sewer line was being performed at the time of the damage.
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2023-08-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | FALLING WATERS LANDSCAPES | ENCINITAS | CA | N | Y | No | No | Yes | No | No | Excavator provided no markings for the proposed excavation on site. | No | Was using a mini excavator to trench for new drains when he hit the gas. No USA.
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2023-12-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER | MOUNTAIN VIEW | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Putting fence post in when they managed to damage the gas.
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2023-09-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | VCI CONSTRUCTION LLC | UPLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Was using an air knife to bore from the face of curb under the sidewalk to the property line to set his boxes.
San Diego Gas and Electric | N | SAN DIEGO | ENCINITAS | 2023-03-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ALFREDO CHAVEZ | ENCINITAS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging with a shovel to put in new drains and hit the gas line.
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2023-12-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CASEY COLEMAN | EL CAJON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Grading the driveway when gas line was struck
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2023-02-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ACR BUILDERS | MISSION VIEJO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Crew hit the gas line while using the mini excavator.
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2023-11-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | PATRIOT PORTABLE RESTROOMS | ESCONDIDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging up the mailbox to move it closer to the street. Hit the gas with a shovel.
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2023-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | JUAN SANTOS GARCIA | ESCONDIDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Juan Santos Garcia stated on June 30th at 1:22pm that he assumed he was not digging deep enough to hit any utilities.
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2023-03-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ROTO ROOTER | VISTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging for the sewer and hit the gas line with the shovel.
San Diego Gas and Electric | N | SAN DIEGO | ESCONDIDO | 2023-02-03 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CE WILSON CORPORATION | SPRING VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Digging with an excavator and cut the 2inch plastic main. Did state marks were accurate.
San Diego Gas and Electric | N | SAN DIEGO | FALLBROOK | 2023-11-29 | Operator excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 18 |  | SDGE | ESCONDIDO | CA | Y | Y | Yes | No | Yes | No | No | Yes | Yes | 2" plastic gas main had been damaged with pin bar.
San Diego Gas and Electric | N | SAN DIEGO | FALLBROOK | 2023-09-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CUSTOM CONCEPT CONSTRUCTION | FALLBROOK | CA | N | Y | Yes | No | Yes | No | No | Excavator provided no markings for the proposed excavation on site. | No | Was digging by the meter when he hit the gas. He stated he knew the gas was there but managed to damage the gas.
San Diego Gas and Electric | N | SAN DIEGO | FALLBROOK | 2023-05-01 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | GEORGE SANCHEZ CONST | RAMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | George Sanchez stated on May 1st at 12:20pm that he had potholed all the utilities in the work area and had the 2? plastic gas main exposed at 33? and still managed to damage it with his excavator. stated that all the marks were accurate.
San Diego Gas and Electric | N | SAN DIEGO | FALLBROOK | 2023-08-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | THE LANDSCAPE COMPANY | SAN DIEGO | CA | N | Y | No | No | Yes | No | No | Excavator provided no markings for the proposed excavation on site. | No | Was digging with a shovel to put in drains when he struck the gas.
San Diego Gas and Electric | N | SAN DIEGO | FALLBROOK | 2023-06-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | RICHARD BEVAN | FALLBROOK | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | The gas line had been damaged while trenching with mini excavator to upgrade electric.
San Diego Gas and Electric | N | SAN DIEGO | FALLBROOK | 2023-07-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | PALM ENGINEERING | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Was using an excavator to get underneath the gas and managed to hit it.
San Diego Gas and Electric | N | SAN DIEGO | FALLBROOK | 2023-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | JAQUIN ALVARO | FALLBROOK | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Using a pickaxe to dig when he managed to hit the gas.
San Diego Gas and Electric | N | SAN DIEGO | FALLBROOK | 2023-11-20 | Third party excavation damage | Main | Polyethylene Pipe | Grader/Scraper | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | PALM ENGINEERING | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Operator managed to hit the gas even though they had potholed it and knew the depth.
San Diego Gas and Electric | N | SAN DIEGO | LA JOLLA | 2023-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | PRICELESS SERVICES INC. | ESCONDIDO | CA | N | Y | Yes | Yes | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | Yes | Spoke with Dan Kassel of Priceless Services via telephone who stated workers were excavating to pot for the existing 1/2" plastic gas service for a retaining wall installation. Dan stated the worker damaged the gas service with a trenching shovel.
San Diego Gas and Electric | N | SAN DIEGO | LA JOLLA | 2023-02-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | JACKSON DESIGN AND REMODELING | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Nicked a potholed exposed ï¿½ï¿½ï¿½inch plastic joint gas service line with a shovel.
San Diego Gas and Electric | N | SAN DIEGO | LA JOLLA | 2023-06-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MBB CONSTRUCTION INC. | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The 1/2" plastic gas service was damaged with a shovel.
San Diego Gas and Electric | N | SAN DIEGO | LA JOLLA | 2023-10-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | JC WILDING & CO | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2" plastic gas service was damaged with a shovel while attempting to trench for a new patio footing.
San Diego Gas and Electric | N | SAN DIEGO | LA JOLLA | 2023-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MARIATECILA COMUMALE | LA JOLLA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavating to install drains near the foundation of the home when she damaged the 1/2" plastic gas service with a shovel.
San Diego Gas and Electric | N | SAN DIEGO | LA JOLLA | 2023-10-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SAMUEL GARCES | LA JOLLA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Handyman had damaged the gas with a shovel.
San Diego Gas and Electric | N | SAN DIEGO | LA JOLLA | 2023-03-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | LOYA CONSTRUCTION INC | NATIONAL CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1inch plastic gas service line while excavating with mini excavator.
San Diego Gas and Electric | N | SAN DIEGO | LA JOLLA | 2023-04-06 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 3 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | OHLA USA INC. | IRVINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On-site, I spoke to Carlos Molina, Resident Engineer of City of San Diego, and Lazaro Guerrero, Superintendent of OHLA USA, Inc., who informed me they used mechanized equipment to uncover the sand over the 3" plastic gas main line up until 24" above the top of pipe when they began using hand tools to expose the gas main where they found the electro-fusion coupling fitting was leaking. Carlos stated they have potted for the 3" plastic gas main previously as work has continued over many months. Lazaro stated they have a valid Dig Alert ticket. I informed Lazaro to continue their efforts to pot for gas and electric utilities with hand tools and to keep their Dig Alert tickets valid.
San Diego Gas and Electric | N | SAN DIEGO | LA MESA | 2023-08-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Augur | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | FIVE STAR COMMUNICATIONS | LAKESIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Five Star Communications stated the gas line had been damaged with a rock wheel trencher while trenching to install a communication conduit.
San Diego Gas and Electric | N | SAN DIEGO | LA MESA | 2023-12-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | JP GENERAL CONTRACTOR | CHULA VISTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavating with mechanized equipment to repair the house sewer line when the gas line was damaged.
San Diego Gas and Electric | N | SAN DIEGO | LA MESA | 2023-10-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ALONSO GARCï¿½A CONTRACTOR | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2" plastic gas service line had been damaged while trenching with a chipping tool.
San Diego Gas and Electric | N | SAN DIEGO | LEMON GROVE | 2023-05-30 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | CITY OF LEMON GROVE | LEMON GROVE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On-site I spoke to Sam Landoros foreman with City of Lemon Grove Public Works who stated the gas line had been damaged while excavating to repair sinkhole with a backhoe.
San Diego Gas and Electric | N | SAN DIEGO | LEMON GROVE | 2023-09-21 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | WEG ENGINEERING | ALPINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 2? plastic gas main had been damaged while trenching to install wet utilities with mechanized equipment.
San Diego Gas and Electric | N | SAN DIEGO | LEMON GROVE | 2023-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | DS HOMES | NA |  | N | Y | No | No | Yes | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged the 1? plastic gas service line while excavating with mechanized equipment. Unable to provide a valid USA dig alert ticket.
San Diego Gas and Electric | N | SAN DIEGO | NATIONAL CITY | 2023-06-21 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | ARMSTRONG BUILDERS INC. | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Kiim explained the 2" plastic gas service was damaged by a trackhoe. Kiim reported the 2" plastic gas service was recently installed by Loya Constructors Inc. Kiim was educated on Dig Alert law and safe digging practices along with advisement to calling in a new USA ticket. With that, Kiim was informed of the legal start date and time. Kiim was provided contact information for further questions or concerns.
San Diego Gas and Electric | N | SAN DIEGO | NATIONAL CITY | 2023-02-09 | Third party excavation damage | Main | Steel | Trencher | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | HHS CONSTRUCTION | EL CAJON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Trenching with the rock wheel trencher to install telephone conduit and damaged the 3/4inch steel gas service.
San Diego Gas and Electric | N | SAN DIEGO | NATIONAL CITY | 2023-04-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOMEOWNER MELISSA AJERO | NATIONAL CITY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | On-site I spoke to homeowner Melissa Ajero who stated her self and her friends were trenching to repair her sewer line when they damaged the 1" plastic gas line with a shovel. Melissa did not know she was required to request a dig alert ticket. I informed her and educated her in dig alert law and gave her information, I advised her to request a ticket before continuing her proposed work.
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2023-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ACCURATE UNDERGROUND & GRADING | RAMONA | CA | N | Y | Yes | No | Yes | No | No | Yes | Yes | Hit it with an excavator.
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2023-09-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | UNITED CONCRETE | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Was digging next to the gas meter and managed to damage it.
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2023-04-10 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 16 |  | LOUIS PLUMBING | NA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Louie Vela who stated on April 10th at 12:40pm that he was using a mini excavator with no USA ticket. stated that he knows what a USA ticket was but never called one in.
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2023-10-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | OMEGA PAVERS | VISTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2023-12-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | JOSE CABRERA | OCEANSIDE | CA | N | Y | Yes | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavating to install a new sewer line when he damaged the 1/2" plastic gas service with a shovel. Invalid USA
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2023-01-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | JESSE TELLEZ/JESSE''S ELECTRIC | OCEANSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hand digging trench when he the gas line with a shovel.
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2023-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | FINAL SCAPE FX LANDSCAPING | CHULA VISTA | CA | N | Y | No | No | No | No | No | Yes | No | 1/2? plastic gas line had been damaged with a shovel, while clearing dirt out of the already dug trench. Jeff added they had trenched to place electric conduit for the homeowner and his crew was only clearing dirt with shovel and struck the buried gas line. Jeff provided USA B230530696, which expired 3/22/23. I explained to Jeff this ticket was no longer valid and they needed to re-notify.
San Diego Gas and Electric | N | SAN DIEGO | OCEANSIDE | 2023-01-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | HR PLUMBING | OCEANSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Potholing with a shovel when he damaged 2inch plastic pipe.
San Diego Gas and Electric | N | SAN DIEGO | OLIVENHAIN | 2023-02-28 | Operator excavation damage | Main | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | SDGE | ESCONDIDO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Crew was investigating a gas leak and struck 2inch gas main with a pin bar.
San Diego Gas and Electric | N | SAN DIEGO | OLIVENHAIN | 2023-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MENAS TEAM CONSTRUCTION | SPRING VALLEY | CA | N | Y | Yes | No | Yes | No | No | Yes | Yes | Gas partially exposed when he managed to damage it. Stated the marks were accurate.
San Diego Gas and Electric | N | SAN DIEGO | OLIVENHAIN | 2023-05-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | TOOLSON CONSTRUCTION COMPANY INC | ENCINITAS | CA | N | Y | No | No | No | No | No | Yes | No | Brent Toolsen stated on May 10th at 3:40pm that he knew the gas was there and that the mark out was good. BRENT TOOLSON stated that he shouldn''t have assumed the gas was a little over from were he was digging with his electric jackhammer.
San Diego Gas and Electric | N | SAN DIEGO | OLIVENHAIN | 2023-10-17 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 4 |  | DRAVES PIPELINE INC | SAN MARCOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Using his mini excavator to dig when he managed to hit the gas.
San Diego Gas and Electric | N | SAN DIEGO | POWAY | 2023-01-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | AMP ELECTRIC | SPRING VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Removing mud and water out of the trench and damaged the gas pipe.
San Diego Gas and Electric | N | SAN DIEGO | POWAY | 2023-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NEW VISION HARDSCAPE | ORANGE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Using a pickaxe to dig his trench when he managed to damage the gas.
San Diego Gas and Electric | N | SAN DIEGO | POWAY | 2023-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | S E PIPE LINE | SANTA FE SPRINGS | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Crew was digging receiving holes for the new gas service when the gas was hit with a shovel. Stated that the mark out was dead on and they simply just managed to hit the gas.
San Diego Gas and Electric | N | SAN DIEGO | POWAY | 2023-09-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | OAK PARK PLUMBING | NEWBURY PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Was digging to relocate the gas meter when he managed to hit the gas with a shovel. He stated that the gas mark outs were accurate.
San Diego Gas and Electric | N | SAN DIEGO | POWAY | 2023-11-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | JACK COHEN | MILLBRAE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavating to mitigate tree roots from further cracking his concreted driveway. Was using a shovel when he damaged the 1/2" plastic gas service
San Diego Gas and Electric | N | SAN DIEGO | POWAY | 2023-06-05 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4390 |  | 13 |  | PACIFIC GRADING AND EROSION CONTROL | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Jerry Cale stated on June 5th at 11:55am that he was scraping the side of the wall when he damaged the gas with the mini excavator.
San Diego Gas and Electric | N | SAN DIEGO | POWAY | 2023-12-12 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ONE STOP METAL FABRICATION | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Using a post hole digger when he smelled and heard the gas blowing.
San Diego Gas and Electric | N | SAN DIEGO | POWAY | 2023-03-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | LENNER AT HOMESTEAD AT THE FARM | POWAY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Using the mini excavator and hit the gas line.
San Diego Gas and Electric | N | SAN DIEGO | POWAY | 2023-07-14 | Third party excavation damage | Main | Steel | Boring Equipment | 4 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 66918 |  | 433 |  | PAL GENERAL ENGINEERING | NA |  | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | On July 14, 2023 SDG&E responded to a third-party excavation incident. A third-party contractor struck a 4 inch steel natural gas main while boring without a valid USA ticket, resulting in a release of natural gas. SDG&E crews controlled the release of natural gas. No injuries or fatalities resulted from this incident. This incident was reported to the CPUC when SDG&E became aware of media coverage.
San Diego Gas and Electric | N | SAN DIEGO | RANCHO SANTA FE | 2023-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | VAN LYONS | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Hit the gas with a shovel while exposing the gas.
San Diego Gas and Electric | N | SAN DIEGO | RANCHO SANTA FE | 2023-04-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | PACIFICA ENTERPRISES MGMNT GROUP INC | RANCHO SANTA FE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes, Brian Richardson stated on April 17th at 2:53pm that he knew the stub was in the area and still managed to hit it with his mini excavator.
San Diego Gas and Electric | N | SAN DIEGO | RANCHO SANTA FE | 2023-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ITS CONCRETE | RANCHO SANTA FE | CA | N | Y | Yes | No | Yes | No | No | Yes | Yes | Digging to expose the gas when he managed to damage the gas service. Digging with a shovel when he hit the gas.
San Diego Gas and Electric | N | SAN DIEGO | RANCHO SANTA FE | 2023-05-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | RANCO PACIFIC CONST | RANCHO SANTA FE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Nelson Perez who was digging stated on May 9th at 10:30am that he was digging to make the trench wider and expose the gas when he hit it with his shovel. Nelson stated that he had part of the gas exposed and assumed that it went straight but it went at a 45 degree angle were he started to dig more to expand the trench and struck the gas with his shovel.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-12-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | BLOSSOM VALLEY GRADING | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1? plastic gas line was damaged with a probe while trying to find it to determine its depth.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-04-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HYPER CONSTRUCTION | RAMONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | On-site, I spoke to Kathy Gooden of Hyper Construction who stated she was working as a sub-contractor for Stel Builders, excavating in the rear of the property to install electric underground when the 1" plastic gas service was damaged. Kathy stated neither contractor had valid Dig Alert tickets and they were unaware of the SDG&E gas service in the work area.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-08-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CITY OF SAN DIEGO | SANTEE | CA | N | Y | Yes | No | Yes | No | No | Yes | Yes | Excavation was taking place to repair the water service for the listed address when damage to the SDG&E 1/2" plastic joint gas service occurred.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | KMP PLUMBING | ESCONDIDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Jayden Rivera, excavator of KMP Plumbing, stated excavation was being completed to expose the 1/2" plastic gas service from the meter set assembly (MSA) to the 2" plastic gas fitting when the damage was caused by a shovel. Jayden stated he was aware of the location of the gas service line from a previous mark out. Jayden stated there is no valid USA ticket for KMP Plumbing.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-10-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | AM ORTEGA | LAKESIDE | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1/2" plastic joint gas service was damaged with a shovel while attempting to replace the gas service for the property.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-06-08 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | SE PIPELINE | SANTA FE SPRINGS | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavating near the gas MSA to install a new gas service when the existing 1/2" plastic gas line was damaged with a shovel.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-04-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | RICK MITCHELL | SAN DIEGO | CA | N | Y | No | No | No | No | No | Yes | No | Homeowner, Rick Mitchell, stated while digging to find his phone line, he hit the 1/2? plastic joint gas service with a shovel.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-09-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 4 |  | SMITH ELECTRICAL CONTRACTING INC | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavation was taking place after SDG&E inspectors requested the new electric conduit be placed at 30" deep. Octavio stated that the 1/2" plastic joint gas service was damaged with a shovel when exposing the last few inches of the trench.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-11-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 4 |  | ARB | LAKE FOREST | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavating near the gas MSA to pothole when they damaged the 1/2" plastic joint gas service with a shovel.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ALBERTO REYES LANDSCAPING | ESCONDIDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging 2 ft all the way and hit the gas pipe.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-08-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | PRICELESS SERVICES | ESCONDIDO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavation was taking place with shovels to prepare for the new gas service trench when the existing 1/2" plastic service was damaged.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-05-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | SEMPER SOLARIS | SAN DIEGO | CA | N | Y | Yes | No | No | No | No | Yes | Yes | On-site I spoke to Rick Peek foreman with Semper Solaris who stated he was cutting a piece of the conduit he had recently installed with a hand-saw, when he accidentally cut into the gas line that is sitting right below.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-04-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | AMPAM PARKS MECHANICAL | CARSON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Yes, Bob stated on April 13th at 2:15pm that his operator was digging with the excavator to put in private gas. Bob Hernandez stated that they didn''t have a USA ticket.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | OGC ELECTRIC WORKS | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Trenching for electric upgrade when he hit the gas with a shovel.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-08-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NORTH COUNTY FENCE & FABRICATION | MENIFEE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Joe stated on August 22nd at 11:30am that he was using the mini excavator when he hit the gas.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-08-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | NORTH COUNTY FENCE & FABRICATION | MENIFEE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Joe stated on August 22nd at 2:20pm that he was digging with a shovel when he hit the gas.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-05-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | PIERRE KLEE | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The homeowner, Pierre Klee, stated he was attempting to remove a concrete slab between his home and the ADU on his property when he and a friend ground through the SDG&E 3/4" steel gas service that was laying just underneath the concrete slab.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-09-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 5 |  | NA | GARDEN GROVE | CA | N | Y | No | No | Yes | No | No | Excavator provided no markings for the proposed excavation on site. | No | Was doing landscape work when he hit the gas service.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-01-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | BELL DESIGNS PAVERS AND TURF | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Using a saw when cutting for a drain and cut the gas pipe.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-09-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 5 |  | KTA CONSTRUCTION INC | SANTA CLARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Was using the mini excavator to move dirt from the trench and managed to hit the gas. He also stated that he knew the gas was there because he had potholed it before digging with the mini excavator.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-12-27 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 1.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ORTIZ CORPORATION | NATIONAL CITY | CA | N | Y | Yes | No | Yes | No | No | Yes | Yes | Excavation was taking place with an excavator while attempting to trench for a storm drain when the 1 1/2" steel gas stub was bent. Excavator accidentally pulled the gas stub with the bucket of the trackhoe.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-06-26 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 3 |  | CITY OF SAN DIEGO | SAN DEIGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Oscar Garcia stated on June 26th at 11:30am that they were pulling the new water service that was attached to the old water line to feed it through when they hit the gas line.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HECTOR JIMENEZ | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | On-site I met homeowner Hector Jimenez who stated the gas line had been damaged while trenching to upgrade electric with a shovel. Hector was unable to provide a valid USA dig alert ticket and was now aware it was not a good idea to trench without calling one in.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-11-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HENKELS & MCCOY | BLUE BELL | PA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hand digging when they damaged the gas.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | JOHN GWINN | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Crew cut the fully exposed ?inch steel pipe with inserted ï¿½ï¿½ï¿½inch plastic service line with Hackzall.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | STRUCTWELL CONSTRUCTION | SAN DIEGO | CA | N | Y | No | No | No | No | No | Yes | No | On-site Structwell Construction crew stated the 1/2" plastic gas line had been damaged while trenching with a shovel. The crew added they were aware the line was there since they had exposed approx. 15'' of it and were following it when they accidentally hit it. The crew is working to relocate the gas line along with the meter. Andrew Ridley foreman with Structwell Construction provided USA B230170575 which I explained it had expired 2/14/2023 and no longer valid.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-10-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | PHIL | TORRANCE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Working to install a fence for the homeowner when he damaged the 1" plastic gas service with a pole hole digger.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-04-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 36 |  | NUNEZ HANDYMAN | SAN DIEGO | CA | N | Y | No | No | No | No | No | Yes | No | The gas line had been damaged while trenching to upgrade electric with a shovel. Luis informed me they had found and exposed most of the gas main, however they were asked to make the trench deeper and that''s when the damaged a portion of the gas that was not fully uncovered yet. Luis provided USA A230470022, which expired 3/16/2023 and is no longer valid.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-05-02 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | BURTECH PIPELINE | ENCINITAS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The gas line had been damaged while trenching with backhoe to install new sewer main.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-03-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 3 |  | SUSAN HENEGAR | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Gas line had been potholed the workers damaged the pipe with a shovel while making the hole bigger.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-07-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 4 |  | CATS EXCAVATING INC | SAN DIEGO | CA | N | Y | Yes | No | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | CATS Excavating Inc stated the poly gas service line had been damaged while grading with mechanized equipment for street improvements. Expired USA.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | BURTECH PIPELINE | ENCINITAS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No damage to SUOF. | On-site I spoke to Leonard Batad foreman for Burtech Pipeline who stated the 3/4 Steel gas line had been pothole and once exposed they noticed it was leaking corroded pipe.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-12-19 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 32 |  | SC VALLEY ENGINEERING INC | EL CAJON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavating for sewer renewal when he damaged the 3/4" steel joint gas service with a trackhoe.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-03-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | SEMA CONSTRUCTION | RIVERSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged gas service line while grading with skeet steer.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-06-30 | Operator excavation damage | Main | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 84 |  | SDGE | ESCONDIDO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Jose Padilla who stated his crew damaged the 3/4" steel stub while replacing concrete alley panel with mini excavator. Jose informed us the crew was also using hand tools to pothole the marked gas main, but when to scrape the ground with the mini excavator and struck the 3/4" steel stub punch tee at the main, which was at approx 18" in depth.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | METROPOLITAN MAPPING | SAN DIEGO | CA | N | Y | No | No | Yes | No | No | Excavator provided no markings for the proposed excavation on site. | No | Gas line had been damaged while placing survey markers (whiskers) within the lot. Driving in nails for approx. 5? when he struck the gas line.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | T PETERS CONSTRUCTION | LAKESIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Potholing with a shovel to expose the 1/2" plastic joint gas service at the time of the damage. Existing gas facilities are located, however plans have now halted. Valid USA ticket.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-09-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | PALMEIRA GARDEN LLC | NA |  | N | Y | No | No | Yes | No | No | Excavator provided no markings for the proposed excavation on site. | No | Gas service line had been damaged while digging to lower the dirt bank with mechanized equipment.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | E. LARA CONSTRUCTION | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged the 1/2? plastic service insert in steel while trenching with a backhoe.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-11-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | JOHN ALBINI | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1" plastic service line had been damaged while placing wooden stakes for a retaining wall.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 5 |  | TEYO?S LANDSCAPE CONSTRUCTION INC. | CHULA VISTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | On 6/23/2023 SDGE was made aware of a third party damage at 3211 Thorn St, San Diego. Contractor struck a 1/2in service line with a mini excavator while trenching to install fence. Crews arrived and controlled the flow of gas. This incident was reported to the CPUC due to the release of gas and once SDGE was made aware of media coverage.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-10-25 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 24 |  | SUKUT CONSTRUCTION | SANTA ANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1" steel gas service was damaged with a trackhoe while excavating for a water main renewal trench.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | COLWELL EQUIPMENT | RAMONA | CA | N | Y | No | No | Yes | No | No | Excavator provided no markings for the proposed excavation on site. | No | Was grading to level topsoil in preparation for pouring concrete when the 1/2" plastic gas service stub was damaged. Did not have a valid USA ticket and was unaware of the SDG&E facility.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-01-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 3 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | CRISTALYN WALTON | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Lowering the grade in the front yard with a hand tool and cut the gas line ?inch steel line.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-02-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 26 |  | MORELLO CONCRETE CONSTRUCTION INC | SANTEE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged gas line while grading with mini excavator.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-12-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 5 |  | PACIFIC LANDSCAPING AND MAINTENANCE | SACRAMENTO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Installing fence posts with a pole digger when he damaged the 1/2" plastic gas service.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ING CONSTRUCTION | SAN DIEGO | CA | N | Y | No | No | Yes | No | No | Excavator provided no markings for the proposed excavation on site. | No | Gas line had been damaged while trying to expose it with hand tools. Did not have a valid USA dig alert ticket.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-09-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | REBUILDING CALIFORNIA | SANTA ROSA | CA | N | Y | No | No | Yes | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavation was taking place to re-expose the utilities for trench inspection; in doing so, the 1/2" plastic gas service was damaged with a mini excavator. Provided an USA ticket number.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-03-20 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 4 |  | THE LLWEWLLYN GROUP | SAN DIEGO | CA | N | Y | No | No | Yes | No | No | Excavator provided no markings for the proposed excavation on site. | No | Put the bucket down in the wrong spot and hit the 2inch plastic main.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-09-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MIRAMAR GENERAL ENGINEERING | NATIONAL CITY | CA | N | Y | No | No | Yes | No | No | Excavator provided no markings for the proposed excavation on site. | No | Crew damaged the 1? plastic gas line while excavating with mechanized equipment. Alex informed me they are currently excavating to place ped ramps for the City of San Diego. No valid USA.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-04-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 3 |  | CHRIS SALAZAR | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | On-site I spoke to Chris Salazar who stated he exposed the steel line and assumed it was an abandoned pipe, so he used a grinder to cut it out of his way. Chris is trenching to install a drain pipe without a valid USA dig alert ticket. The gas line was damaged after being exposed and being cut into with a grinder.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-04-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | CALHOMECO | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On-site I spoke to Shawn Stone foreman for CALHOMECO who stated his operator damaged the gas line while scraping ground for ADU foundation with mechanized equipment. Shawn added they had seen the marks and were trying to be careful around the area they knew the marks were for the existing gas were, but they were not expecting the gas to be that shallow.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-04-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | SOCAL HOME WORX LLC | LA MESA | CA | N | Y | No | No | No | No | No | Yes | No | On-site, spoke to Shawn Stone of CalHome Co. who stated Brian Peterson of SoCal Home Worx LLC was excavating near the gas MSA to relocate the gas service when the existing 1/2" plastic joint gas service was damaged with a trenching shovel. Brian stated he did not have a valid USA ticket. Shawn stated he was unaware his USA ticket (#A230810695) was expired as of 04/19/23.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-11-30 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SDGE | SAN DIEGO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Sunrise Bobcat Inc. was assisting SDG&E gas maintenance crew workers to pothole for the 1 1/2" steel gas service with a mini excavator when the facility was damaged.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-04-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DUKES CONSTRUCTION | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | On-site I spoke to Jason Dukes who stated he was removing a tree and cutting its roots with a handsaw when he sawed into the gas line. Jason added he was not aware the roots had tangled all around the gas service line.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 6 |  | S C VALLEY ENGINEERING INC | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Marked gas line started leaking while backfilling and rolling dirt in the trench. Had been trenching to install new sewer and water lines.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-10-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CEMENT CUTTING INC | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Sawcutting the asphalt when the 3/4" steel gas service was damaged.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-10-11 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | SDGE | SAN DIEGO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavation was taking place to install a new gas service, however SDG&E trench Inspectors requested the trench be dug to a deeper depth. As equipment operators attempted to scrape a few inches of dirt, the 1/2" plastic gas service was damaged with a trackhoe.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | DEVELOSCAPES LANDSCAPE CONSTRUCTION | VALLEY CENTER | CA | N | Y | No | No | Yes | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit the 3/4" steel gas service with a mini excavator.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-05-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | ECO DESIGN SAN DIEGO | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Antonio Melchior of Eco Design San Diego stated he was excavating at the planter box to remove it and place pavers. Antonio stated the 1/2" plastic gas service was damaged with a mini-excavator. Antonio stated he did not have a valid USA ticket but is aware of Dig Alert law.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-12-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ARCADIAN LANDSCAPING | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavating a trench line for the property?s electric conduit upgrade when the 1/2" plastic gas service was damaged with a shovel.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | COOKSON ENTERPRISES INC | ESCONDIDO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Gas line had been damaged while trenching with a backhoe. Crew potholed and found a 3/4? steel service and assumed that was the active gas service line crossing the proposed trench.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-05-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | SOLID GROUND CONSTRUCTION | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While on-site, Nick Aldous of Solid Ground Construction stated he was excavating near the 1" plastic gas service when he scraped the top of the pipe with his backhoe. Nick stated he does not have a validation USA ticket. Nick also stated the he recently installed the 1" plastic gas service, so he knew the whereabouts of the service but still managed to damage it.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-12-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | PRO FLOW MASTERS INC | SANTEE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Installing new sewer clean out for the homeowner, when the 1/2" plastic gas service was damaged with a shovel.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-09-27 | Third party excavation damage | Riser | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CARLSBAD CONCRETE CUTTING | CARLSBAD | CA | N | Y | No | No | Yes | No | No | Excavator provided no markings for the proposed excavation on site. | No | Was digging footings when he hit the gas with a shovel. He also stated that he knew the gas was there because he was right next to the gas meter. He also stated he knew what a dig alert ticket was but didn?t call one in.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-01-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | WEST TECH CONTRACTING INC. | ESCONDIDO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Digging to expose gas service and hit the 1inch service with a backhoe.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-03-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | HOME LEAK AND DRAIN CONSTRUCTION | CHULA VISTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged the gas line with a shovel while excavating to repair homeowner?s sewer line.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-06-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | CHRIS BELL CONSTRUCTION | NA | CA | N | Y | No | No | No | No | No | Yes | No | Chris Bell of Chris Bell Construction stated he was excavating to pothole the 1/2" plastic joint gas service when he damaged the gas line with a shovel. Chris stated his Dig Alert ticket was expired, however he previous had the gas marked and was aware of the location of the 1/2" plastic joint gas service. Chris stated he is currently waiting for the gas MSA to be relocated near the rear of the property.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | AR ENGINEERING CONSTRUCTION | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Isaias stated they damaged the joint gas service with a pick ax. Isaias explained he was unaware of Dig Alert law and would call in a USA ticket. Isaias was educated on Dig Alert law regarding delineations, legal start time and potholing to locate SDG&E utilities.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-10-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | TESSITORE CONCRETE | CHULA VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavation was taking place to install sewer lines for the new ADU being built on the property. Trying to expose the remaining 1/2" plastic gas service when the line was damaged by a shovel.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-02-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | BENJAMIN THOMPSON | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavating with a shovel and hit gas service line.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-04-10 | Third party excavation damage | Main | Steel | Miscellaneous/Other | 1.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | THE CITY OF SAN DIEGO | SAN DEIGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | On-site I spoke to Micheal Gray electrical supervisor with the City of San Diego who stated his crew had been boring to instal electric wire for a streetlight project. Micheal and his crew added they assumed they were going to be shallow and were not going to come across any existing utilities. The City of San Diego failed to request a valid USA dig alert ticket for boring to install electric wire.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-10-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | EDGAR HERNANDEZ | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While removing the tree stump, he said he damaged the gas service with a shovel.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-03-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | DW CONSTRUCTION | ALPINE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavating with a mini excavator to expose the marked gas service and damaged the poly gas service.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-10-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | PALM ENGINEERING CONSTRUCTION COMPANY | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1/2" plastic gas service was damaged with a trackhoe excavating for sewer replacement.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-10-03 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | FRASSICA INC | CORONA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged the 1/2? plastic service insert in steel with a sawzall.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | URBAN SEED LANDSCAPING | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Cut the partial exposed gas line while removing the tree roots.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1585 |  | 2 |  | AM ORTEGA | NA |  | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On Thursday August 3, 2023 SDG&E responded to a third-party excavation incident located at 4726 Kansas St, San Diego, San Diego. A third-party contractor struck a half inch plastic natural gas service while excavating with a post hole digger, resulting in a release of natural gas. SDG&E crews controlled and repaired the release of natural gas. No injuries or fatalities resulted from this incident. This incident was reported to the CPUC when SDG&E became aware of media coverage.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-02-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ELECTRICAL INSIGHT | ESCONDIDO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged gas line while trenching with a shovel.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-03-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CITY OF SAN DIEGO | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Pulled 1/2inch plastic at the transitions from steel to poly while removing a trash bag with a backhoe.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-03-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HL MASONRY BUILDERS | ESCONDIDO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Operator of mini excavator hit the 1inch plastic service.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-06-07 | Operator excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SDGE | ESCONDIDO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3/4" steel gas service was cut into while saw cutting asphalt to investigate gas leak. After controlling the leak and removing asphalt we could see gas line sat just below asphalt at approx. 7" deep.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-04-26 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 38 |  | A & A CONTRACTING SERVICES | LEMON GROVE | CA | N | Y | No | No | No | No | No | Yes | No | On-site I spoke to Terry Young foreman for A & A Contracting Services who stated the 2" plastic gas main had been damaged while excavating to replace storm drain with mini excavator.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-05-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SC VALLEY ENGINEERING, INC. | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Jerry Cromwell, working foreman, stated the 1/2" plastic gas service had previously been exposed. Jerry stated when he was excavating with the mechanized equipment, with a spotter in the trench, the spotter told him to finish scooping the last piece of dirt before continuing to expose the gas service with hand tools; Jerry stated he pulled the 1/2" plastic gas service. Jerry admitted to being at fault and stated he follows all dig alert laws.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-11-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | AR BARDSLEY | JAMUL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavating to install a storm drain when he damaged the 1 1/4" plastic gas service with a mini excavator.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | FERNANDO GONZALEZ | SAN RAFAEL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged the gas service near the embankment, approximately one foot from where the gas service was initially potted for. Fernando provided his valid USA ticket.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-10-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MBI EXCAVATION INC | POMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hit the gas with the excavator.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-02-07 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 3 |  | MACGRAY ELECTRIC INC | EL CAJON | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged gas line while removing a tree with mechanized equipment.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-02-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 6 |  | WEST TECH CONTRACTING INC | ESCONDIDO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavating with mini excavator to expose the gas service and accidently hit the ï¿½ï¿½ï¿½inch plastic line. The service line was already potholed and marked.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-04-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | CARVIN ELECTRIC | NA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On-site I spoke to Marvin Contreras foreman for Carvin Electric who stated they were trying to find the marked gas line when they accidentally dug into it with the shovel. Marvin added they are trenching to upgrade the electric for the homeowner and had seen the marks for the gas service line.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-01-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | DRAIN MEDIC RX PLUMBING | LEMON GROVE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging to repair a drainpipe and hit 1-1/4inch poly service.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-10-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | PENNY PINCH PLUMBING | LEMON GROVE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit the exposed gas line with hand tool while excavating to move gas meter.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-12-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CUT N CORE | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Gas line had been damaged while excavating to upgrade the electrical panel with a chipping hammer.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1568 |  | 1 |  | ORTIZ CORPORATION | NA |  | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | On Monday July 24, 2023 SDG&E responded to a third-party excavation incident located at 7145 Eckstrom Ave, San Diego, San Diego. A third-party contractor struck a one inch plastic natural gas service while excavating with a track hoe, resulting in a release of natural gas. SDG&E crews controlled the release of natural gas. No injuries or fatalities resulted from this incident. This incident was reported to the CPUC when SDG&E became aware of media coverage.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-02-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 33 |  | BURTECH PIPELINE | ENCINITAS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Gas service line had been damaged while grading with mechanized equipment. Crew had already pot holed to locate the service line.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-11-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | BURTECH PIPELINE | ENCINITAS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Potted and managed to damage gas
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-10-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | SO CAL EXCAVATION | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Gas line had been damaged while trying to pothole it with a shovel.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-11-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | AM ORTEGA | LAKESIDE | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | After vacuum excavation took place, leaking gas was smelled near the property?s gas MSA. Vacuum excavation was taking place to pothole the utilities near the MSA. Unaware of the damage to the 1/2" plastic gas service; subsequently, the damage could have potentially occurred when an unknown concrete contractor graded and poured concrete approximately one month ago.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-09-03 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | SIMS GRADING INC | VISTA | CA | N | Y | No | No | Yes | No | No | Excavator provided no markings for the proposed excavation on site. | No | Brian Sims stated on September 1st at 4:34pm that he was digging around this concrete structure when he managed to damage the gas. Brian Sims stated that he knew the gas was in the area due to a previous mark out.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MCMAHON ENGINEERING CONSTRUCTION | ESCONDIDO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavation was taking place to install steel beams when the 1-1/4" plastic gas service was damaged with a mini excavator. Operator lost sight of the gas service during trenching.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-06-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SMITH ELECTRICAL CONTROL CO. | EL CAJON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The 1/2" plastic joint gas service was damaged by a shovel while trenching to install an upgraded electrical conduit for the customer.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-06-13 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | BLUE PACIFIC ENGINEERING AND CONSTRUCTION | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 06/13/2023 SDG&E crews responded to an incident located at 9130 Dowdy Drive, San Diego, CA. A third-party contractor working on a storm drain had a skid-steer that sank due to a water main break causing a sinkhole. The skid-steer damaged a 3/4 inch steel service causing a release of natural gas.SDG&E crews responded and controlled the release of natural gas. No injuries or fatalities resulted from this incident. This incident was reported to the CPUC when SDG&E became aware of media coverage.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-09-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | INLAND VALLEY PIPELINE | TEMECULA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Gas line had been damaged while trenching with a backhoe to install wet utilities.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-08-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | BY THE BOOK PLUMBING | SALINAS | CA | N | Y | No | No | Yes | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged the 1/2" plastic gas service with a shovel. No USA.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-05-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | FISHEL COMPANY | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Juan Ramirez stated they were attempting to pothole the 1 1/4" plastic gas service when they damaged it with a mini excavator.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-12-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | D & N ELECTRIC INC | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1/2" plastic gas service was damaged with a shovel.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-10-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7640 |  | 5 |  | SUKUT CONSTRUCTION | SANTA ANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On 10/2/2023 SDGE was made aware of a 3rd party damage at Clairemont Dr & Calle Neil in San Diego. SDGE responded and controlled the flow of gas. Investigation relieved that the 3rd party contractor struck a 1in service line with a backhoe while performing sewer work. Permanent repairs have been completed and all customers have been restored. This incident was reported to the CPUC due to gas release and when SDGE was made aware of media coverage.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-09-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CASS ARRIETA CONSTRUCTION | EL CAJON | CA | N | Y | No | No | Yes | No | No | Excavator provided no markings for the proposed excavation on site. | No | Dave stated the SDG&E gas line was damaged with a backhoe. Dave was advised to call in a new USA ticket for the proposed work area.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-02-02 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | LANSDCAPE DEVELOPMENT | CORONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Damaged 2inch plastic stub while excavating with mini excavator.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-04-05 | Operator excavation damage | Main | Polyethylene Pipe | Probing Device | 3 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | SDG&E | ESCONDIDO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Crew investigating a leak stuck pin bar into main.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-11-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 24 |  | FERREIRA COASTAL CONSTRUCTION | RANCHO CUCAMONGA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Potholed the gas and knew the depth but still managed to hit the gas.
San Diego Gas and Electric | N | SAN DIEGO | SAN DIEGO | 2023-06-06 | Third party excavation damage | Miscellaneous/Other | Polyethylene Pipe | Not Available | 3 | 60 | 55 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | FJ WILERT CONTRACTING | CHULA VISTA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | While potting to find the 3" plastic gas main on the NW intersection of Sanyo Ave. and Airway Rd., there appeared to be a damaged conduit that was uncovered near the top of the surface. Kenny stated he called for a remark ticket but did not report the damaged conduit. Unknown How Ga Valve was damaged. Damage found while remarking ticket.
San Diego Gas and Electric | N | SAN DIEGO | SAN MARCOS | 2023-03-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 5 |  | JOHN FIOCCO | SAN MARCOS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging with a shovel for a new drain and hit the gas line.
San Diego Gas and Electric | N | SAN DIEGO | SAN MARCOS | 2023-08-29 | Third party excavation damage | Riser | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | HYPER CONST INC | RAMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Was using the pickaxe to trench when he hit the gas.
San Diego Gas and Electric | N | SAN DIEGO | SAN MARCOS | 2023-10-17 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 4 |  | DREAMCRAFT | VISTA | CA | N | Y | Yes | No | Yes | No | No | Yes | Yes | Using the mini excavator to trench for a panel upgrade when he managed to hit the gas.
San Diego Gas and Electric | N | SAN DIEGO | SAN MARCOS | 2023-05-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | MARK CLARK | SAN MARCOS | CA | N | Y | Yes | No | No | No | No | Yes | Yes | 1/2? plastic gas service hit with a shovel while trenching for a new panel upgrade.
San Diego Gas and Electric | N | SAN DIEGO | SAN MARCOS | 2023-05-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | HHS COMMUNICATIONS | NA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Trenching and he hit the 1/2? plastic gas service.
San Diego Gas and Electric | N | SAN DIEGO | SAN MARCOS | 2023-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1.25 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | PRO SELECT CONSTRUCTION SERVICES | ESCONDIDO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Yes, Antonio Martinez stated on April 21st at 10:45am that they were using a sawzall to cut a tree root when they hit the exposed 1-1/4? plastic gas service.
San Diego Gas and Electric | N | SAN DIEGO | SAN MARCOS | 2023-05-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 7 |  | SEMA | NA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Didn?t pothole the utilities before digging with the excavator. Tony simply stated that he messed up.
San Diego Gas and Electric | N | SAN DIEGO | SAN YSIDRO | 2023-09-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CROWBAR CONSTRUCTION | CARLSBAD | CA | N | Y | No | No | Yes | No | No | Excavator provided no markings for the proposed excavation on site. | No | Crew damaged the 1/2? plastic joint service gas line while excavating with hand tools (shovel). Oscar informed me they are currently trenching to upgrade the electric for the property owner. No valid USA.
San Diego Gas and Electric | N | SAN DIEGO | SANTEE | 2023-02-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | J GINGER MASONRY | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavating with mini excavator to install footings for a wall and damaged 1inch plastic gas service line.
San Diego Gas and Electric | N | SAN DIEGO | SOLANA BEACH | 2023-08-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | UNITED SPECIALTY CONSTRUCTION | ESCONDIDO | CA | N | Y | No | No | Yes | No | No | Excavator provided no markings for the proposed excavation on site. | No | Aureliano Sanchez stated on August 1st at 1:30pm that he was grading for pavers when he hit the gas.
San Diego Gas and Electric | N | SAN DIEGO | SPRING VALLEY | 2023-04-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | LUIS Mï¿½RQUEZ CONTRACTOR | NA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | On-site I spoke to Luis foreman Luis Marquez who stated his worker was trying to re-exposed the marked gas stub when he accidentally hit it with the shovel.
San Diego Gas and Electric | N | SAN DIEGO | SPRING VALLEY | 2023-12-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CHRISTOPHER QUICK | SPRING VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Installing a 6" rebar stake to hold down his aluminum carport when the 1/2" plastic gas service was damaged.
San Diego Gas and Electric | N | SAN DIEGO | SPRING VALLEY | 2023-06-09 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | S E PIPELINE | SANTE FE SPRINGS | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Crew damaged the marked 1/2? plastic service line while potholing with shovel, according to him the ground is hard and came across some roots when they accidentally hit the gas line.
San Diego Gas and Electric | N | SAN DIEGO | VALLEY CENTER | 2023-05-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | PACIFIC PRODUCTION PLUMBING | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Bill Kearney stated on May 15th at 10:03am that his crew exposed the yellow line and didn''t know the line was gas or pressurized and attempted to cut it out of the way with a sawzall to fit the drain pipe.
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2023-07-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | REHAB SOLAR | FALLBROOK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Was using a shovel to dig the trench when he hit the gas.
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2023-06-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | OHP CONSTRUCTION | VISTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Oscar Hernandez stated on June 8th at 1:20pm that his guys were handdigging when they cut through the gas with a shovel.
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2023-08-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | HOMEOWNER | MOUNTAIN VIEW | CA | N | Y | No | No | Yes | No | No | Excavator provided no markings for the proposed excavation on site. | No | Property owner was digging with a shovel to relocate the gas meter and hit the gas.
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2023-05-31 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 7 |  | COSCO FIRE PROTECTION | SAN DIEGO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Tyler Sshelton stated on May 31st at 12:50pm that he was digging to install fire sprinklers when he struck the gas with a digging bar. stated that he did not have a USA ticket when I asked and didn?t even know what that was.
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2023-12-09 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | RON PHIL | VISTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3/4? steel service while trying to remove tree roots with a hand saw.
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2023-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | ALLIANCE DIVERSIFIED | VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Donald Anderson Jr. stated on June 29th at 11:30am that his crew potholed and found a gas line they assumed was the live gas and proceeded to work and dig with an excavator when the 1? pla service was hit.
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2023-03-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | JUAN PAZ | VISTA | CA | N | Y | No | No | Yes | No | No | Excavator provided no markings for the proposed excavation on site. | No | Cutting an old drain and struck the gas line under the drain.
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2023-02-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | GE GENERAL CONSTRUCTION | FALLBROOK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Cut ï¿½ï¿½ï¿½inch fully exposed plastic service.
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2023-04-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | HOMEOWNER DOING THE WORK | VISTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Yes, Alfonso, stated on April 16th at 12:09pm that he was trenching with a mini excavator to upgrade his electric service when he hit the 1" plastic gas service. He stated that he knows what a USA ticket is but never called one in.
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2023-12-06 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | IN THE DIRT ENGINEERING | RAMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Gas line was hit with excavator and that the mark-outs are accurate.
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2023-01-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | BILL HAYDEN | VISTA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hand digging and damaged the gas line.
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2023-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | C H WESTGATE INC | SOLANA BEACH | CA | N | Y | Yes | No | No | No | No | Yes | Yes | Dewey Westgate stated on Mat 12th at 2:00pm that he had the gas fully exposed to install new utilities when he hit the 1/2" plastic gas service with a shovel.
San Diego Gas and Electric | N | SAN DIEGO | VISTA | 2023-08-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MIKES INLAND AND COASTAL LANDSCAPE | SAN DIEGO | CA | N | Y | No | No | Yes | No | No | Excavator provided no markings for the proposed excavation on site. | No | Was using the mini excavator to dig for a irrigation sleeve when he hit the gas.
Southern California Gas Company | N | FRESNO | KINGSBURG | 2023-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | DCW CONTRACTORS INC | VISALIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | SCG responded to damage, upon arrival, crew found damaged 1/2 plastic gas line by 3rd party contractor. Contractor failed to pothole the 1/2 plastic gas line as required.
Southern California Gas Company | N | FRESNO | KINGSBURG | 2023-06-12 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 3 | 25 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CVIN LLC | FRESNO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Locator went off of measurements for the locate and was out of our buffer for a valid mark, his comments on the korterra do not match his actual procedure used to obtain his locate, Maps Update Request will be submitted. The Employee counseling is still pending for employee.
Southern California Gas Company | N | FRESNO | LATON | 2023-05-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 15 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | SHANE V BERGSTROM | LATON | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Occupant damaged a 1/2 plastic gas line while digging for utilities work, crew made permanent repairs, damaging party was educated about USA law.
Southern California Gas Company | N | FRESNO | ORANGE COVE | 2023-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 36 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | REX MOORE GROUP INC | FRESNO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party subcontractor damaged a 1/2 plastic gas line while working yard.
Southern California Gas Company | N | FRESNO | REEDLEY | 2023-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | VARGAS CONSTRUCTION | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged service repaired by crew, no usa by contractor
Southern California Gas Company | N | FRESNO | REEDLEY | 2023-10-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | EMMETTS EXCAVATION INC | CLOVIS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor damaged a 1/2 plastic gas line.
Southern California Gas Company | N | FRESNO | REEDLEY | 2023-12-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DENNIS W MILLS CONSTRUCTION | KERMAN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service while installing electrical conduit. Contractor did have a valid USA and damaged service while hand digging.
Southern California Gas Company | N | FRESNO | REEDLEY | 2023-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Farm Equipment | 0.5 | 10 | 10 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ANTHONY BALLEKIAN | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged service repaired by crew, no usa
Southern California Gas Company | N | FRESNO | REEDLEY | 2023-07-13 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 2 |  | DCW | VISALIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor was excavating to install new water main for a new subdivision, they damaged a 2 plastic main. Contractor failed to pothole the 2 plastic gas line as required.
Southern California Gas Company | N | IMPERIAL | BRAWLEY | 2023-05-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 36 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | PRIMO CONSTRUCTION | BRAWLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was probing along water main and hit 1/2'''' cts service line. The contractor did not have a USA and is fully responsible.
Southern California Gas Company | N | IMPERIAL | BRAWLEY | 2023-09-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | PATTY''S LONCHERIA | BRWALEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The occupant was digging to repair a sewer line, when they damaged a plastic gas line. The occupant did not have a USA ticket.
Southern California Gas Company | N | IMPERIAL | BRAWLEY | 2023-05-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 2 |  | NA | BRAWLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party was looking for water houseline and damaged gas line
Southern California Gas Company | N | IMPERIAL | BRAWLEY | 2023-12-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | POWER PLUS | ANAHEIM | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was using a sharpshooter while excavating and damaged a plastic gas line. They did not have a USA.
Southern California Gas Company | N | IMPERIAL | BRAWLEY | 2023-05-02 | Operator excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 36 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | NPL | EASTVALE | CA | Y | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 2nd party contractor NPL was making a permanent repair on a SCG asphalt patch when they damaged stl service. The contractor did not have a USA.
Southern California Gas Company | N | IMPERIAL | BRAWLEY | 2023-04-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | FRANK | BRAWLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 service damaged with posthole digger. No USA ticket. Customer advised to call USA two days before work.
Southern California Gas Company | N | IMPERIAL | BRAWLEY | 2023-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MIKE NECIVK | BRAWLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was excavating for landscaping project and damaged a plastic gas service. The contractor did not have a USA.
Southern California Gas Company | N | IMPERIAL | BRAWLEY | 2023-04-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | ISRAEL SANCHEZ | BRAWLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor damaged a plastic gas service while excavating to install a water pipeline. The contractor did not have a USA and is fully responsible.
Southern California Gas Company | N | IMPERIAL | CALEXICO | 2023-10-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | HOMEOWNER | CALEXICO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged plastic gas service. No USA
Southern California Gas Company | N | IMPERIAL | CALEXICO | 2023-06-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | FRANCISCO LUNA | CALEXICO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was digging with a shovel when they damaged a plastic gas service. The homeowner did not have a USA and is fully responsible.
Southern California Gas Company | N | IMPERIAL | CALEXICO | 2023-03-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | VERDUGO CONCRETE CONSTRUCTION INC | SPRING VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was digging with a backhoe to install footing for a retaining wall and damaged a 2-inch plastic main. The contractor did not have a USA and is fully responsible.
Southern California Gas Company | N | IMPERIAL | CALEXICO | 2023-01-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JOSHUA ESPINOZA | IMPERIAL | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was excavating with a shovel to expose the sewer line when they damaged a plastic gas line. The contractor did not have a USA and is fully responsible.
Southern California Gas Company | N | IMPERIAL | CALEXICO | 2023-06-14 | Third party excavation damage | Meter | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | DAVID SIM | CALEXICO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was excavating when they damaged a plastic gas service. The contractor did not have a USA and is fully responsible.
Southern California Gas Company | N | IMPERIAL | CALIPATRIA | 2023-05-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MANUEL YANEZ | CALEXICO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was excavating with a backhoe and damaged a plastic service. The Contractor did not have a USA and is fully responsible.
Southern California Gas Company | N | IMPERIAL | EL CENTRO | 2023-01-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 1 |  | HILDA MENDOZA | EL CENTRO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer/contractor did not notify USA. Trenching for sewer and cut service. Homeowner attempted to repair on their own. Damage called in by neighbor. cut 1/2 repaired by Co. crew.
Southern California Gas Company | N | IMPERIAL | EL CENTRO | 2023-01-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 29 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | ROC CONSTRUCTION | IMPERIAL | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor damaged a plastic gas line with a backhoe while digging a trench. The contractor did not have a USA and is fully responsible.
Southern California Gas Company | N | IMPERIAL | EL CENTRO | 2023-01-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 29 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  |  | NA | 3 AND 1 ELECTRIC | RANCHO CUCAMONGA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was trenching for electric when they damaged a plastic gas line. The contractor did not have a USA and is fully responsible.
Southern California Gas Company | N | IMPERIAL | EL CENTRO | 2023-01-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 35 | 29 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | 3N1 ELECTRIC | CHINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was excavating with backhoe and damaged a plastic gas line. The contractor did not have a USA and is fully responsible.
Southern California Gas Company | N | IMPERIAL | EL CENTRO | 2023-11-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DIONICIO T RAMOS | EL CENTRO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged plastic service while digging to clear clogged sewer line. No USA.
Southern California Gas Company | N | IMPERIAL | HEBER | 2023-01-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 2 |  | ALONSO A GUIRRE | HEBER | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The home owner was digging with a posthole digger and damaged a plastic gas line. The home owner did not have a USA and is fully responsible.
Southern California Gas Company | N | IMPERIAL | HEBER | 2023-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 42 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | HEBER | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was excavating when they damaged a plastic gas line. The contractor fled the scene, they did not have a USA and is fully responsible.
Southern California Gas Company | N | IMPERIAL | IMPERIAL | 2023-10-30 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ARIZONA PIPELINE | HESPERIA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Second party contractor was potholing the existing service when they damaged the plastic service.
Southern California Gas Company | N | IMPERIAL | IMPERIAL | 2023-06-14 | Third party excavation damage | Miscellaneous/Other | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 52 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | PACIFIC WEST DEVELOPMENT | TEMECULA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was excavating with a back hoe when they damaged a 2 inch plastic main. The contractor did not have a USA and is fully responsible.
Southern California Gas Company | N | IMPERIAL | IMPERIAL | 2023-08-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ROVE ENGINEERING | IMPERIAL | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | The third-party contractor was digging to install a water line when they damaged a unknown, unmarked cutback stub.
Southern California Gas Company | N | IMPERIAL | IMPERIAL | 2023-10-05 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 52 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ARB | LAKE FOREST | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | Second party contractor miss marked gas service and bored right into it.
Southern California Gas Company | N | IMPERIAL | IMPERIAL | 2023-10-09 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ARIZONA PIPELINE | RIALTO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Second party contractor damaged a plastic service while hand digging to expose it.
Southern California Gas Company | N | IMPERIAL | IMPERIAL | 2023-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | GREGORIO ESRADA | IMPERIAL | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was excavating when they damaged a 1/2 plastic gas service. The contractor did not have a USA.
Southern California Gas Company | N | IMPERIAL | NILAND | 2023-10-19 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | ARIZONA PIPELINE | CORONA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Second party contractor damaged service while hand digging to expose it.
Southern California Gas Company | N | IMPERIAL | NILAND | 2023-05-24 | Operator excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NPL | EASTVALE | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Approved. No USA
Southern California Gas Company | N | IMPERIAL | WESTMORLAND | 2023-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 2 |  | FERNANDO FLORES | WESTMORLAND | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged 1/2in service while digging to install fence. Homeowner did not have USA ticket. ETR monitored the area and stood by until Gas Ops arrived. Gas was not migrating to foundation and was more than 15? away from home. ETR handed over responsibilities to Gas Ops upon their arrival at 7:30 p.m. Gas was under at 8:15 p.m. and repairs were completed at 9:00 p.m. There were no evacuations, street closures, media, or injuries. Gas Ops took underground samples after repairs and found 0 detected.
Southern California Gas Company | N | KERN | ARVIN | 2023-05-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | EVANGELINA VALENCIA | ARVIN | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hit gas service line while digging to remove tree.
Southern California Gas Company | N | KERN | ARVIN | 2023-06-27 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CINDY TRUMP INC | LA HABRA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Code 1 due to evacuations, Contractor hit gas steel service while grading
Southern California Gas Company | N | KERN | ARVIN | 2023-11-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | IGNACIO ROCHA | ARVIN | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | KERN | ARVIN | 2023-05-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CENTRAL VALLEY ASPHALT | LINDSAY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | damaged service caused by contractor potholing with shovel
Southern California Gas Company | N | KERN | BAKERSFIELD | 2023-09-26 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ELITE CONSTRUCTORS | BAKERSFIELD | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Elite Constructors damaged the 1/2'''' plastic service while excavating to install a bollard around the gas meter. Elite marked out the service but failed to properly protect the facilities while excavating. Crew repaired damage.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2023-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 3 |  | R&I COMMUNICATIONS | BLOOMINGTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor R&I communications struck gas service with shovel
Southern California Gas Company | N | KERN | BAKERSFIELD | 2023-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | ZAC DECKER | BAKERSFIELD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The 1/2'''' plastic service was damaged due to the 3rd party excavator failing to notify USA prior to working.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2023-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | UEC | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | UEC worker damaged 1/2 CTS service while hand digging. Worker was aware of the marks and is aware of USA DIG Alerts
Southern California Gas Company | N | KERN | BAKERSFIELD | 2023-05-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MILLAN LANDSCAPE | BAKERSFIELD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Millan Landscaping failed to notify USA prior to excavating resulting in damage to the plastic service. Crew altered to repair the damage.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2023-09-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | R&I COMMUNICATIONS | BLOOMINGTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | R&I communications damaged 1/2 plastic service while digging to expose gas line. Gas lines were accurately marked.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2023-03-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | OUTDOOR DIMENSIONS LLC | ANAHEIM | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party Contractor failed to call in USA prior to excavating resulting in damage in to the 2in plastic service.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2023-08-07 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ELITE CONSTRUCTORS | BAKERSFIELD | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was digging to install meter guards and hit 1/2 CTS service.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2023-11-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | UNDERGROUND EXPRESS COMPANY | BAKERSFIELD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA
Southern California Gas Company | N | KERN | BAKERSFIELD | 2023-10-05 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ELITE CONSTRUCTORS | BAKERSFIELD | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | Elite Constructors damaged the 1/2'''' plastic service while excavating to install a bollard around the gas meter.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2023-07-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ACCURATE TRENCHING INC | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 1/2 plastic stub while digging around gas line, failed to maintain proper clearance
Southern California Gas Company | N | KERN | BAKERSFIELD | 2023-01-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HERRERA MASONRY | BAKERSFIELD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Developer damaged 1/2 plastic line while excavating on private property, USA ticket not valid.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2023-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JAIME JOEL HURTADO | BAKERSFIELD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The third party contractor damaged the 1/2'''' plastic service while excavating to repair a water leak.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2023-09-14 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HERMAN WEISSKER | BAKERSFIELD | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor was digging around gas line and shovel slipped which caused it to hit our 1/2 plastic service.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2023-04-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | TIMOTHY BACHMAN | BAKERSFIELD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged facility while performing work on his property. He was advised to call USA prior to excavating, in the future.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2023-07-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MONTE VISTA | BAKERSFIELD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Gas service was hit with shovel while digging in yard to plant trees. Did not call USA
Southern California Gas Company | N | KERN | BAKERSFIELD | 2023-06-16 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ELITE CONSTRUCTORS INC | BAKERSFIELD | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Do to the force needed to move the soil, the contractor should have used additional caution. This damage could have been prevented by taking additional time and smaller shovel scoops. A Stop the job, was initiated for this damage and I went over the gas standard with the contractor.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2023-02-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DOD CONTSTRUCTION | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor used equipment to dig causing damage to SCG facilities , failed to keep clearance from SCG marks
Southern California Gas Company | N | KERN | BAKERSFIELD | 2023-05-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | JASON FRANTZ | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor damaged gas service while digging with backhoe
Southern California Gas Company | N | KERN | BAKERSFIELD | 2023-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | DIRT WORX INC | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor 1/2 plastic service line while digging
Southern California Gas Company | N | KERN | BAKERSFIELD | 2023-07-25 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SE PIPELINE | SANTA FE SPRINGS | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | SE Pipeline damaged the 1/2'''' plastic service while tunneling to install the new gas service. The crew arrived and capped the damage/old service. SE finished installing the new service. Marks made by SE Pipeline crew.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2023-10-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CROAD ELECTRIC | BAKERSFIELD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged the 1/2 plastic service while probing to locate gas line. Contractor failed to notify USA before doing any excavating.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2023-09-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 40 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | JUAN G | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Homeowner hit svc with shovel.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2023-02-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | UNDERGROUND EXPRESS COMPANY | LAKE ISABELLA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Underground Express damaged service line while excavating to pothole the service.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2023-06-15 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 20001 |  |  | NA | UNDER GROUND EXPRESS COMPANY | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Underground Express failed to pothole the 2'''' gas main prior to boring. This resulted in damage to the main. Crew arrived, controlled gas and repaired damage. FD on scene prior to Control. Marks accurate.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2023-02-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DO IT RIGHT PLUMBING | BAKERSFIELD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Do it Right plumbing damaged the 1/2in plastic service while digging to install a water tank. Inadequate protection of pipe while digging.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2023-04-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | OSCAR SINGER | BAKERSFIED | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage to 1/2 plastic service caused by homeowner, no USA called in.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2023-05-31 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ZAKERY KOSTER | BAKERSFIELD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged the service while trenching for electrical. No USA was called.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2023-03-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | ELLOY CRUZCRANBROOK | BAKERSFIELD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third Party Contractor failed to call in USA prior to trenching which resulted in damage to the 1/2in plastic service.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2023-01-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | GEORGE WHITE | BAKERSFIELD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner failed to notify USA prior to excavating for electrical resulting in damage to the plastic service.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2023-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | RELIANCE FENCE CO INC | BAKERSFIELD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Reliance Fence Co failed to notify USA prior to work which resulted in damage to the 1/2'''' plastic service.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2023-01-31 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | RGF PROPERTIES | BAKERSFIELD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged service while excavating for landscaping and block wall. Crew reparied service and customer was restored.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2023-11-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | MICHAEL G OLOCOTT | BAKERSFIELD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging over service and hit with shovel. No USA
Southern California Gas Company | N | KERN | BAKERSFIELD | 2023-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CAL WATER | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | California Water Service damaged 1/2'''' CTS plastic service while probing for water leak. All gas lines were accurately marked.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2023-06-23 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 4 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 64 |  | STATEWIDE | NIPOMO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 4 plastic main, no USA ticket
Southern California Gas Company | N | KERN | BAKERSFIELD | 2023-08-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ACCURATE TRENCHING INC | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Accurate Trenching damaged the 1'''' plastic service while trenching for utilities. Accurate Trenching failed to hand excavate prior to using the backhoe as well as failing to properly protect the service once it was exposed.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2023-03-23 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | J''S GARDEN WORKS LLC | BAKERSFIELD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscape company excavated without USA causing damage to the 2in plastic main.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2023-07-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | KERN POOLS | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Kern Pools damaged the service while potholing to locate service. Plastic service was correctly marked within the work area.
Southern California Gas Company | N | KERN | BAKERSFIELD | 2023-01-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | UNDERGROUND EXPRESS COMPANY | LAKE ISABELLA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Party Damage to plastic service while potholing. Service was correctly marked.
Southern California Gas Company | N | KERN | CALIFORNIA CITY | 2023-05-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | LINE WORKS | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Socalgas line was struck while pot Holing. Line was marked properly.
Southern California Gas Company | N | KERN | CALIFORNIA CITY | 2023-01-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | LINE WORKS CONSTRUCTION INC | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit us while boring for fiber
Southern California Gas Company | N | KERN | CALIFORNIA CITY | 2023-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | LINE WORK CONSTRUCTION INC | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor working on telecommunications (fiber) and sevard gas service.
Southern California Gas Company | N | KERN | CALIFORNIA CITY | 2023-05-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | J & A RIVERA COMMUNICATION INC | FONTANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor bored without exposing service
Southern California Gas Company | N | KERN | CALIFORNIA CITY | 2023-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MOORE PIPELINE | RIDGECREST | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor hit unmarked cutback while digging sewer
Southern California Gas Company | N | KERN | CALIFORNIA CITY | 2023-01-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CLEAR VIEW HOMES | CALIFORNIA CITY | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Contractor hit service with backhoe when digging. Did dnot have valid USA. Crew arrived and made repairs.
Southern California Gas Company | N | KERN | DELANO | 2023-10-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | EVERARADO ALVARADO | DELANO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The homeowner failed to call 811 prior to excavating to repair a sewer leak in his front yard. While excavating, the homeowner damaged the 1/2'''' plastic service resulting in a leak.
Southern California Gas Company | N | KERN | DELANO | 2023-02-21 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | INNOVATIVE CONSTRUCTION & ELECTRIC INC | CLOVIS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor damaged 2in plastic main. Marks were off due to locator jumping on to electrical lines. Street closed and fire evacuated one building with 6 people.
Southern California Gas Company | N | KERN | DELANO | 2023-05-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | OLGA ERANGAN | DELANO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner damaged 1/2 plastic service while digging with shovel. Failed to notify USA.
Southern California Gas Company | N | KERN | FRAZIER PARK | 2023-08-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HEATHER SIBLEY | FRASIER PARK | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service damaged by customer. no USA on excavation
Southern California Gas Company | N | KERN | FRAZIER PARK | 2023-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SIERRA CONSTRUCTION | BAKERSFIELD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Plastic service line hit while excavating for new water main line. 1/2 IPS service damaged with excavator.
Southern California Gas Company | N | KERN | FRAZIER PARK | 2023-12-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | SCEI | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hand excavating around the exposed 1/2'''' plastic service. The service was correctly located. Damaged the service with a tunnel bar.
Southern California Gas Company | N | KERN | MC FARLAND | 2023-11-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MARTIN CONSTRUCTION | BAKERSFIELD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was pot-hole digging to replace fence. SVC was hit with no USA called in.
Southern California Gas Company | N | KERN | MC FARLAND | 2023-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | JUAN ULLOA | DELANO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service line was hit inside private property. No USA ticket.
Southern California Gas Company | N | KERN | MC FARLAND | 2023-01-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | TROY CONSTRUCTION | PASO ROBLES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | EIR opened due to hit service line by homeowner''s contractor while hand digging in private property.
Southern California Gas Company | N | KERN | MC FARLAND | 2023-01-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | TROY CONSTRUCTION | PASO ROBLES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Troy Construction damaged the 1/2in plastic service while attempting to pothole the service. Crew arrived and controlled gas before making permanent repairs.
Southern California Gas Company | N | KERN | MC FARLAND | 2023-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HUMBERTO | MCFARLAND | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While excavating to repair a fence, the homeowner damaged the 1/2 plastic service. There was a USA for water repairs that was called in by JM Engineering. However, the homeowner did not have his own USA for fence installation.
Southern California Gas Company | N | KERN | MC FARLAND | 2023-03-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | EFI ENGINEERING | TUSTIN | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Code 1 due to mismark by SCG employee. Contractor hit service line while boring.
Southern California Gas Company | N | KERN | MOJAVE | 2023-06-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | S AND B CONSTRUCTION | YORBA LINDA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hit service potholing for location
Southern California Gas Company | N | KERN | ROSAMOND | 2023-08-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HILL VIEW HOMES INC | LANCASTER | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor hit service while excavating for electric utilities. The crew was notified and arrived on the scene to make perm repairs.
Southern California Gas Company | N | KERN | TAFT | 2023-04-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | KENNETH NIELSEN | TAFT | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged 1/2 cts gas service while digging with backhoe. Did not call in USA.
Southern California Gas Company | N | KERN | TEHACHAPI | 2023-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | SIERRA CONTRUCTION | BAKERSFIELD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor hit stub while excavating for electric utilities.
Southern California Gas Company | N | KERN | TEHACHAPI | 2023-08-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | TEHACHAPI PLUMBING | TEHACHAPI | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit service. No USA
Southern California Gas Company | N | KERN | TEHACHAPI | 2023-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | TIMOTHY PETERSON | TEHACHAPI | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor hit service with shovel while excavating near building. No current USA ticket on file.
Southern California Gas Company | N | KERN | TEHACHAPI | 2023-06-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | TEHACHAPI PLUMBING | TEHACHAPI | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit service installing septic
Southern California Gas Company | N | KERN | WASCO | 2023-12-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SAMUEL HUGHES | WASCO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 CTS plastic service hit with post hole digger for frence post.
Southern California Gas Company | N | KERN | WASCO | 2023-01-11 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | WATER ASSOCIATES LLC | BAKERSFIELD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Water Associates LLC damaged the 4in PL main while excavating for electrical. Main was not marked. Locator stated the contractor informed him that the damaged area would not be in their scope of work but did not document the conversation in his notes.
Southern California Gas Company | N | KERN | WASCO | 2023-02-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LANDSCAPE DEVELOPMENT | BAKERSFIELD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The contractor failed to hand expose the service before trenching for irrigation.
Southern California Gas Company | N | KINGS | CORCORAN | 2023-06-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 31 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | ANTHONY NICHOLS | CORCORAN | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged a 1/2 plastic gas line, crew made permanent repair, contractor dug prior to USA ticket being valid.
Southern California Gas Company | N | KINGS | HANFORD | 2023-03-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | KENNETH SILVA | HANFORD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged a 1/2 plastic gas line, crew made permanent repairs. Homeowner was educated about USA law.
Southern California Gas Company | N | KINGS | HANFORD | 2023-10-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | BRENDA VASQUES | HANFORD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Crew arrived to 3rd Party damage to 1/2 Plastic SVC. SVC damaged by auger from fence workers using Auger.
Southern California Gas Company | N | KINGS | HANFORD | 2023-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NORBERTO MEZA AND JUAN GONZALEZ | HANFORD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant damaged a 1/2 plastic gas line while digging to plant a tree in his front yard, crew made permanent repairs.
Southern California Gas Company | N | KINGS | HANFORD | 2023-02-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | GOOD GUY ELECTRIC AND SOLAR | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged a 1/2 plastic gas line while excavating for electrical work, crew made permanent repairs.
Southern California Gas Company | N | KINGS | HANFORD | 2023-05-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | H C D CONSTRUCTION | VISALIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged a 1 plastic gas stub, crew made permanent repairs. Damaging party not on site upon supervisor and crew arrival, damaged facility found taped back.
Southern California Gas Company | N | KINGS | HANFORD | 2023-07-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | DANIEL HEROLD | NA |  | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged a 1/2 plastic gas line while excavating to install electrical line, crew made permanent repairs. Homeowner had a valid USA ticket but the damaging contractor did not.
Southern California Gas Company | N | KINGS | HANFORD | 2023-03-30 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | RT NELSON COMPANY INC | IVANHOE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | End of 2 plastic gas main damaged by 3rd party contractor, crew made permanent repairs, 3rd party contractor was educated about USA law.
Southern California Gas Company | N | KINGS | HANFORD | 2023-07-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ANDERSON AND BALLOU INC | SANGER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | A 1 plastic gas line was damaged by a 3rd party contractor while excavating to install a sewer line, contractor failed to pot hole the gas line as required.
Southern California Gas Company | N | KINGS | HANFORD | 2023-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | IRISH ELECTRIC | TULARE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged a 1/2 plastic gas line, crew made permanent repairs.
Southern California Gas Company | N | KINGS | HANFORD | 2023-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | MATTOS UNDERGROUND CONSTRUCTION INC | LATON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Excavating to make sewer repairs, they damaged an unmarked 1 plastic gas line.
Southern California Gas Company | N | KINGS | HANFORD | 2023-11-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RT TRENCHING | VISALIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged a 1 plastic gas line while excavating for electrical project. Contractor did not have a valid USA ticket.
Southern California Gas Company | N | KINGS | LEMOORE | 2023-02-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ASR ENGINEERING | FRESNO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor damaged a 1 plastic gas line, crew made permanent repairs. ETD failed to mark the damaged gas line, ETD will be counseled.
Southern California Gas Company | N | KINGS | LEMOORE | 2023-03-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | PG&E | SELMA | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Contractor damaged service while digging for electric box. USA called in as emergency ticket was in process of being responded to. Repairs made by oncall crew.
Southern California Gas Company | N | KINGS | LEMOORE | 2023-05-02 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 4 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | 1 OAK CONSTRUCTION | CLOVIS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged a 4 plastic main, location future subdivision, no outages, crew made permanent repairs.
Southern California Gas Company | N | KINGS | LEMOORE | 2023-08-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | ROBERT BUCKLEY | LEMOORE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | SCG responded to third party damage, upon SCG crew arrival, a 1/2 plastic gas line was found damaged by occupant while excavating to install a fence post. Damaging party did not have a valid USA ticket as required.
Southern California Gas Company | N | KINGS | LEMOORE | 2023-09-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | SPECIALIZED UTILITY SERVICES PROGRAM | SACRAMENTO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | 3rd party contractor SUSP was excavating to install a new water line, they damaged a 1/2 IPS gas line, SCG crew made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | AGOURA HILLS | 2023-04-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | JUAN C ALMANGUER LANDSCAPE | AGOURA HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor damaged 1/2 PLA service while trenching. contractor did not have valid usa
Southern California Gas Company | N | LOS ANGELES | AGOURA HILLS | 2023-12-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ROGELIO''S LANDSCAPING | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit 1/2 plastic service while digging trench with hand tool.
Southern California Gas Company | N | LOS ANGELES | AGOURA HILLS | 2023-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | KELLY MORRIS | AGOURA HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Homeowner was digging to install electric line to backyard when damage to 1/2 PE svc occurred. Homeowner had USA and it was marked correctly. Excavator failed to exercise proper caution in the process of excavating.
Southern California Gas Company | N | LOS ANGELES | AGOURA HILLS | 2023-04-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | CM ELECTRIC | SIMI VALLEY | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | service expose with tape around damaged area. Per Chris, line hit while hand digging Hytou Concrete. CM Electrics USA ticket was closed for no delineation requesting a resend. Lius Perez is the owner of Hytou. Hytou did not have a USA ticket. Chris stated Hytou was digging under CM Electric''s USA ticket.
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2023-09-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 5 |  | AIT KIKI CHAN | ALHAMBRA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor struck 1/2 CTS service resulting in 5 outages. Contractor failed to call USA for sewer replacement.
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2023-04-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | HHS CONSTRUCTION | ONTARIO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | ETD, had marked service using company measurement buried wire in concrete. Contractor failed to call back usa or ETD to have marks verified after riser pigtail was exposed seeing it point in the opposite direction of marks, this damage could of been prevented.
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2023-07-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HOMEOWNER | ALHAMBRA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner failed to call USA and dug and damaged 1/2 CTS gas service on private property.
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2023-05-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | ECO CONCRETE INC | SAN GABRIEL | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damage no USA
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2023-02-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 12 |  | SHIVAM PATEL | ALHAMBRA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Worker hit service with shovel while digging.
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2023-12-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | WORKMAN CONSTRUCTORS | POMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor struck service with shovel while potholing.
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2023-12-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DOMINGUEZ GENERAL ENGINEERING | POMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor performing water improvement for the City of Alhambra struck half inch service.
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2023-05-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 6 |  | CITY OF ALHAMBRA | ALHAMBRA | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Damage To Company Property, 1 inch plastic service damaged by contractor with backhoe causing 6 outages. Crew replaced 5 ft of 1 inch plastic. Fire department was on scene. Street closures by city prior to hit line. Street closures from Larch to Alhambra. Once repairs made customer performed restore of all units.
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2023-09-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | JIMENEZ DEMOLITION INC | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor struck 1/2-inch service with backhoe while excavating for water proofing job. Location was clearly marked out and struck within the delineation marks. Contractor failed to hand dig over service.
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2023-12-14 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 6 |  | DORECK CONSTRUCTION | PICO RIVERA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor struck main with backhoe while digging to install water service.
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2023-01-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | OCT CONST | FONTANA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor failed to calling USA prior to doing any work on private property and damaged gas service with wooden stake.
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2023-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 25 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NIZAR KAILANI | ALHAMBRA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner was using a trenching machine to install sprinkler system and struck and damaged 1/2 plastic service
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2023-12-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ALL CONSTRUCTION | POMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor struck service with shovel while potholing.
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2023-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DORECK CONSTRUCTION | PICO RIVERA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | City contractor performing water main work struck 1/2 service with backhoe. USA active, struck within delineated area.
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2023-10-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DORECK CONSTRUCTION | PICO RIVERA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor digging with shovel and struck plastic service.
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2023-10-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DORECK CONSTRUCTION | PICO RIVERA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Failed to use caution and failed to pothole and proceeded to use heavy equipment to trench in the area of a plastic marked service causing damage.
Southern California Gas Company | N | LOS ANGELES | ALHAMBRA | 2023-02-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 7 |  | ZENG LIANGJIE | WALNUT | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was using the claw section of the hammer to dig around broken sewer lateral and struck a 1 plastic service.
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2023-10-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ENVIRONMENTAL LANDSCAPE | ALTADENA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was trenching using an excavator and hit our 1/2 plastic service. No USA.
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2023-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 33 | 28 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | E&R CONSTRUCTION | BALDWIN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor damaged gas service while backfilling trench. There was a valid USA, the marks were correct.
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2023-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 34 | 27 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | M&M SHOWER PAN CO | SUN VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor damaged a 1/2 plastic gas service while installing a sewer lateral. USA was called in and located. The contractor did not maintain the marks.
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2023-11-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | RAMOS NAVARRO EDUARDO | PACOIMA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | A third-party contractor damaged a 1/2 gas service with a pickax while trenching to install a sewer line. No USA.
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2023-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GAGNIER LANDSCAPE | SIERRA MADRE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscape contractor digging for installation of new irrigation lines with no USA ticket damaged 1/2pla gas service approximately 10'' from gas meter with shovel. Company crew arrived and completed permanent repairs.
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2023-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DAMON MCCARTHY | ALTADENA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA was called. Contractor was digging with shovel when 1/2 service was damaged.
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2023-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 32 | 16 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | GORILLA JUNK SERVICES | LONG BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | upon arrival the crew found a plastic service that was pinched back and duct taped. The crew dug up the service, squeezed and installed a plastic cap.
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2023-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MONKEY WRENCH PLUMBING HEATING AND AIR | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging with shovel for customer to repair/replace sewer when PLA service was damage. No USA
Southern California Gas Company | N | LOS ANGELES | ALTADENA | 2023-02-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | YVANEZ JUAN CARLOS | ALTADENA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging with shovel for a clean out for the sewer. Did not called for USA
Southern California Gas Company | N | LOS ANGELES | ARCADIA | 2023-12-13 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | GENTRY BROTHERS INC | IRWINDALE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Grading to repave alley. Our gas line was properly and accurately marked.
Southern California Gas Company | N | LOS ANGELES | ARCADIA | 2023-02-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | WESTERN SUPREME ROOTER INC | ARCADIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging for sewer repairs
Southern California Gas Company | N | LOS ANGELES | ARCADIA | 2023-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ROOTER HERO | POMONA | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | OHS crew arrived to find broken and blowing due to 3rd party contractor digging with shovel to make sewer repairs. Did not call for USA until after the damage.
Southern California Gas Company | N | LOS ANGELES | ARCADIA | 2023-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | INTRACORP | NEWPORT BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Grading for new construction, struck 1/2 IPS service stub with backhoe. Stub was not marked out.
Southern California Gas Company | N | LOS ANGELES | ARCADIA | 2023-06-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | RODEO CONSTRUCTION AND MANAGEMENT INC | WALNUT | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging with backhoe to install new yard line
Southern California Gas Company | N | LOS ANGELES | ARCADIA | 2023-08-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 29 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 5 |  | INTERNATIONAL LINE BUILDERS | JURUPA VALLEY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Third party contractor damaged a 1/2 gas service while potholing utility
Southern California Gas Company | N | LOS ANGELES | ARCADIA | 2023-08-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | EVA NEWMANN BOEHONG | ARCADIA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractors cut through the service performing work for the homeowner.
Southern California Gas Company | N | LOS ANGELES | ARCADIA | 2023-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | LAMASI IRON WORKS | EL MONTE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor damaged a 1/2 gas service while digging to install a fence post. The located marks were accurate.
Southern California Gas Company | N | LOS ANGELES | ARLETA | 2023-02-10 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 32 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | ARIZONA PIPELINE | CORONA | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | Crew hit 3/4 service while trying to find the broken drill rod
Southern California Gas Company | N | LOS ANGELES | ARLETA | 2023-08-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | AQUA SCAPE PLUMBING | ARLETA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was back filling a pool on the property and damaged a steel riser. Mini excavator was the machinery that caused the damaged and the service was marked out with paint and flags.
Southern California Gas Company | N | LOS ANGELES | ARLETA | 2023-08-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | LADWP | GRANADA HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | LADWP was excavating with a backhoe to install a test station, and in the process they struck a 1/2?IPS service. They did have a valid USA, however, they failed to follow procedures of using hand tools when excavating above SoCalGas lines.
Southern California Gas Company | N | LOS ANGELES | ARLETA | 2023-05-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | LADWP | CHINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | DWP damaged 1/2 SOCAL GAS service with backhoe.
Southern California Gas Company | N | LOS ANGELES | ARLETA | 2023-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | LADWP | GRANADA HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | DWP is working on installing a new water main on Arleta Avenue . The Forman stated a piece of asphalt broke and damaged a 1/2 plastic service. After inspecting the damaged section of service line, it appears they hit the line with the and backhoe and pulled it. SoCalGas crew responded to the damage and controlled the release of gas. The crew then made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | ARTESIA | 2023-04-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ALFARO COMMUNICATIONS CONSTRUCTION INC | COMPTON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Upon arrival found blowing gas from pot hole done by contractor performing directional boring. After further investigation was determined that they hit a cut back stub service for 11960 Artesia Blvd. abandoned at SMC for permanent repairs
Southern California Gas Company | N | LOS ANGELES | ARTESIA | 2023-11-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | JUAN PABLO RAMIREZ | ARTESIA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Gas svc was damaged while digging trench. No USA was called.
Southern California Gas Company | N | LOS ANGELES | AZUSA | 2023-11-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | EXCLUSIVE WIRELESS RESOURCES | ANAHEIM | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Crew was digging for power conduit and hit 1in plastic service. Crew had a USA ticket that was expired but service was still accurately marked.
Southern California Gas Company | N | LOS ANGELES | AZUSA | 2023-09-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  |  | NA | CITY OF AZUSA WATER | AZUSA | CA | N | Y | Yes | No | No | No | No | No | No | Water crew called in emergency USA and dug before we could mark lines. They bent back a plastic service in steel casing. Not leaking but plastic was replaced from SMC to riser just in case the plastic got stretched or bent.
Southern California Gas Company | N | LOS ANGELES | BALDWIN PARK | 2023-11-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | MR DESIGN & BUILD INC | PASADENA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractors hit a CTS service with shovel while digging to install electrical lines.
Southern California Gas Company | N | LOS ANGELES | BALDWIN PARK | 2023-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | C ONE COMMUNICATION INC | FONTANA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit cts service while boring in conduit. the 3rd party did not have their own USA called in.
Southern California Gas Company | N | LOS ANGELES | BALDWIN PARK | 2023-11-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | JAY LY | ROSEMEAD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Crew working on house damaged a plastic service while digging for water line. Service was unmarked because crew did not have a USA ticket.
Southern California Gas Company | N | LOS ANGELES | BALDWIN PARK | 2023-04-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | DEBRA VEZINA | BALDWIN PARK | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service damaged by customer fixing water line. Gas under control at 15:00. Crew replaced 1 foot of 1/2inch CTS and riser. once permanent repairs made, Ambient reading in home taken with no gas indications found. No evacuation, no gas migration. No fire department on site.
Southern California Gas Company | N | LOS ANGELES | BALDWIN PARK | 2023-06-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | GREENFIELD CONSTRUCTION | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor should not be billed for damage. Section of homes were abandoned, fenced off, and were getting ready to be demolished. It''s unknown but it seems like a vagrant was looking for copper and ended up severing a 1/2cts gas service.
Southern California Gas Company | N | LOS ANGELES | BELL | 2023-03-09 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 22 |  | D CORP | NUEVO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor working for water company hit mismarked 2 PE main. Valid USA. Company locator had interference when trying to locate main, he went by footage but measured off wrong PL location. No evacuations Altered main with 2 electrofusion couplings.
Southern California Gas Company | N | LOS ANGELES | BELL GARDENS | 2023-09-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CHARLES KING COMPANY | SIGNAL HILL | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | While digging to replace sewer manhole 1 plastic service was damaged with backhoe.
Southern California Gas Company | N | LOS ANGELES | BELL GARDENS | 2023-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | JESUS MENDOZA | BELL GARDENS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Dist crew found 1/2 CTS damaged by home owner trying to upgrade sewer.
Southern California Gas Company | N | LOS ANGELES | BELL GARDENS | 2023-02-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HEYDE AGUILAR | BELL GARDENS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Unlicensed contractor working on sewer line with no USA damaged 1/2 plastic service with shovel.
Southern California Gas Company | N | LOS ANGELES | BELL GARDENS | 2023-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 23 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ALONSO CHAVEZ | BELL GARDENS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | USA called after the damage. PLA service hit with shovel while digging for bollard.
Southern California Gas Company | N | LOS ANGELES | BELLFLOWER | 2023-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | KMH CONSTRUCTION | GARDENA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | NA
Southern California Gas Company | N | LOS ANGELES | BELLFLOWER | 2023-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | JOSE GOMEZ | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit our service when digging for homeowner.
Southern California Gas Company | N | LOS ANGELES | BELLFLOWER | 2023-04-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SCALES CONTRACTING | LONG BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging to install electrical wire contractor hit plastic service with shovel.
Southern California Gas Company | N | LOS ANGELES | BELLFLOWER | 2023-10-13 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  |  | NA | BELCO ELECTRIC | CHINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit gas main while boring.
Southern California Gas Company | N | LOS ANGELES | BELLFLOWER | 2023-09-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ROBERT BRKICH CONSTRUCTION | MONROVIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit line that was marked correctly because an abandoned line was right next to the live line. The live line was still in the bank after they exposed what they thought to be the only service, so they dug with the excavator and pulled out the live gas service.
Southern California Gas Company | N | LOS ANGELES | BELLFLOWER | 2023-04-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | L C R EARTHWORK ENGINEERING | ONTARIO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA city contractor hit 2 service with excavator
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2023-03-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 36 | 36 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MESOLITE LLC | MISSION HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Williams Pipeline was excavating to install water main in doing so they pull on the existing gas service which was a insert, But didn''t cause the service to leak sent a crew to make repairs anyway
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2023-03-07 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | WILLIAMS PIPELINE CONTRACTORS INC | MISSION HILLS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | contractor was trenching and struck a mismark gas service
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2023-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DENNIS W MILLS CONSTRUCTION | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party struck steel service with jack hammer while trenching for Irrigation line. No USA
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2023-03-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | WILLIAMS PIPELINE CONTRACTORS | MISSION HILLS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | On 3/28/2023 Mid City LA on call Distribution was notified of a hit service at 1118 Coldwater Canyon Dr Beverly Hills California 90210, The contractor had a valid USA ticket, and the ticket was addressed by SCG. SCG Markings were off by about 15 feet. Distribution arrived, controlled gas, and made permanent repairs to service line.
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2023-09-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | AG PLUMBING | ANAHEIM | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor cut into 1/2 plastic service with Sawzall while excavating for drain repair with no USA. SCG controlled gas, and made permanent repairs to service.
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2023-06-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | WILLIAMS PIPELINE CONTRACTORS | MISSION HILLS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | The third party pothole and found pipe where the gas service was L&M. As the contractor excavated the service was found feet away from the mark.
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2023-06-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ADVANCED CABLE TECH | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | The third party contractor is trenching in the neighborhood for a pretty large spread. The contractor pothole and found a black pipe that appears to be a conduit of some kind. He felt confident that he found pipe at the marked location. Continued trenching when he found the found the service with the backhoe. I spoke with the contractor about his other findings with our services while potholing in other sections of the delineation. and asked him if any of our steel services looks like the damage pipe or the fond pipe. He stated they look like the damage pipe. I asked him to call SCG or myself to get an ETD to verify any pipe that does not look similar. He agreed to do that moving forward.
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2023-04-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | WILLIAMS PIPELINE CONTRACTOR INC | MISSION HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival 3rd party damaged a 1/2 cts service. It was done by a back hoe operator. The plastic service mark lined up where the service was found and damaged.
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2023-11-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | WILLIAMS PIPELINE CONTRACTORS | MISSION HILLS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd Party contractor with valid USA hit unmarked 1/2 plastic service.
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2023-04-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | RUDY HERNANDEZ | MISSION HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor hit mark gas service with a shovel when pot holing
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2023-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | VIDO ARTUKOVICH & SON | SOUTH EL MONTE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | The damaged 3/4 STL service was marked incorrectly. The mark was 20 ft away from excavation.
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2023-04-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | VICTOR DEL TORO | BEVERLY HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner & Contractor didn''t call for a USA ticket and hit own gas service while digging for gas house line. Homeowner & Contractor was advised by company crew to call Underground Service Alert at 811 whenever digging, even when in private property.
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2023-07-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 11 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ZOX INDUSTRIES | SANTA MONICA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | NA
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2023-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ELISEO DURAN PLUMBING | BEVERLY HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working on trench for drain and water line when they damaged our 1/2 CTS service. Crew responded and cut service back to PL to prevent further damage. Hollywood supervision was made aware of cutback. Contractor did not have a USA ticket on file.
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2023-10-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | WA RASIC CONSTRUCTION | LONG BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party stuck gas service with backhoe. Failed to locate gas service. Invalid dig ticket.
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2023-02-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CITY OF BEVERLY HILLS | BEVERLY HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party damaged PLA gas service, no USA.
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2023-11-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ROBERT HALL EXCAVATING | LA CRESCENTA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor struck 3/4 steel gas service with auger while drilling for support beams. No valid USA was called.
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2023-07-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ADVANCED POOL LANDSCAPING AND PLASTERING | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party pool contractor installing water lines hit service with hand tools while digging with no USA. SCG Responded, controlled gas, and made permanent repairs to service.
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2023-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | GNL BACKHOE SERVICES | BEVERLY HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Demoing when damaging the gas service 1/2 plastic
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2023-04-12 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 1 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 14 |  | BEVERLY HILLS WATER DEPARTMENT | BEVERLY HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | City of BH Public Works crew cleaning out a drain, damaged a 2 PA main. NO USA for location.
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2023-10-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 38 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CEILBRIGHT SERVICES | BEVERLY HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was renovating the house and while digging by hand for suport columns they damged the 1/2 plastic service with a shovel
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2023-08-03 | Third party excavation damage | Main | Polyethylene Pipe | Trencher | 2 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | FORE CONTRACTORS INC | NORCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Party contractor was trenching to install electrical conduits hit & damaged a 2 PLA main. Area was marked correctly. Marks visible.
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2023-02-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | YOUNG UNDERGROUND CONST | WINNETKA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1 PE service damaged by 3rd party contractor installing electrical conduits. Current USA ticket. Service marked out correctly.
Southern California Gas Company | N | LOS ANGELES | BEVERLY HILLS | 2023-09-27 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 3 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7769 |  | 0 |  | TIM GREENLEAF ENGINEERING | HUNTINGTON BEACH | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | The locator completed the ticket. Upon excavating the third party company damaged the 3 steel main. Main was altered for permanent repairs.
Southern California Gas Company | N | LOS ANGELES | BRADBURY | 2023-11-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | INTERNATIONAL LINE BUILDERS | RIVERSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | OHS crew arrived to find 3rd party contractor was digging to locate gas line, but hit our 1/2 svc with a shovel.
Southern California Gas Company | N | LOS ANGELES | BRADBURY | 2023-11-02 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 3 | 0 |  | 0 | 0 |  | 3177 |  | 26 |  | PERRY C THOMAS CONSTRUCTION | MONROVIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor digging for sewer hit a 2in plastic main that was clearly marked. 2in damage ignited while crew was working near it and 3 employees were injured.
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2023-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | WALKERS FENCING | SAN FERNANDO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1/2 inch plastic service. No USA
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2023-08-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CITY OF BURBANK | BURBANK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas service and did not call for an USA ticket.
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2023-04-19 | Third party excavation damage | Miscellaneous/Other | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | JC BUILDERS | NEWBURRY PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working on private property damaged inserted cts service. Contractor did not have a valid USA. Company crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2023-03-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | Q CONSTRUCTION INC | SUNLAND | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor did not have USA for his work. Contractor was excavating in yard and hit the gas service.
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2023-06-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 3 |  | R AND N ELECTRIC | VAN NUYS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | hit plastic service
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2023-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | PACIFIC TRADES COMPANY | BURBANK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hired unlicensed contractor to perform work at residence. While excavating, contractor damaged service line.
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2023-09-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MANNY NEYMARIAN | BURBANK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage service
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2023-04-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | GREEN WORKS | WOODLAND HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor failed to call 811. Damaged 1/2 cts pla service
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2023-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CHI CONSTRUCTION | ANAHEIM | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged existing 3/4 STL service cutback.
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2023-10-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MARIPOSA TREE MANAGEMENT | IRWINDALE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor damaged 1/2 plastic service.
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2023-03-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | CHI CONSTRUCTION | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd company contractor damaged 1 P service while trying expose
Southern California Gas Company | N | LOS ANGELES | BURBANK | 2023-11-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 15 |  | CMR CONSTRUCTION | VALENCIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit service while installing bollard.
Southern California Gas Company | N | LOS ANGELES | CALABASAS | 2023-11-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ARTS CUSTOM HOMES | CALABASAS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Developer was digging for footing install when he struck plastic service line with shovel. No USA
Southern California Gas Company | N | LOS ANGELES | CALABASAS | 2023-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ART HODGES | SIMI VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Damaged by hand tools
Southern California Gas Company | N | LOS ANGELES | CALABASAS | 2023-03-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | GLADIATOR CONSTRUCTION | ENCINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Code 1, Damaged service
Southern California Gas Company | N | LOS ANGELES | CALABASAS | 2023-01-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | THOUSAND OAKS PLUMBING | THOUSAND OAKS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged the 1/2 plastic service while performing plumbing repairs for the home owner.
Southern California Gas Company | N | LOS ANGELES | CALABASAS | 2023-04-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | R G GRADING AND RENTAL | AGOURA HILLS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor was digging with an EXPIRED ticket hit marked stub service
Southern California Gas Company | N | LOS ANGELES | CALABASAS | 2023-08-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | J&H ENGINERRING | CAMARILLO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit line no active USA ticket found contractor did not have ticket number hand tool damage.
Southern California Gas Company | N | LOS ANGELES | CALABASAS | 2023-05-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | LAGMAN CONSULTING INC | CHATSWORTH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage to company property 3 party.
Southern California Gas Company | N | LOS ANGELES | CALABASAS | 2023-10-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | STREGEN GROUP | AGOURA HILLS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 3rd party contractor hit our gas line with shovel. USA has expired
Southern California Gas Company | N | LOS ANGELES | CALABASAS | 2023-10-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | CALIFORNIA BORING | HIDDEN HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While boring to install sewer line, Cal bore hit 1 plastic line with machine.
Southern California Gas Company | N | LOS ANGELES | CANOGA PARK | 2023-12-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 10 |  | LADWP | CANOGA PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While digging to install new water main DWP struck plastic line with backhoe.
Southern California Gas Company | N | LOS ANGELES | CANOGA PARK | 2023-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | REYES VENEGAS | WOODLAND HILLS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging to build a ADU owner builder hit plastic line with shovel. No USA.
Southern California Gas Company | N | LOS ANGELES | CANOGA PARK | 2023-06-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | THE BNYN INC | VALLEY VILLAGE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged line by demo crew did not pothole to verify.
Southern California Gas Company | N | LOS ANGELES | CANOGA PARK | 2023-06-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | NA | VALLEY VILLAGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged caused by developer did not call USA company notified through neighbor odor complaint.
Southern California Gas Company | N | LOS ANGELES | CANYON COUNTRY | 2023-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 30 |  | REAL PRIME CONSTRUCTION INC | VAN NUYS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA, contractor broke 1 Plastic service with jackhammer. Crew arrived and made repairs and reinstated service.
Southern California Gas Company | N | LOS ANGELES | CANYON COUNTRY | 2023-05-08 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  | 18 |  | A AND L COMMUNICATIONS | NORTH HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Pot holed and exposed main but damaged by directional bore due to rod locator not calibrated.
Southern California Gas Company | N | LOS ANGELES | CANYON COUNTRY | 2023-03-07 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | S & S DIRECTIONAL DRILLING INC | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was digging for phone coduit and forgot that main crossed trench in a 45. Main was marked accurately.
Southern California Gas Company | N | LOS ANGELES | CANYON COUNTRY | 2023-06-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | DESERT PLUMBING INC | AGUA DULCE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | contractor hit 1 IPS Service while excavating for install new water service line
Southern California Gas Company | N | LOS ANGELES | CARSON | 2023-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LUIS RAMOS | CARSON | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage Caused By Homeowner Digging To Make Repairs To Sewer/Water Line. Cut Out 1Ft Section Of Damaged 1/2 Cts Pipe And Installed 2 1/2 Cts Couplings As Well As New 1 Ft Section Of 1/2 Cts Pipe.
Southern California Gas Company | N | LOS ANGELES | CARSON | 2023-05-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 38 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | BRANDYWINE HOMES | IRVINE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1 stub damaged by construction crew installing rebars for foundation, no USA was called in by company. Crew squeezed and capped stub to complete repairs.
Southern California Gas Company | N | LOS ANGELES | CARSON | 2023-02-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | LUCAS BUILDERS INC | LA HABRA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor caused damage to 1 gas service when trenching for new water main. USA was up to date and visibly marked.
Southern California Gas Company | N | LOS ANGELES | CARSON | 2023-04-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | 3 FLOWERS CONSTRUCTION | NA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging in yard to install fence and pavers damaged service with hand tools. Contractor did not have a USA. Company crew made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | CASTAIC | 2023-11-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | HOT LINE CONSTRUCTION | SANTA PAULA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party damaged plastic service with a shovel. USA was current and marks visible.
Southern California Gas Company | N | LOS ANGELES | CASTAIC | 2023-02-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GM PLUMBING SEPTIC AND SEWER INC | PALMDALE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | hit service.
Southern California Gas Company | N | LOS ANGELES | CASTAIC | 2023-01-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | RAMIREZ JORGE | VENTURA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA. 1/2 inch service was found ripped and tied together by contractor on site. Distribution was called out to make repairs. No street closures, police, or media. No injuries. No evacuations.
Southern California Gas Company | N | LOS ANGELES | CERRITOS | 2023-10-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SPORS TURF INNOVATIONS | SAN DIMAS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging out tree roots to remove stump, a shovel hit and cracked a coupling. There were USA markings but they were not for the company that hit the line.
Southern California Gas Company | N | LOS ANGELES | CERRITOS | 2023-05-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 7 |  | MUIR-CHASE PLUMBING | LOS ANGELES | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor hit service line while excavating. Crew popped open a pothole upstream of leak and squeezed service.
Southern California Gas Company | N | LOS ANGELES | CERRITOS | 2023-08-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 6 |  | JT SITE SERVICES INC | UPLAND | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1 plastic service damaged with backhoe digging to install walls for trash enclosure.
Southern California Gas Company | N | LOS ANGELES | CERRITOS | 2023-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | STORMCON INC | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractors hit 1 service with backhoe while pot holing for gas line.
Southern California Gas Company | N | LOS ANGELES | CHATSWORTH | 2023-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | FLAMINGO CONSTRUCTION | STUDIO CITY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged our riser with a tunnel bar while exposing our service so that they can run a new line for a fire pit.
Southern California Gas Company | N | LOS ANGELES | CHATSWORTH | 2023-03-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CM BACKHOE SERVICE INC. | RIVERSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | while digging for sewer install contractor struck plastic service line with mini excavator. contractor didnt look around area for marks which where on the street and g on curb
Southern California Gas Company | N | LOS ANGELES | CHATSWORTH | 2023-01-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | LM BROTHERS AND ASSOCIATES INC. | CHATSWORTH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service was hit by contractor while digging out Trees. No Valid USA
Southern California Gas Company | N | LOS ANGELES | CHATSWORTH | 2023-06-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | PULTE HOMES | PLEASANTON | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor digging for sewer installation on new housing track damaged service stub with backhoe. Area was marked with flags and paint. USA ticket was expired at time of excavation. Company crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | CHATSWORTH | 2023-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HONEST PLUMBING | RANCHO CASCADES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit our gas service while digging for sewer. No USA
Southern California Gas Company | N | LOS ANGELES | CHATSWORTH | 2023-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | BROOKS LANDSCAPE CONSTRUCTION | CHATSWORTH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor was trenching to install a new drain line. While in the process, they struck a 1/2? plastic service. The contractor had a valid USA, but failed to follow standard procedures.
Southern California Gas Company | N | LOS ANGELES | CHATSWORTH | 2023-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | BROOKS LANDSCAPE CONSTRUCTION | CHATSWORTH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor hit gas service with shovel while digging for drainage
Southern California Gas Company | N | LOS ANGELES | CLAREMONT | 2023-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | JA SALAZAR CONSTRUCTION | LA HABRA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Hit plastic service line. Crew was installing water here and hit the service. The service wouldn''t locate so it was marked by measurements. The marks were not correct.
Southern California Gas Company | N | LOS ANGELES | CLAREMONT | 2023-05-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 32 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MKP CONSTRUCTION | FONTANA | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor should be charged for damage due to not having an updated USA ticket.3rd party contractors were working on/around the sewer and severed a 1/2 plastic gas service with a shovel. Damaging Contractor stated that the pipe was improperly installed but 2nd party contractor installed the gas services and mains to the approved depth that was provided by the developer.
Southern California Gas Company | N | LOS ANGELES | CLAREMONT | 2023-07-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | OC CONCRETE | CORONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Pipe was damaged while company was grading to install the footings for a new property.
Southern California Gas Company | N | LOS ANGELES | COMMERCE | 2023-04-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | ALMA FLORES | COMMERCE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractors damaged in the process of digging out trench for new sewer line.
Southern California Gas Company | N | LOS ANGELES | COMPTON | 2023-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 38 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ANDY GUMP CONSTRUCTION | NORTH HOLLYWOOD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor crew damaged 1 plastic service while digging hole to replace power pole on private property, service was damaged by shovel.
Southern California Gas Company | N | LOS ANGELES | COMPTON | 2023-04-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 44 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | DAVID COBIAN | COMPTON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging in yard for tree removal damaged gas service. Contractor did not have a valid USA. Company crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | COMPTON | 2023-08-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | FERNANDO GONZALEZ | LONG BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service while digging footing for block wall. Contractor did not have a valid USA.
Southern California Gas Company | N | LOS ANGELES | COMPTON | 2023-07-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 38 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | JR CONSTRUCTION | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service was correctly marked with paint and flags. Crew was digging trench to the address for a new gas line when the operator dug into 1IPS plastic service with backhoe. No emergency services on site, no injuries or death to report.
Southern California Gas Company | N | LOS ANGELES | COMPTON | 2023-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | MOLINAR DESIGNS | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractors installing water service for the customer damaged a 1/2 CTS plastic service with shovel while digging trench. No USA was called in.
Southern California Gas Company | N | LOS ANGELES | COMPTON | 2023-08-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 38 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | WA RASIC | LONG BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival, ETR found a damaged line by contractor using a backhoe. ETR issued an RFA for distribution and stood by. Distribution arrived and repaired damaged line.
Southern California Gas Company | N | LOS ANGELES | COMPTON | 2023-08-10 | Third party excavation damage | Main | Steel | Boring Equipment | 2 | 38 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CITY OF COMPTON | COMPTON | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Crew working for Compton Department of Water installing a water service, bored into 2 steel main and damaged pipe. Main was correctly marked, and marks were visible.
Southern California Gas Company | N | LOS ANGELES | COMPTON | 2023-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 38 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | WA RASIC | LONG BEACH | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Locator failed to mark delineated area. Gas service was not located.
Southern California Gas Company | N | LOS ANGELES | COMPTON | 2023-11-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | WA RASIC CONSTRUCTION | LONG BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1/2 plastic service damaged by contractors digging with shovel in parkway to install fire hydrant.
Southern California Gas Company | N | LOS ANGELES | COVINA | 2023-06-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | WIND HOME CONSTRUCTION | COVINA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner was digging to make improvements to his property and hit our 1/2 cts svc. Crew showed up to find broken and blowing. repairs svc using two couplings and piece of pla 1/2 cts.
Southern California Gas Company | N | LOS ANGELES | COVINA | 2023-02-22 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 1 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | LDR GOLDEN INC. | MISSION VIEJO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor partially grading for new foundation pushed against steel service stretching steel and causing steel to leak at three separate points 18'' before meter. No USA notification by contractor. Crew arrived and performed service abandonment at SMC.
Southern California Gas Company | N | LOS ANGELES | COVINA | 2023-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | CARTER CONSTRUCTION | COVINA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | OHS crew arrived to find broken and blowing due to 3rd party contractor hitting our 3/4 svc with mini excavator while digging to remove tree stump.
Southern California Gas Company | N | LOS ANGELES | CUDAHY | 2023-07-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 23 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | BIG CITY DEMO | DOWNEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | USA called. Location marked. Cust was trenching for new facilities and pulled on service.
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2023-06-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 18 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | INNOCENTI CONSTRUCTION | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor dug into service; broken and blowing. Crew arrived on scene and were able to control gas and alter the service.
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2023-09-07 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 28 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | INNOCENTI CONSTRUCTION | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor installing water line hit 2 main with sharp shooter crew dug up control holes and altered main and made repairs.
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2023-06-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 18 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | INNOCENTI CONSTRUCTION | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor dug into 1/2 ips service damaging it. Crew arrived on scene, pinched and altered the service.
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2023-10-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | INNOCENTI CONSTRUCTION INC | SAN DIMAS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor dug into 1/2 plastic service while operating a backhoe.
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2023-09-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GONZALEZ PLUMBING | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Third party contractor damaged plastic service while working on replacing sewer lateral.
Southern California Gas Company | N | LOS ANGELES | CULVER CITY | 2023-12-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NA | CULVER CITY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Private contractor damaged plastic service with shovel while trenching.
Southern California Gas Company | N | LOS ANGELES | DIAMOND BAR | 2023-04-17 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NPL | BREA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | All USA''s were valid, contractor struck gas service while exposing Edison to shoot new gas service in.
Southern California Gas Company | N | LOS ANGELES | DIAMOND BAR | 2023-02-28 | Operator excavation damage | Main | Polyethylene Pipe | Hand Tools | 1 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 3 |  | NPL | BREA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Crew spoke with contractor and explained that they need to be more careful when digging around plastic gas lines.
Southern California Gas Company | N | LOS ANGELES | DIAMOND BAR | 2023-09-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ILB | JURUPA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractors damaged. SCG pipe was marked.
Southern California Gas Company | N | LOS ANGELES | DIAMOND BAR | 2023-06-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HUANLONG MAI | UPLAND | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit service while trenching to install sewer. no USA called crew spoke with contractors and explained how important it is to call Dig Alert.
Southern California Gas Company | N | LOS ANGELES | DIAMOND BAR | 2023-09-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 47 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | NORWALK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Doty Bros working for Walnut Valley Water Co, did not notify USA and began excavating to replace water service under USA ticket obtained by Walnut Valley Water. While digging with backhoe operator pulled on 1/2 PA service, stretched and snapped service.
Southern California Gas Company | N | LOS ANGELES | DOWNEY | 2023-10-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | ROOTER GUARD | VAN NUYS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor nicked 1/2 CTS line with shovel while excavating to install a clean out. Contractor did not have a USA ticket
Southern California Gas Company | N | LOS ANGELES | DOWNEY | 2023-04-19 | Operator excavation damage | A service line with no excess flow valve installed | Material not known | Hand Tools | 0 | 40 | 36 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | SOCALGAS | ALISO VIEJO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The call was placed by an anonymous caller. tech arrived on the scene to find distribution working on the service line making repairs. Technician comments indicate no damage to company facilities.
Southern California Gas Company | N | LOS ANGELES | DOWNEY | 2023-08-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | DAMON INC | DOWNEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Customer was digging trench for gas company who was going to come out and upgrade service from 1/2 line to 1 line. Hit line with shovel.
Southern California Gas Company | N | LOS ANGELES | DOWNEY | 2023-07-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | RICARDO GONZALEZ | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 1/2 CTS service branch while excavating with shovel to put in water line. Crew repaired section with new pipe and couplings.
Southern California Gas Company | N | LOS ANGELES | DOWNEY | 2023-08-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HIGH VOLTAGE ELECTRIC | BELL GARDENS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Arrived on site, crew was working, 1/2 CTS pipe was sliced and a coupling was all it took to repair.
Southern California Gas Company | N | LOS ANGELES | EAST RANCHO DOMINGUEZ | 2023-11-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BIG BEN ENGINEERING | IRVINE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Damage to gas service. USA was called in but failed to be marked.
Southern California Gas Company | N | LOS ANGELES | EL MONTE | 2023-12-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | JORDANAIR INC | GLENDORA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor struck service with shovel while digging.
Southern California Gas Company | N | LOS ANGELES | EL MONTE | 2023-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SAN GABRIEL WATER DISTRICT | ROSEMEAD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | San Gabriel water company struck 3/4 service with backhoe. Service previously abandoned at the PL, crew abandoned at SMC to eliminate. No USA.
Southern California Gas Company | N | LOS ANGELES | EL MONTE | 2023-05-30 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CHRISTENSEN BROTHERS GENERAL ENGINEERING TEAM INC | APPLE VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor conducting sewer work for the city of El Monte struck 3/4 steel service which was correctly marked. Contractor tried to cover up marks with dirt and altered their delineation marks. Original Marks located and photos taken. Permanent repairs made by altering the service. No fire, no police, and streets were blocked off previously for the work that was in progress.
Southern California Gas Company | N | LOS ANGELES | EL MONTE | 2023-02-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | INNOVATIVE CONSTRUCTION SOLUTIONS | COSTA MESA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit service with back hoe.
Southern California Gas Company | N | LOS ANGELES | EL MONTE | 2023-09-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DOMINGUUZ | POMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor struck service while digging trench.
Southern California Gas Company | N | LOS ANGELES | EL MONTE | 2023-10-04 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 4 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | DOTY BROS | NORWALK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | City contractor performing water main work struck abandoned AB Nipple cap on 4-inch steel stub.
Southern California Gas Company | N | LOS ANGELES | EL MONTE | 2023-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 2 | 45 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GREENFIELD LANDSCAPING & MAINTENANCE | HACIENDA HEIGHTS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor removing tree stump struck 2-inch steel service.
Southern California Gas Company | N | LOS ANGELES | EL SEGUNDO | 2023-09-21 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 4 | 120 | 112 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 18502 |  |  | NA | TTS ENGINEERING | STANTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | NA
Southern California Gas Company | N | LOS ANGELES | EL SEGUNDO | 2023-01-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 24 | 21 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CAM DEVELOPMENT CORP | EL SEGUNDO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor was machine excavating trench with mini-excavator to install concrete footing when he struck our 1/2 PE gas service. He folded service back and didn''t dig outside of 2'' tolerance zone. Paint and flags were installed and accurate. USA was valid. Contractor at fault. Damage Prevention was onsite as well and agrees.
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2023-09-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | SAUL GRANDE | HUNTINGTON PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Contractor cut into casing damaging CTS line
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2023-10-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | GENESIS CO | ENCINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor digging around pool to install waterfall damaged 1/2 plastic service with hand tools. Contractor did not have a valid USA.
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2023-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | D PARRISH CONSTRUCTION LLC | MARINA DEL REY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging to install fence, contractor struck plastic line with a post hole digger. Crew showed up and made permanent repairs. No USA
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2023-01-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ROBERTO DOMINGUEZ | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit plastic line while digging
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2023-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HG COMMUNICATIONS INC. | CHATSWORTH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit gas service while hand digging. No USA
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2023-03-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | JOHN LAUTERBACH | CHATSWORTH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was replacing a water drain line for the customer and while in the process of excavating, they struck a 1/2? plastic inserted service. SoCalGas crew responded and controlled the release of gas. The crew then made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2023-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | EDS LANDSCAPING | LANCASTER | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | landscapers hit branch plastic service line with shovel. crew made repairs and called in restore
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2023-02-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | FRANK MORAN | ENCINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was excavating with hand tools and stuck a 1/2? plastic service with a sharpshooter. The contractor did not have a valid USA. SoCalGas crew responded and controlled the release by pinching the line. They then made permanent repairs
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2023-04-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MONOPOLY TEXTILE | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was utilizing a skid steer with a breaker and while in the process, they struck a 1/2 plastic service. SoCalGas already had an Service Maintenance order to perform an abandonment and contractor started work prior to SoCalGas crew performing the necessary work. SoCalGas crews arrived on scene and found the existing condition. The crew cut back the service to responded and controlled the release and then completed the abandonment.
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2023-10-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Incorrect markings. DWP hit out gas service.
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2023-07-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 37 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | HOME PLUMING AND REMODELING | VALLEY VILLAGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging to install pipe in trench. contractor struck plastic service line with shovel. crew showed up and made permanent repairs
Southern California Gas Company | N | LOS ANGELES | ENCINO | 2023-04-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | STYLE BUILDING | ENCINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third Party Contractor was removing a tree located on the side of the home which is where Socalgas service runs. During the process the contractors struck a 1/2 plastic service with a shovel. The contractor did not have a valid USA. The crew responded and controlled the release of gas and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | GARDENA | 2023-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | AQP PROPERTY MANAGEMENT | SOUTH GATE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 1/2'''' plastic service with shovel while trenching. USA was not called.
Southern California Gas Company | N | LOS ANGELES | GARDENA | 2023-10-24 | Third party excavation damage | Main | Steel | Boring Equipment | 4 | 59 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | H&M COMMUNICATIONS | COMPTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 4 steel main was struck with Accu Bore equipment by third party contractors installing telecommunications.
Southern California Gas Company | N | LOS ANGELES | GARDENA | 2023-08-02 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MAX OUT INC | GARDENA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was digging to install a bollard when he accidently hit the plastic service. Service was marked out with flags.
Southern California Gas Company | N | LOS ANGELES | GARDENA | 2023-11-01 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 35 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | CALIFORNIA PAVING AND GRADING CO | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Grading to extend curb and gutter when they struck our 3/4 steel service. No USA.
Southern California Gas Company | N | LOS ANGELES | GARDENA | 2023-09-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | DIVERSIFIED COMMUNICATIONS SERVICES | BREA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While digging trench and trying to expose the gas line, pipe was struck with a shovel. Sub contractor taped 1 PE pipe. USA was valid and marks visible
Southern California Gas Company | N | LOS ANGELES | GARDENA | 2023-05-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GEC20 | GARDENA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Bobcat operator damaged shallow service. Service only 11 when damaged in private property.
Southern California Gas Company | N | LOS ANGELES | GARDENA | 2023-12-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | IGNACIO GONZALES | GARDENA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor digging out footing for a fence hit and severed already exposed gas line with a shovel. No USA
Southern California Gas Company | N | LOS ANGELES | GARDENA | 2023-11-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | OLTMAN''S CONSTRUCTION | WHITTIER | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage to service when demolishing building. Service was not marked.
Southern California Gas Company | N | LOS ANGELES | GARDENA | 2023-04-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | POPPIN BACKHOE SERVICES | LONG BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA was requested prior to start of work.
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2023-11-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | WA RASIC CONSTRUCTION | LONG BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor was working on sewer in public street and struck our 1/2 inch plastic service within 24 inches of delineations. Valid USA. Contractor did not maintain marked delineations.
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2023-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | NAHID LACIURA | GLENDALE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA.
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2023-11-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | EUNICE SAUL | GLENDALE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Plumber hit 1/2 IPS with shovel while excavating trench for sewer line.
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2023-10-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | QUALITY STRIPING SERVICES | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor replacing damaged bollards while re-striping parking lot and hit 1/2 CTS service with shovel. No USA.
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2023-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 13 |  | FC CONSTRUCTION | GLENDALE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor partially severed our 3/4 service. There were several knicks found along entire service line from a shovel. Service had to be altered as a result. Contractor was digging trench for sewer line. There was no USA.
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2023-05-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | SOCAL PLUMBING AND ROOTER | GLENDALE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1/2cts service with shovel while trenching for new water service. No USA
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2023-08-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NOEL ALADAZYAN | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Contractor was grading driveway and damaged our 1/2 CTS with a shovel. There was no active USA.
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2023-06-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BAIRON | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Contractor was repairing retaining wall and clearing existing concrete to replace driveway. While attempting to excavate and remove tree stumps along wall, struck our 1/2 service with a shovel.
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2023-06-19 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DANIEL PASILLA | GLENDALE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was excavating to remove drain with electric jack hammer and struck 1/2 inch steel service. No USA
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2023-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | HEYDORFF CONSTRUCTION | BURBANK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was digging with mini excavator and hit 1 plastic service while trenching to install sewer line. No USA.
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2023-08-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | G POGHOSYAN | GLENDALE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit gas service while digging for irrigation. No USA
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2023-02-16 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | VCI CONSTRUCTION LLC | UPLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Marked 2 main damage not within 24
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2023-03-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | J DE SIGIO CONSTRUCTION INC | BALDWIN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working for City of Glendale already excavated for water main install. Contractor dropped shovel on top of our service and severed line. Service was already exposed. There was a valid USA and within 24 inches of delineations. There was also a G on the curb.
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2023-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 4 |  | GLENDALE WATER AND POWER | GLENDALE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Valid USA. Locator error on markings. Municipality was trenching to install electrical lines and hit 1/2 CTS service that was mismarked with backhoe.
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2023-11-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NA | GLENDALE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1/2 IPS with shovel
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2023-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HOMEOWNER | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | LOS ANGELES | GLENDALE | 2023-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ETVART GARAPITIAN | GLENDALE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hired family members to replace sewage line for ADU and struck 1/2 service.
Southern California Gas Company | N | LOS ANGELES | GLENDORA | 2023-01-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | BOUDREAU PIPELINE CORPORATION | COROMA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was digging an excavation to install water pipe and damaged a 1/2 PE CTS Gas Line that was encased. The working area was all dirt and there was a fresh paint marking on a rock over the service near the damaged. Backhoe Operator thought all utilities were abandoned in the work area. Contractor should be billed for the damage.
Southern California Gas Company | N | LOS ANGELES | GLENDORA | 2023-08-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | GENTRY BROTHERS INC | BALDWIN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | All gas services and mains where marked correctly. They were open trenching and hit this service and snagged another steel service nearby.
Southern California Gas Company | N | LOS ANGELES | GLENDORA | 2023-04-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | R Z CONSTRUCTION | UPLAND | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Pipe was damaged by contractor digging to install a retaining wall. Pipe was hit by a mini excavator.
Southern California Gas Company | N | LOS ANGELES | GLENDORA | 2023-05-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | RZ CONCRETE INC | UPLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor should be billed for the damage due to negligence on protecting a gas line that was marked/flagged.
Southern California Gas Company | N | LOS ANGELES | GLENDORA | 2023-05-01 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 4 |  | SPECIALIZE AND LAING CONSTRUCTION | GLENDORA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor struck 2 inch main with backhoe while excavating for electrical conduit. Gas was under control at 5:42pm. No Evacuations. Fire department departed once gas was under control. Permanent repairs made.
Southern California Gas Company | N | LOS ANGELES | GLENDORA | 2023-11-21 | Third party excavation damage | A service line with an excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | GENTRY BROTHERS INC | IRWINDALE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service was struck by backhoe operator while prepping for paving operations. Line was marked.
Southern California Gas Company | N | LOS ANGELES | GLENDORA | 2023-07-31 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | GENTRY BROTHERS INC | BALDWIN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Water project damage. Hit a stub on an abandoned service line. Contractor knew the line was there and dug with a backhoe anyway. Line was marked correctly, and it was hit within the delineated area.
Southern California Gas Company | N | LOS ANGELES | GLENDORA | 2023-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  |  | NA | GENTRY BROTHERS INC | IRWINDALE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Service damaged by contractor. service was marked correctly at SMC and at curb face but between the two marks the service did a dog leg that was not in GIS. There was no way for the locator to know the dog leg existed and this is where the contractor hit the service. They were not at fault and the locator was not at fault either. This is a records/mapping issue. adam al-rayess
Southern California Gas Company | N | LOS ANGELES | GLENDORA | 2023-12-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ROBERT RIGGO | CHINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Developer was using backhoe to install drainage when backhoe damaged 1/2 PLA service. No USA
Southern California Gas Company | N | LOS ANGELES | GLENDORA | 2023-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 55 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | ECKER CONCRETE | GLENDORA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | company trenching for new development trenched through newly installed service. it was clearly marked.
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2023-09-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MIKE KARAYAN | GRANADA HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damage service while digging for sewer. No USA
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2023-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ALBERT AND EDWIN | GRANADA HILLS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was excavating for new sewer line without a valid USA . While in the process, the third party contractor struck a 1/2 plastic service with a shovel.
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2023-11-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | OLMOS GARDEN AND DESIGN | GRANADA HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Damaged by mini excavator
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2023-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SILVA BOGHOSIAN | GRANADA HILLS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | home owner was digging to install gas line when they struck plastic branch with shovel. crew showed up and made permanent repairs to line
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2023-08-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | GOP ELECTRIC | GRANADA HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While digging to install conduit contractor struck plastic service line with shovel. Crew showed up and made permanent repairs
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2023-06-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CLEMEMTE PALMS | THERMAL | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA, contractor damaged 1/2 CTS made repairs, damage prevention notified Alex Alvarez
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2023-08-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 4 |  | JUAN ESPARZA | ARLETA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3 party damage to company property.
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2023-11-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ASPHALT PROFESSIONALS | NEWBURY PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Peforming street work with a valid USA. The contractor hit a 1/2 plastic service with hand tools that was marked correctly and within the delineation area.
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2023-09-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | SARA GREEN | GRANADA HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was excavating without a valid USA to install a sub pump at the front left corner of the home. While in the process, the homeowner struck a 1/2 plastic service. SoCalGas crew responded, controlled the release, then made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2023-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NON STOP PLUMBING | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | damaged plastic service
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2023-04-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 2 |  | J&J CUSTOM POOLS | GRANADA HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor digging for pool hit our service with shovel. No USA
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2023-03-24 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  | 8 |  | SWE SEWER SOLUTIONS & ENGINEERING | GLENDORA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | while digging to install sewer line plumber hit 2 plastic line with excavator. no USA. crew squeezed line and made repairs
Southern California Gas Company | N | LOS ANGELES | GRANADA HILLS | 2023-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | GRANADA HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor struck a 1/2? plastic service while excavating for a sewer line with hand tools. The contractor failed to call in a USA prior to performing the work. SoCalGas crew responded and controlled the release by pinching the service. The crew then made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | HACIENDA HEIGHTS | 2023-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LY ENGINEERING INC | SAN BERNARDINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 3/4 STL service. No USA .
Southern California Gas Company | N | LOS ANGELES | HACIENDA HEIGHTS | 2023-12-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MS LANDSCAPE & GARDEN SERVICE INC | STANTON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage due to not notifying 811. Damaging an 1/2 gas service with a shovel while digging.
Southern California Gas Company | N | LOS ANGELES | HACIENDA HEIGHTS | 2023-11-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | ALVAREZ BUILDING COMPANY | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit service line while digging to remove tree roots.
Southern California Gas Company | N | LOS ANGELES | HACIENDA HEIGHTS | 2023-06-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | INTERNATIONAL LINE BUILDERS | JURUPA VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor hit service while digging
Southern California Gas Company | N | LOS ANGELES | HACIENDA HEIGHTS | 2023-02-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | THE MAGIC SNAKE PLUMBING SERVICES INC | JURUPA VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit plastic service under the water line they were exposing.
Southern California Gas Company | N | LOS ANGELES | HACIENDA HEIGHTS | 2023-03-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | MOTIVE INSFRASTRUCTURE SOLUTIONS | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Crew spoke with contractor about using extreme caution when working around our PLA lines.
Southern California Gas Company | N | LOS ANGELES | HACIENDA HEIGHTS | 2023-10-02 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 23 |  | SAN GABRIEL WATER COMPANY | EL MONTE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Water company was digging with backhoe to make repairs on a leaking water valve, they did not call for a USA and hit our 1-inch main causing broken and blowing.
Southern California Gas Company | N | LOS ANGELES | HARBOR CITY | 2023-05-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ISAAC LOTZOS | HARBOR CITY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner was excavating for grading and struck our service line with a shovel. The owner did not have USA.
Southern California Gas Company | N | LOS ANGELES | HARBOR CITY | 2023-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 5 |  | AL GARCIA PLUMBING | TORRANCE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging a trench with a shovel to install a new gas houseline when they struck our service. The contractor did not have USA. Crews made repairs.
Southern California Gas Company | N | LOS ANGELES | HARBOR CITY | 2023-05-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | A AND A CONSTRUCTION | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging a trench for a sewer damaged plastic service with hand tools. Contractor did not have a valid USA. Company crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | HAWTHORNE | 2023-06-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 24 | 21 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JOSE BERMUDEZ | HAWTHORNE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner Jose Bermudez was machine excavating trench with mini excavator to install drainage when he struck our 1/2 PLA gas service. NO USA, homeowner AT FAULT.
Southern California Gas Company | N | LOS ANGELES | HAWTHORNE | 2023-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 21 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | ROTO ROOTERS SERVICES INC | ALHAMBRA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | NA
Southern California Gas Company | N | LOS ANGELES | HAWTHORNE | 2023-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 24 | 21 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | IVAN ELIZARARAS | HAWTHORNE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working for homeowner denies doing any damage. No USA, contractor had entire trench opened and multiple utilities exposed.
Southern California Gas Company | N | LOS ANGELES | HAWTHORNE | 2023-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 21 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | BELCO ELECNOR GROUP | CHINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor had previously exposed pipe and had it marked on sidewalk. He accidently hit the 1/2'''' IPS plastic gas line while digging around it.
Southern California Gas Company | N | LOS ANGELES | HAWTHORNE | 2023-06-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | KRISTIAN DAVALOS | HAWTHORNE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No U.S.A. ticket called in
Southern California Gas Company | N | LOS ANGELES | HERMOSA BEACH | 2023-05-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DRAINS GUYS | GARDENA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor Drain Guys was machine excavating with chipping gun hammer to install new water service when they struck our 1/2 PLA gas service. No USA, contractor was at fault
Southern California Gas Company | N | LOS ANGELES | HERMOSA BEACH | 2023-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 27 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MAYA CONSTRUCTION INC | LAWNDALE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit 1/2" plastic line that was marked correctly.
Southern California Gas Company | N | LOS ANGELES | HERMOSA BEACH | 2023-10-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | HHS CONSTRUCTION | ONTARIO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Hit 1'''' plastic service while excavating for ground bed for AT&T. They had a valid USA but service was not marked.
Southern California Gas Company | N | LOS ANGELES | HERMOSA BEACH | 2023-11-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | FERNANDO MORALES | HERMOSA BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was digging near gas line for service alteration scheduled for the next day when they hit service with a pick. No USA
Southern California Gas Company | N | LOS ANGELES | HERMOSA BEACH | 2023-05-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | PEARCE CONSTRUCTION | HERMOSA BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Customer did not fully expose the line within the delineated area.
Southern California Gas Company | N | LOS ANGELES | HERMOSA BEACH | 2023-03-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ROGER HUNTER | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor was hand excavating trench w/ shovel to install conduit when they struck our 1/2 gas service. Marked accurate, USA valid, contractor AT FAULT
Southern California Gas Company | N | LOS ANGELES | HIDDEN HILLS | 2023-07-31 | Third party excavation damage | Main | Polyethylene Pipe | Grader/Scraper | 2 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  |  | NA | UNITED EXCAVATION GROUP INC | WEST HILLS | CA | N | Y | Yes | No | Yes | No | No | Yes | Yes | 3rd party contractor hit our gas main while grading. USA ticket expired. Failed to pot hole before digging or grading with machinery
Southern California Gas Company | N | LOS ANGELES | HIDDEN HILLS | 2023-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | UNLICENSED DAY LABORERS | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | while digging to install fence post, laborers hired by homeowner struck plastic line with shovel, crew showed up and made permanent repairs
Southern California Gas Company | N | LOS ANGELES | HIDDEN HILLS | 2023-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | UNITED EXCAVATION GROUP INC | WEST HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service with excavator while digging trench. Contractor did have a valid USA and marks where clear and visible, flags and paint.
Southern California Gas Company | N | LOS ANGELES | HIDDEN HILLS | 2023-10-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | UNITED EXCAVATION | WEST HILLS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging for basement on empty lot damaged 1/2 CTS plastic service. Contractor did not have a valid USA on file.
Southern California Gas Company | N | LOS ANGELES | HIDDEN HILLS | 2023-07-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | WESTERN BUILD CONTRUCTION | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging contractor struck plastic line with shovel
Southern California Gas Company | N | LOS ANGELES | HOLLYWOOD | 2023-10-16 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | JJL LANDSCAPING | LA PUENTE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor didn''t call for a USA ticket and nicked gas service with shovel while digging to repair sewer line.
Southern California Gas Company | N | LOS ANGELES | HUNTINGTON PARK | 2023-11-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | ROOTER HERO PLUMBING | HUNTINGTON PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Contractor hit gas line while digging for sewer
Southern California Gas Company | N | LOS ANGELES | HUNTINGTON PARK | 2023-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  |  | NA | SOCAL EDISON | COMPTON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | Valid USA. Hit by shovel. Digging to replace pole
Southern California Gas Company | N | LOS ANGELES | HUNTINGTON PARK | 2023-10-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | LUIS CORTEZ | HUNTINGTON PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was excavating for a electrical line when they damaged 1/2 PE gas line.
Southern California Gas Company | N | LOS ANGELES | HUNTINGTON PARK | 2023-10-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 17 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | LESLIE RIVAS | HUNTINGTON PARK | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged line using shovel attempting to remove a tree stump
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2023-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 18 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | DAVID VARQUIZO | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor dug into 1 plastic service; broken and blowing. Crew arrived on scene, performed pressure control and altered the service.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2023-10-06 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 18 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | MATTUCI PLUMBING | GARDENA | CA | Y | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor dug into plastic service while hand digging to locate sewer lateral.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2023-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | PHK CONSTRUCTION &AMP; ENTERPRISE | FULLERTON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | third party dug into plastic svc
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2023-06-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 17 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | JOSE FLORES | INGLEWOOD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging trench for electric conduit damaged plastic service. Contractor did not have a valid USA. Company crew responded and made permanent repairs. No fire, police, or media on scene.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2023-01-13 | Third party excavation damage | Meter | Steel | Backhoe/Trackhoe | 0.75 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | PEARCE CONSTRUCTION | TORRANCE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was working at 424 and 426 Warren Ln in Inglewood and exposed service and broke nipple downstream of service valve at 422 Warren Ln. Responding ETR issued RFA for Gas-Ops to confirm no underground indications found. ETR rebuilt MSA at 422 Warren Ln and restored gas service.
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2023-12-06 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 20 | 17 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | CITY LIGHT AND POWER | UPLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit main
Southern California Gas Company | N | LOS ANGELES | INGLEWOOD | 2023-10-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | GOLDEN CREST | INGLEWOOD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | LOS ANGELES | LA CANADA FLINTRIDGE | 2023-10-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | KENDALL HALES | LA CRESCENTA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Excavator dug prior to valid start date. Contractor damaged 2 plastic service and plugged it.
Southern California Gas Company | N | LOS ANGELES | LA CANADA FLINTRIDGE | 2023-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | VINASUA LOPEZ | LA CANADA FLINTRIDGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3 party damage to company property.
Southern California Gas Company | N | LOS ANGELES | LA CANADA FLINTRIDGE | 2023-03-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | SARIAN POOL | MONTEBELLO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | service damaged while contractor was installing a pool
Southern California Gas Company | N | LOS ANGELES | LA CANADA FLINTRIDGE | 2023-11-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | UNLICENSED DAY LABORERS | LA CANADA FLINTRIDGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage to company property. No USA.
Southern California Gas Company | N | LOS ANGELES | LA CANADA FLINTRIDGE | 2023-02-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | L&M CONCRETE | COVINA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party hired by homeowner was digging to remove a rock and also run drainage line. Hit and damaged 1/2 inch plastic service. There was no USA.
Southern California Gas Company | N | LOS ANGELES | LA CANADA FLINTRIDGE | 2023-01-18 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | J.A. CUTTING INC. | PALMDALE | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party Contractor excavated prior to valid USA Tix. There were no delineations or flag present. Contractor struck and damaged double strap clamp on 2 inch steel main and damaged clamps on both sides of double strap with excavator. Contractor stated they were digging for tree removal. Upon further investigation, sewage line was being installed. All damaged clamps replaced for permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LA CRESCENTA | 2023-10-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | CRESCENTA VALLEY WATER DIST | LA CRESCENTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | 3 party damage. Digging outside of USA ticket.
Southern California Gas Company | N | LOS ANGELES | LA CRESCENTA | 2023-11-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CLAUDIA MCCOLLUM | LA CRESCENTA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. 3rd party contractor was trenching for water line replacement and struck 1/2 plastic gas service with shovel.
Southern California Gas Company | N | LOS ANGELES | LA CRESCENTA | 2023-08-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DIBARA MASONRY LLC | NA |  | N | Y | Yes | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage to company property. USA was expired marks not visible.
Southern California Gas Company | N | LOS ANGELES | LA CRESCENTA | 2023-02-02 | Operator excavation damage | Main | Steel | Boring Equipment | 2 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | TEICHERT PIPELINES | CHINO | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | Company contractor damaged steel main by not following company standards. Company crew made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LA CRESCENTA | 2023-07-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GWP | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Valid USA. Municipality failed to hand expose marked 1/2 CTS gas service prior to trenching with backhoe. During the trenching process the 1/2 CTS service was struck and damaged. Company crew made repairs.
Southern California Gas Company | N | LOS ANGELES | LA CRESCENTA | 2023-02-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | HARD HAT ROOTER | BURBANK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was excavating with hand tools to expose the sewer line and while in the process, they damaged a 1/2? plastic service that was inserted in a 3/4? steel line. SoCalGas crew responded and controlled the release by squeezing the service line. The crew then made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LA CRESCENTA | 2023-10-10 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 3 |  | PHILLIPS SPECIALTY PAVING | MONTROSE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third pary contractor breaking driveway to repair root damage with bobcat and ripped out 3/4 steel service line. No USA.
Southern California Gas Company | N | LOS ANGELES | LA HABRA HEIGHTS | 2023-11-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | EDGAR OCHOA | LA HABRA HEIGHTS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Pulled our steel service out of the ground with a mini excavator while working on a retaining wall in La Habra Heights.
Southern California Gas Company | N | LOS ANGELES | LA MIRADA | 2023-11-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | WA RASIC CONSTRUCTION | LONG BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1 IPS service caused by backhoe
Southern California Gas Company | N | LOS ANGELES | LA PUENTE | 2023-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JORDAN PORRAS | LA PUENTE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Damaged PLA service. Crew arrived , controlled leak , and repaired service.
Southern California Gas Company | N | LOS ANGELES | LA PUENTE | 2023-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NOVA STAR CONSTRUCTION | GARDEN GROVE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor broke branch service with backhoe.
Southern California Gas Company | N | LOS ANGELES | LA PUENTE | 2023-05-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | INTERNATIONAL LINE BUILDERS | JURUPA VALLEY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor damaged 1/2 plastic service with shovel. Marked correctly on sidewalk
Southern California Gas Company | N | LOS ANGELES | LA PUENTE | 2023-09-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ROAD PAZ BROS INC | CORONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Sub-contractor for Suburban Water Company was digging an excavation to replace a fire hydrant and their backhoe severed a 1 PE gas service and didn''t have a USA.
Southern California Gas Company | N | LOS ANGELES | LA VERNE | 2023-12-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 9 |  | ACOSTA & SONS | SUN VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | Contractor hit the 1/2 inch service with a small track hoe.
Southern California Gas Company | N | LOS ANGELES | LA VERNE | 2023-03-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DYNACENTRIC KDC INC | LOS ALAMITOS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Excavator damaged service with backhoe due to service not being marked out because of tracer wire issues. Perm repairs made by cutting out damaged portion and fusing in new section. B Cawley 3/24/23
Southern California Gas Company | N | LOS ANGELES | LA VERNE | 2023-06-14 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 2 | 53 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | TEMP POWER SYSTEMS | RANCHO SANTA MARGARITA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor bored through 2in plastic main without a USA ticket.
Southern California Gas Company | N | LOS ANGELES | LAKEWOOD | 2023-12-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 10 |  | BIG BEN ENGINEERING | IRVINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1 plastic service hit with backhoe while digging trench for water main
Southern California Gas Company | N | LOS ANGELES | LAKEWOOD | 2023-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GEOFF WILKINSON | LAKEWOOD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Handyman was digging out roots and hit the service with a shovel. No USA
Southern California Gas Company | N | LOS ANGELES | LAKEWOOD | 2023-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RESCUE ROOTER | ORANGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 plastic service hit by plumber with shovel while digging to make repairs for sewer repair.
Southern California Gas Company | N | LOS ANGELES | LAKEWOOD | 2023-10-07 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 1 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | PASCUAL VILLANUEVA GARCIA | LAKEWOOD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1-inch STL service damaged by homeowner trying to cut out tree roots.
Southern California Gas Company | N | LOS ANGELES | LAKEWOOD | 2023-10-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | STARKS CONSTRUCTION LLC | LAKEWOOD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging trench to put in block wall. Hit line with pick.
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2023-12-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 17 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SOCAL EDISON | LANCASTER | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | NA
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2023-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | RACE COMMUNICATIONS | TEHACHAPI | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Utility company hit service while boring for fiber project.
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2023-11-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | ALLIED PLUS LOW VOLTAGE | LA HABRA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hit service while potholing with sharpshooter.
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2023-12-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | PRIME BORE | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hit service potholing
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2023-12-11 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  |  | NA | ALLIED PLUS LOW VOLTAGE | LA HABRA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Fiber contractor hit main with shovel while potholing.
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2023-05-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ADAME COMMUNICATIONS | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit service while digging with shovel. C/S arrived to meet time. crew showed up and made repairs.
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2023-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CLEAR SOURCE COMMUNICATIONS | LAWNDALE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit service while potholing
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2023-05-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | SENNZA LOW VOLTAGE SYSTEMS | ALPINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit service in street while pot holing
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2023-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | PRIMEBORE | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit service while exposing
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2023-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | PRIMEBORE | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit service while potholing. Crew arrived and made permanent repairs
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2023-08-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | PRIMEBORE | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit service while potholing location
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2023-09-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | CLEAR SOURCE CONSTRUCTION | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit service while potholing
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2023-11-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CLEARSOURCE COMMUNICATIONS | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor that was boring for fiber install hit service with shovel when potholing.
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2023-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | PRIMEBORE DIRECTIONAL BORING CORP | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor with no USA hit service while potholing
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2023-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | WALYBERTH CAZARES | LANCASTER | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner did not call 811 . Struck gas line
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2023-11-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | S&B CONSTRUCTION SERVICES INC | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | No | Boring contractor hit service.
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2023-12-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | EFI ENGINEERING | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit service while potholing
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2023-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | EFI ENGINEERING | TUSTIN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit service while potholing
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2023-11-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | ALLIED PLUS | LA HABRA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor bored and hit service They did not pothole in bore path
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2023-11-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | SOCAL CABLE COMMUNICATION INC | LANCASTER | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit line. Service line was marked correctly
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2023-07-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | CASEMON COMMUNICATIONS | FONTANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor installing fiber hit our service while digging with a shovel. The crew arrived and made repairs and the leak was repaired
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2023-06-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SOCAL CABLE COMMUNICATION | EL MONTE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor was potholing gas service. struck 1/2 ips service with sharp shooter
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2023-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | CASEMON COMMUNICATIONS | FONTANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor hit service with shovel while digging for fiber project. Crew arrived and made perm repairs to service.
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2023-05-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | GLADY PARRA | LANCASTER | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner struck gas line did not know gas line was there did not notify 811
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2023-04-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ADAME COMMUNICATIONS | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | usa was marked properly contractor struck line trying to expose
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2023-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 3 |  | DPT INC | SAN BERNARDINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | NA
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2023-08-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | BLACK ROCK DRILLING GROUP LLC | ALTA LOMA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit service while boring for fiber project. Crew arrived to make repairs.
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2023-09-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | BLACK ROCK DRILLING GROUP LLC | RANCHO CUCAMONGA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contracor hit service while boring for fiber.
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2023-05-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | HORIZON LIGHTING | IRVINE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit service installing fiber
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2023-08-03 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | SAM HILL & SONS INC | VENTURA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit main digging for sewer
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2023-09-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | PRIMEBORE | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit service while potholing. Crew repaired the service
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2023-09-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | PABLO ORTIZ | LANCASTER | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer hit service while digging a hole for a fence post. No USA
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2023-04-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GALVAN UNDERGROUND ENGINEERING INC | MORENO VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit service while boring for fiber optic project.
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2023-06-13 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | RACE COMMUNICATIONS | TEHACHAPI | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Race hit main without potholing They were working under a different companys USA
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2023-03-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | EDGAR PALACIOS | LANCASTER | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Service line was hit while homeowner was digging a trench on the side of his house. Homeowner did call for USA but started to dig before the legal start date of that USA ticket. Service was marked correctly by flags within delineation. Homeowner failed to pothole and verify our gas line and in the process of digging his trench hit the service.
Southern California Gas Company | N | LOS ANGELES | LANCASTER | 2023-11-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CASEMON COMMUNICATIONS | FONTANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit service while excavating for utilities for fiber project.
Southern California Gas Company | N | LOS ANGELES | LAWNDALE | 2023-07-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 21 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | TRIANGLE ENTERPRISE | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was grading with a backhoe in order to install driveway apron when 1/2 inch ips plastic service was damaged. Contractor had valid USA and main marks were visible and marked correctly.
Southern California Gas Company | N | LOS ANGELES | LAWNDALE | 2023-12-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 30 | 21 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | PACIFIC BEAR CONSTRUCTION | SAN CLEMENTE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was hand excavating with a shovel to install electrical when they struck our 1 PE gas service. USA not valid.
Southern California Gas Company | N | LOS ANGELES | LAWNDALE | 2023-09-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 25 | 21 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MICHAEL PELLETIER | LONG BEACH | CA | N | Y | Yes | No | Yes | No | No | Yes | Yes | Contractor was trenching for electrical work and damaged the service while pot holing. Their USA was expired.
Southern California Gas Company | N | LOS ANGELES | LAWNDALE | 2023-05-16 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ADAME CONSTRUCTION | LAWNDALE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Workers cut into live gas service thinking it was abandoned.
Southern California Gas Company | N | LOS ANGELES | LAWNDALE | 2023-05-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MANNY''S ROOTER SERVICE | TORRANCE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Property was in an unsafe condition. It was boarded up but occupied with squatters. Locater was not able to access the property, but marked by measurements.
Southern California Gas Company | N | LOS ANGELES | LAWNDALE | 2023-01-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ULTRA CON | CORONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | Contractor was hand excavating with shovel to install footing when they struck our 1/2 PLA service. In process of demoing house to build garage where meter/service is located. USA ticket current. However, no abandonment order created and no meeting with SoCal Gas planner about re-route of service. Contractor aware they were at fault at knew they shouldn''t of dug prior to meeting with planner and having an abandonment order. Also was told by ETD to not dig, which states on notes of USA ticket.
Southern California Gas Company | N | LOS ANGELES | LOMITA | 2023-08-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 33 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | DANIEL NAVARRO | LOMITA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA . Customer was excavating to plant tree.
Southern California Gas Company | N | LOS ANGELES | LOMITA | 2023-05-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | PAUL SHEEN CORP | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was machine excavating with backhoe to install conduit for electrical when they struck our 1/2 PLA gas service. No USA, contractor at fault
Southern California Gas Company | N | LOS ANGELES | LOMITA | 2023-08-14 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 12 |  | HERMAN WEISSKER | LONG BEACH | CA | Y | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor doing work for SoCalGas hit our exposed service with a hand tool. Service was exposed and tool bounced off hard surface striking the 1/2 CTS pipe.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-11-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SANDRA BROADZINSKI | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The 1/2 CTS service was damaged with hand tool.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-08-22 | Third party excavation damage | Main | Material not known | Backhoe/Trackhoe | 0 | 30 | 18 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | GERONAMO CONCRETE | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging trench when they damaged plastic service. Contractor did not have a USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-11-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 59 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | LOS ANGELES STREET SERVICES | LOS ANGELES | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | 1 plastic service damaged by contractors using trencher while installing irrigation system.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-08-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DIAMOND LANDSCAPING | SYLMAR | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 2nd party contractor was digging trench for new gas service. Was hand digging could not find service. 1 plastic service was damaged.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-05-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 18 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HAFCO | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractors hit 1/2 svc while digging in private property to install drain. Crew responded and did immediate service alteration.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-02-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | DWP | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Water company was excavating when they struck mismarked service with backhoe. marks where off ETD scanned the area and was having a hard time getting a good signal. EE went off of measurements.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-05-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | LADWP | NORTHRIDGE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | LADWP was trenching to install new water main while trenching they hit a 1/2 CTS inserted in 3/4 STL cutback that wasn''t on our map. Crew went out and abandoned cutback at SMC.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-09-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | LADWP failed to expose gas service prior to trenching. Gas service was marked right on the marks.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ELECNOR BELCO GROUP | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit a 1/2 cts line while trenching. crew arrived on scene, controlled gas and altered service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-12-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | LANDSCAPE SUPPORT SERVICES | SHERMAN OAKS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit while excavating for conduit.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-04-06 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 6 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | SYGNOS INC | SAN MARCOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor had hole open installing new water main they were probing to see gas
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 59 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MNR CONSTRUCTION INC | LA VERNE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | Locator mismarked service and as a result, city of LA contractor damaged service in the process of excavating for the replacement of sewer line.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 1 |  | OSBIDA RODAS | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. 1 plastic service hit by shovel while digging to install new sewer.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | WILSHIRE CONSTRUCTION | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Company was doing landscape work and cut through a plastic service with a shovel. no USA was called in for the work.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | TOMER MALIKI | WINNETKA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged plastic service with shovel.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SUNSHINE CONSTRUCTION | VENICE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | SVC hit with shovel
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-07-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 37 | 13 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SCHLOMO | BUENA PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor while excavating damaged the 1/2 CTS plastic service with a pick axe.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 10 |  | QUAKER 5 | SANTA MONICA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was digging inside property while digging 3rd party contractor hit and knicked 3/4 steel service with electric jackhammer.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-01-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 45 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ALL ABOUT LANDSCAPE | NORTHRIDGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging on property to install irrigation line when they hit the gas service. Contractor did not have a valid USA. Company crew made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CONTRERAS TRUCKING | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas service and did not call for an Underground Service Alert (USA) ticket. The crew onsite informed the contractor to always call Underground Service Alert (USA) at 811 Dig alert before digging, even when in private property.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-09-19 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | HERITAGE DISPOSAL INC | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Developer/contractor was demolishing structure with excavator and struck our 3/4 inch steel service. There was no USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-11-09 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 5 |  | MR FLOW ROOTER & PLUMBING | VAN NUYS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged gas line with saw.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | A&S CONTRACTORS | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party excavating to install a new yard line. While excavating the 1 steel casing was cut and through the 1/2 plastic service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-05-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 18 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | LADWP | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor dug into 1/2 ips service with backhoe. Crew arrived and dug up service in parkway to squeeze and repair. They replaced 1'' of 1/2 ips.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | H2O PLUMBING | RESEDA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party struck gas service while installing sewer line with shovel No USA was call
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BRIAN LITTLE | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscaper was removing tree stump with an axe when they damaged the gas service. Landscaper did not have a valid USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-03-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | PLUMBING BROTHER AND ROOTER | NORTH HOLLYWOOD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas line with excavator while excavating for sewer lateral. contractor claimed marks were not visible but failed to call 811 for remarks.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-07-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 8 |  | CATALINA PACIFIC UTILITIES | LOS ANGELES | CA | N | Y | Yes | No | No | No | No | Yes | Yes | Contractor damaged service line that had not been marked. USA ticket was not valid yet. Struck service using backhoe in the process of trenching in public street to install electrical conduit.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-02-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 4 |  | GMC SANCHEZ PLUMBER | FONTANA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit out service line no usa crew altered svc
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-07-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 18 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | 316 ENGINEERING AND CONSTRUCTION | ROSEMEAD | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Third party contractor dug into 1 plastic line while excavating.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-08-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | JOSE VASQUEZ | TORRANCE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor didn''t call for a USA ticket and nicked gas service with shovel while digging to repair sewer line.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-04-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 4 |  | RAYMOND | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor didn''t call for a USA ticket and nicked gas service with shovel while digging to repair sewer line. Homeowner and contractor was advised by company crew to call Underground Service Alert at 811 whenever digging, even when in private property
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-03-07 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 0.75 | 60 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | SERVITEK ELECTRIC | WALNUT | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Servitek Electric damaged 3/4 steel service while boring in new conduits.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-05-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LADWP | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit line with backhoe. USA called, USA valid. Mark was off by 3 feet. Plastic service, no wire. Measurements off by 3 feet. Confirmed with damage prevention.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-02-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  |  | NA | DAVID ELLIOT | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor struck gas service with shovel while trying to make repair''s for a sewer line
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 38 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ELROD FENCE COMPANT | JURUPA VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Crew damaged 1 plastic service with auger at property line while digging holes for fencing. No USA called in.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-08-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CARE PLUMBING INC | GLENDALE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party plumber was digging to repair sewer for homeowner. Struck our 1/2 service with shovel. No valid USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-02-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | RAMONA INCORPORATED | BALDWIN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor digging and installing sewer hit service with exc/backhoe crew Altered gas service
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-10-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | JLG LANDSACPING | CANYON COUNTRY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Contractor damaged the plastic service while hand digging.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-11-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LESTO GROUP CONSTRUCTION | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party struck gas service with shovel while trenching for conduct. No USA ticket
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-05-09 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 150 | 150 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CMF HOME BUILDERS | BEVERLY HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | Yes | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was working on property while trenching for footing for fencing 3rd party contractor nicked 3/4 HP service crew went out and fixed the line. 3rd party contractor had no idea what USA was, had contractor stop the job and Damage prevention went out and explained to contractor what was needed for working around a HP Service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-07-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | MLJ BUILDERS | CANYON COUNTRY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavation damaged by backhoe No USA Grading for building foundation. Contractor hit 1/2 CTS service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-05-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 5 |  | MNR CONSTRUCTION INC | LA VERNE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged correctly marked gas facility while digging with a backhoe. Gas company crew on site informed contractor to expose all underground located gas pipelines by hand digging. On site crew also advised the contractor to use more caution while excavating around underground substructures, even if by hand.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-08-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | OCEAN DEVELOPMENT | HUNTINGTON BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas service and did not call for an USA ticket.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-02-10 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | PIONEER PAVING | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor hit plastic main with backhoe, Gas Main was Mark in Yellow paint company Fail to Pot hole
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-02-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | THE GREENLY LLC | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service that was marked properly.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-12-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MNR CONSTRUCTION INC | LA VERNE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Company fixing drain hit 1/2'''' service with backhoe.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-10-16 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CARNEY ENGINEERING CONSTRUCTION INC | TORRANCE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Mark was off. 3rd party contractor struck main with backhoe causing the damage
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-09-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 23 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 10 |  | LA HOUSING AUTHORITY | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Housing Authority crew working on water leak damaged 1 plastic service with a backhoe that dropped 8 units in complex. USA was called in, but service was not correctly located due to poor and false signal.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-02-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | FRANCISCO ROJAS | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party damage with sharp shooter, hand tool / shovel.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-04-07 | Third party excavation damage | Meter | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CRS PLUMBING | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA hit 1 plastic service. Crew responded controlled gas and made permanent repairs to service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-04-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | P B BROWN | PALM DESERT | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Second time contractor hit this service. 3rd party contractor hit unmarked gas service with hand tool. SCG Distribution responded, controlled gas, and made permanent repairs to service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-08-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GOLD METAL PLUMBING | GRANADA HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was digging in the property to install new drainage in the process of digging 3rd party contractor damaged 1/2 IPS service with an electric jackhammer. 3rd party contractor had no USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-08-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | GOLD METAL PLUMBING | GRANADA HILLS | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | 3rd party contractor hit plastic service
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-10-09 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | ARIZONA PIPELINE | LOS ANGELES | CA | Y | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | APC was potholing to locate service line to MSA and struck our 1/2 CTS with a shovel.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-04-12 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | LA CONCRETE AND FRAMING | NEWBURY PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Developer was excavating for irrigation and damaged a steel service. crew arrived dug out control holes and repaired the service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-06-25 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MAXAMILLION LUCERO | NORTH HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was digging up sewer main in the process of digging 3rd party contractor hit 1/2 IPS service with shovel.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-11-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SALAS EXCAVATING | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | In the process of grading 3rd party contractor hit and damaged 2-inch plastic service with excavator. 3rd party contractor had no USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-01-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | CHARLOTT CULINA | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor was digging a hole to install wires for homeowner when they struck plastic service line with shovel, crew showed up and stopped service and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-01-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit and pulled with backhoe/exc inserted service and bent back and used wire to keep it in place.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-06-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | JAMES SPENCER | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging for post damaged CTS plastic service. Contractor did not have a valid USA. Company crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-06-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | RC DRILLING | THOUSAND OAKS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor was drilling and struck 1 Inch gas service
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-01-24 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 38 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | LADWP while working on water main break pulled steel service before GAS CO could locate and mark delineated area. 3/4 service was pull hard enough in street to cause the riser to be snapped under the service valve. Crew pinched service and began replacement of service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-11-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | YAIR GOVHARI | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor working for homeowner hit 1/2 plastic service while digging with no USA ticket.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-10-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SERLING GARDEN NURSERY | MOORPARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party hit plastic service with shovel while trenching to install tress
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-03-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CARLOS SOTERO | DOWNEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Crew found that the contractor had left a 1/2 plastic service cut and folded back. No USA. The ETR had spoken to the owner and was told that the damage happened with a shovel while trenching.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-10-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | TELOS PROPERTIES | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party damage to plastic service while trenching.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-02-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | G CHANG | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1/2 CTS service with shovel by homeowner repairing sewer line. NO USA called in.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-02-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | METRO | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor struck 3 inch gas service with back-hoe and rip off punch tee failed to exposed gas service by hand
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-09-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CNM | SIMI VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was breaking concrete for new concrete and damaged inserted service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-05-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | VICKERS CONSTRUCTION MANAGEMENT | PASADENA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor struck gas service, EE mark gas service with Yellow paint contractor fail to pothole before digging
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-03-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 22 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | BIG BEN ENGINEERING | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor covered marks with mud and tried to claim that he didn''t see them.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-05-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SASA JUVIC ROLLA LLC | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1/2 CTS service with shovel while crew digging along foundation to install water proofing. NO USA called in for location
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-05-31 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SASA JOVIC | LOS ANGLES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit gas service with shovel while digging to install irrigation line
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-03-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | EMMANUEL | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1/2 PE service by homeowner digging to repair sewer line. NO USA called in for location.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-12-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Unmarked gas line hit with backhoe while trenching
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-04-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MORLEY BUILDERS INC | SANTA MONICA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged correctly marked gas facility while digging with a backhoe. Gas company crew on site informed contractor to expose all underground located gas pipelines by hand digging. On site crew also advised the contractor to use more caution while excavating around underground substructures, even if by hand.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 18 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor dug into 1/2 CTS line while trenching to install a fence.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-01-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | DEPARTMENT OF WATER AND POWER | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | DWP damaged 1/2 pla service with shovel while excavating crew Alter service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-11-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 26 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party damage excavating with no USA and damaged Gas Company facility.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-10-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | WILLIAM ROBLES | LYNWOOD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor struck gas service when clearing out bushes. No USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MR KAPLAN | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged plastic service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-05-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 18 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DOUBLE JAY PLUMBING | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Private contractor cut our gas line while digging to install a water line. Upon crew arrival, the service was found broken and blowing. Crew pinched the line to control the gas, then replaced the damaged section with new plastic.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-10-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | LEVEL UP CONCRETE | SUN VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Owner hired landscape company to knock down trees. Contractor did not notify dig alert. Landscaper damaged a 1/2 service that ran under the tree.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-04-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CAL FUTURE CONSTRUCTION INC | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was grading parking lot with a backhoe and struck our service line. No USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-12-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | PRIME BUILD | MANHATTAN |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While excavating without a valid USA ticket contractor struck 1 steel service on property
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-08-20 | Third party excavation damage | Miscellaneous/Other | Steel | Miscellaneous/Other | 0.75 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | ACR PROFESSIONAL PULMBER | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber cut through steel service under garage. Dug up control hole in street and pinched plastic svc. Under garage service becomes steel.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-09-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LANDMARK CONSTRUCTION | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas service and did not call for an Underground Service Alert (USA) ticket.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-11-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 59 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 7 |  | RESOURCE ENVIRONMENTAL INC | LONG BEACH | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 1 plastic service damaged by crew excavating. Service was not marked.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-07-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CARLOS DAVID PINEDA | NA |  | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was digging out trench on property to install water lines on property, when contractor was trenching hit and struck 1/2 IPS service with electric jackhammer, 3rd party contractor had no USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-10-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DCLA | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas service and did not call for a USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-05-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SEWER LINE SERVICES | GRANADA HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor damaged a 1/2 inch plastic service when excavating for a sewer repair. dig alert was not contacted prior to excavation.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-08-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DYSON ENG | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer was digging out a tree stump that happened to be directly over our 1/2 plastic gas service line. Customer failed to call for USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-03-27 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | TRICANA GROUP | TUSTIN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged correctly marked gas facility while digging with a backhoe. Gas company crew on site informed contractor to expose all underground located gas pipelines by hand digging. On site crew also advised the contractor to use more caution while excavating around underground substructures, even if by hand.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-08-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | JOE WEBER EQUIPMENT AND EXCAVATING INC | BURBANK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit 1 inch gas service with excavator. Contractor was digging with no USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-09-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | JOE WEBER EQUIPMENT AND EXCAVATING INC | BURBANK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged correctly marked gas facility while digging with a backhoe.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-03-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Directional Drilling | 0.75 | 60 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | SEDANO BUILDERS | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor using a core drill machine to install fencing post damaged a 3/4 steel service. NO USA WAS CALLED IN FOR LOCATION
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-02-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | OROKIN PEST CONTROL | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | while using hogger to drill holes to install pest control tablets they struck plastic line
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-07-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ALL SEASON ROOTER & PLUMBING | SAN FERNANDO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumbing contractor damaged service in the process of making plumbing repairs. According to plumber, the service was ripped while pulling roots by hand.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | FROGTOWN CONSTRUCTION | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. 3rd party contractor hit 1/2 plastic service with backhoe.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-12-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ALL TIME PLUMBING EC INC | VAN NUYS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1/2 plastic service while digging trench for drain. Plumber did not have a valid USA on file.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-02-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  | 2 |  | NONSTOP PLUMBING | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor when trenching to install sewer line when they hit the gas service No USA was call
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | QUEST CONTRACTOR | ORANGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 2 plastic service while grading in private property. No USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-10-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MAC INC | MISSION HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged gas service with shovel while trenching to install electrical conduit
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-04-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | The service was damaged and pulled with a backhoe. The 1/2 cts service is incased inside 1 steel pipe. The damaged section was removed along with the section of steel pipe. There was approximately 4'' of cts and two couplings used for repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-05-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | PROPERTY DUNE ROOTER | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer working on exposing sewer line for replacement, struck our service line with a shovel.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LC GENERAL CONSTRUCTION INC | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Contractor was working on sewer lateral and hit 1/2 CTS plastic service while hand trenching with shovel and pick.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-11-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ELIZABETH WARD | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Owner hired company to work on landscape. No USA wad called in & the company used a sawzall to cut through a 1 plastic service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-02-01 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ZAREH NARGHIZIAN | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA obtained. The home owner hired landscaping crew and during the process the service was damaged.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-09-28 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | HERMAN WEISSKER INC | LONG BEACH | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 2nd party struck gas service with sharp shooter
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | RED LILY PLUMBING | LOS ANGELES | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Plumbing company struck inserted 1/2 CTS service in the process of exposing sewer line needing repair.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-09-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NA | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas service and did not call for an Underground Service Alert (USA) ticket.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-12-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LADWP | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage to company property. No valid USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CANON EQUITY PARTNERS | BEVERLY HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party Contractor hit 1 plastic service with hand tools while digging for home remodel with no USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-04-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | SANDOVAL GENERAL CONSTRUCTION INC | LYNWOOD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavation damage done with hand shovel. Contactors working on drainage. No valid USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-11-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | GIRAFFE | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | In the process of digging to install cement molds, contractor damaged 1/2 PE service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-11-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | EMADRED | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The pipe was cut where the pipe exited the casing.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-06-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ANDRES PONCE | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging to plant trees damaged CTS service line. Company crew responded and made permanent repairs. No evacuations, fire department, police, or media on scene.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-10-12 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 20 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | WA RASIC CONSTRUCTION | LONG BEACH | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Third party contractor dug into 2 plastic main while open trenching with backhoe.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-05-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was demoing a building when a big piece of concrete fell and damaged the gas riser. no usa was present.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-12-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | RJC | SANTA MONICA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor struck plastic service with shovel while trenching for conduit. Digging with no USA ticket
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-05-09 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CHRIS OLSON | SUNLAND | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor struck gas service while grading to install for a dumpster for a demo project
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-10-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SKETCHLEY & MASON | LOS ANGELES | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The contractor had no USA ticket.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-11-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 1/2 plastic service was not marked.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-08-22 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 20 | 17 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ABRAHAM YERA | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 1 gas service while excavating. Crew arrived and abandoned at SMC.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-06-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NA | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor dug into cts line. Crew arrived on scene, performed pressure control and altered service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-02-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NICHOLAS TARDITTI | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was digging to find sewer line in the process of digging 3rd party contractor hit and damaged 1/2 plastic service. 3rd party contractor had no USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | JUAN RAMIREZ | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit gas service while digging trench for sewer. Contractor did not have a USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | TIP TOP DRAIN PROS | CANOGA PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor cut 3/4 steel gas service with sawzall while install a irrigation line
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-03-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 7 |  | RAMONA INC | ARCADIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor digging to install sewer hit Service line with sharpshooter while pot holing. Markes where right on the gas line
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-09-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ISIDRO DEMOLITION | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor is installing a new retainer wall and failed to call in for a USA. Contractor damaged a 1/2 plastic service with an excavator.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | BLU JAY PLUMBER & ROOTING | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working on drain for home damaged service with hand tools. Contractor did not have a valid USA. Company crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-07-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ORANTES CONTRUCTIOON | NORTH HOLLYWOOD | CA | N | Y | Yes | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor performing home improvement hit marked service with hand tools while digging on expired USA ticket. SCG responded, controlled gas, and made permanent repairs to service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-06-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA hit line by hand tools owner would not provide contact information
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-11-30 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 60 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MILLER | ORANGE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged correctly marked gas facility while digging with a backhoe.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-10-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | M PADILLO INC | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party was digging to find the sewer. In doing so, they struck the gas service. No USA was called
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-06-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | NA | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. 3rd Party Contractor was excavating to install a water line and struck our 1/2 service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-01-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ARELLANO AND SON CONSTRUCTION CORP | ARLETA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was trenching in yard to install new drainpipe while trenching contractor hit 1/2 service with shovel. 3rd party contractor did not have a USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-04-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 21 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 4 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Upon arrival 1/2 IPS service was damaged by third party. There was a current USA. The foreman informed me that the ETD let him know that he did not have a good signal while locating and to pothole before digging. There was a service marked in front of each service. Two pipes where found at or near the markings. Upon excavating the service (standard and branch) was found in front of the driveway. GIS did not show proper location of service. In Service History it showed all four service to be branched but in the notes it mentioned what address feeds the other three services.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-01-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | WEST COAST BACK HOE | LODI | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged service that was incorrectly marked. After an investigation of returning to the location with the employee, reviewing GIS it was found that the 810 locator was picking up power/electric in the same property. There was a previous mark and his read were high over that mark which was directly in-line with the MSA. Service had an offset of 35'' in private property. ETD was coached and informed to use all resources if he had a doubt on any service locate.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-01-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MARTIN CO | BAKERSFIELD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | contractor hit 1/2 plastic gas service while trenching to install conduit
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-10-05 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 18 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ALAMEDA CONSTRUCTION INC | COMPTON | CA | Y | Y | Yes | Yes | Yes | Yes | No | No | No | Contractor damaged 1/2 plastic line with shovel. Crew arrived on scene, performed pressure control and altered service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-12-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MID & TAKTA CONCRETE | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While trenching to install a new copper water line from the water meter in the public parkway, the gas service was damaged on private property.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-05-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | GENERAL PLUMBING | BEVERLY HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | plumbing company was running new water line for homeowner and damaged the gas service with a shovel. no usa was called in.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-09-13 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 1 |  | SOCAL BUILDERS AND DESIGN INC | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hit with in delineation, marked correctly. Contractor grading property did not expose 1 gas service properly. The contractor was using an excavator and struck the gas service causing damage.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-06-15 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 55 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | SE PIPELINE | SANTA FE SPRINGS | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor does own locating
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-02-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | CITY LIGHT AND POWER | LONG BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit line, no USA. 3rd party contractor hit service while installing power pole ground rod. SCG responded, controlled gas, and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-06-23 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 25 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  |  | NA | FOOS EXCAVATING | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was grading hillside with excavator and struck our 2 inch steel main. Working for owner. No USA. Also, entered damaging party info from paper CPDR.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 19 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CCS CONSTRUCTION | MARINA DEL REY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-09-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | J&S CONSTRUCTION | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage to company property. No valid USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-12-23 | Third party excavation damage | A service line with an excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | CHRIS GRANDIDGE | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was working on the property. While in the process of trenching to install new sewer line 3rd party contractor hit and damaged 1 inch plastic line with excavator. 3rd party contractor had no USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-12-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 17 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ENRIQUE RAMIREZ | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor digging footing for brick wall with no USA ticket hit 1/2 plastic service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-07-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 25 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | UNLICENSED DAY LABORERS | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | OHS crew arrived to find damaged svc due to grading being done by 3rd party contractor.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 23 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | DWP used a backhoe to excavate within 24 of valid USA markings. Backhoe hit our service and severed the 1/2 service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-06-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LAUSD | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | changes made to type and subtype.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-04-27 | Operator excavation damage | Main | Steel | Miscellaneous/Other | 1.25 | 43 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | HERMAN WEISKER INC | JURUPA VALLEY | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 2nd party contractor cut into 1 1/4 main while cutting 2 casing. Company crew dugg control hole and repaired with weld.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-07-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | GARAGE DOORS FOR LESS | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit plastic service when trenching.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-05-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | GONZALEZ REMOVAL | C |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor Hit gas service with backhoe
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-11-27 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | SHMUEL RAIGORODSKY | LOS ANGELES | CA | N | Y | Yes | Excavation occurred on private property by a non-contractor. | Yes | Yes | No | Yes | Yes | The third party company damaged the service with a backhoe while trenching for sewer.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-08-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 22 | 19 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | SILVER STAR PLUMBING | REDONDO BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor dug into 1 plastic line while digging for irrigation line. Crew responded on scene and altered 1 plastic service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-10-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ELIAS HOLGUIN | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor hit accurately marked 1/2 plastic service with hand tools while exposing it.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-10-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | HOLGUIN CONCRETE | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer cut service near riser. No USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-11-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 22 | 19 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | LADWP | SAN PEDRO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Working on water services when they hit gas service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-06-21 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 4 |  | MATTHEW AND STEWART CO | SIGNAL HILL | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Third party contractor for LADWP struck our service. Third party contractor was excavating with back hoe to access sewer pipes in public street. Valid USA. Company employee marked delineation with No SCG and failed to use all Company resources.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 30 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 12 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | LADWP damaged plastic service while probing for water leak. LADWP did have an emergency USA and was marked out except for 1 service that did not show on GIS.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-07-20 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10001 |  | 21 |  | BYU WA RASIC | LONG BEACH | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged a 2? plastic main that was incorrectly marked.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-01-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DIEGO CHAVEZ | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was excavating and damaged the PLA service in the process.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 23 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | FELIX KAWAMURA | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner digging area around cleanout with hand tools and struck our service. No USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-01-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | ROCIO CORTEZ | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | customer was hand digging for irrigation line and struck the gas line, crew pinch gas service and made repairs
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Directional Drilling | 0.75 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | LA STREET LIGHTING | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | NA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | DWP was doing a leak investigation on water leak, crew hit our gas service DWP was digging ahead scheduled with no valid USA. Gas service was not marked due to DWP digging ahead of scheduled.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-10-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | WILLIAM GRIFFEN | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor installing fence pole damaged service line.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-10-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Distribution investigated and pot holed and found the 1 Plastic Service severed. How damaged occurred or when it occurred is unknown.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-11-17 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 0.75 | 22 | 19 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  | 1 |  | CITY OF LOS ANGELES BUREAU OF STREET LIGHTING | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | They were boring and hit our line
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-02-28 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 55 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DSRM COMMUNICATIONS | POMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Subcontractor conducting excavation with boring equipment struck 2 plastic main. Struck in delineated area. Contractor was boring for cable utility. Andrew Rodriguez from damage prevention onsite. Photos taken. Police and fire both were on scene. street closures in both directions due to the severity of leakage. Permanent repairs were made.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NATURE SCAPE LANDSCAPE | CALABASAS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damage to company property. No USA was called in.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-05-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 18 | 16 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  | 1 |  | WESTERN SUPREME ROOTER INC | ARCADIA | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | No USA plumber damaged .50
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 18 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | GEORDE DELUNA | CULVER CITY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavation damage No USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-05-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ARMAND ASG | SAN DIMAS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damage of 1/2 PLA service with shovel while doing landscape work. NO USA for location.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-10-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ALEX EMERSON | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Property owner had workers removing old fencing when they struck the 1/2 CTS pipe during excavating for post removal.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-06-28 | Operator excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ALAMEDA CONSTRUCTION SERVICES | COMPTON | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged 1/2? PLA service that was incorrectly marked. After an investigation with Gas Company Locator, reviewing GIS, Service History, and measurements it was found that the damaged service could not be located by means of direct hook up due to no locate wire. Employee used measurements to locate. Service was mismarked by approximately 4?.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-06-21 | Third party excavation damage | Miscellaneous/Other | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | looks like 3rd party contractor did not want to wait for the abandonment order of svc for next day so they just cut the svc and tied it back and continued their work. OHS Crew arrived and made repairs by pinching and fusing on a cap. abandonment was done next day by district.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-04-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 59 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | BRYAN POTKIN | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor damaged service line with shovel in the process of trenching to install new sewer lines.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-03-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | EVE HYMAN | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | On Sunday 3/26/23, Mid City LA on call Distribution was notified of a hit 1/2in plastic service at 5140 Raleigh St Los Angeles California 90004. (Hollywood District) Plumber hit the service while digging for sewer repair without a USA. Homeowner has accepted all responsibility for damage. SCG crew responded, controlled gas, and made permanent repairs to pipeline.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-11-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MARK COMPANY | ORANGE | CA | N | Y | Yes | Yes | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor installing electrical box damaged 1 plastic service with excavator. Contractor failed to delineate work area, and no markings were provided as a result.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | J AVILES | NA |  | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plastic service damaged by contractor while digging for drain repair. Contractor did not have a valid USA on file.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-09-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | DWP struck 1/2 plastic service with backhoe while installing water main, gas service was mark with yellow paint
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | BRIGHTVIEW LANDSCAPING | SAN FERNANDO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor installing irrigation lines was excavating with excavator and damaged a 1 PE service. Due to big dirt lot no marks were present near damaged site but were present 40'' away. contractor failed to call in for remarks. Service was marked on street and flags were present 40'' away.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-01-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | WA RASIC | LONG BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator failed to expose two feet by hand on either side of the markings. Excavator found a pipeline believed to be the service and dug with backhoe 1 foot away hitting actual service line. Crew arrived, controlled gas, and made permanent repairs to pipeline.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-02-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | SILVINO PARKER | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was digging trench for new sewer line while trenching 3rd party contractor hit and damaged 1/2 plastic service. 3rd party contractor did not call in USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-08-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 23 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | RCR CONSTRUCTION | JURUPA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was using a motorized auger within 24 of marked delineation. Struck 1/2 service while installing fence posts. USA was valid.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-11-17 | Third party excavation damage | Riser | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | THE DEMOLITION TWIN | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While grading lot contractor hit AL riser causing it to leak.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-04-13 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | EDWARDS BUILDERS | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was excavating to pour concrete for foundation and in the process struck our steel service with an excavator.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-11-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | SUNSHINE FOUNDATION REPAIRS | NORTHRIDGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Hit line. Damaged by hand tools
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | ALEJANDRO MENDEZ | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage to company property. No USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-02-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DIAZ PLUMBING | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber was digging with a hand shovel to excavate and repair sewer line. Struck and damaged 1/2 inch Adyl-A. There was no USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-02-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 20001 |  | 1 |  | HOLLENBECK PALM | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hollenbeck Palms Maintenance was repairing a water leak and hit our 1? gas service. SCG responded, controlled gas, and made permanent repairs to service. USA ticket was called in after damaging service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-08-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 22 | 19 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | COMFORT MASTERS | SIGNAL HILL | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor dug into 1/2 CTS service while trenching to replace sewer lateral.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-09-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | GRACE LIANG | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While contractors were framing to pour cement for a driveway, they stuck the gas service with a metal stake hitting our gas service
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-08-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 4 |  | WA RASIC | BELL GARDENS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | SCG received notification from WA Rasic regarding a hit ï¿½? IPS Plastic service line. The contractor was excavating under a valid USA ticket and, while attempting to hand expose our service line, struck it with a sharpshooter shovel.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-11-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NA | THOUSAND OAKS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party struck 1/2 plastic gas service while trenching to move the house line for the pool
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-12-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | FLORES CONSTRUCTION | DOWNEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damage plastic service with shovel while trenching to install railroads ties for a support wall
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-02-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  |  | NA | G DOMINGUEZ | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was excavating to install a retaining wall when they struck the existing plastic gas service with No dig alert
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-03-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ANDREWS BROTHERS CONCRETE INC | AGOURA HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging and struck service within 24 inches of delineation. Valid USA; flags were used to mark service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-04-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ANDREWS BROTHERS CONCRETE INC | AGOURA HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | while trenching for remodel contractor struck plastic line
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | FRONEN CONSTRUCTION | STUDIO CITY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | EE locate service, interference with tracer wire issues
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor performing trench excavation in the garage and into the public sidewalk area without proper USA ticket damaged 1/2 PE gas service with handtools.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-06-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ROBBYS ROOTER INC | PALMDALE | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor damaged 1/2 cts service while excavating with a backhoe.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | OGANES | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hit unmarked 1/2 plastic service with hand tools while digging for home renovation with no USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-02-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | DELFINO ROSALES | LOS ANGELES | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Customer damaged a 1/2? service when digging fence post holes. The customer had a valid USA. SoCalGas crew responded and controlled the release of gas by pinching the service. They then made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-09-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CONTRACTOR JORGE PEREZ | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | District was notified of a damaged ï¿½? Plastic Service. 3rd Party contractor excavating for sewer repair with No USA hit service with hand tools.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-11-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | VCI CONSTRUCTION | UPLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor was using an excavator to remove a rock. Did not maintain space and used excavator within 24 inches of delineation. Struck our 1/2 inch plastic service. USA valid, marks accurate.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-10-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | LADWP | NORTH HOLLYWOOD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Damage was caused by a backhoe
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 18 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 0 |  | MR HARPER | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Upon arrival, 3/4 STL service was broken and blowing. Riser was ripped from service by uniloader
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-11-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CITY OF LOS ANGELES BUREAU OF STREET LIGHTING | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party struck plastic service with clay spade while trenching for street light
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-11-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CITY OF LOS ANGELES | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was trenching to install a brick wall in doing so they struck our gas service
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-05-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DEMETRIO PLAZA | AGOURA HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The third party contractor was using power tool to cut drain and damaged service line.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-05-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DEMETRIO PLAZA | AGOURA HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The third party contractor was using power tool and caused to cut into the gas pipe.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-01-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GOOD PANDA LANDSCAPE AND DESIGN INC | BEVERLY HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was digging to install new trees for homeowner while digging holes 3rd party contractor hit and damaged 1 Plastic service. 3rd party contractor did not have a USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-12-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 7 |  | G&A UNDERGROUND UTILITIES | VAN NUYS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor digging trench to install electrical conduits for DWP damaged a 1 unmarked plastic service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-07-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | LADWP digging on expired USA ticket hit unmarked 1 plastic service line.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-09-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | HOME MADE BUILDERS | ENCINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Crew found leaking 3/4 steel service, the service was damaged with a backhoe.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | BUILDING BLOCKS CONSTRUCTION | MONTEBELLO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | OHS crew arrived to find broken and blowing due to 3rd party contractor hitting our svc with backhoe while doing new construction work.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-08-17 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ALPHA STRUCTURAL | SUNLAND | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was drilling in the ground with a jackhammer to install posts for a retaining wall. While in the process, the contractor struck a 3/4 steel service. The contractor did not have a valid USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 38 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | AVELINO PLANCARTE | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner caused damage to gas service when digging out for new post in private property. No USA was present at the time of the damage.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 18 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | WEINSTOCK CONSTRUCTION | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 1/2 Insert by drilling a pin hole through casing.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-02-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MAYRA LUGO | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged own gas service while digging to install a block wall. Since the homeowner was completely unaware of 811; Underground Service Alert, Gas company crew on site informed the homeowner to call Underground Service Alert (USA) at 811 anytime when planning to dig so the utilities can be located, even in private property.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-10-26 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | DWP | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party struck 2 inch gas main with backhoe. Failed to pothole before digging.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-01-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  |  | NA | JASON LUY | WEST HOLLYWOOD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor employee was hand trenching to install fire sprinkler line and struck the gas line
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-09-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 43 |  | OL DEVELOPMENT | SUN VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged service that was incorrectly marked.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-03-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  |  | NA | ZAMORA PLUMBING INC | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit line no USA. SCG responded and made permanent repairs to 1/2 plastic service. House was evacuated for safety, evacuations lifted after gas was under control.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-11-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 27 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HEFLIN & SON | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor repairing homeowner''s sewer damaged service. No USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-04-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NAIM CONSTRUCTION | WOODLAND HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3 party damaged 1/2CTSplastic service ripped with backhoe
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-11-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DRAIN AID | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit and damaged 1/2 CTS service with shovel. 3rd party contractor had no USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-11-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | RUSS FRID | NA |  | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged own gas service while digging to repair own sewer line.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-02-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | PAVERS | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA obtained. Third party damaged 1/2 CTS service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-02-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | THE DRAIN CO. | PANORAMA CITY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA, 3rd party damage, contractor performing sewer work for homeowner. Damaged 1/2 CTS Service with shovel during excavation. Company crew made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-11-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DG LANDWORKS | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor struck 1/2 plastic service with shovel while demoing for driveway. USA ticket not vaild
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-07-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | FRANCISCO ROJAS | INGLEWOOD | CA | N | Y | Yes | No | No | No | No | Yes | Yes | Contractor was doing landscape work when they damaged gas service with excavator. No legal USA ticket was present due to digging after ticket expired.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-08-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | SILVINO JUAREZ | SAN DIEGO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service line in the process of looking for sewer line without having called USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-06-14 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | DWP | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor pulled on 3/4 steel pipe with excavator. Crew reported to scene and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-11-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NIKOLAS AROVEUNIAN | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged gas service. No USA ticket.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-10-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | LEIGH CONSTRUCTION | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was trenching to install new sewer when they damaged a plastic service that branched off the standard service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-05-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NEC GROUP | COMMERCE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Valid USA, service was marked accurately. 3rd party contractor hit 1/2 inch Plastic service with hand tool while exposing it. SCG Distribution responded controlled gas and made permanent repairs to service.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-06-30 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | A pole was being installed. The third party contractor dug a hole next to the gas main before introducing the auger. The auger is what damaged the 2 PLA main. The contractor did see the marks prior to the excavation.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | GRBCON INC | BALDWIN PARK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | GRBCON has a USA B231000427 and the crew was working when they pulled and broke mismarked 1/2 CTS PLA service. While the crew was installing sewer.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-05-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | JILK HEAVY CONSTRUCTION | BREA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor struck gas service with backhoe
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-09-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | FERNANDO MASIAS | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner was digging trench to have new gas line installed when service was hit.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-02-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ENZO CARSERTA LANDSCAPING | NORTHRIDGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit gas service with shovel while installing Irrigation line
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CASERTA ENZO LANDSCAPING INC | NORTHRIDGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1 PLA service damaged by landscaping contractor installing irrigation lines & electrical lighting. No USA
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-08-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 11 | 11 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | PVI RENOVATIONS | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party company was trenching
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-07-12 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 18 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Upon crew arrival, 3/4 STL riser was broken and blowing.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-04-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  | 1 |  | CITY OF LOS ANGELES | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | City of Los Angles was Grading to repair the streets when that struck a Shallow Gas service that was 6 inches deep right below the curb and gutter
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | CITY OF LA PUBLIC WORKS | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The damage was outside the delineated area.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-01-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | TIGRAM HOVSEPYAN | GLENDALE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA damaged by hand tools.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-03-02 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  |  | NA | STEEL IMPRESSION | SYLMAR | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hit 1 inch plastic gas service while excavating to install for a post, so that they can put up a fence
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SPIFFY CONSTRUCTION | ALTADENA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging for sewer installation when they damaged plastic gas service. Contractor did not have a valid USA.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 35 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hand exposed an abandon steel gas service then continued to excavate and hit a 1/2? Plastic service with a backhoe. 1/2? Plastic service was correctly marked.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-04-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | KREATIVE CONSTRUCTION | WINNETKA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA, 3rd party contractor cut into unmarked 1/2 plastic gas service with saw while trenching. SCG Distribution responded controlled gas and made permanent repairs to service line.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-07-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | LOPEZ ELECTRIC | BURBANK | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Contractor hit 2 service. Contractor turned off curb valve in sidewalk.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 23 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NA | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plastic service damaged by 3rd party contractor installing water service for homeowner, crew left scene before company personnel arrived. No emergency crews on site, no injuries or death to report. Service was altered to complete permanent repairs.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-04-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 23 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | EBENEZER CONSTRUCTION | DOWNEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service while trying to expose line because they smelled gas.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-08-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 6 |  | EM CONTRACTORS | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged correctly marked gas facility while attempting to hand expose.
Southern California Gas Company | N | LOS ANGELES | LOS ANGELES | 2023-09-27 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Augur | 0.75 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CITY OF LOS ANGELES | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | City of LA public works hit miss marked 3/4 STL service with auger. Service was damaged 3'' of marks.
Southern California Gas Company | N | LOS ANGELES | LYNWOOD | 2023-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 39 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | INDY''S DEMOLITION | HUNTINGTON PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor caused damage to gas service while digging for new sewer line. No usa was present or visible.
Southern California Gas Company | N | LOS ANGELES | MALIBU | 2023-01-18 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 20 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GARNERO INC | MALIBU | CA | Y | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor stated he hit service line1/2 plastic line was damaged by hand shovel and was sheared through. Home is vacant and under construction No usa number given, contractor stated he was unsure of what that was.
Southern California Gas Company | N | LOS ANGELES | MALIBU | 2023-11-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | SOCAL EDISON | THOUSAND OAKS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1/2 plastic service with shovel.
Southern California Gas Company | N | LOS ANGELES | MALIBU | 2023-12-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HOTLINE CONSTRUCTION | SANTA PAULA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor was working and digging with backhoe. While in the process of digging 3rd party contractor hit and damaged 1/2 service contractor had a valid USA and marks were visible.
Southern California Gas Company | N | LOS ANGELES | MALIBU | 2023-12-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 18 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MIKE FAVIO | MALIBU | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Homeowner was digging to install irrigation when service was hit with hand tool at the front left side of yard.
Southern California Gas Company | N | LOS ANGELES | MALIBU | 2023-10-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CEDRO CONSTRUCTION | SANTA PAULA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor was digging to work on the water line. In the process of potholing gas service 3rd party contractor hit and damaged 1/2 IPS service with shovel. 3rd party contractor had a USA and marks were accurate.
Southern California Gas Company | N | LOS ANGELES | MALIBU | 2023-06-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | PEERLESS LANDSCAPE | MALIBU | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 1 PE service when grading to install a tree. contractor did not have a valid USA ticket. crew pinched and repaired service.
Southern California Gas Company | N | LOS ANGELES | MALIBU | 2023-10-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ABEL CORONA | RESEDA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor struck plastic service with a stake.
Southern California Gas Company | N | LOS ANGELES | MALIBU | 2023-12-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 48 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | PASTER CONSTRUCTION | BEVERLY HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plastic service damaged buy shovel while installing water. No USA
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2023-03-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ISRAEL IRON WORK | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was working while live gas was on the property. Should have worked with FPA prior to starting work.
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2023-01-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CARLSON AND SON INC | MANHATTAN BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was hand excavating pipe when pipe was damaged. Pipe was hit due to tree roots in the same excavation, that looked similar to gas pipes.
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2023-02-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | BEAREE CONSTRUCTION | TORRANCE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While hand excavating to expose the gas line, contractor accidently hit the pipe causing it to leak. Contractor was NOT able to avoid hitting the pipe, due to the hard soil and the pipe and roots looked identical.
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2023-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | COURSELLE PLUMBING | GARDENA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging trying to locate the sewer when he accidently damaged the 1/2'''' CTS plastic pipe. USA was not called.
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2023-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | UNLIMITED COMMINICATIONS | BUENA PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Communications company damage P.E. service pulling in PVC conduit.
Southern California Gas Company | N | LOS ANGELES | MANHATTAN BEACH | 2023-11-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | PEARCE CONSTRUCTION | TORRANCE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was installing wooden stakes for the framing of a concrete wall when a stake came in contact with the plastic service. USA was not called.
Southern California Gas Company | N | LOS ANGELES | MARINA DEL REY | 2023-10-18 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Augur | 0.75 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | STRONG TIES CONSTRUCTION | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor was working in back of property to install some poles. While in the process of augering the property 3rd party contractor hit and damaged 3/4 steel service line. 3rd party contractor did have a valid USA.
Southern California Gas Company | N | LOS ANGELES | MAYWOOD | 2023-06-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 33 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | WILLBERTO CABALLERO | MAYWOOD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Homeowner cut into service in casing with a Sawzall thinking it was an old corroded pipe. Homeowner did have a valid USA and marks were off by 2 feet. District supervisors were notified of mismark. Company crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | MAYWOOD | 2023-01-26 | Third party excavation damage | Riser | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 23 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  |  | NA | TRANSTECH/TORO ENTERPRISES | CHINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged by contractor. While clearing debris with back hoe, contractor pulled riser and snapped service line. Riser was on fence line in a baseball field. No USA was called due to no excavation. Service repaired as a cutback.
Southern California Gas Company | N | LOS ANGELES | MISSION HILLS | 2023-02-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 34 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | DC DRILLING INC | JURUPA VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Crew damaged the service while installing cable with a drill rig
Southern California Gas Company | N | LOS ANGELES | MISSION HILLS | 2023-03-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | JOSE A VALENCIA | MISSION HILLS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Code 1, gas at foundation.
Southern California Gas Company | N | LOS ANGELES | MONROVIA | 2023-07-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | JT SITE SERVICES INC | LA VERNE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to pothole prior to using trencher. Gas main and gas services were properly located and marked.
Southern California Gas Company | N | LOS ANGELES | MONROVIA | 2023-01-17 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  |  | NA | PACIFIC UTILITIES INC | CARLSBAD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was digging with mini excavator over marked gas line.
Southern California Gas Company | N | LOS ANGELES | MONROVIA | 2023-05-17 | Third party excavation damage | Main | Steel | Boring Equipment | 2 | 34 | 27 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | DOMINGUEZ GENERAL ENGINEERING | POMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged a steel gas main with an accu bore while installing water services, Contractor did not pot hole the utilities for verification of location and depth
Southern California Gas Company | N | LOS ANGELES | MONROVIA | 2023-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | DAMARY MONTANEZ | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party damage, contractor damaged 3/4 steel service with backhoe. Failed to pothole marked line on valid ticket. Replaced service to make permanent repairs.
Southern California Gas Company | N | LOS ANGELES | MONROVIA | 2023-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 28 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | V I P GLOBAL INVESTMENT | ARCADIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | third party contractor damaged gas service while installing sewer line. No USA was called in
Southern California Gas Company | N | LOS ANGELES | MONTEBELLO | 2023-08-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SAN GABRIEL VALLEY WATER CO | EL MONTE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Damage to a 1/2 plastic service line. Valid USA ticket. Excavating within their delineation using a backhoe. Regrettably, our service line had been inaccurately marked by 5 feet, which resulted in the contractor unintentionally damaging it.
Southern California Gas Company | N | LOS ANGELES | MONTEBELLO | 2023-05-18 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RIVER GATE TOWNHOMES | MONTEBELLO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 2 plastic main while installing underground electrical. Crew arrived and dug control hole to squeeze main and make permanent repairs.
Southern California Gas Company | N | LOS ANGELES | MONTEBELLO | 2023-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ROBERT BRKICH CONSTRUCTION | MONROVIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor hit 1/2'''' plastic service in steel casing with backhoe while digging for new sewer.
Southern California Gas Company | N | LOS ANGELES | MONTEBELLO | 2023-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DOTY BROS | NORWALK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor hit accurately marked 3/4 steel service with backhoe while installing water main.
Southern California Gas Company | N | LOS ANGELES | MONTEBELLO | 2023-07-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | E&E IRON WORKS | LA PUENTE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor installing fence hit 1 plastic service with hand tools while digging with no USA. SCG Responded, controlled gas, and made permanent repairs to service.
Southern California Gas Company | N | LOS ANGELES | MONTEBELLO | 2023-10-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | PONDEROSA PINES | DOWNEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor struck 1/2 plastic service with shovel while trenching for irrigation line. No USA
Southern California Gas Company | N | LOS ANGELES | MONTEBELLO | 2023-06-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GC QUALITY SERVICES | MONTEBELLO | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor didn''t call for a USA ticket and nicked gas service with shovel while digging to repair sewer line. Homeowner and contractor were advised by company crew to call Underground Service Alert (USA) at 811 whenever digging, even when in private property.
Southern California Gas Company | N | LOS ANGELES | MONTEREY PARK | 2023-06-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | FERREIRA CONSTRUCTION | RANCHO CUCAMONGA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While excavating to install a new water line for the city of MPK, Contractor struck service. This was the 4th damage for this contractor on the same street.
Southern California Gas Company | N | LOS ANGELES | MONTEREY PARK | 2023-05-08 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 6 |  | CITY OF MONTERAY PARK | MONTEREY PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged 2-inch plastic main by city of Monterey Park water department. Main struck within the delineation. Fire department departed prior to the arrival of the company crew.
Southern California Gas Company | N | LOS ANGELES | MONTEREY PARK | 2023-05-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 23 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | FERREIRA CONSTRUCTION | RANCHO CUCAMONGA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavation Damage to 1/2-inch CTS service. Damaged with backhoe by 3rd party. Only 1 outage. Crew conducted permanent repairs. No fire department, no police and no evacuations. Claims notified.
Southern California Gas Company | N | LOS ANGELES | MONTEREY PARK | 2023-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 5 |  | BIG BEN ENGINEERING | IRVINE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor hit service with backhoe while digging.
Southern California Gas Company | N | LOS ANGELES | MONTEREY PARK | 2023-07-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | BIG BEN ENGINEERING | IRVINE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | Backhoe operator for Big Ben damaged 1/2 IPS service while trenching for new water main for the City of Monterey Park
Southern California Gas Company | N | LOS ANGELES | MONTEREY PARK | 2023-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor struck steel service.
Southern California Gas Company | N | LOS ANGELES | MONTEREY PARK | 2023-07-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 8 |  | MJ PIPELINE | JURUPA VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor struck 2 plastic service with backhoe while digging trench.
Southern California Gas Company | N | LOS ANGELES | MONTEREY PARK | 2023-06-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ENRIQUE VAZQUEZ | SAN FERNANDO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor struck service with backhoe while digging.
Southern California Gas Company | N | LOS ANGELES | MONTEREY PARK | 2023-09-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 21 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 16 |  | ROCHA LANDSCAPING | NORTH HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit service with trencher.
Southern California Gas Company | N | LOS ANGELES | MONTEREY PARK | 2023-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | FERREIRA CONSTRUCTION | RANCHO CUCAMONGA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service with backhoe
Southern California Gas Company | N | LOS ANGELES | MONTEREY PARK | 2023-06-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | FERREIRA CONSTRUCTION | RANCHO CUCAMONGA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor for the city installing new water main struck 3/4 service. Damage was within delineations. Photos taken.
Southern California Gas Company | N | LOS ANGELES | MONTEREY PARK | 2023-10-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ED CHAN | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging a trench for new sewer and hit our 2 service with backhoe. Properly marked by SCG.
Southern California Gas Company | N | LOS ANGELES | MONTROSE | 2023-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | LUIS RICARDO ANDRADE FLORES | CASTAIC | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage to company property, 3rd party.
Southern California Gas Company | N | LOS ANGELES | MONTROSE | 2023-08-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | TOTAL SERVICE PLUMBING | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | OHS crew arrived to find broken and blowing due to 3rd party contractor hitting our service while digging with a shovel to make plumbing repairs.
Southern California Gas Company | N | LOS ANGELES | NEWHALL | 2023-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | KEANE CONSTRUCTION INC | VALENCIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | hit 3/4 service steel with backhoe no USA
Southern California Gas Company | N | LOS ANGELES | NEWHALL | 2023-01-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | PAULUS ENGINEERING INC | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Digging to install a new water main
Southern California Gas Company | N | LOS ANGELES | NEWHALL | 2023-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | WHITEHOUSE CONSTRUCTION | VALENCIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 plastic service damaged by contractor while digging trench for drain. Contractor did not have a valid USA on file. Company crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | NORTH HILLS | 2023-11-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | DWP | NORTH HOLLYWOOD | CA | N | Y | Yes | Yes | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Invalid USA. Hit the 1/2 plastic service with a backhoe
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2023-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NA | ALTADENA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | upon crews arrival 3rd party contractor had departed ... checked usa tickets for a active ticket or completed no usa called in . no information on contractor
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2023-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | VAGRAM GALSTOUSEIAN | NORTH HOLLYWOOD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damage was found by locator who showed up to locate the gas facilities.
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2023-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SARJIS NERSESYAN | NORTH HOLLYWOOD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hired unlicensed contractor to dig a trench on the side of the residence. Contractor failed to call in USA ticket. While digging the contractor damaged our 1/2 CTS PLA service line. Contractor then proceeded to backfill the area of the trench where the damage occurred leading to gas migrating to the residence next door causing evacuations.
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2023-09-14 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 60 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 25 |  | JR FILANC | ESCONDIDO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor damaged a 3 inch steel main. Employee failed to locate and mark 1 inch stub that resulted on the damaged.
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2023-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ANDRE HACOBIAN | LA CANADA FLINTRIDGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party trenching without USA, damaged 1/2 PE service with backhoe.
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2023-08-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | BRIGHT-SIDE PLUMBING | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service damaged by contractor while excavating for sewer with hand tools. Crew arrived and made permanent repairs. Contractor did not have a valid USA.
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2023-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | VINCENT MATAVOSSIAN | NORTH HOLLYWOOD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Business owner was installing new drainage system, owner did not contact USA, in process of excavation business owner damaged PLA service line.
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2023-08-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 25 |  | VCI CONSTRUCTION | UPLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Third party contractor was doing construction work when service was cut with saw.
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2023-10-03 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 2 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  | 15 |  | JR FILANC CONSTRUCTION COMPANY INC | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Service history showed service was abandoned at SMC. Unknown copper stub was damaged while contractor was excavating.
Southern California Gas Company | N | LOS ANGELES | NORTH HOLLYWOOD | 2023-07-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | MNR CONSTRUCTION INC | LA VERNE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Third party contractor damaged a stub that was miss marked because facility records were wrong.
Southern California Gas Company | N | LOS ANGELES | NORTHRIDGE | 2023-01-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | NORTHRIDGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA hit line by 3rd party contractor.
Southern California Gas Company | N | LOS ANGELES | NORTHRIDGE | 2023-06-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 2 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 21 |  | PG SHORING & DRILLING | SAN FERNANDO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | while hogging to install metal beams for building, contractor struck 2 plastic service. crew showed up and shut off poly valve and made permanent repairs
Southern California Gas Company | N | LOS ANGELES | NORTHRIDGE | 2023-04-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MARTIN SADAFI | NORTHRIDGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd. party contractor hit our service line with shovel while digging for footing. No USA
Southern California Gas Company | N | LOS ANGELES | NORTHRIDGE | 2023-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | MONTANO BUILDERS | NORTHRIDGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 inch service damaged by 3rd party contractor while they were hand digging with shovel to install sewer line. No USA called.
Southern California Gas Company | N | LOS ANGELES | NORTHRIDGE | 2023-02-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | GARCIA AND SONS PLUMBING | SUN VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor hire by homeowner was digging holes to install new sewer line when they struck plastic line with shovel. contractor had no USA ticket
Southern California Gas Company | N | LOS ANGELES | NORWALK | 2023-10-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CALIFORNIA PROFESSIONAL ENGINEERING INC | ROWLAND HEIGHTS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Traffic signal company located line through potholing. Hit line with shovel.
Southern California Gas Company | N | LOS ANGELES | NORWALK | 2023-01-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ELIAS TREJO | NORWALK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner struck 1/2 plastic service with mini backhoe while excavating new sewer. NO USA. Company crew controlled gas and made perm repairs.
Southern California Gas Company | N | LOS ANGELES | NORWALK | 2023-11-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SOCAL SEWER & WATER | LONG BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor was potholing and hit gas line with shovel.
Southern California Gas Company | N | LOS ANGELES | NORWALK | 2023-06-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | STEPHEN DORECK EQUIPMENT RENTALS INC | PICO RIVERA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | ETD couldnt get to meter, marked as branch from GIS, service history showed standard.
Southern California Gas Company | N | LOS ANGELES | NORWALK | 2023-04-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SASCO | FULLERTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1/2 CTS service damaged by shovel while digging for a pole in parkway of neighborhood.
Southern California Gas Company | N | LOS ANGELES | NORWALK | 2023-07-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | D CORPORATION GENERAL CONTRACTING AND ENGINEERING | NUEVO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The 3rd party company was pulling their pipe back with a boring machine when the head of the bore machine fell off and damaged our 2 plastic main.
Southern California Gas Company | N | LOS ANGELES | NORWALK | 2023-07-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SUNWEST ELECTRIC | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1 plastic service hit with backhoe while digging to install electrical conduit.
Southern California Gas Company | N | LOS ANGELES | NORWALK | 2023-07-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 32 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NA | NORWALK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging to install a wall. Unknown contractor hit branch service. No USA
Southern California Gas Company | N | LOS ANGELES | PACIFIC PALISADES | 2023-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | MOORE FOUNDATIONS | RESEDA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | ALL USA marks were good, contractor hit 2 PLA main with excavator.
Southern California Gas Company | N | LOS ANGELES | PACIFIC PALISADES | 2023-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | HOMEOWNER | PACIFIC PALISADES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Property owner was digging for construction and hit our gas line within the delineation. SoCalGas has no record of delineating this property. The customer left the seine before I arrived and had the opportunity to ask questions.
Southern California Gas Company | N | LOS ANGELES | PACIFIC PALISADES | 2023-02-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ROOTER EXPERT | SUN VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was digging hole to find sewer lateral while digging contractor hit 1/2 plastic service, Contractor did not have a USA ticket.
Southern California Gas Company | N | LOS ANGELES | PACIFIC PALISADES | 2023-07-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ALISAL BUILDERS CORP | MARINA DEL REY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor damaged PLA service while exposing the line.
Southern California Gas Company | N | LOS ANGELES | PACIFIC PALISADES | 2023-01-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MARK STEVENS | NEWBURY PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was trenching on property with excavator for new gas line when digging contractor hit and struck a 1 Adalay service. 3rd party contractor had no USA.
Southern California Gas Company | N | LOS ANGELES | PACOIMA | 2023-03-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ROBIN KASHANI | PACOIMA | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | hit line . locator closed out as no access ...
Southern California Gas Company | N | LOS ANGELES | PACOIMA | 2023-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MICHAEL METCAP | PACOIMA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | eir opened to damage. no ccslb small contractor company no license
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2023-05-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JOSE ABDUL VELASCO | PALMDALE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | home owner did not call 811 did not know gas like was there
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2023-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | EDWARD MORTAYA | PALMDALE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner augered through service planting trees No USA USA was called after
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2023-09-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | THE POLCYN | PALMDALE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2023-08-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | NORITA DONES | PALMDALE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer hit service line while doing some landscaping
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2023-10-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MARK DAVIS | LAKE LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hit service with auger. No USA
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2023-06-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | VACANT ACCOUNT | PALMDALE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner doing a remodel hit service No USA
Southern California Gas Company | N | LOS ANGELES | PALMDALE | 2023-01-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MARIO CAMPOS | PALMDALE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Neighbor hit service installing fence post
Southern California Gas Company | N | LOS ANGELES | PALOS VERDES ESTATES | 2023-07-17 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | SHIELDS SEWER CONTRACTING | PALOS VERDES ESTATES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor hit 1 PLA main with mini excavator while trenching to install conduit. USA valid.
Southern California Gas Company | N | LOS ANGELES | PALOS VERDES ESTATES | 2023-05-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SRL CONSTRUCTION | HERMOSA BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service due to no U.S.A. ticket request to provide service location.
Southern California Gas Company | N | LOS ANGELES | PALOS VERDES ESTATES | 2023-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | KANES LANDSPACING | TORRANCE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage from no USA and trying to complete sprinkler installation in a tight area with substructures.
Southern California Gas Company | N | LOS ANGELES | PALOS VERDES ESTATES | 2023-03-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | JGC INC | NORTH HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was hand excavating to install post for fence (for 2220 Thorley Pl) when they struck 1/2 CTS service (branch) at 2224 Thorley Pl. NO USA, Contractor AT FAULT.
Southern California Gas Company | N | LOS ANGELES | PALOS VERDES ESTATES | 2023-11-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | R BUTLIG | PALOS VERDES ESTATES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavating to install a retaining wall when they accidently hit the plastic service with a shovel. USA was not called.
Southern California Gas Company | N | LOS ANGELES | PALOS VERDES ESTATES | 2023-05-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | PAUL HIGGINS | PALOS VERDES ESTATES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was hand excavating with shovel / pic to install new concrete footing when they struck our 1/2 PE gas service (inside 3/4 steel casing). No USA, contractor AT FAULT.
Southern California Gas Company | N | LOS ANGELES | PALOS VERDES ESTATES | 2023-04-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | GUSTAVO CALZADILLA | PALOS VERDES ESTATES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service was damaged by homeowner crew digging to repair sewer lines NO USA.
Southern California Gas Company | N | LOS ANGELES | PALOS VERDES ESTATES | 2023-02-21 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 45 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DOTY BROS | NORWALK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service was properly marked. Water Co used backhoe to remove a rock from trench and moved service enough in the process through indirect contact to cause a leak. Should be charged.
Southern California Gas Company | N | LOS ANGELES | PALOS VERDES ESTATES | 2023-05-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 45 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MORIST CONSTRUCTION | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging a trench for electric conduit on private property when they struck 1 plastic gas service with hand tools. Company crew responded and made permanent repairs. No fire, police, or media on scene.
Southern California Gas Company | N | LOS ANGELES | PANORAMA CITY | 2023-12-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | MOSES AKOPYAN | PANORAMA CITY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was performing work without a valid USA. The contractor was using a skidsteer to grade the front yard. While in the process, the contractor struck a 1/2 plastic insert service.
Southern California Gas Company | N | LOS ANGELES | PANORAMA CITY | 2023-02-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | EZEKIEL GARCIA | PANORAMA CITY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA customer damaged the SoCalGas line by shovel
Southern California Gas Company | N | LOS ANGELES | PANORAMA CITY | 2023-12-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SATENIK HARUTYUNYAN | PANORAMA CITY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was trenching without a valid USA. The contractor was excavating with a backhoe to install a sewer line for a new ADU and struck a 1/2 plastic service.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2023-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | RENE CARDONA PROPERTY MAINTENANCE | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Gas Ops On Call crew arrived to find customer''s maintenance crew hit CTS plastic service line with a shovel while digging to install new sewer line.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2023-06-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 28 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | J & A POOLS INC | PACOIMA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party excavation damage. Contractor struck plastic service within the delineation area. Contractor dumped spoils from the excavation onto the markings.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2023-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | JC WESTERN FENCE CO INC | ALTADENA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | A fencing company struck a plastic service while performing trenching work.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2023-06-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | E L PLUMBING CONSTRUCTION | PASADENA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to use safe excavation practices while digging directly over our marked Utilites.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2023-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 38 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ON DEMAND CONTRACTORS INC | ANAHEIM | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor struck a 1/2 unknown gas service while boring. No USA.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2023-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CONSULTING SIMONYAN | PASADENA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was using jack hammer when damaged plastic service.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2023-02-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 2 |  | WESTERN SUPREME ROOTER INC | ARCADIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor trying to cut out tree root under water line and they hit our plastic svc.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2023-03-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ARTHUR AGATAT | PASADENA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was digging to make repairs to other facilities and while removing roots he hit our pla service
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2023-02-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | QUALITY VINYL PRODUCT | NORTH HOLLYWOOD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer was digger with post hole digger and hit svc.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2023-08-14 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 35 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GR MARTINEZ INC | NA |  | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | OHS crew arrived to find a hit service that had been previously cut back, but left in the yard. Valid USA and marked no SCG. 3rd party contractor was grading and hit an unknown unmarked svc left in the yard where work was taking place.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2023-02-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | GROUND CONTROL CONSTRUCTION SERVICES | SOUTH PASADENA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Subcontractor hired to dig trench for water line that will connect Fire valve to fire sprinkler system did not notify USA and damaged gas plastic service with mini excavator approximately 15'' from MSA. Company crew arrived and completed permanent repairs.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2023-09-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MORNING GLORY GARDENING AND LANDSCAPING SERVICES | PASADENA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1/2inch PA service. Hit with a pick while landscapers were trying to remove a tree. There was no USA called in for the work they were doing.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2023-07-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | RAMCOR | COMPTON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor grading for foundation damaged 1/2 PE service. No USA
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2023-05-04 | Operator excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 6 | 34 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SOCALGAS | PASADENA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Company crew pogoed through a plastic gas main while performing a leak investigation
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2023-05-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | JAVIER SANCHEZ | PASADENA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit gas line while digging.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2023-12-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1.25 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ROBERT BRKICH CONSTRUCTION CORP | MONROVIA | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was trenching for new water main when an unmarked stub was damaged. Contractor did have a USA
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2023-05-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | WEI PI CONSTRUCTION CORPORATION | SOUTH EL MONTE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was digging a trench with backhoe on private property and severed a 1PE Gas Service. No valid USA Ticket at the time of incident.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2023-07-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 34 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | HANDYMAN | PASADENA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor damaged 1/2 gas service while trenching for sewer installation. No USA was called in.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2023-10-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DSRM COMMUNICATIONS | POMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged 1/2 plastic service with shovel while potholing. Service was marked correctly with yellow paint.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2023-05-25 | Operator excavation damage | Main | Steel | Not Available | 6 | 32 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SOCALGAS | PASADENA | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | Company crew damaged a 1 1/4 direct tie stub on a 6 steel main. The stub was pulled out of the main with a backhoe.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2023-06-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 29 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | PERRY THOMAS | MONROVIA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | third party contractor damaged an unmarked 1/2'' plastic service. There were no records indicating there was a service in the area. The service did not supply any customers and the company crew abandoned the service.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2023-01-23 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 4 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | SOUTHERN CALIFORNIA GAS COMPANY | PASADENA | CA | Y | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | LCT was investigating gas leak when 4 plastic service was Damage.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2023-08-30 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 23 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NUMBER PLUMBING | MONTEREY PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | OHS crew arrived to find a 3rd party plumbing contractor had hit our service with a shovel causing broken and blowing. No USA called.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2023-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 29 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ALI IFAILY | PASADENA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contactor damaged a 1/2 plastic gas service while trenching for sewer lateral installation. No USA was called in.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2023-04-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ROLS INC | HUNTINGTON PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party plumber was digging to repair sewer and hit our svc line.
Southern California Gas Company | N | LOS ANGELES | PASADENA | 2023-05-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | WJ LANDSCAPE MAINTENANCE INC | MONROVIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor trenching for new irrigation line when gas service was damaged with trencher.
Southern California Gas Company | N | LOS ANGELES | PICO RIVERA | 2023-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | BAYVIEW DEMOLITION SERVICES | OAKLAND | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While remodeling highschool and replacing water service, contractor hit 2 plastic service on school grounds. Our utility was not marked due to miscommunication with locator.
Southern California Gas Company | N | LOS ANGELES | PICO RIVERA | 2023-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | BAYVIEW SERVICES | PARAMOUNT | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Service mismarked. Damaged 2 service.
Southern California Gas Company | N | LOS ANGELES | PICO RIVERA | 2023-12-12 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 65 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 3 |  | KANA SUBSURFACE ENGINEERING | RIVERSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party excavator working to extend driveway apron under a valid USA. They hit the 2 plastic main with their backhoe.
Southern California Gas Company | N | LOS ANGELES | PICO RIVERA | 2023-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | PARAMOUNT PLUMBING | PARAMOUNT | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber was digging with a shovel working on a sewer line. Hit our service.
Southern California Gas Company | N | LOS ANGELES | POMONA | 2023-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ANTONIO NICOLAS | POMONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | OHS crew arrived to find hit service hit with shovel.
Southern California Gas Company | N | LOS ANGELES | POMONA | 2023-07-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CHRISTIAN TORRES | MONTEBELLO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit service with shovel while digging.
Southern California Gas Company | N | LOS ANGELES | POMONA | 2023-06-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GAIL TITUS | POMONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner did not call in USA and caused damage to gas service
Southern California Gas Company | N | LOS ANGELES | POMONA | 2023-12-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | CALI FIRST REMODEL INC | NORTH HOLLYWOOD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Struck service with pick axe while digging.
Southern California Gas Company | N | LOS ANGELES | POMONA | 2023-11-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 7 |  | INTERNATIONAL LINE BUILDERS | TUALATIN | OR | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor was doing an emergency repair on Edison Line and ended up damaging an 1/2 CTS gas Line with a shovel
Southern California Gas Company | N | LOS ANGELES | POMONA | 2023-09-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | POMONA VALLEY PLUMBING | POMONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor did not have a USA ticket.
Southern California Gas Company | N | LOS ANGELES | PORTER RANCH | 2023-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | AMERICAN MASONRY AND GENERAL CONTRACTING | SIMI VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2in service was damaged with a shovel while digging trench to install Retaining wall, No USA
Southern California Gas Company | N | LOS ANGELES | PORTER RANCH | 2023-08-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CONSTRUCTION | FULLERTON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor digging hit our gas service with pike axe. No USA
Southern California Gas Company | N | LOS ANGELES | PORTER RANCH | 2023-05-31 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  | 1 |  | REGENCY CONCRETE | LONG BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit our 2 main with backhoe. No USA called in
Southern California Gas Company | N | LOS ANGELES | PORTER RANCH | 2023-03-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CLOVER MASONRY | PORTER RANCH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd. party contractor was digging with backhoe and damage riser. NO Valid USA
Southern California Gas Company | N | LOS ANGELES | RANCHO CASCADES | 2023-09-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | GARDENER | RANCHO CASCADES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Gardner for homeowner performing work. While excavating gardener damaged 1/2 CTS service line.
Southern California Gas Company | N | LOS ANGELES | RANCHO CASCADES | 2023-11-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CEASER HERNANDEZ | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer installing drains. Damaged branch in the process.
Southern California Gas Company | N | LOS ANGELES | RANCHO PALOS VERDES | 2023-10-18 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | HARRIOT PARKER | RANCHO PALOS VERDES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 3/4'''' steel service with jackhammer while trying to replace fence post. USA was not called.
Southern California Gas Company | N | LOS ANGELES | RANCHO PALOS VERDES | 2023-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | KRISTIAN KORDIC | RANCHO PALOS VERDES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner hit shallow PE service with shovel. No USA landscape altered service.
Southern California Gas Company | N | LOS ANGELES | RANCHO PALOS VERDES | 2023-09-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DAVID ELLIOT | RANCHO PALOS VERDES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit our service with a shovel while excavating. The contractor did not have USA. Crew made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | RANCHO PALOS VERDES | 2023-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 59 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MAVERICK CONSTRUCTION | LONG BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1 service damaged by mini excavator. No USA.
Southern California Gas Company | N | LOS ANGELES | RANCHO PALOS VERDES | 2023-09-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MAVERICK CONSTRUCTION | LONG BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Sub contractor was digging trench to run a drain pipe and hit our newly installed 1 service about 3 feet away from the riser. No USA ticket.
Southern California Gas Company | N | LOS ANGELES | RANCHO PALOS VERDES | 2023-05-31 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 40001 |  | 6 |  | WA RASIC CONSTRUCTION CO | LONG BEACH | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Per locator remarks. Marked out with flags and offsets FOSII Noel Forst- Gas Company EE who performed the marks did everything per policy and standard. There were multiple utilities / conduit running throughout the excavation area not of GIS / service history. Also, some gas utilities without tracer wire. The foreman / operator for the 3rd party contractor (WAR Construction) who was machine excavating trench to install electrical conduit admitted he didn''t find (physically see) our pipeline where the original marking was (4'' off). So he decided to keep digging instead of calling for verification or remarks. USA was valid.
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2023-04-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | SAUL GARCIA | REDONDO BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging to install a drain pipe when they damaged gas service. Contractor did not have a valid USA. Company crew responded and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2023-09-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SP BEAGLE PLUMBING | HERMOSA BEACH | CA | N | Y | Yes | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor (SP Beagle Engineering) was machine excavating trench to install conduit for electrical when struck our 1/2 PLA gas service. USA was not valid
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2023-07-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | RTB RESIDENTIAL REMODELING | SANTA ANA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was digging / grading for new home extension when they struck the 1/2'''' plastic service with a shovel. No USA.
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2023-07-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | JAMES HERZIKOFF | REDONDO BEACH | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor for homeowner was digging in order to install post for new deck when his shovel damaged 1/2'''' plastic service. No USA
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2023-03-14 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HENKLES AND MCCOY | POMONA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor Henkels and McCoy were hand excavating SMC with shovel to verify steel main when they struck our 1/2 PE gas service. Marks were visible and accurate, USA was valid, Veriforce was valid and crew had work order for address. Expressed to contractor to be careful while hand excavating our gas utilities. Contractor at fault.
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2023-09-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | SP BEAGLE PLUMBING | HERMOSA BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor was hand excavating with shovel when they struck our marked 1/2 PLA gas service. USA valid.
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2023-06-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 24 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | GD PLUMBING | SOUTH GATE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was hand excavating trench with shovel when they struck our 1/2 PE service. NO USA. Contractor at FAULT.
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2023-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 34 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MOON VALLEY NURSERY | TORRANCE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscaper was digging to plant trees with hand tools when they damaged gas service. Contractor did not have a valid USA.
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2023-08-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | WA RASIC | BELL GARDENS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor WAR Construction was machine excavating trench with backhoe when they struck our known / marked 1/2 PE gas service. USA valid.
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2023-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | WA RASIC | LONG BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor struck service with mini excavator while doing work for water main.
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2023-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | J S FINE | REDONDO BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Shallow service was damaged from concrete removal. Contractor new he had adequate clearance if service was installed properly.
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2023-05-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MS CONSTRUCTION MANAGEMENT GROUP | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor digging to expose other utilities when they hit service line. Service was marked in the street and had flags in parkway. Contractor had a valid USA, but failed to exercise caution while digging near gas service.
Southern California Gas Company | N | LOS ANGELES | REDONDO BEACH | 2023-04-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 24 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | W A RASIC | LONG BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor (WAR Construction) was machine excavating trench to install water when they struck our 1 PE gas service. Marks were visible and accurate. Contractor said they knew the marks were there but they forgot cause plate was covering it. They also tried controlling the gas and clamped the service themselves Contractor admitted they were AT FAULT.
Southern California Gas Company | N | LOS ANGELES | RESEDA | 2023-12-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ALB PLUMBING | RESEDA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | ALB Plumbing were digging to instill new sewer hit our gasline with shovel. USA was not called in
Southern California Gas Company | N | LOS ANGELES | RESEDA | 2023-08-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | PEDRO RANGEL | RESEDA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1/2 service, contractor had no USA.
Southern California Gas Company | N | LOS ANGELES | RESEDA | 2023-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | WEST VALLEY WATER | NORTHRIDGE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | Broken and Blowing damage by DWP, mismark. Backhoe ripped standard service while trenching for new water main.
Southern California Gas Company | N | LOS ANGELES | RESEDA | 2023-05-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ADEEDO | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | while digging to install new sewer line for homeowner. Adeedo struck plastic service line with shovel, crew showed up and got gas under control and made permanent repairs, company had no USA
Southern California Gas Company | N | LOS ANGELES | ROLLING HILLS | 2023-07-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 50 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | PROCELL | VISTA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor reported the smell of gas after boring in 4 conduits. Upon centering leak and exposing it, they had nicked the top of a 1/2 IPS service.
Southern California Gas Company | N | LOS ANGELES | ROLLING HILLS ESTATES | 2023-10-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JME CONSTRUCTION | ROLLING HILLS ESTATES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor sawed through 3/4 steel service encased in a large root. No USA
Southern California Gas Company | N | LOS ANGELES | ROLLING HILLS ESTATES | 2023-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ALBERT CHANEY | ROLLING HILLS ESTATES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged service while digging for wall. Crew responded and repaired service. No valid USA
Southern California Gas Company | N | LOS ANGELES | ROSEMEAD | 2023-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | FG REAL ESTATE DEVELOPMENT | GARDEN GROVE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | Contractor hit plastic service while digging trench.
Southern California Gas Company | N | LOS ANGELES | ROSEMEAD | 2023-07-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | HOTLINE CONSTRUCTION | BRENTWOOD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor excavating to install a new pole for Edison, struck 1/2-inch service with a shovel. Service was struck within 6 inches of our delineation.
Southern California Gas Company | N | LOS ANGELES | ROSEMEAD | 2023-11-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | JESSIE DEL CAMPO | ROSEMEAD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Found broken and blowing 1/2 IPS service.
Southern California Gas Company | N | LOS ANGELES | ROSEMEAD | 2023-12-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NEW BEAR WIND INC | MONTCLAIR | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 1/2 PLA service with mini excavator while digging trench for new waterline.
Southern California Gas Company | N | LOS ANGELES | ROSEMEAD | 2023-10-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | DOTY BROS | NORWALK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3 party contractor excavating for city waterway improvement struck 1/2 service. No SCG marking found.
Southern California Gas Company | N | LOS ANGELES | ROSEMEAD | 2023-03-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | F.S CONTRACTORS INC | SYLMAR | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor broke service while excavating.
Southern California Gas Company | N | LOS ANGELES | ROSEMEAD | 2023-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | RJ ALLEN INC | GARDEN GROVE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was working on house line. Struck service while digging.
Southern California Gas Company | N | LOS ANGELES | ROWLAND HEIGHTS | 2023-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | YING JIE LI | ROWLAND HEIGHTS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 ips damaged by a contractor digging to install a fence post.
Southern California Gas Company | N | LOS ANGELES | ROWLAND HEIGHTS | 2023-04-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | LANDSCAPING GUYS INC. | VICTORVILLE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was using a mini excavator to install communication conduit When gas service was damage.
Southern California Gas Company | N | LOS ANGELES | ROWLAND HEIGHTS | 2023-11-03 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 11 |  | CLEARSOURCE COMMUNICATIONS | LAWNDALE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | They hit 1in plastic main with hand tools digging below the box. Main was located and marked correctly. Marks were visible.
Southern California Gas Company | N | LOS ANGELES | ROWLAND HEIGHTS | 2023-10-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | ROWLAND HEIGHTS | CA | N | Y | Yes | No | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged an 1/2 gas service. Homeowner did not have a USA ticket.
Southern California Gas Company | N | LOS ANGELES | ROWLAND HEIGHTS | 2023-08-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 47 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | AG CONSTRUCTION | ONTARIO | CA | N | Y | Yes | No | No | No | No | Yes | Yes | Contractor damaged PLA service line. Contractor began work before USA ticket was valid.
Southern California Gas Company | N | LOS ANGELES | SAN DIMAS | 2023-01-26 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1 | 47 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ADAME COMMUNICATIONS | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor thought he was prying on a rock but was hooked on the bottom edge of the punch tee cap. He pulled hard enough to force the cap to side off, damaging the plastic threads in the process.
Southern California Gas Company | N | LOS ANGELES | SAN DIMAS | 2023-01-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 47 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ADAME COMMUNICATIONS INC | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Line was cut in the street by a contractor who was installing conduit for cable. He hit it with a sharp shooter while digging a spot hole for boring purposes.
Southern California Gas Company | N | LOS ANGELES | SAN DIMAS | 2023-07-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | OASIS DESIGN AND CONSTRUCTION | POMONA | CA | N | Y | Yes | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor severed a 1/2'''' PLA service with a shovel that wasn''t marked and dug before the valid start time/date.
Southern California Gas Company | N | LOS ANGELES | SAN DIMAS | 2023-10-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MLC CONSTRUCTION | WEST COVINA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor who was installing sewer hit our 1/2 svc with a shovel, causing broken and blowing. No USA called.
Southern California Gas Company | N | LOS ANGELES | SAN DIMAS | 2023-09-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | LONG LIU | SAN DIMAS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner installed plastic garden boarder in the front yard. Installed long plastic spikes to secure the plastic boarder and one of the spike punctured our service. Customer did not call USA.
Southern California Gas Company | N | LOS ANGELES | SAN FERNANDO | 2023-12-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1398 |  | 28 |  | 3M PLUMBING | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging to make sewer repairs with no USA and damaged gas service.
Southern California Gas Company | N | LOS ANGELES | SAN FERNANDO | 2023-02-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | JUAN GARCIA TORREZ | SAN FERNANDO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor failed to call USA
Southern California Gas Company | N | LOS ANGELES | SAN FERNANDO | 2023-05-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ANGEL LIRA | SAN FERNANDO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner did not notify USA
Southern California Gas Company | N | LOS ANGELES | SAN GABRIEL | 2023-10-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | FRAIJO BROTHERS | COVINA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor struck gas service with sharp shooter, while digging pot hole.
Southern California Gas Company | N | LOS ANGELES | SAN GABRIEL | 2023-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | FAN CONSTRUCTION | SAN GABRIEL | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 3rd party contractor excavating with an expired ticket. Struck 1/2 plastic branch service in driveway with a backhoe.
Southern California Gas Company | N | LOS ANGELES | SAN GABRIEL | 2023-05-16 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ZENG CUE | SAN GABRIEL | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Tenant hit service with shovel while working on yard.
Southern California Gas Company | N | LOS ANGELES | SAN GABRIEL | 2023-11-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | GRACE ROOTER & PLUMBING | ONTARIO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Damage by excavation to 1/2 gas service
Southern California Gas Company | N | LOS ANGELES | SAN GABRIEL | 2023-06-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MY TOWN BUILDING | FRAZIER PARK | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | While excavating for pool in back yard, contractor struck 1/2 service. Service history incorrect showing service running down driveway. Service altered to go around pool.
Southern California Gas Company | N | LOS ANGELES | SAN GABRIEL | 2023-10-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NA | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowners'' landscaper was digging hole for fencing post and struck our 1/2 plastic service. No USA called in.
Southern California Gas Company | N | LOS ANGELES | SAN MARINO | 2023-09-13 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | TEICHERT PIPELINE | ONTARIO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Teichert was digging to replace gas service when gas service was damage with shovel.
Southern California Gas Company | N | LOS ANGELES | SAN MARINO | 2023-11-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JRC WROUGHT IRON | ROSEMEAD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 service was damaged with tunnel bar while digging to install fence post. No USA
Southern California Gas Company | N | LOS ANGELES | SAN MARINO | 2023-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | SERGIOS PLUMBING | COMPTON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged service by foundation in the process of trying to remove old house line and it was an inserted PE cts service in 3/4 steel.
Southern California Gas Company | N | LOS ANGELES | SAN MARINO | 2023-04-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CABD CONSTRUCTION | SUN VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging with shovel when gas service was damage.
Southern California Gas Company | N | LOS ANGELES | SAN MARINO | 2023-12-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 25 | 23 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MY DESIGN REMODELING | NORTHRIDGE | CA | N | Y | Yes | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was digging a trench to install drainage and severed a 1/2 gas line with a shovel. No USA
Southern California Gas Company | N | LOS ANGELES | SAN MARINO | 2023-09-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 33 | 27 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | AMERICAN STAR CONSTRUCTION INC | MONTEREY PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged gas service while trenching for an electric trench. No USA was called in.
Southern California Gas Company | N | LOS ANGELES | SAN PEDRO | 2023-03-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LADWP | SAN PEDRO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Water company open trenching the street pulled a 3/4 steel service that was mismarked by about 5 feet. Service was inserted but locate became poor passing private property onto the street and followed an unidentified line. Employee used service history, used footage and locator for locating service. Dug up on private property and found were cts came out of 3/4 steel for about 3 feet and was reinserted out to the SMC. No locate wire was tied to that portion of the service causing a short for an accurate locate. Water Company was advised that locate was not strong and to pothole for the service and to contact us if service was not in the correct location. Water Company failed to do so and continued to excavate with backhoe while simultaneously hand digging a few feet away for the service.
Southern California Gas Company | N | LOS ANGELES | SAN PEDRO | 2023-06-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | VCI CONSTRUCTION LLC | UPLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | GIS showed 1 service on the property that was located but did not cross the delineation marked out by 3rd party contractor. 2nd service was coming off a building far back into the property, no history of service on GIS, or land markings to indicate the service crossed the delineation.
Southern California Gas Company | N | LOS ANGELES | SAN PEDRO | 2023-09-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | AM BUILDERS & REMODELING INC | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractors installing fence and a new water line for homeowner, damaged 1 plastic service in the process. No USA was called in.
Southern California Gas Company | N | LOS ANGELES | SAN PEDRO | 2023-03-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | STEPHEN SCHMIDT | SAN PEDRO | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Customer was hand digging around exposed gas line and struck service with shovel while installing. Trench was dug out all the way out to the main, line was exposed in various locations.
Southern California Gas Company | N | LOS ANGELES | SAN PEDRO | 2023-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | FOUNDATION TECHNOLOGY | SANTA CLARITA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service was already exposed. 3rd party contractor failed to protect our facilities by digging with a mini excavator.
Southern California Gas Company | N | LOS ANGELES | SANTA CLARITA | 2023-08-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | WILCOX & WILCOX | CANOGA PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit cap of stub service with backhoe. Contractor dug before legal start date of ticket.
Southern California Gas Company | N | LOS ANGELES | SANTA CLARITA | 2023-09-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 2 |  | SHELL BACK PLUMBING AND DRAIN | VALENCIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was excavating over service and struck 1/2 CTS PLA service.
Southern California Gas Company | N | LOS ANGELES | SANTA CLARITA | 2023-09-13 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | VANKIRK ELECTRIC | BEVERLY HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was excavating a trench with a backhoe and struck a marked 2 main. Main was properly marked, paint was clear and visible, shaded with sand and had warning mesh above the main in accordance with company policy.
Southern California Gas Company | N | LOS ANGELES | SANTA CLARITA | 2023-10-04 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SAM HILL & SONS INC | VENTURA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to use hand tools over 2 plastic main and hit end of main with backhoe.
Southern California Gas Company | N | LOS ANGELES | SANTA FE SPRINGS | 2023-06-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 1 | 80 | 80 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DARIO DE LA RIVA | SANTA FE SPRINGS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor saw cut through shallow HP service line while trying to make repairs to cement ramp to building. NO USA was called before work was started.
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2023-07-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HALO CONTRUCTION | SANTA MONICA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor failed to pothole prior to using trencher.
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2023-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | JULIA ADELE DESIGN | SANTA MONICA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service while attempting to expose line.
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2023-07-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PALOMO CONSTRUCTION | WOODLAND HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was working on the property excavating to remove tree while in the process of removing tree 3rd party contractor hit and damaged 1/2 IPS service. 3rd party contractor had no USA.
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2023-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ROOTER RUNNER | VAN NUYS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumbing company was fixing a sewer when they tried to dig out the sewer they damaged a 1/2 ips service at the MSA. due to the sewer being exposed and cut open and the damage happening right next to the sewer the gas migrated inside the house. ETR evacuated house from workers and opened doors and windows to vent the gas out. crew arrived and dug out a control hole, pinched and fixed the gas line.
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2023-04-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | BEN G LUNSKY | SANTA MONICA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Developer hired a contractor to install irrigation lines and the contractor damaged the exposed gas service at the riser pigtail. Dig alert was never contacted.
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2023-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ADEEDO PLUMBER | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumbing company was digging to repair a sewer line when they damaged a plastic service with a shovel.
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2023-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CM CONSTRUCTION | TUJUNGA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor crew had dug up old steel line and thought that was the gas line. The marks on the street said 1/2 PLA service. Locators marks are accurate.
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2023-03-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | SUMMERS PLUS | TORRANCE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was digging in street for new electrical lines while digging with backhoe 3rd party contractor hit a 3/4 steel service.
Southern California Gas Company | N | LOS ANGELES | SANTA MONICA | 2023-09-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | LEIGHTON GROUP | IRVINE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged unmarked 1 PLA cross lot service while taking soil samples.
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2023-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | VALLEY VILLAGE MANAGEMENT CORPORATION | VALLEY VILLAGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Unlicensed 3rd party contractor was excavating with hand tools for footing. While in the process, the third party contractor struck a 1/2? plastic service. SoCalGas crew responded and controlled the release and then made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2023-02-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | R & R PLUMBING | INGLEWOOD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Third party contractor was excavating to replace a section of sewer line and while in the process, the contractor struck a 1? service with a backhoe. SoCalGas crew responded and controlled the release by pinching the service. They then made permanent repairs. The contractor did have a valid USA.
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2023-04-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | UNLICENSED DAY LABORERS | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd. party contractor digging to put in a fence hit service with shovel. No USA
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2023-03-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MARIO LOPEZ | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | An unlicensed landscaper performing work on behalf of the homeowner was digging a whole to install a tree. While in the process, the landscaper damaged a 1/2? plastic service with a shovel. SoCalGas crews responded and controlled the release of gas by pinching the service line. The crew then made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2023-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | RAMONA INC | BALDWIN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor stuck a 1/2 plastic stub and a 1 service while excavating to install a new sewer line. The contractor initially hit an unmarked stub; the crew responded, controlled the release and then made permanent repairs. The third party contractor then struck a 1 plastic service; the crew responded a second time and controlled the release of gas and then made permanent repairs. The contractor did have a valid USA, but failed to follow proper procedures when excavating.
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2023-08-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | SIMPLY DONE INC | VAN NUYS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was excavating for the property sewer line without a valid USA. While in the process, they struck a 1/2 plastic service with a shovel.
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2023-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | RAMONA INC | BALDWIN PARK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Third party contractor struck a 1 inch plastic service with a backhoe while excavating for a sewer line. SoCalGas GIS shows there is a 3/4 inch steel service
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2023-08-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | SUPREME REMODELING | VAN NUYS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was excavating for irrigation, and while in the process, they struck a 1/2 plastic service with a pickax. The contractors did not have a valid USA.
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2023-03-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CHARLES VANYO | TORRANCE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | This incident appears to be an excavation damage, however, the Third Party contractor stated they were performing landscaping activities on the side of the home where the gas meter and service run. The contractor stated they smelled gas and decided to dig up the area where they smelled gas to see if they could fix it. They noticed it was a plastic gas line and made the decision to call SoCalGas so we could come fix the leak. SoCalGas crew responded and controlled the release of gas by pinching the gas line and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2023-04-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LADWP | NORTH HOLLYWOOD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor LADWP damaged a 1/2 plastic service while excavating. The contractor thought they were fine to continue with their work because they saw a line that was not SoCalGas. They continued to excavate and damaged the line as they did not maintain clearance. They tried to blame SoCalGas because the ETD informed them the line was in casing and the section they hit was not. The marks were accurate and the contractor should have called to verify the line they found. SoCalGas crew responded and controlled the release of gas and made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2023-04-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | SUNIL DHIR | SHERMAN OAKS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Unknown Third Party Contractor working for the homeowner damaged a 1/2 plastic service with hand tools. When speaking with some of the workers on site, they stated they have no clue how the damage occurred and it was that was for a couple days. The damaging party bent the 1/2 plastic service back and tied it with a plastic bag to stop the leakage. CSF went out to the order and noticed the leakage and called in an RFA for Distribution. SCG Crew responded and controlled the release of gas and altered the service to eliminate the leakage
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2023-11-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 1 |  | NA | SHERMAN OAKS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Damaged by hand tools.
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2023-05-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NUMA BROTHERS CONSTRUCTION INC | LOS ANGELES | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner/contractor was excavating with a backhoe and struck a 1/2 plastic service. The contractor stated he called in an abandonment last year and thought the line was abandoned. After speaking with the district planner, it was found that the contractor did not return emails or phone calls, so the District Planner canceled the order. SoCalGas crew responded and performed a cutback as the contractor buried and placed foundation over the live service and riser.
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2023-11-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | OL DEVELOPMENT | SUN VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was performing work with a valid USA. While in the process of excavating, the contractor struck a 1 plastic service with a tunnel bar
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2023-12-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 4 |  | MICHAEL OCHOA | SUN VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged 1 PE service that was properly marked. USA Valid.
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2023-08-17 | Third party excavation damage | Riser | Steel | Grader/Scraper | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | CSH PROPERTIES | STUDIO CITY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged our riser while grading, completed a cut and thread to eliminate the leak. Third party contractor was using a skid steer to grade and clean up the front yard without a valid USA. While in the process, the contractor struck a 3/4 steel service riser below grade.
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2023-11-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | RUBEN GEVORKYAN | SHERMAN OAK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was performing work to install a new fence without a valid USA. The homeowner was using hand tools to dig out the fence post and damaged a 1/2 plastic service.
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2023-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | HOME PLUMBING AND REMODEL | VALLEY VILLAGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was excavating with hand tools without a valid USA. While in the process, the contractor struck a 1/2 plastic branch service.
Southern California Gas Company | N | LOS ANGELES | SHERMAN OAKS | 2023-04-17 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 3 |  | ADEER AZARIAN | SHERMAN OAKS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor was digging with equpiment when they pulled on steel line and broke it
Southern California Gas Company | N | LOS ANGELES | SIERRA MADRE | 2023-04-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | RYAN SCHAUER | SIERRA MADRE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Work on property seemed to be for drainage. No one was onsite at ETR arrival. 1/2cts service was nicked with shovel on the side. Crew arrived and controlled leak and completed permanent repairs.
Southern California Gas Company | N | LOS ANGELES | SIERRA MADRE | 2023-03-09 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 28 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HARDY & HARPER INC | SANTA ANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor damaged gas service while saw cutting the road for a water replacement project
Southern California Gas Company | N | LOS ANGELES | SIERRA MADRE | 2023-12-07 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HHS | AZUSA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor damaged a 2 steel main while trenching for conduits. The contractor was digging within the tolerance zone with heavy equipment. The contractor did have a valid USA.
Southern California Gas Company | N | LOS ANGELES | SIERRA MADRE | 2023-07-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | INTERNATIONAL LINE BUILDERS | JURUPA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to use caution when digging over marked gas line.
Southern California Gas Company | N | LOS ANGELES | SOUTH EL MONTE | 2023-11-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | RICHARD WONG | SOUTH EL MONTE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor excavating with a backhoe and struck 1/2 plastic service.
Southern California Gas Company | N | LOS ANGELES | SOUTH EL MONTE | 2023-12-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | TE ROBERTS INC | IRVINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor struck service with shovel while potholing.
Southern California Gas Company | N | LOS ANGELES | SOUTH EL MONTE | 2023-08-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | TURN AROUND COMMUNICATIONS | SOUTH EL MONTE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor, failed to verify exposed line after ETD marked plastic and they potholed a steel line and proceeded to bore in conduit. Contractor spudded in and damaged 1 plastic service.
Southern California Gas Company | N | LOS ANGELES | SOUTH GATE | 2023-11-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HARRISON BUILDING | HUNTINGTON BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit service while digging trench for utilities for an ADU
Southern California Gas Company | N | LOS ANGELES | SOUTH GATE | 2023-12-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ELITE PRIME CORP | DOWNEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractors digging water trench hit 1/2 IPS service with shovel.
Southern California Gas Company | N | LOS ANGELES | SOUTH GATE | 2023-10-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 5 |  | DORECK CONSTRUCTION | PICO RIVERA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1/2 plastic service damaged with backhoe by 3rd party contractors installing new water main for the City of Southgate.
Southern California Gas Company | N | LOS ANGELES | SOUTH GATE | 2023-11-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | STEVE DORECK | PICO RIVERA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor caused damaged to gas service when excavating for new water line installation. USA was valid, line marked, but contractor failed to hand expose.
Southern California Gas Company | N | LOS ANGELES | SOUTH GATE | 2023-11-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | DORECK CONSTRUCTION | PICO RIVERA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1/2 plastic service damaged by contractors installing water main for city.
Southern California Gas Company | N | LOS ANGELES | SOUTH GATE | 2023-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | DORECK CONSTRUCTION | PICO RIVERA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1/2 plastic service damaged by contractors using sharpshooter to exposed service.
Southern California Gas Company | N | LOS ANGELES | SOUTH GATE | 2023-11-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 36 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DORECK CONSTRUCTION | PICO RIVERA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged 1/2 CTS service with hand tools. Contractor did have a valid USA and service was marked.
Southern California Gas Company | N | LOS ANGELES | SOUTH GATE | 2023-07-31 | Third party excavation damage | Meter | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | TA ENTERPRISES | FULLERTON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | While trenching to install new sewer contractor hit gas line. USA was notified. Marks were off by 3''
Southern California Gas Company | N | LOS ANGELES | SOUTH GATE | 2023-01-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 38 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 3 |  | BUILDING MAINTENANCE | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Maintenace worker caused damage to gas service when exposing water service. no usa was present.
Southern California Gas Company | N | LOS ANGELES | SOUTH PASADENA | 2023-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 37 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | KSM CONSTRUCTION | LA CRESCENTA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor damaged a 1/2 plastic gas service while trenching for water service installation. No USA was called in.
Southern California Gas Company | N | LOS ANGELES | SOUTH PASADENA | 2023-08-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DESIGN MANAGEMENT AND CONSTRUCTION SERVICES | VALENCIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged gas service while trenching for water/sewer lines. No USA.
Southern California Gas Company | N | LOS ANGELES | STUDIO CITY | 2023-05-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | FLAMINGO CONTRUCTION | STUDIO CITY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Developer 3rd Party Contractor digging for footings on property failed to hand expose our 1 Service Pipe. No USA however there were some old gas marks showing there was a gas service in the vicinity. Gas Co Crew made permanent repairs and reinstated inactive service
Southern California Gas Company | N | LOS ANGELES | STUDIO CITY | 2023-05-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | HOMEOWNER | STUDIO CITY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | while digging a trench contractor working for home owner struck plastic line crew showed up and made repairs no usa
Southern California Gas Company | N | LOS ANGELES | STUDIO CITY | 2023-04-25 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | MLADEN BUNTICH CONT CO | UPLAND | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was excavating in the street with a backhoe and damaged a 3/4 steel service. The contractor pulled on roots for a tree and didn''t realize the root was surrounding our service line. The contractor called in an emergency L&M instead of calling in the damage that occurred. SCG crew responded and controlled the release of gas by squeezing the line. The cut back the service and a crew came out the next day to make permanent repairs.
Southern California Gas Company | N | LOS ANGELES | STUDIO CITY | 2023-01-23 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 1 | 32 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | TIM ROBINSON | BELLFLOWER | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor dug over are service trying to find a house line leak that customer service tagged him out for NO Usa
Southern California Gas Company | N | LOS ANGELES | STUDIO CITY | 2023-06-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | STUDIO CITY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party Contractor hired on behalf of homeowner was digging near riser location for grade changes, adding planters/steps, damaged gas service with shovel/pick. Due to grade change crew had to further excavate down to proper grade for our service pipe and to secure riser. No USA on file. Crew repaired with 1/2 CTS, Section of Pipe and New Riser.
Southern California Gas Company | N | LOS ANGELES | STUDIO CITY | 2023-11-28 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SOCALGAS | VAN NUYS | CA | Y | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | LST was using a Pogo to take gas samples and struck a 1/2 plastic service.
Southern California Gas Company | N | LOS ANGELES | SUN VALLEY | 2023-11-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 2 | 60 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | A1 FENCE COMPANY | ANAHEIM | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor augered through a 2 inch plastic service. No USA called in for this job.
Southern California Gas Company | N | LOS ANGELES | SUN VALLEY | 2023-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | ARMANDO IRON WORKS | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging for fence post damaged plastic gas service. Contractor did not have a valid USA. Company crew made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | SUN VALLEY | 2023-01-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | PENCE CONSTRUCTION | REDLANDS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Accurate marks not properly maintained
Southern California Gas Company | N | LOS ANGELES | SUN VALLEY | 2023-11-07 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1 | 59 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 8 |  | STEVE YUN | SUN VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavation damage 1 PLA main.
Southern California Gas Company | N | LOS ANGELES | SUN VALLEY | 2023-03-18 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SAM KISHSIAN | SUN VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | home owner greading lot struck gas line no usa
Southern California Gas Company | N | LOS ANGELES | SUN VALLEY | 2023-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | GLENDALE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage Service. No USA
Southern California Gas Company | N | LOS ANGELES | SUN VALLEY | 2023-09-18 | Third party excavation damage | Riser | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JAVIER AVILA | SUN VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner running his own gas line for houseline. Struck riser. No USA . Called off hours during oncall
Southern California Gas Company | N | LOS ANGELES | SUN VALLEY | 2023-07-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | RAZMIK HONARCHIAN | SUN VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator damaged 1/2 IPS service while digging to install new septic tank. Crew made repairs by replacing damaged section of PLA pipe.
Southern California Gas Company | N | LOS ANGELES | SUN VALLEY | 2023-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MARO TAHMADYAN | SUN VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit PE service. No USA
Southern California Gas Company | N | LOS ANGELES | SUNLAND | 2023-01-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | KORDICH CONSTRUCTION INC | CYPRESS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | pla service struck while repairing sewer line
Southern California Gas Company | N | LOS ANGELES | SUNLAND | 2023-07-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | SPEEDY VINYL FENCING INC | NORTH HOLLYWOOD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 1/2 CTS PLA service.
Southern California Gas Company | N | LOS ANGELES | SUNLAND | 2023-11-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | UNLICENSED DAY LABORERS | SUNLAND | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged service while removing a tree.
Southern California Gas Company | N | LOS ANGELES | SUNLAND | 2023-02-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ALEX GONZALES | SUNLAND | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No usa called in . struck gas line while grading
Southern California Gas Company | N | LOS ANGELES | SUNLAND | 2023-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | EDWARD HAYRAPETIAN | SUNLAND | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | PE service damaged
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2023-01-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 25001 |  | 2 |  | XEBEC BUILDING COMPANY INC | SEAL BEACH | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd Party damaged 2 service.
Southern California Gas Company | N | LOS ANGELES | SYLMAR | 2023-05-11 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 1 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | LADWP | NORTH HOLLYWOOD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | DWP pulled a cut back service that was unknown
Southern California Gas Company | N | LOS ANGELES | TARZANA | 2023-03-16 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2000 |  | 1 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3 party damage to service.
Southern California Gas Company | N | LOS ANGELES | TARZANA | 2023-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  |  | NA | HOMEMADE CUSTOM BUILDERS | ENCINO | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor had dug up service out of ground and was grading on an empty lot. From information that I gathered from crew, damage may have been intentional to expedite service abandonment. Company crew abandoned service at SMC.
Southern California Gas Company | N | LOS ANGELES | TARZANA | 2023-12-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | PROBITY CONSTRUCTION & DEVELOP | TARZANA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage to company property. No USA
Southern California Gas Company | N | LOS ANGELES | TARZANA | 2023-11-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | UNLICENSED DAY LABORERS | TARZANA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage to company property by homeowner.
Southern California Gas Company | N | LOS ANGELES | TARZANA | 2023-10-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ET DEVEMLOPMENT | TARZANA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1/2 plastic service while digging trench with hand tools. Contractor did not have a valid USA on file.
Southern California Gas Company | N | LOS ANGELES | TEMPLE CITY | 2023-08-10 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 2 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 3 |  | SOCALGAS | ALHAMBRA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Company crew accidently caused damage to company facility while in the process of investigating active leak in the location of incident.
Southern California Gas Company | N | LOS ANGELES | TOPANGA | 2023-12-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ALL CONSTRUCTION | SIMI VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging to put in meter guard for fire hydrant and hit our gas lines. No USA
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2023-01-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 26 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 13 |  | LADWP | SAN PEDRO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor hit 1/2 ips service in the street while excavating to replace water main with back hoe. Service was mismarked, GIS had inaccurate information, listed main as 6 steel but is actually 2 PLA. Service was listed as 3/4 steel but is actually plastic a little bit past PL and transitions into steel which led to the locate bleeding off when hooked up to riser. ETD used footage as well, spoke to contractor about locate not being very strong and were advised to hand dig, found 3/4 steel and thought it was the service, proceeded to use back hoe.
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2023-03-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 6 |  | DRAIN IT PLUMBING | WHITTIER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor was hand excavating with shovel to repair water line when they struck our 1/2 gas service. Marks were accurate from old ticket / contractor had no current USA ticket and only knew of damage cause contractor called in an emergency USA ticket. Contractor is AT FAULT.
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2023-01-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 24 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 11 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was excavating to replace water main, when they hit 1/2 IPS service with backhoe. Contractor believed the gas service was 1'' steel, which was an abandoned service.
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2023-04-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 24 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 37 |  | GOTHIC LANDSCAPING | TORRANCE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party was grading dirt to level for future housing when they struck our 3/4 steel service at 1439 Plaza Del Amo. Service was pulled off 2 steel main. Marks were accurate and the contractor admitted they knew the marks were there and they were aware of our service. They also expressed they were at fault and said the operator was new and wasn''t experienced. USA was valid. Contractor was AT FAULT.
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2023-10-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | GOLDEN CONSTRUCTION GROUP | NORTHRIDGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While trenching for sewer install, contractor damaged 1/2'''' IPS service. USA was not called.
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2023-07-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 3 |  | CAL-PACIFIC BUILDERS | TORRANCE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor building ADU damaged plastic service while trenching with a mini excavator. Contractor did have a USA and struck service within delineation.
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2023-10-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 22 | 22 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | VIDMAR INC | SOUTH EL MONTE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator overlooked markings for service.
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2023-04-12 | Third party excavation damage | Main | Steel | Augur | 2 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  |  | NA | VIDMAR | LONG BEACH | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 2 steel main was augured into, and contractor didn''t have a USA ticket. No evacuations were made and main was bypassed and stopped to complete repairs of the damaged portion. Repairs were made by cutting out damaged pipe and welded in approximately 4 inch of 2 steel pipe. No outages as main was bypassed.
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2023-02-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | RELIABLE CABLE T V CONTRACTORS INC | GARDENA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor was machine excavating trench to install conduit for cable when they struck our 1 PE gas service. USA valid, the main and service was marked but the service was marked outside the delineation. ETD did put in notes the main and 3 services were marked out that encompassed the USA ticket. During investigation, it shows contractor did not hand excavate service. Contractor possibly at fault, will be determined by claims.
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2023-10-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | ON DEMAND CONTRACTORS INC | WHITTIER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While hand excavating, contractor damaged a 1/2 CTS service covered by tree roots.
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2023-02-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | ASPHALT PROTOMETAL''S | NEWBURY PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was grading dirt lot on private property to install future street with backhoe when they struck our 2 PE Main. No valid USA. Contractor is AT FAULT.
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2023-10-25 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 2 | 30 | 24 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | PETERSON BROTHERS CONSTRUCTION INC | ANAHEIM | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging to install install ballards. 3rd party contractor was augering to install bollards when they struck our 2 PE gas main. No USA valid.
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2023-05-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | DOMINGUEZ GENERAL CONTRACTOR | POMONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Not to be charged to to unlocatable service.
Southern California Gas Company | N | LOS ANGELES | TORRANCE | 2023-03-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  |  | NA | VIDO ARTUKOVICH AND SON INC | SOUTH EL MONTE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Locator marked SMC to stele service on property. Parcel should only be served with one service according to tariffs. 3 P.E. service was not detected in GIS. and wasn''t located but L&M Ee.
Southern California Gas Company | N | LOS ANGELES | TUJUNGA | 2023-02-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ALFREDO CARRANZA | TUJUNGA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No usa called in . struck service line during sewer repair
Southern California Gas Company | N | LOS ANGELES | VALENCIA | 2023-06-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | STAY GREEN INC | SANTA CLARITA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Valid USA all marks were visible and marled correctly. 3 party contractor failed to expose 1 plastic service, which resulted in damaging 1 line with the use of trencher. Company crew made repairs.
Southern California Gas Company | N | LOS ANGELES | VALENCIA | 2023-04-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | FREDES ALVARADO | NORTH HOLLYWOOD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | no ccslb small contractor no license did not call for usa struck gas line
Southern California Gas Company | N | LOS ANGELES | VALENCIA | 2023-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | BIG E MASONRY SOLUTIONS | CASTAIC | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA
Southern California Gas Company | N | LOS ANGELES | VALENCIA | 2023-07-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | CPG SOLAR | NORTH HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Contractor hit 1/2 CTS service while installing solar panels.
Southern California Gas Company | N | LOS ANGELES | VALENCIA | 2023-10-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | WILCOX & WILCOX | CANOGA PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 1/2 IPS Service stub while digging for conduit installation. Damage was done with hand tools (shovel). Contractor did not have a USA.
Southern California Gas Company | N | LOS ANGELES | VALENCIA | 2023-05-23 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 38 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ELITE CONSTRUCTION INC | BAKERSFIELD | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Gipp contractor installing meter guards damaged service. Line was located by them.
Southern California Gas Company | N | LOS ANGELES | VALENCIA | 2023-01-18 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 15001 |  |  | NA | SUTTLES PLUMBING INC | SIMI VALLEY | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Crew working to repair water line hit 4 main with backhoe prior to usa ticket being valid
Southern California Gas Company | N | LOS ANGELES | VALLEY VILLAGE | 2023-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NA | VALLEY VILLAGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was excavating to trench out the gas line so ARB contractor could come out and make alteration to the service. While in the process, they struck a 1/2? plastic service with a pickax.
Southern California Gas Company | N | LOS ANGELES | VALLEY VILLAGE | 2023-02-28 | Third party excavation damage | Meter | Steel | Backhoe/Trackhoe | 0.75 | 40 | 35 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ET DEVELOPMENT | NORTH HOLLYWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was moving debris and leveling the ground when they uprooted the service for the property. SoCalGas crew responded and performed a leak investigation; no leakage found. The responding crew clamshelled the service valve and informed the customer the line was live and then let them know they need to call in an abandonment so they could safely perform the needed work.
Southern California Gas Company | N | LOS ANGELES | VALLEY VILLAGE | 2023-04-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ET DEVELOPMENT | NORTH HOLLYWOOD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | house is under construction while digging contractor pulled up steel line with 1/2 cts line inserted . they bent line and broke plastic line. crew cut steel and exsposed cts and squeezed and made permanent repairs
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2023-10-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ITAMAR EDSHTAIN | VAN NUYS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 1/2 CTS service with backhoe. Contractor did not have a valid USA.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2023-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | HC BUILDERS | ENCINO | CA | N | Y | Yes | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was excavating with a backhoe on an empty lot without a valid USA. While in the process, the contractor struck a 3/4 steel service. The contractor had an expired USA and they failed to follow the required procedures when excavating.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2023-04-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LG BUILDERS | NORTH HOLLYWOOD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was excavating and in the process they struck a 1/2 inch plastic service with a backhoe. The contractor called in a USASoCalGas technician marked and flagged the location of the service correctly. The contractor removed the flags and thought the gas service was deeper than it was. SoCalGas crews responded, controlled the release, pressure tested the service from the damage to the riser, and then made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2023-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | LADWP | CHINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | DWP hit marked gas line.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2023-05-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | LADWP | NORTHRIDGE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | DWP Rep stated one of their employees working on site slipped and a shovel damaged SoCalGas utilities. I noticed DWP was excavating with a backhoe when trenching to install a new water line and they were using the backhoe within 3 feet of SoCalGas utilities when they should have been using hand tools. All services were correctly located and marked by SoCalGas ETD. SoCalGas Crew responded and controlled the release of gas and then made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2023-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | GNG VINYL FENCING PATIO COVERS | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging to install fence, contractor struck plastic line with pothole digger. Crew showed up and made permanent repairs
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2023-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ARIEL DAVID | VAN NUYS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was excavating and failed to call in USA. The contractor was installing a gas line for a pool at new residential dwelling. While in the process, the contractor struck the branch service line that feeds 5637 with a shovel. SoCalGas crew responded and controlled the release of gas by pinching the service. The crew then made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2023-12-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 14 |  | RH PACIFIC BUILDERS | GLENDALE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No valid USA. Damaged 1/2 IPS line.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2023-05-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | G AND A | VAN NUYS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor damaged a 1? service line with a backhoe when excavating to install a water line. The service was as properly located and marked, however, the contractor stated he thought the line was deeper than it was. SoCalGas crew responded and controlled the release of gas. They then made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2023-12-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HOMEOWNER | VAN NUYS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage to company property 1/2 service. No USA
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2023-07-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | EMERSON PLUMBING | SOUTH PASADENA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was trenching to install conduit for a water fountain. While in the process, the contractor struck a 1/2 plastic service with a pickaxe.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2023-06-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 45 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | DANNY AKOPYAN | BURBANK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor cutting root with electric saw cut through riser. Company crew responded and replaced riser. Contractor did not have a valid USA.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2023-09-05 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | WRA CONSTRUCTION | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor was using a backhoe to remove water and mud from the driveway apron area with a valid USA, however, they failed to request remarks as they removed then when performing road work. While in the process, the third party contractor struck a 2 main
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2023-09-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | REMODEL ME | SHERMAN OAKS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor trenching for ADU utilities without a valid dig alert ticket damaged 1/2 IPS service in the yard.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2023-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MIGUEL RODRIGUEZ | VAN NUYS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavating with a shovel and did not have a valid USA.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2023-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | EDUARDO ALVAREZ | VAN NUYS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damage service while hang digging. No USA
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2023-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ROBLEDS LANDSCAPING | LONG BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was excavating multiple holes to install new trees. While in the process, the contractor struck a 1 plastic service with a shovel. SoCalGas crew responded and controlled the release of gas, and then made permanent repairs. The contractors failed to call in a USA prior to performing the work.
Southern California Gas Company | N | LOS ANGELES | VAN NUYS | 2023-05-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 11 |  | NISSI PLUMBING | SUN VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor struck a 1/2? plastic service when conducting emergency sewer repair. SoCalGas crew responded and controlled the release of gas by pinching the service line. The crew then made permanent repairs. The contractor did not have a valid USA.
Southern California Gas Company | N | LOS ANGELES | VENICE | 2023-04-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | MATTHEW ABD STEWART COMPANY INC | SIGNAL HILL | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | third party contractor was installing sewer and claimed they potholed the service. Service was missed marked. LOCATOR PICKED UP SIGNAL ON RIGHT SIDE OF HOME BUT SERVICE WAS DAMAGED ON LEFT SIDE OF HOME. CONTRACTOR FAILED TO CALL 811 TO COME BACK AND LOCATE SERVICE AFTER FAILING TO FIND WHEN POTHOLING. 3RD PARTY CONTRACTOR CONTINUNED TO TRENCH AFTER NOT FINDING SERVICE.
Southern California Gas Company | N | LOS ANGELES | VENICE | 2023-09-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | LADWP was installing a new water line when they damaged a 1/2 plastic service.
Southern California Gas Company | N | LOS ANGELES | VENICE | 2023-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ML CONSTRUCTION | MARINA DEL REY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was digging for new footing for home in the process of digging 3rd party contractor hit 1/2 CTS service with shovel. Contractor had no USA
Southern California Gas Company | N | LOS ANGELES | VENICE | 2023-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | VCI CONSTRUCTION | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was trenching on property for new building while trenching 3rd party contractor hit and damaged 1/2 CTS pipe with shovel. 3rd party contractor Did not have a USA.
Southern California Gas Company | N | LOS ANGELES | VENICE | 2023-05-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | VALLERNAUD CONSTRUCTION | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was excavating for new irrigation lines without notifying dig alert and damaged a 1/2 plastic service.
Southern California Gas Company | N | LOS ANGELES | VENICE | 2023-05-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 18 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RAFA CONSTRUCTION INC | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor dug into plastic service with backhoe. Crew was able to control gas and perform service alteration.
Southern California Gas Company | N | LOS ANGELES | VENICE | 2023-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | KAY VIRBILA | VENICE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hired a landscaper to do landscaping work for her and they were digging to install some trees and they damaged a 1/2 PLA Service. the owner had the house remodeled and in the process they altered with the meter location moving the meter to a new location. no planner was contacted. crew cut back service and advised owner to call for a planner to plan a new service location. no USA was called in.
Southern California Gas Company | N | LOS ANGELES | VIEW PARK | 2023-08-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 22 | 19 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GNK CONSTRUCTION | OAK PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit service with mini excavator.
Southern California Gas Company | N | LOS ANGELES | VIEW PARK | 2023-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | BUILDERS ELITE TEAM | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1/2 service with shovel.
Southern California Gas Company | N | LOS ANGELES | VIEW PARK | 2023-12-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | BUILDERS ELITE TEAM | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1/2 service with shovel.
Southern California Gas Company | N | LOS ANGELES | VIEW PARK | 2023-06-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 18 | 18 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SOCAL EDISON | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor dug into plastic service; broken and blowing. Crew arrived on scene, were able to control gas and altered the service.
Southern California Gas Company | N | LOS ANGELES | WALNUT | 2023-09-26 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 47 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | SE PIPELINE | SANTA FE SPRINGS | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | Crew failed to expose branch service while installing new service for the standard. They struck the branch while attempting to accubore in new gas service.
Southern California Gas Company | N | LOS ANGELES | WALNUT | 2023-08-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | TRI COUNTY DEVELOPMENT CONSTRUCTION | RIVERSIDE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Third party contractor hit our service while potholing to bore in conduits.
Southern California Gas Company | N | LOS ANGELES | WALNUT | 2023-12-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Individual contractor hit service line with a pickaxe while digging to repair customer''s sewer line.
Southern California Gas Company | N | LOS ANGELES | WALNUT | 2023-12-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ELIAS MARTINEZ | WALNUT | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | In the process of digging with mini excavator the crew damaged 1/2 PLA branch service to neighboring house which is owned by the same person.
Southern California Gas Company | N | LOS ANGELES | WALNUT | 2023-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | DEMO CONCRETE SPECIALISTS | GARDEN GROVE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage 1/2? PLA service. No USA.
Southern California Gas Company | N | LOS ANGELES | WALNUT | 2023-04-14 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 3 |  | DOTY BROS | NORWALK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | USA was called . Marking were at approx.2ft from damage line . Crew arrived dug out control holes and controlled damaged pipe .
Southern California Gas Company | N | LOS ANGELES | WEST COVINA | 2023-06-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | BUILD CAL LANDSCAPE | GLENDALE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging with backhoe to install block wall
Southern California Gas Company | N | LOS ANGELES | WEST COVINA | 2023-12-17 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CARLOS DAVALOS | WEST COVINA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was digging with shovels to install fence post. No USA was called.
Southern California Gas Company | N | LOS ANGELES | WEST COVINA | 2023-03-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 55 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  | 1 |  | I RAMIREZ CORP | SAN FERNANDO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor was boring in fiber optic line and hit a 1 pla svc, mismarked.
Southern California Gas Company | N | LOS ANGELES | WEST COVINA | 2023-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | SABER | PARAMOUNT | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was raising concrete foundation to level the house. The work being performed did not have a USA, and contractor hit our PLA gas service when excavating.
Southern California Gas Company | N | LOS ANGELES | WEST COVINA | 2023-10-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SASCO | FULLERTON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Relocating street light foundation and pierced a 1/2 CTS gas service due to mis-mark.
Southern California Gas Company | N | LOS ANGELES | WEST COVINA | 2023-08-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | JOSE MELENDEZ | POMONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | LOS ANGELES | WEST HILLS | 2023-12-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | LA STRADA PIPELINE | WEST HILLS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Digging to install new water main. DWP struck plastic service line with backhoe. Gas service was accurately marked
Southern California Gas Company | N | LOS ANGELES | WEST HILLS | 2023-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CXC CONTRACTING | THOUSAND OAKS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit our service with a shovel. Gas line was running thru a garage. so we eliminated hazard by doing a over head by-pass outside of garage. No USA
Southern California Gas Company | N | LOS ANGELES | WEST HOLLYWOOD | 2023-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | WESTERN WATER TROUBLE | LOS ANGELES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | contractor struck gas service with backhoe ,
Southern California Gas Company | N | LOS ANGELES | WEST HOLLYWOOD | 2023-09-23 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 119 | 119 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 5 |  | SALMA AMRANI | WEST HOLLYWOOD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor cut into 204 psi 3/4 HP STL service while digging for sewer repair with no USA.
Southern California Gas Company | N | LOS ANGELES | WEST HOLLYWOOD | 2023-04-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | COAST TO COAST PLUMBING AND ROOTER | SHERMAN OAKS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | SCG crew repaired damaged 1 PLA service. Contractor began to dig before the service was located and marked, ticket had not reach legal start time.
Southern California Gas Company | N | LOS ANGELES | WEST HOLLYWOOD | 2023-04-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | SWINERTON | WEST HOLLYWOOD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor hit gas service with excavator
Southern California Gas Company | N | LOS ANGELES | WEST HOLLYWOOD | 2023-09-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | LADWP | LOS ANGELES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | DWP struck gas service with backhoe, service was mark with yellow paint
Southern California Gas Company | N | LOS ANGELES | WEST HOLLYWOOD | 2023-01-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  |  | NA | MSL ELECTRIC, INC. | WEST HOLLYWOOD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | MSL company was excavating with mini-X and struck gas service, fail to pothole existing gas service, gas service was mark in yellow paint
Southern California Gas Company | N | LOS ANGELES | WESTLAKE VILLAGE | 2023-09-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | SILVER LINE | GARDENA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | A 1 PLA stub was damaged by a backhoe when a 3rd party was digging to install a below ground garage driveway.
Southern California Gas Company | N | LOS ANGELES | WESTLAKE VILLAGE | 2023-08-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 75 |  | CUSTOM CONCRETE PROFESSIONALS | CAMARILLO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 1 plastic service with backhoe while removing tree stump. No USA
Southern California Gas Company | N | LOS ANGELES | WESTLAKE VILLAGE | 2023-10-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NATHAN YORK CONSTRUCTION | SIMI VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | USA valid. Contractor hit 1/2 IPS line accurately marked. Damaged with hand tools
Southern California Gas Company | N | LOS ANGELES | WESTLAKE VILLAGE | 2023-01-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | EDISON | WESTLAKE VILLAGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Edison was hand digging when they hit a PLA service.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2023-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | WHITTIER | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor conducting repair work for customer owned houseline at 10732 struck service with hand tools. Contractors i8mmediately departed scene upon arrival of the ETR. Crew Used a 3/4x6 Adams Clamp to make repairs. Aerated area and left no hazardous conditions upon departure. No evacuations., no fire, no news media. Once repairs made customer service conducted restore.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2023-07-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 1.25 | 32 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | HHS COMMUNICATIONS | AZUSA | CA | N | Y | Yes | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was boring in new conduit for Spectrum when their bore came in contact with a steel stub from a previous cut back. USA was called but contractor did not receive a positive response from company locator.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2023-06-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MIGUEL LOPEZ | WHITTIER | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hit service while installing a new sewer line. NO USA was called
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2023-07-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DM&G CONSTRUCTION | IRVINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor working for RMPP damaged our plastic gas service in earth on private property while excavating with a shovel to install a bollard in front of the residential gas meter. There was a valid USA and the marks were good. SCG crew made permanent repairs.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2023-11-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 65 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HHS CONSTRUCTION | ONTARIO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor built a cable box above our facilities and drove a grounding rod into our service.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2023-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 32 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | RAY BUENO | LA HABRA HEIGHTS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner dad hit service while grading for new walking path. NO USA beforehand
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2023-02-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 33 | 33 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | J DE SIGIO | BALDWIN PARK | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Service was pulled by backhoe operator while digging to install new water main.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2023-02-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ADAME COMMUNICATION | ANAHIEM | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor did not have a USA for the location of damage. Crew told contractor that this could have been all avoided if the called for a USA.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2023-07-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ABEL VENEGAS | WHITTIER | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner Abel Venegas had a general contractor working on his driveway with an excavator and in the process of leveling some dirt in the driveway, contractor damaged our 1 plastic service with an excavator. No USA was called.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2023-06-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | WHITTIER | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | homeowner EE digging with hand tools
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2023-10-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ALL RIGHT ELECTRIC INC | FOUNTAIN VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractors hit 1 plastic service with mini excavator while digging to install electrical conduit.
Southern California Gas Company | N | LOS ANGELES | WHITTIER | 2023-09-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | GRAHAM PLUMBING | BREA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractors damaged 1/2 inch CTS service
Southern California Gas Company | N | LOS ANGELES | WILMINGTON | 2023-02-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | WALTON CONSTRUCTION INC | SAN DIMAS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor digging with a Mini-Ex and damaged our 1 PE pipe, tripping the EFV. Sub contractor working off contractor USA, no valid USA. Pipe was previously marked and exposed 6 feet from damage.
Southern California Gas Company | N | LOS ANGELES | WILMINGTON | 2023-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 38 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | MIGUEL GOMEZ | WILMINGTON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged service line while digging a trench for electrical line. In the process of digging with a shovel SoCalGas service line was hit. The homeowner did not have a valid USA ticket.
Southern California Gas Company | N | LOS ANGELES | WILMINGTON | 2023-01-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DANIA URIBE RAYA | WILMINGTON | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging for sprinkler line when they struck our line. There was no USA.
Southern California Gas Company | N | LOS ANGELES | WINNETKA | 2023-10-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  |  | NA | DAVID NIA | PORTER RANCH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging to exposed service. Developer struck plastic line with shovel. Expired USA ticket
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2023-04-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SMG DEMO INC | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | while trenching next to house . contractor hit plastic line with shovel
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2023-09-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MICHAEL DUBKIN | WOODLAND HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging contractor struck plastic line. Crew showed up and made final repairs
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2023-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ACOSTA PIPELINE | WOODLAND HILLS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 3rd party contractor cut through service before verifying that it was gas. Expired USA
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2023-11-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NINJA PLUMBER | CHATSWORTH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA for work being conducted
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2023-07-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ARGELIO PEREZ | WOODLAND HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit line. No USA
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2023-05-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | NA |  | N | N | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No damage to SUOF. | No damage to SUOF. | No | No damage to SUOF. | No damage to SUOF. | while digging to install a tree homeowner struck plastic service line with shovel. crew showed up and stopped service and made permanent repairs. crew found service to be to shallow due to homeowner taking out dirt from over service area. crew opened trenched and lowered service to proper depth and backfilled
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2023-05-24 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 37 | 37 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ELI EZRA | SAN BERNARDINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | there was no leak contractor pulled service line and crew repaired kinked service line
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2023-09-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | INCREDIBLE PLUMBER | NORTHRIDGE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party plumber digging to install water hit our service with clay spade. Contractor failing to expose our line before using pneumatic tools
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2023-07-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SL HOME DESIGN | WOODLAND HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging trench contractor doing work for home owner struck plastic service line with shovel. Didnt have USA.
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2023-02-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | BOAZ HILLEL | WOODLAND HILLS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was digging a trench to install a drain near a 1? service and struck the service with a shovel. SoCalGas crew responded and controlled the release of gas by squeezing the service. The crew then made permanent repairs and placed the line back in service. Customer did not have a valid USA.
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2023-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | JERMAX CONSTRUCTION | SAN FERNANDO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging to install house line, contractor struck plastic service line with shovel.
Southern California Gas Company | N | LOS ANGELES | WOODLAND HILLS | 2023-04-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | JACOB SID | WOODLAND HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | home owner claims that someone broke into property and tried to steal copper line which has cts plastic line inserted. when they broke the coper line it broke gas service. crew stopped gas and did a cut back due to construction still going on
Southern California Gas Company | N | ORANGE | ALISO VIEJO | 2023-10-30 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | PARK WEST | RANCHO SANTA MARGARITA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit 1/2'''' plastic service that feeds backup generator. No USA was called in
Southern California Gas Company | N | ORANGE | ALISO VIEJO | 2023-08-22 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | NA | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor digging without USA hit 2'''' plastic main.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2023-01-31 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MIKE BUBALO CONSTRUCTION | BALDWIN PARK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | contractor digging for city of yorba linda water department hit our 3 main with an excavator.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2023-07-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 1 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | A-1 APACHE PLUMBING INC | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged Riser trying to expose gas service by bar/hand. No USA
Southern California Gas Company | N | ORANGE | ANAHEIM | 2023-10-16 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | VASILJ INC | BALDWIN PARK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor damaged 3/4 inch steel gas service with backhoe. Stub not marked.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2023-10-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MS TRUCKING SERVICE | ORANGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working on house cut service with shovel near the riser.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2023-11-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NEXT CONSTRUCTION | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Electrician digging trench by MSA damaged plastic service with shovel. No USA was called.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2023-07-12 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | NA |  | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was having some was believed to landscaping work done in the front of their yard. In the process ripped out at 3/4 STL service. No active USA and contractor fled scene before our arrival.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2023-04-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1.25 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | A C SPRAGGINS | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor ripped up a 3/4 steel cut back service with a backhoe. Contractor failed to maintain USA marks on prvt property
Southern California Gas Company | N | ORANGE | ANAHEIM | 2023-10-14 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ALFREDO LOPEZ | ANAHEIM | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Private contractor damaged a 1-inch plastic gas main with a shovel while attempting to make repairs on a water line.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2023-01-27 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BOUDREAU PIPELINE CORPORATION | CORONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party Contractor damaged 2 Main with backhoe. No USA.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2023-12-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HOTLINE CONSTRUCTION INC | CORONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor damaged 1 PE service while excavating to install conduit. This was a result of a mis-mark by a company employee.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2023-08-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | SOLEX | LOS ANGELES | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor working for the city of Anaheim dug through 1 PE service in two places with backhoe.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2023-10-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | SOLEX ENERGIES | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1 plastic service was damaged by contractors while digging a trench with an electric jackhammer.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2023-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | RC PRO CONSTRUCTION | ANAHEIM | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged Service with pickaxe while remodeling garage.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2023-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | PROFICIENCY FIRE PROTECTION | TORRANCE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor digging with backhoe and working to install new water hit our 2 plastic svc. Svc was marked correctly.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2023-01-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | AMERICAN WRECKING | SOUTH EL MONTE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor grading for developer struck a cut back service. contractor grading for developer struck a cut back service.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2023-07-14 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SE PIPELINE | SANTA FE SPRINGS | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor struck plastic gas service due to improper potholing technique.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2023-06-13 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | PAULUS ENGINEERING INC | ANAHEIM | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | third party contractor was digging with a backhoe and struck our gas main.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2023-07-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | LINCOLN CONTRUCTION | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor knew where the service was. They covered the marks while digging their trench. They hit the service with a sharp shooter while looking to expose it.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2023-07-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | ANAHEIM | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscaper was removing bushes for homeowner, he did not call USA. Damaged our gas service while excavating roots.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2023-06-06 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ASPLUNDH CONSTRUCTION | BUENA PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | third party contractor was digging and struck plastic main. it was potholed but the operator and spotter forgot are pipe was there.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2023-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ASPLUNDH CONSTRUCTION | BUENA PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor hit our plastic service while hand digging.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2023-05-10 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | VERTEX BUILDERS | LOS ALAMITOS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor digging for drain line hit our gas line while digging
Southern California Gas Company | N | ORANGE | ANAHEIM | 2023-08-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | STRONGARM ENVIRONMENTAL FIELD SERVICES INC | FULLERTON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor digging with a backhoe struck our gas line.
Southern California Gas Company | N | ORANGE | ANAHEIM | 2023-03-08 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 10001 |  |  | NA | CITY OF ANAHEIM WATER | ANAHEIM | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | On 3-8-2023 SoCalGas responded to an incident at 999 S Boone Circle, Anaheim, Ca. The City of Anaheim Public Utilities struck a 4-inch plastic main while excavating with a backhoe resulting in a fire and release of natural gas. SoCalGas crews responded and controlled the gas leak, no USA ticket requested by Anaheim Public Utilities. No injuries or fatalities resulted from this incident This incident was reported to the CPUC when SoCalGas became aware of media coverage.
Southern California Gas Company | N | ORANGE | BREA | 2023-03-23 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 66 |  | GENTRY BROS. INC. | BALDWIN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Cause of incident: Third party damage to underground plastic SoCal Gas facilities during water infrastructure improvement project. Approximately 65 outages occurred, which were restored following permanent repairs to Company facility.
Southern California Gas Company | N | ORANGE | BREA | 2023-09-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  |  | NA | H&M COMMUNICATIONS | PALMDALE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service was marked correctly. Contractor was hand digging when he hit service with sharp shooter.
Southern California Gas Company | N | ORANGE | BREA | 2023-11-07 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | LEGACY B COMMUNICATIONS | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Boring for telecommunications
Southern California Gas Company | N | ORANGE | BREA | 2023-03-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | VIDO SAMARZICH INC | RANCHO CUCAMONGA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service was marked and visible. Crew had exposed steel pipe and they thought it was the gas service. They dug with the backhoe and cut our plastic service in half.
Southern California Gas Company | N | ORANGE | BREA | 2023-03-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | VIDO SAMARZICH INC | RANCHO CUCAMONGA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Vido Samarzich, Inc. was replacing the water main and services at Sievers St. They knew where the service was due to being marked correctly. Marks were visible. Service was completely wrapped with a tree root and they damaged it with their shovel.
Southern California Gas Company | N | ORANGE | BREA | 2023-03-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | VIDO SAMARZICH | RANCHO CUCAMONGA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Crew was working on a water main replacement. They knew where the service was since they had damaged the same service the week before. Crew claims they were hand digging but the pipe was damaged with a backhoe.
Southern California Gas Company | N | ORANGE | BREA | 2023-02-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | VIDO SAMARZICH INC | RANCHO CUCAMONGA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor working for brea water department probed through our gas service.
Southern California Gas Company | N | ORANGE | BREA | 2023-08-11 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 3 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | TEAM FISHEL | SANTA ANA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor struck our 3 plastic main while boring.
Southern California Gas Company | N | ORANGE | BREA | 2023-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 56 |  | SOCALGAS | PICO RIVERA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Plumbing company struck inserted 1/2 CTS service in the process of exposing sewer line needing repair.
Southern California Gas Company | N | ORANGE | BUENA PARK | 2023-08-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CABLECOM | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged 1 service with shovel. USA called. Gas marks were correct.
Southern California Gas Company | N | ORANGE | BUENA PARK | 2023-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | S&S DIRECTIONAL DRILLING | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged 1/2 IPS gas service with shovel.
Southern California Gas Company | N | ORANGE | CITY OF MISSION VIEJO | 2023-06-12 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | FYDAQ COMPANY INC | FULLERTON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor did not notify USA and hit newly installed 2'''' PLA main with backhoe in new housing tract.
Southern California Gas Company | N | ORANGE | CORONA DEL MAR | 2023-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | TE ROBERTS INCORPORATED | IRVINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third Party Contractor Hit Service With Backhoe When Installing Water Main On Street. Etd Marks Were Within The 2Ft Clearance . Crew Repair Service.
Southern California Gas Company | N | ORANGE | CORONA DEL MAR | 2023-03-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | TE ROBERTS INCORPERATED | IRVINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party hit service with backhoe when installing a new water main. USA valid. Locator has picture and video of his marking.
Southern California Gas Company | N | ORANGE | CORONA DEL MAR | 2023-05-31 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | SE PIPELINE | SANTA FE SPRINGS | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Gas company contractor hit existing gas service with accubore while attempting to install the new gas service.
Southern California Gas Company | N | ORANGE | CORONA DEL MAR | 2023-11-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 46 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MODULE LANDSCAPE CONSTRUCTION | IRVINE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1/2 IPS service. USA ticket expired. Contractor hit gas service while digging with shovel in front yard.
Southern California Gas Company | N | ORANGE | CORONA DEL MAR | 2023-12-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 46 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BURKHARD BROTHERS CONSTRUCTION | TUSTIN | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Third party damage
Southern California Gas Company | N | ORANGE | COSTA MESA | 2023-08-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | OC POOL SCAPES | SANTA ANA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. 3rd party hit service when digging to install front pool.
Southern California Gas Company | N | ORANGE | COSTA MESA | 2023-07-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MARZOLA CONSTRUCTION CO INC | LA MIRADA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit plastic service line with backhoe while excavating in new business construction development. Did have valid USA ticket. Marks were within 24 of damage. Contractor failed to maintain marks during construction.
Southern California Gas Company | N | ORANGE | COSTA MESA | 2023-12-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CANELLO CONSTRUCTION | LAGUNA NIGUEL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | NA
Southern California Gas Company | N | ORANGE | COTO DE CAZA | 2023-09-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SOCAL CONCEPTS | IRVINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor hit 1/2'''' plastic service while exposing. USA was called in and marks were accurate
Southern California Gas Company | N | ORANGE | CYPRESS | 2023-06-27 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 1 | 42 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | CYPRESS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged gas service when they installed footing. No USA.
Southern California Gas Company | N | ORANGE | CYPRESS | 2023-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CALIMINGO POOLS | NEWPORT BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1/2 CTS gas service with shovel while trenching for pool line. No USA.
Southern California Gas Company | N | ORANGE | DANA POINT | 2023-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | PACIFIC COAST LANDSCAPING | FULLERTON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit 1/2'''' pla service with shovel. No USA
Southern California Gas Company | N | ORANGE | DANA POINT | 2023-11-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | EMPIRE PIPELINE | CARLSBAD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party damaged 1/2 CTS service with excavator while digging trench. Damage was a result of company locator error.
Southern California Gas Company | N | ORANGE | DANA POINT | 2023-12-14 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 32 |  | CONSTRU ONE | ONTARIO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor failed to hand expose per USA policy.
Southern California Gas Company | N | ORANGE | DANA POINT | 2023-08-16 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 6 |  | NPL | BREA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | NPL hit plastic service with shovel while hand exposing
Southern California Gas Company | N | ORANGE | DANA POINT | 2023-07-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MARQUAND CONTRACTING CORP | IRVINE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit plastic service when trenching for drain . No USA
Southern California Gas Company | N | ORANGE | DANA POINT | 2023-02-21 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | SE PIPELINE | SANTA FE SPRINGS | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractors for DIMP job cut into 1/2in plastic service with hacksaw that was in 2in plastic casing
Southern California Gas Company | N | ORANGE | DANA POINT | 2023-03-20 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | Z S W INC | DANA POINT | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 2 plastic main. Made temporary repairs. Came back 2 day later and made permeant repairs to the 2 main.
Southern California Gas Company | N | ORANGE | DANA POINT | 2023-09-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 5 |  | CCL CONTRACTING INC | ESCONDIDO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor did not pothole over our 2'''' PLA gas main, and hit our line while digging.
Southern California Gas Company | N | ORANGE | FOUNTAIN VALLEY | 2023-08-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | OPTIMA CONSTRUCTION | COSTA MESA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Updated from drainage to fencing. No USA contractor hit plastic service
Southern California Gas Company | N | ORANGE | FOUNTAIN VALLEY | 2023-03-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | VCI BUILDS | FOUNTAIN VALLEY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Damaged 1/2 PLA service, Expired USA, correctly marked. Damaged by shovel.
Southern California Gas Company | N | ORANGE | FOUNTAIN VALLEY | 2023-12-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GARDEN PROS | ORANGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1 IPS gas service with rebar. No USA
Southern California Gas Company | N | ORANGE | FOUNTAIN VALLEY | 2023-09-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NA | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit 1/2'''' plastic service. Failed to notify USA.
Southern California Gas Company | N | ORANGE | FOUNTAIN VALLEY | 2023-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | RAY''S CONCRETE SYSTEM | ORANGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | OHS crew arrived to find 3rd party contractor was digging for sewer extension with a trenching machine. Contractor did not call USA and hit our svc causing broken and blowing.
Southern California Gas Company | N | ORANGE | FOUNTAIN VALLEY | 2023-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 44 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NEXT CONSTRUCTION | WESTMINSTER | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contactors were digging for a plumbing issue and hit 1/2-inch plastic service with a shovel. No USA was called.
Southern California Gas Company | N | ORANGE | FOUNTAIN VALLEY | 2023-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | JP HAULING | SANTA ANA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1/2 IPS service with backhoe. No USA
Southern California Gas Company | N | ORANGE | FULLERTON | 2023-04-12 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 55 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | FULLERTON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor digging for repairs and hit our gas svc.
Southern California Gas Company | N | ORANGE | FULLERTON | 2023-07-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | LUCAS BUILDERS INC | LA HABRA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor exposed old steel pipe and assumed that was the gas line. Markings were accurate.
Southern California Gas Company | N | ORANGE | FULLERTON | 2023-06-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PR CONSTRUCTION INC | ORANGE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | contractor digging struck our gas line while using hand tools.
Southern California Gas Company | N | ORANGE | FULLERTON | 2023-12-01 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 4 |  | BIG BEN ENGINEERING | IRVINE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Facilities mismarked
Southern California Gas Company | N | ORANGE | FULLERTON | 2023-04-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MARTINEZ FIRE PROTECTION | SAN BERNARDINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit gas service, crew pinched line and made repairs.
Southern California Gas Company | N | ORANGE | FULLERTON | 2023-06-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | GAW CONTRACTING | FULLERTON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Location was previously marked under separate contractors expired USA ticket. Contractor assumed they could piggyback off of GC''s USA ticket. After nicking 1/2 PLA service with shovel, contractor cut and folded back service.
Southern California Gas Company | N | ORANGE | FULLERTON | 2023-11-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | KB CONSTRUCTION | FULLERTON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor dig in with shovel
Southern California Gas Company | N | ORANGE | FULLERTON | 2023-03-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 20 |  | BIG BEN ENGINEERING | IRVINE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor working under valid USA ticket to install water main struck and damaged unmarked 1 plastic service. No record of service on GIS or Epoch.
Southern California Gas Company | N | ORANGE | FULLERTON | 2023-04-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GARRY IMANSE | FULLERTON | CA | N | Y | Yes | Excavation occurred on private property by a non-contractor. | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner struck 1/2 plastic service while excavating for new sewer install. USA expired April 10th. Delineation on sidewalk, unable to see marks in backyard due to spoil. Company crew controlled gas & made perm repairs.
Southern California Gas Company | N | ORANGE | FULLERTON | 2023-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | BUTLER AMERICA TELECOM | FULLERTON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor digging for conduit hit our gasline with a shovel.
Southern California Gas Company | N | ORANGE | FULLERTON | 2023-01-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | LAT LONG INFRASTRUCTURE | AUSTIN | TX | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | contractor installing casing or fiber optics struck our gas line while hand digging.
Southern California Gas Company | N | ORANGE | FULLERTON | 2023-09-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ARIZONA PIPELINE | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor struck 1/2 service while hand digging.
Southern California Gas Company | N | ORANGE | FULLERTON | 2023-02-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | PRAMIRA INC | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | marks accurate. Contractor failed to pothole
Southern California Gas Company | N | ORANGE | FULLERTON | 2023-03-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | BIG BEN ENGINEERING | IRVINE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | contractor replacing water main struck our plastic service while digging with a backhoe.
Southern California Gas Company | N | ORANGE | FULLERTON | 2023-08-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 6 |  | BIG BEN ENGINEERING | FULLERTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | They damaged our 2 plastic gas line with their backhoe.
Southern California Gas Company | N | ORANGE | FULLERTON | 2023-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 55 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LOMA VISTA MEMORIAL PARK | FULLERTON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | OHS crew arrived to find broken and blowing 2 PLA svc. 3rd party contractor was digging with backhoe for burial site and hit our svc.
Southern California Gas Company | N | ORANGE | FULLERTON | 2023-09-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | BIG BEN ENGINEERING | IRVINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was hand digging over service mark when he hit service.
Southern California Gas Company | N | ORANGE | FULLERTON | 2023-09-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | BIG BEN ENGINEERING | IRVINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | SVC was marked and visible. Contractor was hand digging looking for the service when he damaged it.
Southern California Gas Company | N | ORANGE | FULLERTON | 2023-09-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | BIG BEN ENGINEERING | IRVINE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | ETD wrote to pothole service because he could'' not locate. Contractor did not pothole.
Southern California Gas Company | N | ORANGE | GARDEN GROVE | 2023-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 42 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CITY OF GARDEN GROVE PUBLIC WORKS | GARDEN GROVE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor damaged 1/2 IPS gas service with sharpshooter. USA Called. Service not marked. Locator will have a note to file and will have a coaching meeting 7/14.
Southern California Gas Company | N | ORANGE | GARDEN GROVE | 2023-07-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ANCHOR BUILDINGS | GARDEN GROVE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor struck 1/2 plastic service with shovel while excavating new sewer line. No valid USA . Company crew controlled gas & made perm repairs.
Southern California Gas Company | N | ORANGE | GARDEN GROVE | 2023-11-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ULTIMATE KONSTRUCTION | GARDEN GROVE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 1 plastic service while trenching.
Southern California Gas Company | N | ORANGE | GARDEN GROVE | 2023-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 44 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 5 |  | SULLY MILLER CONTRACTING CO | BREA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractors for the city of garden grove damaged a 1/2-inch ips service with a shovel. USA was called and service was marked correctly.
Southern California Gas Company | N | ORANGE | GARDEN GROVE | 2023-09-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RJ NOBLE | ORANGE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged 1/2 CTS gas service with pulverizer. 3rd Party contractor said they had seen the gas service but still hit it with a pulverizer by accident. Gas marks are good.
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2023-05-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 42 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ORYAN CONSTRUCTION | HUNTINGTON BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Party contractor damaged 1/2 CTS gas service with backhoe. USA was called but failed to hand dig the service.
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2023-09-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | CSL BUILDERS | BUENA PARK | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged 1/2 CTS gas service with a shovel trying to pothole. USA good.
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2023-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | KAG CONSTRUCTION | FULLERTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Party contractor damaged 1/2 CTS gas service with a shovel. Marked correctly.
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2023-08-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | D''AMBRA CONSTRUCTION | HUNTINGTON BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor dug into 1 plastic service with shovel while digging trench for water line
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2023-04-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 42 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | TY NGO | HUNTINGTON BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party Contractor damaged 1/2 IPS with backhoe. No USA
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2023-03-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | AC SPRAGGINS | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Party contractor damaged 1 gas service with a backhoe. Contractor failed to verify gas service before using the backhoe.
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2023-10-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | LINDAHL INC | HARBOR CITY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1/2 CTS gas service with a shovel. No USA
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2023-07-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 42 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TTS ENGINEERING | STANTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged 1/2 IPS gas service with a backhoe. 3rd party contractor failed to hand expose 1/2 IPS gas service.
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2023-11-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MARK CABELLERO POOLS AND SPA INC | HUNTINGTON BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1/2 IPS service with shovel. No USA
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2023-08-04 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ARIZONA PIPELINE | CORONA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | NA
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2023-10-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | DELTA PIPELINE INC | LONG BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged 1 IPS service with backhoe
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2023-08-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CAL-WEST NURSERIES INC | NORCO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged gas service with mini backhoe. No USA.
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2023-05-22 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 1 | 42 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GREENLEAF ENGINEERING | HUNTINGTON BEACH | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party contractor Damaged 1/2IPS gas service with a shovel. Hand digging the service. USA ticket was good just a mistake trying to hand dig.
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2023-05-09 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | WE ONEAL | EL SEGUNDO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Party contractor digging for new parking lot damaged 2 plastic service with a backhoe. 3rd Party Contractor failed to pothole. USA was called and marks were accurate.
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2023-05-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 44 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ALPHA STRUCTURAL | YORBA LINDA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit plastic service while digging to place a drain. USA was called and service was marked correctly.
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2023-07-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 42 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | OLTMANS CONSTRUCTION | VICTORVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged 2 gas main with backhoe. Main was marked correctly 3rd party contractor failed to hand expose 2 gas main.
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2023-09-11 | Operator excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ARIZONA PIPELINE | RIALTO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Arizona Pipeline was doing a service replacement for the Gas Company and struck an old line while exposing it. USA was valid.
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2023-03-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | ARIZONA PIPELINE COMPANY | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged 1/2 PLA service, valid USA. Marked correctly, 3rd Party contractor digging over plastic with Backhoe.
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2023-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MAKRAM YOUSSEF | HUNTINGTON BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Party Contractor damaged 1/2 CTS gas service with a shovel. USA was called and marks were marked correctly.
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2023-04-17 | Third party excavation damage | Main | Steel | Grader/Scraper | 3 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  |  | NA | PAVEMENT RECYCLING | JURUPA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Party contractor damaged 3 steel main with pulverizer while grading. Didn''t pothole 3 steel main.
Southern California Gas Company | N | ORANGE | HUNTINGTON BEACH | 2023-04-18 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 44 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ORION CONTRUCTION | VISTA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Orion Construction was digging for the City of Huntington Beach. Doing some water pipeline work. The job was USA and the Gas line was marked correctly.
Southern California Gas Company | N | ORANGE | IRVINE | 2023-02-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CAL WEST UNDERGROUND INC | NORCO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit 1/2 ips service stub with a shovel. No USA
Southern California Gas Company | N | ORANGE | IRVINE | 2023-12-18 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SHOFFEITT PIPLINE | IRVINE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractors damaged 2 plastic main. At the end of main with backhoe.
Southern California Gas Company | N | ORANGE | IRVINE | 2023-09-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | KDC CONSTRUCTION | ORANGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party Contactor damaged service in joint trench while trying to expose electrical. No USA
Southern California Gas Company | N | ORANGE | IRVINE | 2023-07-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MARK COMPANY | ORANGE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit plastic service when trenching.
Southern California Gas Company | N | ORANGE | IRVINE | 2023-04-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | CABLECOM | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor hit 1 inch plastic service with bore while boring cable conduit underneath service.
Southern California Gas Company | N | ORANGE | IRVINE | 2023-04-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SANA ANA CONCRETE | RIVERSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | New housing tract, developer digging for foundations and hit 1 inch pla svc with EFV with backhoe.
Southern California Gas Company | N | ORANGE | IRVINE | 2023-05-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LENNAR HOMES | IRVINE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging by riser without USA and struck 1 inch pla service. Permanent repairs made same day by crew
Southern California Gas Company | N | ORANGE | IRVINE | 2023-12-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LEATHERWOOD CONSTRUCTION | FOUNTIAN VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | NA
Southern California Gas Company | N | ORANGE | IRVINE | 2023-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | EVELIO MARTINEZ MARQUEZ | CORONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Outside force damage. Tree roots wrapped around gas service. When homeowner removed the tree that''s when the roots pulled the gas service. No USA
Southern California Gas Company | N | ORANGE | IRVINE | 2023-12-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | SOCAL EDISON | SANTA ANA | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Damaged 1/2 PLA service with shovel. Edison crew damaged line while digging for short & did not call USA
Southern California Gas Company | N | ORANGE | IRVINE | 2023-09-13 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 6 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | UTILITY PACIFIC INSTALLATION | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor digging for land developer damaged punch tee cap on main.
Southern California Gas Company | N | ORANGE | LA HABRA | 2023-07-19 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 4 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 13540 |  |  | NA | CAL PROMAX ENGINEERING | PLACENTIA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor was augering to install a pole.
Southern California Gas Company | N | ORANGE | LA HABRA | 2023-07-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | JR INVESTMENT LP | ANAHEIM | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was excavating on the front driveway and struck 1/2 plastic service with backhoe. No valid USA ticket.
Southern California Gas Company | N | ORANGE | LADERA RANCH | 2023-09-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | JOHN ERTZ INC | LAKE HAVASU CITY | AZ | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 3rd party contractor hit 1/2" plastic service while hand exposing. USA was notified
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2023-07-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MCKEOWN PLUMBING | LAGUNA BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1/2 plastic service with a shovel while repairing sewer line. USA ticket is valid. No delineation found. Locator accurately marked service with flags.
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2023-04-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | RDM | COSTA MESA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit 1/2'''' CTS service. No USA, no new markings from other utilities.
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2023-04-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RDM | COSTA MESA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 1/2 inch CTS service with hand tools. NO USA
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2023-11-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SULLY MILLER | BREA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Broke nipple off stopcock with his backhoe.
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2023-11-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | DB ELECTRIC | EASTVALE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor dug before ticket was valid and also did not hand expose our gas line.
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2023-10-27 | Third party excavation damage | Main | Steel | Miscellaneous/Other | 2 | 50 | 44 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | LOZANOS CONSTRUCTION | LAKE FOREST | CA | N | Y | Yes | Yes | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2023-07-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | DENNIS PISZKIEWIC | LAGUNA BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA 1/2 CTS service hit by stake
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2023-08-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | ROSS WAITE CONSTRUCTION | SAN CLEMENTE | CA | N | Y | Yes | No | Yes | No | No | Yes | Yes | Third party contractor struck gas service while excavating by building. Failed to maintain marks. USA Ticket was expired.
Southern California Gas Company | N | ORANGE | LAGUNA BEACH | 2023-11-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ASPLUNDH CONSTRUCTION | BUENA PARK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor hit 1/2'''' plastic service. Service mismarked
Southern California Gas Company | N | ORANGE | LAGUNA HILLS | 2023-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JOHN WITCZAK | LAGUNA HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit 1/2'''' service with shovel. permanent repairs made by crew.
Southern California Gas Company | N | ORANGE | LAGUNA HILLS | 2023-08-22 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 6 |  | HUERTA CONSTRUCTION | BUENA PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor hit 1'''' plastic main with shovel while hand digging. USA was called and marks were accurate
Southern California Gas Company | N | ORANGE | LAGUNA HILLS | 2023-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SCC STRUCTURAL CONCRETE | LAKE ELSINORE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor struck 1/2 plastic service with mini excavator while trenching for a fence. USA was notified. Verified marks were accurate.
Southern California Gas Company | N | ORANGE | LAGUNA NIGUEL | 2023-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | TELA SAMPO | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit 1/2 CTS service to 24491 Los Serrano Dr while digging with post digger to install fence post. No USA.
Southern California Gas Company | N | ORANGE | LAGUNA NIGUEL | 2023-12-19 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 30001 |  | 1 |  | R3 CONTRACTORS | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | No | NA
Southern California Gas Company | N | ORANGE | LAGUNA NIGUEL | 2023-05-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | JC GRADING | LAKE ELSINORE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Third party contractor damaged 1/2IPS svc while trenching for electrical conduit. USA not valid. Contractor hit service with a bobcat.
Southern California Gas Company | N | ORANGE | LAKE FOREST | 2023-01-12 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | ARIZONA PIPELINE COMPANY | CORONA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | DIMP Project. 2nd Party Contractor hit 1/2in plastic service with shovel while potholing. SCG ticket, Contractor''s responsibility to locate everything SCG related.
Southern California Gas Company | N | ORANGE | LAKE FOREST | 2023-06-07 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ARIZONA PIPELINE COMPANY | CORONA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was digging a pick up hole to install the new gas service when a laborer hit the plastic service with a shovel. Visible marks are within 2 inch
Southern California Gas Company | N | ORANGE | LAKE FOREST | 2023-11-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SCOTT BALDERAS | LAKE FOREST | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner planted tree and hit 1'''' PLA service with tree stake by hammering it into the ground. No USA called in
Southern California Gas Company | N | ORANGE | LOS ALAMITOS | 2023-07-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 1 | 44 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | VASILJ INC | BALDWIN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor hit a plastic service while hand digging to find the service. USA was valid.
Southern California Gas Company | N | ORANGE | MISSION VIEJO | 2023-08-22 | Operator excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | SE PIPELINE | SANTA FE SPRINGS | CA | Y | Y | Yes | No | Yes | Yes | No | Yes | Yes | NA
Southern California Gas Company | N | ORANGE | MISSION VIEJO | 2023-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SEVERSON PLUMBING | IRVINE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit 1/2'''' plastic service. Failed to notify USA
Southern California Gas Company | N | ORANGE | MISSION VIEJO | 2023-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ROBERT SMITH | MISSION VIEJO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | ETD did not mark service per his notes he spoke with homeowner and cust. potholed and found the service. homeowner hit service in area he did not pothole. USA was vaild . Spoke with MVN about accident.
Southern California Gas Company | N | ORANGE | MISSION VIEJO | 2023-08-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | EC CONSTRUCTORS | LAKESIDE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Crew repaired damaged PLA service, by way of pinching service and altering the PLA service.
Southern California Gas Company | N | ORANGE | MISSION VIEJO | 2023-06-13 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SE PIPELINE | SANTA FE SPRINGS | CA | Y | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | DIMP Job - company contractor bored into 1/2'''' plastic service while replacing service. Fire Department evacuated 1 resident from 1 home. Evacuations lifted after service was pinched.
Southern California Gas Company | N | ORANGE | MISSION VIEJO | 2023-08-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | OC BUILDING GROUP | SANTA ANA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor hit service with shovel while excavating near building. No current USA ticket on file.
Southern California Gas Company | N | ORANGE | MISSION VIEJO | 2023-10-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 47 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | JA HOME IMPROVEMENT INC | IRVINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor dug down to expose gas facilities, but hit our 1/2 IPS service below a root. Valid USA and visible correct marks.
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2023-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | META CONSTRUCTION CO INC | SANTA ANA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1/2 IPS gas service with shovel. No USA
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2023-04-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | DBC CONSULTING | NEWPORT BEACH | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | USA not valid expired in OCT of 2022. 3rd Party Contractor hit plastic service when excavating property. Teichert abandoned 3 services at location. Working with damage prevention on this incident.
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2023-02-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 44 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ASPLUNDH CONSTRUCTION CORPORATION | ANAHEIM | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor damaged 1/2 CTS service while trenching. Gas marks were only by measurement.
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2023-02-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 44 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ASPLUNDH CONSTRUCTION | ANAHEIM | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd Party damaged 1/2 CTS service while trenching. Gas mark were measurement only.
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2023-08-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 55 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | AMERICAN WRECKING INC | SOUTH EL MONTE | CA | N | Y | Yes | Yes | No | Yes | No | No | No | OHS crew arrived to find 3rd party contractor was digging with backhoe to cut and cap a sewer and hit our 2 unmarked svc that had been cut back previously, causing broken and blowing. USA was called in, but no svc info to mark.
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2023-05-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | REID VITARELLI | NEWPORT BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner''s son was digging for Edison and hit the gas service with a shovel. No USA
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2023-10-02 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | HOTLINE CONSTRUCTION | CORONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractors were digging to place new conduit in trench when they damaged a 2 PLA main with a backhoe.
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2023-05-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | EPCO PLUMBING | HUNTINGTON BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit service. found damaged .5 ips service that was hit with shovel while trenching for water line. No USA
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2023-05-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | STEVEN THOMPSON | NEWPORT BEACH | CA | N | Y | Yes | No | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1 plastic service with pickaxe trenching for block wall. No USA
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2023-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | HOTLINE CONSTRUCTION | BRENTWOOD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged 1/2 PLA service with backhoe. USA valid & marked correctly. Damaged with excavator. Did not hand expose.
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2023-09-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOTLINE CONSTRUCTION | BRENTWOOD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Third party contractor was trenching to install power conduit with valid USA, pot-holed marks from locator and did not find service. Contractor failed to call for re-marks and proceeded to dig with backhoe and damaged 1/2 service.
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2023-11-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 46 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | STREAMLINE CONSTRUCTION | MISSION VIEJO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1/2 service. No USA. third party contractor damaged service with a shovel while trenching
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2023-09-25 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 46 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TE ROBERTS | IRVINE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Third party hit stub when excavating to install a new water main for the city of Newport Beach.
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2023-04-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MEADOW LANDSCAPE | COSTA MESA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 1/2 pla service, did not notify USA prior to excavating.
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2023-07-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | HOTLINE CONSTRUCTION | CORONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Third party doing work for the City of Newport Beach hit unmark service with backhoe when trenching for water.
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2023-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 36 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | SAUL AVILA | LAKE ELSINORE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Developer open trenching with mini excavator damaged 1/2 ips service line
Southern California Gas Company | N | ORANGE | NEWPORT BEACH | 2023-10-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CASTLETON DEVELOPMENT AND MANAGEMENT INC | ANAHEIM | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA 3rd contactor hit plastic service with shovel.
Southern California Gas Company | N | ORANGE | NEWPORT COAST | 2023-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 46 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | POOL PROZ | TRABUCO CANYON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged 1/2'''' IPS service with electric clay spade while trying to expose service. USA was called and markings were accurate
Southern California Gas Company | N | ORANGE | ORANGE | 2023-10-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | VCI CONSTRUCTION LLC | UPLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | While digging with an excavator, VCI Construction damaged a mismarked 2 plastic gas main.
Southern California Gas Company | N | ORANGE | ORANGE | 2023-11-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | AG VINYL FENCING INC | ANAHEIM | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor installing a new fence dug through 1/2 IPS service with post hole digger.
Southern California Gas Company | N | ORANGE | ORANGE | 2023-02-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | N&H CONSTRUCTION | GARDEN GROVE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | was not able to go to this incident since I was at the 2 damage that was going on at the same time.
Southern California Gas Company | N | ORANGE | ORANGE | 2023-02-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | PARTNERS PLUMBING INC | LAKE FOREST | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 Ips Pla Service Hit With Shovel By Contractor While Doing Sewer Work With No Usa
Southern California Gas Company | N | ORANGE | PLACENTIA | 2023-10-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | PACIFIC COAST LANDSCAPING | FULLERTON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Installing a drain line. They did not call USA. They damaged the plastic service with a shovel.
Southern California Gas Company | N | ORANGE | PLACENTIA | 2023-10-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ARIZONA PIPELINE | CORONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged service close to riser while potholing. Marks were a bit off according to LCT.
Southern California Gas Company | N | ORANGE | SAN CLEMENTE | 2023-04-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 1 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CITY OF SAN CLEMENTE | SAN CLEMENTE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Water company was repairing water leak and hit 1inch plastic service with a probe. Ticket was not valid yet but marks were accurate anyway.
Southern California Gas Company | N | ORANGE | SAN CLEMENTE | 2023-09-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | LOUIE CAMACHO | SAN JUAN CAPISTRANO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor hit 1/2'''' plastic service while hand exposing. USA called and service markings were accurate
Southern California Gas Company | N | ORANGE | SAN CLEMENTE | 2023-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RICARDO LUNA LANDSCAPE | SAN CLEMENTE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | ORANGE | SAN CLEMENTE | 2023-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NA | SAN CLEMENTE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party replacing a drain damaged gas line with shovel by meter
Southern California Gas Company | N | ORANGE | SAN CLEMENTE | 2023-07-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CH ANDERSON CONSTRUCTION | SAN CLEMENTE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor trenching for a drain damaged 1/2'''' plastic service with a shovel. No USA.
Southern California Gas Company | N | ORANGE | SAN CLEMENTE | 2023-09-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SHORELINE GENERAL CONTRACTORS | SAN CLEMENTE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor Damaged 1/2 IPS gas service with shovel. No USA.
Southern California Gas Company | N | ORANGE | SAN CLEMENTE | 2023-09-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | K ANDERSON | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit 1/2'''' plastic service. Did not notify USA
Southern California Gas Company | N | ORANGE | SAN CLEMENTE | 2023-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | COSTAL COM LLC | LA HABRA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | OHS crew arrived to find 3rd party contractor boring to install communication conduits and damaged a 1/2 plastic svc with bore. USA was called and marks were correct.
Southern California Gas Company | N | ORANGE | SAN CLEMENTE | 2023-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ZSW CONSTRUCTION | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit 1/2'''' plastic service with shovel while hand exposing. Contractor did not have their own USA ticket
Southern California Gas Company | N | ORANGE | SAN CLEMENTE | 2023-04-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SALVADOR | SANTA ANA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 3rd party contractor working 619 Calle Hildalgo was digging to install electrical and damaged our service with a shovel. LCT Hau Tsan and his CT arrived, controlled the gas and made repairs. They cut out the damaged section of 1/2 cts and fused in the new section.
Southern California Gas Company | N | ORANGE | SAN CLEMENTE | 2023-10-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TEAM FISHEL | SANTA ANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor bored into exposed 1/2'''' plastic service.
Southern California Gas Company | N | ORANGE | SAN JUAN CAPISTRANO | 2023-06-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | AVL CONCRETE BREAKING | FONTANA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit 1/2 plastic service with a shovel while installing pavers. No USA
Southern California Gas Company | N | ORANGE | SAN JUAN CAPISTRANO | 2023-01-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SANTA MARGARITA WATER DISTRICT | RANCHO SANTA MARGARITA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Santa Margarita Water District hit 1/2 ips service after already exposing it. It was damaged while they were replacing a water main.
Southern California Gas Company | N | ORANGE | SAN JUAN CAPISTRANO | 2023-12-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | KENNEY MIKE LANDSCAPE CONSTRUCTION | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 1/2'''' service while working on plumbing.
Southern California Gas Company | N | ORANGE | SAN JUAN CAPISTRANO | 2023-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | SANTA ANA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1 service with an auger. No USA. No Customer of record on file. Unable to obtain owner information.
Southern California Gas Company | N | ORANGE | SAN JUAN CAPISTRANO | 2023-01-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | L&S CONSTRUCTION | ORANGE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor struck 1/2 plastic service with a probe. USA properly marked and visible.
Southern California Gas Company | N | ORANGE | SAN JUAN CAPISTRANO | 2023-04-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | T 9 ENTERPRISES INC | LA VERNE | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor failed to delineate proposed work area for locator, and then hit 2 pla service
Southern California Gas Company | N | ORANGE | SAN JUAN CAPISTRANO | 2023-02-01 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | FLAMINGO CONST INC | STUDIO CITY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor trenching for water installation, hit newly installed 2in plastic main. 3rd party contractor later admitted they did not have a USA ticket for the area they were digging
Southern California Gas Company | N | ORANGE | SAN JUAN CAPISTRANO | 2023-12-07 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | EXTREME CONCRETE | COMMERCE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Backhoe hooked and damaged 2 plastic main while trenching for footing.
Southern California Gas Company | N | ORANGE | SAN JUAN CAPISTRANO | 2023-10-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | ECHO HOMES INC | IRVINE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1/2 IPS gas service with shovel. No USA.
Southern California Gas Company | N | ORANGE | SAN JUAN CAPISTRANO | 2023-01-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | ELIAS MATTA | SAN JUAN CAPISTRANO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was digging with a shovel without a USA ticket and hit 1/2in pla service.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2023-07-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | PAULUS ENGINEERING INC | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor hit 1/2'''' CTS service with shovel while hand exposing
Southern California Gas Company | N | ORANGE | SANTA ANA | 2023-03-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MARK COMPANY | ORANGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was grading earth with backhoe and sliced through the gas service.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2023-02-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 44 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | AMERICAN WIRELESS CONSTRUCTION INC | STANTON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 1/2 Ips un-able to locate was damaged by mini excavator. Crew maid repairs and tried best to locate service. No info in service history or GIS. Will work with planner to update service history.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2023-12-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | Third party damage stuck outside delineation
Southern California Gas Company | N | ORANGE | SANTA ANA | 2023-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SHAHRAM BEHNIA | SANTA ANA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged 1/2 IPS service with shovel while digging for drainage install.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2023-08-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LEAK PRO PLUMBING | RIVERSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1/2 service damaged with clay spade on dig-in. Valid USA & marked correctly with paint.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2023-09-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | EVERSINCE | SANTA FE SPRINGS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | OHS crew arrived to find broken and blowing due to 3rd party contractor digging to install fencing post.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2023-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ALVARO GONZALEZ | SANTA ANA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1/2 cts service with shovel, tied back by contractor, No USA.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2023-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | APC POOLS | CORONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1/2 IPS gas service with backhoe. No USA.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2023-12-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | CARLOS APARICIO | SANTA ANA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Struck line with shovel while excavating to install new sewer line. No USA on file
Southern California Gas Company | N | ORANGE | SANTA ANA | 2023-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | BECKER PIPELINE | RIVERSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Digging over 1/2 PLA service with backhoe & damaged service. USA valid & service marked correctly.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2023-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | FELIX TALAVERA | SANTA ANA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | OHS crew arrived to find a broken and blowing svc due to home owner digging with shovel without USA.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2023-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | UNLIMITED HAULING | ORANGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Santa Ana crew arrived to find a 3rd party contractor installing conduit for electrical had hit our service causing broken and blowing. No USA called.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2023-09-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BLU LAKE CONSTRUCTION CO | IRVINE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer service was called and upon arrival they found a leaking exposed service. No USA
Southern California Gas Company | N | ORANGE | SANTA ANA | 2023-08-16 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DYNAELECTRIC | LOS ALAMITOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor hit main with backhoe. Gas marking were spot on.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2023-10-31 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | VALDEZ UNDERGROUND | BLOOMINGTON | CA | N | Y | Yes | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 3 new business main with excavator while digging trench. 3rd party contractor dug prior to renewing USA ticket.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2023-12-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 1.25 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | BRITO FIRE PROTECTION INC | WEST COVINA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor utilizing hand tool-sawzall cut 1 1/4 line. No USA.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2023-04-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | FERREIRA LOST | RANCHO CUCAMONGA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Party Contractor was digging to install water. We correctly marked our service, but the contractor found a 1 service while pot holing and assumed that it was our service and proceeded to dig with a backhoe. The contractors hit and damaged our 2 plastic service. Our OHS crew out of Downey Arrived and controlled the gas. The crew made repairs using a stick of 2, 1 fused coupling and 1 electrofusion.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2023-05-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | PABLOS PLUMBING | RIVERSIDE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 1/2 IPS service hit by backhoe. service was appx 10 feet away from mark on asphalt. LCT hooked up to bare wire and could not get any kind of signal and measurement were off on service history.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2023-08-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ACE LOW VOLTAGE | ANAHEIM | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | NA
Southern California Gas Company | N | ORANGE | SANTA ANA | 2023-10-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | RJ ELECTRIC | RANCHO CUCAMONGA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor hit plastic service due to mis-marks.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2023-02-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | FERREIRA COASTAL CONSTRUCTION CO | RANCHO CUCAMONGA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Party contractor hit 1 gas service with a backhoe. Had a valid USA but 3rd party contractor failed to hand dig and expose 1service.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2023-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 36 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ANCHOR BUILDER | GARDEN GROVE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 CTS damaged by backhoe while trenching for sewer
Southern California Gas Company | N | ORANGE | SANTA ANA | 2023-08-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MANUEL JUAREZ | EL MONTE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While digging in area and removing roots 1/2 plastic service was damaged. No USA was called in prior to digging.
Southern California Gas Company | N | ORANGE | SANTA ANA | 2023-08-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MANUEL JUAREZ | EL MONTE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | People working for homeowner were digging for sewer repair. The gas service was exposed due to earlier damage. Person digging said he was trying to clean around gas service when he hit the service.
Southern California Gas Company | N | ORANGE | SEAL BEACH | 2023-06-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PRECISION DEMOLITION | HUNTINGTON BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1/2 PLA service, damaged with backhoe while removing footing for mobile home unit. No USA
Southern California Gas Company | N | ORANGE | SEAL BEACH | 2023-10-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | COASTLINE MASONRY INC | LONG BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged 1/2 IPS gas service and branched service with shovel.
Southern California Gas Company | N | ORANGE | SILVERADO | 2023-11-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Probing Device | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | BISTLINE ENGINEERING INC | SAN CLEMENTE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor hit 1'''' plastic service with probe while potholing for line
Southern California Gas Company | N | ORANGE | STANTON | 2023-04-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 55 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 7 |  | HARTLEY LANDSCAPE AND CONSTRUCTION | BREA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor hit svc line
Southern California Gas Company | N | ORANGE | STANTON | 2023-02-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | BENS ASPHALT | RIVERSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party contractor damaged 1/2 IPS Gas Service with a shovel while they were trenching.
Southern California Gas Company | N | ORANGE | TRABUCO CANYON | 2023-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SOCAL CONCEPTS | IRVINE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | OHS crew arrived to find that a 3rd party contractor had hit our 1/2 pla svc with a shovel while digging to reroute the sewer.
Southern California Gas Company | N | ORANGE | TRABUCO CANYON | 2023-10-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | FERREIRA CONSTRUCTION CO | RANCHO CUCAMONGA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 3rd party contractor hit 1/2'''' plastic service while hand exposing. USA was called in and marks were accurate
Southern California Gas Company | N | ORANGE | TRABUCO CANYON | 2023-10-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MOON VALLEY NURSERIES | IRVINE | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit 1/2'''' plastic service while planting tree.
Southern California Gas Company | N | ORANGE | TUSTIN | 2023-10-10 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 0.75 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CAMARILLO DRILLING | NUEVO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | 3rd party hit service when boring for telecommunications. Struck outside of delineations.
Southern California Gas Company | N | ORANGE | TUSTIN | 2023-07-05 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 44 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 37 |  | CAMARILLO DRILLING | NUEVO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor hit 2 plastic main. Contractor did not pothole marks and verify main depth. USA marks were correct.
Southern California Gas Company | N | ORANGE | TUSTIN | 2023-06-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | M GENERAL CONSTRUCTION | COMPTON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contactor was installing a fence and hit service while digging. NO USA
Southern California Gas Company | N | ORANGE | TUSTIN | 2023-06-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | J&M LEYVA | PERRIS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd Party Contractor hit plastic service will boring. They did not pothole service . USA marking were 3 feet off.
Southern California Gas Company | N | ORANGE | TUSTIN | 2023-10-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | OAK RIDGE LANDSCAPE | VALENCIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit 1'''' service 5 feet from meter with backhoe. No USA called in
Southern California Gas Company | N | ORANGE | TUSTIN | 2023-06-05 | Third party excavation damage | Main | Steel | Boring Equipment | 2 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 42 |  | ALLIED PLUS | LA HABRA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor failed to pothole marks for 2'''' steel main before boring and hit the 2main that was accurately marked.
Southern California Gas Company | N | ORANGE | TUSTIN | 2023-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 2 |  | J & M LEYVA GENERAL ENGINEERING | PERRIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged service while boring contrctor potholed but did not verify location of service
Southern California Gas Company | N | ORANGE | WESTMINSTER | 2023-05-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ETHAN DOUNG CONSTRUCTION CO | WESTMINSTER | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party. Homeowner called his friend to install his plumbing. Hit 1/2 IPS gas service at the riser. No USA
Southern California Gas Company | N | ORANGE | WESTMINSTER | 2023-06-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MODERN MUSE CONSTRUCTION | GARDEN GROVE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damage 1/2 CTS gas service with shovel. No USA.
Southern California Gas Company | N | ORANGE | WESTMINSTER | 2023-05-19 | Third party excavation damage | Main | Steel | Hand Tools | 3 | 42 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | BRASH | WESTMINSTER | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 3 steel gas main with backhoe. 3rd party contractor failed to hand expose 3 steel gas main. USA was called and mark were accurate.
Southern California Gas Company | N | ORANGE | WESTMINSTER | 2023-01-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 44 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ARIZONA PIPELINE | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was potholing are service for an electrical job when he struck are line with a shovel. USA was valid and marks were on.
Southern California Gas Company | N | ORANGE | YORBA LINDA | 2023-06-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GERARDO VASQUEZ | YORBA LINDA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party worker was installing new drain line for homeowner. He did not call USA and damaged branch service.
Southern California Gas Company | N | ORANGE | YORBA LINDA | 2023-05-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NATURESCAPE POOLS | PERRIS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Separate contractor had expired USA at location for pool line install. Damage occurred by pool company Naturescape Pools. Stub service that was cutback was not shown on GIS, and not marked under previous contractors USA ticket.. Service was folded back and damaged by unknown tools in multiple locations.
Southern California Gas Company | N | ORANGE | YORBA LINDA | 2023-07-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NATHAN HILL | YORBA LINDA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer did not call USA. Svc was not marked.
Southern California Gas Company | N | ORANGE | YORBA LINDA | 2023-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | OCTAVIO CASTRO | YORBA LINDA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor struck 1/2 plastic srevice with shovel while excavating new sewer installation for ADU.
Southern California Gas Company | N | ORANGE | YORBA LINDA | 2023-07-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | GCI CONSTRUCTION | SAN CLEMENTE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor knew where the gas service was, he was looking for it when he damaged it.
Southern California Gas Company | N | RIVERSIDE | BANNING | 2023-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | CITY OF BANNING WATER | BANNING | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Mis located service by SBN late crew LCT. FTL at SBN is aware and has addressed his employee about this issue.
Southern California Gas Company | N | RIVERSIDE | BANNING | 2023-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ACCO ENGINEERED SYSTEMS | COMMERCE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | CONTRACTOR WAS HAND DIGGING TO REPLACE IRRIGATION LINE. NO USA
Southern California Gas Company | N | RIVERSIDE | BANNING | 2023-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ALFREDO SANCHEZ | BANNING | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was running gasline to backhouse when they hit the service. No valid USA.
Southern California Gas Company | N | RIVERSIDE | BANNING | 2023-08-03 | Operator excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | TEICHERT | ONTARIO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | SoCalGas Co contractor (Teichert) hit the EFV on the service while hand exposing to find same for an anode install.
Southern California Gas Company | N | RIVERSIDE | BEAUMONT | 2023-11-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GOTHIC LANDSCAPE | RIVERSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged our IPS service with a trencher causing broken and blowing. USA was called and marks were clear.
Southern California Gas Company | N | RIVERSIDE | BEAUMONT | 2023-08-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | GOTHIC LANDSCAPING | VALENCIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | OHS crew arrived to find broken and blowing service due to 3rd party contractors doing grading work hit our 1/2 IPS svc. Contractor did not call USA.
Southern California Gas Company | N | RIVERSIDE | BEAUMONT | 2023-05-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | FAIRWAY LANDSCAPE AND IRRIGATION INC | RIVERSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit service with backhoe. Found service folded over and zip tied closed. Pinched and installed two feet of 3/4 plastic pipe with two 3/4 socket couplings.
Southern California Gas Company | N | RIVERSIDE | BEAUMONT | 2023-10-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | RGCI EARTH WORK | TUSTIN | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was trenching for fence. No valid USA.
Southern California Gas Company | N | RIVERSIDE | BEAUMONT | 2023-08-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | FAIRWAY LANDSCAPE AND IRRIGATION | RIVERSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service damaged by 3rd party contractor. No USA called for this work.
Southern California Gas Company | N | RIVERSIDE | BEAUMONT | 2023-04-24 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | J PIPELINE INC | CHINO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor hit 2 plastic main with backhoe while trenching. Locator did not use all additional resources. Did not notify district management to address situation.
Southern California Gas Company | N | RIVERSIDE | BEAUMONT | 2023-11-20 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 2 |  | BEAUMONT-CHERRY VALLEY WATER DISTRICT | BEAUMONT | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Struck main with shovel
Southern California Gas Company | N | RIVERSIDE | BEAUMONT | 2023-09-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Trencher | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 4 |  | MCC EQUIPMENT RENTALS LLC | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Damage to 3/4 steel service. Service was not marked. Contractor had valid USA. Service was altered for repair and to be replaced at later date.
Southern California Gas Company | N | RIVERSIDE | BERMUDA DUNES | 2023-04-24 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 12 |  | BP CONSTRUCTION | PALM DESERT | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor hit a 1/2 plastic service with a shovel because he failed to properly delineate the excavation area. Contractor delineated with white paint in the grass area at multiple locations to install the footing for (126) post lights inside a private complex apartments. Contractor recall USA ticket to be properly mark at every single location where he plans to dig.
Southern California Gas Company | N | RIVERSIDE | BLYTHE | 2023-01-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  |  | NA | LAMBERTO IGE | BLYTHE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner digging to install fence post. No USA. Cut 1/2 service with posthole digger. Co crew repaired. Arrival and departure includes travel time for crew from El Centro to Blythe and back.
Southern California Gas Company | N | RIVERSIDE | CALIMESA | 2023-09-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | INTERNATIONAL PAVING SERVICES | SAN BERNARDINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contactor damaged 1/2 PLA service while grading to do new street paving in front of address.
Southern California Gas Company | N | RIVERSIDE | CALIMESA | 2023-11-03 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 13 |  | ARIZONA PIPELINE | FRESNO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | Struck 2in plastic main while working outside of delineation marked area while placing new electrical into ground.
Southern California Gas Company | N | RIVERSIDE | CALIMESA | 2023-05-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ALI ARAB | MORENO VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer damaged 1/2 inch service with shovel no usa
Southern California Gas Company | N | RIVERSIDE | CATHEDRAL CITY | 2023-02-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | PABLO GONZALES | CATHEDRAL CITY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1/2 plastic service by shovel. No emergency services on site. No evacuations, injuries or road closures. Permanent repairs made.
Southern California Gas Company | N | RIVERSIDE | CATHEDRAL CITY | 2023-03-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | PALM SPRINGS LEAK DETECTION INC | INDIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavation Damage/Damage to Company Property. Plumber hit service line while digging for sewage line. No fire department, no police, no media and no injuries. Paseo Circulo East closed between 35983 and 35937 due to damage being at service line to curb vault. Control time 11:15am, Roads were re-opened at 11:30am. Restores followed after permanent repairs were made.
Southern California Gas Company | N | RIVERSIDE | CATHEDRAL CITY | 2023-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | WESTERN CONSTRUCTION SPECIALISTS | NORWALK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | While excavating to replace power pole, excavator damaged inserted 1/2 CTS cutback. No landmarks, indicators of service. Unable to locate. Stub abandoned at SMC.
Southern California Gas Company | N | RIVERSIDE | CATHEDRAL CITY | 2023-04-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | D S M MASONRY | CALIMESA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor damaged a 1 plastic service while digging to install the foundation for a brick wall. Contractor stated not having a valid USA ticket. Distribution crew responded to make repairs to the service using 4inch of coiled plastic pipe and two 1 fusion socket couplings.
Southern California Gas Company | N | RIVERSIDE | CATHEDRAL CITY | 2023-02-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | PREMIER BROADBAND SERVICES | ANAHEIM | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Third party contractor while placing conduits or Frontier used improper excavation practices while exposing the gas service hitting it with a shovel.
Southern California Gas Company | N | RIVERSIDE | CATHEDRAL CITY | 2023-04-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | NA |  | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer damaged 1/2 CTS service while excavating for landscape installation. No USA and customer left before the crews arrival.
Southern California Gas Company | N | RIVERSIDE | CATHEDRAL CITY | 2023-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | RICHARD DUFFLE | CATHEDRAL CITY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor failed to notify USA Dig Alert before digging to installed posts for a fence hitting a 1/2 post fence.
Southern California Gas Company | N | RIVERSIDE | CHERRY VALLEY | 2023-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | TED OLIVER | CHERRY VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner damage plastic service with post hole digger, NO USA
Southern California Gas Company | N | RIVERSIDE | CHERRY VALLEY | 2023-02-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HERMAN WEISSKER INC | JURUPA VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Service damage due to no wire to locate the plastic service and the GIS mapping was not posted correctly. Wire was added to the svc. to main connection and for the 12 feet of exposed service.
Southern California Gas Company | N | RIVERSIDE | COACHELLA | 2023-02-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | ALLA LIGHTING SERVICE INC | COLTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator failed to pothole at location where they were crossing service. Depth changed from where they potholed it and damaged service. Valid USA
Southern California Gas Company | N | RIVERSIDE | COACHELLA | 2023-05-31 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MILAGRO LANDSCAPING | RIVERSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor failed to notify USA Dig Alert before trenching for irrigation damaging a 1 plastic service in private property.
Southern California Gas Company | N | RIVERSIDE | COACHELLA | 2023-03-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | SHIRLEY JAMES A CONSTRUCTION INC | YUCCA VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third Party contractor damaged the 1 plastic line digging it to relocate the riser. LCT relocate the riser to the correct location while making permanent repairs to the damage 1 plastic service.
Southern California Gas Company | N | RIVERSIDE | COACHELLA | 2023-03-31 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  | 5 |  | BLANCO CONSTRUCTION | BUENA PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor installing fiber conduits for Frontier, failed to expose 2 plastic main before boring hitting a 2 plastic main.
Southern California Gas Company | N | RIVERSIDE | COACHELLA | 2023-03-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NA | COACHELLA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer was removing a tree in the backyard and hit our service. He did not call 811. Crew came and repaired. No evacuation, no road closures, no emergency services, no injuries.
Southern California Gas Company | N | RIVERSIDE | COACHELLA | 2023-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | RAMON VILLANUEVA | COACHELLA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner had worker digging to install stubs for ADU being built in the rear of the property and damaged 1/2 CTS line.
Southern California Gas Company | N | RIVERSIDE | COACHELLA | 2023-02-02 | Third party excavation damage | Main | Polyethylene Pipe | Trencher | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | SOCAL SANDBAGS | CORONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage was caused by third party contractor while excavating with a Trencher to install a street sign for the Fire Dept. Damage was to a 2 main in a new business construction site.
Southern California Gas Company | N | RIVERSIDE | COACHELLA | 2023-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | DAVE WILLIAMS PLUMBING & ELECTRICAL | PALM DESERT | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor failed to notify USA dig alert before digging with backhoe to install conduits for fire alarm hitting a 1/2 IPS service.
Southern California Gas Company | N | RIVERSIDE | COACHELLA | 2023-06-21 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NEXT EXPERIENCE BACKHOE SERVICE | HEMET | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Main marked with offsets. Marked correctly. Excavator digging for sewer, failed to pothole main where excavating
Southern California Gas Company | N | RIVERSIDE | COLTON | 2023-11-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MERCED MEDINA | COLTON | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Approved. No USA
Southern California Gas Company | N | RIVERSIDE | CORONA | 2023-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | CJWC WALTON BROS | MURRIETA | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Backhoe damaged main in new development
Southern California Gas Company | N | RIVERSIDE | CORONA | 2023-08-14 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | J&M LEYVA GENERAL ENGINEERING | PERRIS | CA | N | Y | Yes | Yes | No | Yes | No | No | No | 2 plastic main hit in new business track with backhoe on a no marks required USA ticket.
Southern California Gas Company | N | RIVERSIDE | CORONA | 2023-08-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LA STRADA PIPELINE | LAKE FOREST | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1 PE pipe was hit while digging with backhoe.
Southern California Gas Company | N | RIVERSIDE | CORONA | 2023-07-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MTZ CREATIVE CONCRETE INC | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Concrete company hit service with clay spade while digging for drainage.
Southern California Gas Company | N | RIVERSIDE | CORONA | 2023-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | OPTIMUM INC | BLOOMINGTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third-Party Damage, boring contractor hit 1/2 IPS service with shovel while potholing. Accurately marked service, marks visible. Valid USA.
Southern California Gas Company | N | RIVERSIDE | CORONA | 2023-12-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | KLS GENERAL CONSTRUCTION | ANAHEIM | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | RIVERSIDE | CORONA | 2023-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ALEJANDRO AGUIRRE | CORONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1/2 service line by homeowner excavating to repair water service line in private without a valid USA ticket.
Southern California Gas Company | N | RIVERSIDE | CORONA | 2023-08-03 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | WALSH GROUP | CONCORD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third-Party Damage. Valid and accurately marked USA. Excavator struck 4 in plastic main while digging for road work project.
Southern California Gas Company | N | RIVERSIDE | CORONA | 2023-03-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | PLATINUM LANDSCAPING | PALM DESERT | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscaping contractor excavating with heavy equipment damaged 1/2 ips service line to vacant tract home. Damaging party wasn''t on scene upon arrival. No USA ticket on file.
Southern California Gas Company | N | RIVERSIDE | CORONA | 2023-06-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | FRANK INNOVATIVE ELECTRIC | RIVERSIDE | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 2 inch pla main with mini excavator. Contractor dug before USA was valid. Crew made permanent repairs.
Southern California Gas Company | N | RIVERSIDE | CORONA | 2023-08-02 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | CAL-WEST LANDSCAPE | NORCO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Backhoe hit main. No USA
Southern California Gas Company | N | RIVERSIDE | CORONA | 2023-08-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 55 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | J&M LEYVA GENERAL ENGINEERING | PERRIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor bored through 1 plastic stub. Stub was accurately marked, was struck outside of pothole area. Valid USA.
Southern California Gas Company | N | RIVERSIDE | CORONA | 2023-02-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | DOUGLAS PIPELINE INC | LAKE ELSINORE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third Party Contractor hit marked 1 Plastic Stub while excavating for utilities.
Southern California Gas Company | N | RIVERSIDE | CORONA | 2023-02-06 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | D.B. ELECTRIC, INC | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third Party Contractor hit accurately marked 4 Plastic main with backhoe. Valid USA, failed to hand dig within tolerance zone.
Southern California Gas Company | N | RIVERSIDE | CORONA | 2023-06-09 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | KANA PIPELINE | RIVERSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Main damaged in new business area. Main repaired with 2 straight stick and 2 electrofusion couplings.
Southern California Gas Company | N | RIVERSIDE | CORONA | 2023-01-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | CEASER PEREZ | CORONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged PE service while grading property with no dig alert called in to locate it out. Per his conversation with LCT had it exposed but nicked it with digging tool by accident.
Southern California Gas Company | N | RIVERSIDE | CORONA | 2023-10-19 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 3 |  | WEKA INC | SAN BERNANDINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractors excavating with backhoe damaged gas main.
Southern California Gas Company | N | RIVERSIDE | CORONA | 2023-08-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | ISABEL MERCADO | CORONA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner hit service with trencher
Southern California Gas Company | N | RIVERSIDE | DESERT HOT SPRINGS | 2023-01-25 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | ONIX PAVING COMPANY | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor was grading when they damaged a plastic service. the contractor failed to pothole and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | DESERT HOT SPRINGS | 2023-01-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | DESERT HOT SPRINGS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit service with shovel digging to plant palm tree. No media, no evacuation, no injuries, no fire, no explosions, no road closures. Customer did not provide info for handyman who was performing work. Riverside County Fire Dept departed once we arrived. Crew repaired damaged service.
Southern California Gas Company | N | RIVERSIDE | DESERT HOT SPRINGS | 2023-01-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | JOSE PARRA | DESERT HOT SPRINGS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The third party contractor was using a probe to find the septic tank and damaged the plastic service. The contractor did not have a USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | DESERT HOT SPRINGS | 2023-03-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | DESERT HOT SPRINGS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging for water line and hit service line.
Southern California Gas Company | N | RIVERSIDE | DESERT HOT SPRINGS | 2023-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | EP INC | SAN BERNARDINO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Valid USA. Excavator damaged 1/2 unmarked stub. Crew working to install fiber optic conduit
Southern California Gas Company | N | RIVERSIDE | DESERT HOT SPRINGS | 2023-03-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HP COMMUNICATION | FONTANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor fail to use proper excavation practices while exposing the gas service. He damaged the long side 1 plastic service with a backhoe.
Southern California Gas Company | N | RIVERSIDE | DESERT HOT SPRINGS | 2023-11-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ELECTRIC PATROL INC | SAN BERNARDINO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Mismarked service. Hit 1/2 service.
Southern California Gas Company | N | RIVERSIDE | DESERT HOT SPRINGS | 2023-11-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | CHARLIE HOOSIER | YUCAIPA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor hit 1 plastic service with auger when installing post for new fence. No USA
Southern California Gas Company | N | RIVERSIDE | DESERT HOT SPRINGS | 2023-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | LAWRANCE EDGE | DESERT HOT SPRINGS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Renter at property damaged a 1/2 plastic service with a shovel while installing a post fence. The responsible party failed to notified USA Dig Alert.
Southern California Gas Company | N | RIVERSIDE | DESERT HOT SPRINGS | 2023-08-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BOBS EQUIPMENT | CATHEDRAL CITY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor grading lot and hit buried riser and broke 1/2 CTS service.
Southern California Gas Company | N | RIVERSIDE | DESERT HOT SPRINGS | 2023-05-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ELMER REDDISH | BEAUMONT | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third Party contractor failed to call USA Dig Alert before starting to grade front yard to build pool damaging 1/2 IPS service line. Crew made permanent repair altering 2 ft of 1/2 IPS pipe.
Southern California Gas Company | N | RIVERSIDE | DESERT HOT SPRINGS | 2023-05-09 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | ARIZONA PIPELINE CO | CORONA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | APC was replacing a 1/2 CTS branch service with a 1 plastic service by boring. Contractor failed to expose the service to determine clearance before digging the bore hole damaging the service with a shovel. Contractor notified the Capital Inspector right away to send distribution crews to make permanent repairs.
Southern California Gas Company | N | RIVERSIDE | DESERT HOT SPRINGS | 2023-07-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 1 |  | FRONTIER COMMUNICATIONS | RANCHO MIRAGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Previous damage. Found telecommunications conduit installed over top of 1/2 service. Service was damaged, taped and reburied without notification to SCG. No valid USA ticket on file.
Southern California Gas Company | N | RIVERSIDE | DESERT HOT SPRINGS | 2023-06-28 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 4 |  | HP COMMUNICATIONS | FONTANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor hit a 2 plastic main while boring parallel to gas line to install fiber for telecommunication. Gas line was properly mark in the street but contractor was boring too close to it between the curb and the 2 plastic main.
Southern California Gas Company | N | RIVERSIDE | DESERT HOT SPRINGS | 2023-05-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SHERYL PILAND | DESERT HOT SPRINGS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor did not call for a USA Ticket prior to start digging to build a pool hitting a 1/2 IPS service in private property.
Southern California Gas Company | N | RIVERSIDE | DESERT HOT SPRINGS | 2023-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | EMERALD SPRINGS | DESERT HOT SPRINGS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Pipe severed. Encroachment discovered. Abandoned service at SMC.
Southern California Gas Company | N | RIVERSIDE | DESERT HOT SPRINGS | 2023-06-29 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 26 |  | ELECTRIC PATROL INC | SAN BERNARDINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor hit 2 plastic main with a mini-excavator while trenching/pot holing to install fiber conduits/cable. This is the second damage from the same contractor in the last 24 hours. DPA is aware of this damage and is going to visit contractor at the job site the following morning to discuss both damages.
Southern California Gas Company | N | RIVERSIDE | DESERT HOT SPRINGS | 2023-10-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ELECTRIC PATROL INC | SAN BERNARDINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged 1/2 service during boring operations. Contractor was installing conduit for fiber optic cable and did not pothole service. USA ticket was valid, and marks were visible and correct.
Southern California Gas Company | N | RIVERSIDE | DESERT HOT SPRINGS | 2023-10-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | EP INC | SAN BERNARDINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor hit a service with a shovel while installing communication conduits for fiber optic.
Southern California Gas Company | N | RIVERSIDE | EASTVALE | 2023-06-02 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 4 |  | MERLIN JOHNSON CONSTRUCTION | MENTONE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 2 PE main was damaged by 3rd party contractor while using a splitter to replace the water service. Main was marked accurately and marks were visible. Contractor failed to hand expose.
Southern California Gas Company | N | RIVERSIDE | EASTVALE | 2023-12-28 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | JURUPA COMMUNITY SERVICES | JURUPA VALLEY | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Water company hit gas main with pipe puller.
Southern California Gas Company | N | RIVERSIDE | EASTVALE | 2023-07-11 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | WEKA | SAN BERNARDINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Water contractor hit gas main with pipe puller.
Southern California Gas Company | N | RIVERSIDE | HEMET | 2023-08-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 52 | 48 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | PACIFIC UTILITY INSTALLATION INC | CORONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA
Southern California Gas Company | N | RIVERSIDE | HEMET | 2023-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | FERREIRA CONSTRUCTION | PERRIS | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | RIVERSIDE | HEMET | 2023-12-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MAYAN DRYWALL INC | HEMET | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging to find sewer failed to notify USA. Struck PLA service with shovel.
Southern California Gas Company | N | RIVERSIDE | HEMET | 2023-08-25 | Operator excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | APL | CORONA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 2nd party contractor crew APC struck service while excavating for service replacement. Laborer striked the service with a shovel. Crew worked swiftly and safely to control gas and made permanent repairs.
Southern California Gas Company | N | RIVERSIDE | HEMET | 2023-07-24 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ARIZONA PIPELINE | CORONA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While cleaning up bell hole contractor struck gas service with shovel. Gas crew arrived on site and repaired damaged section.
Southern California Gas Company | N | RIVERSIDE | HEMET | 2023-01-24 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JOSE MACIAS | HEMET | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer exposed heavy corroded 3/4 service pipe causing a pit to pop. There was no USA ticket for the dig in.
Southern California Gas Company | N | RIVERSIDE | HEMET | 2023-12-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 2 |  | JEREMY JEFFERY | WINCHESTER | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage 1/2CTS service with mini excavator. No USA was called.
Southern California Gas Company | N | RIVERSIDE | HEMET | 2023-05-16 | Third party excavation damage | Main | Polyethylene Pipe | Grader/Scraper | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | LARRY VACINTO CONSTRUCTION | REDLANDS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor struck our 2 gas stub. Locator had put down flags in the dirt but contractor did not hand dig gas service to verify depth before grading.
Southern California Gas Company | N | RIVERSIDE | HEMET | 2023-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ALL AMERICAN ASPHALT | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Approved. did not pothole before grinding street.
Southern California Gas Company | N | RIVERSIDE | HEMET | 2023-01-25 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ARIZONA PIPELINE COMPANY | CORONA | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | Approved
Southern California Gas Company | N | RIVERSIDE | HEMET | 2023-12-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 8 |  | CURTIS DRILLING | ESCONDIDO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was using auger to set post of car port and struck gas service. Did not hand dig to verify gas line before using the auger.
Southern California Gas Company | N | RIVERSIDE | HEMET | 2023-05-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | K CHAUDHURI | HEMET | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Approved. No USA
Southern California Gas Company | N | RIVERSIDE | HEMET | 2023-03-22 | Third party excavation damage | Riser | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | CAL FIRE | HEMET | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Cal-fire was grading a field when they struck our 1/2 service with their plow. Crew arrived onsite and abandoned the service at the smc.
Southern California Gas Company | N | RIVERSIDE | HEMET | 2023-05-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CARRIE DURANT | HEMET | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | H/O Hit service while digging for fence post, No USA
Southern California Gas Company | N | RIVERSIDE | HEMET | 2023-10-04 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | ARIZONA PIPELINE | RIALTO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1/2 service damaged. Damaged with shovel.
Southern California Gas Company | N | RIVERSIDE | HEMET | 2023-08-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 4 |  | MR ELECTRIC | MURRIETA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | RIVERSIDE | HEMET | 2023-07-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 55 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NA | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA
Southern California Gas Company | N | RIVERSIDE | HOMELAND | 2023-11-09 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | RANCHO WEST LANDSCAPE | MURRIETA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Had expired USA ticket and did not hand expose pipe while digging. Had visible marks of main location on curb from previous ticket.
Southern California Gas Company | N | RIVERSIDE | HOMELAND | 2023-06-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 52 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | EMWD | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Approved. Water company damaged line on Water box install/removal.
Southern California Gas Company | N | RIVERSIDE | HOMELAND | 2023-07-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | UTILITY PACIFIC INSTALLATION | CORONA | CA | N | Y | Yes | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Pacific utility hit 1/2 IPS stub in new housing tract without a valid USA.
Southern California Gas Company | N | RIVERSIDE | INDIAN WELLS | 2023-09-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | CALBORE | ANAHEIM | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 1in plastic service damaged while boring in new gas houseline.
Southern California Gas Company | N | RIVERSIDE | INDIAN WELLS | 2023-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | H2O LANDSCAPE & MAINTENANCE | PALM DESERT | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor failed to notify USA Dig Alert before trenching to install drainage damaging a 1/2 IPS service with a shovel.
Southern California Gas Company | N | RIVERSIDE | INDIAN WELLS | 2023-01-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | JASON WHITLEY | INDIAN WELLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was digging to plant a palm tree and damaged plastic service. The contractor did not call in a USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | INDIAN WELLS | 2023-08-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CITADEL COMMUNICATIONS | INDIO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor digging with no USA, installing communications damaged our 1/2 CTS service with a shovel.
Southern California Gas Company | N | RIVERSIDE | INDIAN WELLS | 2023-12-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DESERT SCAPE MANAGEMENT | INDIO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor hit a 1/2 CTS service with a shovel while working on an irrigation line. The contractor failed to contact USA Dig Alert before digging.
Southern California Gas Company | N | RIVERSIDE | INDIAN WELLS | 2023-02-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | LA HACIENDA LANDSCAPING | INDIO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Excavator digging to install drainage at home damaged service
Southern California Gas Company | N | RIVERSIDE | INDIAN WELLS | 2023-10-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PRO LANDSCAPE | THOUSAND PALMS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor hit a 1/2 IPS service with a shovel while doing some irrigation work. The contractor failed to notify USA Dig Alert before digging.
Southern California Gas Company | N | RIVERSIDE | INDIAN WELLS | 2023-08-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | H2O LANDSCAPE & MAINTENANCE | PALM DESERT | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging for drainage sliced 1/2 IPS service causing damage.
Southern California Gas Company | N | RIVERSIDE | INDIAN WELLS | 2023-01-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MELO POOLS INC | PALM DESERT | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Pool company damage 1/2 plastic service when installing a pool conduit. Contractor did not call for USA marks before digging.
Southern California Gas Company | N | RIVERSIDE | INDIAN WELLS | 2023-08-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | MACO EQUIPMENT | THOUSAND PALMS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor failed to notify USA dig alert before digging with backhoe removing Palm tree hitting 1 plastic service.
Southern California Gas Company | N | RIVERSIDE | INDIAN WELLS | 2023-10-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | PC CONSTRUCTION | PALM DESERT | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged a 1/2 CTS stub with a backhoe, digging for electrical lines.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2023-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | VINCERE INDUSTRIES INC | THOUSAND PALMS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumbing contractor digging for sewer lateral damaged 1/2 CTS service.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2023-12-18 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 19 |  | HERITAGE PALM GROUNDS CREW | INDIO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Excavating to plant tree. Damaged 2 PE main. 19 outages
Southern California Gas Company | N | RIVERSIDE | INDIO | 2023-01-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | VACATION POOLS INC. | INDIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1/2 IPS service was damaged by 3rd party contractor while excavating to install pool line.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2023-07-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | TBU INC | BEAUMONT | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1in stub while trenching with backhoe.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2023-03-17 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RIVERA EQUIPMENT DBA | OAK HILLS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged 2 plastic main (stub) with a track-hoe thinking that the main was abandoned. He failed to expose it by hand.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2023-07-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | RC CONSTRUCTION SERVICES INC | RIALTO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor digging to install a bollard for meter protection damaged a 1 PE service.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2023-07-31 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | RC CONSTRUCTION SERVICES INC | RIALTO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor hit a 1 plastic service with a wood stake while framing to pour concrete in a sidewalk. Contractor failed to notified USA Dig Alert before construction started.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2023-01-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | CAST PLUMBING | INDIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor cut a 1 plastic service thinking it was something else rather than a gas service.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2023-10-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | INDIO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor failed to notify USA/Dig Alert before digging to install fence post inside a private trailer park hitting a 1/2 CTS service with a shovel.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2023-03-20 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | LAS PALMAS DE LA QUINTA | INDIO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Maintenance workers from trailer park (Las Palmas De La Quinta) failed to call USA Dig Alert before installing (2) galvanized posts to chain lot 299 hitting 1/2 plastic service with one of the posts.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2023-09-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | DESERT ISLES LANDSCAPE AND POOL CONTRACTOR | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor failed to notify USA Dig Alert before digging for landscaping work hitting a 1/2 CTS gas line in private property.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2023-01-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | H2O LANDSCAPE AND MAINTENANCE | PALM DESERT | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA notification. Excavating to plant trees and irrigation, Contractor damaged 1 service
Southern California Gas Company | N | RIVERSIDE | INDIO | 2023-10-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | SCORPION BACKHOE INC | WINCHESTER | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Third party contractor damaged a 1 plastic service with a backhoe while trenching alongside a 2 plastic main. Expired USA
Southern California Gas Company | N | RIVERSIDE | INDIO | 2023-01-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DANIEL FLORES | INDIO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged a 1/2 CTS gas service line when installing an irrigation pipe. Homeowner failed to notify USA Dig Alert before digging.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2023-01-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | TRICIA MORA | INDIO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage to plastic service was caused by a 3rd party while excavating for drainpipe installation. Damaging party was a friend of the customer and the customer was unaware they could not work under an expired USA Ticket. Flags and marks were present form the old ticket.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2023-03-14 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 10 |  | RANCHO CASA BLANCA HOA | INDIO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Maintenance workers inside the trailer park damaged a 2 plastic main with a sharpshooter/shovel while excavating to install an electric conduit.
Southern California Gas Company | N | RIVERSIDE | INDIO | 2023-01-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | M&J GRADING | INDIO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor failed to call Dig Alert before grading causing damage to 1 plastic service .
Southern California Gas Company | N | RIVERSIDE | INDIO | 2023-02-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 6 |  | POWER PLUS | DESERT HOT SPRINGS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Reported as a Code 1, discovered to be unreported damage. Temp power pole installed over stub service damaging it in the process. No valid or accurate USA on file. Original call was for CSO leak outside source unknown
Southern California Gas Company | N | RIVERSIDE | INDIO | 2023-08-17 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | SCORPION BACKHOE INC | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor failed to expose by hand 2 main before using backhoe, hitting 2 plastic main. Main was properly marked.
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2023-11-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GROUNDEX INC | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Damaged 1 PE stub by 3rd party contractor while directional boring. Active USA ticket. Stub was not marked.
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2023-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | JURUPA VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner working in yard failed to notify USA and struck PLA service with shovel.
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2023-01-07 | Third party excavation damage | Riser | Polyethylene Pipe | Not Available | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | LENNAR HOMES OF CALIFORNIA | CORONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1 service was hit and tied back by unknown. A security guard walking the property for the developer saw it and called it in
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2023-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 29 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SUPERIOR MASONRY | COLTON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per ETR on scene stated that backhoe operator that damaged service line left the Job site after the dig in.
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2023-06-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 6 |  | ALL CITIES ENGINEERING | JURUPA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to pothole marked 2 PLA main and struck with backhoe
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2023-09-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 29 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | JAVIER ORTIZ | JURUPA VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2023-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | DAVID TOURES | JURUPA VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hit pla service w/ shovel while digging on property. No USA
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2023-10-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 29 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | JIM DOIRON | JURUPA VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 CTS service was damaged by 3rd party contractor while probing. No active USA ticket.
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2023-05-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NA | RIVERSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Approved, No USA Called in.
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2023-04-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | BLANCA ROBINSON | JURUPA VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged 1/2 PLA service with a shovel. NO DIG ALERT was called in.
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2023-03-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | ALL CITIES ENGINEERING | JURUPA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor was hand digging to expose the gas service and damaged 1/2 CTS service.
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2023-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ARIZONA PIPELINE | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1/2 CTS service damaged by 3rd party contractor while hand excavating to install electrical conduit.
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2023-04-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MJ PIPELINE CONSTRUCTION | JURUPA VALLEY | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | While digging to install sewer lateral, 3rd party contractor damaged a 1 PLA service with backhoe. It looks like USA ticket was called in the same day of the damage.
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2023-10-10 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 29 | 29 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 4 |  | JURUPA VALLEY COMMUNITY SERVICES | JURUPA VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | NA
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2023-07-27 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 35 | 29 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  |  | NA | TK CONSTRRCTTION | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 2 PD main was damaged by 3rd party contractor excavating to install a water service for a hydrant. 2 PD main marks were off by 5''. Locator picked up signal that turned out to be the abandoned main. Footage from GIS matched with what he marked.
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2023-08-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | WEST BAY ASTHALT WORKS | PERRIS | CA | N | Y | Yes | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit line while grading, dug before valid USA start time
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2023-08-18 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | B SALGADO | JURUPA VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1'''' PE service was damaged by homeowner while driving stakes into the ground. No USA Ticket.
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2023-01-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ALL CITIES ENGINEERING | DOWNEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor did not pot hole where they were trenching and hit service in casing with backhoe. The rest of the marks were removed and not maintained.
Southern California Gas Company | N | RIVERSIDE | JURUPA VALLEY | 2023-05-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ALL CITIES ENGINEERING | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Added materials used.
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2023-08-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DSM MASONRY | VALENCIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 1 service while digging for the footing for a block wall.
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2023-06-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CAFORIO DEVELOPMENT GROUP LLC | OAK HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Excavator trenching to install conduit and damaged service
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2023-05-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CAFORIO DEVELOPMENT GROUP | RANCHO CUCAMONGA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor doing electrical work hit and damaged a 1 plastic service with a shovel. The contractor stated not have a valid USA ticket prior doing the digging.
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2023-05-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | NP MECHANICAL | CORONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No emergency services on site. Contractor performing work for developer hit service while digging for sewer. New development, no meters installed. ETR on scene issued assist for gas ops. Stood by and monitored. No restore once repairs made due to no meters installed.
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2023-09-22 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 0 |  | VERTICAL INTEGRITY | LA QUINTA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor failed to notify USA Dig Alert before digging placing electric conduits with a backhoe hitting a 2" plastic main.
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2023-06-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | CDG CONSTRUCTION | LA QUINTA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Irrigation contractor installing conduit and cut thru 1 PE service.
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2023-05-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | INLAND BUILDERS | SANTA ANA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service damaged by shovel while excavating to tie in water service line
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2023-08-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | CROSS FIRE GROUP | NA |  | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor failed to delineate work area, so ETD called him with no answer. Excavator start digging and hit 1 plastic service.
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2023-07-27 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NPL | EASTVALE | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | SCG contractor NPL damaged a plastic gas service while potholing it with a shovel for a replacement.
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2023-05-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | AJP INC | PALM DESERT | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No emergency services on site. Contractor for homeowner digging for sewer repair hit service. No USA was called in. No injuries, no media, no fatalities. Homeowner was not home causing no evacuations.
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2023-10-14 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MACO EQUIPMENT RENTALS | THOUSAND PALMS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contactor digging to install Edison conduits damaged our 2 PE main. Failed to pothole correctly.
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2023-07-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ANDREW PIERCE CORP | PALM DESERT | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party contractor failed to notify USA Dig Alert before making some repair to an irrigation valve before digging with a shovel and damaging a 1 gas service line.
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2023-02-23 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 6 |  | D & D ENGINEERING | THERMAL | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Excavator demolishing concrete planter that was installed over 2 PE main and struck with gad attachment on backhoe. 6 outages
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2023-04-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | MAUI POOLS | INDIO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor hit a 1 plastic service line with a shovel when digging to install the footing for a brick wall. Contractor stated not having a valid USA ticket. Distribution crew repaired the damage with 2 fusion socket couplings and 1 inch of coiled plastic pipe.
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2023-04-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | WILLIAMS HOMES | VALENCIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | ETR responded to A2 source unknown. Upon arrival, ETR, found a damaged service. There was no one on site. No Fire no police and no responsible party. ETR issued assist for Gas Ops and stood by for arrival. Gas Ops made repairs no restore needed, home being built.
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2023-02-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | BB&L GRADING & UNDERGROUND | INDIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor failed to expose by hand a marked 1/2 cts gas service while installing Dry Utilities, instead he used a mini excavator causing damage to the line.
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2023-04-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MR. CERVANTES LANDCARE | UPLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Valid USA. Damaged 1 stub at location. GIS and service history incorrect. Stub line under foundation of building and abandoned at main.
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2023-02-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | PACIFIC WEST UNDERGROUND | YUCAIPA | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Unknown stub at location. Also, when locator arrived, no delineations at site. Excavator notified per EPR code and failed to recall ticket
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2023-12-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CJW GENERAL CONTRACTORS | MURRIETA | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Contractor damaged 1 PE while digging to install new sewer line. Contractor started digging before USA was valid.
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2023-09-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | M&M DESERT LANDSCAPE | THERMAL | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor failed to call USA Dig Alert before excavating to plant a palm tree hitting a 1 plastic service with a backhoe.
Southern California Gas Company | N | RIVERSIDE | LA QUINTA | 2023-01-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | PACIFIC WEST UNDERGROUND INC. | YUCAIPA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Damaged 1 service by 3rd party contractor while excavating with backhoe. Contractor was installing conduit for electric utility.
Southern California Gas Company | N | RIVERSIDE | LA QUITA | 2023-05-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | UNITED BROTHERS CONCRETE INC | PALM DESERT | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Service hit by stake while framing for sidewalk
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2023-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | 4 BERISTAIN BROS | LAKE ELSINORE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor damaged 1 PLA stub w/hand tool. No USA was requested.
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2023-05-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 59 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | PERRIS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA at the time of incident. Contractor hit a gas service while working on tele. comms. for Frontier.
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2023-11-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CAISTEAL BUILDERS INC | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | NA
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2023-06-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MIRAMONTE LANDSCAPING | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscaper failed to notify USA and struck pla service.
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2023-09-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 19 |  | MURRIETA DEVELOPMENT | TEMECULA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor damaged 2 PLA main with backhoe. Gas main was marked, but dirt was covering the marks.
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2023-04-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | KEC ENGINEERING | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service was already exposed and the laborer still hit it with a shovel.
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2023-06-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | KEC | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third Party Contractor damaged 1/2CTS PLA service while hand digging with a shovel..
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2023-07-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | KEC ENGINEERING | CORONA | CA | N | Y | Yes | No | Yes | No | No | Yes | Yes | Third party contractor damaged 1/2 PLA service with backhoe. USA ticket had expired.
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2023-12-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ADOBE LANDSCAPING | ANAHEIM | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA at the time of the incident.
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2023-04-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | HEATHER HALL | LAKE ELSINORE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Friend of homeowner was digging for an unknown reason in the yard and hit a plastic service with an unknown hand tool. The subject left the property following the damage and never returned.
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2023-07-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | GOTSIC LANDSCAPE | WILDOMAR | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA at the time of the incident. Service had been installed 2 days prior to damage.
Southern California Gas Company | N | RIVERSIDE | LAKE ELSINORE | 2023-09-21 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ELSINORE VALLEY MUNICIPAL WATER DISTRICT | LAKE ELSINORE | CA | N | Y | Yes | No | No | No | No | Yes | Yes | Water Company backhoe operator damaged a 2 plastic main while digging hole for a water service installation. They were working on an expired Dig Alert ticket at the time of the incident.
Southern California Gas Company | N | RIVERSIDE | MANIFEE | 2023-04-27 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 2 | 59 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | SIERRA PACIFIC ELECTRICAL | JURUPA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged a 2 plastic main while operating auger for electrical install. Marks were good and the contractor didn''t expose the main before digging.
Southern California Gas Company | N | RIVERSIDE | MECCA | 2023-01-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 44 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JOSE TORRES | MECCA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The homeowner was digging with a shovel for a drain pipe when they damaged a plastic gas line. The homeowner did not call USA and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2023-12-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | RIGO GONZALEZ | PALM DESERT | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas service with mini excavator. USA was valid but contractor did not hand expose gas service before digging with equipment
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2023-09-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | GREEN BEE CONCRETE | PERRIS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor failed to notify USA and struck 1/2 PLA svc while digging for sewer with backhoe.
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2023-04-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ACE CAPITAL ENGINEERING | LAKE FOREST | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | Approved. Did not pot hole
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2023-08-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | AMERICAN LANSCAPING | REDLANDS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA at the time of incident.
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2023-10-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NU-TECH CONSTRUCTION SERVICES | NUEVO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hand digging to repair water line. Service struck. Accurately marked PLA service.
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2023-06-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PLATINUM LANDSCAPING INC | PALM DESERT | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Developer hit riser.
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2023-05-30 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 48 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ARIZONA PIPELINE CO | HESPERIA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Approved. Contractor damaged line while exposing for DIMP job.
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2023-06-26 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | PACIFIC UTILITY INSTALLATION INC | ANAHEIM | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damaged 2PLA main with auger. No USA
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2023-04-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | JPI DEVELOPMENT GROUP INC. | MURRIETA | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Third Party Contractor damaged 2PLA gas line with backhoe.
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2023-05-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | PIERRE LANDSCAPE | SAN MARCOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third Party Contractor damaged 1PLA service with mini-excavator. Did NOT hand expose marked service.
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2023-08-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 1 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | WOLVERINE FENCE CO | ONTARIO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA at time of incident.
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2023-06-14 | Third party excavation damage | Miscellaneous/Other | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | H7 CONTRACTING | MURRIETA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | 3rd party contractor pulled cap off from service stub while trenching for other utilities.
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2023-05-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | AMERICAN LANDSCAPE | REDLANDS | CA | N | N | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No | No damage to SUOF. | No damage to SUOF. | No USA at the time of the damage
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2023-11-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ADVANCED ERROSION SERVICES | HEMET | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged a plastic service with a backhoe while grading at the property.
Southern California Gas Company | N | RIVERSIDE | MENIFEE | 2023-08-09 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | HEATH CONTRACTING AND ENGINEERING | MURRIETA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged a 2 plastic main with a backhoe while digging with a backhoe for a conduit.
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2023-12-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 53 | 48 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | TERRANCE PIERSON | RIVERSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Service line hit.
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2023-05-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 52 | 48 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | EMWD | MORENO VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Approved. EMWD hit line with sharp shooter
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2023-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NA | MORENO VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 PA service damaged by 3rd party contractor while excavating to install a fence post. No USA ticket.
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2023-02-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | ACE CAPITAL | LAKE FOREST | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While potholing for a bore contractor struck 1/2 gas service with shovel. Gas service was marked out and the company had a valid USA. Contractor didn''t practice safe digging procedures.
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2023-05-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | MORENO VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2023-07-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | FABIAN URIBE | MORENO VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA, Contractor hit line with post hole digger.
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2023-02-01 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Trencher | 0.75 | 43 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LAT LONGINFRCSTUCTURE LLC | AUSTIN |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Approved. Lat Long did not pothole facility before running blade across. Ended up severing the line and crew ended up replacing Service.
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2023-01-25 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 54 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | LOPEZ RICHARD CONSTRUCTION INC | CORONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage- Third party contractor hit the end of the main with backhoe when installing the sewer. the contractor did not notify USA
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2023-03-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | RICHARD LOPEZ CONSTRUCTION | CORONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Trenching for telephone. Contractor gave USA ticket number yet that was for stormdrain and they were digging telephone when they damaged service. No USA called for installing telephone.
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2023-10-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NA | WHITTIER | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Landlord installing new sewer lines by hired contractor. Crew hit 1/2 plastic service with jackhammer while trenching.
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2023-08-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 48 | 48 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | ALS PRO SERVICES | MORENO VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2023-08-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 51 | 48 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | BLACKHAWK ELECTRICAL | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2023-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | PARADISE CONSTRUCTION | PERRIS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor making repair on water pipe failed to contact USA and struck 2 PLA service.
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2023-05-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | PARADISE CONSTRUCTION | PERRIS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Approved, No USA. this is the one we evacuated the school.
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2023-08-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MIGUEL MOLINA | MORENO VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Mini excavator digging for landscape work hit service. No USA called
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2023-11-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | FERRERIA COASTAL CONSTRUCTION | RANCHO CUCAMONGA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | NA
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2023-05-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | TRINIDAD JUAREZ | MORENO VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Approved. No USA
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2023-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NELVI CONSTRUCTION INC | RIVERSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging trench for home addition and struct our 1/2 service with shovel. no usa was called in.
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2023-02-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NELVI CONSTRUTION,INC | SAN BERNARDINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer was digging trench for sewer lateral and struck gas service with shovel. Crew was previously out there the day pior and repaired a similar damage. No USA was called in
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2023-11-10 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | LB3 ENTERPRISE | LAKESIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA.
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2023-04-04 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | RICHARD LOPEZ CONSTRUCTION | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Approved. Contractor had Expired USA Ticket from Jan of 2023. Also had previously damaged the 2 PLA on Bethany Rd and we told them to make sure to refresh if they''ll be doing any other work in future. Damage Prevention was on scene for both. Crew inserted a new SVC and installed a Curb Valve due to not being able to relocate to a new location due to windows and vents near by.
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2023-06-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | RICHARD LOPEZ CONSTRUCTION | CORONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1/2 IPS gas facilities while excavating to install electrical. Company crew made permanent repairs. There was no DigAlert ticket on file. Billing is recommended.
Southern California Gas Company | N | RIVERSIDE | MORENO VALLEY | 2023-11-08 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | SIERRA PACIFIC ELECTRICAL | RIVERSIDE | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | No delineation found.
Southern California Gas Company | N | RIVERSIDE | MURRIETA | 2023-05-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | FAMILY PRIDE PLUMBING | LAKE ELSINORE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third Party Contractor damaged 1/2PLA CTS service with shovel.
Southern California Gas Company | N | RIVERSIDE | MURRIETA | 2023-07-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 4 |  | WESTERN STATES FIRE PROTECTION CO | LAKEWOOD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | RIVERSIDE | MURRIETA | 2023-03-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ANGELA SOSA | MURRIETA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner digging footings for a wall failed to notify USA and struck PLA branch service. Fire department was called and evacuated residents and blocked street.
Southern California Gas Company | N | RIVERSIDE | MURRIETA | 2023-09-08 | Third party excavation damage | Main | Polyethylene Pipe | Grader/Scraper | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 3 |  | HAMEL CONTRACTING | MURRIETA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third Party Contractor damaged 2 PLA main with a skid steer while grading.
Southern California Gas Company | N | RIVERSIDE | MURRIETA | 2023-09-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BLUE TOP INCORP | APPLE VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA at time of damage.
Southern California Gas Company | N | RIVERSIDE | MURRIETA | 2023-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | JP ELECTRIC | VISTA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third Party Contractor damaged 1PLA stub with a backhoe. No dig alert at time of the damage.
Southern California Gas Company | N | RIVERSIDE | MURRIETA | 2023-03-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | TWIN OAKS LANDSCAPING | WRIGHTWOOD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third Party Contractor damaged 1/2 PLA IPS service with trencher. NO USA was called.
Southern California Gas Company | N | RIVERSIDE | NORCO | 2023-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CORONA-NORCO UNIFIED SCHOOL DISTRICT | NORCO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit our svc with a backhoe causing broken and blowing.
Southern California Gas Company | N | RIVERSIDE | NORCO | 2023-06-02 | Third party excavation damage | Main | Material not known | Backhoe/Trackhoe | 0 | 60 | 55 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  |  | NA | ALABBASI INC | PERRIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third Party Damage, contractor for City of Norco pulled up on 2 steel main with backhoe while excavating for storm drain installation. Valid and accurately marked USA. Contractor failed to hand expose, no gas leak, damaged main was altered to make permanent repairs.
Southern California Gas Company | N | RIVERSIDE | NORCO | 2023-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | AID BUILDERS INC | LOS ALAMITOS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Backhoe struck PE service while digging
Southern California Gas Company | N | RIVERSIDE | NORCO | 2023-10-30 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ACCESS GENERAL CONTRACTING INC | CORONA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Second party contractor damaged accurately marked 1/2 plastic service with sharp shooter while digging for bollard post install. Valid USA.
Southern California Gas Company | N | RIVERSIDE | NORCO | 2023-09-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ALEJANDRO FERNANDEZ | NORCO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | OHS crew arrived to find 3rd party contractor was digging to install guard rails. Contractor damaged our 1/2 cts service causing broken and blowing.
Southern California Gas Company | N | RIVERSIDE | NORCO | 2023-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | H&M GENERAL CONTRACTORS | HIGHLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third Party Damage, contractor damaged 3/4 steel service with backhoe. Failed to pothole marked line on valid ticket. Replaced service to make permanent repairs.
Southern California Gas Company | N | RIVERSIDE | NORCO | 2023-06-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CHRIS | POMONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Third Party Damage, valid USA, contractor struck unmarked cutback, cutback was unmapped in GIS.
Southern California Gas Company | N | RIVERSIDE | NORCO | 2023-01-17 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | CEM CONSTRUCTION CORP | MONTEBELLO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third Party Damage, Valid and accurately marked.
Southern California Gas Company | N | RIVERSIDE | NORCO | 2023-05-26 | Operator excavation damage | Main | Polyethylene Pipe | Directional Drilling | 3 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ARIZONA PIPELINE CO | HESPERIA | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor struck and damaged 3PEM while directional drilling for main replacement.
Southern California Gas Company | N | RIVERSIDE | NORCO | 2023-02-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GCI CALIFORNIA CONSTRUCTION | SAN CLEMENTE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | contractor damaged line with shovel while trenching for drain.
Southern California Gas Company | N | RIVERSIDE | NORCO | 2023-07-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | BORDEN EXCAVATING | CALIMESA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third-party contractor struck 1/2 IPS service while excavating for water line repair. Valid and accurately marked USA.
Southern California Gas Company | N | RIVERSIDE | NORTH PALM SPRINGS | 2023-04-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | TTS ENGINEERING | STANTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Marks visible USA valid. Potholed service 4 inch away failed to protect in place. 1 Building evacuated
Southern California Gas Company | N | RIVERSIDE | NUEVO | 2023-01-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | JUAN CARLOS GARCIA | NUEVO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Approved. No USA called in
Southern California Gas Company | N | RIVERSIDE | NUEVO | 2023-11-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ANTHONY CASTELLON | NUEVO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer doing work at property with no USA and struck PLA service with post hole diggers.
Southern California Gas Company | N | RIVERSIDE | NUEVO | 2023-04-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MESA FENCE | PERRIS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Approved. Talked to the locator and he closed out the ticket under EPR code 21 No Access. Also in his notes he stated that he spoke to the home owner and notified him to tell the contractor to give access so we could perform locate and they did not but continued to proceed with work.
Southern California Gas Company | N | RIVERSIDE | NUEVO | 2023-08-10 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 12 |  | EASTERN MUNICIPAL WATER DISTRICT | PERRIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | NA
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2023-01-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MACO EQUIP | THOUSAND PALMS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor was excavating with a shovel when they damaged a plastic service. The contractor moved flags and did not maintain them. The contractor is fully responsible.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2023-10-04 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SOCALGAS | PALM DESERT | CA | Y | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | ETR was collecting ground sample while punching bar holes with a Po-Go hitting a 1/2 CTS service.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2023-08-08 | Third party excavation damage | Main | Polyethylene Pipe | Grader/Scraper | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JASPER COMPANIES | COSTA MESA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor for developer hit 2 plastic main while digging footing for retaining wall.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2023-08-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | WOODBRIDGE | MISSION VIEJO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor hit 1 plastic stub with a backhoe while installing a sewer line.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2023-08-24 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | PACIFIC WEST UNDERGROUND | YUCAIPA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging without a valid USA ticket for the area they are working in, damaged our 2 PE main with excavator.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2023-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | VASQUEZ BROTHERS LANDSCAPING | PALM DESERT | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 CTS service damaged while removing tree stump with shovel.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2023-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | NEW WEST LANDSCAPE | INDIO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging to install irrigation lines, hit 1/2 CTS service.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2023-11-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | RWC GENERAL CONTRACTOR | CATHEDRAL CITY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Contractor excavating to install sewer at address and damaged 1/2 PLA service.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2023-04-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ROSA AVILES | PALM DESERT | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Laborers working for homeowner to build block wall. Damaged service while digging trench for footings
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2023-11-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MIGUEL RAMIREZ | PALM DESERT | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service blowing due to being damaged with a shovel.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2023-09-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ARIZONA PIPELINE | CORONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | APC, digging for SoCal Edison hit 1/2 CTS service that ETD did not mark due to tracer wire issues and service feeding pool on the next street.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2023-09-11 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | PALM DESERT | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor damaged a 2 plastic main with a shovel while installing a drainage conduit in the backyard. The contractor or homeowner failed to notify USA Dig Alert before starting to dig.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2023-07-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | OC HILLS MASONRY INC | ANAHEIM | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Excavator digging to install irrigation for landscaping.
Southern California Gas Company | N | RIVERSIDE | PALM DESERT | 2023-07-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ARK PLUMBING | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 1/2 CTS gas line while repairing waterline. Did not have a USA.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2023-03-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NA | DESERT HOT SPRINGS | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Third party contractor doing lanscaping work (removing a stump) hit a 1/2 CTS plastic service with a shovel. The contractor did not have a valid USA ticket, ticket was expired since 6-1-2022.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2023-01-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | PREMIER BROADBAND SERVICES, INC | CORONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Service marked by measurements due to access issues. Marks indicated 1/2 PLA service, but excavator found 3/4 steel abandoned service and continued to bore without verifying
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2023-02-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | MJ PIPELINE CONSTRUCTION | JURUPA VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. While excavating for natural gas houseline for property, 2 service was damaged
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2023-02-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Directional Drilling | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | BLANCO CONSTRUCTION INC | BUENA PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor damaged 1/2 CTS pipe while installing fiber conduit for Frontier. Contractor failed to expose service running underneath concrete driveway instead took his chance damaging the service.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2023-02-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 4 |  | BLANCO CONSTRUCTION | BUENA PARK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Excavator potholed for service and didn''t locate it. Failed to recall for SCG to remark. Damaged 1/2 service resulting in 4 outages. Locator expressed bad signal from tracer wire and requested excavator contact him if unable to locate facilities
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2023-04-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 0.75 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | SEBASTAIN MONVOY | FONTANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third Party Contractor damaged 3/4 steel service while performing directional boring work to install Fiber conduit for Frontier. Contractor failed to expose service that was marked 24 from the damage location.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2023-04-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Directional Drilling | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CASEMON COMMUNICATION | FONTANA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Excavator contacted Locator for remarks because they could not find service but failed to wait for Locator to remark and continued to bore at location and damaged service. Initial marks 11'' off.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2023-01-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | RBC CONSTRUCTION, INC. | PALM DESERT | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Expired USA ticket. No delineations at original call in on 9/20/22. Excavator never renewed/updated ticket
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2023-03-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | TURN AROUND COMMUNICATIONS | EL MONTE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Third party contractor damaged service gas line when installing a communication conduit by directional boring method for Frontier. ETD failed to mark the service.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2023-01-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | TURN AROUND COMMUNICATIONS | COVINA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit our service at the street while boring for telecom work . They were a 3rd party doing work for Frontier. No emergency services, no injuries, no evacuations, no media. Crew made permanent repair on 1/2 plastic service.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2023-02-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | BLANCO CONSTRUCTION INC | BUENA PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third contractor damaged a plastic gas service while directional boring. The contractor failed to pothole the service and is fully responsible.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2023-11-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DESERT PRIDE CONSTRUCTION | INDIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor hit a marked 1/2 CTS service with a shovel while digging.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2023-12-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | DESERT PRIDE CONSTRUCTION & PAINTING INC | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged a 1/2 CTS service on an expired ticket.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2023-01-03 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Boring Equipment | 0.75 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | PREMIER BROADBAND SERVICES, INC | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator boring to installing fiber optic cable. Service not potholed. Ticket never called in for remarks for SCG. Excavator agreed marks were good. Original ticket dates back to October 2022.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2023-07-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HOYT CONSTRUCTION | THOUSAND PALMS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractors hit 1/2 CTS service while digging irrigation lines.
Southern California Gas Company | N | RIVERSIDE | PALM SPRINGS | 2023-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 4 |  | LA STRADA PIPELINE | LAKE FOREST | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor damaged a 1 plastic service while repairing a lateral sewer line in public property. The contractor provided a USA ticket that was for a different location in the neighborhood but not were the excavation was done.
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2023-11-07 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | SUB ZERO EXCAVATION | SIMI VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Did not pothole and verify before digging.
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2023-08-17 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 55 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | BCR | PERRIS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Upon arrival, damage to 3/4 STL service by grader. No USA was called.
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2023-06-30 | Third party excavation damage | Main | Polyethylene Pipe | Not Available | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | DIRT GRADING | CHINO HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 2in PE main damaged by 3rd party contractor with backhoe.
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2023-05-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | NA | PERRIS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Approved. No USA
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2023-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | CARLOS CAMPOS | PERRIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Homeowner hit pla service while trenching for new water houseline.
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2023-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | JUAN R CARDENAS | PERRIS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner digging on property did not notify USA and nicked PLA svc.
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2023-06-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NA | SEE DAMAGE REPORT |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | OHS crew arrived to find broken and blowing 1 PLA svc. 3rd party contractor damaged svc using a backhoe. OHS crew made repairs using 3'' of 1 PLA and 2 1 couplings.
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2023-06-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SAMBRANO PLUMBING | RIVERSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged a 1/2 IPS service line while excavating to make plumbing repairs. The service was located and marked correctly. Company crew made permanent repairs. Contractor failed to exercise caution while excavating near company facilities. Billing is recommended.
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2023-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NA | PERRIS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Approved. did not call in for a USA ticket
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2023-06-20 | Third party excavation damage | Main | Polyethylene Pipe | Trencher | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ARTISTIC MAINTENANCE INC | LAKE FOREST | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While trenching for subs contractor struck our 2'''' gas main with ditch witch trenching machine. crew arrived and pinched gas main and replaced damaged section.
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2023-06-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NA | ANAHEIM | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Approved. No USA, hit stub with backhoe
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2023-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ALLEN KEY | PERRIS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage -third party contractor hit service with shovel. No USA
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2023-10-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SUB ZERO EXCAVATION | SIMI VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hit line. Did not use caution while exposing. Marked correctly.
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2023-01-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 43 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | GRANITE CONSTRUCTION COMPANY | INDIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Approved. 2 SVC Line struck. line was marked accurately.
Southern California Gas Company | N | RIVERSIDE | PERRIS | 2023-10-24 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 6 | 53 | 48 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  |  | NA | H7 CONTRACTING & ENGINEERING | MURRIETA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 6 Main Damage
Southern California Gas Company | N | RIVERSIDE | RANCHO MIRAGE | 2023-10-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | RAMMELL CONSTRUCTION | PALM SPRINGS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor failed to notify USA/Dig Alert before digging, damaging a 1/2 CTS Service with a backhoe while trying to install a swimming pool equipment.
Southern California Gas Company | N | RIVERSIDE | RANCHO MIRAGE | 2023-10-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CONSERVE LANDCARE | CALABASAS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party company making repair to an irrigation valve hit & damaged a 1/2 plastic service. Contractor failed to notify USA Dig Alert before digging.
Southern California Gas Company | N | RIVERSIDE | RANCHO MIRAGE | 2023-01-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | STATEWIDEDE SERVICES | LA QUINTA | CA | N | Y | Yes | Yes | No | Yes | No | No | No | Third party contractor installing electrical conduit and working outside of delineation hit a plastic service. Locator stated that the line was not mark but where the line was hit is at F/O 18 Jill Terrace and the ticket states for 17 Jill Terrace, Rancho Mirage.
Southern California Gas Company | N | RIVERSIDE | RANCHO MIRAGE | 2023-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ARIZONA PIPELINE | CORONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Tracer wire issues, location has bare wire located off service history measurements.
Southern California Gas Company | N | RIVERSIDE | RANCHO MIRAGE | 2023-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | POTABLE IRRIGATION | RANCHO MIRAGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor removing tree stump and hit 1 PE service.
Southern California Gas Company | N | RIVERSIDE | RANCHO MIRAGE | 2023-08-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | SOCAL BUILDERS | PALM DESERT | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Third party contractor hit 1/2 CTS service with a trencher while doing demolition work. Utility was marked but contractor started digging before 48 hrs.
Southern California Gas Company | N | RIVERSIDE | RANCHO MIRAGE | 2023-10-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MANUEL QUINTERO | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner had a worker digging to install a tree and damaged our 1/2 CTS service.
Southern California Gas Company | N | RIVERSIDE | RANCHO MIRAGE | 2023-08-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | RG CONCRETE | PALM DESERT | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor hit a 1 plastic service while trenching to install a drainage pipe. The contractor failed to notify USA Dig Alert before digging.
Southern California Gas Company | N | RIVERSIDE | RANCHO MIRAGE | 2023-06-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GALLARDO LANDSCAPING | RANCHO MIRAGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Lanscaping company damaged a 1/2 CTS Service with a shovel while excavating to remove a tree. Contractor stated not having a valid USA ticket.
Southern California Gas Company | N | RIVERSIDE | RANCHO MIRAGE | 2023-08-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | EVANKOS REMODEL | PALM DESERT | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor hit a 1/2 CTS branch service with a shovel while working on a sewer line. Third party contractor failed to notify USA Dig Alert before digging.
Southern California Gas Company | N | RIVERSIDE | RANCHO MIRAGE | 2023-10-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | EVANKOS PAINT AND REMODEL | PALM DESERT | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1/2 CTS service while excavating for pool line. Contactor put the shovel through the service.
Southern California Gas Company | N | RIVERSIDE | RANCHO MIRAGE | 2023-04-19 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  | 14 |  | ALEX HERNANDEZ | COACHELLA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 2 PE main while digging for sewer line.
Southern California Gas Company | N | RIVERSIDE | RANCHO MIRAGE | 2023-04-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MACO | THOUSAND PALMS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Facilities marked correctly. Valid USA. Excavator failed to pothole service
Southern California Gas Company | N | RIVERSIDE | RANCHO MIRAGE | 2023-05-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MACO | THOUSAND PALMS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Edison contractor digging to install electric damaged SoCalGas line with shovel.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2023-12-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 48 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DOTY BROS | NORWALK | CA | N | Y | Yes | Yes | Yes | Yes | No | No | Yes | 1/2 IPS service damaged by 3rd party contractor with sharpshooter while hand digging. Valid USA. Marks not visible at the time of damage.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2023-04-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | BORDEN EXCAVATING | CALIMESA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Corrections have been made.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2023-12-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | INDUSTRIAL ASPHALT | PERRIS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 1/2 PE service. No USA was called prior to digging.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2023-08-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DIAMOND HOUSE CONTRUCTION AND PLUMBING | RIVERSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 PE service damaged by 3rd party contractor with backhoe while excavating to install new septic system. No USA Ticket.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2023-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | SHANNON SAFFO | RIVERSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1/2 IPS service by homeowner. No USA ticket.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2023-10-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | OSCAR VALERIO | RIVERSIDE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1 PLA service damaged by 3rd party contractor while grading. No USA ticket.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2023-11-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | VYKOUK | RIVERSIDE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner struck 1/2 IPS Service. No USA.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2023-07-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | TONY LANDSCAPING | RIVERSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | OHS crew arrived to find 3rd party contractor and damaged 1/2 IPS service with jackhammer.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2023-10-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CHI CONTRACTORS | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1/2 CTS service damaged by 3rd party contractor with backhoe. USA ticket was valid, marks were accurate and visible. Contractor Failed to hand excavate.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2023-08-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 55 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CP CONSTRUCTION | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party hit 1 PE service with backhoe excavating for sewer.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2023-03-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | JOSE ESQUEDA | RIVERSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | H/O hit svc while digging w/ post hole digger to install fence post. No USA
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2023-10-19 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 15001 |  |  | NA | MARK COMPANY | ORANGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2023-01-26 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CHRISTIAN BARLOWS | RIVERSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner digging in front yard struck service with a pick ax while hand digging with no USA. Fire dept on scene shut down street in front of address.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2023-07-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 48 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | NUWAVE INTERNATIONAL INDUSTRIES | SIGNAL HILL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1PE pipe was damaged by 3rd Party contractor while hand excavating with shovel.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2023-07-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 48 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | COMET ELECTRIC | CANOGA PARK | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 1/2 CTS service was damaged by 3rd party contractor while boring. Service was not marked. This was a big project that actually had 2 USA tickets called in. Locator forgot to go back to mark out this service.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2023-08-03 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 48 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DMG | RIVERSIDE | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1/2 CTS service damaged by 2nd party contractor while hand excavating to install a meter guard.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2023-02-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 48 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ROGERS INTERNATIONAL | TOPEKA | KS | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged 1/2 plastic service while boring. Contractor failed to pothole service where it was marked.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2023-02-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ABELINE MARTINEZ | RIVERSIDE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Approved. Did not have a validd USA ticket.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2023-04-19 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ASPLUNCH CONSTRUCTION LLC | HORSHAM |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 2 PA main damaged by 3rd party contractor. The main was mismarked 5''. Locator hooked up to the only service on the 2 PA main to locate the main were it transitions from steel to plastic. Was getting a weak signal. Used all company resources to mark the area.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2023-03-08 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 48 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ALABBASI | PERRIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Marks show 2 PLA main. Contractor stated they only found 2 steel main when they pot holed. They failed to find plastic main. Continued digging with excavator, damaging the 2 PA main.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2023-03-07 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 48 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | AL ABBASIR | PERRIS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3/4 steel service damaged by 3rd party contractor with excavator. Active USA ticket. Marks were washed away by heavy rains. No remarks requested on ticket.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2023-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | GREG REAF SNYDER | RIVERSIDE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged plastic service with saw. No USA.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2023-02-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 48 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MAMCO DBA ALABBASI | PERRIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1/2 PLA service damaged with shovel while potholing. Service was properly marked. Marks were visible.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2023-05-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ALLEN DIAZ | RIVERSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA at the time of incident.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2023-05-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 48 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NICOLAS SERRATO | RIVERSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 CTS service damaged by Occupant while grading a hillside. NO USA ticket.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2023-12-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 48 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | 24 HOUR EXPRESS SERVICES | MURRIETA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 IPS service damaged by 3rd party contractor while using powered clay spade. No USA Ticket.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2023-08-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 48 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | HUI HUI HUANG | RIVERSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 plastic service damaged by homeowner with a backhoe while excavating to repair a water line. No USA ticket.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2023-09-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | CARLOS ENCISO | RIVERSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 1/2 PLA service while digging for sewer repair. No USA.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2023-08-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 42 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CHI CONSTRUCTION | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party damage to 1/2 CTS service, damaged by backhoe while trenching for water main. SCG crew altered service.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2023-08-31 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 48 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SOCALGAS | RIVERSIDE | CA | Y | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Company employee was conducting a leak investigation and pogoed through a PE service.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2023-03-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JOSE VALENCIA | RIVERSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | homeowners contractor installing wall struck properly marked plastic service, paint and flags, with backhoe.
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2023-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 42 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | PLYCO CORP | JURUPA VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Upon arrival 1/2 IPS Service was damaged by a jack hammer
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2023-12-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | BUILDING PROJECTS MJ INC | BELL GARDENS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | NA
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2023-11-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RUFUS BUILDING SERVICE | FALLBROOK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Digging with auger and hit service
Southern California Gas Company | N | RIVERSIDE | RIVERSIDE | 2023-05-18 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 48 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 14 |  | BORDEN EXCAVATING | CALIMESA | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 2 PLA main by 3rd party contractor while excavating to replace water main. Dug prior to having marks. Foreman stated that he did not see that there was a 2 PLA main in his plans. Ticket was originally closed out with No Delineation. Contractor failed to update ticket properly.
Southern California Gas Company | N | RIVERSIDE | SAN JACINTO | 2023-01-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 42 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ALSPHALT FABRIC & ENGINEERING | SIGNAL HILL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Approved. Contractor damaged service and failed to utilize caution while exposing.
Southern California Gas Company | N | RIVERSIDE | SAN JACINTO | 2023-01-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 23 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | A E SPORT ATLHETIC | SIGNAL HILL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Approved. contractor hit line for 2nd time. did a PL cutback
Southern California Gas Company | N | RIVERSIDE | SAN JACINTO | 2023-04-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SUNNYDAY LANDSCAPE | SAN BERNARDINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Approved. No USA Called in.
Southern California Gas Company | N | RIVERSIDE | SAN JACINTO | 2023-05-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | PACIFIC UTILITY INSTALLATION | CORONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA, called in rush ticket after.
Southern California Gas Company | N | RIVERSIDE | SAN JACINTO | 2023-10-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LYDIA OLMELO | SAN JACINTO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner digging post holes for fence struck 1/2 service. No USA
Southern California Gas Company | N | RIVERSIDE | SAN JACINTO | 2023-05-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | 4 WEST PIPELINE INC | CANYON LAKE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Approved. Developer hit Stub off main left too long, RCC Crew went back out to job and did proper ABD at SMC
Southern California Gas Company | N | RIVERSIDE | SAN JACINTO | 2023-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | TOM PHILLIPS | SAN JACINTO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner cut through service while removing a tree. No USA
Southern California Gas Company | N | RIVERSIDE | TEMECULA | 2023-01-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 41 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | COLONIAL ELECTRIC CO | CHINO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged a gas service while trenching with backhoe
Southern California Gas Company | N | RIVERSIDE | TEMECULA | 2023-07-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 55 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | A CUT ABOVE GRADING INC | MURRIETA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | NA
Southern California Gas Company | N | RIVERSIDE | TEMECULA | 2023-05-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | PEACE OF MIND ELEC. | TEMECULA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third Party Contractor damaged marked and exposed 1/2PLA service with shovel.
Southern California Gas Company | N | RIVERSIDE | TEMECULA | 2023-05-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CASS ARRIETA | TEMECULA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | N/A
Southern California Gas Company | N | RIVERSIDE | TEMECULA | 2023-10-18 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | GOTHIC LANDSCAPE | RIVERSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged 2 PLA main with mini-excavator
Southern California Gas Company | N | RIVERSIDE | TEMECULA | 2023-08-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | REYLENN PROPERTIES | SOLANA BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1 PLA stub with backhoe. No USA was requested.
Southern California Gas Company | N | RIVERSIDE | TEMECULA | 2023-02-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | TELLEZ ASPHALT PAVING COMPANY | LAKE ELSINORE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third Party Contractor damaged 1/2PLA branch service while hand digging. NO USA was called.
Southern California Gas Company | N | RIVERSIDE | TEMECULA | 2023-11-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CHAMBERLIN BACKHOE SERVICE | PLACENTIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | RIVERSIDE | TEMECULA | 2023-03-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 49 | 49 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | GARY SCHWARZENBACK | MURRIETA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged a 1/2 plastic branch with a post hole digger. No USA at the time of damage.
Southern California Gas Company | N | RIVERSIDE | TEMECULA | 2023-12-27 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | KYLE GALLAGHER | TEMECULA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 2 PLA main with mini-excavator while digging for sewer. No USA was called in.
Southern California Gas Company | N | RIVERSIDE | WILDOMAR | 2023-02-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ZIMPRICH ENGINEERING, INC | IRVINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Locator marked service using company measurements and GIS showed a straight service. Damage occurred because the service roped around the yard instead of continuing to go straight.
Southern California Gas Company | N | RIVERSIDE | WILDOMAR | 2023-06-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | KIP INC | MURRIETA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | USA was good at the location and marked correctly
Southern California Gas Company | N | RIVERSIDE | WILDOMAR | 2023-11-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 53 | 46 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | JOSH HERNANDEZ | VISTA | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | No delineations
Southern California Gas Company | N | RIVERSIDE | WILDOMAR | 2023-06-05 | Third party excavation damage | Main | Polyethylene Pipe | Miscellaneous/Other | 2 | 59 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | EARTHWORKS | JURUPA VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA at the time of incident. According to the notes 52'' of 2 were abandoned due to pipe being discovered being shallow. New install to be planned.
Southern California Gas Company | N | RIVERSIDE | WILDOMAR | 2023-11-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 13 |  | STEPHAN ARMENDARIZ | CORONA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Damaged unmarked 1 PLA service while boring
Southern California Gas Company | N | RIVERSIDE | WILDOMAR | 2023-10-31 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | H7 CONTRACTING & ENGINEERING | MURRIETA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was digging with a backhoe and damaged gas.
Southern California Gas Company | N | RIVERSIDE | WILDOMAR | 2023-01-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 41 | 41 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | TOVEY SHULTZ CONSTRUCTION | LAKE ELSINORE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | A contractor was working at this location without a valid USA ticket. They damaged a 1/2 plastic CTS stub with hand tools. LCT Solis made repairs and capped the stub.
Southern California Gas Company | N | RIVERSIDE | WILDOMAR | 2023-11-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | FAIRCHILD PLUMBING | ONTARIO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged a 1/2 plastic stub while scraping dirt with the backhoe
Southern California Gas Company | N | RIVERSIDE | WILDOMAR | 2023-10-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | FERREIRA CONSTRUCTION | RANCHO CUCAMONGA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged 1/2 CTS PLA service with hand tools
Southern California Gas Company | N | RIVERSIDE | WILDOMAR | 2023-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | FERREIRA CONSTRUCTION | RANCHO CUCAMONGA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor claims to have damaged a plastic service while hand digging.
Southern California Gas Company | N | RIVERSIDE | WILDOMAR | 2023-05-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 51 | 48 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BANYON CONSTRUCTION | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Approved. No USA
Southern California Gas Company | N | RIVERSIDE | WINCHESTER | 2023-03-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | JEFF CARPENTER INC. | PERRIS | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | approved, damage prevention made some changes.
Southern California Gas Company | N | RIVERSIDE | WINCHESTER | 2023-07-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | DOUGLAS PIPELINE | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA Called in.
Southern California Gas Company | N | RIVERSIDE | WINCHESTER | 2023-10-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 54 | 48 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | COLBY PACKER PACIFIC SHORES | CORONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | RIVERSIDE | WINCHESTER | 2023-07-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 55 | 51 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | HORIZON BACKHOE | WINCHESTER | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | SCG contractor NPL damaged a plastic gas service while potholing it with a shovel for a replacement.
Southern California Gas Company | N | RIVERSIDE | WINCHESTER | 2023-09-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 53 | 48 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ALVIZIA CORPORATION | SAN DIEGO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA
Southern California Gas Company | N | RIVERSIDE | WINCHESTER | 2023-02-10 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | PACIFIC PRODUCTION PLUMBING | RIVERSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third Part Contractor damaged 2PLA gas main with backhoe. No DIG ALERT ticket was called in.
Southern California Gas Company | N | RIVERSIDE | WINCHESTER | 2023-10-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ACTION POWER | LAKE FOREST | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor installing temp power poles failed to notify USA and struck PLA service stub.
Southern California Gas Company | N | RIVERSIDE | WINCHESTER | 2023-07-06 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 55 | 52 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | DOUGLAS PIPELINE | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA called in and contractor being negligent.
Southern California Gas Company | N | RIVERSIDE | WINCHESTER | 2023-04-03 | Third party excavation damage | Main | Polyethylene Pipe | Grader/Scraper | 4 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JMI TAYLOR MORRISON HOMES | RIVERSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third Party Contractor damaged 4 inch pla main with a loader while grading. No dig alert was called in.
Southern California Gas Company | N | SAN BERNARDINO | BLOOMINGTON | 2023-03-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | C P CONSTRUCTION CO INC | UPLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | EMPLOYEE FOUND DAMAGED 1/2 PLA CTS SERVICE
Southern California Gas Company | N | SAN BERNARDINO | BLOOMINGTON | 2023-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | NK DEMOLITION | SAN BERNARDINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner installed plastic garden boarder in the front yard. Installed long plastic spikes to secure the plastic boarder and one of the spike punctured our service. Customer did not call USA.
Southern California Gas Company | N | SAN BERNARDINO | BLOOMINGTON | 2023-03-28 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 55 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 57 |  | C P CONSTRUCTION | ONTARIO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | C P construction excavating on santa ana ave to install water utility and damaged 2 PLA, was not marked for this intersection. -M.Horne DPA.
Southern California Gas Company | N | SAN BERNARDINO | BLOOMINGTON | 2023-12-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NK DEMOLITION | SAN BERNARDINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit plastic service with backhoe
Southern California Gas Company | N | SAN BERNARDINO | BLOOMINGTON | 2023-12-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | RICHMOND HOMES | SAN BERNARDINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was demoing house and hit plastic service
Southern California Gas Company | N | SAN BERNARDINO | BLOOMINGTON | 2023-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | MCKINNEY CONSTRUCTION | FONTANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit 2 plastic main with backhoe while installing water line
Southern California Gas Company | N | SAN BERNARDINO | BLOOMINGTON | 2023-12-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | JIM WILLIAMS | BLOOMINGTON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While removing a tree from the property the homeowner''s contractor hit the branch service to their own home. They did not call USA prior to the damage.
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2023-09-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  |  | NA | CA STATE PRISON | CHINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Chino State prison maintenance crew was digging with a backhoe and never called in a USA and damaged our 4 plastic service.
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2023-12-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | RICHMOND HOMES | CHINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA was called in by contractor digging. Contractor hit 1/2 service.
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2023-10-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | SUPERIOR MASONRY | COLTON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor building wall hit plastic service
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2023-12-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | WORKMAN CONSTRUCTORS | CORONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA was called in by contractor digging. Contractor hit 1/2 service.
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2023-12-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | WHITE HOUSE SANITATION | PERRIS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hand digging over new septic pit site with shovel when they hit our 1/2 service line.
Southern California Gas Company | N | SAN BERNARDINO | CHINO | 2023-12-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 2 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | OPTIMUM INC | BLOOMINGTON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Telecommunications company was working to install a fiber conduit when they struck an un-marked 2 service stub at a vacant empty lot at gutter plate location.
Southern California Gas Company | N | SAN BERNARDINO | CHINO HILLS | 2023-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | CHARLES FLYNN | CHINO HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer was trenching for footing to build a wall with backhoe, when he struck 1/2 CTS service.
Southern California Gas Company | N | SAN BERNARDINO | CHINO HILLS | 2023-12-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | LUANS CONSTRUCTION INC | CHINO HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Installing drain lines on his property. No USA was called. Line strike on 1/2 plastic service. Service line was damaged by a shovel.
Southern California Gas Company | N | SAN BERNARDINO | CHINO HILLS | 2023-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JS PIPELINE INC | CHINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA was called in and contractor hit service line.
Southern California Gas Company | N | SAN BERNARDINO | CHINO HILLS | 2023-07-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | INTERNATIONAL LINE BUILDERS | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | All USA marks were good, contractor hit 1/2 service with shovel.
Southern California Gas Company | N | SAN BERNARDINO | COLTON | 2023-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | IRVINE FENCE CO | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit plastic service digging for footings of chain link fence
Southern California Gas Company | N | SAN BERNARDINO | COLTON | 2023-07-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | JOHN HINSLEY | ONTARIO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party septic tank contractor was digging trench with heavy equipment. Contractor claims 1/2 service pipe damage was done with shovel when performing digging operations.
Southern California Gas Company | N | SAN BERNARDINO | COLTON | 2023-08-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1.25 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | RC HEDLEY CONSULTING | HIGHLAND RANCH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor removing concrete from parking lot damaged steel service
Southern California Gas Company | N | SAN BERNARDINO | COLTON | 2023-05-30 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | BORDEN EXCAVATING | CALIMESA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | svc was hit and not called in.
Southern California Gas Company | N | SAN BERNARDINO | COLTON | 2023-05-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 50 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 22 |  | OPTIMUM | BLOOMINGTON | CA | N | Y | Yes | No | No | Yes | No | Yes | No | Spoke with Ernesto with Optimum, crew began excavation before legal start time and date
Southern California Gas Company | N | SAN BERNARDINO | COLTON | 2023-09-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | PHILLIP SMITH | COLTON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor failed to call for USA and when digging large hole to do some electrical work, they hit the 1/2 plastic service line in private property with a shovel.
Southern California Gas Company | N | SAN BERNARDINO | COLTON | 2023-06-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PREMIER POOLS AND SPAS | ONTARIO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor trenching for pool gas line
Southern California Gas Company | N | SAN BERNARDINO | COLTON | 2023-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 0.75 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GERARDO FLORES | COLTON | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was grading with a bobcat and hit the 3/4 service. LCT clamped the service and put it in for replacement.
Southern California Gas Company | N | SAN BERNARDINO | COLTON | 2023-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ANDREW MODESTI | COLTON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer was trenching to install wall in private property when he struck and damaged 1/2 PE service
Southern California Gas Company | N | SAN BERNARDINO | COLTON | 2023-03-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 3 |  | JOSE RENTERIA | COLTON | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per Conversation with LCT, homeowner was grading property hillside with a bobcat machine and damaged gas service. -M.Horne DPA.
Southern California Gas Company | N | SAN BERNARDINO | COLTON | 2023-05-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 55 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | BORDEN EXCAVATING INC | CALIMESA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While grinding street contractor hit plastic service inserted into steel casing contractor did not pothole by hand
Southern California Gas Company | N | SAN BERNARDINO | COLTON | 2023-08-30 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | TITLE WAVE ENTERPRISES | COLTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 1 plastic service
Southern California Gas Company | N | SAN BERNARDINO | CRESTLINE | 2023-10-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | FAITH ELECTRIC | REDLANDS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was potholing for gas service and struck it with shovel.
Southern California Gas Company | N | SAN BERNARDINO | CRESTLINE | 2023-09-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | KIRKLY CONSTRUCTION | REDLANDS | CA | N | Y | Yes | Yes | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | SAN BERNARDINO | CRESTLINE | 2023-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | RAYS PLUMBING | CRESTLINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | plumber/contractor failed to maintain locate marks in area of work. Flags and marks removed.
Southern California Gas Company | N | SAN BERNARDINO | CRESTLINE | 2023-06-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | TONY CARPENTRY | RUNNING SPRINGS | CA | N | N | Yes | Yes | No | Yes | No | Yes | Yes | contractor worked ahead of the start time for the USA / work performed. Locator arrived to mark the area and found the service damaged.
Southern California Gas Company | N | SAN BERNARDINO | CRESTLINE | 2023-12-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Augur | 0.75 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | PRO ENERGY SERVICES | RIVERSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Auguring for new anchor install for power pole and hit 3/4 steel service. No valid USA
Southern California Gas Company | N | SAN BERNARDINO | CRESTLINE | 2023-09-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MICK HILL ENTERPRISES | CEDARPINES PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA was called for this work. service struck while grading for driveway replacement.
Southern California Gas Company | N | SAN BERNARDINO | CRESTLINE | 2023-05-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MIKE GUSTAFSON | SAN BERNARDINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damage. contractor hit service while hand digging with shovel. no valid USA
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2023-08-25 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 7 |  | TE ROBERTS INC | IRVINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit 2 plastic main with backhoe while installing water line
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2023-10-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ALARCON SONS INC | BALDWIN PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2023-10-19 | Third party excavation damage | Main | Polyethylene Pipe | Grader/Scraper | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | MILLIE AND SERVERSON GENERAL CONTRACTORS | LOS ALAMITOS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Grading company severed 2 plastic main
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2023-07-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | TA RIVARD INC | JURUPA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit plastic service with backhoe
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2023-11-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RAY HUERTA | RIVERSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party plumbing contractor was working to install lines when they hit a 1/2 PE service line with backhoe. No USA.
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2023-09-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | EC PLUMBING | AZUSA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Sewer contractor was replacing service line and using mini excavator to dig trench, when they struck the 1 gas service to the building. The contractor did not have valid USA or delineations.
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2023-06-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | PATRITTI LANDSCAPING | FONTANA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Lanscaping company damaged 1 plastic service
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2023-10-02 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NA | FONTANA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging to make sewer repairs and hit our 1/2 IPS service with a shovel. No USA was called.
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2023-08-07 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 32 | 32 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 52 |  | AC SPRAGGINS | ONTARIO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging to extend communications conduit when they hit our 2 plastic main. No USA
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2023-03-27 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | APPLE VALLEY CO | APPLE VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | they assumed they knew were existing dry utilities were in the area, excavating with backhoe and damaged 2 PL without a USA ticket
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2023-09-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | JGINGER MASONRY | RIVERSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 1/2 plastic service
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2023-05-16 | Third party excavation damage | Main | Material not known | Backhoe/Trackhoe | 0 | 50 | 50 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | DANIEL RAMIREZ | FONTANA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Had a conversation with the developer Robert Soto, Legacy Plumbing Cesar Navarro and Ramfam Demo Daniel Ramirez to gather information on this damage. Legacy Plumbing hired RamFam Demo to perform excavation to install new sewer facility. Ramfam did not have a USA ticket and damaged 2 PLA using a backhoe but did not result in gas blowing or leak. I contacted Daniel Ramirez and stated a USA ticket is required by law prior to starting excavation.
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2023-06-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | J AND J CUSTOM FAB | RIALTO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | OHS crew arrived to find broken and blowing. 3rd party contractor was digging to install new fence and hit our 1/2 svc with shovel. OHS crew made repairs using 1'' of 1/2 pla and 2 couplings.
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2023-03-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | JUAN VALENCIA | FONTANA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer digging in yard of his home and damaged service
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2023-02-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | WILSON A D INC | NORCO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | 1/2 inch plastic ips service damaged with damaged with the backhole while excavating DAMAGED WITH BACKHOE WHILE EXCAVATING FOR ELECT INSTALL.
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2023-12-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | INTERIOR DEMOLITION INC | NEWHALL | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Gas service hit by crew
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2023-09-20 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | FONTANA WATER COMPANY | FONTANA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Fontana Water digging with backhoe to make water main repairs hit our 2 main causing broken and blowing. USA was not called.
Southern California Gas Company | N | SAN BERNARDINO | FONTANA | 2023-05-11 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 55 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 2 |  | T E ROBERTS | IRVINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged 2 plastic main with backhoe Per conversation with TE Roberts Frank Romero, backhoe operator damaged 2 facility. Contractors did not use hand tools to pothole prior to using power equipment and did not keep power equipment out of the tolerance zone. -M.Horne DPA.
Southern California Gas Company | N | SAN BERNARDINO | GRAND TERRACE | 2023-06-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HERMAN WEISSIKER | RIVERSIDE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Un-marked stub due to no record on GIS or maps for this location. So Cal Gas locator marked NO GAS for this location. Area was delineated only on one side of street not going into side of 2 plastic main. No record of this stub to allow locator possibility to mark location of forgotten stub.
Southern California Gas Company | N | SAN BERNARDINO | GREEN VALLEY LAKE | 2023-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | GREEN VALLEY LAKE MUTUAL WATER | GREEN VALLEY LAKE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor cut into service casing and plastic with Sawzall.
Southern California Gas Company | N | SAN BERNARDINO | GREEN VALLEY LAKE | 2023-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | DAMON FRIEDMAN | GREEN VALLEY LAKE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was using sawzall to cut roots out of the way and cut into the 3/4 steel line.
Southern California Gas Company | N | SAN BERNARDINO | HIGHLAND | 2023-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | EFI ENGINEERING | TUSTIN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Svc hit well boring
Southern California Gas Company | N | SAN BERNARDINO | HIGHLAND | 2023-05-31 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 54 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ONEWAYDRILLING | WHITTIER | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 2 main while augering for soil samples. No USA.
Southern California Gas Company | N | SAN BERNARDINO | HIGHLAND | 2023-04-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SKL CONSTRUCTION | RANCHO CUCAMONGA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer dug with no USA
Southern California Gas Company | N | SAN BERNARDINO | HIGHLAND | 2023-05-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HERMAN WEISSKER | JURUPA VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Third party contractor hand digging for new electrical conduit and damaged mismarked 1/2 PLA facility. -M.Horne DPA.
Southern California Gas Company | N | SAN BERNARDINO | HIGHLAND | 2023-08-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HAMPTON TEDDER | MONTCLAIR | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Svc hit
Southern California Gas Company | N | SAN BERNARDINO | HIGHLAND | 2023-07-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | DOUG JONES | HIGHLAND | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit exposed marked gas service. Service was marked after the prior damage.
Southern California Gas Company | N | SAN BERNARDINO | HIGHLAND | 2023-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | JACOBSSON INC | PALM DESERT | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | Per conversation with Jacobsson Foreman Jesus Oseguera, crew was excavating using an excavator, damaged 1 PLA and then shut the gas valve off. After verifying delineations and measuring with Jesus, crew was excavating outside of their delineated work area. Crew also did not pothole facility prior to using power equipment nor keep power equipment out of the tolerance zone. -M.Horne DPA.
Southern California Gas Company | N | SAN BERNARDINO | HIGHLAND | 2023-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ETHAN INVESTMENTS | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Property owner was demoing the house and was digging out what looked to be a large planter and came in contact with the gas service.
Southern California Gas Company | N | SAN BERNARDINO | JURUPA VALLEY | 2023-08-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | WEST VALLEY WATER DISTRICT | RIALTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Water company damaged 1 plastic service with backhoe
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2023-05-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | GREGORY BRENNAN | LAKE ARROWHEAD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was digging with hand tools to install a water service to his house when he struck our 1/2 cts service pipe near the riser.
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2023-10-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  | 1 |  | FAITH ELECTRIC | REDLANDS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Power pole replacement. Contractor was auguring down and struck service. Had a valid USA.
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2023-12-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | DAVID FURGESON | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit line with shovel
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2023-06-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | GARETT MOREAU | LAKE ARROWHEAD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was landscaping/gardening and hit our 1/2 CTS svc with a pick. OHS crew made repairs with piece of CTS and two couplings.
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2023-09-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CALIFORNIA BUILDERS | REDLANDS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging to install awning/driveway and struck gas service. No USA
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2023-09-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CHUCK MURPHY COMPANY | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor struck service with shovel, no valid usa.
Southern California Gas Company | N | SAN BERNARDINO | LAKE ARROWHEAD | 2023-05-30 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CARLOS ESPARZA | LANCASTER | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damage by third party contractor. Operator snagged 3/4'''' steel service with backhoe.
Southern California Gas Company | N | SAN BERNARDINO | LOMA LINDA | 2023-10-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | OWNER | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Digging to make sewer repairs and while trying to remove tree roots they hit our 1/2 gas svc. No USA was called.
Southern California Gas Company | N | SAN BERNARDINO | LOMA LINDA | 2023-04-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CEASER ESPINOZA | WILDOMAR | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per Conversation with Cesar Espinoza, he was hired by a Rebecca Turnerto perform the work. They were digging using hand tools and damaged the 1/2 PLA. No USA Ticket and per Cesar there is no need to have one
Southern California Gas Company | N | SAN BERNARDINO | MONTCLAIR | 2023-07-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | KYLE GILMORE CONSTRUCTION CO | MONTCLAIR | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA was called in and contractor hit 1 service with backhoe.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2023-06-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | TILDEN COIL | RIVERSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was digging with a backhoe at the school and didn''t hand expose our marked gas service and hit it.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2023-10-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HIGH LIGHT ELECTRIC | COLTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party company damaged our 1-inch plastic service with a mini excavator. They had a valid USA and our marks were correct however the 3rd party electric company failed to hand expose our service.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2023-05-07 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SEVERIANO MEZA OTAZ | ONTARIO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer was installing new sewer line and was cutting tree roots with reciprocating saw when he cut into 3/4 steel service. Crew clamped service and eliminated leak.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2023-09-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NA | ONTARIO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner had worker digging a trench for a new sewer line going back to an addition being built when he struck the gas line with a shovel cutting it completely through this was a 1/2 service line.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2023-12-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NAHID LACIURA | BALDWIN PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | All USA marks were good. Contractor hit gas service
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2023-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | CAL WEST UNDERGROUND INC | NORCO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party failed to pothole prior to boring and damaged our 1/2 IPS plastic service.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2023-05-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NORSTAR ENGINEERING | RANCHO CUCAMONGA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | ALL USA marks were good, contractor did not expose gas line.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2023-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | INTERNATIONAL LINE BUILDERS | JURUPA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | SoCal Edison''s contractors damaged our 1/2 plastic service with a shovel while potholing. Our facility was marked correctly.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2023-11-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  | 1 |  | CT&T CONCRETE PAVING | POMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | USA marks were good. Did not hand expose 3/4 service before digging with backhoe
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2023-05-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | PACIFIC UTILITIES INSTALLATION | CORONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd partydamaged 1 inch stub with mini excavator
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2023-10-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ZEN HOME DESIGN INC | WALNUT | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1/2 svc. No USA
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2023-09-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | OCHOAS CUSTOME CONTRUCTION INC | SANTA FE SPRINGS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working for homeowner to install electrical line to back of property damaged 1/2 plastic service line while excavating after having line exposed with no valid USA ticket on hand.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2023-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | JOSE VILLEGAS | ONTARIO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | OHS crew arrived to find 3rd party contractor had stepped on our plastic svc dislodging the coupling fusion causing leak. Crew made repairs using 1'' of plastic and two couplings
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2023-07-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | HOMEOWNER | CORONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA was called in and contractor hit 1/2 IPS service.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2023-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | CIVIL WEST | RIVERSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | ALL USA marks were good, contractor hit 2 service with backhoe.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2023-10-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  | 2 |  | HP COMMUNICATIONS INC | FONTANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | ALL USA marks were good, contractor hit our gas service with backhoe.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2023-12-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DYNAMIC GENOVAL CONSTRUCTION | WHITTIER | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged a 2-inch plastic service while digging to fix leaking water with a mini excavator. No USA.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2023-05-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ILB INC | JURUPA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | ILB contractor installing electrical hit our gas service with shovel. OHS crew made plastic repair fusing two couplings and piece of plastic svc.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2023-07-31 | Third party excavation damage | Main | Polyethylene Pipe | Grader/Scraper | 2 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CW DRIVER | ANAHEIM | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Land owner was grading and damaged an unknown stub. Land owner had a valid USA.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2023-07-25 | Third party excavation damage | Main | Polyethylene Pipe | Directional Drilling | 2 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 3 |  | HP COMMUNICATIONS | FONTANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party communication company was pulling back their pipe with a boring machine and their bore head fell off and damaged our facility. Correct markings
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2023-04-24 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | CAL WEST UNDERGROUND, INC | NORCO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | New business development site. 3rd party excavation company damaged 2 PLA main while excavating to expose stub for future tie-in location in private utility easement location.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2023-11-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | INTERNATIONAL LINE BUILDERS | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | All USA marks were good. contractor hit our gas service with shovel.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2023-08-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | LOMELA BACKHOE CO | EASTVALE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to maintain our marks and damaged our 1/2 plastic service while installing a sewer line. Our marks were right on.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2023-06-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RANCHO WEST LANDSCAPING | MURRIETA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA was called in and contractor hit gas service.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2023-08-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  |  | NA | RICHARD LOPEZ CONSTRUCTION INC | CORONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Developer was digging with no USA and damaged our 1 plastic service with hand tools. Crew altered service and made permanent repairs.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2023-05-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | CAL WEST UNDERGROUND | NORCO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Cal West was trenching and damaged our facility with a shovel. Cal West did not have a USA.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2023-06-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CAL WEST UNDERGROUND | NORCO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA was called in and contractor hit gas service.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2023-07-26 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SOCALGAS | ONTARIO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 1/2 plastic service tee damaged by 2nd party contractor working with company crew main replacement in progress. Crew was able to make permanent repairs with minimal effect to the public.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2023-05-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | BCB CONSTRUCTION | RANCHO CUCAMONGA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged our service with a shovel and did not call in a USA.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2023-07-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | AC PROFESSIONAL ELECTRIC | SAN JACINTO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA was called in and contractor hit 2 PLA service.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2023-01-17 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | CAL WEST UNDERGROUND INC | NORCO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged our facility and did not have a valid USA.
Southern California Gas Company | N | SAN BERNARDINO | ONTARIO | 2023-12-27 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | KB HOMES | WILDOMAR | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA. Contractor hit 2 PLA main.
Southern California Gas Company | N | SAN BERNARDINO | PINON HILLS | 2023-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MARILYN BELLOSO | PINON HILLS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | SVC hit with shovel
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2023-03-16 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 2 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  |  | NA | CONSTRU ONE INC. | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor had a valid USA ticket but did not expose the 2 PLA main, ALL gas marks were on there marks.
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2023-03-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CUCAMONGA VALLEY WATER DISTRICT | RANCHO CUCAMONGA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | All Usa Marks Were Good. Contractor Hit 1 Gas Service.
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2023-10-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 2 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | TRI-COUNTY DEV & CONSTRUCTION | RIVERSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party communication company was boring with no USA and bored into our 2 plastic service.
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2023-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | MUNOZ EXCAVATION AND GRADING | SAN DIMAS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1/2 IPS service by backhoe. No USA
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2023-09-15 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | R&I COMMUNICATIONS | BLOOMINGTON | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | ALL USA marks were good, contractor hit 2 PLA main with excavator.
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2023-12-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | LAKHA WAHLA | RANCHO CUCAMONGA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged service. No USA
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2023-07-26 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | ARIZONA PIPELINE | CORONA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Crew was excavating over existing service to remove rocks and struck service.
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2023-05-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MOTIVE ENERGY TELECOMMUNICATIONS GROUP INC | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | ALL USA marks were GOOD, contractor hit gas line with shovel.
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2023-09-28 | Operator excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 19 |  | SOCALGAS | CHINO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While open trenching for a main replacement, the line was struck with a backhoe causing a release of gas.
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2023-05-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | AMERICAN CIVIL CONSTRUCTION | APPLE VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA was called in and contractor hit gas line with shovel.
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2023-07-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | RANCHO CUCAMONGA VALLEY WATER | RANCHO CUCAMONGA | CA | N | Y | Yes | No | No | No | No | Yes | Yes | Rancho Cucamonga Water damaged our 1/2 plastic service with a backhoe and had no valid USA. Their ticket was expired.
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2023-02-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 0.5 | 60 | 55 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | TCDC INC | RIVERSIDE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | All Times met. Telecom contractor damaged line. Damage repaired no hazard upon leaving on site.
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2023-08-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | CONTRACTOR WORKING FOR HOME OWNER | RANCHO CUCAMONGA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party was digging in the yard with a shovel and no USA on file and damaged our 1/2 plastic service.
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2023-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | CONSTRU ONE INC | ONTARIO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NO USA was called in, contractor hit 1/2 CTS service with shovel.
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2023-11-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ALI ALAOBAIDI | RANCHO CUCAMONGA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA was called in. Contractor hit service with backhoe.
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2023-02-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | VICTOR MANUEL JR BRICENO | UPLAND | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The developer was building a fence and their USA ticket expired 4 months prior to Contruction taking place. They never updated their ticket and ended up damaging our 1/2 ips plastic service with a backhoe. Existing marks faded away and the developer removed concrete and by not extending and updating the USA ticket, they had no idea where our SCG line was.
Southern California Gas Company | N | SAN BERNARDINO | RANCHO CUCAMONGA | 2023-03-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | WILLYS POOL | RANCHO CUCAMONGA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor trenching in order to install pool line. Damaged existing gas line with shovel. Contractor did not have a valid USA ticket.
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2023-09-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CEM CONSTRUCTION CORPORATION | MONTEBELLO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upon arrival 1/2 IPS Service was damaged by contractor for homeowner.
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2023-06-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ES FENCING | CANYON LAKE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Unknown
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2023-05-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MATICH CORP | SAN BERNARDINO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Spoke with EE to check corner lots.
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2023-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SPARTAN CONCRETE AND ASPHALT CUTTING INC. | NORTH PALM SPRINGS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Unknown
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2023-09-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CEM CONTRACTOR | MONTABELLO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | NA
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2023-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CEM CONSTRUCTION CORPORATION | MONTEBELLO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hit service before potholing
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2023-03-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | ASPLUNDH CONSTRUCTION LLC | BUENA PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per conversation with Asplundh Scott Gilman, crew was using a manual ground rod driver for power pole and damaged service, no USA ticket. M.Horne-DPA.
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2023-10-02 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 47 |  | CEM CONSTRUCTION CORPORATION | MONTEBELLO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | NA
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2023-04-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | PBC COMPANY | BREA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per Conversation with PBC Foreman David Beltran, crew was excavating on April 26th sometime in the afternoon and damaged the 1 PLA bent the facility back taped it and did not notify his supervisor 811 911 or the developer for WERMERS, Charlie Pick until the morning of April 27th. PBC was excavating at the time without a valid USA ticket. -M.Horne DPA.
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2023-01-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | MICHAEL PERRY | REDLANDS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Hit with shovel Per Conversation with homeowner, removing posts and hit service- Michael Horne-DPA.
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2023-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CEM CONSTRUCTION CORPORATION | MONTEBELLO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Service hit with backhoe
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2023-08-14 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 3 |  | JOSE BERNAL WEST COAST ARBORIST INC | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor hit plastic service
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2023-09-06 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  | 3 |  | CEM CONSTRUCTION CORPORATION | MONTEBELLO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Trench failed which caused 2 main to break
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2023-10-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CEM CONSTRUCTION CORPORATION | MONTEBELLO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Crew was backing filling
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2023-09-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | CEM CONSTRUCTION CORPORATION | MONTEBELLO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Crew hit service not calling after not finding in pothole
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2023-11-09 | Third party excavation damage | Main | Polyethylene Pipe | Trencher | 2 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RESIDENTIAL ELECTRICAL SYSTEMS INC | IRVINE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Crew hit 2in main with trencher
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2023-03-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ORANGE TRENCHING & PAVING INC | SANTA ANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Crew hit svc potholing Per conversation with Arcelia, crew was hand digging around exposed gas service when damaged occurred, failed to protect exposed line. -Michael Horne DPA.
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2023-03-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ORANGE TRENCHING & PAVING INC | SANTA ANA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | approved
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2023-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MERLIN JOHNSON CONSTRUCTION INC | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Crew hit svc potholing
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2023-05-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DG CONSTRUCTION SERVICES | YUCAIPA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Svc was hit by Mini EX Per conversation with David Genovese, he was excavating using a mini excavator and damaged 1/2 PLA. David states he is aware of 811 but did not think of calling in to obtain a USA ticket
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2023-05-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MARK VANVOORTHUYSEN | MENTONE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Per conversation with Mark Vanvoorthuysen, he was hand digging using a shovel and cut through the 1/2 PLA facility. -M.Horne DPA.
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2023-03-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ROBERT BREAZILE | REDLANDS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | approved
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2023-05-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HINKLEY AND ASSOCIATES | YUCAIPA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Per conversation with Tyler Dunn, crew was excavating using a mini excavator and ripped through the 1/2 PLA. We discussed safe excavation practices and CA 811 excavation laws. Explained to Tyler, power equipment is prohibited within SCG tolerance zones and hand tools are to be used. M.Horne-DPA.
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2023-05-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MDP MASONRY INC | RIALTO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | third party contractor was excavating with a mini excavator, without a USA ticket and damaged the 1/2 PLA. Crew arrived, controlled gas and made permanent repairs to the 1/2 svc.
Southern California Gas Company | N | SAN BERNARDINO | REDLANDS | 2023-08-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | GODDARDS NAVCO | SAN BERNARDINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damage to 1/2 CTS service, damaged by backhoe while trenching for water main. SCG crew altered service.
Southern California Gas Company | N | SAN BERNARDINO | RIALTO | 2023-07-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ARIZONA PIPELINE | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | NA
Southern California Gas Company | N | SAN BERNARDINO | RIALTO | 2023-02-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | DAVID HILL | BEAUMONT | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | PER CONVERSATION WITH OPERATOR RAY CABRAL, HE WAS HIRED BY DAVID HILL TO PERFORM EXCAVATION AT RESIDENCE. RAY ASSUMED GAS WAS NOT IN CONFLICT AND DID NOT FEEL THE FACILITY WITH HIS BUCKET IN THE GROUND. RAY IS UNFAMILAR WITH CA 811 LAWS, DID NOT HAVE USA TICKET AND HAS NEVER CALLED 811 TO OBTAIN ONE.
Southern California Gas Company | N | SAN BERNARDINO | RIALTO | 2023-08-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 1 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | XPRESS CONCRETE INC | COVINA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit plastic service
Southern California Gas Company | N | SAN BERNARDINO | RIALTO | 2023-08-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Augur | 1 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | XPRESS CONCRETE INC | COVINA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor installing meter guard hit plastic service
Southern California Gas Company | N | SAN BERNARDINO | RIALTO | 2023-07-05 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | PACIFIC UTILITY INSTALLATION INC | ANAHEIM | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party damage. Pacific Utility Installation severed 2 PLA main digging to install street lighting.
Southern California Gas Company | N | SAN BERNARDINO | RIALTO | 2023-10-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HILLCREST CONTRACTING | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | NA
Southern California Gas Company | N | SAN BERNARDINO | RIALTO | 2023-07-26 | Third party excavation damage | Miscellaneous/Other | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | CALAT DID | FONTANA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | OHS crew arrived to find broken and blowing due to 3rd party contractor hitting our svc while digging with backhoe to repair broken sewer.
Southern California Gas Company | N | SAN BERNARDINO | RIALTO | 2023-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 55 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | ARM CONSTRUCTION | RIVERSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor trenching for pool line damaged branch service
Southern California Gas Company | N | SAN BERNARDINO | RUNNING SPRINGS | 2023-07-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | FRANK SILVA | RUNNING SPRINGS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer failed to call for an active USA for the work of moving dirt to make a driveway. Their excavator severed the 1 plastic gas service line. Crew was able to squeeze and fuse in a new section.
Southern California Gas Company | N | SAN BERNARDINO | RUNNING SPRINGS | 2023-12-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | INDUSTRIAL ASPHALT | RUNNING SPRINGS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Exposing gas service and struck gas service. No valid USA.
Southern California Gas Company | N | SAN BERNARDINO | RUNNING SPRINGS | 2023-09-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DENNIS REICHENFELD | ARCADIA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Struck the 1/2 PE service. No USA was called for this work.
Southern California Gas Company | N | SAN BERNARDINO | RUNNING SPRINGS | 2023-10-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | BROTHER''S PLUMBING | RUNNING SPRINGS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor was trenching for new water service. Contractor struck service with shovel.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2023-07-31 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SAN BERNARDINO WATER COMPANY | SAN BERNARDINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | SVC hit by water company pulling svc with backhoe
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2023-11-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | EARTH WORKS | TRUCKEE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Crew ran over service
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2023-01-13 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | FRASSICA INC | CORONA | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Contractor dug prior to start time and damage 2PLA main while digging.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2023-03-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SAN BERNARDINO AIRPORT | SAN BERNARDINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Crew was using trencher machine to install fiber and damaged 1 PLA. - M.Horne-DPA.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2023-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | BRIDGE MANAGEMENT | SAN BERNARDINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was excavating over service and struck 1/2" CTS PLA service.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2023-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 35 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CONSTRUCTION ELECTRIC INC | RIVERSIDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was trenching near plastic service and caught it with the teeth of the backhoe. There was no active USA for that area, and no marks visible.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2023-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | SCOTT MCGARVEY | SAN BERNARDINO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner struck and pulled the 3/4 service. No USA was called for this work.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2023-07-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  |  | NA | GCC PIPELINE CONSTRUCTION | PERRIS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2023-03-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HENLEY''S PLUMBING AND AIR | CORONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumbing contractor doing emergency sewer work for homeowner failed to call for USA and damaged the 1/2 plastic service line. They were reminded of the necessity to call 811 before you dig.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2023-07-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | LEONEL VASQUEZ | SAN BERNARDINO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was grading his driveway to pour concrete when he struck our 1 service with hand tool.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2023-06-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | CITY OF SAN BERNARDINO WATER | SAN BERNARDINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Crew parked over USA mark didn''t see started digging with backhoe.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2023-08-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | EFI ENGINEERING | TUSTIN | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | NA
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2023-12-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | JUAN FRANCO | SAN BERNARDINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor damages 1/2 service while excavating to install fence. No USA on file.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2023-11-06 | Third party excavation damage | Main | Polyethylene Pipe | Boring Equipment | 3 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ALLEN LIGHTING | COLTON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Crew hit 3 in unknown stub with bore rig.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2023-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | OPTIMUM INC | BLOOMINGTON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | ETD had signal to long side main but svc cross the lot. SVC history has the same info as longside svc not short side
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2023-01-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HOME OWNER | NORWALK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | approved
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2023-04-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | GRASS MONKEY LANDSCAPE AND DEVELOPMENT INC | SAN BERNARDINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Per conversation with Juan crew was installing excavating with wooden stake and damaged plastic service unfamiliar with 811
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2023-02-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | CODIAK PLUMBING SERVICES | YUCAIPA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | approved
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2023-10-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | OPTIMUM INC | RIVERSIDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Crew potholing
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2023-09-01 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 25 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ROOTER HERO | POMONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2023-09-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 3 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | SAN BERNARDINO WATER COMPANY | SAN BERNARDINO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damage service
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2023-05-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | THREE D SERVICE COMPANY | POMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Per conversation with Justin Bruyneel, crew was excavating using an excavator and damaged 1/2 PLA. Contractors failed to pothole facility prior to using power equipment and they were aware of marks clearly visible in the street. -M.Horne DPA.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2023-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 2 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 6 |  | J & M LEYVA GENERAL ENGINEERING | RIVERSIDE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Both ETD and LCT had same locate that stooped at the back of loading dock for Home Depot. GIS said it was coming off another street.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2023-08-01 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Grader/Scraper | 1 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NA | SAN BERNARDINO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Excavator damaged service in casing. Pulled on casing causing service to sever.
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2023-09-05 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PACIFIC WEST UNDERGROUND | YUCAIPA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third Party contractor was using a backhoe to remove water and mud from the driveway apron area with a valid USA, however, they failed to request remarks as they removed then when performing road work. While in the process, the third party contractor struck a 2 main
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2023-10-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | NOVI ENVIRONMENTAL INC | LAKE ELSINORE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Crew hit unknown stub
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2023-09-07 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BNSF | REDLANDS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | NA
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2023-10-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | COMET ELECTRIC | CHATSWORTH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Crew hit service with shovel
Southern California Gas Company | N | SAN BERNARDINO | SAN BERNARDINO | 2023-03-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | ESTABAN OJEDA | SAN BERNARDINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged service using hand tool while excavating in his backyard and struck CTS service line.
Southern California Gas Company | N | SAN BERNARDINO | TWENTYNINE PALMS | 2023-01-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | 29 PALMS FENCING | TWENTYNINE PALMS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party Contractor was performing work for the customer installing a fence and struck the 1/2 CTS service with a post hole digger.
Southern California Gas Company | N | SAN BERNARDINO | TWENTYNINE PALMS | 2023-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 41 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | WONDER VALLEYFENCE | TWENTYNINE PALMS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit line while installing fence posts. Contractor didn''t have a USA and is fully responsible.
Southern California Gas Company | N | SAN BERNARDINO | TWIN PEAKS | 2023-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | THE STANDARD DESIGN GROUP NURSERIES | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working for homeowner hit gas service. No USA
Southern California Gas Company | N | SAN BERNARDINO | UPLAND | 2023-07-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | CITY OF UPLAND WATER DEPARTMENT | UPLAND | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Upland Water hit 1/2 IPS service while trying to expose it.
Southern California Gas Company | N | SAN BERNARDINO | UPLAND | 2023-08-22 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  |  | NA | MURRIETA DEVELOPMENT | TEMECULA | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | The developer called in a USA and never provided a delineation. The developer then damaged our 2 plastic main with a backhoe.
Southern California Gas Company | N | SAN BERNARDINO | UPLAND | 2023-03-03 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | JESUS MUNOZ JR | UPLAND | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | The backhoe operator was digging a trench to install a water main and hit our 2 plastic main. GIS shows 7'' off and the locator gave a decent signal at 7'' off as well, service history has multiple footages, but the correct measurements are 15'' W of The E PL of 11th Ave. We have reached out to Joe Villagran to get this corrected on GIS. The Locator hooked up to multiple risers and none took him to 15'' off PL.
Southern California Gas Company | N | SAN BERNARDINO | UPLAND | 2023-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | JW FOWLER | SAN DIEGO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | All USA marks were good. Contractor did not hand expose 1/2 CTS service and struck with backhoe.
Southern California Gas Company | N | SAN BERNARDINO | UPLAND | 2023-02-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HOME OWNER | UPLAND | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | home owner lifted service out of ground with backhoe.
Southern California Gas Company | N | SAN BERNARDINO | UPLAND | 2023-11-15 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 2 | 60 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4001 |  | 1 |  | MDM CONSTRUCTION INC | SIMI VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | All USA marks were good, contractor hit 2 PLA main while grading.
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2023-09-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | YUCAIPA WATER DISTRICT | YUCAIPA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor Hit 1/2 plastic service while digging trench with hand tools.
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2023-02-28 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | YVWD | YUCAIPA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | dug before ph
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2023-03-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HORIZON BACKHOE AKA HBE GENERAL CONSTRUCTION | WINCHESTER | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor damaged plastic service line while excavating. ETR called in RFA for potential damage repair. LCT on site confirmed damage. Gas not blowing. EFV stopped the flow of gas. No USA ticket on file.
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2023-07-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | RAMON AVILA | YUCAIPA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was digging near riser with no USA and hit the plastic service line with shovel.
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2023-02-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HHS COMMUNICATIONS | AZUSA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Per HHS Robert Brown and Ariel Coria, Crew was excavating and damaged unmarked 1 PL service.
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2023-07-14 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CONCRETE ALLIANCE | POMONA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor excavating without USA hit gas line.
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2023-01-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | WESTERN CONSTRUCTION SPECIALISTS INC | SEAL BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | approve
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2023-01-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | WESTERN CONSTRUCTION SPECIALISTS INC | SEAL BEACH | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | approve
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2023-11-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MIKE BUTAK | YUCAIPA | CA | N | Y | Yes | No | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Landscape contractor was grading to set forms for concrete driveway when he struck 1/2 plastic service. There were marker flags for our pipe even though the USA ticket was expired.
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2023-12-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ARIZONA PIPELINE | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | USA ticket valid
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2023-04-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | COVARRUBIAS CONSTRUCTION | MURRIETA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Spoke with EE about asking for help when needed on projects tickets. Let EE know that we have here to help.
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2023-02-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HHS CONSTRUCTION | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | approved
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2023-04-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HHS CONSTRUCTION | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Per conversation with HHS Ulysses Llamas crew was excavating with a sharp shooter due to hard soil/roots and damaged 1/2plastic
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2023-03-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | HHS CONSTRUCTION | ONTARIO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | approved
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2023-03-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ALAN BISI | YUCAIPA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Spoke with Alan Bisi, residence where damage occurred is his father''s house and would like any claims mail or phone calls to go directly to Alan. Per Alan, they were excavating for water and damaged service without a valid USA ticket.
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2023-01-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HERMAN WEISSKER | JURUPA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | approved
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2023-09-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | DAVID OLLIS LANDSCAPE DEVELOPMENT | REDLANDS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor with no USA hit service potholing
Southern California Gas Company | N | SAN BERNARDINO | YUCAIPA | 2023-01-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | PHAROS PROPERTIES | LOMA LINDA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | approved
Southern California Gas Company | N | SAN BERNARDINO | YUCCA VALLEY | 2023-03-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | SCHROEDER PLUMBING | YUCCA VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber hit service on branch to neighbor''s house. No emergency responders, no evacuations, no injuries, no road closures. ETR stood by and monitored. Crew arrived and repaired. Called separate tech out for restore on neighbor''s property.
Southern California Gas Company | N | SAN BERNARDINO | YUCCA VALLEY | 2023-07-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | NA | YUCCA VALLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner 1/2 plastic service while hand digging to repair water service line.
Southern California Gas Company | N | SAN BERNARDINO | YUCCA VALLEY | 2023-11-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 4 |  | ACTION PUMPING | YUCCA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged 1/2 IPS pipe with backhoe while excavating for sewer.
Southern California Gas Company | N | SAN BERNARDINO | YUCCA VALLEY | 2023-06-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DAVID LYE | YUCCA VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 1/2 CTS service while excavating with a backhoe. Service was located by ETD about 6 months ago, whiskers were still present, visible and marked correctly, but that ticket has expired. No new ticket for current excavation.
Southern California Gas Company | N | SAN BERNARDINO | YUCCA VALLEY | 2023-10-08 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | FRED DIXON | YUCCA VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hit a 1/2 service line while digging to install a fence post. Homeowner failed to notify USA Dig Alert.
Southern California Gas Company | N | SAN BERNARDINO | YUCCA VALLEY | 2023-12-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | 4S GENERAL ENGINEERING | TEMECULA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged 1/2 IPS service while excavating with shovel to install electric conduit. Contractor did have USA ticket but was working before legal start date.
Southern California Gas Company | N | SAN LUIS OBISPO | ARROYO GRANDE | 2023-08-02 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LAZARO HOME IMPROVEMENTS | NIPOMO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Backhoe hit main. No USA
Southern California Gas Company | N | SAN LUIS OBISPO | ARROYO GRANDE | 2023-11-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | TRUE LANDSCAPE | SANTA MARIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor installing fence post struck 1/2 plastic service with post-hole digger. 811 was not notified.
Southern California Gas Company | N | SAN LUIS OBISPO | ARROYO GRANDE | 2023-07-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | AUBURN OAK BUILDERS | BAKERSFIELD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor excavating hit stub while grading for developer.
Southern California Gas Company | N | SAN LUIS OBISPO | ARROYO GRANDE | 2023-11-13 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  | 11 |  | JJ FISHER CONSTRUCTION | NIPOMO | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor did not renew USA ticket after the scope of work changed.
Southern California Gas Company | N | SAN LUIS OBISPO | ARROYO GRANDE | 2023-08-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | PAUL EHRISMAN CONST | NIPOMO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damaged 1/2 service while excavating water leak. No valid USA.
Southern California Gas Company | N | SAN LUIS OBISPO | ARROYO GRANDE | 2023-08-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | AZTECA BUILDERS | ARROYO GRANDE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Azteca Builders failed to maintain marks and struck a 1/2 plastic service with a shovel while hand digging.
Southern California Gas Company | N | SAN LUIS OBISPO | ATASCADERO | 2023-04-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | TROY WITT | ATASCADERO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Home owner with a trencher was looking for a PVC water line and hit the 1/2 CTS PLA line caused a broken and blowing. Gas Ops able to control the gas and make repair.
Southern California Gas Company | N | SAN LUIS OBISPO | ATASCADERO | 2023-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | KARIN O''BRIEN | ATASCADERO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA, Third party damage on 3/4 STL service. STL service was pulled up by backhoe and it pulled the MSA down into the ground and snapped off nipple above the service valve. The service valve was shut off by contractor. The damage was called into the gas company the following day after the damage. The service was not leaking upon SCG arrival and no gas indications at the foundation. Customer has been referred to the damage prevention team for not reporting the damage to gas company facilities.
Southern California Gas Company | N | SAN LUIS OBISPO | ATASCADERO | 2023-01-13 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SOCAL GAS COMPANY | TEMPLETON | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | LCT Struck Service with Impacto Bar while verifying underground leak indications. 1st party damage.
Southern California Gas Company | N | SAN LUIS OBISPO | ATASCADERO | 2023-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | WIGHTON''S PLUMBING | SAN LUIS OBISPO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damage. Contractor damaged plastic service while hand digging to expose sewer lateral. 811 was not notified.
Southern California Gas Company | N | SAN LUIS OBISPO | ATASCADERO | 2023-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 4 |  | STANLEY PETERSON | ATASCADERO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Third party contractor/ home owner was trenching to replace sewer lateral and damaged 1/2 PLA CTS service. Crew was able to control the gas and make repairs.
Southern California Gas Company | N | SAN LUIS OBISPO | ATASCADERO | 2023-01-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | WESLEY PRICE | MORRO BAY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA, Third party contractor damage. Severed line with post hole digger. 4 units were dropped.
Southern California Gas Company | N | SAN LUIS OBISPO | ATASCADERO | 2023-08-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | WILBER CONSTRUCTION INC | PASO ROBLES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractors hand digging to expose marked 1/2 plastic service in hard soil. Damaged the service with a shovel. Marks accurate and valid 811 ticket.
Southern California Gas Company | N | SAN LUIS OBISPO | ATASCADERO | 2023-09-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | MADRONE LANDSCAPES | ATASCADERO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA third party contractor was digging without USA to install fence damaged 1/2 PLA service. Company crew made repairs.
Southern California Gas Company | N | SAN LUIS OBISPO | ATASCADERO | 2023-02-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | TIMOTHY FORNEY | ATASCADERO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | FD cal for hit service line. No closures, no media. Service restored upon completion of repairs.
Southern California Gas Company | N | SAN LUIS OBISPO | CAMBRIA | 2023-07-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GOWDY ELECTRIC | CAMBRIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor excavating with a valid USA, hit marked gas line.
Southern California Gas Company | N | SAN LUIS OBISPO | CAMBRIA | 2023-08-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | LUIS PLACENTIA LANDSCAPING | CAMBRIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | The homeowner?s contractor digging up dirt to install a landscaping retaining wall struck the branch service gas line.
Southern California Gas Company | N | SAN LUIS OBISPO | CAYUCOS | 2023-01-25 | Operator excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 28 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | SOCAL GAS | SAN LUIS OBISPO | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | corrective actions pending
Southern California Gas Company | N | SAN LUIS OBISPO | CAYUCOS | 2023-08-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | MACIEL FLORES | CAYUCOS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No valid USA. Contractor hit service with shovel.
Southern California Gas Company | N | SAN LUIS OBISPO | GROVER BEACH | 2023-11-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | SECOND GENERATION BUILDERS | BAKERSFIELD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA ticket
Southern California Gas Company | N | SAN LUIS OBISPO | GROVER BEACH | 2023-02-21 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ARB | LAKE FOREST | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 2nd party damage
Southern California Gas Company | N | SAN LUIS OBISPO | GROVER BEACH | 2023-06-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GENE FREITAS | GROVER BEACH | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No valid USA.
Southern California Gas Company | N | SAN LUIS OBISPO | LOS OSOS | 2023-09-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | K PRUITT | LOS OSOS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Tenant was using a shovel to dig a hole to plant a plant and struck the plastic service line. The tenant did not contact underground service alert to locate the utilities.
Southern California Gas Company | N | SAN LUIS OBISPO | LOS OSOS | 2023-03-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ROBERT MORRIS | LOS OSOS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 pla service was damaged by homeowner
Southern California Gas Company | N | SAN LUIS OBISPO | LOS OSOS | 2023-09-20 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | INTEGRITY CONTRACTORS INC | CORONA | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | 2nd party damage to 1/2 plastic service due to contractor failing to locate and hand dig service through their trench before using machine operated equipment.
Southern California Gas Company | N | SAN LUIS OBISPO | LOS OSOS | 2023-10-19 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | INTEGRITY CONTRACTORS | CORONA | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | 2nd party contractor failed to excavate cautiously while exposing service.
Southern California Gas Company | N | SAN LUIS OBISPO | LOS OSOS | 2023-09-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | O''BRIEN CONSTRUCTION | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor excavating did not request USA and damaged gas services. Crews responded and made permanent repairs.
Southern California Gas Company | N | SAN LUIS OBISPO | MORRO BAY | 2023-04-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | MIKE BURTON | MORRO BAY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Homeowner using loppers cut through plastic gas service assuming it was a tree root. USA was notified and marks were visible and accurate.
Southern California Gas Company | N | SAN LUIS OBISPO | NIPOMO | 2023-12-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | PETE AGALOS AND SHANE FERRIS | NIPOMO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner excavating without USA hit service.
Southern California Gas Company | N | SAN LUIS OBISPO | NIPOMO | 2023-06-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | RAMINHA CONSTRUCTION | ATASCADERO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor hit gas service while trying to verify marks using hand tools in hard clay ground.
Southern California Gas Company | N | SAN LUIS OBISPO | NIPOMO | 2023-08-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MIKE TREMPER | NIPOMO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner excavating without USA hit gasline.
Southern California Gas Company | N | SAN LUIS OBISPO | NIPOMO | 2023-11-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | NA | SANTA MARIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Dig-in damage to 1/2'' plastic service. Digging for water line repairs. USA was not called.
Southern California Gas Company | N | SAN LUIS OBISPO | NIPOMO | 2023-10-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | R BAKER CONSTRUCTION | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor excavating with valid USA hit unmarked gas stub. Stub was not mapped, verified unable to back locate.
Southern California Gas Company | N | SAN LUIS OBISPO | NIPOMO | 2023-11-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | VICTOR NORIZ | NIPOMO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor excavating did not request USA and damaged service.
Southern California Gas Company | N | SAN LUIS OBISPO | NIPOMO | 2023-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | DANN RUFFONI | NIPOMO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner excavating without USA hit gas service.
Southern California Gas Company | N | SAN LUIS OBISPO | NIPOMO | 2023-02-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 8 |  | LINE WORKS CONSTRUCTION INC | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor with valid USA potholed and exposed marked gas service. While boring soil underneath rod collapsed, weight and pressure of rotating bore rod cause service to rupture.
Southern California Gas Company | N | SAN LUIS OBISPO | NIPOMO | 2023-08-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CYNDY AND DOUG PECYNA | NIPOMO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Home-owner damaged service line while installation of gate post. Gas utilities were accurately marked with flags and yellow paint. USA was valid while work was being performed.
Southern California Gas Company | N | SAN LUIS OBISPO | NIPOMO | 2023-02-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | WILLIAM G KENGAL | NIPOMO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA ticket. Developer pounding stakes to anchor railroad tie near the gas riser.
Southern California Gas Company | N | SAN LUIS OBISPO | OCEANO | 2023-11-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | FIVE STAR FENCING | GROVER BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1/2 service while digging for fence post. No valid USA.
Southern California Gas Company | N | SAN LUIS OBISPO | PASO ROBLES | 2023-05-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | JOHN NOWAK | LOS OSOS | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damage to our service line. No USA ticket. Landscapers where hammering a long nail to hold a lanscape board in place which struck the 1/2 plastic service branch service. ETR evacuated two residents and contacted the Fire Department to standby until the crew controled the leak. No injuries, No media, no PD, no street closure. Gas-ops made permanent repairs and one premise was restored the same day, the other premise was restored the next day.
Southern California Gas Company | N | SAN LUIS OBISPO | PASO ROBLES | 2023-09-21 | Third party excavation damage | Riser | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | KW CONSTRUCTION | PASO ROBLES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | USA valid, marks accurate, third party contractor failed to hand dig to pothole to find location of pipe. Third party contractor ripped the cap off the 1/2 PLA stub with a backhoe then pinched the service with a vice.
Southern California Gas Company | N | SAN LUIS OBISPO | PASO ROBLES | 2023-04-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | SPECIALTY CONSTRUCTION INC | SAN LUIS OBISPO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor was probing for the 1 PLA service and caused a damage. Crew was able to control the gas and make repairs on same day. USA marks were accurate. USA was valid.
Southern California Gas Company | N | SAN LUIS OBISPO | PASO ROBLES | 2023-03-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 3 |  | WEIDE KURT CONSTRUCTION INC | PASO ROBLES | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor doing street repair damaged 1/2 PLA service with backhoe. Valid USA and Marks were accurate. Contractor didnt pot hole.
Southern California Gas Company | N | SAN LUIS OBISPO | PASO ROBLES | 2023-04-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 4 |  | FENCING 101 | PASO ROBLES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Third party contractor damaged line with post hole digger. Crew able to control and repair same day.
Southern California Gas Company | N | SAN LUIS OBISPO | PASO ROBLES | 2023-06-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | BRYAN STEWART | ATASCADERO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor dig in damage. No USA called in. Crew made repairs and restores were completed.
Southern California Gas Company | N | SAN LUIS OBISPO | PISMO BEACH | 2023-12-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DRAKE EXCAVATING AND AGGREGATES INC | SAN LUIS OBISPO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit 1/2 service while confirming locate marks by pot hole. USA valid. Marks visible and accurate.
Southern California Gas Company | N | SAN LUIS OBISPO | PISMO BEACH | 2023-06-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | KIRK CONSTRUCTION | ATASCADERO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party damage. Failed to pothole facility before machine excavating.
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2023-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ROB REYNOLDS CONSTRUCTION | CRESTON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Valid 811 ticket. Service was clearly marked. Contractors failed to completely hand expose plastic service prior to excavating with backhoe near the service.
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2023-06-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 42 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | JUAN ELIAS | SAN LUIS OBISPO | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Homeowner damaged service while digging to repair drain and water line.
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2023-07-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | RUIFFINO CONSTRUCTION | SANTA MARIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No valid USA
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2023-02-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | BUNYON BROS. TREE SERVICE | SAN LUIS OBISPO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No valid USA
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2023-07-11 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ARB | VENTURA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor ARB hit service while hand digging to expose for installation of new gas service.
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2023-10-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BULLARD & SONS | PASO ROBLES | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | One unmarked 1/2 Plastic sub was damaged during grading.
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2023-06-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 59 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | OAK RIDGE LANDSCAPE | NIPOMO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractrors damaged plastic service while attempting to hand expose facility.
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2023-01-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | WARTON LLC | SANTA MARIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No valid USA
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2023-04-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | ADRIAN ALVERADO | SAN LUIS OBISPO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractors hand digging to install fence post damaged plastic service line
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2023-02-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | FORTINI RYAN DESIGN GROUP INC | SAN LUIS OBISPO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | SCG locator failed to properly mark branch service.
Southern California Gas Company | N | SAN LUIS OBISPO | SAN LUIS OBISPO | 2023-08-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | SOUZA CONSTRUCTION | SAN LUIS OBISPO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractors damaged our gas line as it was mismarked by 4 feet.
Southern California Gas Company | N | SAN LUIS OBISPO | TEMPLETON | 2023-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RCH CONSTRUCTION | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third Party contractor dug into a 1 PLA service with backhoe while trying to excavate around power box. Digging on a expired USA but marks were accurate for SCG.
Southern California Gas Company | N | SANTA BARBARA | CARPINTERIA | 2023-02-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | BRIAN LUMBARDI | CARPINTERIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Property Tenant was digging a trench to re-route gas house line and struck our half inch cts service. No USA
Southern California Gas Company | N | SANTA BARBARA | CARPINTERIA | 2023-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | GIACOMO LAMPARIELLO | CARPINTERIA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Cust hit our service while landscaping in his yard.
Southern California Gas Company | N | SANTA BARBARA | CARPINTERIA | 2023-06-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | PEREZ LANDSCAPING INC | CARPINTERIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hit service line while digging with shovel. Flags out over service
Southern California Gas Company | N | SANTA BARBARA | GOLETA | 2023-10-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ROTO ROOTER | VISTA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging in front of meter for sewer repair and struck service. No USA was called.
Southern California Gas Company | N | SANTA BARBARA | GOLETA | 2023-12-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | GALLEGOS PLUMBING | VENTURA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber hit 1/2 PLA pipe with hand tool while making repairs.
Southern California Gas Company | N | SANTA BARBARA | GUADALUPE | 2023-05-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | GREEN J D CONSTRUCTION | ORCUTT | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor excavating without USA hit gasline service.
Southern California Gas Company | N | SANTA BARBARA | GUADALUPE | 2023-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ANTONIO PEREZ | GUADALUPE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hit 1/2 service near riser while digging for sewer lateral. Guadalupe fire and police on site and evacuated two people from residence upon arrival. Company crew successfully got gas under control and made final repairs. No Valid USA.
Southern California Gas Company | N | SANTA BARBARA | GUADALUPE | 2023-12-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MARGARET ARCHULETA | GUADALUPE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner excavating and removing fence hit 1/2 plastic service. No current USA on file.
Southern California Gas Company | N | SANTA BARBARA | LOMPOC | 2023-10-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ECO LAWN | SANTA BARBARA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscape company hit gas service while removing tree. No USA.
Southern California Gas Company | N | SANTA BARBARA | LOMPOC | 2023-02-04 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | JOHN BROCK | LOMPOC | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Homeowner Damaged service while installing fence post
Southern California Gas Company | N | SANTA BARBARA | LOMPOC | 2023-06-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | VICTOR SAMAGUEY | LOMPOC. | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner excavating without USA hit gasline. Spoke to Victor about the importance of calling 811.
Southern California Gas Company | N | SANTA BARBARA | LOMPOC | 2023-07-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | BOBBY SANCHEZ | ATASCADERO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor excavating with valid USA hit properly marked gasline.
Southern California Gas Company | N | SANTA BARBARA | LOMPOC | 2023-10-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | FOUNDATION SOLUTIONS | ATASCADERO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor excavating without USA hit service.
Southern California Gas Company | N | SANTA BARBARA | LOMPOC | 2023-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | ANDRES FLORES | LOMPOC | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor excavating without USA hit gasline.
Southern California Gas Company | N | SANTA BARBARA | LOMPOC | 2023-03-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | YOUNG ROGER CONSTRUCTION | SANTA MARIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 1/2 service hit by contractor while digging for footing for retaining wall with backhoe. No USA, crew squeezed service and made repairs per policy.
Southern California Gas Company | N | SANTA BARBARA | LOMPOC | 2023-04-19 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | R D Z CONTRACTORS INC | NIPOMO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Party contractor excavating with USA hit marked gas line.
Southern California Gas Company | N | SANTA BARBARA | LOMPOC | 2023-10-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | WALTER BRUNDY | LOMPOC | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor excavating without USA hit gas service.
Southern California Gas Company | N | SANTA BARBARA | LOMPOC | 2023-09-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CARLOS H LOPEZ | LOMPOC | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | The home owner had a valid USA ticket. The gas company mark and locate employee mis marked the gas service line. The customer hit the gas service line while excavating far from the marked gas service .
Southern California Gas Company | N | SANTA BARBARA | LOMPOC | 2023-04-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 48 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ARTHUR KALAYVAIN | LOMPOC | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1/2 PLA BR with metal fence post.
Southern California Gas Company | N | SANTA BARBARA | LOS ALAMOS | 2023-10-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LARA''S CONSTRUCTION | SOLVANG | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor hit exposed service while digging out trench for sewer. Service was marked and USA was valid.
Southern California Gas Company | N | SANTA BARBARA | LOS OLIVOS | 2023-07-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | EMPF | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor excavating without USA hit gasline.
Southern California Gas Company | N | SANTA BARBARA | LOS OLIVOS | 2023-08-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | GEORGE MARTINEZ | LOS OLIVOS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit exposed marked gas service. Service was marked after the prior damage.
Southern California Gas Company | N | SANTA BARBARA | LOS OLIVOS | 2023-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 6 |  | JUAN VIDRIO | LOS ANGELES | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor excavating without USA hit gasline. Explained the importance of calling 811.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-11-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CANILA ACOSTA | SANTA BARBARA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Home owner was digging with shovel and struck service. No USA
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-08-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | BECKER STUDIOS | SANTA BARBARA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor was hand digging and hit it with a shovel
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-04-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 5 |  | PACIFIC NETWORKS | SANTA BARBARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor bored through service while installing cable communication line.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-05-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 9 |  | W SCOTT CONSTRUCTION | SANTA MARIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Developer had contractor drive in a steel stake and struck 1/2 plastic line crew went out and repaired line.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-08-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 9 |  | RW SCOTT CONSTRUCTION | SANTA MARIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor dug over our line and struck line for the 4th time
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-06-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | MORAS CONSTRUCTION | SANTA BARBARA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | 3rd Party Contractor struck service line outside of Delineations with an excavator while clearing lot for construction.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-06-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | LANDSCAPE BY DAVIS | SANTA BARBARA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscapers were digging to lay irrigation and struck 1/2 service line with no USA crew arrived and fixed line
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-12-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ART HODGES | SANTA BARBARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor struck 1/2 inserted line.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-01-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DIONEL LOPEZ | SANTA BARBARA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party was digging to repair a sewer lateral when they damage our plastic service with a shovel. No USA was called.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-04-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | RICK LANDAVERDE | PORTER RANCH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CREATIVE LANDSCAPING | SANTA BARBARA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging in front yard for construction of house. Struck service with shovel.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CREATIVE LANDSCAPING | SANTA BARBARA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor struck service line with backhoe while building home.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-11-10 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.75 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | SOCALGAS | SANTA BARBARA | CA | Y | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | ETR was digging around riser to get to service valve. While digging with shovel he struck a bypass nipple and broke it.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-07-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | PACIFIC POOLS INC | GOLETA | CA | N | Y | Yes | No | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging up trench to install house line for pool and struck half inch service line.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-07-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HAMPTON TEDDER | VENTURA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hampton and Tedder were digging to replace an anchor for SoCal Edison. They were digging and struck the line.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-08-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | TIDWELL EXCAVATION | VENTURA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor while digging for electrical maintenance, struck our service line causing it to leak.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-04-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | STEVE DRAGHI | SANTA BARBARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Homeowner was digging with hand tools to repair a sewer line and damaged our 1/2 PLA service. USA marks were visible.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GOSNELL LANDSCAPE | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging for electrical conduit and struck our 1 service line did not have a valid USA
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-09-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | LOW COST PLUMBING INC | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Party contractor dug and severed 1/2 inch service line
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-10-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | VINYL CONCEPTS | NEWBURY PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging holes to put fence posts in and struck gas service. No USA
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-05-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LIGHT OF THIS WORLD ELECTIC | GOLETA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor while digging with excavator for electrical lines, struck and damaged gas service to MSA
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-06-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | HERBERT TORRES | VENTURA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging and stuck 1/2 plastic service with shovel.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-12-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | PACIFIC NETWORKS | SANTA BARBARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor was digging and breaking out rock that was over the service line. As they broke out the rock they nicked the service line.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NA | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor struck our service with a backhoe while digging a hole for a tree.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-06-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | RICHARD COFFIN | SANTA BARBARA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was digging to fix some irrigation line and struck our 1/2 service line with shovel. Crew arrived and had to install shoring and then was able to fix the service stub
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-05-25 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | LASH CONSTRUCTION | SANTA BARBARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Party Contractor was digging with a valid USA ticket and didn''t realize that there was a 2 main marked and stuck the 2 main line. when crews arrived they were able to bypass and fix the 2 damage.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-11-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | BRIS CARDENAS | SANTA BARBARA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor struck service with shovel while digging for drainage pipe
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-05-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | TRI COUNTY POOLS | CARPINTERIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was digging and struck 1/2 service with shovel within delineation. once crew arrived was able to squeeze and repair line.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-04-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | TIDWELL | VENTURA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Tidwell had a valid USA ticket and misjudged the marking of the service line and struck service with Backhoe
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-07-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | STEVE BELINSKI | SANTA BARBARA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Brother of owner was hand digging to put in fence and struck 1/2 service line.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-09-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | NATIONWIDE GENERAL CONTRACTOR | SAN BERNARDINO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party contractor hit 1/2 plastic service while trenching with hand tools.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-10-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | LEO ORDONEZ | SANTA BARBARA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging for landscaping in area and struck gas service with a shovel. Contractor did not call for USA before digging.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-11-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | HOTLINE CONTRUCTION | SANTA PAULA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was digging for supports for electric pole. Struck service with shovel.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-05-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 3 |  | 101 PLUMBING INC | SANTA BARBARA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party Contractor was digging for sewer and did not obtain USA dig ticket as they were digging, they struck a 1/2 gas service line and through dirt on damage which cause gas to migrate into the structure called for LCT and line was repaired had ETR check ambient and everything was aired out of structure.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-08-08 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 1.25 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 3 |  | TIERRA CONTRACTING INC | SANTA BARBARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor dug up and found service line and another line running parallel to the service about 6 away which was 1 1/4 service line as well in same hole and struck 1 1/4 service.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | JOHN FRANK | SANTA BARBARA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant was installing fence post and struck service line.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-03-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | KGM CONSTRUCTION | SAN LUIS OBISPO | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Contractor struck our service line while digging for a telecommunications line. The contractor walked over to the neighboring house where a SoCal Gas technician was working. They responded until distribution arrived. No injures/fatalities. No Evacuations. No Street Closures. No Media. No first responders.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-06-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ANTONIO E RUIZ | SANTA MARIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit 1/2 inch service with no USA crew arrived and fixed leak
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-06-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NA | SANTA BARBARA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor while digging to remove a tree hit gas service. No USA ticket
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-01-23 | Third party excavation damage | Main | Polyethylene Pipe | Augur | 4 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  |  | NA | FRONTIER COMMUNICATIONS | SANTA BARBARA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damage a 4 plastic main with an augur when attempting to install a communications pole for Frontier Communications.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-05-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | GIFFIN AND CRANE | SANTA BARBARA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor was doing landscaping and as they were digging they stuck the half inch service line with no USA
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-08-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 5 |  | LOW COST PLUMBING INC | SANTA BARBARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor stuck mark 1/2 plastic service
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-03-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | AQUARIAN BACKFLOW | SANTA BARBARA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party contractor struck our service with a shovel as he was installing a water line next to meter
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-06-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | LASH CONSTRUCTION | SANTA BARBARA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | LASH Construction struck our marked out service line with a backhoe. Did not pothole to verify marks.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-11-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | SOCAL EDISON | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor working for Edison struck gas line while trenching for new electrical box.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-11-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | FRED SILSBEE | SANTA BARBARA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was digging in yard and struck gas service with shovel. No USA Called.
Southern California Gas Company | N | SANTA BARBARA | SANTA BARBARA | 2023-11-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ESPINOZA CONCRETE | SANTA BARBARA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Struck gas service with a handheld clay spade
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2023-05-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | JORGE ARCHAVALETA | SANTA MARIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor excavating without USA hit gasline. Spoke to Jorge about the importance of calling 811.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2023-07-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | OAKRIDGE LANDSCAPING INC | VALENCIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Oakridge Landscaping damaged 1/2 service while digging for irrigation line. No valid USA.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2023-09-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | RICKY ADAMS | SANTA MARIA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner excavating without USA hit gasline.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2023-08-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | JAVIER HERNANDEZ | SANTA MARIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractors damaged 1/2 CTS plastic service with a shovel while hand digging to install sewer line. Permanent repairs complete. 811 was not notified.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2023-11-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | HOMEOWNER | SANTA MARIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner installing fence dig-in damage hitting 1/2 plastic service. USA was not called.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2023-02-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 2 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | RED BLOSSOMS FARM | SANTA MARIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 2'' service damaged by Installation of mesh fencing by a T post in two locations.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2023-09-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ELECTRICAL MAINTENANCE PROS | GROVER BEACH | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Electricians installing grounding rod without USA hit gas service.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2023-02-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | WILL J F COMPANY INC THE | SANTA MARIA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor hit unmarked gas stub.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2023-03-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | TERSO DEJESUS | SANTA MARIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Farmers excavating without USA hit 2 Gas Service. Explained the importance of calling 811 to Julio Estrada.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2023-02-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | LINEWORKS | SANTA MARIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractors boring fiber optics, directly hit a marked gasline.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2023-04-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 45 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | EFI ENGINEERING | TUSTIN | CA | N | Y | No | No damage to SUOF. | No damage to SUOF. | No damage to SUOF. | No | Excavator provided no markings for the proposed excavation on site. | No | This damage was not a dig in. Service was exposed prior to boring. Damage occurred when the bore rod was being pulled back and became tangled in the 1/2 plastic service.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2023-04-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | LUIS GUILLEN | SANTA MARIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Owner of property trenching for new sewer lateral for ADU struck plastic service with shovel. There was no USA ticket.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2023-11-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | LAWRENCE DAVIDSON | SANTA MARIA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner excavating for fencing damaged 1/2 plastic service. USA was not called.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2023-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | VERON CONSTRUCTION | SANTA BARBARA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor excavating without USA hit 2 gas stub.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2023-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CESAR SIERRA | ARROYO GRANDE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor excavating without USA hit gasline. Spoke to Cesar Sierra about calling 811.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2023-07-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | HANDYMAN FENCE REPAIR | LOMPOC | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor excavating without USA hit gasline.
Southern California Gas Company | N | SANTA BARBARA | SANTA MARIA | 2023-04-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | JOSEPH ENGINEERING | SANTA MARIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor excavating without a USA hit gasline.
Southern California Gas Company | N | SANTA BARBARA | SANTA YNEZ | 2023-05-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | CUSTOMER | SANTA YNEZ | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hand digging struck plastic service. No USA.
Southern California Gas Company | N | SANTA BARBARA | SANTA YNEZ | 2023-05-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | LUCAS BENNET | SANTA YNEZ | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA Ticket. Customer was hand digging to expose gas line to see how deep it was buried because they were going to pour concrete on the drive way. gas-ops foud te plastic service about 7 deep. Home owner and contactor bent the hit line and tapped it causing the gas leak to stop. Gas-Ops spoke to planning and per their recomendtions, they lowered the pipe to the correct depth. ETR restored service afterwards. No injuries, no PD, No FD, no Media.
Southern California Gas Company | N | SANTA BARBARA | SANTA YNEZ | 2023-02-15 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | MAIN LINE ENGINEERING | LOMPOC | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractors with valid USA hit marked 3/4 gasline. No pothole was done to verify the depth of the service.
Southern California Gas Company | N | SANTA BARBARA | SANTA YNEZ | 2023-02-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DAVID MEXICO | BUELLTON | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractors excavating without USA hit gasline. Informed contractors about the importance of calling 811.
Southern California Gas Company | N | SANTA BARBARA | SANTA YNEZ | 2023-12-22 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  | 9 |  | RACHEL HEDGES | SANTA YNEZ | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA. Handyman working for homeowner hit the gas main while replacing a fence post
Southern California Gas Company | N | SANTA BARBARA | SOLVANG | 2023-09-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MID STATE FENCE | SANTA MARIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor installing fence without USA hit gas service.
Southern California Gas Company | N | SANTA BARBARA | SOLVANG | 2023-06-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | TRACE AGIN | SOLVANG | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damage. Contractor Hit 1/2 service while digging with posthole digger. No valid USA ticket.
Southern California Gas Company | N | SANTA BARBARA | SOLVANG | 2023-11-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | DANIEL THOMPSON | VENTURA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor damaged 1/2 PLA service while digging over service with backhoe within 2'' of marks. Contractor didn''t hand dig to pothole facilities.
Southern California Gas Company | N | SANTA BARBARA | SOLVANG | 2023-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | KAREN HAENEL | SANTA INEZ | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA Ticket. 1/2 plastic service struck by posthole digger.
Southern California Gas Company | N | SANTA BARBARA | SOLVANG | 2023-06-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | UTRERA MASONARY | LOMPOC | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party damage, contractor no valid USA
Southern California Gas Company | N | SANTA BARBARA | SUMMERLAND | 2023-04-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | KENNEY CONSTRUCTION | SANTA BARBARA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor struck service with a backhoe while digging for foundations of a patio
Southern California Gas Company | N | SANTA BARBARA | SUMMERLAND | 2023-05-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | WOODY BOYCE | SANTA BARBARA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | A 3rd party contractor excavating for a new build damaged a 1/2 plastic service with an excavator. The site had an old expired USA ticket but no current valid USA.
Southern California Gas Company | N | SANTA BARBARA | SUMMERLAND | 2023-08-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | LA TIERRA LANDSCAPING | SANTA BARBARA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Landscapers were planting a boxed tree when the hit a 1/2 PLA service with hand tool.
Southern California Gas Company | N | TULARE | ALPAUGH | 2023-11-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | IGNACIO HERNANDEZ | ALPAUGH | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer damaged service line while excavating for fence post. No USA.
Southern California Gas Company | N | TULARE | DINUBA | 2023-08-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ROSA RODRIQUEZ | DINUBA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | SCG crew responded to RFA for a hit line, upon arrival, crew found a damaged 1/2 plastic gas line.
Southern California Gas Company | N | TULARE | DINUBA | 2023-09-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | SIGNATURE POOLS AND SPA | CLOVIS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | 3rd party contractor damaged a 1 plastic gas line while excavating for a new swimming pool project. Contractor excavated outside the delineated area.
Southern California Gas Company | N | TULARE | EARLIMART | 2023-11-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | KENDALL JOSE | EARLIMART | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer damaged plastic service while excavating for fence post. No USA.
Southern California Gas Company | N | TULARE | EXETER | 2023-05-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 20 | 20 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | ELISEO MARTINEZ | EXETER | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer damaged 1/2 plastic service while digging to install a fence post and did not call for USA dig alert.
Southern California Gas Company | N | TULARE | FARMERSVILLE | 2023-04-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | SEVANDO LOZA | FARMERSVILLE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer was digging for fence post with no USA and damaged 1/2 service damaging party was informed about USA law.
Southern California Gas Company | N | TULARE | FARMERSVILLE | 2023-07-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | DNA CONTRACTING | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged a 1/2 plastic gas line while excavating for electrical work.
Southern California Gas Company | N | TULARE | FARMERSVILLE | 2023-09-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | DNA CONTRACTING | VISALIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | SCG crew responded to assist for 3rd party damage, upon arrival, crew found damaged 1/2 plastic gas line. Damaging party was excavating with hand tools for electrical project, contractor failed to pot hole as required.
Southern California Gas Company | N | TULARE | FARMERSVILLE | 2023-09-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | AVISON CONSTRUCTION | MADERA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | SCG crew responded to RFA for damaged gas line, upon arrival, crew investigated and found damaged 3/4 steel to 1/2 plastic transition fitting by 3rd party contractor Avison Construction. During repairs, SCG crew determined that Avison Construction, failed to maintain marks.
Southern California Gas Company | N | TULARE | PIXLEY | 2023-10-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ADELINA RAMOS | PIXLEY | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was excavating to replace fence post and damaged 1/2 service. They did not call USA.
Southern California Gas Company | N | TULARE | PIXLEY | 2023-10-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 55 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CORREA LAND COMPANY LLC | PIXLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party excavator was digging with backhoe and hit the svc while excavating. USA was valid and facility marked.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2023-03-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | HOMEOWNER | PORTERVILLE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged a 1/2 plastic gas line, crew made permanent repairs, homeowner was educated about USA law
Southern California Gas Company | N | TULARE | PORTERVILLE | 2023-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BILLY BLOUNT | PORTERVILLE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor did not have a usa ticket and damaged 1/2'''' service.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2023-07-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | TITANIUM SOLAR | TULARE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Solar contractor was trenching for electrical piping and damaged service, contractor did have a valid USA ticket. Contractor failed to pot hole service.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2023-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | GOOD GUYS ELECTRIC AND SOLAR | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to maintain clearance while excavating and damaged plastic service.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2023-12-18 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  | 2 |  | 99 PIPELINE INC | PORTERVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Damaged a 4 plastic main while excavating with backhoe to install a new sewer line.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2023-06-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | GUILLERMO RAMIREZ | PORTERVILLE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | damaged service repaired by crew, no usa by contractor
Southern California Gas Company | N | TULARE | PORTERVILLE | 2023-09-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | PAUL TORRES | PORTERVILLE | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner Paul Torres was excavating without a valid USA ticket for sewer work using hand tools, he damaged a 1/2 plastic gas line, SCG crew made permanent repairs.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2023-08-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | RIGOBERTO RAMOS | PORTERVILLE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant was excavating to install a post for car port and accidentally damaged a 1/2 plastic gas line, crew made permanent repairs.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2023-06-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DAVID AND SON BACKHOE | LYNDSEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged service repaired by crew, no usa by contractor
Southern California Gas Company | N | TULARE | PORTERVILLE | 2023-03-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | ISIDRO ANDRADE | PORTERVILLE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 1/2 plastic gas line, crew made permanent repairs, damaging party was educated about USA law.
Southern California Gas Company | N | TULARE | PORTERVILLE | 2023-09-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ANDREW FOUCHT | PORTERVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Occupant was excavating to repair sewer line, occupant had a valid USA ticket and line was marked, he damaged service while excavating.
Southern California Gas Company | N | TULARE | SANTA CLARITA | 2023-09-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | SAM HILL & SONS INC | VENTURA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged PLA service while excavating.
Southern California Gas Company | N | TULARE | SPRINGVILLE | 2023-06-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | VTREDA CONSTRUCTION | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer hit neighbors line while digging, no USA, repaired by crew
Southern California Gas Company | N | TULARE | TRAVER | 2023-04-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | OSCAR BRECEDE | TRAVER | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant damaged a 1/2 plastic gas line, crew made permanent repairs. Damaging party was educated about USA law.
Southern California Gas Company | N | TULARE | TRAVER | 2023-06-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | FRANCISCO DEDIOS | TRAVER | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant damaged a 1/2 plastic gas line while digging to install a fence post, crew made permanent repairs and aerated.
Southern California Gas Company | N | TULARE | TULARE | 2023-12-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | ADAME COMMUNICATION INC | ANAHEIM | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Damaged a 1/2 plastic gas line while boring to install a new fiber optic line. Contractor did not have a valid USA ticket.
Southern California Gas Company | N | TULARE | TULARE | 2023-03-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5001 |  | 1 |  | FLOYD JOHNSTON CONSTRUCTION CO INC | CLOVIS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged a 1/2 plastic gas line, crew made permanent repairs, contractor was educated about USA law.
Southern California Gas Company | N | TULARE | TULARE | 2023-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | BAKER FINANCIAL INC | GROVER BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged a 1/2 plastic gas line, crew made permanent repairs. Per ETD Chris Little, yellow flags used to mark the damaged facility were moved from the location flags were originally placed.
Southern California Gas Company | N | TULARE | TULARE | 2023-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ADAME COMMUNICATIONS INC | TULARE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | SCG crew responded to damaged gas line by 3rd party contractor. Upon arrival, crew found damaged 1/2 plastic gas line.
Southern California Gas Company | N | TULARE | TULARE | 2023-08-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GALVAN UNDERGROUND ENGINEERING INC | MORENO VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | SCG crew responded to damaged gas line by 3rd party contractor, upon arrival, crew found damaged 1/2 plastic gas line caused by 3rd party contractor while pot holing to find the 1/2 gas line using hand tools.
Southern California Gas Company | N | TULARE | TULARE | 2023-03-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | ANTHONY SWETLA | TULARE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant damaged a 1/2 plastic gas line while working to repair a sewer line, crew made permanent repairs, damaging party was educated about USA law.
Southern California Gas Company | N | TULARE | TULARE | 2023-10-17 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | ADAME CONSTRUCTION INC | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hand digging and hit 2 main. USA was valid.
Southern California Gas Company | N | TULARE | TULARE | 2023-07-20 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 0.75 | 125 | 100 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 20388 |  |  | NA | SECURITY PAVING COMPANY INC | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The paving contractor pushed down on the valve can with a large excavator which caused the still valve can to push down on the 3/4 service with so much force it cracked the 4 HP main behind the weld. They failed to pothole prior to grading resulting in the damage to SCG facilities.
Southern California Gas Company | N | TULARE | TULARE | 2023-05-09 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | HCD CONSTRUCTION | VISALIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor digging with out a valid USA ticket damaged a 2 plastic gas main while trenching for utilities, contractor was educated about USA law.
Southern California Gas Company | N | TULARE | TULARE | 2023-11-27 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 6 |  | MORRIS LEVIN & SON | TULARE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged a 1 plastic gas line while excavating for sewer repairs.
Southern California Gas Company | N | TULARE | TULARE | 2023-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 1 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 7501 |  | 6 |  | ACI ADAME COMMUNICATION INC | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | SCG crew responded to RFA for hit line, upon arrival, crew found a damaged 1 plastic main by 3rd party contractor ACI. Failed to pot hole as required.
Southern California Gas Company | N | TULARE | TULARE | 2023-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 2 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ACI ADAME COMMUNICATION INC | CORONA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | SCG crew responded to damaged gas line by 3rd party contractor, upon arrival, crew found damaged 2 plastic gas line, permanent repairs made.
Southern California Gas Company | N | TULARE | TULARE | 2023-09-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ACI ADAME COMMUNICATION INC | CORONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Crew responded to 3rd party damage, upon arrival, crew found damaged 1/2 plastic gas line, by 3rd party contractor Adame Communication Inc, contractor damaged the gas line while potholing with shovel to find the gas line
Southern California Gas Company | N | TULARE | TULARE | 2023-09-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | ACI ADAME COMMUNICATION INC | TULARE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was installing communications conduit and damaged our 1/2 service while pot holing.
Southern California Gas Company | N | TULARE | TULARE | 2023-07-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | BORING BROTHERS | LADERA RANCH | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor was boring to install a new communications line and damaged a unmarked 1/2 plastic gas line
Southern California Gas Company | N | TULARE | TULARE | 2023-10-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | ADAME COMMUNICATION INC | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was excavating outside their delineation and damaged 1/2 service.
Southern California Gas Company | N | TULARE | TULARE | 2023-02-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | CITY OF TULARE | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor failed to pot hole service while excavating and damaged the service, crew repaired service and reinstated.
Southern California Gas Company | N | TULARE | TULARE | 2023-03-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | DAWSON-MAULDIN LLC | SELMA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged a 1/2 plastic gas line crew made permanent repairs.
Southern California Gas Company | N | TULARE | TULARE | 2023-03-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | DAWSON-MAULDIN LLC | SELMA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged a 1/2 plastic gas line, crew made permanent repairs.
Southern California Gas Company | N | TULARE | TULARE | 2023-01-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | RENEW AGE | EL SEGUNDO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service while trenching for electrical line, service was marked and visible. Contractor did not pothole.
Southern California Gas Company | N | TULARE | TULARE | 2023-07-26 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 36 | 31 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | FLOYD JOHNSTON CONSTRUCTION | CLOVIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged a 1/2 plastic gas line while working to install a sewer lateral, damaging party failed to pot hole the 1/2 plastic gas line.
Southern California Gas Company | N | TULARE | TULARE | 2023-08-23 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | SALVADOR GAMBOA | TULARE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was excavating to install drainage lines. Homeowner did not call 811.
Southern California Gas Company | N | TULARE | TULARE | 2023-07-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 4 |  | FLOYD JOHNSTON CONSTRUCTION | CLOVIS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was installing sewer line when they damaged our service, contractor had previously pot holed service but failed to notify the new operator that the service was in their excavation.
Southern California Gas Company | N | TULARE | VISALIA | 2023-06-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | WEST VALLEY CONSTRUCTION COMPANY | VISALIA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor damaged unmarked 1 plastic gas line, crew made permanent repairs. MUR being done, ETD being counseled.
Southern California Gas Company | N | TULARE | VISALIA | 2023-09-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ROBERT MARKS PLUMBING | VISALIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | SCG crew responded to RFA for a damaged gas line, upon arrival, crew found damaged 1/2 plastic gas line. During repairs, it was determined that 3rd party contractor Robert S Marks Plumbing was excavating for water line repairs, they failed to pothole the gas line.
Southern California Gas Company | N | TULARE | VISALIA | 2023-07-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | SOCAL EDISON | TULARE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | SCE was excavating to repair electric line and damage
Southern California Gas Company | N | TULARE | VISALIA | 2023-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | TINO''S FENCE INC | VISALIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor was excavating to replace a fence post, he damaged a 1/2 plastic gas line, SCG crew made permanent repairs. Damaging party failed to notify USA.
Southern California Gas Company | N | TULARE | VISALIA | 2023-12-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | CARLOS VASQUEZ | VISALIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged a 1/2 plastic gas line while trenching for electric line. No record of a valid USA ticket.
Southern California Gas Company | N | TULARE | VISALIA | 2023-04-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | RAFAEL RIVERA | VISALIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer was digging for fence post without USA
Southern California Gas Company | N | TULARE | VISALIA | 2023-02-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | BOTHOF CONSTRUCTION | VISALIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged a 1/2 plastic gas line, crew made permanent repairs, contractor was educated about USA law.
Southern California Gas Company | N | TULARE | VISALIA | 2023-04-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | GOOD GUY ELECTRIC AND SOLAR | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was excavating to install electrical line, contractor did not pot hole gas service prior to excavating and damaged service.
Southern California Gas Company | N | TULARE | VISALIA | 2023-11-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | TONY CASARES | VISALIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was excavating for electrical project with hand tools and damaged a 1/2 plastic gas line. No valid USA
Southern California Gas Company | N | TULARE | VISALIA | 2023-06-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | FRANCISCO OCEGUEDA | VISALIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | damaged service repaired by crew, contractor damaged while hand excavating, usa good marks good.
Southern California Gas Company | N | TULARE | VISALIA | 2023-03-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | DANIEL CASTELLANOS | VISALIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged a 1/2 plastic gas line while digging to install a fence, crew made permanent repairs, damaging party was educated about USA law.
Southern California Gas Company | N | TULARE | VISALIA | 2023-06-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | JORGE ZAMARRIPA | VISALIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged a 1/2 plastic gas line while excavating to install electrical conduit, crew made permanent repairs, contractor was educated about USA law.
Southern California Gas Company | N | TULARE | VISALIA | 2023-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | LEO TIDWELL EXCAVATION CORP | SELMA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor failed to pot hole gas service that was marked prior to machine excavating, contractor damaged 1/2 service. Crew squeezed and repaired service line.
Southern California Gas Company | N | TULARE | VISALIA | 2023-08-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | JP ELECTRICAL SOLAR INC | VISALIA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | 3rd party contractor was excavating to install electrical line and damaged a 1/2 plastic gas line, crew made permanent repairs.
Southern California Gas Company | N | TULARE | VISALIA | 2023-03-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | CHARTER OAK LANDSCAPE DEVELOPMENT | VISALIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was installing electrical line and damaged our service, service was marked and visible.
Southern California Gas Company | N | TULARE | VISALIA | 2023-07-20 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Augur | 0.75 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | GABE LEON | PORTERVILLE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor damaged a 3/4 steel gas line while augering to install an anchor.
Southern California Gas Company | N | TULARE | VISALIA | 2023-02-03 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | CALTECH ELECTRICAL SERVICES INC | VISALIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged a 2 plastic main, crew made permanent repairs. Contractor was educated about USA law.
Southern California Gas Company | N | TULARE | VISALIA | 2023-08-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | GOOD GUYS ELECTRIC AND SOLAR | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor was excavating to install electrical line and damaged a 1/2 plastic gas line, crew made permanent repairs.
Southern California Gas Company | N | TULARE | VISALIA | 2023-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | GOOD GUYS ELECTRIC AND SOLAR | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was installing electrical lines for solar and damaged service while excavating with a shovel.
Southern California Gas Company | N | TULARE | VISALIA | 2023-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | JORGE PEINADO | VISALIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service while excavating to repair sewer line, customer did not have a valid USA ticket.
Southern California Gas Company | N | TULARE | VISALIA | 2023-03-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ROBERSON-MCLAUGHLIN | VISALIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | Contractor was excavating to repair sewer without a usa ticket and damaged our service with a shovel.
Southern California Gas Company | N | TULARE | VISALIA | 2023-06-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 13 |  | PLUMB LOCO | VISALIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged a 1 plastic gas line while excavating for water repairs, crew made permanent repairs. Contractor was educated about USA law.
Southern California Gas Company | N | TULARE | VISALIA | 2023-03-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 3 |  | RT NELSON | IVANHOE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was repairing water line and damaged our service, service was marked and visible.
Southern California Gas Company | N | TULARE | VISALIA | 2023-08-08 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 4 |  | GOOD GUYS PLUMBING | VISALIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Crew responded to emergency call for a damaged 2 plastic main, 3rd party contractor was trenching without notifying USA for sewer repairs and damaged a 2 plastic main.
Southern California Gas Company | N | TULARE | VISALIA | 2023-11-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DOMINIC BIANCHI | VISALIA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged a 1/2 plastic gas line.
Southern California Gas Company | N | TULARE | VISALIA | 2023-12-08 | Third party excavation damage | A service line with an excess flow valve installed | Steel | Hand Tools | 0.75 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ASPHALT SEALING AND REPAIR | VISALIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Excavating to install handicap signs when they damaged 1 plastic service. Contractor did not notify USA.
Southern California Gas Company | N | TULARE | VISALIA | 2023-08-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | WESLEY DAGGETT | VISALIA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was repairing their sewer line and hit our gas service while excavating. Homeowner did not call USA dig alert.
Southern California Gas Company | N | TULARE | VISALIA | 2023-08-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | DURANGO FENCING INC | VISALIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Fence contractor previously damaged service. Crew repaired and aireated.
Southern California Gas Company | N | TULARE | VISALIA | 2023-12-26 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  |  | NA | AUTRY PLUMBING | FRESNO | CA | N | Y | Excavation occured on private property by a non-contractor. | No | No | No | No | No | No | Damaged a 2 plastic main while excavating to install water lines to new house. Contractor did not have a valid USA ticket.
Southern California Gas Company | N | TULARE | VISALIA | 2023-08-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Trencher | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | RAINSCAPE | VISALIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | SCG crew responded to 3rd party damage, upon arrival, found damaged 1 plastic gas line by 3rd party contractor excavating for irrigation project, crew made permanent repairs.
Southern California Gas Company | N | TULARE | VISALIA | 2023-08-21 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ASPHALT DESIGN BY JUAN GOMEZ | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | SCG crew responded to 3rd party damage, upon arrival, crew found a damaged 1 plastic gas line, crew made permanent repairs. Damaging party failed to pothole as required.
Southern California Gas Company | N | TULARE | VISALIA | 2023-06-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | MALIBU PACIFIC CONST | NA |  | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor damaged a 1 plastic gas line that was mised marked, crew made permanent repairs.
Southern California Gas Company | N | TULARE | VISALIA | 2023-08-17 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 60 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | LAZAR UNDERGROUND | FRESNO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor was excavating in joint trench to repair a telecommunications line. Contractor damaged a 2 plastic main.
Southern California Gas Company | N | TULARE | VISALIA | 2023-04-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 55 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | GREGORIO MANUEL GARCIA | VISALIA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service damage with no EFV and no USA called.
Southern California Gas Company | N | TULARE | WOODLAKE | 2023-05-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 8 |  | JESUS BALTAZAR | WOODLAKE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant damaged a 1 plastic gas line while working to install a fence, crew made permanent repairs. Damaging party was educated about USA law.
Southern California Gas Company | N | VENTURA | BELL CANYON | 2023-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 30 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | FERNCO CO | WOODLAND HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd. party contractor hit service with shovel while digging for irrigation. No USA
Southern California Gas Company | N | VENTURA | BELL CANYON | 2023-08-23 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MAUREEN ZELLER | BELL CANYON | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Gardner was digging to install drain when he hit plastic line with shovel. Crew showed up and made permanent repairs
Southern California Gas Company | N | VENTURA | BELL CANYON | 2023-04-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 37 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3001 |  | 1 |  | UNLICENSED DAY LABORERS | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | home owner hired people to install new drain. while digging they struck plastic line with shovel. no usa
Southern California Gas Company | N | VENTURA | CAMARILLO | 2023-07-14 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 40 | 40 | N | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | EDDIE | NORTH HILLS | CA | N | Y | Yes | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | A 3rd party contractor damaged the wrap on a 3/4 steel service while excavating with hand tools for the sewer. The USA ticket was expired.
Southern California Gas Company | N | VENTURA | CAMARILLO | 2023-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | ALAN PENUELA | CAMARILLO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | A contractor working for the homeowner damaged a 1/2 plastic service while trenching for a retaining wall. There was a valid USA but the homeowner and contractor did not maintain the marks.
Southern California Gas Company | N | VENTURA | CAMARILLO | 2023-02-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | GRUBER GRADING & AG | OAK VIEW | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Construction company damaged a 1/2 Pla service while digging and grading in the fron yard of address. Contractor did not have a valid usa.
Southern California Gas Company | N | VENTURA | CAMARILLO | 2023-07-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | JOSE GARCIA | CAMARILLO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Customer digging to repair sewer line when they damaged mismarked gas service.
Southern California Gas Company | N | VENTURA | CAMARILLO | 2023-06-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | OXNARD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged gas facilities within the delineation area, Facilities were marked correctly with yellow flags.
Southern California Gas Company | N | VENTURA | CAMARILLO | 2023-01-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Probing Device | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | DREW BLAISDELL | CAMARILLO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | According to home owner, 3rd party contractor was probing and accidentally struck gas service.
Southern California Gas Company | N | VENTURA | CAMARILLO | 2023-04-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MICHAEL GARNICA | CAMARILLO | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged half inch service with shovel while digging to install electrical line
Southern California Gas Company | N | VENTURA | CAMARILLO | 2023-05-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | FIBER TEL COMMUNICATIONS | SYLMAR | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged 1 PLA service while potholing for utilities. The service was marked with yellow paint and flags.
Southern California Gas Company | N | VENTURA | CAMARILLO | 2023-05-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | FIBER TEL COMMUNICATIONS | SYLMAR | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | A 3rd party contractor damaged a 1 stub while boring, Contractor had a valid USA. Spoke with contractor to encourage potholing and communication if necessary.
Southern California Gas Company | N | VENTURA | CAMARILLO | 2023-05-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | MAMMOTH EXCAVATING INC | NEWBURY PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | A 3rd party contractor damaged a 1/2 CTS service while excavating with a mini excavator for water and power lines.
Southern California Gas Company | N | VENTURA | CAMARILLO | 2023-11-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | SAP CONSTRUCTION | GRANADA HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Third party contractor was trenching without a USA ticket and damaged our 1/2 PLA service
Southern California Gas Company | N | VENTURA | CAMARILLO | 2023-09-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | CID BUILDERS | RESEDA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While excavating with hand tools a 3rd party contractor damaged a 1/2 PLA service. There was no USA
Southern California Gas Company | N | VENTURA | FILLMORE | 2023-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CITY OF FILLMORE | FILLMORE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Probing with a sharpened pole to find their waterline. In the process the 1/2 PLA service was struck and damaged. There was a valid USA with correct markings.
Southern California Gas Company | N | VENTURA | FILLMORE | 2023-10-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 3 | 60 | 30 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | FIBERTEL COMMUNICATIONS | SYLMAR | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor struck 3 gas service that feeds mobile home park with no USA
Southern California Gas Company | N | VENTURA | FILLMORE | 2023-04-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | DEVIL MOUNTAIN NURSERY | FILLMORE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | contractor damaged 1 pla service while digging with a backhoe without a valid USA ticket
Southern California Gas Company | N | VENTURA | MOORPARK | 2023-11-14 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 6 | 60 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 30001 |  | 2 |  | SECURITY PAVING COMPANY INC | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Hit 6 plastic main with excavator while digging trench for water main replacement.
Southern California Gas Company | N | VENTURA | MOORPARK | 2023-05-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | SECURITY PAVING | WESTLAKE VILLAGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor was grading lot with NO USA when they damaged 3/4 steel stub service. Crew abandoned stub at SMC for permanent repairs.
Southern California Gas Company | N | VENTURA | MOORPARK | 2023-09-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | V TOL | MOORPARK | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | NA
Southern California Gas Company | N | VENTURA | MOORPARK | 2023-08-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | CAROLINA LAMAS | MOORPARK | CA | N | Y | Yes | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Customer was using a backhoe to dig behind his retaining wall and struck the unmarked gas service. Ticket was not valid until Friday.
Southern California Gas Company | N | VENTURA | MOORPARK | 2023-08-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | OUTDOOR CREATIONS | THOUSAND OAKS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor digging to remove tree damaged 1/2 plastic service. No USA
Southern California Gas Company | N | VENTURA | MOORPARK | 2023-03-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | QUALTEX WIRE LINE | SANTA ANA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor digging with NO USA heard hissing and backfilled gas service to avoid the smell.
Southern California Gas Company | N | VENTURA | NEWBURY PARK | 2023-06-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | RONALD GORECKI | NEWBURY PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was grading part of his property with no USA and as he was grading, he struck the half inch plastic service line. Crew arrived and fixed service.
Southern California Gas Company | N | VENTURA | NEWBURY PARK | 2023-07-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | HARRY WRIGHT | NEWBURY PARK | CA | N | Y | Yes | Excavation occurred on private property by a non-contractor. | No | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 1/2 service while digging a trench with a mini excavator.
Southern California Gas Company | N | VENTURA | NEWBURY PARK | 2023-06-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | BRUCE CORNETT MASONRY CONSTRUCTION | THOUSAND OAKS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Dig-in by 3rd party contractor
Southern California Gas Company | N | VENTURA | NEWBURY PARK | 2023-11-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | JEFF TRIFIRO | NEWBURY PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Handyman was digging to install fence posts and struck service going to meter. No USA called.
Southern California Gas Company | N | VENTURA | NEWBURY PARK | 2023-04-14 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 10 |  | MD ENGINEERING | SIMI VALLEY | CA | N | Y | Yes | No | No | Yes | No | Yes | Yes | Contractor was digging for Sewer install when they hit the main with Mini excavator.
Southern California Gas Company | N | VENTURA | NEWBURY PARK | 2023-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SOCAL EDISON | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner was clearing area to build a deck. He was cutting some roots out of the way but accidentally cut into the 3/4 steel service line with sawzall. There were old flags that marked the service line.
Southern California Gas Company | N | VENTURA | OAK PARK | 2023-01-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | SAMANTHA KANE | OAK PARK | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged the 1/2 plastic service with a hand shovel.
Southern California Gas Company | N | VENTURA | OAK VIEW | 2023-04-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ROBERTO ALVAREZ | SANTA PAULA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 1/2 pla service while digging with a backhoe.
Southern California Gas Company | N | VENTURA | OJAI | 2023-07-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | JERRY KOUS PLUMING | VENTURA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | A 3rd party contractor excavating to work on sewer damaged a 1/2 IPS service with a shovel and had no valid USA
Southern California Gas Company | N | VENTURA | OJAI | 2023-04-04 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | BURNS PACIFIC | THOUSAND OAKS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Party contractor excavating a trench for a new water main damaged a visibly marked 3/4 service with an excavator. The contractor had a valid USA with accurate marks and failed to pothole the gas service.
Southern California Gas Company | N | VENTURA | OJAI | 2023-10-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DOWER CONSTRUCTION | THOUSAND OAKS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd Party contractor damaged a 1/2 PLA service near the riser while digging with hand tools. The contractor was trenching for private utilities. There was valid USA with valid markings.
Southern California Gas Company | N | VENTURA | OJAI | 2023-12-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MORSE STONE AND MASONRY | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | A 3rd party contractor damages a 1/2 PLA service with hand tools while digging trenches for a drain. There was no USA.
Southern California Gas Company | N | VENTURA | OJAI | 2023-10-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 55 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | HANEY LANDSCAPE | OJAI | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor installing conduit for electrical damaged a 1/2 plastic service with hand tools.
Southern California Gas Company | N | VENTURA | OJAI | 2023-01-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 5 |  | CUSTOM CONTURE | VENTURA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | 3rd Party contractor damaged gas service at SMC while digging for a damaged water service that was also caused by them. The 3rd party contractor dug outside of the original USA brackets and failed to amend the USA ticket with new addresses and brackets.
Southern California Gas Company | N | VENTURA | OXNARD | 2023-09-21 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | ARB | LAKE FOREST | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | SoCalGas contractor damaged 1/2 PLA service while digging to install new service.
Southern California Gas Company | N | VENTURA | OXNARD | 2023-12-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | DETRAN RAMIREZ | OXNARD | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Pulled out a tree and in that process pulled on the service and started leaking
Southern California Gas Company | N | VENTURA | OXNARD | 2023-11-06 | Third party excavation damage | Main | Steel | Augur | 2 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2001 |  | 1 |  | 2R DRILLING | CHINO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor was using augur in street and struck our 2 steel main.
Southern California Gas Company | N | VENTURA | OXNARD | 2023-10-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | RR ELECTRIC | MOORPARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged a 1/2 PLA service with a shovel. Service was exposed, there was a valid USA and marked correctly.
Southern California Gas Company | N | VENTURA | OXNARD | 2023-04-03 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 45 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LIGHT AND POWER | VENTURA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd Party contractor was excavating in a new build work area with no valid USA and damaged a 2 gas main while trenching.
Southern California Gas Company | N | VENTURA | OXNARD | 2023-05-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | OSCAR CHILE | OXNARD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 1/2 service while digging to install waterline to ADU
Southern California Gas Company | N | VENTURA | OXNARD | 2023-11-16 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 4 |  | MARC SANCHEZ | OXNARD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Digging to locate a service and damaged our 1 PLA main.
Southern California Gas Company | N | VENTURA | OXNARD | 2023-01-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | PAUL EDMUNDS | OXNARD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor fixing a water service for a business damaged a 1 plastic service in private property, Contractor did not have a valid USA.
Southern California Gas Company | N | VENTURA | OXNARD | 2023-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | J VEGA ENGINEERING INC | OXNARD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | 3rd party contractor digging a trench for a water main on San Clemente Ave stuck the service for 3200 Ocean Dr Oxnard. Mapping and service history showed the service for 3200 Ocean Dr. coming off of Ocean Dr. and not San Clemente Ave.
Southern California Gas Company | N | VENTURA | OXNARD | 2023-08-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | TM ELECTRIC | SANTA PAULA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While excavating a trench with hand tools a 3rd party contractor installing a conduit damaged a 1/2 plastic service. There was no valid USA
Southern California Gas Company | N | VENTURA | OXNARD | 2023-10-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MALISKA CONSTRUCTION | OAK VIEW | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While working to install grounding rods a 3rd party contractor damaged a 1/2 PLA CTS service. There was no Valid USA
Southern California Gas Company | N | VENTURA | OXNARD | 2023-09-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | R&S CONSTRUCTION | VENTURA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged 1/2 service with pothole digger while excavating to pour footing for fence post.
Southern California Gas Company | N | VENTURA | OXNARD | 2023-08-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | MJD CONCRETE WORKS INC | AGOURA HILLS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While framing for concrete a 3rd party contractor damaged a 1 PLA service with a wooden stake. There was no valid USA for the concrete contractor.
Southern California Gas Company | N | VENTURA | OXNARD | 2023-02-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | MANNIGER ELECTRIC | SANTA CLARA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Damaged 2 pla stub w/ EFV. Damaged by contractor digging with no USA. Stub capped for temp repairs due to lack of couplings for proper repair.
Southern California Gas Company | N | VENTURA | OXNARD | 2023-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | RICHARD ZAMECKI | OXNARD | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged 3/4 stub whille excavating. The stub was not marked and was not in our service records.
Southern California Gas Company | N | VENTURA | PORT HUENEME | 2023-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | DLT CONTRUCTION | OXNARD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged while hand digging for sewer repairs. Contractor damaged the 1/2 plastic service while hand tools. There was no valid USA called in.
Southern California Gas Company | N | VENTURA | PORT HUENEME | 2023-12-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | TAURINO LOPEZ | PORT HUENEME | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Worker cut into a encased copper service thinking it was a water line.
Southern California Gas Company | N | VENTURA | SANTA PAULA | 2023-04-16 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | 1ST DEMO INC | SANTA PAULA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor had a valid USA but the addresses were very confusing. Will speak to locator and have a counseling session
Southern California Gas Company | N | VENTURA | SANTA PAULA | 2023-07-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | TIBURCIO ZAMORA | SANTA PAULA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While grading front yard the homeowner damaged a 1/2 CTS Plastic service that was inserted in an abandoned 1 steel yardline. There was no valid USA called in for this address.
Southern California Gas Company | N | VENTURA | SANTA PAULA | 2023-08-11 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | CD LYON INC | VENTURA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | A 3rd party contractor excavating for repairs on a pipeline damaged a 1/2 plastic service with a backhoe. There was a valid USA. Locator had a weak signal and mapping/records were wrong.
Southern California Gas Company | N | VENTURA | SANTA PAULA | 2023-03-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 6 |  | TORO ENTERPRISES | OXNARD | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Toro severed pla service with excavator while installing sewer line.
Southern California Gas Company | N | VENTURA | SANTA PAULA | 2023-05-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ARMONDO VAZQUEZ | SANTA PAULA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit 1/2 PLA Service while trenching.
Southern California Gas Company | N | VENTURA | SANTA ROSA VALLEY | 2023-10-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | ALL AMERICAN PLUMBING & DRAIN | OXNARD | CA | N | Y | Yes | Yes | Yes | Yes | No | No | Yes | Contractor damaged 1/2 plastic service in yard. USA was current and marks were good. Contractor removed flags in yard
Southern California Gas Company | N | VENTURA | SANTA ROSA VALLEY | 2023-01-24 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | WALKER HOME REMODELING | THOUSAND OAKS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit Service while doing electrical work.
Southern California Gas Company | N | VENTURA | SANTA ROSA VALLEY | 2023-04-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | JMR LANDSCAPE DESIGN | OXNARD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Plumber damaged 1/2 PLA service with shovel while digging to repair a sewer line
Southern California Gas Company | N | VENTURA | SIMI VALLEY | 2023-07-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BILL DALATI | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No USA.
Southern California Gas Company | N | VENTURA | SIMI VALLEY | 2023-06-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MARTY VASQUEZ | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor with NO USA was digging for drainage when the damaged 1/2 plastic service.
Southern California Gas Company | N | VENTURA | SIMI VALLEY | 2023-06-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | WAYNE INOLIA | SIMI VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging with expired USA, marks good and visible. Repaired 1/2 stub svc inch
Southern California Gas Company | N | VENTURA | SIMI VALLEY | 2023-09-22 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | USA BUILDERS AND CONSTRUCTION | ANAHEIM | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor damaged 2 PLA service with backhoe. Service was marked correctly.
Southern California Gas Company | N | VENTURA | SIMI VALLEY | 2023-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ABRAHAM YOUSEF | SIMI VALLEY | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor hit service while digging trench for electrical conduit.
Southern California Gas Company | N | VENTURA | SOMIS | 2023-10-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 45 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | POLI LOPEZ | SOMIS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor struck 1 service line in drive way with no USA
Southern California Gas Company | N | VENTURA | SOMIS | 2023-12-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ASSOCIATED SOILS ENG | SIGNAL HILL | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | A 3rd party contractor damages a 2 PLA service while auguring for soil samples. There was a valid USA.
Southern California Gas Company | N | VENTURA | SOMIS | 2023-06-27 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | HERMAN WEISSKER INC | NA |  | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Herman Weissker employee damaged a 1/2 plastic service while potholing for that service with hand tools. There was a valid USA and marks were marked correctly. Employee failed to pothole carefully around the gas facilities.
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2023-10-09 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | ELKINGTON CONSTRUCTION | NEWBURY PARK | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor failed to maintain adequate separation while digging around the SCG Pipe.
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2023-09-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Boring Equipment | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | PACIFIC WEST COMMINCATIONS | SAN DIMAS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | While boring for electric conduits contractor damaged 1/2 service. Contractor had potholed service but failed to maintain clearance during boring operation.
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2023-02-03 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 1 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | NA | WESTLAKE VILLAGE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | No gas found by M&R tech setting MSA. Distribution found 1 plastic service line with EFV had been damaged by an unknown source.
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2023-10-06 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 3 |  | ARIZONA PIPELINE | NORTH HILLS |  | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Company Contractor hit 2" plastic main with backhoe while digging trench for new gas main installation.
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2023-11-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | LORI PECKIKONIS | THOUSAND OAKS | CA | N | Y | Yes | Excavation occurred on private property by a non-contractor. | Yes | Yes | No | Yes | Yes | Homeowner excavating to repair private sewer line damaged the 1/2 IPS plastic service with a mini excavator. USA was expired and markings were not maintained.
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2023-09-19 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | ARIZONA PIPELINE | NORTH HILLS | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 2nd party damage to 1/2 plastic service.
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2023-07-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  |  | NA | PRO LAWNS | THOUSAND OAKS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor hit 1/2 PLA IPS service with a hand tool with potholing for fencing post.
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2023-01-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | SHREWBERRY PLUMBING | WOODLAND HILLS | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor was digging and exposed 2 pla line. Called for SoCal to come out to verify line. ETD was unable to verify if line was a company facility. Contractor drilled into casing and found no leaks. Cut into line with saw and damaged 1/2 cts service. Marks were not good and service history shows 1/2 plastic in 2 casing.
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2023-11-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 2 |  | MCLM LANDSCAPE AND MAINTENANCE CORPORATION | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor digging to install drain line with no USA damaged 1/2 plastic service
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2023-12-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DALANGHAUS | LAKE ELSINORE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Valid USA. 3rd party failed to maintain caution around pipeline
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2023-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | ARTISTIC DESIGN | NA |  | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | The damaging party claimed to have a valid USA but no ticket number was provided and field supervision could not find a valid ticket.
Southern California Gas Company | N | VENTURA | THOUSAND OAKS | 2023-07-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Trencher | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | STEVE ALLEN | THOUSAND OAKS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Homeowner hit 1/2 plastic service while trenching for SCE panel.
Southern California Gas Company | N | VENTURA | VENTURA | 2023-11-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | DAVID GUZMAN CONSTRUCTION | VENTURA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While excavating for water services a 3rd party contractor damaged a 1/2 plastic service with hand tools. There was no valid USA
Southern California Gas Company | N | VENTURA | VENTURA | 2023-04-05 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | ANGEL ALVARADO | FILLMORE | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged a 1 service stub with a backhoe. There was no valid USA for this job.
Southern California Gas Company | N | VENTURA | VENTURA | 2023-10-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 42 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | BRC CONSTRUCTION | SANTA BARBARA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party Contractor was digging with no USA and struck 1/2 IPS service line.
Southern California Gas Company | N | VENTURA | VENTURA | 2023-03-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 59 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | MR. ROOTER PLUMBER | VENTURA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | 3rd party contractor damaged 1/2 service while excavating with a shovel to make sewer repairs
Southern California Gas Company | N | VENTURA | VENTURA | 2023-05-22 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA |  | NA | M R LANDSCAPING | VENTURA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | A 3rd party contractor damaged a 1/2 service with an excavator while digging for utilities.
Southern California Gas Company | N | VENTURA | VENTURA | 2023-09-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | SAM HILL & SONS INC | VENTURA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While excavating for wall footings, service was struck. No USA was called for this work.
Southern California Gas Company | N | VENTURA | VENTURA | 2023-07-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  |  | NA | BSN CONSTRUCTION | VENTURA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Third party contractor damaged stub that was marked by measurements.
Southern California Gas Company | N | VENTURA | VENTURA | 2023-08-29 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Miscellaneous/Other | 0.75 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 2 |  | HOMEOWNER | VENTURA | CA | N | Y | Excavation occured on private property by a non-contractor. | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | While coring for a fence post a 3rd party contractor working for the homeowner damaged a 3/4 steel service. There was no valid USA
Southern California Gas Company | N | VENTURA | VENTURA | 2023-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | SAM HILL & SONS INC | VENTURA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Third party contractor damaged 1/2 service while digging in street. Service was clearly marked less than a foot away from excavation.
Southern California Gas Company | N | VENTURA | VENTURA | 2023-12-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 2 |  | PROVIDER FENCES | OXNARD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Installing a new fence damaged a 1/2 service while excavating for the fence post. There was no valid USA.
Southern California Gas Company | N | VENTURA | VENTURA | 2023-09-26 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  |  | NA | 1 |  | VENTURA WATER CO | VENTURA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Water company damaged a 1/2 CTS service while installing a new water service with their backhoe. There was a valid USA and gas service markings were correct. Water company failed to pothole.
Southern California Gas Company | N | VENTURA | WESTLAKE VILLAGE | 2023-03-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | VINYL CONCEPTS | NEWBURY PARK | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor Digging With No Usa Damaged 1/2 Plastic Service.
Southern California Gas Company | N | VENTURA | WESTLAKE VILLAGE | 2023-03-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1001 |  | 1 |  | NEW VIEW LANDSCAPE | CALABASAS | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor performing landscaping work with NO USA damaged 1/2 CTS service.
Southern California Gas Company | N | VENTURA | WESTLAKE VILLAGE | 2023-11-02 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 50 | 45 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | MILESTONE BUILDERS | THOUSAND OAKS | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | 3rd party contractor struck 1/2 service.
Southern California Gas Company | Y | KINGS | LEMOORE | 2023-08-30 | Third party excavation damage | Transmission Line in a non-HCA area | Steel | Farm Equipment | 20 | 400 | 367 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 344086 |  | 0 |  | STONE LAND CO | STRATFORD | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | On 8/30/2023, SoCalGas crews responded to a third-party damage on L-800 at Nevada Ave & 30th Ave, Lemoore, Kings County. Upon investigation, the 20-inch transmission line was found to be punctured with farming equipment, ripper, causing a release of natural gas. Repairs have been completed as of 08/31/2023, and service had been restored. No injuries or fatalities resulted from this incident. This incident was reported to the DOT and CPUC due to gas release and damages exceeding $139,700. Investigation of the incident determined the third-party contractor was operating without a USA ticket. Accordingly, the incident was also reported to the CA Underground Safety Board (Report# OID28_20230919101530).
Southern California Gas Company | Y | LOS ANGELES | SOUTH GATE | 2023-09-26 | Third party excavation damage | Main | Steel | Grader/Scraper | 6 | 50 | 50 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 55206 |  | 0 |  | VICK CONSTRUCTION | YUCAIPA | CA | N | Y | No | Excavation occurred on private property by a non-contractor. | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | On 9/26/2023 SoCalGas responded to an excavation incident. A third-party contractor struck a 6in steel gas main with grading equipment which caused the release of natural gas. SoCalGas crews controlled the flow of gas and abandoned the main as part of the permanent repairs. Upon investigation of the incident, it was discovered that the third-party contractor was performing excavation activities without a valid USA ticket. There were no injuries or fatalities as a result of this incident. This incident was reported to the CPUC once SoCalGas was made aware of media coverage and then reported to DOT once gas release reached 3MM.
Southern California Gas Company | Y | LOS ANGELES | WALNUT | 2023-10-13 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 8 | 52 | 47 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 56984 |  | 0 |  | T-9 ENTERPRISES | LA VERNE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | On 10-13-2023, a third-party contractor damaged an 8-inch steel gas main at 4200 Valley Blvd, Walnut, CA while grading. SoCalGas crew responded and controlled the release of gas. There were no injuries or further damage resulting from this incident. Investigation of the incident showed there was a valid USA ticket. However, the contractor''s excavation practices were inadequate as it failed to pot-hole the 8-inch main. This incident was reported to DOT and CPUC due to gas release exceeding 3,000,000 cubic feet.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2023-10-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 316 |  | 1 |  | TAHOE HOME REPAIR SERVICES | SOUTH LAKE TAHOE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was digging holes for deck footings and damaged service with a shovel.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2023-09-19 | Third party excavation damage | Main | Polyethylene Pipe | Hand Tools | 2 | 35 | 35 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 95 |  | 0 |  | MEARS | CARSON CITY | NV | N | Y | Yes | No | Yes | Yes | No | Yes | Yes | Contractor was hand digging for gas service and damaged main with a sharpshooter.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2023-09-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 479 |  | 0 |  | UNKNOWN | NA |  | N | Y | No | No | No | No | No | No | Yes | Previous damage on a service line was discovered while investigating a leak.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2023-01-12 | Third party excavation damage | Meter | Polyethylene Pipe | Miscellaneous/Other | 0.75 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | UNKNOWN | NA |  | N | N | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | Yes | Vehicle vs. MSA
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2023-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 434 |  | 1 |  | OCCUPANT | SOUTH LAKE TAHOE | CA | N | N | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | Yes | Homeowner damaged service line with an axe while removing a tree root.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2023-09-07 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 43 | 43 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 1790 |  | 0 |  | VINCIGUERRA CONSTRUCTION | JACKSON | CA | N | Y | Yes | Yes | No | No | No | Yes | Yes | Contractor damaged service that was mapped incorrectly.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2023-08-15 | Third party excavation damage | Miscellaneous/Other | Miscellaneous/Other | Hand Tools | 2 | 43 | 43 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 189 |  | 0 |  | VINCIGUERRA CONSTRUCTION | JACKSON | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged the wrap on the steel main.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2023-09-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 582 |  | 1 |  | MEARS | CARSON CITY | NV | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor was potholing an unlocatable gas service for a trouble locate and hit a 1/2-inch service with a shovel.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2023-05-10 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 199 |  | 1 |  | RYAN YOUNG | VERDI | NV | N | Y | No | No | No | No | No | No | No | Contractor damaged service while working on sewer/septic lines.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2023-08-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.75 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 411 |  | 0 |  | TIESLAU EXCAVATING | SOUTH LAKE TAHOE | CA | N | Y | No | No | No | No | No | No | Yes | Contractor damaged service stub.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2023-06-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 40 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 920 |  | 1 |  | GM LANDSCAPE | SOUTH LAKE TAHOE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Landscaper damaged service with a pick axe.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2023-08-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 488 |  | 1 |  | TAHOE BEAR BOX | CARNELIAN BAY | CA | N | Y | No | No | No | No | No | No | Yes | Contractor damaged service with a shovel while installing a bear box.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2023-02-16 | Third party excavation damage | Miscellaneous/Other | Miscellaneous/Other | Miscellaneous/Other | 0 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 212 |  | 1 |  | SOUTH TAHOE REFUSE | SOUTH LAKE TAHOE | CA | N | N | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | Yes | South Tahoe Refuse was removing snow and ice from roof, falling ice damaged ERT.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2023-10-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 275 |  | 1 |  | OCCUPANT | SOUTH LAKE TAHOE | CA | N | Y | No | Yes | Yes | Yes | No | Yes | Yes | Homeowner damaged service line with a shovel while attempting to remove a bear box.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2023-09-12 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Hand Tools | 0.75 | 35 | 35 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 189 |  | 0 |  | LIBERTY UTILITIES | TAHOE VISTA | CA | N | Y | No | No | No | No | No | No | No | Contractor damaged the wrap on steel service during exposure while hand digging.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2023-07-01 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Augur | 0.75 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 873 |  | 2 |  | OCCUPANT | SOUTH LAKE TAHOE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | Yes | The contractor damaged serviceby digging with an auger.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2023-09-25 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 0.5 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 238 |  | 1 |  | GARDEN ART LANDSCAPING | SOUTH LAKE TAHOE | CA | N | N | No | No | No | No | No | No | Yes | Contractor damaged pipe with a skid steer.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2023-06-26 | Third party excavation damage | Main | Steel | Not Available | 0.75 | 60 | 60 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 89 |  | 0 |  | UNKNOWN | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | Yes | Contractor was hand digging to install new drainage lines and uncovered a previously damaged steel main line.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2023-10-28 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1347 |  | 1 |  | OCCUPANT | SOUTH LAKE TAHOE | CA | N | Y | No | No | No | No | No | No | Yes | The occupant damaged gas line with a rebar stake.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2023-12-27 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Not Available | 0.75 | 35 | 35 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 135 |  | 0 |  | UNKNOWN | NA |  | N | Y | No | No | No | No | No | No | No | Damaged wrap discovered from previous excavation by unknown party.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2023-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.75 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1202 |  | 1 |  | OCCUPANT | SOUTH LAKE TAHOE | CA | N | Y | No | No | No | No | No | No | Yes | Contractor damaged service line with a mini excavator while installing a fence.
Southwest Gas Company | N | EL DORADO | SOUTH LAKE TAHOE | 2023-07-11 | Third party excavation damage | A service line with no excess flow valve installed | Steel | Backhoe/Trackhoe | 0.75 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1277 |  | 0 |  | VINCIGUERRA CONSTRUCTION | JACKSON | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged undocumented stub while digging to install new water main.
Southwest Gas Company | N | NEVADA | TRUCKEE | 2023-07-11 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 8 | 60 | 60 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 189 |  | 0 |  | RUPPERT INC | TAHOE CITY | CA | N | Y | No | Yes | Yes | Yes | Yes | Yes | Yes | Contractor damaged main with a ram hoe while trying to excavate for a conduit.
Southwest Gas Company | N | NEVADA | TRUCKEE | 2023-06-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 777 |  | 2 |  | LOPEZ EXCAVATING | TRUCKEE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | Contractor damaged service with a mini excavator while digging to repair the sewer that was possibly damaged during the installation of the gas line.
Southwest Gas Company | N | NEVADA | TRUCKEE | 2023-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 347 |  | 0 |  | VALCON | CUPERTINO | CA | N | Y | No | No | No | No | No | No | No | Contractor damaged service with an excavator.
Southwest Gas Company | N | NEVADA | TRUCKEE | 2023-09-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 60 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 396 |  | 1 |  | SHAFFER PAVING | TRUCKEE | CA | N | Y | Yes | Yes | No | Yes | No | Yes | No | Contractor damaged pipe sleeving with excavator during underground electrical work.
Southwest Gas Company | N | NEVADA | TRUCKEE | 2023-10-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 571 |  | 1 |  | OCCUPANT | TRUCKEE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Homeowner damaged service line with a mini excavator while trying to remove a tree stump.
Southwest Gas Company | N | NEVADA | TRUCKEE | 2023-06-20 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 35 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 384 |  | 0 |  | MAX-EX | SPARKS | NV | N | Y | No | No | No | No | No | No | No | Contractor damaged service stub with an excavator while doing underground electrical work.
Southwest Gas Company | N | NEVADA | TRUCKEE | 2023-07-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 573 |  | 1 |  | RUPPERT INC | TAHOE CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged pipe while working on water lines due to not following proper potholing procedures.
Southwest Gas Company | N | NEVADA | TRUCKEE | 2023-08-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 666 |  | 1 |  | RUPPERT INC | TAHOE CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged pipe with mini excavator without potholding.
Southwest Gas Company | N | NEVADA | TRUCKEE | 2023-09-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 431 |  | 1 |  | RUPPERT INC | TAHOE CITY | CA | N | Y | No | No | No | No | No | Yes | No | While digging for water lines, the excavator hit service line.
Southwest Gas Company | N | NEVADA | TRUCKEE | 2023-10-28 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1818 |  | 0 |  | MD CONSTUCTION & CONSULTING | TRUCKEE | CA | N | Y | No | No | No | No | No | No | Yes | Contractor damaged Main with a mini excavator while digging for water.
Southwest Gas Company | N | NEVADA | TRUCKEE | 2023-08-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 218 |  | 1 |  | HANSEN BROTHERS ENTERPRISES | GRASS VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Excavator failed to pothole the service and damaged service with an excavator while working on water lines.
Southwest Gas Company | N | NEVADA | TRUCKEE | 2023-08-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 60 | 60 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 405 |  | 0 |  | UNKNOWN | NA |  | N | Y | Yes | Yes | Yes | Yes | No | No | Yes | Contractor exposed the pipe and found a previously damaged on service. Unknown damaging party.
Southwest Gas Company | N | NEVADA | TRUCKEE | 2023-01-31 | Third party excavation damage | Riser | Steel | Miscellaneous/Other | 1 | 60 | 60 | Y | Y | Y | N | 0 | 0 |  | 0 | 0 |  | 965 |  | 1 |  | BARRAZA CONST. INC. | TRUCKEE | CA | N | N | No | No | No | No | No | No | Yes | Contractor was using mini excavator to push snow from property and damaged riser. They were not excavating so they did not have an 811 ticket.
Southwest Gas Company | N | NEVADA | TRUCKEE | 2023-08-24 | Third party excavation damage | Main | Steel | Backhoe/Trackhoe | 8 | 60 | 60 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 189 |  | 0 |  | UNKNOWN | NA |  | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | Contractor notified Southwest Gas of a previous nick in the pipe coating.
Southwest Gas Company | N | PLACER | CARNELIAN BAY | 2023-05-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 60 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 949 |  | 1 |  | HALLS EXCAVATING | TRUCKEE | CA | N | N | Yes | Yes | Yes | Yes | No | Yes | Yes | The contractor was digging to demolish the home and damaged service with a shovel.
Southwest Gas Company | N | PLACER | CARNELIAN BAY | 2023-07-17 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 6 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 5345 |  | 34 |  | Q & D CONSTRUCTION | RENO | NV | N | Y | Yes | Yes | No | Yes | No | No | Yes | Contractor damaged an inline tee with an excavator.
Southwest Gas Company | N | PLACER | CARNELIAN BAY | 2023-02-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2357 |  | 1 |  | UNKNOWN | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | Yes | Previous damage discovered on service, unknowned damage cause or damaging party.
Southwest Gas Company | N | PLACER | CARNELIAN BAY | 2023-11-02 | Operator excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Miscellaneous/Other | 1 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 407 |  | 0 |  | Q & D CONSTRUCTION | RENO | NV | Y | N | Yes | Yes | Yes | Yes | No | Yes | Yes | SWG contractor was cutting sleeving with string and went too far and cut into 1-inch PE.
Southwest Gas Company | N | PLACER | HOMEWOOD | 2023-08-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 572 |  | 1 |  | DAISY WHEEL CONSTRUCTION | TRUCKEE | CA | N | Y | No | No | No | No | No | No | No | Contractor damaged pipe with a post hole digger.
Southwest Gas Company | N | PLACER | HOMEWOOD | 2023-10-05 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1011 |  | 1 |  | THOMPSON BUILDERS | NOVATO | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | During building construction excavator was working outside marked area and hit main.
Southwest Gas Company | N | PLACER | KINGS BEACH | 2023-09-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 807 |  | 1 |  | DIY | KINGS BEACH | CA | N | Y | No | No | No | No | No | No | No | Homeowner was replacing a fence post and damaged service with a shovel.
Southwest Gas Company | N | PLACER | TAHOE CITY | 2023-10-07 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 813 |  | 0 |  | OCCUPANT | TAHOE CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Homeowner damaged service line with a mini excavator while digging for a power conduit.
Southwest Gas Company | N | PLACER | TAHOE CITY | 2023-07-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 519 |  | 1 |  | LINKEY AND SONS CONSTRUCTION | TAHOE CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | No | Contractor damaged service with mini excavator.
Southwest Gas Company | N | PLACER | TAHOE CITY | 2023-08-01 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 725 |  | 1 |  | SIERRA CON INC | SOUTH LAKE TAHOE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service with excavator while digging on the wrong side.
Southwest Gas Company | N | PLACER | TAHOE CITY | 2023-10-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 175 |  | 3 |  | LONGO INCORPORATED | TAHOE CITY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged PE main with a mini excavator while trenching for water due to incorrect locate marks.
Southwest Gas Company | N | PLACER | TAHOE VISTA | 2023-08-17 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 592 |  | 1 |  | OCCUPANT | CARNELIAN BAY | CA | N | Y | No | No | No | No | No | No | No | The customer was hand digging for a water leak on the property when they struck a gas line.
Southwest Gas Company | N | PLACER | TAHOE VISTA | 2023-09-13 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 43 | 43 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 293 |  | 0 |  | SHARPS GENERAL CONSTRUCTION | KINGS BEACH | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged stub with pick axe while digging trench to install new gas service line to the main
Southwest Gas Company | N | SAN BERNARDINO | ADELANTO | 2023-04-12 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 3484 |  | 0 |  | DOUGLAS PIPELINE | LAKE ELSINORE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damagedgas main while excavating.
Southwest Gas Company | N | SAN BERNARDINO | ADELANTO | 2023-01-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 509 |  | 1 |  | EFI ENGINEERING | TUSTIN | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas service while potholing.
Southwest Gas Company | N | SAN BERNARDINO | ADELANTO | 2023-01-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 715 |  | 2 |  | OCCUPANT | ADELANTO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged gas service while excavating.
Southwest Gas Company | N | SAN BERNARDINO | ADELANTO | 2023-01-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 622 |  | 2 |  | CLEAR SOURCE COMMUNICATION | LAWNDALE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service line while excavating.
Southwest Gas Company | N | SAN BERNARDINO | ADELANTO | 2023-04-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 457 |  | 2 |  | SENNZA CONSTRUCTION | ALPINE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas service while digging with a shovel.
Southwest Gas Company | N | SAN BERNARDINO | ADELANTO | 2023-01-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Directional Drilling | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 857 |  | 2 |  | CLEAR SOURCE COMMUNICATION | LAWNDALE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service while directional drilling.
Southwest Gas Company | N | SAN BERNARDINO | ADELANTO | 2023-06-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 444 |  | 1 |  | OCCUPANT | ADELANTO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged gas service line with a shovel.
Southwest Gas Company | N | SAN BERNARDINO | ADELANTO | 2023-03-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | Y | N | N | 0 | 0 |  | 0 | 0 |  | 668 |  | 2 |  | OCCUPANT | ADELANTO | CA | N | Y | No | No | Yes | No | No | Excavator provided no markings for the proposed excavation on site. | No | Occupant damaged service line while excavating.
Southwest Gas Company | N | SAN BERNARDINO | ADELANTO | 2023-11-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 721 |  | 1 |  | OCCUPANT | ADELANTO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged service with a shovel while digging to relocate plumbing line.
Southwest Gas Company | N | SAN BERNARDINO | ADELANTO | 2023-05-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 400 |  | 0 |  | CHRISTIANBELLE ELECTRIC INC | HESPERIA | CA | N | Y | Yes | No | Yes | Yes | No | Yes | No | Contractor damaged gas service while digging with mini excavator. Contractor had a USA dig ticket but it was not valid yet.
Southwest Gas Company | N | SAN BERNARDINO | APPLE VALLEY | 2023-06-30 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 448 |  | 0 |  | OCCUPANT | APPLE VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged service line while excavating.
Southwest Gas Company | N | SAN BERNARDINO | APPLE VALLEY | 2023-04-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 941 |  | 2 |  | GARY MOORE CONSTRUCTION | APPLE VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | No | Yes | Contractor damaged service line while excavating.
Southwest Gas Company | N | SAN BERNARDINO | APPLE VALLEY | 2023-08-08 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 569 |  | 1 |  | SOUTHWEST GAS | LAS VEGAS | NV | Y | Y | Yes | Yes | No | No | No | Yes | Yes | First party damage to service while potholing with a sharpshooter.
Southwest Gas Company | N | SAN BERNARDINO | APPLE VALLEY | 2023-04-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 602 |  | 2 |  | OCCUPANT | APPLE VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged service while digging to install a fence.
Southwest Gas Company | N | SAN BERNARDINO | APPLE VALLEY | 2023-05-25 | Operator excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 591 |  | 1 |  | ARIZONA PIPELINE COMPANY | HESPERIA | CA | Y | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged service while digging.
Southwest Gas Company | N | SAN BERNARDINO | BARSTOW | 2023-04-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1081 |  | 1 |  | CASEMON COMMUNICATION INC | FONTANA | CA | N | Y | Yes | Yes | No | No | No | Yes | Yes | Contractor damaged service line while excavating with a trackhoe.
Southwest Gas Company | N | SAN BERNARDINO | BARSTOW | 2023-09-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 821 |  | 1 |  | PRO INTEGRITY PLUMBING | APPLE VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service damaged with jackhammer while excavating.
Southwest Gas Company | N | SAN BERNARDINO | BARSTOW | 2023-12-21 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 772 |  | 1 |  | ROLAND ENGINEERING | APPLE VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged main with an excavator.
Southwest Gas Company | N | SAN BERNARDINO | BARSTOW | 2023-03-14 | Third party excavation damage | Main | Polyethylene Pipe | Directional Drilling | 2 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 8693 |  | 1 |  | BRIONES COMMUNICATIONS INC | SANTA CLARITA | CA | N | Y | Yes | No | No | No | No | Yes | No | Contractor damaged main while directional drilling.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR CITY | 2023-10-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Not Available | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 245 |  | 0 |  | UNKNOWN | NA |  | N | Y | Yes | Yes | Yes | Yes | No | No | No | Contractor damaged service line while excavating. The property owner refused to reveal who the contractor was performing the work.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR CITY | 2023-07-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 707 |  | 1 |  | CITY OF BIG BEAR LAKE DWP | BIG BEAR LAKE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service line while digging with a backhoe.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR LAKE | 2023-04-29 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 911 |  | 1 |  | OCCUPANT | BIG BEAR LAKE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner hit service line with a backhoe.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR LAKE | 2023-08-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 367 |  | 2 |  | APPLE VALLEY CONSTRUCTION | APPLE VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service line with a mini excavator.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR LAKE | 2023-08-24 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 263 |  | 1 |  | APPLE VALLEY CONSTRUCTION | APPLE VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service line.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR LAKE | 2023-07-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 176 |  | 1 |  | ESTRADA''S CONSTRUCTION, LANDSCAPING & FENCING | BIG BEAR LAKE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service line with shovel while potholing, triggering EFV.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR LAKE | 2023-07-07 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 1 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 519 |  | 2 |  | STALCUP LANDSCAPE INNOVATIONS | BIG BEAR LAKE | CA | N | Y | Yes | No | Yes | No | No | No | No | Contractor damaged service while excavating.
Southwest Gas Company | N | SAN BERNARDINO | BIG BEAR LAKE | 2023-09-08 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 264 |  | 1 |  | MCDONALD CONSTRUCTION | BIG BEAR LAKE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service line with backhoe.
Southwest Gas Company | N | SAN BERNARDINO | DAGGETT | 2023-04-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 717 |  | 1 |  | OCCUPANT | DAGGETT | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged service line with tractor while digging.
Southwest Gas Company | N | SAN BERNARDINO | FAWNSKIN | 2023-10-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 893 |  | 1 |  | PEDRO ZEPEDA | BIG BEAR LAKE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Service line hit while excavating for wood walkway.
Southwest Gas Company | N | SAN BERNARDINO | FAWNSKIN | 2023-09-20 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 283 |  | 1 |  | BEAR CONCRETE | BIG BEAR LAKE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service line with mini excavator.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2023-10-04 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1601 |  | 2 |  | OCCUPANT | HESPERIA | CA | N | Y | No | No | No | No | No | No | No | Homeowner damaged service while excavating.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2023-06-20 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1974 |  | 0 |  | HONEST JOHNS SEPTIC SERVICE | APPLE VALLEY | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged a service to main connection when excavating.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2023-09-18 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 501 |  | 1 |  | OCCUPANT | HESPERIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged service while excavating with a shovel.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2023-12-31 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 908 |  | 2 |  | JOSE FRANCISCO NAVARRO | PERRIS | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service line with excavator.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2023-02-05 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1135 |  | 1 |  | OCCUPANT | HESPERIA | CA | N | Y | Yes | No | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged service line while excavating with mechanical equipment.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2023-08-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 692 |  | 1 |  | OCCUPANT | HESPERIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Homeowner damaged service line while excavating.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2023-05-15 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 487 |  | 0 |  | UNDERGROUND SPECIALIST INC | RANCHO CUCAMONGA | CA | N | Y | Yes | No | Yes | No | No | Yes | No | Contractor damaged service stub with a backhoe while installing electrical conduit.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2023-05-30 | Third party excavation damage | Main | Polyethylene Pipe | Not Available | 2 | 40 | 38 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | UNKNOWN | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | An unknown party damaged main below ground in a housing development.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2023-02-22 | Third party excavation damage | Main | Polyethylene Pipe | Trencher | 2 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 858 |  | 0 |  | ELITE ELECTRIC | RIVERSIDE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas line while excavating.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2023-06-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 549 |  | 0 |  | MACIAS EXCAVATION LLC | MENIFEE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service stub with an excavator while excavating.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2023-11-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 438 |  | 1 |  | OCCUPANT | HESPERIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged service with shovel.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2023-03-31 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 360 |  | 1 |  | HITT CONSTRUCTION COMPANY | APPLE VALLEY | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service while digging.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2023-01-25 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 553 |  | 2 |  | CAMARILLO DRILLING | NUEVO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service line by failing to maintain markings while excavating.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2023-07-03 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 855 |  | 1 |  | OCCUPANT | HESPERIA | CA | N | Y | No | No | No | No | No | No | No | Homeowner damaged service line while digging with a shovel.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2023-06-16 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 34 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 837 |  | 1 |  | OCCUPANT | HESPERIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | Yes | Friend of homeowner damaged service line with mini excavator.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2023-07-14 | Third party excavation damage | Main | Polyethylene Pipe | Not Available | 2 | 60 | 55 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 2387 |  | 0 |  | UNKNOWN | NA |  | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Unknown Party damaged main with unknown object, no release of gas.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2023-07-28 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 967 |  | 1 |  | GSI | VICTORVILLE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service while potholing with a shovel.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2023-01-27 | Operator excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1120 |  | 0 |  | ARIZONA PIPELINE COMPANY | HESPERIA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas line while excavating with mechanical equipment.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2023-05-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 528 |  | 1 |  | CUSTOM MOJAVE POOLS, INC. | HESPERIA | CA | N | Y | Yes | Yes | No | No | No | No | No | Contractor damaged service line while excavating outside the agreed upon work area.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2023-06-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1224 |  | 1 |  | OCCUPANT | HESPERIA | CA | N | Y | No | No | No | No | No | No | No | Homeowner damaged service while excavating to remove a tree stump.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2023-11-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 418 |  | 1 |  | LEGEND CONSTRUCTION SERVICES INC | ONTARIO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service while excavating.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2023-02-06 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 347 |  | 1 |  | OCCUPANT | HESPERIA | CA | N | Y | Yes | No | Yes | Yes | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged service while excavating in his yard.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2023-09-11 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 4 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 4041 |  | 1 |  | ARIZONA PIPELINE COMPANY | HESPERIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged main using a back hoe.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2023-07-03 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 866 |  | 0 |  | SORRENTO HOMES | ADELANTO | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged main while excavating with a backhoe.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2023-09-14 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2496 |  | 2 |  | CITY OF HESPERIA WATER DISTRICT | HESPERIA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | City of Hesperia Water Department damaged gas main with backhoe due to a mismarked facility.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2023-01-31 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 55 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 1913 |  | 0 |  | GROUNDWORK ENGINEERING | CASTAIC | CA | N | Y | Yes | Yes | No | No | No | Yes | Yes | Contractor damaged an unmarked gas line while excavating.
Southwest Gas Company | N | SAN BERNARDINO | HESPERIA | 2023-04-13 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 510 |  | 0 |  | SULLY MILLER CONTRACTING COMPANY | BREA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contractor damaged stub while excavating.
Southwest Gas Company | N | SAN BERNARDINO | NEEDLES | 2023-09-04 | Third party excavation damage | Meter | Steel | Not Available | 0.75 | 60 | 55 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 0 |  | 0 |  | OCCUPANT | NA | CA | N | N | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Vehicle vs. MSA
Southwest Gas Company | N | SAN BERNARDINO | OAK HILLS | 2023-10-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1295 |  | 1 |  | OCCUPANT | OAK HILLS | CA | N | Y | No | No | No | No | No | No | No | Homeowner damage service line with an auger.
Southwest Gas Company | N | SAN BERNARDINO | OAK HILLS | 2023-12-27 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 777 |  | 1 |  | OCCUPANT | OAK HILLS | CA | N | Y | No | No | Yes | No | No | No | No | Homeowner damaged gas service while trenching.
Southwest Gas Company | N | SAN BERNARDINO | OAK HILLS | 2023-08-29 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 491 |  | 0 |  | HOME BUILDER- JOSEPH OJEDA | HESPERIA | CA | N | Y | No | No | Yes | No | No | No | No | Home builder damaged gas service while excavating.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2023-11-03 | Third party excavation damage | Riser | Polyethylene Pipe | Not Available | 1 | 60 | 55 | N | N | N | N | 0 | 0 |  | 0 | 0 |  | 423 |  | 0 |  | DR HORTON | WEST HILLS | CA | N | N | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Discovered bent riser, no release of gas.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2023-10-19 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 372 |  | 1 |  | OCCUPANT | VICTORVILLE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged service while excavating with a mini excavator.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2023-05-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 521 |  | 1 |  | GSI | VICTORVILLE | CA | N | Y | No | No | Yes | No | No | No | Yes | Contractor damaged gas service while digging.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2023-07-12 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 851 |  | 1 |  | OCCUPANT | VICTORVILLE | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Homeowner damaged service with a backhoe while excavating.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2023-01-12 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 54 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 524 |  | 1 |  | NEW WORK CONSTRUCTION CORP | VICTORVILLE | CA | N | Y | Yes | No | Yes | Yes | No | Yes | No | Contractor damaged service while potholing.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2023-11-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1538 |  | 1 |  | NETWORK CONNECTIONS | POMONA | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractors damaged service with shovel while potholing to install fiber optic cable.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2023-06-09 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Augur | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 2535 |  | 1 |  | D.C. HUBBS CONSTRUCTION | YUCAIPA | CA | N | Y | Yes | Yes | No | Yes | No | Yes | Yes | Contactor damaged service with auger while installing guard rail post.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2023-01-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 939 |  | 1 |  | OCCUPANT | VICTORVILLE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged service line while excavating.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2023-03-06 | Third party excavation damage | Main | Polyethylene Pipe | Backhoe/Trackhoe | 2 | 60 | 53 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 9316 |  | 1 |  | MJ PIPELINE CONSTRUCTION | JURUPA VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged main while excavating while mechanical equipment.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2023-12-15 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 35 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1208 |  | 1 |  | THOMPSON FAMILY PLUMBING | HESPERIA | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service while excavating with a shovel.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2023-09-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Grader/Scraper | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 498 |  | 1 |  | OCCUPANT | VICTORVILLE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged service while using a skid steer to remove a tree.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2023-06-21 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 508 |  | 0 |  | ARIZONA PIPELINE COMPANY | HESPERIA | CA | Y | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service while digging.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2023-01-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 986 |  | 3 |  | APPLE VALLEY CONSTRUCTION | APPLE VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged gas service while excavating.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2023-11-11 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 811 |  | 1 |  | SBLA CONSTRUCTION & REMODELING INC | NORTH HOLLYWOOD | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged service line with a post hole digger while excavating to install a fence.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2023-02-14 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 481 |  | 3 |  | OCCUPANT | VICTORVILLE | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged service line while excavating.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2023-03-16 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 38 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 758 |  | 1 |  | APPLE VALLEY CONSTRUCTION | APPLE VALLEY | CA | N | Y | Yes | Yes | Yes | Yes | No | Yes | Yes | Contractor damaged service line while excavating.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2023-02-17 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 36 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1032 |  | 11 |  | APPLE VALLEY CONSTRUCTION | APPLE VALLEY | CA | N | Y | Yes | Yes | No | No | No | Yes | Yes | Contractor damaged stub that was documented as abandoned.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2023-03-27 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 40 | 37 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 371 |  | 0 |  | LOMELI BACKHOE | EASTVALE | CA | N | Y | Yes | No | No | No | No | Yes | No | Contractors damaged gas line while excavating with mechanical equipment.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2023-08-04 | Third party excavation damage | A service line with an excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 974 |  | 0 |  | PACIFIC UTILITY INSTALLATION INC. | CORONA | CA | N | Y | Yes | Yes | No | No | No | No | No | Contractor damaged gas stub while excavating to install Edison box due to line locator not marking newly installed facility.
Southwest Gas Company | N | SAN BERNARDINO | VICTORVILLE | 2023-09-06 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Hand Tools | 1 | 60 | 55 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 363 |  | 0 |  | TRENCHERS WEST CONSTRUCTION CO | ANAHEIM | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Contractor damaged gas stub while excavating.
Southwest Gas Company | N | SAN BERNARDINO | YERMO | 2023-06-10 | Third party excavation damage | A service line with no excess flow valve installed | Polyethylene Pipe | Backhoe/Trackhoe | 0.5 | 40 | 39 | Y | N | N | N | 0 | 0 |  | 0 | 0 |  | 1432 |  | 1 |  | OCCUPANT | YERMO | CA | N | Y | No | No | No | No | No | Excavator provided no markings for the proposed excavation on site. | No | Homeowner damaged service line with a backhoe.