## 2025 Fire Incident Data
Utility Name | Fire Start |  | Location |  |  |  | Fire |  |  | Utility Facility |  |  |  |  | Outage |  |  | Field Observation
| Date | Time | Latitude | Longitude | Material at Origin | Land Use at Origin | Size | Suppressed By | Suppressing Agency | Facility Identification | Other Companies | Voltage (KVolts) | Equipment Involved With Ignition | Type | Was There an Outage | Date | Time | Suspected Initiating Event | Equipment/Facility Failure | Contact From Object | Facility Contacted | Contributing Factor
SCE | 2025-01-01 | 4:29 | 34.0262 | -117.7172 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Chino Valley Fire Department | OH-4908063E | None | 12 | Conductor | Overhead | No | N/A | N/A | Other |  |  |  | Outside Force
SCE | 2025-01-01 | 13:27 | 34.0572 | -118.0468 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-966158E | None | 16 | Conductor | Overhead | No | N/A | N/A | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2025-01-07 | 6:12 | 34.1059 | -117.435 | Building | Urban | Less Than .25 Acres | Customer |  | OH-4603104E | None | 12 | Other | Overhead | No | N/A | N/A | Equipment/Facility Failure | Other |  |  | Unknown
SCE | 2025-01-07 | 8:56 | 34.1599 | -117.6164 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Rancho Cucamonga Fire Department | OH-GT14486 | None | 12 | Conductor | Overhead | Yes | 1/7/25 | 08:56 | Contact From Object |  | Other | Electric Facility | Weather
SCE | 2025-01-07 | 23:44 | 33.9967 | -118.3601 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | Los Angeles County Fire Department | OH-1007735E | None | 16 | Conductor | Overhead | Yes | 1/7/25 | 23:44 | Contact From Object |  | Vegetation | Electric Facility | Weather
SCE | 2025-01-07 | 23:44 | 33.9929 | -118.369 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-4318924E | None | 16 | Conductor | Overhead | Yes | 1/7/25 | 23:44 | Contact From Object |  | Vegetation | Electric Facility | Weather
SCE | 2025-01-08 | 8:51 | 33.7236 | -117.8376 | Building | Urban | Less Than .25 Acres | Fire Agency | Orange County Fire Authority | OH-1677722E | None | 12 | Transformer | Overhead | Yes | 1/8/25 | 08:51 | Contact From Object |  | Other | Electric Facility | Outside Force
SCE | 2025-01-10 | 3:44 | 34.0652 | -117.8003 | Other | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | UG-5201049 | None | 12 | Transformer | Padmounted | No | N/A | N/A | Vandalism/Theft |  |  |  | Outside Force
SCE | 2025-01-11 | 17:20 | 34.7045 | -118.1437 | Vegetation | Urban | Less Than .25 Acres | Self Extinguished |  | OH-736329E | None | 12 | Conductor | Overhead | No | N/A | N/A | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2025-01-12 | 8:49 | 33.9421 | -116.4751 | Other | Urban | Less Than .25 Acres | Fire Agency | Local FD | OH-4500767E | None | 12 | Other | Overhead | Yes | 1/12/25 | 08:49 | Contact From Object |  | Vehicle | Pole | Outside Force
SCE | 2025-01-14 | 19:36 | 33.7507 | -116.982 | Building | Urban | Less Than .25 Acres | Fire Agency | Local FD | OH-2072508E | None | 12 | Conductor | Overhead | Yes | 1/14/25 | 19:36 | Unknown |  |  |  | Unknown
SCE | 2025-01-15 | 16:03 | 33.5978 | -117.2426 | Vegetation | Urban | Less Than .25 Acres | Utility |  | OH-315548S | None | 12 | Switch | Subsurface | No | N/A | N/A | Equipment/Facility Failure | Switch |  |  | Unknown
SCE | 2025-01-20 | 23:38 | 34.1379 | -117.4269 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Local FD | OH-4779002E | None | 12 | Conductor | Overhead | No | N/A | N/A | Contact From Object |  | Other | Electric Facility | Outside Force
SCE | 2025-01-22 | 3:03 | 34.329 | -118.9038 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Ventura County Fire Department | OH-4557632E | AMERICAN DARK FIBER | 16 | Fuse | Overhead | Yes | 1/22/25 | 03:03 | Equipment/Facility Failure | Fuse |  |  | Unknown
SCE | 2025-01-23 | 20:39 | 34.0632 | -117.3497 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | City of Colton Fire Department | OH-1947396E | None | 12 | Capacitor Bank | Overhead | No | N/A | N/A | Equipment/Facility Failure | Capacitor Bank |  |  | Unknown
SCE | 2025-01-24 | 11:49 | 34.1438 | -119.1069 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Ventura County Fire Department | OH-792880E | None | 16 | Capacitor Bank | Overhead | No | N/A | N/A | Equipment/Facility Failure | Capacitor Bank |  |  | Unknown
SCE | 2025-01-24 | 12:33 | 34.1058 | -118.7596 | Other | Rural | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-1335863E | None | 16 | Conductor | Overhead | No | N/A | N/A | Contact From Object |  | Other | Electric Facility | Outside Force
SCE | 2025-01-26 | 8:18 | 34.0738 | -117.4974 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | San Bernardino County Fire Department | OH-1947456E | None | 12 | Conductor | Overhead | Yes | 1/26/25 | 08:18 | Equipment/Facility Failure | Conductor |  |  | Weather
SCE | 2025-01-26 | 13:24 | 34.0111 | -117.9886 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-1528627E | TIME WARNER CABLE | 12 | Conductor | Overhead | Yes | 1/26/25 | 13:24 | Contact From Object |  | Vegetation | Electric Facility | Weather
SCE | 2025-01-27 | 1:52 | 34.5282 | -117.9406 | Vegetation | Rural | Less Than .25 Acres | Self Extinguished |  | OH-4313541E | None | 12 | Other | Overhead | Yes | 1/27/25 | 01:52 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Weather
SCE | 2025-02-02 | 22:12 | 34.4024 | -118.3595 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | U.S. Forest Service | OH-1534785E | None | 16 | Conductor | Overhead | Yes | 2/2/25 | 22:12 | Equipment/Facility Failure | Conductor |  |  | Weather
SCE | 2025-02-04 | 21:52 | 34.4724 | -118.3316 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-4777425E | None | 16 | Conductor | Overhead | Yes | 2/4/25 | 21:52 | Contact From Object |  | Vehicle | Electric Facility | Outside Force
SCE | 2025-02-15 | 10:16 | 33.8276 | -118.071 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-4243102E | None | 12 | Conductor | Overhead | Yes | 2/15/25 | 10:16 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2025-02-21 | 14:36 | 33.8667 | -117.3054 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Riverside County Fire Department | OH-4524014E | None | 12 | Conductor | Overhead | Yes | 2/21/25 | 14:36 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2025-02-27 | 11:45 | 34.1512 | -118.0661 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Arcadia Fire Department | OH-4809011E | None | 16 | Conductor | Overhead | Yes | 2/27/25 | 11:45 | Contact From Object |  | Vegetation | Electric Facility | Outside Force
SCE | 2025-03-05 | 9:40 | 35.1074 | -117.9758 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | California City Fire Department | OH-4177259E | CHARTER COMMUNICATIONS | 12 | Transformer | Overhead | Yes | 3/5/25 | 09:40 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2025-03-19 | 15:26 | 34.1101 | -117.2672 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | San Bernardino County Fire Department | OH-4003908E | None | 12 | Other | Overhead | Yes | 3/19/25 | 15:26 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown
SCE | 2025-03-21 | 20:51 | 34.5004 | -118.0719 | Vegetation | Rural | Less Than .25 Acres | Self Extinguished |  | OH-1927091E | None | 220 | Other | Overhead | No | N/A | N/A | Equipment/Facility Failure | Pole |  |  | Weather
SCE | 2025-03-26 | 22:19 | 33.9541 | -116.5339 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Riverside County Fire Department | OH-4805798E | None | 12 | Other | Overhead | Yes | 3/26/25 | 22:19 | Contact From Object |  | Vehicle | Pole | Outside Force
SCE | 2025-03-26 | 22:19 | 33.9541 | -116.5332 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Riverside County Fire Department | OH-4183248E | None | 12 | Other | Overhead | Yes | 3/26/25 | 22:19 | Contact From Object |  | Vehicle | Pole | Outside Force
SCE | 2025-03-28 | 8:33 | 34.9525 | -118.1318 | Vegetation | Rural | Less Than .25 Acres | Self Extinguished |  | OH-1943713E | None | 12 | Other | Overhead | No | N/A | N/A | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2025-03-28 | 17:42 | 33.769 | -117.8986 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Orange County Fire Authority | OH-1093215E | None | 12 | Other | Overhead | Yes | 3/28/25 | 17:42 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown
SCE | 2025-04-10 | 0:00 | 35.9642 | -119.0648 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Tulare County Fire Department | OH-802060E | None | 12 | Conductor | Overhead | No | N/A | N/A | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2025-04-23 | 13:53 | 34.0409 | -118.657 | Vegetation | Rural | Less Than .25 Acres | Self Extinguished |  | UG-5401226 | None | 16 | Conductor | Padmounted | Yes | 4/23/25 | 13:53 | Contact From Object |  | Other | Electric Facility | Outside Force
SCE | 2025-04-24 | 8:26 | 34.5052 | -117.4248 | Vegetation | Rural | Less Than .25 Acres | Self Extinguished |  | OH-1600059E | None | 12 | Transformer | Overhead | Yes | 4/24/25 | 08:26 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2025-05-01 | 13:43 | 35.0637 | -117.0215 | Vegetation | Rural | Less Than .25 Acres | Self Extinguished |  | OH-4379778E | None | 33 | Transformer | Overhead | Yes | 5/1/25 | 13:43 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2025-05-01 | 17:36 | 33.8027 | -117.2349 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Riverside County Fire Department | OH-2344938E | None | 33 | Lightning Arrestor | Overhead | No | N/A | N/A | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2025-05-01 | 22:16 | 34.7059 | -118.1769 | Building | Rural | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-1183751E | None | 12 | Other | Overhead | Yes | 5/1/25 | 22:16 | Equipment/Facility Failure | Insulator |  |  | Unknown
SCE | 2025-05-10 | 16:48 | 35.1304 | -117.9498 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Kern County Fire Department | OH-2179238E | None | 12 | Other | Overhead | Yes | 5/10/25 | 16:48 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2025-05-12 | 9:01 | 33.8231 | -117.2046 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Riverside County Fire Department | OH-4770480E | None | 12 | Conductor | Overhead | No | N/A | N/A | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2025-05-12 | 15:20 | 35.2767 | -117.9857 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL Fire | OH-1899578E | None | 12 | Other | Overhead | Yes | 5/12/25 | 15:20 | Contact From Object |  | Vehicle | Pole | Outside Force
SCE | 2025-05-13 | 19:47 | 35.9701 | -119.2827 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Tulare County Fire Department | OH-7910T | None | 12 | Lightning Arrestor | Overhead | Yes | 5/13/25 | 19:47 | Contact From Object |  | Other | Electric Facility | Outside Force
SCE | 2025-05-14 | 17:58 | 36.0791 | -119.0184 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Local FD | OH-4565035E |  | 12 | Conductor | Overhead | Yes | 5/14/25 | 17:58 | Contact Between Third Party Facility on Pole and Supply Lines |  | Other | Electric Facility | Outside Force
SCE | 2025-05-20 | 11:41 | 34.1161 | -117.9326 | Other | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-4752909E | None | 12 | Other | Overhead | Yes | 5/20/25 | 11:41 | Contact From Object |  | Vehicle | Pole | Outside Force
SCE | 2025-05-20 | 16:08 | 34.4231 | -117.4761 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Local FD | OH-3005782E | None | 12 | Other | Overhead | Yes | 5/20/25 | 16:08 | Other |  |  |  | Unknown
SCE | 2025-05-24 | 11:56 | 34.329 | -118.9034 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Ventura County Fire Department | OH-4436951E | None | 16 | Fuse | Overhead | Yes | 5/24/25 | 11:56 | Equipment/Facility Failure | Fuse |  |  | Unknown
SCE | 2025-05-25 | 15:26 | 34.4272 | -117.1855 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Apple Valley Fire Department | OH-263498S | None | 12 | Other | Overhead | Yes | 5/25/25 | 15:26 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2025-05-27 | 9:07 | 33.6822 | -117.3274 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | Unknown | OH-2225121E | None | 33 | Other | Overhead | Yes | 5/27/25 | 09:07 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown
SCE | 2025-05-28 | 5:08 | 34.075 | -118.4025 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Beverly Hills Fire Department | OH-817673E | None | 4 | Conductor | Overhead | Yes | 5/28/25 | 05:08 | Contact From Object |  | Vegetation | Electric Facility | Weather
SCE | 2025-05-28 | 21:53 | 33.8857 | -118.2716 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-1328422E | None | 16 | Other | Overhead | Yes | 5/28/25 | 21:53 | Contact From Object |  | Vehicle | Pole | Outside Force
SCE | 2025-05-30 | 8:33 | 34.8012 | -118.8302 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Los Angeles County Fire Department | OH-7015593 | None | 66 | Conductor | Overhead | No | N/A | N/A | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2025-06-02 | 2:37 | 34.6462 | -118.0537 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Local FD | OH-4831999E | None | 12 | Other | Overhead | Yes | 6/2/25 | 02:37 | Contact From Object |  | Vehicle | Pole | Outside Force
SCE | 2025-06-06 | 14:43 | 33.7682 | -117.0817 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Riverside County Fire Department | OH-1971267E | None | 12 | Other | Overhead | No | N/A | N/A | Vandalism/Theft |  |  |  | Unknown
SCE | 2025-06-08 | 19:58 | 35.061 | -118.1943 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Kern County Fire Department | OH-4118252E | None | 12 | Conductor | Overhead | No | N/A | N/A | Wire-Wire Contact |  |  |  | Unknown
SCE | 2025-06-11 | 3:44 | 34.0296 | -118.1235 | Vegetation | Urban | Less Than .25 Acres | Self Extinguished |  | OH-2022233E | CHARTER COMMUNICATIONS | 16 | Other | Overhead | Yes | 6/11/25 | 03:44 | Equipment/Facility Failure | Insulator |  |  | Unknown
SCE | 2025-06-11 | 18:36 | 34.1062 | -116.4314 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Yucca Valley Fire Department | OH-4923604E | None | 12 | Conductor | Overhead | No | N/A | N/A | Contact From Object |  | Vegetation | Electric Facility | Outside Force
SCE | 2025-06-12 | 16:31 | 34.6937 | -117.917 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-4625783E | None | 12 | Other | Overhead | Yes | 6/12/25 | 16:31 | Contact From Object |  | Animal | Pole | Outside Force
SCE | 2025-06-12 | 23:45 | 35.1046 | -117.9319 | Vegetation | Rural | Less Than .25 Acres | Self Extinguished |  | OH-4937314E | None | 33 | Conductor | Overhead | No | N/A | N/A | Vandalism/Theft |  |  |  | Outside Force
SCE | 2025-06-14 | 0:31 | 34.4516 | -119.255 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Local FD | OH-4635125E | TIME WARNER CABLE | 16 | Conductor | Overhead | Yes | 6/14/25 | 00:31 | Contact From Object |  | Vegetation | Electric Facility | Outside Force
SCE | 2025-06-14 | 8:22 | 34.6528 | -118.2175 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-2365433E | None | 12 | Other | Subsurface | Yes | 6/14/25 | 08:22 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2025-06-15 | 10:20 | 33.9514 | -116.4729 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Riverside County Fire Department | OH-35425S | None | 12 | Lightning Arrestor | Overhead | Yes | 6/15/25 | 10:20 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2025-06-15 | 11:33 | 34.9247 | -118.9198 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Kern County Fire Department | OH-7014641 | None | 66 | Conductor | Overhead | No | N/A | N/A | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2025-06-16 | 1:35 | 33.6822 | -117.3274 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Local FD | OH-2225121E | None | 33 | Switch | Overhead | Yes | 6/16/25 | 01:35 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2025-06-19 | 3:42 | 34.6601 | -118.209 | Vegetation | Urban | Less Than .25 Acres | Self Extinguished |  | OH-4484819E | RACE TELECOMMUNICATIONS, INC. | 12 | Other | Overhead | Yes | 6/19/25 | 03:42 | Contact From Object |  | Vehicle | Pole | Outside Force
SCE | 2025-06-20 | 2:38 | 35.4368 | -118.9253 | Vegetation | Rural | .26 - 9.99 Acres | Unknown |  | OH-7023367 | None | 220 | Conductor | Overhead | No | N/A | N/A | Vandalism/Theft |  |  |  | Outside Force
SCE | 2025-06-20 | 17:34 | 33.8956 | -117.2529 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Riverside County Fire Department | OH-4535103E | None | 12 | Conductor | Overhead | Yes | 6/20/25 | 17:34 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2025-06-21 | 16:50 | 33.8146 | -117.1366 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Riverside County Fire Department | OH-4004791E | TIME WARNER CABLE | 12 | Conductor | Overhead | Yes | 6/21/25 | 16:50 | Contact From Object |  | Other | Electric Facility | Outside Force
SCE | 2025-06-23 | 0:07 | 34.5652 | -118.1271 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | Palmdale Fire Department | OH-2383247E | None | 12 | Lightning Arrestor | Overhead | No | N/A | N/A | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2025-06-24 | 2:30 | 35.517 | -119.0084 | Vegetation | Rural | 100 - 299 Acres | Fire Agency | Kern County Fire Department | OH-7022668 | None | 220 | Conductor | Overhead | No | N/A | N/A | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2025-06-25 | 1:11 | 35.7213 | -118.6954 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Kern County Fire Department | OH-4332493E | None | 66 | Switch | Overhead | No | N/A | N/A | Normal Operation | Switch |  | Electric Facility | Unknown
SCE | 2025-06-26 | 15:27 | 33.9463 | -117.9207 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-1659413E | None | 66 | Conductor | Overhead | No | N/A | N/A | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2025-07-01 | 12:45 | 34.1048 | -118.0642 | Vegetation | Urban | Less Than .25 Acres | Customer |  | OH-231675E | None | 16 | Other | Overhead | Yes | 7/1/25 | 12:45 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2025-07-04 | 4:44 | 33.7627 | -117.2344 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Riverside County Fire Department | OH-2343461E | SUNESYS, LLC & TIME WARNER CABLE | 12 | Conductor | Overhead | No | N/A | N/A | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2025-07-05 | 0:25 | 34.0629 | -118.0826 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Local FD | UG-5408156 | None | 16 | Transformer | Padmounted | Yes | 7/5/25 | 00:25 | Vandalism/Theft |  |  |  | Outside Force
SCE | 2025-07-05 | 2:56 | 36.3506 | -119.4186 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Local FD | OH-1504132E | None | 12 | Conductor | Overhead | No | N/A | N/A | Contact From Object |  | Vegetation | Electric Facility | Outside Force
SCE | 2025-07-05 | 16:33 | 34.3853 | -119.411 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Ventura County Fire Department | OH-1089577E | None | 16 | Other | Overhead | Yes | 7/5/25 | 16:33 | Contact From Object |  | Vehicle | Pole | Outside Force
SCE | 2025-07-06 | 16:17 | 36.0562 | -119.3083 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Tulare County Fire Department | OH-4013070E | None | 12 | Conductor | Overhead | Yes | 7/6/25 | 16:17 | Other |  |  |  | Outside Force
SCE | 2025-07-07 | 4:43 | 36.8183 | -119.4318 | Vegetation | Rural | 10 - 99 Acres | Fire Agency | CAL Fire | OH-7020970 | None | 220 | Conductor | Overhead | No | N/A | N/A | Unknown |  |  |  | Unknown
SCE | 2025-07-09 | 11:03 | 34.3807 | -117.2263 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | CAL Fire | OH-67917S | None | 12 | Conductor | Overhead | Yes | 7/9/25 | 11:03 | Vandalism/Theft |  |  |  | Unknown
SCE | 2025-07-14 | 21:05 | 34.4733 | -120.0221 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Santa Barbara County Fire Department | OH-4491448E | None | 16 | Conductor | Overhead | Yes | 7/14/25 | 21:05 | Equipment/Facility Failure | Conductor |  |  | Outside Force
SCE | 2025-07-19 | 10:58 | 34.09 | -117.8853 | Building | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-4153651E | None | 12 | Lightning Arrestor | Overhead | Yes | 7/19/25 | 10:58 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2025-07-21 | 9:38 | 34.839 | -118.1482 | Vegetation | Rural | Less Than .25 Acres | Self Extinguished |  | OH-1184745E | None | 12 | Transformer | Overhead | Yes | 7/21/25 | 09:38 | Equipment/Facility Failure | Transformer |  |  | Unknown
SCE | 2025-07-26 | 15:54 | 34.5373 | -117.311 | Building | Urban | Less Than .25 Acres | Fire Agency | San Bernardino County Fire Department | OH-226493S | None | 12 | Conductor | Overhead | Yes | 7/26/25 | 15:54 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2025-07-27 | 4:54 | 36.4424 | -119.2909 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Tulare County Fire Department | OH-4583609E | None | 12 | Other | Overhead | No | N/A | N/A | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown
SCE | 2025-07-28 | 10:20 | 36.4014 | -118.9518 | Vegetation | Unknown | .26 - 9.99 Acres | Fire Agency | CAL Fire | OH-4434929E | None | 66 | Conductor | Overhead | No | N/A | N/A | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2025-08-04 | 4:46 | 35.0833 | -118.326 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Kern County Fire Department | OH-2274188E | None | 12 | Switch | Overhead | Yes | 8/4/25 | 04:46 | Equipment/Facility Failure | Switch |  |  | Unknown
SCE | 2025-08-04 | 19:36 | 33.7489 | -116.4036 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | CAL Fire | UG-5184233 | None | 12 | Transformer | Subsurface | Yes | 8/4/25 | 19:36 | Unknown |  |  |  | Unknown
SCE | 2025-08-05 | 0:00 | 34.4457 | -118.534 | Building | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-1072514E | TIME WARNER CABLE | 16 | Conductor | Overhead | No | N/A | N/A | Contact From Object |  | Vegetation | Electric Facility | Weather
SCE | 2025-08-05 | 17:51 | 34.2551 | -117.1666 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | San Bernardino County Fire Department | OH-4802114E | None | 12 | Switch | Overhead | Yes | 8/5/25 | 17:51 | Equipment/Facility Failure | Switch |  |  | Unknown
SCE | 2025-08-07 | 19:13 | 33.8983 | -118.0215 | Building | Urban | Less Than .25 Acres | Fire Agency | Local FD | OH-4321102E | None | 12 | Other | Overhead | Yes | 8/7/25 | 19:13 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown
SCE | 2025-08-09 | 12:11 | 34.8201 | -118.2784 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-4778410E | None | 12 | Other | Overhead | Yes | 8/9/25 | 12:11 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown
SCE | 2025-08-10 | 17:25 | 33.7536 | -117.1343 | Vegetation | Unknown | Less Than .25 Acres | Fire Agency | Riverside County Fire Department | UG-5010566 | None | 12 | Other | Subsurface | Yes | 8/10/25 | 17:25 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown
SCE | 2025-08-13 | 14:01 | 33.8808 | -118.2948 | Building | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-1393136E | SUNESYS, LLC & TIME WARNER CABLE | 4 | Conductor | Overhead | Yes | 8/13/25 | 14:01 | Contact From Object |  | Balloons | Electric Facility | Outside Force
SCE | 2025-08-18 | 20:50 | 36.2696 | -119.2967 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Tulare County Fire Department | OH-4563758E | None | 12 | Conductor | Overhead | Yes | 8/18/25 | 20:50 | Contact From Object |  | Vegetation | Electric Facility | Outside Force
SCE | 2025-08-20 | 2:16 | 36.3662 | -119.2762 | Vegetation | Unknown | Less Than .25 Acres | Fire Agency | Tulare County Fire Department | UG-5449092 | None | 12 | Other | Padmounted | Yes | 8/20/25 | 02:16 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown
SCE | 2025-08-21 | 18:02 | 33.7689 | -118.3711 | Vegetation | Urban | .26 - 9.99 Acres | Fire Agency | Los Angeles County Fire Department | OH-4441167E | COX COMMUNICATIONS | 16 | Lightning Arrestor | Overhead | Yes | 8/21/25 | 18:02 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2025-08-25 | 13:42 | 35.112 | -117.9635 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | California CIty Fire Department | OH-46463S | CHARTER COMMUNICATIONS | 12 | Other | Overhead | Yes | 8/25/25 | 13:42 | Contact From Object |  | Vehicle | Communication Facility | Outside Force
SCE | 2025-08-27 | 17:27 | 33.7887 | -116.484 | Vegetation | Unknown | Less Than .25 Acres | Fire Agency | Palm Springs Fire Department | UG-5764662 | None | 12 | Transformer | Padmounted | Yes | 8/27/25 | 17:27 | Vandalism/Theft |  |  |  | Outside Force
SCE | 2025-08-27 | 21:54 | 36.4066 | -119.0495 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | CAL Fire | OH-4932573E | None | 12 | Other | Overhead | Yes | 8/27/25 | 21:54 | Equipment/Facility Failure | Voltage Regulator |  |  | Unknown
SCE | 2025-08-28 | 10:24 | 34.8019 | -118.2111 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Local FD | OH-503666E | None | 12 | Other | Overhead | Yes | 8/28/25 | 10:24 | Equipment/Facility Failure | Pole |  |  | Unknown
SCE | 2025-09-01 | 17:59 | 34.074 | -116.5395 | Vegetation | Rural | Less Than .25 Acres | Self Extinguished |  | OH-2231195E | None | 12 | Transformer | Overhead | Yes | 9/1/25 | 17:59 | Equipment/Facility Failure | Transformer |  |  | Unknown
SCE | 2025-09-01 | 20:07 | 35.8849 | -119.2735 | Building | Urban | Less Than .25 Acres | Fire Agency | Tulare County Fire Department | OH-4811280E | None | 12 | Other | Overhead | No | N/A | N/A | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown
SCE | 2025-09-01 | 23:29 | 36.0495 | -118.9923 | Vegetation | Unknown | Less Than .25 Acres | Fire Agency | Tulare County Fire Department | OH-4978908E | None | 12 | Other | Overhead | Yes | 9/1/25 | 23:29 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown
SCE | 2025-09-02 | 0:00 | 34.4992 | -117.2741 | Vegetation | Unknown | Less Than .25 Acres | Unknown |  | UG-5383485 | None | 12 | Other | Subsurface | No | N/A | N/A | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown
SCE | 2025-09-02 | 15:53 | 34.6164 | -117.9697 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Local FD | OH-1707701E | None | 66 | Conductor | Overhead | No |  |  | Wire-Wire Contact |  |  |  | Weather
SCE | 2025-09-08 | 4:52 | 34.0894 | -118.5931 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-1576560E | None | 16 | Conductor | Overhead | Yes | 9/8/25 | 04:52 | Contact From Object |  | Vegetation | Electric Facility | Outside Force
SCE | 2025-09-17 | 15:45 | 34.5378 | -117.3129 | Building | Urban | Less Than .25 Acres | Fire Agency | San Bernardino County Fire Department | OH-1552706E | CHARTER COMMUNICATIONS | 12 | Conductor | Overhead | Yes | 9/17/25 | 15:45 | Contact From Object |  | Other | Electric Facility | Outside Force
SCE | 2025-09-18 | 12:14 | 33.7126 | -117.7093 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Orange County Fire Authority | OH-4491894E | None | 12 | Transformer | Overhead | Yes | 9/18/25 | 12:14 | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2025-09-29 | 2:01 | 33.7863 | -118.2024 | Building | Urban | Less Than .25 Acres | Fire Agency | Long Beach Fire Department | OH-4443166E | CHARTER COMMUNICATIONS | 12 | Conductor | Subsurface | Yes | 9/29/25 | 02:01 | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | 2025-10-10 | 16:36 | 34.1469 | -117.2965 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | San Bernardino County Fire Department | OH-4467148E | None | 12 | Other | Overhead | Yes | 10/10/25 | 16:36 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown
SCE | 2025-10-13 | 12:54 | 33.9947 | -117.9344 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | UG-5126836 | None | 12 | Other | Padmounted | Yes | 10/13/25 | 12:54 | Vandalism/Theft |  |  |  | Unknown
SCE | 2025-10-18 | 16:48 | 33.9868 | -118.0662 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Local FD | OH-2317691E | None | 16 | Conductor | Overhead | No | N/A | N/A | Contact From Object |  | Animal | Electric Facility | Outside Force
SCE | 2025-10-21 | 16:53 | 34.1531 | -118.9103 | Vegetation | Rural | .26 - 9.99 Acres | Fire Agency | Ventura County Fire Department | OH-4505362E | None | 16 | Other | Overhead | Yes | 10/21/25 | 16:53 | Contact From Object |  | Vehicle | Communication Facility | Outside Force
SCE | 2025-10-23 | 0:00 | 34.0488 | -118.0445 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-891476E | None | 16 | Conductor | Overhead | No | N/A | N/A | Equipment/Facility Failure | Conductor |  |  | Unknown
SCE | 2025-11-03 | 16:24 | 36.1284 | -119.044 | Vegetation | Rural | Less Than .25 Acres | Fire Agency | Tulare County Fire Department | OH-1465143E | None | 12 | Transformer | Overhead | No | N/A | N/A | Equipment/Facility Failure | Transformer |  |  | Unknown
SCE | 2025-11-10 | 13:18 | 34.074 | -118.0765 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | Los Angeles County Fire Department | OH-4818253E | None | 16 | Other | Overhead | Yes | 11/10/25 | 13:18 | Contact From Object |  | Vehicle | Pole | Outside Force
SCE | 2025-11-30 | 4:58 | 34.0231 | -117.0923 | Vegetation | Urban | Less Than .25 Acres | Fire Agency | CAL Fire | OH-4488563E | None | 12 | Other | Overhead | Yes | 11/30/25 | 04:58 | Equipment/Facility Failure | Splice/Clamp/Connector |  |  | Unknown