## PGE2015SMRS_Actual
2015 STANDARDIZED MAINTENANCE REPORT - Actual
EQUIPMENT TYPE | NO. OF FACILITIES | MAINT. TASK | MAINT. UNIT | PLANNED | ACTUAL | EXCEPTION FROM PLANNED | NOTES
Overhead Line Patrol/Inspection (Lines) | 1360 | [5 empty] | Number of reported facilities includes non-CAISO controlled facilities. Additional 2 Circuits added in 2015
Inspection
| 1362 | Detailed Inspections | Line | 682 | 682 | Stacie Doyle | Number of inspections includes those performed on non-CAISO controlled facilities.
|  | Ground Inspections | Line | 33 | 33 | Stacie Doyle | Number of inspections includes those performed on non-CAISO controlled facilities.
|  | Aerial Inspections | Line | 645 | 647 | Stacie Doyle | Number of inspections includes those performed on non-CAISO controlled facilities.
Overhead Line Patrol/Inspection (Structures) | 171791 | [5 empty] | The 2015 Planned Total Structures was typed in error, Total Planned Structure should reflect 169816
Inspection
|  | Detailed Inspections | Structure | 88539 | 90937 | Stacie Doyle | Number of inspections includes those performed on non-CAISO controlled facilities.
|  | Ground Inspections | Structure | 1975 | 1975 | Stacie Doyle | Number of inspections includes those performed on non-CAISO controlled facilities.
|  | Aerial Inspections | Structure | 79289 | 81778 | Stacie Doyle | Number of inspections includes those performed on non-CAISO controlled facilities.
|  | Climbing Inspections (2% 500 kV Critical) | Structure | 13 | 13 | Stacie Doyle | The number of facilities only includes CAISO controlled facilities. The maintenance interval is every three years.
Overhead Line Vegetation Management/Right-Of-Way Maintenance | N/A | [5 empty] | The planned counts are estimates based on historical information and predictions based on last year’s inspections
Maintenance
|  | Trees Removed | Tree | 76000 |  |  | Number of trees removed includes those removed on non-CAISO controlled facilities. Tree count includes only trees > 4 inches Diameter at Breast Height (DBH); smaller trees are counted as brush.
|  | Trees Trimmed | Tree | 49000 |  |  | Number of trees trimmed includes those trimmed on non-CAISO controlled facilities. Tree count includes only trees that are > 4 inches Diameter at Breast Height (DBH); smaller trees are counted as brush. Each year PG&E rounds planned (forecasted) and actual counts for tree trimming.
Overhead Line Structures - Wood Pole | ≈115,000 | [5 empty] | Number of reported facilities includes non-CAISO controlled facilities.
Inspection
|  | Test | Wood Pole | 11065 | 11171 | There is always a difference as our starting number is pulled 6 months before we start and is approximated. A 10% growth or reduction is normal. | The number of reported planned-tests, includes those performed on non-CAISO controlled facilities.
Maintenance
|  | Treatment | Wood Pole | 9604 | 9922 | We do not plan treatments as we do not use dates in the planning process of poles. | Number of actual treatments is dependent upon testing.
|  | Repair | Wood Pole | 248 | 234 | Poles end up not being restored for a couple/few reasons, the two greatest are obstructions/access and poles having been replaced. | Repair means to reinforce (stub) a wood pole by attaching a steel reinforcing member with hydraulic pressure at, or below, ground level. Poles identified as needing to be repaired will be considered for replacement per normal inspection and test program guidelines.
|  | Replace | Wood Pole | 455 |  |  | Number of planned replacements includes non-CAISO controlled facilities. Replace is defined as: Any whole structure replaced or any single leg within an "H" structure configuration. The planned total submitted each year is an estimate that is dependent on funding, engineering, and the availability of crews to perform the work.
Overhead Line Insulators (contamination control) | N/A | [5 empty] | The number of facilities cannot be determined from records and is noted as N/A. Triggered by condition and trouble.
Maintenance
|  | Wash Insulators | Insulator String | 0 | 10175 | Stacie Doyle | Number of reported insulator washes includes those performed on non-CAISO controlled facilities.
Underground Line Patrol/Inspection | 57 | [5 empty] | Number of reported facilities includes in-service CAISO controlled facilities. The difference between 2015 (57) and 2016 (??) is due to ? less underground circuit in 2016.
Inspection
| 36 | Routine (Monthly) on Pipe-Type Circuits | Line | 396 | 396 | Stacie Doyle | Scheduling is based on the filed maintenance practice in effect.
| 21 | Routine (Quarterly) on XLPE Circuits | Line | 67 | 67 | Stacie Doyle | Scheduling is based on the filed maintenance practice in effect. The difference between the 2015 planned and the 2016 planned is that there were different counts of bi-annual inspections in each year and no quarterly inspection is done when that bi-annual inspection is performed.
| 36 | Detailed (Annual) on Pipe-Type Circuits | Line | 36 | 36 | Stacie Doyle | Scheduling is based on the filed maintenance practice in effect.
| 21 | Detailed (Bi-Annual) on XLPE Circuits | Line | 17 | 17 | Stacie Doyle | Scheduling is based on the filed maintenance practice in effect. There are 22 XLPE circuits - 17 bi-annual inspections were completed in 2015, ?? bi-annual inspections will be completed in 2016.
Air Switches | 10884 | [5 empty] | The number of facilities only includes CAISO controlled facilities. The difference between 2015 (10,884) and 2016 (11,000) is due to 676 new and 560 removed or not CAISO controlled.
Inspection
|  | Visual Inspection | Air Switch | N/A | N/A | N/A | This task is performed as part of the station inspection.
|  | Infrared Inspection | Air Switch | N/A | N/A | N/A | This task is performed as part of the station infrared inspection.
Diagnostic/Performance Testing
|  | Diagnostic/Performance Test | Air Switch | 99 | 98 | N/A | Triggered by condition and trouble.
Maintenance
|  | Insulation Coating | Air Switch | 0 | 0 | N/A | Triggered by condition. Performed only in areas at risk of contamination-caused flashovers.
|  | Animal Abatement | Air Switch | 0 | 0 | N/A | Triggered by condition. Performed as required by local conditions.
|  | Lubricate | Air Switch | 0 | 0 | N/A | Triggered by condition and trouble.
|  | Mechanism Service | Air Switch | 0 | 0 | N/A | Triggered by condition and trouble.
|  | Overhaul | Air Switch | 0 | 0 | N/A | Triggered by condition and trouble.
|  | Repair/Adjustment | Air Switch | 0 | 0 | N/A | Triggered by condition and trouble.
Batteries | 597 | [5 empty] | Only includes CAISO controlled facilities at stations and does not include chargers. Batteries listed are for stations that have either a circuit breaker, MOAS, or circuit switcher that are CAISO controlled. The difference between 2015 (597) and 2016 (606) is due to 75 new, 65 removed or not CAISO controlled and 1 Out of Service.
Inspection
|  | Visual Inspection | Battery | N/A | N/A | N/A | This task is performed as part of the station inspection.
Diagnostic/Performance Testing
|  | Diagnostic/Performance Test | Battery | 0 | 0 | N/A | Triggered by condition and trouble.
|  | Battery Resistance Test or 3 Hour Discharge Test | Battery | 617 | 638 |  | Station batteries are replaced at the end of their service life. Stations upgraded to MPAC may result in additional batteries at the station. With on-going replacement activities and MPAC installations, the total battery maintenance intervals will fluctuate. The new Battery Resistance Test and 3 Hour Discharge Tests are done on a 6 month, 1 year and 6 year cycle. The 2016 total of 606 represents 572 VLA , 20 VRLA ,12 NiCad and one NAS Type battery.
Maintenance
|  | Replace Cell | Battery | 0 | 3 | N/A | Triggered by condition and trouble.
Circuit Breakers | 3160 | [5 empty] | The total includes both transmission-class and distribution-class breakers that are slated as being under CAISO operational control. Of the 3,268 breakers, 284 are operating at 500 kV; 2,984 are operating at or below 230 kV. The difference between 2015 (3,160) and 2016 (3,268) is due to 103 removed, out of service or reclassified and 211 new or back in service.
Inspection
|  | Visual Inspection | Circuit Breaker | N/A | N/A | N/A | This task is performed as part of the station inspection.
|  | Infrared Inspection | Circuit Breaker | N/A | N/A | N/A | This task is performed as part of the station infrared inspection.
Diagnostic/Performance Testing
|  | Breaker Oil Analysis (BOA) | Breaker | 95 | 102 | N/A | Triggered by ACC, condition, and trouble. ACC triggered testing at 50% and 100% ACC. Also performed as part of the mech service on OCB's but is not triggered as a separate event.
|  | Air/SF6 Gas Moisture Test | Breaker | 0 | 0 | N/A | Triggered by ACC, condition, and trouble. ACC triggered testing at 100% ACC.
|  | Exercise | Breaker | 3111 | 2458 |  | In previous SMR reports, "Exercise" only included 500kV breakers. PG&E does not conduct Functional Performance Test maintenance for Transmission Class circuit breakers operating at 230kV and below. Therefore, this maintenance task is for all Transmission Class Circuit Breakers regardless of voltage. The total planned is an estimate derived from SAP. If a counter change is noted during a station inspection, the updated counter reading will update SAP which will eliminate the need to perform an Exercise. Therefore, the actual Exercises performed generally will not match the estimate planned.
|  | SF6 Gas Laboratory Test | Breaker | 0 | 6 | N/A | Triggered by condition and trouble. Tested at 100% ACC and before opening the SF6 tank on condition or trouble.
Maintenance
|  | Insulation Coating | Breaker | 0 | 0 | N/A | Triggered by condition. Performed only in areas at risk of contamination-caused flashovers.
|  | Animal Abatement | Breaker | 0 | 0 | N/A | Triggered by condition. Performed as required by local conditions.
|  | Add Oil/Gas | Breaker | 0 | 24 | N/A | Triggered by trouble.
|  | Compressor Service | Breaker | N/A | 0 |  | Triggered by time and installation and is performed as part of the mechanism service on circuit breakers equipped with compressors.
|  | Mechanism Service | Breaker | 401 | 432 | N/A | Triggered by time, condition, and trouble.
|  | Oil or SF6 Gas Leak Repairs | Breaker | 0 | 4 | N/A | Triggered by condition.
|  | Overhaul | Breaker | 34 | 36 | N/A | Triggered by time for tertiary reactor breakers and by ACC or condition for all others.
|  | Repair/Adjustment | Breaker | 0 | 644 | N/A | Triggered by condition and trouble.
Circuit Switchers | 408 | [5 empty] | The number of facilities only includes CAISO controlled facilities. The difference between 2015 (408) and 2016 (407) is due to 13 removals and 12 new.
Inspection
|  | Visual Inspection | Circuit Switcher | N/A | N/A | N/A | This task is performed as part of the station inspection.
|  | Infrared Inspection | Circuit Switcher | N/A | N/A | N/A | This task is performed as part of the station Infrared Inspection.
Diagnostic/Performance Testing
|  | Diagnostic/Performance Test | Circuit Switcher | 11 | 12 | N/A | Triggered by condition and trouble. Performed at 300 operations or 100% ACC.
|  | Mechanism Service | Circuit Switcher | 74 | 74 | N/A | Triggered by ACC, time, condition and trouble. Time triggered once every calendar year for Type A and Type G circuit switchers. Time triggered once every five calendar years for all other type circuit switchers.
Maintenance
|  | Insulation Coating | Circuit Switcher | 0 | 0 | N/A | Triggered by condition. Performed only in areas at risk of contamination-caused flashovers.
|  | Animal Abatement | Circuit Switcher | 0 | 0 | N/A | Triggered by condition. Performed as required by local conditions.
|  | Repair/Adjustment | Circuit Switcher | 0 | 28 | 28 | Triggered by trouble.
Load Tap Changer (LTC) Portion of 3-Phase Voltage-Regulating Devices | 147 | [5 empty] | The number of facilities only includes the voltage regulating portion of CAISO controlled, three-phase, regulating devices. The difference between 2015 (147) and 2016 (157) is due to 13 new, 1 returned to service and 1 reclassified and 4 removed and 1 out of service.
Inspection
|  | Visual Inspection | LTC | N/A | N/A | N/A | This task is performed as part of the station inspection.
|  | Infrared Inspection | LTC | N/A | N/A | N/A | This task is performed as part of the station infrared inspection.
Diagnostic/Performance Testing
|  | Oil Diagnostic Tests - LTC (TASA) | LTC | 147 | 182 | N/A | Triggered by time, condition, trouble, and installation. Time triggered once every calendar year, once following installation, once following overhaul and once following initial energizing.
Maintenance
|  | Insulation Coating | LTC | 0 | 0 | N/A | Triggered by condition. Performed only in areas at risk of contamination-caused flashovers.
|  | Animal Abatement | LTC | 0 | 0 | N/A | Triggered by condition. Performed as required by local conditions.
|  | LTC Overhaul | LTC | 17 | 18 | N/A | Triggered by operations, condition and trouble per the adopted filed maintenance practice in effect. The planned number submitted is an estimate generated by SAP based projections from counter readings previously entered into the database.
|  | LTC Through Neutral (Step-type Voltage Regulators with Reversing Switches) | LTC | 54 | 38 |  | Interval is 3, 6, 9, or 12 months as determined by the headquarters based on equipment conditions and history. Some models may not require operations through neutral. The planned number is an estimate by SAP.
|  | Oil Leak Repairs | LTC | 0 | 1 | N/A | Triggered by condition and trouble.
|  | Repair/Adjustment | LTC | 0 | 45 | N/A | Triggered by trouble.
Motor Operated Air Switches | 733 | [5 empty] | The number of facilities only includes CAISO controlled facilities. The number of facilities only includes CAISO controlled facilities. The difference between 2015 (733) and 2016 (720) is 100 are new and 113 were removed.
Inspection
|  | Visual Inspection | MOAS | N/A | N/A | N/A | This task is performed as part of the station inspection.
|  | Infrared Inspection | MOAS | N/A | N/A | N/A | This task is performed as part of the station Infrared Inspection.
Diagnostic/Performance Testing
|  | Diagnostic/Performance Test | MOAS | 0 | 1 | N/A | Triggered by trouble.
Maintenance
|  | Insulation Coating | MOAS | 0 | 0 | N/A | Triggered by condition. Performed only in areas at risk of contamination-caused flashovers.
|  | Animal Abatement | MOAS | 0 | 0 | N/A | Triggered by condition. Performed as required by local conditions.
|  | Mechanism Service | MOAS | 106 | 110 | N/A | Triggered by time, condition and trouble. Time triggered once every five calendar years.
|  | Overhaul | MOAS | 0 | 0 | N/A | Triggered by condition and trouble.
|  | Repair/Adjustment | MOAS | 0 | 34 | N/A | Triggered by trouble.
Power Transformers | 482 | [5 empty] | Includes in-service CAISO controlled transformers and spares in an operating position. The difference between 2015 (482) and 2016 (484) is due to 25 being removed or out of service or reclassified, 27 new being added or reclassified or returned to service.
Inspection
|  | Visual Inspection | Transformer | N/A | N/A | N/A | This task is performed as part of the station inspection.
|  | Infrared Inspection | Transformer | N/A | N/A | N/A | This task is performed as part of the station infrared inspection.
Diagnostic/Performance Testing
|  | Oil Diagnostic Tests - Main | Transformer | 174 | 246 | N/A | Triggered by time, condition, trouble and installation. Time triggered every year for GSU, Atmoseal and 500 kV, every 2 years for FPE and others rated at or above 400 MVA, and every 6 years for all units used as spares, all others in service and any station service bank over 1 MVA. PG&E has 51 that fall in the GSU, Atmoseal or 500 kV, 57 that are in the FPE, or 400 MVA and above and 376 in the remaining category. At this time PG&E does not have any station service above 1 MVA.
Maintenance
|  | Insulation Coating | Transformer | 0 | 0 | N/A | Triggered by condition. Performed only in areas at risk of contamination-caused flashovers.
|  | Animal Abatement | Transformer | 0 | 0 | N/A | Triggered by condition. Performed as required by local conditions.
|  | Add Make-Up Oil or Nitrogen Gas | Transformer | 0 | 23 | N/A | Triggered by condition and trouble.
|  | Oil Leak Repairs | Transformer | 0 | 30 | N/A | Triggered by condition and trouble.
|  | Repair/Adjustment | Transformer | 0 | 149 | N/A | Triggered by trouble.
|  | Replace Parts | Transformer | 0 | 2 | N/A | Triggered by trouble.
|  | Spare Transformer Tests | Transformer | 2 | 2 | N/A | Triggered by time, condition, and trouble. Time triggered once every twelve calendar years.
Protective Relay Schemes | 11419 | [5 empty] | Includes CAISO controlled schemes only. This is a snapshot in time and continuously varies. The difference between 2015 (11,419) and 2016 (11,302) is 117. This is due to 967 new or reclassified schemes and 1,084 future, out of service, removed, and reclassified schemes.
Transmission Class Trigger Interval
|  | Component performance and scheme functional test | Scheme | 1610 |  |  | Time triggered in accordance with Template/Maintenance Tasks for Relay Schemes. See the adopted maintenance practice for details.
Clean and inspect
|  | Read Voltage/Replace Fuses |  |  | 1709
DFR functional test
Communication component and channel performance test
Reactors | 209 | [5 empty] | The number of facilities only includes CAISO controlled air-core and oil-filled reactors. The difference between 2015 (209) and 2016 (231) is due to 3 removed, 1 returned to service and 24 new.
Inspection
|  | Visual Inspection | Reactor | N/A | N/A | N/A | This task is performed as part of the station inspection.
|  | Infrared Inspection | Reactor | N/A | N/A | N/A | This task is performed as part of the station Infrared Inspection.
|  | Annual Inspection-Out-of-Service (Air-type Reactors Only) | Reactor | 89 | 89 | N/A | Triggered by time, condition, and trouble. Time triggered once every calendar year.
Diagnostic/Performance Testing
|  | Oil Diagnostic Tests | Reactor | 22 | 22 | N/A | Triggered by time, condition, trouble, and installation. Time triggered once every six calendar years for 230 kV and below and once every year for 500 kV.
Maintenance
|  | Insulation Coating | Reactor | 0 | 0 | N/A | Triggered by condition. Performed only in areas at risk of contamination-caused flashovers.
|  | Animal Abatement | Reactor | 0 | 0 | N/A | Triggered by condition. Performed as required by local conditions.
|  | Add Make-Up Oil or Nitrogen Gas | Reactor | 0 | 0 | N/A | Triggered by condition and trouble.
|  | Repair/Adjustment | Reactor | 0 | 4 | N/A | Triggered by trouble.
Regulators | 48 | [5 empty] | The number of facilities includes the voltage regulating portion of CAISO controlled, single-phase and three-phase, regulating devices as noted. The difference between 2015 (48) and 2016 (45) is 3 was removed.
Inspection
|  | Visual Inspection | Regulator | N/A | N/A | N/A | This task is performed as part of the station inspection.
|  | Infrared Inspection | Regulator | N/A | N/A | N/A | This task is performed as part of the station infrared inspection.
Diagnostic/Performance Testing
|  | Oil Diagnostic Tests - Main | Regulator | 24 | 23 | N/A | Triggered by time, condition, trouble, and installation. This item includes 1-year TDA, 2-year TDA, 6-year TDA, and 6-year oil quality tests. It also includes 1-year TASA on single phase regulators.
Maintenance
|  | Single-Phase Overhaul | Regulator | 4 | 3 | N/A | Triggered by condition or trouble.
|  | Insulation Coating | Regulator | 0 | 0 | N/A | Triggered by condition. Performed only in areas at risk of contamination-caused flashovers.
|  | Animal Abatement | Regulator | 0 | 0 | N/A | Triggered by condition. Performed as required by local conditions.
|  | Add Make-Up Oil or Nitrogen Gas | Regulator | 0 | 2 | N/A | Triggered by condition and trouble.
Station | 550 | [5 empty] | Includes stations that have either a circuit breaker, MOAS, or circuit switcher that is considered to be under CAISO operational control. The difference between 2015 (550) and 2016 (563) is due to 13 new.
Inspection
|  | Visual Inspection | Station | 4368 | 6002 |  | Substation visual equipment inspections are scheduled on a monthly basis for high criticality substations (Type 1), and every-other-month for low criticality substations (Type 2). The planned number submitted is a count of station inspection plans and is not a one-to-one relationship to the number of stations. Some of the larger stations have more than one plan; e.g. Gates has 2 plans, Cottonwood has 2 plans, Moss Landing has 3 plans, etc. 402 Stations are on an every other month cycle and 157 are on a monthly cycle and 4 are new and haven't been started yet.
|  | Infrared Inspection | Station | 550 | 558 | N/A | Triggered by time, condition and trouble. Time triggered once every calendar year. Infrared Inspection of all station equipment included in this unit.
Station Series Capacitor Banks | 16 | [5 empty] | Series Capacitors
Inspection
|  | Visual Inspection | Series Capacitor | N/A | N/A | N/A | This task is performed as part of the station inspection.
|  | Infrared Inspection | Series Capacitor | N/A | N/A | N/A | This task is performed as part of the station Infrared Inspection.
|  | Annual Inspection | Series Capacitor | 16 | 16 | N/A | Triggered by time, condition and trouble. Time triggered once every calendar year.
Diagnostic/Performance Testing
|  | Breaker Diagnostic Test | Series Capacitor | Counted as part of breakers | N/A | N/A | Triggered by time, condition, and trouble. Performed on breakers that are an integral part of the capacitor banks and not numbered separately. Time triggered once every calendar year as part of the annual inspection.
Maintenance
|  | Insulation Coating | Series Capacitor | Counted as part of breakers | N/A | N/A | Triggered by condition. Performed only in areas at risk of contamination-caused flashovers.
|  | Animal Abatement | Series Capacitor | 0 | 0 | N/A | Triggered by condition. Performed as required by local conditions.
|  | Compressor Service | Series Capacitor | Counted as part of breakers | N/A | N/A | Triggered by time, condition, and trouble.
|  | Mechanism Service | Series Capacitor | Counted as part of breakers | N/A | N/A | Triggered by time, condition, and trouble. Time triggered once every calendar year as part of the annual inspection.
|  | Overhaul | Series Capacitor | Counted as part of breakers | N/A | N/A | Triggered by condition and trouble.
|  | Repair/Adjustment | Series Capacitor | 0 | 11 | N/A | Triggered by trouble.
Station Shunt Capacitor Banks | 98 | [5 empty] | The total includes individual steps or phases within transmission-class capacitor bank. Also included is the shunt capacitor portion of the SVC at Paul Sweet Sub. The difference between 2015 (98) and 2016 (109) is due to 11 new shunt cap banks.
Inspection
|  | Visual Inspection | Shunt Capacitor | N/A | N/A | N/A | This task is performed as part of the station inspection.
|  | Infrared Inspection | Shunt Capacitor | N/A | N/A | N/A | This task is performed as part of the station infrared inspection.
|  | Annual Inspection | Shunt Capacitor | 98 | 96 | N/A | Triggered by time, condition, and trouble. Time triggered once every calendar year. The difference of 9 is due to the SVC Shunt Caps are done during the SVC Inspection and the plans have been locked.
Maintenance
|  | Insulation Coating | Shunt Capacitor | 0 | 0 | N/A | Triggered by condition. Performed only in areas at risk of contamination-caused flashovers.
|  | Animal Abatement | Shunt Capacitor | 0 | 0 | N/A | Triggered by condition. Performed as required by local conditions.
|  | Repair/Adjustment | Shunt Capacitor | 0 | 12 | N/A | Triggered by trouble.
Static VAR Compensator (SVC) & Static Compensator (STATCOM) | 6 | [5 empty] | PG&E has one STATCOM at Paul Sweet Substation and six Static Var Compensators (SVC's) at: 1. Newark Substation 2. Potrero Substation 3. Pueblo Substation 3. Humboldt Substation 4. Garberville Substation 5. Big River Substation
Inspection
|  | Visual Inspection | SVC & STATCOM | N/A | N/A | N/A | This task is performed as part of the station inspection.
|  | Infrared Inspection | SVC & STATCOM | N/A | N/A | N/A | This task is performed as part of the station infrared inspection.
|  | SVC Maintenance | SVC & STATCOM | 5 | 4 | The difference is due to San Fran A (Potrero PP) not being done due to the Trans Bay Cable being out so no clearance could be scheduled. | This task is not included in the adopted filed maintenance practices. This time based interval is set differently based on manufacturer. The time intervals submitted for this report are: 6 months, 12 months, 24 months, 36 months, and 60 months. This information will be clarified when a revised station maintenance practice is submitted. Pueblo is on a 2 year cycle and was done in 2014 so it will be due in 2016.
Diagnostic/Performance Testing
|  | To Be Determined | SVC & STATCOM | N/A | N/A | N/A | None
Maintenance
|  | To Be Determined | SVC & STATCOM | N/A | N/A | N/A | None
Synchronous Condensers | 6 | [5 empty] | Number of reported facilities includes in-service, CAISO controlled facilities. The difference between 2015 (6) and 2016 (5) is due to San Mateo Condenser #1 being out of service.
Inspection
|  | Visual Inspection | Condenser | N/A | N/A | N/A | This task is performed as part of the station inspection.
|  | Infrared Inspection | Condenser | N/A | N/A | N/A | This task is performed as part of the station Infrared Inspection.
|  | Annual Inspection | Condenser | 8 | 10 | N/A | Triggered by time, condition, and trouble. Time: once every 6 months or once per year.
Diagnostic/Performance Testing
|  | Diagnostic/Performance Test | Condenser | N/A | N/A | N/A | PG&E does not have a "diagnostic/performance test" as a "maintenance task" for condensers. The term diagnostic/performance test is associated with water tests for those condensers with water systems and is maintained as part of the "service" that is done by time, condition, or trouble where the time trigger is 3 years.
Maintenance
|  | Insulation Coating | Condenser | 0 | 0 | N/A | Triggered by condition. Performed only in areas at risk of contamination-caused flashovers.
|  | Animal Abatement | Condenser | 0 | 0 | N/A | Triggered by condition. Performed as required by local conditions.
|  | Add Gas | Condenser | 0 | 0 | N/A | Triggered by condition and trouble.
|  | Oil Leak Repairs | Condenser | 0 | 0 | N/A | Triggered by condition and trouble.
|  | Repair/Adjustment | Condenser | 0 | 36 | N/A | Triggered by condition and trouble.
|  | Overhaul | Condenser | 2 | 2 | N/A | Triggered by time, condition, and trouble. Time triggered once every six calendar years.
|  | Service | Condenser | 0 | 0 | N/A | Triggered by time, condition, and trouble. Time triggered once every three calendar years.