## PGE2017SMRS_ACTUAL
|  | 2017 STANDARDIZED MAINTENANCE REPORT - ACTUAL |  |  |  |  | REVISIONS ARE HIGHLIGHTED IN YELLOW
EQUIPMENT TYPE | NO. OF FACILITIES | MAINT. TASK | MAINT. UNIT | PLANNED | ACTUAL | EXCEPTION FROM PLANNED | NOTES
Overhead Line Patrol/Inspection (Lines) | 1379 | [5 empty] | Number of reported facilities includes non-CAISO controlled facilities. The number of facilities in 2016 was 1,376 and the number of facilities in 2017 is 1,379 due to 3 new circuits added.
Inspection
|  | Detailed Inspections | Line | 535 | 547 | The additional 12 inspections were due to line splits that were created in 2017 as well as shared lines. | Number of inspections includes those performed on non-CAISO controlled facilities.
|  | Ground Inspections | Line | 44 | 44 |  | Number of inspections includes those performed on non-CAISO controlled facilities.
|  | Aerial Inspections | Line | 800 | 800 |  | Number of inspections includes those performed on non-CAISO controlled facilities.
Overhead Line Patrol/Inspection (Structures) | 175854 | [5 empty] | The number of reported facilities includes non-CAISO controlled facilities. The difference between 178,686 in the 2016 and the 175,854 in 2017 Planning SMR is attributed to some locations having assets deleted by the Field Asset Inventory Team (FAI Project).
Inspection
|  | Detailed Inspections | Structure | 68629 | 72518 | In 2017 PG&E added additional inspections due to line reconfigurations which are now set on a maintenance cycle. | Number of inspections includes those performed on non-CAISO controlled facilities.
|  | Ground Inspections | Structure | 2081 | 2081 |  | Number of inspections includes those performed on non-CAISO controlled facilities.
|  | Aerial Inspections | Structure | 105174 | 105174 |  | Number of inspections includes those performed on non-CAISO controlled facilities.
|  | Climbing Inspections (2% 500 kV Critical) | Structure | 72 | 72 |  | The number of facilities only includes CAISO controlled facilities. The maintenance interval is every three years.
Overhead Line Vegetation Management/Right-Of-Way Maintenance | N/A | [5 empty] | The planned counts are estimates based on historical information and predictions based on last year’s inspections.
Maintenance
|  | Trees Removed | Tree | 80000 | 66000 | Trees removed is subject to change from planned due to natural variability in tree growth rates. Actual trees removed fell within normal variance from forecasted for 2017. | Number of trees removed includes those removed on non-CAISO controlled facilities. Tree count includes only trees > 4 inches Diameter at Breast Height (DBH); smaller trees are counted as brush.
|  | Trees Trimmed | Tree | 33000 | 32000 | Trees trimmed is subject to change from planned due to natural variability in tree growth rates. Actual trees trimmed fell within normal variance from forecasted for 2017. | Number of trees trimmed includes those trimmed on non-CAISO controlled facilities. Tree count includes only trees that are > 4 inches Diameter at Breast Height (DBH); smaller trees are counted as brush. Each year PG&E rounds planned (forecasted) and actual counts for tree trimming.
Overhead Line Structures - Wood Pole | ≈115,000 | [5 empty] | Number of reported facilities includes non-CAISO controlled facilities.
Inspection
|  | Test | Wood Pole | 11202 | 12584 |  | The number of reported planned-tests, includes those performed on non-CAISO controlled facilities.
Maintenance
|  | Treatment | Wood Pole | 9745 | 10172 |  | Number of actual treatments is dependent upon testing.
|  | Repair | Wood Pole | 269 | 270 |  | Repair means to reinforce (stub) a wood pole by attaching a steel reinforcing member with hydraulic pressure at, or below, ground level. Poles identified as needing to be repaired will be considered for replacement per normal inspection and test program guidelines.
|  | Replace | Wood Pole | 275 | 385 | The planned total submitted each year is an estimate. The additional 110 poles is attributed to operational efficiencies and backlog reduction. | Number of planned replacements includes non-CAISO controlled facilities. Replace is defined as: Any whole structure replaced or any single leg within an "H" structure configuration. The planned total submitted each year is an estimate that is dependent on funding, engineering, and the availability of crews to perform the work.
Overhead Line Insulators (contamination control) | N/A | [5 empty] | The number of facilities cannot be determined from records and is noted as N/A. Triggered by condition and trouble.
Maintenance
|  | Wash Insulators | Insulator String | 0 | 9857 |  | Number of reported insulator washes includes those performed on non-CAISO controlled facilities. Transmission Line Insulator washing is performed based on local environmental conditions, operating experience and in accordance with pre-determined wash cycles established in SAP.
Underground Line Patrol/Inspection | 57 | [5 empty] | Number of reported facilities includes in-service CAISO controlled facilities.
Inspection
|  | Routine (Monthly) on Pipe-Type Circuits | Line | 396 | 396 |  | Scheduling is based on the filed maintenance practice in effect.
|  | Routine (Quarterly) on XLPE Circuits | Line | 67 | 67 |  | Scheduling is based on the filed maintenance practice in effect.
|  | Detailed (Annual) on Pipe-Type Circuits | Line | 36 | 36 |  | Scheduling is based on the filed maintenance practice in effect.
|  | Detailed (Bi-Annual) on XLPE Circuits | Line | 17 | 17 |  | Scheduling is based on the filed maintenance practice in effect. There are 21 XLPE circuits - 17 bi-annual inspections were completed in 2015, 4 bi-annual inspections will be completed in 2016.
Air Switches | 11083 | [5 empty] | The number of facilities only includes CAISO controlled facilities. The difference between 2016 (11,000) and 2017 (11,083) is due to 368 new and 285 removed or not CAISO controlled. (11,000+368-285=11,083)
Inspection
|  | Visual Inspection | Air Switch | N/A |  |  | This task is performed as part of the station inspection.
|  | Infrared Inspection | Air Switch | N/A |  |  | This task is performed as part of the station infrared inspection.
Diagnostic/Performance Testing
|  | Diagnostic/Performance Test | Air Switch | 56 | 55 | The difference is due to equipment being removed. | Triggered by condition and trouble.
Maintenance
|  | Insulation Coating | Air Switch | 0 | 0 |  | Triggered by condition. Performed only in areas at risk of contamination-caused flashovers.
|  | Animal Abatement | Air Switch | 0 | 0 |  | Triggered by condition. Performed as required by local conditions.
|  | Lubricate | Air Switch | 0 | 0 |  | Triggered by condition and trouble.
|  | Mechanism Service | Air Switch | 0 | 0 |  | Triggered by condition and trouble.
|  | Overhaul | Air Switch | 0 | 0 |  | Triggered by condition and trouble.
|  | Repair/Adjustment | Air Switch | 0 | 140 |  | Triggered by condition and trouble.
Batteries | 601 | [5 empty] | Only includes a count of batteries at stations that have an CAISO-controlled Circuit Breaker, or Motor-Operated Air Switch, or Circuit Switcher. This total does not include battery chargers. The difference between the 2016 total of 604 batteries and the 2017 total of 601 batteries is because 59 were removed, 6 are out of service, and 62 new batteries were installed. (604-59-6+62=601)
Inspection
|  | Visual Inspection | Battery | N/A |  |  | This task is performed as part of the station inspection.
Diagnostic/Performance Testing
|  | Diagnostic/Performance Test | Battery | 0 | 0 |  | Triggered by condition and trouble.
|  | Battery Resistance Test or 3 Hour Discharge Test | Battery | 617 | 620 | The difference of 3 is due to 1 plan being called out 2 additional times and 1 new plan being created after an order was already called under the old plan. | Station batteries are replaced at the end of their service life. Stations upgraded to MPAC may result in additional batteries at the station. With on-going replacement activities and MPAC installations, the total battery maintenance intervals will fluctuate. Battery Resistance Tests or 3 Hour Discharge Tests are done on a 6-month, 1-year or 6-year cycle depending on battery type as outlined in the adopted filed maintenance practice.
Maintenance
|  | Replace Cell | Battery | 0 | 0 |  | Triggered by condition and trouble.
Circuit Breakers | 3371 | [5 empty] | The total includes both transmission-class and distribution-class breakers that are slated as being under CAISO operational control. Of the 3,268 breakers, 284 are operating at 500 kV; 2,984 are operating at or below 230 kV. The difference between the 2016 total of 3,265 breakers and the 2017 total of 3,371 breakers is because 45 were removed, out of service, or reclassified as not being under CAISO control and 151 breakers are either new or returned to service. (3,265-45+151=3,371)
Inspection
|  | Visual Inspection | Circuit Breaker | N/A |  |  | This task is performed as part of the station inspection.
|  | Infrared Inspection | Circuit Breaker | N/A |  |  | This task is performed as part of the station infrared inspection.
Diagnostic/Performance Testing
|  | Breaker Oil Analysis (BOA) | Breaker | 85 | 85 |  | Triggered by ACC, condition, and trouble. ACC triggered testing at 50% and 100% ACC. Also performed as part of the mech service on OCB's but is not triggered as a separate event.
|  | Air/SF6 Gas Moisture Test | Breaker | 1 | 1 |  | Triggered by ACC, condition, and trouble. ACC triggered testing at 100% ACC.
|  | Exercise | Breaker | 3680 | 2619 |  | All Transmission Class Circuit Breakers have an exercise plan. Tertiary reactor breakers (Distribution Class) do not have an exercise plan but have an overhaul plan. The planned total is always an estimate derived from SAP. It is the total of orders that would be generated to be worked if a counter change is not registered in SAP. When a counter change is noted during a station inspection, the updated counter reading will update SAP which will eliminate the need to perform an exercise. Therefore, the Actual exercises performed during 2016 generally will not match the estimated submitted as Planned.
|  | SF6 Gas Laboratory Test | Breaker | 0 | 0 |  | Triggered by condition and trouble. Tested at 100% ACC and before opening the SF6 tank on condition or trouble.
Maintenance
|  | Insulation Coating | Breaker | 0 | 0 |  | Triggered by condition. Performed only in areas at risk of contamination-caused flashovers.
|  | Animal Abatement | Breaker | 0 | 0 |  | Triggered by condition. Performed as required by local conditions.
|  | Add Oil/Gas | Breaker | 0 | 45 |  | Triggered by trouble.
|  | Compressor Service | Breaker | N/A | N/A |  | Triggered by time and installation and is performed as part of the mechanism service on circuit breakers equipped with compressors.
|  | Mechanism Service | Breaker | 312 | 312 |  | Triggered by time, condition, and trouble.
|  | Oil or SF6 Gas Leak Repairs | Breaker | 0 | 0 |  | Triggered by condition.
|  | Overhaul | Breaker | 91 | 37 39 | The difference is due to equipment not yet reaching the number of counter operations required to initiate an order. | Revised from 37 to 39. The 39 are: 33 reactor breakers, 4 reactor breakers done a second time, and 2 oil breakers Triggered by time for tertiary reactor breakers and by ACC or condition for all others.
|  | Repair/Adjustment | Breaker | 0 | 598 |  | Triggered by condition and trouble.
Circuit Switchers | 405 | [5 empty] | The number of facilities only includes CAISO controlled facilities. The difference between 2016 (407) and 2017 (405) is due to 11 removals and/or reclassification and 9 new or in service. (407-11+9=405)
Inspection
|  | Visual Inspection | Circuit Switcher | N/A |  |  | This task is performed as part of the station inspection.
|  | Infrared Inspection | Circuit Switcher | N/A |  |  | This task is performed as part of the station Infrared Inspection.
Diagnostic/Performance Testing
|  | Diagnostic/Performance Test | Circuit Switcher | 7 | 5 | The difference is due to equipment not yet reaching the number of operations required to initiate an order. | Triggered by condition and trouble. Performed at 300 operations or 100% ACC.
|  | Mechanism Service | Circuit Switcher | 98 | 98 |  | Triggered by ACC, time, condition and trouble. Time triggered once every calendar year for Type A and Type G circuit switchers. Time triggered once every five calendar years for all other type circuit switchers.
Maintenance
|  | Insulation Coating | Circuit Switcher | 0 | 0 |  | Triggered by condition. Performed only in areas at risk of contamination-caused flashovers.
|  | Animal Abatement | Circuit Switcher | 0 | 0 |  | Triggered by condition. Performed as required by local conditions.
|  | Repair/Adjustment | Circuit Switcher | 0 | 32 33 |  | Revised from 32 to 33. Triggered by trouble.
Load Tap Changer (LTC) Portion of 3-Phase Voltage-Regulating Devices | 168 | [5 empty] | The number of facilities only includes the voltage regulating portion of CAISO controlled, three-phase, regulating devices. The difference between 2016 (157) and 2017 (168) is due to 5 new and 6 reclassified. (157+5+6=168)
Inspection
|  | Visual Inspection | LTC | N/A |  |  | This task is performed as part of the station inspection.
|  | Infrared Inspection | LTC | N/A |  |  | This task is performed as part of the station infrared inspection.
Diagnostic/Performance Testing
|  | Oil Diagnostic Tests - LTC (TASA) | LTC | 188 | 218 | The difference is due to equipment having accelerated TJH2B test results that require additional tests. | Triggered by time, condition, trouble, and installation. Time triggered once every calendar year, once following installation, once following overhaul and once following initial energizing.
Maintenance
|  | Insulation Coating | LTC | 0 | 0 |  | Triggered by condition. Performed only in areas at risk of contamination-caused flashovers.
|  | Animal Abatement | LTC | 0 | 0 |  | Triggered by condition. Performed as required by local conditions.
|  | LTC Overhaul | LTC | 10 | 7 | The difference is due to equipment not yet reaching the number of operations required to initiate an order. | Triggered by operations, condition and trouble per the adopted filed maintenance practice in effect. The planned number submitted is an estimate generated by SAP based projections from counter readings previously entered into the database.
|  | LTC Through Neutral (Step-type Voltage Regulators with Reversing Switches) | LTC | 64 | 37 | The difference is due to LTC's running through neutral before an order is called and the plan resets itself. | Interval is 3, 6, 9, or 12 months as determined by the headquarters based on equipment conditions and history. Some models may not require operations through neutral. The planned number is an estimate by SAP.
|  | Oil Leak Repairs | LTC | 0 | 0 |  | Triggered by condition and trouble.
|  | Repair/Adjustment | LTC | 0 | 47 |  | Triggered by trouble.
Motor Operated Air Switches | 793 | [5 empty] | The number of facilities only includes CAISO controlled facilities. The difference between 2016 (720) and 2017 (793) is 86 are new or reclassified and 13 were removed and or out of service. (720+86-13=793)
Inspection
|  | Visual Inspection | MOAS | N/A |  |  | This task is performed as part of the station inspection.
|  | Infrared Inspection | MOAS | N/A |  |  | This task is performed as part of the station Infrared Inspection.
Diagnostic/Performance Testing
|  | Diagnostic/Performance Test | MOAS | 0 | 0 |  | Triggered by trouble.
Maintenance
|  | Insulation Coating | MOAS | 0 | 0 |  | Triggered by condition. Performed only in areas at risk of contamination-caused flashovers.
|  | Animal Abatement | MOAS | 0 | 0 |  | Triggered by condition. Performed as required by local conditions.
|  | Mechanism Service | MOAS | 92 | 92 |  | Triggered by time, condition and trouble. Time triggered once every five calendar years.
|  | Overhaul | MOAS | 0 | 0 |  | Triggered by condition and trouble.
|  | Repair/Adjustment | MOAS | 0 | 23 |  | Triggered by trouble.
Power Transformers | 493 | [5 empty] | Includes in-service CAISO controlled transformers and spares in an operating position. The difference between 2016 (484) and 2017 (493) is due to 4 being removed or out of service, and 13 new being added or reclassified or returned to service. (484-4+13=493)
Inspection
|  | Visual Inspection | Transformer | N/A |  |  | This task is performed as part of the station inspection.
|  | Infrared Inspection | Transformer | N/A |  |  | This task is performed as part of the station infrared inspection.
Diagnostic/Performance Testing
|  | Oil Diagnostic Tests - Main | Transformer | 429 | 469 | The difference is due to some equipment being put on a monthly cycle for a period of time and by some equipment having accelerated TJH2B test results that require additional tests. | Triggered by time, condition, trouble and installation. Time triggered every year for GSU, Atmoseal and 500 kV, every 2 years for FPE and others rated at or above 400 MVA, and every 6 years for all units used as spares, all others in service and any station service bank over 1 MVA. At this time PG&E does not have any station service above 1 MVA.
Maintenance
|  | Insulation Coating | Transformer | 0 | 0 |  | Triggered by condition. Performed only in areas at risk of contamination-caused flashovers.
|  | Animal Abatement | Transformer | 0 | 0 |  | Triggered by condition. Performed as required by local conditions.
|  | Add Make-Up Oil or Nitrogen Gas | Transformer | 0 | 8 |  | Triggered by condition and trouble.
|  | Oil Leak Repairs | Transformer | 0 | 0 |  | Triggered by condition and trouble.
|  | Repair/Adjustment | Transformer | 0 | 220 |  | Triggered by trouble.
|  | Replace Parts | Transformer | 0 | 3 |  | Triggered by trouble.
|  | Spare Transformer Tests | Transformer | 0 | 0 |  | Triggered by time, condition, and trouble. Time triggered once every twelve calendar years.
Protective Relay Schemes | 11522 | [5 empty] | Includes CAISO controlled schemes only. This is a snapshot in time and continuously varies. The difference between 2016 (11,302) and 2017 (11,522) is 220. This is due to 608 new or reclassified schemes and 388 future, out of service, removed, and reclassified schemes. (11,302+608-388=11,522)
Transmission Class Trigger Interval
|  | Component performance and scheme functional test | Scheme | 1735 |  |  | Time triggered in accordance with Template/Maintenance Tasks for Relay Schemes. See the adopted maintenance practice for details.
Clean and inspect
|  | Read Voltage/Replace Fuses |  |  | 1625 | 11 were completed early in 2016. 20 reported as planned were not due in 2017. 79 were removed or replaced in 2017. 110 difference between planned and actual.
DFR functional test
Communication component and channel performance test
Reactors | 258 | [5 empty] | The number of facilities only includes CAISO controlled air-core and oil-filled reactors. The difference between 2016 (231) and 2017 (258) is due to 27 new.
Inspection
|  | Visual Inspection | Reactor | N/A |  |  | This task is performed as part of the station inspection.
|  | Infrared Inspection | Reactor | N/A |  |  | This task is performed as part of the station Infrared Inspection.
|  | Annual Inspection-Out-of-Service (Air-type Reactors Only) | Reactor | 109 | 109 |  | Triggered by time, condition, and trouble. Time triggered once every calendar year.
Diagnostic/Performance Testing
|  | Oil Diagnostic Tests | Reactor | 29 | 29 |  | Triggered by time, condition, trouble, and installation. Time triggered once every six calendar years for 230 kV and below and once every year for 500 kV.
Maintenance
|  | Insulation Coating | Reactor | 0 | 0 |  | Triggered by condition. Performed only in areas at risk of contamination-caused flashovers.
|  | Animal Abatement | Reactor | 0 | 0 |  | Triggered by condition. Performed as required by local conditions.
|  | Add Make-Up Oil or Nitrogen Gas | Reactor | 0 | 0 |  | Triggered by condition and trouble.
|  | Repair/Adjustment | Reactor | 0 | 8 |  | Triggered by trouble.
Regulators | 45 | [5 empty] | The number of facilities includes the voltage regulating portion of CAISO controlled, single-phase and three-phase, regulating devices as noted. There is no difference between 2016 and 2017.
Inspection
|  | Visual Inspection | Regulator | N/A |  |  | This task is performed as part of the station inspection.
|  | Infrared Inspection | Regulator | N/A |  |  | This task is performed as part of the station infrared inspection.
Diagnostic/Performance Testing
|  | Oil Diagnostic Tests - Main | Regulator | 33 | 35 | The difference is due to equipment having accelerated TJH2B test results that require additional tests. | Triggered by time, condition, trouble, and installation. This item includes 1-year TDA, 2-year TDA, 6-year TDA, and 6-year oil quality tests. It also includes 1-year TASA on single phase regulators.
Maintenance
|  | Single-Phase Overhaul | Regulator | 4 | 4 |  | Triggered by condition or trouble.
|  | Insulation Coating | Regulator | 0 | 0 |  | Triggered by condition. Performed only in areas at risk of contamination-caused flashovers.
|  | Animal Abatement | Regulator | 0 | 0 |  | Triggered by condition. Performed as required by local conditions.
|  | Add Make-Up Oil or Nitrogen Gas | Regulator | 0 | 0 |  | Triggered by condition and trouble.
Station | 563 |  |  |  |  | No change. | Includes stations that have either a circuit breaker, MOAS, or circuit switcher that is considered to be under CAISO operational control. There was no difference between 2016 and 2017.
Inspection
|  | Visual Inspection | Station | 6125 | 6124 | The difference is due to Healdsburg Jct Sub being removed late in the year. | Substation visual equipment inspections are scheduled on a monthly basis for high criticality substations (Type 1), and every-other-month for low criticality substations (Type 2). The planned number submitted is a count of station inspection plans and is not a one-to-one relationship to the number of stations. Some of the larger stations have more than one plan; e.g. Gates has 2 plans, Cottonwood has 2 plans, Moss Landing has 3 plans, etc.
|  | Infrared Inspection | Station | 562 | 562 |  | Triggered by time, condition and trouble. Time triggered once every calendar year. Infrared Inspection of all station equipment included in this unit.
Station Series Capacitor Banks | 16 | [5 empty] | Series Capacitors
Inspection
|  | Visual Inspection | Series Capacitor | N/A |  |  | This task is performed as part of the station inspection.
|  | Infrared Inspection | Series Capacitor | N/A |  |  | This task is performed as part of the station Infrared Inspection.
|  | Annual Inspection | Series Capacitor | 18 | 18 |  | Triggered by time, condition and trouble. Time triggered once every calendar year. VacaDixon 500KV Series Cap Banks 1 & 2 are now on a semi-annual plan that is why there are 2 extra.
Diagnostic/Performance Testing
|  | Breaker Diagnostic Test | Series Capacitor | Counted as part of breakers |  |  | Triggered by time, condition, and trouble. Performed on breakers that are an integral part of the capacitor banks and not numbered separately. Time triggered once every calendar year as part of the annual inspection.
Maintenance
|  | Insulation Coating | Series Capacitor | Counted as part of breakers |  |  | Triggered by condition. Performed only in areas at risk of contamination-caused flashovers.
|  | Animal Abatement | Series Capacitor | 0 | 0 |  | Triggered by condition. Performed as required by local conditions.
|  | Compressor Service | Series Capacitor | Counted as part of breakers |  |  | Triggered by time, condition, and trouble.
|  | Mechanism Service | Series Capacitor | Counted as part of breakers |  |  | Triggered by time, condition, and trouble. Time triggered once every calendar year as part of the annual inspection.
|  | Overhaul | Series Capacitor | Counted as part of breakers |  |  | Triggered by condition and trouble.
|  | Repair/Adjustment | Series Capacitor | 0 | 12 |  | Triggered by trouble.
Station Shunt Capacitor Banks | 104 | [5 empty] | The total includes individual steps or phases within transmission-class capacitor bank. Also included is the shunt capacitor portion of the SVC at Paul Sweet Sub and Garberville Sub. The difference between 2016 (109) and 2017 (104) is due to 1 new and 6 removed.
Inspection
|  | Visual Inspection | Shunt Capacitor | N/A |  |  | This task is performed as part of the station inspection.
|  | Infrared Inspection | Shunt Capacitor | N/A |  |  | This task is performed as part of the station infrared inspection.
|  | Annual Inspection | Shunt Capacitor | 89 | 110 | The difference is due to 21 being done late in 2016 and again mid 2017 to change the cycle date. | Triggered by time, condition, and trouble. Time triggered once every calendar year. The difference is due to 15 shunt capacitors are part of the SVC's and the maintenance is done during the SVC maintenance.
Maintenance
|  | Insulation Coating | Shunt Capacitor | 0 | 0 |  | Triggered by condition. Performed only in areas at risk of contamination-caused flashovers.
|  | Animal Abatement | Shunt Capacitor | 0 | 0 |  | Triggered by condition. Performed as required by local conditions.
|  | Repair/Adjustment | Shunt Capacitor | 0 | 64 34 |  | Revised from 64 to 34. PG&E found orders that were duplicated. Triggered by trouble.
Static VAR Compensator (SVC) & Static Compensator (STATCOM) | 7 | [5 empty] | PG&E has six Static Var Compensators (SVC's): 1) at Newark Substation, 2) at Potrero Substation, 3) at Pueblo Substation, 4) at Humboldt Substation, 5) at Garberville, 6) at Big River. PG&E has one STATCOM at Paul Sweet Substation.
Inspection
|  | Visual Inspection | SVC & STATCOM | N/A |  |  | This task is performed as part of the station inspection.
|  | Infrared Inspection | SVC & STATCOM | N/A |  |  | This task is performed as part of the station infrared inspection.
|  | SVC & STATCOM Inspection/Service | SVC & STATCOM | 7 | 7 |  | Triggered by time as outlined in the adopted filed maintenance practice.
Diagnostic/Performance Testing
|  | To Be Determined | SVC & STATCOM | N/A |  |  | None
Maintenance
|  | To Be Determined | SVC & STATCOM | N/A |  |  | None
Synchronous Condensers | 4 | [5 empty] | Number of reported facilities includes in-service, CAISO controlled facilities. The difference between 2016 (5) and 2017 (4) is due to San Mateo Condenser #2 being out of service.
Inspection
|  | Visual Inspection | Condenser | N/A |  |  | This task is performed as part of the station inspection.
|  | Infrared Inspection | Condenser | N/A |  |  | This task is performed as part of the station Infrared Inspection.
|  | Annual Inspection | Condenser | 5 | 6 | The difference is due to an additional order being called on 1 piece of equipment based on the previous order being done early. | Triggered by time, condition, and trouble. Time: once every 6 months or once per year.
Diagnostic/Performance Testing
|  | Diagnostic/Performance Test | Condenser | N/A |  |  | PG&E does not have a "diagnostic/performance test" as a "maintenance task" for condensers. The term diagnostic/performance test is associated with water tests for those condensers with water systems and is maintained as part of the "service" that is done by time, condition, or trouble where the time trigger is 3 years.
Maintenance
|  | Insulation Coating | Condenser | 0 | 0 |  | Triggered by condition. Performed only in areas at risk of contamination-caused flashovers.
|  | Animal Abatement | Condenser | 0 | 0 |  | Triggered by condition. Performed as required by local conditions.
|  | Add Gas | Condenser | 0 | 0 |  | Triggered by condition and trouble.
|  | Oil Leak Repairs | Condenser | 0 | 0 |  | Triggered by condition and trouble.
|  | Repair/Adjustment | Condenser | 0 | 30 |  | Triggered by condition and trouble.
|  | Overhaul | Condenser | 0 | 0 |  | Triggered by time, condition, and trouble. Time triggered once every six calendar years.
|  | Service | Condenser | 3 | 3 |  | Triggered by time, condition, and trouble. Time triggered once every three calendar years.