## PGE2016SMRS_Actual
2016 STANDARDIZED MAINTENANCE REPORT - Actual
EQUIPMENT TYPE | NO. OF FACILITIES | MAINT. TASK | MAINT. UNIT | PLANNED | ACTUAL | EXCEPTION FROM PLANNED | NOTES
Overhead Line Patrol/Inspection (Lines) | 1376 |  |  |  |  | The number of facilities in 2016 was 1,376 and the number of facilities in 2017 is 1,379 due to 3 new circuits added. | Number of reported facilities includes non-CAISO controlled facilities.
Inspection
|  | Detailed Inspections | Line | 452 | 489 | The 6 Circuits within the Diablo Loop are now set on a Yearly Detailed Inspection Cycle | Number of inspections includes those performed on non-CAISO controlled facilities.
|  | Ground Inspections | Line | 90 | 91 | Additional Tap Added From ETGIS | Number of inspections includes those performed on non-CAISO controlled facilities.
|  | Aerial Inspections | Line | 820 | 844 | The 6 Circuits within the Diablo Loop are now set on a Quarterly Air Patrol (3 x's annually) | Number of inspections includes those performed on non-CAISO controlled facilities.
Overhead Line Patrol/Inspection (Structures) | 178686 |  |  |  |  | The difference between 178,686 in the 2016 and the 175,854 in 2017 Planning SMR is attributed to some locations having assets deleted by the Field Asset Inventory Team (FAI Project). | The number of reported facilities includes non-CAISO controlled facilities.
Inspection
|  | Detailed Inspections | Structure | 62432 | 64059 | In 2016 PG&E added additional Patrols to the Diablo Loop circuits which are now Inspected Annually | Number of inspections includes those performed on non-CAISO controlled facilities.
|  | Ground Inspections | Structure | 3818 | 5279 | In 2016 PG&E added additional Patrols to the Diablo Loop | Number of inspections includes those performed on non-CAISO controlled facilities.
|  | Aerial Inspections | Structure | 105711 | 109348 | In 2016 PG&E added additional Patrols to the Diablo Loop circuits which are now patrolled on a quarterly basis | Number of inspections includes those performed on non-CAISO controlled facilities.
|  | Climbing Inspections (2% 500 kV Critical) | Structure | 30 | 30 | None | The number of facilities only includes CAISO controlled facilities. The maintenance interval is every three years.
Overhead Line Vegetation Management/Right-Of-Way Maintenance | N/A |  |  |  |  | PG&E removed a lot more trees on distribution due to the drought and bark beetle. Most transmission lines are fairly clear and less affected. Most of the work is due to tree growth. Also, some of the drought/beetle affected trees are pruned rather than removed since we top them rather than cut them at the base. This is common when the trees are far away and only a portion of the top could strike the lines. | The planned counts are estimates based on historical information and predictions based on last year’s inspections.
Maintenance
|  | Trees Removed | Tree | 126000 | 64000 | Trees removed are subject to change from planned due to natural variability in tree growth rates. Actual trees removed fell within normal variance from forecasted for 2016. | Number of trees removed includes those removed on non-CAISO controlled facilities. Tree count includes only trees > 4 inches Diameter at Breast Height (DBH); smaller trees are counted as brush.
|  | Trees Trimmed | Tree | 39000 | 39000 | None | Number of trees trimmed includes those trimmed on non-CAISO controlled facilities. Tree count includes only trees that are > 4 inches Diameter at Breast Height (DBH); smaller trees are counted as brush. Each year PG&E rounds planned (forecasted) and actual counts for tree trimming.
Overhead Line Structures - Wood Pole | ≈115,000 | [5 empty] | Number of reported facilities includes non-CAISO controlled facilities.
Inspection
|  | Test | Wood Pole | 11837 | 12223 | The number has grown due to over 300 multiple pole structures. | The number of reported planned-tests, includes those performed on non-CAISO controlled facilities.
Maintenance
|  | Treatment | Wood Pole | 10262 | 10499 | Number of actual treatments is dependent upon testing. | Number of actual treatments is dependent upon testing.
|  | Repair | Wood Pole | 205 | 202 | Number of actual repair/reinforcements is dependent upon inspections and testing. | Repair means to reinforce (stub) a wood pole by attaching a steel reinforcing member with hydraulic pressure at, or below, ground level. Poles identified as needing to be repaired will be considered for replacement per normal inspection and test program guidelines.
|  | Replace | Wood Pole | 322 | 334 | The planned total submitted each year is an estimate, 12 more poles were replaced than planned. | Number of planned replacements includes non-CAISO controlled facilities. Replace is defined as: Any whole structure replaced or any single leg within an "H" structure configuration. The planned total submitted each year is an estimate that is dependent on funding, engineering, and the availability of crews to perform the work.
Overhead Line Insulators (contamination control) | N/A | [5 empty] | The number of facilities cannot be determined from records and is noted as N/A. Triggered by condition and trouble.
Maintenance
|  | Wash Insulators | Insulator String | 0 | 7581 | None were planned because the trigger for washing is by condition or trouble. | Number of reported insulator washes includes those performed on non-CAISO controlled facilities.
Underground Line Patrol/Inspection | 57 |  |  |  |  | None | Number of reported facilities includes in-service CAISO controlled facilities.
Inspection
|  | Routine (Monthly) on Pipe-Type Circuits | Line | 396 | 396 | None | Scheduling is based on the filed maintenance practice in effect.
|  | Routine (Quarterly) on XLPE Circuits | Line | 80 | 81 | The difference between the 2016 planned and the 2016 actual is that there was a new XLPE Circuit added in 9/2016. 1 Quarterly was completed. | Scheduling is based on the filed maintenance practice in effect.
|  | Detailed (Annual) on Pipe-Type Circuits | Line | 36 | 36 | None | Scheduling is based on the filed maintenance practice in effect.
|  | Detailed (Bi-Annual) on XLPE Circuits | Line | 4 | 5 | There are 22 XLPE Circuits. A new circuit was added in 2016 ETU.9921 ZA#1 XLPE | Scheduling is based on the filed maintenance practice in effect.
Air Switches | 11000 |  |  |  |  | The difference between 2016 (11,000) and 2017 (11,083) is due to 368 new and 285 removed or not CAISO controlled. (11,000+368-285=11,083) | The number of facilities only includes CAISO controlled facilities.
Inspection
|  | Visual Inspection | Air Switch | N/A | N/A | None | This task is performed as part of the station inspection.
|  | Infrared Inspection | Air Switch | N/A | 5 | None | This task is performed as part of the station infrared inspection.
Diagnostic/Performance Testing
|  | Diagnostic/Performance Test | Air Switch | 65 | 59 | The difference is due to 4 being removed and 2 now having infrared in lieu of Daig. Test. | Triggered by condition and trouble.
Maintenance
|  | Insulation Coating | Air Switch | 0 | 0 | None | Triggered by condition. Performed only in areas at risk of contamination-caused flashovers.
|  | Animal Abatement | Air Switch | 0 | 0 | None | Triggered by condition. Performed as required by local conditions.
|  | Lubricate | Air Switch | 0 | 0 | None | Triggered by condition and trouble.
|  | Mechanism Service | Air Switch | 0 | 0 | None | Triggered by condition and trouble.
|  | Overhaul | Air Switch | 0 | 0 | None | Triggered by condition and trouble.
|  | Repair/Adjustment | Air Switch | 0 | 166 | Triggered by condition and trouble. | Triggered by condition and trouble.
Batteries | 604 |  |  |  |  | The difference between the 2016 total of 604 batteries and the 2017 total of 601 batteries is because 59 were removed, 6 are out of service, and 62 new batteries were installed. (604-59-6+62=601) | Only includes CAISO controlled facilities at stations and does not include chargers. Batteries listed are for stations that have either a circuit breaker, MOAS, or circuit switcher that are CAISO controlled.
Inspection
|  | Visual Inspection | Battery | N/A | N/A | None | This task is performed as part of the station inspection.
Diagnostic/Performance Testing
|  | Diagnostic/Performance Test | Battery | 0 | 0 | None | Triggered by condition and trouble.
|  | Battery Resistance Test or 3 Hour Discharge Test | Battery | 624 | 566 | The difference is due to batteries being removed. | Station batteries are replaced at the end of their service life. Stations upgraded to MPAC may result in additional batteries at the station. With on-going replacement activities and MPAC installations, the total battery maintenance intervals will fluctuate. The new Battery Resistance Test and 3 Hour Discharge Tests are done on a 6-month, 1-year or 6-year cycle depending on battery type.
Maintenance
|  | Replace Cell | Battery | 0 | 2 | Triggered by condition and trouble. | Triggered by condition and trouble.
Circuit Breakers | 3265 |  |  |  |  | The difference between the 2016 total of 3,265 breakers and the 2017 total of 3,371 breakers is because 45 were removed, out of service, or reclassified as not being under CAISO control and 151 breakers are either new or returned to service. (3,265-45+151=3,371) | The total includes both transmission-class and distribution-class breakers that are slated as being under CAISO operational control.
Inspection
|  | Visual Inspection | Circuit Breaker | N/A | N/A | None | This task is performed as part of the station inspection.
|  | Infrared Inspection | Circuit Breaker | N/A | N/A | None | This task is performed as part of the station infrared inspection.
Diagnostic/Performance Testing
|  | Breaker Oil Analysis (BOA) | Breaker | 115 | 106 | Triggered by ACC, condition, and trouble. | Triggered by ACC, condition, and trouble. ACC triggered testing at 50% and 100% ACC. Also performed as part of the mech service on OCB's but is not triggered as a separate event.
|  | Air/SF6 Gas Moisture Test | Breaker | 0 | 1 | Triggered by condition and trouble. | Triggered by ACC, condition, and trouble. ACC triggered testing at 100% ACC.
|  | Exercise | Breaker | 3221 | 3081 | The difference between the number of breakers and the Exercise plans is due to tertiary reactor breakers only having an overhaul plan. | This maintenance task is for all Transmission Class Circuit Breakers regardless of voltage. The total planned for 2016 is an estimate derived from SAP. If a counter change is noted during a station inspection, the updated counter reading will update SAP which will eliminate the need to perform an Exercise. Therefore, the actual Exercises performed during 2016 generally will not match the estimate planned.
|  | SF6 Gas Laboratory Test | Breaker | 0 | 3 | Triggered by condition and trouble. | Triggered by condition and trouble. Tested at 100% ACC and before opening the SF6 tank on condition or trouble.
Maintenance
|  | Insulation Coating | Breaker | 0 | 0 | None | Triggered by condition. Performed only in areas at risk of contamination-caused flashovers.
|  | Animal Abatement | Breaker | 0 | 0 | None | Triggered by condition. Performed as required by local conditions.
|  | Add Oil/Gas | Breaker | 0 | 36 | Triggered by trouble. | Triggered by trouble.
|  | Compressor Service | Breaker | N/A | N/A |  | Triggered by time and installation and is performed as part of the mechanism service on circuit breakers equipped with compressors.
|  | Mechanism Service | Breaker | 344 | 323 | The difference of 11 is due to 8 removed , 1 out of service and 2 being done late in 2015 ahead of schedule. | Triggered by time, condition, and trouble.
|  | Oil or SF6 Gas Leak Repairs | Breaker | 0 | 2 | Triggered by condition. | Triggered by condition.
|  | Overhaul | Breaker | 91 | 28 | Partially triggered by condition. | Triggered by time for tertiary reactor breakers and by ACC or condition for all others.
|  | Repair/Adjustment | Breaker | 0 | 619 | Triggered by condition and trouble. | Triggered by condition and trouble.
Circuit Switchers | 407 |  |  |  |  | The difference between 2016 (407) and 2017 (405) is due to 11 removals and/or reclassification and 9 new or in service. (407-11+9=405) | The number of facilities only includes CAISO controlled facilities.
Inspection
|  | Visual Inspection | Circuit Switcher | N/A | N/A | None | This task is performed as part of the station inspection.
|  | Infrared Inspection | Circuit Switcher | N/A | N/A | None | This task is performed as part of the station Infrared Inspection.
Diagnostic/Performance Testing
|  | Diagnostic/Performance Test | Circuit Switcher | 9 | 2 | The difference is due to 1 being removed and the other 6 are not due until 2017 now. | Triggered by condition and trouble. Performed at 300 operations or 100% ACC.
|  | Mechanism Service | Circuit Switcher | 84 | 80 | The difference is due to 1 being removed and 3 being reclassified as MOAS. | Triggered by ACC, time, condition and trouble. Time triggered once every calendar year for Type A and Type G circuit switchers. Time triggered once every five calendar years for all other type circuit switchers.
Maintenance
|  | Insulation Coating | Circuit Switcher | 0 | 0 | None | Triggered by condition. Performed only in areas at risk of contamination-caused flashovers.
|  | Animal Abatement | Circuit Switcher | 0 | 0 | None | Triggered by condition. Performed as required by local conditions.
|  | Repair/Adjustment | Circuit Switcher | 0 | 19 | Triggered by trouble. | Triggered by trouble.
Load Tap Changer (LTC) Portion of 3-Phase Voltage-Regulating Devices | 157 |  |  |  |  | The difference between 2016 (157) and 2017 (168) is due to 5 new and 6 reclassified. (157+5+6=168) | The number of facilities only includes the voltage regulating portion of CAISO controlled, three-phase, regulating devices.
Inspection
|  | Visual Inspection | LTC | N/A | N/A | None | This task is performed as part of the station inspection.
|  | Infrared Inspection | LTC | N/A | N/A | None | This task is performed as part of the station infrared inspection.
Diagnostic/Performance Testing
|  | Oil Diagnostic Tests - LTC (TASA) | LTC | 170 | 201 | The difference is due to accelerated test results form TJH2B requiring more tests then planned. | Triggered by time, condition, trouble, and installation. Time triggered once every calendar year, once following installation, once following overhaul and once following initial energizing.
Maintenance
|  | Insulation Coating | LTC | 0 | 0 | None | Triggered by condition. Performed only in areas at risk of contamination-caused flashovers.
|  | Animal Abatement | LTC | 0 | 0 | None | Triggered by condition. Performed as required by local conditions.
|  | LTC Overhaul | LTC | 8 | 6 | The difference of 2 is due to one not reaching it's counter threshold and the other no longer requires a default 8 year. | Triggered by operations, condition and trouble per the adopted filed maintenance practice in effect. The planned number submitted is an estimate generated by SAP based projections from counter readings previously entered into the database.
|  | LTC Through Neutral (Step-type Voltage Regulators with Reversing Switches) | LTC | 68 | 41 | The difference is due to LTC's running through neutral before the plan is called and it then resets itself. | Interval is 3, 6, 9, or 12 months as determined by the headquarters based on equipment conditions and history. Some models may not require operations through neutral. The planned number is an estimate by SAP.
|  | Oil Leak Repairs | LTC | 0 | 0 | None | Triggered by condition and trouble.
|  | Repair/Adjustment | LTC | 0 | 43 | Triggered by trouble. | Triggered by trouble.
Motor Operated Air Switches | 720 |  |  |  |  | The difference between 2016 (720) and 2017 (793) is 86 are new or reclassified and 13 were removed and or out of service. (720+86-13=793) | The number of facilities only includes CAISO controlled facilities.
Inspection
|  | Visual Inspection | MOAS | N/A | N/A | None | This task is performed as part of the station inspection.
|  | Infrared Inspection | MOAS | N/A | N/A | None | This task is performed as part of the station Infrared Inspection.
Diagnostic/Performance Testing
|  | Diagnostic/Performance Test | MOAS | 0 | 0 | None | Triggered by trouble.
Maintenance
|  | Insulation Coating | MOAS | 0 | 0 | None | Triggered by condition. Performed only in areas at risk of contamination-caused flashovers.
|  | Animal Abatement | MOAS | 0 | 0 | None | Triggered by condition. Performed as required by local conditions.
|  | Mechanism Service | MOAS | 76 | 70 | The difference of 6 is due to 2 MOAS removed, 1 rescheduled to a 5 year from 4 years due in 2017 and 3 due in 2016 but done in 2015. | Triggered by time, condition and trouble. Time triggered once every five calendar years.
|  | Overhaul | MOAS | 0 | 0 | None | Triggered by condition and trouble.
|  | Repair/Adjustment | MOAS | 0 | 37 | Triggered by trouble. | Triggered by trouble.
Power Transformers | 484 |  |  |  |  | The difference between 2016 (484) and 2017 (493) is due to 4 being removed or out of service, and 13 new being added or reclassified or returned to service. (484-4+13=493) | Includes in-service CAISO controlled transformers and spares in an operating position.
Inspection
|  | Visual Inspection | Transformer | N/A | N/A | None | This task is performed as part of the station inspection.
|  | Infrared Inspection | Transformer | N/A | N/A | None | This task is performed as part of the station infrared inspection.
Diagnostic/Performance Testing
|  | Oil Diagnostic Tests - Main | Transformer | 180 | 226 | The additional tests are due to some transformers being put on a monthly for a period of time and by accelerated TJH2B test results. | Triggered by time, condition, trouble and installation. Time triggered every year for GSU, Atmoseal and 500 kV, every 2 years for FPE and others rated at or above 400 MVA, and every 6 years for all units used as spares, all others in service and any station service bank over 1 MVA. At this time PG&E does not have any station service above 1 MVA.
Maintenance
|  | Insulation Coating | Transformer | 0 | 0 | None | Triggered by condition. Performed only in areas at risk of contamination-caused flashovers.
|  | Animal Abatement | Transformer | 0 | 0 | None | Triggered by condition. Performed as required by local conditions.
|  | Add Make-Up Oil or Nitrogen Gas | Transformer | 0 | 11 | Triggered by condition and trouble. | Triggered by condition and trouble.
|  | Oil Leak Repairs | Transformer | 0 | 0 | None | Triggered by condition and trouble.
|  | Repair/Adjustment | Transformer | 0 | 217 | Triggered by trouble. | Triggered by trouble.
|  | Replace Parts | Transformer | 0 | 5 | Triggered by trouble. | Triggered by trouble.
|  | Spare Transformer Tests | Transformer | 4 | 4 | None | Triggered by time, condition, and trouble. Time triggered once every twelve calendar years.
Protective Relay Schemes | 11302 |  |  |  |  | The difference between 2016 (11,302) and 2017 (11,522) is 220. This is due to 608 new or reclassified schemes and 388 future, out of service, removed, and reclassified schemes. (11,302+608-388=11,522) | Includes CAISO controlled schemes only. This is a snapshot in time and continuously varies.
Transmission Class Trigger Interval
|  | Component performance and scheme functional test | Scheme | 1380 |  |  | Time triggered in accordance with Template/Maintenance Tasks for Relay Schemes. See the adopted maintenance practice for details.
Clean and inspect
|  | Read Voltage/Replace Fuses |  |  | 1181 | The difference of 199 is due to 92 changed to 12 Y maintenance cycle per TD-3323S, 66 were completed in 2015, 12 were duplicates, 9 were not due in 2016 and 20 were removed.
DFR functional test
Communication component and channel performance test
Reactors | 231 |  |  |  |  | The difference between 2016 (231) and 2017 (258) is due to 27 new. | The number of facilities only includes CAISO controlled air-core and oil-filled reactors.
Inspection
|  | Visual Inspection | Reactor | N/A | N/A | None | This task is performed as part of the station inspection.
|  | Infrared Inspection | Reactor | N/A | N/A | None | This task is performed as part of the station Infrared Inspection.
|  | Annual Inspection-Out-of-Service (Air-type Reactors Only) | Reactor | 97 | 73 | The difference is due to 24 Air Core Reactors not requiring any maintenance anymore. | Triggered by time, condition, and trouble. Time triggered once every calendar year.
Diagnostic/Performance Testing
|  | Oil Diagnostic Tests | Reactor | 19 | 19 | None | Triggered by time, condition, trouble, and installation. Time triggered once every six calendar years for 230 kV and below and once every year for 500 kV.
Maintenance
|  | Insulation Coating | Reactor | 0 | 0 | None | Triggered by condition. Performed only in areas at risk of contamination-caused flashovers.
|  | Animal Abatement | Reactor | 0 | 0 | None | Triggered by condition. Performed as required by local conditions.
|  | Add Make-Up Oil or Nitrogen Gas | Reactor | 0 | 0 | None | Triggered by condition and trouble.
|  | Repair/Adjustment | Reactor | 0 | 7 | Triggered by trouble. | Triggered by trouble.
Regulators | 45 |  |  |  |  | There is no difference between 2016 and 2017. | The number of facilities includes the voltage regulating portion of CAISO controlled, single-phase and three-phase, regulating devices as noted.
Inspection
|  | Visual Inspection | Regulator | N/A | N/A | None | This task is performed as part of the station inspection.
|  | Infrared Inspection | Regulator | N/A | N/A | None | This task is performed as part of the station infrared inspection.
Diagnostic/Performance Testing
|  | Oil Diagnostic Tests - Main | Regulator | 26 | 31 | The difference of 5 is due to some oil tests coming back as a higher code and requiring accelerated testing. | Triggered by time, condition, trouble, and installation. This item includes 1-year TDA, 2-year TDA, 6-year TDA, and 6-year oil quality tests. It also includes 1-year TASA on single phase regulators.
Maintenance
|  | Single-Phase Overhaul | Regulator | 3 | 3 | None | Triggered by condition or trouble.
|  | Insulation Coating | Regulator | 0 | 0 | None | Triggered by condition. Performed only in areas at risk of contamination-caused flashovers.
|  | Animal Abatement | Regulator | 0 | 0 | None | Triggered by condition. Performed as required by local conditions.
|  | Add Make-Up Oil or Nitrogen Gas | Regulator | 0 | 0 | None | Triggered by condition and trouble.
Station | 563 |  |  |  |  | There was no difference between the 2016 and 2017. | Includes stations that have either a circuit breaker, MOAS, or circuit switcher that is considered to be under CAISO operational control.
Inspection
|  | Visual Inspection | Station | 6187 | 6182 | The difference of 5 is due to several stations changing the month being read to the correct month. | Substation visual equipment inspections are scheduled on a monthly basis for high criticality substations (Type 1), and every-other-month for low criticality substations (Type 2). The planned number submitted is a count of station inspection plans and is not a one-to-one relationship to the number of stations. Some of the larger stations have more than one plan; e.g. Gates has 2 plans, Cottonwood has 2 plans, Moss Landing has 3 plans, etc.
|  | Infrared Inspection | Station | 562 | 562 | None | Triggered by time, condition and trouble. Time triggered once every calendar year. Infrared Inspection of all station equipment included in this unit.
Station Series Capacitor Banks | 16 |  |  |  |  | There was no difference between the 2016 and 2017. | Series Capacitors
Inspection
|  | Visual Inspection | Series Capacitor | N/A | N/A | None | This task is performed as part of the station inspection.
|  | Infrared Inspection | Series Capacitor | N/A | N/A | None | This task is performed as part of the station Infrared Inspection.
|  | Annual Inspection | Series Capacitor | 16 | 18 | The 2 extra are due to VacaDixon 500KV Series Cap Bank 1 & 2 now being on a semi-annual plan. | Triggered by time, condition and trouble. Time triggered once every calendar year.
Diagnostic/Performance Testing
|  | Breaker Diagnostic Test | Series Capacitor | Counted as part of breakers | Counted as part of breakers | None | Triggered by time, condition, and trouble. Performed on breakers that are an integral part of the capacitor banks and not numbered separately. Time triggered once every calendar year as part of the annual inspection.
Maintenance
|  | Insulation Coating | Series Capacitor | Counted as part of breakers | Counted as part of breakers | None | Triggered by condition. Performed only in areas at risk of contamination-caused flashovers.
|  | Animal Abatement | Series Capacitor | 0 | 0 | None | Triggered by condition. Performed as required by local conditions.
|  | Compressor Service | Series Capacitor | Counted as part of breakers | Counted as part of breakers | None | Triggered by time, condition, and trouble.
|  | Mechanism Service | Series Capacitor | Counted as part of breakers | Counted as part of breakers | None | Triggered by time, condition, and trouble. Time triggered once every calendar year as part of the annual inspection.
|  | Overhaul | Series Capacitor | Counted as part of breakers | Counted as part of breakers | None | Triggered by condition and trouble.
|  | Repair/Adjustment | Series Capacitor | 0 | 12 | Triggered by trouble. | Triggered by trouble.
Station Shunt Capacitor Banks | 109 |  |  |  |  | The difference between 2016 (109) and 2017 (104) is due to 1 new and 6 removed. | The total includes individual steps or phases within transmission-class capacitor bank. Also included is the shunt capacitor portion of the SVC at Paul Sweet Sub and Garberville Sub.
Inspection
|  | Visual Inspection | Shunt Capacitor | N/A | N/A | None | This task is performed as part of the station inspection.
|  | Infrared Inspection | Shunt Capacitor | N/A | N/A | None | This task is performed as part of the station infrared inspection.
|  | Annual Inspection | Shunt Capacitor | 89 | 111 | 21 orders were scheduled in Jan and Feb 2017 but completed in Oct and Nov 2016. | Triggered by time, condition, and trouble. Time triggered once every calendar year.
Maintenance
|  | Insulation Coating | Shunt Capacitor | 0 | 0 | None | Triggered by condition. Performed only in areas at risk of contamination-caused flashovers.
|  | Animal Abatement | Shunt Capacitor | 0 | 0 | None | Triggered by condition. Performed as required by local conditions.
|  | Repair/Adjustment | Shunt Capacitor | 0 | 14 | Triggered by trouble. | Triggered by trouble.
Static VAR Compensator (SVC) & Static Compensator (STATCOM) | 7 |  |  |  |  | There was no difference between the 2016 and 2017. | PG&E has six Static Var Compensators (SVC's): 1) at Newark Substation, 2) at Potrero Substation, 3) at Pueblo Substation, 4) at Humboldt Substation, 5) at Garberville, 6) at Big River. PG&E has one STATCOM at Paul Sweet Substation.
Inspection
|  | Visual Inspection | SVC & STATCOM | N/A | N/A | None | This task is performed as part of the station inspection.
|  | Infrared Inspection | SVC & STATCOM | N/A | N/A | None | This task is performed as part of the station infrared inspection.
|  | SVC Maintenance | SVC & STATCOM | 7 | 6 | Pueblo is on a 2 year cycle and was scheduled in 2016 but was done in August 2015 due to the availability of the manufacturer that does the maintenance. | This task is not included in the adopted filed maintenance practices. This time based interval is set differently based on manufacturer. The time intervals submitted for this report are: 6 months, 12 months, 24 months, 36 months, and 60 months. This information will be clarified when a revised station maintenance practice is submitted.
Diagnostic/Performance Testing
|  | To Be Determined | SVC & STATCOM | N/A | N/A | None | None
Maintenance
|  | To Be Determined | SVC & STATCOM | N/A | N/A | None | None
Synchronous Condensers | 5 |  |  |  |  | The difference between 2016 (5) and 2017 (4) is due to San Mateo Condenser #2 being out of service. | Number of reported facilities includes in-service, CAISO controlled facilities.
Inspection
|  | Visual Inspection | Condenser | N/A | N/A | None | This task is performed as part of the station inspection.
|  | Infrared Inspection | Condenser | N/A | N/A | None | This task is performed as part of the station Infrared Inspection.
|  | Annual Inspection | Condenser | 8 | 7 | The difference of one is due to San Mateo being out of service. | Triggered by time, condition, and trouble. Time: once every 6 months or once per year.
Diagnostic/Performance Testing
|  | Diagnostic/Performance Test | Condenser | N/A | N/A | None | PG&E does not have a "diagnostic/performance test" as a "maintenance task" for condensers. The term diagnostic/performance test is associated with water tests for those condensers with water systems and is maintained as part of the "service" that is done by time, condition, or trouble where the time trigger is 3 years.
Maintenance
|  | Insulation Coating | Condenser | 0 | 0 | None | Triggered by condition. Performed only in areas at risk of contamination-caused flashovers.
|  | Animal Abatement | Condenser | 0 | 0 | None | Triggered by condition. Performed as required by local conditions.
|  | Add Gas | Condenser | 0 | 0 | None | Triggered by condition and trouble.
|  | Oil Leak Repairs | Condenser | 0 | 0 | None | Triggered by condition and trouble.
|  | Repair/Adjustment | Condenser | 0 | 0 | None | Triggered by condition and trouble.
|  | Overhaul | Condenser | 1 | 0 | This one was listed incorrectly as an overhaul when it was really a service. | Triggered by time, condition, and trouble. Time triggered once every six calendar years.
|  | Service | Condenser | 0 | 1 | The 2016 Planning SMR should have listed this as 1 service. | Triggered by time, condition, and trouble. Time triggered once every three calendar years.