## PGE2019SMRS_Actual_Revised
2019 STANDARDIZED MAINTENANCE REPORT - ACTUAL (Revised 6/17/20)
EQUIPMENT TYPE | NO. OF FACILITIES | MAINT. TASK | MAINT. UNIT | PLANNED | ACTUAL | EXCEPTION FROM PLANNED | NOTES
Overhead Line Patrol/Inspection (Lines) | 1389 | [5 empty] | Number of reported facilities includes non-CAISO controlled facilities. The number of facilities in 2018 was 1,398 and the number of facilities in 2019 is 1,389 due to reconfiguration of circuits and some circuits that have been moved to Distribution.
Inspection
|  | Detailed Inspections | Line | 680 | 1193 | Number of inspections includes those performed on non-CAISO controlled facilities. The Wildfire Safety Inspection Program (WSIP) started in late December 2018 and for the 2019 actuals the number of WSIP detail inspections were at 518 Enhanced Inspections and 675 Routine Inspections totaling 1193. There were 5 routine inspections cancelled which were identified and completed on 5 of the enhanced inspections. | Number of inspections includes those performed on non-CAISO controlled facilities.
|  | Ground Inspections | Line | 36 | 36 |  | Number of inspections includes those performed on non-CAISO controlled facilities.
|  | Aerial Inspections | Line | 728 | 1715 | Number of inspections includes those performed on non-CAISO controlled facilities. The Planned patrols were increased due to the Wildfire Safety Inspection Program (WSIP) which began after the Camp Fire. In late December 2018 the new WSIP CIRT (Centralized Inspection Review Team) was established and our normal Routine Air Patrols were increased with Drone Patrols. The new Drone Patrols totaled 997 and the Routine Air Patrols totaled 718. There were ten less then planned Air Patrols as they were completed of the newly created Drone Patrols. There were duplicate patrols completed on several of the same circuits. | Number of inspections includes those performed on non-CAISO controlled facilities.
Overhead Line Patrol/Inspection (Structures) | 183301 | [5 empty] | The number of reported facilities includes non-CAISO controlled facilities. The difference between the 2018 182,533 and 2019 182,301 Planning SMR is attributed to some 2 and 3 Pole structures were removed and replaced with single steel or wood poles structures.
Inspection
|  | Detailed Inspections | Structure | 89942 | 134878 | Number of inspections includes those performed on non-CAISO controlled facilities. The Planned inspections were increased due to the Wildfire Safety Inspection Program (WSIP) which began after the Camp Fire. In late December 2018 the new WSIP CIRT (Centralized Inspection Review Team) was established and our normal Detailed Inspections were increased with Enhanced Detail Inspections. The new Enhanced Detail Inspections totaled 50,137 and the Routine Detailed Inspections totaled 84,741 . There were 5201 less structures completed from the planned count however these were completed on the Enhanced Detailed Inspections. there were several structures that were inspection more than once. | Number of inspections includes those performed on non-CAISO controlled facilities.
|  | Ground Inspections | Structure | 1867 | 1867 |  | Number of inspections includes those performed on non-CAISO controlled facilities.
|  | Aerial Inspections | Structure | 91462 | 144439 | The number of reported facilities includes non-CAISO controlled facilities. The Planned structure numbers were increased due to the Wildfire Safety Inspection Program (WSIP) which began after the Camp Fire. In late December 2018 the new WSIP CIRT (Centralized Inspection Review Team) was established and our normal routine work was increased with Drone Inspections. The 2019 actuals number increased as the new Drone Patrols were added for a total of 52,648 Drone Air Patrols and 91,791 Routine Air Patrols completed for a total of 144,439 structures. | Number of inspections includes those performed on non-CAISO controlled facilities.
|  | Climbing Inspections (2% 500 kV Critical) | Structure | 30 | 11 | There were 19 structures on the Table Mtn-Vaca circuit that were scheduled in June 2019 but were moved out due to resources committed to working the Wildfire Safety Inspection Program corrective work. They were scheduled to complete these structures by the end of the year, however due to weather condition and land owner not making it accessible we could not complete them until 1/28/20. | The number of facilities only includes CAISO controlled facilities. The maintenance interval is every three years.
Overhead Line Vegetation Management/Right-Of-Way Maintenance | N/A | [5 empty] | The planned counts are estimates based on historical information and predictions based on last year’s inspections.
Maintenance
|  | Trees Removed | Tree | 113000 | 229366 | 160,366 were removed as part of additional reliability work. | Number of trees removed includes those removed on non-CAISO controlled facilities. Tree count includes only trees > 4 inches Diameter at Breast Height (DBH); smaller trees are counted as brush.
|  | Trees Trimmed | Tree | 47000 | 35000 | Trees trimmed is subject to change from planned due to natural variability in tree growth rates. | Number of trees trimmed includes those trimmed on non-CAISO controlled facilities. Tree count includes only trees that are > 4 inches Diameter at Breast Height (DBH); smaller trees are counted as brush. Each year PG&E rounds planned (forecasted) and actual counts for tree trimming.
Overhead Line Structures - Wood Pole | ≈115,000 | [5 empty] | Number of reported facilities includes non-CAISO controlled facilities.
Inspection
|  | Test | Wood Pole | 13686 | 10866 | Planned number accounts for the number of structures on the lines being inspected. The approximated wood count was 11,527. The approximated plan is 11k a year. The difference here is due to pole replacement and steel. | The planned approximated forecast is actual wood poles. These poles can be included in 1, 2 and or 3 pole structures which can change the planned count by years end.
Maintenance
|  | Treatment | Wood Pole | 12318 | 9820 | Actual wood pole count was reduced from approximated plan number and within that pole count there were numerous poles less than 10 years old which do not require a treatment. | Number of actual treatments is dependent upon testing. New poles and some rejected poles won’t be treated.
|  | Repair | Wood Pole | 238 | 342 | Moving the reinforcement program to a steady state program required pulling 2020 work forward accounting for a larger reinforcement count. | Repair means to reinforce (stub) a wood pole by attaching a steel reinforcing truss with a pneumatic jack hammer.
|  | Replace | Wood Pole | 1237 | 2464 | Number of planned replacements includes non-CAISO controlled facilities. Replace is defined as: Any whole structure replaced or any single leg within an "H" structure configuration. The planned total submitted each year is an estimate that is dependent on funding, engineering, and the availability of crews to perform the work. The 2019 actual numbers were increased due to the WSIP Enhanced and Drone Inspections that were completed. The planned routine pole replacements that were completed was1034. The Enhanced and Drone Inspections created pole replacement LC's for a total of 1430 structures. | Number of planned replacements includes non-CAISO controlled facilities. Replace is defined as: Any whole structure replaced or any single leg within an "H" structure configuration. The planned total submitted each year is an estimate that is dependent on funding, engineering, and the availability of crews to perform the work.
Overhead Line Insulators (contamination control) | N/A | [5 empty] | The number of facilities cannot be determined from records and is noted as N/A. Triggered by condition and trouble.
Maintenance
|  | Wash Insulators | Insulator String | 0 | 14721 | There were 148 wash orders created. 72 ground washes 3509 insulators and 76 helicopter Air patrols 11,181 insulators. | Number of reported insulator washes includes those performed on non-CAISO controlled facilities. Transmission Line Insulator washing is performed based on local environmental conditions, operating experience and in accordance with pre-determined wash cycles established in SAP.
Underground Line Patrol/Inspection | 57 | [5 empty] | Number of reported facilities includes in-service CAISO controlled facilities.
Inspection
|  | Routine (Monthly) on Pipe-Type Circuits | Line | 394 | 394 |  | Scheduling is based on the filed maintenance practice in effect.
|  | Routine (Quarterly) on XLPE Circuits | Line | 81 | 81 |  | Scheduling is based on the filed maintenance practice in effect.
|  | Detailed (Annual) on Pipe-Type Circuits | Line | 36 | 52 |  | Scheduling is based on the filed maintenance practice in effect.
|  | Detailed (Bi-Annual) on XLPE Circuits | Line | 19 | 19 |  | Scheduling is based on the filed maintenance practice in effect. There are 21 XLPE circuits - 4 bi-annual inspections were completed in 2018, 19 bi-annual inspections will be completed in 2019.
Air Switches | 10882 | [5 empty] | The number of facilities only includes CAISO controlled facilities. The difference between the 2018 total of 10,802 and 2019 total of 10,882 is due to 342 being new and 262 being removed, reclassified, out of service or 3rd party. (10,802+342-262=10,882)
Inspection
|  | Visual Inspection | Air Switch | N/A | N/A |  | This task is performed as part of the station inspection.
|  | Infrared Inspection | Air Switch | N/A | N/A |  | This task is performed as part of the station infrared inspection.
Diagnostic/Performance Testing
|  | Diagnostic/Performance Test | Air Switch | 102 | 117 | 15 additional requested by the HQ. | Triggered by condition and trouble.
Maintenance
|  | Insulation Coating | Air Switch | 0 | 0 |  | Triggered by condition. Performed only in areas at risk of contamination-caused flashovers.
|  | Animal Abatement | Air Switch | 0 | 2 |  | Triggered by condition. Performed as required by local conditions.
|  | Lubricate | Air Switch | 0 | 0 |  | Triggered by condition and trouble.
|  | Mechanism Service | Air Switch | 0 | 0 |  | Triggered by condition and trouble.
|  | Overhaul | Air Switch | 0 | 0 |  | Triggered by condition and trouble.
|  | Repair/Adjustment | Air Switch | 0 | 307 | 186 of the 307 unplanned repair activities were a result of our Wildfire Safety Inspection Program. Please see the Air Switch Notifications Tab for detailed information. | Triggered by condition and trouble.
Batteries | 581 | [5 empty] | Only includes a count of batteries at stations that have an CAISO-controlled Circuit Breaker, or Motor-Operated Air Switch, or Circuit Switcher. This total does not include battery chargers. The difference between the 2018 total of 597 and the 2019 total of 581 is due to 31 being new or reclassified and 47 being removed or out of service. (597+31-47=581)
Inspection
|  | Visual Inspection | Battery | N/A | N/A |  | This task is performed as part of the station inspection.
Diagnostic/Performance Testing
|  | Diagnostic/Performance Test | Battery | 0 | 0 |  | Triggered by condition and trouble.
|  | Battery Resistance Test or 3 Hour Discharge Test | Battery | 634 | 634 |  | Station batteries are replaced at the end of their service life. Stations upgraded to MPAC may result in additional batteries at the station. With on-going replacement activities and MPAC installations, the total battery maintenance intervals will fluctuate. Battery Resistance Tests or 3 Hour Discharge Tests are done on a 6-month, 1-year or 6-year cycle depending on battery type as outlined in the adopted filed maintenance practice.
Maintenance
|  | Replace Cell | Battery | 0 | 0 |  | Triggered by condition and trouble.
|  | Repair/Adjustment | Battery/Charger | 0 | 299 | 20 of the 299 unplanned repair activities were a result of our Wildfire Safety Inspection Program. Please see the Battery & Charger Notifications Tab for detailed information. | Triggered by condition and trouble.
Circuit Breakers | 3493 | [5 empty] | The total includes both transmission-class and distribution-class breakers that are slated as being under CAISO operational control. Of the 3,493 breakers, 375 are operating at 500 kV; 3,118 are operating at or below 230 kV. The difference between the 2018 total of 3,458 and the 2019 total of 3,493 is due to 1 more being reported in 2018 (total should have been 3457); 103 breakers being new or reclassified and 67 being removed or out of service. (3,458-1+103-67=3,493)
Inspection
|  | Visual Inspection | Circuit Breaker | N/A | N/A |  | This task is performed as part of the station inspection.
|  | Infrared Inspection | Circuit Breaker | N/A | N/A |  | This task is performed as part of the station infrared inspection.
Diagnostic/Performance Testing
|  | Breaker Oil Analysis (BOA) | Breaker | 65 | 67 | The difference of 2 is due to 1 additional requested by HQ and 1 additional based on condition. | Triggered by ACC, condition, and trouble. ACC triggered testing at 50% and 100% ACC. Also performed as part of the mech service on OCB's but is not triggered as a separate event.
|  | Air/SF6 Gas Moisture Test | Breaker | 0 | 0 |  | Triggered by ACC, condition, and trouble. ACC triggered testing at 100% ACC.
|  | Exercise | Breaker | 4786 | 4190 |  | All Transmission Class Circuit Breakers have an exercise plan. Tertiary reactor breakers (Distribution Class) do not have an exercise plan but have an overhaul plan. The planned total is always an estimate derived from SAP. It is the total of orders that would be generated to be worked if a counter change is not registered in SAP. When a counter change is noted during a station inspection, the updated counter reading will update SAP which will eliminate the need to perform an exercise. Therefore, the Actual exercises performed during 2019 generally will not match the estimated submitted as Planned.
|  | SF6 Gas Laboratory Test | Breaker | 0 | 0 |  | Triggered by condition and trouble. Tested at 100% ACC and before opening the SF6 tank on condition or trouble.
Maintenance
|  | Insulation Coating | Breaker | 0 | 1 |  | Triggered by condition. Performed only in areas at risk of contamination-caused flashovers.
|  | Animal Abatement | Breaker | 0 | 0 |  | Triggered by condition. Performed as required by local conditions.
|  | Add Oil/Gas | Breaker | 0 | 42 |  | Triggered by trouble.
|  | Compressor Service | Breaker | N/A | N/A |  | Triggered by time and installation and is performed as part of the mechanism service on circuit breakers equipped with compressors.
|  | Mechanism Service | Breaker | 510 | 523 | 510 Planned +18 Additional * 528 (Planned + Additional) 528 - 5 Not done * 523 (2019 Actual) * 18 additional mech services were completed at the request of the local headquarters. * 4 of the 5 not done were due to maintenance plan changes so they were not due in 2019. The remaining 1 had an overhaul performed. | Triggered by time, condition, and trouble.
|  | Oil or SF6 Gas Leak Repairs | Breaker | 0 | 2 |  | Triggered by condition.
|  | Overhaul | Breaker | 37 | 38 | Difference due to 2 additional requested by headquarters and 1 not due yet based on number of operations. | Revised from 591 to 33 due to identified errors in SAP. Triggered by time for tertiary reactor breakers and by ACC or condition for all others.
|  | Repair/Adjustment | Breaker | 0 | 540 |  | Triggered by condition and trouble.
Circuit Switchers | 424 | [5 empty] | The number of facilities only includes CAISO controlled facilities. The difference between the 2018 total of 420 and the 2019 total of 424 is due to 10 being new or reclassified and 6 being removed or placed out of service. (420+10-6=424)
Inspection
|  | Visual Inspection | Circuit Switcher | N/A | N/A |  | This task is performed as part of the station inspection.
|  | Infrared Inspection | Circuit Switcher | N/A | N/A |  | This task is performed as part of the station Infrared Inspection.
Diagnostic/Performance Testing
|  | Diagnostic/Performance Test | Circuit Switcher | 10 | 4 | Difference due to 2 BFD's changed to give headquarter time to complete and 4 not being due yet. | Triggered by condition and trouble. Performed at 300 operations or 100% ACC.
|  | Mechanism Service | Circuit Switcher | 92 | 93 | Difference is due to 1 additional requested by headquarters. | Triggered by ACC, time, condition and trouble. Time triggered once every calendar year for Type A and Type G circuit switchers. Time triggered once every five calendar years for all other type circuit switchers.
Maintenance
|  | Insulation Coating | Circuit Switcher | 0 | 0 |  | Triggered by condition. Performed only in areas at risk of contamination-caused flashovers.
|  | Animal Abatement | Circuit Switcher | 0 | 0 |  | Triggered by condition. Performed as required by local conditions.
|  | Repair/Adjustment | Circuit Switcher | 0 | 34 | 13 of the 34 unplanned repair activities were a result of our Wildfire Safety Inspection Program. Please see the CKSW Notifications Tab for detailed information. | Triggered by trouble.
Load Tap Changer (LTC) Portion of 3-Phase Voltage-Regulating Devices | 242 | [5 empty] | The number of facilities only includes the voltage regulating portion of CAISO controlled, three-phase, regulating devices. The difference between the 2018 total of 237 and the 2019 total of 242 is due to 7 being new and 2 being removed or reclassified. (237+7-2=242)
Inspection
|  | Visual Inspection | LTC | N/A | N/A |  | This task is performed as part of the station inspection.
|  | Infrared Inspection | LTC | N/A | N/A |  | This task is performed as part of the station infrared inspection.
Diagnostic/Performance Testing
|  | Oil Diagnostic Tests - LTC (TASA) | LTC | 281 | 317 | The difference is due to equipment having accelerated TJH2B test results that require additional tests. | Triggered by time, condition, trouble, and installation. Time triggered once every calendar year, once following installation, once following overhaul and once following initial energizing.
Maintenance
|  | Insulation Coating | LTC | 0 | 0 |  | Triggered by condition. Performed only in areas at risk of contamination-caused flashovers.
|  | Animal Abatement | LTC | 0 | 0 |  | Triggered by condition. Performed as required by local conditions.
|  | LTC Inspection | LTC | 20 | 18 | The difference is due to equipment not yet reaching the number of operations required to initiate an order. | Triggered by operations, condition and trouble per the adopted filed maintenance practice in effect. The planned number submitted is an estimate generated by SAP based projections from counter readings previously entered into the database.
|  | LTC Through Neutral (Step-type Voltage Regulators with Reversing Switches) | LTC | 126 | 108 | The difference is due to LTC's running through neutral before an order is called and the plan resets itself. | Interval is 3, 6, 9, or 12 months as determined by the headquarters based on equipment conditions and history. Some models may not require operations through neutral. The planned number is an estimate by SAP.
|  | Oil Leak Repairs | LTC | 0 | 0 |  | Triggered by condition and trouble.
|  | Repair/Adjustment | LTC | 0 | 75 |  | Triggered by trouble.
Motor Operated Air Switches | 804 | [5 empty] | The number of facilities only includes CAISO controlled facilities. The difference between the 2018 total of 792 and the 2019 total of 794 is due to 1 more being reported in 2018 (total should have been 791); 18 being new or reclassified and 5 being removed or reclassified. (792-1+18-5-=804)
Inspection
|  | Visual Inspection | MOAS | N/A | N/A |  | This task is performed as part of the station inspection.
|  | Infrared Inspection | MOAS | N/A | N/A |  | This task is performed as part of the station Infrared Inspection.
Diagnostic/Performance Testing
|  | Diagnostic/Performance Test | MOAS | 0 | 0 |  | Triggered by trouble.
Maintenance
|  | Insulation Coating | MOAS | 0 | 0 |  | Triggered by condition. Performed only in areas at risk of contamination-caused flashovers.
|  | Animal Abatement | MOAS | 0 | 0 |  | Triggered by condition. Performed as required by local conditions.
|  | Mechanism Service | MOAS | 70 | 70 |  | Triggered by time, condition and trouble. Time triggered once every five calendar years.
|  | Overhaul | MOAS | 0 | 0 |  | Triggered by condition and trouble.
|  | Repair/Adjustment | MOAS | 0 | 59 | 16 of the 59 unplanned repair activities were a result of our Wildfire Safety Inspection Program. Please see the MOAS Notifications Tab for detailed information. | Triggered by trouble.
Power Transformers | 588 | [5 empty] | Includes in-service CAISO controlled transformers and spares in an operating position. The difference between the 2018 total of 591 and the 2018 total of 588 is due to 8 being new or reclassified and 11 being removed, reclassified or placed out of service. (591+8-11=588)
Inspection
|  | Visual Inspection | Transformer | N/A | N/A |  | This task is performed as part of the station inspection.
|  | Infrared Inspection | Transformer | N/A | N/A |  | This task is performed as part of the station infrared inspection.
Diagnostic/Performance Testing
|  | Oil Diagnostic Tests - Main | Transformer | 417 | 457 | The difference is due to some equipment being put on a monthly cycle for a period of time and by some equipment having accelerated TJH2B test results that require additional tests. | Triggered by time, condition, trouble and installation. Time triggered every year for GSU, Atmoseal and 500 kV, every 2 years for FPE and others rated at or above 400 MVA, and every 6 years for all units used as spares, all others in service and any station service bank over 1 MVA. At this time PG&E does not have any station service above 1 MVA.
Maintenance
|  | Insulation Coating | Transformer | 0 | 1 |  | Triggered by condition. Performed only in areas at risk of contamination-caused flashovers.
|  | Animal Abatement | Transformer | 0 | 1 |  | Triggered by condition. Performed as required by local conditions.
|  | Add Make-Up Oil or Nitrogen Gas | Transformer | 0 | 8 |  | Triggered by condition and trouble.
|  | Oil Leak Repairs | Transformer | 0 | 0 |  | Triggered by condition and trouble.
|  | Repair/Adjustment | Transformer | 0 | 270 | Increase due to WSIP. | Triggered by trouble.
|  | Replace Parts | Transformer | 0 | 6 |  | Triggered by trouble.
|  | Spare Transformer Tests | Transformer | 2 | 2 |  | Triggered by time, condition, and trouble. Time triggered once every twelve calendar years.
Protective Relay Schemes | 11912 | [5 empty] | Includes CAISO controlled schemes only. This is a snapshot in time and continuously varies. The difference between 2018 (11,836) and 2019 (11,912) is 76. This is due to 718 new or reclassified schemes and 642 future, out of service, removed, and reclassified schemes. (11,836+718-642=11,912)
Transmission Class Trigger Interval
|  | Component performance and scheme functional test | Scheme | 2811 | 2569 | The difference is attributed to: 1) 11 completed early and done in 2018. 2) 50 were tested at various times between 2015-2017 and therefore not due in 2019. The maintenance plans in SAP were reset accordingly. 3) 175 were removed or replaced during 2019. 4) 6 were not completed during 2019 due to grid operational constraints preventing clearance scheduling. 1 was completed in January 2020. The remaining 5 will be completed in 2020. | Time triggered in accordance with Template/Maintenance Tasks for Relay Schemes. See the adopted maintenance practice for details.
Clean and inspect
Read Voltage/Replace Fuses
DFR functional test
Communication component and channel performance test
|  | Repair/Adjustment |  | 0 | 353 |  | Triggered by trouble.
Reactors | 285 | [5 empty] | The number of facilities only includes CAISO controlled air-core and oil-filled reactors. The difference between the 2018 total of 276 and the 2019 total of 285 is due to 11 being new or reclassified and 2 being removed. (276+11-2=285)
Inspection
|  | Visual Inspection | Reactor | N/A | N/A |  | This task is performed as part of the station inspection.
|  | Infrared Inspection | Reactor | N/A | N/A |  | This task is performed as part of the station Infrared Inspection.
|  | Annual Inspection-Out-of-Service (Air-type Reactors Only) | Reactor | 110 | 110 |  | Triggered by time, condition, and trouble. Time triggered once every calendar year.
Diagnostic/Performance Testing
|  | Oil Diagnostic Tests | Reactor | 28 | 30 | The difference is due to equipment having accelerated TJH2B test results that require additional tests. | Triggered by time, condition, trouble, and installation. Time triggered once every six calendar years for 230 kV and below and once every year for 500 kV.
Maintenance
|  | Insulation Coating | Reactor | 0 | 0 |  | Triggered by condition. Performed only in areas at risk of contamination-caused flashovers.
|  | Animal Abatement | Reactor | 0 | 0 |  | Triggered by condition. Performed as required by local conditions.
|  | Add Make-Up Oil or Nitrogen Gas | Reactor | 0 | 0 |  | Triggered by condition and trouble.
|  | Repair/Adjustment | Reactor | 0 | 17 | 3 of the 17 unplanned repair activities were a result of our Wildfire Safety Inspection Program. | Triggered by trouble.
Regulators | 41 | [5 empty] | The number of facilities includes the voltage regulating portion of CAISO controlled, single-phase and three-phase, regulating devices as noted. The difference between the 2018 total of 41 and the 2019 total of 41 is due to 1 being new and 1 being removed. (41+1-1=41)
Inspection
|  | Visual Inspection | Regulator | N/A | N/A |  | This task is performed as part of the station inspection.
|  | Infrared Inspection | Regulator | N/A | NA |  | This task is performed as part of the station infrared inspection.
Diagnostic/Performance Testing
|  | Oil Diagnostic Tests - Main | Regulator | 23 | 27 | The difference is due to equipment having accelerated TJH2B test results that require additional tests. | Triggered by time, condition, trouble, and installation. This item includes 1-year TDA, 2-year TDA, 6-year TDA, and 6-year oil quality tests. It also includes 1-year TASA on single phase regulators.
Maintenance
|  | Single-Phase Inspection | Regulator | 3 | 2 | The difference is due to equipment not yet reaching the number of operations required to initiate an order. | Triggered by condition or trouble.
|  | Insulation Coating | Regulator | 0 | 0 |  | Triggered by condition. Performed only in areas at risk of contamination-caused flashovers.
|  | Animal Abatement | Regulator | 0 | 0 |  | Triggered by condition. Performed as required by local conditions.
|  | Add Make-Up Oil or Nitrogen Gas | Regulator | 0 | 0 |  | Triggered by condition and trouble.
|  | Repair/Adjustment | Regulator | 0 | 20 | 5 of the 20 unplanned repair activities were a result of our Wildfire Safety Inspection Program. | Triggered by condition and trouble.
Station | 562 | [5 empty] | Includes stations that have either a circuit breaker, MOAS, or circuit switcher that is considered to be under CAISO operational control. The difference between the 2018 total of 564 and the 2019 total of 562 is due to 2 being removed. (564-2=562)
Inspection
|  | Visual Inspection | Station | 5571 | 5797 | 12 additional should have been included in the Planned number. 214 additional Drone and Ground Inspections were done for WSIP. | Substation visual equipment inspections are scheduled on a monthly basis for high criticality substations (Type 1), and every-other-month for low criticality substations (Type 2). The planned number submitted is a count of station inspection plans and is not a one-to-one relationship to the number of stations. Some of the larger stations have more than one plan; e.g. Gates has 2 plans, Cottonwood has 2 plans, Moss Landing has 3 plans, etc.
|  | Infrared Inspection | Station | 560 | 563 | 2 additional should have been included in the Planned number. 1 additional requested by headquarters. | Triggered by time, condition and trouble. Time triggered once every calendar year. Infrared Inspection of all station equipment included in this unit.
Station Series Capacitor Banks | 15 | [5 empty] | Series Capacitors. The difference between the 2018 total of 16 and the 2019 total of 15 is due to 1 being new and 2 being removed or out of service. (16+1-2=15)
Inspection
|  | Visual Inspection | Series Capacitor | N/A | N/A |  | This task is performed as part of the station inspection.
|  | Infrared Inspection | Series Capacitor | N/A | N/A |  | This task is performed as part of the station Infrared Inspection.
|  | Annual Inspection | Series Capacitor | 16 | 16 |  | Triggered by time, condition and trouble. Time triggered once every calendar year. VacaDixon 500KV Series Cap Bank 1 is on a semi-annual plan; that is why there are 1 extra.
Diagnostic/Performance Testing
|  | Breaker Diagnostic Test | Series Capacitor | Counted as part of breakers | Counted as part of breakers |  | Triggered by time, condition, and trouble. Performed on breakers that are an integral part of the capacitor banks and not numbered separately. Time triggered once every calendar year as part of the annual inspection.
Maintenance
|  | Insulation Coating | Series Capacitor | Counted as part of breakers | Counted as part of breakers |  | Triggered by condition. Performed only in areas at risk of contamination-caused flashovers.
|  | Animal Abatement | Series Capacitor | 0 | 0 |  | Triggered by condition. Performed as required by local conditions.
|  | Compressor Service | Series Capacitor | Counted as part of breakers | Counted as part of breakers |  | Triggered by time, condition, and trouble.
|  | Mechanism Service | Series Capacitor | Counted as part of breakers | Counted as part of breakers |  | Triggered by time, condition, and trouble. Time triggered once every calendar year as part of the annual inspection.
|  | Overhaul | Series Capacitor | Counted as part of breakers | Counted as part of breakers |  | Triggered by condition and trouble.
|  | Repair/Adjustment | Series Capacitor | 0 | 10 |  | Triggered by trouble.
Station Shunt Capacitor Banks | 104 | [5 empty] | The total includes individual steps or phases within transmission-class capacitor bank. Also included is the shunt capacitor portion of the SVC at Paul Sweet Sub and Garberville Sub. There is no difference between 2018 and 2019.
Inspection
|  | Visual Inspection | Shunt Capacitor | N/A | N/A |  | This task is performed as part of the station inspection.
|  | Infrared Inspection | Shunt Capacitor | N/A | N/A |  | This task is performed as part of the station infrared inspection.
|  | Annual Inspection | Shunt Capacitor | 89 | 89 |  | Triggered by time, condition, and trouble. Time triggered once every calendar year. The difference is due to 15 shunt capacitors are part of the SVC's and the maintenance is done during the SVC maintenance.
Maintenance
|  | Insulation Coating | Shunt Capacitor | 0 | 0 |  | Triggered by condition. Performed only in areas at risk of contamination-caused flashovers.
|  | Animal Abatement | Shunt Capacitor | 0 | 0 |  | Triggered by condition. Performed as required by local conditions.
|  | Repair/Adjustment | Shunt Capacitor | 0 | 18 |  | Triggered by trouble.
Static VAR Compensator (SVC) & Static Compensator (STATCOM) | 7 | [5 empty] | PG&E has six Static Var Compensators (SVC's): 1) at Newark Substation, 2) at Potrero Substation, 3) at Pueblo Substation, 4) at Humboldt Substation, 5) at Garberville, 6) at Big River. PG&E has one STATCOM at Paul Sweet Substation. There is no difference between 2018 and 2019.
Inspection
|  | Visual Inspection | SVC & STATCOM | N/A | N/A |  | This task is performed as part of the station inspection.
|  | Infrared Inspection | SVC & STATCOM | N/A | N/A |  | This task is performed as part of the station infrared inspection.
|  | SVC & STATCOM Inspection/Service | SVC & STATCOM | 7 | 7 |  | Triggered by time as outlined in the adopted filed maintenance practice.
Diagnostic/Performance Testing
|  | To Be Determined | SVC & STATCOM | N/A | N/A |  | None
Maintenance
|  | To Be Determined | SVC & STATCOM | N/A | N/A |  | None
Synchronous Condensers | 4 | [5 empty] | Number of reported facilities includes in-service, CAISO controlled facilities. There is no difference between 2018 and 2019.
Inspection
|  | Visual Inspection | Condenser | N/A | N/A |  | This task is performed as part of the station inspection.
|  | Infrared Inspection | Condenser | N/A | N/A |  | This task is performed as part of the station Infrared Inspection.
|  | Annual Inspection | Condenser | 6 | 6 |  | Triggered by time, condition, and trouble. Time: once every 6 months or once per year.
Diagnostic/Performance Testing
|  | Diagnostic/Performance Test | Condenser | N/A | N/A |  | PG&E does not have a "diagnostic/performance test" as a "maintenance task" for condensers. The term diagnostic/performance test is associated with water tests for those condensers with water systems and is maintained as part of the "service" that is done by time, condition, or trouble where the time trigger is 3 years.
Maintenance
|  | Insulation Coating | Condenser | 0 | 0 |  | Triggered by condition. Performed only in areas at risk of contamination-caused flashovers.
|  | Animal Abatement | Condenser | 0 | 0 |  | Triggered by condition. Performed as required by local conditions.
|  | Add Gas | Condenser | 0 | 0 |  | Triggered by condition and trouble.
|  | Oil Leak Repairs | Condenser | 0 | 0 |  | Triggered by condition and trouble.
|  | Repair/Adjustment | Condenser | 0 | 17 |  | Triggered by condition and trouble.
|  | Overhaul | Condenser | 2 | 2 |  | Triggered by time, condition, and trouble. Time triggered once every six calendar years.
|  | Service | Condenser | 0 | 0 |  | Triggered by time, condition, and trouble. Time triggered once every three calendar years.